## in
[9 empty] | Forecast Demand (MVA) | [5 empty] | Maximum Load at risk (MVA) |  |  |  |  | Energy at risk (MWhr) *
Location | Constraint primary driver | Location of constraint (start) | Location of constraint (end) | Network Element | Evoenergy Feeder Reference | Residential customers affected | Residential customers affected * | Asset rating (MVA) * | 2026 | 2027 | 2028 | 2029 | 2030 | Voltage level | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2027 | 2028 | 2029 | 2030 | Preferred network investment 3 | Preferred network investment capital cost | Preferred annual network investment operating cost | Preferred network investment cost accuracy | Preferred network investment cost accuracy | Proposed timing | Demand reduction required to defer investment by 1 year | Annual Deferral Value | Load transfer capability * | Emergency generation | Historic use of existing emergency response | Historic load trace | Historic asset rating
Canberra CDB - S96 City East | Capacity | -35.270038734229594, 149.10894221312157 | -35.27746335995699, 149.13390552684547 | Feeder | Bunda, Chisholme, Quick, Cooyong, Lonsdale | 3153 | 100% | 23.4 | 33.5 | 33.5 | 33.5 | 33.5 | 33.5 | 11kV | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 1963.0788 | 1963.0788 | 1963.0788 | 1963.0788 | 1963.0788 | Construct 11 kV feeder from Civic zone substation to Section 96 in City East | 8918200 | 8918.2 | 30% | -30% | 2025-04-27 | 10.1 | 507445.58 | 0 MVA | N. A. | * There has been no record of emergency generation use | * Separate Excel spreadsheet | * Historic asset rating is equivalent to current asset rating
Kingston | Capacity | -35.31516949092058, 149.1643202721047 | -35.31479392265627, 149.15216638185203 | Feeder | Monash, Kelliher, Mundarin, Power House, Dairy South | 2708 | 100% | 24.6 | 19.6 | 23.9 | 26.5 | 29.1 | 31.7 | 11kV | 0 | 0 | 1.9 | 4.5 | 7.1 | 15.7272 | 45.7883 | 652.0129 | 2817.6534 | 7302.6564 | Construct 11kV feeder from East Lake Zone Substation to Section 68 Kingston | 1800000 | 1800 | 30% | -30% | 2025-04-28 | 1.9 | 102420 | 0 MVA | N. A. | * There has been no record of emergency generation use | * Separate Excel spreadsheet | * Historic asset rating is equivalent to current asset rating
S63 CBD Section | Capacity | -35.270038734229594, 149.10894221312157 | -35.28001738372406, 149.12727577298799 | Feeder | Electric House, Hobart Short, Edinburgh, Edmund Barton, Hobart Long | 1475 | 100% | 21.6 | 33.6 | 34.1 | 35.1 | 36.1 | 36.1 | 11kV | 12 | 12.5 | 13.5 | 14.5 | 14.5 | 3654.5118 | 3966.7997 | 5327.3148 | 8085.406 | 8085.406 | Construct 11 kV feeder from Civic zone substation to B13 S63 CBD Section | 3836900 | 3836.9 | 30% | -30% | 2025-11-26 | 12.5 | 218319.61 | 0 MVA | N. A. | * There has been no record of emergency generation use | * Separate Excel spreadsheet | * Historic asset rating is equivalent to current asset rating
Fyshwick Sec 38 | Capacity | -35.31516949092058, 149.1643202721047 | -35.32254421917943, 149.16378991760465 | Feeder | Cessnock | 78 | 100% | 3.9 | 5.2 | 7.1 | 9.3 | 11.3 | 14.4 | 11kV | 1.3 | 3.2 | 5.4 | 7.4 | 10.5 | 1.3223 | 71.7096 | 1135.1286 | 3494.9096 | 8598.2619 | Construct 11kV feeder from East Lake Zone Substation to Fyshwick Sec 38 | 791654.31 | 791.65 | 30% | -30% | 2025-11-26 | 3.2 | 45045.13 | 0 MVA | N. A. | * There has been no record of emergency generation use | * Separate Excel spreadsheet | * Historic asset rating is equivalent to current asset rating
Lyneham | Capacity | -35.270038734229594, 149.10894221312157 | -35.232770456394476, 149.13370257159178 | Feeder | Swinden, Cowper, Ebden, Duffy | 5873 | 100% | 17.7 | 20.1 | 22 | 23.3 | 25.2 | 25.2 | 11kV | 2.4 | 4.3 | 5.6 | 7.5 | 7.5 | 15.4441 | 39.6798 | 88.8035 | 243.7896 | 243.7896 | Construct 11 kV feeder from Civic zone substation to Lyneham- Canberra Racing Club | 4296631.16 | 4296.63 | 30% | -30% | 2025-04-27 | 4.3 | 244478.31 | 0 MVA | N. A. | * There has been no record of emergency generation use | * Separate Excel spreadsheet | * Historic asset rating is equivalent to current asset rating
Diplomatic Development - Curtin | Capacity | -35.33366738348781, 149.07080620008202 | -35.31633542120226, 149.0775211402255 | Feeder | Yarralumla, Curtin North | 2752 | 100% | 9.3 | 12.5 | 14.6 | 18.1 | 19.2 | 19.2 | 11kV | 3.2 | 5.3 | 8.8 | 9.9 | 9.9 | 7.9326 | 89.0768 | 550.2462 | 687.5076 | 687.5076 | Construct 11 kV feeder from Woden zone substation to Diplomatic Development - Curtin | 8400000 | 8400 | 30% | -30% | 2025-04-28 | 8.8 | 477960 | 0 MVA | N. A. | * There has been no record of emergency generation use | * Separate Excel spreadsheet | * Historic asset rating is equivalent to current asset rating
Woden Town Centre | Capacity | -35.38378812773289, 149.09572263927498 | -35.34223110154254, 149.08557901613392 | Feeder | Devonport, Launceston | 1624 | 100% | 10.1 | 10 | 12.8 | 14.1 | 14.6 | 15.5 | 11kV | 0 | 2.7 | 4 | 4.5 | 5.4 | 0 | 243.4392 | 321.0011 | 416.7842 | 737.6021 | Construct 11 kV feeder from Wanniassa zone substation to Woden Town Centre | 9333000 | 9333 | 30% | -30% | 2025-04-30 | 5.4 | 531047.7 | 0 MVA | N. A. | * There has been no record of emergency generation use | * Separate Excel spreadsheet | * Historic asset rating is equivalent to current asset rating
Fairbairn | Capacity | -35.31516949092058, 149.1643202721047 | -35.30730754030097, 149.2056643301586 | Feeder | Dairy North, Aero Park | 270 | 100% | 7.6 | 10.08 | 10.83 | 11.03 | 11.23 | 11.43 | 11kV | 2.48 | 3.23 | 3.43 | 3.63 | 3.83 | 454.6833 | 1515.3618 | 1828.3099 | 2173.356 | 2558.9018 | Construct 11kV feeder from East Lake Zone Substation to Substation 11502 on Tindal Lane | 7700000 | 7700 | 30% | -30% | 2025-11-26 | 3.23 | 438130 | 0 MVA | N. A. | * There has been no record of emergency generation use | * Separate Excel spreadsheet | * Historic asset rating is equivalent to current asset rating
Hume West | Capacity | -35.40995842668535, 149.14139036955441 | -35.40503530605064, 149.1554267508863 | Feeder | Alderson, Tralee | 689 | 100% | 10.1 | 12.9 | 14.4 | 15.8 | 17.3 | 17.3 | 11kV | 2.8 | 4.3 | 5.7 | 7.2 | 7.2 | 58.8595 | 677.0341 | 2359.7869 | 5459.9055 | 5459.9055 | Construct 11kV feeder from Gilmore Zone Substation to Hume West | 2799900 | 2799.9 | 30% | -30% | 2025-11-26 | 4.3 | 159314.31 | 0 MVA | N. A. | * There has been no record of emergency generation use | * Separate Excel spreadsheet | * Historic asset rating is equivalent to current asset rating
Parkes | Capacity | -35.26934637646486, 149.14978246394512 | -35.29107792153859, 149.14282956857284 | Feeder | Wolseley, Quick, Bowen | 2779 | 100% | 13.5 | 19.7 | 20.1 | 20.6 | 21 | 21.4 | 11kV | 6.2 | 6.6 | 7.1 | 7.5 | 7.9 | 556.5598 | 639.6902 | 870.8912 | 988.1129 | 1171.9352 | Construct 11kV feeder from City East Zone Substation to Canberra CBD S3 & S37 Parkes | 8503400 | 8503.4 | 30% | -30% | 2025-04-27 | 6.6 | 483843.46 | 0 MVA | N. A. | * There has been no record of emergency generation use | * Separate Excel spreadsheet | * Historic asset rating is equivalent to current asset rating
Gungahlin Town Centre | Capacity | -35.17207129278421, 149.1164807071082 | -35.18506605850052, 149.1443413014763 | Feeder | Valley, Gribble, Riley, Gungahlin, Nona, West Street, Hamer, Anthony Rolfe , Flemington | 14411 | 100% | 45.8 | 64.8 | 66.9 | 67.3 | 67.8 | 67.8 | 11kV | 19 | 21.1 | 21.5 | 22 | 22 | 1380.2705 | 2625.2724 | 2990.7479 | 3077.2829 | 3077.2829 | Construct 11kV feeder from Gold Creek zone substation to Gungahlin | 6700000 | 6700 | 30% | -30% | 2025-11-26 | 21.1 | 381230 | 0 MVA | N. A. | * There has been no record of emergency generation use | * Separate Excel spreadsheet | * Historic asset rating is equivalent to current asset rating
Braddon | Capacity | -35.26934637646486, 149.14978246394512 | -35.27532734261299, 149.13094252722405 | Feeder | Braddon, Ijong, Haig, Lonsdale | 4646 | 100% | 19.6 | 21.52 | 23.32 | 24.16 | 24.25 | 24.4 | 11kV | 1.92 | 3.72 | 4.56 | 4.65 | 4.8 | 81.4243 | 244.3684 | 562.3928 | 695.0455 | 915.2866 | Construct 11kV feeder from City East Zone Substation to Braddon | 2200000 | 2200 | 30% | -30% | 1933-04-01 | 4.8 | 125180 | 0 MVA | N. A. | * There has been no record of emergency generation use | * Separate Excel spreadsheet | * Historic asset rating is equivalent to current asset rating
Watson | Capacity | -35.26934637646486, 149.14978246394512 | -35.242052462158256, 149.1621035167452 | Feeder | Mackenzie, Stott | 4159 | 100% | 9.6 | 12.9 | 13.59 | 15.02 | 16.55 | 16.6 | 11kV | 3.3 | 3.99 | 5.42 | 6.95 | 7 | 51.2669 | 119.9645 | 460.3727 | 1173.2094 | 1301.4528 | Construct 11kV feeder from City East Zone Substation to Watson | 8600000 | 8600 | 30% | -30% | 2025-04-30 | 7 | 489340 | 0 MVA | N. A. | * There has been no record of emergency generation use | * Separate Excel spreadsheet | * Historic asset rating is equivalent to current asset rating
Ainslie | Capacity | -35.26934637646486, 149.14978246394512 | -35.24885622899876, 149.13943312982752 | Feeder | Cowper, Wakefield, Ebden | 5128 | 100% | 13.7 | 20.47 | 20.98 | 22.12 | 23.2 | 23.27 | 11kV | 6.77 | 7.28 | 8.42 | 9.5 | 9.57 | 298.5603 | 341.6277 | 545.6549 | 939.5229 | 1060.184 | Construct 11kV feeder from City East Zone Substation to Ainslie | 6600000 | 6600 | 30% | -30% | 2025-04-30 | 9.57 | 375540 | 0 MVA | N. A. | * There has been no record of emergency generation use | * Separate Excel spreadsheet | * Historic asset rating is equivalent to current asset rating
Franklin | Capacity | -35.17207129278421, 149.1164807071082 | -35.189778277436936, 149.15983259672217 | Feeder | Nona , Hamer, Anthony Rolfe | 8207 | 100% | 15.6 | 21.36 | 21.37 | 21.4 | 21.85 | 22.33 | 11kV | 5.76 | 5.77 | 5.8 | 6.25 | 6.73 | 397.2994 | 419.9405 | 451.0033 | 625.9227 | 823.7614 | Construct 11kV feeder from Gold Creek to Franklin | 7155300 | 7155.3 | 30% | -30% | 2025-11-26 | 5.77 | 407136.57 | 0 MVA | N. A. | * There has been no record of emergency generation use | * Separate Excel spreadsheet | * Historic asset rating is equivalent to current asset rating
Canberra CBD | Capacity | -35.270038734229594, 149.10894221312157 | -35.284236680317235, 149.12917423916693 | Feeder | Hobart Short , Binara, Electricity House, Edinburgh, Akuna, Edmund Barton, Lonsdale, King Edward+Belmore | 4113 | 100% | 36.1 | 36.19 | 43.17 | 46.18 | 47.14 | 48.49 | 11kV | 0.09 | 7.07 | 10.08 | 11.04 | 12.39 | 1328.8355 | 2012.6793 | 3416.4208 | 3961.102 | 4858.8762 | Construct 11kV feeder from Civic Zone Substation to Canberra CBD (Feeder 1) | 3836900 | 3836.9 | 30% | -30% | 2025-11-26 | 7.07 | 218319.61 | 0 MVA | N. A. | * There has been no record of emergency generation use | * Separate Excel spreadsheet | * Historic asset rating is equivalent to current asset rating
Molonglo Valley | Capacity | -35.27023133253801, 149.05790206360584 | -35.27023133253801, 149.05790206360584 | Power Trasnfromer | Streeton, Black Mountain, Hilder, Belconnen Way South | 9423 | 100% | 55 | 53.3 | 56 | 57.7 | 59.5 | 61.4 | 132/ 11kV | 0 | 1 | 2.7 | 4.5 | 6.4 | 7801.5904 | 9389.6989 | 10686.2304 | 12205.5531 | 13912.0196 | Install second transformer at Molonglo ZS | 15500000 | 15500 | 30% | -30% | 2025-04-29 | 4.5 | 881950 | 0 MVA | N. A. | * There has been no record of emergency generation use | * Separate Excel spreadsheet | * Historic asset rating is equivalent to current asset rating
Strathnairn | Capacity | -35.222922176612315, 148.99660672667787 | -35.222922176612315, 148.99660672667787 | Zone Substation & Feeders | Weir, Macrossan, Latham | 4154 | 100% | 13.3 | 20.3 | 21.7 | 22.6 | 23.6 | 25.2 | 132/ 11kV | 7 | 8.4 | 9.3 | 10.3 | 11.9 | 999.6433 | 1259.8499 | 1875.7511 | 2700.6083 | 4523.1716 | Construct 132kV/11kV zone substation and associated feeders in Stathnairn | 68545700 | 68545.7 | 30% | -30% | 2025-04-30 | 11.9 | 3900250.33 | 0 MVA | N. A. | * There has been no record of emergency generation use | * Separate Excel spreadsheet | * Historic asset rating is equivalent to current asset rating