## Annual Load
| Peak Demand | 3.3914 | 2024-02-13 14:00 |  | Summer |  | Peak Demand | 5.9787 | 2024-09-22 10:00 |  | Winter
| Dairy North | [5 empty] | Aero Park
| Historical Load (MVA/MW) | [5 empty] | Historical Load (MVA/MW)
Timestamp | 2024 | 2026 | 2027 | 2028 | 2029 | Timestamp | 2024 | 2026 | 2027 | 2028 | 2029
2024-01-01 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2023-11-01 | 1.5166 | 1.797 | 1.797 | 1.797 | 1.797
2024-01-01 01:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2023-11-01 01:00 | 1.5128 | 1.7925 | 1.7925 | 1.7925 | 1.7925
2024-01-01 02:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2023-11-01 02:00 | 1.5052 | 1.7835 | 1.7835 | 1.7835 | 1.7835
2024-01-01 03:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2023-11-01 03:00 | 1.7566 | 2.0815 | 2.0815 | 2.0815 | 2.0815
2024-01-01 04:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2023-11-01 04:00 | 1.9167 | 2.2711 | 2.2711 | 2.2711 | 2.2711
2024-01-01 05:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2023-11-01 05:00 | 2.0996 | 2.4878 | 2.4878 | 2.4878 | 2.4878
2024-01-01 06:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2023-11-01 06:00 | 2.2139 | 2.6233 | 2.6233 | 2.6233 | 2.6233
2024-01-01 07:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2023-11-01 07:00 | 2.5988 | 3.0793 | 3.0793 | 3.0793 | 3.0793
2024-01-01 08:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2023-11-01 08:00 | 2.9798 | 3.5308 | 3.5308 | 3.5308 | 3.5308
2024-01-01 09:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2023-11-01 09:00 | 3.2085 | 3.8017 | 3.8017 | 3.8017 | 3.8017
2024-01-01 10:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2023-11-01 10:00 | 2.7702 | 3.2825 | 3.2825 | 3.2825 | 3.2825
2024-01-01 11:00 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2023-11-01 11:00 | 2.8236 | 3.3457 | 3.3457 | 3.3457 | 3.3457
2024-01-01 12:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2023-11-01 12:00 | 2.8388 | 3.3638 | 3.3638 | 3.3638 | 3.3638
2024-01-01 13:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2023-11-01 13:00 | 2.7512 | 3.2599 | 3.2599 | 3.2599 | 3.2599
2024-01-01 14:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2023-11-01 14:00 | 2.8083 | 3.3277 | 3.3277 | 3.3277 | 3.3277
2024-01-01 15:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2023-11-01 15:00 | 2.8236 | 3.3457 | 3.3457 | 3.3457 | 3.3457 | f
2024-01-01 16:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2023-11-01 16:00 | 3.2847 | 3.892 | 3.892 | 3.892 | 3.892
2024-01-01 17:00 | 1.6957 | 2.1094 | 2.5485 | 2.6071 | 2.6656 | 2023-11-01 17:00 | 3.2542 | 3.8559 | 3.8559 | 3.8559 | 3.8559
2024-01-01 18:00 | 1.6957 | 2.1094 | 2.5485 | 2.6071 | 2.6656 | 2023-11-01 18:00 | 2.9874 | 3.5399 | 3.5399 | 3.5399 | 3.5399
2024-01-01 19:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2023-11-01 19:00 | 2.5797 | 3.0567 | 3.0567 | 3.0567 | 3.0567
2024-01-01 20:00 | 1.7909 | 2.2279 | 2.6917 | 2.7535 | 2.8154 | 2023-11-01 20:00 | 2.6674 | 3.1606 | 3.1606 | 3.1606 | 3.1606
2024-01-01 21:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2023-11-01 21:00 | 2.4845 | 2.9439 | 2.9439 | 2.9439 | 2.9439
2024-01-01 22:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2023-11-01 22:00 | 1.9929 | 2.3614 | 2.3614 | 2.3614 | 2.3614
2024-01-01 23:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2023-11-01 23:00 | 1.8329 | 2.1718 | 2.1718 | 2.1718 | 2.1718
2024-01-02 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2023-11-02 | 1.5433 | 1.8286 | 1.8286 | 1.8286 | 1.8286
2024-01-02 01:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2023-11-02 01:00 | 1.5814 | 1.8738 | 1.8738 | 1.8738 | 1.8738
2024-01-02 02:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2023-11-02 02:00 | 1.5204 | 1.8015 | 1.8015 | 1.8015 | 1.8015
2024-01-02 03:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2023-11-02 03:00 | 1.7414 | 2.0634 | 2.0634 | 2.0634 | 2.0634
2024-01-02 04:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2023-11-02 04:00 | 1.89 | 2.2395 | 2.2395 | 2.2395 | 2.2395
2024-01-02 05:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2023-11-02 05:00 | 2.1529 | 2.5511 | 2.5511 | 2.5511 | 2.5511
2024-01-02 06:00 | 2.0005 | 2.4886 | 3.0067 | 3.0758 | 3.1448 | 2023-11-02 06:00 | 2.1377 | 2.533 | 2.533 | 2.533 | 2.533
2024-01-02 07:00 | 2.2863 | 2.8441 | 3.4362 | 3.5152 | 3.5941 | 2023-11-02 07:00 | 2.4578 | 2.9123 | 2.9123 | 2.9123 | 2.9123
2024-01-02 08:00 | 2.4387 | 3.0337 | 3.6653 | 3.7495 | 3.8337 | 2023-11-02 08:00 | 2.8198 | 3.3412 | 3.3412 | 3.3412 | 3.3412
2024-01-02 09:00 | 2.3816 | 2.9626 | 3.5794 | 3.6616 | 3.7439 | 2023-11-02 09:00 | 2.8884 | 3.4225 | 3.4225 | 3.4225 | 3.4225
2024-01-02 10:00 | 2.3054 | 2.8678 | 3.4648 | 3.5445 | 3.6241 | 2023-11-02 10:00 | 2.5988 | 3.0793 | 3.0793 | 3.0793 | 3.0793
2024-01-02 11:00 | 2.3816 | 2.9626 | 3.5794 | 3.6616 | 3.7439 | 2023-11-02 11:00 | 2.6559 | 3.1471 | 3.1471 | 3.1471 | 3.1471
2024-01-02 12:00 | 2.5721 | 3.1996 | 3.8657 | 3.9546 | 4.0434 | 2023-11-02 12:00 | 2.7779 | 3.2915 | 3.2915 | 3.2915 | 3.2915
2024-01-02 13:00 | 2.6674 | 3.3181 | 4.0089 | 4.101 | 4.1931 | 2023-11-02 13:00 | 2.9341 | 3.4767 | 3.4767 | 3.4767 | 3.4767
2024-01-02 14:00 | 2.6293 | 3.2707 | 3.9516 | 4.0424 | 4.1332 | 2023-11-02 14:00 | 3.0522 | 3.6166 | 3.6166 | 3.6166 | 3.6166
2024-01-02 15:00 | 2.553 | 3.1759 | 3.8371 | 3.9253 | 4.0134 | 2023-11-02 15:00 | 3.1018 | 3.6753 | 3.6753 | 3.6753 | 3.6753
2024-01-02 16:00 | 2.6293 | 3.2707 | 3.9516 | 4.0424 | 4.1332 | 2023-11-02 16:00 | 3.3533 | 3.9733 | 3.9733 | 3.9733 | 3.9733
2024-01-02 17:00 | 2.3816 | 2.9626 | 3.5794 | 3.6616 | 3.7439 | 2023-11-02 17:00 | 3.4028 | 4.032 | 4.032 | 4.032 | 4.032
2024-01-02 18:00 | 2.1339 | 2.6545 | 3.2071 | 3.2808 | 3.3545 | 2023-11-02 18:00 | 3.0522 | 3.6166 | 3.6166 | 3.6166 | 3.6166
2024-01-02 19:00 | 1.9053 | 2.3701 | 2.8635 | 2.9293 | 2.9951 | 2023-11-02 19:00 | 2.5988 | 3.0793 | 3.0793 | 3.0793 | 3.0793
2024-01-02 20:00 | 1.7338 | 2.1568 | 2.6058 | 2.6657 | 2.7255 | 2023-11-02 20:00 | 2.4349 | 2.8852 | 2.8852 | 2.8852 | 2.8852
2024-01-02 21:00 | 1.6957 | 2.1094 | 2.5485 | 2.6071 | 2.6656 | 2023-11-02 21:00 | 2.4845 | 2.9439 | 2.9439 | 2.9439 | 2.9439
2024-01-02 22:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2023-11-02 22:00 | 1.9472 | 2.3072 | 2.3072 | 2.3072 | 2.3072
2024-01-02 23:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2023-11-02 23:00 | 1.6881 | 2.0002 | 2.0002 | 2.0002 | 2.0002
2024-01-03 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2023-11-03 | 1.5623 | 1.8512 | 1.8512 | 1.8512 | 1.8512
2024-01-03 01:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2023-11-03 01:00 | 1.589 | 1.8828 | 1.8828 | 1.8828 | 1.8828
2024-01-03 02:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2023-11-03 02:00 | 1.5509 | 1.8377 | 1.8377 | 1.8377 | 1.8377
2024-01-03 03:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2023-11-03 03:00 | 1.7414 | 2.0634 | 2.0634 | 2.0634 | 2.0634
2024-01-03 04:00 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2023-11-03 04:00 | 1.8595 | 2.2034 | 2.2034 | 2.2034 | 2.2034
2024-01-03 05:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2023-11-03 05:00 | 2.1453 | 2.542 | 2.542 | 2.542 | 2.542
2024-01-03 06:00 | 1.8481 | 2.299 | 2.7776 | 2.8414 | 2.9052 | 2023-11-03 06:00 | 2.4006 | 2.8445 | 2.8445 | 2.8445 | 2.8445
2024-01-03 07:00 | 2.3625 | 2.9389 | 3.5508 | 3.6323 | 3.7139 | 2023-11-03 07:00 | 2.5873 | 3.0658 | 3.0658 | 3.0658 | 3.0658
2024-01-03 08:00 | 2.5721 | 3.1996 | 3.8657 | 3.9546 | 4.0434 | 2023-11-03 08:00 | 3.1284 | 3.7069 | 3.7069 | 3.7069 | 3.7069
2024-01-03 09:00 | 2.5149 | 3.1285 | 3.7798 | 3.8667 | 3.9535 | 2023-11-03 09:00 | 3.1322 | 3.7114 | 3.7114 | 3.7114 | 3.7114
2024-01-03 10:00 | 2.6674 | 3.3181 | 4.0089 | 4.101 | 4.1931 | 2023-11-03 10:00 | 3.1894 | 3.7792 | 3.7792 | 3.7792 | 3.7792
2024-01-03 11:00 | 2.6674 | 3.3181 | 4.0089 | 4.101 | 4.1931 | 2023-11-03 11:00 | 2.8807 | 3.4134 | 3.4134 | 3.4134 | 3.4134
2024-01-03 12:00 | 2.6483 | 3.2944 | 3.9803 | 4.0717 | 4.1632 | 2023-11-03 12:00 | 3.1894 | 3.7792 | 3.7792 | 3.7792 | 3.7792
2024-01-03 13:00 | 2.8579 | 3.5551 | 4.2953 | 4.3939 | 4.4926 | 2023-11-03 13:00 | 3.1513 | 3.734 | 3.734 | 3.734 | 3.734
2024-01-03 14:00 | 2.7817 | 3.4603 | 4.1807 | 4.2768 | 4.3728 | 2023-11-03 14:00 | 3.6428 | 4.3165 | 4.3165 | 4.3165 | 4.3165
2024-01-03 15:00 | 2.7245 | 3.3892 | 4.0948 | 4.1889 | 4.283 | 2023-11-03 15:00 | 3.5819 | 4.2442 | 4.2442 | 4.2442 | 4.2442
2024-01-03 16:00 | 2.7817 | 3.4603 | 4.1807 | 4.2768 | 4.3728 | 2023-11-03 16:00 | 3.4257 | 4.0591 | 4.0591 | 4.0591 | 4.0591
2024-01-03 17:00 | 2.6864 | 3.3418 | 4.0375 | 4.1303 | 4.2231 | 2023-11-03 17:00 | 3.2504 | 3.8514 | 3.8514 | 3.8514 | 3.8514
2024-01-03 18:00 | 2.3244 | 2.8915 | 3.4935 | 3.5737 | 3.654 | 2023-11-03 18:00 | 2.8884 | 3.4225 | 3.4225 | 3.4225 | 3.4225
2024-01-03 19:00 | 1.9624 | 2.4412 | 2.9494 | 3.0172 | 3.0849 | 2023-11-03 19:00 | 2.755 | 3.2644 | 3.2644 | 3.2644 | 3.2644
2024-01-03 20:00 | 1.7909 | 2.2279 | 2.6917 | 2.7535 | 2.8154 | 2023-11-03 20:00 | 2.6445 | 3.1335 | 3.1335 | 3.1335 | 3.1335
2024-01-03 21:00 | 1.6957 | 2.1094 | 2.5485 | 2.6071 | 2.6656 | 2023-11-03 21:00 | 2.2901 | 2.7136 | 2.7136 | 2.7136 | 2.7136
2024-01-03 22:00 | 1.7528 | 2.1805 | 2.6344 | 2.695 | 2.7555 | 2023-11-03 22:00 | 1.9853 | 2.3524 | 2.3524 | 2.3524 | 2.3524
2024-01-03 23:00 | 1.7338 | 2.1568 | 2.6058 | 2.6657 | 2.7255 | 2023-11-03 23:00 | 1.7376 | 2.0589 | 2.0589 | 2.0589 | 2.0589
2024-01-04 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2023-11-04 | 1.7376 | 2.0589 | 2.0589 | 2.0589 | 2.0589
2024-01-04 01:00 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2023-11-04 01:00 | 1.8862 | 2.235 | 2.235 | 2.235 | 2.235
2024-01-04 02:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2023-11-04 02:00 | 1.7757 | 2.1041 | 2.1041 | 2.1041 | 2.1041
2024-01-04 03:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2023-11-04 03:00 | 1.7795 | 2.1086 | 2.1086 | 2.1086 | 2.1086
2024-01-04 04:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2023-11-04 04:00 | 1.8062 | 2.1402 | 2.1402 | 2.1402 | 2.1402
2024-01-04 05:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2023-11-04 05:00 | 2.2215 | 2.6323 | 2.6323 | 2.6323 | 2.6323
2024-01-04 06:00 | 1.9053 | 2.3701 | 2.8635 | 2.9293 | 2.9951 | 2023-11-04 06:00 | 2.1834 | 2.5872 | 2.5872 | 2.5872 | 2.5872
2024-01-04 07:00 | 2.3625 | 2.9389 | 3.5508 | 3.6323 | 3.7139 | 2023-11-04 07:00 | 2.1377 | 2.533 | 2.533 | 2.533 | 2.533
2024-01-04 08:00 | 2.4768 | 3.0811 | 3.7226 | 3.8081 | 3.8936 | 2023-11-04 08:00 | 2.614 | 3.0974 | 3.0974 | 3.0974 | 3.0974
2024-01-04 09:00 | 2.534 | 3.1522 | 3.8085 | 3.896 | 3.9835 | 2023-11-04 09:00 | 2.7741 | 3.287 | 3.287 | 3.287 | 3.287
2024-01-04 10:00 | 2.6293 | 3.2707 | 3.9516 | 4.0424 | 4.1332 | 2023-11-04 10:00 | 3.0294 | 3.5895 | 3.5895 | 3.5895 | 3.5895
2024-01-04 11:00 | 2.6102 | 3.247 | 3.923 | 4.0131 | 4.1033 | 2023-11-04 11:00 | 3.0103 | 3.567 | 3.567 | 3.567 | 3.567
2024-01-04 12:00 | 2.4578 | 3.0574 | 3.6939 | 3.7788 | 3.8637 | 2023-11-04 12:00 | 3.1894 | 3.7792 | 3.7792 | 3.7792 | 3.7792
2024-01-04 13:00 | 2.4197 | 3.01 | 3.6367 | 3.7202 | 3.8038 | 2023-11-04 13:00 | 2.957 | 3.5037 | 3.5037 | 3.5037 | 3.5037
2024-01-04 14:00 | 2.4006 | 2.9863 | 3.608 | 3.6909 | 3.7738 | 2023-11-04 14:00 | 2.9722 | 3.5218 | 3.5218 | 3.5218 | 3.5218
2024-01-04 15:00 | 2.5721 | 3.1996 | 3.8657 | 3.9546 | 4.0434 | 2023-11-04 15:00 | 2.915 | 3.4541 | 3.4541 | 3.4541 | 3.4541
2024-01-04 16:00 | 2.4197 | 3.01 | 3.6367 | 3.7202 | 3.8038 | 2023-11-04 16:00 | 2.7055 | 3.2057 | 3.2057 | 3.2057 | 3.2057
2024-01-04 17:00 | 2.2482 | 2.7967 | 3.3789 | 3.4566 | 3.5342 | 2023-11-04 17:00 | 2.534 | 3.0026 | 3.0026 | 3.0026 | 3.0026
2024-01-04 18:00 | 1.9815 | 2.4649 | 2.9781 | 3.0465 | 3.1149 | 2023-11-04 18:00 | 2.3358 | 2.7678 | 2.7678 | 2.7678 | 2.7678
2024-01-04 19:00 | 1.7338 | 2.1568 | 2.6058 | 2.6657 | 2.7255 | 2023-11-04 19:00 | 2.3168 | 2.7452 | 2.7452 | 2.7452 | 2.7452
2024-01-04 20:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2023-11-04 20:00 | 2.0005 | 2.3704 | 2.3704 | 2.3704 | 2.3704
2024-01-04 21:00 | 1.7147 | 2.1331 | 2.5772 | 2.6364 | 2.6956 | 2023-11-04 21:00 | 1.8824 | 2.2305 | 2.2305 | 2.2305 | 2.2305
2024-01-04 22:00 | 1.7147 | 2.1331 | 2.5772 | 2.6364 | 2.6956 | 2023-11-04 22:00 | 2.0005 | 2.3704 | 2.3704 | 2.3704 | 2.3704
2024-01-04 23:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2023-11-04 23:00 | 1.8024 | 2.1357 | 2.1357 | 2.1357 | 2.1357
2024-01-05 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2023-11-05 | 1.7719 | 2.0995 | 2.0995 | 2.0995 | 2.0995
2024-01-05 01:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2023-11-05 01:00 | 1.5661 | 1.8557 | 1.8557 | 1.8557 | 1.8557
2024-01-05 02:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2023-11-05 02:00 | 1.5585 | 1.8467 | 1.8467 | 1.8467 | 1.8467
2024-01-05 03:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2023-11-05 03:00 | 1.6919 | 2.0047 | 2.0047 | 2.0047 | 2.0047
2024-01-05 04:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2023-11-05 04:00 | 1.8405 | 2.1808 | 2.1808 | 2.1808 | 2.1808
2024-01-05 05:00 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2023-11-05 05:00 | 1.9281 | 2.2847 | 2.2847 | 2.2847 | 2.2847
2024-01-05 06:00 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2023-11-05 06:00 | 1.9624 | 2.3253 | 2.3253 | 2.3253 | 2.3253
2024-01-05 07:00 | 2.0767 | 2.5834 | 3.1212 | 3.1929 | 3.2646 | 2023-11-05 07:00 | 2.332 | 2.7633 | 2.7633 | 2.7633 | 2.7633
2024-01-05 08:00 | 2.1148 | 2.6308 | 3.1785 | 3.2515 | 3.3245 | 2023-11-05 08:00 | 2.4235 | 2.8716 | 2.8716 | 2.8716 | 2.8716
2024-01-05 09:00 | 2.0958 | 2.6071 | 3.1499 | 3.2222 | 3.2946 | 2023-11-05 09:00 | 2.8617 | 3.3909 | 3.3909 | 3.3909 | 3.3909
2024-01-05 10:00 | 2.172 | 2.7019 | 3.2644 | 3.3394 | 3.4144 | 2023-11-05 10:00 | 2.9227 | 3.4631 | 3.4631 | 3.4631 | 3.4631
2024-01-05 11:00 | 2.1529 | 2.6782 | 3.2358 | 3.3101 | 3.3845 | 2023-11-05 11:00 | 2.6254 | 3.1109 | 3.1109 | 3.1109 | 3.1109
2024-01-05 12:00 | 2.1148 | 2.6308 | 3.1785 | 3.2515 | 3.3245 | 2023-11-05 12:00 | 2.8007 | 3.3186 | 3.3186 | 3.3186 | 3.3186
2024-01-05 13:00 | 2.3625 | 2.9389 | 3.5508 | 3.6323 | 3.7139 | 2023-11-05 13:00 | 2.8541 | 3.3818 | 3.3818 | 3.3818 | 3.3818
2024-01-05 14:00 | 2.2673 | 2.8204 | 3.4076 | 3.4859 | 3.5642 | 2023-11-05 14:00 | 2.9379 | 3.4812 | 3.4812 | 3.4812 | 3.4812
2024-01-05 15:00 | 2.3625 | 2.9389 | 3.5508 | 3.6323 | 3.7139 | 2023-11-05 15:00 | 2.8503 | 3.3773 | 3.3773 | 3.3773 | 3.3773
2024-01-05 16:00 | 2.2101 | 2.7493 | 3.3217 | 3.398 | 3.4743 | 2023-11-05 16:00 | 2.5873 | 3.0658 | 3.0658 | 3.0658 | 3.0658
2024-01-05 17:00 | 2.191 | 2.7256 | 3.293 | 3.3687 | 3.4444 | 2023-11-05 17:00 | 2.393 | 2.8355 | 2.8355 | 2.8355 | 2.8355
2024-01-05 18:00 | 2.0577 | 2.5597 | 3.0926 | 3.1636 | 3.2347 | 2023-11-05 18:00 | 2.2634 | 2.682 | 2.682 | 2.682 | 2.682
2024-01-05 19:00 | 1.7147 | 2.1331 | 2.5772 | 2.6364 | 2.6956 | 2023-11-05 19:00 | 2.1758 | 2.5781 | 2.5781 | 2.5781 | 2.5781
2024-01-05 20:00 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2023-11-05 20:00 | 2.2215 | 2.6323 | 2.6323 | 2.6323 | 2.6323
2024-01-05 21:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2023-11-05 21:00 | 2.1453 | 2.542 | 2.542 | 2.542 | 2.542
2024-01-05 22:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2023-11-05 22:00 | 1.9205 | 2.2756 | 2.2756 | 2.2756 | 2.2756
2024-01-05 23:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2023-11-05 23:00 | 1.7071 | 2.0228 | 2.0228 | 2.0228 | 2.0228
2024-01-06 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2023-11-06 | 1.5356 | 1.8196 | 1.8196 | 1.8196 | 1.8196
2024-01-06 01:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2023-11-06 01:00 | 1.6157 | 1.9144 | 1.9144 | 1.9144 | 1.9144
2024-01-06 02:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2023-11-06 02:00 | 1.6728 | 1.9821 | 1.9821 | 1.9821 | 1.9821
2024-01-06 03:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2023-11-06 03:00 | 1.7071 | 2.0228 | 2.0228 | 2.0228 | 2.0228
2024-01-06 04:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2023-11-06 04:00 | 1.9243 | 2.2801 | 2.2801 | 2.2801 | 2.2801
2024-01-06 05:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2023-11-06 05:00 | 2.2139 | 2.6233 | 2.6233 | 2.6233 | 2.6233
2024-01-06 06:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2023-11-06 06:00 | 2.2596 | 2.6775 | 2.6775 | 2.6775 | 2.6775
2024-01-06 07:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2023-11-06 07:00 | 2.4082 | 2.8536 | 2.8536 | 2.8536 | 2.8536
2024-01-06 08:00 | 1.4099 | 1.7539 | 2.119 | 2.1677 | 2.2164 | 2023-11-06 08:00 | 2.9951 | 3.5489 | 3.5489 | 3.5489 | 3.5489
2024-01-06 09:00 | 1.3527 | 1.6828 | 2.0331 | 2.0798 | 2.1265 | 2023-11-06 09:00 | 3.2123 | 3.8063 | 3.8063 | 3.8063 | 3.8063
2024-01-06 10:00 | 1.2194 | 1.5169 | 1.8326 | 1.8748 | 1.9169 | 2023-11-06 10:00 | 2.9036 | 3.4405 | 3.4405 | 3.4405 | 3.4405
2024-01-06 11:00 | 1.2956 | 1.6117 | 1.9472 | 1.9919 | 2.0367 | 2023-11-06 11:00 | 3.0598 | 3.6257 | 3.6257 | 3.6257 | 3.6257
2024-01-06 12:00 | 1.2194 | 1.5169 | 1.8326 | 1.8748 | 1.9169 | 2023-11-06 12:00 | 2.8274 | 3.3502 | 3.3502 | 3.3502 | 3.3502
2024-01-06 13:00 | 1.2194 | 1.5169 | 1.8326 | 1.8748 | 1.9169 | 2023-11-06 13:00 | 3.0598 | 3.6257 | 3.6257 | 3.6257 | 3.6257
2024-01-06 14:00 | 1.2575 | 1.5643 | 1.8899 | 1.9333 | 1.9768 | 2023-11-06 14:00 | 2.8922 | 3.427 | 3.427 | 3.427 | 3.427
2024-01-06 15:00 | 1.3908 | 1.7302 | 2.0904 | 2.1384 | 2.1864 | 2023-11-06 15:00 | 3.0941 | 3.6663 | 3.6663 | 3.6663 | 3.6663
2024-01-06 16:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2023-11-06 16:00 | 3.3533 | 3.9733 | 3.9733 | 3.9733 | 3.9733
2024-01-06 17:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2023-11-06 17:00 | 3.4295 | 4.0636 | 4.0636 | 4.0636 | 4.0636
2024-01-06 18:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2023-11-06 18:00 | 3.0484 | 3.6121 | 3.6121 | 3.6121 | 3.6121
2024-01-06 19:00 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2023-11-06 19:00 | 2.6369 | 3.1245 | 3.1245 | 3.1245 | 3.1245
2024-01-06 20:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2023-11-06 20:00 | 2.4425 | 2.8942 | 2.8942 | 2.8942 | 2.8942
2024-01-06 21:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2023-11-06 21:00 | 2.1377 | 2.533 | 2.533 | 2.533 | 2.533
2024-01-06 22:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2023-11-06 22:00 | 1.8405 | 2.1808 | 2.1808 | 2.1808 | 2.1808
2024-01-06 23:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2023-11-06 23:00 | 1.8024 | 2.1357 | 2.1357 | 2.1357 | 2.1357
2024-01-07 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2023-11-07 | 1.5814 | 1.8738 | 1.8738 | 1.8738 | 1.8738
2024-01-07 01:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2023-11-07 01:00 | 1.6347 | 1.937 | 1.937 | 1.937 | 1.937
2024-01-07 02:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2023-11-07 02:00 | 1.669 | 1.9776 | 1.9776 | 1.9776 | 1.9776
2024-01-07 03:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2023-11-07 03:00 | 1.7986 | 2.1311 | 2.1311 | 2.1311 | 2.1311
2024-01-07 04:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2023-11-07 04:00 | 1.9205 | 2.2756 | 2.2756 | 2.2756 | 2.2756
2024-01-07 05:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2023-11-07 05:00 | 2.0577 | 2.4382 | 2.4382 | 2.4382 | 2.4382
2024-01-07 06:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2023-11-07 06:00 | 2.111 | 2.5014 | 2.5014 | 2.5014 | 2.5014
2024-01-07 07:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2023-11-07 07:00 | 2.3587 | 2.7949 | 2.7949 | 2.7949 | 2.7949
2024-01-07 08:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2023-11-07 08:00 | 2.6902 | 3.1877 | 3.1877 | 3.1877 | 3.1877
2024-01-07 09:00 | 1.3718 | 1.7065 | 2.0617 | 2.1091 | 2.1565 | 2023-11-07 09:00 | 2.7855 | 3.3006 | 3.3006 | 3.3006 | 3.3006
2024-01-07 10:00 | 1.3718 | 1.7065 | 2.0617 | 2.1091 | 2.1565 | 2023-11-07 10:00 | 2.7855 | 3.3006 | 3.3006 | 3.3006 | 3.3006
2024-01-07 11:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2023-11-07 11:00 | 2.9455 | 3.4902 | 3.4902 | 3.4902 | 3.4902
2024-01-07 12:00 | 1.3718 | 1.7065 | 2.0617 | 2.1091 | 2.1565 | 2023-11-07 12:00 | 2.9112 | 3.4496 | 3.4496 | 3.4496 | 3.4496
2024-01-07 13:00 | 1.2765 | 1.588 | 1.9186 | 1.9626 | 2.0067 | 2023-11-07 13:00 | 3.2123 | 3.8063 | 3.8063 | 3.8063 | 3.8063
2024-01-07 14:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2023-11-07 14:00 | 3.2351 | 3.8334 | 3.8334 | 3.8334 | 3.8334
2024-01-07 15:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2023-11-07 15:00 | 3.2466 | 3.8469 | 3.8469 | 3.8469 | 3.8469
2024-01-07 16:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2023-11-07 16:00 | 3.7686 | 4.4655 | 4.4655 | 4.4655 | 4.4655
2024-01-07 17:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2023-11-07 17:00 | 3.3647 | 3.9869 | 3.9869 | 3.9869 | 3.9869
2024-01-07 18:00 | 1.7528 | 2.1805 | 2.6344 | 2.695 | 2.7555 | 2023-11-07 18:00 | 3.2046 | 3.7972 | 3.7972 | 3.7972 | 3.7972
2024-01-07 19:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2023-11-07 19:00 | 2.6102 | 3.0929 | 3.0929 | 3.0929 | 3.0929
2024-01-07 20:00 | 1.6957 | 2.1094 | 2.5485 | 2.6071 | 2.6656 | 2023-11-07 20:00 | 2.4883 | 2.9484 | 2.9484 | 2.9484 | 2.9484
2024-01-07 21:00 | 1.7147 | 2.1331 | 2.5772 | 2.6364 | 2.6956 | 2023-11-07 21:00 | 2.252 | 2.6684 | 2.6684 | 2.6684 | 2.6684
2024-01-07 22:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2023-11-07 22:00 | 1.8862 | 2.235 | 2.235 | 2.235 | 2.235
2024-01-07 23:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2023-11-07 23:00 | 1.7147 | 2.0318 | 2.0318 | 2.0318 | 2.0318
2024-01-08 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2023-11-08 | 1.5737 | 1.8648 | 1.8648 | 1.8648 | 1.8648
2024-01-08 01:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2023-11-08 01:00 | 1.7071 | 2.0228 | 2.0228 | 2.0228 | 2.0228
2024-01-08 02:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2023-11-08 02:00 | 1.6538 | 1.9596 | 1.9596 | 1.9596 | 1.9596
2024-01-08 03:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2023-11-08 03:00 | 1.7986 | 2.1311 | 2.1311 | 2.1311 | 2.1311
2024-01-08 04:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2023-11-08 04:00 | 1.97 | 2.3343 | 2.3343 | 2.3343 | 2.3343
2024-01-08 05:00 | 1.7338 | 2.1568 | 2.6058 | 2.6657 | 2.7255 | 2023-11-08 05:00 | 2.2177 | 2.6278 | 2.6278 | 2.6278 | 2.6278
2024-01-08 06:00 | 2.0577 | 2.5597 | 3.0926 | 3.1636 | 3.2347 | 2023-11-08 06:00 | 2.2825 | 2.7046 | 2.7046 | 2.7046 | 2.7046
2024-01-08 07:00 | 2.7055 | 3.3655 | 4.0662 | 4.1596 | 4.253 | 2023-11-08 07:00 | 2.4997 | 2.9619 | 2.9619 | 2.9619 | 2.9619
2024-01-08 08:00 | 2.7626 | 3.4366 | 4.1521 | 4.2475 | 4.3429 | 2023-11-08 08:00 | 3.0294 | 3.5895 | 3.5895 | 3.5895 | 3.5895
2024-01-08 09:00 | 2.7817 | 3.4603 | 4.1807 | 4.2768 | 4.3728 | 2023-11-08 09:00 | 2.9836 | 3.5354 | 3.5354 | 3.5354 | 3.5354
2024-01-08 10:00 | 2.8388 | 3.5314 | 4.2666 | 4.3647 | 4.4627 | 2023-11-08 10:00 | 3.0675 | 3.6347 | 3.6347 | 3.6347 | 3.6347
2024-01-08 11:00 | 2.8007 | 3.484 | 4.2094 | 4.3061 | 4.4028 | 2023-11-08 11:00 | 3.6086 | 4.2758 | 4.2758 | 4.2758 | 4.2758
2024-01-08 12:00 | 2.7626 | 3.4366 | 4.1521 | 4.2475 | 4.3429 | 2023-11-08 12:00 | 3.6352 | 4.3074 | 4.3074 | 4.3074 | 4.3074
2024-01-08 13:00 | 2.6864 | 3.3418 | 4.0375 | 4.1303 | 4.2231 | 2023-11-08 13:00 | 3.4142 | 4.0456 | 4.0456 | 4.0456 | 4.0456
2024-01-08 14:00 | 2.7817 | 3.4603 | 4.1807 | 4.2768 | 4.3728 | 2023-11-08 14:00 | 3.681 | 4.3616 | 4.3616 | 4.3616 | 4.3616
2024-01-08 15:00 | 2.5149 | 3.1285 | 3.7798 | 3.8667 | 3.9535 | 2023-11-08 15:00 | 3.7381 | 4.4294 | 4.4294 | 4.4294 | 4.4294
2024-01-08 16:00 | 2.553 | 3.1759 | 3.8371 | 3.9253 | 4.0134 | 2023-11-08 16:00 | 3.7762 | 4.4745 | 4.4745 | 4.4745 | 4.4745
2024-01-08 17:00 | 2.534 | 3.1522 | 3.8085 | 3.896 | 3.9835 | 2023-11-08 17:00 | 3.418 | 4.0501 | 4.0501 | 4.0501 | 4.0501
2024-01-08 18:00 | 2.1529 | 2.6782 | 3.2358 | 3.3101 | 3.3845 | 2023-11-08 18:00 | 3.2847 | 3.892 | 3.892 | 3.892 | 3.892
2024-01-08 19:00 | 1.8481 | 2.299 | 2.7776 | 2.8414 | 2.9052 | 2023-11-08 19:00 | 2.7741 | 3.287 | 3.287 | 3.287 | 3.287
2024-01-08 20:00 | 1.7147 | 2.1331 | 2.5772 | 2.6364 | 2.6956 | 2023-11-08 20:00 | 2.4959 | 2.9574 | 2.9574 | 2.9574 | 2.9574
2024-01-08 21:00 | 1.7909 | 2.2279 | 2.6917 | 2.7535 | 2.8154 | 2023-11-08 21:00 | 2.1758 | 2.5781 | 2.5781 | 2.5781 | 2.5781
2024-01-08 22:00 | 1.7528 | 2.1805 | 2.6344 | 2.695 | 2.7555 | 2023-11-08 22:00 | 1.9662 | 2.3298 | 2.3298 | 2.3298 | 2.3298
2024-01-08 23:00 | 1.7338 | 2.1568 | 2.6058 | 2.6657 | 2.7255 | 2023-11-08 23:00 | 1.9815 | 2.3479 | 2.3479 | 2.3479 | 2.3479
2024-01-09 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2023-11-09 | 1.73 | 2.0499 | 2.0499 | 2.0499 | 2.0499
2024-01-09 01:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2023-11-09 01:00 | 1.6804 | 1.9912 | 1.9912 | 1.9912 | 1.9912
2024-01-09 02:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2023-11-09 02:00 | 1.6233 | 1.9234 | 1.9234 | 1.9234 | 1.9234
2024-01-09 03:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2023-11-09 03:00 | 1.7986 | 2.1311 | 2.1311 | 2.1311 | 2.1311
2024-01-09 04:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2023-11-09 04:00 | 2.0539 | 2.4337 | 2.4337 | 2.4337 | 2.4337
2024-01-09 05:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2023-11-09 05:00 | 2.1491 | 2.5465 | 2.5465 | 2.5465 | 2.5465
2024-01-09 06:00 | 1.8672 | 2.3227 | 2.8062 | 2.8707 | 2.9352 | 2023-11-09 06:00 | 2.3397 | 2.7723 | 2.7723 | 2.7723 | 2.7723
2024-01-09 07:00 | 2.2863 | 2.8441 | 3.4362 | 3.5152 | 3.5941 | 2023-11-09 07:00 | 2.473 | 2.9303 | 2.9303 | 2.9303 | 2.9303
2024-01-09 08:00 | 2.3435 | 2.9152 | 3.5221 | 3.603 | 3.684 | 2023-11-09 08:00 | 3.1932 | 3.7837 | 3.7837 | 3.7837 | 3.7837
2024-01-09 09:00 | 2.3054 | 2.8678 | 3.4648 | 3.5445 | 3.6241 | 2023-11-09 09:00 | 3.2961 | 3.9056 | 3.9056 | 3.9056 | 3.9056
2024-01-09 10:00 | 2.5149 | 3.1285 | 3.7798 | 3.8667 | 3.9535 | 2023-11-09 10:00 | 3.3914 | 4.0185 | 4.0185 | 4.0185 | 4.0185
2024-01-09 11:00 | 2.4959 | 3.1048 | 3.7512 | 3.8374 | 3.9236 | 2023-11-09 11:00 | 3.7762 | 4.4745 | 4.4745 | 4.4745 | 4.4745
2024-01-09 12:00 | 2.6674 | 3.3181 | 4.0089 | 4.101 | 4.1931 | 2023-11-09 12:00 | 3.5666 | 4.2262 | 4.2262 | 4.2262 | 4.2262
2024-01-09 13:00 | 2.7055 | 3.3655 | 4.0662 | 4.1596 | 4.253 | 2023-11-09 13:00 | 3.5133 | 4.163 | 4.163 | 4.163 | 4.163
2024-01-09 14:00 | 2.7626 | 3.4366 | 4.1521 | 4.2475 | 4.3429 | 2023-11-09 14:00 | 3.2008 | 3.7927 | 3.7927 | 3.7927 | 3.7927
2024-01-09 15:00 | 2.6864 | 3.3418 | 4.0375 | 4.1303 | 4.2231 | 2023-11-09 15:00 | 2.976 | 3.5263 | 3.5263 | 3.5263 | 3.5263
2024-01-09 16:00 | 2.7436 | 3.4129 | 4.1235 | 4.2182 | 4.3129 | 2023-11-09 16:00 | 3.4104 | 4.041 | 4.041 | 4.041 | 4.041
2024-01-09 17:00 | 2.6483 | 3.2944 | 3.9803 | 4.0717 | 4.1632 | 2023-11-09 17:00 | 3.0789 | 3.6482 | 3.6482 | 3.6482 | 3.6482
2024-01-09 18:00 | 2.5721 | 3.1996 | 3.8657 | 3.9546 | 4.0434 | 2023-11-09 18:00 | 2.9646 | 3.5128 | 3.5128 | 3.5128 | 3.5128
2024-01-09 19:00 | 1.9053 | 2.3701 | 2.8635 | 2.9293 | 2.9951 | 2023-11-09 19:00 | 2.8769 | 3.4089 | 3.4089 | 3.4089 | 3.4089
2024-01-09 20:00 | 1.7338 | 2.1568 | 2.6058 | 2.6657 | 2.7255 | 2023-11-09 20:00 | 2.6559 | 3.1471 | 3.1471 | 3.1471 | 3.1471
2024-01-09 21:00 | 1.6957 | 2.1094 | 2.5485 | 2.6071 | 2.6656 | 2023-11-09 21:00 | 2.2634 | 2.682 | 2.682 | 2.682 | 2.682
2024-01-09 22:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2023-11-09 22:00 | 2.0005 | 2.3704 | 2.3704 | 2.3704 | 2.3704
2024-01-09 23:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2023-11-09 23:00 | 1.7414 | 2.0634 | 2.0634 | 2.0634 | 2.0634
2024-01-10 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2023-11-10 | 1.669 | 1.9776 | 1.9776 | 1.9776 | 1.9776
2024-01-10 01:00 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2023-11-10 01:00 | 1.6385 | 1.9415 | 1.9415 | 1.9415 | 1.9415
2024-01-10 02:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2023-11-10 02:00 | 1.6233 | 1.9234 | 1.9234 | 1.9234 | 1.9234
2024-01-10 03:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2023-11-10 03:00 | 1.81 | 2.1447 | 2.1447 | 2.1447 | 2.1447
2024-01-10 04:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2023-11-10 04:00 | 1.9091 | 2.2621 | 2.2621 | 2.2621 | 2.2621
2024-01-10 05:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2023-11-10 05:00 | 2.1606 | 2.5601 | 2.5601 | 2.5601 | 2.5601
2024-01-10 06:00 | 1.8672 | 2.3227 | 2.8062 | 2.8707 | 2.9352 | 2023-11-10 06:00 | 2.473 | 2.9303 | 2.9303 | 2.9303 | 2.9303
2024-01-10 07:00 | 2.4197 | 3.01 | 3.6367 | 3.7202 | 3.8038 | 2023-11-10 07:00 | 2.4273 | 2.8761 | 2.8761 | 2.8761 | 2.8761
2024-01-10 08:00 | 2.3816 | 2.9626 | 3.5794 | 3.6616 | 3.7439 | 2023-11-10 08:00 | 2.8426 | 3.3683 | 3.3683 | 3.3683 | 3.3683
2024-01-10 09:00 | 2.4006 | 2.9863 | 3.608 | 3.6909 | 3.7738 | 2023-11-10 09:00 | 2.8426 | 3.3683 | 3.3683 | 3.3683 | 3.3683
2024-01-10 10:00 | 2.534 | 3.1522 | 3.8085 | 3.896 | 3.9835 | 2023-11-10 10:00 | 3.0103 | 3.567 | 3.567 | 3.567 | 3.567
2024-01-10 11:00 | 2.7245 | 3.3892 | 4.0948 | 4.1889 | 4.283 | 2023-11-10 11:00 | 3.2389 | 3.8379 | 3.8379 | 3.8379 | 3.8379
2024-01-10 12:00 | 2.9722 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2023-11-10 12:00 | 3.7191 | 4.4068 | 4.4068 | 4.4068 | 4.4068
2024-01-10 13:00 | 3.0865 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2023-11-10 13:00 | 4.1039 | 4.8628 | 4.8628 | 4.8628 | 4.8628
2024-01-10 14:00 | 3.1056 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2023-11-10 14:00 | 3.7343 | 4.4248 | 4.4248 | 4.4248 | 4.4248
2024-01-10 15:00 | 2.7817 | 3.4603 | 4.1807 | 4.2768 | 4.3728 | 2023-11-10 15:00 | 3.8677 | 4.5829 | 4.5829 | 4.5829 | 4.5829
2024-01-10 16:00 | 2.6864 | 3.3418 | 4.0375 | 4.1303 | 4.2231 | 2023-11-10 16:00 | 3.9782 | 4.7138 | 4.7138 | 4.7138 | 4.7138
2024-01-10 17:00 | 2.6674 | 3.3181 | 4.0089 | 4.101 | 4.1931 | 2023-11-10 17:00 | 3.6886 | 4.3707 | 4.3707 | 4.3707 | 4.3707
2024-01-10 18:00 | 2.534 | 3.1522 | 3.8085 | 3.896 | 3.9835 | 2023-11-10 18:00 | 3.4142 | 4.0456 | 4.0456 | 4.0456 | 4.0456
2024-01-10 19:00 | 2.0767 | 2.5834 | 3.1212 | 3.1929 | 3.2646 | 2023-11-10 19:00 | 3.2237 | 3.8198 | 3.8198 | 3.8198 | 3.8198
2024-01-10 20:00 | 1.8862 | 2.3464 | 2.8349 | 2.9 | 2.9651 | 2023-11-10 20:00 | 2.7626 | 3.2735 | 3.2735 | 3.2735 | 3.2735
2024-01-10 21:00 | 1.9053 | 2.3701 | 2.8635 | 2.9293 | 2.9951 | 2023-11-10 21:00 | 2.4197 | 2.8671 | 2.8671 | 2.8671 | 2.8671
2024-01-10 22:00 | 1.8672 | 2.3227 | 2.8062 | 2.8707 | 2.9352 | 2023-11-10 22:00 | 2.111 | 2.5014 | 2.5014 | 2.5014 | 2.5014
2024-01-10 23:00 | 1.7528 | 2.1805 | 2.6344 | 2.695 | 2.7555 | 2023-11-10 23:00 | 1.7795 | 2.1086 | 2.1086 | 2.1086 | 2.1086
2024-01-11 | 1.7719 | 2.2042 | 2.6631 | 2.7242 | 2.7854 | 2023-11-11 | 1.5814 | 1.8738 | 1.8738 | 1.8738 | 1.8738
2024-01-11 01:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2023-11-11 01:00 | 1.6004 | 1.8964 | 1.8964 | 1.8964 | 1.8964
2024-01-11 02:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2023-11-11 02:00 | 1.5928 | 1.8873 | 1.8873 | 1.8873 | 1.8873
2024-01-11 03:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2023-11-11 03:00 | 1.7528 | 2.077 | 2.077 | 2.077 | 2.077
2024-01-11 04:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2023-11-11 04:00 | 1.951 | 2.3118 | 2.3118 | 2.3118 | 2.3118
2024-01-11 05:00 | 1.7719 | 2.2042 | 2.6631 | 2.7242 | 2.7854 | 2023-11-11 05:00 | 2.1301 | 2.524 | 2.524 | 2.524 | 2.524
2024-01-11 06:00 | 2.0386 | 2.536 | 3.064 | 3.1344 | 3.2047 | 2023-11-11 06:00 | 2.1949 | 2.6007 | 2.6007 | 2.6007 | 2.6007
2024-01-11 07:00 | 2.6102 | 3.247 | 3.923 | 4.0131 | 4.1033 | 2023-11-11 07:00 | 2.1834 | 2.5872 | 2.5872 | 2.5872 | 2.5872
2024-01-11 08:00 | 2.8388 | 3.5314 | 4.2666 | 4.3647 | 4.4627 | 2023-11-11 08:00 | 2.2825 | 2.7046 | 2.7046 | 2.7046 | 2.7046
2024-01-11 09:00 | 2.9531 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2023-11-11 09:00 | 2.4425 | 2.8942 | 2.8942 | 2.8942 | 2.8942
2024-01-11 10:00 | 2.9531 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2023-11-11 10:00 | 2.6407 | 3.129 | 3.129 | 3.129 | 3.129
2024-01-11 11:00 | 3.0675 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2023-11-11 11:00 | 2.7588 | 3.269 | 3.269 | 3.269 | 3.269
2024-01-11 12:00 | 3.0865 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2023-11-11 12:00 | 2.816 | 3.3367 | 3.3367 | 3.3367 | 3.3367
2024-01-11 13:00 | 3.1056 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2023-11-11 13:00 | 3.0865 | 3.6573 | 3.6573 | 3.6573 | 3.6573
2024-01-11 14:00 | 3.2199 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2023-11-11 14:00 | 3.1589 | 3.743 | 3.743 | 3.743 | 3.743
2024-01-11 15:00 | 2.9531 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2023-11-11 15:00 | 3.6124 | 4.2804 | 4.2804 | 4.2804 | 4.2804
2024-01-11 16:00 | 2.915 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2023-11-11 16:00 | 3.5133 | 4.163 | 4.163 | 4.163 | 4.163
2024-01-11 17:00 | 2.896 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2023-11-11 17:00 | 3.2389 | 3.8379 | 3.8379 | 3.8379 | 3.8379
2024-01-11 18:00 | 2.534 | 3.1522 | 3.8085 | 3.896 | 3.9835 | 2023-11-11 18:00 | 3.1589 | 3.743 | 3.743 | 3.743 | 3.743
2024-01-11 19:00 | 2.0767 | 2.5834 | 3.1212 | 3.1929 | 3.2646 | 2023-11-11 19:00 | 2.896 | 3.4315 | 3.4315 | 3.4315 | 3.4315
2024-01-11 20:00 | 1.7719 | 2.2042 | 2.6631 | 2.7242 | 2.7854 | 2023-11-11 20:00 | 2.534 | 3.0026 | 3.0026 | 3.0026 | 3.0026
2024-01-11 21:00 | 1.829 | 2.2753 | 2.749 | 2.8121 | 2.8753 | 2023-11-11 21:00 | 2.2787 | 2.7001 | 2.7001 | 2.7001 | 2.7001
2024-01-11 22:00 | 1.7719 | 2.2042 | 2.6631 | 2.7242 | 2.7854 | 2023-11-11 22:00 | 2.1529 | 2.5511 | 2.5511 | 2.5511 | 2.5511
2024-01-11 23:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2023-11-11 23:00 | 1.749 | 2.0724 | 2.0724 | 2.0724 | 2.0724
2024-01-12 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2023-11-12 | 1.7071 | 2.0228 | 2.0228 | 2.0228 | 2.0228
2024-01-12 01:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2023-11-12 01:00 | 1.6347 | 1.937 | 1.937 | 1.937 | 1.937
2024-01-12 02:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2023-11-12 02:00 | 1.6042 | 1.9009 | 1.9009 | 1.9009 | 1.9009
2024-01-12 03:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2023-11-12 03:00 | 1.749 | 2.0724 | 2.0724 | 2.0724 | 2.0724
2024-01-12 04:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2023-11-12 04:00 | 1.8367 | 2.1763 | 2.1763 | 2.1763 | 2.1763
2024-01-12 05:00 | 1.6957 | 2.1094 | 2.5485 | 2.6071 | 2.6656 | 2023-11-12 05:00 | 2.1949 | 2.6007 | 2.6007 | 2.6007 | 2.6007
2024-01-12 06:00 | 2.0767 | 2.5834 | 3.1212 | 3.1929 | 3.2646 | 2023-11-12 06:00 | 2.2787 | 2.7001 | 2.7001 | 2.7001 | 2.7001
2024-01-12 07:00 | 2.553 | 3.1759 | 3.8371 | 3.9253 | 4.0134 | 2023-11-12 07:00 | 2.2177 | 2.6278 | 2.6278 | 2.6278 | 2.6278
2024-01-12 08:00 | 2.7436 | 3.4129 | 4.1235 | 4.2182 | 4.3129 | 2023-11-12 08:00 | 2.2863 | 2.7091 | 2.7091 | 2.7091 | 2.7091
2024-01-12 09:00 | 2.8198 | 3.5077 | 4.238 | 4.3354 | 4.4327 | 2023-11-12 09:00 | 2.816 | 3.3367 | 3.3367 | 3.3367 | 3.3367
2024-01-12 10:00 | 2.8388 | 3.5314 | 4.2666 | 4.3647 | 4.4627 | 2023-11-12 10:00 | 2.7702 | 3.2825 | 3.2825 | 3.2825 | 3.2825
2024-01-12 11:00 | 2.8579 | 3.5551 | 4.2953 | 4.3939 | 4.4926 | 2023-11-12 11:00 | 3.1856 | 3.7747 | 3.7747 | 3.7747 | 3.7747
2024-01-12 12:00 | 2.7436 | 3.4129 | 4.1235 | 4.2182 | 4.3129 | 2023-11-12 12:00 | 3.2961 | 3.9056 | 3.9056 | 3.9056 | 3.9056
2024-01-12 13:00 | 2.9531 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2023-11-12 13:00 | 3.2466 | 3.8469 | 3.8469 | 3.8469 | 3.8469
2024-01-12 14:00 | 3.0103 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2023-11-12 14:00 | 3.1856 | 3.7747 | 3.7747 | 3.7747 | 3.7747
2024-01-12 15:00 | 2.8388 | 3.5314 | 4.2666 | 4.3647 | 4.4627 | 2023-11-12 15:00 | 3.3571 | 3.9778 | 3.9778 | 3.9778 | 3.9778
2024-01-12 16:00 | 2.7626 | 3.4366 | 4.1521 | 4.2475 | 4.3429 | 2023-11-12 16:00 | 3.277 | 3.883 | 3.883 | 3.883 | 3.883
2024-01-12 17:00 | 2.7055 | 3.3655 | 4.0662 | 4.1596 | 4.253 | 2023-11-12 17:00 | 3.2389 | 3.8379 | 3.8379 | 3.8379 | 3.8379
2024-01-12 18:00 | 2.4578 | 3.0574 | 3.6939 | 3.7788 | 3.8637 | 2023-11-12 18:00 | 2.6254 | 3.1109 | 3.1109 | 3.1109 | 3.1109
2024-01-12 19:00 | 2.172 | 2.7019 | 3.2644 | 3.3394 | 3.4144 | 2023-11-12 19:00 | 2.3206 | 2.7497 | 2.7497 | 2.7497 | 2.7497
2024-01-12 20:00 | 1.8481 | 2.299 | 2.7776 | 2.8414 | 2.9052 | 2023-11-12 20:00 | 2.0577 | 2.4382 | 2.4382 | 2.4382 | 2.4382
2024-01-12 21:00 | 1.9243 | 2.3938 | 2.8921 | 2.9586 | 3.025 | 2023-11-12 21:00 | 2.1758 | 2.5781 | 2.5781 | 2.5781 | 2.5781
2024-01-12 22:00 | 1.8672 | 2.3227 | 2.8062 | 2.8707 | 2.9352 | 2023-11-12 22:00 | 1.9167 | 2.2711 | 2.2711 | 2.2711 | 2.2711
2024-01-12 23:00 | 1.8862 | 2.3464 | 2.8349 | 2.9 | 2.9651 | 2023-11-12 23:00 | 1.7566 | 2.0815 | 2.0815 | 2.0815 | 2.0815
2024-01-13 | 1.6957 | 2.1094 | 2.5485 | 2.6071 | 2.6656 | 2023-11-13 | 1.5737 | 1.8648 | 1.8648 | 1.8648 | 1.8648
2024-01-13 01:00 | 1.7338 | 2.1568 | 2.6058 | 2.6657 | 2.7255 | 2023-11-13 01:00 | 1.608 | 1.9054 | 1.9054 | 1.9054 | 1.9054
2024-01-13 02:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2023-11-13 02:00 | 1.6423 | 1.946 | 1.946 | 1.946 | 1.946
2024-01-13 03:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2023-11-13 03:00 | 1.7833 | 2.1131 | 2.1131 | 2.1131 | 2.1131
2024-01-13 04:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2023-11-13 04:00 | 1.9357 | 2.2937 | 2.2937 | 2.2937 | 2.2937
2024-01-13 05:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2023-11-13 05:00 | 2.2063 | 2.6143 | 2.6143 | 2.6143 | 2.6143
2024-01-13 06:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2023-11-13 06:00 | 2.3015 | 2.7271 | 2.7271 | 2.7271 | 2.7271
2024-01-13 07:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2023-11-13 07:00 | 2.5569 | 3.0297 | 3.0297 | 3.0297 | 3.0297
2024-01-13 08:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2023-11-13 08:00 | 3.0865 | 3.6573 | 3.6573 | 3.6573 | 3.6573
2024-01-13 09:00 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2023-11-13 09:00 | 3.1094 | 3.6844 | 3.6844 | 3.6844 | 3.6844
2024-01-13 10:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2023-11-13 10:00 | 3.1627 | 3.7476 | 3.7476 | 3.7476 | 3.7476
2024-01-13 11:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2023-11-13 11:00 | 3.0255 | 3.585 | 3.585 | 3.585 | 3.585
2024-01-13 12:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2023-11-13 12:00 | 3.2618 | 3.865 | 3.865 | 3.865 | 3.865
2024-01-13 13:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2023-11-13 13:00 | 3.3723 | 3.9959 | 3.9959 | 3.9959 | 3.9959
2024-01-13 14:00 | 1.8481 | 2.299 | 2.7776 | 2.8414 | 2.9052 | 2023-11-13 14:00 | 3.178 | 3.7656 | 3.7656 | 3.7656 | 3.7656
2024-01-13 15:00 | 1.8862 | 2.3464 | 2.8349 | 2.9 | 2.9651 | 2023-11-13 15:00 | 3.2732 | 3.8785 | 3.8785 | 3.8785 | 3.8785
2024-01-13 16:00 | 1.7909 | 2.2279 | 2.6917 | 2.7535 | 2.8154 | 2023-11-13 16:00 | 3.559 | 4.2171 | 4.2171 | 4.2171 | 4.2171
2024-01-13 17:00 | 1.6957 | 2.1094 | 2.5485 | 2.6071 | 2.6656 | 2023-11-13 17:00 | 3.62 | 4.2894 | 4.2894 | 4.2894 | 4.2894
2024-01-13 18:00 | 1.7147 | 2.1331 | 2.5772 | 2.6364 | 2.6956 | 2023-11-13 18:00 | 3.3113 | 3.9237 | 3.9237 | 3.9237 | 3.9237
2024-01-13 19:00 | 1.7338 | 2.1568 | 2.6058 | 2.6657 | 2.7255 | 2023-11-13 19:00 | 2.6788 | 3.1741 | 3.1741 | 3.1741 | 3.1741
2024-01-13 20:00 | 1.6957 | 2.1094 | 2.5485 | 2.6071 | 2.6656 | 2023-11-13 20:00 | 2.5149 | 2.98 | 2.98 | 2.98 | 2.98
2024-01-13 21:00 | 1.7909 | 2.2279 | 2.6917 | 2.7535 | 2.8154 | 2023-11-13 21:00 | 2.3549 | 2.7904 | 2.7904 | 2.7904 | 2.7904
2024-01-13 22:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2023-11-13 22:00 | 2.1758 | 2.5781 | 2.5781 | 2.5781 | 2.5781
2024-01-13 23:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2023-11-13 23:00 | 1.871 | 2.2169 | 2.2169 | 2.2169 | 2.2169
2024-01-14 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2023-11-14 | 1.6118 | 1.9099 | 1.9099 | 1.9099 | 1.9099
2024-01-14 01:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2023-11-14 01:00 | 1.6195 | 1.9189 | 1.9189 | 1.9189 | 1.9189
2024-01-14 02:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2023-11-14 02:00 | 1.6881 | 2.0002 | 2.0002 | 2.0002 | 2.0002
2024-01-14 03:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2023-11-14 03:00 | 1.7224 | 2.0408 | 2.0408 | 2.0408 | 2.0408
2024-01-14 04:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2023-11-14 04:00 | 1.8748 | 2.2214 | 2.2214 | 2.2214 | 2.2214
2024-01-14 05:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2023-11-14 05:00 | 2.2596 | 2.6775 | 2.6775 | 2.6775 | 2.6775
2024-01-14 06:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2023-11-14 06:00 | 2.2863 | 2.7091 | 2.7091 | 2.7091 | 2.7091
2024-01-14 07:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2023-11-14 07:00 | 2.5797 | 3.0567 | 3.0567 | 3.0567 | 3.0567
2024-01-14 08:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2023-11-14 08:00 | 2.8312 | 3.3547 | 3.3547 | 3.3547 | 3.3547
2024-01-14 09:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2023-11-14 09:00 | 2.9227 | 3.4631 | 3.4631 | 3.4631 | 3.4631
2024-01-14 10:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2023-11-14 10:00 | 2.9836 | 3.5354 | 3.5354 | 3.5354 | 3.5354
2024-01-14 11:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2023-11-14 11:00 | 3.1056 | 3.6798 | 3.6798 | 3.6798 | 3.6798
2024-01-14 12:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2023-11-14 12:00 | 4.0887 | 4.8447 | 4.8447 | 4.8447 | 4.8447
2024-01-14 13:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2023-11-14 13:00 | 3.7229 | 4.4113 | 4.4113 | 4.4113 | 4.4113
2024-01-14 14:00 | 1.3718 | 1.7065 | 2.0617 | 2.1091 | 2.1565 | 2023-11-14 14:00 | 3.7305 | 4.4203 | 4.4203 | 4.4203 | 4.4203
2024-01-14 15:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2023-11-14 15:00 | 3.6238 | 4.2939 | 4.2939 | 4.2939 | 4.2939
2024-01-14 16:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2023-11-14 16:00 | 3.5476 | 4.2036 | 4.2036 | 4.2036 | 4.2036
2024-01-14 17:00 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2023-11-14 17:00 | 3.479 | 4.1223 | 4.1223 | 4.1223 | 4.1223
2024-01-14 18:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2023-11-14 18:00 | 2.9722 | 3.5218 | 3.5218 | 3.5218 | 3.5218
2024-01-14 19:00 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2023-11-14 19:00 | 2.7741 | 3.287 | 3.287 | 3.287 | 3.287
2024-01-14 20:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2023-11-14 20:00 | 2.534 | 3.0026 | 3.0026 | 3.0026 | 3.0026
2024-01-14 21:00 | 1.6957 | 2.1094 | 2.5485 | 2.6071 | 2.6656 | 2023-11-14 21:00 | 2.2291 | 2.6414 | 2.6414 | 2.6414 | 2.6414
2024-01-14 22:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2023-11-14 22:00 | 2.092 | 2.4788 | 2.4788 | 2.4788 | 2.4788
2024-01-14 23:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2023-11-14 23:00 | 1.8405 | 2.1808 | 2.1808 | 2.1808 | 2.1808
2024-01-15 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2023-11-15 | 1.5814 | 1.8738 | 1.8738 | 1.8738 | 1.8738
2024-01-15 01:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2023-11-15 01:00 | 1.6195 | 1.9189 | 1.9189 | 1.9189 | 1.9189
2024-01-15 02:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2023-11-15 02:00 | 1.6385 | 1.9415 | 1.9415 | 1.9415 | 1.9415
2024-01-15 03:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2023-11-15 03:00 | 1.7262 | 2.0454 | 2.0454 | 2.0454 | 2.0454
2024-01-15 04:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2023-11-15 04:00 | 1.951 | 2.3118 | 2.3118 | 2.3118 | 2.3118
2024-01-15 05:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2023-11-15 05:00 | 2.1225 | 2.5149 | 2.5149 | 2.5149 | 2.5149
2024-01-15 06:00 | 1.829 | 2.2753 | 2.749 | 2.8121 | 2.8753 | 2023-11-15 06:00 | 2.233 | 2.6459 | 2.6459 | 2.6459 | 2.6459
2024-01-15 07:00 | 2.172 | 2.7019 | 3.2644 | 3.3394 | 3.4144 | 2023-11-15 07:00 | 2.5416 | 3.0116 | 3.0116 | 3.0116 | 3.0116
2024-01-15 08:00 | 2.3244 | 2.8915 | 3.4935 | 3.5737 | 3.654 | 2023-11-15 08:00 | 3.0332 | 3.5941 | 3.5941 | 3.5941 | 3.5941
2024-01-15 09:00 | 2.3054 | 2.8678 | 3.4648 | 3.5445 | 3.6241 | 2023-11-15 09:00 | 3.0408 | 3.6031 | 3.6031 | 3.6031 | 3.6031
2024-01-15 10:00 | 2.2673 | 2.8204 | 3.4076 | 3.4859 | 3.5642 | 2023-11-15 10:00 | 3.2085 | 3.8017 | 3.8017 | 3.8017 | 3.8017
2024-01-15 11:00 | 2.3435 | 2.9152 | 3.5221 | 3.603 | 3.684 | 2023-11-15 11:00 | 3.2732 | 3.8785 | 3.8785 | 3.8785 | 3.8785
2024-01-15 12:00 | 2.4387 | 3.0337 | 3.6653 | 3.7495 | 3.8337 | 2023-11-15 12:00 | 3.6086 | 4.2758 | 4.2758 | 4.2758 | 4.2758
2024-01-15 13:00 | 2.534 | 3.1522 | 3.8085 | 3.896 | 3.9835 | 2023-11-15 13:00 | 3.7076 | 4.3932 | 4.3932 | 4.3932 | 4.3932
2024-01-15 14:00 | 2.4387 | 3.0337 | 3.6653 | 3.7495 | 3.8337 | 2023-11-15 14:00 | 3.9172 | 4.6416 | 4.6416 | 4.6416 | 4.6416
2024-01-15 15:00 | 2.3054 | 2.8678 | 3.4648 | 3.5445 | 3.6241 | 2023-11-15 15:00 | 4.1458 | 4.9125 | 4.9125 | 4.9125 | 4.9125
2024-01-15 16:00 | 2.3244 | 2.8915 | 3.4935 | 3.5737 | 3.654 | 2023-11-15 16:00 | 4.0315 | 4.777 | 4.777 | 4.777 | 4.777
2024-01-15 17:00 | 2.1529 | 2.6782 | 3.2358 | 3.3101 | 3.3845 | 2023-11-15 17:00 | 3.5933 | 4.2578 | 4.2578 | 4.2578 | 4.2578
2024-01-15 18:00 | 2.0005 | 2.4886 | 3.0067 | 3.0758 | 3.1448 | 2023-11-15 18:00 | 3.1094 | 3.6844 | 3.6844 | 3.6844 | 3.6844
2024-01-15 19:00 | 1.7528 | 2.1805 | 2.6344 | 2.695 | 2.7555 | 2023-11-15 19:00 | 2.7436 | 3.2509 | 3.2509 | 3.2509 | 3.2509
2024-01-15 20:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2023-11-15 20:00 | 2.6978 | 3.1967 | 3.1967 | 3.1967 | 3.1967
2024-01-15 21:00 | 1.6957 | 2.1094 | 2.5485 | 2.6071 | 2.6656 | 2023-11-15 21:00 | 2.5721 | 3.0477 | 3.0477 | 3.0477 | 3.0477
2024-01-15 22:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2023-11-15 22:00 | 2.0958 | 2.4833 | 2.4833 | 2.4833 | 2.4833
2024-01-15 23:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2023-11-15 23:00 | 1.7986 | 2.1311 | 2.1311 | 2.1311 | 2.1311
2024-01-16 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2023-11-16 | 1.5814 | 1.8738 | 1.8738 | 1.8738 | 1.8738
2024-01-16 01:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2023-11-16 01:00 | 1.6233 | 1.9234 | 1.9234 | 1.9234 | 1.9234
2024-01-16 02:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2023-11-16 02:00 | 1.589 | 1.8828 | 1.8828 | 1.8828 | 1.8828
2024-01-16 03:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2023-11-16 03:00 | 1.749 | 2.0724 | 2.0724 | 2.0724 | 2.0724
2024-01-16 04:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2023-11-16 04:00 | 1.9777 | 2.3434 | 2.3434 | 2.3434 | 2.3434
2024-01-16 05:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2023-11-16 05:00 | 2.1263 | 2.5194 | 2.5194 | 2.5194 | 2.5194
2024-01-16 06:00 | 1.7719 | 2.2042 | 2.6631 | 2.7242 | 2.7854 | 2023-11-16 06:00 | 2.2444 | 2.6594 | 2.6594 | 2.6594 | 2.6594
2024-01-16 07:00 | 2.191 | 2.7256 | 3.293 | 3.3687 | 3.4444 | 2023-11-16 07:00 | 2.5454 | 3.0161 | 3.0161 | 3.0161 | 3.0161
2024-01-16 08:00 | 2.3625 | 2.9389 | 3.5508 | 3.6323 | 3.7139 | 2023-11-16 08:00 | 3.0065 | 3.5624 | 3.5624 | 3.5624 | 3.5624
2024-01-16 09:00 | 2.3244 | 2.8915 | 3.4935 | 3.5737 | 3.654 | 2023-11-16 09:00 | 3.3456 | 3.9643 | 3.9643 | 3.9643 | 3.9643
2024-01-16 10:00 | 2.4578 | 3.0574 | 3.6939 | 3.7788 | 3.8637 | 2023-11-16 10:00 | 3.2351 | 3.8334 | 3.8334 | 3.8334 | 3.8334
2024-01-16 11:00 | 2.3625 | 2.9389 | 3.5508 | 3.6323 | 3.7139 | 2023-11-16 11:00 | 3.3914 | 4.0185 | 4.0185 | 4.0185 | 4.0185
2024-01-16 12:00 | 2.4006 | 2.9863 | 3.608 | 3.6909 | 3.7738 | 2023-11-16 12:00 | 3.3037 | 3.9146 | 3.9146 | 3.9146 | 3.9146
2024-01-16 13:00 | 2.5149 | 3.1285 | 3.7798 | 3.8667 | 3.9535 | 2023-11-16 13:00 | 3.9477 | 4.6777 | 4.6777 | 4.6777 | 4.6777
2024-01-16 14:00 | 2.5721 | 3.1996 | 3.8657 | 3.9546 | 4.0434 | 2023-11-16 14:00 | 3.8105 | 4.5151 | 4.5151 | 4.5151 | 4.5151
2024-01-16 15:00 | 2.5721 | 3.1996 | 3.8657 | 3.9546 | 4.0434 | 2023-11-16 15:00 | 3.7419 | 4.4339 | 4.4339 | 4.4339 | 4.4339
2024-01-16 16:00 | 2.4387 | 3.0337 | 3.6653 | 3.7495 | 3.8337 | 2023-11-16 16:00 | 3.6771 | 4.3571 | 4.3571 | 4.3571 | 4.3571
2024-01-16 17:00 | 2.3244 | 2.8915 | 3.4935 | 3.5737 | 3.654 | 2023-11-16 17:00 | 3.3342 | 3.9507 | 3.9507 | 3.9507 | 3.9507
2024-01-16 18:00 | 2.0005 | 2.4886 | 3.0067 | 3.0758 | 3.1448 | 2023-11-16 18:00 | 2.8998 | 3.436 | 3.436 | 3.436 | 3.436
2024-01-16 19:00 | 1.7338 | 2.1568 | 2.6058 | 2.6657 | 2.7255 | 2023-11-16 19:00 | 2.694 | 3.1922 | 3.1922 | 3.1922 | 3.1922
2024-01-16 20:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2023-11-16 20:00 | 2.6026 | 3.0838 | 3.0838 | 3.0838 | 3.0838
2024-01-16 21:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2023-11-16 21:00 | 2.4273 | 2.8761 | 2.8761 | 2.8761 | 2.8761
2024-01-16 22:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2023-11-16 22:00 | 1.97 | 2.3343 | 2.3343 | 2.3343 | 2.3343
2024-01-16 23:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2023-11-16 23:00 | 1.829 | 2.1673 | 2.1673 | 2.1673 | 2.1673
2024-01-17 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2023-11-17 | 1.6271 | 1.928 | 1.928 | 1.928 | 1.928
2024-01-17 01:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2023-11-17 01:00 | 1.5966 | 1.8918 | 1.8918 | 1.8918 | 1.8918
2024-01-17 02:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2023-11-17 02:00 | 1.6271 | 1.928 | 1.928 | 1.928 | 1.928
2024-01-17 03:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2023-11-17 03:00 | 1.7224 | 2.0408 | 2.0408 | 2.0408 | 2.0408
2024-01-17 04:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2023-11-17 04:00 | 1.9586 | 2.3208 | 2.3208 | 2.3208 | 2.3208
2024-01-17 05:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2023-11-17 05:00 | 2.1606 | 2.5601 | 2.5601 | 2.5601 | 2.5601
2024-01-17 06:00 | 1.8481 | 2.299 | 2.7776 | 2.8414 | 2.9052 | 2023-11-17 06:00 | 2.1987 | 2.6052 | 2.6052 | 2.6052 | 2.6052
2024-01-17 07:00 | 2.2482 | 2.7967 | 3.3789 | 3.4566 | 3.5342 | 2023-11-17 07:00 | 2.675 | 3.1696 | 3.1696 | 3.1696 | 3.1696
2024-01-17 08:00 | 2.4578 | 3.0574 | 3.6939 | 3.7788 | 3.8637 | 2023-11-17 08:00 | 2.9989 | 3.5534 | 3.5534 | 3.5534 | 3.5534
2024-01-17 09:00 | 2.6674 | 3.3181 | 4.0089 | 4.101 | 4.1931 | 2023-11-17 09:00 | 3.0979 | 3.6708 | 3.6708 | 3.6708 | 3.6708
2024-01-17 10:00 | 2.6864 | 3.3418 | 4.0375 | 4.1303 | 4.2231 | 2023-11-17 10:00 | 3.0103 | 3.567 | 3.567 | 3.567 | 3.567
2024-01-17 11:00 | 2.7245 | 3.3892 | 4.0948 | 4.1889 | 4.283 | 2023-11-17 11:00 | 2.976 | 3.5263 | 3.5263 | 3.5263 | 3.5263
2024-01-17 12:00 | 2.7055 | 3.3655 | 4.0662 | 4.1596 | 4.253 | 2023-11-17 12:00 | 3.2046 | 3.7972 | 3.7972 | 3.7972 | 3.7972
2024-01-17 13:00 | 2.6293 | 3.2707 | 3.9516 | 4.0424 | 4.1332 | 2023-11-17 13:00 | 3.3456 | 3.9643 | 3.9643 | 3.9643 | 3.9643
2024-01-17 14:00 | 2.6483 | 3.2944 | 3.9803 | 4.0717 | 4.1632 | 2023-11-17 14:00 | 3.3456 | 3.9643 | 3.9643 | 3.9643 | 3.9643
2024-01-17 15:00 | 2.5721 | 3.1996 | 3.8657 | 3.9546 | 4.0434 | 2023-11-17 15:00 | 3.4942 | 4.1404 | 4.1404 | 4.1404 | 4.1404
2024-01-17 16:00 | 2.4959 | 3.1048 | 3.7512 | 3.8374 | 3.9236 | 2023-11-17 16:00 | 3.5057 | 4.1539 | 4.1539 | 4.1539 | 4.1539
2024-01-17 17:00 | 2.3244 | 2.8915 | 3.4935 | 3.5737 | 3.654 | 2023-11-17 17:00 | 3.4561 | 4.0952 | 4.0952 | 4.0952 | 4.0952
2024-01-17 18:00 | 2.0958 | 2.6071 | 3.1499 | 3.2222 | 3.2946 | 2023-11-17 18:00 | 3.2694 | 3.874 | 3.874 | 3.874 | 3.874
2024-01-17 19:00 | 1.8481 | 2.299 | 2.7776 | 2.8414 | 2.9052 | 2023-11-17 19:00 | 2.8541 | 3.3818 | 3.3818 | 3.3818 | 3.3818
2024-01-17 20:00 | 1.7147 | 2.1331 | 2.5772 | 2.6364 | 2.6956 | 2023-11-17 20:00 | 2.6635 | 3.1561 | 3.1561 | 3.1561 | 3.1561
2024-01-17 21:00 | 1.7909 | 2.2279 | 2.6917 | 2.7535 | 2.8154 | 2023-11-17 21:00 | 2.3168 | 2.7452 | 2.7452 | 2.7452 | 2.7452
2024-01-17 22:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2023-11-17 22:00 | 2.092 | 2.4788 | 2.4788 | 2.4788 | 2.4788
2024-01-17 23:00 | 1.6957 | 2.1094 | 2.5485 | 2.6071 | 2.6656 | 2023-11-17 23:00 | 1.9205 | 2.2756 | 2.2756 | 2.2756 | 2.2756
2024-01-18 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2023-11-18 | 1.6347 | 1.937 | 1.937 | 1.937 | 1.937
2024-01-18 01:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2023-11-18 01:00 | 1.6461 | 1.9505 | 1.9505 | 1.9505 | 1.9505
2024-01-18 02:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2023-11-18 02:00 | 1.6004 | 1.8964 | 1.8964 | 1.8964 | 1.8964
2024-01-18 03:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2023-11-18 03:00 | 1.749 | 2.0724 | 2.0724 | 2.0724 | 2.0724
2024-01-18 04:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2023-11-18 04:00 | 1.8176 | 2.1537 | 2.1537 | 2.1537 | 2.1537
2024-01-18 05:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2023-11-18 05:00 | 1.9853 | 2.3524 | 2.3524 | 2.3524 | 2.3524
2024-01-18 06:00 | 1.829 | 2.2753 | 2.749 | 2.8121 | 2.8753 | 2023-11-18 06:00 | 1.9929 | 2.3614 | 2.3614 | 2.3614 | 2.3614
2024-01-18 07:00 | 2.3435 | 2.9152 | 3.5221 | 3.603 | 3.684 | 2023-11-18 07:00 | 2.111 | 2.5014 | 2.5014 | 2.5014 | 2.5014
2024-01-18 08:00 | 2.2673 | 2.8204 | 3.4076 | 3.4859 | 3.5642 | 2023-11-18 08:00 | 2.4692 | 2.9258 | 2.9258 | 2.9258 | 2.9258
2024-01-18 09:00 | 2.2101 | 2.7493 | 3.3217 | 3.398 | 3.4743 | 2023-11-18 09:00 | 2.694 | 3.1922 | 3.1922 | 3.1922 | 3.1922
2024-01-18 10:00 | 2.3244 | 2.8915 | 3.4935 | 3.5737 | 3.654 | 2023-11-18 10:00 | 2.9531 | 3.4992 | 3.4992 | 3.4992 | 3.4992
2024-01-18 11:00 | 2.2863 | 2.8441 | 3.4362 | 3.5152 | 3.5941 | 2023-11-18 11:00 | 2.8807 | 3.4134 | 3.4134 | 3.4134 | 3.4134
2024-01-18 12:00 | 2.2863 | 2.8441 | 3.4362 | 3.5152 | 3.5941 | 2023-11-18 12:00 | 3.0141 | 3.5715 | 3.5715 | 3.5715 | 3.5715
2024-01-18 13:00 | 2.2482 | 2.7967 | 3.3789 | 3.4566 | 3.5342 | 2023-11-18 13:00 | 3.037 | 3.5986 | 3.5986 | 3.5986 | 3.5986
2024-01-18 14:00 | 2.2482 | 2.7967 | 3.3789 | 3.4566 | 3.5342 | 2023-11-18 14:00 | 3.1856 | 3.7747 | 3.7747 | 3.7747 | 3.7747
2024-01-18 15:00 | 2.2291 | 2.773 | 3.3503 | 3.4273 | 3.5043 | 2023-11-18 15:00 | 3.2389 | 3.8379 | 3.8379 | 3.8379 | 3.8379
2024-01-18 16:00 | 2.2673 | 2.8204 | 3.4076 | 3.4859 | 3.5642 | 2023-11-18 16:00 | 3.2046 | 3.7972 | 3.7972 | 3.7972 | 3.7972
2024-01-18 17:00 | 2.1339 | 2.6545 | 3.2071 | 3.2808 | 3.3545 | 2023-11-18 17:00 | 3.1361 | 3.716 | 3.716 | 3.716 | 3.716
2024-01-18 18:00 | 2.0005 | 2.4886 | 3.0067 | 3.0758 | 3.1448 | 2023-11-18 18:00 | 2.835 | 3.3593 | 3.3593 | 3.3593 | 3.3593
2024-01-18 19:00 | 1.7909 | 2.2279 | 2.6917 | 2.7535 | 2.8154 | 2023-11-18 19:00 | 2.5111 | 2.9755 | 2.9755 | 2.9755 | 2.9755
2024-01-18 20:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2023-11-18 20:00 | 2.1263 | 2.5194 | 2.5194 | 2.5194 | 2.5194
2024-01-18 21:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2023-11-18 21:00 | 2.1263 | 2.5194 | 2.5194 | 2.5194 | 2.5194
2024-01-18 22:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2023-11-18 22:00 | 1.9891 | 2.3569 | 2.3569 | 2.3569 | 2.3569
2024-01-18 23:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2023-11-18 23:00 | 1.7224 | 2.0408 | 2.0408 | 2.0408 | 2.0408
2024-01-19 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2023-11-19 | 1.5928 | 1.8873 | 1.8873 | 1.8873 | 1.8873
2024-01-19 01:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2023-11-19 01:00 | 1.6042 | 1.9009 | 1.9009 | 1.9009 | 1.9009
2024-01-19 02:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2023-11-19 02:00 | 1.5852 | 1.8783 | 1.8783 | 1.8783 | 1.8783
2024-01-19 03:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2023-11-19 03:00 | 1.7033 | 2.0183 | 2.0183 | 2.0183 | 2.0183
2024-01-19 04:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2023-11-19 04:00 | 1.8595 | 2.2034 | 2.2034 | 2.2034 | 2.2034
2024-01-19 05:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2023-11-19 05:00 | 1.9548 | 2.3163 | 2.3163 | 2.3163 | 2.3163
2024-01-19 06:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2023-11-19 06:00 | 2.0691 | 2.4517 | 2.4517 | 2.4517 | 2.4517
2024-01-19 07:00 | 2.0767 | 2.5834 | 3.1212 | 3.1929 | 3.2646 | 2023-11-19 07:00 | 1.97 | 2.3343 | 2.3343 | 2.3343 | 2.3343
2024-01-19 08:00 | 2.1339 | 2.6545 | 3.2071 | 3.2808 | 3.3545 | 2023-11-19 08:00 | 2.3092 | 2.7362 | 2.7362 | 2.7362 | 2.7362
2024-01-19 09:00 | 2.1148 | 2.6308 | 3.1785 | 3.2515 | 3.3245 | 2023-11-19 09:00 | 2.6712 | 3.1651 | 3.1651 | 3.1651 | 3.1651
2024-01-19 10:00 | 2.1339 | 2.6545 | 3.2071 | 3.2808 | 3.3545 | 2023-11-19 10:00 | 2.976 | 3.5263 | 3.5263 | 3.5263 | 3.5263
2024-01-19 11:00 | 2.191 | 2.7256 | 3.293 | 3.3687 | 3.4444 | 2023-11-19 11:00 | 3.1208 | 3.6979 | 3.6979 | 3.6979 | 3.6979
2024-01-19 12:00 | 2.191 | 2.7256 | 3.293 | 3.3687 | 3.4444 | 2023-11-19 12:00 | 3.54 | 4.1946 | 4.1946 | 4.1946 | 4.1946
2024-01-19 13:00 | 2.2863 | 2.8441 | 3.4362 | 3.5152 | 3.5941 | 2023-11-19 13:00 | 3.5323 | 4.1855 | 4.1855 | 4.1855 | 4.1855
2024-01-19 14:00 | 2.3054 | 2.8678 | 3.4648 | 3.5445 | 3.6241 | 2023-11-19 14:00 | 3.86 | 4.5738 | 4.5738 | 4.5738 | 4.5738
2024-01-19 15:00 | 2.2482 | 2.7967 | 3.3789 | 3.4566 | 3.5342 | 2023-11-19 15:00 | 3.5895 | 4.2533 | 4.2533 | 4.2533 | 4.2533
2024-01-19 16:00 | 2.2863 | 2.8441 | 3.4362 | 3.5152 | 3.5941 | 2023-11-19 16:00 | 3.5781 | 4.2397 | 4.2397 | 4.2397 | 4.2397
2024-01-19 17:00 | 2.191 | 2.7256 | 3.293 | 3.3687 | 3.4444 | 2023-11-19 17:00 | 3.3266 | 3.9417 | 3.9417 | 3.9417 | 3.9417
2024-01-19 18:00 | 2.0577 | 2.5597 | 3.0926 | 3.1636 | 3.2347 | 2023-11-19 18:00 | 2.7893 | 3.3051 | 3.3051 | 3.3051 | 3.3051
2024-01-19 19:00 | 1.7909 | 2.2279 | 2.6917 | 2.7535 | 2.8154 | 2023-11-19 19:00 | 2.4463 | 2.8987 | 2.8987 | 2.8987 | 2.8987
2024-01-19 20:00 | 1.7338 | 2.1568 | 2.6058 | 2.6657 | 2.7255 | 2023-11-19 20:00 | 2.233 | 2.6459 | 2.6459 | 2.6459 | 2.6459
2024-01-19 21:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2023-11-19 21:00 | 1.97 | 2.3343 | 2.3343 | 2.3343 | 2.3343
2024-01-19 22:00 | 1.7147 | 2.1331 | 2.5772 | 2.6364 | 2.6956 | 2023-11-19 22:00 | 1.7909 | 2.1221 | 2.1221 | 2.1221 | 2.1221
2024-01-19 23:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2023-11-19 23:00 | 1.7338 | 2.0544 | 2.0544 | 2.0544 | 2.0544
2024-01-20 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2023-11-20 | 1.6347 | 1.937 | 1.937 | 1.937 | 1.937
2024-01-20 01:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2023-11-20 01:00 | 1.6195 | 1.9189 | 1.9189 | 1.9189 | 1.9189
2024-01-20 02:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2023-11-20 02:00 | 1.6004 | 1.8964 | 1.8964 | 1.8964 | 1.8964
2024-01-20 03:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2023-11-20 03:00 | 1.7033 | 2.0183 | 2.0183 | 2.0183 | 2.0183
2024-01-20 04:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2023-11-20 04:00 | 1.871 | 2.2169 | 2.2169 | 2.2169 | 2.2169
2024-01-20 05:00 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2023-11-20 05:00 | 2.1834 | 2.5872 | 2.5872 | 2.5872 | 2.5872
2024-01-20 06:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2023-11-20 06:00 | 2.3968 | 2.84 | 2.84 | 2.84 | 2.84
2024-01-20 07:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2023-11-20 07:00 | 2.816 | 3.3367 | 3.3367 | 3.3367 | 3.3367
2024-01-20 08:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2023-11-20 08:00 | 3.7953 | 4.4971 | 4.4971 | 4.4971 | 4.4971
2024-01-20 09:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2023-11-20 09:00 | 3.6314 | 4.3029 | 4.3029 | 4.3029 | 4.3029
2024-01-20 10:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2023-11-20 10:00 | 3.7305 | 4.4203 | 4.4203 | 4.4203 | 4.4203
2024-01-20 11:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2023-11-20 11:00 | 3.8791 | 4.5964 | 4.5964 | 4.5964 | 4.5964
2024-01-20 12:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2023-11-20 12:00 | 3.9363 | 4.6641 | 4.6641 | 4.6641 | 4.6641
2024-01-20 13:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2023-11-20 13:00 | 3.681 | 4.3616 | 4.3616 | 4.3616 | 4.3616
2024-01-20 14:00 | 1.4289 | 1.7776 | 2.1476 | 2.197 | 2.2463 | 2023-11-20 14:00 | 4.0239 | 4.768 | 4.768 | 4.768 | 4.768
2024-01-20 15:00 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2023-11-20 15:00 | 3.8982 | 4.619 | 4.619 | 4.619 | 4.619
2024-01-20 16:00 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2023-11-20 16:00 | 3.8943 | 4.6145 | 4.6145 | 4.6145 | 4.6145
2024-01-20 17:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2023-11-20 17:00 | 3.5171 | 4.1675 | 4.1675 | 4.1675 | 4.1675
2024-01-20 18:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2023-11-20 18:00 | 3.0865 | 3.6573 | 3.6573 | 3.6573 | 3.6573
2024-01-20 19:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2023-11-20 19:00 | 2.7055 | 3.2057 | 3.2057 | 3.2057 | 3.2057
2024-01-20 20:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2023-11-20 20:00 | 2.3968 | 2.84 | 2.84 | 2.84 | 2.84
2024-01-20 21:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2023-11-20 21:00 | 2.1034 | 2.4924 | 2.4924 | 2.4924 | 2.4924
2024-01-20 22:00 | 1.6957 | 2.1094 | 2.5485 | 2.6071 | 2.6656 | 2023-11-20 22:00 | 1.9891 | 2.3569 | 2.3569 | 2.3569 | 2.3569
2024-01-20 23:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2023-11-20 23:00 | 1.7643 | 2.0905 | 2.0905 | 2.0905 | 2.0905
2024-01-21 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2023-11-21 | 1.6042 | 1.9009 | 1.9009 | 1.9009 | 1.9009
2024-01-21 01:00 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2023-11-21 01:00 | 1.669 | 1.9776 | 1.9776 | 1.9776 | 1.9776
2024-01-21 02:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2023-11-21 02:00 | 1.6652 | 1.9731 | 1.9731 | 1.9731 | 1.9731
2024-01-21 03:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2023-11-21 03:00 | 1.7376 | 2.0589 | 2.0589 | 2.0589 | 2.0589
2024-01-21 04:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2023-11-21 04:00 | 1.9472 | 2.3072 | 2.3072 | 2.3072 | 2.3072
2024-01-21 05:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2023-11-21 05:00 | 2.111 | 2.5014 | 2.5014 | 2.5014 | 2.5014
2024-01-21 06:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2023-11-21 06:00 | 2.2444 | 2.6594 | 2.6594 | 2.6594 | 2.6594
2024-01-21 07:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2023-11-21 07:00 | 2.595 | 3.0748 | 3.0748 | 3.0748 | 3.0748
2024-01-21 08:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2023-11-21 08:00 | 3.0637 | 3.6302 | 3.6302 | 3.6302 | 3.6302
2024-01-21 09:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2023-11-21 09:00 | 3.1551 | 3.7385 | 3.7385 | 3.7385 | 3.7385
2024-01-21 10:00 | 1.3527 | 1.6828 | 2.0331 | 2.0798 | 2.1265 | 2023-11-21 10:00 | 3.4523 | 4.0907 | 4.0907 | 4.0907 | 4.0907
2024-01-21 11:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2023-11-21 11:00 | 3.4485 | 4.0862 | 4.0862 | 4.0862 | 4.0862
2024-01-21 12:00 | 1.3718 | 1.7065 | 2.0617 | 2.1091 | 2.1565 | 2023-11-21 12:00 | 3.6848 | 4.3661 | 4.3661 | 4.3661 | 4.3661
2024-01-21 13:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2023-11-21 13:00 | 3.6886 | 4.3707 | 4.3707 | 4.3707 | 4.3707
2024-01-21 14:00 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2023-11-21 14:00 | 3.7953 | 4.4971 | 4.4971 | 4.4971 | 4.4971
2024-01-21 15:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2023-11-21 15:00 | 3.9782 | 4.7138 | 4.7138 | 4.7138 | 4.7138
2024-01-21 16:00 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2023-11-21 16:00 | 3.9934 | 4.7319 | 4.7319 | 4.7319 | 4.7319
2024-01-21 17:00 | 1.6957 | 2.1094 | 2.5485 | 2.6071 | 2.6656 | 2023-11-21 17:00 | 3.6009 | 4.2668 | 4.2668 | 4.2668 | 4.2668
2024-01-21 18:00 | 1.7338 | 2.1568 | 2.6058 | 2.6657 | 2.7255 | 2023-11-21 18:00 | 3.1703 | 3.7566 | 3.7566 | 3.7566 | 3.7566
2024-01-21 19:00 | 1.7528 | 2.1805 | 2.6344 | 2.695 | 2.7555 | 2023-11-21 19:00 | 2.6026 | 3.0838 | 3.0838 | 3.0838 | 3.0838
2024-01-21 20:00 | 1.7909 | 2.2279 | 2.6917 | 2.7535 | 2.8154 | 2023-11-21 20:00 | 2.3968 | 2.84 | 2.84 | 2.84 | 2.84
2024-01-21 21:00 | 1.7909 | 2.2279 | 2.6917 | 2.7535 | 2.8154 | 2023-11-21 21:00 | 2.3282 | 2.7587 | 2.7587 | 2.7587 | 2.7587
2024-01-21 22:00 | 1.7528 | 2.1805 | 2.6344 | 2.695 | 2.7555 | 2023-11-21 22:00 | 1.9129 | 2.2666 | 2.2666 | 2.2666 | 2.2666
2024-01-21 23:00 | 1.7147 | 2.1331 | 2.5772 | 2.6364 | 2.6956 | 2023-11-21 23:00 | 1.81 | 2.1447 | 2.1447 | 2.1447 | 2.1447
2024-01-22 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2023-11-22 | 1.608 | 1.9054 | 1.9054 | 1.9054 | 1.9054
2024-01-22 01:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2023-11-22 01:00 | 1.6728 | 1.9821 | 1.9821 | 1.9821 | 1.9821
2024-01-22 02:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2023-11-22 02:00 | 1.669 | 1.9776 | 1.9776 | 1.9776 | 1.9776
2024-01-22 03:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2023-11-22 03:00 | 1.7909 | 2.1221 | 2.1221 | 2.1221 | 2.1221
2024-01-22 04:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2023-11-22 04:00 | 2.0462 | 2.4246 | 2.4246 | 2.4246 | 2.4246
2024-01-22 05:00 | 1.7719 | 2.2042 | 2.6631 | 2.7242 | 2.7854 | 2023-11-22 05:00 | 2.1606 | 2.5601 | 2.5601 | 2.5601 | 2.5601
2024-01-22 06:00 | 1.9624 | 2.4412 | 2.9494 | 3.0172 | 3.0849 | 2023-11-22 06:00 | 2.3054 | 2.7317 | 2.7317 | 2.7317 | 2.7317
2024-01-22 07:00 | 2.3816 | 2.9626 | 3.5794 | 3.6616 | 3.7439 | 2023-11-22 07:00 | 2.5264 | 2.9935 | 2.9935 | 2.9935 | 2.9935
2024-01-22 08:00 | 2.4197 | 3.01 | 3.6367 | 3.7202 | 3.8038 | 2023-11-22 08:00 | 2.8312 | 3.3547 | 3.3547 | 3.3547 | 3.3547
2024-01-22 09:00 | 2.4197 | 3.01 | 3.6367 | 3.7202 | 3.8038 | 2023-11-22 09:00 | 3.2618 | 3.865 | 3.865 | 3.865 | 3.865
2024-01-22 10:00 | 2.4959 | 3.1048 | 3.7512 | 3.8374 | 3.9236 | 2023-11-22 10:00 | 3.2542 | 3.8559 | 3.8559 | 3.8559 | 3.8559
2024-01-22 11:00 | 2.6483 | 3.2944 | 3.9803 | 4.0717 | 4.1632 | 2023-11-22 11:00 | 3.3113 | 3.9237 | 3.9237 | 3.9237 | 3.9237
2024-01-22 12:00 | 2.8769 | 3.5788 | 4.3239 | 4.4232 | 4.5226 | 2023-11-22 12:00 | 3.6428 | 4.3165 | 4.3165 | 4.3165 | 4.3165
2024-01-22 13:00 | 2.8198 | 3.5077 | 4.238 | 4.3354 | 4.4327 | 2023-11-22 13:00 | 3.6848 | 4.3661 | 4.3661 | 4.3661 | 4.3661
2024-01-22 14:00 | 2.8198 | 3.5077 | 4.238 | 4.3354 | 4.4327 | 2023-11-22 14:00 | 4.0772 | 4.8312 | 4.8312 | 4.8312 | 4.8312
2024-01-22 15:00 | 2.7626 | 3.4366 | 4.1521 | 4.2475 | 4.3429 | 2023-11-22 15:00 | 3.9401 | 4.6687 | 4.6687 | 4.6687 | 4.6687
2024-01-22 16:00 | 2.6483 | 3.2944 | 3.9803 | 4.0717 | 4.1632 | 2023-11-22 16:00 | 3.8753 | 4.5919 | 4.5919 | 4.5919 | 4.5919
2024-01-22 17:00 | 2.534 | 3.1522 | 3.8085 | 3.896 | 3.9835 | 2023-11-22 17:00 | 3.6848 | 4.3661 | 4.3661 | 4.3661 | 4.3661
2024-01-22 18:00 | 2.1529 | 2.6782 | 3.2358 | 3.3101 | 3.3845 | 2023-11-22 18:00 | 3.2237 | 3.8198 | 3.8198 | 3.8198 | 3.8198
2024-01-22 19:00 | 1.8672 | 2.3227 | 2.8062 | 2.8707 | 2.9352 | 2023-11-22 19:00 | 2.8617 | 3.3909 | 3.3909 | 3.3909 | 3.3909
2024-01-22 20:00 | 1.7528 | 2.1805 | 2.6344 | 2.695 | 2.7555 | 2023-11-22 20:00 | 2.7893 | 3.3051 | 3.3051 | 3.3051 | 3.3051
2024-01-22 21:00 | 1.7719 | 2.2042 | 2.6631 | 2.7242 | 2.7854 | 2023-11-22 21:00 | 2.2863 | 2.7091 | 2.7091 | 2.7091 | 2.7091
2024-01-22 22:00 | 1.7719 | 2.2042 | 2.6631 | 2.7242 | 2.7854 | 2023-11-22 22:00 | 2.1301 | 2.524 | 2.524 | 2.524 | 2.524
2024-01-22 23:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2023-11-22 23:00 | 1.8862 | 2.235 | 2.235 | 2.235 | 2.235
2024-01-23 | 1.7719 | 2.2042 | 2.6631 | 2.7242 | 2.7854 | 2023-11-23 | 1.81 | 2.1447 | 2.1447 | 2.1447 | 2.1447
2024-01-23 01:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2023-11-23 01:00 | 1.6309 | 1.9325 | 1.9325 | 1.9325 | 1.9325
2024-01-23 02:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2023-11-23 02:00 | 1.6728 | 1.9821 | 1.9821 | 1.9821 | 1.9821
2024-01-23 03:00 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2023-11-23 03:00 | 1.7528 | 2.077 | 2.077 | 2.077 | 2.077
2024-01-23 04:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2023-11-23 04:00 | 1.8862 | 2.235 | 2.235 | 2.235 | 2.235
2024-01-23 05:00 | 1.7338 | 2.1568 | 2.6058 | 2.6657 | 2.7255 | 2023-11-23 05:00 | 2.3092 | 2.7362 | 2.7362 | 2.7362 | 2.7362
2024-01-23 06:00 | 1.8862 | 2.3464 | 2.8349 | 2.9 | 2.9651 | 2023-11-23 06:00 | 2.2787 | 2.7001 | 2.7001 | 2.7001 | 2.7001
2024-01-23 07:00 | 2.3625 | 2.9389 | 3.5508 | 3.6323 | 3.7139 | 2023-11-23 07:00 | 2.5797 | 3.0567 | 3.0567 | 3.0567 | 3.0567
2024-01-23 08:00 | 2.4006 | 2.9863 | 3.608 | 3.6909 | 3.7738 | 2023-11-23 08:00 | 3.1361 | 3.716 | 3.716 | 3.716 | 3.716
2024-01-23 09:00 | 2.3816 | 2.9626 | 3.5794 | 3.6616 | 3.7439 | 2023-11-23 09:00 | 3.2885 | 3.8966 | 3.8966 | 3.8966 | 3.8966
2024-01-23 10:00 | 2.4006 | 2.9863 | 3.608 | 3.6909 | 3.7738 | 2023-11-23 10:00 | 3.3952 | 4.023 | 4.023 | 4.023 | 4.023
2024-01-23 11:00 | 2.4197 | 3.01 | 3.6367 | 3.7202 | 3.8038 | 2023-11-23 11:00 | 3.6695 | 4.3481 | 4.3481 | 4.3481 | 4.3481
2024-01-23 12:00 | 2.6483 | 3.2944 | 3.9803 | 4.0717 | 4.1632 | 2023-11-23 12:00 | 3.6695 | 4.3481 | 4.3481 | 4.3481 | 4.3481
2024-01-23 13:00 | 2.6293 | 3.2707 | 3.9516 | 4.0424 | 4.1332 | 2023-11-23 13:00 | 3.8219 | 4.5287 | 4.5287 | 4.5287 | 4.5287
2024-01-23 14:00 | 2.8007 | 3.484 | 4.2094 | 4.3061 | 4.4028 | 2023-11-23 14:00 | 3.6543 | 4.33 | 4.33 | 4.33 | 4.33
2024-01-23 15:00 | 2.8007 | 3.484 | 4.2094 | 4.3061 | 4.4028 | 2023-11-23 15:00 | 3.6543 | 4.33 | 4.33 | 4.33 | 4.33
2024-01-23 16:00 | 2.7245 | 3.3892 | 4.0948 | 4.1889 | 4.283 | 2023-11-23 16:00 | 3.6848 | 4.3661 | 4.3661 | 4.3661 | 4.3661
2024-01-23 17:00 | 2.6483 | 3.2944 | 3.9803 | 4.0717 | 4.1632 | 2023-11-23 17:00 | 3.319 | 3.9327 | 3.9327 | 3.9327 | 3.9327
2024-01-23 18:00 | 2.4578 | 3.0574 | 3.6939 | 3.7788 | 3.8637 | 2023-11-23 18:00 | 2.835 | 3.3593 | 3.3593 | 3.3593 | 3.3593
2024-01-23 19:00 | 1.9243 | 2.3938 | 2.8921 | 2.9586 | 3.025 | 2023-11-23 19:00 | 2.7855 | 3.3006 | 3.3006 | 3.3006 | 3.3006
2024-01-23 20:00 | 1.81 | 2.2516 | 2.7203 | 2.7828 | 2.8453 | 2023-11-23 20:00 | 2.4883 | 2.9484 | 2.9484 | 2.9484 | 2.9484
2024-01-23 21:00 | 1.829 | 2.2753 | 2.749 | 2.8121 | 2.8753 | 2023-11-23 21:00 | 2.4121 | 2.8581 | 2.8581 | 2.8581 | 2.8581
2024-01-23 22:00 | 1.7909 | 2.2279 | 2.6917 | 2.7535 | 2.8154 | 2023-11-23 22:00 | 2.1987 | 2.6052 | 2.6052 | 2.6052 | 2.6052
2024-01-23 23:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2023-11-23 23:00 | 1.8405 | 2.1808 | 2.1808 | 2.1808 | 2.1808
2024-01-24 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2023-11-24 | 1.6957 | 2.0092 | 2.0092 | 2.0092 | 2.0092
2024-01-24 01:00 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2023-11-24 01:00 | 1.6995 | 2.0138 | 2.0138 | 2.0138 | 2.0138
2024-01-24 02:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2023-11-24 02:00 | 1.73 | 2.0499 | 2.0499 | 2.0499 | 2.0499
2024-01-24 03:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2023-11-24 03:00 | 1.8252 | 2.1628 | 2.1628 | 2.1628 | 2.1628
2024-01-24 04:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2023-11-24 04:00 | 2.0158 | 2.3885 | 2.3885 | 2.3885 | 2.3885
2024-01-24 05:00 | 1.6957 | 2.1094 | 2.5485 | 2.6071 | 2.6656 | 2023-11-24 05:00 | 2.2825 | 2.7046 | 2.7046 | 2.7046 | 2.7046
2024-01-24 06:00 | 1.7719 | 2.2042 | 2.6631 | 2.7242 | 2.7854 | 2023-11-24 06:00 | 2.393 | 2.8355 | 2.8355 | 2.8355 | 2.8355
2024-01-24 07:00 | 2.4006 | 2.9863 | 3.608 | 3.6909 | 3.7738 | 2023-11-24 07:00 | 2.8312 | 3.3547 | 3.3547 | 3.3547 | 3.3547
2024-01-24 08:00 | 2.4387 | 3.0337 | 3.6653 | 3.7495 | 3.8337 | 2023-11-24 08:00 | 3.319 | 3.9327 | 3.9327 | 3.9327 | 3.9327
2024-01-24 09:00 | 2.5911 | 3.2233 | 3.8944 | 3.9838 | 4.0733 | 2023-11-24 09:00 | 3.3723 | 3.9959 | 3.9959 | 3.9959 | 3.9959
2024-01-24 10:00 | 2.7436 | 3.4129 | 4.1235 | 4.2182 | 4.3129 | 2023-11-24 10:00 | 3.7076 | 4.3932 | 4.3932 | 4.3932 | 4.3932
2024-01-24 11:00 | 2.7436 | 3.4129 | 4.1235 | 4.2182 | 4.3129 | 2023-11-24 11:00 | 3.8562 | 4.5693 | 4.5693 | 4.5693 | 4.5693
2024-01-24 12:00 | 2.896 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2023-11-24 12:00 | 4.1306 | 4.8944 | 4.8944 | 4.8944 | 4.8944
2024-01-24 13:00 | 2.8579 | 3.5551 | 4.2953 | 4.3939 | 4.4926 | 2023-11-24 13:00 | 3.8982 | 4.619 | 4.619 | 4.619 | 4.619
2024-01-24 14:00 | 2.8388 | 3.5314 | 4.2666 | 4.3647 | 4.4627 | 2023-11-24 14:00 | 3.9972 | 4.7364 | 4.7364 | 4.7364 | 4.7364
2024-01-24 15:00 | 2.6864 | 3.3418 | 4.0375 | 4.1303 | 4.2231 | 2023-11-24 15:00 | 3.7991 | 4.5016 | 4.5016 | 4.5016 | 4.5016
2024-01-24 16:00 | 2.7245 | 3.3892 | 4.0948 | 4.1889 | 4.283 | 2023-11-24 16:00 | 3.9439 | 4.6732 | 4.6732 | 4.6732 | 4.6732
2024-01-24 17:00 | 2.553 | 3.1759 | 3.8371 | 3.9253 | 4.0134 | 2023-11-24 17:00 | 3.5857 | 4.2487 | 4.2487 | 4.2487 | 4.2487
2024-01-24 18:00 | 2.2863 | 2.8441 | 3.4362 | 3.5152 | 3.5941 | 2023-11-24 18:00 | 3.197 | 3.7882 | 3.7882 | 3.7882 | 3.7882
2024-01-24 19:00 | 1.9624 | 2.4412 | 2.9494 | 3.0172 | 3.0849 | 2023-11-24 19:00 | 3.0141 | 3.5715 | 3.5715 | 3.5715 | 3.5715
2024-01-24 20:00 | 1.9243 | 2.3938 | 2.8921 | 2.9586 | 3.025 | 2023-11-24 20:00 | 2.9417 | 3.4857 | 3.4857 | 3.4857 | 3.4857
2024-01-24 21:00 | 1.8672 | 2.3227 | 2.8062 | 2.8707 | 2.9352 | 2023-11-24 21:00 | 2.4806 | 2.9394 | 2.9394 | 2.9394 | 2.9394
2024-01-24 22:00 | 1.829 | 2.2753 | 2.749 | 2.8121 | 2.8753 | 2023-11-24 22:00 | 2.1034 | 2.4924 | 2.4924 | 2.4924 | 2.4924
2024-01-24 23:00 | 1.7338 | 2.1568 | 2.6058 | 2.6657 | 2.7255 | 2023-11-24 23:00 | 1.8862 | 2.235 | 2.235 | 2.235 | 2.235
2024-01-25 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2023-11-25 | 1.6195 | 1.9189 | 1.9189 | 1.9189 | 1.9189
2024-01-25 01:00 | 1.6957 | 2.1094 | 2.5485 | 2.6071 | 2.6656 | 2023-11-25 01:00 | 1.6347 | 1.937 | 1.937 | 1.937 | 1.937
2024-01-25 02:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2023-11-25 02:00 | 1.6461 | 1.9505 | 1.9505 | 1.9505 | 1.9505
2024-01-25 03:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2023-11-25 03:00 | 1.6957 | 2.0092 | 2.0092 | 2.0092 | 2.0092
2024-01-25 04:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2023-11-25 04:00 | 1.8976 | 2.2485 | 2.2485 | 2.2485 | 2.2485
2024-01-25 05:00 | 1.6957 | 2.1094 | 2.5485 | 2.6071 | 2.6656 | 2023-11-25 05:00 | 2.2711 | 2.691 | 2.691 | 2.691 | 2.691
2024-01-25 06:00 | 2.0767 | 2.5834 | 3.1212 | 3.1929 | 3.2646 | 2023-11-25 06:00 | 2.1987 | 2.6052 | 2.6052 | 2.6052 | 2.6052
2024-01-25 07:00 | 2.534 | 3.1522 | 3.8085 | 3.896 | 3.9835 | 2023-11-25 07:00 | 2.4273 | 2.8761 | 2.8761 | 2.8761 | 2.8761
2024-01-25 08:00 | 2.5911 | 3.2233 | 3.8944 | 3.9838 | 4.0733 | 2023-11-25 08:00 | 2.9303 | 3.4721 | 3.4721 | 3.4721 | 3.4721
2024-01-25 09:00 | 2.7055 | 3.3655 | 4.0662 | 4.1596 | 4.253 | 2023-11-25 09:00 | 2.9531 | 3.4992 | 3.4992 | 3.4992 | 3.4992
2024-01-25 10:00 | 2.896 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2023-11-25 10:00 | 3.2123 | 3.8063 | 3.8063 | 3.8063 | 3.8063
2024-01-25 11:00 | 2.896 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2023-11-25 11:00 | 3.2847 | 3.892 | 3.892 | 3.892 | 3.892
2024-01-25 12:00 | 2.9722 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2023-11-25 12:00 | 3.3456 | 3.9643 | 3.9643 | 3.9643 | 3.9643
2024-01-25 13:00 | 2.9722 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2023-11-25 13:00 | 3.3723 | 3.9959 | 3.9959 | 3.9959 | 3.9959
2024-01-25 14:00 | 2.9531 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2023-11-25 14:00 | 3.5781 | 4.2397 | 4.2397 | 4.2397 | 4.2397
2024-01-25 15:00 | 2.9722 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2023-11-25 15:00 | 3.6543 | 4.33 | 4.33 | 4.33 | 4.33
2024-01-25 16:00 | 2.8769 | 3.5788 | 4.3239 | 4.4232 | 4.5226 | 2023-11-25 16:00 | 3.4714 | 4.1133 | 4.1133 | 4.1133 | 4.1133
2024-01-25 17:00 | 2.6864 | 3.3418 | 4.0375 | 4.1303 | 4.2231 | 2023-11-25 17:00 | 3.3342 | 3.9507 | 3.9507 | 3.9507 | 3.9507
2024-01-25 18:00 | 2.2673 | 2.8204 | 3.4076 | 3.4859 | 3.5642 | 2023-11-25 18:00 | 2.6445 | 3.1335 | 3.1335 | 3.1335 | 3.1335
2024-01-25 19:00 | 2.0958 | 2.6071 | 3.1499 | 3.2222 | 3.2946 | 2023-11-25 19:00 | 2.6178 | 3.1019 | 3.1019 | 3.1019 | 3.1019
2024-01-25 20:00 | 1.8862 | 2.3464 | 2.8349 | 2.9 | 2.9651 | 2023-11-25 20:00 | 2.4959 | 2.9574 | 2.9574 | 2.9574 | 2.9574
2024-01-25 21:00 | 1.829 | 2.2753 | 2.749 | 2.8121 | 2.8753 | 2023-11-25 21:00 | 2.2253 | 2.6368 | 2.6368 | 2.6368 | 2.6368
2024-01-25 22:00 | 1.8481 | 2.299 | 2.7776 | 2.8414 | 2.9052 | 2023-11-25 22:00 | 2.0005 | 2.3704 | 2.3704 | 2.3704 | 2.3704
2024-01-25 23:00 | 1.81 | 2.2516 | 2.7203 | 2.7828 | 2.8453 | 2023-11-25 23:00 | 1.7948 | 2.1266 | 2.1266 | 2.1266 | 2.1266
2024-01-26 | 1.6957 | 2.1094 | 2.5485 | 2.6071 | 2.6656 | 2023-11-26 | 1.6842 | 1.9957 | 1.9957 | 1.9957 | 1.9957
2024-01-26 01:00 | 1.7147 | 2.1331 | 2.5772 | 2.6364 | 2.6956 | 2023-11-26 01:00 | 1.6881 | 2.0002 | 2.0002 | 2.0002 | 2.0002
2024-01-26 02:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2023-11-26 02:00 | 1.6309 | 1.9325 | 1.9325 | 1.9325 | 1.9325
2024-01-26 03:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2023-11-26 03:00 | 1.8024 | 2.1357 | 2.1357 | 2.1357 | 2.1357
2024-01-26 04:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2023-11-26 04:00 | 1.9929 | 2.3614 | 2.3614 | 2.3614 | 2.3614
2024-01-26 05:00 | 1.7338 | 2.1568 | 2.6058 | 2.6657 | 2.7255 | 2023-11-26 05:00 | 2.1644 | 2.5646 | 2.5646 | 2.5646 | 2.5646
2024-01-26 06:00 | 1.9243 | 2.3938 | 2.8921 | 2.9586 | 3.025 | 2023-11-26 06:00 | 2.1834 | 2.5872 | 2.5872 | 2.5872 | 2.5872
2024-01-26 07:00 | 1.829 | 2.2753 | 2.749 | 2.8121 | 2.8753 | 2023-11-26 07:00 | 2.0843 | 2.4698 | 2.4698 | 2.4698 | 2.4698
2024-01-26 08:00 | 1.829 | 2.2753 | 2.749 | 2.8121 | 2.8753 | 2023-11-26 08:00 | 2.2253 | 2.6368 | 2.6368 | 2.6368 | 2.6368
2024-01-26 09:00 | 1.829 | 2.2753 | 2.749 | 2.8121 | 2.8753 | 2023-11-26 09:00 | 2.7588 | 3.269 | 3.269 | 3.269 | 3.269
2024-01-26 10:00 | 1.829 | 2.2753 | 2.749 | 2.8121 | 2.8753 | 2023-11-26 10:00 | 3.3037 | 3.9146 | 3.9146 | 3.9146 | 3.9146
2024-01-26 11:00 | 1.829 | 2.2753 | 2.749 | 2.8121 | 2.8753 | 2023-11-26 11:00 | 3.5171 | 4.1675 | 4.1675 | 4.1675 | 4.1675
2024-01-26 12:00 | 1.829 | 2.2753 | 2.749 | 2.8121 | 2.8753 | 2023-11-26 12:00 | 3.4371 | 4.0727 | 4.0727 | 4.0727 | 4.0727
2024-01-26 13:00 | 1.829 | 2.2753 | 2.749 | 2.8121 | 2.8753 | 2023-11-26 13:00 | 3.6886 | 4.3707 | 4.3707 | 4.3707 | 4.3707
2024-01-26 14:00 | 1.829 | 2.2753 | 2.749 | 2.8121 | 2.8753 | 2023-11-26 14:00 | 3.7229 | 4.4113 | 4.4113 | 4.4113 | 4.4113
2024-01-26 15:00 | 1.829 | 2.2753 | 2.749 | 2.8121 | 2.8753 | 2023-11-26 15:00 | 3.5857 | 4.2487 | 4.2487 | 4.2487 | 4.2487
2024-01-26 16:00 | 1.829 | 2.2753 | 2.749 | 2.8121 | 2.8753 | 2023-11-26 16:00 | 3.1475 | 3.7295 | 3.7295 | 3.7295 | 3.7295
2024-01-26 17:00 | 2.0386 | 2.536 | 3.064 | 3.1344 | 3.2047 | 2023-11-26 17:00 | 3.3228 | 3.9372 | 3.9372 | 3.9372 | 3.9372
2024-01-26 18:00 | 1.81 | 2.2516 | 2.7203 | 2.7828 | 2.8453 | 2023-11-26 18:00 | 2.7321 | 3.2374 | 3.2374 | 3.2374 | 3.2374
2024-01-26 19:00 | 1.7909 | 2.2279 | 2.6917 | 2.7535 | 2.8154 | 2023-11-26 19:00 | 2.4044 | 2.8491 | 2.8491 | 2.8491 | 2.8491
2024-01-26 20:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2023-11-26 20:00 | 2.2825 | 2.7046 | 2.7046 | 2.7046 | 2.7046
2024-01-26 21:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2023-11-26 21:00 | 2.2368 | 2.6504 | 2.6504 | 2.6504 | 2.6504
2024-01-26 22:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2023-11-26 22:00 | 2.0196 | 2.393 | 2.393 | 2.393 | 2.393
2024-01-26 23:00 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2023-11-26 23:00 | 1.7986 | 2.1311 | 2.1311 | 2.1311 | 2.1311
2024-01-27 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2023-11-27 | 1.7605 | 2.086 | 2.086 | 2.086 | 2.086
2024-01-27 01:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2023-11-27 01:00 | 1.73 | 2.0499 | 2.0499 | 2.0499 | 2.0499
2024-01-27 02:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2023-11-27 02:00 | 1.7033 | 2.0183 | 2.0183 | 2.0183 | 2.0183
2024-01-27 03:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2023-11-27 03:00 | 1.8672 | 2.2124 | 2.2124 | 2.2124 | 2.2124
2024-01-27 04:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2023-11-27 04:00 | 1.9205 | 2.2756 | 2.2756 | 2.2756 | 2.2756
2024-01-27 05:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2023-11-27 05:00 | 2.2177 | 2.6278 | 2.6278 | 2.6278 | 2.6278
2024-01-27 06:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2023-11-27 06:00 | 2.3663 | 2.8039 | 2.8039 | 2.8039 | 2.8039
2024-01-27 07:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2023-11-27 07:00 | 2.6445 | 3.1335 | 3.1335 | 3.1335 | 3.1335
2024-01-27 08:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2023-11-27 08:00 | 3.117 | 3.6934 | 3.6934 | 3.6934 | 3.6934
2024-01-27 09:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2023-11-27 09:00 | 3.6733 | 4.3526 | 4.3526 | 4.3526 | 4.3526
2024-01-27 10:00 | 1.4099 | 1.7539 | 2.119 | 2.1677 | 2.2164 | 2023-11-27 10:00 | 3.9591 | 4.6912 | 4.6912 | 4.6912 | 4.6912
2024-01-27 11:00 | 1.2956 | 1.6117 | 1.9472 | 1.9919 | 2.0367 | 2023-11-27 11:00 | 4.0163 | 4.759 | 4.759 | 4.759 | 4.759
2024-01-27 12:00 | 1.3146 | 1.6354 | 1.9758 | 2.0212 | 2.0666 | 2023-11-27 12:00 | 3.8639 | 4.5784 | 4.5784 | 4.5784 | 4.5784
2024-01-27 13:00 | 1.2575 | 1.5643 | 1.8899 | 1.9333 | 1.9768 | 2023-11-27 13:00 | 3.9591 | 4.6912 | 4.6912 | 4.6912 | 4.6912
2024-01-27 14:00 | 1.2956 | 1.6117 | 1.9472 | 1.9919 | 2.0367 | 2023-11-27 14:00 | 3.9972 | 4.7364 | 4.7364 | 4.7364 | 4.7364
2024-01-27 15:00 | 1.3718 | 1.7065 | 2.0617 | 2.1091 | 2.1565 | 2023-11-27 15:00 | 3.761 | 4.4564 | 4.4564 | 4.4564 | 4.4564
2024-01-27 16:00 | 1.3908 | 1.7302 | 2.0904 | 2.1384 | 2.1864 | 2023-11-27 16:00 | 3.9667 | 4.7003 | 4.7003 | 4.7003 | 4.7003
2024-01-27 17:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2023-11-27 17:00 | 3.7648 | 4.461 | 4.461 | 4.461 | 4.461
2024-01-27 18:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2023-11-27 18:00 | 3.2656 | 3.8695 | 3.8695 | 3.8695 | 3.8695
2024-01-27 19:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2023-11-27 19:00 | 3.0789 | 3.6482 | 3.6482 | 3.6482 | 3.6482
2024-01-27 20:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2023-11-27 20:00 | 2.6254 | 3.1109 | 3.1109 | 3.1109 | 3.1109
2024-01-27 21:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2023-11-27 21:00 | 2.1377 | 2.533 | 2.533 | 2.533 | 2.533
2024-01-27 22:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2023-11-27 22:00 | 1.9053 | 2.2576 | 2.2576 | 2.2576 | 2.2576
2024-01-27 23:00 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2023-11-27 23:00 | 1.7376 | 2.0589 | 2.0589 | 2.0589 | 2.0589
2024-01-28 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2023-11-28 | 1.6271 | 1.928 | 1.928 | 1.928 | 1.928
2024-01-28 01:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2023-11-28 01:00 | 1.7071 | 2.0228 | 2.0228 | 2.0228 | 2.0228
2024-01-28 02:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2023-11-28 02:00 | 1.6881 | 2.0002 | 2.0002 | 2.0002 | 2.0002
2024-01-28 03:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2023-11-28 03:00 | 1.7414 | 2.0634 | 2.0634 | 2.0634 | 2.0634
2024-01-28 04:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2023-11-28 04:00 | 1.9053 | 2.2576 | 2.2576 | 2.2576 | 2.2576
2024-01-28 05:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2023-11-28 05:00 | 2.2215 | 2.6323 | 2.6323 | 2.6323 | 2.6323
2024-01-28 06:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2023-11-28 06:00 | 2.4349 | 2.8852 | 2.8852 | 2.8852 | 2.8852
2024-01-28 07:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2023-11-28 07:00 | 2.7664 | 3.278 | 3.278 | 3.278 | 3.278
2024-01-28 08:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2023-11-28 08:00 | 3.4714 | 4.1133 | 4.1133 | 4.1133 | 4.1133
2024-01-28 09:00 | 1.3718 | 1.7065 | 2.0617 | 2.1091 | 2.1565 | 2023-11-28 09:00 | 3.902 | 4.6235 | 4.6235 | 4.6235 | 4.6235
2024-01-28 10:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2023-11-28 10:00 | 3.7838 | 4.4835 | 4.4835 | 4.4835 | 4.4835
2024-01-28 11:00 | 1.3337 | 1.6591 | 2.0045 | 2.0505 | 2.0966 | 2023-11-28 11:00 | 3.9515 | 4.6822 | 4.6822 | 4.6822 | 4.6822
2024-01-28 12:00 | 1.3146 | 1.6354 | 1.9758 | 2.0212 | 2.0666 | 2023-11-28 12:00 | 3.7991 | 4.5016 | 4.5016 | 4.5016 | 4.5016
2024-01-28 13:00 | 1.3337 | 1.6591 | 2.0045 | 2.0505 | 2.0966 | 2023-11-28 13:00 | 3.9553 | 4.6867 | 4.6867 | 4.6867 | 4.6867
2024-01-28 14:00 | 1.3718 | 1.7065 | 2.0617 | 2.1091 | 2.1565 | 2023-11-28 14:00 | 3.8943 | 4.6145 | 4.6145 | 4.6145 | 4.6145
2024-01-28 15:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2023-11-28 15:00 | 3.9324 | 4.6596 | 4.6596 | 4.6596 | 4.6596
2024-01-28 16:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2023-11-28 16:00 | 3.5895 | 4.2533 | 4.2533 | 4.2533 | 4.2533
2024-01-28 17:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2023-11-28 17:00 | 3.399 | 4.0275 | 4.0275 | 4.0275 | 4.0275
2024-01-28 18:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2023-11-28 18:00 | 2.976 | 3.5263 | 3.5263 | 3.5263 | 3.5263
2024-01-28 19:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2023-11-28 19:00 | 2.7093 | 3.2103 | 3.2103 | 3.2103 | 3.2103
2024-01-28 20:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2023-11-28 20:00 | 2.4692 | 2.9258 | 2.9258 | 2.9258 | 2.9258
2024-01-28 21:00 | 1.6957 | 2.1094 | 2.5485 | 2.6071 | 2.6656 | 2023-11-28 21:00 | 2.1949 | 2.6007 | 2.6007 | 2.6007 | 2.6007
2024-01-28 22:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2023-11-28 22:00 | 1.9586 | 2.3208 | 2.3208 | 2.3208 | 2.3208
2024-01-28 23:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2023-11-28 23:00 | 1.8367 | 2.1763 | 2.1763 | 2.1763 | 2.1763
2024-01-29 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2023-11-29 | 1.6614 | 1.9686 | 1.9686 | 1.9686 | 1.9686
2024-01-29 01:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2023-11-29 01:00 | 1.7376 | 2.0589 | 2.0589 | 2.0589 | 2.0589
2024-01-29 02:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2023-11-29 02:00 | 1.7338 | 2.0544 | 2.0544 | 2.0544 | 2.0544
2024-01-29 03:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2023-11-29 03:00 | 1.7643 | 2.0905 | 2.0905 | 2.0905 | 2.0905
2024-01-29 04:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2023-11-29 04:00 | 1.8672 | 2.2124 | 2.2124 | 2.2124 | 2.2124
2024-01-29 05:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2023-11-29 05:00 | 2.1301 | 2.524 | 2.524 | 2.524 | 2.524
2024-01-29 06:00 | 1.9624 | 2.4412 | 2.9494 | 3.0172 | 3.0849 | 2023-11-29 06:00 | 2.3435 | 2.7768 | 2.7768 | 2.7768 | 2.7768
2024-01-29 07:00 | 2.191 | 2.7256 | 3.293 | 3.3687 | 3.4444 | 2023-11-29 07:00 | 2.8579 | 3.3864 | 3.3864 | 3.3864 | 3.3864
2024-01-29 08:00 | 2.5911 | 3.2233 | 3.8944 | 3.9838 | 4.0733 | 2023-11-29 08:00 | 3.2885 | 3.8966 | 3.8966 | 3.8966 | 3.8966
2024-01-29 09:00 | 2.6674 | 3.3181 | 4.0089 | 4.101 | 4.1931 | 2023-11-29 09:00 | 3.5095 | 4.1584 | 4.1584 | 4.1584 | 4.1584
2024-01-29 10:00 | 2.7245 | 3.3892 | 4.0948 | 4.1889 | 4.283 | 2023-11-29 10:00 | 3.5362 | 4.19 | 4.19 | 4.19 | 4.19
2024-01-29 11:00 | 2.8198 | 3.5077 | 4.238 | 4.3354 | 4.4327 | 2023-11-29 11:00 | 3.4676 | 4.1088 | 4.1088 | 4.1088 | 4.1088
2024-01-29 12:00 | 2.9531 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2023-11-29 12:00 | 3.6162 | 4.2849 | 4.2849 | 4.2849 | 4.2849
2024-01-29 13:00 | 3.1437 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2023-11-29 13:00 | 3.8791 | 4.5964 | 4.5964 | 4.5964 | 4.5964
2024-01-29 14:00 | 2.896 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2023-11-29 14:00 | 3.4828 | 4.1268 | 4.1268 | 4.1268 | 4.1268
2024-01-29 15:00 | 3.0484 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2023-11-29 15:00 | 3.277 | 3.883 | 3.883 | 3.883 | 3.883
2024-01-29 16:00 | 2.9531 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2023-11-29 16:00 | 3.4028 | 4.032 | 4.032 | 4.032 | 4.032
2024-01-29 17:00 | 2.8769 | 3.5788 | 4.3239 | 4.4232 | 4.5226 | 2023-11-29 17:00 | 3.1208 | 3.6979 | 3.6979 | 3.6979 | 3.6979
2024-01-29 18:00 | 2.6483 | 3.2944 | 3.9803 | 4.0717 | 4.1632 | 2023-11-29 18:00 | 3.0027 | 3.5579 | 3.5579 | 3.5579 | 3.5579
2024-01-29 19:00 | 2.2291 | 2.773 | 3.3503 | 3.4273 | 3.5043 | 2023-11-29 19:00 | 2.6521 | 3.1425 | 3.1425 | 3.1425 | 3.1425
2024-01-29 20:00 | 1.9053 | 2.3701 | 2.8635 | 2.9293 | 2.9951 | 2023-11-29 20:00 | 2.5721 | 3.0477 | 3.0477 | 3.0477 | 3.0477
2024-01-29 21:00 | 1.8862 | 2.3464 | 2.8349 | 2.9 | 2.9651 | 2023-11-29 21:00 | 2.2063 | 2.6143 | 2.6143 | 2.6143 | 2.6143
2024-01-29 22:00 | 1.829 | 2.2753 | 2.749 | 2.8121 | 2.8753 | 2023-11-29 22:00 | 1.9853 | 2.3524 | 2.3524 | 2.3524 | 2.3524
2024-01-29 23:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2023-11-29 23:00 | 1.9014 | 2.2531 | 2.2531 | 2.2531 | 2.2531
2024-01-30 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2023-11-30 | 1.6728 | 1.9821 | 1.9821 | 1.9821 | 1.9821
2024-01-30 01:00 | 1.6957 | 2.1094 | 2.5485 | 2.6071 | 2.6656 | 2023-11-30 01:00 | 1.7414 | 2.0634 | 2.0634 | 2.0634 | 2.0634
2024-01-30 02:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2023-11-30 02:00 | 1.73 | 2.0499 | 2.0499 | 2.0499 | 2.0499
2024-01-30 03:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2023-11-30 03:00 | 1.8024 | 2.1357 | 2.1357 | 2.1357 | 2.1357
2024-01-30 04:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2023-11-30 04:00 | 2.0767 | 2.4608 | 2.4608 | 2.4608 | 2.4608
2024-01-30 05:00 | 1.7338 | 2.1568 | 2.6058 | 2.6657 | 2.7255 | 2023-11-30 05:00 | 2.1263 | 2.5194 | 2.5194 | 2.5194 | 2.5194
2024-01-30 06:00 | 1.9434 | 2.4175 | 2.9208 | 2.9879 | 3.055 | 2023-11-30 06:00 | 2.2749 | 2.6955 | 2.6955 | 2.6955 | 2.6955
2024-01-30 07:00 | 2.2101 | 2.7493 | 3.3217 | 3.398 | 3.4743 | 2023-11-30 07:00 | 2.5149 | 2.98 | 2.98 | 2.98 | 2.98
2024-01-30 08:00 | 2.4959 | 3.1048 | 3.7512 | 3.8374 | 3.9236 | 2023-11-30 08:00 | 3.1513 | 3.734 | 3.734 | 3.734 | 3.734
2024-01-30 09:00 | 2.6674 | 3.3181 | 4.0089 | 4.101 | 4.1931 | 2023-11-30 09:00 | 3.1361 | 3.716 | 3.716 | 3.716 | 3.716
2024-01-30 10:00 | 2.7245 | 3.3892 | 4.0948 | 4.1889 | 4.283 | 2023-11-30 10:00 | 3.3571 | 3.9778 | 3.9778 | 3.9778 | 3.9778
2024-01-30 11:00 | 2.8769 | 3.5788 | 4.3239 | 4.4232 | 4.5226 | 2023-11-30 11:00 | 3.4028 | 4.032 | 4.032 | 4.032 | 4.032
2024-01-30 12:00 | 3.0484 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2023-11-30 12:00 | 3.319 | 3.9327 | 3.9327 | 3.9327 | 3.9327
2024-01-30 13:00 | 3.1818 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2023-11-30 13:00 | 3.4104 | 4.041 | 4.041 | 4.041 | 4.041
2024-01-30 14:00 | 3.1627 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2023-11-30 14:00 | 3.5628 | 4.2217 | 4.2217 | 4.2217 | 4.2217
2024-01-30 15:00 | 3.0675 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2023-11-30 15:00 | 3.7 | 4.3842 | 4.3842 | 4.3842 | 4.3842
2024-01-30 16:00 | 2.9722 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2023-11-30 16:00 | 3.7229 | 4.4113 | 4.4113 | 4.4113 | 4.4113
2024-01-30 17:00 | 2.915 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2023-11-30 17:00 | 3.7152 | 4.4023 | 4.4023 | 4.4023 | 4.4023
2024-01-30 18:00 | 2.4578 | 3.0574 | 3.6939 | 3.7788 | 3.8637 | 2023-11-30 18:00 | 2.9417 | 3.4857 | 3.4857 | 3.4857 | 3.4857
2024-01-30 19:00 | 2.3054 | 2.8678 | 3.4648 | 3.5445 | 3.6241 | 2023-11-30 19:00 | 2.915 | 3.4541 | 3.4541 | 3.4541 | 3.4541
2024-01-30 20:00 | 1.8862 | 2.3464 | 2.8349 | 2.9 | 2.9651 | 2023-11-30 20:00 | 2.553 | 3.0251 | 3.0251 | 3.0251 | 3.0251
2024-01-30 21:00 | 1.8862 | 2.3464 | 2.8349 | 2.9 | 2.9651 | 2023-11-30 21:00 | 2.332 | 2.7633 | 2.7633 | 2.7633 | 2.7633
2024-01-30 22:00 | 1.8862 | 2.3464 | 2.8349 | 2.9 | 2.9651 | 2023-11-30 22:00 | 2.0958 | 2.4833 | 2.4833 | 2.4833 | 2.4833
2024-01-30 23:00 | 1.81 | 2.2516 | 2.7203 | 2.7828 | 2.8453 | 2023-11-30 23:00 | 1.8557 | 2.1989 | 2.1989 | 2.1989 | 2.1989
2024-01-31 | 1.81 | 2.2516 | 2.7203 | 2.7828 | 2.8453 | 2023-12-01 | 1.8557 | 2.1989 | 2.1989 | 2.1989 | 2.1989
2024-01-31 01:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2023-12-01 01:00 | 1.6766 | 1.9867 | 1.9867 | 1.9867 | 1.9867
2024-01-31 02:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2023-12-01 02:00 | 1.6195 | 1.9189 | 1.9189 | 1.9189 | 1.9189
2024-01-31 03:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2023-12-01 03:00 | 1.8367 | 2.1763 | 2.1763 | 2.1763 | 2.1763
2024-01-31 04:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2023-12-01 04:00 | 2.0196 | 2.393 | 2.393 | 2.393 | 2.393
2024-01-31 05:00 | 1.7528 | 2.1805 | 2.6344 | 2.695 | 2.7555 | 2023-12-01 05:00 | 2.233 | 2.6459 | 2.6459 | 2.6459 | 2.6459
2024-01-31 06:00 | 2.0767 | 2.5834 | 3.1212 | 3.1929 | 3.2646 | 2023-12-01 06:00 | 2.4959 | 2.9574 | 2.9574 | 2.9574 | 2.9574
2024-01-31 07:00 | 2.5911 | 3.2233 | 3.8944 | 3.9838 | 4.0733 | 2023-12-01 07:00 | 2.8503 | 3.3773 | 3.3773 | 3.3773 | 3.3773
2024-01-31 08:00 | 2.915 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2023-12-01 08:00 | 3.2046 | 3.7972 | 3.7972 | 3.7972 | 3.7972
2024-01-31 09:00 | 2.9722 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2023-12-01 09:00 | 3.2847 | 3.892 | 3.892 | 3.892 | 3.892
2024-01-31 10:00 | 2.9722 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2023-12-01 10:00 | 3.2046 | 3.7972 | 3.7972 | 3.7972 | 3.7972
2024-01-31 11:00 | 2.8579 | 3.5551 | 4.2953 | 4.3939 | 4.4926 | 2023-12-01 11:00 | 3.6771 | 4.3571 | 4.3571 | 4.3571 | 4.3571
2024-01-31 12:00 | 2.9913 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2023-12-01 12:00 | 3.902 | 4.6235 | 4.6235 | 4.6235 | 4.6235
2024-01-31 13:00 | 3.0484 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2023-12-01 13:00 | 3.8372 | 4.5467 | 4.5467 | 4.5467 | 4.5467
2024-01-31 14:00 | 3.0294 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2023-12-01 14:00 | 3.8143 | 4.5197 | 4.5197 | 4.5197 | 4.5197
2024-01-31 15:00 | 3.0294 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2023-12-01 15:00 | 3.8639 | 4.5784 | 4.5784 | 4.5784 | 4.5784
2024-01-31 16:00 | 2.915 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2023-12-01 16:00 | 3.9324 | 4.6596 | 4.6596 | 4.6596 | 4.6596
2024-01-31 17:00 | 2.8007 | 3.484 | 4.2094 | 4.3061 | 4.4028 | 2023-12-01 17:00 | 3.7838 | 4.4835 | 4.4835 | 4.4835 | 4.4835
2024-01-31 18:00 | 2.3816 | 2.9626 | 3.5794 | 3.6616 | 3.7439 | 2023-12-01 18:00 | 3.2008 | 3.7927 | 3.7927 | 3.7927 | 3.7927
2024-01-31 19:00 | 2.0958 | 2.6071 | 3.1499 | 3.2222 | 3.2946 | 2023-12-01 19:00 | 2.7321 | 3.2374 | 3.2374 | 3.2374 | 3.2374
2024-01-31 20:00 | 1.8481 | 2.299 | 2.7776 | 2.8414 | 2.9052 | 2023-12-01 20:00 | 2.915 | 3.4541 | 3.4541 | 3.4541 | 3.4541
2024-01-31 21:00 | 1.829 | 2.2753 | 2.749 | 2.8121 | 2.8753 | 2023-12-01 21:00 | 2.5759 | 3.0522 | 3.0522 | 3.0522 | 3.0522
2024-01-31 22:00 | 1.7719 | 2.2042 | 2.6631 | 2.7242 | 2.7854 | 2023-12-01 22:00 | 2.0501 | 2.4291 | 2.4291 | 2.4291 | 2.4291
2024-01-31 23:00 | 1.6957 | 2.1094 | 2.5485 | 2.6071 | 2.6656 | 2023-12-01 23:00 | 1.8443 | 2.1853 | 2.1853 | 2.1853 | 2.1853
2024-02-01 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2023-12-02 | 1.5852 | 1.8783 | 1.8783 | 1.8783 | 1.8783
2024-02-01 01:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2023-12-02 01:00 | 1.6576 | 1.9641 | 1.9641 | 1.9641 | 1.9641
2024-02-01 02:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2023-12-02 02:00 | 1.6195 | 1.9189 | 1.9189 | 1.9189 | 1.9189
2024-02-01 03:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2023-12-02 03:00 | 1.7681 | 2.095 | 2.095 | 2.095 | 2.095
2024-02-01 04:00 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2023-12-02 04:00 | 1.8252 | 2.1628 | 2.1628 | 2.1628 | 2.1628
2024-02-01 05:00 | 1.6957 | 2.1094 | 2.5485 | 2.6071 | 2.6656 | 2023-12-02 05:00 | 2.1034 | 2.4924 | 2.4924 | 2.4924 | 2.4924
2024-02-01 06:00 | 1.9243 | 2.3938 | 2.8921 | 2.9586 | 3.025 | 2023-12-02 06:00 | 2.1415 | 2.5375 | 2.5375 | 2.5375 | 2.5375
2024-02-01 07:00 | 2.2291 | 2.773 | 3.3503 | 3.4273 | 3.5043 | 2023-12-02 07:00 | 2.4425 | 2.8942 | 2.8942 | 2.8942 | 2.8942
2024-02-01 08:00 | 2.4006 | 2.9863 | 3.608 | 3.6909 | 3.7738 | 2023-12-02 08:00 | 2.8617 | 3.3909 | 3.3909 | 3.3909 | 3.3909
2024-02-01 09:00 | 2.4197 | 3.01 | 3.6367 | 3.7202 | 3.8038 | 2023-12-02 09:00 | 2.9036 | 3.4405 | 3.4405 | 3.4405 | 3.4405
2024-02-01 10:00 | 2.5149 | 3.1285 | 3.7798 | 3.8667 | 3.9535 | 2023-12-02 10:00 | 3.277 | 3.883 | 3.883 | 3.883 | 3.883
2024-02-01 11:00 | 2.7055 | 3.3655 | 4.0662 | 4.1596 | 4.253 | 2023-12-02 11:00 | 3.4676 | 4.1088 | 4.1088 | 4.1088 | 4.1088
2024-02-01 12:00 | 2.8579 | 3.5551 | 4.2953 | 4.3939 | 4.4926 | 2023-12-02 12:00 | 3.5362 | 4.19 | 4.19 | 4.19 | 4.19
2024-02-01 13:00 | 2.8388 | 3.5314 | 4.2666 | 4.3647 | 4.4627 | 2023-12-02 13:00 | 3.8219 | 4.5287 | 4.5287 | 4.5287 | 4.5287
2024-02-01 14:00 | 2.9913 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2023-12-02 14:00 | 3.5819 | 4.2442 | 4.2442 | 4.2442 | 4.2442
2024-02-01 15:00 | 2.9722 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2023-12-02 15:00 | 3.4257 | 4.0591 | 4.0591 | 4.0591 | 4.0591
2024-02-01 16:00 | 2.9531 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2023-12-02 16:00 | 3.2313 | 3.8288 | 3.8288 | 3.8288 | 3.8288
2024-02-01 17:00 | 2.9722 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2023-12-02 17:00 | 3.2085 | 3.8017 | 3.8017 | 3.8017 | 3.8017
2024-02-01 18:00 | 2.553 | 3.1759 | 3.8371 | 3.9253 | 4.0134 | 2023-12-02 18:00 | 2.5645 | 3.0387 | 3.0387 | 3.0387 | 3.0387
2024-02-01 19:00 | 2.2673 | 2.8204 | 3.4076 | 3.4859 | 3.5642 | 2023-12-02 19:00 | 2.2673 | 2.6865 | 2.6865 | 2.6865 | 2.6865
2024-02-01 20:00 | 1.9624 | 2.4412 | 2.9494 | 3.0172 | 3.0849 | 2023-12-02 20:00 | 2.1644 | 2.5646 | 2.5646 | 2.5646 | 2.5646
2024-02-01 21:00 | 1.9053 | 2.3701 | 2.8635 | 2.9293 | 2.9951 | 2023-12-02 21:00 | 2.1834 | 2.5872 | 2.5872 | 2.5872 | 2.5872
2024-02-01 22:00 | 1.8481 | 2.299 | 2.7776 | 2.8414 | 2.9052 | 2023-12-02 22:00 | 2.0615 | 2.4427 | 2.4427 | 2.4427 | 2.4427
2024-02-01 23:00 | 1.6957 | 2.1094 | 2.5485 | 2.6071 | 2.6656 | 2023-12-02 23:00 | 1.8672 | 2.2124 | 2.2124 | 2.2124 | 2.2124
2024-02-02 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2023-12-03 | 1.6804 | 1.9912 | 1.9912 | 1.9912 | 1.9912
2024-02-02 01:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2023-12-03 01:00 | 1.6957 | 2.0092 | 2.0092 | 2.0092 | 2.0092
2024-02-02 02:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2023-12-03 02:00 | 1.6995 | 2.0138 | 2.0138 | 2.0138 | 2.0138
2024-02-02 03:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2023-12-03 03:00 | 1.7681 | 2.095 | 2.095 | 2.095 | 2.095
2024-02-02 04:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2023-12-03 04:00 | 1.9091 | 2.2621 | 2.2621 | 2.2621 | 2.2621
2024-02-02 05:00 | 1.7147 | 2.1331 | 2.5772 | 2.6364 | 2.6956 | 2023-12-03 05:00 | 2.031 | 2.4066 | 2.4066 | 2.4066 | 2.4066
2024-02-02 06:00 | 1.829 | 2.2753 | 2.749 | 2.8121 | 2.8753 | 2023-12-03 06:00 | 2.0501 | 2.4291 | 2.4291 | 2.4291 | 2.4291
2024-02-02 07:00 | 2.2673 | 2.8204 | 3.4076 | 3.4859 | 3.5642 | 2023-12-03 07:00 | 2.1301 | 2.524 | 2.524 | 2.524 | 2.524
2024-02-02 08:00 | 2.4006 | 2.9863 | 3.608 | 3.6909 | 3.7738 | 2023-12-03 08:00 | 2.1987 | 2.6052 | 2.6052 | 2.6052 | 2.6052
2024-02-02 09:00 | 2.4578 | 3.0574 | 3.6939 | 3.7788 | 3.8637 | 2023-12-03 09:00 | 2.7436 | 3.2509 | 3.2509 | 3.2509 | 3.2509
2024-02-02 10:00 | 2.5149 | 3.1285 | 3.7798 | 3.8667 | 3.9535 | 2023-12-03 10:00 | 3.0637 | 3.6302 | 3.6302 | 3.6302 | 3.6302
2024-02-02 11:00 | 2.6102 | 3.247 | 3.923 | 4.0131 | 4.1033 | 2023-12-03 11:00 | 3.2199 | 3.8153 | 3.8153 | 3.8153 | 3.8153
2024-02-02 12:00 | 2.6293 | 3.2707 | 3.9516 | 4.0424 | 4.1332 | 2023-12-03 12:00 | 2.9913 | 3.5444 | 3.5444 | 3.5444 | 3.5444
2024-02-02 13:00 | 2.6102 | 3.247 | 3.923 | 4.0131 | 4.1033 | 2023-12-03 13:00 | 3.5438 | 4.1991 | 4.1991 | 4.1991 | 4.1991
2024-02-02 14:00 | 2.7055 | 3.3655 | 4.0662 | 4.1596 | 4.253 | 2023-12-03 14:00 | 3.5323 | 4.1855 | 4.1855 | 4.1855 | 4.1855
2024-02-02 15:00 | 2.7436 | 3.4129 | 4.1235 | 4.2182 | 4.3129 | 2023-12-03 15:00 | 3.62 | 4.2894 | 4.2894 | 4.2894 | 4.2894
2024-02-02 16:00 | 2.7245 | 3.3892 | 4.0948 | 4.1889 | 4.283 | 2023-12-03 16:00 | 2.8236 | 3.3457 | 3.3457 | 3.3457 | 3.3457
2024-02-02 17:00 | 2.6864 | 3.3418 | 4.0375 | 4.1303 | 4.2231 | 2023-12-03 17:00 | 2.8617 | 3.3909 | 3.3909 | 3.3909 | 3.3909
2024-02-02 18:00 | 2.553 | 3.1759 | 3.8371 | 3.9253 | 4.0134 | 2023-12-03 18:00 | 2.534 | 3.0026 | 3.0026 | 3.0026 | 3.0026
2024-02-02 19:00 | 2.0577 | 2.5597 | 3.0926 | 3.1636 | 3.2347 | 2023-12-03 19:00 | 2.2749 | 2.6955 | 2.6955 | 2.6955 | 2.6955
2024-02-02 20:00 | 1.9053 | 2.3701 | 2.8635 | 2.9293 | 2.9951 | 2023-12-03 20:00 | 2.3168 | 2.7452 | 2.7452 | 2.7452 | 2.7452
2024-02-02 21:00 | 1.7909 | 2.2279 | 2.6917 | 2.7535 | 2.8154 | 2023-12-03 21:00 | 2.2901 | 2.7136 | 2.7136 | 2.7136 | 2.7136
2024-02-02 22:00 | 1.7909 | 2.2279 | 2.6917 | 2.7535 | 2.8154 | 2023-12-03 22:00 | 1.8405 | 2.1808 | 2.1808 | 2.1808 | 2.1808
2024-02-02 23:00 | 1.7528 | 2.1805 | 2.6344 | 2.695 | 2.7555 | 2023-12-03 23:00 | 1.7185 | 2.0363 | 2.0363 | 2.0363 | 2.0363
2024-02-03 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2023-12-04 | 1.5661 | 1.8557 | 1.8557 | 1.8557 | 1.8557
2024-02-03 01:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2023-12-04 01:00 | 1.6461 | 1.9505 | 1.9505 | 1.9505 | 1.9505
2024-02-03 02:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2023-12-04 02:00 | 1.6118 | 1.9099 | 1.9099 | 1.9099 | 1.9099
2024-02-03 03:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2023-12-04 03:00 | 1.749 | 2.0724 | 2.0724 | 2.0724 | 2.0724
2024-02-03 04:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2023-12-04 04:00 | 1.9053 | 2.2576 | 2.2576 | 2.2576 | 2.2576
2024-02-03 05:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2023-12-04 05:00 | 2.1872 | 2.5917 | 2.5917 | 2.5917 | 2.5917
2024-02-03 06:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2023-12-04 06:00 | 2.2444 | 2.6594 | 2.6594 | 2.6594 | 2.6594
2024-02-03 07:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2023-12-04 07:00 | 2.4845 | 2.9439 | 2.9439 | 2.9439 | 2.9439
2024-02-03 08:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2023-12-04 08:00 | 3.0446 | 3.6076 | 3.6076 | 3.6076 | 3.6076
2024-02-03 09:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2023-12-04 09:00 | 3.1932 | 3.7837 | 3.7837 | 3.7837 | 3.7837
2024-02-03 10:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2023-12-04 10:00 | 3.0484 | 3.6121 | 3.6121 | 3.6121 | 3.6121
2024-02-03 11:00 | 1.3718 | 1.7065 | 2.0617 | 2.1091 | 2.1565 | 2023-12-04 11:00 | 3.1818 | 3.7701 | 3.7701 | 3.7701 | 3.7701
2024-02-03 12:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2023-12-04 12:00 | 3.3418 | 3.9598 | 3.9598 | 3.9598 | 3.9598
2024-02-03 13:00 | 1.4099 | 1.7539 | 2.119 | 2.1677 | 2.2164 | 2023-12-04 13:00 | 3.5171 | 4.1675 | 4.1675 | 4.1675 | 4.1675
2024-02-03 14:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2023-12-04 14:00 | 3.5514 | 4.2081 | 4.2081 | 4.2081 | 4.2081
2024-02-03 15:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2023-12-04 15:00 | 3.681 | 4.3616 | 4.3616 | 4.3616 | 4.3616
2024-02-03 16:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2023-12-04 16:00 | 3.78 | 4.479 | 4.479 | 4.479 | 4.479
2024-02-03 17:00 | 1.9053 | 2.3701 | 2.8635 | 2.9293 | 2.9951 | 2023-12-04 17:00 | 3.6505 | 4.3255 | 4.3255 | 4.3255 | 4.3255
2024-02-03 18:00 | 1.8672 | 2.3227 | 2.8062 | 2.8707 | 2.9352 | 2023-12-04 18:00 | 3.3837 | 4.0094 | 4.0094 | 4.0094 | 4.0094
2024-02-03 19:00 | 1.7719 | 2.2042 | 2.6631 | 2.7242 | 2.7854 | 2023-12-04 19:00 | 2.9379 | 3.4812 | 3.4812 | 3.4812 | 3.4812
2024-02-03 20:00 | 1.7909 | 2.2279 | 2.6917 | 2.7535 | 2.8154 | 2023-12-04 20:00 | 2.534 | 3.0026 | 3.0026 | 3.0026 | 3.0026
2024-02-03 21:00 | 1.7909 | 2.2279 | 2.6917 | 2.7535 | 2.8154 | 2023-12-04 21:00 | 2.2139 | 2.6233 | 2.6233 | 2.6233 | 2.6233
2024-02-03 22:00 | 1.7528 | 2.1805 | 2.6344 | 2.695 | 2.7555 | 2023-12-04 22:00 | 2.1301 | 2.524 | 2.524 | 2.524 | 2.524
2024-02-03 23:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2023-12-04 23:00 | 1.8062 | 2.1402 | 2.1402 | 2.1402 | 2.1402
2024-02-04 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2023-12-05 | 1.6195 | 1.9189 | 1.9189 | 1.9189 | 1.9189
2024-02-04 01:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2023-12-05 01:00 | 1.6766 | 1.9867 | 1.9867 | 1.9867 | 1.9867
2024-02-04 02:00 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2023-12-05 02:00 | 1.6728 | 1.9821 | 1.9821 | 1.9821 | 1.9821
2024-02-04 03:00 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2023-12-05 03:00 | 1.73 | 2.0499 | 2.0499 | 2.0499 | 2.0499
2024-02-04 04:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2023-12-05 04:00 | 1.8329 | 2.1718 | 2.1718 | 2.1718 | 2.1718
2024-02-04 05:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2023-12-05 05:00 | 1.9815 | 2.3479 | 2.3479 | 2.3479 | 2.3479
2024-02-04 06:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2023-12-05 06:00 | 2.3739 | 2.8129 | 2.8129 | 2.8129 | 2.8129
2024-02-04 07:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2023-12-05 07:00 | 2.4806 | 2.9394 | 2.9394 | 2.9394 | 2.9394
2024-02-04 08:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2023-12-05 08:00 | 2.9112 | 3.4496 | 3.4496 | 3.4496 | 3.4496
2024-02-04 09:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2023-12-05 09:00 | 3.6276 | 4.2984 | 4.2984 | 4.2984 | 4.2984
2024-02-04 10:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2023-12-05 10:00 | 3.4942 | 4.1404 | 4.1404 | 4.1404 | 4.1404
2024-02-04 11:00 | 1.7719 | 2.2042 | 2.6631 | 2.7242 | 2.7854 | 2023-12-05 11:00 | 3.9858 | 4.7228 | 4.7228 | 4.7228 | 4.7228
2024-02-04 12:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2023-12-05 12:00 | 4.1954 | 4.9712 | 4.9712 | 4.9712 | 4.9712
2024-02-04 13:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2023-12-05 13:00 | 3.9782 | 4.7138 | 4.7138 | 4.7138 | 4.7138
2024-02-04 14:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2023-12-05 14:00 | 4.0734 | 4.8267 | 4.8267 | 4.8267 | 4.8267
2024-02-04 15:00 | 1.7147 | 2.1331 | 2.5772 | 2.6364 | 2.6956 | 2023-12-05 15:00 | 4.2525 | 5.0389 | 5.0389 | 5.0389 | 5.0389
2024-02-04 16:00 | 1.8862 | 2.3464 | 2.8349 | 2.9 | 2.9651 | 2023-12-05 16:00 | 4.3935 | 5.206 | 5.206 | 5.206 | 5.206
2024-02-04 17:00 | 1.8481 | 2.299 | 2.7776 | 2.8414 | 2.9052 | 2023-12-05 17:00 | 4.1306 | 4.8944 | 4.8944 | 4.8944 | 4.8944
2024-02-04 18:00 | 1.9053 | 2.3701 | 2.8635 | 2.9293 | 2.9951 | 2023-12-05 18:00 | 3.7762 | 4.4745 | 4.4745 | 4.4745 | 4.4745
2024-02-04 19:00 | 1.7528 | 2.1805 | 2.6344 | 2.695 | 2.7555 | 2023-12-05 19:00 | 2.8884 | 3.4225 | 3.4225 | 3.4225 | 3.4225
2024-02-04 20:00 | 1.829 | 2.2753 | 2.749 | 2.8121 | 2.8753 | 2023-12-05 20:00 | 2.6178 | 3.1019 | 3.1019 | 3.1019 | 3.1019
2024-02-04 21:00 | 1.8481 | 2.299 | 2.7776 | 2.8414 | 2.9052 | 2023-12-05 21:00 | 2.4578 | 2.9123 | 2.9123 | 2.9123 | 2.9123
2024-02-04 22:00 | 1.7719 | 2.2042 | 2.6631 | 2.7242 | 2.7854 | 2023-12-05 22:00 | 1.9548 | 2.3163 | 2.3163 | 2.3163 | 2.3163
2024-02-04 23:00 | 1.7147 | 2.1331 | 2.5772 | 2.6364 | 2.6956 | 2023-12-05 23:00 | 1.7833 | 2.1131 | 2.1131 | 2.1131 | 2.1131
2024-02-05 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2023-12-06 | 1.589 | 1.8828 | 1.8828 | 1.8828 | 1.8828
2024-02-05 01:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2023-12-06 01:00 | 1.5661 | 1.8557 | 1.8557 | 1.8557 | 1.8557
2024-02-05 02:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2023-12-06 02:00 | 1.5737 | 1.8648 | 1.8648 | 1.8648 | 1.8648
2024-02-05 03:00 | 1.6957 | 2.1094 | 2.5485 | 2.6071 | 2.6656 | 2023-12-06 03:00 | 1.7643 | 2.0905 | 2.0905 | 2.0905 | 2.0905
2024-02-05 04:00 | 1.6957 | 2.1094 | 2.5485 | 2.6071 | 2.6656 | 2023-12-06 04:00 | 1.9548 | 2.3163 | 2.3163 | 2.3163 | 2.3163
2024-02-05 05:00 | 2.0767 | 2.5834 | 3.1212 | 3.1929 | 3.2646 | 2023-12-06 05:00 | 2.1758 | 2.5781 | 2.5781 | 2.5781 | 2.5781
2024-02-05 06:00 | 2.534 | 3.1522 | 3.8085 | 3.896 | 3.9835 | 2023-12-06 06:00 | 2.3739 | 2.8129 | 2.8129 | 2.8129 | 2.8129
2024-02-05 07:00 | 2.7626 | 3.4366 | 4.1521 | 4.2475 | 4.3429 | 2023-12-06 07:00 | 2.5835 | 3.0613 | 3.0613 | 3.0613 | 3.0613
2024-02-05 08:00 | 3.1627 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2023-12-06 08:00 | 3.056 | 3.6211 | 3.6211 | 3.6211 | 3.6211
2024-02-05 09:00 | 3.1818 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2023-12-06 09:00 | 3.5628 | 4.2217 | 4.2217 | 4.2217 | 4.2217
2024-02-05 10:00 | 3.1246 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2023-12-06 10:00 | 3.86 | 4.5738 | 4.5738 | 4.5738 | 4.5738
2024-02-05 11:00 | 3.1627 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2023-12-06 11:00 | 3.9744 | 4.7093 | 4.7093 | 4.7093 | 4.7093
2024-02-05 12:00 | 3.1056 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2023-12-06 12:00 | 4.1306 | 4.8944 | 4.8944 | 4.8944 | 4.8944
2024-02-05 13:00 | 3.0675 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2023-12-06 13:00 | 4.3135 | 5.1111 | 5.1111 | 5.1111 | 5.1111
2024-02-05 14:00 | 2.9913 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2023-12-06 14:00 | 4.1496 | 4.917 | 4.917 | 4.917 | 4.917
2024-02-05 15:00 | 2.9531 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2023-12-06 15:00 | 4.0582 | 4.8086 | 4.8086 | 4.8086 | 4.8086
2024-02-05 16:00 | 2.896 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2023-12-06 16:00 | 4.1878 | 4.9621 | 4.9621 | 4.9621 | 4.9621
2024-02-05 17:00 | 2.553 | 3.1759 | 3.8371 | 3.9253 | 4.0134 | 2023-12-06 17:00 | 3.9896 | 4.7273 | 4.7273 | 4.7273 | 4.7273
2024-02-05 18:00 | 2.4768 | 3.0811 | 3.7226 | 3.8081 | 3.8936 | 2023-12-06 18:00 | 3.8258 | 4.5332 | 4.5332 | 4.5332 | 4.5332
2024-02-05 19:00 | 2.0767 | 2.5834 | 3.1212 | 3.1929 | 3.2646 | 2023-12-06 19:00 | 2.9227 | 3.4631 | 3.4631 | 3.4631 | 3.4631
2024-02-05 20:00 | 1.8481 | 2.299 | 2.7776 | 2.8414 | 2.9052 | 2023-12-06 20:00 | 2.8465 | 3.3728 | 3.3728 | 3.3728 | 3.3728
2024-02-05 21:00 | 1.7719 | 2.2042 | 2.6631 | 2.7242 | 2.7854 | 2023-12-06 21:00 | 2.5873 | 3.0658 | 3.0658 | 3.0658 | 3.0658
2024-02-05 22:00 | 1.7147 | 2.1331 | 2.5772 | 2.6364 | 2.6956 | 2023-12-06 22:00 | 2.1225 | 2.5149 | 2.5149 | 2.5149 | 2.5149
2024-02-05 23:00 | 1.6957 | 2.1094 | 2.5485 | 2.6071 | 2.6656 | 2023-12-06 23:00 | 1.9053 | 2.2576 | 2.2576 | 2.2576 | 2.2576
2024-02-06 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2023-12-07 | 1.6423 | 1.946 | 1.946 | 1.946 | 1.946
2024-02-06 01:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2023-12-07 01:00 | 1.6461 | 1.9505 | 1.9505 | 1.9505 | 1.9505
2024-02-06 02:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2023-12-07 02:00 | 1.6347 | 1.937 | 1.937 | 1.937 | 1.937
2024-02-06 03:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2023-12-07 03:00 | 1.7719 | 2.0995 | 2.0995 | 2.0995 | 2.0995
2024-02-06 04:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2023-12-07 04:00 | 1.8672 | 2.2124 | 2.2124 | 2.2124 | 2.2124
2024-02-06 05:00 | 1.6957 | 2.1094 | 2.5485 | 2.6071 | 2.6656 | 2023-12-07 05:00 | 2.2901 | 2.7136 | 2.7136 | 2.7136 | 2.7136
2024-02-06 06:00 | 2.1148 | 2.6308 | 3.1785 | 3.2515 | 3.3245 | 2023-12-07 06:00 | 2.3244 | 2.7542 | 2.7542 | 2.7542 | 2.7542
2024-02-06 07:00 | 2.6102 | 3.247 | 3.923 | 4.0131 | 4.1033 | 2023-12-07 07:00 | 2.8426 | 3.3683 | 3.3683 | 3.3683 | 3.3683
2024-02-06 08:00 | 2.7245 | 3.3892 | 4.0948 | 4.1889 | 4.283 | 2023-12-07 08:00 | 3.3647 | 3.9869 | 3.9869 | 3.9869 | 3.9869
2024-02-06 09:00 | 2.8769 | 3.5788 | 4.3239 | 4.4232 | 4.5226 | 2023-12-07 09:00 | 3.6657 | 4.3436 | 4.3436 | 4.3436 | 4.3436
2024-02-06 10:00 | 2.8769 | 3.5788 | 4.3239 | 4.4232 | 4.5226 | 2023-12-07 10:00 | 4.0582 | 4.8086 | 4.8086 | 4.8086 | 4.8086
2024-02-06 11:00 | 2.896 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2023-12-07 11:00 | 4.1878 | 4.9621 | 4.9621 | 4.9621 | 4.9621
2024-02-06 12:00 | 3.0103 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2023-12-07 12:00 | 4.405 | 5.2195 | 5.2195 | 5.2195 | 5.2195
2024-02-06 13:00 | 3.1818 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2023-12-07 13:00 | 4.2373 | 5.0208 | 5.0208 | 5.0208 | 5.0208
2024-02-06 14:00 | 3.1246 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2023-12-07 14:00 | 4.222 | 5.0028 | 5.0028 | 5.0028 | 5.0028
2024-02-06 15:00 | 2.8769 | 3.5788 | 4.3239 | 4.4232 | 4.5226 | 2023-12-07 15:00 | 4.1039 | 4.8628 | 4.8628 | 4.8628 | 4.8628
2024-02-06 16:00 | 2.7626 | 3.4366 | 4.1521 | 4.2475 | 4.3429 | 2023-12-07 16:00 | 4.0239 | 4.768 | 4.768 | 4.768 | 4.768
2024-02-06 17:00 | 2.7055 | 3.3655 | 4.0662 | 4.1596 | 4.253 | 2023-12-07 17:00 | 3.7076 | 4.3932 | 4.3932 | 4.3932 | 4.3932
2024-02-06 18:00 | 2.172 | 2.7019 | 3.2644 | 3.3394 | 3.4144 | 2023-12-07 18:00 | 3.4523 | 4.0907 | 4.0907 | 4.0907 | 4.0907
2024-02-06 19:00 | 1.81 | 2.2516 | 2.7203 | 2.7828 | 2.8453 | 2023-12-07 19:00 | 2.835 | 3.3593 | 3.3593 | 3.3593 | 3.3593
2024-02-06 20:00 | 1.6957 | 2.1094 | 2.5485 | 2.6071 | 2.6656 | 2023-12-07 20:00 | 2.7017 | 3.2012 | 3.2012 | 3.2012 | 3.2012
2024-02-06 21:00 | 1.6957 | 2.1094 | 2.5485 | 2.6071 | 2.6656 | 2023-12-07 21:00 | 2.5035 | 2.9664 | 2.9664 | 2.9664 | 2.9664
2024-02-06 22:00 | 1.6957 | 2.1094 | 2.5485 | 2.6071 | 2.6656 | 2023-12-07 22:00 | 2.0767 | 2.4608 | 2.4608 | 2.4608 | 2.4608
2024-02-06 23:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2023-12-07 23:00 | 1.9319 | 2.2892 | 2.2892 | 2.2892 | 2.2892
2024-02-07 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2023-12-08 | 1.608 | 1.9054 | 1.9054 | 1.9054 | 1.9054
2024-02-07 01:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2023-12-08 01:00 | 1.6576 | 1.9641 | 1.9641 | 1.9641 | 1.9641
2024-02-07 02:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2023-12-08 02:00 | 1.6004 | 1.8964 | 1.8964 | 1.8964 | 1.8964
2024-02-07 03:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2023-12-08 03:00 | 1.8557 | 2.1989 | 2.1989 | 2.1989 | 2.1989
2024-02-07 04:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2023-12-08 04:00 | 2.0805 | 2.4653 | 2.4653 | 2.4653 | 2.4653
2024-02-07 05:00 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2023-12-08 05:00 | 2.2825 | 2.7046 | 2.7046 | 2.7046 | 2.7046
2024-02-07 06:00 | 1.81 | 2.2516 | 2.7203 | 2.7828 | 2.8453 | 2023-12-08 06:00 | 2.4387 | 2.8897 | 2.8897 | 2.8897 | 2.8897
2024-02-07 07:00 | 2.0577 | 2.5597 | 3.0926 | 3.1636 | 3.2347 | 2023-12-08 07:00 | 3.0217 | 3.5805 | 3.5805 | 3.5805 | 3.5805
2024-02-07 08:00 | 2.1339 | 2.6545 | 3.2071 | 3.2808 | 3.3545 | 2023-12-08 08:00 | 3.5438 | 4.1991 | 4.1991 | 4.1991 | 4.1991
2024-02-07 09:00 | 2.1148 | 2.6308 | 3.1785 | 3.2515 | 3.3245 | 2023-12-08 09:00 | 4.1535 | 4.9215 | 4.9215 | 4.9215 | 4.9215
2024-02-07 10:00 | 2.2673 | 2.8204 | 3.4076 | 3.4859 | 3.5642 | 2023-12-08 10:00 | 4.142 | 4.908 | 4.908 | 4.908 | 4.908
2024-02-07 11:00 | 2.3244 | 2.8915 | 3.4935 | 3.5737 | 3.654 | 2023-12-08 11:00 | 4.2449 | 5.0299 | 5.0299 | 5.0299 | 5.0299
2024-02-07 12:00 | 2.4768 | 3.0811 | 3.7226 | 3.8081 | 3.8936 | 2023-12-08 12:00 | 4.3478 | 5.1518 | 5.1518 | 5.1518 | 5.1518
2024-02-07 13:00 | 2.553 | 3.1759 | 3.8371 | 3.9253 | 4.0134 | 2023-12-08 13:00 | 4.8584 | 5.7568 | 5.7568 | 5.7568 | 5.7568
2024-02-07 14:00 | 2.5721 | 3.1996 | 3.8657 | 3.9546 | 4.0434 | 2023-12-08 14:00 | 4.7898 | 5.6755 | 5.6755 | 5.6755 | 5.6755
2024-02-07 15:00 | 2.4768 | 3.0811 | 3.7226 | 3.8081 | 3.8936 | 2023-12-08 15:00 | 4.3249 | 5.1247 | 5.1247 | 5.1247 | 5.1247
2024-02-07 16:00 | 2.4006 | 2.9863 | 3.608 | 3.6909 | 3.7738 | 2023-12-08 16:00 | 4.2487 | 5.0344 | 5.0344 | 5.0344 | 5.0344
2024-02-07 17:00 | 2.2291 | 2.773 | 3.3503 | 3.4273 | 3.5043 | 2023-12-08 17:00 | 4.2144 | 4.9937 | 4.9937 | 4.9937 | 4.9937
2024-02-07 18:00 | 2.0005 | 2.4886 | 3.0067 | 3.0758 | 3.1448 | 2023-12-08 18:00 | 4.1535 | 4.9215 | 4.9215 | 4.9215 | 4.9215
2024-02-07 19:00 | 1.7909 | 2.2279 | 2.6917 | 2.7535 | 2.8154 | 2023-12-08 19:00 | 3.902 | 4.6235 | 4.6235 | 4.6235 | 4.6235
2024-02-07 20:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2023-12-08 20:00 | 3.0675 | 3.6347 | 3.6347 | 3.6347 | 3.6347
2024-02-07 21:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2023-12-08 21:00 | 2.6331 | 3.12 | 3.12 | 3.12 | 3.12
2024-02-07 22:00 | 1.7147 | 2.1331 | 2.5772 | 2.6364 | 2.6956 | 2023-12-08 22:00 | 2.1758 | 2.5781 | 2.5781 | 2.5781 | 2.5781
2024-02-07 23:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2023-12-08 23:00 | 1.9014 | 2.2531 | 2.2531 | 2.2531 | 2.2531
2024-02-08 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2023-12-09 | 1.7681 | 2.095 | 2.095 | 2.095 | 2.095
2024-02-08 01:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2023-12-09 01:00 | 1.7147 | 2.0318 | 2.0318 | 2.0318 | 2.0318
2024-02-08 02:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2023-12-09 02:00 | 1.7719 | 2.0995 | 2.0995 | 2.0995 | 2.0995
2024-02-08 03:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2023-12-09 03:00 | 1.8633 | 2.2079 | 2.2079 | 2.2079 | 2.2079
2024-02-08 04:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2023-12-09 04:00 | 1.9053 | 2.2576 | 2.2576 | 2.2576 | 2.2576
2024-02-08 05:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2023-12-09 05:00 | 2.4121 | 2.8581 | 2.8581 | 2.8581 | 2.8581
2024-02-08 06:00 | 1.8481 | 2.299 | 2.7776 | 2.8414 | 2.9052 | 2023-12-09 06:00 | 2.4806 | 2.9394 | 2.9394 | 2.9394 | 2.9394
2024-02-08 07:00 | 2.2673 | 2.8204 | 3.4076 | 3.4859 | 3.5642 | 2023-12-09 07:00 | 2.5607 | 3.0342 | 3.0342 | 3.0342 | 3.0342
2024-02-08 08:00 | 2.3625 | 2.9389 | 3.5508 | 3.6323 | 3.7139 | 2023-12-09 08:00 | 3.3914 | 4.0185 | 4.0185 | 4.0185 | 4.0185
2024-02-08 09:00 | 2.3054 | 2.8678 | 3.4648 | 3.5445 | 3.6241 | 2023-12-09 09:00 | 3.3875 | 4.014 | 4.014 | 4.014 | 4.014
2024-02-08 10:00 | 2.3244 | 2.8915 | 3.4935 | 3.5737 | 3.654 | 2023-12-09 10:00 | 3.6581 | 4.3345 | 4.3345 | 4.3345 | 4.3345
2024-02-08 11:00 | 2.4578 | 3.0574 | 3.6939 | 3.7788 | 3.8637 | 2023-12-09 11:00 | 3.761 | 4.4564 | 4.4564 | 4.4564 | 4.4564
2024-02-08 12:00 | 2.4959 | 3.1048 | 3.7512 | 3.8374 | 3.9236 | 2023-12-09 12:00 | 3.7305 | 4.4203 | 4.4203 | 4.4203 | 4.4203
2024-02-08 13:00 | 2.4387 | 3.0337 | 3.6653 | 3.7495 | 3.8337 | 2023-12-09 13:00 | 3.7076 | 4.3932 | 4.3932 | 4.3932 | 4.3932
2024-02-08 14:00 | 2.4197 | 3.01 | 3.6367 | 3.7202 | 3.8038 | 2023-12-09 14:00 | 4.0353 | 4.7815 | 4.7815 | 4.7815 | 4.7815
2024-02-08 15:00 | 2.3816 | 2.9626 | 3.5794 | 3.6616 | 3.7439 | 2023-12-09 15:00 | 4.5345 | 5.373 | 5.373 | 5.373 | 5.373
2024-02-08 16:00 | 2.4578 | 3.0574 | 3.6939 | 3.7788 | 3.8637 | 2023-12-09 16:00 | 4.2411 | 5.0253 | 5.0253 | 5.0253 | 5.0253
2024-02-08 17:00 | 2.2863 | 2.8441 | 3.4362 | 3.5152 | 3.5941 | 2023-12-09 17:00 | 3.4599 | 4.0997 | 4.0997 | 4.0997 | 4.0997
2024-02-08 18:00 | 2.1148 | 2.6308 | 3.1785 | 3.2515 | 3.3245 | 2023-12-09 18:00 | 2.8731 | 3.4044 | 3.4044 | 3.4044 | 3.4044
2024-02-08 19:00 | 1.7719 | 2.2042 | 2.6631 | 2.7242 | 2.7854 | 2023-12-09 19:00 | 2.6674 | 3.1606 | 3.1606 | 3.1606 | 3.1606
2024-02-08 20:00 | 1.6957 | 2.1094 | 2.5485 | 2.6071 | 2.6656 | 2023-12-09 20:00 | 2.2253 | 2.6368 | 2.6368 | 2.6368 | 2.6368
2024-02-08 21:00 | 1.7147 | 2.1331 | 2.5772 | 2.6364 | 2.6956 | 2023-12-09 21:00 | 2.1758 | 2.5781 | 2.5781 | 2.5781 | 2.5781
2024-02-08 22:00 | 1.7147 | 2.1331 | 2.5772 | 2.6364 | 2.6956 | 2023-12-09 22:00 | 2.0158 | 2.3885 | 2.3885 | 2.3885 | 2.3885
2024-02-08 23:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2023-12-09 23:00 | 1.9929 | 2.3614 | 2.3614 | 2.3614 | 2.3614
2024-02-09 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2023-12-10 | 1.6957 | 2.0092 | 2.0092 | 2.0092 | 2.0092
2024-02-09 01:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2023-12-10 01:00 | 1.7224 | 2.0408 | 2.0408 | 2.0408 | 2.0408
2024-02-09 02:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2023-12-10 02:00 | 1.6614 | 1.9686 | 1.9686 | 1.9686 | 1.9686
2024-02-09 03:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2023-12-10 03:00 | 1.7185 | 2.0363 | 2.0363 | 2.0363 | 2.0363
2024-02-09 04:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2023-12-10 04:00 | 1.9357 | 2.2937 | 2.2937 | 2.2937 | 2.2937
2024-02-09 05:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2023-12-10 05:00 | 2.1034 | 2.4924 | 2.4924 | 2.4924 | 2.4924
2024-02-09 06:00 | 1.7528 | 2.1805 | 2.6344 | 2.695 | 2.7555 | 2023-12-10 06:00 | 2.1186 | 2.5104 | 2.5104 | 2.5104 | 2.5104
2024-02-09 07:00 | 2.0958 | 2.6071 | 3.1499 | 3.2222 | 3.2946 | 2023-12-10 07:00 | 2.2749 | 2.6955 | 2.6955 | 2.6955 | 2.6955
2024-02-09 08:00 | 2.1148 | 2.6308 | 3.1785 | 3.2515 | 3.3245 | 2023-12-10 08:00 | 3.0217 | 3.5805 | 3.5805 | 3.5805 | 3.5805
2024-02-09 09:00 | 2.0577 | 2.5597 | 3.0926 | 3.1636 | 3.2347 | 2023-12-10 09:00 | 3.0675 | 3.6347 | 3.6347 | 3.6347 | 3.6347
2024-02-09 10:00 | 2.2673 | 2.8204 | 3.4076 | 3.4859 | 3.5642 | 2023-12-10 10:00 | 2.9798 | 3.5308 | 3.5308 | 3.5308 | 3.5308
2024-02-09 11:00 | 2.2863 | 2.8441 | 3.4362 | 3.5152 | 3.5941 | 2023-12-10 11:00 | 3.1703 | 3.7566 | 3.7566 | 3.7566 | 3.7566
2024-02-09 12:00 | 2.4006 | 2.9863 | 3.608 | 3.6909 | 3.7738 | 2023-12-10 12:00 | 3.319 | 3.9327 | 3.9327 | 3.9327 | 3.9327
2024-02-09 13:00 | 2.4006 | 2.9863 | 3.608 | 3.6909 | 3.7738 | 2023-12-10 13:00 | 3.5133 | 4.163 | 4.163 | 4.163 | 4.163
2024-02-09 14:00 | 2.4387 | 3.0337 | 3.6653 | 3.7495 | 3.8337 | 2023-12-10 14:00 | 3.3609 | 3.9824 | 3.9824 | 3.9824 | 3.9824
2024-02-09 15:00 | 2.5149 | 3.1285 | 3.7798 | 3.8667 | 3.9535 | 2023-12-10 15:00 | 3.54 | 4.1946 | 4.1946 | 4.1946 | 4.1946
2024-02-09 16:00 | 2.4768 | 3.0811 | 3.7226 | 3.8081 | 3.8936 | 2023-12-10 16:00 | 3.5247 | 4.1765 | 4.1765 | 4.1765 | 4.1765
2024-02-09 17:00 | 2.3625 | 2.9389 | 3.5508 | 3.6323 | 3.7139 | 2023-12-10 17:00 | 3.2351 | 3.8334 | 3.8334 | 3.8334 | 3.8334
2024-02-09 18:00 | 2.1339 | 2.6545 | 3.2071 | 3.2808 | 3.3545 | 2023-12-10 18:00 | 2.8503 | 3.3773 | 3.3773 | 3.3773 | 3.3773
2024-02-09 19:00 | 1.8481 | 2.299 | 2.7776 | 2.8414 | 2.9052 | 2023-12-10 19:00 | 2.5569 | 3.0297 | 3.0297 | 3.0297 | 3.0297
2024-02-09 20:00 | 1.7338 | 2.1568 | 2.6058 | 2.6657 | 2.7255 | 2023-12-10 20:00 | 2.233 | 2.6459 | 2.6459 | 2.6459 | 2.6459
2024-02-09 21:00 | 1.7338 | 2.1568 | 2.6058 | 2.6657 | 2.7255 | 2023-12-10 21:00 | 2.2863 | 2.7091 | 2.7091 | 2.7091 | 2.7091
2024-02-09 22:00 | 1.6957 | 2.1094 | 2.5485 | 2.6071 | 2.6656 | 2023-12-10 22:00 | 2.0158 | 2.3885 | 2.3885 | 2.3885 | 2.3885
2024-02-09 23:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2023-12-10 23:00 | 1.8214 | 2.1582 | 2.1582 | 2.1582 | 2.1582
2024-02-10 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2023-12-11 | 1.8214 | 2.1582 | 2.1582 | 2.1582 | 2.1582
2024-02-10 01:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2023-12-11 01:00 | 1.81 | 2.1447 | 2.1447 | 2.1447 | 2.1447
2024-02-10 02:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2023-12-11 02:00 | 1.8176 | 2.1537 | 2.1537 | 2.1537 | 2.1537
2024-02-10 03:00 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2023-12-11 03:00 | 1.8976 | 2.2485 | 2.2485 | 2.2485 | 2.2485
2024-02-10 04:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2023-12-11 04:00 | 1.9853 | 2.3524 | 2.3524 | 2.3524 | 2.3524
2024-02-10 05:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2023-12-11 05:00 | 2.1987 | 2.6052 | 2.6052 | 2.6052 | 2.6052
2024-02-10 06:00 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2023-12-11 06:00 | 2.5302 | 2.9981 | 2.9981 | 2.9981 | 2.9981
2024-02-10 07:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2023-12-11 07:00 | 2.9189 | 3.4586 | 3.4586 | 3.4586 | 3.4586
2024-02-10 08:00 | 1.4099 | 1.7539 | 2.119 | 2.1677 | 2.2164 | 2023-12-11 08:00 | 3.5704 | 4.2307 | 4.2307 | 4.2307 | 4.2307
2024-02-10 09:00 | 1.2956 | 1.6117 | 1.9472 | 1.9919 | 2.0367 | 2023-12-11 09:00 | 3.8829 | 4.6009 | 4.6009 | 4.6009 | 4.6009
2024-02-10 10:00 | 1.3718 | 1.7065 | 2.0617 | 2.1091 | 2.1565 | 2023-12-11 10:00 | 4.3097 | 5.1066 | 5.1066 | 5.1066 | 5.1066
2024-02-10 11:00 | 1.4099 | 1.7539 | 2.119 | 2.1677 | 2.2164 | 2023-12-11 11:00 | 4.2983 | 5.0931 | 5.0931 | 5.0931 | 5.0931
2024-02-10 12:00 | 1.3908 | 1.7302 | 2.0904 | 2.1384 | 2.1864 | 2023-12-11 12:00 | 4.3211 | 5.1202 | 5.1202 | 5.1202 | 5.1202
2024-02-10 13:00 | 1.3908 | 1.7302 | 2.0904 | 2.1384 | 2.1864 | 2023-12-11 13:00 | 4.4926 | 5.3233 | 5.3233 | 5.3233 | 5.3233
2024-02-10 14:00 | 1.3718 | 1.7065 | 2.0617 | 2.1091 | 2.1565 | 2023-12-11 14:00 | 4.2411 | 5.0253 | 5.0253 | 5.0253 | 5.0253
2024-02-10 15:00 | 1.4289 | 1.7776 | 2.1476 | 2.197 | 2.2463 | 2023-12-11 15:00 | 4.4164 | 5.233 | 5.233 | 5.233 | 5.233
2024-02-10 16:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2023-12-11 16:00 | 4.405 | 5.2195 | 5.2195 | 5.2195 | 5.2195
2024-02-10 17:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2023-12-11 17:00 | 4.1878 | 4.9621 | 4.9621 | 4.9621 | 4.9621
2024-02-10 18:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2023-12-11 18:00 | 3.5362 | 4.19 | 4.19 | 4.19 | 4.19
2024-02-10 19:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2023-12-11 19:00 | 3.1703 | 3.7566 | 3.7566 | 3.7566 | 3.7566
2024-02-10 20:00 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2023-12-11 20:00 | 2.816 | 3.3367 | 3.3367 | 3.3367 | 3.3367
2024-02-10 21:00 | 1.6957 | 2.1094 | 2.5485 | 2.6071 | 2.6656 | 2023-12-11 21:00 | 2.454 | 2.9077 | 2.9077 | 2.9077 | 2.9077
2024-02-10 22:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2023-12-11 22:00 | 2.172 | 2.5736 | 2.5736 | 2.5736 | 2.5736
2024-02-10 23:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2023-12-11 23:00 | 1.9091 | 2.2621 | 2.2621 | 2.2621 | 2.2621
2024-02-11 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2023-12-12 | 1.7681 | 2.095 | 2.095 | 2.095 | 2.095
2024-02-11 01:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2023-12-12 01:00 | 1.7719 | 2.0995 | 2.0995 | 2.0995 | 2.0995
2024-02-11 02:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2023-12-12 02:00 | 1.7414 | 2.0634 | 2.0634 | 2.0634 | 2.0634
2024-02-11 03:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2023-12-12 03:00 | 1.8443 | 2.1853 | 2.1853 | 2.1853 | 2.1853
2024-02-11 04:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2023-12-12 04:00 | 2.0196 | 2.393 | 2.393 | 2.393 | 2.393
2024-02-11 05:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2023-12-12 05:00 | 2.4121 | 2.8581 | 2.8581 | 2.8581 | 2.8581
2024-02-11 06:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2023-12-12 06:00 | 2.5988 | 3.0793 | 3.0793 | 3.0793 | 3.0793
2024-02-11 07:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2023-12-12 07:00 | 3.2847 | 3.892 | 3.892 | 3.892 | 3.892
2024-02-11 08:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2023-12-12 08:00 | 3.7305 | 4.4203 | 4.4203 | 4.4203 | 4.4203
2024-02-11 09:00 | 1.3908 | 1.7302 | 2.0904 | 2.1384 | 2.1864 | 2023-12-12 09:00 | 3.8562 | 4.5693 | 4.5693 | 4.5693 | 4.5693
2024-02-11 10:00 | 1.4099 | 1.7539 | 2.119 | 2.1677 | 2.2164 | 2023-12-12 10:00 | 4.001 | 4.7409 | 4.7409 | 4.7409 | 4.7409
2024-02-11 11:00 | 1.3718 | 1.7065 | 2.0617 | 2.1091 | 2.1565 | 2023-12-12 11:00 | 3.7381 | 4.4294 | 4.4294 | 4.4294 | 4.4294
2024-02-11 12:00 | 1.3337 | 1.6591 | 2.0045 | 2.0505 | 2.0966 | 2023-12-12 12:00 | 4.3935 | 5.206 | 5.206 | 5.206 | 5.206
2024-02-11 13:00 | 1.3146 | 1.6354 | 1.9758 | 2.0212 | 2.0666 | 2023-12-12 13:00 | 3.9591 | 4.6912 | 4.6912 | 4.6912 | 4.6912
2024-02-11 14:00 | 1.2765 | 1.588 | 1.9186 | 1.9626 | 2.0067 | 2023-12-12 14:00 | 4.1992 | 4.9757 | 4.9757 | 4.9757 | 4.9757
2024-02-11 15:00 | 1.3718 | 1.7065 | 2.0617 | 2.1091 | 2.1565 | 2023-12-12 15:00 | 4.2182 | 4.9983 | 4.9983 | 4.9983 | 4.9983
2024-02-11 16:00 | 1.4289 | 1.7776 | 2.1476 | 2.197 | 2.2463 | 2023-12-12 16:00 | 4.2068 | 4.9847 | 4.9847 | 4.9847 | 4.9847
2024-02-11 17:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2023-12-12 17:00 | 4.3973 | 5.2105 | 5.2105 | 5.2105 | 5.2105
2024-02-11 18:00 | 1.6957 | 2.1094 | 2.5485 | 2.6071 | 2.6656 | 2023-12-12 18:00 | 3.3875 | 4.014 | 4.014 | 4.014 | 4.014
2024-02-11 19:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2023-12-12 19:00 | 3.1551 | 3.7385 | 3.7385 | 3.7385 | 3.7385
2024-02-11 20:00 | 1.6957 | 2.1094 | 2.5485 | 2.6071 | 2.6656 | 2023-12-12 20:00 | 2.7893 | 3.3051 | 3.3051 | 3.3051 | 3.3051
2024-02-11 21:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2023-12-12 21:00 | 2.5988 | 3.0793 | 3.0793 | 3.0793 | 3.0793
2024-02-11 22:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2023-12-12 22:00 | 2.092 | 2.4788 | 2.4788 | 2.4788 | 2.4788
2024-02-11 23:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2023-12-12 23:00 | 1.8786 | 2.226 | 2.226 | 2.226 | 2.226
2024-02-12 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2023-12-13 | 1.7719 | 2.0995 | 2.0995 | 2.0995 | 2.0995
2024-02-12 01:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2023-12-13 01:00 | 1.669 | 1.9776 | 1.9776 | 1.9776 | 1.9776
2024-02-12 02:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2023-12-13 02:00 | 1.6385 | 1.9415 | 1.9415 | 1.9415 | 1.9415
2024-02-12 03:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2023-12-13 03:00 | 1.81 | 2.1447 | 2.1447 | 2.1447 | 2.1447
2024-02-12 04:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2023-12-13 04:00 | 2.1872 | 2.5917 | 2.5917 | 2.5917 | 2.5917
2024-02-12 05:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2023-12-13 05:00 | 2.313 | 2.7407 | 2.7407 | 2.7407 | 2.7407
2024-02-12 06:00 | 1.7528 | 2.1805 | 2.6344 | 2.695 | 2.7555 | 2023-12-13 06:00 | 2.6254 | 3.1109 | 3.1109 | 3.1109 | 3.1109
2024-02-12 07:00 | 2.3054 | 2.8678 | 3.4648 | 3.5445 | 3.6241 | 2023-12-13 07:00 | 3.197 | 3.7882 | 3.7882 | 3.7882 | 3.7882
2024-02-12 08:00 | 2.3435 | 2.9152 | 3.5221 | 3.603 | 3.684 | 2023-12-13 08:00 | 3.3952 | 4.023 | 4.023 | 4.023 | 4.023
2024-02-12 09:00 | 2.6864 | 3.3418 | 4.0375 | 4.1303 | 4.2231 | 2023-12-13 09:00 | 3.7343 | 4.4248 | 4.4248 | 4.4248 | 4.4248
2024-02-12 10:00 | 2.8579 | 3.5551 | 4.2953 | 4.3939 | 4.4926 | 2023-12-13 10:00 | 3.7343 | 4.4248 | 4.4248 | 4.4248 | 4.4248
2024-02-12 11:00 | 2.8769 | 3.5788 | 4.3239 | 4.4232 | 4.5226 | 2023-12-13 11:00 | 4.1458 | 4.9125 | 4.9125 | 4.9125 | 4.9125
2024-02-12 12:00 | 3.0294 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2023-12-13 12:00 | 4.565 | 5.4091 | 5.4091 | 5.4091 | 5.4091
2024-02-12 13:00 | 3.0675 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2023-12-13 13:00 | 4.5459 | 5.3866 | 5.3866 | 5.3866 | 5.3866
2024-02-12 14:00 | 3.2199 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2023-12-13 14:00 | 4.3897 | 5.2014 | 5.2014 | 5.2014 | 5.2014
2024-02-12 15:00 | 3.0865 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2023-12-13 15:00 | 4.3211 | 5.1202 | 5.1202 | 5.1202 | 5.1202
2024-02-12 16:00 | 3.0865 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2023-12-13 16:00 | 4.5459 | 5.3866 | 5.3866 | 5.3866 | 5.3866
2024-02-12 17:00 | 2.8769 | 3.5788 | 4.3239 | 4.4232 | 4.5226 | 2023-12-13 17:00 | 4.3173 | 5.1157 | 5.1157 | 5.1157 | 5.1157
2024-02-12 18:00 | 2.4768 | 3.0811 | 3.7226 | 3.8081 | 3.8936 | 2023-12-13 18:00 | 3.5819 | 4.2442 | 4.2442 | 4.2442 | 4.2442
2024-02-12 19:00 | 2.2673 | 2.8204 | 3.4076 | 3.4859 | 3.5642 | 2023-12-13 19:00 | 3.4447 | 4.0817 | 4.0817 | 4.0817 | 4.0817
2024-02-12 20:00 | 1.9243 | 2.3938 | 2.8921 | 2.9586 | 3.025 | 2023-12-13 20:00 | 3.2313 | 3.8288 | 3.8288 | 3.8288 | 3.8288
2024-02-12 21:00 | 1.8481 | 2.299 | 2.7776 | 2.8414 | 2.9052 | 2023-12-13 21:00 | 2.4654 | 2.9213 | 2.9213 | 2.9213 | 2.9213
2024-02-12 22:00 | 1.7909 | 2.2279 | 2.6917 | 2.7535 | 2.8154 | 2023-12-13 22:00 | 2.2139 | 2.6233 | 2.6233 | 2.6233 | 2.6233
2024-02-12 23:00 | 1.7338 | 2.1568 | 2.6058 | 2.6657 | 2.7255 | 2023-12-13 23:00 | 1.9053 | 2.2576 | 2.2576 | 2.2576 | 2.2576
2024-02-13 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2023-12-14 | 1.9586 | 2.3208 | 2.3208 | 2.3208 | 2.3208
2024-02-13 01:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2023-12-14 01:00 | 1.871 | 2.2169 | 2.2169 | 2.2169 | 2.2169
2024-02-13 02:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2023-12-14 02:00 | 1.7452 | 2.0679 | 2.0679 | 2.0679 | 2.0679
2024-02-13 03:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2023-12-14 03:00 | 1.9815 | 2.3479 | 2.3479 | 2.3479 | 2.3479
2024-02-13 04:00 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2023-12-14 04:00 | 2.1186 | 2.5104 | 2.5104 | 2.5104 | 2.5104
2024-02-13 05:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2023-12-14 05:00 | 2.2787 | 2.7001 | 2.7001 | 2.7001 | 2.7001
2024-02-13 06:00 | 2.0386 | 2.536 | 3.064 | 3.1344 | 3.2047 | 2023-12-14 06:00 | 2.7702 | 3.2825 | 3.2825 | 3.2825 | 3.2825
2024-02-13 07:00 | 2.3816 | 2.9626 | 3.5794 | 3.6616 | 3.7439 | 2023-12-14 07:00 | 3.2504 | 3.8514 | 3.8514 | 3.8514 | 3.8514
2024-02-13 08:00 | 2.7245 | 3.3892 | 4.0948 | 4.1889 | 4.283 | 2023-12-14 08:00 | 3.8334 | 4.5422 | 4.5422 | 4.5422 | 4.5422
2024-02-13 09:00 | 2.915 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2023-12-14 09:00 | 4.3021 | 5.0976 | 5.0976 | 5.0976 | 5.0976
2024-02-13 10:00 | 2.9913 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2023-12-14 10:00 | 4.4354 | 5.2556 | 5.2556 | 5.2556 | 5.2556
2024-02-13 11:00 | 2.9913 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2023-12-14 11:00 | 4.5307 | 5.3685 | 5.3685 | 5.3685 | 5.3685
2024-02-13 12:00 | 3.1437 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2023-12-14 12:00 | 4.3287 | 5.1292 | 5.1292 | 5.1292 | 5.1292
2024-02-13 13:00 | 3.3723 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2023-12-14 13:00 | 4.4774 | 5.3053 | 5.3053 | 5.3053 | 5.3053
2024-02-13 14:00 | 3.3914 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2023-12-14 14:00 | 4.4202 | 5.2376 | 5.2376 | 5.2376 | 5.2376
2024-02-13 15:00 | 3.258 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2023-12-14 15:00 | 4.2754 | 5.066 | 5.066 | 5.066 | 5.066
2024-02-13 16:00 | 3.0294 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2023-12-14 16:00 | 4.3364 | 5.1382 | 5.1382 | 5.1382 | 5.1382
2024-02-13 17:00 | 2.7626 | 3.4366 | 4.1521 | 4.2475 | 4.3429 | 2023-12-14 17:00 | 3.681 | 4.3616 | 4.3616 | 4.3616 | 4.3616
2024-02-13 18:00 | 2.3816 | 2.9626 | 3.5794 | 3.6616 | 3.7439 | 2023-12-14 18:00 | 3.3799 | 4.0049 | 4.0049 | 4.0049 | 4.0049
2024-02-13 19:00 | 1.9243 | 2.3938 | 2.8921 | 2.9586 | 3.025 | 2023-12-14 19:00 | 3.037 | 3.5986 | 3.5986 | 3.5986 | 3.5986
2024-02-13 20:00 | 1.9243 | 2.3938 | 2.8921 | 2.9586 | 3.025 | 2023-12-14 20:00 | 2.957 | 3.5037 | 3.5037 | 3.5037 | 3.5037
2024-02-13 21:00 | 1.7909 | 2.2279 | 2.6917 | 2.7535 | 2.8154 | 2023-12-14 21:00 | 2.3282 | 2.7587 | 2.7587 | 2.7587 | 2.7587
2024-02-13 22:00 | 1.6957 | 2.1094 | 2.5485 | 2.6071 | 2.6656 | 2023-12-14 22:00 | 2.092 | 2.4788 | 2.4788 | 2.4788 | 2.4788
2024-02-13 23:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2023-12-14 23:00 | 1.8633 | 2.2079 | 2.2079 | 2.2079 | 2.2079
2024-02-14 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2023-12-15 | 1.8176 | 2.1537 | 2.1537 | 2.1537 | 2.1537
2024-02-14 01:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2023-12-15 01:00 | 1.7414 | 2.0634 | 2.0634 | 2.0634 | 2.0634
2024-02-14 02:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2023-12-15 02:00 | 1.7071 | 2.0228 | 2.0228 | 2.0228 | 2.0228
2024-02-14 03:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2023-12-15 03:00 | 1.8214 | 2.1582 | 2.1582 | 2.1582 | 2.1582
2024-02-14 04:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2023-12-15 04:00 | 2.0615 | 2.4427 | 2.4427 | 2.4427 | 2.4427
2024-02-14 05:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2023-12-15 05:00 | 2.2063 | 2.6143 | 2.6143 | 2.6143 | 2.6143
2024-02-14 06:00 | 2.1339 | 2.6545 | 3.2071 | 3.2808 | 3.3545 | 2023-12-15 06:00 | 2.3854 | 2.8265 | 2.8265 | 2.8265 | 2.8265
2024-02-14 07:00 | 2.5911 | 3.2233 | 3.8944 | 3.9838 | 4.0733 | 2023-12-15 07:00 | 2.5149 | 2.98 | 2.98 | 2.98 | 2.98
2024-02-14 08:00 | 2.6293 | 3.2707 | 3.9516 | 4.0424 | 4.1332 | 2023-12-15 08:00 | 2.8617 | 3.3909 | 3.3909 | 3.3909 | 3.3909
2024-02-14 09:00 | 2.7436 | 3.4129 | 4.1235 | 4.2182 | 4.3129 | 2023-12-15 09:00 | 3.7838 | 4.4835 | 4.4835 | 4.4835 | 4.4835
2024-02-14 10:00 | 2.9722 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2023-12-15 10:00 | 3.8982 | 4.619 | 4.619 | 4.619 | 4.619
2024-02-14 11:00 | 2.915 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2023-12-15 11:00 | 4.1763 | 4.9486 | 4.9486 | 4.9486 | 4.9486
2024-02-14 12:00 | 2.896 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2023-12-15 12:00 | 3.7991 | 4.5016 | 4.5016 | 4.5016 | 4.5016
2024-02-14 13:00 | 2.896 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2023-12-15 13:00 | 4.2335 | 5.0163 | 5.0163 | 5.0163 | 5.0163
2024-02-14 14:00 | 2.7436 | 3.4129 | 4.1235 | 4.2182 | 4.3129 | 2023-12-15 14:00 | 4.3973 | 5.2105 | 5.2105 | 5.2105 | 5.2105
2024-02-14 15:00 | 2.7055 | 3.3655 | 4.0662 | 4.1596 | 4.253 | 2023-12-15 15:00 | 4.3707 | 5.1789 | 5.1789 | 5.1789 | 5.1789
2024-02-14 16:00 | 2.8198 | 3.5077 | 4.238 | 4.3354 | 4.4327 | 2023-12-15 16:00 | 4.1687 | 4.9396 | 4.9396 | 4.9396 | 4.9396
2024-02-14 17:00 | 2.5721 | 3.1996 | 3.8657 | 3.9546 | 4.0434 | 2023-12-15 17:00 | 3.8524 | 4.5648 | 4.5648 | 4.5648 | 4.5648
2024-02-14 18:00 | 2.2863 | 2.8441 | 3.4362 | 3.5152 | 3.5941 | 2023-12-15 18:00 | 3.5057 | 4.1539 | 4.1539 | 4.1539 | 4.1539
2024-02-14 19:00 | 1.829 | 2.2753 | 2.749 | 2.8121 | 2.8753 | 2023-12-15 19:00 | 3.4257 | 4.0591 | 4.0591 | 4.0591 | 4.0591
2024-02-14 20:00 | 1.7338 | 2.1568 | 2.6058 | 2.6657 | 2.7255 | 2023-12-15 20:00 | 2.976 | 3.5263 | 3.5263 | 3.5263 | 3.5263
2024-02-14 21:00 | 1.6957 | 2.1094 | 2.5485 | 2.6071 | 2.6656 | 2023-12-15 21:00 | 2.4997 | 2.9619 | 2.9619 | 2.9619 | 2.9619
2024-02-14 22:00 | 1.7338 | 2.1568 | 2.6058 | 2.6657 | 2.7255 | 2023-12-15 22:00 | 2.1339 | 2.5285 | 2.5285 | 2.5285 | 2.5285
2024-02-14 23:00 | 1.7147 | 2.1331 | 2.5772 | 2.6364 | 2.6956 | 2023-12-15 23:00 | 1.8252 | 2.1628 | 2.1628 | 2.1628 | 2.1628
2024-02-15 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2023-12-16 | 1.6576 | 1.9641 | 1.9641 | 1.9641 | 1.9641
2024-02-15 01:00 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2023-12-16 01:00 | 1.6728 | 1.9821 | 1.9821 | 1.9821 | 1.9821
2024-02-15 02:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2023-12-16 02:00 | 1.6576 | 1.9641 | 1.9641 | 1.9641 | 1.9641
2024-02-15 03:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2023-12-16 03:00 | 1.7376 | 2.0589 | 2.0589 | 2.0589 | 2.0589
2024-02-15 04:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2023-12-16 04:00 | 1.9396 | 2.2982 | 2.2982 | 2.2982 | 2.2982
2024-02-15 05:00 | 1.7147 | 2.1331 | 2.5772 | 2.6364 | 2.6956 | 2023-12-16 05:00 | 2.0805 | 2.4653 | 2.4653 | 2.4653 | 2.4653
2024-02-15 06:00 | 1.9053 | 2.3701 | 2.8635 | 2.9293 | 2.9951 | 2023-12-16 06:00 | 2.0882 | 2.4743 | 2.4743 | 2.4743 | 2.4743
2024-02-15 07:00 | 2.3054 | 2.8678 | 3.4648 | 3.5445 | 3.6241 | 2023-12-16 07:00 | 2.1834 | 2.5872 | 2.5872 | 2.5872 | 2.5872
2024-02-15 08:00 | 2.4006 | 2.9863 | 3.608 | 3.6909 | 3.7738 | 2023-12-16 08:00 | 2.1872 | 2.5917 | 2.5917 | 2.5917 | 2.5917
2024-02-15 09:00 | 2.4578 | 3.0574 | 3.6939 | 3.7788 | 3.8637 | 2023-12-16 09:00 | 2.1186 | 2.5104 | 2.5104 | 2.5104 | 2.5104
2024-02-15 10:00 | 2.4768 | 3.0811 | 3.7226 | 3.8081 | 3.8936 | 2023-12-16 10:00 | 2.3816 | 2.822 | 2.822 | 2.822 | 2.822
2024-02-15 11:00 | 2.4387 | 3.0337 | 3.6653 | 3.7495 | 3.8337 | 2023-12-16 11:00 | 2.7893 | 3.3051 | 3.3051 | 3.3051 | 3.3051
2024-02-15 12:00 | 2.534 | 3.1522 | 3.8085 | 3.896 | 3.9835 | 2023-12-16 12:00 | 2.7893 | 3.3051 | 3.3051 | 3.3051 | 3.3051
2024-02-15 13:00 | 2.4768 | 3.0811 | 3.7226 | 3.8081 | 3.8936 | 2023-12-16 13:00 | 3.0484 | 3.6121 | 3.6121 | 3.6121 | 3.6121
2024-02-15 14:00 | 2.4387 | 3.0337 | 3.6653 | 3.7495 | 3.8337 | 2023-12-16 14:00 | 2.8388 | 3.3638 | 3.3638 | 3.3638 | 3.3638
2024-02-15 15:00 | 2.4197 | 3.01 | 3.6367 | 3.7202 | 3.8038 | 2023-12-16 15:00 | 3.0408 | 3.6031 | 3.6031 | 3.6031 | 3.6031
2024-02-15 16:00 | 2.3435 | 2.9152 | 3.5221 | 3.603 | 3.684 | 2023-12-16 16:00 | 3.3113 | 3.9237 | 3.9237 | 3.9237 | 3.9237
2024-02-15 17:00 | 2.2101 | 2.7493 | 3.3217 | 3.398 | 3.4743 | 2023-12-16 17:00 | 2.9189 | 3.4586 | 3.4586 | 3.4586 | 3.4586
2024-02-15 18:00 | 2.0767 | 2.5834 | 3.1212 | 3.1929 | 3.2646 | 2023-12-16 18:00 | 2.4959 | 2.9574 | 2.9574 | 2.9574 | 2.9574
2024-02-15 19:00 | 1.8481 | 2.299 | 2.7776 | 2.8414 | 2.9052 | 2023-12-16 19:00 | 2.6978 | 3.1967 | 3.1967 | 3.1967 | 3.1967
2024-02-15 20:00 | 1.7528 | 2.1805 | 2.6344 | 2.695 | 2.7555 | 2023-12-16 20:00 | 2.2711 | 2.691 | 2.691 | 2.691 | 2.691
2024-02-15 21:00 | 1.6957 | 2.1094 | 2.5485 | 2.6071 | 2.6656 | 2023-12-16 21:00 | 2.1186 | 2.5104 | 2.5104 | 2.5104 | 2.5104
2024-02-15 22:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2023-12-16 22:00 | 1.8672 | 2.2124 | 2.2124 | 2.2124 | 2.2124
2024-02-15 23:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2023-12-16 23:00 | 1.7757 | 2.1041 | 2.1041 | 2.1041 | 2.1041
2024-02-16 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2023-12-17 | 1.7224 | 2.0408 | 2.0408 | 2.0408 | 2.0408
2024-02-16 01:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2023-12-17 01:00 | 1.6957 | 2.0092 | 2.0092 | 2.0092 | 2.0092
2024-02-16 02:00 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2023-12-17 02:00 | 1.6423 | 1.946 | 1.946 | 1.946 | 1.946
2024-02-16 03:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2023-12-17 03:00 | 1.7033 | 2.0183 | 2.0183 | 2.0183 | 2.0183
2024-02-16 04:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2023-12-17 04:00 | 1.8405 | 2.1808 | 2.1808 | 2.1808 | 2.1808
2024-02-16 05:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2023-12-17 05:00 | 2.2101 | 2.6188 | 2.6188 | 2.6188 | 2.6188
2024-02-16 06:00 | 1.8672 | 2.3227 | 2.8062 | 2.8707 | 2.9352 | 2023-12-17 06:00 | 2.1491 | 2.5465 | 2.5465 | 2.5465 | 2.5465
2024-02-16 07:00 | 2.3244 | 2.8915 | 3.4935 | 3.5737 | 3.654 | 2023-12-17 07:00 | 2.1148 | 2.5059 | 2.5059 | 2.5059 | 2.5059
2024-02-16 08:00 | 2.3244 | 2.8915 | 3.4935 | 3.5737 | 3.654 | 2023-12-17 08:00 | 2.5264 | 2.9935 | 2.9935 | 2.9935 | 2.9935
2024-02-16 09:00 | 2.4578 | 3.0574 | 3.6939 | 3.7788 | 3.8637 | 2023-12-17 09:00 | 2.9265 | 3.4676 | 3.4676 | 3.4676 | 3.4676
2024-02-16 10:00 | 2.4006 | 2.9863 | 3.608 | 3.6909 | 3.7738 | 2023-12-17 10:00 | 3.0027 | 3.5579 | 3.5579 | 3.5579 | 3.5579
2024-02-16 11:00 | 2.4768 | 3.0811 | 3.7226 | 3.8081 | 3.8936 | 2023-12-17 11:00 | 3.1056 | 3.6798 | 3.6798 | 3.6798 | 3.6798
2024-02-16 12:00 | 2.6483 | 3.2944 | 3.9803 | 4.0717 | 4.1632 | 2023-12-17 12:00 | 2.6712 | 3.1651 | 3.1651 | 3.1651 | 3.1651
2024-02-16 13:00 | 2.6674 | 3.3181 | 4.0089 | 4.101 | 4.1931 | 2023-12-17 13:00 | 3.0217 | 3.5805 | 3.5805 | 3.5805 | 3.5805
2024-02-16 14:00 | 2.7055 | 3.3655 | 4.0662 | 4.1596 | 4.253 | 2023-12-17 14:00 | 2.957 | 3.5037 | 3.5037 | 3.5037 | 3.5037
2024-02-16 15:00 | 2.7626 | 3.4366 | 4.1521 | 4.2475 | 4.3429 | 2023-12-17 15:00 | 2.9455 | 3.4902 | 3.4902 | 3.4902 | 3.4902
2024-02-16 16:00 | 2.7626 | 3.4366 | 4.1521 | 4.2475 | 4.3429 | 2023-12-17 16:00 | 2.7436 | 3.2509 | 3.2509 | 3.2509 | 3.2509
2024-02-16 17:00 | 2.7436 | 3.4129 | 4.1235 | 4.2182 | 4.3129 | 2023-12-17 17:00 | 2.9874 | 3.5399 | 3.5399 | 3.5399 | 3.5399
2024-02-16 18:00 | 2.5149 | 3.1285 | 3.7798 | 3.8667 | 3.9535 | 2023-12-17 18:00 | 2.6559 | 3.1471 | 3.1471 | 3.1471 | 3.1471
2024-02-16 19:00 | 2.0386 | 2.536 | 3.064 | 3.1344 | 3.2047 | 2023-12-17 19:00 | 2.5911 | 3.0703 | 3.0703 | 3.0703 | 3.0703
2024-02-16 20:00 | 1.8862 | 2.3464 | 2.8349 | 2.9 | 2.9651 | 2023-12-17 20:00 | 2.3358 | 2.7678 | 2.7678 | 2.7678 | 2.7678
2024-02-16 21:00 | 1.8481 | 2.299 | 2.7776 | 2.8414 | 2.9052 | 2023-12-17 21:00 | 2.1263 | 2.5194 | 2.5194 | 2.5194 | 2.5194
2024-02-16 22:00 | 1.7528 | 2.1805 | 2.6344 | 2.695 | 2.7555 | 2023-12-17 22:00 | 2.0043 | 2.375 | 2.375 | 2.375 | 2.375
2024-02-16 23:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2023-12-17 23:00 | 1.7909 | 2.1221 | 2.1221 | 2.1221 | 2.1221
2024-02-17 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2023-12-18 | 1.6461 | 1.9505 | 1.9505 | 1.9505 | 1.9505
2024-02-17 01:00 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2023-12-18 01:00 | 1.73 | 2.0499 | 2.0499 | 2.0499 | 2.0499
2024-02-17 02:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2023-12-18 02:00 | 1.6652 | 1.9731 | 1.9731 | 1.9731 | 1.9731
2024-02-17 03:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2023-12-18 03:00 | 1.8176 | 2.1537 | 2.1537 | 2.1537 | 2.1537
2024-02-17 04:00 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2023-12-18 04:00 | 2.0158 | 2.3885 | 2.3885 | 2.3885 | 2.3885
2024-02-17 05:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2023-12-18 05:00 | 2.252 | 2.6684 | 2.6684 | 2.6684 | 2.6684
2024-02-17 06:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2023-12-18 06:00 | 2.5645 | 3.0387 | 3.0387 | 3.0387 | 3.0387
2024-02-17 07:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2023-12-18 07:00 | 3.0522 | 3.6166 | 3.6166 | 3.6166 | 3.6166
2024-02-17 08:00 | 1.2384 | 1.5406 | 1.8613 | 1.904 | 1.9468 | 2023-12-18 08:00 | 3.5552 | 4.2126 | 4.2126 | 4.2126 | 4.2126
2024-02-17 09:00 | 0.97168 | 1.2087 | 1.4604 | 1.4939 | 1.5275 | 2023-12-18 09:00 | 3.2313 | 3.8288 | 3.8288 | 3.8288 | 3.8288
2024-02-17 10:00 | 1.2384 | 1.5406 | 1.8613 | 1.904 | 1.9468 | 2023-12-18 10:00 | 3.2313 | 3.8288 | 3.8288 | 3.8288 | 3.8288
2024-02-17 11:00 | 0.038105 | 0.047402 | 0.05727 | 0.058586 | 0.059902 | 2023-12-18 11:00 | 3.2313 | 3.8288 | 3.8288 | 3.8288 | 3.8288
2024-02-17 12:00 | 0.057158 | 0.071103 | 0.085905 | 0.087879 | 0.089853 | 2023-12-18 12:00 | 3.2313 | 3.8288 | 3.8288 | 3.8288 | 3.8288
2024-02-17 13:00 | 1.086 | 1.351 | 1.6322 | 1.6697 | 1.7072 | 2023-12-18 13:00 | 3.2313 | 3.8288 | 3.8288 | 3.8288 | 3.8288
2024-02-17 14:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2023-12-18 14:00 | 3.2313 | 3.8288 | 3.8288 | 3.8288 | 3.8288
2024-02-17 15:00 | 1.3908 | 1.7302 | 2.0904 | 2.1384 | 2.1864 | 2023-12-18 15:00 | 3.2313 | 3.8288 | 3.8288 | 3.8288 | 3.8288
2024-02-17 16:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2023-12-18 16:00 | 3.2313 | 3.8288 | 3.8288 | 3.8288 | 3.8288
2024-02-17 17:00 | 1.6957 | 2.1094 | 2.5485 | 2.6071 | 2.6656 | 2023-12-18 17:00 | 3.2313 | 3.8288 | 3.8288 | 3.8288 | 3.8288
2024-02-17 18:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2023-12-18 18:00 | 3.2427 | 3.8424 | 3.8424 | 3.8424 | 3.8424
2024-02-17 19:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2023-12-18 19:00 | 2.7169 | 3.2193 | 3.2193 | 3.2193 | 3.2193
2024-02-17 20:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2023-12-18 20:00 | 2.6902 | 3.1877 | 3.1877 | 3.1877 | 3.1877
2024-02-17 21:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2023-12-18 21:00 | 2.5645 | 3.0387 | 3.0387 | 3.0387 | 3.0387
2024-02-17 22:00 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2023-12-18 22:00 | 2.0196 | 2.393 | 2.393 | 2.393 | 2.393
2024-02-17 23:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2023-12-18 23:00 | 1.9472 | 2.3072 | 2.3072 | 2.3072 | 2.3072
2024-02-18 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2023-12-19 | 1.8405 | 2.1808 | 2.1808 | 2.1808 | 2.1808
2024-02-18 01:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2023-12-19 01:00 | 1.9396 | 2.2982 | 2.2982 | 2.2982 | 2.2982
2024-02-18 02:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2023-12-19 02:00 | 1.8214 | 2.1582 | 2.1582 | 2.1582 | 2.1582
2024-02-18 03:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2023-12-19 03:00 | 1.7757 | 2.1041 | 2.1041 | 2.1041 | 2.1041
2024-02-18 04:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2023-12-19 04:00 | 2.1491 | 2.5465 | 2.5465 | 2.5465 | 2.5465
2024-02-18 05:00 | 1.6957 | 2.1094 | 2.5485 | 2.6071 | 2.6656 | 2023-12-19 05:00 | 2.252 | 2.6684 | 2.6684 | 2.6684 | 2.6684
2024-02-18 06:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2023-12-19 06:00 | 2.8045 | 3.3231 | 3.3231 | 3.3231 | 3.3231
2024-02-18 07:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2023-12-19 07:00 | 3.117 | 3.6934 | 3.6934 | 3.6934 | 3.6934
2024-02-18 08:00 | 0.15242 | 0.18961 | 0.22908 | 0.23434 | 0.23961 | 2023-12-19 08:00 | 3.479 | 4.1223 | 4.1223 | 4.1223 | 4.1223
2024-02-18 09:00 | 0.26674 | 0.33181 | 0.40089 | 0.4101 | 0.41931 | 2023-12-19 09:00 | 4.0163 | 4.759 | 4.759 | 4.759 | 4.759
2024-02-18 10:00 | 0.11432 | 0.14221 | 0.17181 | 0.17576 | 0.17971 | 2023-12-19 10:00 | 3.9629 | 4.6957 | 4.6957 | 4.6957 | 4.6957
2024-02-18 11:00 | 0.93358 | 1.1613 | 1.4031 | 1.4354 | 1.4676 | 2023-12-19 11:00 | 4.1649 | 4.935 | 4.935 | 4.935 | 4.935
2024-02-18 12:00 | 0.17147 | 0.21331 | 0.25772 | 0.26364 | 0.26956 | 2023-12-19 12:00 | 4.3707 | 5.1789 | 5.1789 | 5.1789 | 5.1789
2024-02-18 13:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2023-12-19 13:00 | 4.5917 | 5.4407 | 5.4407 | 5.4407 | 5.4407
2024-02-18 14:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2023-12-19 14:00 | 4.9803 | 5.9013 | 5.9013 | 5.9013 | 5.9013
2024-02-18 15:00 | 0.057158 | 0.071103 | 0.085905 | 0.087879 | 0.089853 | 2023-12-19 15:00 | 5.0032 | 5.9284 | 5.9284 | 5.9284 | 5.9284
2024-02-18 16:00 | 0.7621 | 0.94804 | 1.1454 | 1.1717 | 1.198 | 2023-12-19 16:00 | 3.982 | 4.7183 | 4.7183 | 4.7183 | 4.7183
2024-02-18 17:00 | 1.1622 | 1.4458 | 1.7467 | 1.7869 | 1.827 | 2023-12-19 17:00 | 3.681 | 4.3616 | 4.3616 | 4.3616 | 4.3616
2024-02-18 18:00 | 1.7719 | 2.2042 | 2.6631 | 2.7242 | 2.7854 | 2023-12-19 18:00 | 3.3875 | 4.014 | 4.014 | 4.014 | 4.014
2024-02-18 19:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2023-12-19 19:00 | 2.9874 | 3.5399 | 3.5399 | 3.5399 | 3.5399
2024-02-18 20:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2023-12-19 20:00 | 2.4502 | 2.9032 | 2.9032 | 2.9032 | 2.9032
2024-02-18 21:00 | 1.7147 | 2.1331 | 2.5772 | 2.6364 | 2.6956 | 2023-12-19 21:00 | 2.2787 | 2.7001 | 2.7001 | 2.7001 | 2.7001
2024-02-18 22:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2023-12-19 22:00 | 2.1529 | 2.5511 | 2.5511 | 2.5511 | 2.5511
2024-02-18 23:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2023-12-19 23:00 | 1.7566 | 2.0815 | 2.0815 | 2.0815 | 2.0815
2024-02-19 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2023-12-20 | 1.5661 | 1.8557 | 1.8557 | 1.8557 | 1.8557
2024-02-19 01:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2023-12-20 01:00 | 1.669 | 1.9776 | 1.9776 | 1.9776 | 1.9776
2024-02-19 02:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2023-12-20 02:00 | 1.6652 | 1.9731 | 1.9731 | 1.9731 | 1.9731
2024-02-19 03:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2023-12-20 03:00 | 1.7833 | 2.1131 | 2.1131 | 2.1131 | 2.1131
2024-02-19 04:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2023-12-20 04:00 | 2.0043 | 2.375 | 2.375 | 2.375 | 2.375
2024-02-19 05:00 | 1.7147 | 2.1331 | 2.5772 | 2.6364 | 2.6956 | 2023-12-20 05:00 | 2.1796 | 2.5827 | 2.5827 | 2.5827 | 2.5827
2024-02-19 06:00 | 1.9243 | 2.3938 | 2.8921 | 2.9586 | 3.025 | 2023-12-20 06:00 | 2.3892 | 2.831 | 2.831 | 2.831 | 2.831
2024-02-19 07:00 | 2.0005 | 2.4886 | 3.0067 | 3.0758 | 3.1448 | 2023-12-20 07:00 | 2.6788 | 3.1741 | 3.1741 | 3.1741 | 3.1741
2024-02-19 08:00 | 2.3625 | 2.9389 | 3.5508 | 3.6323 | 3.7139 | 2023-12-20 08:00 | 3.2847 | 3.892 | 3.892 | 3.892 | 3.892
2024-02-19 09:00 | 2.4959 | 3.1048 | 3.7512 | 3.8374 | 3.9236 | 2023-12-20 09:00 | 3.5704 | 4.2307 | 4.2307 | 4.2307 | 4.2307
2024-02-19 10:00 | 2.3435 | 2.9152 | 3.5221 | 3.603 | 3.684 | 2023-12-20 10:00 | 3.6124 | 4.2804 | 4.2804 | 4.2804 | 4.2804
2024-02-19 11:00 | 2.3625 | 2.9389 | 3.5508 | 3.6323 | 3.7139 | 2023-12-20 11:00 | 3.6924 | 4.3752 | 4.3752 | 4.3752 | 4.3752
2024-02-19 12:00 | 2.553 | 3.1759 | 3.8371 | 3.9253 | 4.0134 | 2023-12-20 12:00 | 3.4028 | 4.032 | 4.032 | 4.032 | 4.032
2024-02-19 13:00 | 2.0196 | 2.5123 | 3.0353 | 3.1051 | 3.1748 | 2023-12-20 13:00 | 3.3875 | 4.014 | 4.014 | 4.014 | 4.014
2024-02-19 14:00 | 2.3244 | 2.8915 | 3.4935 | 3.5737 | 3.654 | 2023-12-20 14:00 | 3.2694 | 3.874 | 3.874 | 3.874 | 3.874
2024-02-19 15:00 | 2.3244 | 2.8915 | 3.4935 | 3.5737 | 3.654 | 2023-12-20 15:00 | 3.197 | 3.7882 | 3.7882 | 3.7882 | 3.7882
2024-02-19 16:00 | 2.7245 | 3.3892 | 4.0948 | 4.1889 | 4.283 | 2023-12-20 16:00 | 3.1703 | 3.7566 | 3.7566 | 3.7566 | 3.7566
2024-02-19 17:00 | 2.172 | 2.7019 | 3.2644 | 3.3394 | 3.4144 | 2023-12-20 17:00 | 2.976 | 3.5263 | 3.5263 | 3.5263 | 3.5263
2024-02-19 18:00 | 2.0577 | 2.5597 | 3.0926 | 3.1636 | 3.2347 | 2023-12-20 18:00 | 2.8465 | 3.3728 | 3.3728 | 3.3728 | 3.3728
2024-02-19 19:00 | 1.81 | 2.2516 | 2.7203 | 2.7828 | 2.8453 | 2023-12-20 19:00 | 2.3968 | 2.84 | 2.84 | 2.84 | 2.84
2024-02-19 20:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2023-12-20 20:00 | 2.4197 | 2.8671 | 2.8671 | 2.8671 | 2.8671
2024-02-19 21:00 | 1.7147 | 2.1331 | 2.5772 | 2.6364 | 2.6956 | 2023-12-20 21:00 | 2.2787 | 2.7001 | 2.7001 | 2.7001 | 2.7001
2024-02-19 22:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2023-12-20 22:00 | 2.1301 | 2.524 | 2.524 | 2.524 | 2.524
2024-02-19 23:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2023-12-20 23:00 | 1.7795 | 2.1086 | 2.1086 | 2.1086 | 2.1086
2024-02-20 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2023-12-21 | 1.6423 | 1.946 | 1.946 | 1.946 | 1.946
2024-02-20 01:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2023-12-21 01:00 | 1.7147 | 2.0318 | 2.0318 | 2.0318 | 2.0318
2024-02-20 02:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2023-12-21 02:00 | 1.7605 | 2.086 | 2.086 | 2.086 | 2.086
2024-02-20 03:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2023-12-21 03:00 | 1.6957 | 2.0092 | 2.0092 | 2.0092 | 2.0092
2024-02-20 04:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2023-12-21 04:00 | 2.0539 | 2.4337 | 2.4337 | 2.4337 | 2.4337
2024-02-20 05:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2023-12-21 05:00 | 2.1796 | 2.5827 | 2.5827 | 2.5827 | 2.5827
2024-02-20 06:00 | 1.9624 | 2.4412 | 2.9494 | 3.0172 | 3.0849 | 2023-12-21 06:00 | 2.1949 | 2.6007 | 2.6007 | 2.6007 | 2.6007
2024-02-20 07:00 | 2.191 | 2.7256 | 3.293 | 3.3687 | 3.4444 | 2023-12-21 07:00 | 2.5835 | 3.0613 | 3.0613 | 3.0613 | 3.0613
2024-02-20 08:00 | 2.3435 | 2.9152 | 3.5221 | 3.603 | 3.684 | 2023-12-21 08:00 | 3.0255 | 3.585 | 3.585 | 3.585 | 3.585
2024-02-20 09:00 | 2.3054 | 2.8678 | 3.4648 | 3.5445 | 3.6241 | 2023-12-21 09:00 | 2.8846 | 3.418 | 3.418 | 3.418 | 3.418
2024-02-20 10:00 | 2.534 | 3.1522 | 3.8085 | 3.896 | 3.9835 | 2023-12-21 10:00 | 2.9455 | 3.4902 | 3.4902 | 3.4902 | 3.4902
2024-02-20 11:00 | 2.3625 | 2.9389 | 3.5508 | 3.6323 | 3.7139 | 2023-12-21 11:00 | 2.9951 | 3.5489 | 3.5489 | 3.5489 | 3.5489
2024-02-20 12:00 | 2.4197 | 3.01 | 3.6367 | 3.7202 | 3.8038 | 2023-12-21 12:00 | 3.418 | 4.0501 | 4.0501 | 4.0501 | 4.0501
2024-02-20 13:00 | 2.4197 | 3.01 | 3.6367 | 3.7202 | 3.8038 | 2023-12-21 13:00 | 3.5209 | 4.172 | 4.172 | 4.172 | 4.172
2024-02-20 14:00 | 2.6674 | 3.3181 | 4.0089 | 4.101 | 4.1931 | 2023-12-21 14:00 | 3.4066 | 4.0365 | 4.0365 | 4.0365 | 4.0365
2024-02-20 15:00 | 2.4578 | 3.0574 | 3.6939 | 3.7788 | 3.8637 | 2023-12-21 15:00 | 3.3037 | 3.9146 | 3.9146 | 3.9146 | 3.9146
2024-02-20 16:00 | 1.2956 | 1.6117 | 1.9472 | 1.9919 | 2.0367 | 2023-12-21 16:00 | 3.3037 | 3.9146 | 3.9146 | 3.9146 | 3.9146
2024-02-20 17:00 | 2.2101 | 2.7493 | 3.3217 | 3.398 | 3.4743 | 2023-12-21 17:00 | 3.1361 | 3.716 | 3.716 | 3.716 | 3.716
2024-02-20 18:00 | 1.8672 | 2.3227 | 2.8062 | 2.8707 | 2.9352 | 2023-12-21 18:00 | 2.6902 | 3.1877 | 3.1877 | 3.1877 | 3.1877
2024-02-20 19:00 | 1.8672 | 2.3227 | 2.8062 | 2.8707 | 2.9352 | 2023-12-21 19:00 | 2.5264 | 2.9935 | 2.9935 | 2.9935 | 2.9935
2024-02-20 20:00 | 1.7909 | 2.2279 | 2.6917 | 2.7535 | 2.8154 | 2023-12-21 20:00 | 2.5187 | 2.9845 | 2.9845 | 2.9845 | 2.9845
2024-02-20 21:00 | 1.81 | 2.2516 | 2.7203 | 2.7828 | 2.8453 | 2023-12-21 21:00 | 2.4387 | 2.8897 | 2.8897 | 2.8897 | 2.8897
2024-02-20 22:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2023-12-21 22:00 | 2.0615 | 2.4427 | 2.4427 | 2.4427 | 2.4427
2024-02-20 23:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2023-12-21 23:00 | 1.7414 | 2.0634 | 2.0634 | 2.0634 | 2.0634
2024-02-21 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2023-12-22 | 1.6957 | 2.0092 | 2.0092 | 2.0092 | 2.0092
2024-02-21 01:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2023-12-22 01:00 | 1.6995 | 2.0138 | 2.0138 | 2.0138 | 2.0138
2024-02-21 02:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2023-12-22 02:00 | 1.7109 | 2.0273 | 2.0273 | 2.0273 | 2.0273
2024-02-21 03:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2023-12-22 03:00 | 1.8329 | 2.1718 | 2.1718 | 2.1718 | 2.1718
2024-02-21 04:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2023-12-22 04:00 | 1.9281 | 2.2847 | 2.2847 | 2.2847 | 2.2847
2024-02-21 05:00 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2023-12-22 05:00 | 2.0577 | 2.4382 | 2.4382 | 2.4382 | 2.4382
2024-02-21 06:00 | 1.829 | 2.2753 | 2.749 | 2.8121 | 2.8753 | 2023-12-22 06:00 | 2.1529 | 2.5511 | 2.5511 | 2.5511 | 2.5511
2024-02-21 07:00 | 2.2482 | 2.7967 | 3.3789 | 3.4566 | 3.5342 | 2023-12-22 07:00 | 2.1148 | 2.5059 | 2.5059 | 2.5059 | 2.5059
2024-02-21 08:00 | 2.3625 | 2.9389 | 3.5508 | 3.6323 | 3.7139 | 2023-12-22 08:00 | 2.6635 | 3.1561 | 3.1561 | 3.1561 | 3.1561
2024-02-21 09:00 | 2.3054 | 2.8678 | 3.4648 | 3.5445 | 3.6241 | 2023-12-22 09:00 | 2.6483 | 3.138 | 3.138 | 3.138 | 3.138
2024-02-21 10:00 | 2.4387 | 3.0337 | 3.6653 | 3.7495 | 3.8337 | 2023-12-22 10:00 | 2.7207 | 3.2238 | 3.2238 | 3.2238 | 3.2238
2024-02-21 11:00 | 2.534 | 3.1522 | 3.8085 | 3.896 | 3.9835 | 2023-12-22 11:00 | 2.6902 | 3.1877 | 3.1877 | 3.1877 | 3.1877
2024-02-21 12:00 | 2.4959 | 3.1048 | 3.7512 | 3.8374 | 3.9236 | 2023-12-22 12:00 | 2.5226 | 2.989 | 2.989 | 2.989 | 2.989
2024-02-21 13:00 | 2.534 | 3.1522 | 3.8085 | 3.896 | 3.9835 | 2023-12-22 13:00 | 3.7114 | 4.3977 | 4.3977 | 4.3977 | 4.3977
2024-02-21 14:00 | 2.4387 | 3.0337 | 3.6653 | 3.7495 | 3.8337 | 2023-12-22 14:00 | 3.5323 | 4.1855 | 4.1855 | 4.1855 | 4.1855
2024-02-21 15:00 | 2.5721 | 3.1996 | 3.8657 | 3.9546 | 4.0434 | 2023-12-22 15:00 | 3.3075 | 3.9191 | 3.9191 | 3.9191 | 3.9191
2024-02-21 16:00 | 2.3625 | 2.9389 | 3.5508 | 3.6323 | 3.7139 | 2023-12-22 16:00 | 3.4257 | 4.0591 | 4.0591 | 4.0591 | 4.0591
2024-02-21 17:00 | 2.3054 | 2.8678 | 3.4648 | 3.5445 | 3.6241 | 2023-12-22 17:00 | 3.3228 | 3.9372 | 3.9372 | 3.9372 | 3.9372
2024-02-21 18:00 | 1.829 | 2.2753 | 2.749 | 2.8121 | 2.8753 | 2023-12-22 18:00 | 3.2237 | 3.8198 | 3.8198 | 3.8198 | 3.8198
2024-02-21 19:00 | 1.6957 | 2.1094 | 2.5485 | 2.6071 | 2.6656 | 2023-12-22 19:00 | 3.0332 | 3.5941 | 3.5941 | 3.5941 | 3.5941
2024-02-21 20:00 | 1.8481 | 2.299 | 2.7776 | 2.8414 | 2.9052 | 2023-12-22 20:00 | 2.7626 | 3.2735 | 3.2735 | 3.2735 | 3.2735
2024-02-21 21:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2023-12-22 21:00 | 2.5759 | 3.0522 | 3.0522 | 3.0522 | 3.0522
2024-02-21 22:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2023-12-22 22:00 | 2.3358 | 2.7678 | 2.7678 | 2.7678 | 2.7678
2024-02-21 23:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2023-12-22 23:00 | 1.8786 | 2.226 | 2.226 | 2.226 | 2.226
2024-02-22 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2023-12-23 | 1.6957 | 2.0092 | 2.0092 | 2.0092 | 2.0092
2024-02-22 01:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2023-12-23 01:00 | 1.6957 | 2.0092 | 2.0092 | 2.0092 | 2.0092
2024-02-22 02:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2023-12-23 02:00 | 1.749 | 2.0724 | 2.0724 | 2.0724 | 2.0724
2024-02-22 03:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2023-12-23 03:00 | 1.8748 | 2.2214 | 2.2214 | 2.2214 | 2.2214
2024-02-22 04:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2023-12-23 04:00 | 2.0196 | 2.393 | 2.393 | 2.393 | 2.393
2024-02-22 05:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2023-12-23 05:00 | 2.0653 | 2.4472 | 2.4472 | 2.4472 | 2.4472
2024-02-22 06:00 | 1.9053 | 2.3701 | 2.8635 | 2.9293 | 2.9951 | 2023-12-23 06:00 | 2.0843 | 2.4698 | 2.4698 | 2.4698 | 2.4698
2024-02-22 07:00 | 1.9243 | 2.3938 | 2.8921 | 2.9586 | 3.025 | 2023-12-23 07:00 | 2.1263 | 2.5194 | 2.5194 | 2.5194 | 2.5194
2024-02-22 08:00 | 1.1432 | 1.4221 | 1.7181 | 1.7576 | 1.7971 | 2023-12-23 08:00 | 2.3739 | 2.8129 | 2.8129 | 2.8129 | 2.8129
2024-02-22 09:00 | 1.3718 | 1.7065 | 2.0617 | 2.1091 | 2.1565 | 2023-12-23 09:00 | 2.4159 | 2.8626 | 2.8626 | 2.8626 | 2.8626
2024-02-22 10:00 | 1.3527 | 1.6828 | 2.0331 | 2.0798 | 2.1265 | 2023-12-23 10:00 | 2.4959 | 2.9574 | 2.9574 | 2.9574 | 2.9574
2024-02-22 11:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2023-12-23 11:00 | 2.1415 | 2.5375 | 2.5375 | 2.5375 | 2.5375
2024-02-22 12:00 | 1.9243 | 2.3938 | 2.8921 | 2.9586 | 3.025 | 2023-12-23 12:00 | 2.5454 | 3.0161 | 3.0161 | 3.0161 | 3.0161
2024-02-22 13:00 | 2.0577 | 2.5597 | 3.0926 | 3.1636 | 3.2347 | 2023-12-23 13:00 | 3.2237 | 3.8198 | 3.8198 | 3.8198 | 3.8198
2024-02-22 14:00 | 2.1148 | 2.6308 | 3.1785 | 3.2515 | 3.3245 | 2023-12-23 14:00 | 3.3914 | 4.0185 | 4.0185 | 4.0185 | 4.0185
2024-02-22 15:00 | 2.1529 | 2.6782 | 3.2358 | 3.3101 | 3.3845 | 2023-12-23 15:00 | 3.2199 | 3.8153 | 3.8153 | 3.8153 | 3.8153
2024-02-22 16:00 | 2.3625 | 2.9389 | 3.5508 | 3.6323 | 3.7139 | 2023-12-23 16:00 | 3.2389 | 3.8379 | 3.8379 | 3.8379 | 3.8379
2024-02-22 17:00 | 2.6102 | 3.247 | 3.923 | 4.0131 | 4.1033 | 2023-12-23 17:00 | 3.1475 | 3.7295 | 3.7295 | 3.7295 | 3.7295
2024-02-22 18:00 | 2.1339 | 2.6545 | 3.2071 | 3.2808 | 3.3545 | 2023-12-23 18:00 | 2.6293 | 3.1154 | 3.1154 | 3.1154 | 3.1154
2024-02-22 19:00 | 2.0577 | 2.5597 | 3.0926 | 3.1636 | 3.2347 | 2023-12-23 19:00 | 2.3473 | 2.7813 | 2.7813 | 2.7813 | 2.7813
2024-02-22 20:00 | 2.0005 | 2.4886 | 3.0067 | 3.0758 | 3.1448 | 2023-12-23 20:00 | 2.2368 | 2.6504 | 2.6504 | 2.6504 | 2.6504
2024-02-22 21:00 | 1.829 | 2.2753 | 2.749 | 2.8121 | 2.8753 | 2023-12-23 21:00 | 2.1949 | 2.6007 | 2.6007 | 2.6007 | 2.6007
2024-02-22 22:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2023-12-23 22:00 | 2.2291 | 2.6414 | 2.6414 | 2.6414 | 2.6414
2024-02-22 23:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2023-12-23 23:00 | 2.0805 | 2.4653 | 2.4653 | 2.4653 | 2.4653
2024-02-23 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2023-12-24 | 1.7262 | 2.0454 | 2.0454 | 2.0454 | 2.0454
2024-02-23 01:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2023-12-24 01:00 | 1.8443 | 2.1853 | 2.1853 | 2.1853 | 2.1853
2024-02-23 02:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2023-12-24 02:00 | 1.749 | 2.0724 | 2.0724 | 2.0724 | 2.0724
2024-02-23 03:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2023-12-24 03:00 | 1.8252 | 2.1628 | 2.1628 | 2.1628 | 2.1628
2024-02-23 04:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2023-12-24 04:00 | 2.0158 | 2.3885 | 2.3885 | 2.3885 | 2.3885
2024-02-23 05:00 | 1.7147 | 2.1331 | 2.5772 | 2.6364 | 2.6956 | 2023-12-24 05:00 | 2.0767 | 2.4608 | 2.4608 | 2.4608 | 2.4608
2024-02-23 06:00 | 1.9434 | 2.4175 | 2.9208 | 2.9879 | 3.055 | 2023-12-24 06:00 | 2.0653 | 2.4472 | 2.4472 | 2.4472 | 2.4472
2024-02-23 07:00 | 2.0958 | 2.6071 | 3.1499 | 3.2222 | 3.2946 | 2023-12-24 07:00 | 2.2939 | 2.7181 | 2.7181 | 2.7181 | 2.7181
2024-02-23 08:00 | 2.2482 | 2.7967 | 3.3789 | 3.4566 | 3.5342 | 2023-12-24 08:00 | 2.4044 | 2.8491 | 2.8491 | 2.8491 | 2.8491
2024-02-23 09:00 | 2.4959 | 3.1048 | 3.7512 | 3.8374 | 3.9236 | 2023-12-24 09:00 | 2.5721 | 3.0477 | 3.0477 | 3.0477 | 3.0477
2024-02-23 10:00 | 2.8007 | 3.484 | 4.2094 | 4.3061 | 4.4028 | 2023-12-24 10:00 | 2.6559 | 3.1471 | 3.1471 | 3.1471 | 3.1471
2024-02-23 11:00 | 2.7626 | 3.4366 | 4.1521 | 4.2475 | 4.3429 | 2023-12-24 11:00 | 2.5911 | 3.0703 | 3.0703 | 3.0703 | 3.0703
2024-02-23 12:00 | 2.7055 | 3.3655 | 4.0662 | 4.1596 | 4.253 | 2023-12-24 12:00 | 3.0065 | 3.5624 | 3.5624 | 3.5624 | 3.5624
2024-02-23 13:00 | 2.6674 | 3.3181 | 4.0089 | 4.101 | 4.1931 | 2023-12-24 13:00 | 3.0751 | 3.6437 | 3.6437 | 3.6437 | 3.6437
2024-02-23 14:00 | 2.5149 | 3.1285 | 3.7798 | 3.8667 | 3.9535 | 2023-12-24 14:00 | 2.8388 | 3.3638 | 3.3638 | 3.3638 | 3.3638
2024-02-23 15:00 | 2.4578 | 3.0574 | 3.6939 | 3.7788 | 3.8637 | 2023-12-24 15:00 | 3.1513 | 3.734 | 3.734 | 3.734 | 3.734
2024-02-23 16:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2023-12-24 16:00 | 2.7969 | 3.3141 | 3.3141 | 3.3141 | 3.3141
2024-02-23 17:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2023-12-24 17:00 | 2.4235 | 2.8716 | 2.8716 | 2.8716 | 2.8716
2024-02-23 18:00 | 2.0386 | 2.536 | 3.064 | 3.1344 | 3.2047 | 2023-12-24 18:00 | 2.1682 | 2.5691 | 2.5691 | 2.5691 | 2.5691
2024-02-23 19:00 | 1.9243 | 2.3938 | 2.8921 | 2.9586 | 3.025 | 2023-12-24 19:00 | 1.8557 | 2.1989 | 2.1989 | 2.1989 | 2.1989
2024-02-23 20:00 | 1.7719 | 2.2042 | 2.6631 | 2.7242 | 2.7854 | 2023-12-24 20:00 | 1.8748 | 2.2214 | 2.2214 | 2.2214 | 2.2214
2024-02-23 21:00 | 1.7909 | 2.2279 | 2.6917 | 2.7535 | 2.8154 | 2023-12-24 21:00 | 2.012 | 2.384 | 2.384 | 2.384 | 2.384
2024-02-23 22:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2023-12-24 22:00 | 1.8443 | 2.1853 | 2.1853 | 2.1853 | 2.1853
2024-02-23 23:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2023-12-24 23:00 | 1.7224 | 2.0408 | 2.0408 | 2.0408 | 2.0408
2024-02-24 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2023-12-25 | 1.467 | 1.7383 | 1.7383 | 1.7383 | 1.7383
2024-02-24 01:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2023-12-25 01:00 | 1.5318 | 1.8151 | 1.8151 | 1.8151 | 1.8151
2024-02-24 02:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2023-12-25 02:00 | 1.4442 | 1.7112 | 1.7112 | 1.7112 | 1.7112
2024-02-24 03:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2023-12-25 03:00 | 1.509 | 1.788 | 1.788 | 1.788 | 1.788
2024-02-24 04:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2023-12-25 04:00 | 1.6233 | 1.9234 | 1.9234 | 1.9234 | 1.9234
2024-02-24 05:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2023-12-25 05:00 | 1.6538 | 1.9596 | 1.9596 | 1.9596 | 1.9596
2024-02-24 06:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2023-12-25 06:00 | 1.5356 | 1.8196 | 1.8196 | 1.8196 | 1.8196
2024-02-24 07:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2023-12-25 07:00 | 1.6004 | 1.8964 | 1.8964 | 1.8964 | 1.8964
2024-02-24 08:00 | 0.80021 | 0.99544 | 1.2027 | 1.2303 | 1.2579 | 2023-12-25 08:00 | 1.6118 | 1.9099 | 1.9099 | 1.9099 | 1.9099
2024-02-24 09:00 | 0.74305 | 0.92433 | 1.1168 | 1.1424 | 1.1681 | 2023-12-25 09:00 | 1.4823 | 1.7564 | 1.7564 | 1.7564 | 1.7564
2024-02-24 10:00 | 0.60968 | 0.75843 | 0.91632 | 0.93738 | 0.95843 | 2023-12-25 10:00 | 1.6538 | 1.9596 | 1.9596 | 1.9596 | 1.9596
2024-02-24 11:00 | 0.362 | 0.45032 | 0.54407 | 0.55657 | 0.56907 | 2023-12-25 11:00 | 1.7605 | 2.086 | 2.086 | 2.086 | 2.086
2024-02-24 12:00 | 0.62873 | 0.78213 | 0.94496 | 0.96667 | 0.98838 | 2023-12-25 12:00 | 1.6842 | 1.9957 | 1.9957 | 1.9957 | 1.9957
2024-02-24 13:00 | 0.83831 | 1.0428 | 1.2599 | 1.2889 | 1.3178 | 2023-12-25 13:00 | 1.5699 | 1.8602 | 1.8602 | 1.8602 | 1.8602
2024-02-24 14:00 | 0.32389 | 0.40292 | 0.4868 | 0.49798 | 0.50917 | 2023-12-25 14:00 | 1.7528 | 2.077 | 2.077 | 2.077 | 2.077
2024-02-24 15:00 | 0.17147 | 0.21331 | 0.25772 | 0.26364 | 0.26956 | 2023-12-25 15:00 | 1.6804 | 1.9912 | 1.9912 | 1.9912 | 1.9912
2024-02-24 16:00 | 1.4099 | 1.7539 | 2.119 | 2.1677 | 2.2164 | 2023-12-25 16:00 | 1.6728 | 1.9821 | 1.9821 | 1.9821 | 1.9821
2024-02-24 17:00 | 0.41916 | 0.52142 | 0.62997 | 0.64445 | 0.65892 | 2023-12-25 17:00 | 1.8024 | 2.1357 | 2.1357 | 2.1357 | 2.1357
2024-02-24 18:00 | 1.4099 | 1.7539 | 2.119 | 2.1677 | 2.2164 | 2023-12-25 18:00 | 1.749 | 2.0724 | 2.0724 | 2.0724 | 2.0724
2024-02-24 19:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2023-12-25 19:00 | 1.8176 | 2.1537 | 2.1537 | 2.1537 | 2.1537
2024-02-24 20:00 | 1.7528 | 2.1805 | 2.6344 | 2.695 | 2.7555 | 2023-12-25 20:00 | 1.7871 | 2.1176 | 2.1176 | 2.1176 | 2.1176
2024-02-24 21:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2023-12-25 21:00 | 1.7757 | 2.1041 | 2.1041 | 2.1041 | 2.1041
2024-02-24 22:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2023-12-25 22:00 | 1.7071 | 2.0228 | 2.0228 | 2.0228 | 2.0228
2024-02-24 23:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2023-12-25 23:00 | 1.6004 | 1.8964 | 1.8964 | 1.8964 | 1.8964
2024-02-25 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2023-12-26 | 1.5166 | 1.797 | 1.797 | 1.797 | 1.797
2024-02-25 01:00 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2023-12-26 01:00 | 1.5204 | 1.8015 | 1.8015 | 1.8015 | 1.8015
2024-02-25 02:00 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2023-12-26 02:00 | 1.6423 | 1.946 | 1.946 | 1.946 | 1.946
2024-02-25 03:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2023-12-26 03:00 | 1.7262 | 2.0454 | 2.0454 | 2.0454 | 2.0454
2024-02-25 04:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2023-12-26 04:00 | 2.0158 | 2.3885 | 2.3885 | 2.3885 | 2.3885
2024-02-25 05:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2023-12-26 05:00 | 2.3054 | 2.7317 | 2.7317 | 2.7317 | 2.7317
2024-02-25 06:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2023-12-26 06:00 | 2.1034 | 2.4924 | 2.4924 | 2.4924 | 2.4924
2024-02-25 07:00 | 1.3718 | 1.7065 | 2.0617 | 2.1091 | 2.1565 | 2023-12-26 07:00 | 2.3054 | 2.7317 | 2.7317 | 2.7317 | 2.7317
2024-02-25 08:00 | 0.64779 | 0.80583 | 0.97359 | 0.99596 | 1.0183 | 2023-12-26 08:00 | 2.2749 | 2.6955 | 2.6955 | 2.6955 | 2.6955
2024-02-25 09:00 | 0.038105 | 0.047402 | 0.05727 | 0.058586 | 0.059902 | 2023-12-26 09:00 | 2.1796 | 2.5827 | 2.5827 | 2.5827 | 2.5827
2024-02-25 10:00 | 0.13897 | 0.17288 | 0.20887 | 0.21367 | 0.21847 | 2023-12-26 10:00 | 2.252 | 2.6684 | 2.6684 | 2.6684 | 2.6684
2024-02-25 11:00 | 0.74305 | 0.92433 | 1.1168 | 1.1424 | 1.1681 | 2023-12-26 11:00 | 2.9417 | 3.4857 | 3.4857 | 3.4857 | 3.4857
2024-02-25 12:00 | 0.21077 | 0.26219 | 0.31678 | 0.32405 | 0.33133 | 2023-12-26 12:00 | 2.976 | 3.5263 | 3.5263 | 3.5263 | 3.5263
2024-02-25 13:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2023-12-26 13:00 | 3.2923 | 3.9011 | 3.9011 | 3.9011 | 3.9011
2024-02-25 14:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2023-12-26 14:00 | 3.3571 | 3.9778 | 3.9778 | 3.9778 | 3.9778
2024-02-25 15:00 | 0.11432 | 0.14221 | 0.17181 | 0.17576 | 0.17971 | 2023-12-26 15:00 | 3.1284 | 3.7069 | 3.7069 | 3.7069 | 3.7069
2024-02-25 16:00 | 0.60968 | 0.75843 | 0.91632 | 0.93738 | 0.95843 | 2023-12-26 16:00 | 3.1361 | 3.716 | 3.716 | 3.716 | 3.716
2024-02-25 17:00 | 1.2003 | 1.4932 | 1.804 | 1.8455 | 1.8869 | 2023-12-26 17:00 | 2.7398 | 3.2464 | 3.2464 | 3.2464 | 3.2464
2024-02-25 18:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2023-12-26 18:00 | 2.5454 | 3.0161 | 3.0161 | 3.0161 | 3.0161
2024-02-25 19:00 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2023-12-26 19:00 | 2.2825 | 2.7046 | 2.7046 | 2.7046 | 2.7046
2024-02-25 20:00 | 1.81 | 2.2516 | 2.7203 | 2.7828 | 2.8453 | 2023-12-26 20:00 | 2.2063 | 2.6143 | 2.6143 | 2.6143 | 2.6143
2024-02-25 21:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2023-12-26 21:00 | 2.0577 | 2.4382 | 2.4382 | 2.4382 | 2.4382
2024-02-25 22:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2023-12-26 22:00 | 1.7909 | 2.1221 | 2.1221 | 2.1221 | 2.1221
2024-02-25 23:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2023-12-26 23:00 | 1.6538 | 1.9596 | 1.9596 | 1.9596 | 1.9596
2024-02-26 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2023-12-27 | 1.5013 | 1.779 | 1.779 | 1.779 | 1.779
2024-02-26 01:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2023-12-27 01:00 | 1.5471 | 1.8331 | 1.8331 | 1.8331 | 1.8331
2024-02-26 02:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2023-12-27 02:00 | 1.5661 | 1.8557 | 1.8557 | 1.8557 | 1.8557
2024-02-26 03:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2023-12-27 03:00 | 1.7033 | 2.0183 | 2.0183 | 2.0183 | 2.0183
2024-02-26 04:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2023-12-27 04:00 | 1.8481 | 2.1898 | 2.1898 | 2.1898 | 2.1898
2024-02-26 05:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2023-12-27 05:00 | 2.0501 | 2.4291 | 2.4291 | 2.4291 | 2.4291
2024-02-26 06:00 | 1.81 | 2.2516 | 2.7203 | 2.7828 | 2.8453 | 2023-12-27 06:00 | 2.2291 | 2.6414 | 2.6414 | 2.6414 | 2.6414
2024-02-26 07:00 | 2.191 | 2.7256 | 3.293 | 3.3687 | 3.4444 | 2023-12-27 07:00 | 2.5492 | 3.0206 | 3.0206 | 3.0206 | 3.0206
2024-02-26 08:00 | 2.3244 | 2.8915 | 3.4935 | 3.5737 | 3.654 | 2023-12-27 08:00 | 2.7055 | 3.2057 | 3.2057 | 3.2057 | 3.2057
2024-02-26 09:00 | 2.3054 | 2.8678 | 3.4648 | 3.5445 | 3.6241 | 2023-12-27 09:00 | 2.6712 | 3.1651 | 3.1651 | 3.1651 | 3.1651
2024-02-26 10:00 | 1.829 | 2.2753 | 2.749 | 2.8121 | 2.8753 | 2023-12-27 10:00 | 2.7398 | 3.2464 | 3.2464 | 3.2464 | 3.2464
2024-02-26 11:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2023-12-27 11:00 | 2.393 | 2.8355 | 2.8355 | 2.8355 | 2.8355
2024-02-26 12:00 | 1.6957 | 2.1094 | 2.5485 | 2.6071 | 2.6656 | 2023-12-27 12:00 | 2.4387 | 2.8897 | 2.8897 | 2.8897 | 2.8897
2024-02-26 13:00 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2023-12-27 13:00 | 3.498 | 4.1449 | 4.1449 | 4.1449 | 4.1449
2024-02-26 14:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2023-12-27 14:00 | 3.6352 | 4.3074 | 4.3074 | 4.3074 | 4.3074
2024-02-26 15:00 | 1.4099 | 1.7539 | 2.119 | 2.1677 | 2.2164 | 2023-12-27 15:00 | 3.4485 | 4.0862 | 4.0862 | 4.0862 | 4.0862
2024-02-26 16:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2023-12-27 16:00 | 2.5873 | 3.0658 | 3.0658 | 3.0658 | 3.0658
2024-02-26 17:00 | 2.4959 | 3.1048 | 3.7512 | 3.8374 | 3.9236 | 2023-12-27 17:00 | 3.0751 | 3.6437 | 3.6437 | 3.6437 | 3.6437
2024-02-26 18:00 | 2.2863 | 2.8441 | 3.4362 | 3.5152 | 3.5941 | 2023-12-27 18:00 | 2.8655 | 3.3954 | 3.3954 | 3.3954 | 3.3954
2024-02-26 19:00 | 1.9243 | 2.3938 | 2.8921 | 2.9586 | 3.025 | 2023-12-27 19:00 | 2.4349 | 2.8852 | 2.8852 | 2.8852 | 2.8852
2024-02-26 20:00 | 1.7528 | 2.1805 | 2.6344 | 2.695 | 2.7555 | 2023-12-27 20:00 | 2.2901 | 2.7136 | 2.7136 | 2.7136 | 2.7136
2024-02-26 21:00 | 1.6957 | 2.1094 | 2.5485 | 2.6071 | 2.6656 | 2023-12-27 21:00 | 2.2939 | 2.7181 | 2.7181 | 2.7181 | 2.7181
2024-02-26 22:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2023-12-27 22:00 | 2.1072 | 2.4969 | 2.4969 | 2.4969 | 2.4969
2024-02-26 23:00 | 1.6957 | 2.1094 | 2.5485 | 2.6071 | 2.6656 | 2023-12-27 23:00 | 1.9205 | 2.2756 | 2.2756 | 2.2756 | 2.2756
2024-02-27 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2023-12-28 | 1.6347 | 1.937 | 1.937 | 1.937 | 1.937
2024-02-27 01:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2023-12-28 01:00 | 1.5966 | 1.8918 | 1.8918 | 1.8918 | 1.8918
2024-02-27 02:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2023-12-28 02:00 | 1.6004 | 1.8964 | 1.8964 | 1.8964 | 1.8964
2024-02-27 03:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2023-12-28 03:00 | 1.6881 | 2.0002 | 2.0002 | 2.0002 | 2.0002
2024-02-27 04:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2023-12-28 04:00 | 1.8557 | 2.1989 | 2.1989 | 2.1989 | 2.1989
2024-02-27 05:00 | 1.7338 | 2.1568 | 2.6058 | 2.6657 | 2.7255 | 2023-12-28 05:00 | 2.1339 | 2.5285 | 2.5285 | 2.5285 | 2.5285
2024-02-27 06:00 | 1.9243 | 2.3938 | 2.8921 | 2.9586 | 3.025 | 2023-12-28 06:00 | 2.2215 | 2.6323 | 2.6323 | 2.6323 | 2.6323
2024-02-27 07:00 | 2.3435 | 2.9152 | 3.5221 | 3.603 | 3.684 | 2023-12-28 07:00 | 2.2634 | 2.682 | 2.682 | 2.682 | 2.682
2024-02-27 08:00 | 2.3816 | 2.9626 | 3.5794 | 3.6616 | 3.7439 | 2023-12-28 08:00 | 2.012 | 2.384 | 2.384 | 2.384 | 2.384
2024-02-27 09:00 | 2.2291 | 2.773 | 3.3503 | 3.4273 | 3.5043 | 2023-12-28 09:00 | 2.3587 | 2.7949 | 2.7949 | 2.7949 | 2.7949
2024-02-27 10:00 | 2.3435 | 2.9152 | 3.5221 | 3.603 | 3.684 | 2023-12-28 10:00 | 2.9227 | 3.4631 | 3.4631 | 3.4631 | 3.4631
2024-02-27 11:00 | 2.2291 | 2.773 | 3.3503 | 3.4273 | 3.5043 | 2023-12-28 11:00 | 3.4371 | 4.0727 | 4.0727 | 4.0727 | 4.0727
2024-02-27 12:00 | 2.0386 | 2.536 | 3.064 | 3.1344 | 3.2047 | 2023-12-28 12:00 | 3.6314 | 4.3029 | 4.3029 | 4.3029 | 4.3029
2024-02-27 13:00 | 2.3435 | 2.9152 | 3.5221 | 3.603 | 3.684 | 2023-12-28 13:00 | 3.8943 | 4.6145 | 4.6145 | 4.6145 | 4.6145
2024-02-27 14:00 | 2.4387 | 3.0337 | 3.6653 | 3.7495 | 3.8337 | 2023-12-28 14:00 | 3.7419 | 4.4339 | 4.4339 | 4.4339 | 4.4339
2024-02-27 15:00 | 2.4768 | 3.0811 | 3.7226 | 3.8081 | 3.8936 | 2023-12-28 15:00 | 3.5552 | 4.2126 | 4.2126 | 4.2126 | 4.2126
2024-02-27 16:00 | 2.2863 | 2.8441 | 3.4362 | 3.5152 | 3.5941 | 2023-12-28 16:00 | 3.5933 | 4.2578 | 4.2578 | 4.2578 | 4.2578
2024-02-27 17:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2023-12-28 17:00 | 3.4599 | 4.0997 | 4.0997 | 4.0997 | 4.0997
2024-02-27 18:00 | 2.1339 | 2.6545 | 3.2071 | 3.2808 | 3.3545 | 2023-12-28 18:00 | 3.0484 | 3.6121 | 3.6121 | 3.6121 | 3.6121
2024-02-27 19:00 | 1.9243 | 2.3938 | 2.8921 | 2.9586 | 3.025 | 2023-12-28 19:00 | 2.6521 | 3.1425 | 3.1425 | 3.1425 | 3.1425
2024-02-27 20:00 | 1.7338 | 2.1568 | 2.6058 | 2.6657 | 2.7255 | 2023-12-28 20:00 | 2.5073 | 2.971 | 2.971 | 2.971 | 2.971
2024-02-27 21:00 | 1.7147 | 2.1331 | 2.5772 | 2.6364 | 2.6956 | 2023-12-28 21:00 | 2.2215 | 2.6323 | 2.6323 | 2.6323 | 2.6323
2024-02-27 22:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2023-12-28 22:00 | 1.951 | 2.3118 | 2.3118 | 2.3118 | 2.3118
2024-02-27 23:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2023-12-28 23:00 | 1.8252 | 2.1628 | 2.1628 | 2.1628 | 2.1628
2024-02-28 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2023-12-29 | 1.6766 | 1.9867 | 1.9867 | 1.9867 | 1.9867
2024-02-28 01:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2023-12-29 01:00 | 1.6195 | 1.9189 | 1.9189 | 1.9189 | 1.9189
2024-02-28 02:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2023-12-29 02:00 | 1.6804 | 1.9912 | 1.9912 | 1.9912 | 1.9912
2024-02-28 03:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2023-12-29 03:00 | 1.8329 | 2.1718 | 2.1718 | 2.1718 | 2.1718
2024-02-28 04:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2023-12-29 04:00 | 2.0501 | 2.4291 | 2.4291 | 2.4291 | 2.4291
2024-02-28 05:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2023-12-29 05:00 | 2.1987 | 2.6052 | 2.6052 | 2.6052 | 2.6052
2024-02-28 06:00 | 2.0577 | 2.5597 | 3.0926 | 3.1636 | 3.2347 | 2023-12-29 06:00 | 2.1377 | 2.533 | 2.533 | 2.533 | 2.533
2024-02-28 07:00 | 2.191 | 2.7256 | 3.293 | 3.3687 | 3.4444 | 2023-12-29 07:00 | 2.5226 | 2.989 | 2.989 | 2.989 | 2.989
2024-02-28 08:00 | 2.4578 | 3.0574 | 3.6939 | 3.7788 | 3.8637 | 2023-12-29 08:00 | 2.8007 | 3.3186 | 3.3186 | 3.3186 | 3.3186
2024-02-28 09:00 | 1.3908 | 1.7302 | 2.0904 | 2.1384 | 2.1864 | 2023-12-29 09:00 | 3.0522 | 3.6166 | 3.6166 | 3.6166 | 3.6166
2024-02-28 10:00 | 1.81 | 2.2516 | 2.7203 | 2.7828 | 2.8453 | 2023-12-29 10:00 | 3.0179 | 3.576 | 3.576 | 3.576 | 3.576
2024-02-28 11:00 | 2.3244 | 2.8915 | 3.4935 | 3.5737 | 3.654 | 2023-12-29 11:00 | 3.479 | 4.1223 | 4.1223 | 4.1223 | 4.1223
2024-02-28 12:00 | 2.534 | 3.1522 | 3.8085 | 3.896 | 3.9835 | 2023-12-29 12:00 | 3.479 | 4.1223 | 4.1223 | 4.1223 | 4.1223
2024-02-28 13:00 | 2.534 | 3.1522 | 3.8085 | 3.896 | 3.9835 | 2023-12-29 13:00 | 3.5133 | 4.163 | 4.163 | 4.163 | 4.163
2024-02-28 14:00 | 2.8579 | 3.5551 | 4.2953 | 4.3939 | 4.4926 | 2023-12-29 14:00 | 3.2732 | 3.8785 | 3.8785 | 3.8785 | 3.8785
2024-02-28 15:00 | 2.7436 | 3.4129 | 4.1235 | 4.2182 | 4.3129 | 2023-12-29 15:00 | 3.2199 | 3.8153 | 3.8153 | 3.8153 | 3.8153
2024-02-28 16:00 | 3.2389 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2023-12-29 16:00 | 3.3151 | 3.9282 | 3.9282 | 3.9282 | 3.9282
2024-02-28 17:00 | 2.9531 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2023-12-29 17:00 | 3.1094 | 3.6844 | 3.6844 | 3.6844 | 3.6844
2024-02-28 18:00 | 2.553 | 3.1759 | 3.8371 | 3.9253 | 4.0134 | 2023-12-29 18:00 | 2.6369 | 3.1245 | 3.1245 | 3.1245 | 3.1245
2024-02-28 19:00 | 2.3435 | 2.9152 | 3.5221 | 3.603 | 3.684 | 2023-12-29 19:00 | 2.7779 | 3.2915 | 3.2915 | 3.2915 | 3.2915
2024-02-28 20:00 | 1.9815 | 2.4649 | 2.9781 | 3.0465 | 3.1149 | 2023-12-29 20:00 | 2.6674 | 3.1606 | 3.1606 | 3.1606 | 3.1606
2024-02-28 21:00 | 1.8862 | 2.3464 | 2.8349 | 2.9 | 2.9651 | 2023-12-29 21:00 | 2.2406 | 2.6549 | 2.6549 | 2.6549 | 2.6549
2024-02-28 22:00 | 1.8862 | 2.3464 | 2.8349 | 2.9 | 2.9651 | 2023-12-29 22:00 | 1.871 | 2.2169 | 2.2169 | 2.2169 | 2.2169
2024-02-28 23:00 | 1.81 | 2.2516 | 2.7203 | 2.7828 | 2.8453 | 2023-12-29 23:00 | 1.9396 | 2.2982 | 2.2982 | 2.2982 | 2.2982
2024-02-29 | 1.7338 | 2.1568 | 2.6058 | 2.6657 | 2.7255 | 2023-12-30 | 1.6576 | 1.9641 | 1.9641 | 1.9641 | 1.9641
2024-02-29 01:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2023-12-30 01:00 | 1.7909 | 2.1221 | 2.1221 | 2.1221 | 2.1221
2024-02-29 02:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2023-12-30 02:00 | 1.749 | 2.0724 | 2.0724 | 2.0724 | 2.0724
2024-02-29 03:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2023-12-30 03:00 | 1.7757 | 2.1041 | 2.1041 | 2.1041 | 2.1041
2024-02-29 04:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2023-12-30 04:00 | 1.9205 | 2.2756 | 2.2756 | 2.2756 | 2.2756
2024-02-29 05:00 | 1.7528 | 2.1805 | 2.6344 | 2.695 | 2.7555 | 2023-12-30 05:00 | 2.0843 | 2.4698 | 2.4698 | 2.4698 | 2.4698
2024-02-29 06:00 | 1.9624 | 2.4412 | 2.9494 | 3.0172 | 3.0849 | 2023-12-30 06:00 | 2.0234 | 2.3975 | 2.3975 | 2.3975 | 2.3975
2024-02-29 07:00 | 2.3054 | 2.8678 | 3.4648 | 3.5445 | 3.6241 | 2023-12-30 07:00 | 1.89 | 2.2395 | 2.2395 | 2.2395 | 2.2395
2024-02-29 08:00 | 2.915 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2023-12-30 08:00 | 2.0234 | 2.3975 | 2.3975 | 2.3975 | 2.3975
2024-02-29 09:00 | 3.1246 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2023-12-30 09:00 | 1.9472 | 2.3072 | 2.3072 | 2.3072 | 2.3072
2024-02-29 10:00 | 3.0103 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2023-12-30 10:00 | 2.3778 | 2.8174 | 2.8174 | 2.8174 | 2.8174
2024-02-29 11:00 | 2.9341 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2023-12-30 11:00 | 2.4311 | 2.8807 | 2.8807 | 2.8807 | 2.8807
2024-02-29 12:00 | 3.2199 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2023-12-30 12:00 | 2.3168 | 2.7452 | 2.7452 | 2.7452 | 2.7452
2024-02-29 13:00 | 3.0484 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2023-12-30 13:00 | 2.5988 | 3.0793 | 3.0793 | 3.0793 | 3.0793
2024-02-29 14:00 | 3.0294 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2023-12-30 14:00 | 2.6445 | 3.1335 | 3.1335 | 3.1335 | 3.1335
2024-02-29 15:00 | 3.0865 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2023-12-30 15:00 | 2.6293 | 3.1154 | 3.1154 | 3.1154 | 3.1154
2024-02-29 16:00 | 2.9341 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2023-12-30 16:00 | 2.7055 | 3.2057 | 3.2057 | 3.2057 | 3.2057
2024-02-29 17:00 | 2.7055 | 3.3655 | 4.0662 | 4.1596 | 4.253 | 2023-12-30 17:00 | 2.7512 | 3.2599 | 3.2599 | 3.2599 | 3.2599
2024-02-29 18:00 | 2.6102 | 3.247 | 3.923 | 4.0131 | 4.1033 | 2023-12-30 18:00 | 2.534 | 3.0026 | 3.0026 | 3.0026 | 3.0026
2024-02-29 19:00 | 2.2482 | 2.7967 | 3.3789 | 3.4566 | 3.5342 | 2023-12-30 19:00 | 2.252 | 2.6684 | 2.6684 | 2.6684 | 2.6684
2024-02-29 20:00 | 1.9624 | 2.4412 | 2.9494 | 3.0172 | 3.0849 | 2023-12-30 20:00 | 2.0691 | 2.4517 | 2.4517 | 2.4517 | 2.4517
2024-02-29 21:00 | 1.9624 | 2.4412 | 2.9494 | 3.0172 | 3.0849 | 2023-12-30 21:00 | 2.2673 | 2.6865 | 2.6865 | 2.6865 | 2.6865
2024-02-29 22:00 | 1.9434 | 2.4175 | 2.9208 | 2.9879 | 3.055 | 2023-12-30 22:00 | 1.9472 | 2.3072 | 2.3072 | 2.3072 | 2.3072
2024-02-29 23:00 | 1.8481 | 2.299 | 2.7776 | 2.8414 | 2.9052 | 2023-12-30 23:00 | 1.7224 | 2.0408 | 2.0408 | 2.0408 | 2.0408
2024-03-01 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2023-12-31 | 1.669 | 1.9776 | 1.9776 | 1.9776 | 1.9776
2024-03-01 01:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2023-12-31 01:00 | 1.6766 | 1.9867 | 1.9867 | 1.9867 | 1.9867
2024-03-01 02:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2023-12-31 02:00 | 1.7033 | 2.0183 | 2.0183 | 2.0183 | 2.0183
2024-03-01 03:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2023-12-31 03:00 | 1.8938 | 2.244 | 2.244 | 2.244 | 2.244
2024-03-01 04:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2023-12-31 04:00 | 2.0043 | 2.375 | 2.375 | 2.375 | 2.375
2024-03-01 05:00 | 1.7719 | 2.2042 | 2.6631 | 2.7242 | 2.7854 | 2023-12-31 05:00 | 2.0729 | 2.4562 | 2.4562 | 2.4562 | 2.4562
2024-03-01 06:00 | 2.1148 | 2.6308 | 3.1785 | 3.2515 | 3.3245 | 2023-12-31 06:00 | 2.0272 | 2.4021 | 2.4021 | 2.4021 | 2.4021
2024-03-01 07:00 | 2.3625 | 2.9389 | 3.5508 | 3.6323 | 3.7139 | 2023-12-31 07:00 | 2.2215 | 2.6323 | 2.6323 | 2.6323 | 2.6323
2024-03-01 08:00 | 2.1529 | 2.6782 | 3.2358 | 3.3101 | 3.3845 | 2023-12-31 08:00 | 2.5378 | 3.0071 | 3.0071 | 3.0071 | 3.0071
2024-03-01 09:00 | 2.0577 | 2.5597 | 3.0926 | 3.1636 | 3.2347 | 2023-12-31 09:00 | 2.595 | 3.0748 | 3.0748 | 3.0748 | 3.0748
2024-03-01 10:00 | 2.4006 | 2.9863 | 3.608 | 3.6909 | 3.7738 | 2023-12-31 10:00 | 2.7245 | 3.2283 | 3.2283 | 3.2283 | 3.2283
2024-03-01 11:00 | 2.5149 | 3.1285 | 3.7798 | 3.8667 | 3.9535 | 2023-12-31 11:00 | 2.6864 | 3.1832 | 3.1832 | 3.1832 | 3.1832
2024-03-01 12:00 | 2.8007 | 3.484 | 4.2094 | 4.3061 | 4.4028 | 2023-12-31 12:00 | 3.0637 | 3.6302 | 3.6302 | 3.6302 | 3.6302
2024-03-01 13:00 | 2.8198 | 3.5077 | 4.238 | 4.3354 | 4.4327 | 2023-12-31 13:00 | 2.7588 | 3.269 | 3.269 | 3.269 | 3.269
2024-03-01 14:00 | 3.0294 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2023-12-31 14:00 | 2.534 | 3.0026 | 3.0026 | 3.0026 | 3.0026
2024-03-01 15:00 | 3.0675 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2023-12-31 15:00 | 2.6978 | 3.1967 | 3.1967 | 3.1967 | 3.1967
2024-03-01 16:00 | 2.8007 | 3.484 | 4.2094 | 4.3061 | 4.4028 | 2023-12-31 16:00 | 2.4768 | 2.9348 | 2.9348 | 2.9348 | 2.9348
2024-03-01 17:00 | 2.6293 | 3.2707 | 3.9516 | 4.0424 | 4.1332 | 2023-12-31 17:00 | 2.2749 | 2.6955 | 2.6955 | 2.6955 | 2.6955
2024-03-01 18:00 | 2.1339 | 2.6545 | 3.2071 | 3.2808 | 3.3545 | 2023-12-31 18:00 | 2.0424 | 2.4201 | 2.4201 | 2.4201 | 2.4201
2024-03-01 19:00 | 1.9815 | 2.4649 | 2.9781 | 3.0465 | 3.1149 | 2023-12-31 19:00 | 1.8862 | 2.235 | 2.235 | 2.235 | 2.235
2024-03-01 20:00 | 1.9053 | 2.3701 | 2.8635 | 2.9293 | 2.9951 | 2023-12-31 20:00 | 1.9091 | 2.2621 | 2.2621 | 2.2621 | 2.2621
2024-03-01 21:00 | 1.7719 | 2.2042 | 2.6631 | 2.7242 | 2.7854 | 2023-12-31 21:00 | 1.9548 | 2.3163 | 2.3163 | 2.3163 | 2.3163
2024-03-01 22:00 | 1.7719 | 2.2042 | 2.6631 | 2.7242 | 2.7854 | 2023-12-31 22:00 | 1.7185 | 2.0363 | 2.0363 | 2.0363 | 2.0363
2024-03-01 23:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2023-12-31 23:00 | 1.6538 | 1.9596 | 1.9596 | 1.9596 | 1.9596
2024-03-02 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2024-01-01 | 1.5318 | 1.8151 | 1.8151 | 1.8151 | 1.8151
2024-03-02 01:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2024-01-01 01:00 | 1.5356 | 1.8196 | 1.8196 | 1.8196 | 1.8196
2024-03-02 02:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-01-01 02:00 | 1.5242 | 1.8061 | 1.8061 | 1.8061 | 1.8061
2024-03-02 03:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-01-01 03:00 | 1.6347 | 1.937 | 1.937 | 1.937 | 1.937
2024-03-02 04:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-01-01 04:00 | 1.7033 | 2.0183 | 2.0183 | 2.0183 | 2.0183
2024-03-02 05:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2024-01-01 05:00 | 1.8595 | 2.2034 | 2.2034 | 2.2034 | 2.2034
2024-03-02 06:00 | 1.6957 | 2.1094 | 2.5485 | 2.6071 | 2.6656 | 2024-01-01 06:00 | 1.8405 | 2.1808 | 2.1808 | 2.1808 | 2.1808
2024-03-02 07:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2024-01-01 07:00 | 2.0539 | 2.4337 | 2.4337 | 2.4337 | 2.4337
2024-03-02 08:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2024-01-01 08:00 | 2.0767 | 2.4608 | 2.4608 | 2.4608 | 2.4608
2024-03-02 09:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-01-01 09:00 | 2.2901 | 2.7136 | 2.7136 | 2.7136 | 2.7136
2024-03-02 10:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2024-01-01 10:00 | 2.2787 | 2.7001 | 2.7001 | 2.7001 | 2.7001
2024-03-02 11:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2024-01-01 11:00 | 2.5797 | 3.0567 | 3.0567 | 3.0567 | 3.0567
2024-03-02 12:00 | 1.3908 | 1.7302 | 2.0904 | 2.1384 | 2.1864 | 2024-01-01 12:00 | 2.3511 | 2.7858 | 2.7858 | 2.7858 | 2.7858
2024-03-02 13:00 | 0.51442 | 0.63992 | 0.77315 | 0.79091 | 0.80867 | 2024-01-01 13:00 | 2.252 | 2.6684 | 2.6684 | 2.6684 | 2.6684
2024-03-02 14:00 | 0.68589 | 0.85323 | 1.0309 | 1.0545 | 1.0782 | 2024-01-01 14:00 | 2.2177 | 2.6278 | 2.6278 | 2.6278 | 2.6278
2024-03-02 15:00 | 0.724 | 0.90063 | 1.0881 | 1.1131 | 1.1381 | 2024-01-01 15:00 | 2.6826 | 3.1787 | 3.1787 | 3.1787 | 3.1787
2024-03-02 16:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2024-01-01 16:00 | 2.7702 | 3.2825 | 3.2825 | 3.2825 | 3.2825
2024-03-02 17:00 | 0.53347 | 0.66362 | 0.80178 | 0.8202 | 0.83862 | 2024-01-01 17:00 | 2.7359 | 3.2419 | 3.2419 | 3.2419 | 3.2419
2024-03-02 18:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-01-01 18:00 | 2.3435 | 2.7768 | 2.7768 | 2.7768 | 2.7768
2024-03-02 19:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2024-01-01 19:00 | 2.2406 | 2.6549 | 2.6549 | 2.6549 | 2.6549
2024-03-02 20:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2024-01-01 20:00 | 2.0539 | 2.4337 | 2.4337 | 2.4337 | 2.4337
2024-03-02 21:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2024-01-01 21:00 | 2.0501 | 2.4291 | 2.4291 | 2.4291 | 2.4291
2024-03-02 22:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2024-01-01 22:00 | 1.8672 | 2.2124 | 2.2124 | 2.2124 | 2.2124
2024-03-02 23:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2024-01-01 23:00 | 1.7643 | 2.0905 | 2.0905 | 2.0905 | 2.0905
2024-03-03 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2024-01-02 | 1.6957 | 2.0092 | 2.0092 | 2.0092 | 2.0092
2024-03-03 01:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-01-02 01:00 | 1.7033 | 2.0183 | 2.0183 | 2.0183 | 2.0183
2024-03-03 02:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2024-01-02 02:00 | 1.6309 | 1.9325 | 1.9325 | 1.9325 | 1.9325
2024-03-03 03:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-01-02 03:00 | 1.749 | 2.0724 | 2.0724 | 2.0724 | 2.0724
2024-03-03 04:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-01-02 04:00 | 1.8557 | 2.1989 | 2.1989 | 2.1989 | 2.1989
2024-03-03 05:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-01-02 05:00 | 2.1567 | 2.5556 | 2.5556 | 2.5556 | 2.5556
2024-03-03 06:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2024-01-02 06:00 | 2.3739 | 2.8129 | 2.8129 | 2.8129 | 2.8129
2024-03-03 07:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-01-02 07:00 | 2.6064 | 3.0884 | 3.0884 | 3.0884 | 3.0884
2024-03-03 08:00 | 0.87642 | 1.0902 | 1.3172 | 1.3475 | 1.3777 | 2024-01-02 08:00 | 3.197 | 3.7882 | 3.7882 | 3.7882 | 3.7882
2024-03-03 09:00 | 0.095263 | 0.1185 | 0.14318 | 0.14646 | 0.14975 | 2024-01-02 09:00 | 3.4561 | 4.0952 | 4.0952 | 4.0952 | 4.0952
2024-03-03 10:00 | 0.17708 | 0.22028 | 0.26614 | 0.27225 | 0.27837 | 2024-01-02 10:00 | 3.1399 | 3.7205 | 3.7205 | 3.7205 | 3.7205
2024-03-03 11:00 | 0.7621 | 0.94804 | 1.1454 | 1.1717 | 1.198 | 2024-01-02 11:00 | 3.0027 | 3.5579 | 3.5579 | 3.5579 | 3.5579
2024-03-03 12:00 | 0.26793 | 0.33329 | 0.40268 | 0.41193 | 0.42118 | 2024-01-02 12:00 | 3.2923 | 3.9011 | 3.9011 | 3.9011 | 3.9011
2024-03-03 13:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-01-02 13:00 | 4.0201 | 4.7635 | 4.7635 | 4.7635 | 4.7635
2024-03-03 14:00 | 0.41916 | 0.52142 | 0.62997 | 0.64445 | 0.65892 | 2024-01-02 14:00 | 3.6543 | 4.33 | 4.33 | 4.33 | 4.33
2024-03-03 15:00 | 0.095263 | 0.1185 | 0.14318 | 0.14646 | 0.14975 | 2024-01-02 15:00 | 3.8982 | 4.619 | 4.619 | 4.619 | 4.619
2024-03-03 16:00 | 0.66684 | 0.82953 | 1.0022 | 1.0253 | 1.0483 | 2024-01-02 16:00 | 3.6124 | 4.2804 | 4.2804 | 4.2804 | 4.2804
2024-03-03 17:00 | 1.2956 | 1.6117 | 1.9472 | 1.9919 | 2.0367 | 2024-01-02 17:00 | 3.5019 | 4.1494 | 4.1494 | 4.1494 | 4.1494
2024-03-03 18:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2024-01-02 18:00 | 3.2046 | 3.7972 | 3.7972 | 3.7972 | 3.7972
2024-03-03 19:00 | 1.6957 | 2.1094 | 2.5485 | 2.6071 | 2.6656 | 2024-01-02 19:00 | 2.6826 | 3.1787 | 3.1787 | 3.1787 | 3.1787
2024-03-03 20:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2024-01-02 20:00 | 2.3358 | 2.7678 | 2.7678 | 2.7678 | 2.7678
2024-03-03 21:00 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2024-01-02 21:00 | 2.2406 | 2.6549 | 2.6549 | 2.6549 | 2.6549
2024-03-03 22:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-01-02 22:00 | 2.1377 | 2.533 | 2.533 | 2.533 | 2.533
2024-03-03 23:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2024-01-02 23:00 | 1.7681 | 2.095 | 2.095 | 2.095 | 2.095
2024-03-04 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-01-03 | 1.7643 | 2.0905 | 2.0905 | 2.0905 | 2.0905
2024-03-04 01:00 | 1.4289 | 1.7776 | 2.1476 | 2.197 | 2.2463 | 2024-01-03 01:00 | 1.6652 | 1.9731 | 1.9731 | 1.9731 | 1.9731
2024-03-04 02:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-01-03 02:00 | 1.6233 | 1.9234 | 1.9234 | 1.9234 | 1.9234
2024-03-04 03:00 | 1.4289 | 1.7776 | 2.1476 | 2.197 | 2.2463 | 2024-01-03 03:00 | 1.8443 | 2.1853 | 2.1853 | 2.1853 | 2.1853
2024-03-04 04:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-01-03 04:00 | 1.8824 | 2.2305 | 2.2305 | 2.2305 | 2.2305
2024-03-04 05:00 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2024-01-03 05:00 | 2.3244 | 2.7542 | 2.7542 | 2.7542 | 2.7542
2024-03-04 06:00 | 1.9243 | 2.3938 | 2.8921 | 2.9586 | 3.025 | 2024-01-03 06:00 | 2.5911 | 3.0703 | 3.0703 | 3.0703 | 3.0703
2024-03-04 07:00 | 1.9434 | 2.4175 | 2.9208 | 2.9879 | 3.055 | 2024-01-03 07:00 | 2.835 | 3.3593 | 3.3593 | 3.3593 | 3.3593
2024-03-04 08:00 | 0.85737 | 1.0665 | 1.2886 | 1.3182 | 1.3478 | 2024-01-03 08:00 | 3.3494 | 3.9688 | 3.9688 | 3.9688 | 3.9688
2024-03-04 09:00 | 0.45726 | 0.56882 | 0.68724 | 0.70303 | 0.71882 | 2024-01-03 09:00 | 3.4257 | 4.0591 | 4.0591 | 4.0591 | 4.0591
2024-03-04 10:00 | 0.64779 | 0.80583 | 0.97359 | 0.99596 | 1.0183 | 2024-01-03 10:00 | 3.8715 | 4.5874 | 4.5874 | 4.5874 | 4.5874
2024-03-04 11:00 | 0.85737 | 1.0665 | 1.2886 | 1.3182 | 1.3478 | 2024-01-03 11:00 | 3.9591 | 4.6912 | 4.6912 | 4.6912 | 4.6912
2024-03-04 12:00 | 0.87642 | 1.0902 | 1.3172 | 1.3475 | 1.3777 | 2024-01-03 12:00 | 3.8829 | 4.6009 | 4.6009 | 4.6009 | 4.6009
2024-03-04 13:00 | 0.93358 | 1.1613 | 1.4031 | 1.4354 | 1.4676 | 2024-01-03 13:00 | 3.8715 | 4.5874 | 4.5874 | 4.5874 | 4.5874
2024-03-04 14:00 | 0.95263 | 1.185 | 1.4318 | 1.4646 | 1.4975 | 2024-01-03 14:00 | 4.0353 | 4.7815 | 4.7815 | 4.7815 | 4.7815
2024-03-04 15:00 | 1.0288 | 1.2798 | 1.5463 | 1.5818 | 1.6173 | 2024-01-03 15:00 | 4.3173 | 5.1157 | 5.1157 | 5.1157 | 5.1157
2024-03-04 16:00 | 0.93358 | 1.1613 | 1.4031 | 1.4354 | 1.4676 | 2024-01-03 16:00 | 4.3097 | 5.1066 | 5.1066 | 5.1066 | 5.1066
2024-03-04 17:00 | 0.89547 | 1.1139 | 1.3458 | 1.3768 | 1.4077 | 2024-01-03 17:00 | 3.8067 | 4.5106 | 4.5106 | 4.5106 | 4.5106
2024-03-04 18:00 | 1.7909 | 2.2279 | 2.6917 | 2.7535 | 2.8154 | 2024-01-03 18:00 | 3.2961 | 3.9056 | 3.9056 | 3.9056 | 3.9056
2024-03-04 19:00 | 1.7147 | 2.1331 | 2.5772 | 2.6364 | 2.6956 | 2024-01-03 19:00 | 2.915 | 3.4541 | 3.4541 | 3.4541 | 3.4541
2024-03-04 20:00 | 1.7338 | 2.1568 | 2.6058 | 2.6657 | 2.7255 | 2024-01-03 20:00 | 2.6369 | 3.1245 | 3.1245 | 3.1245 | 3.1245
2024-03-04 21:00 | 1.6957 | 2.1094 | 2.5485 | 2.6071 | 2.6656 | 2024-01-03 21:00 | 2.3282 | 2.7587 | 2.7587 | 2.7587 | 2.7587
2024-03-04 22:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2024-01-03 22:00 | 1.9738 | 2.3388 | 2.3388 | 2.3388 | 2.3388
2024-03-04 23:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2024-01-03 23:00 | 1.9053 | 2.2576 | 2.2576 | 2.2576 | 2.2576
2024-03-05 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-01-04 | 1.6614 | 1.9686 | 1.9686 | 1.9686 | 1.9686
2024-03-05 01:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-01-04 01:00 | 1.6995 | 2.0138 | 2.0138 | 2.0138 | 2.0138
2024-03-05 02:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-01-04 02:00 | 1.6842 | 1.9957 | 1.9957 | 1.9957 | 1.9957
2024-03-05 03:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-01-04 03:00 | 1.8252 | 2.1628 | 2.1628 | 2.1628 | 2.1628
2024-03-05 04:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-01-04 04:00 | 1.8481 | 2.1898 | 2.1898 | 2.1898 | 2.1898
2024-03-05 05:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2024-01-04 05:00 | 2.2596 | 2.6775 | 2.6775 | 2.6775 | 2.6775
2024-03-05 06:00 | 1.7338 | 2.1568 | 2.6058 | 2.6657 | 2.7255 | 2024-01-04 06:00 | 2.4502 | 2.9032 | 2.9032 | 2.9032 | 2.9032
2024-03-05 07:00 | 2.0577 | 2.5597 | 3.0926 | 3.1636 | 3.2347 | 2024-01-04 07:00 | 2.8007 | 3.3186 | 3.3186 | 3.3186 | 3.3186
2024-03-05 08:00 | 1.4099 | 1.7539 | 2.119 | 2.1677 | 2.2164 | 2024-01-04 08:00 | 3.3571 | 3.9778 | 3.9778 | 3.9778 | 3.9778
2024-03-05 09:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2024-01-04 09:00 | 3.5362 | 4.19 | 4.19 | 4.19 | 4.19
2024-03-05 10:00 | 0.93358 | 1.1613 | 1.4031 | 1.4354 | 1.4676 | 2024-01-04 10:00 | 4.0811 | 4.8357 | 4.8357 | 4.8357 | 4.8357
2024-03-05 11:00 | 0.60968 | 0.75843 | 0.91632 | 0.93738 | 0.95843 | 2024-01-04 11:00 | 4.1535 | 4.9215 | 4.9215 | 4.9215 | 4.9215
2024-03-05 12:00 | 1.0098 | 1.2561 | 1.5177 | 1.5525 | 1.5874 | 2024-01-04 12:00 | 4.1192 | 4.8809 | 4.8809 | 4.8809 | 4.8809
2024-03-05 13:00 | 1.0098 | 1.2561 | 1.5177 | 1.5525 | 1.5874 | 2024-01-04 13:00 | 4.1306 | 4.8944 | 4.8944 | 4.8944 | 4.8944
2024-03-05 14:00 | 1.1241 | 1.3984 | 1.6895 | 1.7283 | 1.7671 | 2024-01-04 14:00 | 3.4371 | 4.0727 | 4.0727 | 4.0727 | 4.0727
2024-03-05 15:00 | 1.1813 | 1.4695 | 1.7754 | 1.8162 | 1.857 | 2024-01-04 15:00 | 3.9172 | 4.6416 | 4.6416 | 4.6416 | 4.6416
2024-03-05 16:00 | 1.3337 | 1.6591 | 2.0045 | 2.0505 | 2.0966 | 2024-01-04 16:00 | 4.1954 | 4.9712 | 4.9712 | 4.9712 | 4.9712
2024-03-05 17:00 | 1.6957 | 2.1094 | 2.5485 | 2.6071 | 2.6656 | 2024-01-04 17:00 | 3.761 | 4.4564 | 4.4564 | 4.4564 | 4.4564
2024-03-05 18:00 | 2.0386 | 2.536 | 3.064 | 3.1344 | 3.2047 | 2024-01-04 18:00 | 3.2123 | 3.8063 | 3.8063 | 3.8063 | 3.8063
2024-03-05 19:00 | 1.9624 | 2.4412 | 2.9494 | 3.0172 | 3.0849 | 2024-01-04 19:00 | 2.7131 | 3.2148 | 3.2148 | 3.2148 | 3.2148
2024-03-05 20:00 | 1.7719 | 2.2042 | 2.6631 | 2.7242 | 2.7854 | 2024-01-04 20:00 | 2.4425 | 2.8942 | 2.8942 | 2.8942 | 2.8942
2024-03-05 21:00 | 1.6957 | 2.1094 | 2.5485 | 2.6071 | 2.6656 | 2024-01-04 21:00 | 2.6178 | 3.1019 | 3.1019 | 3.1019 | 3.1019
2024-03-05 22:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2024-01-04 22:00 | 2.5111 | 2.9755 | 2.9755 | 2.9755 | 2.9755
2024-03-05 23:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2024-01-04 23:00 | 2.3663 | 2.8039 | 2.8039 | 2.8039 | 2.8039
2024-03-06 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2024-01-05 | 2.2063 | 2.6143 | 2.6143 | 2.6143 | 2.6143
2024-03-06 01:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-01-05 01:00 | 2.1949 | 2.6007 | 2.6007 | 2.6007 | 2.6007
2024-03-06 02:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-01-05 02:00 | 2.1682 | 2.5691 | 2.5691 | 2.5691 | 2.5691
2024-03-06 03:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-01-05 03:00 | 2.3854 | 2.8265 | 2.8265 | 2.8265 | 2.8265
2024-03-06 04:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2024-01-05 04:00 | 2.4654 | 2.9213 | 2.9213 | 2.9213 | 2.9213
2024-03-06 05:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2024-01-05 05:00 | 2.8083 | 3.3277 | 3.3277 | 3.3277 | 3.3277
2024-03-06 06:00 | 1.8481 | 2.299 | 2.7776 | 2.8414 | 2.9052 | 2024-01-05 06:00 | 2.6674 | 3.1606 | 3.1606 | 3.1606 | 3.1606
2024-03-06 07:00 | 1.9624 | 2.4412 | 2.9494 | 3.0172 | 3.0849 | 2024-01-05 07:00 | 2.6445 | 3.1335 | 3.1335 | 3.1335 | 3.1335
2024-03-06 08:00 | 2.3625 | 2.9389 | 3.5508 | 3.6323 | 3.7139 | 2024-01-05 08:00 | 3.5781 | 4.2397 | 4.2397 | 4.2397 | 4.2397
2024-03-06 09:00 | 2.0767 | 2.5834 | 3.1212 | 3.1929 | 3.2646 | 2024-01-05 09:00 | 3.681 | 4.3616 | 4.3616 | 4.3616 | 4.3616
2024-03-06 10:00 | 1.7528 | 2.1805 | 2.6344 | 2.695 | 2.7555 | 2024-01-05 10:00 | 3.2466 | 3.8469 | 3.8469 | 3.8469 | 3.8469
2024-03-06 11:00 | 1.829 | 2.2753 | 2.749 | 2.8121 | 2.8753 | 2024-01-05 11:00 | 2.9951 | 3.5489 | 3.5489 | 3.5489 | 3.5489
2024-03-06 12:00 | 1.9053 | 2.3701 | 2.8635 | 2.9293 | 2.9951 | 2024-01-05 12:00 | 3.3533 | 3.9733 | 3.9733 | 3.9733 | 3.9733
2024-03-06 13:00 | 2.7055 | 3.3655 | 4.0662 | 4.1596 | 4.253 | 2024-01-05 13:00 | 3.4866 | 4.1314 | 4.1314 | 4.1314 | 4.1314
2024-03-06 14:00 | 2.3054 | 2.8678 | 3.4648 | 3.5445 | 3.6241 | 2024-01-05 14:00 | 3.3533 | 3.9733 | 3.9733 | 3.9733 | 3.9733
2024-03-06 15:00 | 2.6483 | 3.2944 | 3.9803 | 4.0717 | 4.1632 | 2024-01-05 15:00 | 3.5514 | 4.2081 | 4.2081 | 4.2081 | 4.2081
2024-03-06 16:00 | 2.553 | 3.1759 | 3.8371 | 3.9253 | 4.0134 | 2024-01-05 16:00 | 3.3952 | 4.023 | 4.023 | 4.023 | 4.023
2024-03-06 17:00 | 2.4768 | 3.0811 | 3.7226 | 3.8081 | 3.8936 | 2024-01-05 17:00 | 3.3761 | 4.0004 | 4.0004 | 4.0004 | 4.0004
2024-03-06 18:00 | 2.0958 | 2.6071 | 3.1499 | 3.2222 | 3.2946 | 2024-01-05 18:00 | 3.3151 | 3.9282 | 3.9282 | 3.9282 | 3.9282
2024-03-06 19:00 | 1.81 | 2.2516 | 2.7203 | 2.7828 | 2.8453 | 2024-01-05 19:00 | 2.8998 | 3.436 | 3.436 | 3.436 | 3.436
2024-03-06 20:00 | 1.81 | 2.2516 | 2.7203 | 2.7828 | 2.8453 | 2024-01-05 20:00 | 2.534 | 3.0026 | 3.0026 | 3.0026 | 3.0026
2024-03-06 21:00 | 1.7528 | 2.1805 | 2.6344 | 2.695 | 2.7555 | 2024-01-05 21:00 | 2.454 | 2.9077 | 2.9077 | 2.9077 | 2.9077
2024-03-06 22:00 | 1.7338 | 2.1568 | 2.6058 | 2.6657 | 2.7255 | 2024-01-05 22:00 | 1.8595 | 2.2034 | 2.2034 | 2.2034 | 2.2034
2024-03-06 23:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2024-01-05 23:00 | 1.7643 | 2.0905 | 2.0905 | 2.0905 | 2.0905
2024-03-07 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2024-01-06 | 1.669 | 1.9776 | 1.9776 | 1.9776 | 1.9776
2024-03-07 01:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-01-06 01:00 | 1.5737 | 1.8648 | 1.8648 | 1.8648 | 1.8648
2024-03-07 02:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2024-01-06 02:00 | 1.5928 | 1.8873 | 1.8873 | 1.8873 | 1.8873
2024-03-07 03:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-01-06 03:00 | 1.7185 | 2.0363 | 2.0363 | 2.0363 | 2.0363
2024-03-07 04:00 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2024-01-06 04:00 | 1.8405 | 2.1808 | 2.1808 | 2.1808 | 2.1808
2024-03-07 05:00 | 1.6957 | 2.1094 | 2.5485 | 2.6071 | 2.6656 | 2024-01-06 05:00 | 2.2596 | 2.6775 | 2.6775 | 2.6775 | 2.6775
2024-03-07 06:00 | 2.0196 | 2.5123 | 3.0353 | 3.1051 | 3.1748 | 2024-01-06 06:00 | 2.0729 | 2.4562 | 2.4562 | 2.4562 | 2.4562
2024-03-07 07:00 | 2.0005 | 2.4886 | 3.0067 | 3.0758 | 3.1448 | 2024-01-06 07:00 | 2.0348 | 2.4111 | 2.4111 | 2.4111 | 2.4111
2024-03-07 08:00 | 1.3146 | 1.6354 | 1.9758 | 2.0212 | 2.0666 | 2024-01-06 08:00 | 2.5073 | 2.971 | 2.971 | 2.971 | 2.971
2024-03-07 09:00 | 1.105 | 1.3747 | 1.6608 | 1.699 | 1.7372 | 2024-01-06 09:00 | 2.4692 | 2.9258 | 2.9258 | 2.9258 | 2.9258
2024-03-07 10:00 | 1.3718 | 1.7065 | 2.0617 | 2.1091 | 2.1565 | 2024-01-06 10:00 | 2.3435 | 2.7768 | 2.7768 | 2.7768 | 2.7768
2024-03-07 11:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-01-06 11:00 | 2.313 | 2.7407 | 2.7407 | 2.7407 | 2.7407
2024-03-07 12:00 | 1.7528 | 2.1805 | 2.6344 | 2.695 | 2.7555 | 2024-01-06 12:00 | 2.553 | 3.0251 | 3.0251 | 3.0251 | 3.0251
2024-03-07 13:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2024-01-06 13:00 | 2.7474 | 3.2554 | 3.2554 | 3.2554 | 3.2554
2024-03-07 14:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2024-01-06 14:00 | 2.6293 | 3.1154 | 3.1154 | 3.1154 | 3.1154
2024-03-07 15:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2024-01-06 15:00 | 2.8769 | 3.4089 | 3.4089 | 3.4089 | 3.4089
2024-03-07 16:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2024-01-06 16:00 | 3.056 | 3.6211 | 3.6211 | 3.6211 | 3.6211
2024-03-07 17:00 | 2.2863 | 2.8441 | 3.4362 | 3.5152 | 3.5941 | 2024-01-06 17:00 | 2.7855 | 3.3006 | 3.3006 | 3.3006 | 3.3006
2024-03-07 18:00 | 2.1339 | 2.6545 | 3.2071 | 3.2808 | 3.3545 | 2024-01-06 18:00 | 2.5607 | 3.0342 | 3.0342 | 3.0342 | 3.0342
2024-03-07 19:00 | 1.7338 | 2.1568 | 2.6058 | 2.6657 | 2.7255 | 2024-01-06 19:00 | 2.1834 | 2.5872 | 2.5872 | 2.5872 | 2.5872
2024-03-07 20:00 | 1.7147 | 2.1331 | 2.5772 | 2.6364 | 2.6956 | 2024-01-06 20:00 | 1.9853 | 2.3524 | 2.3524 | 2.3524 | 2.3524
2024-03-07 21:00 | 1.6957 | 2.1094 | 2.5485 | 2.6071 | 2.6656 | 2024-01-06 21:00 | 2.0462 | 2.4246 | 2.4246 | 2.4246 | 2.4246
2024-03-07 22:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2024-01-06 22:00 | 1.9624 | 2.3253 | 2.3253 | 2.3253 | 2.3253
2024-03-07 23:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2024-01-06 23:00 | 1.6957 | 2.0092 | 2.0092 | 2.0092 | 2.0092
2024-03-08 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-01-07 | 1.5776 | 1.8693 | 1.8693 | 1.8693 | 1.8693
2024-03-08 01:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-01-07 01:00 | 1.589 | 1.8828 | 1.8828 | 1.8828 | 1.8828
2024-03-08 02:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-01-07 02:00 | 1.5928 | 1.8873 | 1.8873 | 1.8873 | 1.8873
2024-03-08 03:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-01-07 03:00 | 1.6766 | 1.9867 | 1.9867 | 1.9867 | 1.9867
2024-03-08 04:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-01-07 04:00 | 1.8633 | 2.2079 | 2.2079 | 2.2079 | 2.2079
2024-03-08 05:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2024-01-07 05:00 | 2.0958 | 2.4833 | 2.4833 | 2.4833 | 2.4833
2024-03-08 06:00 | 1.9434 | 2.4175 | 2.9208 | 2.9879 | 3.055 | 2024-01-07 06:00 | 2.0386 | 2.4156 | 2.4156 | 2.4156 | 2.4156
2024-03-08 07:00 | 2.2101 | 2.7493 | 3.3217 | 3.398 | 3.4743 | 2024-01-07 07:00 | 2.0615 | 2.4427 | 2.4427 | 2.4427 | 2.4427
2024-03-08 08:00 | 2.3054 | 2.8678 | 3.4648 | 3.5445 | 3.6241 | 2024-01-07 08:00 | 2.252 | 2.6684 | 2.6684 | 2.6684 | 2.6684
2024-03-08 09:00 | 2.2863 | 2.8441 | 3.4362 | 3.5152 | 3.5941 | 2024-01-07 09:00 | 2.0272 | 2.4021 | 2.4021 | 2.4021 | 2.4021
2024-03-08 10:00 | 2.3625 | 2.9389 | 3.5508 | 3.6323 | 3.7139 | 2024-01-07 10:00 | 2.5492 | 3.0206 | 3.0206 | 3.0206 | 3.0206
2024-03-08 11:00 | 2.3816 | 2.9626 | 3.5794 | 3.6616 | 3.7439 | 2024-01-07 11:00 | 2.8541 | 3.3818 | 3.3818 | 3.3818 | 3.3818
2024-03-08 12:00 | 1.7719 | 2.2042 | 2.6631 | 2.7242 | 2.7854 | 2024-01-07 12:00 | 2.7626 | 3.2735 | 3.2735 | 3.2735 | 3.2735
2024-03-08 13:00 | 2.3816 | 2.9626 | 3.5794 | 3.6616 | 3.7439 | 2024-01-07 13:00 | 2.7283 | 3.2328 | 3.2328 | 3.2328 | 3.2328
2024-03-08 14:00 | 2.4768 | 3.0811 | 3.7226 | 3.8081 | 3.8936 | 2024-01-07 14:00 | 3.4447 | 4.0817 | 4.0817 | 4.0817 | 4.0817
2024-03-08 15:00 | 1.9434 | 2.4175 | 2.9208 | 2.9879 | 3.055 | 2024-01-07 15:00 | 3.6314 | 4.3029 | 4.3029 | 4.3029 | 4.3029
2024-03-08 16:00 | 2.5911 | 3.2233 | 3.8944 | 3.9838 | 4.0733 | 2024-01-07 16:00 | 3.0827 | 3.6527 | 3.6527 | 3.6527 | 3.6527
2024-03-08 17:00 | 2.2863 | 2.8441 | 3.4362 | 3.5152 | 3.5941 | 2024-01-07 17:00 | 3.197 | 3.7882 | 3.7882 | 3.7882 | 3.7882
2024-03-08 18:00 | 2.0577 | 2.5597 | 3.0926 | 3.1636 | 3.2347 | 2024-01-07 18:00 | 2.7321 | 3.2374 | 3.2374 | 3.2374 | 3.2374
2024-03-08 19:00 | 1.829 | 2.2753 | 2.749 | 2.8121 | 2.8753 | 2024-01-07 19:00 | 2.3739 | 2.8129 | 2.8129 | 2.8129 | 2.8129
2024-03-08 20:00 | 1.81 | 2.2516 | 2.7203 | 2.7828 | 2.8453 | 2024-01-07 20:00 | 2.2215 | 2.6323 | 2.6323 | 2.6323 | 2.6323
2024-03-08 21:00 | 1.829 | 2.2753 | 2.749 | 2.8121 | 2.8753 | 2024-01-07 21:00 | 2.0081 | 2.3795 | 2.3795 | 2.3795 | 2.3795
2024-03-08 22:00 | 1.8481 | 2.299 | 2.7776 | 2.8414 | 2.9052 | 2024-01-07 22:00 | 1.9662 | 2.3298 | 2.3298 | 2.3298 | 2.3298
2024-03-08 23:00 | 1.7719 | 2.2042 | 2.6631 | 2.7242 | 2.7854 | 2024-01-07 23:00 | 1.9243 | 2.2801 | 2.2801 | 2.2801 | 2.2801
2024-03-09 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2024-01-08 | 1.7262 | 2.0454 | 2.0454 | 2.0454 | 2.0454
2024-03-09 01:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2024-01-08 01:00 | 1.7719 | 2.0995 | 2.0995 | 2.0995 | 2.0995
2024-03-09 02:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2024-01-08 02:00 | 1.7909 | 2.1221 | 2.1221 | 2.1221 | 2.1221
2024-03-09 03:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2024-01-08 03:00 | 1.9091 | 2.2621 | 2.2621 | 2.2621 | 2.2621
2024-03-09 04:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2024-01-08 04:00 | 2.111 | 2.5014 | 2.5014 | 2.5014 | 2.5014
2024-03-09 05:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2024-01-08 05:00 | 2.4159 | 2.8626 | 2.8626 | 2.8626 | 2.8626
2024-03-09 06:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2024-01-08 06:00 | 2.8807 | 3.4134 | 3.4134 | 3.4134 | 3.4134
2024-03-09 07:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-01-08 07:00 | 3.2694 | 3.874 | 3.874 | 3.874 | 3.874
2024-03-09 08:00 | 1.0098 | 1.2561 | 1.5177 | 1.5525 | 1.5874 | 2024-01-08 08:00 | 4.043 | 4.7906 | 4.7906 | 4.7906 | 4.7906
2024-03-09 09:00 | 1.3527 | 1.6828 | 2.0331 | 2.0798 | 2.1265 | 2024-01-08 09:00 | 4.1306 | 4.8944 | 4.8944 | 4.8944 | 4.8944
2024-03-09 10:00 | 0.15242 | 0.18961 | 0.22908 | 0.23434 | 0.23961 | 2024-01-08 10:00 | 4.0353 | 4.7815 | 4.7815 | 4.7815 | 4.7815
2024-03-09 11:00 | 1.4289 | 1.7776 | 2.1476 | 2.197 | 2.2463 | 2024-01-08 11:00 | 4.2716 | 5.0615 | 5.0615 | 5.0615 | 5.0615
2024-03-09 12:00 | 0.81926 | 1.0191 | 1.2313 | 1.2596 | 1.2879 | 2024-01-08 12:00 | 3.921 | 4.6461 | 4.6461 | 4.6461 | 4.6461
2024-03-09 13:00 | 0.83831 | 1.0428 | 1.2599 | 1.2889 | 1.3178 | 2024-01-08 13:00 | 3.8181 | 4.5242 | 4.5242 | 4.5242 | 4.5242
2024-03-09 14:00 | 1.2575 | 1.5643 | 1.8899 | 1.9333 | 1.9768 | 2024-01-08 14:00 | 3.9553 | 4.6867 | 4.6867 | 4.6867 | 4.6867
2024-03-09 15:00 | 1.2194 | 1.5169 | 1.8326 | 1.8748 | 1.9169 | 2024-01-08 15:00 | 3.9058 | 4.628 | 4.628 | 4.628 | 4.628
2024-03-09 16:00 | 0.19053 | 0.23701 | 0.28635 | 0.29293 | 0.29951 | 2024-01-08 16:00 | 3.7572 | 4.4519 | 4.4519 | 4.4519 | 4.4519
2024-03-09 17:00 | 0.49537 | 0.61622 | 0.74451 | 0.76162 | 0.77872 | 2024-01-08 17:00 | 3.62 | 4.2894 | 4.2894 | 4.2894 | 4.2894
2024-03-09 18:00 | 1.8481 | 2.299 | 2.7776 | 2.8414 | 2.9052 | 2024-01-08 18:00 | 3.2656 | 3.8695 | 3.8695 | 3.8695 | 3.8695
2024-03-09 19:00 | 1.7147 | 2.1331 | 2.5772 | 2.6364 | 2.6956 | 2024-01-08 19:00 | 2.6369 | 3.1245 | 3.1245 | 3.1245 | 3.1245
2024-03-09 20:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2024-01-08 20:00 | 2.4044 | 2.8491 | 2.8491 | 2.8491 | 2.8491
2024-03-09 21:00 | 1.7909 | 2.2279 | 2.6917 | 2.7535 | 2.8154 | 2024-01-08 21:00 | 2.1758 | 2.5781 | 2.5781 | 2.5781 | 2.5781
2024-03-09 22:00 | 1.6957 | 2.1094 | 2.5485 | 2.6071 | 2.6656 | 2024-01-08 22:00 | 2.0424 | 2.4201 | 2.4201 | 2.4201 | 2.4201
2024-03-09 23:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2024-01-08 23:00 | 1.7566 | 2.0815 | 2.0815 | 2.0815 | 2.0815
2024-03-10 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-01-09 | 1.5928 | 1.8873 | 1.8873 | 1.8873 | 1.8873
2024-03-10 01:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-01-09 01:00 | 1.6233 | 1.9234 | 1.9234 | 1.9234 | 1.9234
2024-03-10 02:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-01-09 02:00 | 1.6881 | 2.0002 | 2.0002 | 2.0002 | 2.0002
2024-03-10 03:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-01-09 03:00 | 1.8367 | 2.1763 | 2.1763 | 2.1763 | 2.1763
2024-03-10 04:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-01-09 04:00 | 2.092 | 2.4788 | 2.4788 | 2.4788 | 2.4788
2024-03-10 05:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2024-01-09 05:00 | 2.1225 | 2.5149 | 2.5149 | 2.5149 | 2.5149
2024-03-10 06:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2024-01-09 06:00 | 2.3739 | 2.8129 | 2.8129 | 2.8129 | 2.8129
2024-03-10 07:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-01-09 07:00 | 2.8045 | 3.3231 | 3.3231 | 3.3231 | 3.3231
2024-03-10 08:00 | 0.97168 | 1.2087 | 1.4604 | 1.4939 | 1.5275 | 2024-01-09 08:00 | 3.5171 | 4.1675 | 4.1675 | 4.1675 | 4.1675
2024-03-10 09:00 | 0.19053 | 0.23701 | 0.28635 | 0.29293 | 0.29951 | 2024-01-09 09:00 | 3.6886 | 4.3707 | 4.3707 | 4.3707 | 4.3707
2024-03-10 10:00 | 0.3295 | 0.40989 | 0.49522 | 0.5066 | 0.51797 | 2024-01-09 10:00 | 3.5552 | 4.2126 | 4.2126 | 4.2126 | 4.2126
2024-03-10 11:00 | 0.93358 | 1.1613 | 1.4031 | 1.4354 | 1.4676 | 2024-01-09 11:00 | 3.7572 | 4.4519 | 4.4519 | 4.4519 | 4.4519
2024-03-10 12:00 | 0.45845 | 0.5703 | 0.68903 | 0.70486 | 0.72069 | 2024-01-09 12:00 | 3.841 | 4.5513 | 4.5513 | 4.5513 | 4.5513
2024-03-10 13:00 | 1.7719 | 2.2042 | 2.6631 | 2.7242 | 2.7854 | 2024-01-09 13:00 | 4.0925 | 4.8493 | 4.8493 | 4.8493 | 4.8493
2024-03-10 14:00 | 0.66684 | 0.82953 | 1.0022 | 1.0253 | 1.0483 | 2024-01-09 14:00 | 3.9401 | 4.6687 | 4.6687 | 4.6687 | 4.6687
2024-03-10 15:00 | 0 | 0 | 0 | 0 | 0 | 2024-01-09 15:00 | 4.1649 | 4.935 | 4.935 | 4.935 | 4.935
2024-03-10 16:00 | 0.7621 | 0.94804 | 1.1454 | 1.1717 | 1.198 | 2024-01-09 16:00 | 4.1725 | 4.9441 | 4.9441 | 4.9441 | 4.9441
2024-03-10 17:00 | 0.24768 | 0.30811 | 0.37226 | 0.38081 | 0.38936 | 2024-01-09 17:00 | 3.8448 | 4.5558 | 4.5558 | 4.5558 | 4.5558
2024-03-10 18:00 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2024-01-09 18:00 | 3.2123 | 3.8063 | 3.8063 | 3.8063 | 3.8063
2024-03-10 19:00 | 1.9243 | 2.3938 | 2.8921 | 2.9586 | 3.025 | 2024-01-09 19:00 | 2.7017 | 3.2012 | 3.2012 | 3.2012 | 3.2012
2024-03-10 20:00 | 1.7719 | 2.2042 | 2.6631 | 2.7242 | 2.7854 | 2024-01-09 20:00 | 2.1796 | 2.5827 | 2.5827 | 2.5827 | 2.5827
2024-03-10 21:00 | 1.7147 | 2.1331 | 2.5772 | 2.6364 | 2.6956 | 2024-01-09 21:00 | 2.1644 | 2.5646 | 2.5646 | 2.5646 | 2.5646
2024-03-10 22:00 | 1.6957 | 2.1094 | 2.5485 | 2.6071 | 2.6656 | 2024-01-09 22:00 | 1.8862 | 2.235 | 2.235 | 2.235 | 2.235
2024-03-10 23:00 | 1.6957 | 2.1094 | 2.5485 | 2.6071 | 2.6656 | 2024-01-09 23:00 | 1.7986 | 2.1311 | 2.1311 | 2.1311 | 2.1311
2024-03-11 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2024-01-10 | 1.6652 | 1.9731 | 1.9731 | 1.9731 | 1.9731
2024-03-11 01:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-01-10 01:00 | 1.7071 | 2.0228 | 2.0228 | 2.0228 | 2.0228
2024-03-11 02:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2024-01-10 02:00 | 1.7376 | 2.0589 | 2.0589 | 2.0589 | 2.0589
2024-03-11 03:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-01-10 03:00 | 1.8443 | 2.1853 | 2.1853 | 2.1853 | 2.1853
2024-03-11 04:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-01-10 04:00 | 1.9281 | 2.2847 | 2.2847 | 2.2847 | 2.2847
2024-03-11 05:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2024-01-10 05:00 | 2.2825 | 2.7046 | 2.7046 | 2.7046 | 2.7046
2024-03-11 06:00 | 1.6957 | 2.1094 | 2.5485 | 2.6071 | 2.6656 | 2024-01-10 06:00 | 2.5035 | 2.9664 | 2.9664 | 2.9664 | 2.9664
2024-03-11 07:00 | 1.8862 | 2.3464 | 2.8349 | 2.9 | 2.9651 | 2024-01-10 07:00 | 2.6331 | 3.12 | 3.12 | 3.12 | 3.12
2024-03-11 08:00 | 1.3718 | 1.7065 | 2.0617 | 2.1091 | 2.1565 | 2024-01-10 08:00 | 3.5857 | 4.2487 | 4.2487 | 4.2487 | 4.2487
2024-03-11 09:00 | 1.1813 | 1.4695 | 1.7754 | 1.8162 | 1.857 | 2024-01-10 09:00 | 3.4028 | 4.032 | 4.032 | 4.032 | 4.032
2024-03-11 10:00 | 1.105 | 1.3747 | 1.6608 | 1.699 | 1.7372 | 2024-01-10 10:00 | 3.6771 | 4.3571 | 4.3571 | 4.3571 | 4.3571
2024-03-11 11:00 | 0.91452 | 1.1376 | 1.3745 | 1.4061 | 1.4376 | 2024-01-10 11:00 | 3.5247 | 4.1765 | 4.1765 | 4.1765 | 4.1765
2024-03-11 12:00 | 0.49537 | 0.61622 | 0.74451 | 0.76162 | 0.77872 | 2024-01-10 12:00 | 4.3783 | 5.1879 | 5.1879 | 5.1879 | 5.1879
2024-03-11 13:00 | 0.78115 | 0.97174 | 1.174 | 1.201 | 1.228 | 2024-01-10 13:00 | 4.3897 | 5.2014 | 5.2014 | 5.2014 | 5.2014
2024-03-11 14:00 | 0.78115 | 0.97174 | 1.174 | 1.201 | 1.228 | 2024-01-10 14:00 | 4.626 | 5.4814 | 5.4814 | 5.4814 | 5.4814
2024-03-11 15:00 | 1.3527 | 1.6828 | 2.0331 | 2.0798 | 2.1265 | 2024-01-10 15:00 | 4.0391 | 4.786 | 4.786 | 4.786 | 4.786
2024-03-11 16:00 | 1.7528 | 2.1805 | 2.6344 | 2.695 | 2.7555 | 2024-01-10 16:00 | 3.9896 | 4.7273 | 4.7273 | 4.7273 | 4.7273
2024-03-11 17:00 | 1.81 | 2.2516 | 2.7203 | 2.7828 | 2.8453 | 2024-01-10 17:00 | 3.6886 | 4.3707 | 4.3707 | 4.3707 | 4.3707
2024-03-11 18:00 | 1.8862 | 2.3464 | 2.8349 | 2.9 | 2.9651 | 2024-01-10 18:00 | 3.3609 | 3.9824 | 3.9824 | 3.9824 | 3.9824
2024-03-11 19:00 | 1.7719 | 2.2042 | 2.6631 | 2.7242 | 2.7854 | 2024-01-10 19:00 | 3.1589 | 3.743 | 3.743 | 3.743 | 3.743
2024-03-11 20:00 | 1.7528 | 2.1805 | 2.6344 | 2.695 | 2.7555 | 2024-01-10 20:00 | 2.9303 | 3.4721 | 3.4721 | 3.4721 | 3.4721
2024-03-11 21:00 | 1.7147 | 2.1331 | 2.5772 | 2.6364 | 2.6956 | 2024-01-10 21:00 | 2.4768 | 2.9348 | 2.9348 | 2.9348 | 2.9348
2024-03-11 22:00 | 1.7147 | 2.1331 | 2.5772 | 2.6364 | 2.6956 | 2024-01-10 22:00 | 2.2291 | 2.6414 | 2.6414 | 2.6414 | 2.6414
2024-03-11 23:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2024-01-10 23:00 | 1.8519 | 2.1944 | 2.1944 | 2.1944 | 2.1944
2024-03-12 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-01-11 | 1.6652 | 1.9731 | 1.9731 | 1.9731 | 1.9731
2024-03-12 01:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2024-01-11 01:00 | 1.6385 | 1.9415 | 1.9415 | 1.9415 | 1.9415
2024-03-12 02:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-01-11 02:00 | 1.6195 | 1.9189 | 1.9189 | 1.9189 | 1.9189
2024-03-12 03:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-01-11 03:00 | 1.7909 | 2.1221 | 2.1221 | 2.1221 | 2.1221
2024-03-12 04:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-01-11 04:00 | 1.9396 | 2.2982 | 2.2982 | 2.2982 | 2.2982
2024-03-12 05:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2024-01-11 05:00 | 2.2977 | 2.7226 | 2.7226 | 2.7226 | 2.7226
2024-03-12 06:00 | 1.8481 | 2.299 | 2.7776 | 2.8414 | 2.9052 | 2024-01-11 06:00 | 2.5492 | 3.0206 | 3.0206 | 3.0206 | 3.0206
2024-03-12 07:00 | 1.9434 | 2.4175 | 2.9208 | 2.9879 | 3.055 | 2024-01-11 07:00 | 3.0903 | 3.6618 | 3.6618 | 3.6618 | 3.6618
2024-03-12 08:00 | 1.9243 | 2.3938 | 2.8921 | 2.9586 | 3.025 | 2024-01-11 08:00 | 3.8562 | 4.5693 | 4.5693 | 4.5693 | 4.5693
2024-03-12 09:00 | 0.80021 | 0.99544 | 1.2027 | 1.2303 | 1.2579 | 2024-01-11 09:00 | 4.0696 | 4.8222 | 4.8222 | 4.8222 | 4.8222
2024-03-12 10:00 | 1.3527 | 1.6828 | 2.0331 | 2.0798 | 2.1265 | 2024-01-11 10:00 | 4.2678 | 5.057 | 5.057 | 5.057 | 5.057
2024-03-12 11:00 | 2.2291 | 2.773 | 3.3503 | 3.4273 | 3.5043 | 2024-01-11 11:00 | 4.1992 | 4.9757 | 4.9757 | 4.9757 | 4.9757
2024-03-12 12:00 | 1.8481 | 2.299 | 2.7776 | 2.8414 | 2.9052 | 2024-01-11 12:00 | 4.6069 | 5.4588 | 5.4588 | 5.4588 | 5.4588
2024-03-12 13:00 | 2.1339 | 2.6545 | 3.2071 | 3.2808 | 3.3545 | 2024-01-11 13:00 | 4.3821 | 5.1924 | 5.1924 | 5.1924 | 5.1924
2024-03-12 14:00 | 3.0103 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2024-01-11 14:00 | 4.6145 | 5.4678 | 5.4678 | 5.4678 | 5.4678
2024-03-12 15:00 | 2.7626 | 3.4366 | 4.1521 | 4.2475 | 4.3429 | 2024-01-11 15:00 | 4.645 | 5.504 | 5.504 | 5.504 | 5.504
2024-03-12 16:00 | 2.8007 | 3.484 | 4.2094 | 4.3061 | 4.4028 | 2024-01-11 16:00 | 4.1344 | 4.8989 | 4.8989 | 4.8989 | 4.8989
2024-03-12 17:00 | 2.553 | 3.1759 | 3.8371 | 3.9253 | 4.0134 | 2024-01-11 17:00 | 4.1268 | 4.8899 | 4.8899 | 4.8899 | 4.8899
2024-03-12 18:00 | 2.0767 | 2.5834 | 3.1212 | 3.1929 | 3.2646 | 2024-01-11 18:00 | 3.3418 | 3.9598 | 3.9598 | 3.9598 | 3.9598
2024-03-12 19:00 | 1.9815 | 2.4649 | 2.9781 | 3.0465 | 3.1149 | 2024-01-11 19:00 | 3.0903 | 3.6618 | 3.6618 | 3.6618 | 3.6618
2024-03-12 20:00 | 1.8672 | 2.3227 | 2.8062 | 2.8707 | 2.9352 | 2024-01-11 20:00 | 2.5111 | 2.9755 | 2.9755 | 2.9755 | 2.9755
2024-03-12 21:00 | 1.7528 | 2.1805 | 2.6344 | 2.695 | 2.7555 | 2024-01-11 21:00 | 2.2101 | 2.6188 | 2.6188 | 2.6188 | 2.6188
2024-03-12 22:00 | 1.7147 | 2.1331 | 2.5772 | 2.6364 | 2.6956 | 2024-01-11 22:00 | 1.951 | 2.3118 | 2.3118 | 2.3118 | 2.3118
2024-03-12 23:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2024-01-11 23:00 | 2.0005 | 2.3704 | 2.3704 | 2.3704 | 2.3704
2024-03-13 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-01-12 | 2.012 | 2.384 | 2.384 | 2.384 | 2.384
2024-03-13 01:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2024-01-12 01:00 | 1.7185 | 2.0363 | 2.0363 | 2.0363 | 2.0363
2024-03-13 02:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-01-12 02:00 | 1.7414 | 2.0634 | 2.0634 | 2.0634 | 2.0634
2024-03-13 03:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-01-12 03:00 | 1.8633 | 2.2079 | 2.2079 | 2.2079 | 2.2079
2024-03-13 04:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-01-12 04:00 | 2.0348 | 2.4111 | 2.4111 | 2.4111 | 2.4111
2024-03-13 05:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2024-01-12 05:00 | 2.4463 | 2.8987 | 2.8987 | 2.8987 | 2.8987
2024-03-13 06:00 | 1.8481 | 2.299 | 2.7776 | 2.8414 | 2.9052 | 2024-01-12 06:00 | 2.8388 | 3.3638 | 3.3638 | 3.3638 | 3.3638
2024-03-13 07:00 | 2.0386 | 2.536 | 3.064 | 3.1344 | 3.2047 | 2024-01-12 07:00 | 3.0217 | 3.5805 | 3.5805 | 3.5805 | 3.5805
2024-03-13 08:00 | 2.3625 | 2.9389 | 3.5508 | 3.6323 | 3.7139 | 2024-01-12 08:00 | 3.6124 | 4.2804 | 4.2804 | 4.2804 | 4.2804
2024-03-13 09:00 | 1.7719 | 2.2042 | 2.6631 | 2.7242 | 2.7854 | 2024-01-12 09:00 | 4.0353 | 4.7815 | 4.7815 | 4.7815 | 4.7815
2024-03-13 10:00 | 2.0196 | 2.5123 | 3.0353 | 3.1051 | 3.1748 | 2024-01-12 10:00 | 4.4011 | 5.215 | 5.215 | 5.215 | 5.215
2024-03-13 11:00 | 2.0958 | 2.6071 | 3.1499 | 3.2222 | 3.2946 | 2024-01-12 11:00 | 4.3668 | 5.1743 | 5.1743 | 5.1743 | 5.1743
2024-03-13 12:00 | 2.3244 | 2.8915 | 3.4935 | 3.5737 | 3.654 | 2024-01-12 12:00 | 4.6564 | 5.5175 | 5.5175 | 5.5175 | 5.5175
2024-03-13 13:00 | 2.8007 | 3.484 | 4.2094 | 4.3061 | 4.4028 | 2024-01-12 13:00 | 4.4507 | 5.2737 | 5.2737 | 5.2737 | 5.2737
2024-03-13 14:00 | 2.8198 | 3.5077 | 4.238 | 4.3354 | 4.4327 | 2024-01-12 14:00 | 4.504 | 5.3369 | 5.3369 | 5.3369 | 5.3369
2024-03-13 15:00 | 2.6864 | 3.3418 | 4.0375 | 4.1303 | 4.2231 | 2024-01-12 15:00 | 4.3097 | 5.1066 | 5.1066 | 5.1066 | 5.1066
2024-03-13 16:00 | 2.8388 | 3.5314 | 4.2666 | 4.3647 | 4.4627 | 2024-01-12 16:00 | 4.4774 | 5.3053 | 5.3053 | 5.3053 | 5.3053
2024-03-13 17:00 | 2.6864 | 3.3418 | 4.0375 | 4.1303 | 4.2231 | 2024-01-12 17:00 | 4.0544 | 4.8041 | 4.8041 | 4.8041 | 4.8041
2024-03-13 18:00 | 2.3435 | 2.9152 | 3.5221 | 3.603 | 3.684 | 2024-01-12 18:00 | 3.9477 | 4.6777 | 4.6777 | 4.6777 | 4.6777
2024-03-13 19:00 | 1.7909 | 2.2279 | 2.6917 | 2.7535 | 2.8154 | 2024-01-12 19:00 | 3.5552 | 4.2126 | 4.2126 | 4.2126 | 4.2126
2024-03-13 20:00 | 1.7909 | 2.2279 | 2.6917 | 2.7535 | 2.8154 | 2024-01-12 20:00 | 3.056 | 3.6211 | 3.6211 | 3.6211 | 3.6211
2024-03-13 21:00 | 1.81 | 2.2516 | 2.7203 | 2.7828 | 2.8453 | 2024-01-12 21:00 | 2.6521 | 3.1425 | 3.1425 | 3.1425 | 3.1425
2024-03-13 22:00 | 1.7719 | 2.2042 | 2.6631 | 2.7242 | 2.7854 | 2024-01-12 22:00 | 2.1415 | 2.5375 | 2.5375 | 2.5375 | 2.5375
2024-03-13 23:00 | 1.7528 | 2.1805 | 2.6344 | 2.695 | 2.7555 | 2024-01-12 23:00 | 2.0043 | 2.375 | 2.375 | 2.375 | 2.375
2024-03-14 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2024-01-13 | 1.7833 | 2.1131 | 2.1131 | 2.1131 | 2.1131
2024-03-14 01:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2024-01-13 01:00 | 1.7795 | 2.1086 | 2.1086 | 2.1086 | 2.1086
2024-03-14 02:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2024-01-13 02:00 | 1.7528 | 2.077 | 2.077 | 2.077 | 2.077
2024-03-14 03:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2024-01-13 03:00 | 1.9167 | 2.2711 | 2.2711 | 2.2711 | 2.2711
2024-03-14 04:00 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2024-01-13 04:00 | 1.9815 | 2.3479 | 2.3479 | 2.3479 | 2.3479
2024-03-14 05:00 | 1.7909 | 2.2279 | 2.6917 | 2.7535 | 2.8154 | 2024-01-13 05:00 | 2.2825 | 2.7046 | 2.7046 | 2.7046 | 2.7046
2024-03-14 06:00 | 2.0386 | 2.536 | 3.064 | 3.1344 | 3.2047 | 2024-01-13 06:00 | 2.3397 | 2.7723 | 2.7723 | 2.7723 | 2.7723
2024-03-14 07:00 | 2.3625 | 2.9389 | 3.5508 | 3.6323 | 3.7139 | 2024-01-13 07:00 | 2.454 | 2.9077 | 2.9077 | 2.9077 | 2.9077
2024-03-14 08:00 | 2.4959 | 3.1048 | 3.7512 | 3.8374 | 3.9236 | 2024-01-13 08:00 | 3.0675 | 3.6347 | 3.6347 | 3.6347 | 3.6347
2024-03-14 09:00 | 2.4959 | 3.1048 | 3.7512 | 3.8374 | 3.9236 | 2024-01-13 09:00 | 3.4333 | 4.0681 | 4.0681 | 4.0681 | 4.0681
2024-03-14 10:00 | 2.3816 | 2.9626 | 3.5794 | 3.6616 | 3.7439 | 2024-01-13 10:00 | 3.4485 | 4.0862 | 4.0862 | 4.0862 | 4.0862
2024-03-14 11:00 | 2.8198 | 3.5077 | 4.238 | 4.3354 | 4.4327 | 2024-01-13 11:00 | 3.319 | 3.9327 | 3.9327 | 3.9327 | 3.9327
2024-03-14 12:00 | 2.8007 | 3.484 | 4.2094 | 4.3061 | 4.4028 | 2024-01-13 12:00 | 3.7 | 4.3842 | 4.3842 | 4.3842 | 4.3842
2024-03-14 13:00 | 2.8198 | 3.5077 | 4.238 | 4.3354 | 4.4327 | 2024-01-13 13:00 | 3.7191 | 4.4068 | 4.4068 | 4.4068 | 4.4068
2024-03-14 14:00 | 2.6864 | 3.3418 | 4.0375 | 4.1303 | 4.2231 | 2024-01-13 14:00 | 4.1573 | 4.926 | 4.926 | 4.926 | 4.926
2024-03-14 15:00 | 2.553 | 3.1759 | 3.8371 | 3.9253 | 4.0134 | 2024-01-13 15:00 | 4.3402 | 5.1427 | 5.1427 | 5.1427 | 5.1427
2024-03-14 16:00 | 2.553 | 3.1759 | 3.8371 | 3.9253 | 4.0134 | 2024-01-13 16:00 | 4.2297 | 5.0118 | 5.0118 | 5.0118 | 5.0118
2024-03-14 17:00 | 2.4197 | 3.01 | 3.6367 | 3.7202 | 3.8038 | 2024-01-13 17:00 | 3.2313 | 3.8288 | 3.8288 | 3.8288 | 3.8288
2024-03-14 18:00 | 2.0577 | 2.5597 | 3.0926 | 3.1636 | 3.2347 | 2024-01-13 18:00 | 3.0675 | 3.6347 | 3.6347 | 3.6347 | 3.6347
2024-03-14 19:00 | 1.7528 | 2.1805 | 2.6344 | 2.695 | 2.7555 | 2024-01-13 19:00 | 2.534 | 3.0026 | 3.0026 | 3.0026 | 3.0026
2024-03-14 20:00 | 1.7338 | 2.1568 | 2.6058 | 2.6657 | 2.7255 | 2024-01-13 20:00 | 2.0882 | 2.4743 | 2.4743 | 2.4743 | 2.4743
2024-03-14 21:00 | 1.7338 | 2.1568 | 2.6058 | 2.6657 | 2.7255 | 2024-01-13 21:00 | 2.1415 | 2.5375 | 2.5375 | 2.5375 | 2.5375
2024-03-14 22:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2024-01-13 22:00 | 1.9434 | 2.3027 | 2.3027 | 2.3027 | 2.3027
2024-03-14 23:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-01-13 23:00 | 1.6842 | 1.9957 | 1.9957 | 1.9957 | 1.9957
2024-03-15 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2024-01-14 | 1.6919 | 2.0047 | 2.0047 | 2.0047 | 2.0047
2024-03-15 01:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-01-14 01:00 | 1.6042 | 1.9009 | 1.9009 | 1.9009 | 1.9009
2024-03-15 02:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-01-14 02:00 | 1.6385 | 1.9415 | 1.9415 | 1.9415 | 1.9415
2024-03-15 03:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-01-14 03:00 | 1.7033 | 2.0183 | 2.0183 | 2.0183 | 2.0183
2024-03-15 04:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-01-14 04:00 | 1.8214 | 2.1582 | 2.1582 | 2.1582 | 2.1582
2024-03-15 05:00 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2024-01-14 05:00 | 1.9929 | 2.3614 | 2.3614 | 2.3614 | 2.3614
2024-03-15 06:00 | 1.9053 | 2.3701 | 2.8635 | 2.9293 | 2.9951 | 2024-01-14 06:00 | 2.2215 | 2.6323 | 2.6323 | 2.6323 | 2.6323
2024-03-15 07:00 | 2.0386 | 2.536 | 3.064 | 3.1344 | 3.2047 | 2024-01-14 07:00 | 2.2406 | 2.6549 | 2.6549 | 2.6549 | 2.6549
2024-03-15 08:00 | 2.2101 | 2.7493 | 3.3217 | 3.398 | 3.4743 | 2024-01-14 08:00 | 2.7245 | 3.2283 | 3.2283 | 3.2283 | 3.2283
2024-03-15 09:00 | 2.1529 | 2.6782 | 3.2358 | 3.3101 | 3.3845 | 2024-01-14 09:00 | 3.1322 | 3.7114 | 3.7114 | 3.7114 | 3.7114
2024-03-15 10:00 | 2.1339 | 2.6545 | 3.2071 | 3.2808 | 3.3545 | 2024-01-14 10:00 | 3.0103 | 3.567 | 3.567 | 3.567 | 3.567
2024-03-15 11:00 | 2.0767 | 2.5834 | 3.1212 | 3.1929 | 3.2646 | 2024-01-14 11:00 | 3.0903 | 3.6618 | 3.6618 | 3.6618 | 3.6618
2024-03-15 12:00 | 1.8481 | 2.299 | 2.7776 | 2.8414 | 2.9052 | 2024-01-14 12:00 | 3.3609 | 3.9824 | 3.9824 | 3.9824 | 3.9824
2024-03-15 13:00 | 1.9243 | 2.3938 | 2.8921 | 2.9586 | 3.025 | 2024-01-14 13:00 | 3.178 | 3.7656 | 3.7656 | 3.7656 | 3.7656
2024-03-15 14:00 | 2.1148 | 2.6308 | 3.1785 | 3.2515 | 3.3245 | 2024-01-14 14:00 | 2.976 | 3.5263 | 3.5263 | 3.5263 | 3.5263
2024-03-15 15:00 | 2.0577 | 2.5597 | 3.0926 | 3.1636 | 3.2347 | 2024-01-14 15:00 | 3.3113 | 3.9237 | 3.9237 | 3.9237 | 3.9237
2024-03-15 16:00 | 1.7719 | 2.2042 | 2.6631 | 2.7242 | 2.7854 | 2024-01-14 16:00 | 3.1094 | 3.6844 | 3.6844 | 3.6844 | 3.6844
2024-03-15 17:00 | 1.7719 | 2.2042 | 2.6631 | 2.7242 | 2.7854 | 2024-01-14 17:00 | 2.8312 | 3.3547 | 3.3547 | 3.3547 | 3.3547
2024-03-15 18:00 | 1.7338 | 2.1568 | 2.6058 | 2.6657 | 2.7255 | 2024-01-14 18:00 | 2.6254 | 3.1109 | 3.1109 | 3.1109 | 3.1109
2024-03-15 19:00 | 1.6957 | 2.1094 | 2.5485 | 2.6071 | 2.6656 | 2024-01-14 19:00 | 2.1758 | 2.5781 | 2.5781 | 2.5781 | 2.5781
2024-03-15 20:00 | 1.6957 | 2.1094 | 2.5485 | 2.6071 | 2.6656 | 2024-01-14 20:00 | 2.1834 | 2.5872 | 2.5872 | 2.5872 | 2.5872
2024-03-15 21:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2024-01-14 21:00 | 1.8976 | 2.2485 | 2.2485 | 2.2485 | 2.2485
2024-03-15 22:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2024-01-14 22:00 | 1.9396 | 2.2982 | 2.2982 | 2.2982 | 2.2982
2024-03-15 23:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-01-14 23:00 | 1.6004 | 1.8964 | 1.8964 | 1.8964 | 1.8964
2024-03-16 | 1.4289 | 1.7776 | 2.1476 | 2.197 | 2.2463 | 2024-01-15 | 1.4937 | 1.7699 | 1.7699 | 1.7699 | 1.7699
2024-03-16 01:00 | 1.4289 | 1.7776 | 2.1476 | 2.197 | 2.2463 | 2024-01-15 01:00 | 1.5394 | 1.8241 | 1.8241 | 1.8241 | 1.8241
2024-03-16 02:00 | 1.4289 | 1.7776 | 2.1476 | 2.197 | 2.2463 | 2024-01-15 02:00 | 1.6233 | 1.9234 | 1.9234 | 1.9234 | 1.9234
2024-03-16 03:00 | 1.4099 | 1.7539 | 2.119 | 2.1677 | 2.2164 | 2024-01-15 03:00 | 1.7414 | 2.0634 | 2.0634 | 2.0634 | 2.0634
2024-03-16 04:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-01-15 04:00 | 1.9053 | 2.2576 | 2.2576 | 2.2576 | 2.2576
2024-03-16 05:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-01-15 05:00 | 2.1796 | 2.5827 | 2.5827 | 2.5827 | 2.5827
2024-03-16 06:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-01-15 06:00 | 2.3168 | 2.7452 | 2.7452 | 2.7452 | 2.7452
2024-03-16 07:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-01-15 07:00 | 2.6559 | 3.1471 | 3.1471 | 3.1471 | 3.1471
2024-03-16 08:00 | 1.3718 | 1.7065 | 2.0617 | 2.1091 | 2.1565 | 2024-01-15 08:00 | 2.9341 | 3.4767 | 3.4767 | 3.4767 | 3.4767
2024-03-16 09:00 | 0.724 | 0.90063 | 1.0881 | 1.1131 | 1.1381 | 2024-01-15 09:00 | 3.2809 | 3.8875 | 3.8875 | 3.8875 | 3.8875
2024-03-16 10:00 | 0.43821 | 0.54512 | 0.65861 | 0.67374 | 0.68887 | 2024-01-15 10:00 | 3.2732 | 3.8785 | 3.8785 | 3.8785 | 3.8785
2024-03-16 11:00 | 0.30484 | 0.37921 | 0.45816 | 0.46869 | 0.47921 | 2024-01-15 11:00 | 3.3494 | 3.9688 | 3.9688 | 3.9688 | 3.9688
2024-03-16 12:00 | 0.24768 | 0.30811 | 0.37226 | 0.38081 | 0.38936 | 2024-01-15 12:00 | 3.4257 | 4.0591 | 4.0591 | 4.0591 | 4.0591
2024-03-16 13:00 | 0.34295 | 0.42662 | 0.51543 | 0.52727 | 0.53912 | 2024-01-15 13:00 | 3.4638 | 4.1043 | 4.1043 | 4.1043 | 4.1043
2024-03-16 14:00 | 0.26674 | 0.33181 | 0.40089 | 0.4101 | 0.41931 | 2024-01-15 14:00 | 3.2008 | 3.7927 | 3.7927 | 3.7927 | 3.7927
2024-03-16 15:00 | 1.3337 | 1.6591 | 2.0045 | 2.0505 | 2.0966 | 2024-01-15 15:00 | 3.1627 | 3.7476 | 3.7476 | 3.7476 | 3.7476
2024-03-16 16:00 | 1.4289 | 1.7776 | 2.1476 | 2.197 | 2.2463 | 2024-01-15 16:00 | 3.1665 | 3.7521 | 3.7521 | 3.7521 | 3.7521
2024-03-16 17:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2024-01-15 17:00 | 3.1665 | 3.7521 | 3.7521 | 3.7521 | 3.7521
2024-03-16 18:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-01-15 18:00 | 3.0217 | 3.5805 | 3.5805 | 3.5805 | 3.5805
2024-03-16 19:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2024-01-15 19:00 | 2.5873 | 3.0658 | 3.0658 | 3.0658 | 3.0658
2024-03-16 20:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-01-15 20:00 | 2.1987 | 2.6052 | 2.6052 | 2.6052 | 2.6052
2024-03-16 21:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2024-01-15 21:00 | 2.0996 | 2.4878 | 2.4878 | 2.4878 | 2.4878
2024-03-16 22:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-01-15 22:00 | 1.871 | 2.2169 | 2.2169 | 2.2169 | 2.2169
2024-03-16 23:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-01-15 23:00 | 1.7452 | 2.0679 | 2.0679 | 2.0679 | 2.0679
2024-03-17 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-01-16 | 1.5699 | 1.8602 | 1.8602 | 1.8602 | 1.8602
2024-03-17 01:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-01-16 01:00 | 1.6042 | 1.9009 | 1.9009 | 1.9009 | 1.9009
2024-03-17 02:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-01-16 02:00 | 1.7376 | 2.0589 | 2.0589 | 2.0589 | 2.0589
2024-03-17 03:00 | 1.4289 | 1.7776 | 2.1476 | 2.197 | 2.2463 | 2024-01-16 03:00 | 1.7414 | 2.0634 | 2.0634 | 2.0634 | 2.0634
2024-03-17 04:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-01-16 04:00 | 1.8786 | 2.226 | 2.226 | 2.226 | 2.226
2024-03-17 05:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-01-16 05:00 | 2.1263 | 2.5194 | 2.5194 | 2.5194 | 2.5194
2024-03-17 06:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-01-16 06:00 | 2.2444 | 2.6594 | 2.6594 | 2.6594 | 2.6594
2024-03-17 07:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2024-01-16 07:00 | 2.5149 | 2.98 | 2.98 | 2.98 | 2.98
2024-03-17 08:00 | 1.4289 | 1.7776 | 2.1476 | 2.197 | 2.2463 | 2024-01-16 08:00 | 3.4104 | 4.041 | 4.041 | 4.041 | 4.041
2024-03-17 09:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-01-16 09:00 | 3.3037 | 3.9146 | 3.9146 | 3.9146 | 3.9146
2024-03-17 10:00 | 1.2956 | 1.6117 | 1.9472 | 1.9919 | 2.0367 | 2024-01-16 10:00 | 3.4371 | 4.0727 | 4.0727 | 4.0727 | 4.0727
2024-03-17 11:00 | 1.4289 | 1.7776 | 2.1476 | 2.197 | 2.2463 | 2024-01-16 11:00 | 3.4257 | 4.0591 | 4.0591 | 4.0591 | 4.0591
2024-03-17 12:00 | 1.2194 | 1.5169 | 1.8326 | 1.8748 | 1.9169 | 2024-01-16 12:00 | 3.6467 | 4.321 | 4.321 | 4.321 | 4.321
2024-03-17 13:00 | 0.95263 | 1.185 | 1.4318 | 1.4646 | 1.4975 | 2024-01-16 13:00 | 3.3914 | 4.0185 | 4.0185 | 4.0185 | 4.0185
2024-03-17 14:00 | 1.0479 | 1.3035 | 1.5749 | 1.6111 | 1.6473 | 2024-01-16 14:00 | 3.9248 | 4.6506 | 4.6506 | 4.6506 | 4.6506
2024-03-17 15:00 | 1.3337 | 1.6591 | 2.0045 | 2.0505 | 2.0966 | 2024-01-16 15:00 | 3.8753 | 4.5919 | 4.5919 | 4.5919 | 4.5919
2024-03-17 16:00 | 1.3527 | 1.6828 | 2.0331 | 2.0798 | 2.1265 | 2024-01-16 16:00 | 3.7229 | 4.4113 | 4.4113 | 4.4113 | 4.4113
2024-03-17 17:00 | 1.2003 | 1.4932 | 1.804 | 1.8455 | 1.8869 | 2024-01-16 17:00 | 3.479 | 4.1223 | 4.1223 | 4.1223 | 4.1223
2024-03-17 18:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-01-16 18:00 | 3.1018 | 3.6753 | 3.6753 | 3.6753 | 3.6753
2024-03-17 19:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2024-01-16 19:00 | 2.4425 | 2.8942 | 2.8942 | 2.8942 | 2.8942
2024-03-17 20:00 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2024-01-16 20:00 | 2.3587 | 2.7949 | 2.7949 | 2.7949 | 2.7949
2024-03-17 21:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2024-01-16 21:00 | 2.2596 | 2.6775 | 2.6775 | 2.6775 | 2.6775
2024-03-17 22:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2024-01-16 22:00 | 1.7757 | 2.1041 | 2.1041 | 2.1041 | 2.1041
2024-03-17 23:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-01-16 23:00 | 1.7224 | 2.0408 | 2.0408 | 2.0408 | 2.0408
2024-03-18 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-01-17 | 1.669 | 1.9776 | 1.9776 | 1.9776 | 1.9776
2024-03-18 01:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-01-17 01:00 | 1.5699 | 1.8602 | 1.8602 | 1.8602 | 1.8602
2024-03-18 02:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-01-17 02:00 | 1.5699 | 1.8602 | 1.8602 | 1.8602 | 1.8602
2024-03-18 03:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-01-17 03:00 | 1.7566 | 2.0815 | 2.0815 | 2.0815 | 2.0815
2024-03-18 04:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-01-17 04:00 | 2.0005 | 2.3704 | 2.3704 | 2.3704 | 2.3704
2024-03-18 05:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2024-01-17 05:00 | 2.3206 | 2.7497 | 2.7497 | 2.7497 | 2.7497
2024-03-18 06:00 | 1.829 | 2.2753 | 2.749 | 2.8121 | 2.8753 | 2024-01-17 06:00 | 2.3968 | 2.84 | 2.84 | 2.84 | 2.84
2024-03-18 07:00 | 2.0196 | 2.5123 | 3.0353 | 3.1051 | 3.1748 | 2024-01-17 07:00 | 2.7055 | 3.2057 | 3.2057 | 3.2057 | 3.2057
2024-03-18 08:00 | 1.105 | 1.3747 | 1.6608 | 1.699 | 1.7372 | 2024-01-17 08:00 | 3.1551 | 3.7385 | 3.7385 | 3.7385 | 3.7385
2024-03-18 09:00 | 2.2863 | 2.8441 | 3.4362 | 3.5152 | 3.5941 | 2024-01-17 09:00 | 3.4752 | 4.1178 | 4.1178 | 4.1178 | 4.1178
2024-03-18 10:00 | 2.1339 | 2.6545 | 3.2071 | 3.2808 | 3.3545 | 2024-01-17 10:00 | 3.9515 | 4.6822 | 4.6822 | 4.6822 | 4.6822
2024-03-18 11:00 | 1.8481 | 2.299 | 2.7776 | 2.8414 | 2.9052 | 2024-01-17 11:00 | 4.3821 | 5.1924 | 5.1924 | 5.1924 | 5.1924
2024-03-18 12:00 | 2.4768 | 3.0811 | 3.7226 | 3.8081 | 3.8936 | 2024-01-17 12:00 | 4.2944 | 5.0886 | 5.0886 | 5.0886 | 5.0886
2024-03-18 13:00 | 2.3816 | 2.9626 | 3.5794 | 3.6616 | 3.7439 | 2024-01-17 13:00 | 4.2487 | 5.0344 | 5.0344 | 5.0344 | 5.0344
2024-03-18 14:00 | 2.4197 | 3.01 | 3.6367 | 3.7202 | 3.8038 | 2024-01-17 14:00 | 3.9439 | 4.6732 | 4.6732 | 4.6732 | 4.6732
2024-03-18 15:00 | 2.0577 | 2.5597 | 3.0926 | 3.1636 | 3.2347 | 2024-01-17 15:00 | 3.6276 | 4.2984 | 4.2984 | 4.2984 | 4.2984
2024-03-18 16:00 | 1.9053 | 2.3701 | 2.8635 | 2.9293 | 2.9951 | 2024-01-17 16:00 | 3.6886 | 4.3707 | 4.3707 | 4.3707 | 4.3707
2024-03-18 17:00 | 1.9624 | 2.4412 | 2.9494 | 3.0172 | 3.0849 | 2024-01-17 17:00 | 3.6352 | 4.3074 | 4.3074 | 4.3074 | 4.3074
2024-03-18 18:00 | 1.9053 | 2.3701 | 2.8635 | 2.9293 | 2.9951 | 2024-01-17 18:00 | 3.0255 | 3.585 | 3.585 | 3.585 | 3.585
2024-03-18 19:00 | 1.7528 | 2.1805 | 2.6344 | 2.695 | 2.7555 | 2024-01-17 19:00 | 2.7359 | 3.2419 | 3.2419 | 3.2419 | 3.2419
2024-03-18 20:00 | 1.7338 | 2.1568 | 2.6058 | 2.6657 | 2.7255 | 2024-01-17 20:00 | 2.2406 | 2.6549 | 2.6549 | 2.6549 | 2.6549
2024-03-18 21:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2024-01-17 21:00 | 2.1872 | 2.5917 | 2.5917 | 2.5917 | 2.5917
2024-03-18 22:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2024-01-17 22:00 | 2.0234 | 2.3975 | 2.3975 | 2.3975 | 2.3975
2024-03-18 23:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2024-01-17 23:00 | 1.7871 | 2.1176 | 2.1176 | 2.1176 | 2.1176
2024-03-19 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2024-01-18 | 1.6614 | 1.9686 | 1.9686 | 1.9686 | 1.9686
2024-03-19 01:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2024-01-18 01:00 | 1.7071 | 2.0228 | 2.0228 | 2.0228 | 2.0228
2024-03-19 02:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-01-18 02:00 | 1.749 | 2.0724 | 2.0724 | 2.0724 | 2.0724
2024-03-19 03:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-01-18 03:00 | 1.8938 | 2.244 | 2.244 | 2.244 | 2.244
2024-03-19 04:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-01-18 04:00 | 2.0462 | 2.4246 | 2.4246 | 2.4246 | 2.4246
2024-03-19 05:00 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2024-01-18 05:00 | 2.2787 | 2.7001 | 2.7001 | 2.7001 | 2.7001
2024-03-19 06:00 | 1.7528 | 2.1805 | 2.6344 | 2.695 | 2.7555 | 2024-01-18 06:00 | 2.5187 | 2.9845 | 2.9845 | 2.9845 | 2.9845
2024-03-19 07:00 | 1.9243 | 2.3938 | 2.8921 | 2.9586 | 3.025 | 2024-01-18 07:00 | 2.8007 | 3.3186 | 3.3186 | 3.3186 | 3.3186
2024-03-19 08:00 | 1.7147 | 2.1331 | 2.5772 | 2.6364 | 2.6956 | 2024-01-18 08:00 | 3.0789 | 3.6482 | 3.6482 | 3.6482 | 3.6482
2024-03-19 09:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2024-01-18 09:00 | 3.2085 | 3.8017 | 3.8017 | 3.8017 | 3.8017
2024-03-19 10:00 | 2.4387 | 3.0337 | 3.6653 | 3.7495 | 3.8337 | 2024-01-18 10:00 | 3.1932 | 3.7837 | 3.7837 | 3.7837 | 3.7837
2024-03-19 11:00 | 2.3816 | 2.9626 | 3.5794 | 3.6616 | 3.7439 | 2024-01-18 11:00 | 2.9074 | 3.4451 | 3.4451 | 3.4451 | 3.4451
2024-03-19 12:00 | 2.0005 | 2.4886 | 3.0067 | 3.0758 | 3.1448 | 2024-01-18 12:00 | 2.8388 | 3.3638 | 3.3638 | 3.3638 | 3.3638
2024-03-19 13:00 | 1.829 | 2.2753 | 2.749 | 2.8121 | 2.8753 | 2024-01-18 13:00 | 2.8998 | 3.436 | 3.436 | 3.436 | 3.436
2024-03-19 14:00 | 2.4578 | 3.0574 | 3.6939 | 3.7788 | 3.8637 | 2024-01-18 14:00 | 3.0484 | 3.6121 | 3.6121 | 3.6121 | 3.6121
2024-03-19 15:00 | 2.3435 | 2.9152 | 3.5221 | 3.603 | 3.684 | 2024-01-18 15:00 | 2.9455 | 3.4902 | 3.4902 | 3.4902 | 3.4902
2024-03-19 16:00 | 2.191 | 2.7256 | 3.293 | 3.3687 | 3.4444 | 2024-01-18 16:00 | 3.1437 | 3.725 | 3.725 | 3.725 | 3.725
2024-03-19 17:00 | 1.8862 | 2.3464 | 2.8349 | 2.9 | 2.9651 | 2024-01-18 17:00 | 3.3418 | 3.9598 | 3.9598 | 3.9598 | 3.9598
2024-03-19 18:00 | 1.9815 | 2.4649 | 2.9781 | 3.0465 | 3.1149 | 2024-01-18 18:00 | 3.0484 | 3.6121 | 3.6121 | 3.6121 | 3.6121
2024-03-19 19:00 | 1.8672 | 2.3227 | 2.8062 | 2.8707 | 2.9352 | 2024-01-18 19:00 | 2.7436 | 3.2509 | 3.2509 | 3.2509 | 3.2509
2024-03-19 20:00 | 1.6957 | 2.1094 | 2.5485 | 2.6071 | 2.6656 | 2024-01-18 20:00 | 2.4387 | 2.8897 | 2.8897 | 2.8897 | 2.8897
2024-03-19 21:00 | 1.7528 | 2.1805 | 2.6344 | 2.695 | 2.7555 | 2024-01-18 21:00 | 2.0805 | 2.4653 | 2.4653 | 2.4653 | 2.4653
2024-03-19 22:00 | 1.7147 | 2.1331 | 2.5772 | 2.6364 | 2.6956 | 2024-01-18 22:00 | 2.0158 | 2.3885 | 2.3885 | 2.3885 | 2.3885
2024-03-19 23:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2024-01-18 23:00 | 1.7795 | 2.1086 | 2.1086 | 2.1086 | 2.1086
2024-03-20 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-01-19 | 1.5699 | 1.8602 | 1.8602 | 1.8602 | 1.8602
2024-03-20 01:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-01-19 01:00 | 1.5509 | 1.8377 | 1.8377 | 1.8377 | 1.8377
2024-03-20 02:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-01-19 02:00 | 1.5966 | 1.8918 | 1.8918 | 1.8918 | 1.8918
2024-03-20 03:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-01-19 03:00 | 1.7452 | 2.0679 | 2.0679 | 2.0679 | 2.0679
2024-03-20 04:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-01-19 04:00 | 1.9891 | 2.3569 | 2.3569 | 2.3569 | 2.3569
2024-03-20 05:00 | 1.7719 | 2.2042 | 2.6631 | 2.7242 | 2.7854 | 2024-01-19 05:00 | 2.1263 | 2.5194 | 2.5194 | 2.5194 | 2.5194
2024-03-20 06:00 | 2.0386 | 2.536 | 3.064 | 3.1344 | 3.2047 | 2024-01-19 06:00 | 2.1682 | 2.5691 | 2.5691 | 2.5691 | 2.5691
2024-03-20 07:00 | 2.2101 | 2.7493 | 3.3217 | 3.398 | 3.4743 | 2024-01-19 07:00 | 2.3892 | 2.831 | 2.831 | 2.831 | 2.831
2024-03-20 08:00 | 2.2673 | 2.8204 | 3.4076 | 3.4859 | 3.5642 | 2024-01-19 08:00 | 2.5873 | 3.0658 | 3.0658 | 3.0658 | 3.0658
2024-03-20 09:00 | 2.191 | 2.7256 | 3.293 | 3.3687 | 3.4444 | 2024-01-19 09:00 | 2.6559 | 3.1471 | 3.1471 | 3.1471 | 3.1471
2024-03-20 10:00 | 1.8672 | 2.3227 | 2.8062 | 2.8707 | 2.9352 | 2024-01-19 10:00 | 2.7741 | 3.287 | 3.287 | 3.287 | 3.287
2024-03-20 11:00 | 2.1148 | 2.6308 | 3.1785 | 3.2515 | 3.3245 | 2024-01-19 11:00 | 3.0179 | 3.576 | 3.576 | 3.576 | 3.576
2024-03-20 12:00 | 1.9243 | 2.3938 | 2.8921 | 2.9586 | 3.025 | 2024-01-19 12:00 | 3.1437 | 3.725 | 3.725 | 3.725 | 3.725
2024-03-20 13:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2024-01-19 13:00 | 3.2085 | 3.8017 | 3.8017 | 3.8017 | 3.8017
2024-03-20 14:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2024-01-19 14:00 | 3.4104 | 4.041 | 4.041 | 4.041 | 4.041
2024-03-20 15:00 | 1.9434 | 2.4175 | 2.9208 | 2.9879 | 3.055 | 2024-01-19 15:00 | 3.4142 | 4.0456 | 4.0456 | 4.0456 | 4.0456
2024-03-20 16:00 | 1.9053 | 2.3701 | 2.8635 | 2.9293 | 2.9951 | 2024-01-19 16:00 | 3.5704 | 4.2307 | 4.2307 | 4.2307 | 4.2307
2024-03-20 17:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2024-01-19 17:00 | 3.5209 | 4.172 | 4.172 | 4.172 | 4.172
2024-03-20 18:00 | 1.9243 | 2.3938 | 2.8921 | 2.9586 | 3.025 | 2024-01-19 18:00 | 3.5019 | 4.1494 | 4.1494 | 4.1494 | 4.1494
2024-03-20 19:00 | 1.7528 | 2.1805 | 2.6344 | 2.695 | 2.7555 | 2024-01-19 19:00 | 3.4028 | 4.032 | 4.032 | 4.032 | 4.032
2024-03-20 20:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2024-01-19 20:00 | 2.835 | 3.3593 | 3.3593 | 3.3593 | 3.3593
2024-03-20 21:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2024-01-19 21:00 | 2.3701 | 2.8084 | 2.8084 | 2.8084 | 2.8084
2024-03-20 22:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2024-01-19 22:00 | 2.0196 | 2.393 | 2.393 | 2.393 | 2.393
2024-03-20 23:00 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2024-01-19 23:00 | 1.7681 | 2.095 | 2.095 | 2.095 | 2.095
2024-03-21 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-01-20 | 1.6614 | 1.9686 | 1.9686 | 1.9686 | 1.9686
2024-03-21 01:00 | 1.4289 | 1.7776 | 2.1476 | 2.197 | 2.2463 | 2024-01-20 01:00 | 1.5928 | 1.8873 | 1.8873 | 1.8873 | 1.8873
2024-03-21 02:00 | 1.4289 | 1.7776 | 2.1476 | 2.197 | 2.2463 | 2024-01-20 02:00 | 1.6271 | 1.928 | 1.928 | 1.928 | 1.928
2024-03-21 03:00 | 1.3718 | 1.7065 | 2.0617 | 2.1091 | 2.1565 | 2024-01-20 03:00 | 1.8405 | 2.1808 | 2.1808 | 2.1808 | 2.1808
2024-03-21 04:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-01-20 04:00 | 1.8672 | 2.2124 | 2.2124 | 2.2124 | 2.2124
2024-03-21 05:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2024-01-20 05:00 | 2.2482 | 2.6639 | 2.6639 | 2.6639 | 2.6639
2024-03-21 06:00 | 1.6957 | 2.1094 | 2.5485 | 2.6071 | 2.6656 | 2024-01-20 06:00 | 2.0615 | 2.4427 | 2.4427 | 2.4427 | 2.4427
2024-03-21 07:00 | 2.1529 | 2.6782 | 3.2358 | 3.3101 | 3.3845 | 2024-01-20 07:00 | 2.3435 | 2.7768 | 2.7768 | 2.7768 | 2.7768
2024-03-21 08:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2024-01-20 08:00 | 2.5988 | 3.0793 | 3.0793 | 3.0793 | 3.0793
2024-03-21 09:00 | 0.74305 | 0.92433 | 1.1168 | 1.1424 | 1.1681 | 2024-01-20 09:00 | 2.6102 | 3.0929 | 3.0929 | 3.0929 | 3.0929
2024-03-21 10:00 | 0.62873 | 0.78213 | 0.94496 | 0.96667 | 0.98838 | 2024-01-20 10:00 | 3.056 | 3.6211 | 3.6211 | 3.6211 | 3.6211
2024-03-21 11:00 | 0.81926 | 1.0191 | 1.2313 | 1.2596 | 1.2879 | 2024-01-20 11:00 | 3.1361 | 3.716 | 3.716 | 3.716 | 3.716
2024-03-21 12:00 | 0.78115 | 0.97174 | 1.174 | 1.201 | 1.228 | 2024-01-20 12:00 | 3.4333 | 4.0681 | 4.0681 | 4.0681 | 4.0681
2024-03-21 13:00 | 0.60968 | 0.75843 | 0.91632 | 0.93738 | 0.95843 | 2024-01-20 13:00 | 3.178 | 3.7656 | 3.7656 | 3.7656 | 3.7656
2024-03-21 14:00 | 0.62873 | 0.78213 | 0.94496 | 0.96667 | 0.98838 | 2024-01-20 14:00 | 3.3647 | 3.9869 | 3.9869 | 3.9869 | 3.9869
2024-03-21 15:00 | 0.60968 | 0.75843 | 0.91632 | 0.93738 | 0.95843 | 2024-01-20 15:00 | 3.4942 | 4.1404 | 4.1404 | 4.1404 | 4.1404
2024-03-21 16:00 | 0.4001 | 0.49772 | 0.60134 | 0.61515 | 0.62897 | 2024-01-20 16:00 | 3.5019 | 4.1494 | 4.1494 | 4.1494 | 4.1494
2024-03-21 17:00 | 0.7621 | 0.94804 | 1.1454 | 1.1717 | 1.198 | 2024-01-20 17:00 | 3.0941 | 3.6663 | 3.6663 | 3.6663 | 3.6663
2024-03-21 18:00 | 1.81 | 2.2516 | 2.7203 | 2.7828 | 2.8453 | 2024-01-20 18:00 | 2.7359 | 3.2419 | 3.2419 | 3.2419 | 3.2419
2024-03-21 19:00 | 1.7147 | 2.1331 | 2.5772 | 2.6364 | 2.6956 | 2024-01-20 19:00 | 2.6216 | 3.1064 | 3.1064 | 3.1064 | 3.1064
2024-03-21 20:00 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2024-01-20 20:00 | 2.2215 | 2.6323 | 2.6323 | 2.6323 | 2.6323
2024-03-21 21:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2024-01-20 21:00 | 1.9548 | 2.3163 | 2.3163 | 2.3163 | 2.3163
2024-03-21 22:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2024-01-20 22:00 | 2.0805 | 2.4653 | 2.4653 | 2.4653 | 2.4653
2024-03-21 23:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2024-01-20 23:00 | 1.8862 | 2.235 | 2.235 | 2.235 | 2.235
2024-03-22 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-01-21 | 1.7071 | 2.0228 | 2.0228 | 2.0228 | 2.0228
2024-03-22 01:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-01-21 01:00 | 1.73 | 2.0499 | 2.0499 | 2.0499 | 2.0499
2024-03-22 02:00 | 1.4289 | 1.7776 | 2.1476 | 2.197 | 2.2463 | 2024-01-21 02:00 | 1.7414 | 2.0634 | 2.0634 | 2.0634 | 2.0634
2024-03-22 03:00 | 1.4099 | 1.7539 | 2.119 | 2.1677 | 2.2164 | 2024-01-21 03:00 | 1.7909 | 2.1221 | 2.1221 | 2.1221 | 2.1221
2024-03-22 04:00 | 1.4289 | 1.7776 | 2.1476 | 2.197 | 2.2463 | 2024-01-21 04:00 | 1.8748 | 2.2214 | 2.2214 | 2.2214 | 2.2214
2024-03-22 05:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2024-01-21 05:00 | 2.0843 | 2.4698 | 2.4698 | 2.4698 | 2.4698
2024-03-22 06:00 | 1.7147 | 2.1331 | 2.5772 | 2.6364 | 2.6956 | 2024-01-21 06:00 | 2.092 | 2.4788 | 2.4788 | 2.4788 | 2.4788
2024-03-22 07:00 | 1.9434 | 2.4175 | 2.9208 | 2.9879 | 3.055 | 2024-01-21 07:00 | 2.313 | 2.7407 | 2.7407 | 2.7407 | 2.7407
2024-03-22 08:00 | 1.4289 | 1.7776 | 2.1476 | 2.197 | 2.2463 | 2024-01-21 08:00 | 2.2558 | 2.673 | 2.673 | 2.673 | 2.673
2024-03-22 09:00 | 0.51442 | 0.63992 | 0.77315 | 0.79091 | 0.80867 | 2024-01-21 09:00 | 2.3015 | 2.7271 | 2.7271 | 2.7271 | 2.7271
2024-03-22 10:00 | 1.9434 | 2.4175 | 2.9208 | 2.9879 | 3.055 | 2024-01-21 10:00 | 2.7131 | 3.2148 | 3.2148 | 3.2148 | 3.2148
2024-03-22 11:00 | 1.81 | 2.2516 | 2.7203 | 2.7828 | 2.8453 | 2024-01-21 11:00 | 2.6978 | 3.1967 | 3.1967 | 3.1967 | 3.1967
2024-03-22 12:00 | 1.3527 | 1.6828 | 2.0331 | 2.0798 | 2.1265 | 2024-01-21 12:00 | 2.8388 | 3.3638 | 3.3638 | 3.3638 | 3.3638
2024-03-22 13:00 | 0.91452 | 1.1376 | 1.3745 | 1.4061 | 1.4376 | 2024-01-21 13:00 | 3.1513 | 3.734 | 3.734 | 3.734 | 3.734
2024-03-22 14:00 | 0.81926 | 1.0191 | 1.2313 | 1.2596 | 1.2879 | 2024-01-21 14:00 | 3.3342 | 3.9507 | 3.9507 | 3.9507 | 3.9507
2024-03-22 15:00 | 0.83831 | 1.0428 | 1.2599 | 1.2889 | 1.3178 | 2024-01-21 15:00 | 3.2809 | 3.8875 | 3.8875 | 3.8875 | 3.8875
2024-03-22 16:00 | 0.80021 | 0.99544 | 1.2027 | 1.2303 | 1.2579 | 2024-01-21 16:00 | 3.2694 | 3.874 | 3.874 | 3.874 | 3.874
2024-03-22 17:00 | 1.3718 | 1.7065 | 2.0617 | 2.1091 | 2.1565 | 2024-01-21 17:00 | 3.2923 | 3.9011 | 3.9011 | 3.9011 | 3.9011
2024-03-22 18:00 | 1.829 | 2.2753 | 2.749 | 2.8121 | 2.8753 | 2024-01-21 18:00 | 2.8731 | 3.4044 | 3.4044 | 3.4044 | 3.4044
2024-03-22 19:00 | 1.7528 | 2.1805 | 2.6344 | 2.695 | 2.7555 | 2024-01-21 19:00 | 2.816 | 3.3367 | 3.3367 | 3.3367 | 3.3367
2024-03-22 20:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2024-01-21 20:00 | 2.2749 | 2.6955 | 2.6955 | 2.6955 | 2.6955
2024-03-22 21:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-01-21 21:00 | 2.1225 | 2.5149 | 2.5149 | 2.5149 | 2.5149
2024-03-22 22:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2024-01-21 22:00 | 1.9205 | 2.2756 | 2.2756 | 2.2756 | 2.2756
2024-03-22 23:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-01-21 23:00 | 1.8405 | 2.1808 | 2.1808 | 2.1808 | 2.1808
2024-03-23 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-01-22 | 1.5547 | 1.8422 | 1.8422 | 1.8422 | 1.8422
2024-03-23 01:00 | 1.4289 | 1.7776 | 2.1476 | 2.197 | 2.2463 | 2024-01-22 01:00 | 1.6042 | 1.9009 | 1.9009 | 1.9009 | 1.9009
2024-03-23 02:00 | 1.4289 | 1.7776 | 2.1476 | 2.197 | 2.2463 | 2024-01-22 02:00 | 1.5661 | 1.8557 | 1.8557 | 1.8557 | 1.8557
2024-03-23 03:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-01-22 03:00 | 1.7643 | 2.0905 | 2.0905 | 2.0905 | 2.0905
2024-03-23 04:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-01-22 04:00 | 1.951 | 2.3118 | 2.3118 | 2.3118 | 2.3118
2024-03-23 05:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2024-01-22 05:00 | 2.1758 | 2.5781 | 2.5781 | 2.5781 | 2.5781
2024-03-23 06:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-01-22 06:00 | 2.4159 | 2.8626 | 2.8626 | 2.8626 | 2.8626
2024-03-23 07:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-01-22 07:00 | 2.8312 | 3.3547 | 3.3547 | 3.3547 | 3.3547
2024-03-23 08:00 | 1.3527 | 1.6828 | 2.0331 | 2.0798 | 2.1265 | 2024-01-22 08:00 | 3.037 | 3.5986 | 3.5986 | 3.5986 | 3.5986
2024-03-23 09:00 | 1.4289 | 1.7776 | 2.1476 | 2.197 | 2.2463 | 2024-01-22 09:00 | 2.9913 | 3.5444 | 3.5444 | 3.5444 | 3.5444
2024-03-23 10:00 | 0.87642 | 1.0902 | 1.3172 | 1.3475 | 1.3777 | 2024-01-22 10:00 | 2.9189 | 3.4586 | 3.4586 | 3.4586 | 3.4586
2024-03-23 11:00 | 0.85737 | 1.0665 | 1.2886 | 1.3182 | 1.3478 | 2024-01-22 11:00 | 3.2847 | 3.892 | 3.892 | 3.892 | 3.892
2024-03-23 12:00 | 0.99073 | 1.2324 | 1.489 | 1.5232 | 1.5574 | 2024-01-22 12:00 | 3.54 | 4.1946 | 4.1946 | 4.1946 | 4.1946
2024-03-23 13:00 | 1.1432 | 1.4221 | 1.7181 | 1.7576 | 1.7971 | 2024-01-22 13:00 | 3.8753 | 4.5919 | 4.5919 | 4.5919 | 4.5919
2024-03-23 14:00 | 0.78115 | 0.97174 | 1.174 | 1.201 | 1.228 | 2024-01-22 14:00 | 4.0048 | 4.7454 | 4.7454 | 4.7454 | 4.7454
2024-03-23 15:00 | 0.97168 | 1.2087 | 1.4604 | 1.4939 | 1.5275 | 2024-01-22 15:00 | 3.9706 | 4.7048 | 4.7048 | 4.7048 | 4.7048
2024-03-23 16:00 | 0.97168 | 1.2087 | 1.4604 | 1.4939 | 1.5275 | 2024-01-22 16:00 | 4.1573 | 4.926 | 4.926 | 4.926 | 4.926
2024-03-23 17:00 | 1.2575 | 1.5643 | 1.8899 | 1.9333 | 1.9768 | 2024-01-22 17:00 | 3.5819 | 4.2442 | 4.2442 | 4.2442 | 4.2442
2024-03-23 18:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-01-22 18:00 | 3.0675 | 3.6347 | 3.6347 | 3.6347 | 3.6347
2024-03-23 19:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-01-22 19:00 | 2.7893 | 3.3051 | 3.3051 | 3.3051 | 3.3051
2024-03-23 20:00 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2024-01-22 20:00 | 2.2139 | 2.6233 | 2.6233 | 2.6233 | 2.6233
2024-03-23 21:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2024-01-22 21:00 | 2.2444 | 2.6594 | 2.6594 | 2.6594 | 2.6594
2024-03-23 22:00 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2024-01-22 22:00 | 1.8062 | 2.1402 | 2.1402 | 2.1402 | 2.1402
2024-03-23 23:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-01-22 23:00 | 1.6728 | 1.9821 | 1.9821 | 1.9821 | 1.9821
2024-03-24 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-01-23 | 1.528 | 1.8106 | 1.8106 | 1.8106 | 1.8106
2024-03-24 01:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-01-23 01:00 | 1.6728 | 1.9821 | 1.9821 | 1.9821 | 1.9821
2024-03-24 02:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-01-23 02:00 | 1.6195 | 1.9189 | 1.9189 | 1.9189 | 1.9189
2024-03-24 03:00 | 1.4289 | 1.7776 | 2.1476 | 2.197 | 2.2463 | 2024-01-23 03:00 | 1.7566 | 2.0815 | 2.0815 | 2.0815 | 2.0815
2024-03-24 04:00 | 1.4289 | 1.7776 | 2.1476 | 2.197 | 2.2463 | 2024-01-23 04:00 | 1.9624 | 2.3253 | 2.3253 | 2.3253 | 2.3253
2024-03-24 05:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-01-23 05:00 | 2.172 | 2.5736 | 2.5736 | 2.5736 | 2.5736
2024-03-24 06:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-01-23 06:00 | 2.2291 | 2.6414 | 2.6414 | 2.6414 | 2.6414
2024-03-24 07:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-01-23 07:00 | 2.7245 | 3.2283 | 3.2283 | 3.2283 | 3.2283
2024-03-24 08:00 | 1.1241 | 1.3984 | 1.6895 | 1.7283 | 1.7671 | 2024-01-23 08:00 | 3.2199 | 3.8153 | 3.8153 | 3.8153 | 3.8153
2024-03-24 09:00 | 1.2003 | 1.4932 | 1.804 | 1.8455 | 1.8869 | 2024-01-23 09:00 | 3.3685 | 3.9914 | 3.9914 | 3.9914 | 3.9914
2024-03-24 10:00 | 0.724 | 0.90063 | 1.0881 | 1.1131 | 1.1381 | 2024-01-23 10:00 | 3.3494 | 3.9688 | 3.9688 | 3.9688 | 3.9688
2024-03-24 11:00 | 0.55252 | 0.68733 | 0.83042 | 0.8495 | 0.86858 | 2024-01-23 11:00 | 3.5247 | 4.1765 | 4.1765 | 4.1765 | 4.1765
2024-03-24 12:00 | 0.59063 | 0.73473 | 0.88769 | 0.90808 | 0.92848 | 2024-01-23 12:00 | 3.4752 | 4.1178 | 4.1178 | 4.1178 | 4.1178
2024-03-24 13:00 | 0.66684 | 0.82953 | 1.0022 | 1.0253 | 1.0483 | 2024-01-23 13:00 | 3.8334 | 4.5422 | 4.5422 | 4.5422 | 4.5422
2024-03-24 14:00 | 0.87642 | 1.0902 | 1.3172 | 1.3475 | 1.3777 | 2024-01-23 14:00 | 3.761 | 4.4564 | 4.4564 | 4.4564 | 4.4564
2024-03-24 15:00 | 0.91452 | 1.1376 | 1.3745 | 1.4061 | 1.4376 | 2024-01-23 15:00 | 3.5095 | 4.1584 | 4.1584 | 4.1584 | 4.1584
2024-03-24 16:00 | 1.1241 | 1.3984 | 1.6895 | 1.7283 | 1.7671 | 2024-01-23 16:00 | 3.9629 | 4.6957 | 4.6957 | 4.6957 | 4.6957
2024-03-24 17:00 | 0.53347 | 0.66362 | 0.80178 | 0.8202 | 0.83862 | 2024-01-23 17:00 | 3.6962 | 4.3797 | 4.3797 | 4.3797 | 4.3797
2024-03-24 18:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-01-23 18:00 | 3.1284 | 3.7069 | 3.7069 | 3.7069 | 3.7069
2024-03-24 19:00 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2024-01-23 19:00 | 2.6902 | 3.1877 | 3.1877 | 3.1877 | 3.1877
2024-03-24 20:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2024-01-23 20:00 | 2.3701 | 2.8084 | 2.8084 | 2.8084 | 2.8084
2024-03-24 21:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-01-23 21:00 | 2.3168 | 2.7452 | 2.7452 | 2.7452 | 2.7452
2024-03-24 22:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2024-01-23 22:00 | 1.9586 | 2.3208 | 2.3208 | 2.3208 | 2.3208
2024-03-24 23:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-01-23 23:00 | 1.7681 | 2.095 | 2.095 | 2.095 | 2.095
2024-03-25 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-01-24 | 1.5737 | 1.8648 | 1.8648 | 1.8648 | 1.8648
2024-03-25 01:00 | 1.4099 | 1.7539 | 2.119 | 2.1677 | 2.2164 | 2024-01-24 01:00 | 1.6233 | 1.9234 | 1.9234 | 1.9234 | 1.9234
2024-03-25 02:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-01-24 02:00 | 1.6347 | 1.937 | 1.937 | 1.937 | 1.937
2024-03-25 03:00 | 1.4289 | 1.7776 | 2.1476 | 2.197 | 2.2463 | 2024-01-24 03:00 | 1.7948 | 2.1266 | 2.1266 | 2.1266 | 2.1266
2024-03-25 04:00 | 1.4099 | 1.7539 | 2.119 | 2.1677 | 2.2164 | 2024-01-24 04:00 | 1.871 | 2.2169 | 2.2169 | 2.2169 | 2.2169
2024-03-25 05:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2024-01-24 05:00 | 2.1949 | 2.6007 | 2.6007 | 2.6007 | 2.6007
2024-03-25 06:00 | 1.6957 | 2.1094 | 2.5485 | 2.6071 | 2.6656 | 2024-01-24 06:00 | 2.3663 | 2.8039 | 2.8039 | 2.8039 | 2.8039
2024-03-25 07:00 | 2.172 | 2.7019 | 3.2644 | 3.3394 | 3.4144 | 2024-01-24 07:00 | 2.6521 | 3.1425 | 3.1425 | 3.1425 | 3.1425
2024-03-25 08:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2024-01-24 08:00 | 3.1132 | 3.6889 | 3.6889 | 3.6889 | 3.6889
2024-03-25 09:00 | 0.95263 | 1.185 | 1.4318 | 1.4646 | 1.4975 | 2024-01-24 09:00 | 3.6771 | 4.3571 | 4.3571 | 4.3571 | 4.3571
2024-03-25 10:00 | 0.91452 | 1.1376 | 1.3745 | 1.4061 | 1.4376 | 2024-01-24 10:00 | 3.8105 | 4.5151 | 4.5151 | 4.5151 | 4.5151
2024-03-25 11:00 | 0.87642 | 1.0902 | 1.3172 | 1.3475 | 1.3777 | 2024-01-24 11:00 | 3.8486 | 4.5603 | 4.5603 | 4.5603 | 4.5603
2024-03-25 12:00 | 1.2003 | 1.4932 | 1.804 | 1.8455 | 1.8869 | 2024-01-24 12:00 | 4.2487 | 5.0344 | 5.0344 | 5.0344 | 5.0344
2024-03-25 13:00 | 1.4289 | 1.7776 | 2.1476 | 2.197 | 2.2463 | 2024-01-24 13:00 | 4.1268 | 4.8899 | 4.8899 | 4.8899 | 4.8899
2024-03-25 14:00 | 1.3908 | 1.7302 | 2.0904 | 2.1384 | 2.1864 | 2024-01-24 14:00 | 4.0849 | 4.8402 | 4.8402 | 4.8402 | 4.8402
2024-03-25 15:00 | 1.4289 | 1.7776 | 2.1476 | 2.197 | 2.2463 | 2024-01-24 15:00 | 4.203 | 4.9802 | 4.9802 | 4.9802 | 4.9802
2024-03-25 16:00 | 1.3908 | 1.7302 | 2.0904 | 2.1384 | 2.1864 | 2024-01-24 16:00 | 4.1039 | 4.8628 | 4.8628 | 4.8628 | 4.8628
2024-03-25 17:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2024-01-24 17:00 | 3.7991 | 4.5016 | 4.5016 | 4.5016 | 4.5016
2024-03-25 18:00 | 1.9434 | 2.4175 | 2.9208 | 2.9879 | 3.055 | 2024-01-24 18:00 | 3.3875 | 4.014 | 4.014 | 4.014 | 4.014
2024-03-25 19:00 | 1.829 | 2.2753 | 2.749 | 2.8121 | 2.8753 | 2024-01-24 19:00 | 3.1551 | 3.7385 | 3.7385 | 3.7385 | 3.7385
2024-03-25 20:00 | 1.81 | 2.2516 | 2.7203 | 2.7828 | 2.8453 | 2024-01-24 20:00 | 2.7817 | 3.2961 | 3.2961 | 3.2961 | 3.2961
2024-03-25 21:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2024-01-24 21:00 | 2.3739 | 2.8129 | 2.8129 | 2.8129 | 2.8129
2024-03-25 22:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2024-01-24 22:00 | 2.0462 | 2.4246 | 2.4246 | 2.4246 | 2.4246
2024-03-25 23:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2024-01-24 23:00 | 1.9472 | 2.3072 | 2.3072 | 2.3072 | 2.3072
2024-03-26 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-01-25 | 1.7833 | 2.1131 | 2.1131 | 2.1131 | 2.1131
2024-03-26 01:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-01-25 01:00 | 1.7338 | 2.0544 | 2.0544 | 2.0544 | 2.0544
2024-03-26 02:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-01-25 02:00 | 1.7452 | 2.0679 | 2.0679 | 2.0679 | 2.0679
2024-03-26 03:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-01-25 03:00 | 1.8443 | 2.1853 | 2.1853 | 2.1853 | 2.1853
2024-03-26 04:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2024-01-25 04:00 | 2.092 | 2.4788 | 2.4788 | 2.4788 | 2.4788
2024-03-26 05:00 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2024-01-25 05:00 | 2.4806 | 2.9394 | 2.9394 | 2.9394 | 2.9394
2024-03-26 06:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2024-01-25 06:00 | 2.5988 | 3.0793 | 3.0793 | 3.0793 | 3.0793
2024-03-26 07:00 | 2.0767 | 2.5834 | 3.1212 | 3.1929 | 3.2646 | 2024-01-25 07:00 | 3.2275 | 3.8243 | 3.8243 | 3.8243 | 3.8243
2024-03-26 08:00 | 1.829 | 2.2753 | 2.749 | 2.8121 | 2.8753 | 2024-01-25 08:00 | 3.8143 | 4.5197 | 4.5197 | 4.5197 | 4.5197
2024-03-26 09:00 | 0.78115 | 0.97174 | 1.174 | 1.201 | 1.228 | 2024-01-25 09:00 | 4.0772 | 4.8312 | 4.8312 | 4.8312 | 4.8312
2024-03-26 10:00 | 0.78115 | 0.97174 | 1.174 | 1.201 | 1.228 | 2024-01-25 10:00 | 4.2335 | 5.0163 | 5.0163 | 5.0163 | 5.0163
2024-03-26 11:00 | 0.7621 | 0.94804 | 1.1454 | 1.1717 | 1.198 | 2024-01-25 11:00 | 4.2792 | 5.0705 | 5.0705 | 5.0705 | 5.0705
2024-03-26 12:00 | 1.1432 | 1.4221 | 1.7181 | 1.7576 | 1.7971 | 2024-01-25 12:00 | 4.5002 | 5.3324 | 5.3324 | 5.3324 | 5.3324
2024-03-26 13:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-01-25 13:00 | 4.4812 | 5.3098 | 5.3098 | 5.3098 | 5.3098
2024-03-26 14:00 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2024-01-25 14:00 | 4.626 | 5.4814 | 5.4814 | 5.4814 | 5.4814
2024-03-26 15:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2024-01-25 15:00 | 4.7784 | 5.662 | 5.662 | 5.662 | 5.662
2024-03-26 16:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2024-01-25 16:00 | 4.5078 | 5.3414 | 5.3414 | 5.3414 | 5.3414
2024-03-26 17:00 | 2.172 | 2.7019 | 3.2644 | 3.3394 | 3.4144 | 2024-01-25 17:00 | 4.3249 | 5.1247 | 5.1247 | 5.1247 | 5.1247
2024-03-26 18:00 | 1.9434 | 2.4175 | 2.9208 | 2.9879 | 3.055 | 2024-01-25 18:00 | 3.6467 | 4.321 | 4.321 | 4.321 | 4.321
2024-03-26 19:00 | 1.81 | 2.2516 | 2.7203 | 2.7828 | 2.8453 | 2024-01-25 19:00 | 3.2961 | 3.9056 | 3.9056 | 3.9056 | 3.9056
2024-03-26 20:00 | 1.7338 | 2.1568 | 2.6058 | 2.6657 | 2.7255 | 2024-01-25 20:00 | 2.6254 | 3.1109 | 3.1109 | 3.1109 | 3.1109
2024-03-26 21:00 | 1.6957 | 2.1094 | 2.5485 | 2.6071 | 2.6656 | 2024-01-25 21:00 | 2.6674 | 3.1606 | 3.1606 | 3.1606 | 3.1606
2024-03-26 22:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2024-01-25 22:00 | 2.1987 | 2.6052 | 2.6052 | 2.6052 | 2.6052
2024-03-26 23:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2024-01-25 23:00 | 2.0196 | 2.393 | 2.393 | 2.393 | 2.393
2024-03-27 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-01-26 | 1.7833 | 2.1131 | 2.1131 | 2.1131 | 2.1131
2024-03-27 01:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-01-26 01:00 | 1.9891 | 2.3569 | 2.3569 | 2.3569 | 2.3569
2024-03-27 02:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-01-26 02:00 | 1.8824 | 2.2305 | 2.2305 | 2.2305 | 2.2305
2024-03-27 03:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-01-26 03:00 | 1.9472 | 2.3072 | 2.3072 | 2.3072 | 2.3072
2024-03-27 04:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-01-26 04:00 | 2.0196 | 2.393 | 2.393 | 2.393 | 2.393
2024-03-27 05:00 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2024-01-26 05:00 | 2.4654 | 2.9213 | 2.9213 | 2.9213 | 2.9213
2024-03-27 06:00 | 1.7719 | 2.2042 | 2.6631 | 2.7242 | 2.7854 | 2024-01-26 06:00 | 2.4845 | 2.9439 | 2.9439 | 2.9439 | 2.9439
2024-03-27 07:00 | 2.0196 | 2.5123 | 3.0353 | 3.1051 | 3.1748 | 2024-01-26 07:00 | 2.4921 | 2.9529 | 2.9529 | 2.9529 | 2.9529
2024-03-27 08:00 | 1.9434 | 2.4175 | 2.9208 | 2.9879 | 3.055 | 2024-01-26 08:00 | 2.4921 | 2.9529 | 2.9529 | 2.9529 | 2.9529
2024-03-27 09:00 | 2.1339 | 2.6545 | 3.2071 | 3.2808 | 3.3545 | 2024-01-26 09:00 | 2.4921 | 2.9529 | 2.9529 | 2.9529 | 2.9529
2024-03-27 10:00 | 1.9815 | 2.4649 | 2.9781 | 3.0465 | 3.1149 | 2024-01-26 10:00 | 2.4921 | 2.9529 | 2.9529 | 2.9529 | 2.9529
2024-03-27 11:00 | 1.81 | 2.2516 | 2.7203 | 2.7828 | 2.8453 | 2024-01-26 11:00 | 2.4921 | 2.9529 | 2.9529 | 2.9529 | 2.9529
2024-03-27 12:00 | 1.4099 | 1.7539 | 2.119 | 2.1677 | 2.2164 | 2024-01-26 12:00 | 2.4921 | 2.9529 | 2.9529 | 2.9529 | 2.9529
2024-03-27 13:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-01-26 13:00 | 2.4921 | 2.9529 | 2.9529 | 2.9529 | 2.9529
2024-03-27 14:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-01-26 14:00 | 2.4921 | 2.9529 | 2.9529 | 2.9529 | 2.9529
2024-03-27 15:00 | 1.4099 | 1.7539 | 2.119 | 2.1677 | 2.2164 | 2024-01-26 15:00 | 2.4921 | 2.9529 | 2.9529 | 2.9529 | 2.9529
2024-03-27 16:00 | 1.3908 | 1.7302 | 2.0904 | 2.1384 | 2.1864 | 2024-01-26 16:00 | 2.4921 | 2.9529 | 2.9529 | 2.9529 | 2.9529
2024-03-27 17:00 | 1.9053 | 2.3701 | 2.8635 | 2.9293 | 2.9951 | 2024-01-26 17:00 | 2.6254 | 3.1109 | 3.1109 | 3.1109 | 3.1109
2024-03-27 18:00 | 1.9434 | 2.4175 | 2.9208 | 2.9879 | 3.055 | 2024-01-26 18:00 | 2.5645 | 3.0387 | 3.0387 | 3.0387 | 3.0387
2024-03-27 19:00 | 1.7909 | 2.2279 | 2.6917 | 2.7535 | 2.8154 | 2024-01-26 19:00 | 2.4654 | 2.9213 | 2.9213 | 2.9213 | 2.9213
2024-03-27 20:00 | 1.7528 | 2.1805 | 2.6344 | 2.695 | 2.7555 | 2024-01-26 20:00 | 2.092 | 2.4788 | 2.4788 | 2.4788 | 2.4788
2024-03-27 21:00 | 1.7528 | 2.1805 | 2.6344 | 2.695 | 2.7555 | 2024-01-26 21:00 | 1.8443 | 2.1853 | 2.1853 | 2.1853 | 2.1853
2024-03-27 22:00 | 1.7338 | 2.1568 | 2.6058 | 2.6657 | 2.7255 | 2024-01-26 22:00 | 1.7757 | 2.1041 | 2.1041 | 2.1041 | 2.1041
2024-03-27 23:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2024-01-26 23:00 | 1.5776 | 1.8693 | 1.8693 | 1.8693 | 1.8693
2024-03-28 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-01-27 | 1.4975 | 1.7744 | 1.7744 | 1.7744 | 1.7744
2024-03-28 01:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-01-27 01:00 | 1.5242 | 1.8061 | 1.8061 | 1.8061 | 1.8061
2024-03-28 02:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-01-27 02:00 | 1.5852 | 1.8783 | 1.8783 | 1.8783 | 1.8783
2024-03-28 03:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-01-27 03:00 | 1.7109 | 2.0273 | 2.0273 | 2.0273 | 2.0273
2024-03-28 04:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-01-27 04:00 | 1.9472 | 2.3072 | 2.3072 | 2.3072 | 2.3072
2024-03-28 05:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2024-01-27 05:00 | 2.1301 | 2.524 | 2.524 | 2.524 | 2.524
2024-03-28 06:00 | 1.7909 | 2.2279 | 2.6917 | 2.7535 | 2.8154 | 2024-01-27 06:00 | 2.0386 | 2.4156 | 2.4156 | 2.4156 | 2.4156
2024-03-28 07:00 | 2.0958 | 2.6071 | 3.1499 | 3.2222 | 3.2946 | 2024-01-27 07:00 | 2.1567 | 2.5556 | 2.5556 | 2.5556 | 2.5556
2024-03-28 08:00 | 2.0196 | 2.5123 | 3.0353 | 3.1051 | 3.1748 | 2024-01-27 08:00 | 2.2673 | 2.6865 | 2.6865 | 2.6865 | 2.6865
2024-03-28 09:00 | 2.1148 | 2.6308 | 3.1785 | 3.2515 | 3.3245 | 2024-01-27 09:00 | 2.9989 | 3.5534 | 3.5534 | 3.5534 | 3.5534
2024-03-28 10:00 | 1.8862 | 2.3464 | 2.8349 | 2.9 | 2.9651 | 2024-01-27 10:00 | 2.6254 | 3.1109 | 3.1109 | 3.1109 | 3.1109
2024-03-28 11:00 | 2.0196 | 2.5123 | 3.0353 | 3.1051 | 3.1748 | 2024-01-27 11:00 | 2.5873 | 3.0658 | 3.0658 | 3.0658 | 3.0658
2024-03-28 12:00 | 2.0767 | 2.5834 | 3.1212 | 3.1929 | 3.2646 | 2024-01-27 12:00 | 2.6254 | 3.1109 | 3.1109 | 3.1109 | 3.1109
2024-03-28 13:00 | 2.172 | 2.7019 | 3.2644 | 3.3394 | 3.4144 | 2024-01-27 13:00 | 2.8045 | 3.3231 | 3.3231 | 3.3231 | 3.3231
2024-03-28 14:00 | 2.2291 | 2.773 | 3.3503 | 3.4273 | 3.5043 | 2024-01-27 14:00 | 2.7817 | 3.2961 | 3.2961 | 3.2961 | 3.2961
2024-03-28 15:00 | 2.172 | 2.7019 | 3.2644 | 3.3394 | 3.4144 | 2024-01-27 15:00 | 2.7664 | 3.278 | 3.278 | 3.278 | 3.278
2024-03-28 16:00 | 1.4289 | 1.7776 | 2.1476 | 2.197 | 2.2463 | 2024-01-27 16:00 | 3.0255 | 3.585 | 3.585 | 3.585 | 3.585
2024-03-28 17:00 | 2.0958 | 2.6071 | 3.1499 | 3.2222 | 3.2946 | 2024-01-27 17:00 | 2.7436 | 3.2509 | 3.2509 | 3.2509 | 3.2509
2024-03-28 18:00 | 1.8672 | 2.3227 | 2.8062 | 2.8707 | 2.9352 | 2024-01-27 18:00 | 2.6407 | 3.129 | 3.129 | 3.129 | 3.129
2024-03-28 19:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2024-01-27 19:00 | 2.3701 | 2.8084 | 2.8084 | 2.8084 | 2.8084
2024-03-28 20:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2024-01-27 20:00 | 2.2406 | 2.6549 | 2.6549 | 2.6549 | 2.6549
2024-03-28 21:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2024-01-27 21:00 | 2.0158 | 2.3885 | 2.3885 | 2.3885 | 2.3885
2024-03-28 22:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2024-01-27 22:00 | 1.9053 | 2.2576 | 2.2576 | 2.2576 | 2.2576
2024-03-28 23:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-01-27 23:00 | 1.6271 | 1.928 | 1.928 | 1.928 | 1.928
2024-03-29 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-01-28 | 1.5509 | 1.8377 | 1.8377 | 1.8377 | 1.8377
2024-03-29 01:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-01-28 01:00 | 1.5471 | 1.8331 | 1.8331 | 1.8331 | 1.8331
2024-03-29 02:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-01-28 02:00 | 1.5242 | 1.8061 | 1.8061 | 1.8061 | 1.8061
2024-03-29 03:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-01-28 03:00 | 1.589 | 1.8828 | 1.8828 | 1.8828 | 1.8828
2024-03-29 04:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2024-01-28 04:00 | 1.8329 | 2.1718 | 2.1718 | 2.1718 | 2.1718
2024-03-29 05:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-01-28 05:00 | 2.191 | 2.5962 | 2.5962 | 2.5962 | 2.5962
2024-03-29 06:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-01-28 06:00 | 2.0996 | 2.4878 | 2.4878 | 2.4878 | 2.4878
2024-03-29 07:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2024-01-28 07:00 | 2.0272 | 2.4021 | 2.4021 | 2.4021 | 2.4021
2024-03-29 08:00 | 1.086 | 1.351 | 1.6322 | 1.6697 | 1.7072 | 2024-01-28 08:00 | 2.2749 | 2.6955 | 2.6955 | 2.6955 | 2.6955
2024-03-29 09:00 | 0.019053 | 0.023701 | 0.028635 | 0.029293 | 0.029951 | 2024-01-28 09:00 | 2.2749 | 2.6955 | 2.6955 | 2.6955 | 2.6955
2024-03-29 10:00 | 0.81926 | 1.0191 | 1.2313 | 1.2596 | 1.2879 | 2024-01-28 10:00 | 2.7283 | 3.2328 | 3.2328 | 3.2328 | 3.2328
2024-03-29 11:00 | 1.9243 | 2.3938 | 2.8921 | 2.9586 | 3.025 | 2024-01-28 11:00 | 2.6407 | 3.129 | 3.129 | 3.129 | 3.129
2024-03-29 12:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2024-01-28 12:00 | 2.8465 | 3.3728 | 3.3728 | 3.3728 | 3.3728
2024-03-29 13:00 | 0.095263 | 0.1185 | 0.14318 | 0.14646 | 0.14975 | 2024-01-28 13:00 | 2.9722 | 3.5218 | 3.5218 | 3.5218 | 3.5218
2024-03-29 14:00 | 0.26674 | 0.33181 | 0.40089 | 0.4101 | 0.41931 | 2024-01-28 14:00 | 2.9798 | 3.5308 | 3.5308 | 3.5308 | 3.5308
2024-03-29 15:00 | 0.34295 | 0.42662 | 0.51543 | 0.52727 | 0.53912 | 2024-01-28 15:00 | 3.1399 | 3.7205 | 3.7205 | 3.7205 | 3.7205
2024-03-29 16:00 | 0.85737 | 1.0665 | 1.2886 | 1.3182 | 1.3478 | 2024-01-28 16:00 | 3.037 | 3.5986 | 3.5986 | 3.5986 | 3.5986
2024-03-29 17:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-01-28 17:00 | 3.037 | 3.5986 | 3.5986 | 3.5986 | 3.5986
2024-03-29 18:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-01-28 18:00 | 2.4921 | 2.9529 | 2.9529 | 2.9529 | 2.9529
2024-03-29 19:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2024-01-28 19:00 | 2.4654 | 2.9213 | 2.9213 | 2.9213 | 2.9213
2024-03-29 20:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2024-01-28 20:00 | 2.191 | 2.5962 | 2.5962 | 2.5962 | 2.5962
2024-03-29 21:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2024-01-28 21:00 | 2.111 | 2.5014 | 2.5014 | 2.5014 | 2.5014
2024-03-29 22:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-01-28 22:00 | 2.0005 | 2.3704 | 2.3704 | 2.3704 | 2.3704
2024-03-29 23:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2024-01-28 23:00 | 1.7528 | 2.077 | 2.077 | 2.077 | 2.077
2024-03-30 | 1.4289 | 1.7776 | 2.1476 | 2.197 | 2.2463 | 2024-01-29 | 1.6385 | 1.9415 | 1.9415 | 1.9415 | 1.9415
2024-03-30 01:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-01-29 01:00 | 1.65 | 1.9551 | 1.9551 | 1.9551 | 1.9551
2024-03-30 02:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-01-29 02:00 | 1.7452 | 2.0679 | 2.0679 | 2.0679 | 2.0679
2024-03-30 03:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-01-29 03:00 | 1.8405 | 2.1808 | 2.1808 | 2.1808 | 2.1808
2024-03-30 04:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-01-29 04:00 | 2.0196 | 2.393 | 2.393 | 2.393 | 2.393
2024-03-30 05:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-01-29 05:00 | 2.3015 | 2.7271 | 2.7271 | 2.7271 | 2.7271
2024-03-30 06:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-01-29 06:00 | 2.3968 | 2.84 | 2.84 | 2.84 | 2.84
2024-03-30 07:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-01-29 07:00 | 2.7969 | 3.3141 | 3.3141 | 3.3141 | 3.3141
2024-03-30 08:00 | 1.1813 | 1.4695 | 1.7754 | 1.8162 | 1.857 | 2024-01-29 08:00 | 3.0179 | 3.576 | 3.576 | 3.576 | 3.576
2024-03-30 09:00 | 1.1241 | 1.3984 | 1.6895 | 1.7283 | 1.7671 | 2024-01-29 09:00 | 3.2809 | 3.8875 | 3.8875 | 3.8875 | 3.8875
2024-03-30 10:00 | 0.97168 | 1.2087 | 1.4604 | 1.4939 | 1.5275 | 2024-01-29 10:00 | 3.6581 | 4.3345 | 4.3345 | 4.3345 | 4.3345
2024-03-30 11:00 | 1.0288 | 1.2798 | 1.5463 | 1.5818 | 1.6173 | 2024-01-29 11:00 | 3.6733 | 4.3526 | 4.3526 | 4.3526 | 4.3526
2024-03-30 12:00 | 0.038105 | 0.047402 | 0.05727 | 0.058586 | 0.059902 | 2024-01-29 12:00 | 3.9629 | 4.6957 | 4.6957 | 4.6957 | 4.6957
2024-03-30 13:00 | 0.095263 | 0.1185 | 0.14318 | 0.14646 | 0.14975 | 2024-01-29 13:00 | 3.8067 | 4.5106 | 4.5106 | 4.5106 | 4.5106
2024-03-30 14:00 | 0.13337 | 0.16591 | 0.20045 | 0.20505 | 0.20966 | 2024-01-29 14:00 | 4.0734 | 4.8267 | 4.8267 | 4.8267 | 4.8267
2024-03-30 15:00 | 0.99073 | 1.2324 | 1.489 | 1.5232 | 1.5574 | 2024-01-29 15:00 | 4.1573 | 4.926 | 4.926 | 4.926 | 4.926
2024-03-30 16:00 | 1.3527 | 1.6828 | 2.0331 | 2.0798 | 2.1265 | 2024-01-29 16:00 | 4.1954 | 4.9712 | 4.9712 | 4.9712 | 4.9712
2024-03-30 17:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2024-01-29 17:00 | 3.8258 | 4.5332 | 4.5332 | 4.5332 | 4.5332
2024-03-30 18:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-01-29 18:00 | 3.5704 | 4.2307 | 4.2307 | 4.2307 | 4.2307
2024-03-30 19:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2024-01-29 19:00 | 3.2618 | 3.865 | 3.865 | 3.865 | 3.865
2024-03-30 20:00 | 1.6957 | 2.1094 | 2.5485 | 2.6071 | 2.6656 | 2024-01-29 20:00 | 2.7931 | 3.3096 | 3.3096 | 3.3096 | 3.3096
2024-03-30 21:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2024-01-29 21:00 | 2.614 | 3.0974 | 3.0974 | 3.0974 | 3.0974
2024-03-30 22:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-01-29 22:00 | 2.0501 | 2.4291 | 2.4291 | 2.4291 | 2.4291
2024-03-30 23:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-01-29 23:00 | 2.0234 | 2.3975 | 2.3975 | 2.3975 | 2.3975
2024-03-31 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2024-01-30 | 1.7071 | 2.0228 | 2.0228 | 2.0228 | 2.0228
2024-03-31 01:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-01-30 01:00 | 1.7605 | 2.086 | 2.086 | 2.086 | 2.086
2024-03-31 02:00 | 1.4289 | 1.7776 | 2.1476 | 2.197 | 2.2463 | 2024-01-30 02:00 | 1.8062 | 2.1402 | 2.1402 | 2.1402 | 2.1402
2024-03-31 03:00 | 1.4289 | 1.7776 | 2.1476 | 2.197 | 2.2463 | 2024-01-30 03:00 | 1.7909 | 2.1221 | 2.1221 | 2.1221 | 2.1221
2024-03-31 04:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-01-30 04:00 | 1.9472 | 2.3072 | 2.3072 | 2.3072 | 2.3072
2024-03-31 05:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-01-30 05:00 | 2.2787 | 2.7001 | 2.7001 | 2.7001 | 2.7001
2024-03-31 06:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-01-30 06:00 | 2.2977 | 2.7226 | 2.7226 | 2.7226 | 2.7226
2024-03-31 07:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-01-30 07:00 | 2.7512 | 3.2599 | 3.2599 | 3.2599 | 3.2599
2024-03-31 08:00 | 1.2384 | 1.5406 | 1.8613 | 1.904 | 1.9468 | 2024-01-30 08:00 | 3.4104 | 4.041 | 4.041 | 4.041 | 4.041
2024-03-31 09:00 | 0 | 0 | 0 | 0 | 0 | 2024-01-30 09:00 | 3.4218 | 4.0546 | 4.0546 | 4.0546 | 4.0546
2024-03-31 10:00 | 0.95263 | 1.185 | 1.4318 | 1.4646 | 1.4975 | 2024-01-30 10:00 | 3.5323 | 4.1855 | 4.1855 | 4.1855 | 4.1855
2024-03-31 11:00 | 0.15242 | 0.18961 | 0.22908 | 0.23434 | 0.23961 | 2024-01-30 11:00 | 3.8867 | 4.6054 | 4.6054 | 4.6054 | 4.6054
2024-03-31 12:00 | 0.83831 | 1.0428 | 1.2599 | 1.2889 | 1.3178 | 2024-01-30 12:00 | 4.043 | 4.7906 | 4.7906 | 4.7906 | 4.7906
2024-03-31 13:00 | 0.17147 | 0.21331 | 0.25772 | 0.26364 | 0.26956 | 2024-01-30 13:00 | 4.584 | 5.4317 | 5.4317 | 5.4317 | 5.4317
2024-03-31 14:00 | 0.20958 | 0.26071 | 0.31499 | 0.32222 | 0.32946 | 2024-01-30 14:00 | 4.2602 | 5.0479 | 5.0479 | 5.0479 | 5.0479
2024-03-31 15:00 | 0.30484 | 0.37921 | 0.45816 | 0.46869 | 0.47921 | 2024-01-30 15:00 | 4.222 | 5.0028 | 5.0028 | 5.0028 | 5.0028
2024-03-31 16:00 | 0.53347 | 0.66362 | 0.80178 | 0.8202 | 0.83862 | 2024-01-30 16:00 | 4.424 | 5.2421 | 5.2421 | 5.2421 | 5.2421
2024-03-31 17:00 | 1.4289 | 1.7776 | 2.1476 | 2.197 | 2.2463 | 2024-01-30 17:00 | 3.9363 | 4.6641 | 4.6641 | 4.6641 | 4.6641
2024-03-31 18:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-01-30 18:00 | 3.7229 | 4.4113 | 4.4113 | 4.4113 | 4.4113
2024-03-31 19:00 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2024-01-30 19:00 | 3.1551 | 3.7385 | 3.7385 | 3.7385 | 3.7385
2024-03-31 20:00 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2024-01-30 20:00 | 2.7436 | 3.2509 | 3.2509 | 3.2509 | 3.2509
2024-03-31 21:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2024-01-30 21:00 | 2.5683 | 3.0432 | 3.0432 | 3.0432 | 3.0432
2024-03-31 22:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2024-01-30 22:00 | 2.1339 | 2.5285 | 2.5285 | 2.5285 | 2.5285
2024-03-31 23:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-01-30 23:00 | 2.0577 | 2.4382 | 2.4382 | 2.4382 | 2.4382
2024-04-01 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-01-31 | 1.7795 | 2.1086 | 2.1086 | 2.1086 | 2.1086
2024-04-01 01:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-01-31 01:00 | 1.8786 | 2.226 | 2.226 | 2.226 | 2.226
2024-04-01 02:00 | 1.4289 | 1.5331 | 1.9032 | 2.0019 | 2.1006 | 2024-01-31 02:00 | 1.9129 | 2.2666 | 2.2666 | 2.2666 | 2.2666
2024-04-01 03:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-01-31 03:00 | 2.0234 | 2.3975 | 2.3975 | 2.3975 | 2.3975
2024-04-01 04:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-01-31 04:00 | 2.1529 | 2.5511 | 2.5511 | 2.5511 | 2.5511
2024-04-01 05:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-01-31 05:00 | 2.4578 | 2.9123 | 2.9123 | 2.9123 | 2.9123
2024-04-01 06:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-01-31 06:00 | 2.6407 | 3.129 | 3.129 | 3.129 | 3.129
2024-04-01 07:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-01-31 07:00 | 3.3609 | 3.9824 | 3.9824 | 3.9824 | 3.9824
2024-04-01 08:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-01-31 08:00 | 4.0963 | 4.8538 | 4.8538 | 4.8538 | 4.8538
2024-04-01 09:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-01-31 09:00 | 4.1916 | 4.9667 | 4.9667 | 4.9667 | 4.9667
2024-04-01 10:00 | 1.0098 | 1.0834 | 1.3449 | 1.4147 | 1.4844 | 2024-01-31 10:00 | 4.1954 | 4.9712 | 4.9712 | 4.9712 | 4.9712
2024-04-01 11:00 | 0.74305 | 0.79723 | 0.98967 | 1.041 | 1.0923 | 2024-01-31 11:00 | 4.1649 | 4.935 | 4.935 | 4.935 | 4.935
2024-04-01 12:00 | 0.07621 | 0.081768 | 0.1015 | 0.10677 | 0.11203 | 2024-01-31 12:00 | 4.3173 | 5.1157 | 5.1157 | 5.1157 | 5.1157
2024-04-01 13:00 | 0.19053 | 0.20442 | 0.25376 | 0.26692 | 0.28008 | 2024-01-31 13:00 | 4.1801 | 4.9531 | 4.9531 | 4.9531 | 4.9531
2024-04-01 14:00 | 0.38105 | 0.40884 | 0.50752 | 0.53384 | 0.56015 | 2024-01-31 14:00 | 4.4926 | 5.3233 | 5.3233 | 5.3233 | 5.3233
2024-04-01 15:00 | 0.53347 | 0.57237 | 0.71053 | 0.74737 | 0.78422 | 2024-01-31 15:00 | 4.4583 | 5.2827 | 5.2827 | 5.2827 | 5.2827
2024-04-01 16:00 | 1.0288 | 1.1039 | 1.3703 | 1.4414 | 1.5124 | 2024-01-31 16:00 | 4.203 | 4.9802 | 4.9802 | 4.9802 | 4.9802
2024-04-01 17:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-01-31 17:00 | 3.8105 | 4.5151 | 4.5151 | 4.5151 | 4.5151
2024-04-01 18:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-01-31 18:00 | 3.6733 | 4.3526 | 4.3526 | 4.3526 | 4.3526
2024-04-01 19:00 | 1.7338 | 1.8602 | 2.3092 | 2.429 | 2.5487 | 2024-01-31 19:00 | 2.9836 | 3.5354 | 3.5354 | 3.5354 | 3.5354
2024-04-01 20:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-01-31 20:00 | 2.7779 | 3.2915 | 3.2915 | 3.2915 | 3.2915
2024-04-01 21:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-01-31 21:00 | 2.5378 | 3.0071 | 3.0071 | 3.0071 | 3.0071
2024-04-01 22:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-01-31 22:00 | 2.0386 | 2.4156 | 2.4156 | 2.4156 | 2.4156
2024-04-01 23:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-01-31 23:00 | 2.1072 | 2.4969 | 2.4969 | 2.4969 | 2.4969
2024-04-02 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-02-01 | 1.8557 | 2.1989 | 2.1989 | 2.1989 | 2.1989
2024-04-02 01:00 | 1.448 | 1.5536 | 1.9286 | 2.0286 | 2.1286 | 2024-02-01 01:00 | 1.8862 | 2.235 | 2.235 | 2.235 | 2.235
2024-04-02 02:00 | 1.448 | 1.5536 | 1.9286 | 2.0286 | 2.1286 | 2024-02-01 02:00 | 1.7376 | 2.0589 | 2.0589 | 2.0589 | 2.0589
2024-04-02 03:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-02-01 03:00 | 1.8519 | 2.1944 | 2.1944 | 2.1944 | 2.1944
2024-04-02 04:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-02-01 04:00 | 2.0158 | 2.3885 | 2.3885 | 2.3885 | 2.3885
2024-04-02 05:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-02-01 05:00 | 2.3168 | 2.7452 | 2.7452 | 2.7452 | 2.7452
2024-04-02 06:00 | 1.9053 | 2.0442 | 2.5376 | 2.6692 | 2.8008 | 2024-02-01 06:00 | 2.595 | 3.0748 | 3.0748 | 3.0748 | 3.0748
2024-04-02 07:00 | 2.2101 | 2.3713 | 2.9436 | 3.0963 | 3.2489 | 2024-02-01 07:00 | 2.9989 | 3.5534 | 3.5534 | 3.5534 | 3.5534
2024-04-02 08:00 | 2.5721 | 2.7597 | 3.4258 | 3.6034 | 3.781 | 2024-02-01 08:00 | 3.7305 | 4.4203 | 4.4203 | 4.4203 | 4.4203
2024-04-02 09:00 | 2.4959 | 2.6779 | 3.3243 | 3.4966 | 3.669 | 2024-02-01 09:00 | 3.6086 | 4.2758 | 4.2758 | 4.2758 | 4.2758
2024-04-02 10:00 | 2.4197 | 2.5961 | 3.2228 | 3.3899 | 3.557 | 2024-02-01 10:00 | 3.3075 | 3.9191 | 3.9191 | 3.9191 | 3.9191
2024-04-02 11:00 | 2.3625 | 2.5348 | 3.1466 | 3.3098 | 3.473 | 2024-02-01 11:00 | 3.6581 | 4.3345 | 4.3345 | 4.3345 | 4.3345
2024-04-02 12:00 | 2.172 | 2.3304 | 2.8929 | 3.0429 | 3.1929 | 2024-02-01 12:00 | 3.6581 | 4.3345 | 4.3345 | 4.3345 | 4.3345
2024-04-02 13:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-02-01 13:00 | 3.902 | 4.6235 | 4.6235 | 4.6235 | 4.6235
2024-04-02 14:00 | 1.9243 | 2.0646 | 2.563 | 2.6959 | 2.8288 | 2024-02-01 14:00 | 4.123 | 4.8854 | 4.8854 | 4.8854 | 4.8854
2024-04-02 15:00 | 0.80021 | 0.85856 | 1.0658 | 1.1211 | 1.1763 | 2024-02-01 15:00 | 3.9972 | 4.7364 | 4.7364 | 4.7364 | 4.7364
2024-04-02 16:00 | 0.7621 | 0.81768 | 1.015 | 1.0677 | 1.1203 | 2024-02-01 16:00 | 4.1496 | 4.917 | 4.917 | 4.917 | 4.917
2024-04-02 17:00 | 2.0386 | 2.1873 | 2.7152 | 2.856 | 2.9968 | 2024-02-01 17:00 | 4.0391 | 4.786 | 4.786 | 4.786 | 4.786
2024-04-02 18:00 | 1.81 | 1.942 | 2.4107 | 2.5357 | 2.6607 | 2024-02-01 18:00 | 3.8029 | 4.5061 | 4.5061 | 4.5061 | 4.5061
2024-04-02 19:00 | 1.7528 | 1.8807 | 2.3346 | 2.4557 | 2.5767 | 2024-02-01 19:00 | 3.3456 | 3.9643 | 3.9643 | 3.9643 | 3.9643
2024-04-02 20:00 | 1.7528 | 1.8807 | 2.3346 | 2.4557 | 2.5767 | 2024-02-01 20:00 | 2.7283 | 3.2328 | 3.2328 | 3.2328 | 3.2328
2024-04-02 21:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-02-01 21:00 | 2.3015 | 2.7271 | 2.7271 | 2.7271 | 2.7271
2024-04-02 22:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-02-01 22:00 | 2.1072 | 2.4969 | 2.4969 | 2.4969 | 2.4969
2024-04-02 23:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-02-01 23:00 | 1.9434 | 2.3027 | 2.3027 | 2.3027 | 2.3027
2024-04-03 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-02-02 | 1.7681 | 2.095 | 2.095 | 2.095 | 2.095
2024-04-03 01:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-02-02 01:00 | 1.7986 | 2.1311 | 2.1311 | 2.1311 | 2.1311
2024-04-03 02:00 | 1.448 | 1.5536 | 1.9286 | 2.0286 | 2.1286 | 2024-02-02 02:00 | 1.6842 | 1.9957 | 1.9957 | 1.9957 | 1.9957
2024-04-03 03:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-02-02 03:00 | 1.8862 | 2.235 | 2.235 | 2.235 | 2.235
2024-04-03 04:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-02-02 04:00 | 2.031 | 2.4066 | 2.4066 | 2.4066 | 2.4066
2024-04-03 05:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-02-02 05:00 | 2.2939 | 2.7181 | 2.7181 | 2.7181 | 2.7181
2024-04-03 06:00 | 1.7719 | 1.9011 | 2.36 | 2.4823 | 2.6047 | 2024-02-02 06:00 | 2.3511 | 2.7858 | 2.7858 | 2.7858 | 2.7858
2024-04-03 07:00 | 2.0767 | 2.2282 | 2.766 | 2.9094 | 3.0528 | 2024-02-02 07:00 | 2.6064 | 3.0884 | 3.0884 | 3.0884 | 3.0884
2024-04-03 08:00 | 2.0386 | 2.1873 | 2.7152 | 2.856 | 2.9968 | 2024-02-02 08:00 | 3.2389 | 3.8379 | 3.8379 | 3.8379 | 3.8379
2024-04-03 09:00 | 0.87642 | 0.94033 | 1.1673 | 1.2278 | 1.2884 | 2024-02-02 09:00 | 3.2542 | 3.8559 | 3.8559 | 3.8559 | 3.8559
2024-04-03 10:00 | 0.78115 | 0.83812 | 1.0404 | 1.0944 | 1.1483 | 2024-02-02 10:00 | 3.338 | 3.9553 | 3.9553 | 3.9553 | 3.9553
2024-04-03 11:00 | 1.2765 | 1.3696 | 1.7002 | 1.7884 | 1.8765 | 2024-02-02 11:00 | 3.4142 | 4.0456 | 4.0456 | 4.0456 | 4.0456
2024-04-03 12:00 | 2.0767 | 2.2282 | 2.766 | 2.9094 | 3.0528 | 2024-02-02 12:00 | 3.78 | 4.479 | 4.479 | 4.479 | 4.479
2024-04-03 13:00 | 1.9624 | 2.1055 | 2.6137 | 2.7493 | 2.8848 | 2024-02-02 13:00 | 3.7915 | 4.4926 | 4.4926 | 4.4926 | 4.4926
2024-04-03 14:00 | 2.2863 | 2.453 | 3.0451 | 3.203 | 3.3609 | 2024-02-02 14:00 | 3.7229 | 4.4113 | 4.4113 | 4.4113 | 4.4113
2024-04-03 15:00 | 1.2575 | 1.3492 | 1.6748 | 1.7617 | 1.8485 | 2024-02-02 15:00 | 3.8562 | 4.5693 | 4.5693 | 4.5693 | 4.5693
2024-04-03 16:00 | 2.1339 | 2.2895 | 2.8421 | 2.9895 | 3.1369 | 2024-02-02 16:00 | 4.1611 | 4.9305 | 4.9305 | 4.9305 | 4.9305
2024-04-03 17:00 | 1.9434 | 2.0851 | 2.5884 | 2.7226 | 2.8568 | 2024-02-02 17:00 | 4.0734 | 4.8267 | 4.8267 | 4.8267 | 4.8267
2024-04-03 18:00 | 1.9053 | 2.0442 | 2.5376 | 2.6692 | 2.8008 | 2024-02-02 18:00 | 3.8753 | 4.5919 | 4.5919 | 4.5919 | 4.5919
2024-04-03 19:00 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 2024-02-02 19:00 | 3.5895 | 4.2533 | 4.2533 | 4.2533 | 4.2533
2024-04-03 20:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-02-02 20:00 | 2.9493 | 3.4947 | 3.4947 | 3.4947 | 3.4947
2024-04-03 21:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-02-02 21:00 | 2.4159 | 2.8626 | 2.8626 | 2.8626 | 2.8626
2024-04-03 22:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-02-02 22:00 | 2.191 | 2.5962 | 2.5962 | 2.5962 | 2.5962
2024-04-03 23:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-02-02 23:00 | 1.8405 | 2.1808 | 2.1808 | 2.1808 | 2.1808
2024-04-04 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-02-03 | 1.7185 | 2.0363 | 2.0363 | 2.0363 | 2.0363
2024-04-04 01:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-02-03 01:00 | 1.7262 | 2.0454 | 2.0454 | 2.0454 | 2.0454
2024-04-04 02:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-02-03 02:00 | 1.7757 | 2.1041 | 2.1041 | 2.1041 | 2.1041
2024-04-04 03:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-02-03 03:00 | 1.8176 | 2.1537 | 2.1537 | 2.1537 | 2.1537
2024-04-04 04:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-02-03 04:00 | 1.9586 | 2.3208 | 2.3208 | 2.3208 | 2.3208
2024-04-04 05:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-02-03 05:00 | 2.2901 | 2.7136 | 2.7136 | 2.7136 | 2.7136
2024-04-04 06:00 | 1.8862 | 2.0237 | 2.5122 | 2.6425 | 2.7728 | 2024-02-03 06:00 | 2.313 | 2.7407 | 2.7407 | 2.7407 | 2.7407
2024-04-04 07:00 | 2.1339 | 2.2895 | 2.8421 | 2.9895 | 3.1369 | 2024-02-03 07:00 | 2.7093 | 3.2103 | 3.2103 | 3.2103 | 3.2103
2024-04-04 08:00 | 2.1339 | 2.2895 | 2.8421 | 2.9895 | 3.1369 | 2024-02-03 08:00 | 3.2008 | 3.7927 | 3.7927 | 3.7927 | 3.7927
2024-04-04 09:00 | 2.2291 | 2.3917 | 2.969 | 3.123 | 3.2769 | 2024-02-03 09:00 | 3.1246 | 3.7024 | 3.7024 | 3.7024 | 3.7024
2024-04-04 10:00 | 2.2673 | 2.4326 | 3.0198 | 3.1763 | 3.3329 | 2024-02-03 10:00 | 2.8236 | 3.3457 | 3.3457 | 3.3457 | 3.3457
2024-04-04 11:00 | 1.81 | 1.942 | 2.4107 | 2.5357 | 2.6607 | 2024-02-03 11:00 | 3.1703 | 3.7566 | 3.7566 | 3.7566 | 3.7566
2024-04-04 12:00 | 1.9434 | 2.0851 | 2.5884 | 2.7226 | 2.8568 | 2024-02-03 12:00 | 3.2618 | 3.865 | 3.865 | 3.865 | 3.865
2024-04-04 13:00 | 1.81 | 1.942 | 2.4107 | 2.5357 | 2.6607 | 2024-02-03 13:00 | 3.5209 | 4.172 | 4.172 | 4.172 | 4.172
2024-04-04 14:00 | 1.7909 | 1.9215 | 2.3854 | 2.509 | 2.6327 | 2024-02-03 14:00 | 3.4257 | 4.0591 | 4.0591 | 4.0591 | 4.0591
2024-04-04 15:00 | 2.172 | 2.3304 | 2.8929 | 3.0429 | 3.1929 | 2024-02-03 15:00 | 3.4104 | 4.041 | 4.041 | 4.041 | 4.041
2024-04-04 16:00 | 2.0005 | 2.1464 | 2.6645 | 2.8026 | 2.9408 | 2024-02-03 16:00 | 3.5057 | 4.1539 | 4.1539 | 4.1539 | 4.1539
2024-04-04 17:00 | 2.0005 | 2.1464 | 2.6645 | 2.8026 | 2.9408 | 2024-02-03 17:00 | 3.3342 | 3.9507 | 3.9507 | 3.9507 | 3.9507
2024-04-04 18:00 | 1.7909 | 1.9215 | 2.3854 | 2.509 | 2.6327 | 2024-02-03 18:00 | 3.1208 | 3.6979 | 3.6979 | 3.6979 | 3.6979
2024-04-04 19:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-02-03 19:00 | 2.7283 | 3.2328 | 3.2328 | 3.2328 | 3.2328
2024-04-04 20:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-02-03 20:00 | 2.5988 | 3.0793 | 3.0793 | 3.0793 | 3.0793
2024-04-04 21:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-02-03 21:00 | 2.3663 | 2.8039 | 2.8039 | 2.8039 | 2.8039
2024-04-04 22:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-02-03 22:00 | 2.2711 | 2.691 | 2.691 | 2.691 | 2.691
2024-04-04 23:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-02-03 23:00 | 1.9434 | 2.3027 | 2.3027 | 2.3027 | 2.3027
2024-04-05 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-02-04 | 1.9548 | 2.3163 | 2.3163 | 2.3163 | 2.3163
2024-04-05 01:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-02-04 01:00 | 1.9281 | 2.2847 | 2.2847 | 2.2847 | 2.2847
2024-04-05 02:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-02-04 02:00 | 1.8976 | 2.2485 | 2.2485 | 2.2485 | 2.2485
2024-04-05 03:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-02-04 03:00 | 1.9472 | 2.3072 | 2.3072 | 2.3072 | 2.3072
2024-04-05 04:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-02-04 04:00 | 2.0158 | 2.3885 | 2.3885 | 2.3885 | 2.3885
2024-04-05 05:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-02-04 05:00 | 2.1529 | 2.5511 | 2.5511 | 2.5511 | 2.5511
2024-04-05 06:00 | 1.9053 | 2.0442 | 2.5376 | 2.6692 | 2.8008 | 2024-02-04 06:00 | 2.313 | 2.7407 | 2.7407 | 2.7407 | 2.7407
2024-04-05 07:00 | 2.0577 | 2.2077 | 2.7406 | 2.8827 | 3.0248 | 2024-02-04 07:00 | 2.5683 | 3.0432 | 3.0432 | 3.0432 | 3.0432
2024-04-05 08:00 | 2.2482 | 2.4121 | 2.9944 | 3.1496 | 3.3049 | 2024-02-04 08:00 | 2.9265 | 3.4676 | 3.4676 | 3.4676 | 3.4676
2024-04-05 09:00 | 2.0958 | 2.2486 | 2.7914 | 2.9361 | 3.0808 | 2024-02-04 09:00 | 3.1475 | 3.7295 | 3.7295 | 3.7295 | 3.7295
2024-04-05 10:00 | 2.191 | 2.3508 | 2.9183 | 3.0696 | 3.2209 | 2024-02-04 10:00 | 3.2999 | 3.9101 | 3.9101 | 3.9101 | 3.9101
2024-04-05 11:00 | 2.1339 | 2.2895 | 2.8421 | 2.9895 | 3.1369 | 2024-02-04 11:00 | 3.6162 | 4.2849 | 4.2849 | 4.2849 | 4.2849
2024-04-05 12:00 | 2.1339 | 2.2895 | 2.8421 | 2.9895 | 3.1369 | 2024-02-04 12:00 | 3.8029 | 4.5061 | 4.5061 | 4.5061 | 4.5061
2024-04-05 13:00 | 2.1148 | 2.2691 | 2.8167 | 2.9628 | 3.1089 | 2024-02-04 13:00 | 3.9782 | 4.7138 | 4.7138 | 4.7138 | 4.7138
2024-04-05 14:00 | 2.0196 | 2.1668 | 2.6899 | 2.8293 | 2.9688 | 2024-02-04 14:00 | 3.761 | 4.4564 | 4.4564 | 4.4564 | 4.4564
2024-04-05 15:00 | 1.9815 | 2.126 | 2.6391 | 2.776 | 2.9128 | 2024-02-04 15:00 | 3.8067 | 4.5106 | 4.5106 | 4.5106 | 4.5106
2024-04-05 16:00 | 1.9624 | 2.1055 | 2.6137 | 2.7493 | 2.8848 | 2024-02-04 16:00 | 3.7305 | 4.4203 | 4.4203 | 4.4203 | 4.4203
2024-04-05 17:00 | 1.9053 | 2.0442 | 2.5376 | 2.6692 | 2.8008 | 2024-02-04 17:00 | 3.5857 | 4.2487 | 4.2487 | 4.2487 | 4.2487
2024-04-05 18:00 | 1.7338 | 1.8602 | 2.3092 | 2.429 | 2.5487 | 2024-02-04 18:00 | 3.037 | 3.5986 | 3.5986 | 3.5986 | 3.5986
2024-04-05 19:00 | 1.7338 | 1.8602 | 2.3092 | 2.429 | 2.5487 | 2024-02-04 19:00 | 2.9303 | 3.4721 | 3.4721 | 3.4721 | 3.4721
2024-04-05 20:00 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 2024-02-04 20:00 | 2.4806 | 2.9394 | 2.9394 | 2.9394 | 2.9394
2024-04-05 21:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-02-04 21:00 | 2.4883 | 2.9484 | 2.9484 | 2.9484 | 2.9484
2024-04-05 22:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-02-04 22:00 | 2.1872 | 2.5917 | 2.5917 | 2.5917 | 2.5917
2024-04-05 23:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-02-04 23:00 | 2.0767 | 2.4608 | 2.4608 | 2.4608 | 2.4608
2024-04-06 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-02-05 | 2.0081 | 2.3795 | 2.3795 | 2.3795 | 2.3795
2024-04-06 01:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-02-05 01:00 | 2.0843 | 2.4698 | 2.4698 | 2.4698 | 2.4698
2024-04-06 02:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-02-05 02:00 | 1.9548 | 2.3163 | 2.3163 | 2.3163 | 2.3163
2024-04-06 03:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-02-05 03:00 | 2.0424 | 2.4201 | 2.4201 | 2.4201 | 2.4201
2024-04-06 04:00 | 1.448 | 1.5536 | 1.9286 | 2.0286 | 2.1286 | 2024-02-05 04:00 | 2.252 | 2.6684 | 2.6684 | 2.6684 | 2.6684
2024-04-06 05:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-02-05 05:00 | 2.8884 | 3.4225 | 3.4225 | 3.4225 | 3.4225
2024-04-06 06:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-02-05 06:00 | 3.3456 | 3.9643 | 3.9643 | 3.9643 | 3.9643
2024-04-06 07:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-02-05 07:00 | 3.7191 | 4.4068 | 4.4068 | 4.4068 | 4.4068
2024-04-06 08:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-02-05 08:00 | 4.1154 | 4.8763 | 4.8763 | 4.8763 | 4.8763
2024-04-06 09:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-02-05 09:00 | 4.4659 | 5.2917 | 5.2917 | 5.2917 | 5.2917
2024-04-06 10:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-02-05 10:00 | 4.363 | 5.1698 | 5.1698 | 5.1698 | 5.1698
2024-04-06 11:00 | 1.4099 | 1.5127 | 1.8778 | 1.9752 | 2.0726 | 2024-02-05 11:00 | 4.4964 | 5.3279 | 5.3279 | 5.3279 | 5.3279
2024-04-06 12:00 | 1.2384 | 1.3287 | 1.6494 | 1.735 | 1.8205 | 2024-02-05 12:00 | 4.4392 | 5.2601 | 5.2601 | 5.2601 | 5.2601
2024-04-06 13:00 | 0.60968 | 0.65414 | 0.81204 | 0.85414 | 0.89625 | 2024-02-05 13:00 | 4.4659 | 5.2917 | 5.2917 | 5.2917 | 5.2917
2024-04-06 14:00 | 0.60968 | 0.65414 | 0.81204 | 0.85414 | 0.89625 | 2024-02-05 14:00 | 4.2944 | 5.0886 | 5.0886 | 5.0886 | 5.0886
2024-04-06 15:00 | 0.66684 | 0.71547 | 0.88816 | 0.93422 | 0.98027 | 2024-02-05 15:00 | 4.2106 | 4.9892 | 4.9892 | 4.9892 | 4.9892
2024-04-06 16:00 | 0.85737 | 0.91989 | 1.1419 | 1.2011 | 1.2603 | 2024-02-05 16:00 | 4.2259 | 5.0073 | 5.0073 | 5.0073 | 5.0073
2024-04-06 17:00 | 1.2575 | 1.3492 | 1.6748 | 1.7617 | 1.8485 | 2024-02-05 17:00 | 4.0163 | 4.759 | 4.759 | 4.759 | 4.759
2024-04-06 18:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-02-05 18:00 | 3.3875 | 4.014 | 4.014 | 4.014 | 4.014
2024-04-06 19:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-02-05 19:00 | 2.8807 | 3.4134 | 3.4134 | 3.4134 | 3.4134
2024-04-06 20:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-02-05 20:00 | 2.7779 | 3.2915 | 3.2915 | 3.2915 | 3.2915
2024-04-06 21:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-02-05 21:00 | 2.5264 | 2.9935 | 2.9935 | 2.9935 | 2.9935
2024-04-06 22:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-02-05 22:00 | 2.0158 | 2.3885 | 2.3885 | 2.3885 | 2.3885
2024-04-06 23:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-02-05 23:00 | 1.9396 | 2.2982 | 2.2982 | 2.2982 | 2.2982
2024-04-07 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-02-06 | 1.7681 | 2.095 | 2.095 | 2.095 | 2.095
2024-04-07 01:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-02-06 01:00 | 1.829 | 2.1673 | 2.1673 | 2.1673 | 2.1673
2024-04-07 02:00 | 1.4099 | 1.5127 | 1.8778 | 1.9752 | 2.0726 | 2024-02-06 02:00 | 1.8519 | 2.1944 | 2.1944 | 2.1944 | 2.1944
2024-04-07 03:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-02-06 03:00 | 1.8367 | 2.1763 | 2.1763 | 2.1763 | 2.1763
2024-04-07 04:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-02-06 04:00 | 2.0539 | 2.4337 | 2.4337 | 2.4337 | 2.4337
2024-04-07 05:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-02-06 05:00 | 2.5645 | 3.0387 | 3.0387 | 3.0387 | 3.0387
2024-04-07 06:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-02-06 06:00 | 2.8998 | 3.436 | 3.436 | 3.436 | 3.436
2024-04-07 07:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-02-06 07:00 | 3.5323 | 4.1855 | 4.1855 | 4.1855 | 4.1855
2024-04-07 08:00 | 1.448 | 1.5536 | 1.9286 | 2.0286 | 2.1286 | 2024-02-06 08:00 | 3.9363 | 4.6641 | 4.6641 | 4.6641 | 4.6641
2024-04-07 09:00 | 1.105 | 1.1856 | 1.4718 | 1.5481 | 1.6244 | 2024-02-06 09:00 | 4.123 | 4.8854 | 4.8854 | 4.8854 | 4.8854
2024-04-07 10:00 | 0.59063 | 0.6337 | 0.78666 | 0.82745 | 0.86824 | 2024-02-06 10:00 | 3.9363 | 4.6641 | 4.6641 | 4.6641 | 4.6641
2024-04-07 11:00 | 0.55252 | 0.59282 | 0.73591 | 0.77407 | 0.81222 | 2024-02-06 11:00 | 4.2182 | 4.9983 | 4.9983 | 4.9983 | 4.9983
2024-04-07 12:00 | 0.53347 | 0.57237 | 0.71053 | 0.74737 | 0.78422 | 2024-02-06 12:00 | 4.2792 | 5.0705 | 5.0705 | 5.0705 | 5.0705
2024-04-07 13:00 | 0.32389 | 0.34751 | 0.43139 | 0.45376 | 0.47613 | 2024-02-06 13:00 | 4.6107 | 5.4633 | 5.4633 | 5.4633 | 5.4633
2024-04-07 14:00 | 0.7621 | 0.81768 | 1.015 | 1.0677 | 1.1203 | 2024-02-06 14:00 | 4.7593 | 5.6394 | 5.6394 | 5.6394 | 5.6394
2024-04-07 15:00 | 0.85737 | 0.91989 | 1.1419 | 1.2011 | 1.2603 | 2024-02-06 15:00 | 4.2563 | 5.0434 | 5.0434 | 5.0434 | 5.0434
2024-04-07 16:00 | 1.0479 | 1.1243 | 1.3957 | 1.4681 | 1.5404 | 2024-02-06 16:00 | 4.2563 | 5.0434 | 5.0434 | 5.0434 | 5.0434
2024-04-07 17:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-02-06 17:00 | 3.9286 | 4.6551 | 4.6551 | 4.6551 | 4.6551
2024-04-07 18:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-02-06 18:00 | 3.6238 | 4.2939 | 4.2939 | 4.2939 | 4.2939
2024-04-07 19:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-02-06 19:00 | 2.8655 | 3.3954 | 3.3954 | 3.3954 | 3.3954
2024-04-07 20:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-02-06 20:00 | 2.3854 | 2.8265 | 2.8265 | 2.8265 | 2.8265
2024-04-07 21:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-02-06 21:00 | 2.0805 | 2.4653 | 2.4653 | 2.4653 | 2.4653
2024-04-07 22:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-02-06 22:00 | 1.8367 | 2.1763 | 2.1763 | 2.1763 | 2.1763
2024-04-07 23:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-02-06 23:00 | 1.6919 | 2.0047 | 2.0047 | 2.0047 | 2.0047
2024-04-08 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-02-07 | 1.5623 | 1.8512 | 1.8512 | 1.8512 | 1.8512
2024-04-08 01:00 | 1.4289 | 1.5331 | 1.9032 | 2.0019 | 2.1006 | 2024-02-07 01:00 | 1.5699 | 1.8602 | 1.8602 | 1.8602 | 1.8602
2024-04-08 02:00 | 1.448 | 1.5536 | 1.9286 | 2.0286 | 2.1286 | 2024-02-07 02:00 | 1.5547 | 1.8422 | 1.8422 | 1.8422 | 1.8422
2024-04-08 03:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-02-07 03:00 | 1.6652 | 1.9731 | 1.9731 | 1.9731 | 1.9731
2024-04-08 04:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-02-07 04:00 | 1.8481 | 2.1898 | 2.1898 | 2.1898 | 2.1898
2024-04-08 05:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-02-07 05:00 | 2.1263 | 2.5194 | 2.5194 | 2.5194 | 2.5194
2024-04-08 06:00 | 1.7719 | 1.9011 | 2.36 | 2.4823 | 2.6047 | 2024-02-07 06:00 | 2.2711 | 2.691 | 2.691 | 2.691 | 2.691
2024-04-08 07:00 | 2.2482 | 2.4121 | 2.9944 | 3.1496 | 3.3049 | 2024-02-07 07:00 | 2.5111 | 2.9755 | 2.9755 | 2.9755 | 2.9755
2024-04-08 08:00 | 2.191 | 2.3508 | 2.9183 | 3.0696 | 3.2209 | 2024-02-07 08:00 | 2.9493 | 3.4947 | 3.4947 | 3.4947 | 3.4947
2024-04-08 09:00 | 1.9624 | 2.1055 | 2.6137 | 2.7493 | 2.8848 | 2024-02-07 09:00 | 2.9493 | 3.4947 | 3.4947 | 3.4947 | 3.4947
2024-04-08 10:00 | 1.8481 | 1.9829 | 2.4615 | 2.5891 | 2.7167 | 2024-02-07 10:00 | 2.7664 | 3.278 | 3.278 | 3.278 | 3.278
2024-04-08 11:00 | 1.829 | 1.9624 | 2.4361 | 2.5624 | 2.6887 | 2024-02-07 11:00 | 3.1589 | 3.743 | 3.743 | 3.743 | 3.743
2024-04-08 12:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-02-07 12:00 | 3.5514 | 4.2081 | 4.2081 | 4.2081 | 4.2081
2024-04-08 13:00 | 1.7909 | 1.9215 | 2.3854 | 2.509 | 2.6327 | 2024-02-07 13:00 | 3.7762 | 4.4745 | 4.4745 | 4.4745 | 4.4745
2024-04-08 14:00 | 1.7528 | 1.8807 | 2.3346 | 2.4557 | 2.5767 | 2024-02-07 14:00 | 3.8486 | 4.5603 | 4.5603 | 4.5603 | 4.5603
2024-04-08 15:00 | 0.97168 | 1.0425 | 1.2942 | 1.3613 | 1.4284 | 2024-02-07 15:00 | 3.6619 | 4.339 | 4.339 | 4.339 | 4.339
2024-04-08 16:00 | 2.0958 | 2.2486 | 2.7914 | 2.9361 | 3.0808 | 2024-02-07 16:00 | 3.4638 | 4.1043 | 4.1043 | 4.1043 | 4.1043
2024-04-08 17:00 | 2.0958 | 2.2486 | 2.7914 | 2.9361 | 3.0808 | 2024-02-07 17:00 | 3.4904 | 4.1359 | 4.1359 | 4.1359 | 4.1359
2024-04-08 18:00 | 1.9434 | 2.0851 | 2.5884 | 2.7226 | 2.8568 | 2024-02-07 18:00 | 3.178 | 3.7656 | 3.7656 | 3.7656 | 3.7656
2024-04-08 19:00 | 1.81 | 1.942 | 2.4107 | 2.5357 | 2.6607 | 2024-02-07 19:00 | 2.7893 | 3.3051 | 3.3051 | 3.3051 | 3.3051
2024-04-08 20:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-02-07 20:00 | 2.5454 | 3.0161 | 3.0161 | 3.0161 | 3.0161
2024-04-08 21:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-02-07 21:00 | 2.454 | 2.9077 | 2.9077 | 2.9077 | 2.9077
2024-04-08 22:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-02-07 22:00 | 1.9662 | 2.3298 | 2.3298 | 2.3298 | 2.3298
2024-04-08 23:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-02-07 23:00 | 1.7528 | 2.077 | 2.077 | 2.077 | 2.077
2024-04-09 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-02-08 | 1.5128 | 1.7925 | 1.7925 | 1.7925 | 1.7925
2024-04-09 01:00 | 1.448 | 1.5536 | 1.9286 | 2.0286 | 2.1286 | 2024-02-08 01:00 | 1.6118 | 1.9099 | 1.9099 | 1.9099 | 1.9099
2024-04-09 02:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-02-08 02:00 | 1.5661 | 1.8557 | 1.8557 | 1.8557 | 1.8557
2024-04-09 03:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-02-08 03:00 | 1.7338 | 2.0544 | 2.0544 | 2.0544 | 2.0544
2024-04-09 04:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-02-08 04:00 | 1.9205 | 2.2756 | 2.2756 | 2.2756 | 2.2756
2024-04-09 05:00 | 1.7338 | 1.8602 | 2.3092 | 2.429 | 2.5487 | 2024-02-08 05:00 | 2.2444 | 2.6594 | 2.6594 | 2.6594 | 2.6594
2024-04-09 06:00 | 1.7528 | 1.8807 | 2.3346 | 2.4557 | 2.5767 | 2024-02-08 06:00 | 2.3854 | 2.8265 | 2.8265 | 2.8265 | 2.8265
2024-04-09 07:00 | 2.0958 | 2.2486 | 2.7914 | 2.9361 | 3.0808 | 2024-02-08 07:00 | 2.8617 | 3.3909 | 3.3909 | 3.3909 | 3.3909
2024-04-09 08:00 | 2.1339 | 2.2895 | 2.8421 | 2.9895 | 3.1369 | 2024-02-08 08:00 | 3.0598 | 3.6257 | 3.6257 | 3.6257 | 3.6257
2024-04-09 09:00 | 2.191 | 2.3508 | 2.9183 | 3.0696 | 3.2209 | 2024-02-08 09:00 | 3.1703 | 3.7566 | 3.7566 | 3.7566 | 3.7566
2024-04-09 10:00 | 2.172 | 2.3304 | 2.8929 | 3.0429 | 3.1929 | 2024-02-08 10:00 | 3.2999 | 3.9101 | 3.9101 | 3.9101 | 3.9101
2024-04-09 11:00 | 2.2291 | 2.3917 | 2.969 | 3.123 | 3.2769 | 2024-02-08 11:00 | 3.4028 | 4.032 | 4.032 | 4.032 | 4.032
2024-04-09 12:00 | 2.2291 | 2.3917 | 2.969 | 3.123 | 3.2769 | 2024-02-08 12:00 | 3.5666 | 4.2262 | 4.2262 | 4.2262 | 4.2262
2024-04-09 13:00 | 2.2101 | 2.3713 | 2.9436 | 3.0963 | 3.2489 | 2024-02-08 13:00 | 3.5666 | 4.2262 | 4.2262 | 4.2262 | 4.2262
2024-04-09 14:00 | 1.9243 | 2.0646 | 2.563 | 2.6959 | 2.8288 | 2024-02-08 14:00 | 3.6581 | 4.3345 | 4.3345 | 4.3345 | 4.3345
2024-04-09 15:00 | 1.8481 | 1.9829 | 2.4615 | 2.5891 | 2.7167 | 2024-02-08 15:00 | 3.479 | 4.1223 | 4.1223 | 4.1223 | 4.1223
2024-04-09 16:00 | 2.0577 | 2.2077 | 2.7406 | 2.8827 | 3.0248 | 2024-02-08 16:00 | 3.7724 | 4.47 | 4.47 | 4.47 | 4.47
2024-04-09 17:00 | 2.0577 | 2.2077 | 2.7406 | 2.8827 | 3.0248 | 2024-02-08 17:00 | 3.3837 | 4.0094 | 4.0094 | 4.0094 | 4.0094
2024-04-09 18:00 | 1.9434 | 2.0851 | 2.5884 | 2.7226 | 2.8568 | 2024-02-08 18:00 | 3.0865 | 3.6573 | 3.6573 | 3.6573 | 3.6573
2024-04-09 19:00 | 1.829 | 1.9624 | 2.4361 | 2.5624 | 2.6887 | 2024-02-08 19:00 | 2.6635 | 3.1561 | 3.1561 | 3.1561 | 3.1561
2024-04-09 20:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-02-08 20:00 | 2.2634 | 2.682 | 2.682 | 2.682 | 2.682
2024-04-09 21:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-02-08 21:00 | 2.0386 | 2.4156 | 2.4156 | 2.4156 | 2.4156
2024-04-09 22:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-02-08 22:00 | 1.7566 | 2.0815 | 2.0815 | 2.0815 | 2.0815
2024-04-09 23:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-02-08 23:00 | 1.8252 | 2.1628 | 2.1628 | 2.1628 | 2.1628
2024-04-10 | 1.448 | 1.5536 | 1.9286 | 2.0286 | 2.1286 | 2024-02-09 | 1.608 | 1.9054 | 1.9054 | 1.9054 | 1.9054
2024-04-10 01:00 | 1.448 | 1.5536 | 1.9286 | 2.0286 | 2.1286 | 2024-02-09 01:00 | 1.6042 | 1.9009 | 1.9009 | 1.9009 | 1.9009
2024-04-10 02:00 | 1.448 | 1.5536 | 1.9286 | 2.0286 | 2.1286 | 2024-02-09 02:00 | 1.5699 | 1.8602 | 1.8602 | 1.8602 | 1.8602
2024-04-10 03:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-02-09 03:00 | 1.7224 | 2.0408 | 2.0408 | 2.0408 | 2.0408
2024-04-10 04:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-02-09 04:00 | 1.9319 | 2.2892 | 2.2892 | 2.2892 | 2.2892
2024-04-10 05:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-02-09 05:00 | 2.1796 | 2.5827 | 2.5827 | 2.5827 | 2.5827
2024-04-10 06:00 | 1.7338 | 1.8602 | 2.3092 | 2.429 | 2.5487 | 2024-02-09 06:00 | 2.3854 | 2.8265 | 2.8265 | 2.8265 | 2.8265
2024-04-10 07:00 | 1.7909 | 1.9215 | 2.3854 | 2.509 | 2.6327 | 2024-02-09 07:00 | 2.7398 | 3.2464 | 3.2464 | 3.2464 | 3.2464
2024-04-10 08:00 | 2.0767 | 2.2282 | 2.766 | 2.9094 | 3.0528 | 2024-02-09 08:00 | 2.9722 | 3.5218 | 3.5218 | 3.5218 | 3.5218
2024-04-10 09:00 | 1.8862 | 2.0237 | 2.5122 | 2.6425 | 2.7728 | 2024-02-09 09:00 | 2.8198 | 3.3412 | 3.3412 | 3.3412 | 3.3412
2024-04-10 10:00 | 2.0005 | 2.1464 | 2.6645 | 2.8026 | 2.9408 | 2024-02-09 10:00 | 2.8846 | 3.418 | 3.418 | 3.418 | 3.418
2024-04-10 11:00 | 1.7528 | 1.8807 | 2.3346 | 2.4557 | 2.5767 | 2024-02-09 11:00 | 3.0713 | 3.6392 | 3.6392 | 3.6392 | 3.6392
2024-04-10 12:00 | 1.9243 | 2.0646 | 2.563 | 2.6959 | 2.8288 | 2024-02-09 12:00 | 3.6695 | 4.3481 | 4.3481 | 4.3481 | 4.3481
2024-04-10 13:00 | 1.8481 | 1.9829 | 2.4615 | 2.5891 | 2.7167 | 2024-02-09 13:00 | 3.5057 | 4.1539 | 4.1539 | 4.1539 | 4.1539
2024-04-10 14:00 | 1.9624 | 2.1055 | 2.6137 | 2.7493 | 2.8848 | 2024-02-09 14:00 | 3.7915 | 4.4926 | 4.4926 | 4.4926 | 4.4926
2024-04-10 15:00 | 0.93358 | 1.0017 | 1.2434 | 1.3079 | 1.3724 | 2024-02-09 15:00 | 3.8486 | 4.5603 | 4.5603 | 4.5603 | 4.5603
2024-04-10 16:00 | 1.9624 | 2.1055 | 2.6137 | 2.7493 | 2.8848 | 2024-02-09 16:00 | 3.9286 | 4.6551 | 4.6551 | 4.6551 | 4.6551
2024-04-10 17:00 | 1.9434 | 2.0851 | 2.5884 | 2.7226 | 2.8568 | 2024-02-09 17:00 | 3.6962 | 4.3797 | 4.3797 | 4.3797 | 4.3797
2024-04-10 18:00 | 1.9624 | 2.1055 | 2.6137 | 2.7493 | 2.8848 | 2024-02-09 18:00 | 3.5819 | 4.2442 | 4.2442 | 4.2442 | 4.2442
2024-04-10 19:00 | 1.7719 | 1.9011 | 2.36 | 2.4823 | 2.6047 | 2024-02-09 19:00 | 3.4104 | 4.041 | 4.041 | 4.041 | 4.041
2024-04-10 20:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-02-09 20:00 | 2.9836 | 3.5354 | 3.5354 | 3.5354 | 3.5354
2024-04-10 21:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-02-09 21:00 | 2.5492 | 3.0206 | 3.0206 | 3.0206 | 3.0206
2024-04-10 22:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-02-09 22:00 | 2.2177 | 2.6278 | 2.6278 | 2.6278 | 2.6278
2024-04-10 23:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-02-09 23:00 | 1.7566 | 2.0815 | 2.0815 | 2.0815 | 2.0815
2024-04-11 | 1.4289 | 1.5331 | 1.9032 | 2.0019 | 2.1006 | 2024-02-10 | 1.5699 | 1.8602 | 1.8602 | 1.8602 | 1.8602
2024-04-11 01:00 | 1.448 | 1.5536 | 1.9286 | 2.0286 | 2.1286 | 2024-02-10 01:00 | 1.6271 | 1.928 | 1.928 | 1.928 | 1.928
2024-04-11 02:00 | 1.4099 | 1.5127 | 1.8778 | 1.9752 | 2.0726 | 2024-02-10 02:00 | 1.6423 | 1.946 | 1.946 | 1.946 | 1.946
2024-04-11 03:00 | 1.448 | 1.5536 | 1.9286 | 2.0286 | 2.1286 | 2024-02-10 03:00 | 1.7224 | 2.0408 | 2.0408 | 2.0408 | 2.0408
2024-04-11 04:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-02-10 04:00 | 1.9586 | 2.3208 | 2.3208 | 2.3208 | 2.3208
2024-04-11 05:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-02-10 05:00 | 2.1415 | 2.5375 | 2.5375 | 2.5375 | 2.5375
2024-04-11 06:00 | 1.7909 | 1.9215 | 2.3854 | 2.509 | 2.6327 | 2024-02-10 06:00 | 2.2634 | 2.682 | 2.682 | 2.682 | 2.682
2024-04-11 07:00 | 1.8862 | 2.0237 | 2.5122 | 2.6425 | 2.7728 | 2024-02-10 07:00 | 2.2901 | 2.7136 | 2.7136 | 2.7136 | 2.7136
2024-04-11 08:00 | 1.3146 | 1.4105 | 1.751 | 1.8417 | 1.9325 | 2024-02-10 08:00 | 2.6445 | 3.1335 | 3.1335 | 3.1335 | 3.1335
2024-04-11 09:00 | 1.086 | 1.1652 | 1.4464 | 1.5214 | 1.5964 | 2024-02-10 09:00 | 2.7741 | 3.287 | 3.287 | 3.287 | 3.287
2024-04-11 10:00 | 1.086 | 1.1652 | 1.4464 | 1.5214 | 1.5964 | 2024-02-10 10:00 | 3.0065 | 3.5624 | 3.5624 | 3.5624 | 3.5624
2024-04-11 11:00 | 1.1432 | 1.2265 | 1.5226 | 1.6015 | 1.6805 | 2024-02-10 11:00 | 3.1018 | 3.6753 | 3.6753 | 3.6753 | 3.6753
2024-04-11 12:00 | 1.1432 | 1.2265 | 1.5226 | 1.6015 | 1.6805 | 2024-02-10 12:00 | 3.1818 | 3.7701 | 3.7701 | 3.7701 | 3.7701
2024-04-11 13:00 | 1.0479 | 1.1243 | 1.3957 | 1.4681 | 1.5404 | 2024-02-10 13:00 | 3.1665 | 3.7521 | 3.7521 | 3.7521 | 3.7521
2024-04-11 14:00 | 1.0479 | 1.1243 | 1.3957 | 1.4681 | 1.5404 | 2024-02-10 14:00 | 3.1361 | 3.716 | 3.716 | 3.716 | 3.716
2024-04-11 15:00 | 1.086 | 1.1652 | 1.4464 | 1.5214 | 1.5964 | 2024-02-10 15:00 | 3.2085 | 3.8017 | 3.8017 | 3.8017 | 3.8017
2024-04-11 16:00 | 2.0958 | 2.2486 | 2.7914 | 2.9361 | 3.0808 | 2024-02-10 16:00 | 3.1665 | 3.7521 | 3.7521 | 3.7521 | 3.7521
2024-04-11 17:00 | 2.0577 | 2.2077 | 2.7406 | 2.8827 | 3.0248 | 2024-02-10 17:00 | 3.0675 | 3.6347 | 3.6347 | 3.6347 | 3.6347
2024-04-11 18:00 | 1.9243 | 2.0646 | 2.563 | 2.6959 | 2.8288 | 2024-02-10 18:00 | 2.7626 | 3.2735 | 3.2735 | 3.2735 | 3.2735
2024-04-11 19:00 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 2024-02-10 19:00 | 2.4845 | 2.9439 | 2.9439 | 2.9439 | 2.9439
2024-04-11 20:00 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 2024-02-10 20:00 | 2.2444 | 2.6594 | 2.6594 | 2.6594 | 2.6594
2024-04-11 21:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-02-10 21:00 | 2.2977 | 2.7226 | 2.7226 | 2.7226 | 2.7226
2024-04-11 22:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-02-10 22:00 | 2.1796 | 2.5827 | 2.5827 | 2.5827 | 2.5827
2024-04-11 23:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-02-10 23:00 | 1.7566 | 2.0815 | 2.0815 | 2.0815 | 2.0815
2024-04-12 | 1.448 | 1.5536 | 1.9286 | 2.0286 | 2.1286 | 2024-02-11 | 1.6271 | 1.928 | 1.928 | 1.928 | 1.928
2024-04-12 01:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-02-11 01:00 | 1.5814 | 1.8738 | 1.8738 | 1.8738 | 1.8738
2024-04-12 02:00 | 1.4289 | 1.5331 | 1.9032 | 2.0019 | 2.1006 | 2024-02-11 02:00 | 1.5737 | 1.8648 | 1.8648 | 1.8648 | 1.8648
2024-04-12 03:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-02-11 03:00 | 1.7147 | 2.0318 | 2.0318 | 2.0318 | 2.0318
2024-04-12 04:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-02-11 04:00 | 1.8405 | 2.1808 | 2.1808 | 2.1808 | 2.1808
2024-04-12 05:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-02-11 05:00 | 2.092 | 2.4788 | 2.4788 | 2.4788 | 2.4788
2024-04-12 06:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-02-11 06:00 | 2.252 | 2.6684 | 2.6684 | 2.6684 | 2.6684
2024-04-12 07:00 | 1.8481 | 1.9829 | 2.4615 | 2.5891 | 2.7167 | 2024-02-11 07:00 | 2.191 | 2.5962 | 2.5962 | 2.5962 | 2.5962
2024-04-12 08:00 | 0.89547 | 0.96077 | 1.1927 | 1.2545 | 1.3164 | 2024-02-11 08:00 | 2.4692 | 2.9258 | 2.9258 | 2.9258 | 2.9258
2024-04-12 09:00 | 0.89547 | 0.96077 | 1.1927 | 1.2545 | 1.3164 | 2024-02-11 09:00 | 2.5988 | 3.0793 | 3.0793 | 3.0793 | 3.0793
2024-04-12 10:00 | 0.97168 | 1.0425 | 1.2942 | 1.3613 | 1.4284 | 2024-02-11 10:00 | 2.6978 | 3.1967 | 3.1967 | 3.1967 | 3.1967
2024-04-12 11:00 | 1.7719 | 1.9011 | 2.36 | 2.4823 | 2.6047 | 2024-02-11 11:00 | 2.7817 | 3.2961 | 3.2961 | 3.2961 | 3.2961
2024-04-12 12:00 | 0.97168 | 1.0425 | 1.2942 | 1.3613 | 1.4284 | 2024-02-11 12:00 | 2.7969 | 3.3141 | 3.3141 | 3.3141 | 3.3141
2024-04-12 13:00 | 1.81 | 1.942 | 2.4107 | 2.5357 | 2.6607 | 2024-02-11 13:00 | 2.9455 | 3.4902 | 3.4902 | 3.4902 | 3.4902
2024-04-12 14:00 | 1.8481 | 1.9829 | 2.4615 | 2.5891 | 2.7167 | 2024-02-11 14:00 | 2.976 | 3.5263 | 3.5263 | 3.5263 | 3.5263
2024-04-12 15:00 | 2.0577 | 2.2077 | 2.7406 | 2.8827 | 3.0248 | 2024-02-11 15:00 | 2.9608 | 3.5083 | 3.5083 | 3.5083 | 3.5083
2024-04-12 16:00 | 1.8862 | 2.0237 | 2.5122 | 2.6425 | 2.7728 | 2024-02-11 16:00 | 3.0332 | 3.5941 | 3.5941 | 3.5941 | 3.5941
2024-04-12 17:00 | 1.9053 | 2.0442 | 2.5376 | 2.6692 | 2.8008 | 2024-02-11 17:00 | 2.9646 | 3.5128 | 3.5128 | 3.5128 | 3.5128
2024-04-12 18:00 | 1.8862 | 2.0237 | 2.5122 | 2.6425 | 2.7728 | 2024-02-11 18:00 | 2.6064 | 3.0884 | 3.0884 | 3.0884 | 3.0884
2024-04-12 19:00 | 1.7909 | 1.9215 | 2.3854 | 2.509 | 2.6327 | 2024-02-11 19:00 | 2.5264 | 2.9935 | 2.9935 | 2.9935 | 2.9935
2024-04-12 20:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-02-11 20:00 | 2.4654 | 2.9213 | 2.9213 | 2.9213 | 2.9213
2024-04-12 21:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-02-11 21:00 | 2.3435 | 2.7768 | 2.7768 | 2.7768 | 2.7768
2024-04-12 22:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-02-11 22:00 | 2.0462 | 2.4246 | 2.4246 | 2.4246 | 2.4246
2024-04-12 23:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-02-11 23:00 | 1.7071 | 2.0228 | 2.0228 | 2.0228 | 2.0228
2024-04-13 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-02-12 | 1.6004 | 1.8964 | 1.8964 | 1.8964 | 1.8964
2024-04-13 01:00 | 1.4099 | 1.5127 | 1.8778 | 1.9752 | 2.0726 | 2024-02-12 01:00 | 1.608 | 1.9054 | 1.9054 | 1.9054 | 1.9054
2024-04-13 02:00 | 1.4099 | 1.5127 | 1.8778 | 1.9752 | 2.0726 | 2024-02-12 02:00 | 1.589 | 1.8828 | 1.8828 | 1.8828 | 1.8828
2024-04-13 03:00 | 1.3527 | 1.4514 | 1.8017 | 1.8951 | 1.9885 | 2024-02-12 03:00 | 1.7528 | 2.077 | 2.077 | 2.077 | 2.077
2024-04-13 04:00 | 1.4099 | 1.5127 | 1.8778 | 1.9752 | 2.0726 | 2024-02-12 04:00 | 1.9548 | 2.3163 | 2.3163 | 2.3163 | 2.3163
2024-04-13 05:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-02-12 05:00 | 2.1872 | 2.5917 | 2.5917 | 2.5917 | 2.5917
2024-04-13 06:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-02-12 06:00 | 2.5226 | 2.989 | 2.989 | 2.989 | 2.989
2024-04-13 07:00 | 1.4289 | 1.5331 | 1.9032 | 2.0019 | 2.1006 | 2024-02-12 07:00 | 2.6978 | 3.1967 | 3.1967 | 3.1967 | 3.1967
2024-04-13 08:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-02-12 08:00 | 2.8503 | 3.3773 | 3.3773 | 3.3773 | 3.3773
2024-04-13 09:00 | 1.3908 | 1.4923 | 1.8525 | 1.9485 | 2.0446 | 2024-02-12 09:00 | 3.1856 | 3.7747 | 3.7747 | 3.7747 | 3.7747
2024-04-13 10:00 | 0.43821 | 0.47016 | 0.58365 | 0.61391 | 0.64418 | 2024-02-12 10:00 | 3.2847 | 3.892 | 3.892 | 3.892 | 3.892
2024-04-13 11:00 | 1.1241 | 1.2061 | 1.4972 | 1.5748 | 1.6525 | 2024-02-12 11:00 | 3.4295 | 4.0636 | 4.0636 | 4.0636 | 4.0636
2024-04-13 12:00 | 0.97168 | 1.0425 | 1.2942 | 1.3613 | 1.4284 | 2024-02-12 12:00 | 3.9553 | 4.6867 | 4.6867 | 4.6867 | 4.6867
2024-04-13 13:00 | 0.64779 | 0.69502 | 0.86279 | 0.90752 | 0.95226 | 2024-02-12 13:00 | 4.4164 | 5.233 | 5.233 | 5.233 | 5.233
2024-04-13 14:00 | 0.91452 | 0.98121 | 1.2181 | 1.2812 | 1.3444 | 2024-02-12 14:00 | 4.4583 | 5.2827 | 5.2827 | 5.2827 | 5.2827
2024-04-13 15:00 | 0 | 0 | 0 | 0 | 0 | 2024-02-12 15:00 | 4.4507 | 5.2737 | 5.2737 | 5.2737 | 5.2737
2024-04-13 16:00 | 1.4099 | 1.5127 | 1.8778 | 1.9752 | 2.0726 | 2024-02-12 16:00 | 4.1801 | 4.9531 | 4.9531 | 4.9531 | 4.9531
2024-04-13 17:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-02-12 17:00 | 3.9706 | 4.7048 | 4.7048 | 4.7048 | 4.7048
2024-04-13 18:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-02-12 18:00 | 3.7495 | 4.4429 | 4.4429 | 4.4429 | 4.4429
2024-04-13 19:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-02-12 19:00 | 3.2313 | 3.8288 | 3.8288 | 3.8288 | 3.8288
2024-04-13 20:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-02-12 20:00 | 2.9112 | 3.4496 | 3.4496 | 3.4496 | 3.4496
2024-04-13 21:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-02-12 21:00 | 2.4463 | 2.8987 | 2.8987 | 2.8987 | 2.8987
2024-04-13 22:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-02-12 22:00 | 2.1148 | 2.5059 | 2.5059 | 2.5059 | 2.5059
2024-04-13 23:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-02-12 23:00 | 1.8252 | 2.1628 | 2.1628 | 2.1628 | 2.1628
2024-04-14 | 1.4289 | 1.5331 | 1.9032 | 2.0019 | 2.1006 | 2024-02-13 | 1.6233 | 1.9234 | 1.9234 | 1.9234 | 1.9234
2024-04-14 01:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-02-13 01:00 | 1.6195 | 1.9189 | 1.9189 | 1.9189 | 1.9189
2024-04-14 02:00 | 1.4099 | 1.5127 | 1.8778 | 1.9752 | 2.0726 | 2024-02-13 02:00 | 1.7033 | 2.0183 | 2.0183 | 2.0183 | 2.0183
2024-04-14 03:00 | 1.4289 | 1.5331 | 1.9032 | 2.0019 | 2.1006 | 2024-02-13 03:00 | 1.7262 | 2.0454 | 2.0454 | 2.0454 | 2.0454
2024-04-14 04:00 | 1.4099 | 1.5127 | 1.8778 | 1.9752 | 2.0726 | 2024-02-13 04:00 | 1.9243 | 2.2801 | 2.2801 | 2.2801 | 2.2801
2024-04-14 05:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-02-13 05:00 | 2.2215 | 2.6323 | 2.6323 | 2.6323 | 2.6323
2024-04-14 06:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-02-13 06:00 | 2.5149 | 2.98 | 2.98 | 2.98 | 2.98
2024-04-14 07:00 | 1.3908 | 1.4923 | 1.8525 | 1.9485 | 2.0446 | 2024-02-13 07:00 | 2.7207 | 3.2238 | 3.2238 | 3.2238 | 3.2238
2024-04-14 08:00 | 1.0669 | 1.1447 | 1.4211 | 1.4947 | 1.5684 | 2024-02-13 08:00 | 3.559 | 4.2171 | 4.2171 | 4.2171 | 4.2171
2024-04-14 09:00 | 0.66684 | 0.71547 | 0.88816 | 0.93422 | 0.98027 | 2024-02-13 09:00 | 3.559 | 4.2171 | 4.2171 | 4.2171 | 4.2171
2024-04-14 10:00 | 0.83831 | 0.89944 | 1.1165 | 1.1744 | 1.2323 | 2024-02-13 10:00 | 3.9591 | 4.6912 | 4.6912 | 4.6912 | 4.6912
2024-04-14 11:00 | 0.78115 | 0.83812 | 1.0404 | 1.0944 | 1.1483 | 2024-02-13 11:00 | 3.4942 | 4.1404 | 4.1404 | 4.1404 | 4.1404
2024-04-14 12:00 | 0.85737 | 0.91989 | 1.1419 | 1.2011 | 1.2603 | 2024-02-13 12:00 | 4.5955 | 5.4453 | 5.4453 | 5.4453 | 5.4453
2024-04-14 13:00 | 0.78115 | 0.83812 | 1.0404 | 1.0944 | 1.1483 | 2024-02-13 13:00 | 4.7936 | 5.68 | 5.68 | 5.68 | 5.68
2024-04-14 14:00 | 1.1622 | 1.247 | 1.5479 | 1.6282 | 1.7085 | 2024-02-13 14:00 | 4.7403 | 5.6168 | 5.6168 | 5.6168 | 5.6168
2024-04-14 15:00 | 0.057158 | 0.061326 | 0.076128 | 0.080076 | 0.084023 | 2024-02-13 15:00 | 4.6336 | 5.4904 | 5.4904 | 5.4904 | 5.4904
2024-04-14 16:00 | 1.4289 | 1.5331 | 1.9032 | 2.0019 | 2.1006 | 2024-02-13 16:00 | 4.3173 | 5.1157 | 5.1157 | 5.1157 | 5.1157
2024-04-14 17:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-02-13 17:00 | 4.1306 | 4.8944 | 4.8944 | 4.8944 | 4.8944
2024-04-14 18:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-02-13 18:00 | 3.2008 | 3.7927 | 3.7927 | 3.7927 | 3.7927
2024-04-14 19:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-02-13 19:00 | 2.9493 | 3.4947 | 3.4947 | 3.4947 | 3.4947
2024-04-14 20:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-02-13 20:00 | 2.6064 | 3.0884 | 3.0884 | 3.0884 | 3.0884
2024-04-14 21:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-02-13 21:00 | 2.2253 | 2.6368 | 2.6368 | 2.6368 | 2.6368
2024-04-14 22:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-02-13 22:00 | 1.9396 | 2.2982 | 2.2982 | 2.2982 | 2.2982
2024-04-14 23:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-02-13 23:00 | 1.7262 | 2.0454 | 2.0454 | 2.0454 | 2.0454
2024-04-15 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-02-14 | 1.5737 | 1.8648 | 1.8648 | 1.8648 | 1.8648
2024-04-15 01:00 | 1.448 | 1.5536 | 1.9286 | 2.0286 | 2.1286 | 2024-02-14 01:00 | 1.6157 | 1.9144 | 1.9144 | 1.9144 | 1.9144
2024-04-15 02:00 | 1.4289 | 1.5331 | 1.9032 | 2.0019 | 2.1006 | 2024-02-14 02:00 | 1.6042 | 1.9009 | 1.9009 | 1.9009 | 1.9009
2024-04-15 03:00 | 1.3527 | 1.4514 | 1.8017 | 1.8951 | 1.9885 | 2024-02-14 03:00 | 1.829 | 2.1673 | 2.1673 | 2.1673 | 2.1673
2024-04-15 04:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-02-14 04:00 | 1.9129 | 2.2666 | 2.2666 | 2.2666 | 2.2666
2024-04-15 05:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-02-14 05:00 | 2.3015 | 2.7271 | 2.7271 | 2.7271 | 2.7271
2024-04-15 06:00 | 1.7909 | 1.9215 | 2.3854 | 2.509 | 2.6327 | 2024-02-14 06:00 | 2.8083 | 3.3277 | 3.3277 | 3.3277 | 3.3277
2024-04-15 07:00 | 2.0767 | 2.2282 | 2.766 | 2.9094 | 3.0528 | 2024-02-14 07:00 | 3.1437 | 3.725 | 3.725 | 3.725 | 3.725
2024-04-15 08:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-02-14 08:00 | 3.8562 | 4.5693 | 4.5693 | 4.5693 | 4.5693
2024-04-15 09:00 | 1.1432 | 1.2265 | 1.5226 | 1.6015 | 1.6805 | 2024-02-14 09:00 | 3.7495 | 4.4429 | 4.4429 | 4.4429 | 4.4429
2024-04-15 10:00 | 1.2003 | 1.2878 | 1.5987 | 1.6816 | 1.7645 | 2024-02-14 10:00 | 4.0391 | 4.786 | 4.786 | 4.786 | 4.786
2024-04-15 11:00 | 1.9434 | 2.0851 | 2.5884 | 2.7226 | 2.8568 | 2024-02-14 11:00 | 4.0887 | 4.8447 | 4.8447 | 4.8447 | 4.8447
2024-04-15 12:00 | 1.9624 | 2.1055 | 2.6137 | 2.7493 | 2.8848 | 2024-02-14 12:00 | 4.1801 | 4.9531 | 4.9531 | 4.9531 | 4.9531
2024-04-15 13:00 | 1.1622 | 1.247 | 1.5479 | 1.6282 | 1.7085 | 2024-02-14 13:00 | 4.0353 | 4.7815 | 4.7815 | 4.7815 | 4.7815
2024-04-15 14:00 | 1.1622 | 1.247 | 1.5479 | 1.6282 | 1.7085 | 2024-02-14 14:00 | 3.639 | 4.312 | 4.312 | 4.312 | 4.312
2024-04-15 15:00 | 1.1622 | 1.247 | 1.5479 | 1.6282 | 1.7085 | 2024-02-14 15:00 | 4.0391 | 4.786 | 4.786 | 4.786 | 4.786
2024-04-15 16:00 | 2.0386 | 2.1873 | 2.7152 | 2.856 | 2.9968 | 2024-02-14 16:00 | 3.7572 | 4.4519 | 4.4519 | 4.4519 | 4.4519
2024-04-15 17:00 | 2.0386 | 2.1873 | 2.7152 | 2.856 | 2.9968 | 2024-02-14 17:00 | 3.7419 | 4.4339 | 4.4339 | 4.4339 | 4.4339
2024-04-15 18:00 | 2.0386 | 2.1873 | 2.7152 | 2.856 | 2.9968 | 2024-02-14 18:00 | 3.4599 | 4.0997 | 4.0997 | 4.0997 | 4.0997
2024-04-15 19:00 | 1.7338 | 1.8602 | 2.3092 | 2.429 | 2.5487 | 2024-02-14 19:00 | 3.0903 | 3.6618 | 3.6618 | 3.6618 | 3.6618
2024-04-15 20:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-02-14 20:00 | 2.5492 | 3.0206 | 3.0206 | 3.0206 | 3.0206
2024-04-15 21:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-02-14 21:00 | 2.2901 | 2.7136 | 2.7136 | 2.7136 | 2.7136
2024-04-15 22:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-02-14 22:00 | 2.1415 | 2.5375 | 2.5375 | 2.5375 | 2.5375
2024-04-15 23:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-02-14 23:00 | 1.871 | 2.2169 | 2.2169 | 2.2169 | 2.2169
2024-04-16 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-02-15 | 1.5623 | 1.8512 | 1.8512 | 1.8512 | 1.8512
2024-04-16 01:00 | 1.4289 | 1.5331 | 1.9032 | 2.0019 | 2.1006 | 2024-02-15 01:00 | 1.5585 | 1.8467 | 1.8467 | 1.8467 | 1.8467
2024-04-16 02:00 | 1.4099 | 1.5127 | 1.8778 | 1.9752 | 2.0726 | 2024-02-15 02:00 | 1.5433 | 1.8286 | 1.8286 | 1.8286 | 1.8286
2024-04-16 03:00 | 1.4099 | 1.5127 | 1.8778 | 1.9752 | 2.0726 | 2024-02-15 03:00 | 1.6919 | 2.0047 | 2.0047 | 2.0047 | 2.0047
2024-04-16 04:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-02-15 04:00 | 1.8252 | 2.1628 | 2.1628 | 2.1628 | 2.1628
2024-04-16 05:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-02-15 05:00 | 2.1529 | 2.5511 | 2.5511 | 2.5511 | 2.5511
2024-04-16 06:00 | 1.7909 | 1.9215 | 2.3854 | 2.509 | 2.6327 | 2024-02-15 06:00 | 2.4425 | 2.8942 | 2.8942 | 2.8942 | 2.8942
2024-04-16 07:00 | 1.9624 | 2.1055 | 2.6137 | 2.7493 | 2.8848 | 2024-02-15 07:00 | 2.7588 | 3.269 | 3.269 | 3.269 | 3.269
2024-04-16 08:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-02-15 08:00 | 3.3685 | 3.9914 | 3.9914 | 3.9914 | 3.9914
2024-04-16 09:00 | 1.3718 | 1.4718 | 1.8271 | 1.9218 | 2.0166 | 2024-02-15 09:00 | 3.4104 | 4.041 | 4.041 | 4.041 | 4.041
2024-04-16 10:00 | 1.3908 | 1.4923 | 1.8525 | 1.9485 | 2.0446 | 2024-02-15 10:00 | 3.4485 | 4.0862 | 4.0862 | 4.0862 | 4.0862
2024-04-16 11:00 | 1.448 | 1.5536 | 1.9286 | 2.0286 | 2.1286 | 2024-02-15 11:00 | 3.3837 | 4.0094 | 4.0094 | 4.0094 | 4.0094
2024-04-16 12:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-02-15 12:00 | 3.6924 | 4.3752 | 4.3752 | 4.3752 | 4.3752
2024-04-16 13:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-02-15 13:00 | 3.8181 | 4.5242 | 4.5242 | 4.5242 | 4.5242
2024-04-16 14:00 | 1.4289 | 1.5331 | 1.9032 | 2.0019 | 2.1006 | 2024-02-15 14:00 | 3.7953 | 4.4971 | 4.4971 | 4.4971 | 4.4971
2024-04-16 15:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-02-15 15:00 | 3.6543 | 4.33 | 4.33 | 4.33 | 4.33
2024-04-16 16:00 | 2.172 | 2.3304 | 2.8929 | 3.0429 | 3.1929 | 2024-02-15 16:00 | 3.6695 | 4.3481 | 4.3481 | 4.3481 | 4.3481
2024-04-16 17:00 | 2.0577 | 2.2077 | 2.7406 | 2.8827 | 3.0248 | 2024-02-15 17:00 | 3.3228 | 3.9372 | 3.9372 | 3.9372 | 3.9372
2024-04-16 18:00 | 2.0196 | 2.1668 | 2.6899 | 2.8293 | 2.9688 | 2024-02-15 18:00 | 2.7931 | 3.3096 | 3.3096 | 3.3096 | 3.3096
2024-04-16 19:00 | 1.829 | 1.9624 | 2.4361 | 2.5624 | 2.6887 | 2024-02-15 19:00 | 2.7474 | 3.2554 | 3.2554 | 3.2554 | 3.2554
2024-04-16 20:00 | 1.7528 | 1.8807 | 2.3346 | 2.4557 | 2.5767 | 2024-02-15 20:00 | 2.4159 | 2.8626 | 2.8626 | 2.8626 | 2.8626
2024-04-16 21:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-02-15 21:00 | 2.3397 | 2.7723 | 2.7723 | 2.7723 | 2.7723
2024-04-16 22:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-02-15 22:00 | 2.0805 | 2.4653 | 2.4653 | 2.4653 | 2.4653
2024-04-16 23:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-02-15 23:00 | 1.7909 | 2.1221 | 2.1221 | 2.1221 | 2.1221
2024-04-17 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-02-16 | 1.5394 | 1.8241 | 1.8241 | 1.8241 | 1.8241
2024-04-17 01:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-02-16 01:00 | 1.608 | 1.9054 | 1.9054 | 1.9054 | 1.9054
2024-04-17 02:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-02-16 02:00 | 1.5623 | 1.8512 | 1.8512 | 1.8512 | 1.8512
2024-04-17 03:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-02-16 03:00 | 1.7643 | 2.0905 | 2.0905 | 2.0905 | 2.0905
2024-04-17 04:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-02-16 04:00 | 1.9472 | 2.3072 | 2.3072 | 2.3072 | 2.3072
2024-04-17 05:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-02-16 05:00 | 2.2444 | 2.6594 | 2.6594 | 2.6594 | 2.6594
2024-04-17 06:00 | 1.7528 | 1.8807 | 2.3346 | 2.4557 | 2.5767 | 2024-02-16 06:00 | 2.8198 | 3.3412 | 3.3412 | 3.3412 | 3.3412
2024-04-17 07:00 | 2.2101 | 2.3713 | 2.9436 | 3.0963 | 3.2489 | 2024-02-16 07:00 | 3.0294 | 3.5895 | 3.5895 | 3.5895 | 3.5895
2024-04-17 08:00 | 2.2101 | 2.3713 | 2.9436 | 3.0963 | 3.2489 | 2024-02-16 08:00 | 3.6543 | 4.33 | 4.33 | 4.33 | 4.33
2024-04-17 09:00 | 2.0958 | 2.2486 | 2.7914 | 2.9361 | 3.0808 | 2024-02-16 09:00 | 3.8219 | 4.5287 | 4.5287 | 4.5287 | 4.5287
2024-04-17 10:00 | 2.172 | 2.3304 | 2.8929 | 3.0429 | 3.1929 | 2024-02-16 10:00 | 3.62 | 4.2894 | 4.2894 | 4.2894 | 4.2894
2024-04-17 11:00 | 2.1529 | 2.3099 | 2.8675 | 3.0162 | 3.1649 | 2024-02-16 11:00 | 3.8982 | 4.619 | 4.619 | 4.619 | 4.619
2024-04-17 12:00 | 2.2673 | 2.4326 | 3.0198 | 3.1763 | 3.3329 | 2024-02-16 12:00 | 4.123 | 4.8854 | 4.8854 | 4.8854 | 4.8854
2024-04-17 13:00 | 2.0767 | 2.2282 | 2.766 | 2.9094 | 3.0528 | 2024-02-16 13:00 | 3.7267 | 4.4158 | 4.4158 | 4.4158 | 4.4158
2024-04-17 14:00 | 2.0767 | 2.2282 | 2.766 | 2.9094 | 3.0528 | 2024-02-16 14:00 | 4.2259 | 5.0073 | 5.0073 | 5.0073 | 5.0073
2024-04-17 15:00 | 2.0958 | 2.2486 | 2.7914 | 2.9361 | 3.0808 | 2024-02-16 15:00 | 4.1496 | 4.917 | 4.917 | 4.917 | 4.917
2024-04-17 16:00 | 2.0767 | 2.2282 | 2.766 | 2.9094 | 3.0528 | 2024-02-16 16:00 | 3.982 | 4.7183 | 4.7183 | 4.7183 | 4.7183
2024-04-17 17:00 | 2.0005 | 2.1464 | 2.6645 | 2.8026 | 2.9408 | 2024-02-16 17:00 | 4.1535 | 4.9215 | 4.9215 | 4.9215 | 4.9215
2024-04-17 18:00 | 2.0958 | 2.2486 | 2.7914 | 2.9361 | 3.0808 | 2024-02-16 18:00 | 4.0849 | 4.8402 | 4.8402 | 4.8402 | 4.8402
2024-04-17 19:00 | 1.8481 | 1.9829 | 2.4615 | 2.5891 | 2.7167 | 2024-02-16 19:00 | 3.8715 | 4.5874 | 4.5874 | 4.5874 | 4.5874
2024-04-17 20:00 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 2024-02-16 20:00 | 2.976 | 3.5263 | 3.5263 | 3.5263 | 3.5263
2024-04-17 21:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-02-16 21:00 | 2.595 | 3.0748 | 3.0748 | 3.0748 | 3.0748
2024-04-17 22:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-02-16 22:00 | 2.1491 | 2.5465 | 2.5465 | 2.5465 | 2.5465
2024-04-17 23:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-02-16 23:00 | 1.8252 | 2.1628 | 2.1628 | 2.1628 | 2.1628
2024-04-18 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-02-17 | 1.6804 | 1.9912 | 1.9912 | 1.9912 | 1.9912
2024-04-18 01:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-02-17 01:00 | 1.8214 | 2.1582 | 2.1582 | 2.1582 | 2.1582
2024-04-18 02:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-02-17 02:00 | 1.65 | 1.9551 | 1.9551 | 1.9551 | 1.9551
2024-04-18 03:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-02-17 03:00 | 1.8024 | 2.1357 | 2.1357 | 2.1357 | 2.1357
2024-04-18 04:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-02-17 04:00 | 2.012 | 2.384 | 2.384 | 2.384 | 2.384
2024-04-18 05:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-02-17 05:00 | 2.3282 | 2.7587 | 2.7587 | 2.7587 | 2.7587
2024-04-18 06:00 | 1.7719 | 1.9011 | 2.36 | 2.4823 | 2.6047 | 2024-02-17 06:00 | 2.4006 | 2.8445 | 2.8445 | 2.8445 | 2.8445
2024-04-18 07:00 | 2.0767 | 2.2282 | 2.766 | 2.9094 | 3.0528 | 2024-02-17 07:00 | 2.4121 | 2.8581 | 2.8581 | 2.8581 | 2.8581
2024-04-18 08:00 | 2.2673 | 2.4326 | 3.0198 | 3.1763 | 3.3329 | 2024-02-17 08:00 | 2.7931 | 3.3096 | 3.3096 | 3.3096 | 3.3096
2024-04-18 09:00 | 2.0386 | 2.1873 | 2.7152 | 2.856 | 2.9968 | 2024-02-17 09:00 | 2.7741 | 3.287 | 3.287 | 3.287 | 3.287
2024-04-18 10:00 | 2.0767 | 2.2282 | 2.766 | 2.9094 | 3.0528 | 2024-02-17 10:00 | 3.3266 | 3.9417 | 3.9417 | 3.9417 | 3.9417
2024-04-18 11:00 | 2.0196 | 2.1668 | 2.6899 | 2.8293 | 2.9688 | 2024-02-17 11:00 | 3.7343 | 4.4248 | 4.4248 | 4.4248 | 4.4248
2024-04-18 12:00 | 1.9815 | 2.126 | 2.6391 | 2.776 | 2.9128 | 2024-02-17 12:00 | 3.3533 | 3.9733 | 3.9733 | 3.9733 | 3.9733
2024-04-18 13:00 | 1.9434 | 2.0851 | 2.5884 | 2.7226 | 2.8568 | 2024-02-17 13:00 | 3.9706 | 4.7048 | 4.7048 | 4.7048 | 4.7048
2024-04-18 14:00 | 1.1241 | 1.2061 | 1.4972 | 1.5748 | 1.6525 | 2024-02-17 14:00 | 4.0391 | 4.786 | 4.786 | 4.786 | 4.786
2024-04-18 15:00 | 2.0005 | 2.1464 | 2.6645 | 2.8026 | 2.9408 | 2024-02-17 15:00 | 3.982 | 4.7183 | 4.7183 | 4.7183 | 4.7183
2024-04-18 16:00 | 1.9053 | 2.0442 | 2.5376 | 2.6692 | 2.8008 | 2024-02-17 16:00 | 3.8905 | 4.61 | 4.61 | 4.61 | 4.61
2024-04-18 17:00 | 2.0958 | 2.2486 | 2.7914 | 2.9361 | 3.0808 | 2024-02-17 17:00 | 3.5323 | 4.1855 | 4.1855 | 4.1855 | 4.1855
2024-04-18 18:00 | 2.0958 | 2.2486 | 2.7914 | 2.9361 | 3.0808 | 2024-02-17 18:00 | 2.7702 | 3.2825 | 3.2825 | 3.2825 | 3.2825
2024-04-18 19:00 | 1.8481 | 1.9829 | 2.4615 | 2.5891 | 2.7167 | 2024-02-17 19:00 | 2.7321 | 3.2374 | 3.2374 | 3.2374 | 3.2374
2024-04-18 20:00 | 1.7719 | 1.9011 | 2.36 | 2.4823 | 2.6047 | 2024-02-17 20:00 | 2.4692 | 2.9258 | 2.9258 | 2.9258 | 2.9258
2024-04-18 21:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-02-17 21:00 | 2.2711 | 2.691 | 2.691 | 2.691 | 2.691
2024-04-18 22:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-02-17 22:00 | 2.1034 | 2.4924 | 2.4924 | 2.4924 | 2.4924
2024-04-18 23:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-02-17 23:00 | 1.7185 | 2.0363 | 2.0363 | 2.0363 | 2.0363
2024-04-19 | 1.3718 | 1.4718 | 1.8271 | 1.9218 | 2.0166 | 2024-02-18 | 1.6766 | 1.9867 | 1.9867 | 1.9867 | 1.9867
2024-04-19 01:00 | 1.4289 | 1.5331 | 1.9032 | 2.0019 | 2.1006 | 2024-02-18 01:00 | 1.6385 | 1.9415 | 1.9415 | 1.9415 | 1.9415
2024-04-19 02:00 | 1.3908 | 1.4923 | 1.8525 | 1.9485 | 2.0446 | 2024-02-18 02:00 | 1.6271 | 1.928 | 1.928 | 1.928 | 1.928
2024-04-19 03:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-02-18 03:00 | 1.8252 | 2.1628 | 2.1628 | 2.1628 | 2.1628
2024-04-19 04:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-02-18 04:00 | 1.9091 | 2.2621 | 2.2621 | 2.2621 | 2.2621
2024-04-19 05:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-02-18 05:00 | 2.1872 | 2.5917 | 2.5917 | 2.5917 | 2.5917
2024-04-19 06:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-02-18 06:00 | 2.233 | 2.6459 | 2.6459 | 2.6459 | 2.6459
2024-04-19 07:00 | 2.1339 | 2.2895 | 2.8421 | 2.9895 | 3.1369 | 2024-02-18 07:00 | 2.553 | 3.0251 | 3.0251 | 3.0251 | 3.0251
2024-04-19 08:00 | 2.3244 | 2.4939 | 3.0959 | 3.2564 | 3.4169 | 2024-02-18 08:00 | 2.5759 | 3.0522 | 3.0522 | 3.0522 | 3.0522
2024-04-19 09:00 | 2.0767 | 2.2282 | 2.766 | 2.9094 | 3.0528 | 2024-02-18 09:00 | 2.896 | 3.4315 | 3.4315 | 3.4315 | 3.4315
2024-04-19 10:00 | 1.2956 | 1.39 | 1.7256 | 1.815 | 1.9045 | 2024-02-18 10:00 | 2.9189 | 3.4586 | 3.4586 | 3.4586 | 3.4586
2024-04-19 11:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-02-18 11:00 | 3.4142 | 4.0456 | 4.0456 | 4.0456 | 4.0456
2024-04-19 12:00 | 2.1339 | 2.2895 | 2.8421 | 2.9895 | 3.1369 | 2024-02-18 12:00 | 3.921 | 4.6461 | 4.6461 | 4.6461 | 4.6461
2024-04-19 13:00 | 2.0386 | 2.1873 | 2.7152 | 2.856 | 2.9968 | 2024-02-18 13:00 | 4.5459 | 5.3866 | 5.3866 | 5.3866 | 5.3866
2024-04-19 14:00 | 2.0005 | 2.1464 | 2.6645 | 2.8026 | 2.9408 | 2024-02-18 14:00 | 4.3326 | 5.1337 | 5.1337 | 5.1337 | 5.1337
2024-04-19 15:00 | 2.0005 | 2.1464 | 2.6645 | 2.8026 | 2.9408 | 2024-02-18 15:00 | 3.2656 | 3.8695 | 3.8695 | 3.8695 | 3.8695
2024-04-19 16:00 | 2.0005 | 2.1464 | 2.6645 | 2.8026 | 2.9408 | 2024-02-18 16:00 | 3.5933 | 4.2578 | 4.2578 | 4.2578 | 4.2578
2024-04-19 17:00 | 1.9815 | 2.126 | 2.6391 | 2.776 | 2.9128 | 2024-02-18 17:00 | 3.4218 | 4.0546 | 4.0546 | 4.0546 | 4.0546
2024-04-19 18:00 | 1.9053 | 2.0442 | 2.5376 | 2.6692 | 2.8008 | 2024-02-18 18:00 | 3.1361 | 3.716 | 3.716 | 3.716 | 3.716
2024-04-19 19:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-02-18 19:00 | 2.534 | 3.0026 | 3.0026 | 3.0026 | 3.0026
2024-04-19 20:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-02-18 20:00 | 2.3968 | 2.84 | 2.84 | 2.84 | 2.84
2024-04-19 21:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-02-18 21:00 | 2.191 | 2.5962 | 2.5962 | 2.5962 | 2.5962
2024-04-19 22:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-02-18 22:00 | 2.0805 | 2.4653 | 2.4653 | 2.4653 | 2.4653
2024-04-19 23:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-02-18 23:00 | 1.7566 | 2.0815 | 2.0815 | 2.0815 | 2.0815
2024-04-20 | 1.4099 | 1.5127 | 1.8778 | 1.9752 | 2.0726 | 2024-02-19 | 1.6995 | 2.0138 | 2.0138 | 2.0138 | 2.0138
2024-04-20 01:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-02-19 01:00 | 1.5547 | 1.8422 | 1.8422 | 1.8422 | 1.8422
2024-04-20 02:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-02-19 02:00 | 1.5623 | 1.8512 | 1.8512 | 1.8512 | 1.8512
2024-04-20 03:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-02-19 03:00 | 1.7643 | 2.0905 | 2.0905 | 2.0905 | 2.0905
2024-04-20 04:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-02-19 04:00 | 1.9777 | 2.3434 | 2.3434 | 2.3434 | 2.3434
2024-04-20 05:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-02-19 05:00 | 2.2673 | 2.6865 | 2.6865 | 2.6865 | 2.6865
2024-04-20 06:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-02-19 06:00 | 2.5797 | 3.0567 | 3.0567 | 3.0567 | 3.0567
2024-04-20 07:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-02-19 07:00 | 2.7931 | 3.3096 | 3.3096 | 3.3096 | 3.3096
2024-04-20 08:00 | 0.17147 | 0.18398 | 0.22839 | 0.24023 | 0.25207 | 2024-02-19 08:00 | 3.2237 | 3.8198 | 3.8198 | 3.8198 | 3.8198
2024-04-20 09:00 | 0.095263 | 0.10221 | 0.12688 | 0.13346 | 0.14004 | 2024-02-19 09:00 | 3.7305 | 4.4203 | 4.4203 | 4.4203 | 4.4203
2024-04-20 10:00 | 0.89547 | 0.96077 | 1.1927 | 1.2545 | 1.3164 | 2024-02-19 10:00 | 3.6657 | 4.3436 | 4.3436 | 4.3436 | 4.3436
2024-04-20 11:00 | 0.80021 | 0.85856 | 1.0658 | 1.1211 | 1.1763 | 2024-02-19 11:00 | 3.902 | 4.6235 | 4.6235 | 4.6235 | 4.6235
2024-04-20 12:00 | 0.41916 | 0.44972 | 0.55827 | 0.58722 | 0.61617 | 2024-02-19 12:00 | 4.142 | 4.908 | 4.908 | 4.908 | 4.908
2024-04-20 13:00 | 0.30484 | 0.32707 | 0.40602 | 0.42707 | 0.44812 | 2024-02-19 13:00 | 3.7648 | 4.461 | 4.461 | 4.461 | 4.461
2024-04-20 14:00 | 0.85737 | 0.91989 | 1.1419 | 1.2011 | 1.2603 | 2024-02-19 14:00 | 3.7152 | 4.4023 | 4.4023 | 4.4023 | 4.4023
2024-04-20 15:00 | 0.019053 | 0.020442 | 0.025376 | 0.026692 | 0.028008 | 2024-02-19 15:00 | 3.7152 | 4.4023 | 4.4023 | 4.4023 | 4.4023
2024-04-20 16:00 | 1.3146 | 1.4105 | 1.751 | 1.8417 | 1.9325 | 2024-02-19 16:00 | 3.9972 | 4.7364 | 4.7364 | 4.7364 | 4.7364
2024-04-20 17:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-02-19 17:00 | 3.9096 | 4.6325 | 4.6325 | 4.6325 | 4.6325
2024-04-20 18:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-02-19 18:00 | 3.5247 | 4.1765 | 4.1765 | 4.1765 | 4.1765
2024-04-20 19:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-02-19 19:00 | 2.8579 | 3.3864 | 3.3864 | 3.3864 | 3.3864
2024-04-20 20:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-02-19 20:00 | 2.7702 | 3.2825 | 3.2825 | 3.2825 | 3.2825
2024-04-20 21:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-02-19 21:00 | 2.3473 | 2.7813 | 2.7813 | 2.7813 | 2.7813
2024-04-20 22:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-02-19 22:00 | 1.9472 | 2.3072 | 2.3072 | 2.3072 | 2.3072
2024-04-20 23:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-02-19 23:00 | 1.7071 | 2.0228 | 2.0228 | 2.0228 | 2.0228
2024-04-21 | 1.448 | 1.5536 | 1.9286 | 2.0286 | 2.1286 | 2024-02-20 | 1.5204 | 1.8015 | 1.8015 | 1.8015 | 1.8015
2024-04-21 01:00 | 1.4099 | 1.5127 | 1.8778 | 1.9752 | 2.0726 | 2024-02-20 01:00 | 1.6004 | 1.8964 | 1.8964 | 1.8964 | 1.8964
2024-04-21 02:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-02-20 02:00 | 1.5661 | 1.8557 | 1.8557 | 1.8557 | 1.8557
2024-04-21 03:00 | 1.4289 | 1.5331 | 1.9032 | 2.0019 | 2.1006 | 2024-02-20 03:00 | 1.7071 | 2.0228 | 2.0228 | 2.0228 | 2.0228
2024-04-21 04:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-02-20 04:00 | 1.8367 | 2.1763 | 2.1763 | 2.1763 | 2.1763
2024-04-21 05:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-02-20 05:00 | 2.1682 | 2.5691 | 2.5691 | 2.5691 | 2.5691
2024-04-21 06:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-02-20 06:00 | 2.534 | 3.0026 | 3.0026 | 3.0026 | 3.0026
2024-04-21 07:00 | 1.4289 | 1.5331 | 1.9032 | 2.0019 | 2.1006 | 2024-02-20 07:00 | 2.8769 | 3.4089 | 3.4089 | 3.4089 | 3.4089
2024-04-21 08:00 | 0.28579 | 0.30663 | 0.38064 | 0.40038 | 0.42012 | 2024-02-20 08:00 | 3.2732 | 3.8785 | 3.8785 | 3.8785 | 3.8785
2024-04-21 09:00 | 0.89547 | 0.96077 | 1.1927 | 1.2545 | 1.3164 | 2024-02-20 09:00 | 3.6047 | 4.2713 | 4.2713 | 4.2713 | 4.2713
2024-04-21 10:00 | 0 | 0 | 0 | 0 | 0 | 2024-02-20 10:00 | 3.6924 | 4.3752 | 4.3752 | 4.3752 | 4.3752
2024-04-21 11:00 | 0.057158 | 0.061326 | 0.076128 | 0.080076 | 0.084023 | 2024-02-20 11:00 | 3.5819 | 4.2442 | 4.2442 | 4.2442 | 4.2442
2024-04-21 12:00 | 0.057158 | 0.061326 | 0.076128 | 0.080076 | 0.084023 | 2024-02-20 12:00 | 3.7229 | 4.4113 | 4.4113 | 4.4113 | 4.4113
2024-04-21 13:00 | 0.07621 | 0.081768 | 0.1015 | 0.10677 | 0.11203 | 2024-02-20 13:00 | 3.7991 | 4.5016 | 4.5016 | 4.5016 | 4.5016
2024-04-21 14:00 | 0.15242 | 0.16354 | 0.20301 | 0.21354 | 0.22406 | 2024-02-20 14:00 | 3.6962 | 4.3797 | 4.3797 | 4.3797 | 4.3797
2024-04-21 15:00 | 0.4001 | 0.42928 | 0.5329 | 0.56053 | 0.58816 | 2024-02-20 15:00 | 3.9286 | 4.6551 | 4.6551 | 4.6551 | 4.6551
2024-04-21 16:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-02-20 16:00 | 3.9782 | 4.7138 | 4.7138 | 4.7138 | 4.7138
2024-04-21 17:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-02-20 17:00 | 3.6505 | 4.3255 | 4.3255 | 4.3255 | 4.3255
2024-04-21 18:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-02-20 18:00 | 3.178 | 3.7656 | 3.7656 | 3.7656 | 3.7656
2024-04-21 19:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-02-20 19:00 | 2.7855 | 3.3006 | 3.3006 | 3.3006 | 3.3006
2024-04-21 20:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-02-20 20:00 | 2.5073 | 2.971 | 2.971 | 2.971 | 2.971
2024-04-21 21:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-02-20 21:00 | 2.2596 | 2.6775 | 2.6775 | 2.6775 | 2.6775
2024-04-21 22:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-02-20 22:00 | 1.9205 | 2.2756 | 2.2756 | 2.2756 | 2.2756
2024-04-21 23:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-02-20 23:00 | 1.89 | 2.2395 | 2.2395 | 2.2395 | 2.2395
2024-04-22 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-02-21 | 1.5852 | 1.8783 | 1.8783 | 1.8783 | 1.8783
2024-04-22 01:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-02-21 01:00 | 1.5661 | 1.8557 | 1.8557 | 1.8557 | 1.8557
2024-04-22 02:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-02-21 02:00 | 1.5509 | 1.8377 | 1.8377 | 1.8377 | 1.8377
2024-04-22 03:00 | 1.4289 | 1.5331 | 1.9032 | 2.0019 | 2.1006 | 2024-02-21 03:00 | 1.7033 | 2.0183 | 2.0183 | 2.0183 | 2.0183
2024-04-22 04:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-02-21 04:00 | 1.9929 | 2.3614 | 2.3614 | 2.3614 | 2.3614
2024-04-22 05:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-02-21 05:00 | 2.191 | 2.5962 | 2.5962 | 2.5962 | 2.5962
2024-04-22 06:00 | 1.7528 | 1.8807 | 2.3346 | 2.4557 | 2.5767 | 2024-02-21 06:00 | 2.4235 | 2.8716 | 2.8716 | 2.8716 | 2.8716
2024-04-22 07:00 | 2.4578 | 2.637 | 3.2735 | 3.4433 | 3.613 | 2024-02-21 07:00 | 2.7283 | 3.2328 | 3.2328 | 3.2328 | 3.2328
2024-04-22 08:00 | 2.534 | 2.7188 | 3.375 | 3.55 | 3.725 | 2024-02-21 08:00 | 3.2427 | 3.8424 | 3.8424 | 3.8424 | 3.8424
2024-04-22 09:00 | 2.2673 | 2.4326 | 3.0198 | 3.1763 | 3.3329 | 2024-02-21 09:00 | 3.7991 | 4.5016 | 4.5016 | 4.5016 | 4.5016
2024-04-22 10:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-02-21 10:00 | 3.6086 | 4.2758 | 4.2758 | 4.2758 | 4.2758
2024-04-22 11:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-02-21 11:00 | 3.8105 | 4.5151 | 4.5151 | 4.5151 | 4.5151
2024-04-22 12:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-02-21 12:00 | 3.5171 | 4.1675 | 4.1675 | 4.1675 | 4.1675
2024-04-22 13:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-02-21 13:00 | 4.0277 | 4.7725 | 4.7725 | 4.7725 | 4.7725
2024-04-22 14:00 | 1.3908 | 1.4923 | 1.8525 | 1.9485 | 2.0446 | 2024-02-21 14:00 | 3.7724 | 4.47 | 4.47 | 4.47 | 4.47
2024-04-22 15:00 | 1.4099 | 1.5127 | 1.8778 | 1.9752 | 2.0726 | 2024-02-21 15:00 | 3.6009 | 4.2668 | 4.2668 | 4.2668 | 4.2668
2024-04-22 16:00 | 2.1529 | 2.3099 | 2.8675 | 3.0162 | 3.1649 | 2024-02-21 16:00 | 3.6581 | 4.3345 | 4.3345 | 4.3345 | 4.3345
2024-04-22 17:00 | 2.1148 | 2.2691 | 2.8167 | 2.9628 | 3.1089 | 2024-02-21 17:00 | 3.6086 | 4.2758 | 4.2758 | 4.2758 | 4.2758
2024-04-22 18:00 | 2.1148 | 2.2691 | 2.8167 | 2.9628 | 3.1089 | 2024-02-21 18:00 | 3.3151 | 3.9282 | 3.9282 | 3.9282 | 3.9282
2024-04-22 19:00 | 1.7719 | 1.9011 | 2.36 | 2.4823 | 2.6047 | 2024-02-21 19:00 | 2.915 | 3.4541 | 3.4541 | 3.4541 | 3.4541
2024-04-22 20:00 | 1.7338 | 1.8602 | 2.3092 | 2.429 | 2.5487 | 2024-02-21 20:00 | 2.8007 | 3.3186 | 3.3186 | 3.3186 | 3.3186
2024-04-22 21:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-02-21 21:00 | 2.3892 | 2.831 | 2.831 | 2.831 | 2.831
2024-04-22 22:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-02-21 22:00 | 2.1644 | 2.5646 | 2.5646 | 2.5646 | 2.5646
2024-04-22 23:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-02-21 23:00 | 1.7566 | 2.0815 | 2.0815 | 2.0815 | 2.0815
2024-04-23 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-02-22 | 1.509 | 1.788 | 1.788 | 1.788 | 1.788
2024-04-23 01:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-02-22 01:00 | 1.6157 | 1.9144 | 1.9144 | 1.9144 | 1.9144
2024-04-23 02:00 | 1.448 | 1.5536 | 1.9286 | 2.0286 | 2.1286 | 2024-02-22 02:00 | 1.5776 | 1.8693 | 1.8693 | 1.8693 | 1.8693
2024-04-23 03:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-02-22 03:00 | 1.7757 | 2.1041 | 2.1041 | 2.1041 | 2.1041
2024-04-23 04:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-02-22 04:00 | 1.9014 | 2.2531 | 2.2531 | 2.2531 | 2.2531
2024-04-23 05:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-02-22 05:00 | 2.2939 | 2.7181 | 2.7181 | 2.7181 | 2.7181
2024-04-23 06:00 | 1.81 | 1.942 | 2.4107 | 2.5357 | 2.6607 | 2024-02-22 06:00 | 2.4806 | 2.9394 | 2.9394 | 2.9394 | 2.9394
2024-04-23 07:00 | 2.0577 | 2.2077 | 2.7406 | 2.8827 | 3.0248 | 2024-02-22 07:00 | 2.6369 | 3.1245 | 3.1245 | 3.1245 | 3.1245
2024-04-23 08:00 | 1.8481 | 1.9829 | 2.4615 | 2.5891 | 2.7167 | 2024-02-22 08:00 | 3.3609 | 3.9824 | 3.9824 | 3.9824 | 3.9824
2024-04-23 09:00 | 1.3527 | 1.4514 | 1.8017 | 1.8951 | 1.9885 | 2024-02-22 09:00 | 3.3304 | 3.9462 | 3.9462 | 3.9462 | 3.9462
2024-04-23 10:00 | 1.2575 | 1.3492 | 1.6748 | 1.7617 | 1.8485 | 2024-02-22 10:00 | 3.3037 | 3.9146 | 3.9146 | 3.9146 | 3.9146
2024-04-23 11:00 | 1.3146 | 1.4105 | 1.751 | 1.8417 | 1.9325 | 2024-02-22 11:00 | 3.5019 | 4.1494 | 4.1494 | 4.1494 | 4.1494
2024-04-23 12:00 | 1.4289 | 1.5331 | 1.9032 | 2.0019 | 2.1006 | 2024-02-22 12:00 | 3.5971 | 4.2623 | 4.2623 | 4.2623 | 4.2623
2024-04-23 13:00 | 1.9053 | 2.0442 | 2.5376 | 2.6692 | 2.8008 | 2024-02-22 13:00 | 4.0925 | 4.8493 | 4.8493 | 4.8493 | 4.8493
2024-04-23 14:00 | 1.1813 | 1.2674 | 1.5733 | 1.6549 | 1.7365 | 2024-02-22 14:00 | 4.1001 | 4.8583 | 4.8583 | 4.8583 | 4.8583
2024-04-23 15:00 | 1.2194 | 1.3083 | 1.6241 | 1.7083 | 1.7925 | 2024-02-22 15:00 | 4.4812 | 5.3098 | 5.3098 | 5.3098 | 5.3098
2024-04-23 16:00 | 2.0386 | 2.1873 | 2.7152 | 2.856 | 2.9968 | 2024-02-22 16:00 | 4.424 | 5.2421 | 5.2421 | 5.2421 | 5.2421
2024-04-23 17:00 | 2.0005 | 2.1464 | 2.6645 | 2.8026 | 2.9408 | 2024-02-22 17:00 | 4.1801 | 4.9531 | 4.9531 | 4.9531 | 4.9531
2024-04-23 18:00 | 1.9815 | 2.126 | 2.6391 | 2.776 | 2.9128 | 2024-02-22 18:00 | 3.6924 | 4.3752 | 4.3752 | 4.3752 | 4.3752
2024-04-23 19:00 | 1.81 | 1.942 | 2.4107 | 2.5357 | 2.6607 | 2024-02-22 19:00 | 3.2427 | 3.8424 | 3.8424 | 3.8424 | 3.8424
2024-04-23 20:00 | 1.7719 | 1.9011 | 2.36 | 2.4823 | 2.6047 | 2024-02-22 20:00 | 2.7436 | 3.2509 | 3.2509 | 3.2509 | 3.2509
2024-04-23 21:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-02-22 21:00 | 2.4692 | 2.9258 | 2.9258 | 2.9258 | 2.9258
2024-04-23 22:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-02-22 22:00 | 2.2253 | 2.6368 | 2.6368 | 2.6368 | 2.6368
2024-04-23 23:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-02-22 23:00 | 2.0043 | 2.375 | 2.375 | 2.375 | 2.375
2024-04-24 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-02-23 | 1.6233 | 1.9234 | 1.9234 | 1.9234 | 1.9234
2024-04-24 01:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-02-23 01:00 | 1.6881 | 2.0002 | 2.0002 | 2.0002 | 2.0002
2024-04-24 02:00 | 1.448 | 1.5536 | 1.9286 | 2.0286 | 2.1286 | 2024-02-23 02:00 | 1.608 | 1.9054 | 1.9054 | 1.9054 | 1.9054
2024-04-24 03:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-02-23 03:00 | 1.829 | 2.1673 | 2.1673 | 2.1673 | 2.1673
2024-04-24 04:00 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 2024-02-23 04:00 | 2.0081 | 2.3795 | 2.3795 | 2.3795 | 2.3795
2024-04-24 05:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-02-23 05:00 | 2.313 | 2.7407 | 2.7407 | 2.7407 | 2.7407
2024-04-24 06:00 | 1.7719 | 1.9011 | 2.36 | 2.4823 | 2.6047 | 2024-02-23 06:00 | 2.6102 | 3.0929 | 3.0929 | 3.0929 | 3.0929
2024-04-24 07:00 | 2.0386 | 2.1873 | 2.7152 | 2.856 | 2.9968 | 2024-02-23 07:00 | 2.9913 | 3.5444 | 3.5444 | 3.5444 | 3.5444
2024-04-24 08:00 | 2.1339 | 2.2895 | 2.8421 | 2.9895 | 3.1369 | 2024-02-23 08:00 | 3.7534 | 4.4474 | 4.4474 | 4.4474 | 4.4474
2024-04-24 09:00 | 2.0386 | 2.1873 | 2.7152 | 2.856 | 2.9968 | 2024-02-23 09:00 | 4.1115 | 4.8718 | 4.8718 | 4.8718 | 4.8718
2024-04-24 10:00 | 1.8481 | 1.9829 | 2.4615 | 2.5891 | 2.7167 | 2024-02-23 10:00 | 4.4354 | 5.2556 | 5.2556 | 5.2556 | 5.2556
2024-04-24 11:00 | 1.3718 | 1.4718 | 1.8271 | 1.9218 | 2.0166 | 2024-02-23 11:00 | 4.4964 | 5.3279 | 5.3279 | 5.3279 | 5.3279
2024-04-24 12:00 | 1.3908 | 1.4923 | 1.8525 | 1.9485 | 2.0446 | 2024-02-23 12:00 | 4.584 | 5.4317 | 5.4317 | 5.4317 | 5.4317
2024-04-24 13:00 | 1.1622 | 1.247 | 1.5479 | 1.6282 | 1.7085 | 2024-02-23 13:00 | 4.4164 | 5.233 | 5.233 | 5.233 | 5.233
2024-04-24 14:00 | 1.0669 | 1.1447 | 1.4211 | 1.4947 | 1.5684 | 2024-02-23 14:00 | 4.3592 | 5.1653 | 5.1653 | 5.1653 | 5.1653
2024-04-24 15:00 | 1.0669 | 1.1447 | 1.4211 | 1.4947 | 1.5684 | 2024-02-23 15:00 | 3.9591 | 4.6912 | 4.6912 | 4.6912 | 4.6912
2024-04-24 16:00 | 1.9243 | 2.0646 | 2.563 | 2.6959 | 2.8288 | 2024-02-23 16:00 | 4.1763 | 4.9486 | 4.9486 | 4.9486 | 4.9486
2024-04-24 17:00 | 2.1529 | 2.3099 | 2.8675 | 3.0162 | 3.1649 | 2024-02-23 17:00 | 4.3783 | 5.1879 | 5.1879 | 5.1879 | 5.1879
2024-04-24 18:00 | 2.0386 | 2.1873 | 2.7152 | 2.856 | 2.9968 | 2024-02-23 18:00 | 3.902 | 4.6235 | 4.6235 | 4.6235 | 4.6235
2024-04-24 19:00 | 1.7528 | 1.8807 | 2.3346 | 2.4557 | 2.5767 | 2024-02-23 19:00 | 3.62 | 4.2894 | 4.2894 | 4.2894 | 4.2894
2024-04-24 20:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-02-23 20:00 | 2.9074 | 3.4451 | 3.4451 | 3.4451 | 3.4451
2024-04-24 21:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-02-23 21:00 | 2.4387 | 2.8897 | 2.8897 | 2.8897 | 2.8897
2024-04-24 22:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-02-23 22:00 | 2.191 | 2.5962 | 2.5962 | 2.5962 | 2.5962
2024-04-24 23:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-02-23 23:00 | 1.8214 | 2.1582 | 2.1582 | 2.1582 | 2.1582
2024-04-25 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-02-24 | 1.669 | 1.9776 | 1.9776 | 1.9776 | 1.9776
2024-04-25 01:00 | 1.4289 | 1.5331 | 1.9032 | 2.0019 | 2.1006 | 2024-02-24 01:00 | 1.5966 | 1.8918 | 1.8918 | 1.8918 | 1.8918
2024-04-25 02:00 | 1.448 | 1.5536 | 1.9286 | 2.0286 | 2.1286 | 2024-02-24 02:00 | 1.5737 | 1.8648 | 1.8648 | 1.8648 | 1.8648
2024-04-25 03:00 | 1.4289 | 1.5331 | 1.9032 | 2.0019 | 2.1006 | 2024-02-24 03:00 | 1.7338 | 2.0544 | 2.0544 | 2.0544 | 2.0544
2024-04-25 04:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-02-24 04:00 | 1.9319 | 2.2892 | 2.2892 | 2.2892 | 2.2892
2024-04-25 05:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-02-24 05:00 | 2.0501 | 2.4291 | 2.4291 | 2.4291 | 2.4291
2024-04-25 06:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-02-24 06:00 | 2.2558 | 2.673 | 2.673 | 2.673 | 2.673
2024-04-25 07:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-02-24 07:00 | 2.2825 | 2.7046 | 2.7046 | 2.7046 | 2.7046
2024-04-25 08:00 | 0.66684 | 0.71547 | 0.88816 | 0.93422 | 0.98027 | 2024-02-24 08:00 | 2.6369 | 3.1245 | 3.1245 | 3.1245 | 3.1245
2024-04-25 09:00 | 0.4001 | 0.42928 | 0.5329 | 0.56053 | 0.58816 | 2024-02-24 09:00 | 3.1742 | 3.7611 | 3.7611 | 3.7611 | 3.7611
2024-04-25 10:00 | 0.34295 | 0.36795 | 0.45677 | 0.48045 | 0.50414 | 2024-02-24 10:00 | 2.8998 | 3.436 | 3.436 | 3.436 | 3.436
2024-04-25 11:00 | 0.41916 | 0.44972 | 0.55827 | 0.58722 | 0.61617 | 2024-02-24 11:00 | 3.0827 | 3.6527 | 3.6527 | 3.6527 | 3.6527
2024-04-25 12:00 | 0.43821 | 0.47016 | 0.58365 | 0.61391 | 0.64418 | 2024-02-24 12:00 | 3.319 | 3.9327 | 3.9327 | 3.9327 | 3.9327
2024-04-25 13:00 | 0.34295 | 0.36795 | 0.45677 | 0.48045 | 0.50414 | 2024-02-24 13:00 | 3.2961 | 3.9056 | 3.9056 | 3.9056 | 3.9056
2024-04-25 14:00 | 0.32389 | 0.34751 | 0.43139 | 0.45376 | 0.47613 | 2024-02-24 14:00 | 3.4066 | 4.0365 | 4.0365 | 4.0365 | 4.0365
2024-04-25 15:00 | 0.57158 | 0.61326 | 0.76128 | 0.80076 | 0.84023 | 2024-02-24 15:00 | 2.9265 | 3.4676 | 3.4676 | 3.4676 | 3.4676
2024-04-25 16:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-02-24 16:00 | 3.1132 | 3.6889 | 3.6889 | 3.6889 | 3.6889
2024-04-25 17:00 | 1.7338 | 1.8602 | 2.3092 | 2.429 | 2.5487 | 2024-02-24 17:00 | 3.1284 | 3.7069 | 3.7069 | 3.7069 | 3.7069
2024-04-25 18:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-02-24 18:00 | 2.5873 | 3.0658 | 3.0658 | 3.0658 | 3.0658
2024-04-25 19:00 | 1.7719 | 1.9011 | 2.36 | 2.4823 | 2.6047 | 2024-02-24 19:00 | 2.3549 | 2.7904 | 2.7904 | 2.7904 | 2.7904
2024-04-25 20:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-02-24 20:00 | 2.3511 | 2.7858 | 2.7858 | 2.7858 | 2.7858
2024-04-25 21:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-02-24 21:00 | 2.4273 | 2.8761 | 2.8761 | 2.8761 | 2.8761
2024-04-25 22:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-02-24 22:00 | 2.0158 | 2.3885 | 2.3885 | 2.3885 | 2.3885
2024-04-25 23:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-02-24 23:00 | 1.6766 | 1.9867 | 1.9867 | 1.9867 | 1.9867
2024-04-26 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-02-25 | 1.5737 | 1.8648 | 1.8648 | 1.8648 | 1.8648
2024-04-26 01:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-02-25 01:00 | 1.5814 | 1.8738 | 1.8738 | 1.8738 | 1.8738
2024-04-26 02:00 | 1.4289 | 1.5331 | 1.9032 | 2.0019 | 2.1006 | 2024-02-25 02:00 | 1.5433 | 1.8286 | 1.8286 | 1.8286 | 1.8286
2024-04-26 03:00 | 1.448 | 1.5536 | 1.9286 | 2.0286 | 2.1286 | 2024-02-25 03:00 | 1.7033 | 2.0183 | 2.0183 | 2.0183 | 2.0183
2024-04-26 04:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-02-25 04:00 | 1.7719 | 2.0995 | 2.0995 | 2.0995 | 2.0995
2024-04-26 05:00 | 1.7338 | 1.8602 | 2.3092 | 2.429 | 2.5487 | 2024-02-25 05:00 | 2.1263 | 2.5194 | 2.5194 | 2.5194 | 2.5194
2024-04-26 06:00 | 1.7338 | 1.8602 | 2.3092 | 2.429 | 2.5487 | 2024-02-25 06:00 | 2.1529 | 2.5511 | 2.5511 | 2.5511 | 2.5511
2024-04-26 07:00 | 2.0196 | 2.1668 | 2.6899 | 2.8293 | 2.9688 | 2024-02-25 07:00 | 2.3397 | 2.7723 | 2.7723 | 2.7723 | 2.7723
2024-04-26 08:00 | 1.81 | 1.942 | 2.4107 | 2.5357 | 2.6607 | 2024-02-25 08:00 | 2.4425 | 2.8942 | 2.8942 | 2.8942 | 2.8942
2024-04-26 09:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-02-25 09:00 | 2.5454 | 3.0161 | 3.0161 | 3.0161 | 3.0161
2024-04-26 10:00 | 1.2956 | 1.39 | 1.7256 | 1.815 | 1.9045 | 2024-02-25 10:00 | 2.5721 | 3.0477 | 3.0477 | 3.0477 | 3.0477
2024-04-26 11:00 | 1.448 | 1.5536 | 1.9286 | 2.0286 | 2.1286 | 2024-02-25 11:00 | 2.6254 | 3.1109 | 3.1109 | 3.1109 | 3.1109
2024-04-26 12:00 | 1.3718 | 1.4718 | 1.8271 | 1.9218 | 2.0166 | 2024-02-25 12:00 | 2.816 | 3.3367 | 3.3367 | 3.3367 | 3.3367
2024-04-26 13:00 | 1.2765 | 1.3696 | 1.7002 | 1.7884 | 1.8765 | 2024-02-25 13:00 | 2.8998 | 3.436 | 3.436 | 3.436 | 3.436
2024-04-26 14:00 | 1.2003 | 1.2878 | 1.5987 | 1.6816 | 1.7645 | 2024-02-25 14:00 | 3.1208 | 3.6979 | 3.6979 | 3.6979 | 3.6979
2024-04-26 15:00 | 1.4289 | 1.5331 | 1.9032 | 2.0019 | 2.1006 | 2024-02-25 15:00 | 3.2199 | 3.8153 | 3.8153 | 3.8153 | 3.8153
2024-04-26 16:00 | 2.0005 | 2.1464 | 2.6645 | 2.8026 | 2.9408 | 2024-02-25 16:00 | 3.1018 | 3.6753 | 3.6753 | 3.6753 | 3.6753
2024-04-26 17:00 | 2.1339 | 2.2895 | 2.8421 | 2.9895 | 3.1369 | 2024-02-25 17:00 | 2.9798 | 3.5308 | 3.5308 | 3.5308 | 3.5308
2024-04-26 18:00 | 1.8862 | 2.0237 | 2.5122 | 2.6425 | 2.7728 | 2024-02-25 18:00 | 2.7779 | 3.2915 | 3.2915 | 3.2915 | 3.2915
2024-04-26 19:00 | 1.7528 | 1.8807 | 2.3346 | 2.4557 | 2.5767 | 2024-02-25 19:00 | 2.5569 | 3.0297 | 3.0297 | 3.0297 | 3.0297
2024-04-26 20:00 | 1.7719 | 1.9011 | 2.36 | 2.4823 | 2.6047 | 2024-02-25 20:00 | 2.4044 | 2.8491 | 2.8491 | 2.8491 | 2.8491
2024-04-26 21:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-02-25 21:00 | 2.3968 | 2.84 | 2.84 | 2.84 | 2.84
2024-04-26 22:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-02-25 22:00 | 2.0043 | 2.375 | 2.375 | 2.375 | 2.375
2024-04-26 23:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-02-25 23:00 | 1.6995 | 2.0138 | 2.0138 | 2.0138 | 2.0138
2024-04-27 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-02-26 | 1.5623 | 1.8512 | 1.8512 | 1.8512 | 1.8512
2024-04-27 01:00 | 1.4099 | 1.5127 | 1.8778 | 1.9752 | 2.0726 | 2024-02-26 01:00 | 1.589 | 1.8828 | 1.8828 | 1.8828 | 1.8828
2024-04-27 02:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-02-26 02:00 | 1.5699 | 1.8602 | 1.8602 | 1.8602 | 1.8602
2024-04-27 03:00 | 1.4289 | 1.5331 | 1.9032 | 2.0019 | 2.1006 | 2024-02-26 03:00 | 1.73 | 2.0499 | 2.0499 | 2.0499 | 2.0499
2024-04-27 04:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-02-26 04:00 | 1.89 | 2.2395 | 2.2395 | 2.2395 | 2.2395
2024-04-27 05:00 | 1.448 | 1.5536 | 1.9286 | 2.0286 | 2.1286 | 2024-02-26 05:00 | 2.1987 | 2.6052 | 2.6052 | 2.6052 | 2.6052
2024-04-27 06:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-02-26 06:00 | 2.6064 | 3.0884 | 3.0884 | 3.0884 | 3.0884
2024-04-27 07:00 | 1.4289 | 1.5331 | 1.9032 | 2.0019 | 2.1006 | 2024-02-26 07:00 | 2.8198 | 3.3412 | 3.3412 | 3.3412 | 3.3412
2024-04-27 08:00 | 1.3527 | 1.4514 | 1.8017 | 1.8951 | 1.9885 | 2024-02-26 08:00 | 3.6352 | 4.3074 | 4.3074 | 4.3074 | 4.3074
2024-04-27 09:00 | 1.3908 | 1.4923 | 1.8525 | 1.9485 | 2.0446 | 2024-02-26 09:00 | 3.5438 | 4.1991 | 4.1991 | 4.1991 | 4.1991
2024-04-27 10:00 | 0.66684 | 0.71547 | 0.88816 | 0.93422 | 0.98027 | 2024-02-26 10:00 | 3.5628 | 4.2217 | 4.2217 | 4.2217 | 4.2217
2024-04-27 11:00 | 0.22863 | 0.2453 | 0.30451 | 0.3203 | 0.33609 | 2024-02-26 11:00 | 3.5666 | 4.2262 | 4.2262 | 4.2262 | 4.2262
2024-04-27 12:00 | 0.095263 | 0.10221 | 0.12688 | 0.13346 | 0.14004 | 2024-02-26 12:00 | 3.5285 | 4.181 | 4.181 | 4.181 | 4.181
2024-04-27 13:00 | 0.07621 | 0.081768 | 0.1015 | 0.10677 | 0.11203 | 2024-02-26 13:00 | 3.7572 | 4.4519 | 4.4519 | 4.4519 | 4.4519
2024-04-27 14:00 | 0.95263 | 1.0221 | 1.2688 | 1.3346 | 1.4004 | 2024-02-26 14:00 | 3.8372 | 4.5467 | 4.5467 | 4.5467 | 4.5467
2024-04-27 15:00 | 0.30484 | 0.32707 | 0.40602 | 0.42707 | 0.44812 | 2024-02-26 15:00 | 3.7915 | 4.4926 | 4.4926 | 4.4926 | 4.4926
2024-04-27 16:00 | 1.4099 | 1.5127 | 1.8778 | 1.9752 | 2.0726 | 2024-02-26 16:00 | 3.902 | 4.6235 | 4.6235 | 4.6235 | 4.6235
2024-04-27 17:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-02-26 17:00 | 3.7991 | 4.5016 | 4.5016 | 4.5016 | 4.5016
2024-04-27 18:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-02-26 18:00 | 3.5933 | 4.2578 | 4.2578 | 4.2578 | 4.2578
2024-04-27 19:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-02-26 19:00 | 3.0332 | 3.5941 | 3.5941 | 3.5941 | 3.5941
2024-04-27 20:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-02-26 20:00 | 2.7283 | 3.2328 | 3.2328 | 3.2328 | 3.2328
2024-04-27 21:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-02-26 21:00 | 2.332 | 2.7633 | 2.7633 | 2.7633 | 2.7633
2024-04-27 22:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-02-26 22:00 | 2.1377 | 2.533 | 2.533 | 2.533 | 2.533
2024-04-27 23:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-02-26 23:00 | 1.8481 | 2.1898 | 2.1898 | 2.1898 | 2.1898
2024-04-28 | 1.3908 | 1.4923 | 1.8525 | 1.9485 | 2.0446 | 2024-02-27 | 1.6004 | 1.8964 | 1.8964 | 1.8964 | 1.8964
2024-04-28 01:00 | 1.4289 | 1.5331 | 1.9032 | 2.0019 | 2.1006 | 2024-02-27 01:00 | 1.6195 | 1.9189 | 1.9189 | 1.9189 | 1.9189
2024-04-28 02:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-02-27 02:00 | 1.6423 | 1.946 | 1.946 | 1.946 | 1.946
2024-04-28 03:00 | 1.448 | 1.5536 | 1.9286 | 2.0286 | 2.1286 | 2024-02-27 03:00 | 1.7643 | 2.0905 | 2.0905 | 2.0905 | 2.0905
2024-04-28 04:00 | 1.448 | 1.5536 | 1.9286 | 2.0286 | 2.1286 | 2024-02-27 04:00 | 1.9091 | 2.2621 | 2.2621 | 2.2621 | 2.2621
2024-04-28 05:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-02-27 05:00 | 2.191 | 2.5962 | 2.5962 | 2.5962 | 2.5962
2024-04-28 06:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-02-27 06:00 | 2.5721 | 3.0477 | 3.0477 | 3.0477 | 3.0477
2024-04-28 07:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-02-27 07:00 | 3.0141 | 3.5715 | 3.5715 | 3.5715 | 3.5715
2024-04-28 08:00 | 1.2956 | 1.39 | 1.7256 | 1.815 | 1.9045 | 2024-02-27 08:00 | 3.3837 | 4.0094 | 4.0094 | 4.0094 | 4.0094
2024-04-28 09:00 | 0.32389 | 0.34751 | 0.43139 | 0.45376 | 0.47613 | 2024-02-27 09:00 | 3.5819 | 4.2442 | 4.2442 | 4.2442 | 4.2442
2024-04-28 10:00 | 0.85737 | 0.91989 | 1.1419 | 1.2011 | 1.2603 | 2024-02-27 10:00 | 3.7572 | 4.4519 | 4.4519 | 4.4519 | 4.4519
2024-04-28 11:00 | 0.97168 | 1.0425 | 1.2942 | 1.3613 | 1.4284 | 2024-02-27 11:00 | 3.8105 | 4.5151 | 4.5151 | 4.5151 | 4.5151
2024-04-28 12:00 | 0.45726 | 0.49061 | 0.60903 | 0.64061 | 0.67218 | 2024-02-27 12:00 | 3.6771 | 4.3571 | 4.3571 | 4.3571 | 4.3571
2024-04-28 13:00 | 0.83831 | 0.89944 | 1.1165 | 1.1744 | 1.2323 | 2024-02-27 13:00 | 4.001 | 4.7409 | 4.7409 | 4.7409 | 4.7409
2024-04-28 14:00 | 0.51442 | 0.55193 | 0.68516 | 0.72068 | 0.75621 | 2024-02-27 14:00 | 4.0734 | 4.8267 | 4.8267 | 4.8267 | 4.8267
2024-04-28 15:00 | 1.3527 | 1.4514 | 1.8017 | 1.8951 | 1.9885 | 2024-02-27 15:00 | 3.9134 | 4.637 | 4.637 | 4.637 | 4.637
2024-04-28 16:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-02-27 16:00 | 3.86 | 4.5738 | 4.5738 | 4.5738 | 4.5738
2024-04-28 17:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-02-27 17:00 | 3.7572 | 4.4519 | 4.4519 | 4.4519 | 4.4519
2024-04-28 18:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-02-27 18:00 | 3.681 | 4.3616 | 4.3616 | 4.3616 | 4.3616
2024-04-28 19:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-02-27 19:00 | 3.197 | 3.7882 | 3.7882 | 3.7882 | 3.7882
2024-04-28 20:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-02-27 20:00 | 2.835 | 3.3593 | 3.3593 | 3.3593 | 3.3593
2024-04-28 21:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-02-27 21:00 | 2.4616 | 2.9168 | 2.9168 | 2.9168 | 2.9168
2024-04-28 22:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-02-27 22:00 | 2.2063 | 2.6143 | 2.6143 | 2.6143 | 2.6143
2024-04-28 23:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-02-27 23:00 | 2.1339 | 2.5285 | 2.5285 | 2.5285 | 2.5285
2024-04-29 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-02-28 | 1.829 | 2.1673 | 2.1673 | 2.1673 | 2.1673
2024-04-29 01:00 | 1.3908 | 1.4923 | 1.8525 | 1.9485 | 2.0446 | 2024-02-28 01:00 | 1.8138 | 2.1492 | 2.1492 | 2.1492 | 2.1492
2024-04-29 02:00 | 1.448 | 1.5536 | 1.9286 | 2.0286 | 2.1286 | 2024-02-28 02:00 | 1.7643 | 2.0905 | 2.0905 | 2.0905 | 2.0905
2024-04-29 03:00 | 1.448 | 1.5536 | 1.9286 | 2.0286 | 2.1286 | 2024-02-28 03:00 | 1.9091 | 2.2621 | 2.2621 | 2.2621 | 2.2621
2024-04-29 04:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-02-28 04:00 | 2.1529 | 2.5511 | 2.5511 | 2.5511 | 2.5511
2024-04-29 05:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-02-28 05:00 | 2.5645 | 3.0387 | 3.0387 | 3.0387 | 3.0387
2024-04-29 06:00 | 1.7528 | 1.8807 | 2.3346 | 2.4557 | 2.5767 | 2024-02-28 06:00 | 3.0065 | 3.5624 | 3.5624 | 3.5624 | 3.5624
2024-04-29 07:00 | 2.0767 | 2.2282 | 2.766 | 2.9094 | 3.0528 | 2024-02-28 07:00 | 3.3914 | 4.0185 | 4.0185 | 4.0185 | 4.0185
2024-04-29 08:00 | 2.1339 | 2.2895 | 2.8421 | 2.9895 | 3.1369 | 2024-02-28 08:00 | 3.4752 | 4.1178 | 4.1178 | 4.1178 | 4.1178
2024-04-29 09:00 | 2.1339 | 2.2895 | 2.8421 | 2.9895 | 3.1369 | 2024-02-28 09:00 | 3.6771 | 4.3571 | 4.3571 | 4.3571 | 4.3571
2024-04-29 10:00 | 2.2482 | 2.4121 | 2.9944 | 3.1496 | 3.3049 | 2024-02-28 10:00 | 3.6581 | 4.3345 | 4.3345 | 4.3345 | 4.3345
2024-04-29 11:00 | 2.1529 | 2.3099 | 2.8675 | 3.0162 | 3.1649 | 2024-02-28 11:00 | 3.6619 | 4.339 | 4.339 | 4.339 | 4.339
2024-04-29 12:00 | 2.0196 | 2.1668 | 2.6899 | 2.8293 | 2.9688 | 2024-02-28 12:00 | 4.3097 | 5.1066 | 5.1066 | 5.1066 | 5.1066
2024-04-29 13:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-02-28 13:00 | 4.2487 | 5.0344 | 5.0344 | 5.0344 | 5.0344
2024-04-29 14:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-02-28 14:00 | 4.9041 | 5.811 | 5.811 | 5.811 | 5.811
2024-04-29 15:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-02-28 15:00 | 4.8317 | 5.7252 | 5.7252 | 5.7252 | 5.7252
2024-04-29 16:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-02-28 16:00 | 4.847 | 5.7433 | 5.7433 | 5.7433 | 5.7433
2024-04-29 17:00 | 2.172 | 2.3304 | 2.8929 | 3.0429 | 3.1929 | 2024-02-28 17:00 | 4.5993 | 5.4498 | 5.4498 | 5.4498 | 5.4498
2024-04-29 18:00 | 2.0577 | 2.2077 | 2.7406 | 2.8827 | 3.0248 | 2024-02-28 18:00 | 4.3554 | 5.1608 | 5.1608 | 5.1608 | 5.1608
2024-04-29 19:00 | 1.7909 | 1.9215 | 2.3854 | 2.509 | 2.6327 | 2024-02-28 19:00 | 3.3837 | 4.0094 | 4.0094 | 4.0094 | 4.0094
2024-04-29 20:00 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 2024-02-28 20:00 | 3.1284 | 3.7069 | 3.7069 | 3.7069 | 3.7069
2024-04-29 21:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-02-28 21:00 | 2.5873 | 3.0658 | 3.0658 | 3.0658 | 3.0658
2024-04-29 22:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-02-28 22:00 | 2.3663 | 2.8039 | 2.8039 | 2.8039 | 2.8039
2024-04-29 23:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-02-28 23:00 | 2.2787 | 2.7001 | 2.7001 | 2.7001 | 2.7001
2024-04-30 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-02-29 | 1.8748 | 2.2214 | 2.2214 | 2.2214 | 2.2214
2024-04-30 01:00 | 1.4099 | 1.5127 | 1.8778 | 1.9752 | 2.0726 | 2024-02-29 01:00 | 1.9396 | 2.2982 | 2.2982 | 2.2982 | 2.2982
2024-04-30 02:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-02-29 02:00 | 1.8557 | 2.1989 | 2.1989 | 2.1989 | 2.1989
2024-04-30 03:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-02-29 03:00 | 1.951 | 2.3118 | 2.3118 | 2.3118 | 2.3118
2024-04-30 04:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-02-29 04:00 | 2.111 | 2.5014 | 2.5014 | 2.5014 | 2.5014
2024-04-30 05:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-02-29 05:00 | 2.8465 | 3.3728 | 3.3728 | 3.3728 | 3.3728
2024-04-30 06:00 | 1.81 | 1.942 | 2.4107 | 2.5357 | 2.6607 | 2024-02-29 06:00 | 2.8388 | 3.3638 | 3.3638 | 3.3638 | 3.3638
2024-04-30 07:00 | 2.2101 | 2.3713 | 2.9436 | 3.0963 | 3.2489 | 2024-02-29 07:00 | 3.4218 | 4.0546 | 4.0546 | 4.0546 | 4.0546
2024-04-30 08:00 | 2.3244 | 2.4939 | 3.0959 | 3.2564 | 3.4169 | 2024-02-29 08:00 | 4.142 | 4.908 | 4.908 | 4.908 | 4.908
2024-04-30 09:00 | 2.2291 | 2.3917 | 2.969 | 3.123 | 3.2769 | 2024-02-29 09:00 | 4.5345 | 5.373 | 5.373 | 5.373 | 5.373
2024-04-30 10:00 | 2.1529 | 2.3099 | 2.8675 | 3.0162 | 3.1649 | 2024-02-29 10:00 | 4.7327 | 5.6078 | 5.6078 | 5.6078 | 5.6078
2024-04-30 11:00 | 2.172 | 2.3304 | 2.8929 | 3.0429 | 3.1929 | 2024-02-29 11:00 | 4.5879 | 5.4362 | 5.4362 | 5.4362 | 5.4362
2024-04-30 12:00 | 2.0958 | 2.2486 | 2.7914 | 2.9361 | 3.0808 | 2024-02-29 12:00 | 5.1366 | 6.0864 | 6.0864 | 6.0864 | 6.0864
2024-04-30 13:00 | 2.1148 | 2.2691 | 2.8167 | 2.9628 | 3.1089 | 2024-02-29 13:00 | 4.9537 | 5.8697 | 5.8697 | 5.8697 | 5.8697
2024-04-30 14:00 | 1.9815 | 2.126 | 2.6391 | 2.776 | 2.9128 | 2024-02-29 14:00 | 4.6222 | 5.4769 | 5.4769 | 5.4769 | 5.4769
2024-04-30 15:00 | 2.0767 | 2.2282 | 2.766 | 2.9094 | 3.0528 | 2024-02-29 15:00 | 4.7555 | 5.6349 | 5.6349 | 5.6349 | 5.6349
2024-04-30 16:00 | 2.0196 | 2.1668 | 2.6899 | 2.8293 | 2.9688 | 2024-02-29 16:00 | 4.626 | 5.4814 | 5.4814 | 5.4814 | 5.4814
2024-04-30 17:00 | 2.0958 | 2.2486 | 2.7914 | 2.9361 | 3.0808 | 2024-02-29 17:00 | 4.1801 | 4.9531 | 4.9531 | 4.9531 | 4.9531
2024-04-30 18:00 | 1.9434 | 2.0851 | 2.5884 | 2.7226 | 2.8568 | 2024-02-29 18:00 | 3.7534 | 4.4474 | 4.4474 | 4.4474 | 4.4474
2024-04-30 19:00 | 1.7338 | 1.8602 | 2.3092 | 2.429 | 2.5487 | 2024-02-29 19:00 | 3.3952 | 4.023 | 4.023 | 4.023 | 4.023
2024-04-30 20:00 | 1.7338 | 1.8602 | 2.3092 | 2.429 | 2.5487 | 2024-02-29 20:00 | 2.7664 | 3.278 | 3.278 | 3.278 | 3.278
2024-04-30 21:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-02-29 21:00 | 2.6331 | 3.12 | 3.12 | 3.12 | 3.12
2024-04-30 22:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-02-29 22:00 | 2.1225 | 2.5149 | 2.5149 | 2.5149 | 2.5149
2024-04-30 23:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-02-29 23:00 | 1.8976 | 2.2485 | 2.2485 | 2.2485 | 2.2485
2024-05-01 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-03-01 | 1.6804 | 1.9912 | 1.9912 | 1.9912 | 1.9912
2024-05-01 01:00 | 1.4289 | 1.5331 | 1.9032 | 2.0019 | 2.1006 | 2024-03-01 01:00 | 1.7071 | 2.0228 | 2.0228 | 2.0228 | 2.0228
2024-05-01 02:00 | 1.4289 | 1.5331 | 1.9032 | 2.0019 | 2.1006 | 2024-03-01 02:00 | 1.7185 | 2.0363 | 2.0363 | 2.0363 | 2.0363
2024-05-01 03:00 | 1.4289 | 1.5331 | 1.9032 | 2.0019 | 2.1006 | 2024-03-01 03:00 | 1.829 | 2.1673 | 2.1673 | 2.1673 | 2.1673
2024-05-01 04:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-03-01 04:00 | 2.0882 | 2.4743 | 2.4743 | 2.4743 | 2.4743
2024-05-01 05:00 | 1.7719 | 1.9011 | 2.36 | 2.4823 | 2.6047 | 2024-03-01 05:00 | 2.5111 | 2.9755 | 2.9755 | 2.9755 | 2.9755
2024-05-01 06:00 | 1.9243 | 2.0646 | 2.563 | 2.6959 | 2.8288 | 2024-03-01 06:00 | 2.8274 | 3.3502 | 3.3502 | 3.3502 | 3.3502
2024-05-01 07:00 | 2.3054 | 2.4735 | 3.0705 | 3.2297 | 3.3889 | 2024-03-01 07:00 | 3.3647 | 3.9869 | 3.9869 | 3.9869 | 3.9869
2024-05-01 08:00 | 1.9624 | 2.1055 | 2.6137 | 2.7493 | 2.8848 | 2024-03-01 08:00 | 4.3249 | 5.1247 | 5.1247 | 5.1247 | 5.1247
2024-05-01 09:00 | 1.9243 | 2.0646 | 2.563 | 2.6959 | 2.8288 | 2024-03-01 09:00 | 4.3135 | 5.1111 | 5.1111 | 5.1111 | 5.1111
2024-05-01 10:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-03-01 10:00 | 4.5574 | 5.4001 | 5.4001 | 5.4001 | 5.4001
2024-05-01 11:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-03-01 11:00 | 4.5459 | 5.3866 | 5.3866 | 5.3866 | 5.3866
2024-05-01 12:00 | 1.7338 | 1.8602 | 2.3092 | 2.429 | 2.5487 | 2024-03-01 12:00 | 4.9041 | 5.811 | 5.811 | 5.811 | 5.811
2024-05-01 13:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-03-01 13:00 | 4.9994 | 5.9239 | 5.9239 | 5.9239 | 5.9239
2024-05-01 14:00 | 2.0767 | 2.2282 | 2.766 | 2.9094 | 3.0528 | 2024-03-01 14:00 | 5.3538 | 6.3438 | 6.3438 | 6.3438 | 6.3438
2024-05-01 15:00 | 2.0196 | 2.1668 | 2.6899 | 2.8293 | 2.9688 | 2024-03-01 15:00 | 4.946 | 5.8606 | 5.8606 | 5.8606 | 5.8606
2024-05-01 16:00 | 2.0577 | 2.2077 | 2.7406 | 2.8827 | 3.0248 | 2024-03-01 16:00 | 4.7365 | 5.6123 | 5.6123 | 5.6123 | 5.6123
2024-05-01 17:00 | 2.1529 | 2.3099 | 2.8675 | 3.0162 | 3.1649 | 2024-03-01 17:00 | 4.424 | 5.2421 | 5.2421 | 5.2421 | 5.2421
2024-05-01 18:00 | 2.1339 | 2.2895 | 2.8421 | 2.9895 | 3.1369 | 2024-03-01 18:00 | 3.8105 | 4.5151 | 4.5151 | 4.5151 | 4.5151
2024-05-01 19:00 | 1.8862 | 2.0237 | 2.5122 | 2.6425 | 2.7728 | 2024-03-01 19:00 | 3.4371 | 4.0727 | 4.0727 | 4.0727 | 4.0727
2024-05-01 20:00 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 2024-03-01 20:00 | 3.2466 | 3.8469 | 3.8469 | 3.8469 | 3.8469
2024-05-01 21:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-03-01 21:00 | 2.5378 | 3.0071 | 3.0071 | 3.0071 | 3.0071
2024-05-01 22:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-03-01 22:00 | 2.1529 | 2.5511 | 2.5511 | 2.5511 | 2.5511
2024-05-01 23:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-03-01 23:00 | 1.8786 | 2.226 | 2.226 | 2.226 | 2.226
2024-05-02 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-03-02 | 1.6614 | 1.9686 | 1.9686 | 1.9686 | 1.9686
2024-05-02 01:00 | 1.4099 | 1.5127 | 1.8778 | 1.9752 | 2.0726 | 2024-03-02 01:00 | 1.6881 | 2.0002 | 2.0002 | 2.0002 | 2.0002
2024-05-02 02:00 | 1.3908 | 1.4923 | 1.8525 | 1.9485 | 2.0446 | 2024-03-02 02:00 | 1.6652 | 1.9731 | 1.9731 | 1.9731 | 1.9731
2024-05-02 03:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-03-02 03:00 | 1.8024 | 2.1357 | 2.1357 | 2.1357 | 2.1357
2024-05-02 04:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-03-02 04:00 | 1.9357 | 2.2937 | 2.2937 | 2.2937 | 2.2937
2024-05-02 05:00 | 1.829 | 1.9624 | 2.4361 | 2.5624 | 2.6887 | 2024-03-02 05:00 | 2.3892 | 2.831 | 2.831 | 2.831 | 2.831
2024-05-02 06:00 | 1.9243 | 2.0646 | 2.563 | 2.6959 | 2.8288 | 2024-03-02 06:00 | 2.5264 | 2.9935 | 2.9935 | 2.9935 | 2.9935
2024-05-02 07:00 | 2.3435 | 2.5144 | 3.1213 | 3.2831 | 3.4449 | 2024-03-02 07:00 | 2.5873 | 3.0658 | 3.0658 | 3.0658 | 3.0658
2024-05-02 08:00 | 2.3054 | 2.4735 | 3.0705 | 3.2297 | 3.3889 | 2024-03-02 08:00 | 3.1094 | 3.6844 | 3.6844 | 3.6844 | 3.6844
2024-05-02 09:00 | 1.8862 | 2.0237 | 2.5122 | 2.6425 | 2.7728 | 2024-03-02 09:00 | 3.2199 | 3.8153 | 3.8153 | 3.8153 | 3.8153
2024-05-02 10:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-03-02 10:00 | 3.3075 | 3.9191 | 3.9191 | 3.9191 | 3.9191
2024-05-02 11:00 | 1.8481 | 1.9829 | 2.4615 | 2.5891 | 2.7167 | 2024-03-02 11:00 | 3.5704 | 4.2307 | 4.2307 | 4.2307 | 4.2307
2024-05-02 12:00 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 2024-03-02 12:00 | 3.3952 | 4.023 | 4.023 | 4.023 | 4.023
2024-05-02 13:00 | 1.9053 | 2.0442 | 2.5376 | 2.6692 | 2.8008 | 2024-03-02 13:00 | 3.3761 | 4.0004 | 4.0004 | 4.0004 | 4.0004
2024-05-02 14:00 | 1.2956 | 1.39 | 1.7256 | 1.815 | 1.9045 | 2024-03-02 14:00 | 3.3342 | 3.9507 | 3.9507 | 3.9507 | 3.9507
2024-05-02 15:00 | 2.0386 | 2.1873 | 2.7152 | 2.856 | 2.9968 | 2024-03-02 15:00 | 3.3266 | 3.9417 | 3.9417 | 3.9417 | 3.9417
2024-05-02 16:00 | 2.1148 | 2.2691 | 2.8167 | 2.9628 | 3.1089 | 2024-03-02 16:00 | 3.3799 | 4.0049 | 4.0049 | 4.0049 | 4.0049
2024-05-02 17:00 | 2.0386 | 2.1873 | 2.7152 | 2.856 | 2.9968 | 2024-03-02 17:00 | 3.0294 | 3.5895 | 3.5895 | 3.5895 | 3.5895
2024-05-02 18:00 | 2.0386 | 2.1873 | 2.7152 | 2.856 | 2.9968 | 2024-03-02 18:00 | 2.8045 | 3.3231 | 3.3231 | 3.3231 | 3.3231
2024-05-02 19:00 | 1.7909 | 1.9215 | 2.3854 | 2.509 | 2.6327 | 2024-03-02 19:00 | 2.553 | 3.0251 | 3.0251 | 3.0251 | 3.0251
2024-05-02 20:00 | 1.7528 | 1.8807 | 2.3346 | 2.4557 | 2.5767 | 2024-03-02 20:00 | 2.3397 | 2.7723 | 2.7723 | 2.7723 | 2.7723
2024-05-02 21:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-03-02 21:00 | 2.1987 | 2.6052 | 2.6052 | 2.6052 | 2.6052
2024-05-02 22:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-03-02 22:00 | 2.1682 | 2.5691 | 2.5691 | 2.5691 | 2.5691
2024-05-02 23:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-03-02 23:00 | 1.6995 | 2.0138 | 2.0138 | 2.0138 | 2.0138
2024-05-03 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-03-03 | 1.5852 | 1.8783 | 1.8783 | 1.8783 | 1.8783
2024-05-03 01:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-03-03 01:00 | 1.5699 | 1.8602 | 1.8602 | 1.8602 | 1.8602
2024-05-03 02:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-03-03 02:00 | 1.6118 | 1.9099 | 1.9099 | 1.9099 | 1.9099
2024-05-03 03:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-03-03 03:00 | 1.749 | 2.0724 | 2.0724 | 2.0724 | 2.0724
2024-05-03 04:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-03-03 04:00 | 1.7948 | 2.1266 | 2.1266 | 2.1266 | 2.1266
2024-05-03 05:00 | 1.7719 | 1.9011 | 2.36 | 2.4823 | 2.6047 | 2024-03-03 05:00 | 2.1758 | 2.5781 | 2.5781 | 2.5781 | 2.5781
2024-05-03 06:00 | 1.8672 | 2.0033 | 2.4869 | 2.6158 | 2.7448 | 2024-03-03 06:00 | 2.313 | 2.7407 | 2.7407 | 2.7407 | 2.7407
2024-05-03 07:00 | 2.2863 | 2.453 | 3.0451 | 3.203 | 3.3609 | 2024-03-03 07:00 | 2.4463 | 2.8987 | 2.8987 | 2.8987 | 2.8987
2024-05-03 08:00 | 2.2673 | 2.4326 | 3.0198 | 3.1763 | 3.3329 | 2024-03-03 08:00 | 2.4921 | 2.9529 | 2.9529 | 2.9529 | 2.9529
2024-05-03 09:00 | 2.191 | 2.3508 | 2.9183 | 3.0696 | 3.2209 | 2024-03-03 09:00 | 2.4692 | 2.9258 | 2.9258 | 2.9258 | 2.9258
2024-05-03 10:00 | 2.0386 | 2.1873 | 2.7152 | 2.856 | 2.9968 | 2024-03-03 10:00 | 2.7664 | 3.278 | 3.278 | 3.278 | 3.278
2024-05-03 11:00 | 1.9243 | 2.0646 | 2.563 | 2.6959 | 2.8288 | 2024-03-03 11:00 | 2.694 | 3.1922 | 3.1922 | 3.1922 | 3.1922
2024-05-03 12:00 | 1.9053 | 2.0442 | 2.5376 | 2.6692 | 2.8008 | 2024-03-03 12:00 | 2.7245 | 3.2283 | 3.2283 | 3.2283 | 3.2283
2024-05-03 13:00 | 1.8862 | 2.0237 | 2.5122 | 2.6425 | 2.7728 | 2024-03-03 13:00 | 3.0865 | 3.6573 | 3.6573 | 3.6573 | 3.6573
2024-05-03 14:00 | 2.0386 | 2.1873 | 2.7152 | 2.856 | 2.9968 | 2024-03-03 14:00 | 3.2809 | 3.8875 | 3.8875 | 3.8875 | 3.8875
2024-05-03 15:00 | 2.0196 | 2.1668 | 2.6899 | 2.8293 | 2.9688 | 2024-03-03 15:00 | 3.1056 | 3.6798 | 3.6798 | 3.6798 | 3.6798
2024-05-03 16:00 | 2.0577 | 2.2077 | 2.7406 | 2.8827 | 3.0248 | 2024-03-03 16:00 | 2.896 | 3.4315 | 3.4315 | 3.4315 | 3.4315
2024-05-03 17:00 | 1.9815 | 2.126 | 2.6391 | 2.776 | 2.9128 | 2024-03-03 17:00 | 2.835 | 3.3593 | 3.3593 | 3.3593 | 3.3593
2024-05-03 18:00 | 2.0577 | 2.2077 | 2.7406 | 2.8827 | 3.0248 | 2024-03-03 18:00 | 2.7436 | 3.2509 | 3.2509 | 3.2509 | 3.2509
2024-05-03 19:00 | 1.7338 | 1.8602 | 2.3092 | 2.429 | 2.5487 | 2024-03-03 19:00 | 2.5264 | 2.9935 | 2.9935 | 2.9935 | 2.9935
2024-05-03 20:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-03-03 20:00 | 2.5111 | 2.9755 | 2.9755 | 2.9755 | 2.9755
2024-05-03 21:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-03-03 21:00 | 2.4235 | 2.8716 | 2.8716 | 2.8716 | 2.8716
2024-05-03 22:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-03-03 22:00 | 1.9853 | 2.3524 | 2.3524 | 2.3524 | 2.3524
2024-05-03 23:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-03-03 23:00 | 1.7528 | 2.077 | 2.077 | 2.077 | 2.077
2024-05-04 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-03-04 | 1.5737 | 1.8648 | 1.8648 | 1.8648 | 1.8648
2024-05-04 01:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-03-04 01:00 | 1.5585 | 1.8467 | 1.8467 | 1.8467 | 1.8467
2024-05-04 02:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-03-04 02:00 | 1.5661 | 1.8557 | 1.8557 | 1.8557 | 1.8557
2024-05-04 03:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-03-04 03:00 | 1.7147 | 2.0318 | 2.0318 | 2.0318 | 2.0318
2024-05-04 04:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-03-04 04:00 | 1.8672 | 2.2124 | 2.2124 | 2.2124 | 2.2124
2024-05-04 05:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-03-04 05:00 | 2.3816 | 2.822 | 2.822 | 2.822 | 2.822
2024-05-04 06:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-03-04 06:00 | 2.5378 | 3.0071 | 3.0071 | 3.0071 | 3.0071
2024-05-04 07:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-03-04 07:00 | 2.7093 | 3.2103 | 3.2103 | 3.2103 | 3.2103
2024-05-04 08:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-03-04 08:00 | 2.8693 | 3.3999 | 3.3999 | 3.3999 | 3.3999
2024-05-04 09:00 | 1.4099 | 1.5127 | 1.8778 | 1.9752 | 2.0726 | 2024-03-04 09:00 | 2.6902 | 3.1877 | 3.1877 | 3.1877 | 3.1877
2024-05-04 10:00 | 1.4099 | 1.5127 | 1.8778 | 1.9752 | 2.0726 | 2024-03-04 10:00 | 2.816 | 3.3367 | 3.3367 | 3.3367 | 3.3367
2024-05-04 11:00 | 1.4099 | 1.5127 | 1.8778 | 1.9752 | 2.0726 | 2024-03-04 11:00 | 2.8274 | 3.3502 | 3.3502 | 3.3502 | 3.3502
2024-05-04 12:00 | 1.3718 | 1.4718 | 1.8271 | 1.9218 | 2.0166 | 2024-03-04 12:00 | 2.9951 | 3.5489 | 3.5489 | 3.5489 | 3.5489
2024-05-04 13:00 | 1.4099 | 1.5127 | 1.8778 | 1.9752 | 2.0726 | 2024-03-04 13:00 | 3.0637 | 3.6302 | 3.6302 | 3.6302 | 3.6302
2024-05-04 14:00 | 1.3908 | 1.4923 | 1.8525 | 1.9485 | 2.0446 | 2024-03-04 14:00 | 3.2885 | 3.8966 | 3.8966 | 3.8966 | 3.8966
2024-05-04 15:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-03-04 15:00 | 3.0065 | 3.5624 | 3.5624 | 3.5624 | 3.5624
2024-05-04 16:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-03-04 16:00 | 3.4333 | 4.0681 | 4.0681 | 4.0681 | 4.0681
2024-05-04 17:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-03-04 17:00 | 3.3799 | 4.0049 | 4.0049 | 4.0049 | 4.0049
2024-05-04 18:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-03-04 18:00 | 3.0027 | 3.5579 | 3.5579 | 3.5579 | 3.5579
2024-05-04 19:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-03-04 19:00 | 2.8655 | 3.3954 | 3.3954 | 3.3954 | 3.3954
2024-05-04 20:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-03-04 20:00 | 2.4959 | 2.9574 | 2.9574 | 2.9574 | 2.9574
2024-05-04 21:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-03-04 21:00 | 2.3968 | 2.84 | 2.84 | 2.84 | 2.84
2024-05-04 22:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-03-04 22:00 | 1.9815 | 2.3479 | 2.3479 | 2.3479 | 2.3479
2024-05-04 23:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-03-04 23:00 | 1.7566 | 2.0815 | 2.0815 | 2.0815 | 2.0815
2024-05-05 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-03-05 | 1.6842 | 1.9957 | 1.9957 | 1.9957 | 1.9957
2024-05-05 01:00 | 1.448 | 1.5536 | 1.9286 | 2.0286 | 2.1286 | 2024-03-05 01:00 | 1.6576 | 1.9641 | 1.9641 | 1.9641 | 1.9641
2024-05-05 02:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-03-05 02:00 | 1.5699 | 1.8602 | 1.8602 | 1.8602 | 1.8602
2024-05-05 03:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-03-05 03:00 | 1.7033 | 2.0183 | 2.0183 | 2.0183 | 2.0183
2024-05-05 04:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-03-05 04:00 | 1.81 | 2.1447 | 2.1447 | 2.1447 | 2.1447
2024-05-05 05:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-03-05 05:00 | 2.0691 | 2.4517 | 2.4517 | 2.4517 | 2.4517
2024-05-05 06:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-03-05 06:00 | 2.4387 | 2.8897 | 2.8897 | 2.8897 | 2.8897
2024-05-05 07:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-03-05 07:00 | 2.7093 | 3.2103 | 3.2103 | 3.2103 | 3.2103
2024-05-05 08:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-03-05 08:00 | 3.0827 | 3.6527 | 3.6527 | 3.6527 | 3.6527
2024-05-05 09:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-03-05 09:00 | 3.1056 | 3.6798 | 3.6798 | 3.6798 | 3.6798
2024-05-05 10:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-03-05 10:00 | 2.9265 | 3.4676 | 3.4676 | 3.4676 | 3.4676
2024-05-05 11:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-03-05 11:00 | 2.9531 | 3.4992 | 3.4992 | 3.4992 | 3.4992
2024-05-05 12:00 | 1.4289 | 1.5331 | 1.9032 | 2.0019 | 2.1006 | 2024-03-05 12:00 | 3.1932 | 3.7837 | 3.7837 | 3.7837 | 3.7837
2024-05-05 13:00 | 1.448 | 1.5536 | 1.9286 | 2.0286 | 2.1286 | 2024-03-05 13:00 | 3.2923 | 3.9011 | 3.9011 | 3.9011 | 3.9011
2024-05-05 14:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-03-05 14:00 | 3.4142 | 4.0456 | 4.0456 | 4.0456 | 4.0456
2024-05-05 15:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-03-05 15:00 | 3.4828 | 4.1268 | 4.1268 | 4.1268 | 4.1268
2024-05-05 16:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-03-05 16:00 | 3.5628 | 4.2217 | 4.2217 | 4.2217 | 4.2217
2024-05-05 17:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-03-05 17:00 | 3.54 | 4.1946 | 4.1946 | 4.1946 | 4.1946
2024-05-05 18:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-03-05 18:00 | 3.3914 | 4.0185 | 4.0185 | 4.0185 | 4.0185
2024-05-05 19:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-03-05 19:00 | 2.8465 | 3.3728 | 3.3728 | 3.3728 | 3.3728
2024-05-05 20:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-03-05 20:00 | 2.7283 | 3.2328 | 3.2328 | 3.2328 | 3.2328
2024-05-05 21:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-03-05 21:00 | 2.5264 | 2.9935 | 2.9935 | 2.9935 | 2.9935
2024-05-05 22:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-03-05 22:00 | 2.2482 | 2.6639 | 2.6639 | 2.6639 | 2.6639
2024-05-05 23:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-03-05 23:00 | 1.7948 | 2.1266 | 2.1266 | 2.1266 | 2.1266
2024-05-06 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-03-06 | 1.5166 | 1.797 | 1.797 | 1.797 | 1.797
2024-05-06 01:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-03-06 01:00 | 1.589 | 1.8828 | 1.8828 | 1.8828 | 1.8828
2024-05-06 02:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-03-06 02:00 | 1.5471 | 1.8331 | 1.8331 | 1.8331 | 1.8331
2024-05-06 03:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-03-06 03:00 | 1.7224 | 2.0408 | 2.0408 | 2.0408 | 2.0408
2024-05-06 04:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-03-06 04:00 | 1.8519 | 2.1944 | 2.1944 | 2.1944 | 2.1944
2024-05-06 05:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-03-06 05:00 | 2.2368 | 2.6504 | 2.6504 | 2.6504 | 2.6504
2024-05-06 06:00 | 1.8672 | 2.0033 | 2.4869 | 2.6158 | 2.7448 | 2024-03-06 06:00 | 2.4311 | 2.8807 | 2.8807 | 2.8807 | 2.8807
2024-05-06 07:00 | 2.2482 | 2.4121 | 2.9944 | 3.1496 | 3.3049 | 2024-03-06 07:00 | 2.7588 | 3.269 | 3.269 | 3.269 | 3.269
2024-05-06 08:00 | 2.0196 | 2.1668 | 2.6899 | 2.8293 | 2.9688 | 2024-03-06 08:00 | 3.0027 | 3.5579 | 3.5579 | 3.5579 | 3.5579
2024-05-06 09:00 | 2.3244 | 2.4939 | 3.0959 | 3.2564 | 3.4169 | 2024-03-06 09:00 | 3.3418 | 3.9598 | 3.9598 | 3.9598 | 3.9598
2024-05-06 10:00 | 2.2101 | 2.3713 | 2.9436 | 3.0963 | 3.2489 | 2024-03-06 10:00 | 3.6047 | 4.2713 | 4.2713 | 4.2713 | 4.2713
2024-05-06 11:00 | 1.9815 | 2.126 | 2.6391 | 2.776 | 2.9128 | 2024-03-06 11:00 | 3.319 | 3.9327 | 3.9327 | 3.9327 | 3.9327
2024-05-06 12:00 | 2.0577 | 2.2077 | 2.7406 | 2.8827 | 3.0248 | 2024-03-06 12:00 | 3.6924 | 4.3752 | 4.3752 | 4.3752 | 4.3752
2024-05-06 13:00 | 2.0577 | 2.2077 | 2.7406 | 2.8827 | 3.0248 | 2024-03-06 13:00 | 3.6619 | 4.339 | 4.339 | 4.339 | 4.339
2024-05-06 14:00 | 1.9434 | 2.0851 | 2.5884 | 2.7226 | 2.8568 | 2024-03-06 14:00 | 3.8677 | 4.5829 | 4.5829 | 4.5829 | 4.5829
2024-05-06 15:00 | 2.0386 | 2.1873 | 2.7152 | 2.856 | 2.9968 | 2024-03-06 15:00 | 3.8677 | 4.5829 | 4.5829 | 4.5829 | 4.5829
2024-05-06 16:00 | 2.0767 | 2.2282 | 2.766 | 2.9094 | 3.0528 | 2024-03-06 16:00 | 4.1154 | 4.8763 | 4.8763 | 4.8763 | 4.8763
2024-05-06 17:00 | 2.0958 | 2.2486 | 2.7914 | 2.9361 | 3.0808 | 2024-03-06 17:00 | 3.841 | 4.5513 | 4.5513 | 4.5513 | 4.5513
2024-05-06 18:00 | 2.0196 | 2.1668 | 2.6899 | 2.8293 | 2.9688 | 2024-03-06 18:00 | 3.2961 | 3.9056 | 3.9056 | 3.9056 | 3.9056
2024-05-06 19:00 | 1.829 | 1.9624 | 2.4361 | 2.5624 | 2.6887 | 2024-03-06 19:00 | 2.9684 | 3.5173 | 3.5173 | 3.5173 | 3.5173
2024-05-06 20:00 | 1.7909 | 1.9215 | 2.3854 | 2.509 | 2.6327 | 2024-03-06 20:00 | 2.6064 | 3.0884 | 3.0884 | 3.0884 | 3.0884
2024-05-06 21:00 | 1.7528 | 1.8807 | 2.3346 | 2.4557 | 2.5767 | 2024-03-06 21:00 | 2.3511 | 2.7858 | 2.7858 | 2.7858 | 2.7858
2024-05-06 22:00 | 1.4289 | 1.5331 | 1.9032 | 2.0019 | 2.1006 | 2024-03-06 22:00 | 2.0996 | 2.4878 | 2.4878 | 2.4878 | 2.4878
2024-05-06 23:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-03-06 23:00 | 1.7681 | 2.095 | 2.095 | 2.095 | 2.095
2024-05-07 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-03-07 | 1.6309 | 1.9325 | 1.9325 | 1.9325 | 1.9325
2024-05-07 01:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-03-07 01:00 | 1.589 | 1.8828 | 1.8828 | 1.8828 | 1.8828
2024-05-07 02:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-03-07 02:00 | 1.5433 | 1.8286 | 1.8286 | 1.8286 | 1.8286
2024-05-07 03:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-03-07 03:00 | 1.7071 | 2.0228 | 2.0228 | 2.0228 | 2.0228
2024-05-07 04:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-03-07 04:00 | 1.9586 | 2.3208 | 2.3208 | 2.3208 | 2.3208
2024-05-07 05:00 | 1.7528 | 1.8807 | 2.3346 | 2.4557 | 2.5767 | 2024-03-07 05:00 | 2.1301 | 2.524 | 2.524 | 2.524 | 2.524
2024-05-07 06:00 | 1.8672 | 2.0033 | 2.4869 | 2.6158 | 2.7448 | 2024-03-07 06:00 | 2.4273 | 2.8761 | 2.8761 | 2.8761 | 2.8761
2024-05-07 07:00 | 2.2291 | 2.3917 | 2.969 | 3.123 | 3.2769 | 2024-03-07 07:00 | 2.835 | 3.3593 | 3.3593 | 3.3593 | 3.3593
2024-05-07 08:00 | 2.172 | 2.3304 | 2.8929 | 3.0429 | 3.1929 | 2024-03-07 08:00 | 3.2466 | 3.8469 | 3.8469 | 3.8469 | 3.8469
2024-05-07 09:00 | 2.191 | 2.3508 | 2.9183 | 3.0696 | 3.2209 | 2024-03-07 09:00 | 3.2046 | 3.7972 | 3.7972 | 3.7972 | 3.7972
2024-05-07 10:00 | 2.1148 | 2.2691 | 2.8167 | 2.9628 | 3.1089 | 2024-03-07 10:00 | 3.3799 | 4.0049 | 4.0049 | 4.0049 | 4.0049
2024-05-07 11:00 | 2.2863 | 2.453 | 3.0451 | 3.203 | 3.3609 | 2024-03-07 11:00 | 3.7648 | 4.461 | 4.461 | 4.461 | 4.461
2024-05-07 12:00 | 2.1148 | 2.2691 | 2.8167 | 2.9628 | 3.1089 | 2024-03-07 12:00 | 3.9706 | 4.7048 | 4.7048 | 4.7048 | 4.7048
2024-05-07 13:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-03-07 13:00 | 3.7534 | 4.4474 | 4.4474 | 4.4474 | 4.4474
2024-05-07 14:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-03-07 14:00 | 3.9553 | 4.6867 | 4.6867 | 4.6867 | 4.6867
2024-05-07 15:00 | 2.0386 | 2.1873 | 2.7152 | 2.856 | 2.9968 | 2024-03-07 15:00 | 4.1573 | 4.926 | 4.926 | 4.926 | 4.926
2024-05-07 16:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-03-07 16:00 | 4.2297 | 5.0118 | 5.0118 | 5.0118 | 5.0118
2024-05-07 17:00 | 2.2101 | 2.3713 | 2.9436 | 3.0963 | 3.2489 | 2024-03-07 17:00 | 3.9134 | 4.637 | 4.637 | 4.637 | 4.637
2024-05-07 18:00 | 2.2482 | 2.4121 | 2.9944 | 3.1496 | 3.3049 | 2024-03-07 18:00 | 3.3113 | 3.9237 | 3.9237 | 3.9237 | 3.9237
2024-05-07 19:00 | 1.81 | 1.942 | 2.4107 | 2.5357 | 2.6607 | 2024-03-07 19:00 | 3.0141 | 3.5715 | 3.5715 | 3.5715 | 3.5715
2024-05-07 20:00 | 1.7719 | 1.9011 | 2.36 | 2.4823 | 2.6047 | 2024-03-07 20:00 | 2.8541 | 3.3818 | 3.3818 | 3.3818 | 3.3818
2024-05-07 21:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-03-07 21:00 | 2.4997 | 2.9619 | 2.9619 | 2.9619 | 2.9619
2024-05-07 22:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-03-07 22:00 | 2.0653 | 2.4472 | 2.4472 | 2.4472 | 2.4472
2024-05-07 23:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-03-07 23:00 | 1.7719 | 2.0995 | 2.0995 | 2.0995 | 2.0995
2024-05-08 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-03-08 | 1.6042 | 1.9009 | 1.9009 | 1.9009 | 1.9009
2024-05-08 01:00 | 1.448 | 1.5536 | 1.9286 | 2.0286 | 2.1286 | 2024-03-08 01:00 | 1.7033 | 2.0183 | 2.0183 | 2.0183 | 2.0183
2024-05-08 02:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-03-08 02:00 | 1.6004 | 1.8964 | 1.8964 | 1.8964 | 1.8964
2024-05-08 03:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-03-08 03:00 | 1.7833 | 2.1131 | 2.1131 | 2.1131 | 2.1131
2024-05-08 04:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-03-08 04:00 | 1.97 | 2.3343 | 2.3343 | 2.3343 | 2.3343
2024-05-08 05:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-03-08 05:00 | 2.3739 | 2.8129 | 2.8129 | 2.8129 | 2.8129
2024-05-08 06:00 | 1.7719 | 1.9011 | 2.36 | 2.4823 | 2.6047 | 2024-03-08 06:00 | 2.7321 | 3.2374 | 3.2374 | 3.2374 | 3.2374
2024-05-08 07:00 | 2.1339 | 2.2895 | 2.8421 | 2.9895 | 3.1369 | 2024-03-08 07:00 | 3.0408 | 3.6031 | 3.6031 | 3.6031 | 3.6031
2024-05-08 08:00 | 2.3244 | 2.4939 | 3.0959 | 3.2564 | 3.4169 | 2024-03-08 08:00 | 3.3685 | 3.9914 | 3.9914 | 3.9914 | 3.9914
2024-05-08 09:00 | 2.191 | 2.3508 | 2.9183 | 3.0696 | 3.2209 | 2024-03-08 09:00 | 3.6047 | 4.2713 | 4.2713 | 4.2713 | 4.2713
2024-05-08 10:00 | 2.191 | 2.3508 | 2.9183 | 3.0696 | 3.2209 | 2024-03-08 10:00 | 3.6619 | 4.339 | 4.339 | 4.339 | 4.339
2024-05-08 11:00 | 2.0386 | 2.1873 | 2.7152 | 2.856 | 2.9968 | 2024-03-08 11:00 | 3.78 | 4.479 | 4.479 | 4.479 | 4.479
2024-05-08 12:00 | 2.191 | 2.3508 | 2.9183 | 3.0696 | 3.2209 | 2024-03-08 12:00 | 3.4447 | 4.0817 | 4.0817 | 4.0817 | 4.0817
2024-05-08 13:00 | 1.9434 | 2.0851 | 2.5884 | 2.7226 | 2.8568 | 2024-03-08 13:00 | 3.8943 | 4.6145 | 4.6145 | 4.6145 | 4.6145
2024-05-08 14:00 | 2.191 | 2.3508 | 2.9183 | 3.0696 | 3.2209 | 2024-03-08 14:00 | 3.9515 | 4.6822 | 4.6822 | 4.6822 | 4.6822
2024-05-08 15:00 | 2.0767 | 2.2282 | 2.766 | 2.9094 | 3.0528 | 2024-03-08 15:00 | 4.0506 | 4.7996 | 4.7996 | 4.7996 | 4.7996
2024-05-08 16:00 | 2.1529 | 2.3099 | 2.8675 | 3.0162 | 3.1649 | 2024-03-08 16:00 | 4.2068 | 4.9847 | 4.9847 | 4.9847 | 4.9847
2024-05-08 17:00 | 2.1529 | 2.3099 | 2.8675 | 3.0162 | 3.1649 | 2024-03-08 17:00 | 4.1611 | 4.9305 | 4.9305 | 4.9305 | 4.9305
2024-05-08 18:00 | 2.1339 | 2.2895 | 2.8421 | 2.9895 | 3.1369 | 2024-03-08 18:00 | 3.9667 | 4.7003 | 4.7003 | 4.7003 | 4.7003
2024-05-08 19:00 | 1.7909 | 1.9215 | 2.3854 | 2.509 | 2.6327 | 2024-03-08 19:00 | 3.8067 | 4.5106 | 4.5106 | 4.5106 | 4.5106
2024-05-08 20:00 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 2024-03-08 20:00 | 3.4638 | 4.1043 | 4.1043 | 4.1043 | 4.1043
2024-05-08 21:00 | 1.7338 | 1.8602 | 2.3092 | 2.429 | 2.5487 | 2024-03-08 21:00 | 2.6559 | 3.1471 | 3.1471 | 3.1471 | 3.1471
2024-05-08 22:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-03-08 22:00 | 2.313 | 2.7407 | 2.7407 | 2.7407 | 2.7407
2024-05-08 23:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-03-08 23:00 | 2.0729 | 2.4562 | 2.4562 | 2.4562 | 2.4562
2024-05-09 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-03-09 | 1.7147 | 2.0318 | 2.0318 | 2.0318 | 2.0318
2024-05-09 01:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-03-09 01:00 | 1.7528 | 2.077 | 2.077 | 2.077 | 2.077
2024-05-09 02:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-03-09 02:00 | 1.6652 | 1.9731 | 1.9731 | 1.9731 | 1.9731
2024-05-09 03:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-03-09 03:00 | 1.9396 | 2.2982 | 2.2982 | 2.2982 | 2.2982
2024-05-09 04:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-03-09 04:00 | 2.0158 | 2.3885 | 2.3885 | 2.3885 | 2.3885
2024-05-09 05:00 | 1.7528 | 1.8807 | 2.3346 | 2.4557 | 2.5767 | 2024-03-09 05:00 | 2.2977 | 2.7226 | 2.7226 | 2.7226 | 2.7226
2024-05-09 06:00 | 1.9053 | 2.0442 | 2.5376 | 2.6692 | 2.8008 | 2024-03-09 06:00 | 2.4235 | 2.8716 | 2.8716 | 2.8716 | 2.8716
2024-05-09 07:00 | 2.2291 | 2.3917 | 2.969 | 3.123 | 3.2769 | 2024-03-09 07:00 | 2.6521 | 3.1425 | 3.1425 | 3.1425 | 3.1425
2024-05-09 08:00 | 2.3054 | 2.4735 | 3.0705 | 3.2297 | 3.3889 | 2024-03-09 08:00 | 2.9455 | 3.4902 | 3.4902 | 3.4902 | 3.4902
2024-05-09 09:00 | 2.2863 | 2.453 | 3.0451 | 3.203 | 3.3609 | 2024-03-09 09:00 | 2.9836 | 3.5354 | 3.5354 | 3.5354 | 3.5354
2024-05-09 10:00 | 2.3054 | 2.4735 | 3.0705 | 3.2297 | 3.3889 | 2024-03-09 10:00 | 2.8655 | 3.3954 | 3.3954 | 3.3954 | 3.3954
2024-05-09 11:00 | 2.191 | 2.3508 | 2.9183 | 3.0696 | 3.2209 | 2024-03-09 11:00 | 3.2656 | 3.8695 | 3.8695 | 3.8695 | 3.8695
2024-05-09 12:00 | 2.2863 | 2.453 | 3.0451 | 3.203 | 3.3609 | 2024-03-09 12:00 | 3.3456 | 3.9643 | 3.9643 | 3.9643 | 3.9643
2024-05-09 13:00 | 2.1148 | 2.2691 | 2.8167 | 2.9628 | 3.1089 | 2024-03-09 13:00 | 3.5933 | 4.2578 | 4.2578 | 4.2578 | 4.2578
2024-05-09 14:00 | 2.0196 | 2.1668 | 2.6899 | 2.8293 | 2.9688 | 2024-03-09 14:00 | 3.9477 | 4.6777 | 4.6777 | 4.6777 | 4.6777
2024-05-09 15:00 | 2.1148 | 2.2691 | 2.8167 | 2.9628 | 3.1089 | 2024-03-09 15:00 | 3.2694 | 3.874 | 3.874 | 3.874 | 3.874
2024-05-09 16:00 | 2.1339 | 2.2895 | 2.8421 | 2.9895 | 3.1369 | 2024-03-09 16:00 | 3.3151 | 3.9282 | 3.9282 | 3.9282 | 3.9282
2024-05-09 17:00 | 2.0386 | 2.1873 | 2.7152 | 2.856 | 2.9968 | 2024-03-09 17:00 | 3.3151 | 3.9282 | 3.9282 | 3.9282 | 3.9282
2024-05-09 18:00 | 2.0577 | 2.2077 | 2.7406 | 2.8827 | 3.0248 | 2024-03-09 18:00 | 2.9417 | 3.4857 | 3.4857 | 3.4857 | 3.4857
2024-05-09 19:00 | 1.7909 | 1.9215 | 2.3854 | 2.509 | 2.6327 | 2024-03-09 19:00 | 2.8388 | 3.3638 | 3.3638 | 3.3638 | 3.3638
2024-05-09 20:00 | 1.7528 | 1.8807 | 2.3346 | 2.4557 | 2.5767 | 2024-03-09 20:00 | 2.5988 | 3.0793 | 3.0793 | 3.0793 | 3.0793
2024-05-09 21:00 | 1.7528 | 1.8807 | 2.3346 | 2.4557 | 2.5767 | 2024-03-09 21:00 | 2.3625 | 2.7994 | 2.7994 | 2.7994 | 2.7994
2024-05-09 22:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-03-09 22:00 | 2.172 | 2.5736 | 2.5736 | 2.5736 | 2.5736
2024-05-09 23:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-03-09 23:00 | 1.8062 | 2.1402 | 2.1402 | 2.1402 | 2.1402
2024-05-10 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-03-10 | 1.7071 | 2.0228 | 2.0228 | 2.0228 | 2.0228
2024-05-10 01:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-03-10 01:00 | 1.5814 | 1.8738 | 1.8738 | 1.8738 | 1.8738
2024-05-10 02:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-03-10 02:00 | 1.5585 | 1.8467 | 1.8467 | 1.8467 | 1.8467
2024-05-10 03:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-03-10 03:00 | 1.7414 | 2.0634 | 2.0634 | 2.0634 | 2.0634
2024-05-10 04:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-03-10 04:00 | 1.8824 | 2.2305 | 2.2305 | 2.2305 | 2.2305
2024-05-10 05:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-03-10 05:00 | 2.1949 | 2.6007 | 2.6007 | 2.6007 | 2.6007
2024-05-10 06:00 | 1.8672 | 2.0033 | 2.4869 | 2.6158 | 2.7448 | 2024-03-10 06:00 | 2.332 | 2.7633 | 2.7633 | 2.7633 | 2.7633
2024-05-10 07:00 | 2.3054 | 2.4735 | 3.0705 | 3.2297 | 3.3889 | 2024-03-10 07:00 | 2.5302 | 2.9981 | 2.9981 | 2.9981 | 2.9981
2024-05-10 08:00 | 2.2482 | 2.4121 | 2.9944 | 3.1496 | 3.3049 | 2024-03-10 08:00 | 2.694 | 3.1922 | 3.1922 | 3.1922 | 3.1922
2024-05-10 09:00 | 2.2863 | 2.453 | 3.0451 | 3.203 | 3.3609 | 2024-03-10 09:00 | 2.3854 | 2.8265 | 2.8265 | 2.8265 | 2.8265
2024-05-10 10:00 | 2.2101 | 2.3713 | 2.9436 | 3.0963 | 3.2489 | 2024-03-10 10:00 | 2.7055 | 3.2057 | 3.2057 | 3.2057 | 3.2057
2024-05-10 11:00 | 2.2291 | 2.3917 | 2.969 | 3.123 | 3.2769 | 2024-03-10 11:00 | 2.7664 | 3.278 | 3.278 | 3.278 | 3.278
2024-05-10 12:00 | 2.1339 | 2.2895 | 2.8421 | 2.9895 | 3.1369 | 2024-03-10 12:00 | 2.9455 | 3.4902 | 3.4902 | 3.4902 | 3.4902
2024-05-10 13:00 | 2.2482 | 2.4121 | 2.9944 | 3.1496 | 3.3049 | 2024-03-10 13:00 | 2.9189 | 3.4586 | 3.4586 | 3.4586 | 3.4586
2024-05-10 14:00 | 2.2482 | 2.4121 | 2.9944 | 3.1496 | 3.3049 | 2024-03-10 14:00 | 3.117 | 3.6934 | 3.6934 | 3.6934 | 3.6934
2024-05-10 15:00 | 2.2482 | 2.4121 | 2.9944 | 3.1496 | 3.3049 | 2024-03-10 15:00 | 3.1589 | 3.743 | 3.743 | 3.743 | 3.743
2024-05-10 16:00 | 2.0767 | 2.2282 | 2.766 | 2.9094 | 3.0528 | 2024-03-10 16:00 | 3.1703 | 3.7566 | 3.7566 | 3.7566 | 3.7566
2024-05-10 17:00 | 2.0958 | 2.2486 | 2.7914 | 2.9361 | 3.0808 | 2024-03-10 17:00 | 3.0827 | 3.6527 | 3.6527 | 3.6527 | 3.6527
2024-05-10 18:00 | 2.172 | 2.3304 | 2.8929 | 3.0429 | 3.1929 | 2024-03-10 18:00 | 2.7588 | 3.269 | 3.269 | 3.269 | 3.269
2024-05-10 19:00 | 1.829 | 1.9624 | 2.4361 | 2.5624 | 2.6887 | 2024-03-10 19:00 | 2.694 | 3.1922 | 3.1922 | 3.1922 | 3.1922
2024-05-10 20:00 | 1.7719 | 1.9011 | 2.36 | 2.4823 | 2.6047 | 2024-03-10 20:00 | 2.454 | 2.9077 | 2.9077 | 2.9077 | 2.9077
2024-05-10 21:00 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 2024-03-10 21:00 | 2.4235 | 2.8716 | 2.8716 | 2.8716 | 2.8716
2024-05-10 22:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-03-10 22:00 | 2.0843 | 2.4698 | 2.4698 | 2.4698 | 2.4698
2024-05-10 23:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-03-10 23:00 | 1.8748 | 2.2214 | 2.2214 | 2.2214 | 2.2214
2024-05-11 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-03-11 | 1.6881 | 2.0002 | 2.0002 | 2.0002 | 2.0002
2024-05-11 01:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-03-11 01:00 | 1.7033 | 2.0183 | 2.0183 | 2.0183 | 2.0183
2024-05-11 02:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-03-11 02:00 | 1.6423 | 1.946 | 1.946 | 1.946 | 1.946
2024-05-11 03:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-03-11 03:00 | 1.7643 | 2.0905 | 2.0905 | 2.0905 | 2.0905
2024-05-11 04:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-03-11 04:00 | 1.9777 | 2.3434 | 2.3434 | 2.3434 | 2.3434
2024-05-11 05:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-03-11 05:00 | 2.1949 | 2.6007 | 2.6007 | 2.6007 | 2.6007
2024-05-11 06:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-03-11 06:00 | 2.6254 | 3.1109 | 3.1109 | 3.1109 | 3.1109
2024-05-11 07:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-03-11 07:00 | 2.5492 | 3.0206 | 3.0206 | 3.0206 | 3.0206
2024-05-11 08:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-03-11 08:00 | 2.6483 | 3.138 | 3.138 | 3.138 | 3.138
2024-05-11 09:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-03-11 09:00 | 2.5988 | 3.0793 | 3.0793 | 3.0793 | 3.0793
2024-05-11 10:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-03-11 10:00 | 3.1399 | 3.7205 | 3.7205 | 3.7205 | 3.7205
2024-05-11 11:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-03-11 11:00 | 3.1856 | 3.7747 | 3.7747 | 3.7747 | 3.7747
2024-05-11 12:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-03-11 12:00 | 3.338 | 3.9553 | 3.9553 | 3.9553 | 3.9553
2024-05-11 13:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-03-11 13:00 | 3.4561 | 4.0952 | 4.0952 | 4.0952 | 4.0952
2024-05-11 14:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-03-11 14:00 | 3.4561 | 4.0952 | 4.0952 | 4.0952 | 4.0952
2024-05-11 15:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-03-11 15:00 | 3.5704 | 4.2307 | 4.2307 | 4.2307 | 4.2307
2024-05-11 16:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-03-11 16:00 | 3.639 | 4.312 | 4.312 | 4.312 | 4.312
2024-05-11 17:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-03-11 17:00 | 3.5171 | 4.1675 | 4.1675 | 4.1675 | 4.1675
2024-05-11 18:00 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 2024-03-11 18:00 | 2.9531 | 3.4992 | 3.4992 | 3.4992 | 3.4992
2024-05-11 19:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-03-11 19:00 | 2.6216 | 3.1064 | 3.1064 | 3.1064 | 3.1064
2024-05-11 20:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-03-11 20:00 | 2.473 | 2.9303 | 2.9303 | 2.9303 | 2.9303
2024-05-11 21:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-03-11 21:00 | 2.2482 | 2.6639 | 2.6639 | 2.6639 | 2.6639
2024-05-11 22:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-03-11 22:00 | 1.9929 | 2.3614 | 2.3614 | 2.3614 | 2.3614
2024-05-11 23:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-03-11 23:00 | 1.6728 | 1.9821 | 1.9821 | 1.9821 | 1.9821
2024-05-12 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-03-12 | 1.6461 | 1.9505 | 1.9505 | 1.9505 | 1.9505
2024-05-12 01:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-03-12 01:00 | 1.7681 | 2.095 | 2.095 | 2.095 | 2.095
2024-05-12 02:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-03-12 02:00 | 1.5852 | 1.8783 | 1.8783 | 1.8783 | 1.8783
2024-05-12 03:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-03-12 03:00 | 1.7109 | 2.0273 | 2.0273 | 2.0273 | 2.0273
2024-05-12 04:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-03-12 04:00 | 1.871 | 2.2169 | 2.2169 | 2.2169 | 2.2169
2024-05-12 05:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-03-12 05:00 | 2.1034 | 2.4924 | 2.4924 | 2.4924 | 2.4924
2024-05-12 06:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-03-12 06:00 | 2.4578 | 2.9123 | 2.9123 | 2.9123 | 2.9123
2024-05-12 07:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-03-12 07:00 | 2.7741 | 3.287 | 3.287 | 3.287 | 3.287
2024-05-12 08:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-03-12 08:00 | 3.037 | 3.5986 | 3.5986 | 3.5986 | 3.5986
2024-05-12 09:00 | 1.448 | 1.5536 | 1.9286 | 2.0286 | 2.1286 | 2024-03-12 09:00 | 3.056 | 3.6211 | 3.6211 | 3.6211 | 3.6211
2024-05-12 10:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-03-12 10:00 | 3.3723 | 3.9959 | 3.9959 | 3.9959 | 3.9959
2024-05-12 11:00 | 1.4289 | 1.5331 | 1.9032 | 2.0019 | 2.1006 | 2024-03-12 11:00 | 3.6352 | 4.3074 | 4.3074 | 4.3074 | 4.3074
2024-05-12 12:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-03-12 12:00 | 3.5704 | 4.2307 | 4.2307 | 4.2307 | 4.2307
2024-05-12 13:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-03-12 13:00 | 4.0201 | 4.7635 | 4.7635 | 4.7635 | 4.7635
2024-05-12 14:00 | 1.4099 | 1.5127 | 1.8778 | 1.9752 | 2.0726 | 2024-03-12 14:00 | 4.3287 | 5.1292 | 5.1292 | 5.1292 | 5.1292
2024-05-12 15:00 | 1.4099 | 1.5127 | 1.8778 | 1.9752 | 2.0726 | 2024-03-12 15:00 | 4.4621 | 5.2872 | 5.2872 | 5.2872 | 5.2872
2024-05-12 16:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-03-12 16:00 | 4.6374 | 5.4949 | 5.4949 | 5.4949 | 5.4949
2024-05-12 17:00 | 1.7528 | 1.8807 | 2.3346 | 2.4557 | 2.5767 | 2024-03-12 17:00 | 4.1801 | 4.9531 | 4.9531 | 4.9531 | 4.9531
2024-05-12 18:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-03-12 18:00 | 3.7572 | 4.4519 | 4.4519 | 4.4519 | 4.4519
2024-05-12 19:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-03-12 19:00 | 3.0827 | 3.6527 | 3.6527 | 3.6527 | 3.6527
2024-05-12 20:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-03-12 20:00 | 2.5645 | 3.0387 | 3.0387 | 3.0387 | 3.0387
2024-05-12 21:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-03-12 21:00 | 2.4921 | 2.9529 | 2.9529 | 2.9529 | 2.9529
2024-05-12 22:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-03-12 22:00 | 2.0577 | 2.4382 | 2.4382 | 2.4382 | 2.4382
2024-05-12 23:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-03-12 23:00 | 1.8862 | 2.235 | 2.235 | 2.235 | 2.235
2024-05-13 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-03-13 | 1.6385 | 1.9415 | 1.9415 | 1.9415 | 1.9415
2024-05-13 01:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-03-13 01:00 | 1.5814 | 1.8738 | 1.8738 | 1.8738 | 1.8738
2024-05-13 02:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-03-13 02:00 | 1.5356 | 1.8196 | 1.8196 | 1.8196 | 1.8196
2024-05-13 03:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-03-13 03:00 | 1.6995 | 2.0138 | 2.0138 | 2.0138 | 2.0138
2024-05-13 04:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-03-13 04:00 | 1.9662 | 2.3298 | 2.3298 | 2.3298 | 2.3298
2024-05-13 05:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-03-13 05:00 | 2.3625 | 2.7994 | 2.7994 | 2.7994 | 2.7994
2024-05-13 06:00 | 1.8862 | 2.0237 | 2.5122 | 2.6425 | 2.7728 | 2024-03-13 06:00 | 2.595 | 3.0748 | 3.0748 | 3.0748 | 3.0748
2024-05-13 07:00 | 2.4768 | 2.6574 | 3.2989 | 3.4699 | 3.641 | 2024-03-13 07:00 | 2.7321 | 3.2374 | 3.2374 | 3.2374 | 3.2374
2024-05-13 08:00 | 2.0767 | 2.2282 | 2.766 | 2.9094 | 3.0528 | 2024-03-13 08:00 | 3.2885 | 3.8966 | 3.8966 | 3.8966 | 3.8966
2024-05-13 09:00 | 1.7909 | 1.9215 | 2.3854 | 2.509 | 2.6327 | 2024-03-13 09:00 | 3.7343 | 4.4248 | 4.4248 | 4.4248 | 4.4248
2024-05-13 10:00 | 1.81 | 1.942 | 2.4107 | 2.5357 | 2.6607 | 2024-03-13 10:00 | 3.7724 | 4.47 | 4.47 | 4.47 | 4.47
2024-05-13 11:00 | 1.829 | 1.9624 | 2.4361 | 2.5624 | 2.6887 | 2024-03-13 11:00 | 3.9896 | 4.7273 | 4.7273 | 4.7273 | 4.7273
2024-05-13 12:00 | 1.8481 | 1.9829 | 2.4615 | 2.5891 | 2.7167 | 2024-03-13 12:00 | 3.841 | 4.5513 | 4.5513 | 4.5513 | 4.5513
2024-05-13 13:00 | 1.829 | 1.9624 | 2.4361 | 2.5624 | 2.6887 | 2024-03-13 13:00 | 4.3897 | 5.2014 | 5.2014 | 5.2014 | 5.2014
2024-05-13 14:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-03-13 14:00 | 4.1458 | 4.9125 | 4.9125 | 4.9125 | 4.9125
2024-05-13 15:00 | 1.8481 | 1.9829 | 2.4615 | 2.5891 | 2.7167 | 2024-03-13 15:00 | 4.1687 | 4.9396 | 4.9396 | 4.9396 | 4.9396
2024-05-13 16:00 | 2.1339 | 2.2895 | 2.8421 | 2.9895 | 3.1369 | 2024-03-13 16:00 | 4.3211 | 5.1202 | 5.1202 | 5.1202 | 5.1202
2024-05-13 17:00 | 2.0767 | 2.2282 | 2.766 | 2.9094 | 3.0528 | 2024-03-13 17:00 | 3.9896 | 4.7273 | 4.7273 | 4.7273 | 4.7273
2024-05-13 18:00 | 2.1529 | 2.3099 | 2.8675 | 3.0162 | 3.1649 | 2024-03-13 18:00 | 3.6505 | 4.3255 | 4.3255 | 4.3255 | 4.3255
2024-05-13 19:00 | 1.7909 | 1.9215 | 2.3854 | 2.509 | 2.6327 | 2024-03-13 19:00 | 3.2237 | 3.8198 | 3.8198 | 3.8198 | 3.8198
2024-05-13 20:00 | 1.7719 | 1.9011 | 2.36 | 2.4823 | 2.6047 | 2024-03-13 20:00 | 3.0675 | 3.6347 | 3.6347 | 3.6347 | 3.6347
2024-05-13 21:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-03-13 21:00 | 2.553 | 3.0251 | 3.0251 | 3.0251 | 3.0251
2024-05-13 22:00 | 1.7338 | 1.8602 | 2.3092 | 2.429 | 2.5487 | 2024-03-13 22:00 | 2.0615 | 2.4427 | 2.4427 | 2.4427 | 2.4427
2024-05-13 23:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-03-13 23:00 | 1.8824 | 2.2305 | 2.2305 | 2.2305 | 2.2305
2024-05-14 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-03-14 | 1.669 | 1.9776 | 1.9776 | 1.9776 | 1.9776
2024-05-14 01:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-03-14 01:00 | 1.7757 | 2.1041 | 2.1041 | 2.1041 | 2.1041
2024-05-14 02:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-03-14 02:00 | 1.7109 | 2.0273 | 2.0273 | 2.0273 | 2.0273
2024-05-14 03:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-03-14 03:00 | 1.9281 | 2.2847 | 2.2847 | 2.2847 | 2.2847
2024-05-14 04:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-03-14 04:00 | 2.0767 | 2.4608 | 2.4608 | 2.4608 | 2.4608
2024-05-14 05:00 | 1.7909 | 1.9215 | 2.3854 | 2.509 | 2.6327 | 2024-03-14 05:00 | 2.393 | 2.8355 | 2.8355 | 2.8355 | 2.8355
2024-05-14 06:00 | 1.9053 | 2.0442 | 2.5376 | 2.6692 | 2.8008 | 2024-03-14 06:00 | 2.7664 | 3.278 | 3.278 | 3.278 | 3.278
2024-05-14 07:00 | 2.4578 | 2.637 | 3.2735 | 3.4433 | 3.613 | 2024-03-14 07:00 | 3.1856 | 3.7747 | 3.7747 | 3.7747 | 3.7747
2024-05-14 08:00 | 2.4768 | 2.6574 | 3.2989 | 3.4699 | 3.641 | 2024-03-14 08:00 | 3.8867 | 4.6054 | 4.6054 | 4.6054 | 4.6054
2024-05-14 09:00 | 2.0005 | 2.1464 | 2.6645 | 2.8026 | 2.9408 | 2024-03-14 09:00 | 4.0887 | 4.8447 | 4.8447 | 4.8447 | 4.8447
2024-05-14 10:00 | 1.9053 | 2.0442 | 2.5376 | 2.6692 | 2.8008 | 2024-03-14 10:00 | 4.142 | 4.908 | 4.908 | 4.908 | 4.908
2024-05-14 11:00 | 2.0767 | 2.2282 | 2.766 | 2.9094 | 3.0528 | 2024-03-14 11:00 | 4.2563 | 5.0434 | 5.0434 | 5.0434 | 5.0434
2024-05-14 12:00 | 2.0005 | 2.1464 | 2.6645 | 2.8026 | 2.9408 | 2024-03-14 12:00 | 4.3135 | 5.1111 | 5.1111 | 5.1111 | 5.1111
2024-05-14 13:00 | 1.81 | 1.942 | 2.4107 | 2.5357 | 2.6607 | 2024-03-14 13:00 | 4.283 | 5.075 | 5.075 | 5.075 | 5.075
2024-05-14 14:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-03-14 14:00 | 4.142 | 4.908 | 4.908 | 4.908 | 4.908
2024-05-14 15:00 | 2.0005 | 2.1464 | 2.6645 | 2.8026 | 2.9408 | 2024-03-14 15:00 | 4.2563 | 5.0434 | 5.0434 | 5.0434 | 5.0434
2024-05-14 16:00 | 2.1529 | 2.3099 | 2.8675 | 3.0162 | 3.1649 | 2024-03-14 16:00 | 4.3935 | 5.206 | 5.206 | 5.206 | 5.206
2024-05-14 17:00 | 2.0577 | 2.2077 | 2.7406 | 2.8827 | 3.0248 | 2024-03-14 17:00 | 4.3478 | 5.1518 | 5.1518 | 5.1518 | 5.1518
2024-05-14 18:00 | 2.0386 | 2.1873 | 2.7152 | 2.856 | 2.9968 | 2024-03-14 18:00 | 3.479 | 4.1223 | 4.1223 | 4.1223 | 4.1223
2024-05-14 19:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-03-14 19:00 | 3.1932 | 3.7837 | 3.7837 | 3.7837 | 3.7837
2024-05-14 20:00 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 2024-03-14 20:00 | 2.7245 | 3.2283 | 3.2283 | 3.2283 | 3.2283
2024-05-14 21:00 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 2024-03-14 21:00 | 2.4806 | 2.9394 | 2.9394 | 2.9394 | 2.9394
2024-05-14 22:00 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 2024-03-14 22:00 | 2.092 | 2.4788 | 2.4788 | 2.4788 | 2.4788
2024-05-14 23:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-03-14 23:00 | 1.8519 | 2.1944 | 2.1944 | 2.1944 | 2.1944
2024-05-15 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-03-15 | 1.8976 | 2.2485 | 2.2485 | 2.2485 | 2.2485
2024-05-15 01:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-03-15 01:00 | 1.829 | 2.1673 | 2.1673 | 2.1673 | 2.1673
2024-05-15 02:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-03-15 02:00 | 1.7147 | 2.0318 | 2.0318 | 2.0318 | 2.0318
2024-05-15 03:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-03-15 03:00 | 1.8024 | 2.1357 | 2.1357 | 2.1357 | 2.1357
2024-05-15 04:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-03-15 04:00 | 2.0234 | 2.3975 | 2.3975 | 2.3975 | 2.3975
2024-05-15 05:00 | 1.7338 | 1.8602 | 2.3092 | 2.429 | 2.5487 | 2024-03-15 05:00 | 2.3206 | 2.7497 | 2.7497 | 2.7497 | 2.7497
2024-05-15 06:00 | 1.8862 | 2.0237 | 2.5122 | 2.6425 | 2.7728 | 2024-03-15 06:00 | 2.7093 | 3.2103 | 3.2103 | 3.2103 | 3.2103
2024-05-15 07:00 | 2.2482 | 2.4121 | 2.9944 | 3.1496 | 3.3049 | 2024-03-15 07:00 | 2.8579 | 3.3864 | 3.3864 | 3.3864 | 3.3864
2024-05-15 08:00 | 2.0767 | 2.2282 | 2.766 | 2.9094 | 3.0528 | 2024-03-15 08:00 | 3.117 | 3.6934 | 3.6934 | 3.6934 | 3.6934
2024-05-15 09:00 | 2.0196 | 2.1668 | 2.6899 | 2.8293 | 2.9688 | 2024-03-15 09:00 | 3.3571 | 3.9778 | 3.9778 | 3.9778 | 3.9778
2024-05-15 10:00 | 2.2482 | 2.4121 | 2.9944 | 3.1496 | 3.3049 | 2024-03-15 10:00 | 3.4218 | 4.0546 | 4.0546 | 4.0546 | 4.0546
2024-05-15 11:00 | 1.8862 | 2.0237 | 2.5122 | 2.6425 | 2.7728 | 2024-03-15 11:00 | 3.7572 | 4.4519 | 4.4519 | 4.4519 | 4.4519
2024-05-15 12:00 | 1.8672 | 2.0033 | 2.4869 | 2.6158 | 2.7448 | 2024-03-15 12:00 | 3.8219 | 4.5287 | 4.5287 | 4.5287 | 4.5287
2024-05-15 13:00 | 1.7909 | 1.9215 | 2.3854 | 2.509 | 2.6327 | 2024-03-15 13:00 | 3.5819 | 4.2442 | 4.2442 | 4.2442 | 4.2442
2024-05-15 14:00 | 2.0005 | 2.1464 | 2.6645 | 2.8026 | 2.9408 | 2024-03-15 14:00 | 3.3266 | 3.9417 | 3.9417 | 3.9417 | 3.9417
2024-05-15 15:00 | 2.172 | 2.3304 | 2.8929 | 3.0429 | 3.1929 | 2024-03-15 15:00 | 3.479 | 4.1223 | 4.1223 | 4.1223 | 4.1223
2024-05-15 16:00 | 2.191 | 2.3508 | 2.9183 | 3.0696 | 3.2209 | 2024-03-15 16:00 | 3.2999 | 3.9101 | 3.9101 | 3.9101 | 3.9101
2024-05-15 17:00 | 2.1529 | 2.3099 | 2.8675 | 3.0162 | 3.1649 | 2024-03-15 17:00 | 3.2351 | 3.8334 | 3.8334 | 3.8334 | 3.8334
2024-05-15 18:00 | 2.0196 | 2.1668 | 2.6899 | 2.8293 | 2.9688 | 2024-03-15 18:00 | 3.0675 | 3.6347 | 3.6347 | 3.6347 | 3.6347
2024-05-15 19:00 | 1.7909 | 1.9215 | 2.3854 | 2.509 | 2.6327 | 2024-03-15 19:00 | 3.0332 | 3.5941 | 3.5941 | 3.5941 | 3.5941
2024-05-15 20:00 | 1.7338 | 1.8602 | 2.3092 | 2.429 | 2.5487 | 2024-03-15 20:00 | 2.6254 | 3.1109 | 3.1109 | 3.1109 | 3.1109
2024-05-15 21:00 | 1.7338 | 1.8602 | 2.3092 | 2.429 | 2.5487 | 2024-03-15 21:00 | 2.4578 | 2.9123 | 2.9123 | 2.9123 | 2.9123
2024-05-15 22:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-03-15 22:00 | 2.0843 | 2.4698 | 2.4698 | 2.4698 | 2.4698
2024-05-15 23:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-03-15 23:00 | 1.8519 | 2.1944 | 2.1944 | 2.1944 | 2.1944
2024-05-16 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-03-16 | 1.871 | 2.2169 | 2.2169 | 2.2169 | 2.2169
2024-05-16 01:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-03-16 01:00 | 1.8824 | 2.2305 | 2.2305 | 2.2305 | 2.2305
2024-05-16 02:00 | 1.448 | 1.5536 | 1.9286 | 2.0286 | 2.1286 | 2024-03-16 02:00 | 1.7605 | 2.086 | 2.086 | 2.086 | 2.086
2024-05-16 03:00 | 1.448 | 1.5536 | 1.9286 | 2.0286 | 2.1286 | 2024-03-16 03:00 | 1.8595 | 2.2034 | 2.2034 | 2.2034 | 2.2034
2024-05-16 04:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-03-16 04:00 | 1.9396 | 2.2982 | 2.2982 | 2.2982 | 2.2982
2024-05-16 05:00 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 2024-03-16 05:00 | 2.111 | 2.5014 | 2.5014 | 2.5014 | 2.5014
2024-05-16 06:00 | 1.9053 | 2.0442 | 2.5376 | 2.6692 | 2.8008 | 2024-03-16 06:00 | 2.2863 | 2.7091 | 2.7091 | 2.7091 | 2.7091
2024-05-16 07:00 | 2.3816 | 2.5552 | 3.172 | 3.3365 | 3.501 | 2024-03-16 07:00 | 2.3168 | 2.7452 | 2.7452 | 2.7452 | 2.7452
2024-05-16 08:00 | 2.2291 | 2.3917 | 2.969 | 3.123 | 3.2769 | 2024-03-16 08:00 | 2.7931 | 3.3096 | 3.3096 | 3.3096 | 3.3096
2024-05-16 09:00 | 2.1148 | 2.2691 | 2.8167 | 2.9628 | 3.1089 | 2024-03-16 09:00 | 2.896 | 3.4315 | 3.4315 | 3.4315 | 3.4315
2024-05-16 10:00 | 2.2101 | 2.3713 | 2.9436 | 3.0963 | 3.2489 | 2024-03-16 10:00 | 2.7893 | 3.3051 | 3.3051 | 3.3051 | 3.3051
2024-05-16 11:00 | 2.0958 | 2.2486 | 2.7914 | 2.9361 | 3.0808 | 2024-03-16 11:00 | 2.957 | 3.5037 | 3.5037 | 3.5037 | 3.5037
2024-05-16 12:00 | 2.2291 | 2.3917 | 2.969 | 3.123 | 3.2769 | 2024-03-16 12:00 | 3.0294 | 3.5895 | 3.5895 | 3.5895 | 3.5895
2024-05-16 13:00 | 2.0196 | 2.1668 | 2.6899 | 2.8293 | 2.9688 | 2024-03-16 13:00 | 3.1665 | 3.7521 | 3.7521 | 3.7521 | 3.7521
2024-05-16 14:00 | 2.0577 | 2.2077 | 2.7406 | 2.8827 | 3.0248 | 2024-03-16 14:00 | 3.0141 | 3.5715 | 3.5715 | 3.5715 | 3.5715
2024-05-16 15:00 | 2.1529 | 2.3099 | 2.8675 | 3.0162 | 3.1649 | 2024-03-16 15:00 | 2.9836 | 3.5354 | 3.5354 | 3.5354 | 3.5354
2024-05-16 16:00 | 2.2101 | 2.3713 | 2.9436 | 3.0963 | 3.2489 | 2024-03-16 16:00 | 2.8998 | 3.436 | 3.436 | 3.436 | 3.436
2024-05-16 17:00 | 2.2101 | 2.3713 | 2.9436 | 3.0963 | 3.2489 | 2024-03-16 17:00 | 2.896 | 3.4315 | 3.4315 | 3.4315 | 3.4315
2024-05-16 18:00 | 2.1148 | 2.2691 | 2.8167 | 2.9628 | 3.1089 | 2024-03-16 18:00 | 2.4006 | 2.8445 | 2.8445 | 2.8445 | 2.8445
2024-05-16 19:00 | 1.8862 | 2.0237 | 2.5122 | 2.6425 | 2.7728 | 2024-03-16 19:00 | 2.3739 | 2.8129 | 2.8129 | 2.8129 | 2.8129
2024-05-16 20:00 | 1.7338 | 1.8602 | 2.3092 | 2.429 | 2.5487 | 2024-03-16 20:00 | 2.3358 | 2.7678 | 2.7678 | 2.7678 | 2.7678
2024-05-16 21:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-03-16 21:00 | 2.2215 | 2.6323 | 2.6323 | 2.6323 | 2.6323
2024-05-16 22:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-03-16 22:00 | 1.9891 | 2.3569 | 2.3569 | 2.3569 | 2.3569
2024-05-16 23:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-03-16 23:00 | 1.7909 | 2.1221 | 2.1221 | 2.1221 | 2.1221
2024-05-17 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-03-17 | 1.7033 | 2.0183 | 2.0183 | 2.0183 | 2.0183
2024-05-17 01:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-03-17 01:00 | 1.7566 | 2.0815 | 2.0815 | 2.0815 | 2.0815
2024-05-17 02:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-03-17 02:00 | 1.7986 | 2.1311 | 2.1311 | 2.1311 | 2.1311
2024-05-17 03:00 | 1.448 | 1.5536 | 1.9286 | 2.0286 | 2.1286 | 2024-03-17 03:00 | 1.7948 | 2.1266 | 2.1266 | 2.1266 | 2.1266
2024-05-17 04:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-03-17 04:00 | 1.9281 | 2.2847 | 2.2847 | 2.2847 | 2.2847
2024-05-17 05:00 | 1.8481 | 1.9829 | 2.4615 | 2.5891 | 2.7167 | 2024-03-17 05:00 | 2.1758 | 2.5781 | 2.5781 | 2.5781 | 2.5781
2024-05-17 06:00 | 1.9624 | 2.1055 | 2.6137 | 2.7493 | 2.8848 | 2024-03-17 06:00 | 2.3054 | 2.7317 | 2.7317 | 2.7317 | 2.7317
2024-05-17 07:00 | 2.2863 | 2.453 | 3.0451 | 3.203 | 3.3609 | 2024-03-17 07:00 | 2.6331 | 3.12 | 3.12 | 3.12 | 3.12
2024-05-17 08:00 | 2.2863 | 2.453 | 3.0451 | 3.203 | 3.3609 | 2024-03-17 08:00 | 2.8083 | 3.3277 | 3.3277 | 3.3277 | 3.3277
2024-05-17 09:00 | 2.3625 | 2.5348 | 3.1466 | 3.3098 | 3.473 | 2024-03-17 09:00 | 2.9265 | 3.4676 | 3.4676 | 3.4676 | 3.4676
2024-05-17 10:00 | 2.1529 | 2.3099 | 2.8675 | 3.0162 | 3.1649 | 2024-03-17 10:00 | 3.0865 | 3.6573 | 3.6573 | 3.6573 | 3.6573
2024-05-17 11:00 | 1.9053 | 2.0442 | 2.5376 | 2.6692 | 2.8008 | 2024-03-17 11:00 | 3.2237 | 3.8198 | 3.8198 | 3.8198 | 3.8198
2024-05-17 12:00 | 1.9624 | 2.1055 | 2.6137 | 2.7493 | 2.8848 | 2024-03-17 12:00 | 3.3075 | 3.9191 | 3.9191 | 3.9191 | 3.9191
2024-05-17 13:00 | 2.0577 | 2.2077 | 2.7406 | 2.8827 | 3.0248 | 2024-03-17 13:00 | 3.3342 | 3.9507 | 3.9507 | 3.9507 | 3.9507
2024-05-17 14:00 | 1.9053 | 2.0442 | 2.5376 | 2.6692 | 2.8008 | 2024-03-17 14:00 | 3.2542 | 3.8559 | 3.8559 | 3.8559 | 3.8559
2024-05-17 15:00 | 2.1148 | 2.2691 | 2.8167 | 2.9628 | 3.1089 | 2024-03-17 15:00 | 3.2123 | 3.8063 | 3.8063 | 3.8063 | 3.8063
2024-05-17 16:00 | 1.9815 | 2.126 | 2.6391 | 2.776 | 2.9128 | 2024-03-17 16:00 | 3.1437 | 3.725 | 3.725 | 3.725 | 3.725
2024-05-17 17:00 | 2.0577 | 2.2077 | 2.7406 | 2.8827 | 3.0248 | 2024-03-17 17:00 | 2.9531 | 3.4992 | 3.4992 | 3.4992 | 3.4992
2024-05-17 18:00 | 1.9434 | 2.0851 | 2.5884 | 2.7226 | 2.8568 | 2024-03-17 18:00 | 2.5302 | 2.9981 | 2.9981 | 2.9981 | 2.9981
2024-05-17 19:00 | 1.829 | 1.9624 | 2.4361 | 2.5624 | 2.6887 | 2024-03-17 19:00 | 2.4273 | 2.8761 | 2.8761 | 2.8761 | 2.8761
2024-05-17 20:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-03-17 20:00 | 2.1949 | 2.6007 | 2.6007 | 2.6007 | 2.6007
2024-05-17 21:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-03-17 21:00 | 2.1301 | 2.524 | 2.524 | 2.524 | 2.524
2024-05-17 22:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-03-17 22:00 | 1.9243 | 2.2801 | 2.2801 | 2.2801 | 2.2801
2024-05-17 23:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-03-17 23:00 | 1.5852 | 1.8783 | 1.8783 | 1.8783 | 1.8783
2024-05-18 | 1.4289 | 1.5331 | 1.9032 | 2.0019 | 2.1006 | 2024-03-18 | 1.5776 | 1.8693 | 1.8693 | 1.8693 | 1.8693
2024-05-18 01:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-03-18 01:00 | 1.5623 | 1.8512 | 1.8512 | 1.8512 | 1.8512
2024-05-18 02:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-03-18 02:00 | 1.528 | 1.8106 | 1.8106 | 1.8106 | 1.8106
2024-05-18 03:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-03-18 03:00 | 1.7566 | 2.0815 | 2.0815 | 2.0815 | 2.0815
2024-05-18 04:00 | 1.448 | 1.5536 | 1.9286 | 2.0286 | 2.1286 | 2024-03-18 04:00 | 1.97 | 2.3343 | 2.3343 | 2.3343 | 2.3343
2024-05-18 05:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-03-18 05:00 | 2.2673 | 2.6865 | 2.6865 | 2.6865 | 2.6865
2024-05-18 06:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-03-18 06:00 | 2.595 | 3.0748 | 3.0748 | 3.0748 | 3.0748
2024-05-18 07:00 | 1.4099 | 1.5127 | 1.8778 | 1.9752 | 2.0726 | 2024-03-18 07:00 | 3.0903 | 3.6618 | 3.6618 | 3.6618 | 3.6618
2024-05-18 08:00 | 1.4099 | 1.5127 | 1.8778 | 1.9752 | 2.0726 | 2024-03-18 08:00 | 2.9722 | 3.5218 | 3.5218 | 3.5218 | 3.5218
2024-05-18 09:00 | 1.1813 | 1.2674 | 1.5733 | 1.6549 | 1.7365 | 2024-03-18 09:00 | 3.5819 | 4.2442 | 4.2442 | 4.2442 | 4.2442
2024-05-18 10:00 | 1.2003 | 1.2878 | 1.5987 | 1.6816 | 1.7645 | 2024-03-18 10:00 | 3.7686 | 4.4655 | 4.4655 | 4.4655 | 4.4655
2024-05-18 11:00 | 1.2575 | 1.3492 | 1.6748 | 1.7617 | 1.8485 | 2024-03-18 11:00 | 3.6581 | 4.3345 | 4.3345 | 4.3345 | 4.3345
2024-05-18 12:00 | 0.95263 | 1.0221 | 1.2688 | 1.3346 | 1.4004 | 2024-03-18 12:00 | 4.123 | 4.8854 | 4.8854 | 4.8854 | 4.8854
2024-05-18 13:00 | 1.2384 | 1.3287 | 1.6494 | 1.735 | 1.8205 | 2024-03-18 13:00 | 3.7152 | 4.4023 | 4.4023 | 4.4023 | 4.4023
2024-05-18 14:00 | 1.2384 | 1.3287 | 1.6494 | 1.735 | 1.8205 | 2024-03-18 14:00 | 4.0277 | 4.7725 | 4.7725 | 4.7725 | 4.7725
2024-05-18 15:00 | 1.4099 | 1.5127 | 1.8778 | 1.9752 | 2.0726 | 2024-03-18 15:00 | 3.8639 | 4.5784 | 4.5784 | 4.5784 | 4.5784
2024-05-18 16:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-03-18 16:00 | 3.8982 | 4.619 | 4.619 | 4.619 | 4.619
2024-05-18 17:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-03-18 17:00 | 3.5362 | 4.19 | 4.19 | 4.19 | 4.19
2024-05-18 18:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-03-18 18:00 | 3.3037 | 3.9146 | 3.9146 | 3.9146 | 3.9146
2024-05-18 19:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-03-18 19:00 | 2.7474 | 3.2554 | 3.2554 | 3.2554 | 3.2554
2024-05-18 20:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-03-18 20:00 | 2.7055 | 3.2057 | 3.2057 | 3.2057 | 3.2057
2024-05-18 21:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-03-18 21:00 | 2.2177 | 2.6278 | 2.6278 | 2.6278 | 2.6278
2024-05-18 22:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-03-18 22:00 | 2.0196 | 2.393 | 2.393 | 2.393 | 2.393
2024-05-18 23:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-03-18 23:00 | 1.81 | 2.1447 | 2.1447 | 2.1447 | 2.1447
2024-05-19 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-03-19 | 1.6157 | 1.9144 | 1.9144 | 1.9144 | 1.9144
2024-05-19 01:00 | 1.448 | 1.5536 | 1.9286 | 2.0286 | 2.1286 | 2024-03-19 01:00 | 1.7452 | 2.0679 | 2.0679 | 2.0679 | 2.0679
2024-05-19 02:00 | 1.3908 | 1.4923 | 1.8525 | 1.9485 | 2.0446 | 2024-03-19 02:00 | 1.6347 | 1.937 | 1.937 | 1.937 | 1.937
2024-05-19 03:00 | 1.4289 | 1.5331 | 1.9032 | 2.0019 | 2.1006 | 2024-03-19 03:00 | 1.8329 | 2.1718 | 2.1718 | 2.1718 | 2.1718
2024-05-19 04:00 | 1.4289 | 1.5331 | 1.9032 | 2.0019 | 2.1006 | 2024-03-19 04:00 | 1.97 | 2.3343 | 2.3343 | 2.3343 | 2.3343
2024-05-19 05:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-03-19 05:00 | 2.2291 | 2.6414 | 2.6414 | 2.6414 | 2.6414
2024-05-19 06:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-03-19 06:00 | 2.5111 | 2.9755 | 2.9755 | 2.9755 | 2.9755
2024-05-19 07:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-03-19 07:00 | 2.896 | 3.4315 | 3.4315 | 3.4315 | 3.4315
2024-05-19 08:00 | 1.4289 | 1.5331 | 1.9032 | 2.0019 | 2.1006 | 2024-03-19 08:00 | 3.1818 | 3.7701 | 3.7701 | 3.7701 | 3.7701
2024-05-19 09:00 | 1.086 | 1.1652 | 1.4464 | 1.5214 | 1.5964 | 2024-03-19 09:00 | 3.4295 | 4.0636 | 4.0636 | 4.0636 | 4.0636
2024-05-19 10:00 | 0.95263 | 1.0221 | 1.2688 | 1.3346 | 1.4004 | 2024-03-19 10:00 | 3.7305 | 4.4203 | 4.4203 | 4.4203 | 4.4203
2024-05-19 11:00 | 1.2384 | 1.3287 | 1.6494 | 1.735 | 1.8205 | 2024-03-19 11:00 | 4.0201 | 4.7635 | 4.7635 | 4.7635 | 4.7635
2024-05-19 12:00 | 1.1432 | 1.2265 | 1.5226 | 1.6015 | 1.6805 | 2024-03-19 12:00 | 3.8181 | 4.5242 | 4.5242 | 4.5242 | 4.5242
2024-05-19 13:00 | 1.1622 | 1.247 | 1.5479 | 1.6282 | 1.7085 | 2024-03-19 13:00 | 3.6962 | 4.3797 | 4.3797 | 4.3797 | 4.3797
2024-05-19 14:00 | 1.1622 | 1.247 | 1.5479 | 1.6282 | 1.7085 | 2024-03-19 14:00 | 3.7267 | 4.4158 | 4.4158 | 4.4158 | 4.4158
2024-05-19 15:00 | 1.1622 | 1.247 | 1.5479 | 1.6282 | 1.7085 | 2024-03-19 15:00 | 3.9439 | 4.6732 | 4.6732 | 4.6732 | 4.6732
2024-05-19 16:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-03-19 16:00 | 3.9248 | 4.6506 | 4.6506 | 4.6506 | 4.6506
2024-05-19 17:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-03-19 17:00 | 3.9248 | 4.6506 | 4.6506 | 4.6506 | 4.6506
2024-05-19 18:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-03-19 18:00 | 3.6924 | 4.3752 | 4.3752 | 4.3752 | 4.3752
2024-05-19 19:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-03-19 19:00 | 3.0408 | 3.6031 | 3.6031 | 3.6031 | 3.6031
2024-05-19 20:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-03-19 20:00 | 2.473 | 2.9303 | 2.9303 | 2.9303 | 2.9303
2024-05-19 21:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-03-19 21:00 | 2.2215 | 2.6323 | 2.6323 | 2.6323 | 2.6323
2024-05-19 22:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-03-19 22:00 | 1.9586 | 2.3208 | 2.3208 | 2.3208 | 2.3208
2024-05-19 23:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-03-19 23:00 | 1.8481 | 2.1898 | 2.1898 | 2.1898 | 2.1898
2024-05-20 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-03-20 | 1.7147 | 2.0318 | 2.0318 | 2.0318 | 2.0318
2024-05-20 01:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-03-20 01:00 | 1.6804 | 1.9912 | 1.9912 | 1.9912 | 1.9912
2024-05-20 02:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-03-20 02:00 | 1.6919 | 2.0047 | 2.0047 | 2.0047 | 2.0047
2024-05-20 03:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-03-20 03:00 | 1.8748 | 2.2214 | 2.2214 | 2.2214 | 2.2214
2024-05-20 04:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-03-20 04:00 | 2.1377 | 2.533 | 2.533 | 2.533 | 2.533
2024-05-20 05:00 | 1.7909 | 1.9215 | 2.3854 | 2.509 | 2.6327 | 2024-03-20 05:00 | 2.5835 | 3.0613 | 3.0613 | 3.0613 | 3.0613
2024-05-20 06:00 | 2.3435 | 2.5144 | 3.1213 | 3.2831 | 3.4449 | 2024-03-20 06:00 | 2.976 | 3.5263 | 3.5263 | 3.5263 | 3.5263
2024-05-20 07:00 | 2.534 | 2.7188 | 3.375 | 3.55 | 3.725 | 2024-03-20 07:00 | 3.3914 | 4.0185 | 4.0185 | 4.0185 | 4.0185
2024-05-20 08:00 | 2.7055 | 2.9027 | 3.6034 | 3.7902 | 3.9771 | 2024-03-20 08:00 | 3.498 | 4.1449 | 4.1449 | 4.1449 | 4.1449
2024-05-20 09:00 | 2.4387 | 2.6166 | 3.2481 | 3.4166 | 3.585 | 2024-03-20 09:00 | 3.7991 | 4.5016 | 4.5016 | 4.5016 | 4.5016
2024-05-20 10:00 | 2.4006 | 2.5757 | 3.1974 | 3.3632 | 3.529 | 2024-03-20 10:00 | 3.5666 | 4.2262 | 4.2262 | 4.2262 | 4.2262
2024-05-20 11:00 | 2.3816 | 2.5552 | 3.172 | 3.3365 | 3.501 | 2024-03-20 11:00 | 3.7838 | 4.4835 | 4.4835 | 4.4835 | 4.4835
2024-05-20 12:00 | 2.0577 | 2.2077 | 2.7406 | 2.8827 | 3.0248 | 2024-03-20 12:00 | 3.6162 | 4.2849 | 4.2849 | 4.2849 | 4.2849
2024-05-20 13:00 | 2.2101 | 2.3713 | 2.9436 | 3.0963 | 3.2489 | 2024-03-20 13:00 | 3.5438 | 4.1991 | 4.1991 | 4.1991 | 4.1991
2024-05-20 14:00 | 2.3816 | 2.5552 | 3.172 | 3.3365 | 3.501 | 2024-03-20 14:00 | 3.4561 | 4.0952 | 4.0952 | 4.0952 | 4.0952
2024-05-20 15:00 | 2.2863 | 2.453 | 3.0451 | 3.203 | 3.3609 | 2024-03-20 15:00 | 3.3228 | 3.9372 | 3.9372 | 3.9372 | 3.9372
2024-05-20 16:00 | 2.1529 | 2.3099 | 2.8675 | 3.0162 | 3.1649 | 2024-03-20 16:00 | 3.3952 | 4.023 | 4.023 | 4.023 | 4.023
2024-05-20 17:00 | 2.2101 | 2.3713 | 2.9436 | 3.0963 | 3.2489 | 2024-03-20 17:00 | 3.3075 | 3.9191 | 3.9191 | 3.9191 | 3.9191
2024-05-20 18:00 | 2.3054 | 2.4735 | 3.0705 | 3.2297 | 3.3889 | 2024-03-20 18:00 | 3.056 | 3.6211 | 3.6211 | 3.6211 | 3.6211
2024-05-20 19:00 | 1.8672 | 2.0033 | 2.4869 | 2.6158 | 2.7448 | 2024-03-20 19:00 | 2.7245 | 3.2283 | 3.2283 | 3.2283 | 3.2283
2024-05-20 20:00 | 1.7338 | 1.8602 | 2.3092 | 2.429 | 2.5487 | 2024-03-20 20:00 | 2.6559 | 3.1471 | 3.1471 | 3.1471 | 3.1471
2024-05-20 21:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-03-20 21:00 | 2.2863 | 2.7091 | 2.7091 | 2.7091 | 2.7091
2024-05-20 22:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-03-20 22:00 | 1.8672 | 2.2124 | 2.2124 | 2.2124 | 2.2124
2024-05-20 23:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-03-20 23:00 | 1.73 | 2.0499 | 2.0499 | 2.0499 | 2.0499
2024-05-21 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-03-21 | 1.669 | 1.9776 | 1.9776 | 1.9776 | 1.9776
2024-05-21 01:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-03-21 01:00 | 1.6118 | 1.9099 | 1.9099 | 1.9099 | 1.9099
2024-05-21 02:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-03-21 02:00 | 1.5699 | 1.8602 | 1.8602 | 1.8602 | 1.8602
2024-05-21 03:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-03-21 03:00 | 1.7071 | 2.0228 | 2.0228 | 2.0228 | 2.0228
2024-05-21 04:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-03-21 04:00 | 1.9853 | 2.3524 | 2.3524 | 2.3524 | 2.3524
2024-05-21 05:00 | 1.7528 | 1.8807 | 2.3346 | 2.4557 | 2.5767 | 2024-03-21 05:00 | 2.2139 | 2.6233 | 2.6233 | 2.6233 | 2.6233
2024-05-21 06:00 | 2.2482 | 2.4121 | 2.9944 | 3.1496 | 3.3049 | 2024-03-21 06:00 | 2.4806 | 2.9394 | 2.9394 | 2.9394 | 2.9394
2024-05-21 07:00 | 2.4387 | 2.6166 | 3.2481 | 3.4166 | 3.585 | 2024-03-21 07:00 | 3.0637 | 3.6302 | 3.6302 | 3.6302 | 3.6302
2024-05-21 08:00 | 2.4578 | 2.637 | 3.2735 | 3.4433 | 3.613 | 2024-03-21 08:00 | 2.9417 | 3.4857 | 3.4857 | 3.4857 | 3.4857
2024-05-21 09:00 | 2.3625 | 2.5348 | 3.1466 | 3.3098 | 3.473 | 2024-03-21 09:00 | 2.835 | 3.3593 | 3.3593 | 3.3593 | 3.3593
2024-05-21 10:00 | 2.3244 | 2.4939 | 3.0959 | 3.2564 | 3.4169 | 2024-03-21 10:00 | 2.6902 | 3.1877 | 3.1877 | 3.1877 | 3.1877
2024-05-21 11:00 | 2.2482 | 2.4121 | 2.9944 | 3.1496 | 3.3049 | 2024-03-21 11:00 | 2.8769 | 3.4089 | 3.4089 | 3.4089 | 3.4089
2024-05-21 12:00 | 2.1529 | 2.3099 | 2.8675 | 3.0162 | 3.1649 | 2024-03-21 12:00 | 2.9646 | 3.5128 | 3.5128 | 3.5128 | 3.5128
2024-05-21 13:00 | 2.1148 | 2.2691 | 2.8167 | 2.9628 | 3.1089 | 2024-03-21 13:00 | 2.7779 | 3.2915 | 3.2915 | 3.2915 | 3.2915
2024-05-21 14:00 | 2.2101 | 2.3713 | 2.9436 | 3.0963 | 3.2489 | 2024-03-21 14:00 | 2.8236 | 3.3457 | 3.3457 | 3.3457 | 3.3457
2024-05-21 15:00 | 2.172 | 2.3304 | 2.8929 | 3.0429 | 3.1929 | 2024-03-21 15:00 | 3.0179 | 3.576 | 3.576 | 3.576 | 3.576
2024-05-21 16:00 | 2.1339 | 2.2895 | 2.8421 | 2.9895 | 3.1369 | 2024-03-21 16:00 | 3.0751 | 3.6437 | 3.6437 | 3.6437 | 3.6437
2024-05-21 17:00 | 2.1339 | 2.2895 | 2.8421 | 2.9895 | 3.1369 | 2024-03-21 17:00 | 3.1208 | 3.6979 | 3.6979 | 3.6979 | 3.6979
2024-05-21 18:00 | 2.0958 | 2.2486 | 2.7914 | 2.9361 | 3.0808 | 2024-03-21 18:00 | 2.9303 | 3.4721 | 3.4721 | 3.4721 | 3.4721
2024-05-21 19:00 | 1.9053 | 2.0442 | 2.5376 | 2.6692 | 2.8008 | 2024-03-21 19:00 | 2.8731 | 3.4044 | 3.4044 | 3.4044 | 3.4044
2024-05-21 20:00 | 1.7909 | 1.9215 | 2.3854 | 2.509 | 2.6327 | 2024-03-21 20:00 | 2.6788 | 3.1741 | 3.1741 | 3.1741 | 3.1741
2024-05-21 21:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-03-21 21:00 | 2.4806 | 2.9394 | 2.9394 | 2.9394 | 2.9394
2024-05-21 22:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-03-21 22:00 | 1.8976 | 2.2485 | 2.2485 | 2.2485 | 2.2485
2024-05-21 23:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-03-21 23:00 | 1.9434 | 2.3027 | 2.3027 | 2.3027 | 2.3027
2024-05-22 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-03-22 | 1.5585 | 1.8467 | 1.8467 | 1.8467 | 1.8467
2024-05-22 01:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-03-22 01:00 | 1.6423 | 1.946 | 1.946 | 1.946 | 1.946
2024-05-22 02:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-03-22 02:00 | 1.5623 | 1.8512 | 1.8512 | 1.8512 | 1.8512
2024-05-22 03:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-03-22 03:00 | 1.7338 | 2.0544 | 2.0544 | 2.0544 | 2.0544
2024-05-22 04:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-03-22 04:00 | 1.9396 | 2.2982 | 2.2982 | 2.2982 | 2.2982
2024-05-22 05:00 | 1.7528 | 1.8807 | 2.3346 | 2.4557 | 2.5767 | 2024-03-22 05:00 | 2.2596 | 2.6775 | 2.6775 | 2.6775 | 2.6775
2024-05-22 06:00 | 1.9624 | 2.1055 | 2.6137 | 2.7493 | 2.8848 | 2024-03-22 06:00 | 2.4768 | 2.9348 | 2.9348 | 2.9348 | 2.9348
2024-05-22 07:00 | 2.534 | 2.7188 | 3.375 | 3.55 | 3.725 | 2024-03-22 07:00 | 2.8122 | 3.3322 | 3.3322 | 3.3322 | 3.3322
2024-05-22 08:00 | 2.5721 | 2.7597 | 3.4258 | 3.6034 | 3.781 | 2024-03-22 08:00 | 2.9036 | 3.4405 | 3.4405 | 3.4405 | 3.4405
2024-05-22 09:00 | 2.3816 | 2.5552 | 3.172 | 3.3365 | 3.501 | 2024-03-22 09:00 | 2.8236 | 3.3457 | 3.3457 | 3.3457 | 3.3457
2024-05-22 10:00 | 2.2673 | 2.4326 | 3.0198 | 3.1763 | 3.3329 | 2024-03-22 10:00 | 2.595 | 3.0748 | 3.0748 | 3.0748 | 3.0748
2024-05-22 11:00 | 2.0767 | 2.2282 | 2.766 | 2.9094 | 3.0528 | 2024-03-22 11:00 | 3.2923 | 3.9011 | 3.9011 | 3.9011 | 3.9011
2024-05-22 12:00 | 2.2291 | 2.3917 | 2.969 | 3.123 | 3.2769 | 2024-03-22 12:00 | 3.2237 | 3.8198 | 3.8198 | 3.8198 | 3.8198
2024-05-22 13:00 | 2.1148 | 2.2691 | 2.8167 | 2.9628 | 3.1089 | 2024-03-22 13:00 | 3.0713 | 3.6392 | 3.6392 | 3.6392 | 3.6392
2024-05-22 14:00 | 2.1339 | 2.2895 | 2.8421 | 2.9895 | 3.1369 | 2024-03-22 14:00 | 3.1208 | 3.6979 | 3.6979 | 3.6979 | 3.6979
2024-05-22 15:00 | 2.1529 | 2.3099 | 2.8675 | 3.0162 | 3.1649 | 2024-03-22 15:00 | 3.0979 | 3.6708 | 3.6708 | 3.6708 | 3.6708
2024-05-22 16:00 | 2.1148 | 2.2691 | 2.8167 | 2.9628 | 3.1089 | 2024-03-22 16:00 | 3.4866 | 4.1314 | 4.1314 | 4.1314 | 4.1314
2024-05-22 17:00 | 2.2101 | 2.3713 | 2.9436 | 3.0963 | 3.2489 | 2024-03-22 17:00 | 3.5476 | 4.2036 | 4.2036 | 4.2036 | 4.2036
2024-05-22 18:00 | 2.172 | 2.3304 | 2.8929 | 3.0429 | 3.1929 | 2024-03-22 18:00 | 3.4104 | 4.041 | 4.041 | 4.041 | 4.041
2024-05-22 19:00 | 1.81 | 1.942 | 2.4107 | 2.5357 | 2.6607 | 2024-03-22 19:00 | 3.2732 | 3.8785 | 3.8785 | 3.8785 | 3.8785
2024-05-22 20:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-03-22 20:00 | 2.7207 | 3.2238 | 3.2238 | 3.2238 | 3.2238
2024-05-22 21:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-03-22 21:00 | 2.3549 | 2.7904 | 2.7904 | 2.7904 | 2.7904
2024-05-22 22:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-03-22 22:00 | 1.9472 | 2.3072 | 2.3072 | 2.3072 | 2.3072
2024-05-22 23:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-03-22 23:00 | 1.8595 | 2.2034 | 2.2034 | 2.2034 | 2.2034
2024-05-23 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-03-23 | 1.7909 | 2.1221 | 2.1221 | 2.1221 | 2.1221
2024-05-23 01:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-03-23 01:00 | 1.7376 | 2.0589 | 2.0589 | 2.0589 | 2.0589
2024-05-23 02:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-03-23 02:00 | 1.6042 | 1.9009 | 1.9009 | 1.9009 | 1.9009
2024-05-23 03:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-03-23 03:00 | 1.6652 | 1.9731 | 1.9731 | 1.9731 | 1.9731
2024-05-23 04:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-03-23 04:00 | 1.8862 | 2.235 | 2.235 | 2.235 | 2.235
2024-05-23 05:00 | 1.7909 | 1.9215 | 2.3854 | 2.509 | 2.6327 | 2024-03-23 05:00 | 2.1301 | 2.524 | 2.524 | 2.524 | 2.524
2024-05-23 06:00 | 2.0005 | 2.1464 | 2.6645 | 2.8026 | 2.9408 | 2024-03-23 06:00 | 2.3244 | 2.7542 | 2.7542 | 2.7542 | 2.7542
2024-05-23 07:00 | 2.5721 | 2.7597 | 3.4258 | 3.6034 | 3.781 | 2024-03-23 07:00 | 2.3778 | 2.8174 | 2.8174 | 2.8174 | 2.8174
2024-05-23 08:00 | 2.6864 | 2.8823 | 3.578 | 3.7636 | 3.9491 | 2024-03-23 08:00 | 2.7664 | 3.278 | 3.278 | 3.278 | 3.278
2024-05-23 09:00 | 2.2101 | 2.3713 | 2.9436 | 3.0963 | 3.2489 | 2024-03-23 09:00 | 2.8236 | 3.3457 | 3.3457 | 3.3457 | 3.3457
2024-05-23 10:00 | 2.2673 | 2.4326 | 3.0198 | 3.1763 | 3.3329 | 2024-03-23 10:00 | 2.9836 | 3.5354 | 3.5354 | 3.5354 | 3.5354
2024-05-23 11:00 | 2.2863 | 2.453 | 3.0451 | 3.203 | 3.3609 | 2024-03-23 11:00 | 2.9265 | 3.4676 | 3.4676 | 3.4676 | 3.4676
2024-05-23 12:00 | 2.2673 | 2.4326 | 3.0198 | 3.1763 | 3.3329 | 2024-03-23 12:00 | 3.1703 | 3.7566 | 3.7566 | 3.7566 | 3.7566
2024-05-23 13:00 | 2.4959 | 2.6779 | 3.3243 | 3.4966 | 3.669 | 2024-03-23 13:00 | 3.1818 | 3.7701 | 3.7701 | 3.7701 | 3.7701
2024-05-23 14:00 | 2.0767 | 2.2282 | 2.766 | 2.9094 | 3.0528 | 2024-03-23 14:00 | 3.0903 | 3.6618 | 3.6618 | 3.6618 | 3.6618
2024-05-23 15:00 | 2.0958 | 2.2486 | 2.7914 | 2.9361 | 3.0808 | 2024-03-23 15:00 | 3.0789 | 3.6482 | 3.6482 | 3.6482 | 3.6482
2024-05-23 16:00 | 2.1529 | 2.3099 | 2.8675 | 3.0162 | 3.1649 | 2024-03-23 16:00 | 3.0827 | 3.6527 | 3.6527 | 3.6527 | 3.6527
2024-05-23 17:00 | 2.2291 | 2.3917 | 2.969 | 3.123 | 3.2769 | 2024-03-23 17:00 | 2.8083 | 3.3277 | 3.3277 | 3.3277 | 3.3277
2024-05-23 18:00 | 2.2101 | 2.3713 | 2.9436 | 3.0963 | 3.2489 | 2024-03-23 18:00 | 2.5302 | 2.9981 | 2.9981 | 2.9981 | 2.9981
2024-05-23 19:00 | 1.81 | 1.942 | 2.4107 | 2.5357 | 2.6607 | 2024-03-23 19:00 | 2.5378 | 3.0071 | 3.0071 | 3.0071 | 3.0071
2024-05-23 20:00 | 1.7528 | 1.8807 | 2.3346 | 2.4557 | 2.5767 | 2024-03-23 20:00 | 2.2596 | 2.6775 | 2.6775 | 2.6775 | 2.6775
2024-05-23 21:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-03-23 21:00 | 2.0843 | 2.4698 | 2.4698 | 2.4698 | 2.4698
2024-05-23 22:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-03-23 22:00 | 1.7528 | 2.077 | 2.077 | 2.077 | 2.077
2024-05-23 23:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-03-23 23:00 | 1.6842 | 1.9957 | 1.9957 | 1.9957 | 1.9957
2024-05-24 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-03-24 | 1.6118 | 1.9099 | 1.9099 | 1.9099 | 1.9099
2024-05-24 01:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-03-24 01:00 | 1.6118 | 1.9099 | 1.9099 | 1.9099 | 1.9099
2024-05-24 02:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-03-24 02:00 | 1.5585 | 1.8467 | 1.8467 | 1.8467 | 1.8467
2024-05-24 03:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-03-24 03:00 | 1.6842 | 1.9957 | 1.9957 | 1.9957 | 1.9957
2024-05-24 04:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-03-24 04:00 | 1.9357 | 2.2937 | 2.2937 | 2.2937 | 2.2937
2024-05-24 05:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-03-24 05:00 | 2.1491 | 2.5465 | 2.5465 | 2.5465 | 2.5465
2024-05-24 06:00 | 1.9434 | 2.0851 | 2.5884 | 2.7226 | 2.8568 | 2024-03-24 06:00 | 2.4273 | 2.8761 | 2.8761 | 2.8761 | 2.8761
2024-05-24 07:00 | 2.4578 | 2.637 | 3.2735 | 3.4433 | 3.613 | 2024-03-24 07:00 | 2.4845 | 2.9439 | 2.9439 | 2.9439 | 2.9439
2024-05-24 08:00 | 2.3625 | 2.5348 | 3.1466 | 3.3098 | 3.473 | 2024-03-24 08:00 | 2.5569 | 3.0297 | 3.0297 | 3.0297 | 3.0297
2024-05-24 09:00 | 2.172 | 2.3304 | 2.8929 | 3.0429 | 3.1929 | 2024-03-24 09:00 | 2.6369 | 3.1245 | 3.1245 | 3.1245 | 3.1245
2024-05-24 10:00 | 2.0005 | 2.1464 | 2.6645 | 2.8026 | 2.9408 | 2024-03-24 10:00 | 2.8236 | 3.3457 | 3.3457 | 3.3457 | 3.3457
2024-05-24 11:00 | 2.0958 | 2.2486 | 2.7914 | 2.9361 | 3.0808 | 2024-03-24 11:00 | 2.7626 | 3.2735 | 3.2735 | 3.2735 | 3.2735
2024-05-24 12:00 | 1.9624 | 2.1055 | 2.6137 | 2.7493 | 2.8848 | 2024-03-24 12:00 | 3.1513 | 3.734 | 3.734 | 3.734 | 3.734
2024-05-24 13:00 | 2.0958 | 2.2486 | 2.7914 | 2.9361 | 3.0808 | 2024-03-24 13:00 | 2.7321 | 3.2374 | 3.2374 | 3.2374 | 3.2374
2024-05-24 14:00 | 2.0196 | 2.1668 | 2.6899 | 2.8293 | 2.9688 | 2024-03-24 14:00 | 2.755 | 3.2644 | 3.2644 | 3.2644 | 3.2644
2024-05-24 15:00 | 2.0577 | 2.2077 | 2.7406 | 2.8827 | 3.0248 | 2024-03-24 15:00 | 2.8579 | 3.3864 | 3.3864 | 3.3864 | 3.3864
2024-05-24 16:00 | 2.2291 | 2.3917 | 2.969 | 3.123 | 3.2769 | 2024-03-24 16:00 | 2.8541 | 3.3818 | 3.3818 | 3.3818 | 3.3818
2024-05-24 17:00 | 2.1529 | 2.3099 | 2.8675 | 3.0162 | 3.1649 | 2024-03-24 17:00 | 2.8693 | 3.3999 | 3.3999 | 3.3999 | 3.3999
2024-05-24 18:00 | 2.0577 | 2.2077 | 2.7406 | 2.8827 | 3.0248 | 2024-03-24 18:00 | 2.6597 | 3.1516 | 3.1516 | 3.1516 | 3.1516
2024-05-24 19:00 | 1.9243 | 2.0646 | 2.563 | 2.6959 | 2.8288 | 2024-03-24 19:00 | 2.5378 | 3.0071 | 3.0071 | 3.0071 | 3.0071
2024-05-24 20:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-03-24 20:00 | 2.3854 | 2.8265 | 2.8265 | 2.8265 | 2.8265
2024-05-24 21:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-03-24 21:00 | 1.9891 | 2.3569 | 2.3569 | 2.3569 | 2.3569
2024-05-24 22:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-03-24 22:00 | 1.8976 | 2.2485 | 2.2485 | 2.2485 | 2.2485
2024-05-24 23:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-03-24 23:00 | 1.6576 | 1.9641 | 1.9641 | 1.9641 | 1.9641
2024-05-25 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-03-25 | 1.6614 | 1.9686 | 1.9686 | 1.9686 | 1.9686
2024-05-25 01:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-03-25 01:00 | 1.669 | 1.9776 | 1.9776 | 1.9776 | 1.9776
2024-05-25 02:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-03-25 02:00 | 1.6385 | 1.9415 | 1.9415 | 1.9415 | 1.9415
2024-05-25 03:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-03-25 03:00 | 1.7224 | 2.0408 | 2.0408 | 2.0408 | 2.0408
2024-05-25 04:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-03-25 04:00 | 1.9548 | 2.3163 | 2.3163 | 2.3163 | 2.3163
2024-05-25 05:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-03-25 05:00 | 2.1949 | 2.6007 | 2.6007 | 2.6007 | 2.6007
2024-05-25 06:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-03-25 06:00 | 2.5683 | 3.0432 | 3.0432 | 3.0432 | 3.0432
2024-05-25 07:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-03-25 07:00 | 2.8693 | 3.3999 | 3.3999 | 3.3999 | 3.3999
2024-05-25 08:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-03-25 08:00 | 3.1094 | 3.6844 | 3.6844 | 3.6844 | 3.6844
2024-05-25 09:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-03-25 09:00 | 2.8426 | 3.3683 | 3.3683 | 3.3683 | 3.3683
2024-05-25 10:00 | 1.4289 | 1.5331 | 1.9032 | 2.0019 | 2.1006 | 2024-03-25 10:00 | 2.9493 | 3.4947 | 3.4947 | 3.4947 | 3.4947
2024-05-25 11:00 | 1.3146 | 1.4105 | 1.751 | 1.8417 | 1.9325 | 2024-03-25 11:00 | 3.0941 | 3.6663 | 3.6663 | 3.6663 | 3.6663
2024-05-25 12:00 | 1.3718 | 1.4718 | 1.8271 | 1.9218 | 2.0166 | 2024-03-25 12:00 | 3.1818 | 3.7701 | 3.7701 | 3.7701 | 3.7701
2024-05-25 13:00 | 1.2956 | 1.39 | 1.7256 | 1.815 | 1.9045 | 2024-03-25 13:00 | 3.1246 | 3.7024 | 3.7024 | 3.7024 | 3.7024
2024-05-25 14:00 | 1.2765 | 1.3696 | 1.7002 | 1.7884 | 1.8765 | 2024-03-25 14:00 | 3.1856 | 3.7747 | 3.7747 | 3.7747 | 3.7747
2024-05-25 15:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-03-25 15:00 | 3.2199 | 3.8153 | 3.8153 | 3.8153 | 3.8153
2024-05-25 16:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-03-25 16:00 | 3.6276 | 4.2984 | 4.2984 | 4.2984 | 4.2984
2024-05-25 17:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-03-25 17:00 | 3.5133 | 4.163 | 4.163 | 4.163 | 4.163
2024-05-25 18:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-03-25 18:00 | 3.3342 | 3.9507 | 3.9507 | 3.9507 | 3.9507
2024-05-25 19:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-03-25 19:00 | 2.9798 | 3.5308 | 3.5308 | 3.5308 | 3.5308
2024-05-25 20:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-03-25 20:00 | 2.6978 | 3.1967 | 3.1967 | 3.1967 | 3.1967
2024-05-25 21:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-03-25 21:00 | 2.3015 | 2.7271 | 2.7271 | 2.7271 | 2.7271
2024-05-25 22:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-03-25 22:00 | 1.9091 | 2.2621 | 2.2621 | 2.2621 | 2.2621
2024-05-25 23:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-03-25 23:00 | 1.7795 | 2.1086 | 2.1086 | 2.1086 | 2.1086
2024-05-26 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-03-26 | 1.6881 | 2.0002 | 2.0002 | 2.0002 | 2.0002
2024-05-26 01:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-03-26 01:00 | 1.5966 | 1.8918 | 1.8918 | 1.8918 | 1.8918
2024-05-26 02:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-03-26 02:00 | 1.5928 | 1.8873 | 1.8873 | 1.8873 | 1.8873
2024-05-26 03:00 | 1.4289 | 1.5331 | 1.9032 | 2.0019 | 2.1006 | 2024-03-26 03:00 | 1.8024 | 2.1357 | 2.1357 | 2.1357 | 2.1357
2024-05-26 04:00 | 1.448 | 1.5536 | 1.9286 | 2.0286 | 2.1286 | 2024-03-26 04:00 | 1.9053 | 2.2576 | 2.2576 | 2.2576 | 2.2576
2024-05-26 05:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-03-26 05:00 | 2.2215 | 2.6323 | 2.6323 | 2.6323 | 2.6323
2024-05-26 06:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-03-26 06:00 | 2.6597 | 3.1516 | 3.1516 | 3.1516 | 3.1516
2024-05-26 07:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-03-26 07:00 | 2.7893 | 3.3051 | 3.3051 | 3.3051 | 3.3051
2024-05-26 08:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-03-26 08:00 | 3.0675 | 3.6347 | 3.6347 | 3.6347 | 3.6347
2024-05-26 09:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-03-26 09:00 | 3.0027 | 3.5579 | 3.5579 | 3.5579 | 3.5579
2024-05-26 10:00 | 1.4099 | 1.5127 | 1.8778 | 1.9752 | 2.0726 | 2024-03-26 10:00 | 2.8655 | 3.3954 | 3.3954 | 3.3954 | 3.3954
2024-05-26 11:00 | 1.086 | 1.1652 | 1.4464 | 1.5214 | 1.5964 | 2024-03-26 11:00 | 2.8541 | 3.3818 | 3.3818 | 3.3818 | 3.3818
2024-05-26 12:00 | 1.0288 | 1.1039 | 1.3703 | 1.4414 | 1.5124 | 2024-03-26 12:00 | 3.1132 | 3.6889 | 3.6889 | 3.6889 | 3.6889
2024-05-26 13:00 | 0.93358 | 1.0017 | 1.2434 | 1.3079 | 1.3724 | 2024-03-26 13:00 | 3.2847 | 3.892 | 3.892 | 3.892 | 3.892
2024-05-26 14:00 | 0.93358 | 1.0017 | 1.2434 | 1.3079 | 1.3724 | 2024-03-26 14:00 | 3.6543 | 4.33 | 4.33 | 4.33 | 4.33
2024-05-26 15:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-03-26 15:00 | 3.4942 | 4.1404 | 4.1404 | 4.1404 | 4.1404
2024-05-26 16:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-03-26 16:00 | 3.54 | 4.1946 | 4.1946 | 4.1946 | 4.1946
2024-05-26 17:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-03-26 17:00 | 3.5476 | 4.2036 | 4.2036 | 4.2036 | 4.2036
2024-05-26 18:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-03-26 18:00 | 3.3799 | 4.0049 | 4.0049 | 4.0049 | 4.0049
2024-05-26 19:00 | 1.829 | 1.9624 | 2.4361 | 2.5624 | 2.6887 | 2024-03-26 19:00 | 3.0446 | 3.6076 | 3.6076 | 3.6076 | 3.6076
2024-05-26 20:00 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 2024-03-26 20:00 | 2.4959 | 2.9574 | 2.9574 | 2.9574 | 2.9574
2024-05-26 21:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-03-26 21:00 | 2.2673 | 2.6865 | 2.6865 | 2.6865 | 2.6865
2024-05-26 22:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-03-26 22:00 | 2.2368 | 2.6504 | 2.6504 | 2.6504 | 2.6504
2024-05-26 23:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-03-26 23:00 | 2.1796 | 2.5827 | 2.5827 | 2.5827 | 2.5827
2024-05-27 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-03-27 | 1.6042 | 1.9009 | 1.9009 | 1.9009 | 1.9009
2024-05-27 01:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-03-27 01:00 | 1.73 | 2.0499 | 2.0499 | 2.0499 | 2.0499
2024-05-27 02:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-03-27 02:00 | 1.7033 | 2.0183 | 2.0183 | 2.0183 | 2.0183
2024-05-27 03:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-03-27 03:00 | 1.7833 | 2.1131 | 2.1131 | 2.1131 | 2.1131
2024-05-27 04:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-03-27 04:00 | 2.0615 | 2.4427 | 2.4427 | 2.4427 | 2.4427
2024-05-27 05:00 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 2024-03-27 05:00 | 2.252 | 2.6684 | 2.6684 | 2.6684 | 2.6684
2024-05-27 06:00 | 1.7338 | 1.8602 | 2.3092 | 2.429 | 2.5487 | 2024-03-27 06:00 | 2.5797 | 3.0567 | 3.0567 | 3.0567 | 3.0567
2024-05-27 07:00 | 1.7719 | 1.9011 | 2.36 | 2.4823 | 2.6047 | 2024-03-27 07:00 | 2.8807 | 3.4134 | 3.4134 | 3.4134 | 3.4134
2024-05-27 08:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-03-27 08:00 | 3.1399 | 3.7205 | 3.7205 | 3.7205 | 3.7205
2024-05-27 09:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-03-27 09:00 | 3.1818 | 3.7701 | 3.7701 | 3.7701 | 3.7701
2024-05-27 10:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-03-27 10:00 | 3.2161 | 3.8108 | 3.8108 | 3.8108 | 3.8108
2024-05-27 11:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-03-27 11:00 | 3.2008 | 3.7927 | 3.7927 | 3.7927 | 3.7927
2024-05-27 12:00 | 1.4099 | 1.5127 | 1.8778 | 1.9752 | 2.0726 | 2024-03-27 12:00 | 3.2123 | 3.8063 | 3.8063 | 3.8063 | 3.8063
2024-05-27 13:00 | 1.2575 | 1.3492 | 1.6748 | 1.7617 | 1.8485 | 2024-03-27 13:00 | 3.2694 | 3.874 | 3.874 | 3.874 | 3.874
2024-05-27 14:00 | 1.2384 | 1.3287 | 1.6494 | 1.735 | 1.8205 | 2024-03-27 14:00 | 3.3342 | 3.9507 | 3.9507 | 3.9507 | 3.9507
2024-05-27 15:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-03-27 15:00 | 3.4104 | 4.041 | 4.041 | 4.041 | 4.041
2024-05-27 16:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-03-27 16:00 | 3.6047 | 4.2713 | 4.2713 | 4.2713 | 4.2713
2024-05-27 17:00 | 1.7528 | 1.8807 | 2.3346 | 2.4557 | 2.5767 | 2024-03-27 17:00 | 3.5285 | 4.181 | 4.181 | 4.181 | 4.181
2024-05-27 18:00 | 1.7909 | 1.9215 | 2.3854 | 2.509 | 2.6327 | 2024-03-27 18:00 | 3.2618 | 3.865 | 3.865 | 3.865 | 3.865
2024-05-27 19:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-03-27 19:00 | 3.1284 | 3.7069 | 3.7069 | 3.7069 | 3.7069
2024-05-27 20:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-03-27 20:00 | 2.6674 | 3.1606 | 3.1606 | 3.1606 | 3.1606
2024-05-27 21:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-03-27 21:00 | 2.4959 | 2.9574 | 2.9574 | 2.9574 | 2.9574
2024-05-27 22:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-03-27 22:00 | 2.0501 | 2.4291 | 2.4291 | 2.4291 | 2.4291
2024-05-27 23:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-03-27 23:00 | 2.012 | 2.384 | 2.384 | 2.384 | 2.384
2024-05-28 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-03-28 | 1.6157 | 1.9144 | 1.9144 | 1.9144 | 1.9144
2024-05-28 01:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-03-28 01:00 | 1.6995 | 2.0138 | 2.0138 | 2.0138 | 2.0138
2024-05-28 02:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-03-28 02:00 | 1.7414 | 2.0634 | 2.0634 | 2.0634 | 2.0634
2024-05-28 03:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-03-28 03:00 | 1.8329 | 2.1718 | 2.1718 | 2.1718 | 2.1718
2024-05-28 04:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-03-28 04:00 | 1.9281 | 2.2847 | 2.2847 | 2.2847 | 2.2847
2024-05-28 05:00 | 1.8481 | 1.9829 | 2.4615 | 2.5891 | 2.7167 | 2024-03-28 05:00 | 2.2596 | 2.6775 | 2.6775 | 2.6775 | 2.6775
2024-05-28 06:00 | 2.0958 | 2.2486 | 2.7914 | 2.9361 | 3.0808 | 2024-03-28 06:00 | 2.553 | 3.0251 | 3.0251 | 3.0251 | 3.0251
2024-05-28 07:00 | 2.534 | 2.7188 | 3.375 | 3.55 | 3.725 | 2024-03-28 07:00 | 2.9417 | 3.4857 | 3.4857 | 3.4857 | 3.4857
2024-05-28 08:00 | 2.7436 | 2.9436 | 3.6542 | 3.8436 | 4.0331 | 2024-03-28 08:00 | 3.4866 | 4.1314 | 4.1314 | 4.1314 | 4.1314
2024-05-28 09:00 | 2.4578 | 2.637 | 3.2735 | 3.4433 | 3.613 | 2024-03-28 09:00 | 3.4638 | 4.1043 | 4.1043 | 4.1043 | 4.1043
2024-05-28 10:00 | 2.3244 | 2.4939 | 3.0959 | 3.2564 | 3.4169 | 2024-03-28 10:00 | 3.3837 | 4.0094 | 4.0094 | 4.0094 | 4.0094
2024-05-28 11:00 | 2.2101 | 2.3713 | 2.9436 | 3.0963 | 3.2489 | 2024-03-28 11:00 | 3.8334 | 4.5422 | 4.5422 | 4.5422 | 4.5422
2024-05-28 12:00 | 2.3054 | 2.4735 | 3.0705 | 3.2297 | 3.3889 | 2024-03-28 12:00 | 3.6733 | 4.3526 | 4.3526 | 4.3526 | 4.3526
2024-05-28 13:00 | 2.2291 | 2.3917 | 2.969 | 3.123 | 3.2769 | 2024-03-28 13:00 | 3.8905 | 4.61 | 4.61 | 4.61 | 4.61
2024-05-28 14:00 | 2.191 | 2.3508 | 2.9183 | 3.0696 | 3.2209 | 2024-03-28 14:00 | 4.1496 | 4.917 | 4.917 | 4.917 | 4.917
2024-05-28 15:00 | 2.191 | 2.3508 | 2.9183 | 3.0696 | 3.2209 | 2024-03-28 15:00 | 3.9515 | 4.6822 | 4.6822 | 4.6822 | 4.6822
2024-05-28 16:00 | 2.2863 | 2.453 | 3.0451 | 3.203 | 3.3609 | 2024-03-28 16:00 | 3.7991 | 4.5016 | 4.5016 | 4.5016 | 4.5016
2024-05-28 17:00 | 2.2291 | 2.3917 | 2.969 | 3.123 | 3.2769 | 2024-03-28 17:00 | 3.78 | 4.479 | 4.479 | 4.479 | 4.479
2024-05-28 18:00 | 2.191 | 2.3508 | 2.9183 | 3.0696 | 3.2209 | 2024-03-28 18:00 | 3.2732 | 3.8785 | 3.8785 | 3.8785 | 3.8785
2024-05-28 19:00 | 1.9053 | 2.0442 | 2.5376 | 2.6692 | 2.8008 | 2024-03-28 19:00 | 3.0294 | 3.5895 | 3.5895 | 3.5895 | 3.5895
2024-05-28 20:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-03-28 20:00 | 2.6026 | 3.0838 | 3.0838 | 3.0838 | 3.0838
2024-05-28 21:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-03-28 21:00 | 2.3206 | 2.7497 | 2.7497 | 2.7497 | 2.7497
2024-05-28 22:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-03-28 22:00 | 2.1453 | 2.542 | 2.542 | 2.542 | 2.542
2024-05-28 23:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-03-28 23:00 | 2.0539 | 2.4337 | 2.4337 | 2.4337 | 2.4337
2024-05-29 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-03-29 | 1.6423 | 1.946 | 1.946 | 1.946 | 1.946
2024-05-29 01:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-03-29 01:00 | 1.589 | 1.8828 | 1.8828 | 1.8828 | 1.8828
2024-05-29 02:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-03-29 02:00 | 1.5013 | 1.779 | 1.779 | 1.779 | 1.779
2024-05-29 03:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-03-29 03:00 | 1.6118 | 1.9099 | 1.9099 | 1.9099 | 1.9099
2024-05-29 04:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-03-29 04:00 | 1.65 | 1.9551 | 1.9551 | 1.9551 | 1.9551
2024-05-29 05:00 | 1.7528 | 1.8807 | 2.3346 | 2.4557 | 2.5767 | 2024-03-29 05:00 | 1.7719 | 2.0995 | 2.0995 | 2.0995 | 2.0995
2024-05-29 06:00 | 2.0005 | 2.1464 | 2.6645 | 2.8026 | 2.9408 | 2024-03-29 06:00 | 1.8519 | 2.1944 | 2.1944 | 2.1944 | 2.1944
2024-05-29 07:00 | 2.5911 | 2.7801 | 3.4512 | 3.6301 | 3.809 | 2024-03-29 07:00 | 2.0615 | 2.4427 | 2.4427 | 2.4427 | 2.4427
2024-05-29 08:00 | 2.6293 | 2.821 | 3.5019 | 3.6835 | 3.8651 | 2024-03-29 08:00 | 2.0615 | 2.4427 | 2.4427 | 2.4427 | 2.4427
2024-05-29 09:00 | 2.3244 | 2.4939 | 3.0959 | 3.2564 | 3.4169 | 2024-03-29 09:00 | 1.7757 | 2.1041 | 2.1041 | 2.1041 | 2.1041
2024-05-29 10:00 | 2.2673 | 2.4326 | 3.0198 | 3.1763 | 3.3329 | 2024-03-29 10:00 | 1.9548 | 2.3163 | 2.3163 | 2.3163 | 2.3163
2024-05-29 11:00 | 2.2101 | 2.3713 | 2.9436 | 3.0963 | 3.2489 | 2024-03-29 11:00 | 1.8443 | 2.1853 | 2.1853 | 2.1853 | 2.1853
2024-05-29 12:00 | 2.1339 | 2.2895 | 2.8421 | 2.9895 | 3.1369 | 2024-03-29 12:00 | 1.749 | 2.0724 | 2.0724 | 2.0724 | 2.0724
2024-05-29 13:00 | 2.172 | 2.3304 | 2.8929 | 3.0429 | 3.1929 | 2024-03-29 13:00 | 1.9624 | 2.3253 | 2.3253 | 2.3253 | 2.3253
2024-05-29 14:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-03-29 14:00 | 1.9053 | 2.2576 | 2.2576 | 2.2576 | 2.2576
2024-05-29 15:00 | 2.1529 | 2.3099 | 2.8675 | 3.0162 | 3.1649 | 2024-03-29 15:00 | 1.9053 | 2.2576 | 2.2576 | 2.2576 | 2.2576
2024-05-29 16:00 | 2.2291 | 2.3917 | 2.969 | 3.123 | 3.2769 | 2024-03-29 16:00 | 1.9053 | 2.2576 | 2.2576 | 2.2576 | 2.2576
2024-05-29 17:00 | 2.2101 | 2.3713 | 2.9436 | 3.0963 | 3.2489 | 2024-03-29 17:00 | 2.3206 | 2.7497 | 2.7497 | 2.7497 | 2.7497
2024-05-29 18:00 | 2.191 | 2.3508 | 2.9183 | 3.0696 | 3.2209 | 2024-03-29 18:00 | 2.2673 | 2.6865 | 2.6865 | 2.6865 | 2.6865
2024-05-29 19:00 | 1.81 | 1.942 | 2.4107 | 2.5357 | 2.6607 | 2024-03-29 19:00 | 2.2291 | 2.6414 | 2.6414 | 2.6414 | 2.6414
2024-05-29 20:00 | 1.7338 | 1.8602 | 2.3092 | 2.429 | 2.5487 | 2024-03-29 20:00 | 2.191 | 2.5962 | 2.5962 | 2.5962 | 2.5962
2024-05-29 21:00 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 2024-03-29 21:00 | 1.9929 | 2.3614 | 2.3614 | 2.3614 | 2.3614
2024-05-29 22:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-03-29 22:00 | 1.7795 | 2.1086 | 2.1086 | 2.1086 | 2.1086
2024-05-29 23:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-03-29 23:00 | 1.6271 | 1.928 | 1.928 | 1.928 | 1.928
2024-05-30 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-03-30 | 1.6118 | 1.9099 | 1.9099 | 1.9099 | 1.9099
2024-05-30 01:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-03-30 01:00 | 1.5814 | 1.8738 | 1.8738 | 1.8738 | 1.8738
2024-05-30 02:00 | 1.448 | 1.5536 | 1.9286 | 2.0286 | 2.1286 | 2024-03-30 02:00 | 1.6004 | 1.8964 | 1.8964 | 1.8964 | 1.8964
2024-05-30 03:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-03-30 03:00 | 1.8176 | 2.1537 | 2.1537 | 2.1537 | 2.1537
2024-05-30 04:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-03-30 04:00 | 2.0577 | 2.4382 | 2.4382 | 2.4382 | 2.4382
2024-05-30 05:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-03-30 05:00 | 2.2291 | 2.6414 | 2.6414 | 2.6414 | 2.6414
2024-05-30 06:00 | 1.9434 | 2.0851 | 2.5884 | 2.7226 | 2.8568 | 2024-03-30 06:00 | 2.3015 | 2.7271 | 2.7271 | 2.7271 | 2.7271
2024-05-30 07:00 | 2.534 | 2.7188 | 3.375 | 3.55 | 3.725 | 2024-03-30 07:00 | 2.2901 | 2.7136 | 2.7136 | 2.7136 | 2.7136
2024-05-30 08:00 | 2.4768 | 2.6574 | 3.2989 | 3.4699 | 3.641 | 2024-03-30 08:00 | 2.4654 | 2.9213 | 2.9213 | 2.9213 | 2.9213
2024-05-30 09:00 | 2.3816 | 2.5552 | 3.172 | 3.3365 | 3.501 | 2024-03-30 09:00 | 2.5226 | 2.989 | 2.989 | 2.989 | 2.989
2024-05-30 10:00 | 2.1148 | 2.2691 | 2.8167 | 2.9628 | 3.1089 | 2024-03-30 10:00 | 2.4502 | 2.9032 | 2.9032 | 2.9032 | 2.9032
2024-05-30 11:00 | 2.2673 | 2.4326 | 3.0198 | 3.1763 | 3.3329 | 2024-03-30 11:00 | 2.6788 | 3.1741 | 3.1741 | 3.1741 | 3.1741
2024-05-30 12:00 | 2.172 | 2.3304 | 2.8929 | 3.0429 | 3.1929 | 2024-03-30 12:00 | 2.9112 | 3.4496 | 3.4496 | 3.4496 | 3.4496
2024-05-30 13:00 | 2.2101 | 2.3713 | 2.9436 | 3.0963 | 3.2489 | 2024-03-30 13:00 | 3.056 | 3.6211 | 3.6211 | 3.6211 | 3.6211
2024-05-30 14:00 | 2.3054 | 2.4735 | 3.0705 | 3.2297 | 3.3889 | 2024-03-30 14:00 | 3.1932 | 3.7837 | 3.7837 | 3.7837 | 3.7837
2024-05-30 15:00 | 2.2673 | 2.4326 | 3.0198 | 3.1763 | 3.3329 | 2024-03-30 15:00 | 3.4371 | 4.0727 | 4.0727 | 4.0727 | 4.0727
2024-05-30 16:00 | 2.2291 | 2.3917 | 2.969 | 3.123 | 3.2769 | 2024-03-30 16:00 | 3.5857 | 4.2487 | 4.2487 | 4.2487 | 4.2487
2024-05-30 17:00 | 2.3054 | 2.4735 | 3.0705 | 3.2297 | 3.3889 | 2024-03-30 17:00 | 3.338 | 3.9553 | 3.9553 | 3.9553 | 3.9553
2024-05-30 18:00 | 2.191 | 2.3508 | 2.9183 | 3.0696 | 3.2209 | 2024-03-30 18:00 | 2.9074 | 3.4451 | 3.4451 | 3.4451 | 3.4451
2024-05-30 19:00 | 1.9434 | 2.0851 | 2.5884 | 2.7226 | 2.8568 | 2024-03-30 19:00 | 2.6293 | 3.1154 | 3.1154 | 3.1154 | 3.1154
2024-05-30 20:00 | 1.829 | 1.9624 | 2.4361 | 2.5624 | 2.6887 | 2024-03-30 20:00 | 2.5378 | 3.0071 | 3.0071 | 3.0071 | 3.0071
2024-05-30 21:00 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 2024-03-30 21:00 | 2.2787 | 2.7001 | 2.7001 | 2.7001 | 2.7001
2024-05-30 22:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-03-30 22:00 | 1.8862 | 2.235 | 2.235 | 2.235 | 2.235
2024-05-30 23:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-03-30 23:00 | 1.749 | 2.0724 | 2.0724 | 2.0724 | 2.0724
2024-05-31 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-03-31 | 1.6461 | 1.9505 | 1.9505 | 1.9505 | 1.9505
2024-05-31 01:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-03-31 01:00 | 1.5623 | 1.8512 | 1.8512 | 1.8512 | 1.8512
2024-05-31 02:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-03-31 02:00 | 1.65 | 1.9551 | 1.9551 | 1.9551 | 1.9551
2024-05-31 03:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-03-31 03:00 | 1.65 | 1.9551 | 1.9551 | 1.9551 | 1.9551
2024-05-31 04:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-03-31 04:00 | 1.7757 | 2.1041 | 2.1041 | 2.1041 | 2.1041
2024-05-31 05:00 | 1.7338 | 1.8602 | 2.3092 | 2.429 | 2.5487 | 2024-03-31 05:00 | 2.0501 | 2.4291 | 2.4291 | 2.4291 | 2.4291
2024-05-31 06:00 | 1.9053 | 2.0442 | 2.5376 | 2.6692 | 2.8008 | 2024-03-31 06:00 | 2.1339 | 2.5285 | 2.5285 | 2.5285 | 2.5285
2024-05-31 07:00 | 2.3625 | 2.5348 | 3.1466 | 3.3098 | 3.473 | 2024-03-31 07:00 | 2.2253 | 2.6368 | 2.6368 | 2.6368 | 2.6368
2024-05-31 08:00 | 2.3816 | 2.5552 | 3.172 | 3.3365 | 3.501 | 2024-03-31 08:00 | 2.3701 | 2.8084 | 2.8084 | 2.8084 | 2.8084
2024-05-31 09:00 | 2.4006 | 2.5757 | 3.1974 | 3.3632 | 3.529 | 2024-03-31 09:00 | 2.1758 | 2.5781 | 2.5781 | 2.5781 | 2.5781
2024-05-31 10:00 | 2.4578 | 2.637 | 3.2735 | 3.4433 | 3.613 | 2024-03-31 10:00 | 2.092 | 2.4788 | 2.4788 | 2.4788 | 2.4788
2024-05-31 11:00 | 2.4387 | 2.6166 | 3.2481 | 3.4166 | 3.585 | 2024-03-31 11:00 | 2.1529 | 2.5511 | 2.5511 | 2.5511 | 2.5511
2024-05-31 12:00 | 2.3054 | 2.4735 | 3.0705 | 3.2297 | 3.3889 | 2024-03-31 12:00 | 2.5149 | 2.98 | 2.98 | 2.98 | 2.98
2024-05-31 13:00 | 1.9815 | 2.126 | 2.6391 | 2.776 | 2.9128 | 2024-03-31 13:00 | 2.4425 | 2.8942 | 2.8942 | 2.8942 | 2.8942
2024-05-31 14:00 | 1.9434 | 2.0851 | 2.5884 | 2.7226 | 2.8568 | 2024-03-31 14:00 | 2.4883 | 2.9484 | 2.9484 | 2.9484 | 2.9484
2024-05-31 15:00 | 2.172 | 2.3304 | 2.8929 | 3.0429 | 3.1929 | 2024-03-31 15:00 | 2.614 | 3.0974 | 3.0974 | 3.0974 | 3.0974
2024-05-31 16:00 | 2.1148 | 2.2691 | 2.8167 | 2.9628 | 3.1089 | 2024-03-31 16:00 | 2.7398 | 3.2464 | 3.2464 | 3.2464 | 3.2464
2024-05-31 17:00 | 2.191 | 2.3508 | 2.9183 | 3.0696 | 3.2209 | 2024-03-31 17:00 | 2.7855 | 3.3006 | 3.3006 | 3.3006 | 3.3006
2024-05-31 18:00 | 2.172 | 2.3304 | 2.8929 | 3.0429 | 3.1929 | 2024-03-31 18:00 | 2.4463 | 2.8987 | 2.8987 | 2.8987 | 2.8987
2024-05-31 19:00 | 1.8672 | 2.0033 | 2.4869 | 2.6158 | 2.7448 | 2024-03-31 19:00 | 2.4806 | 2.9394 | 2.9394 | 2.9394 | 2.9394
2024-05-31 20:00 | 1.829 | 1.9624 | 2.4361 | 2.5624 | 2.6887 | 2024-03-31 20:00 | 2.1796 | 2.5827 | 2.5827 | 2.5827 | 2.5827
2024-05-31 21:00 | 1.7338 | 1.8602 | 2.3092 | 2.429 | 2.5487 | 2024-03-31 21:00 | 2.1415 | 2.5375 | 2.5375 | 2.5375 | 2.5375
2024-05-31 22:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-03-31 22:00 | 1.6919 | 2.0047 | 2.0047 | 2.0047 | 2.0047
2024-05-31 23:00 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 2024-03-31 23:00 | 1.6309 | 1.9325 | 1.9325 | 1.9325 | 1.9325
2024-06-01 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-04-01 | 1.5776 | 1.8388 | 1.8388 | 1.8388 | 1.8388
2024-06-01 01:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-04-01 01:00 | 1.6614 | 1.9365 | 1.9365 | 1.9365 | 1.9365
2024-06-01 02:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-04-01 02:00 | 1.6957 | 1.9765 | 1.9765 | 1.9765 | 1.9765
2024-06-01 03:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-04-01 03:00 | 1.8443 | 2.1497 | 2.1497 | 2.1497 | 2.1497
2024-06-01 04:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-04-01 04:00 | 1.9472 | 2.2696 | 2.2696 | 2.2696 | 2.2696
2024-06-01 05:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-04-01 05:00 | 2.1796 | 2.5405 | 2.5405 | 2.5405 | 2.5405
2024-06-01 06:00 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 2024-04-01 06:00 | 2.5683 | 2.9936 | 2.9936 | 2.9936 | 2.9936
2024-06-01 07:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-04-01 07:00 | 2.553 | 2.9758 | 2.9758 | 2.9758 | 2.9758
2024-06-01 08:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-04-01 08:00 | 2.9874 | 3.4821 | 3.4821 | 3.4821 | 3.4821
2024-06-01 09:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-04-01 09:00 | 3.056 | 3.5621 | 3.5621 | 3.5621 | 3.5621
2024-06-01 10:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-04-01 10:00 | 2.9265 | 3.4111 | 3.4111 | 3.4111 | 3.4111
2024-06-01 11:00 | 1.4099 | 1.5127 | 1.8778 | 1.9752 | 2.0726 | 2024-04-01 11:00 | 2.9531 | 3.4422 | 3.4422 | 3.4422 | 3.4422
2024-06-01 12:00 | 1.448 | 1.5536 | 1.9286 | 2.0286 | 2.1286 | 2024-04-01 12:00 | 3.0827 | 3.5932 | 3.5932 | 3.5932 | 3.5932
2024-06-01 13:00 | 1.4289 | 1.5331 | 1.9032 | 2.0019 | 2.1006 | 2024-04-01 13:00 | 3.1856 | 3.7131 | 3.7131 | 3.7131 | 3.7131
2024-06-01 14:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-04-01 14:00 | 3.2542 | 3.793 | 3.793 | 3.793 | 3.793
2024-06-01 15:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-04-01 15:00 | 3.4561 | 4.0284 | 4.0284 | 4.0284 | 4.0284
2024-06-01 16:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-04-01 16:00 | 3.4828 | 4.0595 | 4.0595 | 4.0595 | 4.0595
2024-06-01 17:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-04-01 17:00 | 3.1437 | 3.6642 | 3.6642 | 3.6642 | 3.6642
2024-06-01 18:00 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 2024-04-01 18:00 | 2.8617 | 3.3356 | 3.3356 | 3.3356 | 3.3356
2024-06-01 19:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-04-01 19:00 | 2.6712 | 3.1135 | 3.1135 | 3.1135 | 3.1135
2024-06-01 20:00 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 2024-04-01 20:00 | 2.4616 | 2.8692 | 2.8692 | 2.8692 | 2.8692
2024-06-01 21:00 | 1.7528 | 1.8807 | 2.3346 | 2.4557 | 2.5767 | 2024-04-01 21:00 | 2.2101 | 2.5761 | 2.5761 | 2.5761 | 2.5761
2024-06-01 22:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-04-01 22:00 | 2.111 | 2.4606 | 2.4606 | 2.4606 | 2.4606
2024-06-01 23:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-04-01 23:00 | 1.7681 | 2.0609 | 2.0609 | 2.0609 | 2.0609
2024-06-02 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-04-02 | 1.6957 | 1.9765 | 1.9765 | 1.9765 | 1.9765
2024-06-02 01:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-04-02 01:00 | 1.7185 | 2.0031 | 2.0031 | 2.0031 | 2.0031
2024-06-02 02:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-04-02 02:00 | 1.7071 | 1.9898 | 1.9898 | 1.9898 | 1.9898
2024-06-02 03:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-04-02 03:00 | 1.7909 | 2.0875 | 2.0875 | 2.0875 | 2.0875
2024-06-02 04:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-04-02 04:00 | 1.8938 | 2.2074 | 2.2074 | 2.2074 | 2.2074
2024-06-02 05:00 | 1.81 | 1.942 | 2.4107 | 2.5357 | 2.6607 | 2024-04-02 05:00 | 2.2177 | 2.5849 | 2.5849 | 2.5849 | 2.5849
2024-06-02 06:00 | 1.7338 | 1.8602 | 2.3092 | 2.429 | 2.5487 | 2024-04-02 06:00 | 2.6064 | 3.038 | 3.038 | 3.038 | 3.038
2024-06-02 07:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-04-02 07:00 | 2.9455 | 3.4333 | 3.4333 | 3.4333 | 3.4333
2024-06-02 08:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-04-02 08:00 | 3.498 | 4.0773 | 4.0773 | 4.0773 | 4.0773
2024-06-02 09:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-04-02 09:00 | 3.8448 | 4.4815 | 4.4815 | 4.4815 | 4.4815
2024-06-02 10:00 | 1.3527 | 1.4514 | 1.8017 | 1.8951 | 1.9885 | 2024-04-02 10:00 | 3.6314 | 4.2327 | 4.2327 | 4.2327 | 4.2327
2024-06-02 11:00 | 1.2575 | 1.3492 | 1.6748 | 1.7617 | 1.8485 | 2024-04-02 11:00 | 3.7457 | 4.366 | 4.366 | 4.366 | 4.366
2024-06-02 12:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-04-02 12:00 | 3.7953 | 4.4237 | 4.4237 | 4.4237 | 4.4237
2024-06-02 13:00 | 1.1432 | 1.2265 | 1.5226 | 1.6015 | 1.6805 | 2024-04-02 13:00 | 3.6505 | 4.2549 | 4.2549 | 4.2549 | 4.2549
2024-06-02 14:00 | 1.4289 | 1.5331 | 1.9032 | 2.0019 | 2.1006 | 2024-04-02 14:00 | 3.5362 | 4.1217 | 4.1217 | 4.1217 | 4.1217
2024-06-02 15:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-04-02 15:00 | 3.1703 | 3.6953 | 3.6953 | 3.6953 | 3.6953
2024-06-02 16:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-04-02 16:00 | 3.2313 | 3.7664 | 3.7664 | 3.7664 | 3.7664
2024-06-02 17:00 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 2024-04-02 17:00 | 3.0065 | 3.5043 | 3.5043 | 3.5043 | 3.5043
2024-06-02 18:00 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 2024-04-02 18:00 | 2.9303 | 3.4155 | 3.4155 | 3.4155 | 3.4155
2024-06-02 19:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-04-02 19:00 | 2.6521 | 3.0913 | 3.0913 | 3.0913 | 3.0913
2024-06-02 20:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-04-02 20:00 | 2.5416 | 2.9625 | 2.9625 | 2.9625 | 2.9625
2024-06-02 21:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-04-02 21:00 | 2.2139 | 2.5805 | 2.5805 | 2.5805 | 2.5805
2024-06-02 22:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-04-02 22:00 | 1.81 | 2.1097 | 2.1097 | 2.1097 | 2.1097
2024-06-02 23:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-04-02 23:00 | 1.7376 | 2.0253 | 2.0253 | 2.0253 | 2.0253
2024-06-03 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-04-03 | 1.6461 | 1.9187 | 1.9187 | 1.9187 | 1.9187
2024-06-03 01:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-04-03 01:00 | 1.7871 | 2.0831 | 2.0831 | 2.0831 | 2.0831
2024-06-03 02:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-04-03 02:00 | 1.749 | 2.0386 | 2.0386 | 2.0386 | 2.0386
2024-06-03 03:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-04-03 03:00 | 1.7338 | 2.0209 | 2.0209 | 2.0209 | 2.0209
2024-06-03 04:00 | 1.7338 | 1.8602 | 2.3092 | 2.429 | 2.5487 | 2024-04-03 04:00 | 2.031 | 2.3673 | 2.3673 | 2.3673 | 2.3673
2024-06-03 05:00 | 1.7528 | 1.8807 | 2.3346 | 2.4557 | 2.5767 | 2024-04-03 05:00 | 2.1987 | 2.5627 | 2.5627 | 2.5627 | 2.5627
2024-06-03 06:00 | 2.0386 | 2.1873 | 2.7152 | 2.856 | 2.9968 | 2024-04-03 06:00 | 2.5416 | 2.9625 | 2.9625 | 2.9625 | 2.9625
2024-06-03 07:00 | 2.5721 | 2.7597 | 3.4258 | 3.6034 | 3.781 | 2024-04-03 07:00 | 2.7131 | 3.1623 | 3.1623 | 3.1623 | 3.1623
2024-06-03 08:00 | 2.6102 | 2.8005 | 3.4765 | 3.6568 | 3.8371 | 2024-04-03 08:00 | 3.1132 | 3.6287 | 3.6287 | 3.6287 | 3.6287
2024-06-03 09:00 | 2.6102 | 2.8005 | 3.4765 | 3.6568 | 3.8371 | 2024-04-03 09:00 | 3.0484 | 3.5532 | 3.5532 | 3.5532 | 3.5532
2024-06-03 10:00 | 2.6293 | 2.821 | 3.5019 | 3.6835 | 3.8651 | 2024-04-03 10:00 | 2.8426 | 3.3133 | 3.3133 | 3.3133 | 3.3133
2024-06-03 11:00 | 2.4959 | 2.6779 | 3.3243 | 3.4966 | 3.669 | 2024-04-03 11:00 | 2.8426 | 3.3133 | 3.3133 | 3.3133 | 3.3133
2024-06-03 12:00 | 2.5149 | 2.6983 | 3.3496 | 3.5233 | 3.697 | 2024-04-03 12:00 | 3.6505 | 4.2549 | 4.2549 | 4.2549 | 4.2549
2024-06-03 13:00 | 2.4578 | 2.637 | 3.2735 | 3.4433 | 3.613 | 2024-04-03 13:00 | 3.5171 | 4.0995 | 4.0995 | 4.0995 | 4.0995
2024-06-03 14:00 | 2.3625 | 2.5348 | 3.1466 | 3.3098 | 3.473 | 2024-04-03 14:00 | 3.7495 | 4.3704 | 4.3704 | 4.3704 | 4.3704
2024-06-03 15:00 | 2.3054 | 2.4735 | 3.0705 | 3.2297 | 3.3889 | 2024-04-03 15:00 | 3.5743 | 4.1661 | 4.1661 | 4.1661 | 4.1661
2024-06-03 16:00 | 2.2482 | 2.4121 | 2.9944 | 3.1496 | 3.3049 | 2024-04-03 16:00 | 3.1742 | 3.6998 | 3.6998 | 3.6998 | 3.6998
2024-06-03 17:00 | 2.3244 | 2.4939 | 3.0959 | 3.2564 | 3.4169 | 2024-04-03 17:00 | 3.2161 | 3.7486 | 3.7486 | 3.7486 | 3.7486
2024-06-03 18:00 | 2.2863 | 2.453 | 3.0451 | 3.203 | 3.3609 | 2024-04-03 18:00 | 3.1322 | 3.6509 | 3.6509 | 3.6509 | 3.6509
2024-06-03 19:00 | 1.9053 | 2.0442 | 2.5376 | 2.6692 | 2.8008 | 2024-04-03 19:00 | 2.7359 | 3.189 | 3.189 | 3.189 | 3.189
2024-06-03 20:00 | 1.8862 | 2.0237 | 2.5122 | 2.6425 | 2.7728 | 2024-04-03 20:00 | 2.3663 | 2.7582 | 2.7582 | 2.7582 | 2.7582
2024-06-03 21:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-04-03 21:00 | 2.1072 | 2.4561 | 2.4561 | 2.4561 | 2.4561
2024-06-03 22:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-04-03 22:00 | 1.9129 | 2.2296 | 2.2296 | 2.2296 | 2.2296
2024-06-03 23:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-04-03 23:00 | 1.7338 | 2.0209 | 2.0209 | 2.0209 | 2.0209
2024-06-04 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-04-04 | 1.5661 | 1.8255 | 1.8255 | 1.8255 | 1.8255
2024-06-04 01:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-04-04 01:00 | 1.5623 | 1.821 | 1.821 | 1.821 | 1.821
2024-06-04 02:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-04-04 02:00 | 1.5661 | 1.8255 | 1.8255 | 1.8255 | 1.8255
2024-06-04 03:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-04-04 03:00 | 1.6804 | 1.9587 | 1.9587 | 1.9587 | 1.9587
2024-06-04 04:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-04-04 04:00 | 1.9014 | 2.2163 | 2.2163 | 2.2163 | 2.2163
2024-06-04 05:00 | 1.7909 | 1.9215 | 2.3854 | 2.509 | 2.6327 | 2024-04-04 05:00 | 2.2444 | 2.616 | 2.616 | 2.616 | 2.616
2024-06-04 06:00 | 2.0577 | 2.2077 | 2.7406 | 2.8827 | 3.0248 | 2024-04-04 06:00 | 2.8083 | 3.2734 | 3.2734 | 3.2734 | 3.2734
2024-06-04 07:00 | 2.4197 | 2.5961 | 3.2228 | 3.3899 | 3.557 | 2024-04-04 07:00 | 3.0332 | 3.5354 | 3.5354 | 3.5354 | 3.5354
2024-06-04 08:00 | 2.553 | 2.7392 | 3.4004 | 3.5767 | 3.753 | 2024-04-04 08:00 | 3.1475 | 3.6687 | 3.6687 | 3.6687 | 3.6687
2024-06-04 09:00 | 2.534 | 2.7188 | 3.375 | 3.55 | 3.725 | 2024-04-04 09:00 | 3.2999 | 3.8463 | 3.8463 | 3.8463 | 3.8463
2024-06-04 10:00 | 2.4768 | 2.6574 | 3.2989 | 3.4699 | 3.641 | 2024-04-04 10:00 | 3.3228 | 3.873 | 3.873 | 3.873 | 3.873
2024-06-04 11:00 | 2.2863 | 2.453 | 3.0451 | 3.203 | 3.3609 | 2024-04-04 11:00 | 3.4599 | 4.0329 | 4.0329 | 4.0329 | 4.0329
2024-06-04 12:00 | 2.3054 | 2.4735 | 3.0705 | 3.2297 | 3.3889 | 2024-04-04 12:00 | 3.2885 | 3.833 | 3.833 | 3.833 | 3.833
2024-06-04 13:00 | 2.3244 | 2.4939 | 3.0959 | 3.2564 | 3.4169 | 2024-04-04 13:00 | 3.3418 | 3.8952 | 3.8952 | 3.8952 | 3.8952
2024-06-04 14:00 | 2.2482 | 2.4121 | 2.9944 | 3.1496 | 3.3049 | 2024-04-04 14:00 | 3.3952 | 3.9574 | 3.9574 | 3.9574 | 3.9574
2024-06-04 15:00 | 2.3244 | 2.4939 | 3.0959 | 3.2564 | 3.4169 | 2024-04-04 15:00 | 3.4866 | 4.064 | 4.064 | 4.064 | 4.064
2024-06-04 16:00 | 2.2673 | 2.4326 | 3.0198 | 3.1763 | 3.3329 | 2024-04-04 16:00 | 3.5971 | 4.1928 | 4.1928 | 4.1928 | 4.1928
2024-06-04 17:00 | 2.3054 | 2.4735 | 3.0705 | 3.2297 | 3.3889 | 2024-04-04 17:00 | 3.5971 | 4.1928 | 4.1928 | 4.1928 | 4.1928
2024-06-04 18:00 | 2.3244 | 2.4939 | 3.0959 | 3.2564 | 3.4169 | 2024-04-04 18:00 | 3.338 | 3.8907 | 3.8907 | 3.8907 | 3.8907
2024-06-04 19:00 | 1.9243 | 2.0646 | 2.563 | 2.6959 | 2.8288 | 2024-04-04 19:00 | 2.7207 | 3.1712 | 3.1712 | 3.1712 | 3.1712
2024-06-04 20:00 | 1.81 | 1.942 | 2.4107 | 2.5357 | 2.6607 | 2024-04-04 20:00 | 2.6216 | 3.0557 | 3.0557 | 3.0557 | 3.0557
2024-06-04 21:00 | 1.7909 | 1.9215 | 2.3854 | 2.509 | 2.6327 | 2024-04-04 21:00 | 2.1949 | 2.5583 | 2.5583 | 2.5583 | 2.5583
2024-06-04 22:00 | 1.7528 | 1.8807 | 2.3346 | 2.4557 | 2.5767 | 2024-04-04 22:00 | 1.9586 | 2.2829 | 2.2829 | 2.2829 | 2.2829
2024-06-04 23:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-04-04 23:00 | 1.7147 | 1.9987 | 1.9987 | 1.9987 | 1.9987
2024-06-05 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-04-05 | 1.5318 | 1.7855 | 1.7855 | 1.7855 | 1.7855
2024-06-05 01:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-04-05 01:00 | 1.6004 | 1.8654 | 1.8654 | 1.8654 | 1.8654
2024-06-05 02:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-04-05 02:00 | 1.5471 | 1.8032 | 1.8032 | 1.8032 | 1.8032
2024-06-05 03:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-04-05 03:00 | 1.6957 | 1.9765 | 1.9765 | 1.9765 | 1.9765
2024-06-05 04:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-04-05 04:00 | 2.0234 | 2.3584 | 2.3584 | 2.3584 | 2.3584
2024-06-05 05:00 | 1.8481 | 1.9829 | 2.4615 | 2.5891 | 2.7167 | 2024-04-05 05:00 | 2.3892 | 2.7848 | 2.7848 | 2.7848 | 2.7848
2024-06-05 06:00 | 2.0767 | 2.2282 | 2.766 | 2.9094 | 3.0528 | 2024-04-05 06:00 | 2.6978 | 3.1446 | 3.1446 | 3.1446 | 3.1446
2024-06-05 07:00 | 2.7245 | 2.9232 | 3.6288 | 3.8169 | 4.0051 | 2024-04-05 07:00 | 3.0675 | 3.5754 | 3.5754 | 3.5754 | 3.5754
2024-06-05 08:00 | 2.534 | 2.7188 | 3.375 | 3.55 | 3.725 | 2024-04-05 08:00 | 3.5971 | 4.1928 | 4.1928 | 4.1928 | 4.1928
2024-06-05 09:00 | 2.5149 | 2.6983 | 3.3496 | 3.5233 | 3.697 | 2024-04-05 09:00 | 3.5171 | 4.0995 | 4.0995 | 4.0995 | 4.0995
2024-06-05 10:00 | 2.4006 | 2.5757 | 3.1974 | 3.3632 | 3.529 | 2024-04-05 10:00 | 3.7343 | 4.3527 | 4.3527 | 4.3527 | 4.3527
2024-06-05 11:00 | 2.4768 | 2.6574 | 3.2989 | 3.4699 | 3.641 | 2024-04-05 11:00 | 3.5781 | 4.1706 | 4.1706 | 4.1706 | 4.1706
2024-06-05 12:00 | 2.4578 | 2.637 | 3.2735 | 3.4433 | 3.613 | 2024-04-05 12:00 | 3.6543 | 4.2594 | 4.2594 | 4.2594 | 4.2594
2024-06-05 13:00 | 2.3435 | 2.5144 | 3.1213 | 3.2831 | 3.4449 | 2024-04-05 13:00 | 3.681 | 4.2905 | 4.2905 | 4.2905 | 4.2905
2024-06-05 14:00 | 2.3054 | 2.4735 | 3.0705 | 3.2297 | 3.3889 | 2024-04-05 14:00 | 3.7076 | 4.3216 | 4.3216 | 4.3216 | 4.3216
2024-06-05 15:00 | 2.3054 | 2.4735 | 3.0705 | 3.2297 | 3.3889 | 2024-04-05 15:00 | 3.5781 | 4.1706 | 4.1706 | 4.1706 | 4.1706
2024-06-05 16:00 | 2.2673 | 2.4326 | 3.0198 | 3.1763 | 3.3329 | 2024-04-05 16:00 | 3.5781 | 4.1706 | 4.1706 | 4.1706 | 4.1706
2024-06-05 17:00 | 2.3054 | 2.4735 | 3.0705 | 3.2297 | 3.3889 | 2024-04-05 17:00 | 3.4599 | 4.0329 | 4.0329 | 4.0329 | 4.0329
2024-06-05 18:00 | 2.1529 | 2.3099 | 2.8675 | 3.0162 | 3.1649 | 2024-04-05 18:00 | 3.2961 | 3.8419 | 3.8419 | 3.8419 | 3.8419
2024-06-05 19:00 | 1.8862 | 2.0237 | 2.5122 | 2.6425 | 2.7728 | 2024-04-05 19:00 | 2.9836 | 3.4777 | 3.4777 | 3.4777 | 3.4777
2024-06-05 20:00 | 1.7909 | 1.9215 | 2.3854 | 2.509 | 2.6327 | 2024-04-05 20:00 | 2.7512 | 3.2068 | 3.2068 | 3.2068 | 3.2068
2024-06-05 21:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-04-05 21:00 | 2.4006 | 2.7981 | 2.7981 | 2.7981 | 2.7981
2024-06-05 22:00 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 2024-04-05 22:00 | 1.9586 | 2.2829 | 2.2829 | 2.2829 | 2.2829
2024-06-05 23:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-04-05 23:00 | 1.7795 | 2.0742 | 2.0742 | 2.0742 | 2.0742
2024-06-06 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-04-06 | 1.81 | 2.1097 | 2.1097 | 2.1097 | 2.1097
2024-06-06 01:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-04-06 01:00 | 1.7109 | 1.9942 | 1.9942 | 1.9942 | 1.9942
2024-06-06 02:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-04-06 02:00 | 1.6881 | 1.9676 | 1.9676 | 1.9676 | 1.9676
2024-06-06 03:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-04-06 03:00 | 1.8672 | 2.1763 | 2.1763 | 2.1763 | 2.1763
2024-06-06 04:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-04-06 04:00 | 1.9967 | 2.3273 | 2.3273 | 2.3273 | 2.3273
2024-06-06 05:00 | 1.7338 | 1.8602 | 2.3092 | 2.429 | 2.5487 | 2024-04-06 05:00 | 2.3054 | 2.6871 | 2.6871 | 2.6871 | 2.6871
2024-06-06 06:00 | 2.0386 | 2.1873 | 2.7152 | 2.856 | 2.9968 | 2024-04-06 06:00 | 2.4121 | 2.8115 | 2.8115 | 2.8115 | 2.8115
2024-06-06 07:00 | 2.4387 | 2.6166 | 3.2481 | 3.4166 | 3.585 | 2024-04-06 07:00 | 2.9074 | 3.3889 | 3.3889 | 3.3889 | 3.3889
2024-06-06 08:00 | 2.6102 | 2.8005 | 3.4765 | 3.6568 | 3.8371 | 2024-04-06 08:00 | 3.0065 | 3.5043 | 3.5043 | 3.5043 | 3.5043
2024-06-06 09:00 | 2.534 | 2.7188 | 3.375 | 3.55 | 3.725 | 2024-04-06 09:00 | 3.3571 | 3.913 | 3.913 | 3.913 | 3.913
2024-06-06 10:00 | 2.4197 | 2.5961 | 3.2228 | 3.3899 | 3.557 | 2024-04-06 10:00 | 3.277 | 3.8197 | 3.8197 | 3.8197 | 3.8197
2024-06-06 11:00 | 2.2482 | 2.4121 | 2.9944 | 3.1496 | 3.3049 | 2024-04-06 11:00 | 3.2885 | 3.833 | 3.833 | 3.833 | 3.833
2024-06-06 12:00 | 2.2482 | 2.4121 | 2.9944 | 3.1496 | 3.3049 | 2024-04-06 12:00 | 3.1742 | 3.6998 | 3.6998 | 3.6998 | 3.6998
2024-06-06 13:00 | 2.3054 | 2.4735 | 3.0705 | 3.2297 | 3.3889 | 2024-04-06 13:00 | 2.8846 | 3.3622 | 3.3622 | 3.3622 | 3.3622
2024-06-06 14:00 | 2.0958 | 2.2486 | 2.7914 | 2.9361 | 3.0808 | 2024-04-06 14:00 | 3.0941 | 3.6065 | 3.6065 | 3.6065 | 3.6065
2024-06-06 15:00 | 2.1529 | 2.3099 | 2.8675 | 3.0162 | 3.1649 | 2024-04-06 15:00 | 3.1208 | 3.6376 | 3.6376 | 3.6376 | 3.6376
2024-06-06 16:00 | 2.2482 | 2.4121 | 2.9944 | 3.1496 | 3.3049 | 2024-04-06 16:00 | 3.4104 | 3.9751 | 3.9751 | 3.9751 | 3.9751
2024-06-06 17:00 | 2.2291 | 2.3917 | 2.969 | 3.123 | 3.2769 | 2024-04-06 17:00 | 2.9836 | 3.4777 | 3.4777 | 3.4777 | 3.4777
2024-06-06 18:00 | 2.2101 | 2.3713 | 2.9436 | 3.0963 | 3.2489 | 2024-04-06 18:00 | 2.8807 | 3.3578 | 3.3578 | 3.3578 | 3.3578
2024-06-06 19:00 | 1.9053 | 2.0442 | 2.5376 | 2.6692 | 2.8008 | 2024-04-06 19:00 | 2.4768 | 2.887 | 2.887 | 2.887 | 2.887
2024-06-06 20:00 | 1.829 | 1.9624 | 2.4361 | 2.5624 | 2.6887 | 2024-04-06 20:00 | 2.2939 | 2.6738 | 2.6738 | 2.6738 | 2.6738
2024-06-06 21:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-04-06 21:00 | 2.1796 | 2.5405 | 2.5405 | 2.5405 | 2.5405
2024-06-06 22:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-04-06 22:00 | 1.9853 | 2.314 | 2.314 | 2.314 | 2.314
2024-06-06 23:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-04-06 23:00 | 1.7262 | 2.012 | 2.012 | 2.012 | 2.012
2024-06-07 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-04-07 | 1.7338 | 2.0209 | 2.0209 | 2.0209 | 2.0209
2024-06-07 01:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-04-07 01:00 | 1.6842 | 1.9631 | 1.9631 | 1.9631 | 1.9631
2024-06-07 02:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-04-07 02:00 | 1.6347 | 1.9054 | 1.9054 | 1.9054 | 1.9054
2024-06-07 03:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-04-07 03:00 | 1.7605 | 2.052 | 2.052 | 2.052 | 2.052
2024-06-07 04:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-04-07 04:00 | 1.9662 | 2.2918 | 2.2918 | 2.2918 | 2.2918
2024-06-07 05:00 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 2024-04-07 05:00 | 2.2482 | 2.6205 | 2.6205 | 2.6205 | 2.6205
2024-06-07 06:00 | 1.9243 | 2.0646 | 2.563 | 2.6959 | 2.8288 | 2024-04-07 06:00 | 2.3549 | 2.7448 | 2.7448 | 2.7448 | 2.7448
2024-06-07 07:00 | 2.4578 | 2.637 | 3.2735 | 3.4433 | 3.613 | 2024-04-07 07:00 | 2.5378 | 2.958 | 2.958 | 2.958 | 2.958
2024-06-07 08:00 | 2.4387 | 2.6166 | 3.2481 | 3.4166 | 3.585 | 2024-04-07 08:00 | 2.6483 | 3.0868 | 3.0868 | 3.0868 | 3.0868
2024-06-07 09:00 | 2.4578 | 2.637 | 3.2735 | 3.4433 | 3.613 | 2024-04-07 09:00 | 2.835 | 3.3045 | 3.3045 | 3.3045 | 3.3045
2024-06-07 10:00 | 2.3625 | 2.5348 | 3.1466 | 3.3098 | 3.473 | 2024-04-07 10:00 | 2.9608 | 3.451 | 3.451 | 3.451 | 3.451
2024-06-07 11:00 | 2.1529 | 2.3099 | 2.8675 | 3.0162 | 3.1649 | 2024-04-07 11:00 | 3.3342 | 3.8863 | 3.8863 | 3.8863 | 3.8863
2024-06-07 12:00 | 2.2673 | 2.4326 | 3.0198 | 3.1763 | 3.3329 | 2024-04-07 12:00 | 3.2427 | 3.7797 | 3.7797 | 3.7797 | 3.7797
2024-06-07 13:00 | 2.1529 | 2.3099 | 2.8675 | 3.0162 | 3.1649 | 2024-04-07 13:00 | 3.5323 | 4.1173 | 4.1173 | 4.1173 | 4.1173
2024-06-07 14:00 | 2.1529 | 2.3099 | 2.8675 | 3.0162 | 3.1649 | 2024-04-07 14:00 | 3.2847 | 3.8286 | 3.8286 | 3.8286 | 3.8286
2024-06-07 15:00 | 2.191 | 2.3508 | 2.9183 | 3.0696 | 3.2209 | 2024-04-07 15:00 | 3.3266 | 3.8774 | 3.8774 | 3.8774 | 3.8774
2024-06-07 16:00 | 2.1529 | 2.3099 | 2.8675 | 3.0162 | 3.1649 | 2024-04-07 16:00 | 3.0713 | 3.5798 | 3.5798 | 3.5798 | 3.5798
2024-06-07 17:00 | 2.1529 | 2.3099 | 2.8675 | 3.0162 | 3.1649 | 2024-04-07 17:00 | 3.3266 | 3.8774 | 3.8774 | 3.8774 | 3.8774
2024-06-07 18:00 | 2.1529 | 2.3099 | 2.8675 | 3.0162 | 3.1649 | 2024-04-07 18:00 | 2.7626 | 3.2201 | 3.2201 | 3.2201 | 3.2201
2024-06-07 19:00 | 1.81 | 1.942 | 2.4107 | 2.5357 | 2.6607 | 2024-04-07 19:00 | 2.4387 | 2.8426 | 2.8426 | 2.8426 | 2.8426
2024-06-07 20:00 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 2024-04-07 20:00 | 2.1949 | 2.5583 | 2.5583 | 2.5583 | 2.5583
2024-06-07 21:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-04-07 21:00 | 2.012 | 2.3451 | 2.3451 | 2.3451 | 2.3451
2024-06-07 22:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-04-07 22:00 | 1.8938 | 2.2074 | 2.2074 | 2.2074 | 2.2074
2024-06-07 23:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-04-07 23:00 | 1.7338 | 2.0209 | 2.0209 | 2.0209 | 2.0209
2024-06-08 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-04-08 | 1.589 | 1.8521 | 1.8521 | 1.8521 | 1.8521
2024-06-08 01:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-04-08 01:00 | 1.5585 | 1.8166 | 1.8166 | 1.8166 | 1.8166
2024-06-08 02:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-04-08 02:00 | 1.5661 | 1.8255 | 1.8255 | 1.8255 | 1.8255
2024-06-08 03:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-04-08 03:00 | 1.8138 | 2.1141 | 2.1141 | 2.1141 | 2.1141
2024-06-08 04:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-04-08 04:00 | 2.0424 | 2.3806 | 2.3806 | 2.3806 | 2.3806
2024-06-08 05:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-04-08 05:00 | 2.2825 | 2.6605 | 2.6605 | 2.6605 | 2.6605
2024-06-08 06:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-04-08 06:00 | 2.6712 | 3.1135 | 3.1135 | 3.1135 | 3.1135
2024-06-08 07:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-04-08 07:00 | 2.9493 | 3.4377 | 3.4377 | 3.4377 | 3.4377
2024-06-08 08:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-04-08 08:00 | 3.4523 | 4.024 | 4.024 | 4.024 | 4.024
2024-06-08 09:00 | 1.1813 | 1.2674 | 1.5733 | 1.6549 | 1.7365 | 2024-04-08 09:00 | 3.6314 | 4.2327 | 4.2327 | 4.2327 | 4.2327
2024-06-08 10:00 | 1.1622 | 1.247 | 1.5479 | 1.6282 | 1.7085 | 2024-04-08 10:00 | 3.6124 | 4.2105 | 4.2105 | 4.2105 | 4.2105
2024-06-08 11:00 | 1.2003 | 1.2878 | 1.5987 | 1.6816 | 1.7645 | 2024-04-08 11:00 | 3.6047 | 4.2016 | 4.2016 | 4.2016 | 4.2016
2024-06-08 12:00 | 1.2575 | 1.3492 | 1.6748 | 1.7617 | 1.8485 | 2024-04-08 12:00 | 3.9286 | 4.5792 | 4.5792 | 4.5792 | 4.5792
2024-06-08 13:00 | 1.1241 | 1.2061 | 1.4972 | 1.5748 | 1.6525 | 2024-04-08 13:00 | 3.7953 | 4.4237 | 4.4237 | 4.4237 | 4.4237
2024-06-08 14:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-04-08 14:00 | 3.1132 | 3.6287 | 3.6287 | 3.6287 | 3.6287
2024-06-08 15:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-04-08 15:00 | 3.5133 | 4.0951 | 4.0951 | 4.0951 | 4.0951
2024-06-08 16:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-04-08 16:00 | 3.8448 | 4.4815 | 4.4815 | 4.4815 | 4.4815
2024-06-08 17:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-04-08 17:00 | 3.5819 | 4.175 | 4.175 | 4.175 | 4.175
2024-06-08 18:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-04-08 18:00 | 2.9493 | 3.4377 | 3.4377 | 3.4377 | 3.4377
2024-06-08 19:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-04-08 19:00 | 2.6864 | 3.1312 | 3.1312 | 3.1312 | 3.1312
2024-06-08 20:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-04-08 20:00 | 2.4616 | 2.8692 | 2.8692 | 2.8692 | 2.8692
2024-06-08 21:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-04-08 21:00 | 2.0805 | 2.4251 | 2.4251 | 2.4251 | 2.4251
2024-06-08 22:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-04-08 22:00 | 1.8443 | 2.1497 | 2.1497 | 2.1497 | 2.1497
2024-06-08 23:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-04-08 23:00 | 1.7071 | 1.9898 | 1.9898 | 1.9898 | 1.9898
2024-06-09 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-04-09 | 1.5737 | 1.8343 | 1.8343 | 1.8343 | 1.8343
2024-06-09 01:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-04-09 01:00 | 1.6652 | 1.9409 | 1.9409 | 1.9409 | 1.9409
2024-06-09 02:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-04-09 02:00 | 1.6195 | 1.8876 | 1.8876 | 1.8876 | 1.8876
2024-06-09 03:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-04-09 03:00 | 1.749 | 2.0386 | 2.0386 | 2.0386 | 2.0386
2024-06-09 04:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-04-09 04:00 | 1.9281 | 2.2474 | 2.2474 | 2.2474 | 2.2474
2024-06-09 05:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-04-09 05:00 | 2.1377 | 2.4917 | 2.4917 | 2.4917 | 2.4917
2024-06-09 06:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-04-09 06:00 | 2.5759 | 3.0024 | 3.0024 | 3.0024 | 3.0024
2024-06-09 07:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-04-09 07:00 | 2.8503 | 3.3222 | 3.3222 | 3.3222 | 3.3222
2024-06-09 08:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-04-09 08:00 | 3.2961 | 3.8419 | 3.8419 | 3.8419 | 3.8419
2024-06-09 09:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-04-09 09:00 | 3.4295 | 3.9973 | 3.9973 | 3.9973 | 3.9973
2024-06-09 10:00 | 1.3146 | 1.4105 | 1.751 | 1.8417 | 1.9325 | 2024-04-09 10:00 | 3.4866 | 4.064 | 4.064 | 4.064 | 4.064
2024-06-09 11:00 | 1.2384 | 1.3287 | 1.6494 | 1.735 | 1.8205 | 2024-04-09 11:00 | 3.5438 | 4.1306 | 4.1306 | 4.1306 | 4.1306
2024-06-09 12:00 | 0.99073 | 1.063 | 1.3196 | 1.388 | 1.4564 | 2024-04-09 12:00 | 3.6771 | 4.286 | 4.286 | 4.286 | 4.286
2024-06-09 13:00 | 1.2194 | 1.3083 | 1.6241 | 1.7083 | 1.7925 | 2024-04-09 13:00 | 3.7267 | 4.3438 | 4.3438 | 4.3438 | 4.3438
2024-06-09 14:00 | 1.105 | 1.1856 | 1.4718 | 1.5481 | 1.6244 | 2024-04-09 14:00 | 3.3533 | 3.9085 | 3.9085 | 3.9085 | 3.9085
2024-06-09 15:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-04-09 15:00 | 3.3037 | 3.8508 | 3.8508 | 3.8508 | 3.8508
2024-06-09 16:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-04-09 16:00 | 3.2199 | 3.7531 | 3.7531 | 3.7531 | 3.7531
2024-06-09 17:00 | 1.7338 | 1.8602 | 2.3092 | 2.429 | 2.5487 | 2024-04-09 17:00 | 3.338 | 3.8907 | 3.8907 | 3.8907 | 3.8907
2024-06-09 18:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-04-09 18:00 | 3.0522 | 3.5576 | 3.5576 | 3.5576 | 3.5576
2024-06-09 19:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-04-09 19:00 | 2.8884 | 3.3666 | 3.3666 | 3.3666 | 3.3666
2024-06-09 20:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-04-09 20:00 | 2.5454 | 2.9669 | 2.9669 | 2.9669 | 2.9669
2024-06-09 21:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-04-09 21:00 | 2.2596 | 2.6338 | 2.6338 | 2.6338 | 2.6338
2024-06-09 22:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-04-09 22:00 | 1.8329 | 2.1364 | 2.1364 | 2.1364 | 2.1364
2024-06-09 23:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-04-09 23:00 | 1.8824 | 2.1941 | 2.1941 | 2.1941 | 2.1941
2024-06-10 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-04-10 | 1.5814 | 1.8432 | 1.8432 | 1.8432 | 1.8432
2024-06-10 01:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-04-10 01:00 | 1.6118 | 1.8787 | 1.8787 | 1.8787 | 1.8787
2024-06-10 02:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-04-10 02:00 | 1.5928 | 1.8565 | 1.8565 | 1.8565 | 1.8565
2024-06-10 03:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-04-10 03:00 | 1.8024 | 2.1008 | 2.1008 | 2.1008 | 2.1008
2024-06-10 04:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-04-10 04:00 | 1.9586 | 2.2829 | 2.2829 | 2.2829 | 2.2829
2024-06-10 05:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-04-10 05:00 | 2.313 | 2.696 | 2.696 | 2.696 | 2.696
2024-06-10 06:00 | 1.7528 | 1.8807 | 2.3346 | 2.4557 | 2.5767 | 2024-04-10 06:00 | 2.4806 | 2.8914 | 2.8914 | 2.8914 | 2.8914
2024-06-10 07:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-04-10 07:00 | 2.8998 | 3.38 | 3.38 | 3.38 | 3.38
2024-06-10 08:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-04-10 08:00 | 3.0522 | 3.5576 | 3.5576 | 3.5576 | 3.5576
2024-06-10 09:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-04-10 09:00 | 3.4333 | 4.0018 | 4.0018 | 4.0018 | 4.0018
2024-06-10 10:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-04-10 10:00 | 3.4333 | 4.0018 | 4.0018 | 4.0018 | 4.0018
2024-06-10 11:00 | 1.3908 | 1.4923 | 1.8525 | 1.9485 | 2.0446 | 2024-04-10 11:00 | 3.0903 | 3.602 | 3.602 | 3.602 | 3.602
2024-06-10 12:00 | 1.3718 | 1.4718 | 1.8271 | 1.9218 | 2.0166 | 2024-04-10 12:00 | 3.258 | 3.7975 | 3.7975 | 3.7975 | 3.7975
2024-06-10 13:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-04-10 13:00 | 3.2999 | 3.8463 | 3.8463 | 3.8463 | 3.8463
2024-06-10 14:00 | 1.3527 | 1.4514 | 1.8017 | 1.8951 | 1.9885 | 2024-04-10 14:00 | 3.479 | 4.0551 | 4.0551 | 4.0551 | 4.0551
2024-06-10 15:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-04-10 15:00 | 3.2466 | 3.7841 | 3.7841 | 3.7841 | 3.7841
2024-06-10 16:00 | 1.7528 | 1.8807 | 2.3346 | 2.4557 | 2.5767 | 2024-04-10 16:00 | 3.3647 | 3.9218 | 3.9218 | 3.9218 | 3.9218
2024-06-10 17:00 | 1.7528 | 1.8807 | 2.3346 | 2.4557 | 2.5767 | 2024-04-10 17:00 | 3.3075 | 3.8552 | 3.8552 | 3.8552 | 3.8552
2024-06-10 18:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-04-10 18:00 | 3.2427 | 3.7797 | 3.7797 | 3.7797 | 3.7797
2024-06-10 19:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-04-10 19:00 | 2.9341 | 3.4199 | 3.4199 | 3.4199 | 3.4199
2024-06-10 20:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-04-10 20:00 | 2.5454 | 2.9669 | 2.9669 | 2.9669 | 2.9669
2024-06-10 21:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-04-10 21:00 | 2.3778 | 2.7715 | 2.7715 | 2.7715 | 2.7715
2024-06-10 22:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-04-10 22:00 | 1.7795 | 2.0742 | 2.0742 | 2.0742 | 2.0742
2024-06-10 23:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-04-10 23:00 | 1.7566 | 2.0475 | 2.0475 | 2.0475 | 2.0475
2024-06-11 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-04-11 | 1.6728 | 1.9498 | 1.9498 | 1.9498 | 1.9498
2024-06-11 01:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-04-11 01:00 | 1.5928 | 1.8565 | 1.8565 | 1.8565 | 1.8565
2024-06-11 02:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-04-11 02:00 | 1.5737 | 1.8343 | 1.8343 | 1.8343 | 1.8343
2024-06-11 03:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-04-11 03:00 | 1.6728 | 1.9498 | 1.9498 | 1.9498 | 1.9498
2024-06-11 04:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-04-11 04:00 | 1.9777 | 2.3051 | 2.3051 | 2.3051 | 2.3051
2024-06-11 05:00 | 1.7719 | 1.9011 | 2.36 | 2.4823 | 2.6047 | 2024-04-11 05:00 | 2.3778 | 2.7715 | 2.7715 | 2.7715 | 2.7715
2024-06-11 06:00 | 2.0767 | 2.2282 | 2.766 | 2.9094 | 3.0528 | 2024-04-11 06:00 | 2.5873 | 3.0158 | 3.0158 | 3.0158 | 3.0158
2024-06-11 07:00 | 2.6483 | 2.8414 | 3.5273 | 3.7102 | 3.8931 | 2024-04-11 07:00 | 2.7931 | 3.2556 | 3.2556 | 3.2556 | 3.2556
2024-06-11 08:00 | 2.7245 | 2.9232 | 3.6288 | 3.8169 | 4.0051 | 2024-04-11 08:00 | 2.9112 | 3.3933 | 3.3933 | 3.3933 | 3.3933
2024-06-11 09:00 | 2.4959 | 2.6779 | 3.3243 | 3.4966 | 3.669 | 2024-04-11 09:00 | 3.0179 | 3.5177 | 3.5177 | 3.5177 | 3.5177
2024-06-11 10:00 | 2.4959 | 2.6779 | 3.3243 | 3.4966 | 3.669 | 2024-04-11 10:00 | 2.7359 | 3.189 | 3.189 | 3.189 | 3.189
2024-06-11 11:00 | 2.4959 | 2.6779 | 3.3243 | 3.4966 | 3.669 | 2024-04-11 11:00 | 2.7207 | 3.1712 | 3.1712 | 3.1712 | 3.1712
2024-06-11 12:00 | 2.553 | 2.7392 | 3.4004 | 3.5767 | 3.753 | 2024-04-11 12:00 | 3.0065 | 3.5043 | 3.5043 | 3.5043 | 3.5043
2024-06-11 13:00 | 2.4768 | 2.6574 | 3.2989 | 3.4699 | 3.641 | 2024-04-11 13:00 | 3.037 | 3.5399 | 3.5399 | 3.5399 | 3.5399
2024-06-11 14:00 | 2.4006 | 2.5757 | 3.1974 | 3.3632 | 3.529 | 2024-04-11 14:00 | 3.2237 | 3.7575 | 3.7575 | 3.7575 | 3.7575
2024-06-11 15:00 | 2.2863 | 2.453 | 3.0451 | 3.203 | 3.3609 | 2024-04-11 15:00 | 3.3304 | 3.8819 | 3.8819 | 3.8819 | 3.8819
2024-06-11 16:00 | 2.3625 | 2.5348 | 3.1466 | 3.3098 | 3.473 | 2024-04-11 16:00 | 3.7229 | 4.3393 | 4.3393 | 4.3393 | 4.3393
2024-06-11 17:00 | 2.3244 | 2.4939 | 3.0959 | 3.2564 | 3.4169 | 2024-04-11 17:00 | 3.4714 | 4.0462 | 4.0462 | 4.0462 | 4.0462
2024-06-11 18:00 | 2.3054 | 2.4735 | 3.0705 | 3.2297 | 3.3889 | 2024-04-11 18:00 | 3.3418 | 3.8952 | 3.8952 | 3.8952 | 3.8952
2024-06-11 19:00 | 1.8862 | 2.0237 | 2.5122 | 2.6425 | 2.7728 | 2024-04-11 19:00 | 2.6712 | 3.1135 | 3.1135 | 3.1135 | 3.1135
2024-06-11 20:00 | 1.8481 | 1.9829 | 2.4615 | 2.5891 | 2.7167 | 2024-04-11 20:00 | 2.4692 | 2.8781 | 2.8781 | 2.8781 | 2.8781
2024-06-11 21:00 | 1.7338 | 1.8602 | 2.3092 | 2.429 | 2.5487 | 2024-04-11 21:00 | 2.2863 | 2.6649 | 2.6649 | 2.6649 | 2.6649
2024-06-11 22:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-04-11 22:00 | 2.0805 | 2.4251 | 2.4251 | 2.4251 | 2.4251
2024-06-11 23:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-04-11 23:00 | 1.7681 | 2.0609 | 2.0609 | 2.0609 | 2.0609
2024-06-12 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-04-12 | 1.5661 | 1.8255 | 1.8255 | 1.8255 | 1.8255
2024-06-12 01:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-04-12 01:00 | 1.5585 | 1.8166 | 1.8166 | 1.8166 | 1.8166
2024-06-12 02:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-04-12 02:00 | 1.589 | 1.8521 | 1.8521 | 1.8521 | 1.8521
2024-06-12 03:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-04-12 03:00 | 1.7071 | 1.9898 | 1.9898 | 1.9898 | 1.9898
2024-06-12 04:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-04-12 04:00 | 1.9777 | 2.3051 | 2.3051 | 2.3051 | 2.3051
2024-06-12 05:00 | 1.7909 | 1.9215 | 2.3854 | 2.509 | 2.6327 | 2024-04-12 05:00 | 2.2825 | 2.6605 | 2.6605 | 2.6605 | 2.6605
2024-06-12 06:00 | 1.9624 | 2.1055 | 2.6137 | 2.7493 | 2.8848 | 2024-04-12 06:00 | 2.4044 | 2.8026 | 2.8026 | 2.8026 | 2.8026
2024-06-12 07:00 | 2.6483 | 2.8414 | 3.5273 | 3.7102 | 3.8931 | 2024-04-12 07:00 | 2.5264 | 2.9447 | 2.9447 | 2.9447 | 2.9447
2024-06-12 08:00 | 2.4768 | 2.6574 | 3.2989 | 3.4699 | 3.641 | 2024-04-12 08:00 | 3.0217 | 3.5221 | 3.5221 | 3.5221 | 3.5221
2024-06-12 09:00 | 2.4387 | 2.6166 | 3.2481 | 3.4166 | 3.585 | 2024-04-12 09:00 | 2.8541 | 3.3267 | 3.3267 | 3.3267 | 3.3267
2024-06-12 10:00 | 2.3244 | 2.4939 | 3.0959 | 3.2564 | 3.4169 | 2024-04-12 10:00 | 2.8807 | 3.3578 | 3.3578 | 3.3578 | 3.3578
2024-06-12 11:00 | 2.3816 | 2.5552 | 3.172 | 3.3365 | 3.501 | 2024-04-12 11:00 | 3.2466 | 3.7841 | 3.7841 | 3.7841 | 3.7841
2024-06-12 12:00 | 2.2291 | 2.3917 | 2.969 | 3.123 | 3.2769 | 2024-04-12 12:00 | 2.9417 | 3.4288 | 3.4288 | 3.4288 | 3.4288
2024-06-12 13:00 | 2.0767 | 2.2282 | 2.766 | 2.9094 | 3.0528 | 2024-04-12 13:00 | 3.1361 | 3.6553 | 3.6553 | 3.6553 | 3.6553
2024-06-12 14:00 | 2.0577 | 2.2077 | 2.7406 | 2.8827 | 3.0248 | 2024-04-12 14:00 | 3.4409 | 4.0107 | 4.0107 | 4.0107 | 4.0107
2024-06-12 15:00 | 2.2673 | 2.4326 | 3.0198 | 3.1763 | 3.3329 | 2024-04-12 15:00 | 3.4523 | 4.024 | 4.024 | 4.024 | 4.024
2024-06-12 16:00 | 2.2673 | 2.4326 | 3.0198 | 3.1763 | 3.3329 | 2024-04-12 16:00 | 3.7495 | 4.3704 | 4.3704 | 4.3704 | 4.3704
2024-06-12 17:00 | 2.2863 | 2.453 | 3.0451 | 3.203 | 3.3609 | 2024-04-12 17:00 | 3.6543 | 4.2594 | 4.2594 | 4.2594 | 4.2594
2024-06-12 18:00 | 2.3435 | 2.5144 | 3.1213 | 3.2831 | 3.4449 | 2024-04-12 18:00 | 3.498 | 4.0773 | 4.0773 | 4.0773 | 4.0773
2024-06-12 19:00 | 1.829 | 1.9624 | 2.4361 | 2.5624 | 2.6887 | 2024-04-12 19:00 | 2.8807 | 3.3578 | 3.3578 | 3.3578 | 3.3578
2024-06-12 20:00 | 1.7528 | 1.8807 | 2.3346 | 2.4557 | 2.5767 | 2024-04-12 20:00 | 2.6064 | 3.038 | 3.038 | 3.038 | 3.038
2024-06-12 21:00 | 1.7719 | 1.9011 | 2.36 | 2.4823 | 2.6047 | 2024-04-12 21:00 | 2.2177 | 2.5849 | 2.5849 | 2.5849 | 2.5849
2024-06-12 22:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-04-12 22:00 | 1.9281 | 2.2474 | 2.2474 | 2.2474 | 2.2474
2024-06-12 23:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-04-12 23:00 | 1.7262 | 2.012 | 2.012 | 2.012 | 2.012
2024-06-13 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-04-13 | 1.5471 | 1.8032 | 1.8032 | 1.8032 | 1.8032
2024-06-13 01:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-04-13 01:00 | 1.7643 | 2.0564 | 2.0564 | 2.0564 | 2.0564
2024-06-13 02:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-04-13 02:00 | 1.6957 | 1.9765 | 1.9765 | 1.9765 | 1.9765
2024-06-13 03:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-04-13 03:00 | 1.7605 | 2.052 | 2.052 | 2.052 | 2.052
2024-06-13 04:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-04-13 04:00 | 1.8672 | 2.1763 | 2.1763 | 2.1763 | 2.1763
2024-06-13 05:00 | 1.8862 | 2.0237 | 2.5122 | 2.6425 | 2.7728 | 2024-04-13 05:00 | 2.2025 | 2.5672 | 2.5672 | 2.5672 | 2.5672
2024-06-13 06:00 | 2.1339 | 2.2895 | 2.8421 | 2.9895 | 3.1369 | 2024-04-13 06:00 | 2.3854 | 2.7804 | 2.7804 | 2.7804 | 2.7804
2024-06-13 07:00 | 2.8198 | 3.0254 | 3.7557 | 3.9504 | 4.1451 | 2024-04-13 07:00 | 2.473 | 2.8825 | 2.8825 | 2.8825 | 2.8825
2024-06-13 08:00 | 2.7245 | 2.9232 | 3.6288 | 3.8169 | 4.0051 | 2024-04-13 08:00 | 2.8503 | 3.3222 | 3.3222 | 3.3222 | 3.3222
2024-06-13 09:00 | 2.3244 | 2.4939 | 3.0959 | 3.2564 | 3.4169 | 2024-04-13 09:00 | 2.7436 | 3.1979 | 3.1979 | 3.1979 | 3.1979
2024-06-13 10:00 | 2.3816 | 2.5552 | 3.172 | 3.3365 | 3.501 | 2024-04-13 10:00 | 2.5607 | 2.9847 | 2.9847 | 2.9847 | 2.9847
2024-06-13 11:00 | 2.0767 | 2.2282 | 2.766 | 2.9094 | 3.0528 | 2024-04-13 11:00 | 2.4845 | 2.8958 | 2.8958 | 2.8958 | 2.8958
2024-06-13 12:00 | 2.1148 | 2.2691 | 2.8167 | 2.9628 | 3.1089 | 2024-04-13 12:00 | 2.5607 | 2.9847 | 2.9847 | 2.9847 | 2.9847
2024-06-13 13:00 | 2.191 | 2.3508 | 2.9183 | 3.0696 | 3.2209 | 2024-04-13 13:00 | 2.6026 | 3.0335 | 3.0335 | 3.0335 | 3.0335
2024-06-13 14:00 | 2.3816 | 2.5552 | 3.172 | 3.3365 | 3.501 | 2024-04-13 14:00 | 2.8198 | 3.2867 | 3.2867 | 3.2867 | 3.2867
2024-06-13 15:00 | 2.3435 | 2.5144 | 3.1213 | 3.2831 | 3.4449 | 2024-04-13 15:00 | 3.0217 | 3.5221 | 3.5221 | 3.5221 | 3.5221
2024-06-13 16:00 | 2.3435 | 2.5144 | 3.1213 | 3.2831 | 3.4449 | 2024-04-13 16:00 | 3.2008 | 3.7308 | 3.7308 | 3.7308 | 3.7308
2024-06-13 17:00 | 2.3625 | 2.5348 | 3.1466 | 3.3098 | 3.473 | 2024-04-13 17:00 | 2.9379 | 3.4244 | 3.4244 | 3.4244 | 3.4244
2024-06-13 18:00 | 2.2482 | 2.4121 | 2.9944 | 3.1496 | 3.3049 | 2024-04-13 18:00 | 2.7702 | 3.229 | 3.229 | 3.229 | 3.229
2024-06-13 19:00 | 1.8862 | 2.0237 | 2.5122 | 2.6425 | 2.7728 | 2024-04-13 19:00 | 2.4387 | 2.8426 | 2.8426 | 2.8426 | 2.8426
2024-06-13 20:00 | 1.81 | 1.942 | 2.4107 | 2.5357 | 2.6607 | 2024-04-13 20:00 | 2.2673 | 2.6427 | 2.6427 | 2.6427 | 2.6427
2024-06-13 21:00 | 1.7528 | 1.8807 | 2.3346 | 2.4557 | 2.5767 | 2024-04-13 21:00 | 1.9777 | 2.3051 | 2.3051 | 2.3051 | 2.3051
2024-06-13 22:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-04-13 22:00 | 1.7948 | 2.0919 | 2.0919 | 2.0919 | 2.0919
2024-06-13 23:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-04-13 23:00 | 1.8252 | 2.1275 | 2.1275 | 2.1275 | 2.1275
2024-06-14 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-04-14 | 1.7262 | 2.012 | 2.012 | 2.012 | 2.012
2024-06-14 01:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-04-14 01:00 | 1.5737 | 1.8343 | 1.8343 | 1.8343 | 1.8343
2024-06-14 02:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-04-14 02:00 | 1.6118 | 1.8787 | 1.8787 | 1.8787 | 1.8787
2024-06-14 03:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-04-14 03:00 | 1.7681 | 2.0609 | 2.0609 | 2.0609 | 2.0609
2024-06-14 04:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-04-14 04:00 | 1.9014 | 2.2163 | 2.2163 | 2.2163 | 2.2163
2024-06-14 05:00 | 1.7909 | 1.9215 | 2.3854 | 2.509 | 2.6327 | 2024-04-14 05:00 | 2.1758 | 2.5361 | 2.5361 | 2.5361 | 2.5361
2024-06-14 06:00 | 2.0767 | 2.2282 | 2.766 | 2.9094 | 3.0528 | 2024-04-14 06:00 | 2.2596 | 2.6338 | 2.6338 | 2.6338 | 2.6338
2024-06-14 07:00 | 2.7817 | 2.9845 | 3.7049 | 3.897 | 4.0891 | 2024-04-14 07:00 | 2.1491 | 2.505 | 2.505 | 2.505 | 2.505
2024-06-14 08:00 | 2.6293 | 2.821 | 3.5019 | 3.6835 | 3.8651 | 2024-04-14 08:00 | 2.3854 | 2.7804 | 2.7804 | 2.7804 | 2.7804
2024-06-14 09:00 | 2.5149 | 2.6983 | 3.3496 | 3.5233 | 3.697 | 2024-04-14 09:00 | 2.6102 | 3.0424 | 3.0424 | 3.0424 | 3.0424
2024-06-14 10:00 | 2.5721 | 2.7597 | 3.4258 | 3.6034 | 3.781 | 2024-04-14 10:00 | 2.7131 | 3.1623 | 3.1623 | 3.1623 | 3.1623
2024-06-14 11:00 | 2.2291 | 2.3917 | 2.969 | 3.123 | 3.2769 | 2024-04-14 11:00 | 2.534 | 2.9536 | 2.9536 | 2.9536 | 2.9536
2024-06-14 12:00 | 2.3435 | 2.5144 | 3.1213 | 3.2831 | 3.4449 | 2024-04-14 12:00 | 2.6521 | 3.0913 | 3.0913 | 3.0913 | 3.0913
2024-06-14 13:00 | 2.2291 | 2.3917 | 2.969 | 3.123 | 3.2769 | 2024-04-14 13:00 | 2.7398 | 3.1934 | 3.1934 | 3.1934 | 3.1934
2024-06-14 14:00 | 2.1529 | 2.3099 | 2.8675 | 3.0162 | 3.1649 | 2024-04-14 14:00 | 2.7512 | 3.2068 | 3.2068 | 3.2068 | 3.2068
2024-06-14 15:00 | 2.2482 | 2.4121 | 2.9944 | 3.1496 | 3.3049 | 2024-04-14 15:00 | 2.8312 | 3.3 | 3.3 | 3.3 | 3.3
2024-06-14 16:00 | 2.172 | 2.3304 | 2.8929 | 3.0429 | 3.1929 | 2024-04-14 16:00 | 3.0675 | 3.5754 | 3.5754 | 3.5754 | 3.5754
2024-06-14 17:00 | 2.191 | 2.3508 | 2.9183 | 3.0696 | 3.2209 | 2024-04-14 17:00 | 3.0255 | 3.5265 | 3.5265 | 3.5265 | 3.5265
2024-06-14 18:00 | 2.1339 | 2.2895 | 2.8421 | 2.9895 | 3.1369 | 2024-04-14 18:00 | 2.7436 | 3.1979 | 3.1979 | 3.1979 | 3.1979
2024-06-14 19:00 | 1.9243 | 2.0646 | 2.563 | 2.6959 | 2.8288 | 2024-04-14 19:00 | 2.4997 | 2.9136 | 2.9136 | 2.9136 | 2.9136
2024-06-14 20:00 | 1.7338 | 1.8602 | 2.3092 | 2.429 | 2.5487 | 2024-04-14 20:00 | 2.2253 | 2.5938 | 2.5938 | 2.5938 | 2.5938
2024-06-14 21:00 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 2024-04-14 21:00 | 1.9586 | 2.2829 | 2.2829 | 2.2829 | 2.2829
2024-06-14 22:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-04-14 22:00 | 1.8024 | 2.1008 | 2.1008 | 2.1008 | 2.1008
2024-06-14 23:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-04-14 23:00 | 1.589 | 1.8521 | 1.8521 | 1.8521 | 1.8521
2024-06-15 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-04-15 | 1.5394 | 1.7944 | 1.7944 | 1.7944 | 1.7944
2024-06-15 01:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-04-15 01:00 | 1.5623 | 1.821 | 1.821 | 1.821 | 1.821
2024-06-15 02:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-04-15 02:00 | 1.5928 | 1.8565 | 1.8565 | 1.8565 | 1.8565
2024-06-15 03:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-04-15 03:00 | 1.7566 | 2.0475 | 2.0475 | 2.0475 | 2.0475
2024-06-15 04:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-04-15 04:00 | 2.0996 | 2.4473 | 2.4473 | 2.4473 | 2.4473
2024-06-15 05:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-04-15 05:00 | 2.2139 | 2.5805 | 2.5805 | 2.5805 | 2.5805
2024-06-15 06:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-04-15 06:00 | 2.4692 | 2.8781 | 2.8781 | 2.8781 | 2.8781
2024-06-15 07:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-04-15 07:00 | 2.6597 | 3.1002 | 3.1002 | 3.1002 | 3.1002
2024-06-15 08:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-04-15 08:00 | 2.915 | 3.3977 | 3.3977 | 3.3977 | 3.3977
2024-06-15 09:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-04-15 09:00 | 2.7741 | 3.2334 | 3.2334 | 3.2334 | 3.2334
2024-06-15 10:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-04-15 10:00 | 2.7283 | 3.1801 | 3.1801 | 3.1801 | 3.1801
2024-06-15 11:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-04-15 11:00 | 2.957 | 3.4466 | 3.4466 | 3.4466 | 3.4466
2024-06-15 12:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-04-15 12:00 | 3.7686 | 4.3926 | 4.3926 | 4.3926 | 4.3926
2024-06-15 13:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-04-15 13:00 | 3.197 | 3.7264 | 3.7264 | 3.7264 | 3.7264
2024-06-15 14:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-04-15 14:00 | 3.4714 | 4.0462 | 4.0462 | 4.0462 | 4.0462
2024-06-15 15:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-04-15 15:00 | 3.3342 | 3.8863 | 3.8863 | 3.8863 | 3.8863
2024-06-15 16:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-04-15 16:00 | 3.6543 | 4.2594 | 4.2594 | 4.2594 | 4.2594
2024-06-15 17:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-04-15 17:00 | 3.5362 | 4.1217 | 4.1217 | 4.1217 | 4.1217
2024-06-15 18:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-04-15 18:00 | 3.0979 | 3.6109 | 3.6109 | 3.6109 | 3.6109
2024-06-15 19:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-04-15 19:00 | 2.6026 | 3.0335 | 3.0335 | 3.0335 | 3.0335
2024-06-15 20:00 | 1.7338 | 1.8602 | 2.3092 | 2.429 | 2.5487 | 2024-04-15 20:00 | 2.5569 | 2.9802 | 2.9802 | 2.9802 | 2.9802
2024-06-15 21:00 | 1.7528 | 1.8807 | 2.3346 | 2.4557 | 2.5767 | 2024-04-15 21:00 | 2.2177 | 2.5849 | 2.5849 | 2.5849 | 2.5849
2024-06-15 22:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-04-15 22:00 | 1.81 | 2.1097 | 2.1097 | 2.1097 | 2.1097
2024-06-15 23:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-04-15 23:00 | 1.7376 | 2.0253 | 2.0253 | 2.0253 | 2.0253
2024-06-16 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-04-16 | 1.6309 | 1.901 | 1.901 | 1.901 | 1.901
2024-06-16 01:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-04-16 01:00 | 1.6195 | 1.8876 | 1.8876 | 1.8876 | 1.8876
2024-06-16 02:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-04-16 02:00 | 1.6385 | 1.9098 | 1.9098 | 1.9098 | 1.9098
2024-06-16 03:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-04-16 03:00 | 1.8214 | 2.123 | 2.123 | 2.123 | 2.123
2024-06-16 04:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-04-16 04:00 | 2.0805 | 2.4251 | 2.4251 | 2.4251 | 2.4251
2024-06-16 05:00 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 2024-04-16 05:00 | 2.3244 | 2.7093 | 2.7093 | 2.7093 | 2.7093
2024-06-16 06:00 | 1.7528 | 1.8807 | 2.3346 | 2.4557 | 2.5767 | 2024-04-16 06:00 | 2.4959 | 2.9092 | 2.9092 | 2.9092 | 2.9092
2024-06-16 07:00 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 2024-04-16 07:00 | 2.6674 | 3.109 | 3.109 | 3.109 | 3.109
2024-06-16 08:00 | 1.81 | 1.942 | 2.4107 | 2.5357 | 2.6607 | 2024-04-16 08:00 | 2.816 | 3.2823 | 3.2823 | 3.2823 | 3.2823
2024-06-16 09:00 | 1.4099 | 1.5127 | 1.8778 | 1.9752 | 2.0726 | 2024-04-16 09:00 | 2.9112 | 3.3933 | 3.3933 | 3.3933 | 3.3933
2024-06-16 10:00 | 1.3908 | 1.4923 | 1.8525 | 1.9485 | 2.0446 | 2024-04-16 10:00 | 2.7055 | 3.1535 | 3.1535 | 3.1535 | 3.1535
2024-06-16 11:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-04-16 11:00 | 2.7969 | 3.2601 | 3.2601 | 3.2601 | 3.2601
2024-06-16 12:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-04-16 12:00 | 3.056 | 3.5621 | 3.5621 | 3.5621 | 3.5621
2024-06-16 13:00 | 0.74305 | 0.79723 | 0.98967 | 1.041 | 1.0923 | 2024-04-16 13:00 | 3.3456 | 3.8996 | 3.8996 | 3.8996 | 3.8996
2024-06-16 14:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-04-16 14:00 | 3.2923 | 3.8374 | 3.8374 | 3.8374 | 3.8374
2024-06-16 15:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-04-16 15:00 | 3.639 | 4.2416 | 4.2416 | 4.2416 | 4.2416
2024-06-16 16:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-04-16 16:00 | 3.7114 | 4.326 | 4.326 | 4.326 | 4.326
2024-06-16 17:00 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 2024-04-16 17:00 | 3.5666 | 4.1572 | 4.1572 | 4.1572 | 4.1572
2024-06-16 18:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-04-16 18:00 | 3.2275 | 3.7619 | 3.7619 | 3.7619 | 3.7619
2024-06-16 19:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-04-16 19:00 | 2.7207 | 3.1712 | 3.1712 | 3.1712 | 3.1712
2024-06-16 20:00 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 2024-04-16 20:00 | 2.7283 | 3.1801 | 3.1801 | 3.1801 | 3.1801
2024-06-16 21:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-04-16 21:00 | 2.1567 | 2.5139 | 2.5139 | 2.5139 | 2.5139
2024-06-16 22:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-04-16 22:00 | 1.8367 | 2.1408 | 2.1408 | 2.1408 | 2.1408
2024-06-16 23:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-04-16 23:00 | 1.7757 | 2.0697 | 2.0697 | 2.0697 | 2.0697
2024-06-17 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-04-17 | 1.7338 | 2.0209 | 2.0209 | 2.0209 | 2.0209
2024-06-17 01:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-04-17 01:00 | 1.6157 | 1.8832 | 1.8832 | 1.8832 | 1.8832
2024-06-17 02:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-04-17 02:00 | 1.6042 | 1.8699 | 1.8699 | 1.8699 | 1.8699
2024-06-17 03:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-04-17 03:00 | 1.7643 | 2.0564 | 2.0564 | 2.0564 | 2.0564
2024-06-17 04:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-04-17 04:00 | 2.0577 | 2.3984 | 2.3984 | 2.3984 | 2.3984
2024-06-17 05:00 | 1.8672 | 2.0033 | 2.4869 | 2.6158 | 2.7448 | 2024-04-17 05:00 | 2.1834 | 2.545 | 2.545 | 2.545 | 2.545
2024-06-17 06:00 | 2.3625 | 2.5348 | 3.1466 | 3.3098 | 3.473 | 2024-04-17 06:00 | 2.3663 | 2.7582 | 2.7582 | 2.7582 | 2.7582
2024-06-17 07:00 | 2.7626 | 2.9641 | 3.6795 | 3.8703 | 4.0611 | 2024-04-17 07:00 | 2.8922 | 3.3711 | 3.3711 | 3.3711 | 3.3711
2024-06-17 08:00 | 2.7817 | 2.9845 | 3.7049 | 3.897 | 4.0891 | 2024-04-17 08:00 | 3.2123 | 3.7442 | 3.7442 | 3.7442 | 3.7442
2024-06-17 09:00 | 2.553 | 2.7392 | 3.4004 | 3.5767 | 3.753 | 2024-04-17 09:00 | 3.3609 | 3.9174 | 3.9174 | 3.9174 | 3.9174
2024-06-17 10:00 | 2.4387 | 2.6166 | 3.2481 | 3.4166 | 3.585 | 2024-04-17 10:00 | 3.3151 | 3.8641 | 3.8641 | 3.8641 | 3.8641
2024-06-17 11:00 | 2.0577 | 2.2077 | 2.7406 | 2.8827 | 3.0248 | 2024-04-17 11:00 | 3.3799 | 3.9396 | 3.9396 | 3.9396 | 3.9396
2024-06-17 12:00 | 2.1529 | 2.3099 | 2.8675 | 3.0162 | 3.1649 | 2024-04-17 12:00 | 3.5704 | 4.1617 | 4.1617 | 4.1617 | 4.1617
2024-06-17 13:00 | 2.2863 | 2.453 | 3.0451 | 3.203 | 3.3609 | 2024-04-17 13:00 | 3.5019 | 4.0817 | 4.0817 | 4.0817 | 4.0817
2024-06-17 14:00 | 2.0577 | 2.2077 | 2.7406 | 2.8827 | 3.0248 | 2024-04-17 14:00 | 3.3151 | 3.8641 | 3.8641 | 3.8641 | 3.8641
2024-06-17 15:00 | 2.2101 | 2.3713 | 2.9436 | 3.0963 | 3.2489 | 2024-04-17 15:00 | 3.5476 | 4.135 | 4.135 | 4.135 | 4.135
2024-06-17 16:00 | 2.2291 | 2.3917 | 2.969 | 3.123 | 3.2769 | 2024-04-17 16:00 | 3.6047 | 4.2016 | 4.2016 | 4.2016 | 4.2016
2024-06-17 17:00 | 2.3625 | 2.5348 | 3.1466 | 3.3098 | 3.473 | 2024-04-17 17:00 | 3.4447 | 4.0151 | 4.0151 | 4.0151 | 4.0151
2024-06-17 18:00 | 2.3625 | 2.5348 | 3.1466 | 3.3098 | 3.473 | 2024-04-17 18:00 | 3.2275 | 3.7619 | 3.7619 | 3.7619 | 3.7619
2024-06-17 19:00 | 1.9624 | 2.1055 | 2.6137 | 2.7493 | 2.8848 | 2024-04-17 19:00 | 2.6674 | 3.109 | 3.109 | 3.109 | 3.109
2024-06-17 20:00 | 1.7909 | 1.9215 | 2.3854 | 2.509 | 2.6327 | 2024-04-17 20:00 | 2.4692 | 2.8781 | 2.8781 | 2.8781 | 2.8781
2024-06-17 21:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-04-17 21:00 | 2.3358 | 2.7226 | 2.7226 | 2.7226 | 2.7226
2024-06-17 22:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-04-17 22:00 | 1.81 | 2.1097 | 2.1097 | 2.1097 | 2.1097
2024-06-17 23:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-04-17 23:00 | 1.7566 | 2.0475 | 2.0475 | 2.0475 | 2.0475
2024-06-18 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-04-18 | 1.5776 | 1.8388 | 1.8388 | 1.8388 | 1.8388
2024-06-18 01:00 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 2024-04-18 01:00 | 1.6461 | 1.9187 | 1.9187 | 1.9187 | 1.9187
2024-06-18 02:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-04-18 02:00 | 1.5852 | 1.8477 | 1.8477 | 1.8477 | 1.8477
2024-06-18 03:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-04-18 03:00 | 1.669 | 1.9454 | 1.9454 | 1.9454 | 1.9454
2024-06-18 04:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-04-18 04:00 | 2.0081 | 2.3407 | 2.3407 | 2.3407 | 2.3407
2024-06-18 05:00 | 1.8481 | 1.9829 | 2.4615 | 2.5891 | 2.7167 | 2024-04-18 05:00 | 2.3168 | 2.7004 | 2.7004 | 2.7004 | 2.7004
2024-06-18 06:00 | 2.4197 | 2.5961 | 3.2228 | 3.3899 | 3.557 | 2024-04-18 06:00 | 2.3435 | 2.7315 | 2.7315 | 2.7315 | 2.7315
2024-06-18 07:00 | 2.8388 | 3.0458 | 3.781 | 3.9771 | 4.1731 | 2024-04-18 07:00 | 2.8312 | 3.3 | 3.3 | 3.3 | 3.3
2024-06-18 08:00 | 2.7245 | 2.9232 | 3.6288 | 3.8169 | 4.0051 | 2024-04-18 08:00 | 3.2313 | 3.7664 | 3.7664 | 3.7664 | 3.7664
2024-06-18 09:00 | 2.534 | 2.7188 | 3.375 | 3.55 | 3.725 | 2024-04-18 09:00 | 3.117 | 3.6331 | 3.6331 | 3.6331 | 3.6331
2024-06-18 10:00 | 2.2863 | 2.453 | 3.0451 | 3.203 | 3.3609 | 2024-04-18 10:00 | 3.6543 | 4.2594 | 4.2594 | 4.2594 | 4.2594
2024-06-18 11:00 | 2.2101 | 2.3713 | 2.9436 | 3.0963 | 3.2489 | 2024-04-18 11:00 | 3.4447 | 4.0151 | 4.0151 | 4.0151 | 4.0151
2024-06-18 12:00 | 2.191 | 2.3508 | 2.9183 | 3.0696 | 3.2209 | 2024-04-18 12:00 | 3.3952 | 3.9574 | 3.9574 | 3.9574 | 3.9574
2024-06-18 13:00 | 2.2291 | 2.3917 | 2.969 | 3.123 | 3.2769 | 2024-04-18 13:00 | 3.2504 | 3.7886 | 3.7886 | 3.7886 | 3.7886
2024-06-18 14:00 | 2.1339 | 2.2895 | 2.8421 | 2.9895 | 3.1369 | 2024-04-18 14:00 | 3.2885 | 3.833 | 3.833 | 3.833 | 3.833
2024-06-18 15:00 | 2.2673 | 2.4326 | 3.0198 | 3.1763 | 3.3329 | 2024-04-18 15:00 | 3.3266 | 3.8774 | 3.8774 | 3.8774 | 3.8774
2024-06-18 16:00 | 2.2482 | 2.4121 | 2.9944 | 3.1496 | 3.3049 | 2024-04-18 16:00 | 3.5933 | 4.1883 | 4.1883 | 4.1883 | 4.1883
2024-06-18 17:00 | 2.2863 | 2.453 | 3.0451 | 3.203 | 3.3609 | 2024-04-18 17:00 | 3.4676 | 4.0418 | 4.0418 | 4.0418 | 4.0418
2024-06-18 18:00 | 2.3435 | 2.5144 | 3.1213 | 3.2831 | 3.4449 | 2024-04-18 18:00 | 3.1094 | 3.6243 | 3.6243 | 3.6243 | 3.6243
2024-06-18 19:00 | 1.8481 | 1.9829 | 2.4615 | 2.5891 | 2.7167 | 2024-04-18 19:00 | 2.5416 | 2.9625 | 2.9625 | 2.9625 | 2.9625
2024-06-18 20:00 | 1.8481 | 1.9829 | 2.4615 | 2.5891 | 2.7167 | 2024-04-18 20:00 | 2.4616 | 2.8692 | 2.8692 | 2.8692 | 2.8692
2024-06-18 21:00 | 1.7338 | 1.8602 | 2.3092 | 2.429 | 2.5487 | 2024-04-18 21:00 | 2.2291 | 2.5983 | 2.5983 | 2.5983 | 2.5983
2024-06-18 22:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-04-18 22:00 | 1.7681 | 2.0609 | 2.0609 | 2.0609 | 2.0609
2024-06-18 23:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-04-18 23:00 | 1.8481 | 2.1541 | 2.1541 | 2.1541 | 2.1541
2024-06-19 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-04-19 | 1.6576 | 1.932 | 1.932 | 1.932 | 1.932
2024-06-19 01:00 | 1.7338 | 1.8602 | 2.3092 | 2.429 | 2.5487 | 2024-04-19 01:00 | 1.6195 | 1.8876 | 1.8876 | 1.8876 | 1.8876
2024-06-19 02:00 | 1.81 | 1.942 | 2.4107 | 2.5357 | 2.6607 | 2024-04-19 02:00 | 1.6157 | 1.8832 | 1.8832 | 1.8832 | 1.8832
2024-06-19 03:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-04-19 03:00 | 1.8024 | 2.1008 | 2.1008 | 2.1008 | 2.1008
2024-06-19 04:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-04-19 04:00 | 2.0196 | 2.354 | 2.354 | 2.354 | 2.354
2024-06-19 05:00 | 2.0196 | 2.1668 | 2.6899 | 2.8293 | 2.9688 | 2024-04-19 05:00 | 2.2558 | 2.6294 | 2.6294 | 2.6294 | 2.6294
2024-06-19 06:00 | 2.3816 | 2.5552 | 3.172 | 3.3365 | 3.501 | 2024-04-19 06:00 | 2.4578 | 2.8648 | 2.8648 | 2.8648 | 2.8648
2024-06-19 07:00 | 2.8388 | 3.0458 | 3.781 | 3.9771 | 4.1731 | 2024-04-19 07:00 | 2.9798 | 3.4732 | 3.4732 | 3.4732 | 3.4732
2024-06-19 08:00 | 2.8579 | 3.0663 | 3.8064 | 4.0038 | 4.2012 | 2024-04-19 08:00 | 3.2275 | 3.7619 | 3.7619 | 3.7619 | 3.7619
2024-06-19 09:00 | 2.8388 | 3.0458 | 3.781 | 3.9771 | 4.1731 | 2024-04-19 09:00 | 3.3761 | 3.9352 | 3.9352 | 3.9352 | 3.9352
2024-06-19 10:00 | 2.5721 | 2.7597 | 3.4258 | 3.6034 | 3.781 | 2024-04-19 10:00 | 2.915 | 3.3977 | 3.3977 | 3.3977 | 3.3977
2024-06-19 11:00 | 2.2482 | 2.4121 | 2.9944 | 3.1496 | 3.3049 | 2024-04-19 11:00 | 2.9265 | 3.4111 | 3.4111 | 3.4111 | 3.4111
2024-06-19 12:00 | 2.2673 | 2.4326 | 3.0198 | 3.1763 | 3.3329 | 2024-04-19 12:00 | 3.6238 | 4.2239 | 4.2239 | 4.2239 | 4.2239
2024-06-19 13:00 | 2.172 | 2.3304 | 2.8929 | 3.0429 | 3.1929 | 2024-04-19 13:00 | 3.7267 | 4.3438 | 4.3438 | 4.3438 | 4.3438
2024-06-19 14:00 | 2.1529 | 2.3099 | 2.8675 | 3.0162 | 3.1649 | 2024-04-19 14:00 | 3.6505 | 4.2549 | 4.2549 | 4.2549 | 4.2549
2024-06-19 15:00 | 2.2482 | 2.4121 | 2.9944 | 3.1496 | 3.3049 | 2024-04-19 15:00 | 3.7762 | 4.4015 | 4.4015 | 4.4015 | 4.4015
2024-06-19 16:00 | 2.2482 | 2.4121 | 2.9944 | 3.1496 | 3.3049 | 2024-04-19 16:00 | 3.7 | 4.3127 | 4.3127 | 4.3127 | 4.3127
2024-06-19 17:00 | 2.3244 | 2.4939 | 3.0959 | 3.2564 | 3.4169 | 2024-04-19 17:00 | 3.6276 | 4.2283 | 4.2283 | 4.2283 | 4.2283
2024-06-19 18:00 | 2.2863 | 2.453 | 3.0451 | 3.203 | 3.3609 | 2024-04-19 18:00 | 3.4218 | 3.9885 | 3.9885 | 3.9885 | 3.9885
2024-06-19 19:00 | 1.9434 | 2.0851 | 2.5884 | 2.7226 | 2.8568 | 2024-04-19 19:00 | 2.9836 | 3.4777 | 3.4777 | 3.4777 | 3.4777
2024-06-19 20:00 | 1.7338 | 1.8602 | 2.3092 | 2.429 | 2.5487 | 2024-04-19 20:00 | 2.6331 | 3.0691 | 3.0691 | 3.0691 | 3.0691
2024-06-19 21:00 | 1.7338 | 1.8602 | 2.3092 | 2.429 | 2.5487 | 2024-04-19 21:00 | 2.3206 | 2.7049 | 2.7049 | 2.7049 | 2.7049
2024-06-19 22:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-04-19 22:00 | 1.8405 | 2.1452 | 2.1452 | 2.1452 | 2.1452
2024-06-19 23:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-04-19 23:00 | 1.7871 | 2.0831 | 2.0831 | 2.0831 | 2.0831
2024-06-20 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-04-20 | 1.7033 | 1.9853 | 1.9853 | 1.9853 | 1.9853
2024-06-20 01:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-04-20 01:00 | 1.65 | 1.9232 | 1.9232 | 1.9232 | 1.9232
2024-06-20 02:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-04-20 02:00 | 1.6347 | 1.9054 | 1.9054 | 1.9054 | 1.9054
2024-06-20 03:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-04-20 03:00 | 1.7719 | 2.0653 | 2.0653 | 2.0653 | 2.0653
2024-06-20 04:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-04-20 04:00 | 1.8976 | 2.2119 | 2.2119 | 2.2119 | 2.2119
2024-06-20 05:00 | 1.8481 | 1.9829 | 2.4615 | 2.5891 | 2.7167 | 2024-04-20 05:00 | 2.2101 | 2.5761 | 2.5761 | 2.5761 | 2.5761
2024-06-20 06:00 | 2.191 | 2.3508 | 2.9183 | 3.0696 | 3.2209 | 2024-04-20 06:00 | 2.3739 | 2.767 | 2.767 | 2.767 | 2.767
2024-06-20 07:00 | 2.6293 | 2.821 | 3.5019 | 3.6835 | 3.8651 | 2024-04-20 07:00 | 2.1987 | 2.5627 | 2.5627 | 2.5627 | 2.5627
2024-06-20 08:00 | 2.6483 | 2.8414 | 3.5273 | 3.7102 | 3.8931 | 2024-04-20 08:00 | 2.5645 | 2.9891 | 2.9891 | 2.9891 | 2.9891
2024-06-20 09:00 | 2.5721 | 2.7597 | 3.4258 | 3.6034 | 3.781 | 2024-04-20 09:00 | 2.6369 | 3.0735 | 3.0735 | 3.0735 | 3.0735
2024-06-20 10:00 | 2.4197 | 2.5961 | 3.2228 | 3.3899 | 3.557 | 2024-04-20 10:00 | 2.9379 | 3.4244 | 3.4244 | 3.4244 | 3.4244
2024-06-20 11:00 | 2.2482 | 2.4121 | 2.9944 | 3.1496 | 3.3049 | 2024-04-20 11:00 | 3.0751 | 3.5843 | 3.5843 | 3.5843 | 3.5843
2024-06-20 12:00 | 1.9243 | 2.0646 | 2.563 | 2.6959 | 2.8288 | 2024-04-20 12:00 | 3.2123 | 3.7442 | 3.7442 | 3.7442 | 3.7442
2024-06-20 13:00 | 2.191 | 2.3508 | 2.9183 | 3.0696 | 3.2209 | 2024-04-20 13:00 | 2.9798 | 3.4732 | 3.4732 | 3.4732 | 3.4732
2024-06-20 14:00 | 2.1339 | 2.2895 | 2.8421 | 2.9895 | 3.1369 | 2024-04-20 14:00 | 3.117 | 3.6331 | 3.6331 | 3.6331 | 3.6331
2024-06-20 15:00 | 2.3816 | 2.5552 | 3.172 | 3.3365 | 3.501 | 2024-04-20 15:00 | 2.9303 | 3.4155 | 3.4155 | 3.4155 | 3.4155
2024-06-20 16:00 | 2.3435 | 2.5144 | 3.1213 | 3.2831 | 3.4449 | 2024-04-20 16:00 | 3.0484 | 3.5532 | 3.5532 | 3.5532 | 3.5532
2024-06-20 17:00 | 2.3625 | 2.5348 | 3.1466 | 3.3098 | 3.473 | 2024-04-20 17:00 | 2.9874 | 3.4821 | 3.4821 | 3.4821 | 3.4821
2024-06-20 18:00 | 2.4006 | 2.5757 | 3.1974 | 3.3632 | 3.529 | 2024-04-20 18:00 | 2.6102 | 3.0424 | 3.0424 | 3.0424 | 3.0424
2024-06-20 19:00 | 1.8862 | 2.0237 | 2.5122 | 2.6425 | 2.7728 | 2024-04-20 19:00 | 2.3854 | 2.7804 | 2.7804 | 2.7804 | 2.7804
2024-06-20 20:00 | 1.7528 | 1.8807 | 2.3346 | 2.4557 | 2.5767 | 2024-04-20 20:00 | 2.0767 | 2.4206 | 2.4206 | 2.4206 | 2.4206
2024-06-20 21:00 | 1.7528 | 1.8807 | 2.3346 | 2.4557 | 2.5767 | 2024-04-20 21:00 | 2.0158 | 2.3495 | 2.3495 | 2.3495 | 2.3495
2024-06-20 22:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-04-20 22:00 | 2.0386 | 2.3762 | 2.3762 | 2.3762 | 2.3762
2024-06-20 23:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-04-20 23:00 | 1.6614 | 1.9365 | 1.9365 | 1.9365 | 1.9365
2024-06-21 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-04-21 | 1.6652 | 1.9409 | 1.9409 | 1.9409 | 1.9409
2024-06-21 01:00 | 1.448 | 1.5536 | 1.9286 | 2.0286 | 2.1286 | 2024-04-21 01:00 | 1.6309 | 1.901 | 1.901 | 1.901 | 1.901
2024-06-21 02:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-04-21 02:00 | 1.608 | 1.8743 | 1.8743 | 1.8743 | 1.8743
2024-06-21 03:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-04-21 03:00 | 1.749 | 2.0386 | 2.0386 | 2.0386 | 2.0386
2024-06-21 04:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-04-21 04:00 | 1.9243 | 2.243 | 2.243 | 2.243 | 2.243
2024-06-21 05:00 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 2024-04-21 05:00 | 2.1491 | 2.505 | 2.505 | 2.505 | 2.505
2024-06-21 06:00 | 1.9624 | 2.1055 | 2.6137 | 2.7493 | 2.8848 | 2024-04-21 06:00 | 2.5302 | 2.9491 | 2.9491 | 2.9491 | 2.9491
2024-06-21 07:00 | 2.6674 | 2.8619 | 3.5527 | 3.7369 | 3.9211 | 2024-04-21 07:00 | 2.4159 | 2.8159 | 2.8159 | 2.8159 | 2.8159
2024-06-21 08:00 | 2.4578 | 2.637 | 3.2735 | 3.4433 | 3.613 | 2024-04-21 08:00 | 2.3206 | 2.7049 | 2.7049 | 2.7049 | 2.7049
2024-06-21 09:00 | 2.4959 | 2.6779 | 3.3243 | 3.4966 | 3.669 | 2024-04-21 09:00 | 2.3435 | 2.7315 | 2.7315 | 2.7315 | 2.7315
2024-06-21 10:00 | 2.4197 | 2.5961 | 3.2228 | 3.3899 | 3.557 | 2024-04-21 10:00 | 2.4311 | 2.8337 | 2.8337 | 2.8337 | 2.8337
2024-06-21 11:00 | 2.3244 | 2.4939 | 3.0959 | 3.2564 | 3.4169 | 2024-04-21 11:00 | 2.473 | 2.8825 | 2.8825 | 2.8825 | 2.8825
2024-06-21 12:00 | 2.0958 | 2.2486 | 2.7914 | 2.9361 | 3.0808 | 2024-04-21 12:00 | 2.614 | 3.0469 | 3.0469 | 3.0469 | 3.0469
2024-06-21 13:00 | 2.3054 | 2.4735 | 3.0705 | 3.2297 | 3.3889 | 2024-04-21 13:00 | 2.4883 | 2.9003 | 2.9003 | 2.9003 | 2.9003
2024-06-21 14:00 | 2.2673 | 2.4326 | 3.0198 | 3.1763 | 3.3329 | 2024-04-21 14:00 | 2.5911 | 3.0202 | 3.0202 | 3.0202 | 3.0202
2024-06-21 15:00 | 2.0005 | 2.1464 | 2.6645 | 2.8026 | 2.9408 | 2024-04-21 15:00 | 2.9265 | 3.4111 | 3.4111 | 3.4111 | 3.4111
2024-06-21 16:00 | 2.191 | 2.3508 | 2.9183 | 3.0696 | 3.2209 | 2024-04-21 16:00 | 2.896 | 3.3755 | 3.3755 | 3.3755 | 3.3755
2024-06-21 17:00 | 2.2482 | 2.4121 | 2.9944 | 3.1496 | 3.3049 | 2024-04-21 17:00 | 2.8426 | 3.3133 | 3.3133 | 3.3133 | 3.3133
2024-06-21 18:00 | 2.172 | 2.3304 | 2.8929 | 3.0429 | 3.1929 | 2024-04-21 18:00 | 2.6826 | 3.1268 | 3.1268 | 3.1268 | 3.1268
2024-06-21 19:00 | 1.8672 | 2.0033 | 2.4869 | 2.6158 | 2.7448 | 2024-04-21 19:00 | 2.2406 | 2.6116 | 2.6116 | 2.6116 | 2.6116
2024-06-21 20:00 | 1.7338 | 1.8602 | 2.3092 | 2.429 | 2.5487 | 2024-04-21 20:00 | 2.0805 | 2.4251 | 2.4251 | 2.4251 | 2.4251
2024-06-21 21:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-04-21 21:00 | 2.0043 | 2.3362 | 2.3362 | 2.3362 | 2.3362
2024-06-21 22:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-04-21 22:00 | 1.7033 | 1.9853 | 1.9853 | 1.9853 | 1.9853
2024-06-21 23:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-04-21 23:00 | 1.6576 | 1.932 | 1.932 | 1.932 | 1.932
2024-06-22 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-04-22 | 1.6385 | 1.9098 | 1.9098 | 1.9098 | 1.9098
2024-06-22 01:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-04-22 01:00 | 1.5623 | 1.821 | 1.821 | 1.821 | 1.821
2024-06-22 02:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-04-22 02:00 | 1.6157 | 1.8832 | 1.8832 | 1.8832 | 1.8832
2024-06-22 03:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-04-22 03:00 | 1.7757 | 2.0697 | 2.0697 | 2.0697 | 2.0697
2024-06-22 04:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-04-22 04:00 | 1.9586 | 2.2829 | 2.2829 | 2.2829 | 2.2829
2024-06-22 05:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-04-22 05:00 | 2.2101 | 2.5761 | 2.5761 | 2.5761 | 2.5761
2024-06-22 06:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-04-22 06:00 | 2.4578 | 2.8648 | 2.8648 | 2.8648 | 2.8648
2024-06-22 07:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-04-22 07:00 | 2.835 | 3.3045 | 3.3045 | 3.3045 | 3.3045
2024-06-22 08:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-04-22 08:00 | 3.2237 | 3.7575 | 3.7575 | 3.7575 | 3.7575
2024-06-22 09:00 | 1.1622 | 1.247 | 1.5479 | 1.6282 | 1.7085 | 2024-04-22 09:00 | 3.3875 | 3.9485 | 3.9485 | 3.9485 | 3.9485
2024-06-22 10:00 | 1.105 | 1.1856 | 1.4718 | 1.5481 | 1.6244 | 2024-04-22 10:00 | 2.8007 | 3.2645 | 3.2645 | 3.2645 | 3.2645
2024-06-22 11:00 | 0.97168 | 1.0425 | 1.2942 | 1.3613 | 1.4284 | 2024-04-22 11:00 | 2.9036 | 3.3844 | 3.3844 | 3.3844 | 3.3844
2024-06-22 12:00 | 1.2765 | 1.3696 | 1.7002 | 1.7884 | 1.8765 | 2024-04-22 12:00 | 3.1399 | 3.6598 | 3.6598 | 3.6598 | 3.6598
2024-06-22 13:00 | 1.3146 | 1.4105 | 1.751 | 1.8417 | 1.9325 | 2024-04-22 13:00 | 3.3723 | 3.9307 | 3.9307 | 3.9307 | 3.9307
2024-06-22 14:00 | 1.3527 | 1.4514 | 1.8017 | 1.8951 | 1.9885 | 2024-04-22 14:00 | 3.2809 | 3.8241 | 3.8241 | 3.8241 | 3.8241
2024-06-22 15:00 | 1.4289 | 1.5331 | 1.9032 | 2.0019 | 2.1006 | 2024-04-22 15:00 | 3.62 | 4.2194 | 4.2194 | 4.2194 | 4.2194
2024-06-22 16:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-04-22 16:00 | 3.7953 | 4.4237 | 4.4237 | 4.4237 | 4.4237
2024-06-22 17:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-04-22 17:00 | 3.2542 | 3.793 | 3.793 | 3.793 | 3.793
2024-06-22 18:00 | 1.829 | 1.9624 | 2.4361 | 2.5624 | 2.6887 | 2024-04-22 18:00 | 3.0294 | 3.531 | 3.531 | 3.531 | 3.531
2024-06-22 19:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-04-22 19:00 | 2.6559 | 3.0957 | 3.0957 | 3.0957 | 3.0957
2024-06-22 20:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-04-22 20:00 | 2.4159 | 2.8159 | 2.8159 | 2.8159 | 2.8159
2024-06-22 21:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-04-22 21:00 | 2.1529 | 2.5094 | 2.5094 | 2.5094 | 2.5094
2024-06-22 22:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-04-22 22:00 | 1.8176 | 2.1186 | 2.1186 | 2.1186 | 2.1186
2024-06-22 23:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-04-22 23:00 | 1.8024 | 2.1008 | 2.1008 | 2.1008 | 2.1008
2024-06-23 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-04-23 | 1.7185 | 2.0031 | 2.0031 | 2.0031 | 2.0031
2024-06-23 01:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-04-23 01:00 | 1.6538 | 1.9276 | 1.9276 | 1.9276 | 1.9276
2024-06-23 02:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-04-23 02:00 | 1.6233 | 1.8921 | 1.8921 | 1.8921 | 1.8921
2024-06-23 03:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-04-23 03:00 | 1.7185 | 2.0031 | 2.0031 | 2.0031 | 2.0031
2024-06-23 04:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-04-23 04:00 | 1.9929 | 2.3229 | 2.3229 | 2.3229 | 2.3229
2024-06-23 05:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-04-23 05:00 | 2.1949 | 2.5583 | 2.5583 | 2.5583 | 2.5583
2024-06-23 06:00 | 1.7719 | 1.9011 | 2.36 | 2.4823 | 2.6047 | 2024-04-23 06:00 | 2.5835 | 3.0113 | 3.0113 | 3.0113 | 3.0113
2024-06-23 07:00 | 1.7909 | 1.9215 | 2.3854 | 2.509 | 2.6327 | 2024-04-23 07:00 | 2.9608 | 3.451 | 3.451 | 3.451 | 3.451
2024-06-23 08:00 | 1.829 | 1.9624 | 2.4361 | 2.5624 | 2.6887 | 2024-04-23 08:00 | 2.8731 | 3.3489 | 3.3489 | 3.3489 | 3.3489
2024-06-23 09:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-04-23 09:00 | 2.9531 | 3.4422 | 3.4422 | 3.4422 | 3.4422
2024-06-23 10:00 | 1.3146 | 1.4105 | 1.751 | 1.8417 | 1.9325 | 2024-04-23 10:00 | 2.7207 | 3.1712 | 3.1712 | 3.1712 | 3.1712
2024-06-23 11:00 | 1.3146 | 1.4105 | 1.751 | 1.8417 | 1.9325 | 2024-04-23 11:00 | 2.8807 | 3.3578 | 3.3578 | 3.3578 | 3.3578
2024-06-23 12:00 | 1.2956 | 1.39 | 1.7256 | 1.815 | 1.9045 | 2024-04-23 12:00 | 3.3456 | 3.8996 | 3.8996 | 3.8996 | 3.8996
2024-06-23 13:00 | 1.2575 | 1.3492 | 1.6748 | 1.7617 | 1.8485 | 2024-04-23 13:00 | 3.0751 | 3.5843 | 3.5843 | 3.5843 | 3.5843
2024-06-23 14:00 | 1.2765 | 1.3696 | 1.7002 | 1.7884 | 1.8765 | 2024-04-23 14:00 | 3.1513 | 3.6731 | 3.6731 | 3.6731 | 3.6731
2024-06-23 15:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-04-23 15:00 | 3.2123 | 3.7442 | 3.7442 | 3.7442 | 3.7442
2024-06-23 16:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-04-23 16:00 | 3.7953 | 4.4237 | 4.4237 | 4.4237 | 4.4237
2024-06-23 17:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-04-23 17:00 | 3.5133 | 4.0951 | 4.0951 | 4.0951 | 4.0951
2024-06-23 18:00 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 2024-04-23 18:00 | 3.3037 | 3.8508 | 3.8508 | 3.8508 | 3.8508
2024-06-23 19:00 | 1.7528 | 1.8807 | 2.3346 | 2.4557 | 2.5767 | 2024-04-23 19:00 | 2.5454 | 2.9669 | 2.9669 | 2.9669 | 2.9669
2024-06-23 20:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-04-23 20:00 | 2.4463 | 2.8514 | 2.8514 | 2.8514 | 2.8514
2024-06-23 21:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-04-23 21:00 | 2.2596 | 2.6338 | 2.6338 | 2.6338 | 2.6338
2024-06-23 22:00 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 2024-04-23 22:00 | 1.8862 | 2.1985 | 2.1985 | 2.1985 | 2.1985
2024-06-23 23:00 | 1.7909 | 1.9215 | 2.3854 | 2.509 | 2.6327 | 2024-04-23 23:00 | 1.749 | 2.0386 | 2.0386 | 2.0386 | 2.0386
2024-06-24 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-04-24 | 1.6766 | 1.9543 | 1.9543 | 1.9543 | 1.9543
2024-06-24 01:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-04-24 01:00 | 1.6271 | 1.8965 | 1.8965 | 1.8965 | 1.8965
2024-06-24 02:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-04-24 02:00 | 1.6042 | 1.8699 | 1.8699 | 1.8699 | 1.8699
2024-06-24 03:00 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 2024-04-24 03:00 | 1.7605 | 2.052 | 2.052 | 2.052 | 2.052
2024-06-24 04:00 | 1.7338 | 1.8602 | 2.3092 | 2.429 | 2.5487 | 2024-04-24 04:00 | 2.0272 | 2.3629 | 2.3629 | 2.3629 | 2.3629
2024-06-24 05:00 | 1.9624 | 2.1055 | 2.6137 | 2.7493 | 2.8848 | 2024-04-24 05:00 | 2.2253 | 2.5938 | 2.5938 | 2.5938 | 2.5938
2024-06-24 06:00 | 2.2291 | 2.3917 | 2.969 | 3.123 | 3.2769 | 2024-04-24 06:00 | 2.5149 | 2.9314 | 2.9314 | 2.9314 | 2.9314
2024-06-24 07:00 | 2.7626 | 2.9641 | 3.6795 | 3.8703 | 4.0611 | 2024-04-24 07:00 | 2.8007 | 3.2645 | 3.2645 | 3.2645 | 3.2645
2024-06-24 08:00 | 2.7817 | 2.9845 | 3.7049 | 3.897 | 4.0891 | 2024-04-24 08:00 | 3.5476 | 4.135 | 4.135 | 4.135 | 4.135
2024-06-24 09:00 | 2.534 | 2.7188 | 3.375 | 3.55 | 3.725 | 2024-04-24 09:00 | 3.4066 | 3.9707 | 3.9707 | 3.9707 | 3.9707
2024-06-24 10:00 | 2.2673 | 2.4326 | 3.0198 | 3.1763 | 3.3329 | 2024-04-24 10:00 | 3.5933 | 4.1883 | 4.1883 | 4.1883 | 4.1883
2024-06-24 11:00 | 2.4768 | 2.6574 | 3.2989 | 3.4699 | 3.641 | 2024-04-24 11:00 | 3.3304 | 3.8819 | 3.8819 | 3.8819 | 3.8819
2024-06-24 12:00 | 2.0577 | 2.2077 | 2.7406 | 2.8827 | 3.0248 | 2024-04-24 12:00 | 2.9189 | 3.4022 | 3.4022 | 3.4022 | 3.4022
2024-06-24 13:00 | 2.3244 | 2.4939 | 3.0959 | 3.2564 | 3.4169 | 2024-04-24 13:00 | 3.0065 | 3.5043 | 3.5043 | 3.5043 | 3.5043
2024-06-24 14:00 | 2.3054 | 2.4735 | 3.0705 | 3.2297 | 3.3889 | 2024-04-24 14:00 | 3.2732 | 3.8152 | 3.8152 | 3.8152 | 3.8152
2024-06-24 15:00 | 2.2673 | 2.4326 | 3.0198 | 3.1763 | 3.3329 | 2024-04-24 15:00 | 3.3151 | 3.8641 | 3.8641 | 3.8641 | 3.8641
2024-06-24 16:00 | 2.2673 | 2.4326 | 3.0198 | 3.1763 | 3.3329 | 2024-04-24 16:00 | 3.5971 | 4.1928 | 4.1928 | 4.1928 | 4.1928
2024-06-24 17:00 | 2.2863 | 2.453 | 3.0451 | 3.203 | 3.3609 | 2024-04-24 17:00 | 3.5552 | 4.1439 | 4.1439 | 4.1439 | 4.1439
2024-06-24 18:00 | 2.2673 | 2.4326 | 3.0198 | 3.1763 | 3.3329 | 2024-04-24 18:00 | 3.1284 | 3.6465 | 3.6465 | 3.6465 | 3.6465
2024-06-24 19:00 | 1.9243 | 2.0646 | 2.563 | 2.6959 | 2.8288 | 2024-04-24 19:00 | 2.6902 | 3.1357 | 3.1357 | 3.1357 | 3.1357
2024-06-24 20:00 | 1.7338 | 1.8602 | 2.3092 | 2.429 | 2.5487 | 2024-04-24 20:00 | 2.5378 | 2.958 | 2.958 | 2.958 | 2.958
2024-06-24 21:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-04-24 21:00 | 2.3549 | 2.7448 | 2.7448 | 2.7448 | 2.7448
2024-06-24 22:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-04-24 22:00 | 1.9129 | 2.2296 | 2.2296 | 2.2296 | 2.2296
2024-06-24 23:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-04-24 23:00 | 1.89 | 2.203 | 2.203 | 2.203 | 2.203
2024-06-25 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-04-25 | 1.5776 | 1.8388 | 1.8388 | 1.8388 | 1.8388
2024-06-25 01:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-04-25 01:00 | 1.5852 | 1.8477 | 1.8477 | 1.8477 | 1.8477
2024-06-25 02:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-04-25 02:00 | 1.6957 | 1.9765 | 1.9765 | 1.9765 | 1.9765
2024-06-25 03:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-04-25 03:00 | 1.6423 | 1.9143 | 1.9143 | 1.9143 | 1.9143
2024-06-25 04:00 | 1.3527 | 1.4514 | 1.8017 | 1.8951 | 1.9885 | 2024-04-25 04:00 | 1.7948 | 2.0919 | 2.0919 | 2.0919 | 2.0919
2024-06-25 05:00 | 1.1432 | 1.2265 | 1.5226 | 1.6015 | 1.6805 | 2024-04-25 05:00 | 1.9891 | 2.3185 | 2.3185 | 2.3185 | 2.3185
2024-06-25 06:00 | 2.3244 | 2.4939 | 3.0959 | 3.2564 | 3.4169 | 2024-04-25 06:00 | 2.2139 | 2.5805 | 2.5805 | 2.5805 | 2.5805
2024-06-25 07:00 | 2.8007 | 3.005 | 3.7303 | 3.9237 | 4.1171 | 2024-04-25 07:00 | 2.0691 | 2.4117 | 2.4117 | 2.4117 | 2.4117
2024-06-25 08:00 | 2.8198 | 3.0254 | 3.7557 | 3.9504 | 4.1451 | 2024-04-25 08:00 | 1.9357 | 2.2563 | 2.2563 | 2.2563 | 2.2563
2024-06-25 09:00 | 2.5149 | 2.6983 | 3.3496 | 3.5233 | 3.697 | 2024-04-25 09:00 | 1.7605 | 2.052 | 2.052 | 2.052 | 2.052
2024-06-25 10:00 | 2.4197 | 2.5961 | 3.2228 | 3.3899 | 3.557 | 2024-04-25 10:00 | 2.1377 | 2.4917 | 2.4917 | 2.4917 | 2.4917
2024-06-25 11:00 | 2.3625 | 2.5348 | 3.1466 | 3.3098 | 3.473 | 2024-04-25 11:00 | 2.233 | 2.6027 | 2.6027 | 2.6027 | 2.6027
2024-06-25 12:00 | 2.1529 | 2.3099 | 2.8675 | 3.0162 | 3.1649 | 2024-04-25 12:00 | 2.233 | 2.6027 | 2.6027 | 2.6027 | 2.6027
2024-06-25 13:00 | 2.2673 | 2.4326 | 3.0198 | 3.1763 | 3.3329 | 2024-04-25 13:00 | 2.1872 | 2.5494 | 2.5494 | 2.5494 | 2.5494
2024-06-25 14:00 | 2.2673 | 2.4326 | 3.0198 | 3.1763 | 3.3329 | 2024-04-25 14:00 | 2.5759 | 3.0024 | 3.0024 | 3.0024 | 3.0024
2024-06-25 15:00 | 2.2101 | 2.3713 | 2.9436 | 3.0963 | 3.2489 | 2024-04-25 15:00 | 2.6712 | 3.1135 | 3.1135 | 3.1135 | 3.1135
2024-06-25 16:00 | 2.172 | 2.3304 | 2.8929 | 3.0429 | 3.1929 | 2024-04-25 16:00 | 2.8579 | 3.3311 | 3.3311 | 3.3311 | 3.3311
2024-06-25 17:00 | 2.4387 | 2.6166 | 3.2481 | 3.4166 | 3.585 | 2024-04-25 17:00 | 2.8693 | 3.3444 | 3.3444 | 3.3444 | 3.3444
2024-06-25 18:00 | 2.2101 | 2.3713 | 2.9436 | 3.0963 | 3.2489 | 2024-04-25 18:00 | 2.7017 | 3.149 | 3.149 | 3.149 | 3.149
2024-06-25 19:00 | 1.8862 | 2.0237 | 2.5122 | 2.6425 | 2.7728 | 2024-04-25 19:00 | 2.1834 | 2.545 | 2.545 | 2.545 | 2.545
2024-06-25 20:00 | 1.7719 | 1.9011 | 2.36 | 2.4823 | 2.6047 | 2024-04-25 20:00 | 2.2291 | 2.5983 | 2.5983 | 2.5983 | 2.5983
2024-06-25 21:00 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 2024-04-25 21:00 | 2.0348 | 2.3718 | 2.3718 | 2.3718 | 2.3718
2024-06-25 22:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-04-25 22:00 | 1.7681 | 2.0609 | 2.0609 | 2.0609 | 2.0609
2024-06-25 23:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-04-25 23:00 | 1.7071 | 1.9898 | 1.9898 | 1.9898 | 1.9898
2024-06-26 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-04-26 | 1.6157 | 1.8832 | 1.8832 | 1.8832 | 1.8832
2024-06-26 01:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-04-26 01:00 | 1.5966 | 1.861 | 1.861 | 1.861 | 1.861
2024-06-26 02:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-04-26 02:00 | 1.6042 | 1.8699 | 1.8699 | 1.8699 | 1.8699
2024-06-26 03:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-04-26 03:00 | 1.8176 | 2.1186 | 2.1186 | 2.1186 | 2.1186
2024-06-26 04:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-04-26 04:00 | 2.0196 | 2.354 | 2.354 | 2.354 | 2.354
2024-06-26 05:00 | 1.7909 | 1.9215 | 2.3854 | 2.509 | 2.6327 | 2024-04-26 05:00 | 2.3054 | 2.6871 | 2.6871 | 2.6871 | 2.6871
2024-06-26 06:00 | 2.2863 | 2.453 | 3.0451 | 3.203 | 3.3609 | 2024-04-26 06:00 | 2.4959 | 2.9092 | 2.9092 | 2.9092 | 2.9092
2024-06-26 07:00 | 2.534 | 2.7188 | 3.375 | 3.55 | 3.725 | 2024-04-26 07:00 | 2.8579 | 3.3311 | 3.3311 | 3.3311 | 3.3311
2024-06-26 08:00 | 2.5911 | 2.7801 | 3.4512 | 3.6301 | 3.809 | 2024-04-26 08:00 | 3.0789 | 3.5887 | 3.5887 | 3.5887 | 3.5887
2024-06-26 09:00 | 2.896 | 3.1072 | 3.8572 | 4.0572 | 4.2572 | 2024-04-26 09:00 | 2.7931 | 3.2556 | 3.2556 | 3.2556 | 3.2556
2024-06-26 10:00 | 2.2291 | 2.3917 | 2.969 | 3.123 | 3.2769 | 2024-04-26 10:00 | 2.7626 | 3.2201 | 3.2201 | 3.2201 | 3.2201
2024-06-26 11:00 | 2.1529 | 2.3099 | 2.8675 | 3.0162 | 3.1649 | 2024-04-26 11:00 | 2.7931 | 3.2556 | 3.2556 | 3.2556 | 3.2556
2024-06-26 12:00 | 2.1529 | 2.3099 | 2.8675 | 3.0162 | 3.1649 | 2024-04-26 12:00 | 2.8236 | 3.2911 | 3.2911 | 3.2911 | 3.2911
2024-06-26 13:00 | 2.2863 | 2.453 | 3.0451 | 3.203 | 3.3609 | 2024-04-26 13:00 | 2.9646 | 3.4555 | 3.4555 | 3.4555 | 3.4555
2024-06-26 14:00 | 2.172 | 2.3304 | 2.8929 | 3.0429 | 3.1929 | 2024-04-26 14:00 | 3.197 | 3.7264 | 3.7264 | 3.7264 | 3.7264
2024-06-26 15:00 | 2.2101 | 2.3713 | 2.9436 | 3.0963 | 3.2489 | 2024-04-26 15:00 | 3.4904 | 4.0684 | 4.0684 | 4.0684 | 4.0684
2024-06-26 16:00 | 2.191 | 2.3508 | 2.9183 | 3.0696 | 3.2209 | 2024-04-26 16:00 | 3.6238 | 4.2239 | 4.2239 | 4.2239 | 4.2239
2024-06-26 17:00 | 2.2482 | 2.4121 | 2.9944 | 3.1496 | 3.3049 | 2024-04-26 17:00 | 3.4028 | 3.9662 | 3.9662 | 3.9662 | 3.9662
2024-06-26 18:00 | 2.191 | 2.3508 | 2.9183 | 3.0696 | 3.2209 | 2024-04-26 18:00 | 3.3456 | 3.8996 | 3.8996 | 3.8996 | 3.8996
2024-06-26 19:00 | 1.8481 | 1.9829 | 2.4615 | 2.5891 | 2.7167 | 2024-04-26 19:00 | 3.0979 | 3.6109 | 3.6109 | 3.6109 | 3.6109
2024-06-26 20:00 | 1.7338 | 1.8602 | 2.3092 | 2.429 | 2.5487 | 2024-04-26 20:00 | 2.7093 | 3.1579 | 3.1579 | 3.1579 | 3.1579
2024-06-26 21:00 | 1.7338 | 1.8602 | 2.3092 | 2.429 | 2.5487 | 2024-04-26 21:00 | 2.2939 | 2.6738 | 2.6738 | 2.6738 | 2.6738
2024-06-26 22:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-04-26 22:00 | 1.9929 | 2.3229 | 2.3229 | 2.3229 | 2.3229
2024-06-26 23:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-04-26 23:00 | 1.9548 | 2.2785 | 2.2785 | 2.2785 | 2.2785
2024-06-27 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-04-27 | 1.8252 | 2.1275 | 2.1275 | 2.1275 | 2.1275
2024-06-27 01:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-04-27 01:00 | 1.8138 | 2.1141 | 2.1141 | 2.1141 | 2.1141
2024-06-27 02:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-04-27 02:00 | 1.7948 | 2.0919 | 2.0919 | 2.0919 | 2.0919
2024-06-27 03:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-04-27 03:00 | 1.9129 | 2.2296 | 2.2296 | 2.2296 | 2.2296
2024-06-27 04:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-04-27 04:00 | 2.0005 | 2.3318 | 2.3318 | 2.3318 | 2.3318
2024-06-27 05:00 | 1.9053 | 2.0442 | 2.5376 | 2.6692 | 2.8008 | 2024-04-27 05:00 | 2.2634 | 2.6382 | 2.6382 | 2.6382 | 2.6382
2024-06-27 06:00 | 2.1339 | 2.2895 | 2.8421 | 2.9895 | 3.1369 | 2024-04-27 06:00 | 2.3549 | 2.7448 | 2.7448 | 2.7448 | 2.7448
2024-06-27 07:00 | 2.4768 | 2.6574 | 3.2989 | 3.4699 | 3.641 | 2024-04-27 07:00 | 2.3892 | 2.7848 | 2.7848 | 2.7848 | 2.7848
2024-06-27 08:00 | 2.4578 | 2.637 | 3.2735 | 3.4433 | 3.613 | 2024-04-27 08:00 | 2.8579 | 3.3311 | 3.3311 | 3.3311 | 3.3311
2024-06-27 09:00 | 2.4768 | 2.6574 | 3.2989 | 3.4699 | 3.641 | 2024-04-27 09:00 | 2.816 | 3.2823 | 3.2823 | 3.2823 | 3.2823
2024-06-27 10:00 | 2.172 | 2.3304 | 2.8929 | 3.0429 | 3.1929 | 2024-04-27 10:00 | 2.6864 | 3.1312 | 3.1312 | 3.1312 | 3.1312
2024-06-27 11:00 | 2.1148 | 2.2691 | 2.8167 | 2.9628 | 3.1089 | 2024-04-27 11:00 | 2.473 | 2.8825 | 2.8825 | 2.8825 | 2.8825
2024-06-27 12:00 | 2.0577 | 2.2077 | 2.7406 | 2.8827 | 3.0248 | 2024-04-27 12:00 | 2.6026 | 3.0335 | 3.0335 | 3.0335 | 3.0335
2024-06-27 13:00 | 1.9434 | 2.0851 | 2.5884 | 2.7226 | 2.8568 | 2024-04-27 13:00 | 2.5645 | 2.9891 | 2.9891 | 2.9891 | 2.9891
2024-06-27 14:00 | 2.1148 | 2.2691 | 2.8167 | 2.9628 | 3.1089 | 2024-04-27 14:00 | 2.7283 | 3.1801 | 3.1801 | 3.1801 | 3.1801
2024-06-27 15:00 | 2.2101 | 2.3713 | 2.9436 | 3.0963 | 3.2489 | 2024-04-27 15:00 | 2.7817 | 3.2423 | 3.2423 | 3.2423 | 3.2423
2024-06-27 16:00 | 2.172 | 2.3304 | 2.8929 | 3.0429 | 3.1929 | 2024-04-27 16:00 | 3.0751 | 3.5843 | 3.5843 | 3.5843 | 3.5843
2024-06-27 17:00 | 2.2673 | 2.4326 | 3.0198 | 3.1763 | 3.3329 | 2024-04-27 17:00 | 3.0141 | 3.5132 | 3.5132 | 3.5132 | 3.5132
2024-06-27 18:00 | 2.172 | 2.3304 | 2.8929 | 3.0429 | 3.1929 | 2024-04-27 18:00 | 2.6254 | 3.0602 | 3.0602 | 3.0602 | 3.0602
2024-06-27 19:00 | 1.8481 | 1.9829 | 2.4615 | 2.5891 | 2.7167 | 2024-04-27 19:00 | 2.4235 | 2.8248 | 2.8248 | 2.8248 | 2.8248
2024-06-27 20:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-04-27 20:00 | 2.1415 | 2.4961 | 2.4961 | 2.4961 | 2.4961
2024-06-27 21:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-04-27 21:00 | 2.0158 | 2.3495 | 2.3495 | 2.3495 | 2.3495
2024-06-27 22:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-04-27 22:00 | 1.8557 | 2.163 | 2.163 | 2.163 | 2.163
2024-06-27 23:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-04-27 23:00 | 1.8633 | 2.1719 | 2.1719 | 2.1719 | 2.1719
2024-06-28 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-04-28 | 1.7948 | 2.0919 | 2.0919 | 2.0919 | 2.0919
2024-06-28 01:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-04-28 01:00 | 1.7262 | 2.012 | 2.012 | 2.012 | 2.012
2024-06-28 02:00 | 1.448 | 1.5536 | 1.9286 | 2.0286 | 2.1286 | 2024-04-28 02:00 | 1.7147 | 1.9987 | 1.9987 | 1.9987 | 1.9987
2024-06-28 03:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-04-28 03:00 | 1.9777 | 2.3051 | 2.3051 | 2.3051 | 2.3051
2024-06-28 04:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-04-28 04:00 | 2.0005 | 2.3318 | 2.3318 | 2.3318 | 2.3318
2024-06-28 05:00 | 1.81 | 1.942 | 2.4107 | 2.5357 | 2.6607 | 2024-04-28 05:00 | 2.3435 | 2.7315 | 2.7315 | 2.7315 | 2.7315
2024-06-28 06:00 | 2.191 | 2.3508 | 2.9183 | 3.0696 | 3.2209 | 2024-04-28 06:00 | 2.553 | 2.9758 | 2.9758 | 2.9758 | 2.9758
2024-06-28 07:00 | 2.7436 | 2.9436 | 3.6542 | 3.8436 | 4.0331 | 2024-04-28 07:00 | 2.3625 | 2.7537 | 2.7537 | 2.7537 | 2.7537
2024-06-28 08:00 | 2.6102 | 2.8005 | 3.4765 | 3.6568 | 3.8371 | 2024-04-28 08:00 | 2.5073 | 2.9225 | 2.9225 | 2.9225 | 2.9225
2024-06-28 09:00 | 2.4387 | 2.6166 | 3.2481 | 3.4166 | 3.585 | 2024-04-28 09:00 | 2.4502 | 2.8559 | 2.8559 | 2.8559 | 2.8559
2024-06-28 10:00 | 2.0958 | 2.2486 | 2.7914 | 2.9361 | 3.0808 | 2024-04-28 10:00 | 3.0675 | 3.5754 | 3.5754 | 3.5754 | 3.5754
2024-06-28 11:00 | 2.0577 | 2.2077 | 2.7406 | 2.8827 | 3.0248 | 2024-04-28 11:00 | 3.0484 | 3.5532 | 3.5532 | 3.5532 | 3.5532
2024-06-28 12:00 | 1.8481 | 1.9829 | 2.4615 | 2.5891 | 2.7167 | 2024-04-28 12:00 | 2.8198 | 3.2867 | 3.2867 | 3.2867 | 3.2867
2024-06-28 13:00 | 2.0577 | 2.2077 | 2.7406 | 2.8827 | 3.0248 | 2024-04-28 13:00 | 3.0865 | 3.5976 | 3.5976 | 3.5976 | 3.5976
2024-06-28 14:00 | 2.0577 | 2.2077 | 2.7406 | 2.8827 | 3.0248 | 2024-04-28 14:00 | 2.8693 | 3.3444 | 3.3444 | 3.3444 | 3.3444
2024-06-28 15:00 | 2.191 | 2.3508 | 2.9183 | 3.0696 | 3.2209 | 2024-04-28 15:00 | 2.896 | 3.3755 | 3.3755 | 3.3755 | 3.3755
2024-06-28 16:00 | 2.1339 | 2.2895 | 2.8421 | 2.9895 | 3.1369 | 2024-04-28 16:00 | 2.8884 | 3.3666 | 3.3666 | 3.3666 | 3.3666
2024-06-28 17:00 | 2.3054 | 2.4735 | 3.0705 | 3.2297 | 3.3889 | 2024-04-28 17:00 | 2.7817 | 3.2423 | 3.2423 | 3.2423 | 3.2423
2024-06-28 18:00 | 2.3054 | 2.4735 | 3.0705 | 3.2297 | 3.3889 | 2024-04-28 18:00 | 2.5492 | 2.9714 | 2.9714 | 2.9714 | 2.9714
2024-06-28 19:00 | 1.829 | 1.9624 | 2.4361 | 2.5624 | 2.6887 | 2024-04-28 19:00 | 2.3968 | 2.7937 | 2.7937 | 2.7937 | 2.7937
2024-06-28 20:00 | 1.829 | 1.9624 | 2.4361 | 2.5624 | 2.6887 | 2024-04-28 20:00 | 2.233 | 2.6027 | 2.6027 | 2.6027 | 2.6027
2024-06-28 21:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-04-28 21:00 | 2.0462 | 2.3851 | 2.3851 | 2.3851 | 2.3851
2024-06-28 22:00 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 2024-04-28 22:00 | 1.8557 | 2.163 | 2.163 | 2.163 | 2.163
2024-06-28 23:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-04-28 23:00 | 1.7224 | 2.0076 | 2.0076 | 2.0076 | 2.0076
2024-06-29 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-04-29 | 1.6614 | 1.9365 | 1.9365 | 1.9365 | 1.9365
2024-06-29 01:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-04-29 01:00 | 1.6842 | 1.9631 | 1.9631 | 1.9631 | 1.9631
2024-06-29 02:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-04-29 02:00 | 1.6614 | 1.9365 | 1.9365 | 1.9365 | 1.9365
2024-06-29 03:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-04-29 03:00 | 1.8672 | 2.1763 | 2.1763 | 2.1763 | 2.1763
2024-06-29 04:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-04-29 04:00 | 2.0081 | 2.3407 | 2.3407 | 2.3407 | 2.3407
2024-06-29 05:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-04-29 05:00 | 2.2291 | 2.5983 | 2.5983 | 2.5983 | 2.5983
2024-06-29 06:00 | 1.7338 | 1.8602 | 2.3092 | 2.429 | 2.5487 | 2024-04-29 06:00 | 2.7359 | 3.189 | 3.189 | 3.189 | 3.189
2024-06-29 07:00 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 2024-04-29 07:00 | 2.8541 | 3.3267 | 3.3267 | 3.3267 | 3.3267
2024-06-29 08:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-04-29 08:00 | 3.1246 | 3.642 | 3.642 | 3.642 | 3.642
2024-06-29 09:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-04-29 09:00 | 3.4257 | 3.9929 | 3.9929 | 3.9929 | 3.9929
2024-06-29 10:00 | 1.4289 | 1.5331 | 1.9032 | 2.0019 | 2.1006 | 2024-04-29 10:00 | 3.399 | 3.9618 | 3.9618 | 3.9618 | 3.9618
2024-06-29 11:00 | 1.2384 | 1.3287 | 1.6494 | 1.735 | 1.8205 | 2024-04-29 11:00 | 3.5057 | 4.0862 | 4.0862 | 4.0862 | 4.0862
2024-06-29 12:00 | 1.2956 | 1.39 | 1.7256 | 1.815 | 1.9045 | 2024-04-29 12:00 | 3.258 | 3.7975 | 3.7975 | 3.7975 | 3.7975
2024-06-29 13:00 | 1.2956 | 1.39 | 1.7256 | 1.815 | 1.9045 | 2024-04-29 13:00 | 3.1399 | 3.6598 | 3.6598 | 3.6598 | 3.6598
2024-06-29 14:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-04-29 14:00 | 3.1399 | 3.6598 | 3.6598 | 3.6598 | 3.6598
2024-06-29 15:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-04-29 15:00 | 3.1399 | 3.6598 | 3.6598 | 3.6598 | 3.6598
2024-06-29 16:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-04-29 16:00 | 3.1399 | 3.6598 | 3.6598 | 3.6598 | 3.6598
2024-06-29 17:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-04-29 17:00 | 3.2008 | 3.7308 | 3.7308 | 3.7308 | 3.7308
2024-06-29 18:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-04-29 18:00 | 3.1551 | 3.6776 | 3.6776 | 3.6776 | 3.6776
2024-06-29 19:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-04-29 19:00 | 2.8312 | 3.3 | 3.3 | 3.3 | 3.3
2024-06-29 20:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-04-29 20:00 | 2.4311 | 2.8337 | 2.8337 | 2.8337 | 2.8337
2024-06-29 21:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-04-29 21:00 | 2.172 | 2.5316 | 2.5316 | 2.5316 | 2.5316
2024-06-29 22:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-04-29 22:00 | 1.8595 | 2.1674 | 2.1674 | 2.1674 | 2.1674
2024-06-29 23:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-04-29 23:00 | 1.8062 | 2.1053 | 2.1053 | 2.1053 | 2.1053
2024-06-30 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-04-30 | 1.6842 | 1.9631 | 1.9631 | 1.9631 | 1.9631
2024-06-30 01:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-04-30 01:00 | 1.65 | 1.9232 | 1.9232 | 1.9232 | 1.9232
2024-06-30 02:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-04-30 02:00 | 1.5966 | 1.861 | 1.861 | 1.861 | 1.861
2024-06-30 03:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-04-30 03:00 | 1.7185 | 2.0031 | 2.0031 | 2.0031 | 2.0031
2024-06-30 04:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-04-30 04:00 | 1.9662 | 2.2918 | 2.2918 | 2.2918 | 2.2918
2024-06-30 05:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-04-30 05:00 | 2.092 | 2.4384 | 2.4384 | 2.4384 | 2.4384
2024-06-30 06:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-04-30 06:00 | 2.6597 | 3.1002 | 3.1002 | 3.1002 | 3.1002
2024-06-30 07:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-04-30 07:00 | 3.0103 | 3.5088 | 3.5088 | 3.5088 | 3.5088
2024-06-30 08:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-04-30 08:00 | 3.5362 | 4.1217 | 4.1217 | 4.1217 | 4.1217
2024-06-30 09:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-04-30 09:00 | 3.5362 | 4.1217 | 4.1217 | 4.1217 | 4.1217
2024-06-30 10:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-04-30 10:00 | 3.8943 | 4.5392 | 4.5392 | 4.5392 | 4.5392
2024-06-30 11:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-04-30 11:00 | 3.6238 | 4.2239 | 4.2239 | 4.2239 | 4.2239
2024-06-30 12:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-04-30 12:00 | 3.5819 | 4.175 | 4.175 | 4.175 | 4.175
2024-06-30 13:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-04-30 13:00 | 3.5781 | 4.1706 | 4.1706 | 4.1706 | 4.1706
2024-06-30 14:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-04-30 14:00 | 3.5323 | 4.1173 | 4.1173 | 4.1173 | 4.1173
2024-06-30 15:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-04-30 15:00 | 3.3761 | 3.9352 | 3.9352 | 3.9352 | 3.9352
2024-06-30 16:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-04-30 16:00 | 3.5857 | 4.1794 | 4.1794 | 4.1794 | 4.1794
2024-06-30 17:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-04-30 17:00 | 3.3875 | 3.9485 | 3.9485 | 3.9485 | 3.9485
2024-06-30 18:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-04-30 18:00 | 3.1056 | 3.6198 | 3.6198 | 3.6198 | 3.6198
2024-06-30 19:00 | 1.7909 | 1.9215 | 2.3854 | 2.509 | 2.6327 | 2024-04-30 19:00 | 2.6369 | 3.0735 | 3.0735 | 3.0735 | 3.0735
2024-06-30 20:00 | 1.829 | 1.9624 | 2.4361 | 2.5624 | 2.6887 | 2024-04-30 20:00 | 2.4883 | 2.9003 | 2.9003 | 2.9003 | 2.9003
2024-06-30 21:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-04-30 21:00 | 2.4654 | 2.8736 | 2.8736 | 2.8736 | 2.8736
2024-06-30 22:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-04-30 22:00 | 1.7719 | 2.0653 | 2.0653 | 2.0653 | 2.0653
2024-06-30 23:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-04-30 23:00 | 1.7528 | 2.0431 | 2.0431 | 2.0431 | 2.0431
2024-07-01 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-05-01 | 1.6919 | 1.972 | 1.972 | 1.972 | 1.972
2024-07-01 01:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-05-01 01:00 | 1.6766 | 1.9543 | 1.9543 | 1.9543 | 1.9543
2024-07-01 02:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-05-01 02:00 | 1.6614 | 1.9365 | 1.9365 | 1.9365 | 1.9365
2024-07-01 03:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-05-01 03:00 | 1.7986 | 2.0964 | 2.0964 | 2.0964 | 2.0964
2024-07-01 04:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-05-01 04:00 | 1.9738 | 2.3007 | 2.3007 | 2.3007 | 2.3007
2024-07-01 05:00 | 1.8862 | 2.0237 | 2.5122 | 2.6425 | 2.7728 | 2024-05-01 05:00 | 2.3168 | 2.7004 | 2.7004 | 2.7004 | 2.7004
2024-07-01 06:00 | 2.1529 | 2.3099 | 2.8675 | 3.0162 | 3.1649 | 2024-05-01 06:00 | 2.6331 | 3.0691 | 3.0691 | 3.0691 | 3.0691
2024-07-01 07:00 | 2.7436 | 2.9436 | 3.6542 | 3.8436 | 4.0331 | 2024-05-01 07:00 | 2.7474 | 3.2023 | 3.2023 | 3.2023 | 3.2023
2024-07-01 08:00 | 2.6674 | 2.8619 | 3.5527 | 3.7369 | 3.9211 | 2024-05-01 08:00 | 3.3113 | 3.8597 | 3.8597 | 3.8597 | 3.8597
2024-07-01 09:00 | 2.5149 | 2.6983 | 3.3496 | 3.5233 | 3.697 | 2024-05-01 09:00 | 3.2085 | 3.7397 | 3.7397 | 3.7397 | 3.7397
2024-07-01 10:00 | 2.5721 | 2.7597 | 3.4258 | 3.6034 | 3.781 | 2024-05-01 10:00 | 2.8198 | 3.2867 | 3.2867 | 3.2867 | 3.2867
2024-07-01 11:00 | 2.2863 | 2.453 | 3.0451 | 3.203 | 3.3609 | 2024-05-01 11:00 | 3.0675 | 3.5754 | 3.5754 | 3.5754 | 3.5754
2024-07-01 12:00 | 2.191 | 2.3508 | 2.9183 | 3.0696 | 3.2209 | 2024-05-01 12:00 | 3.0522 | 3.5576 | 3.5576 | 3.5576 | 3.5576
2024-07-01 13:00 | 2.3816 | 2.5552 | 3.172 | 3.3365 | 3.501 | 2024-05-01 13:00 | 3.2389 | 3.7753 | 3.7753 | 3.7753 | 3.7753
2024-07-01 14:00 | 2.2673 | 2.4326 | 3.0198 | 3.1763 | 3.3329 | 2024-05-01 14:00 | 3.5019 | 4.0817 | 4.0817 | 4.0817 | 4.0817
2024-07-01 15:00 | 2.3435 | 2.5144 | 3.1213 | 3.2831 | 3.4449 | 2024-05-01 15:00 | 3.4523 | 4.024 | 4.024 | 4.024 | 4.024
2024-07-01 16:00 | 2.3244 | 2.4939 | 3.0959 | 3.2564 | 3.4169 | 2024-05-01 16:00 | 3.3799 | 3.9396 | 3.9396 | 3.9396 | 3.9396
2024-07-01 17:00 | 2.4578 | 2.637 | 3.2735 | 3.4433 | 3.613 | 2024-05-01 17:00 | 3.2809 | 3.8241 | 3.8241 | 3.8241 | 3.8241
2024-07-01 18:00 | 2.2863 | 2.453 | 3.0451 | 3.203 | 3.3609 | 2024-05-01 18:00 | 3.1399 | 3.6598 | 3.6598 | 3.6598 | 3.6598
2024-07-01 19:00 | 1.8481 | 1.9829 | 2.4615 | 2.5891 | 2.7167 | 2024-05-01 19:00 | 2.8922 | 3.3711 | 3.3711 | 3.3711 | 3.3711
2024-07-01 20:00 | 1.7909 | 1.9215 | 2.3854 | 2.509 | 2.6327 | 2024-05-01 20:00 | 2.6635 | 3.1046 | 3.1046 | 3.1046 | 3.1046
2024-07-01 21:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-05-01 21:00 | 2.2215 | 2.5894 | 2.5894 | 2.5894 | 2.5894
2024-07-01 22:00 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 2024-05-01 22:00 | 1.8786 | 2.1897 | 2.1897 | 2.1897 | 2.1897
2024-07-01 23:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-05-01 23:00 | 1.9472 | 2.2696 | 2.2696 | 2.2696 | 2.2696
2024-07-02 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-05-02 | 1.6538 | 1.9276 | 1.9276 | 1.9276 | 1.9276
2024-07-02 01:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-05-02 01:00 | 1.6614 | 1.9365 | 1.9365 | 1.9365 | 1.9365
2024-07-02 02:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-05-02 02:00 | 1.6195 | 1.8876 | 1.8876 | 1.8876 | 1.8876
2024-07-02 03:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-05-02 03:00 | 1.7376 | 2.0253 | 2.0253 | 2.0253 | 2.0253
2024-07-02 04:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-05-02 04:00 | 1.9357 | 2.2563 | 2.2563 | 2.2563 | 2.2563
2024-07-02 05:00 | 1.7909 | 1.9215 | 2.3854 | 2.509 | 2.6327 | 2024-05-02 05:00 | 2.2711 | 2.6471 | 2.6471 | 2.6471 | 2.6471
2024-07-02 06:00 | 2.1148 | 2.2691 | 2.8167 | 2.9628 | 3.1089 | 2024-05-02 06:00 | 2.8083 | 3.2734 | 3.2734 | 3.2734 | 3.2734
2024-07-02 07:00 | 2.534 | 2.7188 | 3.375 | 3.55 | 3.725 | 2024-05-02 07:00 | 3.3571 | 3.913 | 3.913 | 3.913 | 3.913
2024-07-02 08:00 | 2.6293 | 2.821 | 3.5019 | 3.6835 | 3.8651 | 2024-05-02 08:00 | 3.3685 | 3.9263 | 3.9263 | 3.9263 | 3.9263
2024-07-02 09:00 | 2.2291 | 2.3917 | 2.969 | 3.123 | 3.2769 | 2024-05-02 09:00 | 3.2504 | 3.7886 | 3.7886 | 3.7886 | 3.7886
2024-07-02 10:00 | 2.2863 | 2.453 | 3.0451 | 3.203 | 3.3609 | 2024-05-02 10:00 | 3.0103 | 3.5088 | 3.5088 | 3.5088 | 3.5088
2024-07-02 11:00 | 2.2101 | 2.3713 | 2.9436 | 3.0963 | 3.2489 | 2024-05-02 11:00 | 3.2809 | 3.8241 | 3.8241 | 3.8241 | 3.8241
2024-07-02 12:00 | 2.3054 | 2.4735 | 3.0705 | 3.2297 | 3.3889 | 2024-05-02 12:00 | 3.4447 | 4.0151 | 4.0151 | 4.0151 | 4.0151
2024-07-02 13:00 | 2.3244 | 2.4939 | 3.0959 | 3.2564 | 3.4169 | 2024-05-02 13:00 | 3.4561 | 4.0284 | 4.0284 | 4.0284 | 4.0284
2024-07-02 14:00 | 2.4006 | 2.5757 | 3.1974 | 3.3632 | 3.529 | 2024-05-02 14:00 | 3.4561 | 4.0284 | 4.0284 | 4.0284 | 4.0284
2024-07-02 15:00 | 2.2482 | 2.4121 | 2.9944 | 3.1496 | 3.3049 | 2024-05-02 15:00 | 3.2504 | 3.7886 | 3.7886 | 3.7886 | 3.7886
2024-07-02 16:00 | 2.3816 | 2.5552 | 3.172 | 3.3365 | 3.501 | 2024-05-02 16:00 | 3.4828 | 4.0595 | 4.0595 | 4.0595 | 4.0595
2024-07-02 17:00 | 2.3054 | 2.4735 | 3.0705 | 3.2297 | 3.3889 | 2024-05-02 17:00 | 3.4218 | 3.9885 | 3.9885 | 3.9885 | 3.9885
2024-07-02 18:00 | 2.2291 | 2.3917 | 2.969 | 3.123 | 3.2769 | 2024-05-02 18:00 | 3.2161 | 3.7486 | 3.7486 | 3.7486 | 3.7486
2024-07-02 19:00 | 1.9624 | 2.1055 | 2.6137 | 2.7493 | 2.8848 | 2024-05-02 19:00 | 2.6978 | 3.1446 | 3.1446 | 3.1446 | 3.1446
2024-07-02 20:00 | 1.7338 | 1.8602 | 2.3092 | 2.429 | 2.5487 | 2024-05-02 20:00 | 2.4654 | 2.8736 | 2.8736 | 2.8736 | 2.8736
2024-07-02 21:00 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 2024-05-02 21:00 | 2.3854 | 2.7804 | 2.7804 | 2.7804 | 2.7804
2024-07-02 22:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-05-02 22:00 | 1.9091 | 2.2252 | 2.2252 | 2.2252 | 2.2252
2024-07-02 23:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-05-02 23:00 | 1.7986 | 2.0964 | 2.0964 | 2.0964 | 2.0964
2024-07-03 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-05-03 | 1.65 | 1.9232 | 1.9232 | 1.9232 | 1.9232
2024-07-03 01:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-05-03 01:00 | 1.6347 | 1.9054 | 1.9054 | 1.9054 | 1.9054
2024-07-03 02:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-05-03 02:00 | 1.6766 | 1.9543 | 1.9543 | 1.9543 | 1.9543
2024-07-03 03:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-05-03 03:00 | 1.9243 | 2.243 | 2.243 | 2.243 | 2.243
2024-07-03 04:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-05-03 04:00 | 2.0196 | 2.354 | 2.354 | 2.354 | 2.354
2024-07-03 05:00 | 1.7719 | 1.9011 | 2.36 | 2.4823 | 2.6047 | 2024-05-03 05:00 | 2.3701 | 2.7626 | 2.7626 | 2.7626 | 2.7626
2024-07-03 06:00 | 1.9434 | 2.0851 | 2.5884 | 2.7226 | 2.8568 | 2024-05-03 06:00 | 2.5683 | 2.9936 | 2.9936 | 2.9936 | 2.9936
2024-07-03 07:00 | 2.6293 | 2.821 | 3.5019 | 3.6835 | 3.8651 | 2024-05-03 07:00 | 3.0332 | 3.5354 | 3.5354 | 3.5354 | 3.5354
2024-07-03 08:00 | 2.6293 | 2.821 | 3.5019 | 3.6835 | 3.8651 | 2024-05-03 08:00 | 3.5323 | 4.1173 | 4.1173 | 4.1173 | 4.1173
2024-07-03 09:00 | 2.2673 | 2.4326 | 3.0198 | 3.1763 | 3.3329 | 2024-05-03 09:00 | 3.5323 | 4.1173 | 4.1173 | 4.1173 | 4.1173
2024-07-03 10:00 | 2.191 | 2.3508 | 2.9183 | 3.0696 | 3.2209 | 2024-05-03 10:00 | 3.4561 | 4.0284 | 4.0284 | 4.0284 | 4.0284
2024-07-03 11:00 | 2.1339 | 2.2895 | 2.8421 | 2.9895 | 3.1369 | 2024-05-03 11:00 | 3.5743 | 4.1661 | 4.1661 | 4.1661 | 4.1661
2024-07-03 12:00 | 2.172 | 2.3304 | 2.8929 | 3.0429 | 3.1929 | 2024-05-03 12:00 | 3.2427 | 3.7797 | 3.7797 | 3.7797 | 3.7797
2024-07-03 13:00 | 2.2101 | 2.3713 | 2.9436 | 3.0963 | 3.2489 | 2024-05-03 13:00 | 3.1132 | 3.6287 | 3.6287 | 3.6287 | 3.6287
2024-07-03 14:00 | 2.172 | 2.3304 | 2.8929 | 3.0429 | 3.1929 | 2024-05-03 14:00 | 3.4942 | 4.0728 | 4.0728 | 4.0728 | 4.0728
2024-07-03 15:00 | 2.3244 | 2.4939 | 3.0959 | 3.2564 | 3.4169 | 2024-05-03 15:00 | 3.5781 | 4.1706 | 4.1706 | 4.1706 | 4.1706
2024-07-03 16:00 | 2.3054 | 2.4735 | 3.0705 | 3.2297 | 3.3889 | 2024-05-03 16:00 | 3.4257 | 3.9929 | 3.9929 | 3.9929 | 3.9929
2024-07-03 17:00 | 2.3816 | 2.5552 | 3.172 | 3.3365 | 3.501 | 2024-05-03 17:00 | 3.498 | 4.0773 | 4.0773 | 4.0773 | 4.0773
2024-07-03 18:00 | 2.2673 | 2.4326 | 3.0198 | 3.1763 | 3.3329 | 2024-05-03 18:00 | 3.2656 | 3.8064 | 3.8064 | 3.8064 | 3.8064
2024-07-03 19:00 | 1.9434 | 2.0851 | 2.5884 | 2.7226 | 2.8568 | 2024-05-03 19:00 | 2.9455 | 3.4333 | 3.4333 | 3.4333 | 3.4333
2024-07-03 20:00 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 2024-05-03 20:00 | 2.6102 | 3.0424 | 3.0424 | 3.0424 | 3.0424
2024-07-03 21:00 | 1.7528 | 1.8807 | 2.3346 | 2.4557 | 2.5767 | 2024-05-03 21:00 | 2.3701 | 2.7626 | 2.7626 | 2.7626 | 2.7626
2024-07-03 22:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-05-03 22:00 | 1.81 | 2.1097 | 2.1097 | 2.1097 | 2.1097
2024-07-03 23:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-05-03 23:00 | 1.829 | 2.1319 | 2.1319 | 2.1319 | 2.1319
2024-07-04 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-05-04 | 1.7719 | 2.0653 | 2.0653 | 2.0653 | 2.0653
2024-07-04 01:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-05-04 01:00 | 1.6804 | 1.9587 | 1.9587 | 1.9587 | 1.9587
2024-07-04 02:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-05-04 02:00 | 1.6347 | 1.9054 | 1.9054 | 1.9054 | 1.9054
2024-07-04 03:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-05-04 03:00 | 1.7719 | 2.0653 | 2.0653 | 2.0653 | 2.0653
2024-07-04 04:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-05-04 04:00 | 1.9243 | 2.243 | 2.243 | 2.243 | 2.243
2024-07-04 05:00 | 1.7528 | 1.8807 | 2.3346 | 2.4557 | 2.5767 | 2024-05-04 05:00 | 2.2139 | 2.5805 | 2.5805 | 2.5805 | 2.5805
2024-07-04 06:00 | 2.0005 | 2.1464 | 2.6645 | 2.8026 | 2.9408 | 2024-05-04 06:00 | 2.3397 | 2.7271 | 2.7271 | 2.7271 | 2.7271
2024-07-04 07:00 | 2.553 | 2.7392 | 3.4004 | 3.5767 | 3.753 | 2024-05-04 07:00 | 2.3549 | 2.7448 | 2.7448 | 2.7448 | 2.7448
2024-07-04 08:00 | 2.6102 | 2.8005 | 3.4765 | 3.6568 | 3.8371 | 2024-05-04 08:00 | 2.7359 | 3.189 | 3.189 | 3.189 | 3.189
2024-07-04 09:00 | 2.534 | 2.7188 | 3.375 | 3.55 | 3.725 | 2024-05-04 09:00 | 3.0332 | 3.5354 | 3.5354 | 3.5354 | 3.5354
2024-07-04 10:00 | 2.3625 | 2.5348 | 3.1466 | 3.3098 | 3.473 | 2024-05-04 10:00 | 3.0713 | 3.5798 | 3.5798 | 3.5798 | 3.5798
2024-07-04 11:00 | 2.3435 | 2.5144 | 3.1213 | 3.2831 | 3.4449 | 2024-05-04 11:00 | 3.2542 | 3.793 | 3.793 | 3.793 | 3.793
2024-07-04 12:00 | 2.4006 | 2.5757 | 3.1974 | 3.3632 | 3.529 | 2024-05-04 12:00 | 3.0675 | 3.5754 | 3.5754 | 3.5754 | 3.5754
2024-07-04 13:00 | 2.2863 | 2.453 | 3.0451 | 3.203 | 3.3609 | 2024-05-04 13:00 | 3.1703 | 3.6953 | 3.6953 | 3.6953 | 3.6953
2024-07-04 14:00 | 2.2673 | 2.4326 | 3.0198 | 3.1763 | 3.3329 | 2024-05-04 14:00 | 3.0941 | 3.6065 | 3.6065 | 3.6065 | 3.6065
2024-07-04 15:00 | 2.2101 | 2.3713 | 2.9436 | 3.0963 | 3.2489 | 2024-05-04 15:00 | 3.0027 | 3.4999 | 3.4999 | 3.4999 | 3.4999
2024-07-04 16:00 | 2.3244 | 2.4939 | 3.0959 | 3.2564 | 3.4169 | 2024-05-04 16:00 | 3.0941 | 3.6065 | 3.6065 | 3.6065 | 3.6065
2024-07-04 17:00 | 2.3054 | 2.4735 | 3.0705 | 3.2297 | 3.3889 | 2024-05-04 17:00 | 3.0751 | 3.5843 | 3.5843 | 3.5843 | 3.5843
2024-07-04 18:00 | 2.2101 | 2.3713 | 2.9436 | 3.0963 | 3.2489 | 2024-05-04 18:00 | 2.8388 | 3.3089 | 3.3089 | 3.3089 | 3.3089
2024-07-04 19:00 | 1.829 | 1.9624 | 2.4361 | 2.5624 | 2.6887 | 2024-05-04 19:00 | 2.3358 | 2.7226 | 2.7226 | 2.7226 | 2.7226
2024-07-04 20:00 | 1.7909 | 1.9215 | 2.3854 | 2.509 | 2.6327 | 2024-05-04 20:00 | 2.3168 | 2.7004 | 2.7004 | 2.7004 | 2.7004
2024-07-04 21:00 | 1.7719 | 1.9011 | 2.36 | 2.4823 | 2.6047 | 2024-05-04 21:00 | 2.1034 | 2.4517 | 2.4517 | 2.4517 | 2.4517
2024-07-04 22:00 | 1.7528 | 1.8807 | 2.3346 | 2.4557 | 2.5767 | 2024-05-04 22:00 | 1.7414 | 2.0298 | 2.0298 | 2.0298 | 2.0298
2024-07-04 23:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-05-04 23:00 | 1.7681 | 2.0609 | 2.0609 | 2.0609 | 2.0609
2024-07-05 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-05-05 | 1.7605 | 2.052 | 2.052 | 2.052 | 2.052
2024-07-05 01:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-05-05 01:00 | 1.6614 | 1.9365 | 1.9365 | 1.9365 | 1.9365
2024-07-05 02:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-05-05 02:00 | 1.6118 | 1.8787 | 1.8787 | 1.8787 | 1.8787
2024-07-05 03:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-05-05 03:00 | 1.8672 | 2.1763 | 2.1763 | 2.1763 | 2.1763
2024-07-05 04:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-05-05 04:00 | 1.9548 | 2.2785 | 2.2785 | 2.2785 | 2.2785
2024-07-05 05:00 | 1.8862 | 2.0237 | 2.5122 | 2.6425 | 2.7728 | 2024-05-05 05:00 | 2.1644 | 2.5228 | 2.5228 | 2.5228 | 2.5228
2024-07-05 06:00 | 2.1339 | 2.2895 | 2.8421 | 2.9895 | 3.1369 | 2024-05-05 06:00 | 2.3892 | 2.7848 | 2.7848 | 2.7848 | 2.7848
2024-07-05 07:00 | 2.3435 | 2.5144 | 3.1213 | 3.2831 | 3.4449 | 2024-05-05 07:00 | 2.3587 | 2.7493 | 2.7493 | 2.7493 | 2.7493
2024-07-05 08:00 | 2.3816 | 2.5552 | 3.172 | 3.3365 | 3.501 | 2024-05-05 08:00 | 2.9189 | 3.4022 | 3.4022 | 3.4022 | 3.4022
2024-07-05 09:00 | 2.2673 | 2.4326 | 3.0198 | 3.1763 | 3.3329 | 2024-05-05 09:00 | 3.0179 | 3.5177 | 3.5177 | 3.5177 | 3.5177
2024-07-05 10:00 | 2.2673 | 2.4326 | 3.0198 | 3.1763 | 3.3329 | 2024-05-05 10:00 | 3.3914 | 3.9529 | 3.9529 | 3.9529 | 3.9529
2024-07-05 11:00 | 2.3244 | 2.4939 | 3.0959 | 3.2564 | 3.4169 | 2024-05-05 11:00 | 3.3037 | 3.8508 | 3.8508 | 3.8508 | 3.8508
2024-07-05 12:00 | 2.2291 | 2.3917 | 2.969 | 3.123 | 3.2769 | 2024-05-05 12:00 | 3.2809 | 3.8241 | 3.8241 | 3.8241 | 3.8241
2024-07-05 13:00 | 2.172 | 2.3304 | 2.8929 | 3.0429 | 3.1929 | 2024-05-05 13:00 | 3.2504 | 3.7886 | 3.7886 | 3.7886 | 3.7886
2024-07-05 14:00 | 2.0577 | 2.2077 | 2.7406 | 2.8827 | 3.0248 | 2024-05-05 14:00 | 3.3342 | 3.8863 | 3.8863 | 3.8863 | 3.8863
2024-07-05 15:00 | 2.2482 | 2.4121 | 2.9944 | 3.1496 | 3.3049 | 2024-05-05 15:00 | 3.1894 | 3.7175 | 3.7175 | 3.7175 | 3.7175
2024-07-05 16:00 | 2.191 | 2.3508 | 2.9183 | 3.0696 | 3.2209 | 2024-05-05 16:00 | 3.0675 | 3.5754 | 3.5754 | 3.5754 | 3.5754
2024-07-05 17:00 | 2.2673 | 2.4326 | 3.0198 | 3.1763 | 3.3329 | 2024-05-05 17:00 | 3.1018 | 3.6154 | 3.6154 | 3.6154 | 3.6154
2024-07-05 18:00 | 2.191 | 2.3508 | 2.9183 | 3.0696 | 3.2209 | 2024-05-05 18:00 | 2.7855 | 3.2467 | 3.2467 | 3.2467 | 3.2467
2024-07-05 19:00 | 1.7909 | 1.9215 | 2.3854 | 2.509 | 2.6327 | 2024-05-05 19:00 | 2.4121 | 2.8115 | 2.8115 | 2.8115 | 2.8115
2024-07-05 20:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-05-05 20:00 | 2.4692 | 2.8781 | 2.8781 | 2.8781 | 2.8781
2024-07-05 21:00 | 1.7719 | 1.9011 | 2.36 | 2.4823 | 2.6047 | 2024-05-05 21:00 | 2.1987 | 2.5627 | 2.5627 | 2.5627 | 2.5627
2024-07-05 22:00 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 2024-05-05 22:00 | 1.8367 | 2.1408 | 2.1408 | 2.1408 | 2.1408
2024-07-05 23:00 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 2024-05-05 23:00 | 1.6842 | 1.9631 | 1.9631 | 1.9631 | 1.9631
2024-07-06 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-05-06 | 1.6118 | 1.8787 | 1.8787 | 1.8787 | 1.8787
2024-07-06 01:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-05-06 01:00 | 1.6004 | 1.8654 | 1.8654 | 1.8654 | 1.8654
2024-07-06 02:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-05-06 02:00 | 1.6271 | 1.8965 | 1.8965 | 1.8965 | 1.8965
2024-07-06 03:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-05-06 03:00 | 1.8062 | 2.1053 | 2.1053 | 2.1053 | 2.1053
2024-07-06 04:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-05-06 04:00 | 1.9891 | 2.3185 | 2.3185 | 2.3185 | 2.3185
2024-07-06 05:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-05-06 05:00 | 2.233 | 2.6027 | 2.6027 | 2.6027 | 2.6027
2024-07-06 06:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-05-06 06:00 | 2.7131 | 3.1623 | 3.1623 | 3.1623 | 3.1623
2024-07-06 07:00 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 2024-05-06 07:00 | 2.9874 | 3.4821 | 3.4821 | 3.4821 | 3.4821
2024-07-06 08:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-05-06 08:00 | 3.418 | 3.984 | 3.984 | 3.984 | 3.984
2024-07-06 09:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-05-06 09:00 | 3.5057 | 4.0862 | 4.0862 | 4.0862 | 4.0862
2024-07-06 10:00 | 1.4289 | 1.5331 | 1.9032 | 2.0019 | 2.1006 | 2024-05-06 10:00 | 3.4066 | 3.9707 | 3.9707 | 3.9707 | 3.9707
2024-07-06 11:00 | 1.3908 | 1.4923 | 1.8525 | 1.9485 | 2.0446 | 2024-05-06 11:00 | 3.2275 | 3.7619 | 3.7619 | 3.7619 | 3.7619
2024-07-06 12:00 | 1.3527 | 1.4514 | 1.8017 | 1.8951 | 1.9885 | 2024-05-06 12:00 | 3.3266 | 3.8774 | 3.8774 | 3.8774 | 3.8774
2024-07-06 13:00 | 1.3527 | 1.4514 | 1.8017 | 1.8951 | 1.9885 | 2024-05-06 13:00 | 3.1627 | 3.6864 | 3.6864 | 3.6864 | 3.6864
2024-07-06 14:00 | 1.2575 | 1.3492 | 1.6748 | 1.7617 | 1.8485 | 2024-05-06 14:00 | 3.3151 | 3.8641 | 3.8641 | 3.8641 | 3.8641
2024-07-06 15:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-05-06 15:00 | 3.3533 | 3.9085 | 3.9085 | 3.9085 | 3.9085
2024-07-06 16:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-05-06 16:00 | 3.4257 | 3.9929 | 3.9929 | 3.9929 | 3.9929
2024-07-06 17:00 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 2024-05-06 17:00 | 3.6238 | 4.2239 | 4.2239 | 4.2239 | 4.2239
2024-07-06 18:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-05-06 18:00 | 3.2237 | 3.7575 | 3.7575 | 3.7575 | 3.7575
2024-07-06 19:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-05-06 19:00 | 2.7093 | 3.1579 | 3.1579 | 3.1579 | 3.1579
2024-07-06 20:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-05-06 20:00 | 2.6674 | 3.109 | 3.109 | 3.109 | 3.109
2024-07-06 21:00 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 2024-05-06 21:00 | 2.4197 | 2.8203 | 2.8203 | 2.8203 | 2.8203
2024-07-06 22:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-05-06 22:00 | 1.9281 | 2.2474 | 2.2474 | 2.2474 | 2.2474
2024-07-06 23:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-05-06 23:00 | 1.9091 | 2.2252 | 2.2252 | 2.2252 | 2.2252
2024-07-07 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-05-07 | 1.7719 | 2.0653 | 2.0653 | 2.0653 | 2.0653
2024-07-07 01:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-05-07 01:00 | 1.6919 | 1.972 | 1.972 | 1.972 | 1.972
2024-07-07 02:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-05-07 02:00 | 1.7224 | 2.0076 | 2.0076 | 2.0076 | 2.0076
2024-07-07 03:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-05-07 03:00 | 1.8138 | 2.1141 | 2.1141 | 2.1141 | 2.1141
2024-07-07 04:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-05-07 04:00 | 2.1225 | 2.4739 | 2.4739 | 2.4739 | 2.4739
2024-07-07 05:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-05-07 05:00 | 2.5492 | 2.9714 | 2.9714 | 2.9714 | 2.9714
2024-07-07 06:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-05-07 06:00 | 2.6978 | 3.1446 | 3.1446 | 3.1446 | 3.1446
2024-07-07 07:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-05-07 07:00 | 3.0751 | 3.5843 | 3.5843 | 3.5843 | 3.5843
2024-07-07 08:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-05-07 08:00 | 3.4752 | 4.0506 | 4.0506 | 4.0506 | 4.0506
2024-07-07 09:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-05-07 09:00 | 3.6428 | 4.2461 | 4.2461 | 4.2461 | 4.2461
2024-07-07 10:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-05-07 10:00 | 3.418 | 3.984 | 3.984 | 3.984 | 3.984
2024-07-07 11:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-05-07 11:00 | 3.4561 | 4.0284 | 4.0284 | 4.0284 | 4.0284
2024-07-07 12:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-05-07 12:00 | 3.5895 | 4.1839 | 4.1839 | 4.1839 | 4.1839
2024-07-07 13:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-05-07 13:00 | 3.277 | 3.8197 | 3.8197 | 3.8197 | 3.8197
2024-07-07 14:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-05-07 14:00 | 3.399 | 3.9618 | 3.9618 | 3.9618 | 3.9618
2024-07-07 15:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-05-07 15:00 | 3.2656 | 3.8064 | 3.8064 | 3.8064 | 3.8064
2024-07-07 16:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-05-07 16:00 | 3.5171 | 4.0995 | 4.0995 | 4.0995 | 4.0995
2024-07-07 17:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-05-07 17:00 | 3.4752 | 4.0506 | 4.0506 | 4.0506 | 4.0506
2024-07-07 18:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-05-07 18:00 | 3.0103 | 3.5088 | 3.5088 | 3.5088 | 3.5088
2024-07-07 19:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-05-07 19:00 | 2.8007 | 3.2645 | 3.2645 | 3.2645 | 3.2645
2024-07-07 20:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-05-07 20:00 | 2.3968 | 2.7937 | 2.7937 | 2.7937 | 2.7937
2024-07-07 21:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-05-07 21:00 | 2.2063 | 2.5716 | 2.5716 | 2.5716 | 2.5716
2024-07-07 22:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-05-07 22:00 | 1.9053 | 2.2207 | 2.2207 | 2.2207 | 2.2207
2024-07-07 23:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-05-07 23:00 | 1.8367 | 2.1408 | 2.1408 | 2.1408 | 2.1408
2024-07-08 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-05-08 | 1.6385 | 1.9098 | 1.9098 | 1.9098 | 1.9098
2024-07-08 01:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-05-08 01:00 | 1.6538 | 1.9276 | 1.9276 | 1.9276 | 1.9276
2024-07-08 02:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-05-08 02:00 | 1.6157 | 1.8832 | 1.8832 | 1.8832 | 1.8832
2024-07-08 03:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-05-08 03:00 | 1.7833 | 2.0786 | 2.0786 | 2.0786 | 2.0786
2024-07-08 04:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-05-08 04:00 | 2.0196 | 2.354 | 2.354 | 2.354 | 2.354
2024-07-08 05:00 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 2024-05-08 05:00 | 2.3015 | 2.6827 | 2.6827 | 2.6827 | 2.6827
2024-07-08 06:00 | 2.0577 | 2.2077 | 2.7406 | 2.8827 | 3.0248 | 2024-05-08 06:00 | 2.6559 | 3.0957 | 3.0957 | 3.0957 | 3.0957
2024-07-08 07:00 | 2.4387 | 2.6166 | 3.2481 | 3.4166 | 3.585 | 2024-05-08 07:00 | 3.2161 | 3.7486 | 3.7486 | 3.7486 | 3.7486
2024-07-08 08:00 | 2.4768 | 2.6574 | 3.2989 | 3.4699 | 3.641 | 2024-05-08 08:00 | 3.4485 | 4.0195 | 4.0195 | 4.0195 | 4.0195
2024-07-08 09:00 | 2.4578 | 2.637 | 3.2735 | 3.4433 | 3.613 | 2024-05-08 09:00 | 3.6771 | 4.286 | 4.286 | 4.286 | 4.286
2024-07-08 10:00 | 2.3054 | 2.4735 | 3.0705 | 3.2297 | 3.3889 | 2024-05-08 10:00 | 3.5323 | 4.1173 | 4.1173 | 4.1173 | 4.1173
2024-07-08 11:00 | 2.2482 | 2.4121 | 2.9944 | 3.1496 | 3.3049 | 2024-05-08 11:00 | 3.3723 | 3.9307 | 3.9307 | 3.9307 | 3.9307
2024-07-08 12:00 | 2.172 | 2.3304 | 2.8929 | 3.0429 | 3.1929 | 2024-05-08 12:00 | 3.2466 | 3.7841 | 3.7841 | 3.7841 | 3.7841
2024-07-08 13:00 | 2.4006 | 2.5757 | 3.1974 | 3.3632 | 3.529 | 2024-05-08 13:00 | 3.3799 | 3.9396 | 3.9396 | 3.9396 | 3.9396
2024-07-08 14:00 | 2.3244 | 2.4939 | 3.0959 | 3.2564 | 3.4169 | 2024-05-08 14:00 | 3.3304 | 3.8819 | 3.8819 | 3.8819 | 3.8819
2024-07-08 15:00 | 2.2673 | 2.4326 | 3.0198 | 3.1763 | 3.3329 | 2024-05-08 15:00 | 3.2046 | 3.7353 | 3.7353 | 3.7353 | 3.7353
2024-07-08 16:00 | 2.2482 | 2.4121 | 2.9944 | 3.1496 | 3.3049 | 2024-05-08 16:00 | 3.4066 | 3.9707 | 3.9707 | 3.9707 | 3.9707
2024-07-08 17:00 | 2.2101 | 2.3713 | 2.9436 | 3.0963 | 3.2489 | 2024-05-08 17:00 | 3.3875 | 3.9485 | 3.9485 | 3.9485 | 3.9485
2024-07-08 18:00 | 2.172 | 2.3304 | 2.8929 | 3.0429 | 3.1929 | 2024-05-08 18:00 | 2.9913 | 3.4866 | 3.4866 | 3.4866 | 3.4866
2024-07-08 19:00 | 1.829 | 1.9624 | 2.4361 | 2.5624 | 2.6887 | 2024-05-08 19:00 | 2.7169 | 3.1668 | 3.1668 | 3.1668 | 3.1668
2024-07-08 20:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-05-08 20:00 | 2.6864 | 3.1312 | 3.1312 | 3.1312 | 3.1312
2024-07-08 21:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-05-08 21:00 | 2.4121 | 2.8115 | 2.8115 | 2.8115 | 2.8115
2024-07-08 22:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-05-08 22:00 | 1.8329 | 2.1364 | 2.1364 | 2.1364 | 2.1364
2024-07-08 23:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-05-08 23:00 | 1.8329 | 2.1364 | 2.1364 | 2.1364 | 2.1364
2024-07-09 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-05-09 | 1.6576 | 1.932 | 1.932 | 1.932 | 1.932
2024-07-09 01:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-05-09 01:00 | 1.7224 | 2.0076 | 2.0076 | 2.0076 | 2.0076
2024-07-09 02:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-05-09 02:00 | 1.7338 | 2.0209 | 2.0209 | 2.0209 | 2.0209
2024-07-09 03:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-05-09 03:00 | 1.6842 | 1.9631 | 1.9631 | 1.9631 | 1.9631
2024-07-09 04:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-05-09 04:00 | 1.9967 | 2.3273 | 2.3273 | 2.3273 | 2.3273
2024-07-09 05:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-05-09 05:00 | 2.393 | 2.7893 | 2.7893 | 2.7893 | 2.7893
2024-07-09 06:00 | 1.9243 | 2.0646 | 2.563 | 2.6959 | 2.8288 | 2024-05-09 06:00 | 2.4806 | 2.8914 | 2.8914 | 2.8914 | 2.8914
2024-07-09 07:00 | 2.3625 | 2.5348 | 3.1466 | 3.3098 | 3.473 | 2024-05-09 07:00 | 2.9455 | 3.4333 | 3.4333 | 3.4333 | 3.4333
2024-07-09 08:00 | 2.4197 | 2.5961 | 3.2228 | 3.3899 | 3.557 | 2024-05-09 08:00 | 3.5971 | 4.1928 | 4.1928 | 4.1928 | 4.1928
2024-07-09 09:00 | 2.3625 | 2.5348 | 3.1466 | 3.3098 | 3.473 | 2024-05-09 09:00 | 3.6619 | 4.2683 | 4.2683 | 4.2683 | 4.2683
2024-07-09 10:00 | 2.2673 | 2.4326 | 3.0198 | 3.1763 | 3.3329 | 2024-05-09 10:00 | 3.338 | 3.8907 | 3.8907 | 3.8907 | 3.8907
2024-07-09 11:00 | 2.2101 | 2.3713 | 2.9436 | 3.0963 | 3.2489 | 2024-05-09 11:00 | 3.4104 | 3.9751 | 3.9751 | 3.9751 | 3.9751
2024-07-09 12:00 | 2.3435 | 2.5144 | 3.1213 | 3.2831 | 3.4449 | 2024-05-09 12:00 | 3.5095 | 4.0906 | 4.0906 | 4.0906 | 4.0906
2024-07-09 13:00 | 2.2291 | 2.3917 | 2.969 | 3.123 | 3.2769 | 2024-05-09 13:00 | 3.5247 | 4.1084 | 4.1084 | 4.1084 | 4.1084
2024-07-09 14:00 | 2.2482 | 2.4121 | 2.9944 | 3.1496 | 3.3049 | 2024-05-09 14:00 | 3.338 | 3.8907 | 3.8907 | 3.8907 | 3.8907
2024-07-09 15:00 | 2.1148 | 2.2691 | 2.8167 | 2.9628 | 3.1089 | 2024-05-09 15:00 | 3.3571 | 3.913 | 3.913 | 3.913 | 3.913
2024-07-09 16:00 | 2.2101 | 2.3713 | 2.9436 | 3.0963 | 3.2489 | 2024-05-09 16:00 | 3.4828 | 4.0595 | 4.0595 | 4.0595 | 4.0595
2024-07-09 17:00 | 2.2673 | 2.4326 | 3.0198 | 3.1763 | 3.3329 | 2024-05-09 17:00 | 3.3761 | 3.9352 | 3.9352 | 3.9352 | 3.9352
2024-07-09 18:00 | 2.191 | 2.3508 | 2.9183 | 3.0696 | 3.2209 | 2024-05-09 18:00 | 3.2961 | 3.8419 | 3.8419 | 3.8419 | 3.8419
2024-07-09 19:00 | 1.8481 | 1.9829 | 2.4615 | 2.5891 | 2.7167 | 2024-05-09 19:00 | 2.7588 | 3.2156 | 3.2156 | 3.2156 | 3.2156
2024-07-09 20:00 | 1.7528 | 1.8807 | 2.3346 | 2.4557 | 2.5767 | 2024-05-09 20:00 | 2.6635 | 3.1046 | 3.1046 | 3.1046 | 3.1046
2024-07-09 21:00 | 1.829 | 1.9624 | 2.4361 | 2.5624 | 2.6887 | 2024-05-09 21:00 | 2.3739 | 2.767 | 2.767 | 2.767 | 2.767
2024-07-09 22:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-05-09 22:00 | 1.8062 | 2.1053 | 2.1053 | 2.1053 | 2.1053
2024-07-09 23:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-05-09 23:00 | 1.8176 | 2.1186 | 2.1186 | 2.1186 | 2.1186
2024-07-10 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-05-10 | 1.669 | 1.9454 | 1.9454 | 1.9454 | 1.9454
2024-07-10 01:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-05-10 01:00 | 1.65 | 1.9232 | 1.9232 | 1.9232 | 1.9232
2024-07-10 02:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-05-10 02:00 | 1.6347 | 1.9054 | 1.9054 | 1.9054 | 1.9054
2024-07-10 03:00 | 1.448 | 1.5536 | 1.9286 | 2.0286 | 2.1286 | 2024-05-10 03:00 | 1.7909 | 2.0875 | 2.0875 | 2.0875 | 2.0875
2024-07-10 04:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-05-10 04:00 | 2.0729 | 2.4162 | 2.4162 | 2.4162 | 2.4162
2024-07-10 05:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-05-10 05:00 | 2.3739 | 2.767 | 2.767 | 2.767 | 2.767
2024-07-10 06:00 | 2.0005 | 2.1464 | 2.6645 | 2.8026 | 2.9408 | 2024-05-10 06:00 | 2.5911 | 3.0202 | 3.0202 | 3.0202 | 3.0202
2024-07-10 07:00 | 2.4768 | 2.6574 | 3.2989 | 3.4699 | 3.641 | 2024-05-10 07:00 | 3.0903 | 3.602 | 3.602 | 3.602 | 3.602
2024-07-10 08:00 | 2.4768 | 2.6574 | 3.2989 | 3.4699 | 3.641 | 2024-05-10 08:00 | 3.4485 | 4.0195 | 4.0195 | 4.0195 | 4.0195
2024-07-10 09:00 | 2.4387 | 2.6166 | 3.2481 | 3.4166 | 3.585 | 2024-05-10 09:00 | 3.5628 | 4.1528 | 4.1528 | 4.1528 | 4.1528
2024-07-10 10:00 | 2.2482 | 2.4121 | 2.9944 | 3.1496 | 3.3049 | 2024-05-10 10:00 | 3.5323 | 4.1173 | 4.1173 | 4.1173 | 4.1173
2024-07-10 11:00 | 2.172 | 2.3304 | 2.8929 | 3.0429 | 3.1929 | 2024-05-10 11:00 | 3.6467 | 4.2505 | 4.2505 | 4.2505 | 4.2505
2024-07-10 12:00 | 2.0958 | 2.2486 | 2.7914 | 2.9361 | 3.0808 | 2024-05-10 12:00 | 3.6047 | 4.2016 | 4.2016 | 4.2016 | 4.2016
2024-07-10 13:00 | 2.1148 | 2.2691 | 2.8167 | 2.9628 | 3.1089 | 2024-05-10 13:00 | 3.7152 | 4.3304 | 4.3304 | 4.3304 | 4.3304
2024-07-10 14:00 | 2.1339 | 2.2895 | 2.8421 | 2.9895 | 3.1369 | 2024-05-10 14:00 | 3.5362 | 4.1217 | 4.1217 | 4.1217 | 4.1217
2024-07-10 15:00 | 2.1339 | 2.2895 | 2.8421 | 2.9895 | 3.1369 | 2024-05-10 15:00 | 3.6886 | 4.2994 | 4.2994 | 4.2994 | 4.2994
2024-07-10 16:00 | 2.2291 | 2.3917 | 2.969 | 3.123 | 3.2769 | 2024-05-10 16:00 | 3.681 | 4.2905 | 4.2905 | 4.2905 | 4.2905
2024-07-10 17:00 | 2.2101 | 2.3713 | 2.9436 | 3.0963 | 3.2489 | 2024-05-10 17:00 | 3.6962 | 4.3082 | 4.3082 | 4.3082 | 4.3082
2024-07-10 18:00 | 2.2482 | 2.4121 | 2.9944 | 3.1496 | 3.3049 | 2024-05-10 18:00 | 3.5133 | 4.0951 | 4.0951 | 4.0951 | 4.0951
2024-07-10 19:00 | 1.7719 | 1.9011 | 2.36 | 2.4823 | 2.6047 | 2024-05-10 19:00 | 3.0865 | 3.5976 | 3.5976 | 3.5976 | 3.5976
2024-07-10 20:00 | 1.8672 | 2.0033 | 2.4869 | 2.6158 | 2.7448 | 2024-05-10 20:00 | 2.7321 | 3.1845 | 3.1845 | 3.1845 | 3.1845
2024-07-10 21:00 | 1.7909 | 1.9215 | 2.3854 | 2.509 | 2.6327 | 2024-05-10 21:00 | 2.4121 | 2.8115 | 2.8115 | 2.8115 | 2.8115
2024-07-10 22:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-05-10 22:00 | 2.0424 | 2.3806 | 2.3806 | 2.3806 | 2.3806
2024-07-10 23:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-05-10 23:00 | 1.7871 | 2.0831 | 2.0831 | 2.0831 | 2.0831
2024-07-11 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-05-11 | 1.7071 | 1.9898 | 1.9898 | 1.9898 | 1.9898
2024-07-11 01:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-05-11 01:00 | 1.6118 | 1.8787 | 1.8787 | 1.8787 | 1.8787
2024-07-11 02:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-05-11 02:00 | 1.6195 | 1.8876 | 1.8876 | 1.8876 | 1.8876
2024-07-11 03:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-05-11 03:00 | 1.7262 | 2.012 | 2.012 | 2.012 | 2.012
2024-07-11 04:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-05-11 04:00 | 1.8938 | 2.2074 | 2.2074 | 2.2074 | 2.2074
2024-07-11 05:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-05-11 05:00 | 2.2634 | 2.6382 | 2.6382 | 2.6382 | 2.6382
2024-07-11 06:00 | 1.9434 | 2.0851 | 2.5884 | 2.7226 | 2.8568 | 2024-05-11 06:00 | 2.4387 | 2.8426 | 2.8426 | 2.8426 | 2.8426
2024-07-11 07:00 | 2.553 | 2.7392 | 3.4004 | 3.5767 | 3.753 | 2024-05-11 07:00 | 2.6064 | 3.038 | 3.038 | 3.038 | 3.038
2024-07-11 08:00 | 2.534 | 2.7188 | 3.375 | 3.55 | 3.725 | 2024-05-11 08:00 | 2.9036 | 3.3844 | 3.3844 | 3.3844 | 3.3844
2024-07-11 09:00 | 2.5721 | 2.7597 | 3.4258 | 3.6034 | 3.781 | 2024-05-11 09:00 | 3.1399 | 3.6598 | 3.6598 | 3.6598 | 3.6598
2024-07-11 10:00 | 2.4578 | 2.637 | 3.2735 | 3.4433 | 3.613 | 2024-05-11 10:00 | 3.1056 | 3.6198 | 3.6198 | 3.6198 | 3.6198
2024-07-11 11:00 | 2.4768 | 2.6574 | 3.2989 | 3.4699 | 3.641 | 2024-05-11 11:00 | 3.2199 | 3.7531 | 3.7531 | 3.7531 | 3.7531
2024-07-11 12:00 | 2.2863 | 2.453 | 3.0451 | 3.203 | 3.3609 | 2024-05-11 12:00 | 3.2923 | 3.8374 | 3.8374 | 3.8374 | 3.8374
2024-07-11 13:00 | 2.4578 | 2.637 | 3.2735 | 3.4433 | 3.613 | 2024-05-11 13:00 | 3.338 | 3.8907 | 3.8907 | 3.8907 | 3.8907
2024-07-11 14:00 | 2.2482 | 2.4121 | 2.9944 | 3.1496 | 3.3049 | 2024-05-11 14:00 | 3.2656 | 3.8064 | 3.8064 | 3.8064 | 3.8064
2024-07-11 15:00 | 2.191 | 2.3508 | 2.9183 | 3.0696 | 3.2209 | 2024-05-11 15:00 | 3.1475 | 3.6687 | 3.6687 | 3.6687 | 3.6687
2024-07-11 16:00 | 2.2482 | 2.4121 | 2.9944 | 3.1496 | 3.3049 | 2024-05-11 16:00 | 3.1132 | 3.6287 | 3.6287 | 3.6287 | 3.6287
2024-07-11 17:00 | 2.2101 | 2.3713 | 2.9436 | 3.0963 | 3.2489 | 2024-05-11 17:00 | 3.0217 | 3.5221 | 3.5221 | 3.5221 | 3.5221
2024-07-11 18:00 | 2.191 | 2.3508 | 2.9183 | 3.0696 | 3.2209 | 2024-05-11 18:00 | 2.9189 | 3.4022 | 3.4022 | 3.4022 | 3.4022
2024-07-11 19:00 | 1.7719 | 1.9011 | 2.36 | 2.4823 | 2.6047 | 2024-05-11 19:00 | 2.3473 | 2.736 | 2.736 | 2.736 | 2.736
2024-07-11 20:00 | 1.7719 | 1.9011 | 2.36 | 2.4823 | 2.6047 | 2024-05-11 20:00 | 2.3663 | 2.7582 | 2.7582 | 2.7582 | 2.7582
2024-07-11 21:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-05-11 21:00 | 2.1796 | 2.5405 | 2.5405 | 2.5405 | 2.5405
2024-07-11 22:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-05-11 22:00 | 1.8633 | 2.1719 | 2.1719 | 2.1719 | 2.1719
2024-07-11 23:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-05-11 23:00 | 1.7109 | 1.9942 | 1.9942 | 1.9942 | 1.9942
2024-07-12 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-05-12 | 1.6195 | 1.8876 | 1.8876 | 1.8876 | 1.8876
2024-07-12 01:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-05-12 01:00 | 1.6385 | 1.9098 | 1.9098 | 1.9098 | 1.9098
2024-07-12 02:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-05-12 02:00 | 1.7224 | 2.0076 | 2.0076 | 2.0076 | 2.0076
2024-07-12 03:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-05-12 03:00 | 1.7566 | 2.0475 | 2.0475 | 2.0475 | 2.0475
2024-07-12 04:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-05-12 04:00 | 1.9434 | 2.2652 | 2.2652 | 2.2652 | 2.2652
2024-07-12 05:00 | 1.7338 | 1.8602 | 2.3092 | 2.429 | 2.5487 | 2024-05-12 05:00 | 2.2673 | 2.6427 | 2.6427 | 2.6427 | 2.6427
2024-07-12 06:00 | 1.9624 | 2.1055 | 2.6137 | 2.7493 | 2.8848 | 2024-05-12 06:00 | 2.2749 | 2.6516 | 2.6516 | 2.6516 | 2.6516
2024-07-12 07:00 | 2.4768 | 2.6574 | 3.2989 | 3.4699 | 3.641 | 2024-05-12 07:00 | 2.5302 | 2.9491 | 2.9491 | 2.9491 | 2.9491
2024-07-12 08:00 | 2.4578 | 2.637 | 3.2735 | 3.4433 | 3.613 | 2024-05-12 08:00 | 2.7207 | 3.1712 | 3.1712 | 3.1712 | 3.1712
2024-07-12 09:00 | 2.4387 | 2.6166 | 3.2481 | 3.4166 | 3.585 | 2024-05-12 09:00 | 2.595 | 3.0247 | 3.0247 | 3.0247 | 3.0247
2024-07-12 10:00 | 2.3816 | 2.5552 | 3.172 | 3.3365 | 3.501 | 2024-05-12 10:00 | 2.9036 | 3.3844 | 3.3844 | 3.3844 | 3.3844
2024-07-12 11:00 | 2.2291 | 2.3917 | 2.969 | 3.123 | 3.2769 | 2024-05-12 11:00 | 2.8541 | 3.3267 | 3.3267 | 3.3267 | 3.3267
2024-07-12 12:00 | 2.172 | 2.3304 | 2.8929 | 3.0429 | 3.1929 | 2024-05-12 12:00 | 3.0408 | 3.5443 | 3.5443 | 3.5443 | 3.5443
2024-07-12 13:00 | 2.2291 | 2.3917 | 2.969 | 3.123 | 3.2769 | 2024-05-12 13:00 | 3.2085 | 3.7397 | 3.7397 | 3.7397 | 3.7397
2024-07-12 14:00 | 2.2291 | 2.3917 | 2.969 | 3.123 | 3.2769 | 2024-05-12 14:00 | 3.0675 | 3.5754 | 3.5754 | 3.5754 | 3.5754
2024-07-12 15:00 | 2.191 | 2.3508 | 2.9183 | 3.0696 | 3.2209 | 2024-05-12 15:00 | 2.8541 | 3.3267 | 3.3267 | 3.3267 | 3.3267
2024-07-12 16:00 | 2.172 | 2.3304 | 2.8929 | 3.0429 | 3.1929 | 2024-05-12 16:00 | 2.9189 | 3.4022 | 3.4022 | 3.4022 | 3.4022
2024-07-12 17:00 | 2.191 | 2.3508 | 2.9183 | 3.0696 | 3.2209 | 2024-05-12 17:00 | 2.9913 | 3.4866 | 3.4866 | 3.4866 | 3.4866
2024-07-12 18:00 | 2.191 | 2.3508 | 2.9183 | 3.0696 | 3.2209 | 2024-05-12 18:00 | 2.6483 | 3.0868 | 3.0868 | 3.0868 | 3.0868
2024-07-12 19:00 | 1.9243 | 2.0646 | 2.563 | 2.6959 | 2.8288 | 2024-05-12 19:00 | 2.6483 | 3.0868 | 3.0868 | 3.0868 | 3.0868
2024-07-12 20:00 | 1.829 | 1.9624 | 2.4361 | 2.5624 | 2.6887 | 2024-05-12 20:00 | 2.313 | 2.696 | 2.696 | 2.696 | 2.696
2024-07-12 21:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-05-12 21:00 | 2.2368 | 2.6072 | 2.6072 | 2.6072 | 2.6072
2024-07-12 22:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-05-12 22:00 | 2.0348 | 2.3718 | 2.3718 | 2.3718 | 2.3718
2024-07-12 23:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-05-12 23:00 | 1.9205 | 2.2385 | 2.2385 | 2.2385 | 2.2385
2024-07-13 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-05-13 | 1.7871 | 2.0831 | 2.0831 | 2.0831 | 2.0831
2024-07-13 01:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-05-13 01:00 | 1.6118 | 1.8787 | 1.8787 | 1.8787 | 1.8787
2024-07-13 02:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-05-13 02:00 | 1.6614 | 1.9365 | 1.9365 | 1.9365 | 1.9365
2024-07-13 03:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-05-13 03:00 | 1.7719 | 2.0653 | 2.0653 | 2.0653 | 2.0653
2024-07-13 04:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-05-13 04:00 | 2.191 | 2.5539 | 2.5539 | 2.5539 | 2.5539
2024-07-13 05:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-05-13 05:00 | 2.2863 | 2.6649 | 2.6649 | 2.6649 | 2.6649
2024-07-13 06:00 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 2024-05-13 06:00 | 2.5988 | 3.0291 | 3.0291 | 3.0291 | 3.0291
2024-07-13 07:00 | 1.7338 | 1.8602 | 2.3092 | 2.429 | 2.5487 | 2024-05-13 07:00 | 2.8579 | 3.3311 | 3.3311 | 3.3311 | 3.3311
2024-07-13 08:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-05-13 08:00 | 3.2313 | 3.7664 | 3.7664 | 3.7664 | 3.7664
2024-07-13 09:00 | 1.4099 | 1.5127 | 1.8778 | 1.9752 | 2.0726 | 2024-05-13 09:00 | 3.1589 | 3.682 | 3.682 | 3.682 | 3.682
2024-07-13 10:00 | 1.3718 | 1.4718 | 1.8271 | 1.9218 | 2.0166 | 2024-05-13 10:00 | 2.9112 | 3.3933 | 3.3933 | 3.3933 | 3.3933
2024-07-13 11:00 | 1.3718 | 1.4718 | 1.8271 | 1.9218 | 2.0166 | 2024-05-13 11:00 | 3.0294 | 3.531 | 3.531 | 3.531 | 3.531
2024-07-13 12:00 | 1.3718 | 1.4718 | 1.8271 | 1.9218 | 2.0166 | 2024-05-13 12:00 | 3.1742 | 3.6998 | 3.6998 | 3.6998 | 3.6998
2024-07-13 13:00 | 1.3337 | 1.4309 | 1.7763 | 1.8684 | 1.9605 | 2024-05-13 13:00 | 3.1665 | 3.6909 | 3.6909 | 3.6909 | 3.6909
2024-07-13 14:00 | 1.2003 | 1.2878 | 1.5987 | 1.6816 | 1.7645 | 2024-05-13 14:00 | 3.3685 | 3.9263 | 3.9263 | 3.9263 | 3.9263
2024-07-13 15:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-05-13 15:00 | 3.2656 | 3.8064 | 3.8064 | 3.8064 | 3.8064
2024-07-13 16:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-05-13 16:00 | 3.479 | 4.0551 | 4.0551 | 4.0551 | 4.0551
2024-07-13 17:00 | 1.7528 | 1.8807 | 2.3346 | 2.4557 | 2.5767 | 2024-05-13 17:00 | 3.399 | 3.9618 | 3.9618 | 3.9618 | 3.9618
2024-07-13 18:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-05-13 18:00 | 3.0484 | 3.5532 | 3.5532 | 3.5532 | 3.5532
2024-07-13 19:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-05-13 19:00 | 2.7702 | 3.229 | 3.229 | 3.229 | 3.229
2024-07-13 20:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-05-13 20:00 | 2.4654 | 2.8736 | 2.8736 | 2.8736 | 2.8736
2024-07-13 21:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-05-13 21:00 | 2.332 | 2.7182 | 2.7182 | 2.7182 | 2.7182
2024-07-13 22:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-05-13 22:00 | 1.8862 | 2.1985 | 2.1985 | 2.1985 | 2.1985
2024-07-13 23:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-05-13 23:00 | 1.81 | 2.1097 | 2.1097 | 2.1097 | 2.1097
2024-07-14 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-05-14 | 1.6919 | 1.972 | 1.972 | 1.972 | 1.972
2024-07-14 01:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-05-14 01:00 | 1.6423 | 1.9143 | 1.9143 | 1.9143 | 1.9143
2024-07-14 02:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-05-14 02:00 | 1.6423 | 1.9143 | 1.9143 | 1.9143 | 1.9143
2024-07-14 03:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-05-14 03:00 | 1.7033 | 1.9853 | 1.9853 | 1.9853 | 1.9853
2024-07-14 04:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-05-14 04:00 | 1.9967 | 2.3273 | 2.3273 | 2.3273 | 2.3273
2024-07-14 05:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-05-14 05:00 | 2.3282 | 2.7137 | 2.7137 | 2.7137 | 2.7137
2024-07-14 06:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-05-14 06:00 | 2.8693 | 3.3444 | 3.3444 | 3.3444 | 3.3444
2024-07-14 07:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-05-14 07:00 | 3.1056 | 3.6198 | 3.6198 | 3.6198 | 3.6198
2024-07-14 08:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-05-14 08:00 | 3.3647 | 3.9218 | 3.9218 | 3.9218 | 3.9218
2024-07-14 09:00 | 1.3527 | 1.4514 | 1.8017 | 1.8951 | 1.9885 | 2024-05-14 09:00 | 3.3418 | 3.8952 | 3.8952 | 3.8952 | 3.8952
2024-07-14 10:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-05-14 10:00 | 3.0675 | 3.5754 | 3.5754 | 3.5754 | 3.5754
2024-07-14 11:00 | 1.2384 | 1.3287 | 1.6494 | 1.735 | 1.8205 | 2024-05-14 11:00 | 3.0865 | 3.5976 | 3.5976 | 3.5976 | 3.5976
2024-07-14 12:00 | 1.3527 | 1.4514 | 1.8017 | 1.8951 | 1.9885 | 2024-05-14 12:00 | 3.0332 | 3.5354 | 3.5354 | 3.5354 | 3.5354
2024-07-14 13:00 | 1.086 | 1.1652 | 1.4464 | 1.5214 | 1.5964 | 2024-05-14 13:00 | 3.0827 | 3.5932 | 3.5932 | 3.5932 | 3.5932
2024-07-14 14:00 | 1.2765 | 1.3696 | 1.7002 | 1.7884 | 1.8765 | 2024-05-14 14:00 | 3.3456 | 3.8996 | 3.8996 | 3.8996 | 3.8996
2024-07-14 15:00 | 1.448 | 1.5536 | 1.9286 | 2.0286 | 2.1286 | 2024-05-14 15:00 | 3.2809 | 3.8241 | 3.8241 | 3.8241 | 3.8241
2024-07-14 16:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-05-14 16:00 | 3.4828 | 4.0595 | 4.0595 | 4.0595 | 4.0595
2024-07-14 17:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-05-14 17:00 | 3.4599 | 4.0329 | 4.0329 | 4.0329 | 4.0329
2024-07-14 18:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-05-14 18:00 | 3.2809 | 3.8241 | 3.8241 | 3.8241 | 3.8241
2024-07-14 19:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-05-14 19:00 | 2.9608 | 3.451 | 3.451 | 3.451 | 3.451
2024-07-14 20:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-05-14 20:00 | 2.8541 | 3.3267 | 3.3267 | 3.3267 | 3.3267
2024-07-14 21:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-05-14 21:00 | 2.4387 | 2.8426 | 2.8426 | 2.8426 | 2.8426
2024-07-14 22:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-05-14 22:00 | 2.1834 | 2.545 | 2.545 | 2.545 | 2.545
2024-07-14 23:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-05-14 23:00 | 2.0043 | 2.3362 | 2.3362 | 2.3362 | 2.3362
2024-07-15 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-05-15 | 1.8595 | 2.1674 | 2.1674 | 2.1674 | 2.1674
2024-07-15 01:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-05-15 01:00 | 1.8443 | 2.1497 | 2.1497 | 2.1497 | 2.1497
2024-07-15 02:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-05-15 02:00 | 1.8672 | 2.1763 | 2.1763 | 2.1763 | 2.1763
2024-07-15 03:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-05-15 03:00 | 1.9319 | 2.2518 | 2.2518 | 2.2518 | 2.2518
2024-07-15 04:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-05-15 04:00 | 2.3015 | 2.6827 | 2.6827 | 2.6827 | 2.6827
2024-07-15 05:00 | 1.829 | 1.9624 | 2.4361 | 2.5624 | 2.6887 | 2024-05-15 05:00 | 2.4463 | 2.8514 | 2.8514 | 2.8514 | 2.8514
2024-07-15 06:00 | 2.3244 | 2.4939 | 3.0959 | 3.2564 | 3.4169 | 2024-05-15 06:00 | 2.5378 | 2.958 | 2.958 | 2.958 | 2.958
2024-07-15 07:00 | 2.4959 | 2.6779 | 3.3243 | 3.4966 | 3.669 | 2024-05-15 07:00 | 3.0446 | 3.5487 | 3.5487 | 3.5487 | 3.5487
2024-07-15 08:00 | 2.5911 | 2.7801 | 3.4512 | 3.6301 | 3.809 | 2024-05-15 08:00 | 3.2351 | 3.7708 | 3.7708 | 3.7708 | 3.7708
2024-07-15 09:00 | 2.3816 | 2.5552 | 3.172 | 3.3365 | 3.501 | 2024-05-15 09:00 | 3.4561 | 4.0284 | 4.0284 | 4.0284 | 4.0284
2024-07-15 10:00 | 2.4768 | 2.6574 | 3.2989 | 3.4699 | 3.641 | 2024-05-15 10:00 | 3.4104 | 3.9751 | 3.9751 | 3.9751 | 3.9751
2024-07-15 11:00 | 2.3625 | 2.5348 | 3.1466 | 3.3098 | 3.473 | 2024-05-15 11:00 | 3.3799 | 3.9396 | 3.9396 | 3.9396 | 3.9396
2024-07-15 12:00 | 2.2291 | 2.3917 | 2.969 | 3.123 | 3.2769 | 2024-05-15 12:00 | 3.1056 | 3.6198 | 3.6198 | 3.6198 | 3.6198
2024-07-15 13:00 | 2.4006 | 2.5757 | 3.1974 | 3.3632 | 3.529 | 2024-05-15 13:00 | 3.0675 | 3.5754 | 3.5754 | 3.5754 | 3.5754
2024-07-15 14:00 | 2.2291 | 2.3917 | 2.969 | 3.123 | 3.2769 | 2024-05-15 14:00 | 3.3228 | 3.873 | 3.873 | 3.873 | 3.873
2024-07-15 15:00 | 2.2673 | 2.4326 | 3.0198 | 3.1763 | 3.3329 | 2024-05-15 15:00 | 3.3571 | 3.913 | 3.913 | 3.913 | 3.913
2024-07-15 16:00 | 2.4959 | 2.6779 | 3.3243 | 3.4966 | 3.669 | 2024-05-15 16:00 | 3.5514 | 4.1395 | 4.1395 | 4.1395 | 4.1395
2024-07-15 17:00 | 2.4387 | 2.6166 | 3.2481 | 3.4166 | 3.585 | 2024-05-15 17:00 | 3.5171 | 4.0995 | 4.0995 | 4.0995 | 4.0995
2024-07-15 18:00 | 2.3625 | 2.5348 | 3.1466 | 3.3098 | 3.473 | 2024-05-15 18:00 | 2.9913 | 3.4866 | 3.4866 | 3.4866 | 3.4866
2024-07-15 19:00 | 1.9053 | 2.0442 | 2.5376 | 2.6692 | 2.8008 | 2024-05-15 19:00 | 2.9379 | 3.4244 | 3.4244 | 3.4244 | 3.4244
2024-07-15 20:00 | 1.7909 | 1.9215 | 2.3854 | 2.509 | 2.6327 | 2024-05-15 20:00 | 2.6026 | 3.0335 | 3.0335 | 3.0335 | 3.0335
2024-07-15 21:00 | 1.7528 | 1.8807 | 2.3346 | 2.4557 | 2.5767 | 2024-05-15 21:00 | 2.5378 | 2.958 | 2.958 | 2.958 | 2.958
2024-07-15 22:00 | 1.7338 | 1.8602 | 2.3092 | 2.429 | 2.5487 | 2024-05-15 22:00 | 1.8824 | 2.1941 | 2.1941 | 2.1941 | 2.1941
2024-07-15 23:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-05-15 23:00 | 1.8672 | 2.1763 | 2.1763 | 2.1763 | 2.1763
2024-07-16 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-05-16 | 1.6461 | 1.9187 | 1.9187 | 1.9187 | 1.9187
2024-07-16 01:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-05-16 01:00 | 1.65 | 1.9232 | 1.9232 | 1.9232 | 1.9232
2024-07-16 02:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-05-16 02:00 | 1.6271 | 1.8965 | 1.8965 | 1.8965 | 1.8965
2024-07-16 03:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-05-16 03:00 | 1.8024 | 2.1008 | 2.1008 | 2.1008 | 2.1008
2024-07-16 04:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-05-16 04:00 | 1.951 | 2.274 | 2.274 | 2.274 | 2.274
2024-07-16 05:00 | 1.7909 | 1.9215 | 2.3854 | 2.509 | 2.6327 | 2024-05-16 05:00 | 2.252 | 2.6249 | 2.6249 | 2.6249 | 2.6249
2024-07-16 06:00 | 2.191 | 2.3508 | 2.9183 | 3.0696 | 3.2209 | 2024-05-16 06:00 | 2.5797 | 3.0069 | 3.0069 | 3.0069 | 3.0069
2024-07-16 07:00 | 2.5149 | 2.6983 | 3.3496 | 3.5233 | 3.697 | 2024-05-16 07:00 | 3.2313 | 3.7664 | 3.7664 | 3.7664 | 3.7664
2024-07-16 08:00 | 2.6102 | 2.8005 | 3.4765 | 3.6568 | 3.8371 | 2024-05-16 08:00 | 3.3837 | 3.944 | 3.944 | 3.944 | 3.944
2024-07-16 09:00 | 2.4578 | 2.637 | 3.2735 | 3.4433 | 3.613 | 2024-05-16 09:00 | 3.3837 | 3.944 | 3.944 | 3.944 | 3.944
2024-07-16 10:00 | 2.5149 | 2.6983 | 3.3496 | 3.5233 | 3.697 | 2024-05-16 10:00 | 3.5171 | 4.0995 | 4.0995 | 4.0995 | 4.0995
2024-07-16 11:00 | 2.2863 | 2.453 | 3.0451 | 3.203 | 3.3609 | 2024-05-16 11:00 | 3.4028 | 3.9662 | 3.9662 | 3.9662 | 3.9662
2024-07-16 12:00 | 2.2291 | 2.3917 | 2.969 | 3.123 | 3.2769 | 2024-05-16 12:00 | 3.4942 | 4.0728 | 4.0728 | 4.0728 | 4.0728
2024-07-16 13:00 | 2.3435 | 2.5144 | 3.1213 | 3.2831 | 3.4449 | 2024-05-16 13:00 | 3.3342 | 3.8863 | 3.8863 | 3.8863 | 3.8863
2024-07-16 14:00 | 2.3244 | 2.4939 | 3.0959 | 3.2564 | 3.4169 | 2024-05-16 14:00 | 3.3952 | 3.9574 | 3.9574 | 3.9574 | 3.9574
2024-07-16 15:00 | 2.3244 | 2.4939 | 3.0959 | 3.2564 | 3.4169 | 2024-05-16 15:00 | 3.3571 | 3.913 | 3.913 | 3.913 | 3.913
2024-07-16 16:00 | 2.3244 | 2.4939 | 3.0959 | 3.2564 | 3.4169 | 2024-05-16 16:00 | 3.5933 | 4.1883 | 4.1883 | 4.1883 | 4.1883
2024-07-16 17:00 | 2.2291 | 2.3917 | 2.969 | 3.123 | 3.2769 | 2024-05-16 17:00 | 3.5514 | 4.1395 | 4.1395 | 4.1395 | 4.1395
2024-07-16 18:00 | 2.1339 | 2.2895 | 2.8421 | 2.9895 | 3.1369 | 2024-05-16 18:00 | 3.3761 | 3.9352 | 3.9352 | 3.9352 | 3.9352
2024-07-16 19:00 | 1.829 | 1.9624 | 2.4361 | 2.5624 | 2.6887 | 2024-05-16 19:00 | 3.178 | 3.7042 | 3.7042 | 3.7042 | 3.7042
2024-07-16 20:00 | 1.7909 | 1.9215 | 2.3854 | 2.509 | 2.6327 | 2024-05-16 20:00 | 2.8693 | 3.3444 | 3.3444 | 3.3444 | 3.3444
2024-07-16 21:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-05-16 21:00 | 2.5721 | 2.998 | 2.998 | 2.998 | 2.998
2024-07-16 22:00 | 1.7338 | 1.8602 | 2.3092 | 2.429 | 2.5487 | 2024-05-16 22:00 | 2.2177 | 2.5849 | 2.5849 | 2.5849 | 2.5849
2024-07-16 23:00 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 2024-05-16 23:00 | 2.0577 | 2.3984 | 2.3984 | 2.3984 | 2.3984
2024-07-17 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-05-17 | 1.9243 | 2.243 | 2.243 | 2.243 | 2.243
2024-07-17 01:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-05-17 01:00 | 2.0767 | 2.4206 | 2.4206 | 2.4206 | 2.4206
2024-07-17 02:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-05-17 02:00 | 1.9243 | 2.243 | 2.243 | 2.243 | 2.243
2024-07-17 03:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-05-17 03:00 | 2.0767 | 2.4206 | 2.4206 | 2.4206 | 2.4206
2024-07-17 04:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-05-17 04:00 | 2.3358 | 2.7226 | 2.7226 | 2.7226 | 2.7226
2024-07-17 05:00 | 1.7719 | 1.9011 | 2.36 | 2.4823 | 2.6047 | 2024-05-17 05:00 | 2.6445 | 3.0824 | 3.0824 | 3.0824 | 3.0824
2024-07-17 06:00 | 2.0577 | 2.2077 | 2.7406 | 2.8827 | 3.0248 | 2024-05-17 06:00 | 2.8579 | 3.3311 | 3.3311 | 3.3311 | 3.3311
2024-07-17 07:00 | 2.3625 | 2.5348 | 3.1466 | 3.3098 | 3.473 | 2024-05-17 07:00 | 3.2809 | 3.8241 | 3.8241 | 3.8241 | 3.8241
2024-07-17 08:00 | 2.6674 | 2.8619 | 3.5527 | 3.7369 | 3.9211 | 2024-05-17 08:00 | 3.5819 | 4.175 | 4.175 | 4.175 | 4.175
2024-07-17 09:00 | 2.4006 | 2.5757 | 3.1974 | 3.3632 | 3.529 | 2024-05-17 09:00 | 3.7648 | 4.3882 | 4.3882 | 4.3882 | 4.3882
2024-07-17 10:00 | 2.0958 | 2.2486 | 2.7914 | 2.9361 | 3.0808 | 2024-05-17 10:00 | 3.4828 | 4.0595 | 4.0595 | 4.0595 | 4.0595
2024-07-17 11:00 | 2.1529 | 2.3099 | 2.8675 | 3.0162 | 3.1649 | 2024-05-17 11:00 | 3.0979 | 3.6109 | 3.6109 | 3.6109 | 3.6109
2024-07-17 12:00 | 2.2482 | 2.4121 | 2.9944 | 3.1496 | 3.3049 | 2024-05-17 12:00 | 3.1818 | 3.7086 | 3.7086 | 3.7086 | 3.7086
2024-07-17 13:00 | 2.2863 | 2.453 | 3.0451 | 3.203 | 3.3609 | 2024-05-17 13:00 | 3.2427 | 3.7797 | 3.7797 | 3.7797 | 3.7797
2024-07-17 14:00 | 2.2482 | 2.4121 | 2.9944 | 3.1496 | 3.3049 | 2024-05-17 14:00 | 3.2199 | 3.7531 | 3.7531 | 3.7531 | 3.7531
2024-07-17 15:00 | 2.2673 | 2.4326 | 3.0198 | 3.1763 | 3.3329 | 2024-05-17 15:00 | 3.3113 | 3.8597 | 3.8597 | 3.8597 | 3.8597
2024-07-17 16:00 | 2.3054 | 2.4735 | 3.0705 | 3.2297 | 3.3889 | 2024-05-17 16:00 | 3.5362 | 4.1217 | 4.1217 | 4.1217 | 4.1217
2024-07-17 17:00 | 2.3054 | 2.4735 | 3.0705 | 3.2297 | 3.3889 | 2024-05-17 17:00 | 3.6657 | 4.2727 | 4.2727 | 4.2727 | 4.2727
2024-07-17 18:00 | 2.2673 | 2.4326 | 3.0198 | 3.1763 | 3.3329 | 2024-05-17 18:00 | 3.4599 | 4.0329 | 4.0329 | 4.0329 | 4.0329
2024-07-17 19:00 | 2.0196 | 2.1668 | 2.6899 | 2.8293 | 2.9688 | 2024-05-17 19:00 | 3.037 | 3.5399 | 3.5399 | 3.5399 | 3.5399
2024-07-17 20:00 | 1.7338 | 1.8602 | 2.3092 | 2.429 | 2.5487 | 2024-05-17 20:00 | 2.8617 | 3.3356 | 3.3356 | 3.3356 | 3.3356
2024-07-17 21:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-05-17 21:00 | 2.332 | 2.7182 | 2.7182 | 2.7182 | 2.7182
2024-07-17 22:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-05-17 22:00 | 2.1034 | 2.4517 | 2.4517 | 2.4517 | 2.4517
2024-07-17 23:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-05-17 23:00 | 1.9853 | 2.314 | 2.314 | 2.314 | 2.314
2024-07-18 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 2024-05-18 | 1.6309 | 1.901 | 1.901 | 1.901 | 1.901
2024-07-18 01:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-05-18 01:00 | 1.5661 | 1.8255 | 1.8255 | 1.8255 | 1.8255
2024-07-18 02:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-05-18 02:00 | 1.5661 | 1.8255 | 1.8255 | 1.8255 | 1.8255
2024-07-18 03:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-05-18 03:00 | 1.7109 | 1.9942 | 1.9942 | 1.9942 | 1.9942
2024-07-18 04:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-05-18 04:00 | 1.8976 | 2.2119 | 2.2119 | 2.2119 | 2.2119
2024-07-18 05:00 | 1.81 | 1.942 | 2.4107 | 2.5357 | 2.6607 | 2024-05-18 05:00 | 2.1148 | 2.465 | 2.465 | 2.465 | 2.465
2024-07-18 06:00 | 2.0196 | 2.1668 | 2.6899 | 2.8293 | 2.9688 | 2024-05-18 06:00 | 2.3168 | 2.7004 | 2.7004 | 2.7004 | 2.7004
2024-07-18 07:00 | 2.4959 | 2.6779 | 3.3243 | 3.4966 | 3.669 | 2024-05-18 07:00 | 2.1529 | 2.5094 | 2.5094 | 2.5094 | 2.5094
2024-07-18 08:00 | 2.5911 | 2.7801 | 3.4512 | 3.6301 | 3.809 | 2024-05-18 08:00 | 1.8748 | 2.1852 | 2.1852 | 2.1852 | 2.1852
2024-07-18 09:00 | 2.6293 | 2.821 | 3.5019 | 3.6835 | 3.8651 | 2024-05-18 09:00 | 2.0615 | 2.4028 | 2.4028 | 2.4028 | 2.4028
2024-07-18 10:00 | 2.4768 | 2.6574 | 3.2989 | 3.4699 | 3.641 | 2024-05-18 10:00 | 1.9319 | 2.2518 | 2.2518 | 2.2518 | 2.2518
2024-07-18 11:00 | 2.0386 | 2.1873 | 2.7152 | 2.856 | 2.9968 | 2024-05-18 11:00 | 2.332 | 2.7182 | 2.7182 | 2.7182 | 2.7182
2024-07-18 12:00 | 2.3054 | 2.4735 | 3.0705 | 3.2297 | 3.3889 | 2024-05-18 12:00 | 2.191 | 2.5539 | 2.5539 | 2.5539 | 2.5539
2024-07-18 13:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-05-18 13:00 | 2.553 | 2.9758 | 2.9758 | 2.9758 | 2.9758
2024-07-18 14:00 | 1.9243 | 2.0646 | 2.563 | 2.6959 | 2.8288 | 2024-05-18 14:00 | 2.4578 | 2.8648 | 2.8648 | 2.8648 | 2.8648
2024-07-18 15:00 | 1.829 | 1.9624 | 2.4361 | 2.5624 | 2.6887 | 2024-05-18 15:00 | 2.3892 | 2.7848 | 2.7848 | 2.7848 | 2.7848
2024-07-18 16:00 | 2.2291 | 2.3917 | 2.969 | 3.123 | 3.2769 | 2024-05-18 16:00 | 2.5721 | 2.998 | 2.998 | 2.998 | 2.998
2024-07-18 17:00 | 2.4197 | 2.5961 | 3.2228 | 3.3899 | 3.557 | 2024-05-18 17:00 | 2.5264 | 2.9447 | 2.9447 | 2.9447 | 2.9447
2024-07-18 18:00 | 2.3625 | 2.5348 | 3.1466 | 3.3098 | 3.473 | 2024-05-18 18:00 | 2.1415 | 2.4961 | 2.4961 | 2.4961 | 2.4961
2024-07-18 19:00 | 1.9053 | 2.0442 | 2.5376 | 2.6692 | 2.8008 | 2024-05-18 19:00 | 1.9091 | 2.2252 | 2.2252 | 2.2252 | 2.2252
2024-07-18 20:00 | 1.7719 | 1.9011 | 2.36 | 2.4823 | 2.6047 | 2024-05-18 20:00 | 1.5737 | 1.8343 | 1.8343 | 1.8343 | 1.8343
2024-07-18 21:00 | 1.81 | 1.942 | 2.4107 | 2.5357 | 2.6607 | 2024-05-18 21:00 | 1.3718 | 1.5989 | 1.5989 | 1.5989 | 1.5989
2024-07-18 22:00 | 1.7528 | 1.8807 | 2.3346 | 2.4557 | 2.5767 | 2024-05-18 22:00 | 1.1584 | 1.3502 | 1.3502 | 1.3502 | 1.3502
2024-07-18 23:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-05-18 23:00 | 0.97168 | 1.1326 | 1.1326 | 1.1326 | 1.1326
2024-07-19 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-05-19 | 0.92214 | 1.0748 | 1.0748 | 1.0748 | 1.0748
2024-07-19 01:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-05-19 01:00 | 0.91071 | 1.0615 | 1.0615 | 1.0615 | 1.0615
2024-07-19 02:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-05-19 02:00 | 0.94501 | 1.1015 | 1.1015 | 1.1015 | 1.1015
2024-07-19 03:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-05-19 03:00 | 0.98692 | 1.1503 | 1.1503 | 1.1503 | 1.1503
2024-07-19 04:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-05-19 04:00 | 1.1851 | 1.3813 | 1.3813 | 1.3813 | 1.3813
2024-07-19 05:00 | 1.8672 | 2.0033 | 2.4869 | 2.6158 | 2.7448 | 2024-05-19 05:00 | 1.4328 | 1.67 | 1.67 | 1.67 | 1.67
2024-07-19 06:00 | 2.0386 | 2.1873 | 2.7152 | 2.856 | 2.9968 | 2024-05-19 06:00 | 1.4937 | 1.7411 | 1.7411 | 1.7411 | 1.7411
2024-07-19 07:00 | 2.3816 | 2.5552 | 3.172 | 3.3365 | 3.501 | 2024-05-19 07:00 | 1.5318 | 1.7855 | 1.7855 | 1.7855 | 1.7855
2024-07-19 08:00 | 2.6483 | 2.8414 | 3.5273 | 3.7102 | 3.8931 | 2024-05-19 08:00 | 1.9929 | 2.3229 | 2.3229 | 2.3229 | 2.3229
2024-07-19 09:00 | 2.3435 | 2.5144 | 3.1213 | 3.2831 | 3.4449 | 2024-05-19 09:00 | 2.1758 | 2.5361 | 2.5361 | 2.5361 | 2.5361
2024-07-19 10:00 | 2.2673 | 2.4326 | 3.0198 | 3.1763 | 3.3329 | 2024-05-19 10:00 | 2.092 | 2.4384 | 2.4384 | 2.4384 | 2.4384
2024-07-19 11:00 | 1.7528 | 1.8807 | 2.3346 | 2.4557 | 2.5767 | 2024-05-19 11:00 | 2.0767 | 2.4206 | 2.4206 | 2.4206 | 2.4206
2024-07-19 12:00 | 2.2863 | 2.453 | 3.0451 | 3.203 | 3.3609 | 2024-05-19 12:00 | 2.1377 | 2.4917 | 2.4917 | 2.4917 | 2.4917
2024-07-19 13:00 | 2.2673 | 2.4326 | 3.0198 | 3.1763 | 3.3329 | 2024-05-19 13:00 | 2.2177 | 2.5849 | 2.5849 | 2.5849 | 2.5849
2024-07-19 14:00 | 2.3435 | 2.5144 | 3.1213 | 3.2831 | 3.4449 | 2024-05-19 14:00 | 2.1834 | 2.545 | 2.545 | 2.545 | 2.545
2024-07-19 15:00 | 2.2863 | 2.453 | 3.0451 | 3.203 | 3.3609 | 2024-05-19 15:00 | 3.3075 | 3.8552 | 3.8552 | 3.8552 | 3.8552
2024-07-19 16:00 | 2.2482 | 2.4121 | 2.9944 | 3.1496 | 3.3049 | 2024-05-19 16:00 | 3.197 | 3.7264 | 3.7264 | 3.7264 | 3.7264
2024-07-19 17:00 | 2.4387 | 2.6166 | 3.2481 | 3.4166 | 3.585 | 2024-05-19 17:00 | 3.1551 | 3.6776 | 3.6776 | 3.6776 | 3.6776
2024-07-19 18:00 | 2.4387 | 2.6166 | 3.2481 | 3.4166 | 3.585 | 2024-05-19 18:00 | 2.9341 | 3.4199 | 3.4199 | 3.4199 | 3.4199
2024-07-19 19:00 | 1.8481 | 1.9829 | 2.4615 | 2.5891 | 2.7167 | 2024-05-19 19:00 | 2.4235 | 2.8248 | 2.8248 | 2.8248 | 2.8248
2024-07-19 20:00 | 1.7719 | 1.9011 | 2.36 | 2.4823 | 2.6047 | 2024-05-19 20:00 | 2.454 | 2.8603 | 2.8603 | 2.8603 | 2.8603
2024-07-19 21:00 | 1.7528 | 1.8807 | 2.3346 | 2.4557 | 2.5767 | 2024-05-19 21:00 | 2.111 | 2.4606 | 2.4606 | 2.4606 | 2.4606
2024-07-19 22:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-05-19 22:00 | 2.031 | 2.3673 | 2.3673 | 2.3673 | 2.3673
2024-07-19 23:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-05-19 23:00 | 1.7719 | 2.0653 | 2.0653 | 2.0653 | 2.0653
2024-07-20 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-05-20 | 1.7452 | 2.0342 | 2.0342 | 2.0342 | 2.0342
2024-07-20 01:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-05-20 01:00 | 1.6919 | 1.972 | 1.972 | 1.972 | 1.972
2024-07-20 02:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-05-20 02:00 | 1.6919 | 1.972 | 1.972 | 1.972 | 1.972
2024-07-20 03:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-05-20 03:00 | 1.8481 | 2.1541 | 2.1541 | 2.1541 | 2.1541
2024-07-20 04:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-05-20 04:00 | 2.0843 | 2.4295 | 2.4295 | 2.4295 | 2.4295
2024-07-20 05:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-05-20 05:00 | 2.3054 | 2.6871 | 2.6871 | 2.6871 | 2.6871
2024-07-20 06:00 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 2024-05-20 06:00 | 2.4921 | 2.9047 | 2.9047 | 2.9047 | 2.9047
2024-07-20 07:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-05-20 07:00 | 2.8807 | 3.3578 | 3.3578 | 3.3578 | 3.3578
2024-07-20 08:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-05-20 08:00 | 3.5133 | 4.0951 | 4.0951 | 4.0951 | 4.0951
2024-07-20 09:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-05-20 09:00 | 3.4409 | 4.0107 | 4.0107 | 4.0107 | 4.0107
2024-07-20 10:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-05-20 10:00 | 3.0522 | 3.5576 | 3.5576 | 3.5576 | 3.5576
2024-07-20 11:00 | 1.3337 | 1.4309 | 1.7763 | 1.8684 | 1.9605 | 2024-05-20 11:00 | 3.2809 | 3.8241 | 3.8241 | 3.8241 | 3.8241
2024-07-20 12:00 | 1.3337 | 1.4309 | 1.7763 | 1.8684 | 1.9605 | 2024-05-20 12:00 | 3.0865 | 3.5976 | 3.5976 | 3.5976 | 3.5976
2024-07-20 13:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-05-20 13:00 | 2.9531 | 3.4422 | 3.4422 | 3.4422 | 3.4422
2024-07-20 14:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-05-20 14:00 | 3.3723 | 3.9307 | 3.9307 | 3.9307 | 3.9307
2024-07-20 15:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-05-20 15:00 | 3.399 | 3.9618 | 3.9618 | 3.9618 | 3.9618
2024-07-20 16:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-05-20 16:00 | 3.3952 | 3.9574 | 3.9574 | 3.9574 | 3.9574
2024-07-20 17:00 | 1.8672 | 2.0033 | 2.4869 | 2.6158 | 2.7448 | 2024-05-20 17:00 | 3.3456 | 3.8996 | 3.8996 | 3.8996 | 3.8996
2024-07-20 18:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-05-20 18:00 | 3.0713 | 3.5798 | 3.5798 | 3.5798 | 3.5798
2024-07-20 19:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-05-20 19:00 | 2.8655 | 3.34 | 3.34 | 3.34 | 3.34
2024-07-20 20:00 | 1.7338 | 1.8602 | 2.3092 | 2.429 | 2.5487 | 2024-05-20 20:00 | 2.614 | 3.0469 | 3.0469 | 3.0469 | 3.0469
2024-07-20 21:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-05-20 21:00 | 2.4921 | 2.9047 | 2.9047 | 2.9047 | 2.9047
2024-07-20 22:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-05-20 22:00 | 1.8938 | 2.2074 | 2.2074 | 2.2074 | 2.2074
2024-07-20 23:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-05-20 23:00 | 1.8786 | 2.1897 | 2.1897 | 2.1897 | 2.1897
2024-07-21 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-05-21 | 1.6118 | 1.8787 | 1.8787 | 1.8787 | 1.8787
2024-07-21 01:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-05-21 01:00 | 1.6804 | 1.9587 | 1.9587 | 1.9587 | 1.9587
2024-07-21 02:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-05-21 02:00 | 1.6042 | 1.8699 | 1.8699 | 1.8699 | 1.8699
2024-07-21 03:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-05-21 03:00 | 1.7109 | 1.9942 | 1.9942 | 1.9942 | 1.9942
2024-07-21 04:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-05-21 04:00 | 2.0196 | 2.354 | 2.354 | 2.354 | 2.354
2024-07-21 05:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-05-21 05:00 | 2.2558 | 2.6294 | 2.6294 | 2.6294 | 2.6294
2024-07-21 06:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-05-21 06:00 | 2.7931 | 3.2556 | 3.2556 | 3.2556 | 3.2556
2024-07-21 07:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-05-21 07:00 | 3.3723 | 3.9307 | 3.9307 | 3.9307 | 3.9307
2024-07-21 08:00 | 1.4099 | 1.5127 | 1.8778 | 1.9752 | 2.0726 | 2024-05-21 08:00 | 3.5476 | 4.135 | 4.135 | 4.135 | 4.135
2024-07-21 09:00 | 1.2575 | 1.3492 | 1.6748 | 1.7617 | 1.8485 | 2024-05-21 09:00 | 3.479 | 4.0551 | 4.0551 | 4.0551 | 4.0551
2024-07-21 10:00 | 1.2765 | 1.3696 | 1.7002 | 1.7884 | 1.8765 | 2024-05-21 10:00 | 3.0675 | 3.5754 | 3.5754 | 3.5754 | 3.5754
2024-07-21 11:00 | 1.2003 | 1.2878 | 1.5987 | 1.6816 | 1.7645 | 2024-05-21 11:00 | 2.9951 | 3.491 | 3.491 | 3.491 | 3.491
2024-07-21 12:00 | 1.2384 | 1.3287 | 1.6494 | 1.735 | 1.8205 | 2024-05-21 12:00 | 3.0103 | 3.5088 | 3.5088 | 3.5088 | 3.5088
2024-07-21 13:00 | 1.2956 | 1.39 | 1.7256 | 1.815 | 1.9045 | 2024-05-21 13:00 | 2.9722 | 3.4644 | 3.4644 | 3.4644 | 3.4644
2024-07-21 14:00 | 1.2575 | 1.3492 | 1.6748 | 1.7617 | 1.8485 | 2024-05-21 14:00 | 3.1894 | 3.7175 | 3.7175 | 3.7175 | 3.7175
2024-07-21 15:00 | 1.4289 | 1.5331 | 1.9032 | 2.0019 | 2.1006 | 2024-05-21 15:00 | 3.2275 | 3.7619 | 3.7619 | 3.7619 | 3.7619
2024-07-21 16:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-05-21 16:00 | 3.6124 | 4.2105 | 4.2105 | 4.2105 | 4.2105
2024-07-21 17:00 | 1.7338 | 1.8602 | 2.3092 | 2.429 | 2.5487 | 2024-05-21 17:00 | 3.418 | 3.984 | 3.984 | 3.984 | 3.984
2024-07-21 18:00 | 1.81 | 1.942 | 2.4107 | 2.5357 | 2.6607 | 2024-05-21 18:00 | 3.1513 | 3.6731 | 3.6731 | 3.6731 | 3.6731
2024-07-21 19:00 | 1.7528 | 1.8807 | 2.3346 | 2.4557 | 2.5767 | 2024-05-21 19:00 | 2.8236 | 3.2911 | 3.2911 | 3.2911 | 3.2911
2024-07-21 20:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-05-21 20:00 | 2.5607 | 2.9847 | 2.9847 | 2.9847 | 2.9847
2024-07-21 21:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-05-21 21:00 | 2.4044 | 2.8026 | 2.8026 | 2.8026 | 2.8026
2024-07-21 22:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-05-21 22:00 | 1.8062 | 2.1053 | 2.1053 | 2.1053 | 2.1053
2024-07-21 23:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-05-21 23:00 | 1.9624 | 2.2874 | 2.2874 | 2.2874 | 2.2874
2024-07-22 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-05-22 | 1.7376 | 2.0253 | 2.0253 | 2.0253 | 2.0253
2024-07-22 01:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-05-22 01:00 | 1.6347 | 1.9054 | 1.9054 | 1.9054 | 1.9054
2024-07-22 02:00 | 1.448 | 1.5536 | 1.9286 | 2.0286 | 2.1286 | 2024-05-22 02:00 | 1.7147 | 1.9987 | 1.9987 | 1.9987 | 1.9987
2024-07-22 03:00 | 1.448 | 1.5536 | 1.9286 | 2.0286 | 2.1286 | 2024-05-22 03:00 | 1.7833 | 2.0786 | 2.0786 | 2.0786 | 2.0786
2024-07-22 04:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-05-22 04:00 | 2.0462 | 2.3851 | 2.3851 | 2.3851 | 2.3851
2024-07-22 05:00 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 2024-05-22 05:00 | 2.1987 | 2.5627 | 2.5627 | 2.5627 | 2.5627
2024-07-22 06:00 | 1.9053 | 2.0442 | 2.5376 | 2.6692 | 2.8008 | 2024-05-22 06:00 | 2.5226 | 2.9403 | 2.9403 | 2.9403 | 2.9403
2024-07-22 07:00 | 2.4959 | 2.6779 | 3.3243 | 3.4966 | 3.669 | 2024-05-22 07:00 | 3.3418 | 3.8952 | 3.8952 | 3.8952 | 3.8952
2024-07-22 08:00 | 2.5911 | 2.7801 | 3.4512 | 3.6301 | 3.809 | 2024-05-22 08:00 | 3.7191 | 4.3349 | 4.3349 | 4.3349 | 4.3349
2024-07-22 09:00 | 2.3816 | 2.5552 | 3.172 | 3.3365 | 3.501 | 2024-05-22 09:00 | 3.5971 | 4.1928 | 4.1928 | 4.1928 | 4.1928
2024-07-22 10:00 | 2.2673 | 2.4326 | 3.0198 | 3.1763 | 3.3329 | 2024-05-22 10:00 | 3.1361 | 3.6553 | 3.6553 | 3.6553 | 3.6553
2024-07-22 11:00 | 2.2101 | 2.3713 | 2.9436 | 3.0963 | 3.2489 | 2024-05-22 11:00 | 3.1894 | 3.7175 | 3.7175 | 3.7175 | 3.7175
2024-07-22 12:00 | 2.3054 | 2.4735 | 3.0705 | 3.2297 | 3.3889 | 2024-05-22 12:00 | 3.0827 | 3.5932 | 3.5932 | 3.5932 | 3.5932
2024-07-22 13:00 | 2.191 | 2.3508 | 2.9183 | 3.0696 | 3.2209 | 2024-05-22 13:00 | 3.3914 | 3.9529 | 3.9529 | 3.9529 | 3.9529
2024-07-22 14:00 | 1.9243 | 2.0646 | 2.563 | 2.6959 | 2.8288 | 2024-05-22 14:00 | 3.399 | 3.9618 | 3.9618 | 3.9618 | 3.9618
2024-07-22 15:00 | 2.0958 | 2.2486 | 2.7914 | 2.9361 | 3.0808 | 2024-05-22 15:00 | 3.6162 | 4.215 | 4.215 | 4.215 | 4.215
2024-07-22 16:00 | 2.2673 | 2.4326 | 3.0198 | 3.1763 | 3.3329 | 2024-05-22 16:00 | 3.6657 | 4.2727 | 4.2727 | 4.2727 | 4.2727
2024-07-22 17:00 | 2.3054 | 2.4735 | 3.0705 | 3.2297 | 3.3889 | 2024-05-22 17:00 | 3.6543 | 4.2594 | 4.2594 | 4.2594 | 4.2594
2024-07-22 18:00 | 2.2291 | 2.3917 | 2.969 | 3.123 | 3.2769 | 2024-05-22 18:00 | 3.2732 | 3.8152 | 3.8152 | 3.8152 | 3.8152
2024-07-22 19:00 | 1.829 | 1.9624 | 2.4361 | 2.5624 | 2.6887 | 2024-05-22 19:00 | 3.0598 | 3.5665 | 3.5665 | 3.5665 | 3.5665
2024-07-22 20:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-05-22 20:00 | 2.7131 | 3.1623 | 3.1623 | 3.1623 | 3.1623
2024-07-22 21:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-05-22 21:00 | 2.1987 | 2.5627 | 2.5627 | 2.5627 | 2.5627
2024-07-22 22:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-05-22 22:00 | 2.0081 | 2.3407 | 2.3407 | 2.3407 | 2.3407
2024-07-22 23:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-05-22 23:00 | 1.9738 | 2.3007 | 2.3007 | 2.3007 | 2.3007
2024-07-23 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-05-23 | 1.7452 | 2.0342 | 2.0342 | 2.0342 | 2.0342
2024-07-23 01:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-05-23 01:00 | 1.6919 | 1.972 | 1.972 | 1.972 | 1.972
2024-07-23 02:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-05-23 02:00 | 1.6919 | 1.972 | 1.972 | 1.972 | 1.972
2024-07-23 03:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-05-23 03:00 | 1.871 | 2.1808 | 2.1808 | 2.1808 | 2.1808
2024-07-23 04:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-05-23 04:00 | 2.1301 | 2.4828 | 2.4828 | 2.4828 | 2.4828
2024-07-23 05:00 | 1.8672 | 2.0033 | 2.4869 | 2.6158 | 2.7448 | 2024-05-23 05:00 | 2.4578 | 2.8648 | 2.8648 | 2.8648 | 2.8648
2024-07-23 06:00 | 2.0196 | 2.1668 | 2.6899 | 2.8293 | 2.9688 | 2024-05-23 06:00 | 2.8731 | 3.3489 | 3.3489 | 3.3489 | 3.3489
2024-07-23 07:00 | 2.5149 | 2.6983 | 3.3496 | 3.5233 | 3.697 | 2024-05-23 07:00 | 3.6086 | 4.2061 | 4.2061 | 4.2061 | 4.2061
2024-07-23 08:00 | 2.6102 | 2.8005 | 3.4765 | 3.6568 | 3.8371 | 2024-05-23 08:00 | 3.8372 | 4.4726 | 4.4726 | 4.4726 | 4.4726
2024-07-23 09:00 | 2.2863 | 2.453 | 3.0451 | 3.203 | 3.3609 | 2024-05-23 09:00 | 3.761 | 4.3837 | 4.3837 | 4.3837 | 4.3837
2024-07-23 10:00 | 2.5911 | 2.7801 | 3.4512 | 3.6301 | 3.809 | 2024-05-23 10:00 | 3.6086 | 4.2061 | 4.2061 | 4.2061 | 4.2061
2024-07-23 11:00 | 2.5911 | 2.7801 | 3.4512 | 3.6301 | 3.809 | 2024-05-23 11:00 | 3.5133 | 4.0951 | 4.0951 | 4.0951 | 4.0951
2024-07-23 12:00 | 2.5911 | 2.7801 | 3.4512 | 3.6301 | 3.809 | 2024-05-23 12:00 | 3.7229 | 4.3393 | 4.3393 | 4.3393 | 4.3393
2024-07-23 13:00 | 2.5911 | 2.7801 | 3.4512 | 3.6301 | 3.809 | 2024-05-23 13:00 | 3.6848 | 4.2949 | 4.2949 | 4.2949 | 4.2949
2024-07-23 14:00 | 2.5911 | 2.7801 | 3.4512 | 3.6301 | 3.809 | 2024-05-23 14:00 | 3.5247 | 4.1084 | 4.1084 | 4.1084 | 4.1084
2024-07-23 15:00 | 1.829 | 1.9624 | 2.4361 | 2.5624 | 2.6887 | 2024-05-23 15:00 | 3.5781 | 4.1706 | 4.1706 | 4.1706 | 4.1706
2024-07-23 16:00 | 2.172 | 2.3304 | 2.8929 | 3.0429 | 3.1929 | 2024-05-23 16:00 | 3.6124 | 4.2105 | 4.2105 | 4.2105 | 4.2105
2024-07-23 17:00 | 2.2101 | 2.3713 | 2.9436 | 3.0963 | 3.2489 | 2024-05-23 17:00 | 3.7724 | 4.3971 | 4.3971 | 4.3971 | 4.3971
2024-07-23 18:00 | 2.172 | 2.3304 | 2.8929 | 3.0429 | 3.1929 | 2024-05-23 18:00 | 3.178 | 3.7042 | 3.7042 | 3.7042 | 3.7042
2024-07-23 19:00 | 1.8672 | 2.0033 | 2.4869 | 2.6158 | 2.7448 | 2024-05-23 19:00 | 3.1094 | 3.6243 | 3.6243 | 3.6243 | 3.6243
2024-07-23 20:00 | 1.7338 | 1.8602 | 2.3092 | 2.429 | 2.5487 | 2024-05-23 20:00 | 2.8731 | 3.3489 | 3.3489 | 3.3489 | 3.3489
2024-07-23 21:00 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 2024-05-23 21:00 | 2.5759 | 3.0024 | 3.0024 | 3.0024 | 3.0024
2024-07-23 22:00 | 1.7528 | 1.8807 | 2.3346 | 2.4557 | 2.5767 | 2024-05-23 22:00 | 2.1225 | 2.4739 | 2.4739 | 2.4739 | 2.4739
2024-07-23 23:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-05-23 23:00 | 2.0424 | 2.3806 | 2.3806 | 2.3806 | 2.3806
2024-07-24 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-05-24 | 1.8672 | 2.1763 | 2.1763 | 2.1763 | 2.1763
2024-07-24 01:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-05-24 01:00 | 1.8557 | 2.163 | 2.163 | 2.163 | 2.163
2024-07-24 02:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-05-24 02:00 | 1.829 | 2.1319 | 2.1319 | 2.1319 | 2.1319
2024-07-24 03:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-05-24 03:00 | 1.9891 | 2.3185 | 2.3185 | 2.3185 | 2.3185
2024-07-24 04:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-05-24 04:00 | 2.1263 | 2.4783 | 2.4783 | 2.4783 | 2.4783
2024-07-24 05:00 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 2024-05-24 05:00 | 2.3054 | 2.6871 | 2.6871 | 2.6871 | 2.6871
2024-07-24 06:00 | 2.0386 | 2.1873 | 2.7152 | 2.856 | 2.9968 | 2024-05-24 06:00 | 2.6293 | 3.0646 | 3.0646 | 3.0646 | 3.0646
2024-07-24 07:00 | 2.534 | 2.7188 | 3.375 | 3.55 | 3.725 | 2024-05-24 07:00 | 3.4028 | 3.9662 | 3.9662 | 3.9662 | 3.9662
2024-07-24 08:00 | 2.6102 | 2.8005 | 3.4765 | 3.6568 | 3.8371 | 2024-05-24 08:00 | 3.5857 | 4.1794 | 4.1794 | 4.1794 | 4.1794
2024-07-24 09:00 | 2.3816 | 2.5552 | 3.172 | 3.3365 | 3.501 | 2024-05-24 09:00 | 3.6505 | 4.2549 | 4.2549 | 4.2549 | 4.2549
2024-07-24 10:00 | 2.1339 | 2.2895 | 2.8421 | 2.9895 | 3.1369 | 2024-05-24 10:00 | 3.3837 | 3.944 | 3.944 | 3.944 | 3.944
2024-07-24 11:00 | 2.0386 | 2.1873 | 2.7152 | 2.856 | 2.9968 | 2024-05-24 11:00 | 3.4638 | 4.0373 | 4.0373 | 4.0373 | 4.0373
2024-07-24 12:00 | 2.0005 | 2.1464 | 2.6645 | 2.8026 | 2.9408 | 2024-05-24 12:00 | 3.3799 | 3.9396 | 3.9396 | 3.9396 | 3.9396
2024-07-24 13:00 | 2.1148 | 2.2691 | 2.8167 | 2.9628 | 3.1089 | 2024-05-24 13:00 | 4.1192 | 4.8012 | 4.8012 | 4.8012 | 4.8012
2024-07-24 14:00 | 1.9815 | 2.126 | 2.6391 | 2.776 | 2.9128 | 2024-05-24 14:00 | 3.8334 | 4.4681 | 4.4681 | 4.4681 | 4.4681
2024-07-24 15:00 | 2.172 | 2.3304 | 2.8929 | 3.0429 | 3.1929 | 2024-05-24 15:00 | 3.8219 | 4.4548 | 4.4548 | 4.4548 | 4.4548
2024-07-24 16:00 | 2.2291 | 2.3917 | 2.969 | 3.123 | 3.2769 | 2024-05-24 16:00 | 3.6162 | 4.215 | 4.215 | 4.215 | 4.215
2024-07-24 17:00 | 2.2673 | 2.4326 | 3.0198 | 3.1763 | 3.3329 | 2024-05-24 17:00 | 3.7114 | 4.326 | 4.326 | 4.326 | 4.326
2024-07-24 18:00 | 2.2863 | 2.453 | 3.0451 | 3.203 | 3.3609 | 2024-05-24 18:00 | 3.5476 | 4.135 | 4.135 | 4.135 | 4.135
2024-07-24 19:00 | 2.0005 | 2.1464 | 2.6645 | 2.8026 | 2.9408 | 2024-05-24 19:00 | 3.0408 | 3.5443 | 3.5443 | 3.5443 | 3.5443
2024-07-24 20:00 | 1.7528 | 1.8807 | 2.3346 | 2.4557 | 2.5767 | 2024-05-24 20:00 | 2.7398 | 3.1934 | 3.1934 | 3.1934 | 3.1934
2024-07-24 21:00 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 2024-05-24 21:00 | 2.7474 | 3.2023 | 3.2023 | 3.2023 | 3.2023
2024-07-24 22:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-05-24 22:00 | 1.9091 | 2.2252 | 2.2252 | 2.2252 | 2.2252
2024-07-24 23:00 | 1.7338 | 1.8602 | 2.3092 | 2.429 | 2.5487 | 2024-05-24 23:00 | 1.951 | 2.274 | 2.274 | 2.274 | 2.274
2024-07-25 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-05-25 | 1.7414 | 2.0298 | 2.0298 | 2.0298 | 2.0298
2024-07-25 01:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-05-25 01:00 | 1.7757 | 2.0697 | 2.0697 | 2.0697 | 2.0697
2024-07-25 02:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-05-25 02:00 | 1.7033 | 1.9853 | 1.9853 | 1.9853 | 1.9853
2024-07-25 03:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-05-25 03:00 | 1.8672 | 2.1763 | 2.1763 | 2.1763 | 2.1763
2024-07-25 04:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-05-25 04:00 | 1.9777 | 2.3051 | 2.3051 | 2.3051 | 2.3051
2024-07-25 05:00 | 1.7909 | 1.9215 | 2.3854 | 2.509 | 2.6327 | 2024-05-25 05:00 | 2.2482 | 2.6205 | 2.6205 | 2.6205 | 2.6205
2024-07-25 06:00 | 2.0577 | 2.2077 | 2.7406 | 2.8827 | 3.0248 | 2024-05-25 06:00 | 2.3549 | 2.7448 | 2.7448 | 2.7448 | 2.7448
2024-07-25 07:00 | 2.4197 | 2.5961 | 3.2228 | 3.3899 | 3.557 | 2024-05-25 07:00 | 2.6407 | 3.078 | 3.078 | 3.078 | 3.078
2024-07-25 08:00 | 2.3435 | 2.5144 | 3.1213 | 3.2831 | 3.4449 | 2024-05-25 08:00 | 2.915 | 3.3977 | 3.3977 | 3.3977 | 3.3977
2024-07-25 09:00 | 2.4197 | 2.5961 | 3.2228 | 3.3899 | 3.557 | 2024-05-25 09:00 | 2.9341 | 3.4199 | 3.4199 | 3.4199 | 3.4199
2024-07-25 10:00 | 2.0767 | 2.2282 | 2.766 | 2.9094 | 3.0528 | 2024-05-25 10:00 | 2.8922 | 3.3711 | 3.3711 | 3.3711 | 3.3711
2024-07-25 11:00 | 2.0577 | 2.2077 | 2.7406 | 2.8827 | 3.0248 | 2024-05-25 11:00 | 2.7702 | 3.229 | 3.229 | 3.229 | 3.229
2024-07-25 12:00 | 2.1529 | 2.3099 | 2.8675 | 3.0162 | 3.1649 | 2024-05-25 12:00 | 2.8579 | 3.3311 | 3.3311 | 3.3311 | 3.3311
2024-07-25 13:00 | 2.2101 | 2.3713 | 2.9436 | 3.0963 | 3.2489 | 2024-05-25 13:00 | 2.8312 | 3.3 | 3.3 | 3.3 | 3.3
2024-07-25 14:00 | 2.3435 | 2.5144 | 3.1213 | 3.2831 | 3.4449 | 2024-05-25 14:00 | 2.9608 | 3.451 | 3.451 | 3.451 | 3.451
2024-07-25 15:00 | 2.191 | 2.3508 | 2.9183 | 3.0696 | 3.2209 | 2024-05-25 15:00 | 2.9608 | 3.451 | 3.451 | 3.451 | 3.451
2024-07-25 16:00 | 2.172 | 2.3304 | 2.8929 | 3.0429 | 3.1929 | 2024-05-25 16:00 | 2.8884 | 3.3666 | 3.3666 | 3.3666 | 3.3666
2024-07-25 17:00 | 2.172 | 2.3304 | 2.8929 | 3.0429 | 3.1929 | 2024-05-25 17:00 | 3.0217 | 3.5221 | 3.5221 | 3.5221 | 3.5221
2024-07-25 18:00 | 2.191 | 2.3508 | 2.9183 | 3.0696 | 3.2209 | 2024-05-25 18:00 | 2.9189 | 3.4022 | 3.4022 | 3.4022 | 3.4022
2024-07-25 19:00 | 1.8672 | 2.0033 | 2.4869 | 2.6158 | 2.7448 | 2024-05-25 19:00 | 2.5607 | 2.9847 | 2.9847 | 2.9847 | 2.9847
2024-07-25 20:00 | 1.81 | 1.942 | 2.4107 | 2.5357 | 2.6607 | 2024-05-25 20:00 | 2.3168 | 2.7004 | 2.7004 | 2.7004 | 2.7004
2024-07-25 21:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-05-25 21:00 | 2.2025 | 2.5672 | 2.5672 | 2.5672 | 2.5672
2024-07-25 22:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-05-25 22:00 | 1.8824 | 2.1941 | 2.1941 | 2.1941 | 2.1941
2024-07-25 23:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-05-25 23:00 | 1.8252 | 2.1275 | 2.1275 | 2.1275 | 2.1275
2024-07-26 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-05-26 | 1.7719 | 2.0653 | 2.0653 | 2.0653 | 2.0653
2024-07-26 01:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-05-26 01:00 | 1.7071 | 1.9898 | 1.9898 | 1.9898 | 1.9898
2024-07-26 02:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-05-26 02:00 | 1.7071 | 1.9898 | 1.9898 | 1.9898 | 1.9898
2024-07-26 03:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-05-26 03:00 | 1.8938 | 2.2074 | 2.2074 | 2.2074 | 2.2074
2024-07-26 04:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-05-26 04:00 | 1.9853 | 2.314 | 2.314 | 2.314 | 2.314
2024-07-26 05:00 | 1.7528 | 1.8807 | 2.3346 | 2.4557 | 2.5767 | 2024-05-26 05:00 | 2.1834 | 2.545 | 2.545 | 2.545 | 2.545
2024-07-26 06:00 | 1.7719 | 1.9011 | 2.36 | 2.4823 | 2.6047 | 2024-05-26 06:00 | 2.3015 | 2.6827 | 2.6827 | 2.6827 | 2.6827
2024-07-26 07:00 | 2.5149 | 2.6983 | 3.3496 | 3.5233 | 3.697 | 2024-05-26 07:00 | 2.4768 | 2.887 | 2.887 | 2.887 | 2.887
2024-07-26 08:00 | 2.4387 | 2.6166 | 3.2481 | 3.4166 | 3.585 | 2024-05-26 08:00 | 2.6064 | 3.038 | 3.038 | 3.038 | 3.038
2024-07-26 09:00 | 2.2482 | 2.4121 | 2.9944 | 3.1496 | 3.3049 | 2024-05-26 09:00 | 2.9951 | 3.491 | 3.491 | 3.491 | 3.491
2024-07-26 10:00 | 2.0767 | 2.2282 | 2.766 | 2.9094 | 3.0528 | 2024-05-26 10:00 | 2.7702 | 3.229 | 3.229 | 3.229 | 3.229
2024-07-26 11:00 | 2.0005 | 2.1464 | 2.6645 | 2.8026 | 2.9408 | 2024-05-26 11:00 | 2.4502 | 2.8559 | 2.8559 | 2.8559 | 2.8559
2024-07-26 12:00 | 2.0386 | 2.1873 | 2.7152 | 2.856 | 2.9968 | 2024-05-26 12:00 | 2.6407 | 3.078 | 3.078 | 3.078 | 3.078
2024-07-26 13:00 | 1.9434 | 2.0851 | 2.5884 | 2.7226 | 2.8568 | 2024-05-26 13:00 | 2.7626 | 3.2201 | 3.2201 | 3.2201 | 3.2201
2024-07-26 14:00 | 2.0196 | 2.1668 | 2.6899 | 2.8293 | 2.9688 | 2024-05-26 14:00 | 2.7055 | 3.1535 | 3.1535 | 3.1535 | 3.1535
2024-07-26 15:00 | 2.1148 | 2.2691 | 2.8167 | 2.9628 | 3.1089 | 2024-05-26 15:00 | 2.9646 | 3.4555 | 3.4555 | 3.4555 | 3.4555
2024-07-26 16:00 | 2.0196 | 2.1668 | 2.6899 | 2.8293 | 2.9688 | 2024-05-26 16:00 | 3.0522 | 3.5576 | 3.5576 | 3.5576 | 3.5576
2024-07-26 17:00 | 2.172 | 2.3304 | 2.8929 | 3.0429 | 3.1929 | 2024-05-26 17:00 | 3.1018 | 3.6154 | 3.6154 | 3.6154 | 3.6154
2024-07-26 18:00 | 2.1339 | 2.2895 | 2.8421 | 2.9895 | 3.1369 | 2024-05-26 18:00 | 2.5607 | 2.9847 | 2.9847 | 2.9847 | 2.9847
2024-07-26 19:00 | 1.8672 | 2.0033 | 2.4869 | 2.6158 | 2.7448 | 2024-05-26 19:00 | 2.2787 | 2.656 | 2.656 | 2.656 | 2.656
2024-07-26 20:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-05-26 20:00 | 2.1377 | 2.4917 | 2.4917 | 2.4917 | 2.4917
2024-07-26 21:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-05-26 21:00 | 2.0805 | 2.4251 | 2.4251 | 2.4251 | 2.4251
2024-07-26 22:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-05-26 22:00 | 1.7871 | 2.0831 | 2.0831 | 2.0831 | 2.0831
2024-07-26 23:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-05-26 23:00 | 1.7338 | 2.0209 | 2.0209 | 2.0209 | 2.0209
2024-07-27 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-05-27 | 1.6576 | 1.932 | 1.932 | 1.932 | 1.932
2024-07-27 01:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-05-27 01:00 | 1.589 | 1.8521 | 1.8521 | 1.8521 | 1.8521
2024-07-27 02:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-05-27 02:00 | 1.6271 | 1.8965 | 1.8965 | 1.8965 | 1.8965
2024-07-27 03:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-05-27 03:00 | 1.7833 | 2.0786 | 2.0786 | 2.0786 | 2.0786
2024-07-27 04:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-05-27 04:00 | 1.9434 | 2.2652 | 2.2652 | 2.2652 | 2.2652
2024-07-27 05:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-05-27 05:00 | 2.3244 | 2.7093 | 2.7093 | 2.7093 | 2.7093
2024-07-27 06:00 | 1.7338 | 1.8602 | 2.3092 | 2.429 | 2.5487 | 2024-05-27 06:00 | 2.4997 | 2.9136 | 2.9136 | 2.9136 | 2.9136
2024-07-27 07:00 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 2024-05-27 07:00 | 2.6178 | 3.0513 | 3.0513 | 3.0513 | 3.0513
2024-07-27 08:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-05-27 08:00 | 3.1361 | 3.6553 | 3.6553 | 3.6553 | 3.6553
2024-07-27 09:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-05-27 09:00 | 3.2199 | 3.7531 | 3.7531 | 3.7531 | 3.7531
2024-07-27 10:00 | 1.2956 | 1.39 | 1.7256 | 1.815 | 1.9045 | 2024-05-27 10:00 | 3.0713 | 3.5798 | 3.5798 | 3.5798 | 3.5798
2024-07-27 11:00 | 1.086 | 1.1652 | 1.4464 | 1.5214 | 1.5964 | 2024-05-27 11:00 | 2.8807 | 3.3578 | 3.3578 | 3.3578 | 3.3578
2024-07-27 12:00 | 1.0098 | 1.0834 | 1.3449 | 1.4147 | 1.4844 | 2024-05-27 12:00 | 2.8083 | 3.2734 | 3.2734 | 3.2734 | 3.2734
2024-07-27 13:00 | 1.086 | 1.1652 | 1.4464 | 1.5214 | 1.5964 | 2024-05-27 13:00 | 2.7245 | 3.1757 | 3.1757 | 3.1757 | 3.1757
2024-07-27 14:00 | 0.97168 | 1.0425 | 1.2942 | 1.3613 | 1.4284 | 2024-05-27 14:00 | 2.9227 | 3.4066 | 3.4066 | 3.4066 | 3.4066
2024-07-27 15:00 | 1.3146 | 1.4105 | 1.751 | 1.8417 | 1.9325 | 2024-05-27 15:00 | 2.9074 | 3.3889 | 3.3889 | 3.3889 | 3.3889
2024-07-27 16:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-05-27 16:00 | 3.2504 | 3.7886 | 3.7886 | 3.7886 | 3.7886
2024-07-27 17:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-05-27 17:00 | 3.1894 | 3.7175 | 3.7175 | 3.7175 | 3.7175
2024-07-27 18:00 | 1.829 | 1.9624 | 2.4361 | 2.5624 | 2.6887 | 2024-05-27 18:00 | 2.9379 | 3.4244 | 3.4244 | 3.4244 | 3.4244
2024-07-27 19:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-05-27 19:00 | 2.7588 | 3.2156 | 3.2156 | 3.2156 | 3.2156
2024-07-27 20:00 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 2024-05-27 20:00 | 2.6521 | 3.0913 | 3.0913 | 3.0913 | 3.0913
2024-07-27 21:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-05-27 21:00 | 2.2025 | 2.5672 | 2.5672 | 2.5672 | 2.5672
2024-07-27 22:00 | 1.7338 | 1.8602 | 2.3092 | 2.429 | 2.5487 | 2024-05-27 22:00 | 1.9434 | 2.2652 | 2.2652 | 2.2652 | 2.2652
2024-07-27 23:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-05-27 23:00 | 1.8938 | 2.2074 | 2.2074 | 2.2074 | 2.2074
2024-07-28 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-05-28 | 1.7262 | 2.012 | 2.012 | 2.012 | 2.012
2024-07-28 01:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-05-28 01:00 | 1.7262 | 2.012 | 2.012 | 2.012 | 2.012
2024-07-28 02:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-05-28 02:00 | 1.81 | 2.1097 | 2.1097 | 2.1097 | 2.1097
2024-07-28 03:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-05-28 03:00 | 1.9129 | 2.2296 | 2.2296 | 2.2296 | 2.2296
2024-07-28 04:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-05-28 04:00 | 2.0158 | 2.3495 | 2.3495 | 2.3495 | 2.3495
2024-07-28 05:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-05-28 05:00 | 2.2787 | 2.656 | 2.656 | 2.656 | 2.656
2024-07-28 06:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-05-28 06:00 | 2.7474 | 3.2023 | 3.2023 | 3.2023 | 3.2023
2024-07-28 07:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-05-28 07:00 | 3.2427 | 3.7797 | 3.7797 | 3.7797 | 3.7797
2024-07-28 08:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-05-28 08:00 | 3.681 | 4.2905 | 4.2905 | 4.2905 | 4.2905
2024-07-28 09:00 | 1.3527 | 1.4514 | 1.8017 | 1.8951 | 1.9885 | 2024-05-28 09:00 | 3.3837 | 3.944 | 3.944 | 3.944 | 3.944
2024-07-28 10:00 | 0.41916 | 0.44972 | 0.55827 | 0.58722 | 0.61617 | 2024-05-28 10:00 | 3.338 | 3.8907 | 3.8907 | 3.8907 | 3.8907
2024-07-28 11:00 | 1.4099 | 1.5127 | 1.8778 | 1.9752 | 2.0726 | 2024-05-28 11:00 | 3.2123 | 3.7442 | 3.7442 | 3.7442 | 3.7442
2024-07-28 12:00 | 1.3908 | 1.4923 | 1.8525 | 1.9485 | 2.0446 | 2024-05-28 12:00 | 3.2618 | 3.8019 | 3.8019 | 3.8019 | 3.8019
2024-07-28 13:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-05-28 13:00 | 3.2046 | 3.7353 | 3.7353 | 3.7353 | 3.7353
2024-07-28 14:00 | 1.3527 | 1.4514 | 1.8017 | 1.8951 | 1.9885 | 2024-05-28 14:00 | 3.3456 | 3.8996 | 3.8996 | 3.8996 | 3.8996
2024-07-28 15:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-05-28 15:00 | 3.5743 | 4.1661 | 4.1661 | 4.1661 | 4.1661
2024-07-28 16:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-05-28 16:00 | 3.5704 | 4.1617 | 4.1617 | 4.1617 | 4.1617
2024-07-28 17:00 | 1.7528 | 1.8807 | 2.3346 | 2.4557 | 2.5767 | 2024-05-28 17:00 | 3.559 | 4.1483 | 4.1483 | 4.1483 | 4.1483
2024-07-28 18:00 | 1.7909 | 1.9215 | 2.3854 | 2.509 | 2.6327 | 2024-05-28 18:00 | 3.2542 | 3.793 | 3.793 | 3.793 | 3.793
2024-07-28 19:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-05-28 19:00 | 2.8769 | 3.3533 | 3.3533 | 3.3533 | 3.3533
2024-07-28 20:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-05-28 20:00 | 2.6674 | 3.109 | 3.109 | 3.109 | 3.109
2024-07-28 21:00 | 1.7338 | 1.8602 | 2.3092 | 2.429 | 2.5487 | 2024-05-28 21:00 | 2.4692 | 2.8781 | 2.8781 | 2.8781 | 2.8781
2024-07-28 22:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-05-28 22:00 | 2.1339 | 2.4872 | 2.4872 | 2.4872 | 2.4872
2024-07-28 23:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-05-28 23:00 | 2.0767 | 2.4206 | 2.4206 | 2.4206 | 2.4206
2024-07-29 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-05-29 | 1.8367 | 2.1408 | 2.1408 | 2.1408 | 2.1408
2024-07-29 01:00 | 1.7528 | 1.8807 | 2.3346 | 2.4557 | 2.5767 | 2024-05-29 01:00 | 1.9129 | 2.2296 | 2.2296 | 2.2296 | 2.2296
2024-07-29 02:00 | 1.7909 | 1.9215 | 2.3854 | 2.509 | 2.6327 | 2024-05-29 02:00 | 1.7986 | 2.0964 | 2.0964 | 2.0964 | 2.0964
2024-07-29 03:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-05-29 03:00 | 2.012 | 2.3451 | 2.3451 | 2.3451 | 2.3451
2024-07-29 04:00 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 2024-05-29 04:00 | 2.1949 | 2.5583 | 2.5583 | 2.5583 | 2.5583
2024-07-29 05:00 | 1.9624 | 2.1055 | 2.6137 | 2.7493 | 2.8848 | 2024-05-29 05:00 | 2.4654 | 2.8736 | 2.8736 | 2.8736 | 2.8736
2024-07-29 06:00 | 2.2291 | 2.3917 | 2.969 | 3.123 | 3.2769 | 2024-05-29 06:00 | 2.6597 | 3.1002 | 3.1002 | 3.1002 | 3.1002
2024-07-29 07:00 | 2.6293 | 2.821 | 3.5019 | 3.6835 | 3.8651 | 2024-05-29 07:00 | 3.3494 | 3.9041 | 3.9041 | 3.9041 | 3.9041
2024-07-29 08:00 | 2.7245 | 2.9232 | 3.6288 | 3.8169 | 4.0051 | 2024-05-29 08:00 | 3.4561 | 4.0284 | 4.0284 | 4.0284 | 4.0284
2024-07-29 09:00 | 2.5149 | 2.6983 | 3.3496 | 3.5233 | 3.697 | 2024-05-29 09:00 | 3.761 | 4.3837 | 4.3837 | 4.3837 | 4.3837
2024-07-29 10:00 | 2.3625 | 2.5348 | 3.1466 | 3.3098 | 3.473 | 2024-05-29 10:00 | 3.4561 | 4.0284 | 4.0284 | 4.0284 | 4.0284
2024-07-29 11:00 | 2.2863 | 2.453 | 3.0451 | 3.203 | 3.3609 | 2024-05-29 11:00 | 3.54 | 4.1261 | 4.1261 | 4.1261 | 4.1261
2024-07-29 12:00 | 2.191 | 2.3508 | 2.9183 | 3.0696 | 3.2209 | 2024-05-29 12:00 | 3.78 | 4.406 | 4.406 | 4.406 | 4.406
2024-07-29 13:00 | 2.2101 | 2.3713 | 2.9436 | 3.0963 | 3.2489 | 2024-05-29 13:00 | 3.418 | 3.984 | 3.984 | 3.984 | 3.984
2024-07-29 14:00 | 2.2101 | 2.3713 | 2.9436 | 3.0963 | 3.2489 | 2024-05-29 14:00 | 3.4218 | 3.9885 | 3.9885 | 3.9885 | 3.9885
2024-07-29 15:00 | 2.3816 | 2.5552 | 3.172 | 3.3365 | 3.501 | 2024-05-29 15:00 | 3.4066 | 3.9707 | 3.9707 | 3.9707 | 3.9707
2024-07-29 16:00 | 2.3054 | 2.4735 | 3.0705 | 3.2297 | 3.3889 | 2024-05-29 16:00 | 3.6771 | 4.286 | 4.286 | 4.286 | 4.286
2024-07-29 17:00 | 2.4387 | 2.6166 | 3.2481 | 3.4166 | 3.585 | 2024-05-29 17:00 | 3.5895 | 4.1839 | 4.1839 | 4.1839 | 4.1839
2024-07-29 18:00 | 2.553 | 2.7392 | 3.4004 | 3.5767 | 3.753 | 2024-05-29 18:00 | 3.3837 | 3.944 | 3.944 | 3.944 | 3.944
2024-07-29 19:00 | 1.9624 | 2.1055 | 2.6137 | 2.7493 | 2.8848 | 2024-05-29 19:00 | 2.9455 | 3.4333 | 3.4333 | 3.4333 | 3.4333
2024-07-29 20:00 | 1.9053 | 2.0442 | 2.5376 | 2.6692 | 2.8008 | 2024-05-29 20:00 | 2.6864 | 3.1312 | 3.1312 | 3.1312 | 3.1312
2024-07-29 21:00 | 1.7719 | 1.9011 | 2.36 | 2.4823 | 2.6047 | 2024-05-29 21:00 | 2.3854 | 2.7804 | 2.7804 | 2.7804 | 2.7804
2024-07-29 22:00 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 2024-05-29 22:00 | 2.0767 | 2.4206 | 2.4206 | 2.4206 | 2.4206
2024-07-29 23:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-05-29 23:00 | 1.9586 | 2.2829 | 2.2829 | 2.2829 | 2.2829
2024-07-30 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-05-30 | 1.8176 | 2.1186 | 2.1186 | 2.1186 | 2.1186
2024-07-30 01:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-05-30 01:00 | 1.7681 | 2.0609 | 2.0609 | 2.0609 | 2.0609
2024-07-30 02:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-05-30 02:00 | 1.7109 | 1.9942 | 1.9942 | 1.9942 | 1.9942
2024-07-30 03:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-05-30 03:00 | 1.8633 | 2.1719 | 2.1719 | 2.1719 | 2.1719
2024-07-30 04:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-05-30 04:00 | 2.111 | 2.4606 | 2.4606 | 2.4606 | 2.4606
2024-07-30 05:00 | 1.9053 | 2.0442 | 2.5376 | 2.6692 | 2.8008 | 2024-05-30 05:00 | 2.2368 | 2.6072 | 2.6072 | 2.6072 | 2.6072
2024-07-30 06:00 | 2.191 | 2.3508 | 2.9183 | 3.0696 | 3.2209 | 2024-05-30 06:00 | 2.4235 | 2.8248 | 2.8248 | 2.8248 | 2.8248
2024-07-30 07:00 | 2.553 | 2.7392 | 3.4004 | 3.5767 | 3.753 | 2024-05-30 07:00 | 3.178 | 3.7042 | 3.7042 | 3.7042 | 3.7042
2024-07-30 08:00 | 2.4959 | 2.6779 | 3.3243 | 3.4966 | 3.669 | 2024-05-30 08:00 | 3.6428 | 4.2461 | 4.2461 | 4.2461 | 4.2461
2024-07-30 09:00 | 2.2291 | 2.3917 | 2.969 | 3.123 | 3.2769 | 2024-05-30 09:00 | 3.7876 | 4.4148 | 4.4148 | 4.4148 | 4.4148
2024-07-30 10:00 | 1.8862 | 2.0237 | 2.5122 | 2.6425 | 2.7728 | 2024-05-30 10:00 | 3.3799 | 3.9396 | 3.9396 | 3.9396 | 3.9396
2024-07-30 11:00 | 2.0386 | 2.1873 | 2.7152 | 2.856 | 2.9968 | 2024-05-30 11:00 | 3.8181 | 4.4504 | 4.4504 | 4.4504 | 4.4504
2024-07-30 12:00 | 2.172 | 2.3304 | 2.8929 | 3.0429 | 3.1929 | 2024-05-30 12:00 | 3.559 | 4.1483 | 4.1483 | 4.1483 | 4.1483
2024-07-30 13:00 | 2.172 | 2.3304 | 2.8929 | 3.0429 | 3.1929 | 2024-05-30 13:00 | 3.8296 | 4.4637 | 4.4637 | 4.4637 | 4.4637
2024-07-30 14:00 | 1.9624 | 2.1055 | 2.6137 | 2.7493 | 2.8848 | 2024-05-30 14:00 | 3.9858 | 4.6458 | 4.6458 | 4.6458 | 4.6458
2024-07-30 15:00 | 2.1529 | 2.3099 | 2.8675 | 3.0162 | 3.1649 | 2024-05-30 15:00 | 3.6771 | 4.286 | 4.286 | 4.286 | 4.286
2024-07-30 16:00 | 2.2291 | 2.3917 | 2.969 | 3.123 | 3.2769 | 2024-05-30 16:00 | 3.7419 | 4.3615 | 4.3615 | 4.3615 | 4.3615
2024-07-30 17:00 | 2.2863 | 2.453 | 3.0451 | 3.203 | 3.3609 | 2024-05-30 17:00 | 3.7114 | 4.326 | 4.326 | 4.326 | 4.326
2024-07-30 18:00 | 2.2673 | 2.4326 | 3.0198 | 3.1763 | 3.3329 | 2024-05-30 18:00 | 3.1894 | 3.7175 | 3.7175 | 3.7175 | 3.7175
2024-07-30 19:00 | 1.8672 | 2.0033 | 2.4869 | 2.6158 | 2.7448 | 2024-05-30 19:00 | 2.976 | 3.4688 | 3.4688 | 3.4688 | 3.4688
2024-07-30 20:00 | 1.9053 | 2.0442 | 2.5376 | 2.6692 | 2.8008 | 2024-05-30 20:00 | 2.6216 | 3.0557 | 3.0557 | 3.0557 | 3.0557
2024-07-30 21:00 | 1.7338 | 1.8602 | 2.3092 | 2.429 | 2.5487 | 2024-05-30 21:00 | 2.3778 | 2.7715 | 2.7715 | 2.7715 | 2.7715
2024-07-30 22:00 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 2024-05-30 22:00 | 1.9205 | 2.2385 | 2.2385 | 2.2385 | 2.2385
2024-07-30 23:00 | 1.7338 | 1.8602 | 2.3092 | 2.429 | 2.5487 | 2024-05-30 23:00 | 1.8862 | 2.1985 | 2.1985 | 2.1985 | 2.1985
2024-07-31 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-05-31 | 1.7224 | 2.0076 | 2.0076 | 2.0076 | 2.0076
2024-07-31 01:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-05-31 01:00 | 1.73 | 2.0164 | 2.0164 | 2.0164 | 2.0164
2024-07-31 02:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-05-31 02:00 | 1.7605 | 2.052 | 2.052 | 2.052 | 2.052
2024-07-31 03:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-05-31 03:00 | 1.9281 | 2.2474 | 2.2474 | 2.2474 | 2.2474
2024-07-31 04:00 | 1.7528 | 1.8807 | 2.3346 | 2.4557 | 2.5767 | 2024-05-31 04:00 | 2.0424 | 2.3806 | 2.3806 | 2.3806 | 2.3806
2024-07-31 05:00 | 1.7909 | 1.9215 | 2.3854 | 2.509 | 2.6327 | 2024-05-31 05:00 | 2.2673 | 2.6427 | 2.6427 | 2.6427 | 2.6427
2024-07-31 06:00 | 2.0386 | 2.1873 | 2.7152 | 2.856 | 2.9968 | 2024-05-31 06:00 | 2.454 | 2.8603 | 2.8603 | 2.8603 | 2.8603
2024-07-31 07:00 | 2.6102 | 2.8005 | 3.4765 | 3.6568 | 3.8371 | 2024-05-31 07:00 | 3.1742 | 3.6998 | 3.6998 | 3.6998 | 3.6998
2024-07-31 08:00 | 2.3054 | 2.4735 | 3.0705 | 3.2297 | 3.3889 | 2024-05-31 08:00 | 3.8639 | 4.5037 | 4.5037 | 4.5037 | 4.5037
2024-07-31 09:00 | 2.172 | 2.3304 | 2.8929 | 3.0429 | 3.1929 | 2024-05-31 09:00 | 3.9324 | 4.5836 | 4.5836 | 4.5836 | 4.5836
2024-07-31 10:00 | 1.9815 | 2.126 | 2.6391 | 2.776 | 2.9128 | 2024-05-31 10:00 | 4.062 | 4.7346 | 4.7346 | 4.7346 | 4.7346
2024-07-31 11:00 | 1.8672 | 2.0033 | 2.4869 | 2.6158 | 2.7448 | 2024-05-31 11:00 | 4.0849 | 4.7613 | 4.7613 | 4.7613 | 4.7613
2024-07-31 12:00 | 2.3625 | 2.5348 | 3.1466 | 3.3098 | 3.473 | 2024-05-31 12:00 | 3.761 | 4.3837 | 4.3837 | 4.3837 | 4.3837
2024-07-31 13:00 | 2.1148 | 2.2691 | 2.8167 | 2.9628 | 3.1089 | 2024-05-31 13:00 | 3.4599 | 4.0329 | 4.0329 | 4.0329 | 4.0329
2024-07-31 14:00 | 2.1148 | 2.2691 | 2.8167 | 2.9628 | 3.1089 | 2024-05-31 14:00 | 3.4028 | 3.9662 | 3.9662 | 3.9662 | 3.9662
2024-07-31 15:00 | 2.2101 | 2.3713 | 2.9436 | 3.0963 | 3.2489 | 2024-05-31 15:00 | 3.4028 | 3.9662 | 3.9662 | 3.9662 | 3.9662
2024-07-31 16:00 | 2.2101 | 2.3713 | 2.9436 | 3.0963 | 3.2489 | 2024-05-31 16:00 | 3.6619 | 4.2683 | 4.2683 | 4.2683 | 4.2683
2024-07-31 17:00 | 2.2673 | 2.4326 | 3.0198 | 3.1763 | 3.3329 | 2024-05-31 17:00 | 3.7534 | 4.3749 | 4.3749 | 4.3749 | 4.3749
2024-07-31 18:00 | 2.2482 | 2.4121 | 2.9944 | 3.1496 | 3.3049 | 2024-05-31 18:00 | 3.5666 | 4.1572 | 4.1572 | 4.1572 | 4.1572
2024-07-31 19:00 | 2.0577 | 2.2077 | 2.7406 | 2.8827 | 3.0248 | 2024-05-31 19:00 | 3.277 | 3.8197 | 3.8197 | 3.8197 | 3.8197
2024-07-31 20:00 | 1.7338 | 1.8602 | 2.3092 | 2.429 | 2.5487 | 2024-05-31 20:00 | 2.8465 | 3.3178 | 3.3178 | 3.3178 | 3.3178
2024-07-31 21:00 | 1.7528 | 1.8807 | 2.3346 | 2.4557 | 2.5767 | 2024-05-31 21:00 | 2.6369 | 3.0735 | 3.0735 | 3.0735 | 3.0735
2024-07-31 22:00 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 2024-05-31 22:00 | 1.9396 | 2.2607 | 2.2607 | 2.2607 | 2.2607
2024-07-31 23:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-05-31 23:00 | 1.9662 | 2.2918 | 2.2918 | 2.2918 | 2.2918
2024-08-01 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-06-01 | 1.8176 | 2.1186 | 2.1186 | 2.1186 | 2.1186
2024-08-01 01:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-06-01 01:00 | 1.9319 | 2.2518 | 2.2518 | 2.2518 | 2.2518
2024-08-01 02:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-06-01 02:00 | 1.8024 | 2.1008 | 2.1008 | 2.1008 | 2.1008
2024-08-01 03:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-06-01 03:00 | 2.0272 | 2.3629 | 2.3629 | 2.3629 | 2.3629
2024-08-01 04:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-06-01 04:00 | 2.1606 | 2.5183 | 2.5183 | 2.5183 | 2.5183
2024-08-01 05:00 | 1.7528 | 1.8807 | 2.3346 | 2.4557 | 2.5767 | 2024-06-01 05:00 | 2.3968 | 2.7937 | 2.7937 | 2.7937 | 2.7937
2024-08-01 06:00 | 2.0005 | 2.1464 | 2.6645 | 2.8026 | 2.9408 | 2024-06-01 06:00 | 2.5645 | 2.9891 | 2.9891 | 2.9891 | 2.9891
2024-08-01 07:00 | 2.4197 | 2.5961 | 3.2228 | 3.3899 | 3.557 | 2024-06-01 07:00 | 2.7093 | 3.1579 | 3.1579 | 3.1579 | 3.1579
2024-08-01 08:00 | 2.4768 | 2.6574 | 3.2989 | 3.4699 | 3.641 | 2024-06-01 08:00 | 3.2847 | 3.8286 | 3.8286 | 3.8286 | 3.8286
2024-08-01 09:00 | 2.3244 | 2.4939 | 3.0959 | 3.2564 | 3.4169 | 2024-06-01 09:00 | 3.319 | 3.8685 | 3.8685 | 3.8685 | 3.8685
2024-08-01 10:00 | 2.0958 | 2.2486 | 2.7914 | 2.9361 | 3.0808 | 2024-06-01 10:00 | 3.1284 | 3.6465 | 3.6465 | 3.6465 | 3.6465
2024-08-01 11:00 | 2.0386 | 2.1873 | 2.7152 | 2.856 | 2.9968 | 2024-06-01 11:00 | 3.2732 | 3.8152 | 3.8152 | 3.8152 | 3.8152
2024-08-01 12:00 | 2.0005 | 2.1464 | 2.6645 | 2.8026 | 2.9408 | 2024-06-01 12:00 | 3.2961 | 3.8419 | 3.8419 | 3.8419 | 3.8419
2024-08-01 13:00 | 1.7909 | 1.9215 | 2.3854 | 2.509 | 2.6327 | 2024-06-01 13:00 | 3.2237 | 3.7575 | 3.7575 | 3.7575 | 3.7575
2024-08-01 14:00 | 1.8672 | 2.0033 | 2.4869 | 2.6158 | 2.7448 | 2024-06-01 14:00 | 3.2123 | 3.7442 | 3.7442 | 3.7442 | 3.7442
2024-08-01 15:00 | 2.2291 | 2.3917 | 2.969 | 3.123 | 3.2769 | 2024-06-01 15:00 | 3.197 | 3.7264 | 3.7264 | 3.7264 | 3.7264
2024-08-01 16:00 | 2.2673 | 2.4326 | 3.0198 | 3.1763 | 3.3329 | 2024-06-01 16:00 | 3.2618 | 3.8019 | 3.8019 | 3.8019 | 3.8019
2024-08-01 17:00 | 2.3054 | 2.4735 | 3.0705 | 3.2297 | 3.3889 | 2024-06-01 17:00 | 3.1551 | 3.6776 | 3.6776 | 3.6776 | 3.6776
2024-08-01 18:00 | 2.2863 | 2.453 | 3.0451 | 3.203 | 3.3609 | 2024-06-01 18:00 | 2.8998 | 3.38 | 3.38 | 3.38 | 3.38
2024-08-01 19:00 | 1.829 | 1.9624 | 2.4361 | 2.5624 | 2.6887 | 2024-06-01 19:00 | 2.6712 | 3.1135 | 3.1135 | 3.1135 | 3.1135
2024-08-01 20:00 | 1.7338 | 1.8602 | 2.3092 | 2.429 | 2.5487 | 2024-06-01 20:00 | 2.3282 | 2.7137 | 2.7137 | 2.7137 | 2.7137
2024-08-01 21:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-06-01 21:00 | 2.3054 | 2.6871 | 2.6871 | 2.6871 | 2.6871
2024-08-01 22:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-06-01 22:00 | 2.092 | 2.4384 | 2.4384 | 2.4384 | 2.4384
2024-08-01 23:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-06-01 23:00 | 1.8176 | 2.1186 | 2.1186 | 2.1186 | 2.1186
2024-08-02 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-06-02 | 1.7605 | 2.052 | 2.052 | 2.052 | 2.052
2024-08-02 01:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-06-02 01:00 | 1.8252 | 2.1275 | 2.1275 | 2.1275 | 2.1275
2024-08-02 02:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-06-02 02:00 | 1.749 | 2.0386 | 2.0386 | 2.0386 | 2.0386
2024-08-02 03:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-06-02 03:00 | 1.9472 | 2.2696 | 2.2696 | 2.2696 | 2.2696
2024-08-02 04:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-06-02 04:00 | 2.1034 | 2.4517 | 2.4517 | 2.4517 | 2.4517
2024-08-02 05:00 | 1.7528 | 1.8807 | 2.3346 | 2.4557 | 2.5767 | 2024-06-02 05:00 | 2.3397 | 2.7271 | 2.7271 | 2.7271 | 2.7271
2024-08-02 06:00 | 2.0386 | 2.1873 | 2.7152 | 2.856 | 2.9968 | 2024-06-02 06:00 | 2.5187 | 2.9358 | 2.9358 | 2.9358 | 2.9358
2024-08-02 07:00 | 2.4387 | 2.6166 | 3.2481 | 3.4166 | 3.585 | 2024-06-02 07:00 | 2.5607 | 2.9847 | 2.9847 | 2.9847 | 2.9847
2024-08-02 08:00 | 2.6293 | 2.821 | 3.5019 | 3.6835 | 3.8651 | 2024-06-02 08:00 | 2.8998 | 3.38 | 3.38 | 3.38 | 3.38
2024-08-02 09:00 | 2.4387 | 2.6166 | 3.2481 | 3.4166 | 3.585 | 2024-06-02 09:00 | 2.8274 | 3.2956 | 3.2956 | 3.2956 | 3.2956
2024-08-02 10:00 | 2.1529 | 2.3099 | 2.8675 | 3.0162 | 3.1649 | 2024-06-02 10:00 | 2.7855 | 3.2467 | 3.2467 | 3.2467 | 3.2467
2024-08-02 11:00 | 1.9815 | 2.126 | 2.6391 | 2.776 | 2.9128 | 2024-06-02 11:00 | 2.9303 | 3.4155 | 3.4155 | 3.4155 | 3.4155
2024-08-02 12:00 | 2.0196 | 2.1668 | 2.6899 | 2.8293 | 2.9688 | 2024-06-02 12:00 | 3.0751 | 3.5843 | 3.5843 | 3.5843 | 3.5843
2024-08-02 13:00 | 1.9624 | 2.1055 | 2.6137 | 2.7493 | 2.8848 | 2024-06-02 13:00 | 3.0865 | 3.5976 | 3.5976 | 3.5976 | 3.5976
2024-08-02 14:00 | 2.0005 | 2.1464 | 2.6645 | 2.8026 | 2.9408 | 2024-06-02 14:00 | 3.2237 | 3.7575 | 3.7575 | 3.7575 | 3.7575
2024-08-02 15:00 | 1.9815 | 2.126 | 2.6391 | 2.776 | 2.9128 | 2024-06-02 15:00 | 3.1703 | 3.6953 | 3.6953 | 3.6953 | 3.6953
2024-08-02 16:00 | 2.1339 | 2.2895 | 2.8421 | 2.9895 | 3.1369 | 2024-06-02 16:00 | 3.0522 | 3.5576 | 3.5576 | 3.5576 | 3.5576
2024-08-02 17:00 | 2.1529 | 2.3099 | 2.8675 | 3.0162 | 3.1649 | 2024-06-02 17:00 | 3.197 | 3.7264 | 3.7264 | 3.7264 | 3.7264
2024-08-02 18:00 | 2.191 | 2.3508 | 2.9183 | 3.0696 | 3.2209 | 2024-06-02 18:00 | 2.8846 | 3.3622 | 3.3622 | 3.3622 | 3.3622
2024-08-02 19:00 | 1.9434 | 2.0851 | 2.5884 | 2.7226 | 2.8568 | 2024-06-02 19:00 | 2.4654 | 2.8736 | 2.8736 | 2.8736 | 2.8736
2024-08-02 20:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-06-02 20:00 | 2.4883 | 2.9003 | 2.9003 | 2.9003 | 2.9003
2024-08-02 21:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-06-02 21:00 | 2.4159 | 2.8159 | 2.8159 | 2.8159 | 2.8159
2024-08-02 22:00 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 2024-06-02 22:00 | 2.0424 | 2.3806 | 2.3806 | 2.3806 | 2.3806
2024-08-02 23:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-06-02 23:00 | 1.9472 | 2.2696 | 2.2696 | 2.2696 | 2.2696
2024-08-03 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-06-03 | 1.7338 | 2.0209 | 2.0209 | 2.0209 | 2.0209
2024-08-03 01:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-06-03 01:00 | 1.7224 | 2.0076 | 2.0076 | 2.0076 | 2.0076
2024-08-03 02:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-06-03 02:00 | 1.7338 | 2.0209 | 2.0209 | 2.0209 | 2.0209
2024-08-03 03:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-06-03 03:00 | 1.9815 | 2.3096 | 2.3096 | 2.3096 | 2.3096
2024-08-03 04:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-06-03 04:00 | 2.2139 | 2.5805 | 2.5805 | 2.5805 | 2.5805
2024-08-03 05:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-06-03 05:00 | 2.3168 | 2.7004 | 2.7004 | 2.7004 | 2.7004
2024-08-03 06:00 | 1.81 | 1.942 | 2.4107 | 2.5357 | 2.6607 | 2024-06-03 06:00 | 2.6331 | 3.0691 | 3.0691 | 3.0691 | 3.0691
2024-08-03 07:00 | 1.829 | 1.9624 | 2.4361 | 2.5624 | 2.6887 | 2024-06-03 07:00 | 3.1818 | 3.7086 | 3.7086 | 3.7086 | 3.7086
2024-08-03 08:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-06-03 08:00 | 3.8524 | 4.4903 | 4.4903 | 4.4903 | 4.4903
2024-08-03 09:00 | 1.0098 | 1.0834 | 1.3449 | 1.4147 | 1.4844 | 2024-06-03 09:00 | 3.9782 | 4.6369 | 4.6369 | 4.6369 | 4.6369
2024-08-03 10:00 | 1.3146 | 1.4105 | 1.751 | 1.8417 | 1.9325 | 2024-06-03 10:00 | 3.8524 | 4.4903 | 4.4903 | 4.4903 | 4.4903
2024-08-03 11:00 | 1.2575 | 1.3492 | 1.6748 | 1.7617 | 1.8485 | 2024-06-03 11:00 | 3.6505 | 4.2549 | 4.2549 | 4.2549 | 4.2549
2024-08-03 12:00 | 1.2384 | 1.3287 | 1.6494 | 1.735 | 1.8205 | 2024-06-03 12:00 | 3.5781 | 4.1706 | 4.1706 | 4.1706 | 4.1706
2024-08-03 13:00 | 1.1622 | 1.247 | 1.5479 | 1.6282 | 1.7085 | 2024-06-03 13:00 | 3.3456 | 3.8996 | 3.8996 | 3.8996 | 3.8996
2024-08-03 14:00 | 1.0479 | 1.1243 | 1.3957 | 1.4681 | 1.5404 | 2024-06-03 14:00 | 3.3533 | 3.9085 | 3.9085 | 3.9085 | 3.9085
2024-08-03 15:00 | 1.2384 | 1.3287 | 1.6494 | 1.735 | 1.8205 | 2024-06-03 15:00 | 3.3837 | 3.944 | 3.944 | 3.944 | 3.944
2024-08-03 16:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-06-03 16:00 | 3.5133 | 4.0951 | 4.0951 | 4.0951 | 4.0951
2024-08-03 17:00 | 1.7528 | 1.8807 | 2.3346 | 2.4557 | 2.5767 | 2024-06-03 17:00 | 3.5514 | 4.1395 | 4.1395 | 4.1395 | 4.1395
2024-08-03 18:00 | 1.7338 | 1.8602 | 2.3092 | 2.429 | 2.5487 | 2024-06-03 18:00 | 3.4066 | 3.9707 | 3.9707 | 3.9707 | 3.9707
2024-08-03 19:00 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 2024-06-03 19:00 | 3.0065 | 3.5043 | 3.5043 | 3.5043 | 3.5043
2024-08-03 20:00 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 2024-06-03 20:00 | 2.8655 | 3.34 | 3.34 | 3.34 | 3.34
2024-08-03 21:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-06-03 21:00 | 2.3206 | 2.7049 | 2.7049 | 2.7049 | 2.7049
2024-08-03 22:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-06-03 22:00 | 1.9014 | 2.2163 | 2.2163 | 2.2163 | 2.2163
2024-08-03 23:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-06-03 23:00 | 1.8976 | 2.2119 | 2.2119 | 2.2119 | 2.2119
2024-08-04 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-06-04 | 1.7757 | 2.0697 | 2.0697 | 2.0697 | 2.0697
2024-08-04 01:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-06-04 01:00 | 1.871 | 2.1808 | 2.1808 | 2.1808 | 2.1808
2024-08-04 02:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-06-04 02:00 | 1.7414 | 2.0298 | 2.0298 | 2.0298 | 2.0298
2024-08-04 03:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-06-04 03:00 | 1.8557 | 2.163 | 2.163 | 2.163 | 2.163
2024-08-04 04:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-06-04 04:00 | 2.0691 | 2.4117 | 2.4117 | 2.4117 | 2.4117
2024-08-04 05:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-06-04 05:00 | 2.2863 | 2.6649 | 2.6649 | 2.6649 | 2.6649
2024-08-04 06:00 | 1.8672 | 2.0033 | 2.4869 | 2.6158 | 2.7448 | 2024-06-04 06:00 | 2.5492 | 2.9714 | 2.9714 | 2.9714 | 2.9714
2024-08-04 07:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-06-04 07:00 | 3.117 | 3.6331 | 3.6331 | 3.6331 | 3.6331
2024-08-04 08:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-06-04 08:00 | 3.6047 | 4.2016 | 4.2016 | 4.2016 | 4.2016
2024-08-04 09:00 | 1.2956 | 1.39 | 1.7256 | 1.815 | 1.9045 | 2024-06-04 09:00 | 3.6047 | 4.2016 | 4.2016 | 4.2016 | 4.2016
2024-08-04 10:00 | 1.2194 | 1.3083 | 1.6241 | 1.7083 | 1.7925 | 2024-06-04 10:00 | 3.5552 | 4.1439 | 4.1439 | 4.1439 | 4.1439
2024-08-04 11:00 | 1.2575 | 1.3492 | 1.6748 | 1.7617 | 1.8485 | 2024-06-04 11:00 | 3.5285 | 4.1128 | 4.1128 | 4.1128 | 4.1128
2024-08-04 12:00 | 1.3908 | 1.4923 | 1.8525 | 1.9485 | 2.0446 | 2024-06-04 12:00 | 3.7191 | 4.3349 | 4.3349 | 4.3349 | 4.3349
2024-08-04 13:00 | 1.448 | 1.5536 | 1.9286 | 2.0286 | 2.1286 | 2024-06-04 13:00 | 3.6848 | 4.2949 | 4.2949 | 4.2949 | 4.2949
2024-08-04 14:00 | 1.448 | 1.5536 | 1.9286 | 2.0286 | 2.1286 | 2024-06-04 14:00 | 3.3685 | 3.9263 | 3.9263 | 3.9263 | 3.9263
2024-08-04 15:00 | 1.448 | 1.5536 | 1.9286 | 2.0286 | 2.1286 | 2024-06-04 15:00 | 3.5133 | 4.0951 | 4.0951 | 4.0951 | 4.0951
2024-08-04 16:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-06-04 16:00 | 3.6352 | 4.2372 | 4.2372 | 4.2372 | 4.2372
2024-08-04 17:00 | 1.7528 | 1.8807 | 2.3346 | 2.4557 | 2.5767 | 2024-06-04 17:00 | 3.7953 | 4.4237 | 4.4237 | 4.4237 | 4.4237
2024-08-04 18:00 | 1.7338 | 1.8602 | 2.3092 | 2.429 | 2.5487 | 2024-06-04 18:00 | 3.2237 | 3.7575 | 3.7575 | 3.7575 | 3.7575
2024-08-04 19:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-06-04 19:00 | 2.8274 | 3.2956 | 3.2956 | 3.2956 | 3.2956
2024-08-04 20:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-06-04 20:00 | 2.5759 | 3.0024 | 3.0024 | 3.0024 | 3.0024
2024-08-04 21:00 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 2024-06-04 21:00 | 2.4616 | 2.8692 | 2.8692 | 2.8692 | 2.8692
2024-08-04 22:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-06-04 22:00 | 1.9586 | 2.2829 | 2.2829 | 2.2829 | 2.2829
2024-08-04 23:00 | 1.7719 | 1.9011 | 2.36 | 2.4823 | 2.6047 | 2024-06-04 23:00 | 2.0158 | 2.3495 | 2.3495 | 2.3495 | 2.3495
2024-08-05 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-06-05 | 1.9853 | 2.314 | 2.314 | 2.314 | 2.314
2024-08-05 01:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-06-05 01:00 | 1.8481 | 2.1541 | 2.1541 | 2.1541 | 2.1541
2024-08-05 02:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-06-05 02:00 | 1.829 | 2.1319 | 2.1319 | 2.1319 | 2.1319
2024-08-05 03:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-06-05 03:00 | 1.8786 | 2.1897 | 2.1897 | 2.1897 | 2.1897
2024-08-05 04:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-06-05 04:00 | 2.0805 | 2.4251 | 2.4251 | 2.4251 | 2.4251
2024-08-05 05:00 | 1.7719 | 1.9011 | 2.36 | 2.4823 | 2.6047 | 2024-06-05 05:00 | 2.3244 | 2.7093 | 2.7093 | 2.7093 | 2.7093
2024-08-05 06:00 | 2.0005 | 2.1464 | 2.6645 | 2.8026 | 2.9408 | 2024-06-05 06:00 | 2.6216 | 3.0557 | 3.0557 | 3.0557 | 3.0557
2024-08-05 07:00 | 2.534 | 2.7188 | 3.375 | 3.55 | 3.725 | 2024-06-05 07:00 | 3.0484 | 3.5532 | 3.5532 | 3.5532 | 3.5532
2024-08-05 08:00 | 2.7245 | 2.9232 | 3.6288 | 3.8169 | 4.0051 | 2024-06-05 08:00 | 3.7305 | 4.3482 | 4.3482 | 4.3482 | 4.3482
2024-08-05 09:00 | 2.6102 | 2.8005 | 3.4765 | 3.6568 | 3.8371 | 2024-06-05 09:00 | 3.7381 | 4.3571 | 4.3571 | 4.3571 | 4.3571
2024-08-05 10:00 | 2.5721 | 2.7597 | 3.4258 | 3.6034 | 3.781 | 2024-06-05 10:00 | 3.5895 | 4.1839 | 4.1839 | 4.1839 | 4.1839
2024-08-05 11:00 | 2.5149 | 2.6983 | 3.3496 | 3.5233 | 3.697 | 2024-06-05 11:00 | 3.7762 | 4.4015 | 4.4015 | 4.4015 | 4.4015
2024-08-05 12:00 | 2.4006 | 2.5757 | 3.1974 | 3.3632 | 3.529 | 2024-06-05 12:00 | 3.9896 | 4.6502 | 4.6502 | 4.6502 | 4.6502
2024-08-05 13:00 | 2.4578 | 2.637 | 3.2735 | 3.4433 | 3.613 | 2024-06-05 13:00 | 4.0048 | 4.668 | 4.668 | 4.668 | 4.668
2024-08-05 14:00 | 2.4959 | 2.6779 | 3.3243 | 3.4966 | 3.669 | 2024-06-05 14:00 | 3.9439 | 4.5969 | 4.5969 | 4.5969 | 4.5969
2024-08-05 15:00 | 2.4959 | 2.6779 | 3.3243 | 3.4966 | 3.669 | 2024-06-05 15:00 | 3.6505 | 4.2549 | 4.2549 | 4.2549 | 4.2549
2024-08-05 16:00 | 2.191 | 2.3508 | 2.9183 | 3.0696 | 3.2209 | 2024-06-05 16:00 | 3.6581 | 4.2638 | 4.2638 | 4.2638 | 4.2638
2024-08-05 17:00 | 2.2673 | 2.4326 | 3.0198 | 3.1763 | 3.3329 | 2024-06-05 17:00 | 3.7457 | 4.366 | 4.366 | 4.366 | 4.366
2024-08-05 18:00 | 2.3244 | 2.4939 | 3.0959 | 3.2564 | 3.4169 | 2024-06-05 18:00 | 3.4371 | 4.0062 | 4.0062 | 4.0062 | 4.0062
2024-08-05 19:00 | 1.9434 | 2.0851 | 2.5884 | 2.7226 | 2.8568 | 2024-06-05 19:00 | 3.0789 | 3.5887 | 3.5887 | 3.5887 | 3.5887
2024-08-05 20:00 | 1.9624 | 2.1055 | 2.6137 | 2.7493 | 2.8848 | 2024-06-05 20:00 | 2.7283 | 3.1801 | 3.1801 | 3.1801 | 3.1801
2024-08-05 21:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-06-05 21:00 | 2.5645 | 2.9891 | 2.9891 | 2.9891 | 2.9891
2024-08-05 22:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-06-05 22:00 | 2.2787 | 2.656 | 2.656 | 2.656 | 2.656
2024-08-05 23:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-06-05 23:00 | 2.2787 | 2.656 | 2.656 | 2.656 | 2.656
2024-08-06 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-06-06 | 1.9167 | 2.2341 | 2.2341 | 2.2341 | 2.2341
2024-08-06 01:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-06-06 01:00 | 1.9586 | 2.2829 | 2.2829 | 2.2829 | 2.2829
2024-08-06 02:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-06-06 02:00 | 1.951 | 2.274 | 2.274 | 2.274 | 2.274
2024-08-06 03:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-06-06 03:00 | 2.0005 | 2.3318 | 2.3318 | 2.3318 | 2.3318
2024-08-06 04:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-06-06 04:00 | 2.3015 | 2.6827 | 2.6827 | 2.6827 | 2.6827
2024-08-06 05:00 | 1.8481 | 1.9829 | 2.4615 | 2.5891 | 2.7167 | 2024-06-06 05:00 | 2.5149 | 2.9314 | 2.9314 | 2.9314 | 2.9314
2024-08-06 06:00 | 2.1529 | 2.3099 | 2.8675 | 3.0162 | 3.1649 | 2024-06-06 06:00 | 2.8388 | 3.3089 | 3.3089 | 3.3089 | 3.3089
2024-08-06 07:00 | 2.5149 | 2.6983 | 3.3496 | 3.5233 | 3.697 | 2024-06-06 07:00 | 3.2809 | 3.8241 | 3.8241 | 3.8241 | 3.8241
2024-08-06 08:00 | 2.6102 | 2.8005 | 3.4765 | 3.6568 | 3.8371 | 2024-06-06 08:00 | 3.902 | 4.5481 | 4.5481 | 4.5481 | 4.5481
2024-08-06 09:00 | 2.3244 | 2.4939 | 3.0959 | 3.2564 | 3.4169 | 2024-06-06 09:00 | 3.8143 | 4.4459 | 4.4459 | 4.4459 | 4.4459
2024-08-06 10:00 | 2.2291 | 2.3917 | 2.969 | 3.123 | 3.2769 | 2024-06-06 10:00 | 3.7114 | 4.326 | 4.326 | 4.326 | 4.326
2024-08-06 11:00 | 2.1148 | 2.2691 | 2.8167 | 2.9628 | 3.1089 | 2024-06-06 11:00 | 3.6924 | 4.3038 | 4.3038 | 4.3038 | 4.3038
2024-08-06 12:00 | 2.0577 | 2.2077 | 2.7406 | 2.8827 | 3.0248 | 2024-06-06 12:00 | 3.8296 | 4.4637 | 4.4637 | 4.4637 | 4.4637
2024-08-06 13:00 | 2.0196 | 2.1668 | 2.6899 | 2.8293 | 2.9688 | 2024-06-06 13:00 | 4.0048 | 4.668 | 4.668 | 4.668 | 4.668
2024-08-06 14:00 | 2.0386 | 2.1873 | 2.7152 | 2.856 | 2.9968 | 2024-06-06 14:00 | 3.4638 | 4.0373 | 4.0373 | 4.0373 | 4.0373
2024-08-06 15:00 | 2.1529 | 2.3099 | 2.8675 | 3.0162 | 3.1649 | 2024-06-06 15:00 | 3.5171 | 4.0995 | 4.0995 | 4.0995 | 4.0995
2024-08-06 16:00 | 2.191 | 2.3508 | 2.9183 | 3.0696 | 3.2209 | 2024-06-06 16:00 | 3.7991 | 4.4282 | 4.4282 | 4.4282 | 4.4282
2024-08-06 17:00 | 2.0958 | 2.2486 | 2.7914 | 2.9361 | 3.0808 | 2024-06-06 17:00 | 3.7915 | 4.4193 | 4.4193 | 4.4193 | 4.4193
2024-08-06 18:00 | 2.1339 | 2.2895 | 2.8421 | 2.9895 | 3.1369 | 2024-06-06 18:00 | 3.6009 | 4.1972 | 4.1972 | 4.1972 | 4.1972
2024-08-06 19:00 | 1.8481 | 1.9829 | 2.4615 | 2.5891 | 2.7167 | 2024-06-06 19:00 | 3.0103 | 3.5088 | 3.5088 | 3.5088 | 3.5088
2024-08-06 20:00 | 1.81 | 1.942 | 2.4107 | 2.5357 | 2.6607 | 2024-06-06 20:00 | 2.7741 | 3.2334 | 3.2334 | 3.2334 | 3.2334
2024-08-06 21:00 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 2024-06-06 21:00 | 2.6216 | 3.0557 | 3.0557 | 3.0557 | 3.0557
2024-08-06 22:00 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 2024-06-06 22:00 | 2.2406 | 2.6116 | 2.6116 | 2.6116 | 2.6116
2024-08-06 23:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-06-06 23:00 | 2.3358 | 2.7226 | 2.7226 | 2.7226 | 2.7226
2024-08-07 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-06-07 | 2.0958 | 2.4428 | 2.4428 | 2.4428 | 2.4428
2024-08-07 01:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-06-07 01:00 | 1.9929 | 2.3229 | 2.3229 | 2.3229 | 2.3229
2024-08-07 02:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-06-07 02:00 | 1.9205 | 2.2385 | 2.2385 | 2.2385 | 2.2385
2024-08-07 03:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-06-07 03:00 | 2.0386 | 2.3762 | 2.3762 | 2.3762 | 2.3762
2024-08-07 04:00 | 1.7338 | 1.8602 | 2.3092 | 2.429 | 2.5487 | 2024-06-07 04:00 | 2.233 | 2.6027 | 2.6027 | 2.6027 | 2.6027
2024-08-07 05:00 | 1.9434 | 2.0851 | 2.5884 | 2.7226 | 2.8568 | 2024-06-07 05:00 | 2.5988 | 3.0291 | 3.0291 | 3.0291 | 3.0291
2024-08-07 06:00 | 2.1339 | 2.2895 | 2.8421 | 2.9895 | 3.1369 | 2024-06-07 06:00 | 2.9874 | 3.4821 | 3.4821 | 3.4821 | 3.4821
2024-08-07 07:00 | 2.5149 | 2.6983 | 3.3496 | 3.5233 | 3.697 | 2024-06-07 07:00 | 3.3952 | 3.9574 | 3.9574 | 3.9574 | 3.9574
2024-08-07 08:00 | 2.4578 | 2.637 | 3.2735 | 3.4433 | 3.613 | 2024-06-07 08:00 | 3.7076 | 4.3216 | 4.3216 | 4.3216 | 4.3216
2024-08-07 09:00 | 2.3816 | 2.5552 | 3.172 | 3.3365 | 3.501 | 2024-06-07 09:00 | 3.8715 | 4.5126 | 4.5126 | 4.5126 | 4.5126
2024-08-07 10:00 | 2.172 | 2.3304 | 2.8929 | 3.0429 | 3.1929 | 2024-06-07 10:00 | 3.8448 | 4.4815 | 4.4815 | 4.4815 | 4.4815
2024-08-07 11:00 | 2.1148 | 2.2691 | 2.8167 | 2.9628 | 3.1089 | 2024-06-07 11:00 | 3.9591 | 4.6147 | 4.6147 | 4.6147 | 4.6147
2024-08-07 12:00 | 1.9815 | 2.126 | 2.6391 | 2.776 | 2.9128 | 2024-06-07 12:00 | 4.0201 | 4.6858 | 4.6858 | 4.6858 | 4.6858
2024-08-07 13:00 | 2.0005 | 2.1464 | 2.6645 | 2.8026 | 2.9408 | 2024-06-07 13:00 | 3.9058 | 4.5525 | 4.5525 | 4.5525 | 4.5525
2024-08-07 14:00 | 1.9815 | 2.126 | 2.6391 | 2.776 | 2.9128 | 2024-06-07 14:00 | 3.9629 | 4.6191 | 4.6191 | 4.6191 | 4.6191
2024-08-07 15:00 | 2.1148 | 2.2691 | 2.8167 | 2.9628 | 3.1089 | 2024-06-07 15:00 | 3.8524 | 4.4903 | 4.4903 | 4.4903 | 4.4903
2024-08-07 16:00 | 2.0767 | 2.2282 | 2.766 | 2.9094 | 3.0528 | 2024-06-07 16:00 | 4.001 | 4.6636 | 4.6636 | 4.6636 | 4.6636
2024-08-07 17:00 | 2.172 | 2.3304 | 2.8929 | 3.0429 | 3.1929 | 2024-06-07 17:00 | 3.8334 | 4.4681 | 4.4681 | 4.4681 | 4.4681
2024-08-07 18:00 | 2.1148 | 2.2691 | 2.8167 | 2.9628 | 3.1089 | 2024-06-07 18:00 | 3.6428 | 4.2461 | 4.2461 | 4.2461 | 4.2461
2024-08-07 19:00 | 1.829 | 1.9624 | 2.4361 | 2.5624 | 2.6887 | 2024-06-07 19:00 | 3.3228 | 3.873 | 3.873 | 3.873 | 3.873
2024-08-07 20:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-06-07 20:00 | 2.8617 | 3.3356 | 3.3356 | 3.3356 | 3.3356
2024-08-07 21:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-06-07 21:00 | 2.5835 | 3.0113 | 3.0113 | 3.0113 | 3.0113
2024-08-07 22:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-06-07 22:00 | 2.3435 | 2.7315 | 2.7315 | 2.7315 | 2.7315
2024-08-07 23:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-06-07 23:00 | 2.2711 | 2.6471 | 2.6471 | 2.6471 | 2.6471
2024-08-08 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-06-08 | 1.97 | 2.2962 | 2.2962 | 2.2962 | 2.2962
2024-08-08 01:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-06-08 01:00 | 1.9853 | 2.314 | 2.314 | 2.314 | 2.314
2024-08-08 02:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-06-08 02:00 | 2.0158 | 2.3495 | 2.3495 | 2.3495 | 2.3495
2024-08-08 03:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-06-08 03:00 | 2.0767 | 2.4206 | 2.4206 | 2.4206 | 2.4206
2024-08-08 04:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-06-08 04:00 | 2.172 | 2.5316 | 2.5316 | 2.5316 | 2.5316
2024-08-08 05:00 | 1.7338 | 1.8602 | 2.3092 | 2.429 | 2.5487 | 2024-06-08 05:00 | 2.5988 | 3.0291 | 3.0291 | 3.0291 | 3.0291
2024-08-08 06:00 | 2.191 | 2.3508 | 2.9183 | 3.0696 | 3.2209 | 2024-06-08 06:00 | 2.5569 | 2.9802 | 2.9802 | 2.9802 | 2.9802
2024-08-08 07:00 | 2.5149 | 2.6983 | 3.3496 | 3.5233 | 3.697 | 2024-06-08 07:00 | 2.534 | 2.9536 | 2.9536 | 2.9536 | 2.9536
2024-08-08 08:00 | 2.6864 | 2.8823 | 3.578 | 3.7636 | 3.9491 | 2024-06-08 08:00 | 3.0789 | 3.5887 | 3.5887 | 3.5887 | 3.5887
2024-08-08 09:00 | 2.4768 | 2.6574 | 3.2989 | 3.4699 | 3.641 | 2024-06-08 09:00 | 3.2237 | 3.7575 | 3.7575 | 3.7575 | 3.7575
2024-08-08 10:00 | 2.2863 | 2.453 | 3.0451 | 3.203 | 3.3609 | 2024-06-08 10:00 | 2.7588 | 3.2156 | 3.2156 | 3.2156 | 3.2156
2024-08-08 11:00 | 2.0767 | 2.2282 | 2.766 | 2.9094 | 3.0528 | 2024-06-08 11:00 | 3.1361 | 3.6553 | 3.6553 | 3.6553 | 3.6553
2024-08-08 12:00 | 2.1339 | 2.2895 | 2.8421 | 2.9895 | 3.1369 | 2024-06-08 12:00 | 2.8998 | 3.38 | 3.38 | 3.38 | 3.38
2024-08-08 13:00 | 2.172 | 2.3304 | 2.8929 | 3.0429 | 3.1929 | 2024-06-08 13:00 | 3.0713 | 3.5798 | 3.5798 | 3.5798 | 3.5798
2024-08-08 14:00 | 2.1529 | 2.3099 | 2.8675 | 3.0162 | 3.1649 | 2024-06-08 14:00 | 3.2999 | 3.8463 | 3.8463 | 3.8463 | 3.8463
2024-08-08 15:00 | 2.172 | 2.3304 | 2.8929 | 3.0429 | 3.1929 | 2024-06-08 15:00 | 3.2656 | 3.8064 | 3.8064 | 3.8064 | 3.8064
2024-08-08 16:00 | 2.1339 | 2.2895 | 2.8421 | 2.9895 | 3.1369 | 2024-06-08 16:00 | 3.3609 | 3.9174 | 3.9174 | 3.9174 | 3.9174
2024-08-08 17:00 | 2.172 | 2.3304 | 2.8929 | 3.0429 | 3.1929 | 2024-06-08 17:00 | 3.258 | 3.7975 | 3.7975 | 3.7975 | 3.7975
2024-08-08 18:00 | 2.1529 | 2.3099 | 2.8675 | 3.0162 | 3.1649 | 2024-06-08 18:00 | 3.0941 | 3.6065 | 3.6065 | 3.6065 | 3.6065
2024-08-08 19:00 | 1.7909 | 1.9215 | 2.3854 | 2.509 | 2.6327 | 2024-06-08 19:00 | 2.8274 | 3.2956 | 3.2956 | 3.2956 | 3.2956
2024-08-08 20:00 | 1.7528 | 1.8807 | 2.3346 | 2.4557 | 2.5767 | 2024-06-08 20:00 | 2.4806 | 2.8914 | 2.8914 | 2.8914 | 2.8914
2024-08-08 21:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-06-08 21:00 | 2.4273 | 2.8292 | 2.8292 | 2.8292 | 2.8292
2024-08-08 22:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-06-08 22:00 | 2.233 | 2.6027 | 2.6027 | 2.6027 | 2.6027
2024-08-08 23:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-06-08 23:00 | 2.1644 | 2.5228 | 2.5228 | 2.5228 | 2.5228
2024-08-09 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-06-09 | 1.9586 | 2.2829 | 2.2829 | 2.2829 | 2.2829
2024-08-09 01:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-06-09 01:00 | 1.9777 | 2.3051 | 2.3051 | 2.3051 | 2.3051
2024-08-09 02:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-06-09 02:00 | 1.9205 | 2.2385 | 2.2385 | 2.2385 | 2.2385
2024-08-09 03:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-06-09 03:00 | 1.9815 | 2.3096 | 2.3096 | 2.3096 | 2.3096
2024-08-09 04:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-06-09 04:00 | 2.1225 | 2.4739 | 2.4739 | 2.4739 | 2.4739
2024-08-09 05:00 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 2024-06-09 05:00 | 2.3168 | 2.7004 | 2.7004 | 2.7004 | 2.7004
2024-08-09 06:00 | 2.0005 | 2.1464 | 2.6645 | 2.8026 | 2.9408 | 2024-06-09 06:00 | 2.5988 | 3.0291 | 3.0291 | 3.0291 | 3.0291
2024-08-09 07:00 | 2.4387 | 2.6166 | 3.2481 | 3.4166 | 3.585 | 2024-06-09 07:00 | 2.6902 | 3.1357 | 3.1357 | 3.1357 | 3.1357
2024-08-09 08:00 | 2.553 | 2.7392 | 3.4004 | 3.5767 | 3.753 | 2024-06-09 08:00 | 2.9303 | 3.4155 | 3.4155 | 3.4155 | 3.4155
2024-08-09 09:00 | 2.4959 | 2.6779 | 3.3243 | 3.4966 | 3.669 | 2024-06-09 09:00 | 2.9646 | 3.4555 | 3.4555 | 3.4555 | 3.4555
2024-08-09 10:00 | 2.2863 | 2.453 | 3.0451 | 3.203 | 3.3609 | 2024-06-09 10:00 | 3.1627 | 3.6864 | 3.6864 | 3.6864 | 3.6864
2024-08-09 11:00 | 2.0577 | 2.2077 | 2.7406 | 2.8827 | 3.0248 | 2024-06-09 11:00 | 3.1818 | 3.7086 | 3.7086 | 3.7086 | 3.7086
2024-08-09 12:00 | 1.8862 | 2.0237 | 2.5122 | 2.6425 | 2.7728 | 2024-06-09 12:00 | 2.8503 | 3.3222 | 3.3222 | 3.3222 | 3.3222
2024-08-09 13:00 | 1.9815 | 2.126 | 2.6391 | 2.776 | 2.9128 | 2024-06-09 13:00 | 3.0255 | 3.5265 | 3.5265 | 3.5265 | 3.5265
2024-08-09 14:00 | 1.7338 | 1.8602 | 2.3092 | 2.429 | 2.5487 | 2024-06-09 14:00 | 2.9341 | 3.4199 | 3.4199 | 3.4199 | 3.4199
2024-08-09 15:00 | 1.9815 | 2.126 | 2.6391 | 2.776 | 2.9128 | 2024-06-09 15:00 | 3.0865 | 3.5976 | 3.5976 | 3.5976 | 3.5976
2024-08-09 16:00 | 2.0767 | 2.2282 | 2.766 | 2.9094 | 3.0528 | 2024-06-09 16:00 | 3.2542 | 3.793 | 3.793 | 3.793 | 3.793
2024-08-09 17:00 | 2.1148 | 2.2691 | 2.8167 | 2.9628 | 3.1089 | 2024-06-09 17:00 | 3.2199 | 3.7531 | 3.7531 | 3.7531 | 3.7531
2024-08-09 18:00 | 2.0386 | 2.1873 | 2.7152 | 2.856 | 2.9968 | 2024-06-09 18:00 | 2.8388 | 3.3089 | 3.3089 | 3.3089 | 3.3089
2024-08-09 19:00 | 1.81 | 1.942 | 2.4107 | 2.5357 | 2.6607 | 2024-06-09 19:00 | 2.5683 | 2.9936 | 2.9936 | 2.9936 | 2.9936
2024-08-09 20:00 | 1.7338 | 1.8602 | 2.3092 | 2.429 | 2.5487 | 2024-06-09 20:00 | 2.332 | 2.7182 | 2.7182 | 2.7182 | 2.7182
2024-08-09 21:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-06-09 21:00 | 2.2673 | 2.6427 | 2.6427 | 2.6427 | 2.6427
2024-08-09 22:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-06-09 22:00 | 2.1339 | 2.4872 | 2.4872 | 2.4872 | 2.4872
2024-08-09 23:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-06-09 23:00 | 2.252 | 2.6249 | 2.6249 | 2.6249 | 2.6249
2024-08-10 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-06-10 | 2.0615 | 2.4028 | 2.4028 | 2.4028 | 2.4028
2024-08-10 01:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-06-10 01:00 | 1.9319 | 2.2518 | 2.2518 | 2.2518 | 2.2518
2024-08-10 02:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-06-10 02:00 | 1.9548 | 2.2785 | 2.2785 | 2.2785 | 2.2785
2024-08-10 03:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-06-10 03:00 | 2.0729 | 2.4162 | 2.4162 | 2.4162 | 2.4162
2024-08-10 04:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-06-10 04:00 | 2.1834 | 2.545 | 2.545 | 2.545 | 2.545
2024-08-10 05:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-06-10 05:00 | 2.4425 | 2.847 | 2.847 | 2.847 | 2.847
2024-08-10 06:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-06-10 06:00 | 2.614 | 3.0469 | 3.0469 | 3.0469 | 3.0469
2024-08-10 07:00 | 1.7528 | 1.8807 | 2.3346 | 2.4557 | 2.5767 | 2024-06-10 07:00 | 2.8884 | 3.3666 | 3.3666 | 3.3666 | 3.3666
2024-08-10 08:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-06-10 08:00 | 2.9303 | 3.4155 | 3.4155 | 3.4155 | 3.4155
2024-08-10 09:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-06-10 09:00 | 2.9493 | 3.4377 | 3.4377 | 3.4377 | 3.4377
2024-08-10 10:00 | 1.3146 | 1.4105 | 1.751 | 1.8417 | 1.9325 | 2024-06-10 10:00 | 2.976 | 3.4688 | 3.4688 | 3.4688 | 3.4688
2024-08-10 11:00 | 1.1241 | 1.2061 | 1.4972 | 1.5748 | 1.6525 | 2024-06-10 11:00 | 2.9455 | 3.4333 | 3.4333 | 3.4333 | 3.4333
2024-08-10 12:00 | 1.0098 | 1.0834 | 1.3449 | 1.4147 | 1.4844 | 2024-06-10 12:00 | 2.9531 | 3.4422 | 3.4422 | 3.4422 | 3.4422
2024-08-10 13:00 | 1.2956 | 1.39 | 1.7256 | 1.815 | 1.9045 | 2024-06-10 13:00 | 3.0751 | 3.5843 | 3.5843 | 3.5843 | 3.5843
2024-08-10 14:00 | 1.3718 | 1.4718 | 1.8271 | 1.9218 | 2.0166 | 2024-06-10 14:00 | 3.1361 | 3.6553 | 3.6553 | 3.6553 | 3.6553
2024-08-10 15:00 | 1.4289 | 1.5331 | 1.9032 | 2.0019 | 2.1006 | 2024-06-10 15:00 | 3.2656 | 3.8064 | 3.8064 | 3.8064 | 3.8064
2024-08-10 16:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-06-10 16:00 | 3.3685 | 3.9263 | 3.9263 | 3.9263 | 3.9263
2024-08-10 17:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-06-10 17:00 | 3.4523 | 4.024 | 4.024 | 4.024 | 4.024
2024-08-10 18:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-06-10 18:00 | 3.0789 | 3.5887 | 3.5887 | 3.5887 | 3.5887
2024-08-10 19:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-06-10 19:00 | 2.6521 | 3.0913 | 3.0913 | 3.0913 | 3.0913
2024-08-10 20:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-06-10 20:00 | 2.5683 | 2.9936 | 2.9936 | 2.9936 | 2.9936
2024-08-10 21:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-06-10 21:00 | 2.3168 | 2.7004 | 2.7004 | 2.7004 | 2.7004
2024-08-10 22:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-06-10 22:00 | 2.0805 | 2.4251 | 2.4251 | 2.4251 | 2.4251
2024-08-10 23:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-06-10 23:00 | 2.0081 | 2.3407 | 2.3407 | 2.3407 | 2.3407
2024-08-11 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-06-11 | 1.9167 | 2.2341 | 2.2341 | 2.2341 | 2.2341
2024-08-11 01:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-06-11 01:00 | 1.8862 | 2.1985 | 2.1985 | 2.1985 | 2.1985
2024-08-11 02:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-06-11 02:00 | 1.9624 | 2.2874 | 2.2874 | 2.2874 | 2.2874
2024-08-11 03:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-06-11 03:00 | 2.092 | 2.4384 | 2.4384 | 2.4384 | 2.4384
2024-08-11 04:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-06-11 04:00 | 2.2558 | 2.6294 | 2.6294 | 2.6294 | 2.6294
2024-08-11 05:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-06-11 05:00 | 2.4578 | 2.8648 | 2.8648 | 2.8648 | 2.8648
2024-08-11 06:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-06-11 06:00 | 2.8617 | 3.3356 | 3.3356 | 3.3356 | 3.3356
2024-08-11 07:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-06-11 07:00 | 3.1437 | 3.6642 | 3.6642 | 3.6642 | 3.6642
2024-08-11 08:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-06-11 08:00 | 3.5514 | 4.1395 | 4.1395 | 4.1395 | 4.1395
2024-08-11 09:00 | 0.87642 | 0.94033 | 1.1673 | 1.2278 | 1.2884 | 2024-06-11 09:00 | 3.7076 | 4.3216 | 4.3216 | 4.3216 | 4.3216
2024-08-11 10:00 | 0.74305 | 0.79723 | 0.98967 | 1.041 | 1.0923 | 2024-06-11 10:00 | 3.6314 | 4.2327 | 4.2327 | 4.2327 | 4.2327
2024-08-11 11:00 | 1.1813 | 1.2674 | 1.5733 | 1.6549 | 1.7365 | 2024-06-11 11:00 | 3.9439 | 4.5969 | 4.5969 | 4.5969 | 4.5969
2024-08-11 12:00 | 0.85737 | 0.91989 | 1.1419 | 1.2011 | 1.2603 | 2024-06-11 12:00 | 3.9286 | 4.5792 | 4.5792 | 4.5792 | 4.5792
2024-08-11 13:00 | 1.1432 | 1.2265 | 1.5226 | 1.6015 | 1.6805 | 2024-06-11 13:00 | 3.8029 | 4.4326 | 4.4326 | 4.4326 | 4.4326
2024-08-11 14:00 | 0.60968 | 0.65414 | 0.81204 | 0.85414 | 0.89625 | 2024-06-11 14:00 | 3.7876 | 4.4148 | 4.4148 | 4.4148 | 4.4148
2024-08-11 15:00 | 0.80021 | 0.85856 | 1.0658 | 1.1211 | 1.1763 | 2024-06-11 15:00 | 3.6733 | 4.2816 | 4.2816 | 4.2816 | 4.2816
2024-08-11 16:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-06-11 16:00 | 3.78 | 4.406 | 4.406 | 4.406 | 4.406
2024-08-11 17:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-06-11 17:00 | 3.6238 | 4.2239 | 4.2239 | 4.2239 | 4.2239
2024-08-11 18:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-06-11 18:00 | 3.1627 | 3.6864 | 3.6864 | 3.6864 | 3.6864
2024-08-11 19:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-06-11 19:00 | 3.0294 | 3.531 | 3.531 | 3.531 | 3.531
2024-08-11 20:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-06-11 20:00 | 2.8465 | 3.3178 | 3.3178 | 3.3178 | 3.3178
2024-08-11 21:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-06-11 21:00 | 2.6483 | 3.0868 | 3.0868 | 3.0868 | 3.0868
2024-08-11 22:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-06-11 22:00 | 2.2596 | 2.6338 | 2.6338 | 2.6338 | 2.6338
2024-08-11 23:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-06-11 23:00 | 2.1606 | 2.5183 | 2.5183 | 2.5183 | 2.5183
2024-08-12 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-06-12 | 1.97 | 2.2962 | 2.2962 | 2.2962 | 2.2962
2024-08-12 01:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-06-12 01:00 | 1.97 | 2.2962 | 2.2962 | 2.2962 | 2.2962
2024-08-12 02:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-06-12 02:00 | 1.9205 | 2.2385 | 2.2385 | 2.2385 | 2.2385
2024-08-12 03:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-06-12 03:00 | 2.031 | 2.3673 | 2.3673 | 2.3673 | 2.3673
2024-08-12 04:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-06-12 04:00 | 2.4082 | 2.807 | 2.807 | 2.807 | 2.807
2024-08-12 05:00 | 1.829 | 1.9624 | 2.4361 | 2.5624 | 2.6887 | 2024-06-12 05:00 | 2.5073 | 2.9225 | 2.9225 | 2.9225 | 2.9225
2024-08-12 06:00 | 1.9815 | 2.126 | 2.6391 | 2.776 | 2.9128 | 2024-06-12 06:00 | 2.9036 | 3.3844 | 3.3844 | 3.3844 | 3.3844
2024-08-12 07:00 | 2.1148 | 2.2691 | 2.8167 | 2.9628 | 3.1089 | 2024-06-12 07:00 | 3.1818 | 3.7086 | 3.7086 | 3.7086 | 3.7086
2024-08-12 08:00 | 2.3244 | 2.4939 | 3.0959 | 3.2564 | 3.4169 | 2024-06-12 08:00 | 3.5362 | 4.1217 | 4.1217 | 4.1217 | 4.1217
2024-08-12 09:00 | 2.2101 | 2.3713 | 2.9436 | 3.0963 | 3.2489 | 2024-06-12 09:00 | 3.8143 | 4.4459 | 4.4459 | 4.4459 | 4.4459
2024-08-12 10:00 | 1.8481 | 1.9829 | 2.4615 | 2.5891 | 2.7167 | 2024-06-12 10:00 | 3.4866 | 4.064 | 4.064 | 4.064 | 4.064
2024-08-12 11:00 | 1.8862 | 2.0237 | 2.5122 | 2.6425 | 2.7728 | 2024-06-12 11:00 | 3.62 | 4.2194 | 4.2194 | 4.2194 | 4.2194
2024-08-12 12:00 | 1.8862 | 2.0237 | 2.5122 | 2.6425 | 2.7728 | 2024-06-12 12:00 | 3.6086 | 4.2061 | 4.2061 | 4.2061 | 4.2061
2024-08-12 13:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-06-12 13:00 | 3.6619 | 4.2683 | 4.2683 | 4.2683 | 4.2683
2024-08-12 14:00 | 2.2291 | 2.3917 | 2.969 | 3.123 | 3.2769 | 2024-06-12 14:00 | 3.6238 | 4.2239 | 4.2239 | 4.2239 | 4.2239
2024-08-12 15:00 | 2.191 | 2.3508 | 2.9183 | 3.0696 | 3.2209 | 2024-06-12 15:00 | 3.5628 | 4.1528 | 4.1528 | 4.1528 | 4.1528
2024-08-12 16:00 | 2.1339 | 2.2895 | 2.8421 | 2.9895 | 3.1369 | 2024-06-12 16:00 | 3.681 | 4.2905 | 4.2905 | 4.2905 | 4.2905
2024-08-12 17:00 | 2.0196 | 2.1668 | 2.6899 | 2.8293 | 2.9688 | 2024-06-12 17:00 | 3.7381 | 4.3571 | 4.3571 | 4.3571 | 4.3571
2024-08-12 18:00 | 1.9243 | 2.0646 | 2.563 | 2.6959 | 2.8288 | 2024-06-12 18:00 | 3.3304 | 3.8819 | 3.8819 | 3.8819 | 3.8819
2024-08-12 19:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-06-12 19:00 | 3.1437 | 3.6642 | 3.6642 | 3.6642 | 3.6642
2024-08-12 20:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-06-12 20:00 | 2.7626 | 3.2201 | 3.2201 | 3.2201 | 3.2201
2024-08-12 21:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-06-12 21:00 | 2.4806 | 2.8914 | 2.8914 | 2.8914 | 2.8914
2024-08-12 22:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-06-12 22:00 | 2.2444 | 2.616 | 2.616 | 2.616 | 2.616
2024-08-12 23:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-06-12 23:00 | 2.2215 | 2.5894 | 2.5894 | 2.5894 | 2.5894
2024-08-13 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-06-13 | 2.0158 | 2.3495 | 2.3495 | 2.3495 | 2.3495
2024-08-13 01:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-06-13 01:00 | 2.0196 | 2.354 | 2.354 | 2.354 | 2.354
2024-08-13 02:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-06-13 02:00 | 1.9929 | 2.3229 | 2.3229 | 2.3229 | 2.3229
2024-08-13 03:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-06-13 03:00 | 1.9777 | 2.3051 | 2.3051 | 2.3051 | 2.3051
2024-08-13 04:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-06-13 04:00 | 2.2253 | 2.5938 | 2.5938 | 2.5938 | 2.5938
2024-08-13 05:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-06-13 05:00 | 2.5873 | 3.0158 | 3.0158 | 3.0158 | 3.0158
2024-08-13 06:00 | 1.81 | 1.942 | 2.4107 | 2.5357 | 2.6607 | 2024-06-13 06:00 | 3.1208 | 3.6376 | 3.6376 | 3.6376 | 3.6376
2024-08-13 07:00 | 2.2863 | 2.453 | 3.0451 | 3.203 | 3.3609 | 2024-06-13 07:00 | 3.6276 | 4.2283 | 4.2283 | 4.2283 | 4.2283
2024-08-13 08:00 | 2.3435 | 2.5144 | 3.1213 | 3.2831 | 3.4449 | 2024-06-13 08:00 | 3.7152 | 4.3304 | 4.3304 | 4.3304 | 4.3304
2024-08-13 09:00 | 2.2673 | 2.4326 | 3.0198 | 3.1763 | 3.3329 | 2024-06-13 09:00 | 3.6733 | 4.2816 | 4.2816 | 4.2816 | 4.2816
2024-08-13 10:00 | 2.2482 | 2.4121 | 2.9944 | 3.1496 | 3.3049 | 2024-06-13 10:00 | 3.8334 | 4.4681 | 4.4681 | 4.4681 | 4.4681
2024-08-13 11:00 | 2.0767 | 2.2282 | 2.766 | 2.9094 | 3.0528 | 2024-06-13 11:00 | 3.7648 | 4.3882 | 4.3882 | 4.3882 | 4.3882
2024-08-13 12:00 | 2.2101 | 2.3713 | 2.9436 | 3.0963 | 3.2489 | 2024-06-13 12:00 | 3.9058 | 4.5525 | 4.5525 | 4.5525 | 4.5525
2024-08-13 13:00 | 1.8481 | 1.9829 | 2.4615 | 2.5891 | 2.7167 | 2024-06-13 13:00 | 4.001 | 4.6636 | 4.6636 | 4.6636 | 4.6636
2024-08-13 14:00 | 2.1339 | 2.2895 | 2.8421 | 2.9895 | 3.1369 | 2024-06-13 14:00 | 3.8715 | 4.5126 | 4.5126 | 4.5126 | 4.5126
2024-08-13 15:00 | 2.0386 | 2.1873 | 2.7152 | 2.856 | 2.9968 | 2024-06-13 15:00 | 3.7495 | 4.3704 | 4.3704 | 4.3704 | 4.3704
2024-08-13 16:00 | 2.0767 | 2.2282 | 2.766 | 2.9094 | 3.0528 | 2024-06-13 16:00 | 3.6428 | 4.2461 | 4.2461 | 4.2461 | 4.2461
2024-08-13 17:00 | 2.0005 | 2.1464 | 2.6645 | 2.8026 | 2.9408 | 2024-06-13 17:00 | 3.7305 | 4.3482 | 4.3482 | 4.3482 | 4.3482
2024-08-13 18:00 | 2.0196 | 2.1668 | 2.6899 | 2.8293 | 2.9688 | 2024-06-13 18:00 | 3.3609 | 3.9174 | 3.9174 | 3.9174 | 3.9174
2024-08-13 19:00 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 2024-06-13 19:00 | 2.8503 | 3.3222 | 3.3222 | 3.3222 | 3.3222
2024-08-13 20:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-06-13 20:00 | 2.5454 | 2.9669 | 2.9669 | 2.9669 | 2.9669
2024-08-13 21:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-06-13 21:00 | 2.3473 | 2.736 | 2.736 | 2.736 | 2.736
2024-08-13 22:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-06-13 22:00 | 2.092 | 2.4384 | 2.4384 | 2.4384 | 2.4384
2024-08-13 23:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-06-13 23:00 | 1.9396 | 2.2607 | 2.2607 | 2.2607 | 2.2607
2024-08-14 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-06-14 | 1.7071 | 1.9898 | 1.9898 | 1.9898 | 1.9898
2024-08-14 01:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-06-14 01:00 | 1.6957 | 1.9765 | 1.9765 | 1.9765 | 1.9765
2024-08-14 02:00 | 1.3908 | 1.4923 | 1.8525 | 1.9485 | 2.0446 | 2024-06-14 02:00 | 1.6919 | 1.972 | 1.972 | 1.972 | 1.972
2024-08-14 03:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-06-14 03:00 | 1.73 | 2.0164 | 2.0164 | 2.0164 | 2.0164
2024-08-14 04:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-06-14 04:00 | 2.1682 | 2.5272 | 2.5272 | 2.5272 | 2.5272
2024-08-14 05:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-06-14 05:00 | 2.4082 | 2.807 | 2.807 | 2.807 | 2.807
2024-08-14 06:00 | 1.829 | 1.9624 | 2.4361 | 2.5624 | 2.6887 | 2024-06-14 06:00 | 2.9989 | 3.4955 | 3.4955 | 3.4955 | 3.4955
2024-08-14 07:00 | 2.2482 | 2.4121 | 2.9944 | 3.1496 | 3.3049 | 2024-06-14 07:00 | 3.3761 | 3.9352 | 3.9352 | 3.9352 | 3.9352
2024-08-14 08:00 | 2.2482 | 2.4121 | 2.9944 | 3.1496 | 3.3049 | 2024-06-14 08:00 | 4.1649 | 4.8545 | 4.8545 | 4.8545 | 4.8545
2024-08-14 09:00 | 2.2482 | 2.4121 | 2.9944 | 3.1496 | 3.3049 | 2024-06-14 09:00 | 3.9896 | 4.6502 | 4.6502 | 4.6502 | 4.6502
2024-08-14 10:00 | 2.2291 | 2.3917 | 2.969 | 3.123 | 3.2769 | 2024-06-14 10:00 | 3.7267 | 4.3438 | 4.3438 | 4.3438 | 4.3438
2024-08-14 11:00 | 2.172 | 2.3304 | 2.8929 | 3.0429 | 3.1929 | 2024-06-14 11:00 | 3.6428 | 4.2461 | 4.2461 | 4.2461 | 4.2461
2024-08-14 12:00 | 2.2101 | 2.3713 | 2.9436 | 3.0963 | 3.2489 | 2024-06-14 12:00 | 3.9744 | 4.6325 | 4.6325 | 4.6325 | 4.6325
2024-08-14 13:00 | 2.3054 | 2.4735 | 3.0705 | 3.2297 | 3.3889 | 2024-06-14 13:00 | 4.0391 | 4.708 | 4.708 | 4.708 | 4.708
2024-08-14 14:00 | 2.172 | 2.3304 | 2.8929 | 3.0429 | 3.1929 | 2024-06-14 14:00 | 4.0087 | 4.6724 | 4.6724 | 4.6724 | 4.6724
2024-08-14 15:00 | 2.1529 | 2.3099 | 2.8675 | 3.0162 | 3.1649 | 2024-06-14 15:00 | 3.9782 | 4.6369 | 4.6369 | 4.6369 | 4.6369
2024-08-14 16:00 | 2.1339 | 2.2895 | 2.8421 | 2.9895 | 3.1369 | 2024-06-14 16:00 | 4.1992 | 4.8945 | 4.8945 | 4.8945 | 4.8945
2024-08-14 17:00 | 1.9815 | 2.126 | 2.6391 | 2.776 | 2.9128 | 2024-06-14 17:00 | 4.1878 | 4.8812 | 4.8812 | 4.8812 | 4.8812
2024-08-14 18:00 | 2.0386 | 2.1873 | 2.7152 | 2.856 | 2.9968 | 2024-06-14 18:00 | 3.9172 | 4.5658 | 4.5658 | 4.5658 | 4.5658
2024-08-14 19:00 | 1.829 | 1.9624 | 2.4361 | 2.5624 | 2.6887 | 2024-06-14 19:00 | 3.6657 | 4.2727 | 4.2727 | 4.2727 | 4.2727
2024-08-14 20:00 | 1.7338 | 1.8602 | 2.3092 | 2.429 | 2.5487 | 2024-06-14 20:00 | 3.2046 | 3.7353 | 3.7353 | 3.7353 | 3.7353
2024-08-14 21:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-06-14 21:00 | 2.9608 | 3.451 | 3.451 | 3.451 | 3.451
2024-08-14 22:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-06-14 22:00 | 2.5302 | 2.9491 | 2.9491 | 2.9491 | 2.9491
2024-08-14 23:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-06-14 23:00 | 2.2291 | 2.5983 | 2.5983 | 2.5983 | 2.5983
2024-08-15 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-06-15 | 2.1415 | 2.4961 | 2.4961 | 2.4961 | 2.4961
2024-08-15 01:00 | 1.4289 | 1.5331 | 1.9032 | 2.0019 | 2.1006 | 2024-06-15 01:00 | 2.0653 | 2.4073 | 2.4073 | 2.4073 | 2.4073
2024-08-15 02:00 | 1.448 | 1.5536 | 1.9286 | 2.0286 | 2.1286 | 2024-06-15 02:00 | 2.0462 | 2.3851 | 2.3851 | 2.3851 | 2.3851
2024-08-15 03:00 | 1.4289 | 1.5331 | 1.9032 | 2.0019 | 2.1006 | 2024-06-15 03:00 | 2.0501 | 2.3895 | 2.3895 | 2.3895 | 2.3895
2024-08-15 04:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-06-15 04:00 | 2.3358 | 2.7226 | 2.7226 | 2.7226 | 2.7226
2024-08-15 05:00 | 1.7338 | 1.8602 | 2.3092 | 2.429 | 2.5487 | 2024-06-15 05:00 | 2.5835 | 3.0113 | 3.0113 | 3.0113 | 3.0113
2024-08-15 06:00 | 1.829 | 1.9624 | 2.4361 | 2.5624 | 2.6887 | 2024-06-15 06:00 | 2.835 | 3.3045 | 3.3045 | 3.3045 | 3.3045
2024-08-15 07:00 | 2.1529 | 2.3099 | 2.8675 | 3.0162 | 3.1649 | 2024-06-15 07:00 | 2.9989 | 3.4955 | 3.4955 | 3.4955 | 3.4955
2024-08-15 08:00 | 2.2291 | 2.3917 | 2.969 | 3.123 | 3.2769 | 2024-06-15 08:00 | 2.7855 | 3.2467 | 3.2467 | 3.2467 | 3.2467
2024-08-15 09:00 | 2.172 | 2.3304 | 2.8929 | 3.0429 | 3.1929 | 2024-06-15 09:00 | 2.7855 | 3.2467 | 3.2467 | 3.2467 | 3.2467
2024-08-15 10:00 | 2.0577 | 2.2077 | 2.7406 | 2.8827 | 3.0248 | 2024-06-15 10:00 | 2.7855 | 3.2467 | 3.2467 | 3.2467 | 3.2467
2024-08-15 11:00 | 1.8672 | 2.0033 | 2.4869 | 2.6158 | 2.7448 | 2024-06-15 11:00 | 2.7855 | 3.2467 | 3.2467 | 3.2467 | 3.2467
2024-08-15 12:00 | 1.9624 | 2.1055 | 2.6137 | 2.7493 | 2.8848 | 2024-06-15 12:00 | 2.7855 | 3.2467 | 3.2467 | 3.2467 | 3.2467
2024-08-15 13:00 | 2.172 | 2.3304 | 2.8929 | 3.0429 | 3.1929 | 2024-06-15 13:00 | 2.7855 | 3.2467 | 3.2467 | 3.2467 | 3.2467
2024-08-15 14:00 | 2.0196 | 2.1668 | 2.6899 | 2.8293 | 2.9688 | 2024-06-15 14:00 | 3.5057 | 4.0862 | 4.0862 | 4.0862 | 4.0862
2024-08-15 15:00 | 1.4289 | 1.5331 | 1.9032 | 2.0019 | 2.1006 | 2024-06-15 15:00 | 3.5666 | 4.1572 | 4.1572 | 4.1572 | 4.1572
2024-08-15 16:00 | 2.0958 | 2.2486 | 2.7914 | 2.9361 | 3.0808 | 2024-06-15 16:00 | 3.6505 | 4.2549 | 4.2549 | 4.2549 | 4.2549
2024-08-15 17:00 | 1.9624 | 2.1055 | 2.6137 | 2.7493 | 2.8848 | 2024-06-15 17:00 | 3.5971 | 4.1928 | 4.1928 | 4.1928 | 4.1928
2024-08-15 18:00 | 2.0005 | 2.1464 | 2.6645 | 2.8026 | 2.9408 | 2024-06-15 18:00 | 3.1665 | 3.6909 | 3.6909 | 3.6909 | 3.6909
2024-08-15 19:00 | 1.8862 | 2.0237 | 2.5122 | 2.6425 | 2.7728 | 2024-06-15 19:00 | 2.8807 | 3.3578 | 3.3578 | 3.3578 | 3.3578
2024-08-15 20:00 | 1.7528 | 1.8807 | 2.3346 | 2.4557 | 2.5767 | 2024-06-15 20:00 | 2.6712 | 3.1135 | 3.1135 | 3.1135 | 3.1135
2024-08-15 21:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-06-15 21:00 | 2.5721 | 2.998 | 2.998 | 2.998 | 2.998
2024-08-15 22:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-06-15 22:00 | 2.3968 | 2.7937 | 2.7937 | 2.7937 | 2.7937
2024-08-15 23:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-06-15 23:00 | 2.2215 | 2.5894 | 2.5894 | 2.5894 | 2.5894
2024-08-16 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-06-16 | 2.1644 | 2.5228 | 2.5228 | 2.5228 | 2.5228
2024-08-16 01:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-06-16 01:00 | 2.0805 | 2.4251 | 2.4251 | 2.4251 | 2.4251
2024-08-16 02:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-06-16 02:00 | 2.111 | 2.4606 | 2.4606 | 2.4606 | 2.4606
2024-08-16 03:00 | 1.448 | 1.5536 | 1.9286 | 2.0286 | 2.1286 | 2024-06-16 03:00 | 2.332 | 2.7182 | 2.7182 | 2.7182 | 2.7182
2024-08-16 04:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-06-16 04:00 | 2.4883 | 2.9003 | 2.9003 | 2.9003 | 2.9003
2024-08-16 05:00 | 1.7719 | 1.9011 | 2.36 | 2.4823 | 2.6047 | 2024-06-16 05:00 | 2.6293 | 3.0646 | 3.0646 | 3.0646 | 3.0646
2024-08-16 06:00 | 1.829 | 1.9624 | 2.4361 | 2.5624 | 2.6887 | 2024-06-16 06:00 | 2.9684 | 3.4599 | 3.4599 | 3.4599 | 3.4599
2024-08-16 07:00 | 2.191 | 2.3508 | 2.9183 | 3.0696 | 3.2209 | 2024-06-16 07:00 | 3.2542 | 3.793 | 3.793 | 3.793 | 3.793
2024-08-16 08:00 | 2.2101 | 2.3713 | 2.9436 | 3.0963 | 3.2489 | 2024-06-16 08:00 | 3.1132 | 3.6287 | 3.6287 | 3.6287 | 3.6287
2024-08-16 09:00 | 2.3054 | 2.4735 | 3.0705 | 3.2297 | 3.3889 | 2024-06-16 09:00 | 3.0484 | 3.5532 | 3.5532 | 3.5532 | 3.5532
2024-08-16 10:00 | 2.1339 | 2.2895 | 2.8421 | 2.9895 | 3.1369 | 2024-06-16 10:00 | 3.178 | 3.7042 | 3.7042 | 3.7042 | 3.7042
2024-08-16 11:00 | 1.9624 | 2.1055 | 2.6137 | 2.7493 | 2.8848 | 2024-06-16 11:00 | 3.1437 | 3.6642 | 3.6642 | 3.6642 | 3.6642
2024-08-16 12:00 | 2.0005 | 2.1464 | 2.6645 | 2.8026 | 2.9408 | 2024-06-16 12:00 | 3.1551 | 3.6776 | 3.6776 | 3.6776 | 3.6776
2024-08-16 13:00 | 2.0577 | 2.2077 | 2.7406 | 2.8827 | 3.0248 | 2024-06-16 13:00 | 3.0446 | 3.5487 | 3.5487 | 3.5487 | 3.5487
2024-08-16 14:00 | 2.0196 | 2.1668 | 2.6899 | 2.8293 | 2.9688 | 2024-06-16 14:00 | 3.2313 | 3.7664 | 3.7664 | 3.7664 | 3.7664
2024-08-16 15:00 | 2.0005 | 2.1464 | 2.6645 | 2.8026 | 2.9408 | 2024-06-16 15:00 | 3.5095 | 4.0906 | 4.0906 | 4.0906 | 4.0906
2024-08-16 16:00 | 2.0005 | 2.1464 | 2.6645 | 2.8026 | 2.9408 | 2024-06-16 16:00 | 3.6314 | 4.2327 | 4.2327 | 4.2327 | 4.2327
2024-08-16 17:00 | 2.0577 | 2.2077 | 2.7406 | 2.8827 | 3.0248 | 2024-06-16 17:00 | 3.62 | 4.2194 | 4.2194 | 4.2194 | 4.2194
2024-08-16 18:00 | 2.0386 | 2.1873 | 2.7152 | 2.856 | 2.9968 | 2024-06-16 18:00 | 3.3418 | 3.8952 | 3.8952 | 3.8952 | 3.8952
2024-08-16 19:00 | 1.829 | 1.9624 | 2.4361 | 2.5624 | 2.6887 | 2024-06-16 19:00 | 2.915 | 3.3977 | 3.3977 | 3.3977 | 3.3977
2024-08-16 20:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-06-16 20:00 | 2.694 | 3.1401 | 3.1401 | 3.1401 | 3.1401
2024-08-16 21:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-06-16 21:00 | 2.5187 | 2.9358 | 2.9358 | 2.9358 | 2.9358
2024-08-16 22:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-06-16 22:00 | 2.2596 | 2.6338 | 2.6338 | 2.6338 | 2.6338
2024-08-16 23:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-06-16 23:00 | 2.1796 | 2.5405 | 2.5405 | 2.5405 | 2.5405
2024-08-17 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-06-17 | 2.1225 | 2.4739 | 2.4739 | 2.4739 | 2.4739
2024-08-17 01:00 | 1.448 | 1.5536 | 1.9286 | 2.0286 | 2.1286 | 2024-06-17 01:00 | 2.0539 | 2.394 | 2.394 | 2.394 | 2.394
2024-08-17 02:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-06-17 02:00 | 2.0805 | 2.4251 | 2.4251 | 2.4251 | 2.4251
2024-08-17 03:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-06-17 03:00 | 2.2634 | 2.6382 | 2.6382 | 2.6382 | 2.6382
2024-08-17 04:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-06-17 04:00 | 2.5187 | 2.9358 | 2.9358 | 2.9358 | 2.9358
2024-08-17 05:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-06-17 05:00 | 2.8846 | 3.3622 | 3.3622 | 3.3622 | 3.3622
2024-08-17 06:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-06-17 06:00 | 3.2504 | 3.7886 | 3.7886 | 3.7886 | 3.7886
2024-08-17 07:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-06-17 07:00 | 3.418 | 3.984 | 3.984 | 3.984 | 3.984
2024-08-17 08:00 | 1.4099 | 1.5127 | 1.8778 | 1.9752 | 2.0726 | 2024-06-17 08:00 | 4.0087 | 4.6724 | 4.6724 | 4.6724 | 4.6724
2024-08-17 09:00 | 1.2575 | 1.3492 | 1.6748 | 1.7617 | 1.8485 | 2024-06-17 09:00 | 3.9553 | 4.6103 | 4.6103 | 4.6103 | 4.6103
2024-08-17 10:00 | 1.2575 | 1.3492 | 1.6748 | 1.7617 | 1.8485 | 2024-06-17 10:00 | 3.9706 | 4.628 | 4.628 | 4.628 | 4.628
2024-08-17 11:00 | 1.2384 | 1.3287 | 1.6494 | 1.735 | 1.8205 | 2024-06-17 11:00 | 3.681 | 4.2905 | 4.2905 | 4.2905 | 4.2905
2024-08-17 12:00 | 1.2765 | 1.3696 | 1.7002 | 1.7884 | 1.8765 | 2024-06-17 12:00 | 3.8829 | 4.5259 | 4.5259 | 4.5259 | 4.5259
2024-08-17 13:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-06-17 13:00 | 3.86 | 4.4992 | 4.4992 | 4.4992 | 4.4992
2024-08-17 14:00 | 1.4099 | 1.5127 | 1.8778 | 1.9752 | 2.0726 | 2024-06-17 14:00 | 3.5933 | 4.1883 | 4.1883 | 4.1883 | 4.1883
2024-08-17 15:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-06-17 15:00 | 3.8562 | 4.4948 | 4.4948 | 4.4948 | 4.4948
2024-08-17 16:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-06-17 16:00 | 3.9172 | 4.5658 | 4.5658 | 4.5658 | 4.5658
2024-08-17 17:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-06-17 17:00 | 3.9248 | 4.5747 | 4.5747 | 4.5747 | 4.5747
2024-08-17 18:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-06-17 18:00 | 3.5476 | 4.135 | 4.135 | 4.135 | 4.135
2024-08-17 19:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-06-17 19:00 | 3.3799 | 3.9396 | 3.9396 | 3.9396 | 3.9396
2024-08-17 20:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-06-17 20:00 | 2.9455 | 3.4333 | 3.4333 | 3.4333 | 3.4333
2024-08-17 21:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-06-17 21:00 | 2.7626 | 3.2201 | 3.2201 | 3.2201 | 3.2201
2024-08-17 22:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-06-17 22:00 | 2.2596 | 2.6338 | 2.6338 | 2.6338 | 2.6338
2024-08-17 23:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-06-17 23:00 | 2.2673 | 2.6427 | 2.6427 | 2.6427 | 2.6427
2024-08-18 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-06-18 | 2.0615 | 2.4028 | 2.4028 | 2.4028 | 2.4028
2024-08-18 01:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-06-18 01:00 | 2.1263 | 2.4783 | 2.4783 | 2.4783 | 2.4783
2024-08-18 02:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-06-18 02:00 | 2.092 | 2.4384 | 2.4384 | 2.4384 | 2.4384
2024-08-18 03:00 | 1.4099 | 1.5127 | 1.8778 | 1.9752 | 2.0726 | 2024-06-18 03:00 | 2.2063 | 2.5716 | 2.5716 | 2.5716 | 2.5716
2024-08-18 04:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-06-18 04:00 | 2.4692 | 2.8781 | 2.8781 | 2.8781 | 2.8781
2024-08-18 05:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-06-18 05:00 | 2.8579 | 3.3311 | 3.3311 | 3.3311 | 3.3311
2024-08-18 06:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-06-18 06:00 | 3.2885 | 3.833 | 3.833 | 3.833 | 3.833
2024-08-18 07:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-06-18 07:00 | 3.4714 | 4.0462 | 4.0462 | 4.0462 | 4.0462
2024-08-18 08:00 | 1.448 | 1.5536 | 1.9286 | 2.0286 | 2.1286 | 2024-06-18 08:00 | 3.8867 | 4.5303 | 4.5303 | 4.5303 | 4.5303
2024-08-18 09:00 | 1.2575 | 1.3492 | 1.6748 | 1.7617 | 1.8485 | 2024-06-18 09:00 | 3.86 | 4.4992 | 4.4992 | 4.4992 | 4.4992
2024-08-18 10:00 | 1.2765 | 1.3696 | 1.7002 | 1.7884 | 1.8765 | 2024-06-18 10:00 | 3.6124 | 4.2105 | 4.2105 | 4.2105 | 4.2105
2024-08-18 11:00 | 1.2956 | 1.39 | 1.7256 | 1.815 | 1.9045 | 2024-06-18 11:00 | 3.62 | 4.2194 | 4.2194 | 4.2194 | 4.2194
2024-08-18 12:00 | 1.1813 | 1.2674 | 1.5733 | 1.6549 | 1.7365 | 2024-06-18 12:00 | 3.6086 | 4.2061 | 4.2061 | 4.2061 | 4.2061
2024-08-18 13:00 | 1.1241 | 1.2061 | 1.4972 | 1.5748 | 1.6525 | 2024-06-18 13:00 | 3.3228 | 3.873 | 3.873 | 3.873 | 3.873
2024-08-18 14:00 | 1.2956 | 1.39 | 1.7256 | 1.815 | 1.9045 | 2024-06-18 14:00 | 3.319 | 3.8685 | 3.8685 | 3.8685 | 3.8685
2024-08-18 15:00 | 1.448 | 1.5536 | 1.9286 | 2.0286 | 2.1286 | 2024-06-18 15:00 | 3.5095 | 4.0906 | 4.0906 | 4.0906 | 4.0906
2024-08-18 16:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-06-18 16:00 | 3.7419 | 4.3615 | 4.3615 | 4.3615 | 4.3615
2024-08-18 17:00 | 1.7338 | 1.8602 | 2.3092 | 2.429 | 2.5487 | 2024-06-18 17:00 | 3.8334 | 4.4681 | 4.4681 | 4.4681 | 4.4681
2024-08-18 18:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-06-18 18:00 | 3.6314 | 4.2327 | 4.2327 | 4.2327 | 4.2327
2024-08-18 19:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-06-18 19:00 | 2.8465 | 3.3178 | 3.3178 | 3.3178 | 3.3178
2024-08-18 20:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-06-18 20:00 | 2.8884 | 3.3666 | 3.3666 | 3.3666 | 3.3666
2024-08-18 21:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-06-18 21:00 | 2.7321 | 3.1845 | 3.1845 | 3.1845 | 3.1845
2024-08-18 22:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-06-18 22:00 | 2.1225 | 2.4739 | 2.4739 | 2.4739 | 2.4739
2024-08-18 23:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-06-18 23:00 | 2.0081 | 2.3407 | 2.3407 | 2.3407 | 2.3407
2024-08-19 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-06-19 | 1.8557 | 2.163 | 2.163 | 2.163 | 2.163
2024-08-19 01:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-06-19 01:00 | 1.8633 | 2.1719 | 2.1719 | 2.1719 | 2.1719
2024-08-19 02:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-06-19 02:00 | 1.9815 | 2.3096 | 2.3096 | 2.3096 | 2.3096
2024-08-19 03:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-06-19 03:00 | 2.0158 | 2.3495 | 2.3495 | 2.3495 | 2.3495
2024-08-19 04:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-06-19 04:00 | 2.3092 | 2.6915 | 2.6915 | 2.6915 | 2.6915
2024-08-19 05:00 | 1.7338 | 1.8602 | 2.3092 | 2.429 | 2.5487 | 2024-06-19 05:00 | 2.6293 | 3.0646 | 3.0646 | 3.0646 | 3.0646
2024-08-19 06:00 | 1.9434 | 2.0851 | 2.5884 | 2.7226 | 2.8568 | 2024-06-19 06:00 | 2.9913 | 3.4866 | 3.4866 | 3.4866 | 3.4866
2024-08-19 07:00 | 2.4578 | 2.637 | 3.2735 | 3.4433 | 3.613 | 2024-06-19 07:00 | 3.3875 | 3.9485 | 3.9485 | 3.9485 | 3.9485
2024-08-19 08:00 | 2.4578 | 2.637 | 3.2735 | 3.4433 | 3.613 | 2024-06-19 08:00 | 3.9858 | 4.6458 | 4.6458 | 4.6458 | 4.6458
2024-08-19 09:00 | 2.3625 | 2.5348 | 3.1466 | 3.3098 | 3.473 | 2024-06-19 09:00 | 3.9706 | 4.628 | 4.628 | 4.628 | 4.628
2024-08-19 10:00 | 2.3054 | 2.4735 | 3.0705 | 3.2297 | 3.3889 | 2024-06-19 10:00 | 4.0048 | 4.668 | 4.668 | 4.668 | 4.668
2024-08-19 11:00 | 2.3054 | 2.4735 | 3.0705 | 3.2297 | 3.3889 | 2024-06-19 11:00 | 3.5743 | 4.1661 | 4.1661 | 4.1661 | 4.1661
2024-08-19 12:00 | 2.3054 | 2.4735 | 3.0705 | 3.2297 | 3.3889 | 2024-06-19 12:00 | 3.418 | 3.984 | 3.984 | 3.984 | 3.984
2024-08-19 13:00 | 2.3054 | 2.4735 | 3.0705 | 3.2297 | 3.3889 | 2024-06-19 13:00 | 3.479 | 4.0551 | 4.0551 | 4.0551 | 4.0551
2024-08-19 14:00 | 2.3054 | 2.4735 | 3.0705 | 3.2297 | 3.3889 | 2024-06-19 14:00 | 3.62 | 4.2194 | 4.2194 | 4.2194 | 4.2194
2024-08-19 15:00 | 2.0577 | 2.2077 | 2.7406 | 2.8827 | 3.0248 | 2024-06-19 15:00 | 3.6886 | 4.2994 | 4.2994 | 4.2994 | 4.2994
2024-08-19 16:00 | 2.1148 | 2.2691 | 2.8167 | 2.9628 | 3.1089 | 2024-06-19 16:00 | 3.9744 | 4.6325 | 4.6325 | 4.6325 | 4.6325
2024-08-19 17:00 | 2.1148 | 2.2691 | 2.8167 | 2.9628 | 3.1089 | 2024-06-19 17:00 | 3.9934 | 4.6547 | 4.6547 | 4.6547 | 4.6547
2024-08-19 18:00 | 2.0958 | 2.2486 | 2.7914 | 2.9361 | 3.0808 | 2024-06-19 18:00 | 3.6352 | 4.2372 | 4.2372 | 4.2372 | 4.2372
2024-08-19 19:00 | 1.7909 | 1.9215 | 2.3854 | 2.509 | 2.6327 | 2024-06-19 19:00 | 3.0751 | 3.5843 | 3.5843 | 3.5843 | 3.5843
2024-08-19 20:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-06-19 20:00 | 2.6635 | 3.1046 | 3.1046 | 3.1046 | 3.1046
2024-08-19 21:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-06-19 21:00 | 2.5187 | 2.9358 | 2.9358 | 2.9358 | 2.9358
2024-08-19 22:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-06-19 22:00 | 2.3282 | 2.7137 | 2.7137 | 2.7137 | 2.7137
2024-08-19 23:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-06-19 23:00 | 2.0577 | 2.3984 | 2.3984 | 2.3984 | 2.3984
2024-08-20 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-06-20 | 1.9548 | 2.2785 | 2.2785 | 2.2785 | 2.2785
2024-08-20 01:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-06-20 01:00 | 1.9624 | 2.2874 | 2.2874 | 2.2874 | 2.2874
2024-08-20 02:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-06-20 02:00 | 1.8786 | 2.1897 | 2.1897 | 2.1897 | 2.1897
2024-08-20 03:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-06-20 03:00 | 1.9053 | 2.2207 | 2.2207 | 2.2207 | 2.2207
2024-08-20 04:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-06-20 04:00 | 2.1872 | 2.5494 | 2.5494 | 2.5494 | 2.5494
2024-08-20 05:00 | 1.829 | 1.9624 | 2.4361 | 2.5624 | 2.6887 | 2024-06-20 05:00 | 2.4959 | 2.9092 | 2.9092 | 2.9092 | 2.9092
2024-08-20 06:00 | 2.0386 | 2.1873 | 2.7152 | 2.856 | 2.9968 | 2024-06-20 06:00 | 3.0941 | 3.6065 | 3.6065 | 3.6065 | 3.6065
2024-08-20 07:00 | 2.191 | 2.3508 | 2.9183 | 3.0696 | 3.2209 | 2024-06-20 07:00 | 3.5628 | 4.1528 | 4.1528 | 4.1528 | 4.1528
2024-08-20 08:00 | 2.2291 | 2.3917 | 2.969 | 3.123 | 3.2769 | 2024-06-20 08:00 | 3.9172 | 4.5658 | 4.5658 | 4.5658 | 4.5658
2024-08-20 09:00 | 2.191 | 2.3508 | 2.9183 | 3.0696 | 3.2209 | 2024-06-20 09:00 | 4.0506 | 4.7213 | 4.7213 | 4.7213 | 4.7213
2024-08-20 10:00 | 1.9053 | 2.0442 | 2.5376 | 2.6692 | 2.8008 | 2024-06-20 10:00 | 4.001 | 4.6636 | 4.6636 | 4.6636 | 4.6636
2024-08-20 11:00 | 2.0958 | 2.2486 | 2.7914 | 2.9361 | 3.0808 | 2024-06-20 11:00 | 3.8677 | 4.5081 | 4.5081 | 4.5081 | 4.5081
2024-08-20 12:00 | 2.1339 | 2.2895 | 2.8421 | 2.9895 | 3.1369 | 2024-06-20 12:00 | 3.4752 | 4.0506 | 4.0506 | 4.0506 | 4.0506
2024-08-20 13:00 | 1.9434 | 2.0851 | 2.5884 | 2.7226 | 2.8568 | 2024-06-20 13:00 | 3.3761 | 3.9352 | 3.9352 | 3.9352 | 3.9352
2024-08-20 14:00 | 2.2673 | 2.4326 | 3.0198 | 3.1763 | 3.3329 | 2024-06-20 14:00 | 3.62 | 4.2194 | 4.2194 | 4.2194 | 4.2194
2024-08-20 15:00 | 2.1339 | 2.2895 | 2.8421 | 2.9895 | 3.1369 | 2024-06-20 15:00 | 3.6505 | 4.2549 | 4.2549 | 4.2549 | 4.2549
2024-08-20 16:00 | 2.172 | 2.3304 | 2.8929 | 3.0429 | 3.1929 | 2024-06-20 16:00 | 3.7762 | 4.4015 | 4.4015 | 4.4015 | 4.4015
2024-08-20 17:00 | 2.191 | 2.3508 | 2.9183 | 3.0696 | 3.2209 | 2024-06-20 17:00 | 3.8372 | 4.4726 | 4.4726 | 4.4726 | 4.4726
2024-08-20 18:00 | 2.1339 | 2.2895 | 2.8421 | 2.9895 | 3.1369 | 2024-06-20 18:00 | 3.5019 | 4.0817 | 4.0817 | 4.0817 | 4.0817
2024-08-20 19:00 | 1.829 | 1.9624 | 2.4361 | 2.5624 | 2.6887 | 2024-06-20 19:00 | 3.0827 | 3.5932 | 3.5932 | 3.5932 | 3.5932
2024-08-20 20:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-06-20 20:00 | 2.9036 | 3.3844 | 3.3844 | 3.3844 | 3.3844
2024-08-20 21:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-06-20 21:00 | 2.7207 | 3.1712 | 3.1712 | 3.1712 | 3.1712
2024-08-20 22:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-06-20 22:00 | 2.2596 | 2.6338 | 2.6338 | 2.6338 | 2.6338
2024-08-20 23:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-06-20 23:00 | 2.1186 | 2.4695 | 2.4695 | 2.4695 | 2.4695
2024-08-21 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-06-21 | 1.9014 | 2.2163 | 2.2163 | 2.2163 | 2.2163
2024-08-21 01:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-06-21 01:00 | 1.8252 | 2.1275 | 2.1275 | 2.1275 | 2.1275
2024-08-21 02:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-06-21 02:00 | 1.8252 | 2.1275 | 2.1275 | 2.1275 | 2.1275
2024-08-21 03:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-06-21 03:00 | 2.0158 | 2.3495 | 2.3495 | 2.3495 | 2.3495
2024-08-21 04:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-06-21 04:00 | 2.233 | 2.6027 | 2.6027 | 2.6027 | 2.6027
2024-08-21 05:00 | 1.7909 | 1.9215 | 2.3854 | 2.509 | 2.6327 | 2024-06-21 05:00 | 2.6178 | 3.0513 | 3.0513 | 3.0513 | 3.0513
2024-08-21 06:00 | 1.9243 | 2.0646 | 2.563 | 2.6959 | 2.8288 | 2024-06-21 06:00 | 2.9913 | 3.4866 | 3.4866 | 3.4866 | 3.4866
2024-08-21 07:00 | 2.0577 | 2.2077 | 2.7406 | 2.8827 | 3.0248 | 2024-06-21 07:00 | 3.4371 | 4.0062 | 4.0062 | 4.0062 | 4.0062
2024-08-21 08:00 | 1.7719 | 1.9011 | 2.36 | 2.4823 | 2.6047 | 2024-06-21 08:00 | 3.8791 | 4.5214 | 4.5214 | 4.5214 | 4.5214
2024-08-21 09:00 | 2.7245 | 2.9232 | 3.6288 | 3.8169 | 4.0051 | 2024-06-21 09:00 | 3.9896 | 4.6502 | 4.6502 | 4.6502 | 4.6502
2024-08-21 10:00 | 2.7436 | 2.9436 | 3.6542 | 3.8436 | 4.0331 | 2024-06-21 10:00 | 3.7838 | 4.4104 | 4.4104 | 4.4104 | 4.4104
2024-08-21 11:00 | 1.8672 | 2.0033 | 2.4869 | 2.6158 | 2.7448 | 2024-06-21 11:00 | 3.8486 | 4.4859 | 4.4859 | 4.4859 | 4.4859
2024-08-21 12:00 | 2.0386 | 2.1873 | 2.7152 | 2.856 | 2.9968 | 2024-06-21 12:00 | 4.1077 | 4.7879 | 4.7879 | 4.7879 | 4.7879
2024-08-21 13:00 | 2.4768 | 2.6574 | 3.2989 | 3.4699 | 3.641 | 2024-06-21 13:00 | 4.2297 | 4.9301 | 4.9301 | 4.9301 | 4.9301
2024-08-21 14:00 | 2.0005 | 2.1464 | 2.6645 | 2.8026 | 2.9408 | 2024-06-21 14:00 | 3.8334 | 4.4681 | 4.4681 | 4.4681 | 4.4681
2024-08-21 15:00 | 2.2101 | 2.3713 | 2.9436 | 3.0963 | 3.2489 | 2024-06-21 15:00 | 3.5781 | 4.1706 | 4.1706 | 4.1706 | 4.1706
2024-08-21 16:00 | 2.1148 | 2.2691 | 2.8167 | 2.9628 | 3.1089 | 2024-06-21 16:00 | 3.9134 | 4.5614 | 4.5614 | 4.5614 | 4.5614
2024-08-21 17:00 | 2.0577 | 2.2077 | 2.7406 | 2.8827 | 3.0248 | 2024-06-21 17:00 | 3.8753 | 4.517 | 4.517 | 4.517 | 4.517
2024-08-21 18:00 | 2.0577 | 2.2077 | 2.7406 | 2.8827 | 3.0248 | 2024-06-21 18:00 | 3.8181 | 4.4504 | 4.4504 | 4.4504 | 4.4504
2024-08-21 19:00 | 1.9243 | 2.0646 | 2.563 | 2.6959 | 2.8288 | 2024-06-21 19:00 | 3.3914 | 3.9529 | 3.9529 | 3.9529 | 3.9529
2024-08-21 20:00 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 2024-06-21 20:00 | 2.8846 | 3.3622 | 3.3622 | 3.3622 | 3.3622
2024-08-21 21:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-06-21 21:00 | 2.7207 | 3.1712 | 3.1712 | 3.1712 | 3.1712
2024-08-21 22:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-06-21 22:00 | 2.0462 | 2.3851 | 2.3851 | 2.3851 | 2.3851
2024-08-21 23:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-06-21 23:00 | 1.9853 | 2.314 | 2.314 | 2.314 | 2.314
2024-08-22 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-06-22 | 1.7795 | 2.0742 | 2.0742 | 2.0742 | 2.0742
2024-08-22 01:00 | 1.4289 | 1.5331 | 1.9032 | 2.0019 | 2.1006 | 2024-06-22 01:00 | 1.7414 | 2.0298 | 2.0298 | 2.0298 | 2.0298
2024-08-22 02:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-06-22 02:00 | 1.749 | 2.0386 | 2.0386 | 2.0386 | 2.0386
2024-08-22 03:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-06-22 03:00 | 1.9815 | 2.3096 | 2.3096 | 2.3096 | 2.3096
2024-08-22 04:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-06-22 04:00 | 2.0615 | 2.4028 | 2.4028 | 2.4028 | 2.4028
2024-08-22 05:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-06-22 05:00 | 2.4616 | 2.8692 | 2.8692 | 2.8692 | 2.8692
2024-08-22 06:00 | 1.7719 | 1.9011 | 2.36 | 2.4823 | 2.6047 | 2024-06-22 06:00 | 2.6483 | 3.0868 | 3.0868 | 3.0868 | 3.0868
2024-08-22 07:00 | 2.3244 | 2.4939 | 3.0959 | 3.2564 | 3.4169 | 2024-06-22 07:00 | 2.7398 | 3.1934 | 3.1934 | 3.1934 | 3.1934
2024-08-22 08:00 | 2.2101 | 2.3713 | 2.9436 | 3.0963 | 3.2489 | 2024-06-22 08:00 | 2.8846 | 3.3622 | 3.3622 | 3.3622 | 3.3622
2024-08-22 09:00 | 2.2863 | 2.453 | 3.0451 | 3.203 | 3.3609 | 2024-06-22 09:00 | 2.9722 | 3.4644 | 3.4644 | 3.4644 | 3.4644
2024-08-22 10:00 | 1.9624 | 2.1055 | 2.6137 | 2.7493 | 2.8848 | 2024-06-22 10:00 | 3.3037 | 3.8508 | 3.8508 | 3.8508 | 3.8508
2024-08-22 11:00 | 2.191 | 2.3508 | 2.9183 | 3.0696 | 3.2209 | 2024-06-22 11:00 | 2.9646 | 3.4555 | 3.4555 | 3.4555 | 3.4555
2024-08-22 12:00 | 2.191 | 2.3508 | 2.9183 | 3.0696 | 3.2209 | 2024-06-22 12:00 | 2.9913 | 3.4866 | 3.4866 | 3.4866 | 3.4866
2024-08-22 13:00 | 1.9243 | 2.0646 | 2.563 | 2.6959 | 2.8288 | 2024-06-22 13:00 | 3.0217 | 3.5221 | 3.5221 | 3.5221 | 3.5221
2024-08-22 14:00 | 2.1148 | 2.2691 | 2.8167 | 2.9628 | 3.1089 | 2024-06-22 14:00 | 3.0865 | 3.5976 | 3.5976 | 3.5976 | 3.5976
2024-08-22 15:00 | 2.0577 | 2.2077 | 2.7406 | 2.8827 | 3.0248 | 2024-06-22 15:00 | 3.3647 | 3.9218 | 3.9218 | 3.9218 | 3.9218
2024-08-22 16:00 | 2.0767 | 2.2282 | 2.766 | 2.9094 | 3.0528 | 2024-06-22 16:00 | 3.4371 | 4.0062 | 4.0062 | 4.0062 | 4.0062
2024-08-22 17:00 | 1.9815 | 2.126 | 2.6391 | 2.776 | 2.9128 | 2024-06-22 17:00 | 3.3914 | 3.9529 | 3.9529 | 3.9529 | 3.9529
2024-08-22 18:00 | 1.9624 | 2.1055 | 2.6137 | 2.7493 | 2.8848 | 2024-06-22 18:00 | 3.0217 | 3.5221 | 3.5221 | 3.5221 | 3.5221
2024-08-22 19:00 | 1.7909 | 1.9215 | 2.3854 | 2.509 | 2.6327 | 2024-06-22 19:00 | 2.4806 | 2.8914 | 2.8914 | 2.8914 | 2.8914
2024-08-22 20:00 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 2024-06-22 20:00 | 2.5264 | 2.9447 | 2.9447 | 2.9447 | 2.9447
2024-08-22 21:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-06-22 21:00 | 2.233 | 2.6027 | 2.6027 | 2.6027 | 2.6027
2024-08-22 22:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-06-22 22:00 | 2.172 | 2.5316 | 2.5316 | 2.5316 | 2.5316
2024-08-22 23:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-06-22 23:00 | 1.8976 | 2.2119 | 2.2119 | 2.2119 | 2.2119
2024-08-23 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-06-23 | 1.81 | 2.1097 | 2.1097 | 2.1097 | 2.1097
2024-08-23 01:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-06-23 01:00 | 1.7719 | 2.0653 | 2.0653 | 2.0653 | 2.0653
2024-08-23 02:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-06-23 02:00 | 1.8824 | 2.1941 | 2.1941 | 2.1941 | 2.1941
2024-08-23 03:00 | 1.448 | 1.5536 | 1.9286 | 2.0286 | 2.1286 | 2024-06-23 03:00 | 1.9205 | 2.2385 | 2.2385 | 2.2385 | 2.2385
2024-08-23 04:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-06-23 04:00 | 2.0577 | 2.3984 | 2.3984 | 2.3984 | 2.3984
2024-08-23 05:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-06-23 05:00 | 2.4425 | 2.847 | 2.847 | 2.847 | 2.847
2024-08-23 06:00 | 1.8862 | 2.0237 | 2.5122 | 2.6425 | 2.7728 | 2024-06-23 06:00 | 2.755 | 3.2112 | 3.2112 | 3.2112 | 3.2112
2024-08-23 07:00 | 2.191 | 2.3508 | 2.9183 | 3.0696 | 3.2209 | 2024-06-23 07:00 | 2.8693 | 3.3444 | 3.3444 | 3.3444 | 3.3444
2024-08-23 08:00 | 2.2673 | 2.4326 | 3.0198 | 3.1763 | 3.3329 | 2024-06-23 08:00 | 2.896 | 3.3755 | 3.3755 | 3.3755 | 3.3755
2024-08-23 09:00 | 2.2673 | 2.4326 | 3.0198 | 3.1763 | 3.3329 | 2024-06-23 09:00 | 2.9493 | 3.4377 | 3.4377 | 3.4377 | 3.4377
2024-08-23 10:00 | 2.0005 | 2.1464 | 2.6645 | 2.8026 | 2.9408 | 2024-06-23 10:00 | 2.9684 | 3.4599 | 3.4599 | 3.4599 | 3.4599
2024-08-23 11:00 | 2.0005 | 2.1464 | 2.6645 | 2.8026 | 2.9408 | 2024-06-23 11:00 | 2.9379 | 3.4244 | 3.4244 | 3.4244 | 3.4244
2024-08-23 12:00 | 1.7338 | 1.8602 | 2.3092 | 2.429 | 2.5487 | 2024-06-23 12:00 | 2.8998 | 3.38 | 3.38 | 3.38 | 3.38
2024-08-23 13:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-06-23 13:00 | 3.0332 | 3.5354 | 3.5354 | 3.5354 | 3.5354
2024-08-23 14:00 | 1.8481 | 1.9829 | 2.4615 | 2.5891 | 2.7167 | 2024-06-23 14:00 | 3.0408 | 3.5443 | 3.5443 | 3.5443 | 3.5443
2024-08-23 15:00 | 1.8672 | 2.0033 | 2.4869 | 2.6158 | 2.7448 | 2024-06-23 15:00 | 3.2389 | 3.7753 | 3.7753 | 3.7753 | 3.7753
2024-08-23 16:00 | 1.9815 | 2.126 | 2.6391 | 2.776 | 2.9128 | 2024-06-23 16:00 | 3.1208 | 3.6376 | 3.6376 | 3.6376 | 3.6376
2024-08-23 17:00 | 2.0386 | 2.1873 | 2.7152 | 2.856 | 2.9968 | 2024-06-23 17:00 | 3.2656 | 3.8064 | 3.8064 | 3.8064 | 3.8064
2024-08-23 18:00 | 2.0386 | 2.1873 | 2.7152 | 2.856 | 2.9968 | 2024-06-23 18:00 | 3.0027 | 3.4999 | 3.4999 | 3.4999 | 3.4999
2024-08-23 19:00 | 1.7909 | 1.9215 | 2.3854 | 2.509 | 2.6327 | 2024-06-23 19:00 | 2.7321 | 3.1845 | 3.1845 | 3.1845 | 3.1845
2024-08-23 20:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-06-23 20:00 | 2.4235 | 2.8248 | 2.8248 | 2.8248 | 2.8248
2024-08-23 21:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-06-23 21:00 | 2.1301 | 2.4828 | 2.4828 | 2.4828 | 2.4828
2024-08-23 22:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-06-23 22:00 | 1.9014 | 2.2163 | 2.2163 | 2.2163 | 2.2163
2024-08-23 23:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-06-23 23:00 | 1.7986 | 2.0964 | 2.0964 | 2.0964 | 2.0964
2024-08-24 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-06-24 | 1.8024 | 2.1008 | 2.1008 | 2.1008 | 2.1008
2024-08-24 01:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-06-24 01:00 | 1.81 | 2.1097 | 2.1097 | 2.1097 | 2.1097
2024-08-24 02:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-06-24 02:00 | 1.7986 | 2.0964 | 2.0964 | 2.0964 | 2.0964
2024-08-24 03:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-06-24 03:00 | 1.9357 | 2.2563 | 2.2563 | 2.2563 | 2.2563
2024-08-24 04:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-06-24 04:00 | 2.1377 | 2.4917 | 2.4917 | 2.4917 | 2.4917
2024-08-24 05:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-06-24 05:00 | 2.4883 | 2.9003 | 2.9003 | 2.9003 | 2.9003
2024-08-24 06:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-06-24 06:00 | 2.8198 | 3.2867 | 3.2867 | 3.2867 | 3.2867
2024-08-24 07:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-06-24 07:00 | 3.7457 | 4.366 | 4.366 | 4.366 | 4.366
2024-08-24 08:00 | 0.60968 | 0.65414 | 0.81204 | 0.85414 | 0.89625 | 2024-06-24 08:00 | 3.6657 | 4.2727 | 4.2727 | 4.2727 | 4.2727
2024-08-24 09:00 | 0.22863 | 0.2453 | 0.30451 | 0.3203 | 0.33609 | 2024-06-24 09:00 | 4.0163 | 4.6813 | 4.6813 | 4.6813 | 4.6813
2024-08-24 10:00 | 0.26674 | 0.28619 | 0.35527 | 0.37369 | 0.39211 | 2024-06-24 10:00 | 3.639 | 4.2416 | 4.2416 | 4.2416 | 4.2416
2024-08-24 11:00 | 0.24768 | 0.26574 | 0.32989 | 0.34699 | 0.3641 | 2024-06-24 11:00 | 3.7 | 4.3127 | 4.3127 | 4.3127 | 4.3127
2024-08-24 12:00 | 0.97168 | 1.0425 | 1.2942 | 1.3613 | 1.4284 | 2024-06-24 12:00 | 3.8143 | 4.4459 | 4.4459 | 4.4459 | 4.4459
2024-08-24 13:00 | 1.0098 | 1.0834 | 1.3449 | 1.4147 | 1.4844 | 2024-06-24 13:00 | 3.5857 | 4.1794 | 4.1794 | 4.1794 | 4.1794
2024-08-24 14:00 | 0.34295 | 0.36795 | 0.45677 | 0.48045 | 0.50414 | 2024-06-24 14:00 | 3.5895 | 4.1839 | 4.1839 | 4.1839 | 4.1839
2024-08-24 15:00 | 0.22863 | 0.2453 | 0.30451 | 0.3203 | 0.33609 | 2024-06-24 15:00 | 3.9286 | 4.5792 | 4.5792 | 4.5792 | 4.5792
2024-08-24 16:00 | 1.3146 | 1.4105 | 1.751 | 1.8417 | 1.9325 | 2024-06-24 16:00 | 3.9629 | 4.6191 | 4.6191 | 4.6191 | 4.6191
2024-08-24 17:00 | 1.448 | 1.5536 | 1.9286 | 2.0286 | 2.1286 | 2024-06-24 17:00 | 3.8753 | 4.517 | 4.517 | 4.517 | 4.517
2024-08-24 18:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-06-24 18:00 | 3.4142 | 3.9796 | 3.9796 | 3.9796 | 3.9796
2024-08-24 19:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-06-24 19:00 | 2.8884 | 3.3666 | 3.3666 | 3.3666 | 3.3666
2024-08-24 20:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-06-24 20:00 | 2.8388 | 3.3089 | 3.3089 | 3.3089 | 3.3089
2024-08-24 21:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-06-24 21:00 | 2.3778 | 2.7715 | 2.7715 | 2.7715 | 2.7715
2024-08-24 22:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-06-24 22:00 | 1.9396 | 2.2607 | 2.2607 | 2.2607 | 2.2607
2024-08-24 23:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-06-24 23:00 | 1.8595 | 2.1674 | 2.1674 | 2.1674 | 2.1674
2024-08-25 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-06-25 | 1.73 | 2.0164 | 2.0164 | 2.0164 | 2.0164
2024-08-25 01:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-06-25 01:00 | 1.7224 | 2.0076 | 2.0076 | 2.0076 | 2.0076
2024-08-25 02:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-06-25 02:00 | 1.7147 | 1.9987 | 1.9987 | 1.9987 | 1.9987
2024-08-25 03:00 | 1.4099 | 1.5127 | 1.8778 | 1.9752 | 2.0726 | 2024-06-25 03:00 | 1.8519 | 2.1586 | 2.1586 | 2.1586 | 2.1586
2024-08-25 04:00 | 1.448 | 1.5536 | 1.9286 | 2.0286 | 2.1286 | 2024-06-25 04:00 | 2.1034 | 2.4517 | 2.4517 | 2.4517 | 2.4517
2024-08-25 05:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-06-25 05:00 | 2.6407 | 3.078 | 3.078 | 3.078 | 3.078
2024-08-25 06:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-06-25 06:00 | 2.9036 | 3.3844 | 3.3844 | 3.3844 | 3.3844
2024-08-25 07:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-06-25 07:00 | 3.1894 | 3.7175 | 3.7175 | 3.7175 | 3.7175
2024-08-25 08:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-06-25 08:00 | 3.7953 | 4.4237 | 4.4237 | 4.4237 | 4.4237
2024-08-25 09:00 | 1.3718 | 1.4718 | 1.8271 | 1.9218 | 2.0166 | 2024-06-25 09:00 | 3.7876 | 4.4148 | 4.4148 | 4.4148 | 4.4148
2024-08-25 10:00 | 1.2384 | 1.3287 | 1.6494 | 1.735 | 1.8205 | 2024-06-25 10:00 | 3.9248 | 4.5747 | 4.5747 | 4.5747 | 4.5747
2024-08-25 11:00 | 1.1622 | 1.247 | 1.5479 | 1.6282 | 1.7085 | 2024-06-25 11:00 | 3.8943 | 4.5392 | 4.5392 | 4.5392 | 4.5392
2024-08-25 12:00 | 1.3337 | 1.4309 | 1.7763 | 1.8684 | 1.9605 | 2024-06-25 12:00 | 3.7915 | 4.4193 | 4.4193 | 4.4193 | 4.4193
2024-08-25 13:00 | 1.3146 | 1.4105 | 1.751 | 1.8417 | 1.9325 | 2024-06-25 13:00 | 3.54 | 4.1261 | 4.1261 | 4.1261 | 4.1261
2024-08-25 14:00 | 1.3908 | 1.4923 | 1.8525 | 1.9485 | 2.0446 | 2024-06-25 14:00 | 3.7038 | 4.3171 | 4.3171 | 4.3171 | 4.3171
2024-08-25 15:00 | 1.448 | 1.5536 | 1.9286 | 2.0286 | 2.1286 | 2024-06-25 15:00 | 3.7724 | 4.3971 | 4.3971 | 4.3971 | 4.3971
2024-08-25 16:00 | 1.4289 | 1.5331 | 1.9032 | 2.0019 | 2.1006 | 2024-06-25 16:00 | 3.7686 | 4.3926 | 4.3926 | 4.3926 | 4.3926
2024-08-25 17:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-06-25 17:00 | 3.8067 | 4.437 | 4.437 | 4.437 | 4.437
2024-08-25 18:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-06-25 18:00 | 3.559 | 4.1483 | 4.1483 | 4.1483 | 4.1483
2024-08-25 19:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-06-25 19:00 | 3.0637 | 3.571 | 3.571 | 3.571 | 3.571
2024-08-25 20:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-06-25 20:00 | 2.614 | 3.0469 | 3.0469 | 3.0469 | 3.0469
2024-08-25 21:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-06-25 21:00 | 2.5454 | 2.9669 | 2.9669 | 2.9669 | 2.9669
2024-08-25 22:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-06-25 22:00 | 1.8595 | 2.1674 | 2.1674 | 2.1674 | 2.1674
2024-08-25 23:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-06-25 23:00 | 1.8481 | 2.1541 | 2.1541 | 2.1541 | 2.1541
2024-08-26 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-06-26 | 1.7414 | 2.0298 | 2.0298 | 2.0298 | 2.0298
2024-08-26 01:00 | 1.448 | 1.5536 | 1.9286 | 2.0286 | 2.1286 | 2024-06-26 01:00 | 1.7605 | 2.052 | 2.052 | 2.052 | 2.052
2024-08-26 02:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-06-26 02:00 | 1.7719 | 2.0653 | 2.0653 | 2.0653 | 2.0653
2024-08-26 03:00 | 1.4289 | 1.5331 | 1.9032 | 2.0019 | 2.1006 | 2024-06-26 03:00 | 1.8748 | 2.1852 | 2.1852 | 2.1852 | 2.1852
2024-08-26 04:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-06-26 04:00 | 2.0615 | 2.4028 | 2.4028 | 2.4028 | 2.4028
2024-08-26 05:00 | 1.7338 | 1.8602 | 2.3092 | 2.429 | 2.5487 | 2024-06-26 05:00 | 2.3092 | 2.6915 | 2.6915 | 2.6915 | 2.6915
2024-08-26 06:00 | 1.8672 | 2.0033 | 2.4869 | 2.6158 | 2.7448 | 2024-06-26 06:00 | 2.9227 | 3.4066 | 3.4066 | 3.4066 | 3.4066
2024-08-26 07:00 | 2.0386 | 2.1873 | 2.7152 | 2.856 | 2.9968 | 2024-06-26 07:00 | 3.4714 | 4.0462 | 4.0462 | 4.0462 | 4.0462
2024-08-26 08:00 | 2.3625 | 2.5348 | 3.1466 | 3.3098 | 3.473 | 2024-06-26 08:00 | 3.7876 | 4.4148 | 4.4148 | 4.4148 | 4.4148
2024-08-26 09:00 | 1.8481 | 1.9829 | 2.4615 | 2.5891 | 2.7167 | 2024-06-26 09:00 | 3.4866 | 4.064 | 4.064 | 4.064 | 4.064
2024-08-26 10:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-06-26 10:00 | 3.3799 | 3.9396 | 3.9396 | 3.9396 | 3.9396
2024-08-26 11:00 | 1.81 | 1.942 | 2.4107 | 2.5357 | 2.6607 | 2024-06-26 11:00 | 3.6124 | 4.2105 | 4.2105 | 4.2105 | 4.2105
2024-08-26 12:00 | 1.2194 | 1.3083 | 1.6241 | 1.7083 | 1.7925 | 2024-06-26 12:00 | 3.7495 | 4.3704 | 4.3704 | 4.3704 | 4.3704
2024-08-26 13:00 | 1.2194 | 1.3083 | 1.6241 | 1.7083 | 1.7925 | 2024-06-26 13:00 | 3.8524 | 4.4903 | 4.4903 | 4.4903 | 4.4903
2024-08-26 14:00 | 1.105 | 1.1856 | 1.4718 | 1.5481 | 1.6244 | 2024-06-26 14:00 | 4.0582 | 4.7302 | 4.7302 | 4.7302 | 4.7302
2024-08-26 15:00 | 1.81 | 1.942 | 2.4107 | 2.5357 | 2.6607 | 2024-06-26 15:00 | 3.7572 | 4.3793 | 4.3793 | 4.3793 | 4.3793
2024-08-26 16:00 | 2.0386 | 2.1873 | 2.7152 | 2.856 | 2.9968 | 2024-06-26 16:00 | 4.2106 | 4.9078 | 4.9078 | 4.9078 | 4.9078
2024-08-26 17:00 | 2.0767 | 2.2282 | 2.766 | 2.9094 | 3.0528 | 2024-06-26 17:00 | 4.344 | 5.0633 | 5.0633 | 5.0633 | 5.0633
2024-08-26 18:00 | 2.0958 | 2.2486 | 2.7914 | 2.9361 | 3.0808 | 2024-06-26 18:00 | 3.9667 | 4.6236 | 4.6236 | 4.6236 | 4.6236
2024-08-26 19:00 | 1.8672 | 2.0033 | 2.4869 | 2.6158 | 2.7448 | 2024-06-26 19:00 | 3.1627 | 3.6864 | 3.6864 | 3.6864 | 3.6864
2024-08-26 20:00 | 1.7719 | 1.9011 | 2.36 | 2.4823 | 2.6047 | 2024-06-26 20:00 | 3.0865 | 3.5976 | 3.5976 | 3.5976 | 3.5976
2024-08-26 21:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-06-26 21:00 | 2.8693 | 3.3444 | 3.3444 | 3.3444 | 3.3444
2024-08-26 22:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-06-26 22:00 | 2.4654 | 2.8736 | 2.8736 | 2.8736 | 2.8736
2024-08-26 23:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-06-26 23:00 | 2.2101 | 2.5761 | 2.5761 | 2.5761 | 2.5761
2024-08-27 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-06-27 | 2.0691 | 2.4117 | 2.4117 | 2.4117 | 2.4117
2024-08-27 01:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-06-27 01:00 | 2.0691 | 2.4117 | 2.4117 | 2.4117 | 2.4117
2024-08-27 02:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-06-27 02:00 | 2.0805 | 2.4251 | 2.4251 | 2.4251 | 2.4251
2024-08-27 03:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-06-27 03:00 | 2.1301 | 2.4828 | 2.4828 | 2.4828 | 2.4828
2024-08-27 04:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-06-27 04:00 | 2.4121 | 2.8115 | 2.8115 | 2.8115 | 2.8115
2024-08-27 05:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-06-27 05:00 | 2.9227 | 3.4066 | 3.4066 | 3.4066 | 3.4066
2024-08-27 06:00 | 1.829 | 1.9624 | 2.4361 | 2.5624 | 2.6887 | 2024-06-27 06:00 | 3.4028 | 3.9662 | 3.9662 | 3.9662 | 3.9662
2024-08-27 07:00 | 2.1148 | 2.2691 | 2.8167 | 2.9628 | 3.1089 | 2024-06-27 07:00 | 3.6886 | 4.2994 | 4.2994 | 4.2994 | 4.2994
2024-08-27 08:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-06-27 08:00 | 4.3707 | 5.0944 | 5.0944 | 5.0944 | 5.0944
2024-08-27 09:00 | 1.81 | 1.942 | 2.4107 | 2.5357 | 2.6607 | 2024-06-27 09:00 | 4.4164 | 5.1477 | 5.1477 | 5.1477 | 5.1477
2024-08-27 10:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-06-27 10:00 | 4.0391 | 4.708 | 4.708 | 4.708 | 4.708
2024-08-27 11:00 | 1.3337 | 1.4309 | 1.7763 | 1.8684 | 1.9605 | 2024-06-27 11:00 | 3.78 | 4.406 | 4.406 | 4.406 | 4.406
2024-08-27 12:00 | 1.9053 | 2.0442 | 2.5376 | 2.6692 | 2.8008 | 2024-06-27 12:00 | 3.9858 | 4.6458 | 4.6458 | 4.6458 | 4.6458
2024-08-27 13:00 | 2.0196 | 2.1668 | 2.6899 | 2.8293 | 2.9688 | 2024-06-27 13:00 | 3.8219 | 4.4548 | 4.4548 | 4.4548 | 4.4548
2024-08-27 14:00 | 2.0767 | 2.2282 | 2.766 | 2.9094 | 3.0528 | 2024-06-27 14:00 | 4.1306 | 4.8146 | 4.8146 | 4.8146 | 4.8146
2024-08-27 15:00 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 2024-06-27 15:00 | 4.0734 | 4.7479 | 4.7479 | 4.7479 | 4.7479
2024-08-27 16:00 | 1.9243 | 2.0646 | 2.563 | 2.6959 | 2.8288 | 2024-06-27 16:00 | 4.344 | 5.0633 | 5.0633 | 5.0633 | 5.0633
2024-08-27 17:00 | 2.0386 | 2.1873 | 2.7152 | 2.856 | 2.9968 | 2024-06-27 17:00 | 4.3326 | 5.05 | 5.05 | 5.05 | 5.05
2024-08-27 18:00 | 2.0005 | 2.1464 | 2.6645 | 2.8026 | 2.9408 | 2024-06-27 18:00 | 3.841 | 4.477 | 4.477 | 4.477 | 4.477
2024-08-27 19:00 | 1.7528 | 1.8807 | 2.3346 | 2.4557 | 2.5767 | 2024-06-27 19:00 | 3.3952 | 3.9574 | 3.9574 | 3.9574 | 3.9574
2024-08-27 20:00 | 1.829 | 1.9624 | 2.4361 | 2.5624 | 2.6887 | 2024-06-27 20:00 | 3.1589 | 3.682 | 3.682 | 3.682 | 3.682
2024-08-27 21:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-06-27 21:00 | 2.8922 | 3.3711 | 3.3711 | 3.3711 | 3.3711
2024-08-27 22:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-06-27 22:00 | 2.3816 | 2.7759 | 2.7759 | 2.7759 | 2.7759
2024-08-27 23:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-06-27 23:00 | 2.3739 | 2.767 | 2.767 | 2.767 | 2.767
2024-08-28 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-06-28 | 2.3358 | 2.7226 | 2.7226 | 2.7226 | 2.7226
2024-08-28 01:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-06-28 01:00 | 2.1834 | 2.545 | 2.545 | 2.545 | 2.545
2024-08-28 02:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-06-28 02:00 | 2.1682 | 2.5272 | 2.5272 | 2.5272 | 2.5272
2024-08-28 03:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-06-28 03:00 | 2.2406 | 2.6116 | 2.6116 | 2.6116 | 2.6116
2024-08-28 04:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-06-28 04:00 | 2.5073 | 2.9225 | 2.9225 | 2.9225 | 2.9225
2024-08-28 05:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-06-28 05:00 | 2.9722 | 3.4644 | 3.4644 | 3.4644 | 3.4644
2024-08-28 06:00 | 1.829 | 1.9624 | 2.4361 | 2.5624 | 2.6887 | 2024-06-28 06:00 | 3.3723 | 3.9307 | 3.9307 | 3.9307 | 3.9307
2024-08-28 07:00 | 2.2482 | 2.4121 | 2.9944 | 3.1496 | 3.3049 | 2024-06-28 07:00 | 3.9553 | 4.6103 | 4.6103 | 4.6103 | 4.6103
2024-08-28 08:00 | 2.3054 | 2.4735 | 3.0705 | 3.2297 | 3.3889 | 2024-06-28 08:00 | 4.0887 | 4.7657 | 4.7657 | 4.7657 | 4.7657
2024-08-28 09:00 | 2.0005 | 2.1464 | 2.6645 | 2.8026 | 2.9408 | 2024-06-28 09:00 | 4.3173 | 5.0322 | 5.0322 | 5.0322 | 5.0322
2024-08-28 10:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-06-28 10:00 | 3.8486 | 4.4859 | 4.4859 | 4.4859 | 4.4859
2024-08-28 11:00 | 1.3146 | 1.4105 | 1.751 | 1.8417 | 1.9325 | 2024-06-28 11:00 | 3.9363 | 4.5881 | 4.5881 | 4.5881 | 4.5881
2024-08-28 12:00 | 1.7719 | 1.9011 | 2.36 | 2.4823 | 2.6047 | 2024-06-28 12:00 | 4.142 | 4.8279 | 4.8279 | 4.8279 | 4.8279
2024-08-28 13:00 | 2.0958 | 2.2486 | 2.7914 | 2.9361 | 3.0808 | 2024-06-28 13:00 | 3.5133 | 4.0951 | 4.0951 | 4.0951 | 4.0951
2024-08-28 14:00 | 2.0005 | 2.1464 | 2.6645 | 2.8026 | 2.9408 | 2024-06-28 14:00 | 3.8867 | 4.5303 | 4.5303 | 4.5303 | 4.5303
2024-08-28 15:00 | 2.172 | 2.3304 | 2.8929 | 3.0429 | 3.1929 | 2024-06-28 15:00 | 4.1611 | 4.8501 | 4.8501 | 4.8501 | 4.8501
2024-08-28 16:00 | 2.1148 | 2.2691 | 2.8167 | 2.9628 | 3.1089 | 2024-06-28 16:00 | 4.424 | 5.1566 | 5.1566 | 5.1566 | 5.1566
2024-08-28 17:00 | 2.0577 | 2.2077 | 2.7406 | 2.8827 | 3.0248 | 2024-06-28 17:00 | 4.3783 | 5.1033 | 5.1033 | 5.1033 | 5.1033
2024-08-28 18:00 | 2.0196 | 2.1668 | 2.6899 | 2.8293 | 2.9688 | 2024-06-28 18:00 | 4.1763 | 4.8679 | 4.8679 | 4.8679 | 4.8679
2024-08-28 19:00 | 1.8481 | 1.9829 | 2.4615 | 2.5891 | 2.7167 | 2024-06-28 19:00 | 3.9058 | 4.5525 | 4.5525 | 4.5525 | 4.5525
2024-08-28 20:00 | 1.7338 | 1.8602 | 2.3092 | 2.429 | 2.5487 | 2024-06-28 20:00 | 3.4523 | 4.024 | 4.024 | 4.024 | 4.024
2024-08-28 21:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-06-28 21:00 | 2.957 | 3.4466 | 3.4466 | 3.4466 | 3.4466
2024-08-28 22:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-06-28 22:00 | 2.6674 | 3.109 | 3.109 | 3.109 | 3.109
2024-08-28 23:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-06-28 23:00 | 2.4235 | 2.8248 | 2.8248 | 2.8248 | 2.8248
2024-08-29 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-06-29 | 2.2749 | 2.6516 | 2.6516 | 2.6516 | 2.6516
2024-08-29 01:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-06-29 01:00 | 2.0958 | 2.4428 | 2.4428 | 2.4428 | 2.4428
2024-08-29 02:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-06-29 02:00 | 2.0539 | 2.394 | 2.394 | 2.394 | 2.394
2024-08-29 03:00 | 1.448 | 1.5536 | 1.9286 | 2.0286 | 2.1286 | 2024-06-29 03:00 | 2.1186 | 2.4695 | 2.4695 | 2.4695 | 2.4695
2024-08-29 04:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-06-29 04:00 | 2.5264 | 2.9447 | 2.9447 | 2.9447 | 2.9447
2024-08-29 05:00 | 1.7338 | 1.8602 | 2.3092 | 2.429 | 2.5487 | 2024-06-29 05:00 | 2.8388 | 3.3089 | 3.3089 | 3.3089 | 3.3089
2024-08-29 06:00 | 1.9624 | 2.1055 | 2.6137 | 2.7493 | 2.8848 | 2024-06-29 06:00 | 2.8122 | 3.2778 | 3.2778 | 3.2778 | 3.2778
2024-08-29 07:00 | 2.0196 | 2.1668 | 2.6899 | 2.8293 | 2.9688 | 2024-06-29 07:00 | 3.0903 | 3.602 | 3.602 | 3.602 | 3.602
2024-08-29 08:00 | 2.2482 | 2.4121 | 2.9944 | 3.1496 | 3.3049 | 2024-06-29 08:00 | 3.3609 | 3.9174 | 3.9174 | 3.9174 | 3.9174
2024-08-29 09:00 | 2.0577 | 2.2077 | 2.7406 | 2.8827 | 3.0248 | 2024-06-29 09:00 | 3.4142 | 3.9796 | 3.9796 | 3.9796 | 3.9796
2024-08-29 10:00 | 2.191 | 2.3508 | 2.9183 | 3.0696 | 3.2209 | 2024-06-29 10:00 | 3.5171 | 4.0995 | 4.0995 | 4.0995 | 4.0995
2024-08-29 11:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-06-29 11:00 | 3.7381 | 4.3571 | 4.3571 | 4.3571 | 4.3571
2024-08-29 12:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-06-29 12:00 | 3.8105 | 4.4415 | 4.4415 | 4.4415 | 4.4415
2024-08-29 13:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-06-29 13:00 | 3.761 | 4.3837 | 4.3837 | 4.3837 | 4.3837
2024-08-29 14:00 | 1.4289 | 1.5331 | 1.9032 | 2.0019 | 2.1006 | 2024-06-29 14:00 | 3.4942 | 4.0728 | 4.0728 | 4.0728 | 4.0728
2024-08-29 15:00 | 2.1148 | 2.2691 | 2.8167 | 2.9628 | 3.1089 | 2024-06-29 15:00 | 3.6581 | 4.2638 | 4.2638 | 4.2638 | 4.2638
2024-08-29 16:00 | 2.6293 | 2.821 | 3.5019 | 3.6835 | 3.8651 | 2024-06-29 16:00 | 3.5666 | 4.1572 | 4.1572 | 4.1572 | 4.1572
2024-08-29 17:00 | 2.0196 | 2.1668 | 2.6899 | 2.8293 | 2.9688 | 2024-06-29 17:00 | 3.5781 | 4.1706 | 4.1706 | 4.1706 | 4.1706
2024-08-29 18:00 | 2.0005 | 2.1464 | 2.6645 | 2.8026 | 2.9408 | 2024-06-29 18:00 | 3.0598 | 3.5665 | 3.5665 | 3.5665 | 3.5665
2024-08-29 19:00 | 1.81 | 1.942 | 2.4107 | 2.5357 | 2.6607 | 2024-06-29 19:00 | 2.7512 | 3.2068 | 3.2068 | 3.2068 | 3.2068
2024-08-29 20:00 | 1.7338 | 1.8602 | 2.3092 | 2.429 | 2.5487 | 2024-06-29 20:00 | 2.553 | 2.9758 | 2.9758 | 2.9758 | 2.9758
2024-08-29 21:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-06-29 21:00 | 2.3206 | 2.7049 | 2.7049 | 2.7049 | 2.7049
2024-08-29 22:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-06-29 22:00 | 2.313 | 2.696 | 2.696 | 2.696 | 2.696
2024-08-29 23:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-06-29 23:00 | 1.9319 | 2.2518 | 2.2518 | 2.2518 | 2.2518
2024-08-30 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-06-30 | 1.9396 | 2.2607 | 2.2607 | 2.2607 | 2.2607
2024-08-30 01:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-06-30 01:00 | 1.9014 | 2.2163 | 2.2163 | 2.2163 | 2.2163
2024-08-30 02:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-06-30 02:00 | 1.9319 | 2.2518 | 2.2518 | 2.2518 | 2.2518
2024-08-30 03:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-06-30 03:00 | 2.0577 | 2.3984 | 2.3984 | 2.3984 | 2.3984
2024-08-30 04:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-06-30 04:00 | 2.1606 | 2.5183 | 2.5183 | 2.5183 | 2.5183
2024-08-30 05:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-06-30 05:00 | 2.4121 | 2.8115 | 2.8115 | 2.8115 | 2.8115
2024-08-30 06:00 | 1.8862 | 2.0237 | 2.5122 | 2.6425 | 2.7728 | 2024-06-30 06:00 | 2.6788 | 3.1224 | 3.1224 | 3.1224 | 3.1224
2024-08-30 07:00 | 2.1529 | 2.3099 | 2.8675 | 3.0162 | 3.1649 | 2024-06-30 07:00 | 2.9608 | 3.451 | 3.451 | 3.451 | 3.451
2024-08-30 08:00 | 2.2291 | 2.3917 | 2.969 | 3.123 | 3.2769 | 2024-06-30 08:00 | 3.1627 | 3.6864 | 3.6864 | 3.6864 | 3.6864
2024-08-30 09:00 | 2.1148 | 2.2691 | 2.8167 | 2.9628 | 3.1089 | 2024-06-30 09:00 | 3.4409 | 4.0107 | 4.0107 | 4.0107 | 4.0107
2024-08-30 10:00 | 2.0196 | 2.1668 | 2.6899 | 2.8293 | 2.9688 | 2024-06-30 10:00 | 3.7724 | 4.3971 | 4.3971 | 4.3971 | 4.3971
2024-08-30 11:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-06-30 11:00 | 3.7495 | 4.3704 | 4.3704 | 4.3704 | 4.3704
2024-08-30 12:00 | 1.4099 | 1.5127 | 1.8778 | 1.9752 | 2.0726 | 2024-06-30 12:00 | 3.8296 | 4.4637 | 4.4637 | 4.4637 | 4.4637
2024-08-30 13:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-06-30 13:00 | 3.841 | 4.477 | 4.477 | 4.477 | 4.477
2024-08-30 14:00 | 1.8481 | 1.9829 | 2.4615 | 2.5891 | 2.7167 | 2024-06-30 14:00 | 3.6162 | 4.215 | 4.215 | 4.215 | 4.215
2024-08-30 15:00 | 1.8481 | 1.9829 | 2.4615 | 2.5891 | 2.7167 | 2024-06-30 15:00 | 3.4561 | 4.0284 | 4.0284 | 4.0284 | 4.0284
2024-08-30 16:00 | 1.9434 | 2.0851 | 2.5884 | 2.7226 | 2.8568 | 2024-06-30 16:00 | 3.5971 | 4.1928 | 4.1928 | 4.1928 | 4.1928
2024-08-30 17:00 | 1.8672 | 2.0033 | 2.4869 | 2.6158 | 2.7448 | 2024-06-30 17:00 | 3.5743 | 4.1661 | 4.1661 | 4.1661 | 4.1661
2024-08-30 18:00 | 1.8862 | 2.0237 | 2.5122 | 2.6425 | 2.7728 | 2024-06-30 18:00 | 3.1284 | 3.6465 | 3.6465 | 3.6465 | 3.6465
2024-08-30 19:00 | 1.7338 | 1.8602 | 2.3092 | 2.429 | 2.5487 | 2024-06-30 19:00 | 2.8426 | 3.3133 | 3.3133 | 3.3133 | 3.3133
2024-08-30 20:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-06-30 20:00 | 2.7741 | 3.2334 | 3.2334 | 3.2334 | 3.2334
2024-08-30 21:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-06-30 21:00 | 2.4921 | 2.9047 | 2.9047 | 2.9047 | 2.9047
2024-08-30 22:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-06-30 22:00 | 2.2253 | 2.5938 | 2.5938 | 2.5938 | 2.5938
2024-08-30 23:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-06-30 23:00 | 1.8938 | 2.2074 | 2.2074 | 2.2074 | 2.2074
2024-08-31 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-07-01 | 1.9243 | 2.243 | 2.243 | 2.243 | 2.243
2024-08-31 01:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-07-01 01:00 | 1.9053 | 2.2207 | 2.2207 | 2.2207 | 2.2207
2024-08-31 02:00 | 1.448 | 1.5536 | 1.9286 | 2.0286 | 2.1286 | 2024-07-01 02:00 | 1.9053 | 2.2207 | 2.2207 | 2.2207 | 2.2207
2024-08-31 03:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-07-01 03:00 | 2.111 | 2.4606 | 2.4606 | 2.4606 | 2.4606
2024-08-31 04:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-07-01 04:00 | 2.1606 | 2.5183 | 2.5183 | 2.5183 | 2.5183
2024-08-31 05:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-07-01 05:00 | 2.5302 | 2.9491 | 2.9491 | 2.9491 | 2.9491
2024-08-31 06:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-07-01 06:00 | 2.9684 | 3.4599 | 3.4599 | 3.4599 | 3.4599
2024-08-31 07:00 | 1.448 | 1.5536 | 1.9286 | 2.0286 | 2.1286 | 2024-07-01 07:00 | 3.418 | 3.984 | 3.984 | 3.984 | 3.984
2024-08-31 08:00 | 1.1241 | 1.2061 | 1.4972 | 1.5748 | 1.6525 | 2024-07-01 08:00 | 3.7114 | 4.326 | 4.326 | 4.326 | 4.326
2024-08-31 09:00 | 0.91452 | 0.98121 | 1.2181 | 1.2812 | 1.3444 | 2024-07-01 09:00 | 3.6695 | 4.2772 | 4.2772 | 4.2772 | 4.2772
2024-08-31 10:00 | 0.019053 | 0.020442 | 0.025376 | 0.026692 | 0.028008 | 2024-07-01 10:00 | 3.5285 | 4.1128 | 4.1128 | 4.1128 | 4.1128
2024-08-31 11:00 | 0.038105 | 0.040884 | 0.050752 | 0.053384 | 0.056015 | 2024-07-01 11:00 | 3.3761 | 3.9352 | 3.9352 | 3.9352 | 3.9352
2024-08-31 12:00 | 1.1241 | 1.2061 | 1.4972 | 1.5748 | 1.6525 | 2024-07-01 12:00 | 3.7534 | 4.3749 | 4.3749 | 4.3749 | 4.3749
2024-08-31 13:00 | 0.53347 | 0.57237 | 0.71053 | 0.74737 | 0.78422 | 2024-07-01 13:00 | 3.8943 | 4.5392 | 4.5392 | 4.5392 | 4.5392
2024-08-31 14:00 | 0.97168 | 1.0425 | 1.2942 | 1.3613 | 1.4284 | 2024-07-01 14:00 | 3.8753 | 4.517 | 4.517 | 4.517 | 4.517
2024-08-31 15:00 | 1.1813 | 1.2674 | 1.5733 | 1.6549 | 1.7365 | 2024-07-01 15:00 | 3.8372 | 4.4726 | 4.4726 | 4.4726 | 4.4726
2024-08-31 16:00 | 1.448 | 1.5536 | 1.9286 | 2.0286 | 2.1286 | 2024-07-01 16:00 | 4.0163 | 4.6813 | 4.6813 | 4.6813 | 4.6813
2024-08-31 17:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-07-01 17:00 | 3.9286 | 4.5792 | 4.5792 | 4.5792 | 4.5792
2024-08-31 18:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-07-01 18:00 | 3.5285 | 4.1128 | 4.1128 | 4.1128 | 4.1128
2024-08-31 19:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-07-01 19:00 | 3.0865 | 3.5976 | 3.5976 | 3.5976 | 3.5976
2024-08-31 20:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-07-01 20:00 | 2.9265 | 3.4111 | 3.4111 | 3.4111 | 3.4111
2024-08-31 21:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-07-01 21:00 | 2.5645 | 2.9891 | 2.9891 | 2.9891 | 2.9891
2024-08-31 22:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-07-01 22:00 | 2.092 | 2.4384 | 2.4384 | 2.4384 | 2.4384
2024-08-31 23:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-07-01 23:00 | 2.0158 | 2.3495 | 2.3495 | 2.3495 | 2.3495
2024-09-01 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-07-02 | 1.9281 | 2.2474 | 2.2474 | 2.2474 | 2.2474
2024-09-01 01:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-07-02 01:00 | 1.8938 | 2.2074 | 2.2074 | 2.2074 | 2.2074
2024-09-01 02:00 | 1.4289 | 1.5331 | 1.9032 | 2.0019 | 2.1006 | 2024-07-02 02:00 | 1.8252 | 2.1275 | 2.1275 | 2.1275 | 2.1275
2024-09-01 03:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-07-02 03:00 | 1.9319 | 2.2518 | 2.2518 | 2.2518 | 2.2518
2024-09-01 04:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-07-02 04:00 | 2.1758 | 2.5361 | 2.5361 | 2.5361 | 2.5361
2024-09-01 05:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-07-02 05:00 | 2.4654 | 2.8736 | 2.8736 | 2.8736 | 2.8736
2024-09-01 06:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-07-02 06:00 | 2.9112 | 3.3933 | 3.3933 | 3.3933 | 3.3933
2024-09-01 07:00 | 1.3908 | 1.4923 | 1.8525 | 1.9485 | 2.0446 | 2024-07-02 07:00 | 3.2999 | 3.8463 | 3.8463 | 3.8463 | 3.8463
2024-09-01 08:00 | 0.24768 | 0.26574 | 0.32989 | 0.34699 | 0.3641 | 2024-07-02 08:00 | 3.7343 | 4.3527 | 4.3527 | 4.3527 | 4.3527
2024-09-01 09:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-07-02 09:00 | 3.8905 | 4.5348 | 4.5348 | 4.5348 | 4.5348
2024-09-01 10:00 | 0.019053 | 0.020442 | 0.025376 | 0.026692 | 0.028008 | 2024-07-02 10:00 | 3.9706 | 4.628 | 4.628 | 4.628 | 4.628
2024-09-01 11:00 | 0 | 0 | 0 | 0 | 0 | 2024-07-02 11:00 | 3.8791 | 4.5214 | 4.5214 | 4.5214 | 4.5214
2024-09-01 12:00 | 0 | 0 | 0 | 0 | 0 | 2024-07-02 12:00 | 4.2259 | 4.9256 | 4.9256 | 4.9256 | 4.9256
2024-09-01 13:00 | 0.057158 | 0.061326 | 0.076128 | 0.080076 | 0.084023 | 2024-07-02 13:00 | 4.0849 | 4.7613 | 4.7613 | 4.7613 | 4.7613
2024-09-01 14:00 | 0.019053 | 0.020442 | 0.025376 | 0.026692 | 0.028008 | 2024-07-02 14:00 | 3.6352 | 4.2372 | 4.2372 | 4.2372 | 4.2372
2024-09-01 15:00 | 0.4001 | 0.42928 | 0.5329 | 0.56053 | 0.58816 | 2024-07-02 15:00 | 3.9553 | 4.6103 | 4.6103 | 4.6103 | 4.6103
2024-09-01 16:00 | 1.3146 | 1.4105 | 1.751 | 1.8417 | 1.9325 | 2024-07-02 16:00 | 3.9706 | 4.628 | 4.628 | 4.628 | 4.628
2024-09-01 17:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-07-02 17:00 | 3.8639 | 4.5037 | 4.5037 | 4.5037 | 4.5037
2024-09-01 18:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-07-02 18:00 | 3.5438 | 4.1306 | 4.1306 | 4.1306 | 4.1306
2024-09-01 19:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-07-02 19:00 | 3.1284 | 3.6465 | 3.6465 | 3.6465 | 3.6465
2024-09-01 20:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-07-02 20:00 | 3.0598 | 3.5665 | 3.5665 | 3.5665 | 3.5665
2024-09-01 21:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-07-02 21:00 | 2.5111 | 2.9269 | 2.9269 | 2.9269 | 2.9269
2024-09-01 22:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-07-02 22:00 | 2.3473 | 2.736 | 2.736 | 2.736 | 2.736
2024-09-01 23:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-07-02 23:00 | 2.092 | 2.4384 | 2.4384 | 2.4384 | 2.4384
2024-09-02 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-07-03 | 1.9853 | 2.314 | 2.314 | 2.314 | 2.314
2024-09-02 01:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-07-03 01:00 | 1.9815 | 2.3096 | 2.3096 | 2.3096 | 2.3096
2024-09-02 02:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-07-03 02:00 | 1.8786 | 2.1897 | 2.1897 | 2.1897 | 2.1897
2024-09-02 03:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-07-03 03:00 | 1.9891 | 2.3185 | 2.3185 | 2.3185 | 2.3185
2024-09-02 04:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-07-03 04:00 | 2.4273 | 2.8292 | 2.8292 | 2.8292 | 2.8292
2024-09-02 05:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-07-03 05:00 | 2.5797 | 3.0069 | 3.0069 | 3.0069 | 3.0069
2024-09-02 06:00 | 1.7909 | 1.9215 | 2.3854 | 2.509 | 2.6327 | 2024-07-03 06:00 | 2.9189 | 3.4022 | 3.4022 | 3.4022 | 3.4022
2024-09-02 07:00 | 2.2482 | 2.4121 | 2.9944 | 3.1496 | 3.3049 | 2024-07-03 07:00 | 3.3037 | 3.8508 | 3.8508 | 3.8508 | 3.8508
2024-09-02 08:00 | 2.3816 | 2.5552 | 3.172 | 3.3365 | 3.501 | 2024-07-03 08:00 | 3.3571 | 3.913 | 3.913 | 3.913 | 3.913
2024-09-02 09:00 | 2.0767 | 2.2282 | 2.766 | 2.9094 | 3.0528 | 2024-07-03 09:00 | 3.5857 | 4.1794 | 4.1794 | 4.1794 | 4.1794
2024-09-02 10:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-07-03 10:00 | 3.7381 | 4.3571 | 4.3571 | 4.3571 | 4.3571
2024-09-02 11:00 | 1.9243 | 2.0646 | 2.563 | 2.6959 | 2.8288 | 2024-07-03 11:00 | 3.5247 | 4.1084 | 4.1084 | 4.1084 | 4.1084
2024-09-02 12:00 | 2.0196 | 2.1668 | 2.6899 | 2.8293 | 2.9688 | 2024-07-03 12:00 | 4.1306 | 4.8146 | 4.8146 | 4.8146 | 4.8146
2024-09-02 13:00 | 1.8672 | 2.0033 | 2.4869 | 2.6158 | 2.7448 | 2024-07-03 13:00 | 3.5628 | 4.1528 | 4.1528 | 4.1528 | 4.1528
2024-09-02 14:00 | 1.8672 | 2.0033 | 2.4869 | 2.6158 | 2.7448 | 2024-07-03 14:00 | 3.8982 | 4.5436 | 4.5436 | 4.5436 | 4.5436
2024-09-02 15:00 | 2.1148 | 2.2691 | 2.8167 | 2.9628 | 3.1089 | 2024-07-03 15:00 | 3.9172 | 4.5658 | 4.5658 | 4.5658 | 4.5658
2024-09-02 16:00 | 2.2291 | 2.3917 | 2.969 | 3.123 | 3.2769 | 2024-07-03 16:00 | 4.1611 | 4.8501 | 4.8501 | 4.8501 | 4.8501
2024-09-02 17:00 | 2.2101 | 2.3713 | 2.9436 | 3.0963 | 3.2489 | 2024-07-03 17:00 | 4.2983 | 5.01 | 5.01 | 5.01 | 5.01
2024-09-02 18:00 | 2.172 | 2.3304 | 2.8929 | 3.0429 | 3.1929 | 2024-07-03 18:00 | 3.498 | 4.0773 | 4.0773 | 4.0773 | 4.0773
2024-09-02 19:00 | 1.8481 | 1.9829 | 2.4615 | 2.5891 | 2.7167 | 2024-07-03 19:00 | 3.5704 | 4.1617 | 4.1617 | 4.1617 | 4.1617
2024-09-02 20:00 | 1.7528 | 1.8807 | 2.3346 | 2.4557 | 2.5767 | 2024-07-03 20:00 | 3.2275 | 3.7619 | 3.7619 | 3.7619 | 3.7619
2024-09-02 21:00 | 1.829 | 1.9624 | 2.4361 | 2.5624 | 2.6887 | 2024-07-03 21:00 | 2.6864 | 3.1312 | 3.1312 | 3.1312 | 3.1312
2024-09-02 22:00 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 2024-07-03 22:00 | 2.4463 | 2.8514 | 2.8514 | 2.8514 | 2.8514
2024-09-02 23:00 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 2024-07-03 23:00 | 2.4387 | 2.8426 | 2.8426 | 2.8426 | 2.8426
2024-09-03 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-07-04 | 2.1606 | 2.5183 | 2.5183 | 2.5183 | 2.5183
2024-09-03 01:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-07-04 01:00 | 2.1377 | 2.4917 | 2.4917 | 2.4917 | 2.4917
2024-09-03 02:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-07-04 02:00 | 2.1225 | 2.4739 | 2.4739 | 2.4739 | 2.4739
2024-09-03 03:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-07-04 03:00 | 2.3092 | 2.6915 | 2.6915 | 2.6915 | 2.6915
2024-09-03 04:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-07-04 04:00 | 2.4616 | 2.8692 | 2.8692 | 2.8692 | 2.8692
2024-09-03 05:00 | 1.8862 | 2.0237 | 2.5122 | 2.6425 | 2.7728 | 2024-07-04 05:00 | 2.8236 | 3.2911 | 3.2911 | 3.2911 | 3.2911
2024-09-03 06:00 | 1.8862 | 2.0237 | 2.5122 | 2.6425 | 2.7728 | 2024-07-04 06:00 | 3.3494 | 3.9041 | 3.9041 | 3.9041 | 3.9041
2024-09-03 07:00 | 1.9624 | 2.1055 | 2.6137 | 2.7493 | 2.8848 | 2024-07-04 07:00 | 3.8677 | 4.5081 | 4.5081 | 4.5081 | 4.5081
2024-09-03 08:00 | 2.2101 | 2.3713 | 2.9436 | 3.0963 | 3.2489 | 2024-07-04 08:00 | 4.1001 | 4.779 | 4.779 | 4.779 | 4.779
2024-09-03 09:00 | 1.8481 | 1.9829 | 2.4615 | 2.5891 | 2.7167 | 2024-07-04 09:00 | 4.4164 | 5.1477 | 5.1477 | 5.1477 | 5.1477
2024-09-03 10:00 | 1.8481 | 1.9829 | 2.4615 | 2.5891 | 2.7167 | 2024-07-04 10:00 | 4.0849 | 4.7613 | 4.7613 | 4.7613 | 4.7613
2024-09-03 11:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-07-04 11:00 | 4.1801 | 4.8723 | 4.8723 | 4.8723 | 4.8723
2024-09-03 12:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-07-04 12:00 | 4.0887 | 4.7657 | 4.7657 | 4.7657 | 4.7657
2024-09-03 13:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-07-04 13:00 | 4.2944 | 5.0056 | 5.0056 | 5.0056 | 5.0056
2024-09-03 14:00 | 1.4099 | 1.5127 | 1.8778 | 1.9752 | 2.0726 | 2024-07-04 14:00 | 4.4164 | 5.1477 | 5.1477 | 5.1477 | 5.1477
2024-09-03 15:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-07-04 15:00 | 4.3364 | 5.0544 | 5.0544 | 5.0544 | 5.0544
2024-09-03 16:00 | 2.172 | 2.3304 | 2.8929 | 3.0429 | 3.1929 | 2024-07-04 16:00 | 4.4659 | 5.2054 | 5.2054 | 5.2054 | 5.2054
2024-09-03 17:00 | 2.1148 | 2.2691 | 2.8167 | 2.9628 | 3.1089 | 2024-07-04 17:00 | 4.4354 | 5.1699 | 5.1699 | 5.1699 | 5.1699
2024-09-03 18:00 | 2.0958 | 2.2486 | 2.7914 | 2.9361 | 3.0808 | 2024-07-04 18:00 | 3.7191 | 4.3349 | 4.3349 | 4.3349 | 4.3349
2024-09-03 19:00 | 1.8481 | 1.9829 | 2.4615 | 2.5891 | 2.7167 | 2024-07-04 19:00 | 3.4561 | 4.0284 | 4.0284 | 4.0284 | 4.0284
2024-09-03 20:00 | 1.7909 | 1.9215 | 2.3854 | 2.509 | 2.6327 | 2024-07-04 20:00 | 3.1399 | 3.6598 | 3.6598 | 3.6598 | 3.6598
2024-09-03 21:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-07-04 21:00 | 2.8693 | 3.3444 | 3.3444 | 3.3444 | 3.3444
2024-09-03 22:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-07-04 22:00 | 2.5264 | 2.9447 | 2.9447 | 2.9447 | 2.9447
2024-09-03 23:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-07-04 23:00 | 2.4425 | 2.847 | 2.847 | 2.847 | 2.847
2024-09-04 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-07-05 | 2.3397 | 2.7271 | 2.7271 | 2.7271 | 2.7271
2024-09-04 01:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-07-05 01:00 | 2.3092 | 2.6915 | 2.6915 | 2.6915 | 2.6915
2024-09-04 02:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-07-05 02:00 | 2.3739 | 2.767 | 2.767 | 2.767 | 2.767
2024-09-04 03:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-07-05 03:00 | 2.393 | 2.7893 | 2.7893 | 2.7893 | 2.7893
2024-09-04 04:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-07-05 04:00 | 2.7779 | 3.2378 | 3.2378 | 3.2378 | 3.2378
2024-09-04 05:00 | 1.8862 | 2.0237 | 2.5122 | 2.6425 | 2.7728 | 2024-07-05 05:00 | 3.0903 | 3.602 | 3.602 | 3.602 | 3.602
2024-09-04 06:00 | 2.0386 | 2.1873 | 2.7152 | 2.856 | 2.9968 | 2024-07-05 06:00 | 3.4257 | 3.9929 | 3.9929 | 3.9929 | 3.9929
2024-09-04 07:00 | 2.3244 | 2.4939 | 3.0959 | 3.2564 | 3.4169 | 2024-07-05 07:00 | 3.7534 | 4.3749 | 4.3749 | 4.3749 | 4.3749
2024-09-04 08:00 | 2.4387 | 2.6166 | 3.2481 | 3.4166 | 3.585 | 2024-07-05 08:00 | 3.9248 | 4.5747 | 4.5747 | 4.5747 | 4.5747
2024-09-04 09:00 | 2.0577 | 2.2077 | 2.7406 | 2.8827 | 3.0248 | 2024-07-05 09:00 | 4.0239 | 4.6902 | 4.6902 | 4.6902 | 4.6902
2024-09-04 10:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-07-05 10:00 | 4.0734 | 4.7479 | 4.7479 | 4.7479 | 4.7479
2024-09-04 11:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-07-05 11:00 | 4.1916 | 4.8856 | 4.8856 | 4.8856 | 4.8856
2024-09-04 12:00 | 1.9434 | 2.0851 | 2.5884 | 2.7226 | 2.8568 | 2024-07-05 12:00 | 4.3097 | 5.0233 | 5.0233 | 5.0233 | 5.0233
2024-09-04 13:00 | 1.7528 | 1.8807 | 2.3346 | 2.4557 | 2.5767 | 2024-07-05 13:00 | 4.0468 | 4.7169 | 4.7169 | 4.7169 | 4.7169
2024-09-04 14:00 | 1.81 | 1.942 | 2.4107 | 2.5357 | 2.6607 | 2024-07-05 14:00 | 3.902 | 4.5481 | 4.5481 | 4.5481 | 4.5481
2024-09-04 15:00 | 1.448 | 1.5536 | 1.9286 | 2.0286 | 2.1286 | 2024-07-05 15:00 | 3.9439 | 4.5969 | 4.5969 | 4.5969 | 4.5969
2024-09-04 16:00 | 2.0386 | 2.1873 | 2.7152 | 2.856 | 2.9968 | 2024-07-05 16:00 | 4.1649 | 4.8545 | 4.8545 | 4.8545 | 4.8545
2024-09-04 17:00 | 2.1148 | 2.2691 | 2.8167 | 2.9628 | 3.1089 | 2024-07-05 17:00 | 4.1192 | 4.8012 | 4.8012 | 4.8012 | 4.8012
2024-09-04 18:00 | 1.9434 | 2.0851 | 2.5884 | 2.7226 | 2.8568 | 2024-07-05 18:00 | 3.5819 | 4.175 | 4.175 | 4.175 | 4.175
2024-09-04 19:00 | 1.9434 | 2.0851 | 2.5884 | 2.7226 | 2.8568 | 2024-07-05 19:00 | 3.4104 | 3.9751 | 3.9751 | 3.9751 | 3.9751
2024-09-04 20:00 | 1.7528 | 1.8807 | 2.3346 | 2.4557 | 2.5767 | 2024-07-05 20:00 | 3.0217 | 3.5221 | 3.5221 | 3.5221 | 3.5221
2024-09-04 21:00 | 1.7909 | 1.9215 | 2.3854 | 2.509 | 2.6327 | 2024-07-05 21:00 | 2.8579 | 3.3311 | 3.3311 | 3.3311 | 3.3311
2024-09-04 22:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-07-05 22:00 | 2.233 | 2.6027 | 2.6027 | 2.6027 | 2.6027
2024-09-04 23:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-07-05 23:00 | 2.0805 | 2.4251 | 2.4251 | 2.4251 | 2.4251
2024-09-05 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-07-06 | 1.9815 | 2.3096 | 2.3096 | 2.3096 | 2.3096
2024-09-05 01:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-07-06 01:00 | 1.8481 | 2.1541 | 2.1541 | 2.1541 | 2.1541
2024-09-05 02:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-07-06 02:00 | 1.9053 | 2.2207 | 2.2207 | 2.2207 | 2.2207
2024-09-05 03:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-07-06 03:00 | 1.9929 | 2.3229 | 2.3229 | 2.3229 | 2.3229
2024-09-05 04:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-07-06 04:00 | 2.2291 | 2.5983 | 2.5983 | 2.5983 | 2.5983
2024-09-05 05:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-07-06 05:00 | 2.4159 | 2.8159 | 2.8159 | 2.8159 | 2.8159
2024-09-05 06:00 | 1.829 | 1.9624 | 2.4361 | 2.5624 | 2.6887 | 2024-07-06 06:00 | 2.6597 | 3.1002 | 3.1002 | 3.1002 | 3.1002
2024-09-05 07:00 | 1.9815 | 2.126 | 2.6391 | 2.776 | 2.9128 | 2024-07-06 07:00 | 3.0903 | 3.602 | 3.602 | 3.602 | 3.602
2024-09-05 08:00 | 1.7528 | 1.8807 | 2.3346 | 2.4557 | 2.5767 | 2024-07-06 08:00 | 3.2046 | 3.7353 | 3.7353 | 3.7353 | 3.7353
2024-09-05 09:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-07-06 09:00 | 3.3799 | 3.9396 | 3.9396 | 3.9396 | 3.9396
2024-09-05 10:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-07-06 10:00 | 3.1818 | 3.7086 | 3.7086 | 3.7086 | 3.7086
2024-09-05 11:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-07-06 11:00 | 3.399 | 3.9618 | 3.9618 | 3.9618 | 3.9618
2024-09-05 12:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-07-06 12:00 | 3.2085 | 3.7397 | 3.7397 | 3.7397 | 3.7397
2024-09-05 13:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-07-06 13:00 | 3.2542 | 3.793 | 3.793 | 3.793 | 3.793
2024-09-05 14:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-07-06 14:00 | 3.0103 | 3.5088 | 3.5088 | 3.5088 | 3.5088
2024-09-05 15:00 | 2.0005 | 2.1464 | 2.6645 | 2.8026 | 2.9408 | 2024-07-06 15:00 | 3.1665 | 3.6909 | 3.6909 | 3.6909 | 3.6909
2024-09-05 16:00 | 2.0005 | 2.1464 | 2.6645 | 2.8026 | 2.9408 | 2024-07-06 16:00 | 3.4828 | 4.0595 | 4.0595 | 4.0595 | 4.0595
2024-09-05 17:00 | 2.0958 | 2.2486 | 2.7914 | 2.9361 | 3.0808 | 2024-07-06 17:00 | 3.338 | 3.8907 | 3.8907 | 3.8907 | 3.8907
2024-09-05 18:00 | 1.9815 | 2.126 | 2.6391 | 2.776 | 2.9128 | 2024-07-06 18:00 | 2.9951 | 3.491 | 3.491 | 3.491 | 3.491
2024-09-05 19:00 | 1.7909 | 1.9215 | 2.3854 | 2.509 | 2.6327 | 2024-07-06 19:00 | 2.5988 | 3.0291 | 3.0291 | 3.0291 | 3.0291
2024-09-05 20:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-07-06 20:00 | 2.3015 | 2.6827 | 2.6827 | 2.6827 | 2.6827
2024-09-05 21:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-07-06 21:00 | 2.2291 | 2.5983 | 2.5983 | 2.5983 | 2.5983
2024-09-05 22:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-07-06 22:00 | 2.0691 | 2.4117 | 2.4117 | 2.4117 | 2.4117
2024-09-05 23:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-07-06 23:00 | 2.0653 | 2.4073 | 2.4073 | 2.4073 | 2.4073
2024-09-06 | 1.448 | 1.5536 | 1.9286 | 2.0286 | 2.1286 | 2024-07-07 | 1.9091 | 2.2252 | 2.2252 | 2.2252 | 2.2252
2024-09-06 01:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-07-07 01:00 | 1.7948 | 2.0919 | 2.0919 | 2.0919 | 2.0919
2024-09-06 02:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-07-07 02:00 | 1.8938 | 2.2074 | 2.2074 | 2.2074 | 2.2074
2024-09-06 03:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-07-07 03:00 | 1.9319 | 2.2518 | 2.2518 | 2.2518 | 2.2518
2024-09-06 04:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-07-07 04:00 | 2.111 | 2.4606 | 2.4606 | 2.4606 | 2.4606
2024-09-06 05:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-07-07 05:00 | 2.3892 | 2.7848 | 2.7848 | 2.7848 | 2.7848
2024-09-06 06:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-07-07 06:00 | 2.5797 | 3.0069 | 3.0069 | 3.0069 | 3.0069
2024-09-06 07:00 | 1.829 | 1.9624 | 2.4361 | 2.5624 | 2.6887 | 2024-07-07 07:00 | 2.9074 | 3.3889 | 3.3889 | 3.3889 | 3.3889
2024-09-06 08:00 | 1.3718 | 1.4718 | 1.8271 | 1.9218 | 2.0166 | 2024-07-07 08:00 | 2.8426 | 3.3133 | 3.3133 | 3.3133 | 3.3133
2024-09-06 09:00 | 1.1813 | 1.2674 | 1.5733 | 1.6549 | 1.7365 | 2024-07-07 09:00 | 3.1742 | 3.6998 | 3.6998 | 3.6998 | 3.6998
2024-09-06 10:00 | 1.2384 | 1.3287 | 1.6494 | 1.735 | 1.8205 | 2024-07-07 10:00 | 3.3723 | 3.9307 | 3.9307 | 3.9307 | 3.9307
2024-09-06 11:00 | 1.2194 | 1.3083 | 1.6241 | 1.7083 | 1.7925 | 2024-07-07 11:00 | 3.4218 | 3.9885 | 3.9885 | 3.9885 | 3.9885
2024-09-06 12:00 | 1.3337 | 1.4309 | 1.7763 | 1.8684 | 1.9605 | 2024-07-07 12:00 | 3.6352 | 4.2372 | 4.2372 | 4.2372 | 4.2372
2024-09-06 13:00 | 1.3527 | 1.4514 | 1.8017 | 1.8951 | 1.9885 | 2024-07-07 13:00 | 3.5666 | 4.1572 | 4.1572 | 4.1572 | 4.1572
2024-09-06 14:00 | 1.2765 | 1.3696 | 1.7002 | 1.7884 | 1.8765 | 2024-07-07 14:00 | 3.5362 | 4.1217 | 4.1217 | 4.1217 | 4.1217
2024-09-06 15:00 | 1.3146 | 1.4105 | 1.751 | 1.8417 | 1.9325 | 2024-07-07 15:00 | 3.3342 | 3.8863 | 3.8863 | 3.8863 | 3.8863
2024-09-06 16:00 | 1.8672 | 2.0033 | 2.4869 | 2.6158 | 2.7448 | 2024-07-07 16:00 | 3.4447 | 4.0151 | 4.0151 | 4.0151 | 4.0151
2024-09-06 17:00 | 2.0005 | 2.1464 | 2.6645 | 2.8026 | 2.9408 | 2024-07-07 17:00 | 3.4333 | 4.0018 | 4.0018 | 4.0018 | 4.0018
2024-09-06 18:00 | 1.9053 | 2.0442 | 2.5376 | 2.6692 | 2.8008 | 2024-07-07 18:00 | 3.0408 | 3.5443 | 3.5443 | 3.5443 | 3.5443
2024-09-06 19:00 | 1.8862 | 2.0237 | 2.5122 | 2.6425 | 2.7728 | 2024-07-07 19:00 | 2.7131 | 3.1623 | 3.1623 | 3.1623 | 3.1623
2024-09-06 20:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-07-07 20:00 | 2.5645 | 2.9891 | 2.9891 | 2.9891 | 2.9891
2024-09-06 21:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-07-07 21:00 | 2.3473 | 2.736 | 2.736 | 2.736 | 2.736
2024-09-06 22:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-07-07 22:00 | 2.0462 | 2.3851 | 2.3851 | 2.3851 | 2.3851
2024-09-06 23:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-07-07 23:00 | 2.0386 | 2.3762 | 2.3762 | 2.3762 | 2.3762
2024-09-07 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-07-08 | 1.8405 | 2.1452 | 2.1452 | 2.1452 | 2.1452
2024-09-07 01:00 | 1.4289 | 1.5331 | 1.9032 | 2.0019 | 2.1006 | 2024-07-08 01:00 | 1.8062 | 2.1053 | 2.1053 | 2.1053 | 2.1053
2024-09-07 02:00 | 1.3908 | 1.4923 | 1.8525 | 1.9485 | 2.0446 | 2024-07-08 02:00 | 1.871 | 2.1808 | 2.1808 | 2.1808 | 2.1808
2024-09-07 03:00 | 1.448 | 1.5536 | 1.9286 | 2.0286 | 2.1286 | 2024-07-08 03:00 | 1.9243 | 2.243 | 2.243 | 2.243 | 2.243
2024-09-07 04:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-07-08 04:00 | 2.1949 | 2.5583 | 2.5583 | 2.5583 | 2.5583
2024-09-07 05:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-07-08 05:00 | 2.4921 | 2.9047 | 2.9047 | 2.9047 | 2.9047
2024-09-07 06:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-07-08 06:00 | 3.0675 | 3.5754 | 3.5754 | 3.5754 | 3.5754
2024-09-07 07:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-07-08 07:00 | 3.62 | 4.2194 | 4.2194 | 4.2194 | 4.2194
2024-09-07 08:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-07-08 08:00 | 3.8829 | 4.5259 | 4.5259 | 4.5259 | 4.5259
2024-09-07 09:00 | 1.3908 | 1.4923 | 1.8525 | 1.9485 | 2.0446 | 2024-07-08 09:00 | 3.8943 | 4.5392 | 4.5392 | 4.5392 | 4.5392
2024-09-07 10:00 | 1.0669 | 1.1447 | 1.4211 | 1.4947 | 1.5684 | 2024-07-08 10:00 | 4.0506 | 4.7213 | 4.7213 | 4.7213 | 4.7213
2024-09-07 11:00 | 0.59063 | 0.6337 | 0.78666 | 0.82745 | 0.86824 | 2024-07-08 11:00 | 3.9134 | 4.5614 | 4.5614 | 4.5614 | 4.5614
2024-09-07 12:00 | 1.0288 | 1.1039 | 1.3703 | 1.4414 | 1.5124 | 2024-07-08 12:00 | 3.9439 | 4.5969 | 4.5969 | 4.5969 | 4.5969
2024-09-07 13:00 | 0.68589 | 0.73591 | 0.91354 | 0.96091 | 1.0083 | 2024-07-08 13:00 | 3.902 | 4.5481 | 4.5481 | 4.5481 | 4.5481
2024-09-07 14:00 | 0.97168 | 1.0425 | 1.2942 | 1.3613 | 1.4284 | 2024-07-08 14:00 | 3.7876 | 4.4148 | 4.4148 | 4.4148 | 4.4148
2024-09-07 15:00 | 1.2003 | 1.2878 | 1.5987 | 1.6816 | 1.7645 | 2024-07-08 15:00 | 3.8029 | 4.4326 | 4.4326 | 4.4326 | 4.4326
2024-09-07 16:00 | 1.1813 | 1.2674 | 1.5733 | 1.6549 | 1.7365 | 2024-07-08 16:00 | 3.8867 | 4.5303 | 4.5303 | 4.5303 | 4.5303
2024-09-07 17:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-07-08 17:00 | 3.7762 | 4.4015 | 4.4015 | 4.4015 | 4.4015
2024-09-07 18:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-07-08 18:00 | 3.3875 | 3.9485 | 3.9485 | 3.9485 | 3.9485
2024-09-07 19:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-07-08 19:00 | 2.9684 | 3.4599 | 3.4599 | 3.4599 | 3.4599
2024-09-07 20:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-07-08 20:00 | 2.7131 | 3.1623 | 3.1623 | 3.1623 | 3.1623
2024-09-07 21:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-07-08 21:00 | 2.3282 | 2.7137 | 2.7137 | 2.7137 | 2.7137
2024-09-07 22:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-07-08 22:00 | 2.172 | 2.5316 | 2.5316 | 2.5316 | 2.5316
2024-09-07 23:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-07-08 23:00 | 1.9929 | 2.3229 | 2.3229 | 2.3229 | 2.3229
2024-09-08 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-07-09 | 1.8862 | 2.1985 | 2.1985 | 2.1985 | 2.1985
2024-09-08 01:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-07-09 01:00 | 1.7948 | 2.0919 | 2.0919 | 2.0919 | 2.0919
2024-09-08 02:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-07-09 02:00 | 1.7909 | 2.0875 | 2.0875 | 2.0875 | 2.0875
2024-09-08 03:00 | 1.448 | 1.5536 | 1.9286 | 2.0286 | 2.1286 | 2024-07-09 03:00 | 1.951 | 2.274 | 2.274 | 2.274 | 2.274
2024-09-08 04:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-07-09 04:00 | 2.1225 | 2.4739 | 2.4739 | 2.4739 | 2.4739
2024-09-08 05:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-07-09 05:00 | 2.4235 | 2.8248 | 2.8248 | 2.8248 | 2.8248
2024-09-08 06:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-07-09 06:00 | 2.9303 | 3.4155 | 3.4155 | 3.4155 | 3.4155
2024-09-08 07:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-07-09 07:00 | 3.5285 | 4.1128 | 4.1128 | 4.1128 | 4.1128
2024-09-08 08:00 | 1.2956 | 1.39 | 1.7256 | 1.815 | 1.9045 | 2024-07-09 08:00 | 3.7762 | 4.4015 | 4.4015 | 4.4015 | 4.4015
2024-09-08 09:00 | 0 | 0 | 0 | 0 | 0 | 2024-07-09 09:00 | 3.9896 | 4.6502 | 4.6502 | 4.6502 | 4.6502
2024-09-08 10:00 | 0.64779 | 0.69502 | 0.86279 | 0.90752 | 0.95226 | 2024-07-09 10:00 | 3.8143 | 4.4459 | 4.4459 | 4.4459 | 4.4459
2024-09-08 11:00 | 0.62873 | 0.67458 | 0.83741 | 0.88083 | 0.92425 | 2024-07-09 11:00 | 3.9629 | 4.6191 | 4.6191 | 4.6191 | 4.6191
2024-09-08 12:00 | 0.724 | 0.77679 | 0.96429 | 1.0143 | 1.0643 | 2024-07-09 12:00 | 3.9172 | 4.5658 | 4.5658 | 4.5658 | 4.5658
2024-09-08 13:00 | 0.7621 | 0.81768 | 1.015 | 1.0677 | 1.1203 | 2024-07-09 13:00 | 3.9515 | 4.6058 | 4.6058 | 4.6058 | 4.6058
2024-09-08 14:00 | 0.022625 | 0.024275 | 0.030134 | 0.031697 | 0.033259 | 2024-07-09 14:00 | 3.8067 | 4.437 | 4.437 | 4.437 | 4.437
2024-09-08 15:00 | 0.22863 | 0.2453 | 0.30451 | 0.3203 | 0.33609 | 2024-07-09 15:00 | 3.7686 | 4.3926 | 4.3926 | 4.3926 | 4.3926
2024-09-08 16:00 | 1.3908 | 1.4923 | 1.8525 | 1.9485 | 2.0446 | 2024-07-09 16:00 | 3.9477 | 4.6014 | 4.6014 | 4.6014 | 4.6014
2024-09-08 17:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-07-09 17:00 | 3.8905 | 4.5348 | 4.5348 | 4.5348 | 4.5348
2024-09-08 18:00 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 2024-07-09 18:00 | 3.3266 | 3.8774 | 3.8774 | 3.8774 | 3.8774
2024-09-08 19:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-07-09 19:00 | 2.6902 | 3.1357 | 3.1357 | 3.1357 | 3.1357
2024-09-08 20:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-07-09 20:00 | 2.5988 | 3.0291 | 3.0291 | 3.0291 | 3.0291
2024-09-08 21:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-07-09 21:00 | 2.454 | 2.8603 | 2.8603 | 2.8603 | 2.8603
2024-09-08 22:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-07-09 22:00 | 2.0196 | 2.354 | 2.354 | 2.354 | 2.354
2024-09-08 23:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-07-09 23:00 | 1.8557 | 2.163 | 2.163 | 2.163 | 2.163
2024-09-09 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-07-10 | 1.7376 | 2.0253 | 2.0253 | 2.0253 | 2.0253
2024-09-09 01:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-07-10 01:00 | 1.7033 | 1.9853 | 1.9853 | 1.9853 | 1.9853
2024-09-09 02:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-07-10 02:00 | 1.6919 | 1.972 | 1.972 | 1.972 | 1.972
2024-09-09 03:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-07-10 03:00 | 1.9472 | 2.2696 | 2.2696 | 2.2696 | 2.2696
2024-09-09 04:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-07-10 04:00 | 2.1301 | 2.4828 | 2.4828 | 2.4828 | 2.4828
2024-09-09 05:00 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 2024-07-10 05:00 | 2.3473 | 2.736 | 2.736 | 2.736 | 2.736
2024-09-09 06:00 | 1.7528 | 1.8807 | 2.3346 | 2.4557 | 2.5767 | 2024-07-10 06:00 | 2.7359 | 3.189 | 3.189 | 3.189 | 3.189
2024-09-09 07:00 | 1.9053 | 2.0442 | 2.5376 | 2.6692 | 2.8008 | 2024-07-10 07:00 | 3.4752 | 4.0506 | 4.0506 | 4.0506 | 4.0506
2024-09-09 08:00 | 1.448 | 1.5536 | 1.9286 | 2.0286 | 2.1286 | 2024-07-10 08:00 | 3.78 | 4.406 | 4.406 | 4.406 | 4.406
2024-09-09 09:00 | 1.2956 | 1.39 | 1.7256 | 1.815 | 1.9045 | 2024-07-10 09:00 | 3.7076 | 4.3216 | 4.3216 | 4.3216 | 4.3216
2024-09-09 10:00 | 1.7909 | 1.9215 | 2.3854 | 2.509 | 2.6327 | 2024-07-10 10:00 | 4.0506 | 4.7213 | 4.7213 | 4.7213 | 4.7213
2024-09-09 11:00 | 1.105 | 1.1856 | 1.4718 | 1.5481 | 1.6244 | 2024-07-10 11:00 | 3.7495 | 4.3704 | 4.3704 | 4.3704 | 4.3704
2024-09-09 12:00 | 1.7719 | 1.9011 | 2.36 | 2.4823 | 2.6047 | 2024-07-10 12:00 | 3.54 | 4.1261 | 4.1261 | 4.1261 | 4.1261
2024-09-09 13:00 | 1.829 | 1.9624 | 2.4361 | 2.5624 | 2.6887 | 2024-07-10 13:00 | 3.6162 | 4.215 | 4.215 | 4.215 | 4.215
2024-09-09 14:00 | 1.829 | 1.9624 | 2.4361 | 2.5624 | 2.6887 | 2024-07-10 14:00 | 3.559 | 4.1483 | 4.1483 | 4.1483 | 4.1483
2024-09-09 15:00 | 1.829 | 1.9624 | 2.4361 | 2.5624 | 2.6887 | 2024-07-10 15:00 | 3.5095 | 4.0906 | 4.0906 | 4.0906 | 4.0906
2024-09-09 16:00 | 1.8672 | 2.0033 | 2.4869 | 2.6158 | 2.7448 | 2024-07-10 16:00 | 3.86 | 4.4992 | 4.4992 | 4.4992 | 4.4992
2024-09-09 17:00 | 2.1529 | 2.3099 | 2.8675 | 3.0162 | 3.1649 | 2024-07-10 17:00 | 3.681 | 4.2905 | 4.2905 | 4.2905 | 4.2905
2024-09-09 18:00 | 1.9624 | 2.1055 | 2.6137 | 2.7493 | 2.8848 | 2024-07-10 18:00 | 3.319 | 3.8685 | 3.8685 | 3.8685 | 3.8685
2024-09-09 19:00 | 1.81 | 1.942 | 2.4107 | 2.5357 | 2.6607 | 2024-07-10 19:00 | 2.7855 | 3.2467 | 3.2467 | 3.2467 | 3.2467
2024-09-09 20:00 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 2024-07-10 20:00 | 2.7702 | 3.229 | 3.229 | 3.229 | 3.229
2024-09-09 21:00 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 2024-07-10 21:00 | 2.2253 | 2.5938 | 2.5938 | 2.5938 | 2.5938
2024-09-09 22:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-07-10 22:00 | 2.0424 | 2.3806 | 2.3806 | 2.3806 | 2.3806
2024-09-09 23:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-07-10 23:00 | 1.97 | 2.2962 | 2.2962 | 2.2962 | 2.2962
2024-09-10 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-07-11 | 1.73 | 2.0164 | 2.0164 | 2.0164 | 2.0164
2024-09-10 01:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-07-11 01:00 | 1.7071 | 1.9898 | 1.9898 | 1.9898 | 1.9898
2024-09-10 02:00 | 1.4289 | 1.5331 | 1.9032 | 2.0019 | 2.1006 | 2024-07-11 02:00 | 1.6919 | 1.972 | 1.972 | 1.972 | 1.972
2024-09-10 03:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-07-11 03:00 | 1.8519 | 2.1586 | 2.1586 | 2.1586 | 2.1586
2024-09-10 04:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-07-11 04:00 | 2.1567 | 2.5139 | 2.5139 | 2.5139 | 2.5139
2024-09-10 05:00 | 1.7528 | 1.8807 | 2.3346 | 2.4557 | 2.5767 | 2024-07-11 05:00 | 2.3816 | 2.7759 | 2.7759 | 2.7759 | 2.7759
2024-09-10 06:00 | 1.81 | 1.942 | 2.4107 | 2.5357 | 2.6607 | 2024-07-11 06:00 | 2.7245 | 3.1757 | 3.1757 | 3.1757 | 3.1757
2024-09-10 07:00 | 2.0577 | 2.2077 | 2.7406 | 2.8827 | 3.0248 | 2024-07-11 07:00 | 3.1018 | 3.6154 | 3.6154 | 3.6154 | 3.6154
2024-09-10 08:00 | 1.9243 | 2.0646 | 2.563 | 2.6959 | 2.8288 | 2024-07-11 08:00 | 3.6581 | 4.2638 | 4.2638 | 4.2638 | 4.2638
2024-09-10 09:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-07-11 09:00 | 3.9172 | 4.5658 | 4.5658 | 4.5658 | 4.5658
2024-09-10 10:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-07-11 10:00 | 4.043 | 4.7124 | 4.7124 | 4.7124 | 4.7124
2024-09-10 11:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-07-11 11:00 | 3.9477 | 4.6014 | 4.6014 | 4.6014 | 4.6014
2024-09-10 12:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-07-11 12:00 | 3.9629 | 4.6191 | 4.6191 | 4.6191 | 4.6191
2024-09-10 13:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-07-11 13:00 | 3.9629 | 4.6191 | 4.6191 | 4.6191 | 4.6191
2024-09-10 14:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-07-11 14:00 | 3.86 | 4.4992 | 4.4992 | 4.4992 | 4.4992
2024-09-10 15:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-07-11 15:00 | 3.9477 | 4.6014 | 4.6014 | 4.6014 | 4.6014
2024-09-10 16:00 | 2.0577 | 2.2077 | 2.7406 | 2.8827 | 3.0248 | 2024-07-11 16:00 | 4.0506 | 4.7213 | 4.7213 | 4.7213 | 4.7213
2024-09-10 17:00 | 1.9815 | 2.126 | 2.6391 | 2.776 | 2.9128 | 2024-07-11 17:00 | 3.9439 | 4.5969 | 4.5969 | 4.5969 | 4.5969
2024-09-10 18:00 | 1.9243 | 2.0646 | 2.563 | 2.6959 | 2.8288 | 2024-07-11 18:00 | 3.3609 | 3.9174 | 3.9174 | 3.9174 | 3.9174
2024-09-10 19:00 | 1.829 | 1.9624 | 2.4361 | 2.5624 | 2.6887 | 2024-07-11 19:00 | 3.0332 | 3.5354 | 3.5354 | 3.5354 | 3.5354
2024-09-10 20:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-07-11 20:00 | 2.6254 | 3.0602 | 3.0602 | 3.0602 | 3.0602
2024-09-10 21:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-07-11 21:00 | 2.4502 | 2.8559 | 2.8559 | 2.8559 | 2.8559
2024-09-10 22:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-07-11 22:00 | 2.0196 | 2.354 | 2.354 | 2.354 | 2.354
2024-09-10 23:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-07-11 23:00 | 2.1606 | 2.5183 | 2.5183 | 2.5183 | 2.5183
2024-09-11 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-07-12 | 2.031 | 2.3673 | 2.3673 | 2.3673 | 2.3673
2024-09-11 01:00 | 1.4289 | 1.5331 | 1.9032 | 2.0019 | 2.1006 | 2024-07-12 01:00 | 1.9167 | 2.2341 | 2.2341 | 2.2341 | 2.2341
2024-09-11 02:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-07-12 02:00 | 1.9129 | 2.2296 | 2.2296 | 2.2296 | 2.2296
2024-09-11 03:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-07-12 03:00 | 2.0348 | 2.3718 | 2.3718 | 2.3718 | 2.3718
2024-09-11 04:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-07-12 04:00 | 2.1872 | 2.5494 | 2.5494 | 2.5494 | 2.5494
2024-09-11 05:00 | 1.9243 | 2.0646 | 2.563 | 2.6959 | 2.8288 | 2024-07-12 05:00 | 2.6178 | 3.0513 | 3.0513 | 3.0513 | 3.0513
2024-09-11 06:00 | 2.0958 | 2.2486 | 2.7914 | 2.9361 | 3.0808 | 2024-07-12 06:00 | 2.9913 | 3.4866 | 3.4866 | 3.4866 | 3.4866
2024-09-11 07:00 | 2.0767 | 2.2282 | 2.766 | 2.9094 | 3.0528 | 2024-07-12 07:00 | 3.4028 | 3.9662 | 3.9662 | 3.9662 | 3.9662
2024-09-11 08:00 | 1.829 | 1.9624 | 2.4361 | 2.5624 | 2.6887 | 2024-07-12 08:00 | 3.9553 | 4.6103 | 4.6103 | 4.6103 | 4.6103
2024-09-11 09:00 | 1.829 | 1.9624 | 2.4361 | 2.5624 | 2.6887 | 2024-07-12 09:00 | 3.9286 | 4.5792 | 4.5792 | 4.5792 | 4.5792
2024-09-11 10:00 | 2.2863 | 2.453 | 3.0451 | 3.203 | 3.3609 | 2024-07-12 10:00 | 3.9172 | 4.5658 | 4.5658 | 4.5658 | 4.5658
2024-09-11 11:00 | 2.0386 | 2.1873 | 2.7152 | 2.856 | 2.9968 | 2024-07-12 11:00 | 3.921 | 4.5703 | 4.5703 | 4.5703 | 4.5703
2024-09-11 12:00 | 2.0958 | 2.2486 | 2.7914 | 2.9361 | 3.0808 | 2024-07-12 12:00 | 3.9439 | 4.5969 | 4.5969 | 4.5969 | 4.5969
2024-09-11 13:00 | 2.0386 | 2.1873 | 2.7152 | 2.856 | 2.9968 | 2024-07-12 13:00 | 3.8905 | 4.5348 | 4.5348 | 4.5348 | 4.5348
2024-09-11 14:00 | 2.0196 | 2.1668 | 2.6899 | 2.8293 | 2.9688 | 2024-07-12 14:00 | 3.9553 | 4.6103 | 4.6103 | 4.6103 | 4.6103
2024-09-11 15:00 | 1.9815 | 2.126 | 2.6391 | 2.776 | 2.9128 | 2024-07-12 15:00 | 3.8486 | 4.4859 | 4.4859 | 4.4859 | 4.4859
2024-09-11 16:00 | 2.0196 | 2.1668 | 2.6899 | 2.8293 | 2.9688 | 2024-07-12 16:00 | 3.86 | 4.4992 | 4.4992 | 4.4992 | 4.4992
2024-09-11 17:00 | 1.9434 | 2.0851 | 2.5884 | 2.7226 | 2.8568 | 2024-07-12 17:00 | 3.9896 | 4.6502 | 4.6502 | 4.6502 | 4.6502
2024-09-11 18:00 | 1.9053 | 2.0442 | 2.5376 | 2.6692 | 2.8008 | 2024-07-12 18:00 | 3.7572 | 4.3793 | 4.3793 | 4.3793 | 4.3793
2024-09-11 19:00 | 1.829 | 1.9624 | 2.4361 | 2.5624 | 2.6887 | 2024-07-12 19:00 | 3.1665 | 3.6909 | 3.6909 | 3.6909 | 3.6909
2024-09-11 20:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-07-12 20:00 | 2.9836 | 3.4777 | 3.4777 | 3.4777 | 3.4777
2024-09-11 21:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-07-12 21:00 | 2.7398 | 3.1934 | 3.1934 | 3.1934 | 3.1934
2024-09-11 22:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-07-12 22:00 | 2.0615 | 2.4028 | 2.4028 | 2.4028 | 2.4028
2024-09-11 23:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-07-12 23:00 | 1.9281 | 2.2474 | 2.2474 | 2.2474 | 2.2474
2024-09-12 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-07-13 | 1.871 | 2.1808 | 2.1808 | 2.1808 | 2.1808
2024-09-12 01:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-07-13 01:00 | 1.8214 | 2.123 | 2.123 | 2.123 | 2.123
2024-09-12 02:00 | 1.448 | 1.5536 | 1.9286 | 2.0286 | 2.1286 | 2024-07-13 02:00 | 1.7948 | 2.0919 | 2.0919 | 2.0919 | 2.0919
2024-09-12 03:00 | 1.448 | 1.5536 | 1.9286 | 2.0286 | 2.1286 | 2024-07-13 03:00 | 1.8519 | 2.1586 | 2.1586 | 2.1586 | 2.1586
2024-09-12 04:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-07-13 04:00 | 2.0043 | 2.3362 | 2.3362 | 2.3362 | 2.3362
2024-09-12 05:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-07-13 05:00 | 2.5416 | 2.9625 | 2.9625 | 2.9625 | 2.9625
2024-09-12 06:00 | 1.7528 | 1.8807 | 2.3346 | 2.4557 | 2.5767 | 2024-07-13 06:00 | 2.6102 | 3.0424 | 3.0424 | 3.0424 | 3.0424
2024-09-12 07:00 | 2.1339 | 2.2895 | 2.8421 | 2.9895 | 3.1369 | 2024-07-13 07:00 | 2.7245 | 3.1757 | 3.1757 | 3.1757 | 3.1757
2024-09-12 08:00 | 2.4006 | 2.5757 | 3.1974 | 3.3632 | 3.529 | 2024-07-13 08:00 | 3.2237 | 3.7575 | 3.7575 | 3.7575 | 3.7575
2024-09-12 09:00 | 2.2291 | 2.3917 | 2.969 | 3.123 | 3.2769 | 2024-07-13 09:00 | 3.1894 | 3.7175 | 3.7175 | 3.7175 | 3.7175
2024-09-12 10:00 | 2.2482 | 2.4121 | 2.9944 | 3.1496 | 3.3049 | 2024-07-13 10:00 | 2.7398 | 3.1934 | 3.1934 | 3.1934 | 3.1934
2024-09-12 11:00 | 2.2863 | 2.453 | 3.0451 | 3.203 | 3.3609 | 2024-07-13 11:00 | 2.7779 | 3.2378 | 3.2378 | 3.2378 | 3.2378
2024-09-12 12:00 | 2.3244 | 2.4939 | 3.0959 | 3.2564 | 3.4169 | 2024-07-13 12:00 | 2.7588 | 3.2156 | 3.2156 | 3.2156 | 3.2156
2024-09-12 13:00 | 2.2101 | 2.3713 | 2.9436 | 3.0963 | 3.2489 | 2024-07-13 13:00 | 2.8465 | 3.3178 | 3.3178 | 3.3178 | 3.3178
2024-09-12 14:00 | 2.172 | 2.3304 | 2.8929 | 3.0429 | 3.1929 | 2024-07-13 14:00 | 2.8922 | 3.3711 | 3.3711 | 3.3711 | 3.3711
2024-09-12 15:00 | 2.172 | 2.3304 | 2.8929 | 3.0429 | 3.1929 | 2024-07-13 15:00 | 3.0294 | 3.531 | 3.531 | 3.531 | 3.531
2024-09-12 16:00 | 2.1148 | 2.2691 | 2.8167 | 2.9628 | 3.1089 | 2024-07-13 16:00 | 3.1703 | 3.6953 | 3.6953 | 3.6953 | 3.6953
2024-09-12 17:00 | 2.0386 | 2.1873 | 2.7152 | 2.856 | 2.9968 | 2024-07-13 17:00 | 3.1742 | 3.6998 | 3.6998 | 3.6998 | 3.6998
2024-09-12 18:00 | 2.0577 | 2.2077 | 2.7406 | 2.8827 | 3.0248 | 2024-07-13 18:00 | 2.8998 | 3.38 | 3.38 | 3.38 | 3.38
2024-09-12 19:00 | 1.7909 | 1.9215 | 2.3854 | 2.509 | 2.6327 | 2024-07-13 19:00 | 2.3854 | 2.7804 | 2.7804 | 2.7804 | 2.7804
2024-09-12 20:00 | 1.7528 | 1.8807 | 2.3346 | 2.4557 | 2.5767 | 2024-07-13 20:00 | 2.4044 | 2.8026 | 2.8026 | 2.8026 | 2.8026
2024-09-12 21:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-07-13 21:00 | 2.3473 | 2.736 | 2.736 | 2.736 | 2.736
2024-09-12 22:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-07-13 22:00 | 2.1072 | 2.4561 | 2.4561 | 2.4561 | 2.4561
2024-09-12 23:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-07-13 23:00 | 1.8024 | 2.1008 | 2.1008 | 2.1008 | 2.1008
2024-09-13 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-07-14 | 1.7071 | 1.9898 | 1.9898 | 1.9898 | 1.9898
2024-09-13 01:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-07-14 01:00 | 1.6881 | 1.9676 | 1.9676 | 1.9676 | 1.9676
2024-09-13 02:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-07-14 02:00 | 1.8176 | 2.1186 | 2.1186 | 2.1186 | 2.1186
2024-09-13 03:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-07-14 03:00 | 1.8329 | 2.1364 | 2.1364 | 2.1364 | 2.1364
2024-09-13 04:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-07-14 04:00 | 1.97 | 2.2962 | 2.2962 | 2.2962 | 2.2962
2024-09-13 05:00 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 2024-07-14 05:00 | 2.1758 | 2.5361 | 2.5361 | 2.5361 | 2.5361
2024-09-13 06:00 | 1.8481 | 1.9829 | 2.4615 | 2.5891 | 2.7167 | 2024-07-14 06:00 | 2.4387 | 2.8426 | 2.8426 | 2.8426 | 2.8426
2024-09-13 07:00 | 1.9624 | 2.1055 | 2.6137 | 2.7493 | 2.8848 | 2024-07-14 07:00 | 2.8617 | 3.3356 | 3.3356 | 3.3356 | 3.3356
2024-09-13 08:00 | 2.1148 | 2.2691 | 2.8167 | 2.9628 | 3.1089 | 2024-07-14 08:00 | 2.9189 | 3.4022 | 3.4022 | 3.4022 | 3.4022
2024-09-13 09:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-07-14 09:00 | 3.1246 | 3.642 | 3.642 | 3.642 | 3.642
2024-09-13 10:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-07-14 10:00 | 2.8617 | 3.3356 | 3.3356 | 3.3356 | 3.3356
2024-09-13 11:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-07-14 11:00 | 3.1589 | 3.682 | 3.682 | 3.682 | 3.682
2024-09-13 12:00 | 1.3718 | 1.4718 | 1.8271 | 1.9218 | 2.0166 | 2024-07-14 12:00 | 3.1703 | 3.6953 | 3.6953 | 3.6953 | 3.6953
2024-09-13 13:00 | 1.2575 | 1.3492 | 1.6748 | 1.7617 | 1.8485 | 2024-07-14 13:00 | 2.9951 | 3.491 | 3.491 | 3.491 | 3.491
2024-09-13 14:00 | 1.1241 | 1.2061 | 1.4972 | 1.5748 | 1.6525 | 2024-07-14 14:00 | 3.277 | 3.8197 | 3.8197 | 3.8197 | 3.8197
2024-09-13 15:00 | 1.2765 | 1.3696 | 1.7002 | 1.7884 | 1.8765 | 2024-07-14 15:00 | 3.2275 | 3.7619 | 3.7619 | 3.7619 | 3.7619
2024-09-13 16:00 | 1.9624 | 2.1055 | 2.6137 | 2.7493 | 2.8848 | 2024-07-14 16:00 | 3.2732 | 3.8152 | 3.8152 | 3.8152 | 3.8152
2024-09-13 17:00 | 1.9624 | 2.1055 | 2.6137 | 2.7493 | 2.8848 | 2024-07-14 17:00 | 3.2275 | 3.7619 | 3.7619 | 3.7619 | 3.7619
2024-09-13 18:00 | 1.9624 | 2.1055 | 2.6137 | 2.7493 | 2.8848 | 2024-07-14 18:00 | 2.957 | 3.4466 | 3.4466 | 3.4466 | 3.4466
2024-09-13 19:00 | 1.7909 | 1.9215 | 2.3854 | 2.509 | 2.6327 | 2024-07-14 19:00 | 2.4311 | 2.8337 | 2.8337 | 2.8337 | 2.8337
2024-09-13 20:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-07-14 20:00 | 2.393 | 2.7893 | 2.7893 | 2.7893 | 2.7893
2024-09-13 21:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-07-14 21:00 | 2.1529 | 2.5094 | 2.5094 | 2.5094 | 2.5094
2024-09-13 22:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-07-14 22:00 | 1.951 | 2.274 | 2.274 | 2.274 | 2.274
2024-09-13 23:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-07-14 23:00 | 1.8329 | 2.1364 | 2.1364 | 2.1364 | 2.1364
2024-09-14 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-07-15 | 1.8176 | 2.1186 | 2.1186 | 2.1186 | 2.1186
2024-09-14 01:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-07-15 01:00 | 1.749 | 2.0386 | 2.0386 | 2.0386 | 2.0386
2024-09-14 02:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-07-15 02:00 | 1.8176 | 2.1186 | 2.1186 | 2.1186 | 2.1186
2024-09-14 03:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-07-15 03:00 | 1.8748 | 2.1852 | 2.1852 | 2.1852 | 2.1852
2024-09-14 04:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-07-15 04:00 | 2.092 | 2.4384 | 2.4384 | 2.4384 | 2.4384
2024-09-14 05:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-07-15 05:00 | 2.5683 | 2.9936 | 2.9936 | 2.9936 | 2.9936
2024-09-14 06:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-07-15 06:00 | 2.9112 | 3.3933 | 3.3933 | 3.3933 | 3.3933
2024-09-14 07:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-07-15 07:00 | 3.5743 | 4.1661 | 4.1661 | 4.1661 | 4.1661
2024-09-14 08:00 | 1.448 | 1.5536 | 1.9286 | 2.0286 | 2.1286 | 2024-07-15 08:00 | 3.8219 | 4.4548 | 4.4548 | 4.4548 | 4.4548
2024-09-14 09:00 | 0.724 | 0.77679 | 0.96429 | 1.0143 | 1.0643 | 2024-07-15 09:00 | 3.8753 | 4.517 | 4.517 | 4.517 | 4.517
2024-09-14 10:00 | 0.60968 | 0.65414 | 0.81204 | 0.85414 | 0.89625 | 2024-07-15 10:00 | 3.982 | 4.6414 | 4.6414 | 4.6414 | 4.6414
2024-09-14 11:00 | 0.28579 | 0.30663 | 0.38064 | 0.40038 | 0.42012 | 2024-07-15 11:00 | 3.841 | 4.477 | 4.477 | 4.477 | 4.477
2024-09-14 12:00 | 0.07621 | 0.081768 | 0.1015 | 0.10677 | 0.11203 | 2024-07-15 12:00 | 3.9134 | 4.5614 | 4.5614 | 4.5614 | 4.5614
2024-09-14 13:00 | 0.66684 | 0.71547 | 0.88816 | 0.93422 | 0.98027 | 2024-07-15 13:00 | 3.7267 | 4.3438 | 4.3438 | 4.3438 | 4.3438
2024-09-14 14:00 | 1.0479 | 1.1243 | 1.3957 | 1.4681 | 1.5404 | 2024-07-15 14:00 | 3.7953 | 4.4237 | 4.4237 | 4.4237 | 4.4237
2024-09-14 15:00 | 0.91452 | 0.98121 | 1.2181 | 1.2812 | 1.3444 | 2024-07-15 15:00 | 3.8982 | 4.5436 | 4.5436 | 4.5436 | 4.5436
2024-09-14 16:00 | 1.448 | 1.5536 | 1.9286 | 2.0286 | 2.1286 | 2024-07-15 16:00 | 3.8486 | 4.4859 | 4.4859 | 4.4859 | 4.4859
2024-09-14 17:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-07-15 17:00 | 3.7762 | 4.4015 | 4.4015 | 4.4015 | 4.4015
2024-09-14 18:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-07-15 18:00 | 3.4295 | 3.9973 | 3.9973 | 3.9973 | 3.9973
2024-09-14 19:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-07-15 19:00 | 2.8769 | 3.3533 | 3.3533 | 3.3533 | 3.3533
2024-09-14 20:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-07-15 20:00 | 2.6216 | 3.0557 | 3.0557 | 3.0557 | 3.0557
2024-09-14 21:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-07-15 21:00 | 2.4273 | 2.8292 | 2.8292 | 2.8292 | 2.8292
2024-09-14 22:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-07-15 22:00 | 1.9434 | 2.2652 | 2.2652 | 2.2652 | 2.2652
2024-09-14 23:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-07-15 23:00 | 1.9281 | 2.2474 | 2.2474 | 2.2474 | 2.2474
2024-09-15 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-07-16 | 1.7643 | 2.0564 | 2.0564 | 2.0564 | 2.0564
2024-09-15 01:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-07-16 01:00 | 1.7224 | 2.0076 | 2.0076 | 2.0076 | 2.0076
2024-09-15 02:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-07-16 02:00 | 1.7224 | 2.0076 | 2.0076 | 2.0076 | 2.0076
2024-09-15 03:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-07-16 03:00 | 1.8481 | 2.1541 | 2.1541 | 2.1541 | 2.1541
2024-09-15 04:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-07-16 04:00 | 2.0234 | 2.3584 | 2.3584 | 2.3584 | 2.3584
2024-09-15 05:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-07-16 05:00 | 2.2634 | 2.6382 | 2.6382 | 2.6382 | 2.6382
2024-09-15 06:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-07-16 06:00 | 2.8465 | 3.3178 | 3.3178 | 3.3178 | 3.3178
2024-09-15 07:00 | 0.97168 | 1.0425 | 1.2942 | 1.3613 | 1.4284 | 2024-07-16 07:00 | 3.2275 | 3.7619 | 3.7619 | 3.7619 | 3.7619
2024-09-15 08:00 | 0.19053 | 0.20442 | 0.25376 | 0.26692 | 0.28008 | 2024-07-16 08:00 | 3.8105 | 4.4415 | 4.4415 | 4.4415 | 4.4415
2024-09-15 09:00 | 0.095263 | 0.10221 | 0.12688 | 0.13346 | 0.14004 | 2024-07-16 09:00 | 3.8753 | 4.517 | 4.517 | 4.517 | 4.517
2024-09-15 10:00 | 0.81926 | 0.879 | 1.0912 | 1.1478 | 1.2043 | 2024-07-16 10:00 | 3.8677 | 4.5081 | 4.5081 | 4.5081 | 4.5081
2024-09-15 11:00 | 0.51442 | 0.55193 | 0.68516 | 0.72068 | 0.75621 | 2024-07-16 11:00 | 3.7876 | 4.4148 | 4.4148 | 4.4148 | 4.4148
2024-09-15 12:00 | 0.93358 | 1.0017 | 1.2434 | 1.3079 | 1.3724 | 2024-07-16 12:00 | 4.0696 | 4.7435 | 4.7435 | 4.7435 | 4.7435
2024-09-15 13:00 | 0.057158 | 0.061326 | 0.076128 | 0.080076 | 0.084023 | 2024-07-16 13:00 | 4.1458 | 4.8323 | 4.8323 | 4.8323 | 4.8323
2024-09-15 14:00 | 0.22863 | 0.2453 | 0.30451 | 0.3203 | 0.33609 | 2024-07-16 14:00 | 4.3821 | 5.1077 | 5.1077 | 5.1077 | 5.1077
2024-09-15 15:00 | 0.17147 | 0.18398 | 0.22839 | 0.24023 | 0.25207 | 2024-07-16 15:00 | 4.2754 | 4.9833 | 4.9833 | 4.9833 | 4.9833
2024-09-15 16:00 | 1.4099 | 1.5127 | 1.8778 | 1.9752 | 2.0726 | 2024-07-16 16:00 | 4.2411 | 4.9434 | 4.9434 | 4.9434 | 4.9434
2024-09-15 17:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-07-16 17:00 | 4.3211 | 5.0366 | 5.0366 | 5.0366 | 5.0366
2024-09-15 18:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-07-16 18:00 | 3.2504 | 3.7886 | 3.7886 | 3.7886 | 3.7886
2024-09-15 19:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-07-16 19:00 | 2.896 | 3.3755 | 3.3755 | 3.3755 | 3.3755
2024-09-15 20:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-07-16 20:00 | 2.7855 | 3.2467 | 3.2467 | 3.2467 | 3.2467
2024-09-15 21:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-07-16 21:00 | 2.2939 | 2.6738 | 2.6738 | 2.6738 | 2.6738
2024-09-15 22:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-07-16 22:00 | 2.0843 | 2.4295 | 2.4295 | 2.4295 | 2.4295
2024-09-15 23:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-07-16 23:00 | 1.9662 | 2.2918 | 2.2918 | 2.2918 | 2.2918
2024-09-16 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-07-17 | 1.9014 | 2.2163 | 2.2163 | 2.2163 | 2.2163
2024-09-16 01:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-07-17 01:00 | 1.8024 | 2.1008 | 2.1008 | 2.1008 | 2.1008
2024-09-16 02:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-07-17 02:00 | 1.7452 | 2.0342 | 2.0342 | 2.0342 | 2.0342
2024-09-16 03:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-07-17 03:00 | 1.9243 | 2.243 | 2.243 | 2.243 | 2.243
2024-09-16 04:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-07-17 04:00 | 2.1644 | 2.5228 | 2.5228 | 2.5228 | 2.5228
2024-09-16 05:00 | 1.7719 | 1.9011 | 2.36 | 2.4823 | 2.6047 | 2024-07-17 05:00 | 2.3854 | 2.7804 | 2.7804 | 2.7804 | 2.7804
2024-09-16 06:00 | 2.0958 | 2.2486 | 2.7914 | 2.9361 | 3.0808 | 2024-07-17 06:00 | 3.338 | 3.8907 | 3.8907 | 3.8907 | 3.8907
2024-09-16 07:00 | 2.3054 | 2.4735 | 3.0705 | 3.2297 | 3.3889 | 2024-07-17 07:00 | 3.5285 | 4.1128 | 4.1128 | 4.1128 | 4.1128
2024-09-16 08:00 | 2.1339 | 2.2895 | 2.8421 | 2.9895 | 3.1369 | 2024-07-17 08:00 | 3.7381 | 4.3571 | 4.3571 | 4.3571 | 4.3571
2024-09-16 09:00 | 2.3816 | 2.5552 | 3.172 | 3.3365 | 3.501 | 2024-07-17 09:00 | 4.1573 | 4.8457 | 4.8457 | 4.8457 | 4.8457
2024-09-16 10:00 | 2.0958 | 2.2486 | 2.7914 | 2.9361 | 3.0808 | 2024-07-17 10:00 | 4.0353 | 4.7035 | 4.7035 | 4.7035 | 4.7035
2024-09-16 11:00 | 1.7719 | 1.9011 | 2.36 | 2.4823 | 2.6047 | 2024-07-17 11:00 | 4.2106 | 4.9078 | 4.9078 | 4.9078 | 4.9078
2024-09-16 12:00 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 2024-07-17 12:00 | 4.1725 | 4.8634 | 4.8634 | 4.8634 | 4.8634
2024-09-16 13:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-07-17 13:00 | 3.9972 | 4.6591 | 4.6591 | 4.6591 | 4.6591
2024-09-16 14:00 | 1.3337 | 1.4309 | 1.7763 | 1.8684 | 1.9605 | 2024-07-17 14:00 | 3.9706 | 4.628 | 4.628 | 4.628 | 4.628
2024-09-16 15:00 | 2.3054 | 2.4735 | 3.0705 | 3.2297 | 3.3889 | 2024-07-17 15:00 | 3.8524 | 4.4903 | 4.4903 | 4.4903 | 4.4903
2024-09-16 16:00 | 2.191 | 2.3508 | 2.9183 | 3.0696 | 3.2209 | 2024-07-17 16:00 | 3.6962 | 4.3082 | 4.3082 | 4.3082 | 4.3082
2024-09-16 17:00 | 2.172 | 2.3304 | 2.8929 | 3.0429 | 3.1929 | 2024-07-17 17:00 | 3.7305 | 4.3482 | 4.3482 | 4.3482 | 4.3482
2024-09-16 18:00 | 2.0767 | 2.2282 | 2.766 | 2.9094 | 3.0528 | 2024-07-17 18:00 | 3.2656 | 3.8064 | 3.8064 | 3.8064 | 3.8064
2024-09-16 19:00 | 1.7909 | 1.9215 | 2.3854 | 2.509 | 2.6327 | 2024-07-17 19:00 | 2.7359 | 3.189 | 3.189 | 3.189 | 3.189
2024-09-16 20:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-07-17 20:00 | 2.5835 | 3.0113 | 3.0113 | 3.0113 | 3.0113
2024-09-16 21:00 | 1.7528 | 1.8807 | 2.3346 | 2.4557 | 2.5767 | 2024-07-17 21:00 | 2.252 | 2.6249 | 2.6249 | 2.6249 | 2.6249
2024-09-16 22:00 | 1.7338 | 1.8602 | 2.3092 | 2.429 | 2.5487 | 2024-07-17 22:00 | 2.031 | 2.3673 | 2.3673 | 2.3673 | 2.3673
2024-09-16 23:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-07-17 23:00 | 1.9243 | 2.243 | 2.243 | 2.243 | 2.243
2024-09-17 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-07-18 | 1.669 | 1.9454 | 1.9454 | 1.9454 | 1.9454
2024-09-17 01:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-07-18 01:00 | 1.7147 | 1.9987 | 1.9987 | 1.9987 | 1.9987
2024-09-17 02:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-07-18 02:00 | 1.6919 | 1.972 | 1.972 | 1.972 | 1.972
2024-09-17 03:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-07-18 03:00 | 1.8557 | 2.163 | 2.163 | 2.163 | 2.163
2024-09-17 04:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-07-18 04:00 | 2.1415 | 2.4961 | 2.4961 | 2.4961 | 2.4961
2024-09-17 05:00 | 1.829 | 1.9624 | 2.4361 | 2.5624 | 2.6887 | 2024-07-18 05:00 | 2.4197 | 2.8203 | 2.8203 | 2.8203 | 2.8203
2024-09-17 06:00 | 2.0577 | 2.2077 | 2.7406 | 2.8827 | 3.0248 | 2024-07-18 06:00 | 2.7398 | 3.1934 | 3.1934 | 3.1934 | 3.1934
2024-09-17 07:00 | 2.1529 | 2.3099 | 2.8675 | 3.0162 | 3.1649 | 2024-07-18 07:00 | 3.2046 | 3.7353 | 3.7353 | 3.7353 | 3.7353
2024-09-17 08:00 | 1.8481 | 1.9829 | 2.4615 | 2.5891 | 2.7167 | 2024-07-18 08:00 | 4.0658 | 4.7391 | 4.7391 | 4.7391 | 4.7391
2024-09-17 09:00 | 1.2575 | 1.3492 | 1.6748 | 1.7617 | 1.8485 | 2024-07-18 09:00 | 4.0163 | 4.6813 | 4.6813 | 4.6813 | 4.6813
2024-09-17 10:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-07-18 10:00 | 3.4257 | 3.9929 | 3.9929 | 3.9929 | 3.9929
2024-09-17 11:00 | 1.3908 | 1.4923 | 1.8525 | 1.9485 | 2.0446 | 2024-07-18 11:00 | 3.4676 | 4.0418 | 4.0418 | 4.0418 | 4.0418
2024-09-17 12:00 | 1.3908 | 1.4923 | 1.8525 | 1.9485 | 2.0446 | 2024-07-18 12:00 | 3.5857 | 4.1794 | 4.1794 | 4.1794 | 4.1794
2024-09-17 13:00 | 1.3146 | 1.4105 | 1.751 | 1.8417 | 1.9325 | 2024-07-18 13:00 | 3.3647 | 3.9218 | 3.9218 | 3.9218 | 3.9218
2024-09-17 14:00 | 1.2194 | 1.3083 | 1.6241 | 1.7083 | 1.7925 | 2024-07-18 14:00 | 3.4409 | 4.0107 | 4.0107 | 4.0107 | 4.0107
2024-09-17 15:00 | 1.1622 | 1.247 | 1.5479 | 1.6282 | 1.7085 | 2024-07-18 15:00 | 3.6581 | 4.2638 | 4.2638 | 4.2638 | 4.2638
2024-09-17 16:00 | 2.0196 | 2.1668 | 2.6899 | 2.8293 | 2.9688 | 2024-07-18 16:00 | 3.9401 | 4.5925 | 4.5925 | 4.5925 | 4.5925
2024-09-17 17:00 | 2.0196 | 2.1668 | 2.6899 | 2.8293 | 2.9688 | 2024-07-18 17:00 | 3.7953 | 4.4237 | 4.4237 | 4.4237 | 4.4237
2024-09-17 18:00 | 2.0005 | 2.1464 | 2.6645 | 2.8026 | 2.9408 | 2024-07-18 18:00 | 3.319 | 3.8685 | 3.8685 | 3.8685 | 3.8685
2024-09-17 19:00 | 1.81 | 1.942 | 2.4107 | 2.5357 | 2.6607 | 2024-07-18 19:00 | 2.9227 | 3.4066 | 3.4066 | 3.4066 | 3.4066
2024-09-17 20:00 | 1.7338 | 1.8602 | 2.3092 | 2.429 | 2.5487 | 2024-07-18 20:00 | 2.675 | 3.1179 | 3.1179 | 3.1179 | 3.1179
2024-09-17 21:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-07-18 21:00 | 2.4578 | 2.8648 | 2.8648 | 2.8648 | 2.8648
2024-09-17 22:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-07-18 22:00 | 2.2596 | 2.6338 | 2.6338 | 2.6338 | 2.6338
2024-09-17 23:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-07-18 23:00 | 1.9167 | 2.2341 | 2.2341 | 2.2341 | 2.2341
2024-09-18 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-07-19 | 1.8633 | 2.1719 | 2.1719 | 2.1719 | 2.1719
2024-09-18 01:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-07-19 01:00 | 1.7338 | 2.0209 | 2.0209 | 2.0209 | 2.0209
2024-09-18 02:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-07-19 02:00 | 1.65 | 1.9232 | 1.9232 | 1.9232 | 1.9232
2024-09-18 03:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-07-19 03:00 | 1.829 | 2.1319 | 2.1319 | 2.1319 | 2.1319
2024-09-18 04:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-07-19 04:00 | 2.1529 | 2.5094 | 2.5094 | 2.5094 | 2.5094
2024-09-18 05:00 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 2024-07-19 05:00 | 2.3587 | 2.7493 | 2.7493 | 2.7493 | 2.7493
2024-09-18 06:00 | 1.8481 | 1.9829 | 2.4615 | 2.5891 | 2.7167 | 2024-07-19 06:00 | 2.9646 | 3.4555 | 3.4555 | 3.4555 | 3.4555
2024-09-18 07:00 | 2.0386 | 2.1873 | 2.7152 | 2.856 | 2.9968 | 2024-07-19 07:00 | 3.3914 | 3.9529 | 3.9529 | 3.9529 | 3.9529
2024-09-18 08:00 | 1.829 | 1.9624 | 2.4361 | 2.5624 | 2.6887 | 2024-07-19 08:00 | 3.9363 | 4.5881 | 4.5881 | 4.5881 | 4.5881
2024-09-18 09:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-07-19 09:00 | 4.3783 | 5.1033 | 5.1033 | 5.1033 | 5.1033
2024-09-18 10:00 | 1.3908 | 1.4923 | 1.8525 | 1.9485 | 2.0446 | 2024-07-19 10:00 | 4.3287 | 5.0455 | 5.0455 | 5.0455 | 5.0455
2024-09-18 11:00 | 1.3908 | 1.4923 | 1.8525 | 1.9485 | 2.0446 | 2024-07-19 11:00 | 3.9401 | 4.5925 | 4.5925 | 4.5925 | 4.5925
2024-09-18 12:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-07-19 12:00 | 4.3821 | 5.1077 | 5.1077 | 5.1077 | 5.1077
2024-09-18 13:00 | 1.3337 | 1.4309 | 1.7763 | 1.8684 | 1.9605 | 2024-07-19 13:00 | 4.3135 | 5.0278 | 5.0278 | 5.0278 | 5.0278
2024-09-18 14:00 | 1.1622 | 1.247 | 1.5479 | 1.6282 | 1.7085 | 2024-07-19 14:00 | 4.424 | 5.1566 | 5.1566 | 5.1566 | 5.1566
2024-09-18 15:00 | 1.4099 | 1.5127 | 1.8778 | 1.9752 | 2.0726 | 2024-07-19 15:00 | 4.4964 | 5.241 | 5.241 | 5.241 | 5.241
2024-09-18 16:00 | 1.9434 | 2.0851 | 2.5884 | 2.7226 | 2.8568 | 2024-07-19 16:00 | 4.4964 | 5.241 | 5.241 | 5.241 | 5.241
2024-09-18 17:00 | 1.9243 | 2.0646 | 2.563 | 2.6959 | 2.8288 | 2024-07-19 17:00 | 4.5536 | 5.3076 | 5.3076 | 5.3076 | 5.3076
2024-09-18 18:00 | 1.8672 | 2.0033 | 2.4869 | 2.6158 | 2.7448 | 2024-07-19 18:00 | 3.8448 | 4.4815 | 4.4815 | 4.4815 | 4.4815
2024-09-18 19:00 | 1.829 | 1.9624 | 2.4361 | 2.5624 | 2.6887 | 2024-07-19 19:00 | 3.319 | 3.8685 | 3.8685 | 3.8685 | 3.8685
2024-09-18 20:00 | 1.7338 | 1.8602 | 2.3092 | 2.429 | 2.5487 | 2024-07-19 20:00 | 2.915 | 3.3977 | 3.3977 | 3.3977 | 3.3977
2024-09-18 21:00 | 1.7528 | 1.8807 | 2.3346 | 2.4557 | 2.5767 | 2024-07-19 21:00 | 2.5492 | 2.9714 | 2.9714 | 2.9714 | 2.9714
2024-09-18 22:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-07-19 22:00 | 2.1225 | 2.4739 | 2.4739 | 2.4739 | 2.4739
2024-09-18 23:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-07-19 23:00 | 1.9053 | 2.2207 | 2.2207 | 2.2207 | 2.2207
2024-09-19 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-07-20 | 1.9053 | 2.2207 | 2.2207 | 2.2207 | 2.2207
2024-09-19 01:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-07-20 01:00 | 1.7909 | 2.0875 | 2.0875 | 2.0875 | 2.0875
2024-09-19 02:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-07-20 02:00 | 1.7528 | 2.0431 | 2.0431 | 2.0431 | 2.0431
2024-09-19 03:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-07-20 03:00 | 1.8252 | 2.1275 | 2.1275 | 2.1275 | 2.1275
2024-09-19 04:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-07-20 04:00 | 1.9853 | 2.314 | 2.314 | 2.314 | 2.314
2024-09-19 05:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-07-20 05:00 | 2.4044 | 2.8026 | 2.8026 | 2.8026 | 2.8026
2024-09-19 06:00 | 1.8481 | 1.9829 | 2.4615 | 2.5891 | 2.7167 | 2024-07-20 06:00 | 2.4768 | 2.887 | 2.887 | 2.887 | 2.887
2024-09-19 07:00 | 2.1148 | 2.2691 | 2.8167 | 2.9628 | 3.1089 | 2024-07-20 07:00 | 2.835 | 3.3045 | 3.3045 | 3.3045 | 3.3045
2024-09-19 08:00 | 1.9434 | 2.0851 | 2.5884 | 2.7226 | 2.8568 | 2024-07-20 08:00 | 2.9722 | 3.4644 | 3.4644 | 3.4644 | 3.4644
2024-09-19 09:00 | 1.2003 | 1.2878 | 1.5987 | 1.6816 | 1.7645 | 2024-07-20 09:00 | 3.4714 | 4.0462 | 4.0462 | 4.0462 | 4.0462
2024-09-19 10:00 | 1.2194 | 1.3083 | 1.6241 | 1.7083 | 1.7925 | 2024-07-20 10:00 | 3.3875 | 3.9485 | 3.9485 | 3.9485 | 3.9485
2024-09-19 11:00 | 0.85737 | 0.91989 | 1.1419 | 1.2011 | 1.2603 | 2024-07-20 11:00 | 3.2961 | 3.8419 | 3.8419 | 3.8419 | 3.8419
2024-09-19 12:00 | 1.1432 | 1.2265 | 1.5226 | 1.6015 | 1.6805 | 2024-07-20 12:00 | 3.0598 | 3.5665 | 3.5665 | 3.5665 | 3.5665
2024-09-19 13:00 | 1.1622 | 1.247 | 1.5479 | 1.6282 | 1.7085 | 2024-07-20 13:00 | 3.5476 | 4.135 | 4.135 | 4.135 | 4.135
2024-09-19 14:00 | 1.0669 | 1.1447 | 1.4211 | 1.4947 | 1.5684 | 2024-07-20 14:00 | 3.5362 | 4.1217 | 4.1217 | 4.1217 | 4.1217
2024-09-19 15:00 | 1.9624 | 2.1055 | 2.6137 | 2.7493 | 2.8848 | 2024-07-20 15:00 | 3.4333 | 4.0018 | 4.0018 | 4.0018 | 4.0018
2024-09-19 16:00 | 2.172 | 2.3304 | 2.8929 | 3.0429 | 3.1929 | 2024-07-20 16:00 | 3.3647 | 3.9218 | 3.9218 | 3.9218 | 3.9218
2024-09-19 17:00 | 1.9624 | 2.1055 | 2.6137 | 2.7493 | 2.8848 | 2024-07-20 17:00 | 3.3304 | 3.8819 | 3.8819 | 3.8819 | 3.8819
2024-09-19 18:00 | 1.9243 | 2.0646 | 2.563 | 2.6959 | 2.8288 | 2024-07-20 18:00 | 2.9341 | 3.4199 | 3.4199 | 3.4199 | 3.4199
2024-09-19 19:00 | 1.829 | 1.9624 | 2.4361 | 2.5624 | 2.6887 | 2024-07-20 19:00 | 2.6178 | 3.0513 | 3.0513 | 3.0513 | 3.0513
2024-09-19 20:00 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 2024-07-20 20:00 | 2.3816 | 2.7759 | 2.7759 | 2.7759 | 2.7759
2024-09-19 21:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-07-20 21:00 | 2.2368 | 2.6072 | 2.6072 | 2.6072 | 2.6072
2024-09-19 22:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-07-20 22:00 | 2.1453 | 2.5006 | 2.5006 | 2.5006 | 2.5006
2024-09-19 23:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-07-20 23:00 | 1.9548 | 2.2785 | 2.2785 | 2.2785 | 2.2785
2024-09-20 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-07-21 | 1.7909 | 2.0875 | 2.0875 | 2.0875 | 2.0875
2024-09-20 01:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-07-21 01:00 | 1.7795 | 2.0742 | 2.0742 | 2.0742 | 2.0742
2024-09-20 02:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-07-21 02:00 | 1.7795 | 2.0742 | 2.0742 | 2.0742 | 2.0742
2024-09-20 03:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-07-21 03:00 | 1.8443 | 2.1497 | 2.1497 | 2.1497 | 2.1497
2024-09-20 04:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-07-21 04:00 | 2.0462 | 2.3851 | 2.3851 | 2.3851 | 2.3851
2024-09-20 05:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-07-21 05:00 | 2.2406 | 2.6116 | 2.6116 | 2.6116 | 2.6116
2024-09-20 06:00 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 2024-07-21 06:00 | 2.534 | 2.9536 | 2.9536 | 2.9536 | 2.9536
2024-09-20 07:00 | 1.7909 | 1.9215 | 2.3854 | 2.509 | 2.6327 | 2024-07-21 07:00 | 2.8769 | 3.3533 | 3.3533 | 3.3533 | 3.3533
2024-09-20 08:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-07-21 08:00 | 2.915 | 3.3977 | 3.3977 | 3.3977 | 3.3977
2024-09-20 09:00 | 1.105 | 1.1856 | 1.4718 | 1.5481 | 1.6244 | 2024-07-21 09:00 | 2.8083 | 3.2734 | 3.2734 | 3.2734 | 3.2734
2024-09-20 10:00 | 1.2765 | 1.3696 | 1.7002 | 1.7884 | 1.8765 | 2024-07-21 10:00 | 2.896 | 3.3755 | 3.3755 | 3.3755 | 3.3755
2024-09-20 11:00 | 1.105 | 1.1856 | 1.4718 | 1.5481 | 1.6244 | 2024-07-21 11:00 | 2.7931 | 3.2556 | 3.2556 | 3.2556 | 3.2556
2024-09-20 12:00 | 1.1241 | 1.2061 | 1.4972 | 1.5748 | 1.6525 | 2024-07-21 12:00 | 2.9531 | 3.4422 | 3.4422 | 3.4422 | 3.4422
2024-09-20 13:00 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 2024-07-21 13:00 | 2.8465 | 3.3178 | 3.3178 | 3.3178 | 3.3178
2024-09-20 14:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-07-21 14:00 | 2.9684 | 3.4599 | 3.4599 | 3.4599 | 3.4599
2024-09-20 15:00 | 1.8672 | 2.0033 | 2.4869 | 2.6158 | 2.7448 | 2024-07-21 15:00 | 3.3456 | 3.8996 | 3.8996 | 3.8996 | 3.8996
2024-09-20 16:00 | 1.9434 | 2.0851 | 2.5884 | 2.7226 | 2.8568 | 2024-07-21 16:00 | 3.3075 | 3.8552 | 3.8552 | 3.8552 | 3.8552
2024-09-20 17:00 | 1.9434 | 2.0851 | 2.5884 | 2.7226 | 2.8568 | 2024-07-21 17:00 | 3.2923 | 3.8374 | 3.8374 | 3.8374 | 3.8374
2024-09-20 18:00 | 1.9624 | 2.1055 | 2.6137 | 2.7493 | 2.8848 | 2024-07-21 18:00 | 3.0027 | 3.4999 | 3.4999 | 3.4999 | 3.4999
2024-09-20 19:00 | 1.81 | 1.942 | 2.4107 | 2.5357 | 2.6607 | 2024-07-21 19:00 | 2.7702 | 3.229 | 3.229 | 3.229 | 3.229
2024-09-20 20:00 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 2024-07-21 20:00 | 2.3778 | 2.7715 | 2.7715 | 2.7715 | 2.7715
2024-09-20 21:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-07-21 21:00 | 2.3206 | 2.7049 | 2.7049 | 2.7049 | 2.7049
2024-09-20 22:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-07-21 22:00 | 1.871 | 2.1808 | 2.1808 | 2.1808 | 2.1808
2024-09-20 23:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-07-21 23:00 | 1.8633 | 2.1719 | 2.1719 | 2.1719 | 2.1719
2024-09-21 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-07-22 | 1.8405 | 2.1452 | 2.1452 | 2.1452 | 2.1452
2024-09-21 01:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-07-22 01:00 | 1.7224 | 2.0076 | 2.0076 | 2.0076 | 2.0076
2024-09-21 02:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-07-22 02:00 | 1.8367 | 2.1408 | 2.1408 | 2.1408 | 2.1408
2024-09-21 03:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-07-22 03:00 | 1.89 | 2.203 | 2.203 | 2.203 | 2.203
2024-09-21 04:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-07-22 04:00 | 2.0691 | 2.4117 | 2.4117 | 2.4117 | 2.4117
2024-09-21 05:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-07-22 05:00 | 2.3663 | 2.7582 | 2.7582 | 2.7582 | 2.7582
2024-09-21 06:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-07-22 06:00 | 3.0141 | 3.5132 | 3.5132 | 3.5132 | 3.5132
2024-09-21 07:00 | 0.60968 | 0.65414 | 0.81204 | 0.85414 | 0.89625 | 2024-07-22 07:00 | 3.5933 | 4.1883 | 4.1883 | 4.1883 | 4.1883
2024-09-21 08:00 | 1.3527 | 1.4514 | 1.8017 | 1.8951 | 1.9885 | 2024-07-22 08:00 | 3.8334 | 4.4681 | 4.4681 | 4.4681 | 4.4681
2024-09-21 09:00 | 1.0098 | 1.0834 | 1.3449 | 1.4147 | 1.4844 | 2024-07-22 09:00 | 4.1458 | 4.8323 | 4.8323 | 4.8323 | 4.8323
2024-09-21 10:00 | 0.43821 | 0.47016 | 0.58365 | 0.61391 | 0.64418 | 2024-07-22 10:00 | 3.9134 | 4.5614 | 4.5614 | 4.5614 | 4.5614
2024-09-21 11:00 | 0.724 | 0.77679 | 0.96429 | 1.0143 | 1.0643 | 2024-07-22 11:00 | 4.0087 | 4.6724 | 4.6724 | 4.6724 | 4.6724
2024-09-21 12:00 | 0.47631 | 0.51105 | 0.6344 | 0.6673 | 0.70019 | 2024-07-22 12:00 | 3.9858 | 4.6458 | 4.6458 | 4.6458 | 4.6458
2024-09-21 13:00 | 1.105 | 1.1856 | 1.4718 | 1.5481 | 1.6244 | 2024-07-22 13:00 | 3.9782 | 4.6369 | 4.6369 | 4.6369 | 4.6369
2024-09-21 14:00 | 0.99073 | 1.063 | 1.3196 | 1.388 | 1.4564 | 2024-07-22 14:00 | 3.902 | 4.5481 | 4.5481 | 4.5481 | 4.5481
2024-09-21 15:00 | 1.0098 | 1.0834 | 1.3449 | 1.4147 | 1.4844 | 2024-07-22 15:00 | 3.9858 | 4.6458 | 4.6458 | 4.6458 | 4.6458
2024-09-21 16:00 | 1.0288 | 1.1039 | 1.3703 | 1.4414 | 1.5124 | 2024-07-22 16:00 | 4.0506 | 4.7213 | 4.7213 | 4.7213 | 4.7213
2024-09-21 17:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-07-22 17:00 | 3.9972 | 4.6591 | 4.6591 | 4.6591 | 4.6591
2024-09-21 18:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-07-22 18:00 | 3.5133 | 4.0951 | 4.0951 | 4.0951 | 4.0951
2024-09-21 19:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-07-22 19:00 | 2.694 | 3.1401 | 3.1401 | 3.1401 | 3.1401
2024-09-21 20:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-07-22 20:00 | 2.553 | 2.9758 | 2.9758 | 2.9758 | 2.9758
2024-09-21 21:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-07-22 21:00 | 2.2977 | 2.6782 | 2.6782 | 2.6782 | 2.6782
2024-09-21 22:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-07-22 22:00 | 1.9662 | 2.2918 | 2.2918 | 2.2918 | 2.2918
2024-09-21 23:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-07-22 23:00 | 1.9319 | 2.2518 | 2.2518 | 2.2518 | 2.2518
2024-09-22 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-07-23 | 1.9014 | 2.2163 | 2.2163 | 2.2163 | 2.2163
2024-09-22 01:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-07-23 01:00 | 1.7376 | 2.0253 | 2.0253 | 2.0253 | 2.0253
2024-09-22 02:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-07-23 02:00 | 1.7833 | 2.0786 | 2.0786 | 2.0786 | 2.0786
2024-09-22 03:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-07-23 03:00 | 1.8062 | 2.1053 | 2.1053 | 2.1053 | 2.1053
2024-09-22 04:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-07-23 04:00 | 2.2406 | 2.6116 | 2.6116 | 2.6116 | 2.6116
2024-09-22 05:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-07-23 05:00 | 2.4273 | 2.8292 | 2.8292 | 2.8292 | 2.8292
2024-09-22 06:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-07-23 06:00 | 3.1703 | 3.6953 | 3.6953 | 3.6953 | 3.6953
2024-09-22 07:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-07-23 07:00 | 3.8943 | 4.5392 | 4.5392 | 4.5392 | 4.5392
2024-09-22 08:00 | 1.0288 | 1.1039 | 1.3703 | 1.4414 | 1.5124 | 2024-07-23 08:00 | 4.2259 | 4.9256 | 4.9256 | 4.9256 | 4.9256
2024-09-22 09:00 | 0.64779 | 0.69502 | 0.86279 | 0.90752 | 0.95226 | 2024-07-23 09:00 | 4.363 | 5.0855 | 5.0855 | 5.0855 | 5.0855
2024-09-22 10:00 | 0.87642 | 0.94033 | 1.1673 | 1.2278 | 1.2884 | 2024-07-23 10:00 | 5.9787 | 6.9687 | 6.9687 | 6.9687 | 6.9687
2024-09-22 11:00 | 0.97168 | 1.0425 | 1.2942 | 1.3613 | 1.4284 | 2024-07-23 11:00 | 5.9444 | 6.9287 | 6.9287 | 6.9287 | 6.9287
2024-09-22 12:00 | 1.1241 | 1.2061 | 1.4972 | 1.5748 | 1.6525 | 2024-07-23 12:00 | 5.7691 | 6.7244 | 6.7244 | 6.7244 | 6.7244
2024-09-22 13:00 | 0.7621 | 0.81768 | 1.015 | 1.0677 | 1.1203 | 2024-07-23 13:00 | 5.1861 | 6.0449 | 6.0449 | 6.0449 | 6.0449
2024-09-22 14:00 | 0.81926 | 0.879 | 1.0912 | 1.1478 | 1.2043 | 2024-07-23 14:00 | 5.1366 | 5.9871 | 5.9871 | 5.9871 | 5.9871
2024-09-22 15:00 | 0.19053 | 0.20442 | 0.25376 | 0.26692 | 0.28008 | 2024-07-23 15:00 | 3.6543 | 4.2594 | 4.2594 | 4.2594 | 4.2594
2024-09-22 16:00 | 1.105 | 1.1856 | 1.4718 | 1.5481 | 1.6244 | 2024-07-23 16:00 | 3.9172 | 4.5658 | 4.5658 | 4.5658 | 4.5658
2024-09-22 17:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-07-23 17:00 | 4.0582 | 4.7302 | 4.7302 | 4.7302 | 4.7302
2024-09-22 18:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-07-23 18:00 | 3.3952 | 3.9574 | 3.9574 | 3.9574 | 3.9574
2024-09-22 19:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-07-23 19:00 | 2.6674 | 3.109 | 3.109 | 3.109 | 3.109
2024-09-22 20:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-07-23 20:00 | 2.6407 | 3.078 | 3.078 | 3.078 | 3.078
2024-09-22 21:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-07-23 21:00 | 2.3473 | 2.736 | 2.736 | 2.736 | 2.736
2024-09-22 22:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-07-23 22:00 | 2.0272 | 2.3629 | 2.3629 | 2.3629 | 2.3629
2024-09-22 23:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-07-23 23:00 | 1.8862 | 2.1985 | 2.1985 | 2.1985 | 2.1985
2024-09-23 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-07-24 | 1.7071 | 1.9898 | 1.9898 | 1.9898 | 1.9898
2024-09-23 01:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-07-24 01:00 | 1.7871 | 2.0831 | 2.0831 | 2.0831 | 2.0831
2024-09-23 02:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-07-24 02:00 | 1.8252 | 2.1275 | 2.1275 | 2.1275 | 2.1275
2024-09-23 03:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-07-24 03:00 | 1.9167 | 2.2341 | 2.2341 | 2.2341 | 2.2341
2024-09-23 04:00 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 2024-07-24 04:00 | 2.111 | 2.4606 | 2.4606 | 2.4606 | 2.4606
2024-09-23 05:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-07-24 05:00 | 2.4121 | 2.8115 | 2.8115 | 2.8115 | 2.8115
2024-09-23 06:00 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 2024-07-24 06:00 | 3.1589 | 3.682 | 3.682 | 3.682 | 3.682
2024-09-23 07:00 | 1.7528 | 1.8807 | 2.3346 | 2.4557 | 2.5767 | 2024-07-24 07:00 | 3.5666 | 4.1572 | 4.1572 | 4.1572 | 4.1572
2024-09-23 08:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-07-24 08:00 | 4.0734 | 4.7479 | 4.7479 | 4.7479 | 4.7479
2024-09-23 09:00 | 1.3146 | 1.4105 | 1.751 | 1.8417 | 1.9325 | 2024-07-24 09:00 | 3.982 | 4.6414 | 4.6414 | 4.6414 | 4.6414
2024-09-23 10:00 | 1.0479 | 1.1243 | 1.3957 | 1.4681 | 1.5404 | 2024-07-24 10:00 | 3.9058 | 4.5525 | 4.5525 | 4.5525 | 4.5525
2024-09-23 11:00 | 1.1241 | 1.2061 | 1.4972 | 1.5748 | 1.6525 | 2024-07-24 11:00 | 3.7114 | 4.326 | 4.326 | 4.326 | 4.326
2024-09-23 12:00 | 1.1622 | 1.247 | 1.5479 | 1.6282 | 1.7085 | 2024-07-24 12:00 | 3.5019 | 4.0817 | 4.0817 | 4.0817 | 4.0817
2024-09-23 13:00 | 1.2003 | 1.2878 | 1.5987 | 1.6816 | 1.7645 | 2024-07-24 13:00 | 3.7534 | 4.3749 | 4.3749 | 4.3749 | 4.3749
2024-09-23 14:00 | 1.2384 | 1.3287 | 1.6494 | 1.735 | 1.8205 | 2024-07-24 14:00 | 3.6314 | 4.2327 | 4.2327 | 4.2327 | 4.2327
2024-09-23 15:00 | 2.0577 | 2.2077 | 2.7406 | 2.8827 | 3.0248 | 2024-07-24 15:00 | 3.8524 | 4.4903 | 4.4903 | 4.4903 | 4.4903
2024-09-23 16:00 | 2.0767 | 2.2282 | 2.766 | 2.9094 | 3.0528 | 2024-07-24 16:00 | 4.0048 | 4.668 | 4.668 | 4.668 | 4.668
2024-09-23 17:00 | 2.0386 | 2.1873 | 2.7152 | 2.856 | 2.9968 | 2024-07-24 17:00 | 4.0125 | 4.6769 | 4.6769 | 4.6769 | 4.6769
2024-09-23 18:00 | 1.9053 | 2.0442 | 2.5376 | 2.6692 | 2.8008 | 2024-07-24 18:00 | 3.3418 | 3.8952 | 3.8952 | 3.8952 | 3.8952
2024-09-23 19:00 | 1.7909 | 1.9215 | 2.3854 | 2.509 | 2.6327 | 2024-07-24 19:00 | 2.7017 | 3.149 | 3.149 | 3.149 | 3.149
2024-09-23 20:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-07-24 20:00 | 2.6293 | 3.0646 | 3.0646 | 3.0646 | 3.0646
2024-09-23 21:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-07-24 21:00 | 2.2634 | 2.6382 | 2.6382 | 2.6382 | 2.6382
2024-09-23 22:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-07-24 22:00 | 1.9853 | 2.314 | 2.314 | 2.314 | 2.314
2024-09-23 23:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-07-24 23:00 | 1.9853 | 2.314 | 2.314 | 2.314 | 2.314
2024-09-24 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-07-25 | 1.6957 | 1.9765 | 1.9765 | 1.9765 | 1.9765
2024-09-24 01:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-07-25 01:00 | 1.6842 | 1.9631 | 1.9631 | 1.9631 | 1.9631
2024-09-24 02:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-07-25 02:00 | 1.6995 | 1.9809 | 1.9809 | 1.9809 | 1.9809
2024-09-24 03:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-07-25 03:00 | 1.81 | 2.1097 | 2.1097 | 2.1097 | 2.1097
2024-09-24 04:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-07-25 04:00 | 2.092 | 2.4384 | 2.4384 | 2.4384 | 2.4384
2024-09-24 05:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-07-25 05:00 | 2.3739 | 2.767 | 2.767 | 2.767 | 2.767
2024-09-24 06:00 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 2024-07-25 06:00 | 3.2123 | 3.7442 | 3.7442 | 3.7442 | 3.7442
2024-09-24 07:00 | 2.2673 | 2.4326 | 3.0198 | 3.1763 | 3.3329 | 2024-07-25 07:00 | 3.6924 | 4.3038 | 4.3038 | 4.3038 | 4.3038
2024-09-24 08:00 | 2.1339 | 2.2895 | 2.8421 | 2.9895 | 3.1369 | 2024-07-25 08:00 | 3.9439 | 4.5969 | 4.5969 | 4.5969 | 4.5969
2024-09-24 09:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-07-25 09:00 | 4.1992 | 4.8945 | 4.8945 | 4.8945 | 4.8945
2024-09-24 10:00 | 1.7338 | 1.8602 | 2.3092 | 2.429 | 2.5487 | 2024-07-25 10:00 | 3.6314 | 4.2327 | 4.2327 | 4.2327 | 4.2327
2024-09-24 11:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-07-25 11:00 | 3.418 | 3.984 | 3.984 | 3.984 | 3.984
2024-09-24 12:00 | 1.7909 | 1.9215 | 2.3854 | 2.509 | 2.6327 | 2024-07-25 12:00 | 3.639 | 4.2416 | 4.2416 | 4.2416 | 4.2416
2024-09-24 13:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-07-25 13:00 | 3.7991 | 4.4282 | 4.4282 | 4.4282 | 4.4282
2024-09-24 14:00 | 2.3435 | 2.5144 | 3.1213 | 3.2831 | 3.4449 | 2024-07-25 14:00 | 3.8029 | 4.4326 | 4.4326 | 4.4326 | 4.4326
2024-09-24 15:00 | 2.0767 | 2.2282 | 2.766 | 2.9094 | 3.0528 | 2024-07-25 15:00 | 3.6962 | 4.3082 | 4.3082 | 4.3082 | 4.3082
2024-09-24 16:00 | 2.1339 | 2.2895 | 2.8421 | 2.9895 | 3.1369 | 2024-07-25 16:00 | 3.8486 | 4.4859 | 4.4859 | 4.4859 | 4.4859
2024-09-24 17:00 | 2.0767 | 2.2282 | 2.766 | 2.9094 | 3.0528 | 2024-07-25 17:00 | 3.7152 | 4.3304 | 4.3304 | 4.3304 | 4.3304
2024-09-24 18:00 | 1.9053 | 2.0442 | 2.5376 | 2.6692 | 2.8008 | 2024-07-25 18:00 | 3.2961 | 3.8419 | 3.8419 | 3.8419 | 3.8419
2024-09-24 19:00 | 1.81 | 1.942 | 2.4107 | 2.5357 | 2.6607 | 2024-07-25 19:00 | 2.8045 | 3.2689 | 3.2689 | 3.2689 | 3.2689
2024-09-24 20:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-07-25 20:00 | 2.6407 | 3.078 | 3.078 | 3.078 | 3.078
2024-09-24 21:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-07-25 21:00 | 2.5302 | 2.9491 | 2.9491 | 2.9491 | 2.9491
2024-09-24 22:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-07-25 22:00 | 2.0729 | 2.4162 | 2.4162 | 2.4162 | 2.4162
2024-09-24 23:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-07-25 23:00 | 1.8633 | 2.1719 | 2.1719 | 2.1719 | 2.1719
2024-09-25 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-07-26 | 1.8062 | 2.1053 | 2.1053 | 2.1053 | 2.1053
2024-09-25 01:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-07-26 01:00 | 1.8557 | 2.163 | 2.163 | 2.163 | 2.163
2024-09-25 02:00 | 1.448 | 1.5536 | 1.9286 | 2.0286 | 2.1286 | 2024-07-26 02:00 | 1.6766 | 1.9543 | 1.9543 | 1.9543 | 1.9543
2024-09-25 03:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-07-26 03:00 | 1.7871 | 2.0831 | 2.0831 | 2.0831 | 2.0831
2024-09-25 04:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-07-26 04:00 | 2.191 | 2.5539 | 2.5539 | 2.5539 | 2.5539
2024-09-25 05:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-07-26 05:00 | 2.332 | 2.7182 | 2.7182 | 2.7182 | 2.7182
2024-09-25 06:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-07-26 06:00 | 3.2694 | 3.8108 | 3.8108 | 3.8108 | 3.8108
2024-09-25 07:00 | 1.9053 | 2.0442 | 2.5376 | 2.6692 | 2.8008 | 2024-07-26 07:00 | 3.86 | 4.4992 | 4.4992 | 4.4992 | 4.4992
2024-09-25 08:00 | 2.2482 | 2.4121 | 2.9944 | 3.1496 | 3.3049 | 2024-07-26 08:00 | 4.0925 | 4.7702 | 4.7702 | 4.7702 | 4.7702
2024-09-25 09:00 | 2.2863 | 2.453 | 3.0451 | 3.203 | 3.3609 | 2024-07-26 09:00 | 4.0048 | 4.668 | 4.668 | 4.668 | 4.668
2024-09-25 10:00 | 2.0386 | 2.1873 | 2.7152 | 2.856 | 2.9968 | 2024-07-26 10:00 | 3.4142 | 3.9796 | 3.9796 | 3.9796 | 3.9796
2024-09-25 11:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-07-26 11:00 | 3.5781 | 4.1706 | 4.1706 | 4.1706 | 4.1706
2024-09-25 12:00 | 2.1148 | 2.2691 | 2.8167 | 2.9628 | 3.1089 | 2024-07-26 12:00 | 3.4752 | 4.0506 | 4.0506 | 4.0506 | 4.0506
2024-09-25 13:00 | 2.2482 | 2.4121 | 2.9944 | 3.1496 | 3.3049 | 2024-07-26 13:00 | 3.3342 | 3.8863 | 3.8863 | 3.8863 | 3.8863
2024-09-25 14:00 | 2.2101 | 2.3713 | 2.9436 | 3.0963 | 3.2489 | 2024-07-26 14:00 | 3.3837 | 3.944 | 3.944 | 3.944 | 3.944
2024-09-25 15:00 | 2.1339 | 2.2895 | 2.8421 | 2.9895 | 3.1369 | 2024-07-26 15:00 | 3.681 | 4.2905 | 4.2905 | 4.2905 | 4.2905
2024-09-25 16:00 | 2.1529 | 2.3099 | 2.8675 | 3.0162 | 3.1649 | 2024-07-26 16:00 | 3.8181 | 4.4504 | 4.4504 | 4.4504 | 4.4504
2024-09-25 17:00 | 2.0005 | 2.1464 | 2.6645 | 2.8026 | 2.9408 | 2024-07-26 17:00 | 3.8639 | 4.5037 | 4.5037 | 4.5037 | 4.5037
2024-09-25 18:00 | 1.9624 | 2.1055 | 2.6137 | 2.7493 | 2.8848 | 2024-07-26 18:00 | 3.5514 | 4.1395 | 4.1395 | 4.1395 | 4.1395
2024-09-25 19:00 | 1.7528 | 1.8807 | 2.3346 | 2.4557 | 2.5767 | 2024-07-26 19:00 | 3.2313 | 3.7664 | 3.7664 | 3.7664 | 3.7664
2024-09-25 20:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-07-26 20:00 | 2.9989 | 3.4955 | 3.4955 | 3.4955 | 3.4955
2024-09-25 21:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-07-26 21:00 | 2.2863 | 2.6649 | 2.6649 | 2.6649 | 2.6649
2024-09-25 22:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-07-26 22:00 | 2.0234 | 2.3584 | 2.3584 | 2.3584 | 2.3584
2024-09-25 23:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-07-26 23:00 | 2.0005 | 2.3318 | 2.3318 | 2.3318 | 2.3318
2024-09-26 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-07-27 | 1.7719 | 2.0653 | 2.0653 | 2.0653 | 2.0653
2024-09-26 01:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-07-27 01:00 | 1.7643 | 2.0564 | 2.0564 | 2.0564 | 2.0564
2024-09-26 02:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-07-27 02:00 | 1.829 | 2.1319 | 2.1319 | 2.1319 | 2.1319
2024-09-26 03:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-07-27 03:00 | 1.7719 | 2.0653 | 2.0653 | 2.0653 | 2.0653
2024-09-26 04:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-07-27 04:00 | 2.0272 | 2.3629 | 2.3629 | 2.3629 | 2.3629
2024-09-26 05:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-07-27 05:00 | 2.3625 | 2.7537 | 2.7537 | 2.7537 | 2.7537
2024-09-26 06:00 | 1.7909 | 1.9215 | 2.3854 | 2.509 | 2.6327 | 2024-07-27 06:00 | 2.6445 | 3.0824 | 3.0824 | 3.0824 | 3.0824
2024-09-26 07:00 | 2.4959 | 2.6779 | 3.3243 | 3.4966 | 3.669 | 2024-07-27 07:00 | 2.7359 | 3.189 | 3.189 | 3.189 | 3.189
2024-09-26 08:00 | 2.3816 | 2.5552 | 3.172 | 3.3365 | 3.501 | 2024-07-27 08:00 | 3.0751 | 3.5843 | 3.5843 | 3.5843 | 3.5843
2024-09-26 09:00 | 2.4959 | 2.6779 | 3.3243 | 3.4966 | 3.669 | 2024-07-27 09:00 | 3.2656 | 3.8064 | 3.8064 | 3.8064 | 3.8064
2024-09-26 10:00 | 2.3816 | 2.5552 | 3.172 | 3.3365 | 3.501 | 2024-07-27 10:00 | 3.1932 | 3.722 | 3.722 | 3.722 | 3.722
2024-09-26 11:00 | 2.2101 | 2.3713 | 2.9436 | 3.0963 | 3.2489 | 2024-07-27 11:00 | 2.9341 | 3.4199 | 3.4199 | 3.4199 | 3.4199
2024-09-26 12:00 | 2.3816 | 2.5552 | 3.172 | 3.3365 | 3.501 | 2024-07-27 12:00 | 2.8731 | 3.3489 | 3.3489 | 3.3489 | 3.3489
2024-09-26 13:00 | 2.2482 | 2.4121 | 2.9944 | 3.1496 | 3.3049 | 2024-07-27 13:00 | 2.7321 | 3.1845 | 3.1845 | 3.1845 | 3.1845
2024-09-26 14:00 | 2.0005 | 2.1464 | 2.6645 | 2.8026 | 2.9408 | 2024-07-27 14:00 | 2.6331 | 3.0691 | 3.0691 | 3.0691 | 3.0691
2024-09-26 15:00 | 2.1339 | 2.2895 | 2.8421 | 2.9895 | 3.1369 | 2024-07-27 15:00 | 2.9455 | 3.4333 | 3.4333 | 3.4333 | 3.4333
2024-09-26 16:00 | 2.1339 | 2.2895 | 2.8421 | 2.9895 | 3.1369 | 2024-07-27 16:00 | 3.1894 | 3.7175 | 3.7175 | 3.7175 | 3.7175
2024-09-26 17:00 | 2.0577 | 2.2077 | 2.7406 | 2.8827 | 3.0248 | 2024-07-27 17:00 | 3.1627 | 3.6864 | 3.6864 | 3.6864 | 3.6864
2024-09-26 18:00 | 2.0196 | 2.1668 | 2.6899 | 2.8293 | 2.9688 | 2024-07-27 18:00 | 2.7855 | 3.2467 | 3.2467 | 3.2467 | 3.2467
2024-09-26 19:00 | 1.8672 | 2.0033 | 2.4869 | 2.6158 | 2.7448 | 2024-07-27 19:00 | 2.4578 | 2.8648 | 2.8648 | 2.8648 | 2.8648
2024-09-26 20:00 | 1.7338 | 1.8602 | 2.3092 | 2.429 | 2.5487 | 2024-07-27 20:00 | 2.233 | 2.6027 | 2.6027 | 2.6027 | 2.6027
2024-09-26 21:00 | 1.7528 | 1.8807 | 2.3346 | 2.4557 | 2.5767 | 2024-07-27 21:00 | 2.0805 | 2.4251 | 2.4251 | 2.4251 | 2.4251
2024-09-26 22:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-07-27 22:00 | 1.8519 | 2.1586 | 2.1586 | 2.1586 | 2.1586
2024-09-26 23:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-07-27 23:00 | 1.951 | 2.274 | 2.274 | 2.274 | 2.274
2024-09-27 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-07-28 | 1.8214 | 2.123 | 2.123 | 2.123 | 2.123
2024-09-27 01:00 | 1.3908 | 1.4923 | 1.8525 | 1.9485 | 2.0446 | 2024-07-28 01:00 | 1.669 | 1.9454 | 1.9454 | 1.9454 | 1.9454
2024-09-27 02:00 | 1.448 | 1.5536 | 1.9286 | 2.0286 | 2.1286 | 2024-07-28 02:00 | 1.6652 | 1.9409 | 1.9409 | 1.9409 | 1.9409
2024-09-27 03:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-07-28 03:00 | 1.9129 | 2.2296 | 2.2296 | 2.2296 | 2.2296
2024-09-27 04:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-07-28 04:00 | 2.1529 | 2.5094 | 2.5094 | 2.5094 | 2.5094
2024-09-27 05:00 | 1.6576 | 1.7784 | 2.2077 | 2.3222 | 2.4367 | 2024-07-28 05:00 | 2.1949 | 2.5583 | 2.5583 | 2.5583 | 2.5583
2024-09-27 06:00 | 1.6766 | 1.7989 | 2.2331 | 2.3489 | 2.4647 | 2024-07-28 06:00 | 2.3587 | 2.7493 | 2.7493 | 2.7493 | 2.7493
2024-09-27 07:00 | 2.0196 | 2.1668 | 2.6899 | 2.8293 | 2.9688 | 2024-07-28 07:00 | 2.6978 | 3.1446 | 3.1446 | 3.1446 | 3.1446
2024-09-27 08:00 | 1.7338 | 1.8602 | 2.3092 | 2.429 | 2.5487 | 2024-07-28 08:00 | 2.7474 | 3.2023 | 3.2023 | 3.2023 | 3.2023
2024-09-27 09:00 | 2.0577 | 2.2077 | 2.7406 | 2.8827 | 3.0248 | 2024-07-28 09:00 | 2.9608 | 3.451 | 3.451 | 3.451 | 3.451
2024-09-27 10:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-07-28 10:00 | 2.6483 | 3.0868 | 3.0868 | 3.0868 | 3.0868
2024-09-27 11:00 | 1.9434 | 2.0851 | 2.5884 | 2.7226 | 2.8568 | 2024-07-28 11:00 | 3.0789 | 3.5887 | 3.5887 | 3.5887 | 3.5887
2024-09-27 12:00 | 1.81 | 1.942 | 2.4107 | 2.5357 | 2.6607 | 2024-07-28 12:00 | 3.2046 | 3.7353 | 3.7353 | 3.7353 | 3.7353
2024-09-27 13:00 | 0.99073 | 1.063 | 1.3196 | 1.388 | 1.4564 | 2024-07-28 13:00 | 3.3647 | 3.9218 | 3.9218 | 3.9218 | 3.9218
2024-09-27 14:00 | 1.2765 | 1.3696 | 1.7002 | 1.7884 | 1.8765 | 2024-07-28 14:00 | 3.3342 | 3.8863 | 3.8863 | 3.8863 | 3.8863
2024-09-27 15:00 | 0.93358 | 1.0017 | 1.2434 | 1.3079 | 1.3724 | 2024-07-28 15:00 | 3.1627 | 3.6864 | 3.6864 | 3.6864 | 3.6864
2024-09-27 16:00 | 1.9815 | 2.126 | 2.6391 | 2.776 | 2.9128 | 2024-07-28 16:00 | 3.1056 | 3.6198 | 3.6198 | 3.6198 | 3.6198
2024-09-27 17:00 | 2.0005 | 2.1464 | 2.6645 | 2.8026 | 2.9408 | 2024-07-28 17:00 | 3.2161 | 3.7486 | 3.7486 | 3.7486 | 3.7486
2024-09-27 18:00 | 1.8862 | 2.0237 | 2.5122 | 2.6425 | 2.7728 | 2024-07-28 18:00 | 2.8122 | 3.2778 | 3.2778 | 3.2778 | 3.2778
2024-09-27 19:00 | 1.6957 | 1.8193 | 2.2585 | 2.3756 | 2.4927 | 2024-07-28 19:00 | 2.6254 | 3.0602 | 3.0602 | 3.0602 | 3.0602
2024-09-27 20:00 | 1.7338 | 1.8602 | 2.3092 | 2.429 | 2.5487 | 2024-07-28 20:00 | 2.2901 | 2.6693 | 2.6693 | 2.6693 | 2.6693
2024-09-27 21:00 | 1.6385 | 1.758 | 2.1823 | 2.2955 | 2.4087 | 2024-07-28 21:00 | 2.1949 | 2.5583 | 2.5583 | 2.5583 | 2.5583
2024-09-27 22:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-07-28 22:00 | 1.951 | 2.274 | 2.274 | 2.274 | 2.274
2024-09-27 23:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-07-28 23:00 | 1.8519 | 2.1586 | 2.1586 | 2.1586 | 2.1586
2024-09-28 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-07-29 | 1.8405 | 2.1452 | 2.1452 | 2.1452 | 2.1452
2024-09-28 01:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-07-29 01:00 | 1.749 | 2.0386 | 2.0386 | 2.0386 | 2.0386
2024-09-28 02:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-07-29 02:00 | 1.8748 | 2.1852 | 2.1852 | 2.1852 | 2.1852
2024-09-28 03:00 | 1.3718 | 1.4718 | 1.8271 | 1.9218 | 2.0166 | 2024-07-29 03:00 | 1.8786 | 2.1897 | 2.1897 | 2.1897 | 2.1897
2024-09-28 04:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-07-29 04:00 | 2.1529 | 2.5094 | 2.5094 | 2.5094 | 2.5094
2024-09-28 05:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-07-29 05:00 | 2.5607 | 2.9847 | 2.9847 | 2.9847 | 2.9847
2024-09-28 06:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-07-29 06:00 | 3.6543 | 4.2594 | 4.2594 | 4.2594 | 4.2594
2024-09-28 07:00 | 1.448 | 1.5536 | 1.9286 | 2.0286 | 2.1286 | 2024-07-29 07:00 | 3.902 | 4.5481 | 4.5481 | 4.5481 | 4.5481
2024-09-28 08:00 | 1.2003 | 1.2878 | 1.5987 | 1.6816 | 1.7645 | 2024-07-29 08:00 | 4.062 | 4.7346 | 4.7346 | 4.7346 | 4.7346
2024-09-28 09:00 | 1.105 | 1.1856 | 1.4718 | 1.5481 | 1.6244 | 2024-07-29 09:00 | 4.4088 | 5.1388 | 5.1388 | 5.1388 | 5.1388
2024-09-28 10:00 | 1.2003 | 1.2878 | 1.5987 | 1.6816 | 1.7645 | 2024-07-29 10:00 | 3.7991 | 4.4282 | 4.4282 | 4.4282 | 4.4282
2024-09-28 11:00 | 0.81926 | 0.879 | 1.0912 | 1.1478 | 1.2043 | 2024-07-29 11:00 | 3.8029 | 4.4326 | 4.4326 | 4.4326 | 4.4326
2024-09-28 12:00 | 0.80021 | 0.85856 | 1.0658 | 1.1211 | 1.1763 | 2024-07-29 12:00 | 3.7343 | 4.3527 | 4.3527 | 4.3527 | 4.3527
2024-09-28 13:00 | 0.53347 | 0.57237 | 0.71053 | 0.74737 | 0.78422 | 2024-07-29 13:00 | 3.4828 | 4.0595 | 4.0595 | 4.0595 | 4.0595
2024-09-28 14:00 | 0.038105 | 0.040884 | 0.050752 | 0.053384 | 0.056015 | 2024-07-29 14:00 | 3.54 | 4.1261 | 4.1261 | 4.1261 | 4.1261
2024-09-28 15:00 | 0.17147 | 0.18398 | 0.22839 | 0.24023 | 0.25207 | 2024-07-29 15:00 | 3.8562 | 4.4948 | 4.4948 | 4.4948 | 4.4948
2024-09-28 16:00 | 1.1622 | 1.247 | 1.5479 | 1.6282 | 1.7085 | 2024-07-29 16:00 | 3.9858 | 4.6458 | 4.6458 | 4.6458 | 4.6458
2024-09-28 17:00 | 1.3908 | 1.4923 | 1.8525 | 1.9485 | 2.0446 | 2024-07-29 17:00 | 3.9972 | 4.6591 | 4.6591 | 4.6591 | 4.6591
2024-09-28 18:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-07-29 18:00 | 3.5438 | 4.1306 | 4.1306 | 4.1306 | 4.1306
2024-09-28 19:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-07-29 19:00 | 2.9379 | 3.4244 | 3.4244 | 3.4244 | 3.4244
2024-09-28 20:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-07-29 20:00 | 2.5911 | 3.0202 | 3.0202 | 3.0202 | 3.0202
2024-09-28 21:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-07-29 21:00 | 2.2787 | 2.656 | 2.656 | 2.656 | 2.656
2024-09-28 22:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-07-29 22:00 | 2.092 | 2.4384 | 2.4384 | 2.4384 | 2.4384
2024-09-28 23:00 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-07-29 23:00 | 2.0424 | 2.3806 | 2.3806 | 2.3806 | 2.3806
2024-09-29 | 1.5623 | 1.6762 | 2.0808 | 2.1887 | 2.2966 | 2024-07-30 | 1.8633 | 2.1719 | 2.1719 | 2.1719 | 2.1719
2024-09-29 01:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-07-30 01:00 | 1.7681 | 2.0609 | 2.0609 | 2.0609 | 2.0609
2024-09-29 02:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-07-30 02:00 | 1.7909 | 2.0875 | 2.0875 | 2.0875 | 2.0875
2024-09-29 03:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-07-30 03:00 | 1.9243 | 2.243 | 2.243 | 2.243 | 2.243
2024-09-29 04:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-07-30 04:00 | 2.1225 | 2.4739 | 2.4739 | 2.4739 | 2.4739
2024-09-29 05:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-07-30 05:00 | 2.4463 | 2.8514 | 2.8514 | 2.8514 | 2.8514
2024-09-29 06:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-07-30 06:00 | 3.3571 | 3.913 | 3.913 | 3.913 | 3.913
2024-09-29 07:00 | 1.448 | 1.5536 | 1.9286 | 2.0286 | 2.1286 | 2024-07-30 07:00 | 3.8905 | 4.5348 | 4.5348 | 4.5348 | 4.5348
2024-09-29 08:00 | 1.1432 | 1.2265 | 1.5226 | 1.6015 | 1.6805 | 2024-07-30 08:00 | 4.1801 | 4.8723 | 4.8723 | 4.8723 | 4.8723
2024-09-29 09:00 | 0.43821 | 0.47016 | 0.58365 | 0.61391 | 0.64418 | 2024-07-30 09:00 | 4.2563 | 4.9611 | 4.9611 | 4.9611 | 4.9611
2024-09-29 10:00 | 0.7621 | 0.81768 | 1.015 | 1.0677 | 1.1203 | 2024-07-30 10:00 | 3.5704 | 4.1617 | 4.1617 | 4.1617 | 4.1617
2024-09-29 11:00 | 0.20958 | 0.22486 | 0.27914 | 0.29361 | 0.30808 | 2024-07-30 11:00 | 3.4599 | 4.0329 | 4.0329 | 4.0329 | 4.0329
2024-09-29 12:00 | 0.59063 | 0.6337 | 0.78666 | 0.82745 | 0.86824 | 2024-07-30 12:00 | 3.4523 | 4.024 | 4.024 | 4.024 | 4.024
2024-09-29 13:00 | 0.41916 | 0.44972 | 0.55827 | 0.58722 | 0.61617 | 2024-07-30 13:00 | 3.2732 | 3.8152 | 3.8152 | 3.8152 | 3.8152
2024-09-29 14:00 | 0.83831 | 0.89944 | 1.1165 | 1.1744 | 1.2323 | 2024-07-30 14:00 | 3.4866 | 4.064 | 4.064 | 4.064 | 4.064
2024-09-29 15:00 | 1.1241 | 1.2061 | 1.4972 | 1.5748 | 1.6525 | 2024-07-30 15:00 | 3.4866 | 4.064 | 4.064 | 4.064 | 4.064
2024-09-29 16:00 | 1.448 | 1.5536 | 1.9286 | 2.0286 | 2.1286 | 2024-07-30 16:00 | 3.7381 | 4.3571 | 4.3571 | 4.3571 | 4.3571
2024-09-29 17:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-07-30 17:00 | 3.8143 | 4.4459 | 4.4459 | 4.4459 | 4.4459
2024-09-29 18:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-07-30 18:00 | 3.5438 | 4.1306 | 4.1306 | 4.1306 | 4.1306
2024-09-29 19:00 | 1.5433 | 1.6558 | 2.0555 | 2.162 | 2.2686 | 2024-07-30 19:00 | 3.0637 | 3.571 | 3.571 | 3.571 | 3.571
2024-09-29 20:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-07-30 20:00 | 2.5492 | 2.9714 | 2.9714 | 2.9714 | 2.9714
2024-09-29 21:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-07-30 21:00 | 2.3015 | 2.6827 | 2.6827 | 2.6827 | 2.6827
2024-09-29 22:00 | 1.5052 | 1.6149 | 2.0047 | 2.1087 | 2.2126 | 2024-07-30 22:00 | 2.172 | 2.5316 | 2.5316 | 2.5316 | 2.5316
2024-09-29 23:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-07-30 23:00 | 2.0081 | 2.3407 | 2.3407 | 2.3407 | 2.3407
2024-09-30 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-07-31 | 1.7414 | 2.0298 | 2.0298 | 2.0298 | 2.0298
2024-09-30 01:00 | 1.4099 | 1.5127 | 1.8778 | 1.9752 | 2.0726 | 2024-07-31 01:00 | 1.7528 | 2.0431 | 2.0431 | 2.0431 | 2.0431
2024-09-30 02:00 | 1.448 | 1.5536 | 1.9286 | 2.0286 | 2.1286 | 2024-07-31 02:00 | 1.73 | 2.0164 | 2.0164 | 2.0164 | 2.0164
2024-09-30 03:00 | 1.3527 | 1.4514 | 1.8017 | 1.8951 | 1.9885 | 2024-07-31 03:00 | 1.8786 | 2.1897 | 2.1897 | 2.1897 | 2.1897
2024-09-30 04:00 | 1.467 | 1.574 | 1.954 | 2.0553 | 2.1566 | 2024-07-31 04:00 | 2.172 | 2.5316 | 2.5316 | 2.5316 | 2.5316
2024-09-30 05:00 | 1.5814 | 1.6967 | 2.1062 | 2.2154 | 2.3246 | 2024-07-31 05:00 | 2.5073 | 2.9225 | 2.9225 | 2.9225 | 2.9225
2024-09-30 06:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-07-31 06:00 | 3.5819 | 4.175 | 4.175 | 4.175 | 4.175
2024-09-30 07:00 | 2.0767 | 2.2282 | 2.766 | 2.9094 | 3.0528 | 2024-07-31 07:00 | 3.9972 | 4.6591 | 4.6591 | 4.6591 | 4.6591
2024-09-30 08:00 | 1.2575 | 1.3492 | 1.6748 | 1.7617 | 1.8485 | 2024-07-31 08:00 | 4.3211 | 5.0366 | 5.0366 | 5.0366 | 5.0366
2024-09-30 09:00 | 2.0196 | 2.1668 | 2.6899 | 2.8293 | 2.9688 | 2024-07-31 09:00 | 4.485 | 5.2276 | 5.2276 | 5.2276 | 5.2276
2024-09-30 10:00 | 1.9243 | 2.0646 | 2.563 | 2.6959 | 2.8288 | 2024-07-31 10:00 | 4.1154 | 4.7968 | 4.7968 | 4.7968 | 4.7968
2024-09-30 11:00 | 1.8862 | 2.0237 | 2.5122 | 2.6425 | 2.7728 | 2024-07-31 11:00 | 3.7343 | 4.3527 | 4.3527 | 4.3527 | 4.3527
2024-09-30 12:00 | 1.9624 | 2.1055 | 2.6137 | 2.7493 | 2.8848 | 2024-07-31 12:00 | 3.4904 | 4.0684 | 4.0684 | 4.0684 | 4.0684
2024-09-30 13:00 | 1.9815 | 2.126 | 2.6391 | 2.776 | 2.9128 | 2024-07-31 13:00 | 3.4142 | 3.9796 | 3.9796 | 3.9796 | 3.9796
2024-09-30 14:00 | 2.0767 | 2.2282 | 2.766 | 2.9094 | 3.0528 | 2024-07-31 14:00 | 3.3075 | 3.8552 | 3.8552 | 3.8552 | 3.8552
2024-09-30 15:00 | 2.1529 | 2.3099 | 2.8675 | 3.0162 | 3.1649 | 2024-07-31 15:00 | 3.6009 | 4.1972 | 4.1972 | 4.1972 | 4.1972
2024-09-30 16:00 | 2.1148 | 2.2691 | 2.8167 | 2.9628 | 3.1089 | 2024-07-31 16:00 | 3.8448 | 4.4815 | 4.4815 | 4.4815 | 4.4815
2024-09-30 17:00 | 1.9434 | 2.0851 | 2.5884 | 2.7226 | 2.8568 | 2024-07-31 17:00 | 3.8753 | 4.517 | 4.517 | 4.517 | 4.517
2024-09-30 18:00 | 1.8672 | 2.0033 | 2.4869 | 2.6158 | 2.7448 | 2024-07-31 18:00 | 3.277 | 3.8197 | 3.8197 | 3.8197 | 3.8197
2024-09-30 19:00 | 1.7719 | 1.9011 | 2.36 | 2.4823 | 2.6047 | 2024-07-31 19:00 | 2.8312 | 3.3 | 3.3 | 3.3 | 3.3
2024-09-30 20:00 | 1.6195 | 1.7376 | 2.157 | 2.2688 | 2.3807 | 2024-07-31 20:00 | 2.675 | 3.1179 | 3.1179 | 3.1179 | 3.1179
2024-09-30 21:00 | 1.6004 | 1.7171 | 2.1316 | 2.2421 | 2.3526 | 2024-07-31 21:00 | 2.4502 | 2.8559 | 2.8559 | 2.8559 | 2.8559
2024-09-30 22:00 | 1.5242 | 1.6354 | 2.0301 | 2.1354 | 2.2406 | 2024-07-31 22:00 | 2.0462 | 2.3851 | 2.3851 | 2.3851 | 2.3851
2024-09-30 23:00 | 1.4861 | 1.5945 | 1.9793 | 2.082 | 2.1846 | 2024-07-31 23:00 | 1.9891 | 2.3185 | 2.3185 | 2.3185 | 2.3185
2024-10-01 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-08-01 | 1.7643 | 2.0564 | 2.0564 | 2.0564 | 2.0564
2024-10-01 01:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-08-01 01:00 | 1.749 | 2.0386 | 2.0386 | 2.0386 | 2.0386
2024-10-01 02:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-08-01 02:00 | 1.7071 | 1.9898 | 1.9898 | 1.9898 | 1.9898
2024-10-01 03:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-08-01 03:00 | 1.9243 | 2.243 | 2.243 | 2.243 | 2.243
2024-10-01 04:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-08-01 04:00 | 2.172 | 2.5316 | 2.5316 | 2.5316 | 2.5316
2024-10-01 05:00 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2024-08-01 05:00 | 2.4806 | 2.8914 | 2.8914 | 2.8914 | 2.8914
2024-10-01 06:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2024-08-01 06:00 | 3.3456 | 3.8996 | 3.8996 | 3.8996 | 3.8996
2024-10-01 07:00 | 2.172 | 2.7019 | 3.2644 | 3.3394 | 3.4144 | 2024-08-01 07:00 | 3.9248 | 4.5747 | 4.5747 | 4.5747 | 4.5747
2024-10-01 08:00 | 2.2291 | 2.773 | 3.3503 | 3.4273 | 3.5043 | 2024-08-01 08:00 | 4.1649 | 4.8545 | 4.8545 | 4.8545 | 4.8545
2024-10-01 09:00 | 2.2291 | 2.773 | 3.3503 | 3.4273 | 3.5043 | 2024-08-01 09:00 | 3.9782 | 4.6369 | 4.6369 | 4.6369 | 4.6369
2024-10-01 10:00 | 0.57158 | 0.71103 | 0.85905 | 0.87879 | 0.89853 | 2024-08-01 10:00 | 3.7152 | 4.3304 | 4.3304 | 4.3304 | 4.3304
2024-10-01 11:00 | 0.68589 | 0.85323 | 1.0309 | 1.0545 | 1.0782 | 2024-08-01 11:00 | 3.4942 | 4.0728 | 4.0728 | 4.0728 | 4.0728
2024-10-01 12:00 | 0.85737 | 1.0665 | 1.2886 | 1.3182 | 1.3478 | 2024-08-01 12:00 | 3.6314 | 4.2327 | 4.2327 | 4.2327 | 4.2327
2024-10-01 13:00 | 0.78115 | 0.97174 | 1.174 | 1.201 | 1.228 | 2024-08-01 13:00 | 3.4371 | 4.0062 | 4.0062 | 4.0062 | 4.0062
2024-10-01 14:00 | 0.78115 | 0.97174 | 1.174 | 1.201 | 1.228 | 2024-08-01 14:00 | 3.4028 | 3.9662 | 3.9662 | 3.9662 | 3.9662
2024-10-01 15:00 | 0.85737 | 1.0665 | 1.2886 | 1.3182 | 1.3478 | 2024-08-01 15:00 | 3.6238 | 4.2239 | 4.2239 | 4.2239 | 4.2239
2024-10-01 16:00 | 1.7147 | 2.1331 | 2.5772 | 2.6364 | 2.6956 | 2024-08-01 16:00 | 3.8181 | 4.4504 | 4.4504 | 4.4504 | 4.4504
2024-10-01 17:00 | 1.9434 | 2.4175 | 2.9208 | 2.9879 | 3.055 | 2024-08-01 17:00 | 3.9096 | 4.557 | 4.557 | 4.557 | 4.557
2024-10-01 18:00 | 1.9815 | 2.4649 | 2.9781 | 3.0465 | 3.1149 | 2024-08-01 18:00 | 3.2961 | 3.8419 | 3.8419 | 3.8419 | 3.8419
2024-10-01 19:00 | 1.81 | 2.2516 | 2.7203 | 2.7828 | 2.8453 | 2024-08-01 19:00 | 2.8274 | 3.2956 | 3.2956 | 3.2956 | 3.2956
2024-10-01 20:00 | 1.7147 | 2.1331 | 2.5772 | 2.6364 | 2.6956 | 2024-08-01 20:00 | 2.5569 | 2.9802 | 2.9802 | 2.9802 | 2.9802
2024-10-01 21:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2024-08-01 21:00 | 2.2787 | 2.656 | 2.656 | 2.656 | 2.656
2024-10-01 22:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2024-08-01 22:00 | 1.9891 | 2.3185 | 2.3185 | 2.3185 | 2.3185
2024-10-01 23:00 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2024-08-01 23:00 | 2.0729 | 2.4162 | 2.4162 | 2.4162 | 2.4162
2024-10-02 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2024-08-02 | 1.7986 | 2.0964 | 2.0964 | 2.0964 | 2.0964
2024-10-02 01:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2024-08-02 01:00 | 1.7795 | 2.0742 | 2.0742 | 2.0742 | 2.0742
2024-10-02 02:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-08-02 02:00 | 1.7414 | 2.0298 | 2.0298 | 2.0298 | 2.0298
2024-10-02 03:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-08-02 03:00 | 1.9319 | 2.2518 | 2.2518 | 2.2518 | 2.2518
2024-10-02 04:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2024-08-02 04:00 | 2.2368 | 2.6072 | 2.6072 | 2.6072 | 2.6072
2024-10-02 05:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2024-08-02 05:00 | 2.473 | 2.8825 | 2.8825 | 2.8825 | 2.8825
2024-10-02 06:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2024-08-02 06:00 | 3.3418 | 3.8952 | 3.8952 | 3.8952 | 3.8952
2024-10-02 07:00 | 2.0577 | 2.5597 | 3.0926 | 3.1636 | 3.2347 | 2024-08-02 07:00 | 3.9591 | 4.6147 | 4.6147 | 4.6147 | 4.6147
2024-10-02 08:00 | 2.1148 | 2.6308 | 3.1785 | 3.2515 | 3.3245 | 2024-08-02 08:00 | 3.9706 | 4.628 | 4.628 | 4.628 | 4.628
2024-10-02 09:00 | 1.8481 | 2.299 | 2.7776 | 2.8414 | 2.9052 | 2024-08-02 09:00 | 4.1344 | 4.819 | 4.819 | 4.819 | 4.819
2024-10-02 10:00 | 1.81 | 2.2516 | 2.7203 | 2.7828 | 2.8453 | 2024-08-02 10:00 | 3.6771 | 4.286 | 4.286 | 4.286 | 4.286
2024-10-02 11:00 | 2.0196 | 2.5123 | 3.0353 | 3.1051 | 3.1748 | 2024-08-02 11:00 | 3.5095 | 4.0906 | 4.0906 | 4.0906 | 4.0906
2024-10-02 12:00 | 1.9624 | 2.4412 | 2.9494 | 3.0172 | 3.0849 | 2024-08-02 12:00 | 3.5323 | 4.1173 | 4.1173 | 4.1173 | 4.1173
2024-10-02 13:00 | 1.1241 | 1.3984 | 1.6895 | 1.7283 | 1.7671 | 2024-08-02 13:00 | 3.4523 | 4.024 | 4.024 | 4.024 | 4.024
2024-10-02 14:00 | 1.2194 | 1.5169 | 1.8326 | 1.8748 | 1.9169 | 2024-08-02 14:00 | 3.4409 | 4.0107 | 4.0107 | 4.0107 | 4.0107
2024-10-02 15:00 | 1.81 | 2.2516 | 2.7203 | 2.7828 | 2.8453 | 2024-08-02 15:00 | 3.4676 | 4.0418 | 4.0418 | 4.0418 | 4.0418
2024-10-02 16:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2024-08-02 16:00 | 3.921 | 4.5703 | 4.5703 | 4.5703 | 4.5703
2024-10-02 17:00 | 1.9243 | 2.3938 | 2.8921 | 2.9586 | 3.025 | 2024-08-02 17:00 | 3.9324 | 4.5836 | 4.5836 | 4.5836 | 4.5836
2024-10-02 18:00 | 1.8672 | 2.3227 | 2.8062 | 2.8707 | 2.9352 | 2024-08-02 18:00 | 3.5438 | 4.1306 | 4.1306 | 4.1306 | 4.1306
2024-10-02 19:00 | 1.7528 | 2.1805 | 2.6344 | 2.695 | 2.7555 | 2024-08-02 19:00 | 3.2389 | 3.7753 | 3.7753 | 3.7753 | 3.7753
2024-10-02 20:00 | 1.7147 | 2.1331 | 2.5772 | 2.6364 | 2.6956 | 2024-08-02 20:00 | 2.9112 | 3.3933 | 3.3933 | 3.3933 | 3.3933
2024-10-02 21:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2024-08-02 21:00 | 2.6674 | 3.109 | 3.109 | 3.109 | 3.109
2024-10-02 22:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2024-08-02 22:00 | 2.2482 | 2.6205 | 2.6205 | 2.6205 | 2.6205
2024-10-02 23:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2024-08-02 23:00 | 2.2063 | 2.5716 | 2.5716 | 2.5716 | 2.5716
2024-10-03 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-08-03 | 1.951 | 2.274 | 2.274 | 2.274 | 2.274
2024-10-03 01:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-08-03 01:00 | 1.7109 | 1.9942 | 1.9942 | 1.9942 | 1.9942
2024-10-03 02:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-08-03 02:00 | 1.8176 | 2.1186 | 2.1186 | 2.1186 | 2.1186
2024-10-03 03:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-08-03 03:00 | 1.8862 | 2.1985 | 2.1985 | 2.1985 | 2.1985
2024-10-03 04:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-08-03 04:00 | 2.0501 | 2.3895 | 2.3895 | 2.3895 | 2.3895
2024-10-03 05:00 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2024-08-03 05:00 | 2.2368 | 2.6072 | 2.6072 | 2.6072 | 2.6072
2024-10-03 06:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2024-08-03 06:00 | 2.4044 | 2.8026 | 2.8026 | 2.8026 | 2.8026
2024-10-03 07:00 | 2.0386 | 2.536 | 3.064 | 3.1344 | 3.2047 | 2024-08-03 07:00 | 3.0141 | 3.5132 | 3.5132 | 3.5132 | 3.5132
2024-10-03 08:00 | 2.0767 | 2.5834 | 3.1212 | 3.1929 | 3.2646 | 2024-08-03 08:00 | 3.1322 | 3.6509 | 3.6509 | 3.6509 | 3.6509
2024-10-03 09:00 | 0.89547 | 1.1139 | 1.3458 | 1.3768 | 1.4077 | 2024-08-03 09:00 | 3.1818 | 3.7086 | 3.7086 | 3.7086 | 3.7086
2024-10-03 10:00 | 0.62873 | 0.78213 | 0.94496 | 0.96667 | 0.98838 | 2024-08-03 10:00 | 2.9036 | 3.3844 | 3.3844 | 3.3844 | 3.3844
2024-10-03 11:00 | 1.105 | 1.3747 | 1.6608 | 1.699 | 1.7372 | 2024-08-03 11:00 | 2.7398 | 3.1934 | 3.1934 | 3.1934 | 3.1934
2024-10-03 12:00 | 1.2575 | 1.5643 | 1.8899 | 1.9333 | 1.9768 | 2024-08-03 12:00 | 2.6635 | 3.1046 | 3.1046 | 3.1046 | 3.1046
2024-10-03 13:00 | 0.55252 | 0.68733 | 0.83042 | 0.8495 | 0.86858 | 2024-08-03 13:00 | 2.816 | 3.2823 | 3.2823 | 3.2823 | 3.2823
2024-10-03 14:00 | 0.60968 | 0.75843 | 0.91632 | 0.93738 | 0.95843 | 2024-08-03 14:00 | 2.7893 | 3.2512 | 3.2512 | 3.2512 | 3.2512
2024-10-03 15:00 | 0.78115 | 0.97174 | 1.174 | 1.201 | 1.228 | 2024-08-03 15:00 | 3.0103 | 3.5088 | 3.5088 | 3.5088 | 3.5088
2024-10-03 16:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2024-08-03 16:00 | 3.1856 | 3.7131 | 3.7131 | 3.7131 | 3.7131
2024-10-03 17:00 | 2.0005 | 2.4886 | 3.0067 | 3.0758 | 3.1448 | 2024-08-03 17:00 | 3.1665 | 3.6909 | 3.6909 | 3.6909 | 3.6909
2024-10-03 18:00 | 2.0767 | 2.5834 | 3.1212 | 3.1929 | 3.2646 | 2024-08-03 18:00 | 3.0446 | 3.5487 | 3.5487 | 3.5487 | 3.5487
2024-10-03 19:00 | 1.7909 | 2.2279 | 2.6917 | 2.7535 | 2.8154 | 2024-08-03 19:00 | 2.4845 | 2.8958 | 2.8958 | 2.8958 | 2.8958
2024-10-03 20:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2024-08-03 20:00 | 2.3549 | 2.7448 | 2.7448 | 2.7448 | 2.7448
2024-10-03 21:00 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2024-08-03 21:00 | 2.1529 | 2.5094 | 2.5094 | 2.5094 | 2.5094
2024-10-03 22:00 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2024-08-03 22:00 | 2.1034 | 2.4517 | 2.4517 | 2.4517 | 2.4517
2024-10-03 23:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-08-03 23:00 | 1.9738 | 2.3007 | 2.3007 | 2.3007 | 2.3007
2024-10-04 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-08-04 | 1.7909 | 2.0875 | 2.0875 | 2.0875 | 2.0875
2024-10-04 01:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-08-04 01:00 | 1.7795 | 2.0742 | 2.0742 | 2.0742 | 2.0742
2024-10-04 02:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-08-04 02:00 | 1.8862 | 2.1985 | 2.1985 | 2.1985 | 2.1985
2024-10-04 03:00 | 1.4289 | 1.7776 | 2.1476 | 2.197 | 2.2463 | 2024-08-04 03:00 | 1.9014 | 2.2163 | 2.2163 | 2.2163 | 2.2163
2024-10-04 04:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-08-04 04:00 | 1.9891 | 2.3185 | 2.3185 | 2.3185 | 2.3185
2024-10-04 05:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-08-04 05:00 | 2.2711 | 2.6471 | 2.6471 | 2.6471 | 2.6471
2024-10-04 06:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-08-04 06:00 | 2.5035 | 2.9181 | 2.9181 | 2.9181 | 2.9181
2024-10-04 07:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2024-08-04 07:00 | 2.7664 | 3.2245 | 3.2245 | 3.2245 | 3.2245
2024-10-04 08:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2024-08-04 08:00 | 2.8769 | 3.3533 | 3.3533 | 3.3533 | 3.3533
2024-10-04 09:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2024-08-04 09:00 | 2.8007 | 3.2645 | 3.2645 | 3.2645 | 3.2645
2024-10-04 10:00 | 1.9624 | 2.4412 | 2.9494 | 3.0172 | 3.0849 | 2024-08-04 10:00 | 2.9189 | 3.4022 | 3.4022 | 3.4022 | 3.4022
2024-10-04 11:00 | 1.7909 | 2.2279 | 2.6917 | 2.7535 | 2.8154 | 2024-08-04 11:00 | 2.8769 | 3.3533 | 3.3533 | 3.3533 | 3.3533
2024-10-04 12:00 | 2.0196 | 2.5123 | 3.0353 | 3.1051 | 3.1748 | 2024-08-04 12:00 | 3.0979 | 3.6109 | 3.6109 | 3.6109 | 3.6109
2024-10-04 13:00 | 1.9434 | 2.4175 | 2.9208 | 2.9879 | 3.055 | 2024-08-04 13:00 | 3.0827 | 3.5932 | 3.5932 | 3.5932 | 3.5932
2024-10-04 14:00 | 1.9815 | 2.4649 | 2.9781 | 3.0465 | 3.1149 | 2024-08-04 14:00 | 3.1551 | 3.6776 | 3.6776 | 3.6776 | 3.6776
2024-10-04 15:00 | 1.7719 | 2.2042 | 2.6631 | 2.7242 | 2.7854 | 2024-08-04 15:00 | 3.1361 | 3.6553 | 3.6553 | 3.6553 | 3.6553
2024-10-04 16:00 | 1.9624 | 2.4412 | 2.9494 | 3.0172 | 3.0849 | 2024-08-04 16:00 | 3.2313 | 3.7664 | 3.7664 | 3.7664 | 3.7664
2024-10-04 17:00 | 1.829 | 2.2753 | 2.749 | 2.8121 | 2.8753 | 2024-08-04 17:00 | 3.3037 | 3.8508 | 3.8508 | 3.8508 | 3.8508
2024-10-04 18:00 | 1.81 | 2.2516 | 2.7203 | 2.7828 | 2.8453 | 2024-08-04 18:00 | 2.8998 | 3.38 | 3.38 | 3.38 | 3.38
2024-10-04 19:00 | 1.7147 | 2.1331 | 2.5772 | 2.6364 | 2.6956 | 2024-08-04 19:00 | 2.5988 | 3.0291 | 3.0291 | 3.0291 | 3.0291
2024-10-04 20:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2024-08-04 20:00 | 2.3625 | 2.7537 | 2.7537 | 2.7537 | 2.7537
2024-10-04 21:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2024-08-04 21:00 | 2.1301 | 2.4828 | 2.4828 | 2.4828 | 2.4828
2024-10-04 22:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2024-08-04 22:00 | 2.0615 | 2.4028 | 2.4028 | 2.4028 | 2.4028
2024-10-04 23:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2024-08-04 23:00 | 1.8405 | 2.1452 | 2.1452 | 2.1452 | 2.1452
2024-10-05 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-08-05 | 1.9091 | 2.2252 | 2.2252 | 2.2252 | 2.2252
2024-10-05 01:00 | 1.4289 | 1.7776 | 2.1476 | 2.197 | 2.2463 | 2024-08-05 01:00 | 1.8062 | 2.1053 | 2.1053 | 2.1053 | 2.1053
2024-10-05 02:00 | 1.4289 | 1.7776 | 2.1476 | 2.197 | 2.2463 | 2024-08-05 02:00 | 1.9205 | 2.2385 | 2.2385 | 2.2385 | 2.2385
2024-10-05 03:00 | 1.4099 | 1.7539 | 2.119 | 2.1677 | 2.2164 | 2024-08-05 03:00 | 1.9129 | 2.2296 | 2.2296 | 2.2296 | 2.2296
2024-10-05 04:00 | 1.4289 | 1.7776 | 2.1476 | 2.197 | 2.2463 | 2024-08-05 04:00 | 2.1148 | 2.465 | 2.465 | 2.465 | 2.465
2024-10-05 05:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-08-05 05:00 | 2.4959 | 2.9092 | 2.9092 | 2.9092 | 2.9092
2024-10-05 06:00 | 1.4289 | 1.7776 | 2.1476 | 2.197 | 2.2463 | 2024-08-05 06:00 | 3.0903 | 3.602 | 3.602 | 3.602 | 3.602
2024-10-05 07:00 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2024-08-05 07:00 | 3.8181 | 4.4504 | 4.4504 | 4.4504 | 4.4504
2024-10-05 08:00 | 0.68589 | 0.85323 | 1.0309 | 1.0545 | 1.0782 | 2024-08-05 08:00 | 4.3249 | 5.0411 | 5.0411 | 5.0411 | 5.0411
2024-10-05 09:00 | 0.68589 | 0.85323 | 1.0309 | 1.0545 | 1.0782 | 2024-08-05 09:00 | 4.6641 | 5.4364 | 5.4364 | 5.4364 | 5.4364
2024-10-05 10:00 | 0.70494 | 0.87693 | 1.0595 | 1.0838 | 1.1082 | 2024-08-05 10:00 | 4.1725 | 4.8634 | 4.8634 | 4.8634 | 4.8634
2024-10-05 11:00 | 0.62873 | 0.78213 | 0.94496 | 0.96667 | 0.98838 | 2024-08-05 11:00 | 4.2983 | 5.01 | 5.01 | 5.01 | 5.01
2024-10-05 12:00 | 0.47631 | 0.59252 | 0.71588 | 0.73232 | 0.74877 | 2024-08-05 12:00 | 4.1268 | 4.8101 | 4.8101 | 4.8101 | 4.8101
2024-10-05 13:00 | 0.45726 | 0.56882 | 0.68724 | 0.70303 | 0.71882 | 2024-08-05 13:00 | 3.9706 | 4.628 | 4.628 | 4.628 | 4.628
2024-10-05 14:00 | 1.2003 | 1.4932 | 1.804 | 1.8455 | 1.8869 | 2024-08-05 14:00 | 3.9706 | 4.628 | 4.628 | 4.628 | 4.628
2024-10-05 15:00 | 0.99073 | 1.2324 | 1.489 | 1.5232 | 1.5574 | 2024-08-05 15:00 | 3.9706 | 4.628 | 4.628 | 4.628 | 4.628
2024-10-05 16:00 | 1.3908 | 1.7302 | 2.0904 | 2.1384 | 2.1864 | 2024-08-05 16:00 | 4.0391 | 4.708 | 4.708 | 4.708 | 4.708
2024-10-05 17:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-08-05 17:00 | 4.0239 | 4.6902 | 4.6902 | 4.6902 | 4.6902
2024-10-05 18:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-08-05 18:00 | 3.3151 | 3.8641 | 3.8641 | 3.8641 | 3.8641
2024-10-05 19:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-08-05 19:00 | 2.9417 | 3.4288 | 3.4288 | 3.4288 | 3.4288
2024-10-05 20:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2024-08-05 20:00 | 2.675 | 3.1179 | 3.1179 | 3.1179 | 3.1179
2024-10-05 21:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-08-05 21:00 | 2.3358 | 2.7226 | 2.7226 | 2.7226 | 2.7226
2024-10-05 22:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-08-05 22:00 | 2.172 | 2.5316 | 2.5316 | 2.5316 | 2.5316
2024-10-05 23:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-08-05 23:00 | 1.9624 | 2.2874 | 2.2874 | 2.2874 | 2.2874
2024-10-06 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-08-06 | 1.8176 | 2.1186 | 2.1186 | 2.1186 | 2.1186
2024-10-06 01:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-08-06 01:00 | 1.7757 | 2.0697 | 2.0697 | 2.0697 | 2.0697
2024-10-06 03:00 | 1.4289 | 1.7776 | 2.1476 | 2.197 | 2.2463 | 2024-08-06 02:00 | 1.81 | 2.1097 | 2.1097 | 2.1097 | 2.1097
2024-10-06 04:00 | 1.3718 | 1.7065 | 2.0617 | 2.1091 | 2.1565 | 2024-08-06 03:00 | 2.0158 | 2.3495 | 2.3495 | 2.3495 | 2.3495
2024-10-06 05:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2024-08-06 04:00 | 2.1453 | 2.5006 | 2.5006 | 2.5006 | 2.5006
2024-10-06 06:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2024-08-06 05:00 | 2.5721 | 2.998 | 2.998 | 2.998 | 2.998
2024-10-06 07:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-08-06 06:00 | 3.2618 | 3.8019 | 3.8019 | 3.8019 | 3.8019
2024-10-06 08:00 | 1.2765 | 1.588 | 1.9186 | 1.9626 | 2.0067 | 2024-08-06 07:00 | 3.7762 | 4.4015 | 4.4015 | 4.4015 | 4.4015
2024-10-06 09:00 | 0.724 | 0.90063 | 1.0881 | 1.1131 | 1.1381 | 2024-08-06 08:00 | 4.123 | 4.8057 | 4.8057 | 4.8057 | 4.8057
2024-10-06 10:00 | 0.80021 | 0.99544 | 1.2027 | 1.2303 | 1.2579 | 2024-08-06 09:00 | 4.0963 | 4.7746 | 4.7746 | 4.7746 | 4.7746
2024-10-06 11:00 | 0.7621 | 0.94804 | 1.1454 | 1.1717 | 1.198 | 2024-08-06 10:00 | 3.7267 | 4.3438 | 4.3438 | 4.3438 | 4.3438
2024-10-06 12:00 | 1.2765 | 1.588 | 1.9186 | 1.9626 | 2.0067 | 2024-08-06 11:00 | 3.4257 | 3.9929 | 3.9929 | 3.9929 | 3.9929
2024-10-06 13:00 | 1.3337 | 1.6591 | 2.0045 | 2.0505 | 2.0966 | 2024-08-06 12:00 | 3.4142 | 3.9796 | 3.9796 | 3.9796 | 3.9796
2024-10-06 14:00 | 1.3146 | 1.6354 | 1.9758 | 2.0212 | 2.0666 | 2024-08-06 13:00 | 3.2999 | 3.8463 | 3.8463 | 3.8463 | 3.8463
2024-10-06 15:00 | 1.3527 | 1.6828 | 2.0331 | 2.0798 | 2.1265 | 2024-08-06 14:00 | 3.3304 | 3.8819 | 3.8819 | 3.8819 | 3.8819
2024-10-06 16:00 | 1.2194 | 1.5169 | 1.8326 | 1.8748 | 1.9169 | 2024-08-06 15:00 | 3.3647 | 3.9218 | 3.9218 | 3.9218 | 3.9218
2024-10-06 17:00 | 0.68589 | 0.85323 | 1.0309 | 1.0545 | 1.0782 | 2024-08-06 16:00 | 3.8143 | 4.4459 | 4.4459 | 4.4459 | 4.4459
2024-10-06 18:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-08-06 17:00 | 3.7381 | 4.3571 | 4.3571 | 4.3571 | 4.3571
2024-10-06 19:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-08-06 18:00 | 3.3037 | 3.8508 | 3.8508 | 3.8508 | 3.8508
2024-10-06 20:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-08-06 19:00 | 2.7588 | 3.2156 | 3.2156 | 3.2156 | 3.2156
2024-10-06 21:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2024-08-06 20:00 | 2.7512 | 3.2068 | 3.2068 | 3.2068 | 3.2068
2024-10-06 22:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-08-06 21:00 | 2.233 | 2.6027 | 2.6027 | 2.6027 | 2.6027
2024-10-06 23:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-08-06 22:00 | 1.951 | 2.274 | 2.274 | 2.274 | 2.274
2024-10-07 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-08-06 23:00 | 1.8786 | 2.1897 | 2.1897 | 2.1897 | 2.1897
2024-10-07 01:00 | 1.4099 | 1.7539 | 2.119 | 2.1677 | 2.2164 | 2024-08-07 | 1.8176 | 2.1186 | 2.1186 | 2.1186 | 2.1186
2024-10-07 02:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-08-07 01:00 | 1.7605 | 2.052 | 2.052 | 2.052 | 2.052
2024-10-07 03:00 | 1.3718 | 1.7065 | 2.0617 | 2.1091 | 2.1565 | 2024-08-07 02:00 | 1.7414 | 2.0298 | 2.0298 | 2.0298 | 2.0298
2024-10-07 04:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-08-07 03:00 | 1.951 | 2.274 | 2.274 | 2.274 | 2.274
2024-10-07 05:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2024-08-07 04:00 | 2.2025 | 2.5672 | 2.5672 | 2.5672 | 2.5672
2024-10-07 06:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2024-08-07 05:00 | 2.534 | 2.9536 | 2.9536 | 2.9536 | 2.9536
2024-10-07 07:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2024-08-07 06:00 | 3.3723 | 3.9307 | 3.9307 | 3.9307 | 3.9307
2024-10-07 08:00 | 0.13337 | 0.16591 | 0.20045 | 0.20505 | 0.20966 | 2024-08-07 07:00 | 3.7038 | 4.3171 | 4.3171 | 4.3171 | 4.3171
2024-10-07 09:00 | 0.99073 | 1.2324 | 1.489 | 1.5232 | 1.5574 | 2024-08-07 08:00 | 4.0201 | 4.6858 | 4.6858 | 4.6858 | 4.6858
2024-10-07 10:00 | 0.68589 | 0.85323 | 1.0309 | 1.0545 | 1.0782 | 2024-08-07 09:00 | 4.0811 | 4.7568 | 4.7568 | 4.7568 | 4.7568
2024-10-07 11:00 | 0.62873 | 0.78213 | 0.94496 | 0.96667 | 0.98838 | 2024-08-07 10:00 | 3.7838 | 4.4104 | 4.4104 | 4.4104 | 4.4104
2024-10-07 12:00 | 0.55252 | 0.68733 | 0.83042 | 0.8495 | 0.86858 | 2024-08-07 11:00 | 3.5323 | 4.1173 | 4.1173 | 4.1173 | 4.1173
2024-10-07 13:00 | 0.53347 | 0.66362 | 0.80178 | 0.8202 | 0.83862 | 2024-08-07 12:00 | 3.5933 | 4.1883 | 4.1883 | 4.1883 | 4.1883
2024-10-07 14:00 | 0.724 | 0.90063 | 1.0881 | 1.1131 | 1.1381 | 2024-08-07 13:00 | 3.4485 | 4.0195 | 4.0195 | 4.0195 | 4.0195
2024-10-07 15:00 | 0.74305 | 0.92433 | 1.1168 | 1.1424 | 1.1681 | 2024-08-07 14:00 | 3.3075 | 3.8552 | 3.8552 | 3.8552 | 3.8552
2024-10-07 16:00 | 0.51442 | 0.63992 | 0.77315 | 0.79091 | 0.80867 | 2024-08-07 15:00 | 3.479 | 4.0551 | 4.0551 | 4.0551 | 4.0551
2024-10-07 17:00 | 1.3908 | 1.7302 | 2.0904 | 2.1384 | 2.1864 | 2024-08-07 16:00 | 3.761 | 4.3837 | 4.3837 | 4.3837 | 4.3837
2024-10-07 18:00 | 1.4099 | 1.7539 | 2.119 | 2.1677 | 2.2164 | 2024-08-07 17:00 | 3.8219 | 4.4548 | 4.4548 | 4.4548 | 4.4548
2024-10-07 19:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-08-07 18:00 | 3.5514 | 4.1395 | 4.1395 | 4.1395 | 4.1395
2024-10-07 20:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-08-07 19:00 | 3.1703 | 3.6953 | 3.6953 | 3.6953 | 3.6953
2024-10-07 21:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-08-07 20:00 | 2.8122 | 3.2778 | 3.2778 | 3.2778 | 3.2778
2024-10-07 22:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-08-07 21:00 | 2.534 | 2.9536 | 2.9536 | 2.9536 | 2.9536
2024-10-07 23:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-08-07 22:00 | 2.1377 | 2.4917 | 2.4917 | 2.4917 | 2.4917
2024-10-08 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-08-07 23:00 | 1.97 | 2.2962 | 2.2962 | 2.2962 | 2.2962
2024-10-08 01:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-08-08 | 1.8024 | 2.1008 | 2.1008 | 2.1008 | 2.1008
2024-10-08 02:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-08-08 01:00 | 1.7986 | 2.0964 | 2.0964 | 2.0964 | 2.0964
2024-10-08 03:00 | 1.4099 | 1.7539 | 2.119 | 2.1677 | 2.2164 | 2024-08-08 02:00 | 1.8595 | 2.1674 | 2.1674 | 2.1674 | 2.1674
2024-10-08 04:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-08-08 03:00 | 1.9129 | 2.2296 | 2.2296 | 2.2296 | 2.2296
2024-10-08 05:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2024-08-08 04:00 | 2.1987 | 2.5627 | 2.5627 | 2.5627 | 2.5627
2024-10-08 06:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2024-08-08 05:00 | 2.614 | 3.0469 | 3.0469 | 3.0469 | 3.0469
2024-10-08 07:00 | 2.172 | 2.7019 | 3.2644 | 3.3394 | 3.4144 | 2024-08-08 06:00 | 3.5895 | 4.1839 | 4.1839 | 4.1839 | 4.1839
2024-10-08 08:00 | 2.2863 | 2.8441 | 3.4362 | 3.5152 | 3.5941 | 2024-08-08 07:00 | 3.9134 | 4.5614 | 4.5614 | 4.5614 | 4.5614
2024-10-08 09:00 | 2.4578 | 3.0574 | 3.6939 | 3.7788 | 3.8637 | 2024-08-08 08:00 | 4.0887 | 4.7657 | 4.7657 | 4.7657 | 4.7657
2024-10-08 10:00 | 2.2291 | 2.773 | 3.3503 | 3.4273 | 3.5043 | 2024-08-08 09:00 | 4.0544 | 4.7257 | 4.7257 | 4.7257 | 4.7257
2024-10-08 11:00 | 2.1529 | 2.6782 | 3.2358 | 3.3101 | 3.3845 | 2024-08-08 10:00 | 3.8029 | 4.4326 | 4.4326 | 4.4326 | 4.4326
2024-10-08 12:00 | 2.0767 | 2.5834 | 3.1212 | 3.1929 | 3.2646 | 2024-08-08 11:00 | 3.6619 | 4.2683 | 4.2683 | 4.2683 | 4.2683
2024-10-08 13:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-08-08 12:00 | 3.4409 | 4.0107 | 4.0107 | 4.0107 | 4.0107
2024-10-08 14:00 | 1.3908 | 1.7302 | 2.0904 | 2.1384 | 2.1864 | 2024-08-08 13:00 | 3.5095 | 4.0906 | 4.0906 | 4.0906 | 4.0906
2024-10-08 15:00 | 1.2956 | 1.6117 | 1.9472 | 1.9919 | 2.0367 | 2024-08-08 14:00 | 3.4866 | 4.064 | 4.064 | 4.064 | 4.064
2024-10-08 16:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2024-08-08 15:00 | 3.5552 | 4.1439 | 4.1439 | 4.1439 | 4.1439
2024-10-08 17:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-08-08 16:00 | 3.8143 | 4.4459 | 4.4459 | 4.4459 | 4.4459
2024-10-08 18:00 | 1.7528 | 2.1805 | 2.6344 | 2.695 | 2.7555 | 2024-08-08 17:00 | 4.0391 | 4.708 | 4.708 | 4.708 | 4.708
2024-10-08 19:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2024-08-08 18:00 | 3.3533 | 3.9085 | 3.9085 | 3.9085 | 3.9085
2024-10-08 20:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2024-08-08 19:00 | 2.9189 | 3.4022 | 3.4022 | 3.4022 | 3.4022
2024-10-08 21:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2024-08-08 20:00 | 2.7969 | 3.2601 | 3.2601 | 3.2601 | 3.2601
2024-10-08 22:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2024-08-08 21:00 | 2.2939 | 2.6738 | 2.6738 | 2.6738 | 2.6738
2024-10-08 23:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2024-08-08 22:00 | 2.0081 | 2.3407 | 2.3407 | 2.3407 | 2.3407
2024-10-09 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-08-08 23:00 | 2.031 | 2.3673 | 2.3673 | 2.3673 | 2.3673
2024-10-09 01:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2024-08-09 | 1.8824 | 2.1941 | 2.1941 | 2.1941 | 2.1941
2024-10-09 02:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-08-09 01:00 | 1.81 | 2.1097 | 2.1097 | 2.1097 | 2.1097
2024-10-09 03:00 | 1.4289 | 1.7776 | 2.1476 | 2.197 | 2.2463 | 2024-08-09 02:00 | 1.7833 | 2.0786 | 2.0786 | 2.0786 | 2.0786
2024-10-09 04:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-08-09 03:00 | 2.0653 | 2.4073 | 2.4073 | 2.4073 | 2.4073
2024-10-09 05:00 | 1.6957 | 2.1094 | 2.5485 | 2.6071 | 2.6656 | 2024-08-09 04:00 | 2.3435 | 2.7315 | 2.7315 | 2.7315 | 2.7315
2024-10-09 06:00 | 1.7719 | 2.2042 | 2.6631 | 2.7242 | 2.7854 | 2024-08-09 05:00 | 2.473 | 2.8825 | 2.8825 | 2.8825 | 2.8825
2024-10-09 07:00 | 1.8481 | 2.299 | 2.7776 | 2.8414 | 2.9052 | 2024-08-09 06:00 | 3.4333 | 4.0018 | 4.0018 | 4.0018 | 4.0018
2024-10-09 08:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-08-09 07:00 | 3.9096 | 4.557 | 4.557 | 4.557 | 4.557
2024-10-09 09:00 | 1.3146 | 1.6354 | 1.9758 | 2.0212 | 2.0666 | 2024-08-09 08:00 | 4.3478 | 5.0677 | 5.0677 | 5.0677 | 5.0677
2024-10-09 10:00 | 1.8862 | 2.3464 | 2.8349 | 2.9 | 2.9651 | 2024-08-09 09:00 | 4.3097 | 5.0233 | 5.0233 | 5.0233 | 5.0233
2024-10-09 11:00 | 1.8672 | 2.3227 | 2.8062 | 2.8707 | 2.9352 | 2024-08-09 10:00 | 4.0734 | 4.7479 | 4.7479 | 4.7479 | 4.7479
2024-10-09 12:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-08-09 11:00 | 3.5895 | 4.1839 | 4.1839 | 4.1839 | 4.1839
2024-10-09 13:00 | 1.6957 | 2.1094 | 2.5485 | 2.6071 | 2.6656 | 2024-08-09 12:00 | 3.4866 | 4.064 | 4.064 | 4.064 | 4.064
2024-10-09 14:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2024-08-09 13:00 | 3.3151 | 3.8641 | 3.8641 | 3.8641 | 3.8641
2024-10-09 15:00 | 1.3718 | 1.7065 | 2.0617 | 2.1091 | 2.1565 | 2024-08-09 14:00 | 3.3418 | 3.8952 | 3.8952 | 3.8952 | 3.8952
2024-10-09 16:00 | 0.66684 | 0.82953 | 1.0022 | 1.0253 | 1.0483 | 2024-08-09 15:00 | 3.5285 | 4.1128 | 4.1128 | 4.1128 | 4.1128
2024-10-09 17:00 | 0.81926 | 1.0191 | 1.2313 | 1.2596 | 1.2879 | 2024-08-09 16:00 | 3.7686 | 4.3926 | 4.3926 | 4.3926 | 4.3926
2024-10-09 18:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2024-08-09 17:00 | 3.8029 | 4.4326 | 4.4326 | 4.4326 | 4.4326
2024-10-09 19:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2024-08-09 18:00 | 3.4904 | 4.0684 | 4.0684 | 4.0684 | 4.0684
2024-10-09 20:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2024-08-09 19:00 | 3.2351 | 3.7708 | 3.7708 | 3.7708 | 3.7708
2024-10-09 21:00 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2024-08-09 20:00 | 2.8731 | 3.3489 | 3.3489 | 3.3489 | 3.3489
2024-10-09 22:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2024-08-09 21:00 | 2.6178 | 3.0513 | 3.0513 | 3.0513 | 3.0513
2024-10-09 23:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2024-08-09 22:00 | 2.0996 | 2.4473 | 2.4473 | 2.4473 | 2.4473
2024-10-10 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-08-09 23:00 | 2.0653 | 2.4073 | 2.4073 | 2.4073 | 2.4073
2024-10-10 01:00 | 1.4289 | 1.7776 | 2.1476 | 2.197 | 2.2463 | 2024-08-10 | 2.0081 | 2.3407 | 2.3407 | 2.3407 | 2.3407
2024-10-10 02:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-08-10 01:00 | 1.8633 | 2.1719 | 2.1719 | 2.1719 | 2.1719
2024-10-10 03:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-08-10 02:00 | 1.8367 | 2.1408 | 2.1408 | 2.1408 | 2.1408
2024-10-10 04:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-08-10 03:00 | 2.0691 | 2.4117 | 2.4117 | 2.4117 | 2.4117
2024-10-10 05:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2024-08-10 04:00 | 2.2901 | 2.6693 | 2.6693 | 2.6693 | 2.6693
2024-10-10 06:00 | 1.6957 | 2.1094 | 2.5485 | 2.6071 | 2.6656 | 2024-08-10 05:00 | 2.3549 | 2.7448 | 2.7448 | 2.7448 | 2.7448
2024-10-10 07:00 | 1.8672 | 2.3227 | 2.8062 | 2.8707 | 2.9352 | 2024-08-10 06:00 | 2.5569 | 2.9802 | 2.9802 | 2.9802 | 2.9802
2024-10-10 08:00 | 1.2575 | 1.5643 | 1.8899 | 1.9333 | 1.9768 | 2024-08-10 07:00 | 3.2885 | 3.833 | 3.833 | 3.833 | 3.833
2024-10-10 09:00 | 0.66684 | 0.82953 | 1.0022 | 1.0253 | 1.0483 | 2024-08-10 08:00 | 3.4561 | 4.0284 | 4.0284 | 4.0284 | 4.0284
2024-10-10 10:00 | 0.28579 | 0.35551 | 0.42953 | 0.43939 | 0.44926 | 2024-08-10 09:00 | 3.4104 | 3.9751 | 3.9751 | 3.9751 | 3.9751
2024-10-10 11:00 | 0.13337 | 0.16591 | 0.20045 | 0.20505 | 0.20966 | 2024-08-10 10:00 | 3.1589 | 3.682 | 3.682 | 3.682 | 3.682
2024-10-10 12:00 | 0.019053 | 0.023701 | 0.028635 | 0.029293 | 0.029951 | 2024-08-10 11:00 | 3.117 | 3.6331 | 3.6331 | 3.6331 | 3.6331
2024-10-10 13:00 | 0.97168 | 1.2087 | 1.4604 | 1.4939 | 1.5275 | 2024-08-10 12:00 | 2.8807 | 3.3578 | 3.3578 | 3.3578 | 3.3578
2024-10-10 14:00 | 0.11432 | 0.14221 | 0.17181 | 0.17576 | 0.17971 | 2024-08-10 13:00 | 2.9646 | 3.4555 | 3.4555 | 3.4555 | 3.4555
2024-10-10 15:00 | 1.1622 | 1.4458 | 1.7467 | 1.7869 | 1.827 | 2024-08-10 14:00 | 3.0637 | 3.571 | 3.571 | 3.571 | 3.571
2024-10-10 16:00 | 1.2194 | 1.5169 | 1.8326 | 1.8748 | 1.9169 | 2024-08-10 15:00 | 3.2123 | 3.7442 | 3.7442 | 3.7442 | 3.7442
2024-10-10 17:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2024-08-10 16:00 | 3.2085 | 3.7397 | 3.7397 | 3.7397 | 3.7397
2024-10-10 18:00 | 1.7528 | 2.1805 | 2.6344 | 2.695 | 2.7555 | 2024-08-10 17:00 | 3.1018 | 3.6154 | 3.6154 | 3.6154 | 3.6154
2024-10-10 19:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2024-08-10 18:00 | 2.8503 | 3.3222 | 3.3222 | 3.3222 | 3.3222
2024-10-10 20:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2024-08-10 19:00 | 2.5226 | 2.9403 | 2.9403 | 2.9403 | 2.9403
2024-10-10 21:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2024-08-10 20:00 | 2.3168 | 2.7004 | 2.7004 | 2.7004 | 2.7004
2024-10-10 22:00 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2024-08-10 21:00 | 2.1301 | 2.4828 | 2.4828 | 2.4828 | 2.4828
2024-10-10 23:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2024-08-10 22:00 | 2.0272 | 2.3629 | 2.3629 | 2.3629 | 2.3629
2024-10-11 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-08-10 23:00 | 2.0158 | 2.3495 | 2.3495 | 2.3495 | 2.3495
2024-10-11 01:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-08-11 | 1.9548 | 2.2785 | 2.2785 | 2.2785 | 2.2785
2024-10-11 02:00 | 1.4289 | 1.7776 | 2.1476 | 2.197 | 2.2463 | 2024-08-11 01:00 | 1.7948 | 2.0919 | 2.0919 | 2.0919 | 2.0919
2024-10-11 03:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-08-11 02:00 | 1.7909 | 2.0875 | 2.0875 | 2.0875 | 2.0875
2024-10-11 04:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-08-11 03:00 | 1.9434 | 2.2652 | 2.2652 | 2.2652 | 2.2652
2024-10-11 05:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2024-08-11 04:00 | 2.1072 | 2.4561 | 2.4561 | 2.4561 | 2.4561
2024-10-11 06:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2024-08-11 05:00 | 2.2291 | 2.5983 | 2.5983 | 2.5983 | 2.5983
2024-10-11 07:00 | 1.81 | 2.2516 | 2.7203 | 2.7828 | 2.8453 | 2024-08-11 06:00 | 2.4082 | 2.807 | 2.807 | 2.807 | 2.807
2024-10-11 08:00 | 2.0005 | 2.4886 | 3.0067 | 3.0758 | 3.1448 | 2024-08-11 07:00 | 2.5035 | 2.9181 | 2.9181 | 2.9181 | 2.9181
2024-10-11 09:00 | 1.7147 | 2.1331 | 2.5772 | 2.6364 | 2.6956 | 2024-08-11 08:00 | 2.755 | 3.2112 | 3.2112 | 3.2112 | 3.2112
2024-10-11 10:00 | 0.87642 | 1.0902 | 1.3172 | 1.3475 | 1.3777 | 2024-08-11 09:00 | 2.6712 | 3.1135 | 3.1135 | 3.1135 | 3.1135
2024-10-11 11:00 | 0.724 | 0.90063 | 1.0881 | 1.1131 | 1.1381 | 2024-08-11 10:00 | 2.7321 | 3.1845 | 3.1845 | 3.1845 | 3.1845
2024-10-11 12:00 | 0.89547 | 1.1139 | 1.3458 | 1.3768 | 1.4077 | 2024-08-11 11:00 | 2.6293 | 3.0646 | 3.0646 | 3.0646 | 3.0646
2024-10-11 13:00 | 0.362 | 0.45032 | 0.54407 | 0.55657 | 0.56907 | 2024-08-11 12:00 | 2.7779 | 3.2378 | 3.2378 | 3.2378 | 3.2378
2024-10-11 14:00 | 0.62873 | 0.78213 | 0.94496 | 0.96667 | 0.98838 | 2024-08-11 13:00 | 3.3647 | 3.9218 | 3.9218 | 3.9218 | 3.9218
2024-10-11 15:00 | 1.829 | 2.2753 | 2.749 | 2.8121 | 2.8753 | 2024-08-11 14:00 | 2.7359 | 3.189 | 3.189 | 3.189 | 3.189
2024-10-11 16:00 | 1.8672 | 2.3227 | 2.8062 | 2.8707 | 2.9352 | 2024-08-11 15:00 | 2.9036 | 3.3844 | 3.3844 | 3.3844 | 3.3844
2024-10-11 17:00 | 1.7147 | 2.1331 | 2.5772 | 2.6364 | 2.6956 | 2024-08-11 16:00 | 3.0027 | 3.4999 | 3.4999 | 3.4999 | 3.4999
2024-10-11 18:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2024-08-11 17:00 | 3.1322 | 3.6509 | 3.6509 | 3.6509 | 3.6509
2024-10-11 19:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2024-08-11 18:00 | 2.9074 | 3.3889 | 3.3889 | 3.3889 | 3.3889
2024-10-11 20:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2024-08-11 19:00 | 2.5607 | 2.9847 | 2.9847 | 2.9847 | 2.9847
2024-10-11 21:00 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2024-08-11 20:00 | 2.2901 | 2.6693 | 2.6693 | 2.6693 | 2.6693
2024-10-11 22:00 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2024-08-11 21:00 | 2.2444 | 2.616 | 2.616 | 2.616 | 2.616
2024-10-11 23:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2024-08-11 22:00 | 2.1453 | 2.5006 | 2.5006 | 2.5006 | 2.5006
2024-10-12 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-08-11 23:00 | 1.8405 | 2.1452 | 2.1452 | 2.1452 | 2.1452
2024-10-12 01:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-08-12 | 1.7643 | 2.0564 | 2.0564 | 2.0564 | 2.0564
2024-10-12 02:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-08-12 01:00 | 1.7719 | 2.0653 | 2.0653 | 2.0653 | 2.0653
2024-10-12 03:00 | 1.4289 | 1.7776 | 2.1476 | 2.197 | 2.2463 | 2024-08-12 02:00 | 1.8367 | 2.1408 | 2.1408 | 2.1408 | 2.1408
2024-10-12 04:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-08-12 03:00 | 1.9396 | 2.2607 | 2.2607 | 2.2607 | 2.2607
2024-10-12 05:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-08-12 04:00 | 2.1872 | 2.5494 | 2.5494 | 2.5494 | 2.5494
2024-10-12 06:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-08-12 05:00 | 2.4997 | 2.9136 | 2.9136 | 2.9136 | 2.9136
2024-10-12 07:00 | 1.4289 | 1.7776 | 2.1476 | 2.197 | 2.2463 | 2024-08-12 06:00 | 3.0065 | 3.5043 | 3.5043 | 3.5043 | 3.5043
2024-10-12 08:00 | 1.2003 | 1.4932 | 1.804 | 1.8455 | 1.8869 | 2024-08-12 07:00 | 3.4371 | 4.0062 | 4.0062 | 4.0062 | 4.0062
2024-10-12 09:00 | 1.0098 | 1.2561 | 1.5177 | 1.5525 | 1.5874 | 2024-08-12 08:00 | 3.6086 | 4.2061 | 4.2061 | 4.2061 | 4.2061
2024-10-12 10:00 | 0.43821 | 0.54512 | 0.65861 | 0.67374 | 0.68887 | 2024-08-12 09:00 | 3.7953 | 4.4237 | 4.4237 | 4.4237 | 4.4237
2024-10-12 11:00 | 0.20958 | 0.26071 | 0.31499 | 0.32222 | 0.32946 | 2024-08-12 10:00 | 3.7076 | 4.3216 | 4.3216 | 4.3216 | 4.3216
2024-10-12 12:00 | 0.13337 | 0.16591 | 0.20045 | 0.20505 | 0.20966 | 2024-08-12 11:00 | 3.9058 | 4.5525 | 4.5525 | 4.5525 | 4.5525
2024-10-12 13:00 | 0.4001 | 0.49772 | 0.60134 | 0.61515 | 0.62897 | 2024-08-12 12:00 | 3.8296 | 4.4637 | 4.4637 | 4.4637 | 4.4637
2024-10-12 14:00 | 0.47631 | 0.59252 | 0.71588 | 0.73232 | 0.74877 | 2024-08-12 13:00 | 2.9074 | 3.3889 | 3.3889 | 3.3889 | 3.3889
2024-10-12 15:00 | 1.1432 | 1.4221 | 1.7181 | 1.7576 | 1.7971 | 2024-08-12 14:00 | 3.3266 | 3.8774 | 3.8774 | 3.8774 | 3.8774
2024-10-12 16:00 | 1.0479 | 1.3035 | 1.5749 | 1.6111 | 1.6473 | 2024-08-12 15:00 | 3.5285 | 4.1128 | 4.1128 | 4.1128 | 4.1128
2024-10-12 17:00 | 0.53347 | 0.66362 | 0.80178 | 0.8202 | 0.83862 | 2024-08-12 16:00 | 3.4561 | 4.0284 | 4.0284 | 4.0284 | 4.0284
2024-10-12 18:00 | 1.4099 | 1.7539 | 2.119 | 2.1677 | 2.2164 | 2024-08-12 17:00 | 3.399 | 3.9618 | 3.9618 | 3.9618 | 3.9618
2024-10-12 19:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-08-12 18:00 | 3.2504 | 3.7886 | 3.7886 | 3.7886 | 3.7886
2024-10-12 20:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-08-12 19:00 | 2.8083 | 3.2734 | 3.2734 | 3.2734 | 3.2734
2024-10-12 21:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2024-08-12 20:00 | 2.5873 | 3.0158 | 3.0158 | 3.0158 | 3.0158
2024-10-12 22:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2024-08-12 21:00 | 2.4197 | 2.8203 | 2.8203 | 2.8203 | 2.8203
2024-10-12 23:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-08-12 22:00 | 2.1034 | 2.4517 | 2.4517 | 2.4517 | 2.4517
2024-10-13 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-08-12 23:00 | 1.9434 | 2.2652 | 2.2652 | 2.2652 | 2.2652
2024-10-13 01:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-08-13 | 1.7871 | 2.0831 | 2.0831 | 2.0831 | 2.0831
2024-10-13 02:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-08-13 01:00 | 1.7681 | 2.0609 | 2.0609 | 2.0609 | 2.0609
2024-10-13 03:00 | 1.3908 | 1.7302 | 2.0904 | 2.1384 | 2.1864 | 2024-08-13 02:00 | 1.7909 | 2.0875 | 2.0875 | 2.0875 | 2.0875
2024-10-13 04:00 | 1.4289 | 1.7776 | 2.1476 | 2.197 | 2.2463 | 2024-08-13 03:00 | 1.9129 | 2.2296 | 2.2296 | 2.2296 | 2.2296
2024-10-13 05:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2024-08-13 04:00 | 2.1758 | 2.5361 | 2.5361 | 2.5361 | 2.5361
2024-10-13 06:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2024-08-13 05:00 | 2.4197 | 2.8203 | 2.8203 | 2.8203 | 2.8203
2024-10-13 07:00 | 1.3718 | 1.7065 | 2.0617 | 2.1091 | 2.1565 | 2024-08-13 06:00 | 3.0065 | 3.5043 | 3.5043 | 3.5043 | 3.5043
2024-10-13 08:00 | 1.3146 | 1.6354 | 1.9758 | 2.0212 | 2.0666 | 2024-08-13 07:00 | 3.4371 | 4.0062 | 4.0062 | 4.0062 | 4.0062
2024-10-13 09:00 | 0.724 | 0.90063 | 1.0881 | 1.1131 | 1.1381 | 2024-08-13 08:00 | 3.6086 | 4.2061 | 4.2061 | 4.2061 | 4.2061
2024-10-13 10:00 | 0.74305 | 0.92433 | 1.1168 | 1.1424 | 1.1681 | 2024-08-13 09:00 | 3.7953 | 4.4237 | 4.4237 | 4.4237 | 4.4237
2024-10-13 11:00 | 0.70494 | 0.87693 | 1.0595 | 1.0838 | 1.1082 | 2024-08-13 10:00 | 3.7076 | 4.3216 | 4.3216 | 4.3216 | 4.3216
2024-10-13 12:00 | 0.87642 | 1.0902 | 1.3172 | 1.3475 | 1.3777 | 2024-08-13 11:00 | 3.9058 | 4.5525 | 4.5525 | 4.5525 | 4.5525
2024-10-13 13:00 | 1.0098 | 1.2561 | 1.5177 | 1.5525 | 1.5874 | 2024-08-13 12:00 | 3.8296 | 4.4637 | 4.4637 | 4.4637 | 4.4637
2024-10-13 14:00 | 1.1622 | 1.4458 | 1.7467 | 1.7869 | 1.827 | 2024-08-13 13:00 | 3.3304 | 3.8819 | 3.8819 | 3.8819 | 3.8819
2024-10-13 15:00 | 1.1241 | 1.3984 | 1.6895 | 1.7283 | 1.7671 | 2024-08-13 14:00 | 3.4066 | 3.9707 | 3.9707 | 3.9707 | 3.9707
2024-10-13 16:00 | 0.362 | 0.45032 | 0.54407 | 0.55657 | 0.56907 | 2024-08-13 15:00 | 3.54 | 4.1261 | 4.1261 | 4.1261 | 4.1261
2024-10-13 17:00 | 1.3337 | 1.6591 | 2.0045 | 2.0505 | 2.0966 | 2024-08-13 16:00 | 3.5171 | 4.0995 | 4.0995 | 4.0995 | 4.0995
2024-10-13 18:00 | 1.4099 | 1.7539 | 2.119 | 2.1677 | 2.2164 | 2024-08-13 17:00 | 3.54 | 4.1261 | 4.1261 | 4.1261 | 4.1261
2024-10-13 19:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-08-13 18:00 | 3.2999 | 3.8463 | 3.8463 | 3.8463 | 3.8463
2024-10-13 20:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-08-13 19:00 | 2.8655 | 3.34 | 3.34 | 3.34 | 3.34
2024-10-13 21:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2024-08-13 20:00 | 2.675 | 3.1179 | 3.1179 | 3.1179 | 3.1179
2024-10-13 22:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2024-08-13 21:00 | 2.3549 | 2.7448 | 2.7448 | 2.7448 | 2.7448
2024-10-13 23:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2024-08-13 22:00 | 1.9472 | 2.2696 | 2.2696 | 2.2696 | 2.2696
2024-10-14 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-08-13 23:00 | 1.9319 | 2.2518 | 2.2518 | 2.2518 | 2.2518
2024-10-14 01:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-08-14 | 1.8862 | 2.1985 | 2.1985 | 2.1985 | 2.1985
2024-10-14 02:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-08-14 01:00 | 1.7719 | 2.0653 | 2.0653 | 2.0653 | 2.0653
2024-10-14 03:00 | 1.3718 | 1.7065 | 2.0617 | 2.1091 | 2.1565 | 2024-08-14 02:00 | 1.7566 | 2.0475 | 2.0475 | 2.0475 | 2.0475
2024-10-14 04:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-08-14 03:00 | 1.8748 | 2.1852 | 2.1852 | 2.1852 | 2.1852
2024-10-14 05:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2024-08-14 04:00 | 2.2215 | 2.5894 | 2.5894 | 2.5894 | 2.5894
2024-10-14 06:00 | 1.829 | 2.2753 | 2.749 | 2.8121 | 2.8753 | 2024-08-14 05:00 | 2.4121 | 2.8115 | 2.8115 | 2.8115 | 2.8115
2024-10-14 07:00 | 1.81 | 2.2516 | 2.7203 | 2.7828 | 2.8453 | 2024-08-14 06:00 | 2.8807 | 3.3578 | 3.3578 | 3.3578 | 3.3578
2024-10-14 08:00 | 2.191 | 2.7256 | 3.293 | 3.3687 | 3.4444 | 2024-08-14 07:00 | 3.8372 | 4.4726 | 4.4726 | 4.4726 | 4.4726
2024-10-14 09:00 | 1.7909 | 2.2279 | 2.6917 | 2.7535 | 2.8154 | 2024-08-14 08:00 | 3.8143 | 4.4459 | 4.4459 | 4.4459 | 4.4459
2024-10-14 10:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2024-08-14 09:00 | 3.8677 | 4.5081 | 4.5081 | 4.5081 | 4.5081
2024-10-14 11:00 | 2.1339 | 2.6545 | 3.2071 | 3.2808 | 3.3545 | 2024-08-14 10:00 | 3.8677 | 4.5081 | 4.5081 | 4.5081 | 4.5081
2024-10-14 12:00 | 2.1148 | 2.6308 | 3.1785 | 3.2515 | 3.3245 | 2024-08-14 11:00 | 3.9134 | 4.5614 | 4.5614 | 4.5614 | 4.5614
2024-10-14 13:00 | 1.7909 | 2.2279 | 2.6917 | 2.7535 | 2.8154 | 2024-08-14 12:00 | 4.001 | 4.6636 | 4.6636 | 4.6636 | 4.6636
2024-10-14 14:00 | 2.2673 | 2.8204 | 3.4076 | 3.4859 | 3.5642 | 2024-08-14 13:00 | 3.902 | 4.5481 | 4.5481 | 4.5481 | 4.5481
2024-10-14 15:00 | 2.4006 | 2.9863 | 3.608 | 3.6909 | 3.7738 | 2024-08-14 14:00 | 3.498 | 4.0773 | 4.0773 | 4.0773 | 4.0773
2024-10-14 16:00 | 2.2673 | 2.8204 | 3.4076 | 3.4859 | 3.5642 | 2024-08-14 15:00 | 3.5743 | 4.1661 | 4.1661 | 4.1661 | 4.1661
2024-10-14 17:00 | 2.0767 | 2.5834 | 3.1212 | 3.1929 | 3.2646 | 2024-08-14 16:00 | 3.5476 | 4.135 | 4.135 | 4.135 | 4.135
2024-10-14 18:00 | 1.8672 | 2.3227 | 2.8062 | 2.8707 | 2.9352 | 2024-08-14 17:00 | 3.7572 | 4.3793 | 4.3793 | 4.3793 | 4.3793
2024-10-14 19:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2024-08-14 18:00 | 3.2656 | 3.8064 | 3.8064 | 3.8064 | 3.8064
2024-10-14 20:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2024-08-14 19:00 | 2.9531 | 3.4422 | 3.4422 | 3.4422 | 3.4422
2024-10-14 21:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2024-08-14 20:00 | 2.8769 | 3.3533 | 3.3533 | 3.3533 | 3.3533
2024-10-14 22:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2024-08-14 21:00 | 2.6407 | 3.078 | 3.078 | 3.078 | 3.078
2024-10-14 23:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2024-08-14 22:00 | 2.0996 | 2.4473 | 2.4473 | 2.4473 | 2.4473
2024-10-15 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-08-14 23:00 | 2.0272 | 2.3629 | 2.3629 | 2.3629 | 2.3629
2024-10-15 01:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-08-15 | 1.81 | 2.1097 | 2.1097 | 2.1097 | 2.1097
2024-10-15 02:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-08-15 01:00 | 1.7986 | 2.0964 | 2.0964 | 2.0964 | 2.0964
2024-10-15 03:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-08-15 02:00 | 1.7681 | 2.0609 | 2.0609 | 2.0609 | 2.0609
2024-10-15 04:00 | 1.4289 | 1.7776 | 2.1476 | 2.197 | 2.2463 | 2024-08-15 03:00 | 1.8824 | 2.1941 | 2.1941 | 2.1941 | 2.1941
2024-10-15 05:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2024-08-15 04:00 | 2.191 | 2.5539 | 2.5539 | 2.5539 | 2.5539
2024-10-15 06:00 | 1.9053 | 2.3701 | 2.8635 | 2.9293 | 2.9951 | 2024-08-15 05:00 | 2.393 | 2.7893 | 2.7893 | 2.7893 | 2.7893
2024-10-15 07:00 | 2.2863 | 2.8441 | 3.4362 | 3.5152 | 3.5941 | 2024-08-15 06:00 | 3.0522 | 3.5576 | 3.5576 | 3.5576 | 3.5576
2024-10-15 08:00 | 2.3054 | 2.8678 | 3.4648 | 3.5445 | 3.6241 | 2024-08-15 07:00 | 3.4638 | 4.0373 | 4.0373 | 4.0373 | 4.0373
2024-10-15 09:00 | 2.2101 | 2.7493 | 3.3217 | 3.398 | 3.4743 | 2024-08-15 08:00 | 3.8105 | 4.4415 | 4.4415 | 4.4415 | 4.4415
2024-10-15 10:00 | 2.0196 | 2.5123 | 3.0353 | 3.1051 | 3.1748 | 2024-08-15 09:00 | 3.8334 | 4.4681 | 4.4681 | 4.4681 | 4.4681
2024-10-15 11:00 | 2.0386 | 2.536 | 3.064 | 3.1344 | 3.2047 | 2024-08-15 10:00 | 3.277 | 3.8197 | 3.8197 | 3.8197 | 3.8197
2024-10-15 12:00 | 2.2101 | 2.7493 | 3.3217 | 3.398 | 3.4743 | 2024-08-15 11:00 | 3.178 | 3.7042 | 3.7042 | 3.7042 | 3.7042
2024-10-15 13:00 | 2.1339 | 2.6545 | 3.2071 | 3.2808 | 3.3545 | 2024-08-15 12:00 | 3.4028 | 3.9662 | 3.9662 | 3.9662 | 3.9662
2024-10-15 14:00 | 1.9624 | 2.4412 | 2.9494 | 3.0172 | 3.0849 | 2024-08-15 13:00 | 3.5628 | 4.1528 | 4.1528 | 4.1528 | 4.1528
2024-10-15 15:00 | 2.0577 | 2.5597 | 3.0926 | 3.1636 | 3.2347 | 2024-08-15 14:00 | 3.6543 | 4.2594 | 4.2594 | 4.2594 | 4.2594
2024-10-15 16:00 | 2.172 | 2.7019 | 3.2644 | 3.3394 | 3.4144 | 2024-08-15 15:00 | 3.4447 | 4.0151 | 4.0151 | 4.0151 | 4.0151
2024-10-15 17:00 | 2.0005 | 2.4886 | 3.0067 | 3.0758 | 3.1448 | 2024-08-15 16:00 | 3.5476 | 4.135 | 4.135 | 4.135 | 4.135
2024-10-15 18:00 | 1.9053 | 2.3701 | 2.8635 | 2.9293 | 2.9951 | 2024-08-15 17:00 | 3.6276 | 4.2283 | 4.2283 | 4.2283 | 4.2283
2024-10-15 19:00 | 1.7528 | 2.1805 | 2.6344 | 2.695 | 2.7555 | 2024-08-15 18:00 | 3.2809 | 3.8241 | 3.8241 | 3.8241 | 3.8241
2024-10-15 20:00 | 1.7719 | 2.2042 | 2.6631 | 2.7242 | 2.7854 | 2024-08-15 19:00 | 2.7893 | 3.2512 | 3.2512 | 3.2512 | 3.2512
2024-10-15 21:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2024-08-15 20:00 | 2.6712 | 3.1135 | 3.1135 | 3.1135 | 3.1135
2024-10-15 22:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2024-08-15 21:00 | 2.4044 | 2.8026 | 2.8026 | 2.8026 | 2.8026
2024-10-15 23:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-08-15 22:00 | 2.1148 | 2.465 | 2.465 | 2.465 | 2.465
2024-10-16 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-08-15 23:00 | 1.9396 | 2.2607 | 2.2607 | 2.2607 | 2.2607
2024-10-16 01:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-08-16 | 1.8252 | 2.1275 | 2.1275 | 2.1275 | 2.1275
2024-10-16 02:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-08-16 01:00 | 1.8176 | 2.1186 | 2.1186 | 2.1186 | 2.1186
2024-10-16 03:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-08-16 02:00 | 1.8176 | 2.1186 | 2.1186 | 2.1186 | 2.1186
2024-10-16 04:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-08-16 03:00 | 1.8824 | 2.1941 | 2.1941 | 2.1941 | 2.1941
2024-10-16 05:00 | 1.7528 | 2.1805 | 2.6344 | 2.695 | 2.7555 | 2024-08-16 04:00 | 2.1682 | 2.5272 | 2.5272 | 2.5272 | 2.5272
2024-10-16 06:00 | 1.9434 | 2.4175 | 2.9208 | 2.9879 | 3.055 | 2024-08-16 05:00 | 2.3739 | 2.767 | 2.767 | 2.767 | 2.767
2024-10-16 07:00 | 2.0196 | 2.5123 | 3.0353 | 3.1051 | 3.1748 | 2024-08-16 06:00 | 3.056 | 3.5621 | 3.5621 | 3.5621 | 3.5621
2024-10-16 08:00 | 2.0958 | 2.6071 | 3.1499 | 3.2222 | 3.2946 | 2024-08-16 07:00 | 3.3533 | 3.9085 | 3.9085 | 3.9085 | 3.9085
2024-10-16 09:00 | 1.1813 | 1.4695 | 1.7754 | 1.8162 | 1.857 | 2024-08-16 08:00 | 3.9858 | 4.6458 | 4.6458 | 4.6458 | 4.6458
2024-10-16 10:00 | 0.59063 | 0.73473 | 0.88769 | 0.90808 | 0.92848 | 2024-08-16 09:00 | 4.062 | 4.7346 | 4.7346 | 4.7346 | 4.7346
2024-10-16 11:00 | 0.59063 | 0.73473 | 0.88769 | 0.90808 | 0.92848 | 2024-08-16 10:00 | 3.9401 | 4.5925 | 4.5925 | 4.5925 | 4.5925
2024-10-16 12:00 | 0.362 | 0.45032 | 0.54407 | 0.55657 | 0.56907 | 2024-08-16 11:00 | 3.7 | 4.3127 | 4.3127 | 4.3127 | 4.3127
2024-10-16 13:00 | 0.30484 | 0.37921 | 0.45816 | 0.46869 | 0.47921 | 2024-08-16 12:00 | 3.5057 | 4.0862 | 4.0862 | 4.0862 | 4.0862
2024-10-16 14:00 | 0.28579 | 0.35551 | 0.42953 | 0.43939 | 0.44926 | 2024-08-16 13:00 | 3.5095 | 4.0906 | 4.0906 | 4.0906 | 4.0906
2024-10-16 15:00 | 0.43821 | 0.54512 | 0.65861 | 0.67374 | 0.68887 | 2024-08-16 14:00 | 3.4371 | 4.0062 | 4.0062 | 4.0062 | 4.0062
2024-10-16 16:00 | 2.0196 | 2.5123 | 3.0353 | 3.1051 | 3.1748 | 2024-08-16 15:00 | 3.3799 | 3.9396 | 3.9396 | 3.9396 | 3.9396
2024-10-16 17:00 | 2.0767 | 2.5834 | 3.1212 | 3.1929 | 3.2646 | 2024-08-16 16:00 | 3.6771 | 4.286 | 4.286 | 4.286 | 4.286
2024-10-16 18:00 | 1.8672 | 2.3227 | 2.8062 | 2.8707 | 2.9352 | 2024-08-16 17:00 | 3.7915 | 4.4193 | 4.4193 | 4.4193 | 4.4193
2024-10-16 19:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2024-08-16 18:00 | 3.6428 | 4.2461 | 4.2461 | 4.2461 | 4.2461
2024-10-16 20:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2024-08-16 19:00 | 3.2237 | 3.7575 | 3.7575 | 3.7575 | 3.7575
2024-10-16 21:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2024-08-16 20:00 | 2.8541 | 3.3267 | 3.3267 | 3.3267 | 3.3267
2024-10-16 22:00 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2024-08-16 21:00 | 2.7969 | 3.2601 | 3.2601 | 3.2601 | 3.2601
2024-10-16 23:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2024-08-16 22:00 | 2.0729 | 2.4162 | 2.4162 | 2.4162 | 2.4162
2024-10-17 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-08-16 23:00 | 1.9853 | 2.314 | 2.314 | 2.314 | 2.314
2024-10-17 01:00 | 1.3908 | 1.7302 | 2.0904 | 2.1384 | 2.1864 | 2024-08-17 | 1.7071 | 1.9898 | 1.9898 | 1.9898 | 1.9898
2024-10-17 02:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-08-17 01:00 | 1.7224 | 2.0076 | 2.0076 | 2.0076 | 2.0076
2024-10-17 03:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-08-17 02:00 | 1.7833 | 2.0786 | 2.0786 | 2.0786 | 2.0786
2024-10-17 04:00 | 1.4289 | 1.7776 | 2.1476 | 2.197 | 2.2463 | 2024-08-17 03:00 | 1.8786 | 2.1897 | 2.1897 | 2.1897 | 2.1897
2024-10-17 05:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2024-08-17 04:00 | 2.0081 | 2.3407 | 2.3407 | 2.3407 | 2.3407
2024-10-17 06:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2024-08-17 05:00 | 2.2291 | 2.5983 | 2.5983 | 2.5983 | 2.5983
2024-10-17 07:00 | 2.0196 | 2.5123 | 3.0353 | 3.1051 | 3.1748 | 2024-08-17 06:00 | 2.4921 | 2.9047 | 2.9047 | 2.9047 | 2.9047
2024-10-17 08:00 | 1.1241 | 1.3984 | 1.6895 | 1.7283 | 1.7671 | 2024-08-17 07:00 | 2.6674 | 3.109 | 3.109 | 3.109 | 3.109
2024-10-17 09:00 | 0.66684 | 0.82953 | 1.0022 | 1.0253 | 1.0483 | 2024-08-17 08:00 | 2.6712 | 3.1135 | 3.1135 | 3.1135 | 3.1135
2024-10-17 10:00 | 0.53347 | 0.66362 | 0.80178 | 0.8202 | 0.83862 | 2024-08-17 09:00 | 2.3968 | 2.7937 | 2.7937 | 2.7937 | 2.7937
2024-10-17 11:00 | 0.47631 | 0.59252 | 0.71588 | 0.73232 | 0.74877 | 2024-08-17 10:00 | 2.9874 | 3.4821 | 3.4821 | 3.4821 | 3.4821
2024-10-17 12:00 | 1.7719 | 2.2042 | 2.6631 | 2.7242 | 2.7854 | 2024-08-17 11:00 | 3.1551 | 3.6776 | 3.6776 | 3.6776 | 3.6776
2024-10-17 13:00 | 1.81 | 2.2516 | 2.7203 | 2.7828 | 2.8453 | 2024-08-17 12:00 | 3.1818 | 3.7086 | 3.7086 | 3.7086 | 3.7086
2024-10-17 14:00 | 1.2765 | 1.588 | 1.9186 | 1.9626 | 2.0067 | 2024-08-17 13:00 | 3.1894 | 3.7175 | 3.7175 | 3.7175 | 3.7175
2024-10-17 15:00 | 1.9053 | 2.3701 | 2.8635 | 2.9293 | 2.9951 | 2024-08-17 14:00 | 3.178 | 3.7042 | 3.7042 | 3.7042 | 3.7042
2024-10-17 16:00 | 1.6957 | 2.1094 | 2.5485 | 2.6071 | 2.6656 | 2024-08-17 15:00 | 3.0103 | 3.5088 | 3.5088 | 3.5088 | 3.5088
2024-10-17 17:00 | 1.9815 | 2.4649 | 2.9781 | 3.0465 | 3.1149 | 2024-08-17 16:00 | 3.1437 | 3.6642 | 3.6642 | 3.6642 | 3.6642
2024-10-17 18:00 | 1.8672 | 2.3227 | 2.8062 | 2.8707 | 2.9352 | 2024-08-17 17:00 | 2.9989 | 3.4955 | 3.4955 | 3.4955 | 3.4955
2024-10-17 19:00 | 1.7528 | 2.1805 | 2.6344 | 2.695 | 2.7555 | 2024-08-17 18:00 | 2.8007 | 3.2645 | 3.2645 | 3.2645 | 3.2645
2024-10-17 20:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2024-08-17 19:00 | 2.5607 | 2.9847 | 2.9847 | 2.9847 | 2.9847
2024-10-17 21:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2024-08-17 20:00 | 2.3511 | 2.7404 | 2.7404 | 2.7404 | 2.7404
2024-10-17 22:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2024-08-17 21:00 | 2.2673 | 2.6427 | 2.6427 | 2.6427 | 2.6427
2024-10-17 23:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-08-17 22:00 | 1.8976 | 2.2119 | 2.2119 | 2.2119 | 2.2119
2024-10-18 | 1.4289 | 1.7776 | 2.1476 | 2.197 | 2.2463 | 2024-08-17 23:00 | 1.9205 | 2.2385 | 2.2385 | 2.2385 | 2.2385
2024-10-18 01:00 | 1.3908 | 1.7302 | 2.0904 | 2.1384 | 2.1864 | 2024-08-18 | 1.749 | 2.0386 | 2.0386 | 2.0386 | 2.0386
2024-10-18 02:00 | 1.3908 | 1.7302 | 2.0904 | 2.1384 | 2.1864 | 2024-08-18 01:00 | 1.6995 | 1.9809 | 1.9809 | 1.9809 | 1.9809
2024-10-18 03:00 | 1.4289 | 1.7776 | 2.1476 | 2.197 | 2.2463 | 2024-08-18 02:00 | 1.6995 | 1.9809 | 1.9809 | 1.9809 | 1.9809
2024-10-18 04:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-08-18 03:00 | 1.8405 | 2.1452 | 2.1452 | 2.1452 | 2.1452
2024-10-18 05:00 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2024-08-18 04:00 | 2.0272 | 2.3629 | 2.3629 | 2.3629 | 2.3629
2024-10-18 06:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2024-08-18 05:00 | 2.2063 | 2.5716 | 2.5716 | 2.5716 | 2.5716
2024-10-18 07:00 | 2.0005 | 2.4886 | 3.0067 | 3.0758 | 3.1448 | 2024-08-18 06:00 | 2.4425 | 2.847 | 2.847 | 2.847 | 2.847
2024-10-18 08:00 | 2.3625 | 2.9389 | 3.5508 | 3.6323 | 3.7139 | 2024-08-18 07:00 | 2.3816 | 2.7759 | 2.7759 | 2.7759 | 2.7759
2024-10-18 09:00 | 2.2482 | 2.7967 | 3.3789 | 3.4566 | 3.5342 | 2024-08-18 08:00 | 2.5111 | 2.9269 | 2.9269 | 2.9269 | 2.9269
2024-10-18 10:00 | 2.4006 | 2.9863 | 3.608 | 3.6909 | 3.7738 | 2024-08-18 09:00 | 2.9989 | 3.4955 | 3.4955 | 3.4955 | 3.4955
2024-10-18 11:00 | 2.2863 | 2.8441 | 3.4362 | 3.5152 | 3.5941 | 2024-08-18 10:00 | 2.9951 | 3.491 | 3.491 | 3.491 | 3.491
2024-10-18 12:00 | 2.2291 | 2.773 | 3.3503 | 3.4273 | 3.5043 | 2024-08-18 11:00 | 2.9798 | 3.4732 | 3.4732 | 3.4732 | 3.4732
2024-10-18 13:00 | 2.0767 | 2.5834 | 3.1212 | 3.1929 | 3.2646 | 2024-08-18 12:00 | 2.9341 | 3.4199 | 3.4199 | 3.4199 | 3.4199
2024-10-18 14:00 | 2.1529 | 2.6782 | 3.2358 | 3.3101 | 3.3845 | 2024-08-18 13:00 | 3.0865 | 3.5976 | 3.5976 | 3.5976 | 3.5976
2024-10-18 15:00 | 2.0386 | 2.536 | 3.064 | 3.1344 | 3.2047 | 2024-08-18 14:00 | 2.9836 | 3.4777 | 3.4777 | 3.4777 | 3.4777
2024-10-18 16:00 | 2.0005 | 2.4886 | 3.0067 | 3.0758 | 3.1448 | 2024-08-18 15:00 | 3.0446 | 3.5487 | 3.5487 | 3.5487 | 3.5487
2024-10-18 17:00 | 1.9815 | 2.4649 | 2.9781 | 3.0465 | 3.1149 | 2024-08-18 16:00 | 3.056 | 3.5621 | 3.5621 | 3.5621 | 3.5621
2024-10-18 18:00 | 1.7147 | 2.1331 | 2.5772 | 2.6364 | 2.6956 | 2024-08-18 17:00 | 3.037 | 3.5399 | 3.5399 | 3.5399 | 3.5399
2024-10-18 19:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2024-08-18 18:00 | 2.816 | 3.2823 | 3.2823 | 3.2823 | 3.2823
2024-10-18 20:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2024-08-18 19:00 | 2.5416 | 2.9625 | 2.9625 | 2.9625 | 2.9625
2024-10-18 21:00 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2024-08-18 20:00 | 2.313 | 2.696 | 2.696 | 2.696 | 2.696
2024-10-18 22:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2024-08-18 21:00 | 2.313 | 2.696 | 2.696 | 2.696 | 2.696
2024-10-18 23:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-08-18 22:00 | 1.8748 | 2.1852 | 2.1852 | 2.1852 | 2.1852
2024-10-19 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2024-08-18 23:00 | 1.9053 | 2.2207 | 2.2207 | 2.2207 | 2.2207
2024-10-19 01:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-08-19 | 1.6842 | 1.9631 | 1.9631 | 1.9631 | 1.9631
2024-10-19 02:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-08-19 01:00 | 1.6766 | 1.9543 | 1.9543 | 1.9543 | 1.9543
2024-10-19 03:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-08-19 02:00 | 1.7414 | 2.0298 | 2.0298 | 2.0298 | 2.0298
2024-10-19 04:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-08-19 03:00 | 1.829 | 2.1319 | 2.1319 | 2.1319 | 2.1319
2024-10-19 05:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-08-19 04:00 | 2.1339 | 2.4872 | 2.4872 | 2.4872 | 2.4872
2024-10-19 06:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2024-08-19 05:00 | 2.313 | 2.696 | 2.696 | 2.696 | 2.696
2024-10-19 07:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-08-19 06:00 | 3.0789 | 3.5887 | 3.5887 | 3.5887 | 3.5887
2024-10-19 08:00 | 0.85737 | 1.0665 | 1.2886 | 1.3182 | 1.3478 | 2024-08-19 07:00 | 3.7381 | 4.3571 | 4.3571 | 4.3571 | 4.3571
2024-10-19 09:00 | 0.68589 | 0.85323 | 1.0309 | 1.0545 | 1.0782 | 2024-08-19 08:00 | 3.8181 | 4.4504 | 4.4504 | 4.4504 | 4.4504
2024-10-19 10:00 | 0.89547 | 1.1139 | 1.3458 | 1.3768 | 1.4077 | 2024-08-19 09:00 | 3.7838 | 4.4104 | 4.4104 | 4.4104 | 4.4104
2024-10-19 11:00 | 0.89547 | 1.1139 | 1.3458 | 1.3768 | 1.4077 | 2024-08-19 10:00 | 3.5857 | 4.1794 | 4.1794 | 4.1794 | 4.1794
2024-10-19 12:00 | 0.64779 | 0.80583 | 0.97359 | 0.99596 | 1.0183 | 2024-08-19 11:00 | 3.5857 | 4.1794 | 4.1794 | 4.1794 | 4.1794
2024-10-19 13:00 | 0.81926 | 1.0191 | 1.2313 | 1.2596 | 1.2879 | 2024-08-19 12:00 | 3.5857 | 4.1794 | 4.1794 | 4.1794 | 4.1794
2024-10-19 14:00 | 1.3718 | 1.7065 | 2.0617 | 2.1091 | 2.1565 | 2024-08-19 13:00 | 3.5857 | 4.1794 | 4.1794 | 4.1794 | 4.1794
2024-10-19 15:00 | 1.2384 | 1.5406 | 1.8613 | 1.904 | 1.9468 | 2024-08-19 14:00 | 3.5857 | 4.1794 | 4.1794 | 4.1794 | 4.1794
2024-10-19 16:00 | 0.87642 | 1.0902 | 1.3172 | 1.3475 | 1.3777 | 2024-08-19 15:00 | 3.2427 | 3.7797 | 3.7797 | 3.7797 | 3.7797
2024-10-19 17:00 | 0.49537 | 0.61622 | 0.74451 | 0.76162 | 0.77872 | 2024-08-19 16:00 | 3.4295 | 3.9973 | 3.9973 | 3.9973 | 3.9973
2024-10-19 18:00 | 1.3908 | 1.7302 | 2.0904 | 2.1384 | 2.1864 | 2024-08-19 17:00 | 3.6619 | 4.2683 | 4.2683 | 4.2683 | 4.2683
2024-10-19 19:00 | 1.4289 | 1.7776 | 2.1476 | 2.197 | 2.2463 | 2024-08-19 18:00 | 3.2847 | 3.8286 | 3.8286 | 3.8286 | 3.8286
2024-10-19 20:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-08-19 19:00 | 2.7702 | 3.229 | 3.229 | 3.229 | 3.229
2024-10-19 21:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2024-08-19 20:00 | 2.7245 | 3.1757 | 3.1757 | 3.1757 | 3.1757
2024-10-19 22:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-08-19 21:00 | 2.172 | 2.5316 | 2.5316 | 2.5316 | 2.5316
2024-10-19 23:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-08-19 22:00 | 2.0805 | 2.4251 | 2.4251 | 2.4251 | 2.4251
2024-10-20 | 1.4099 | 1.7539 | 2.119 | 2.1677 | 2.2164 | 2024-08-19 23:00 | 1.8938 | 2.2074 | 2.2074 | 2.2074 | 2.2074
2024-10-20 01:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-08-20 | 1.7033 | 1.9853 | 1.9853 | 1.9853 | 1.9853
2024-10-20 02:00 | 1.4099 | 1.7539 | 2.119 | 2.1677 | 2.2164 | 2024-08-20 01:00 | 1.7109 | 1.9942 | 1.9942 | 1.9942 | 1.9942
2024-10-20 03:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-08-20 02:00 | 1.6919 | 1.972 | 1.972 | 1.972 | 1.972
2024-10-20 04:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-08-20 03:00 | 1.8633 | 2.1719 | 2.1719 | 2.1719 | 2.1719
2024-10-20 05:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-08-20 04:00 | 2.1529 | 2.5094 | 2.5094 | 2.5094 | 2.5094
2024-10-20 06:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2024-08-20 05:00 | 2.313 | 2.696 | 2.696 | 2.696 | 2.696
2024-10-20 07:00 | 1.1622 | 1.4458 | 1.7467 | 1.7869 | 1.827 | 2024-08-20 06:00 | 2.9913 | 3.4866 | 3.4866 | 3.4866 | 3.4866
2024-10-20 08:00 | 1.2765 | 1.588 | 1.9186 | 1.9626 | 2.0067 | 2024-08-20 07:00 | 3.4295 | 3.9973 | 3.9973 | 3.9973 | 3.9973
2024-10-20 09:00 | 0.7621 | 0.94804 | 1.1454 | 1.1717 | 1.198 | 2024-08-20 08:00 | 3.8753 | 4.517 | 4.517 | 4.517 | 4.517
2024-10-20 10:00 | 0.74305 | 0.92433 | 1.1168 | 1.1424 | 1.1681 | 2024-08-20 09:00 | 3.8524 | 4.4903 | 4.4903 | 4.4903 | 4.4903
2024-10-20 11:00 | 0.70494 | 0.87693 | 1.0595 | 1.0838 | 1.1082 | 2024-08-20 10:00 | 3.399 | 3.9618 | 3.9618 | 3.9618 | 3.9618
2024-10-20 12:00 | 0.89547 | 1.1139 | 1.3458 | 1.3768 | 1.4077 | 2024-08-20 11:00 | 3.6619 | 4.2683 | 4.2683 | 4.2683 | 4.2683
2024-10-20 13:00 | 1.086 | 1.351 | 1.6322 | 1.6697 | 1.7072 | 2024-08-20 12:00 | 3.5628 | 4.1528 | 4.1528 | 4.1528 | 4.1528
2024-10-20 14:00 | 1.2384 | 1.5406 | 1.8613 | 1.904 | 1.9468 | 2024-08-20 13:00 | 3.3799 | 3.9396 | 3.9396 | 3.9396 | 3.9396
2024-10-20 15:00 | 1.2575 | 1.5643 | 1.8899 | 1.9333 | 1.9768 | 2024-08-20 14:00 | 3.4409 | 4.0107 | 4.0107 | 4.0107 | 4.0107
2024-10-20 16:00 | 0.45726 | 0.56882 | 0.68724 | 0.70303 | 0.71882 | 2024-08-20 15:00 | 3.5362 | 4.1217 | 4.1217 | 4.1217 | 4.1217
2024-10-20 17:00 | 0.41916 | 0.52142 | 0.62997 | 0.64445 | 0.65892 | 2024-08-20 16:00 | 3.4447 | 4.0151 | 4.0151 | 4.0151 | 4.0151
2024-10-20 18:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-08-20 17:00 | 3.4523 | 4.024 | 4.024 | 4.024 | 4.024
2024-10-20 19:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-08-20 18:00 | 3.2427 | 3.7797 | 3.7797 | 3.7797 | 3.7797
2024-10-20 20:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-08-20 19:00 | 2.6978 | 3.1446 | 3.1446 | 3.1446 | 3.1446
2024-10-20 21:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2024-08-20 20:00 | 2.4616 | 2.8692 | 2.8692 | 2.8692 | 2.8692
2024-10-20 22:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2024-08-20 21:00 | 2.3015 | 2.6827 | 2.6827 | 2.6827 | 2.6827
2024-10-20 23:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-08-20 22:00 | 2.0272 | 2.3629 | 2.3629 | 2.3629 | 2.3629
2024-10-21 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-08-20 23:00 | 1.9167 | 2.2341 | 2.2341 | 2.2341 | 2.2341
2024-10-21 01:00 | 1.3908 | 1.7302 | 2.0904 | 2.1384 | 2.1864 | 2024-08-21 | 1.6842 | 1.9631 | 1.9631 | 1.9631 | 1.9631
2024-10-21 02:00 | 1.3908 | 1.7302 | 2.0904 | 2.1384 | 2.1864 | 2024-08-21 01:00 | 1.6957 | 1.9765 | 1.9765 | 1.9765 | 1.9765
2024-10-21 03:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-08-21 02:00 | 1.6804 | 1.9587 | 1.9587 | 1.9587 | 1.9587
2024-10-21 04:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-08-21 03:00 | 1.9243 | 2.243 | 2.243 | 2.243 | 2.243
2024-10-21 05:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2024-08-21 04:00 | 2.1072 | 2.4561 | 2.4561 | 2.4561 | 2.4561
2024-10-21 06:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2024-08-21 05:00 | 2.2596 | 2.6338 | 2.6338 | 2.6338 | 2.6338
2024-10-21 07:00 | 1.7528 | 2.1805 | 2.6344 | 2.695 | 2.7555 | 2024-08-21 06:00 | 2.8617 | 3.3356 | 3.3356 | 3.3356 | 3.3356
2024-10-21 08:00 | 1.0479 | 1.3035 | 1.5749 | 1.6111 | 1.6473 | 2024-08-21 07:00 | 3.1056 | 3.6198 | 3.6198 | 3.6198 | 3.6198
2024-10-21 09:00 | 0.83831 | 1.0428 | 1.2599 | 1.2889 | 1.3178 | 2024-08-21 08:00 | 3.3228 | 3.873 | 3.873 | 3.873 | 3.873
2024-10-21 10:00 | 0.55252 | 0.68733 | 0.83042 | 0.8495 | 0.86858 | 2024-08-21 09:00 | 3.2809 | 3.8241 | 3.8241 | 3.8241 | 3.8241
2024-10-21 11:00 | 0.51442 | 0.63992 | 0.77315 | 0.79091 | 0.80867 | 2024-08-21 10:00 | 3.2237 | 3.7575 | 3.7575 | 3.7575 | 3.7575
2024-10-21 12:00 | 0.57158 | 0.71103 | 0.85905 | 0.87879 | 0.89853 | 2024-08-21 11:00 | 3.1742 | 3.6998 | 3.6998 | 3.6998 | 3.6998
2024-10-21 13:00 | 0.53347 | 0.66362 | 0.80178 | 0.8202 | 0.83862 | 2024-08-21 12:00 | 3.4561 | 4.0284 | 4.0284 | 4.0284 | 4.0284
2024-10-21 14:00 | 0.68589 | 0.85323 | 1.0309 | 1.0545 | 1.0782 | 2024-08-21 13:00 | 3.3609 | 3.9174 | 3.9174 | 3.9174 | 3.9174
2024-10-21 15:00 | 0.7621 | 0.94804 | 1.1454 | 1.1717 | 1.198 | 2024-08-21 14:00 | 3.3914 | 3.9529 | 3.9529 | 3.9529 | 3.9529
2024-10-21 16:00 | 0.78115 | 0.97174 | 1.174 | 1.201 | 1.228 | 2024-08-21 15:00 | 3.2961 | 3.8419 | 3.8419 | 3.8419 | 3.8419
2024-10-21 17:00 | 0.87642 | 1.0902 | 1.3172 | 1.3475 | 1.3777 | 2024-08-21 16:00 | 3.5323 | 4.1173 | 4.1173 | 4.1173 | 4.1173
2024-10-21 18:00 | 1.7909 | 2.2279 | 2.6917 | 2.7535 | 2.8154 | 2024-08-21 17:00 | 3.4104 | 3.9751 | 3.9751 | 3.9751 | 3.9751
2024-10-21 19:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2024-08-21 18:00 | 3.2732 | 3.8152 | 3.8152 | 3.8152 | 3.8152
2024-10-21 20:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2024-08-21 19:00 | 2.8388 | 3.3089 | 3.3089 | 3.3089 | 3.3089
2024-10-21 21:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2024-08-21 20:00 | 2.4768 | 2.887 | 2.887 | 2.887 | 2.887
2024-10-21 22:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-08-21 21:00 | 2.2901 | 2.6693 | 2.6693 | 2.6693 | 2.6693
2024-10-21 23:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2024-08-21 22:00 | 2.0462 | 2.3851 | 2.3851 | 2.3851 | 2.3851
2024-10-22 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-08-21 23:00 | 1.9167 | 2.2341 | 2.2341 | 2.2341 | 2.2341
2024-10-22 01:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2024-08-22 | 1.7605 | 2.052 | 2.052 | 2.052 | 2.052
2024-10-22 02:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-08-22 01:00 | 1.7681 | 2.0609 | 2.0609 | 2.0609 | 2.0609
2024-10-22 03:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-08-22 02:00 | 1.73 | 2.0164 | 2.0164 | 2.0164 | 2.0164
2024-10-22 04:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-08-22 03:00 | 1.8862 | 2.1985 | 2.1985 | 2.1985 | 2.1985
2024-10-22 05:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-08-22 04:00 | 2.1225 | 2.4739 | 2.4739 | 2.4739 | 2.4739
2024-10-22 06:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2024-08-22 05:00 | 2.2977 | 2.6782 | 2.6782 | 2.6782 | 2.6782
2024-10-22 07:00 | 2.0767 | 2.5834 | 3.1212 | 3.1929 | 3.2646 | 2024-08-22 06:00 | 3.0255 | 3.5265 | 3.5265 | 3.5265 | 3.5265
2024-10-22 08:00 | 2.1148 | 2.6308 | 3.1785 | 3.2515 | 3.3245 | 2024-08-22 07:00 | 3.2351 | 3.7708 | 3.7708 | 3.7708 | 3.7708
2024-10-22 09:00 | 1.9815 | 2.4649 | 2.9781 | 3.0465 | 3.1149 | 2024-08-22 08:00 | 3.5552 | 4.1439 | 4.1439 | 4.1439 | 4.1439
2024-10-22 10:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2024-08-22 09:00 | 3.4942 | 4.0728 | 4.0728 | 4.0728 | 4.0728
2024-10-22 11:00 | 1.81 | 2.2516 | 2.7203 | 2.7828 | 2.8453 | 2024-08-22 10:00 | 3.6086 | 4.2061 | 4.2061 | 4.2061 | 4.2061
2024-10-22 12:00 | 1.2956 | 1.6117 | 1.9472 | 1.9919 | 2.0367 | 2024-08-22 11:00 | 3.4333 | 4.0018 | 4.0018 | 4.0018 | 4.0018
2024-10-22 13:00 | 1.7909 | 2.2279 | 2.6917 | 2.7535 | 2.8154 | 2024-08-22 12:00 | 3.5743 | 4.1661 | 4.1661 | 4.1661 | 4.1661
2024-10-22 14:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-08-22 13:00 | 3.6695 | 4.2772 | 4.2772 | 4.2772 | 4.2772
2024-10-22 15:00 | 2.2482 | 2.7967 | 3.3789 | 3.4566 | 3.5342 | 2024-08-22 14:00 | 3.4409 | 4.0107 | 4.0107 | 4.0107 | 4.0107
2024-10-22 16:00 | 2.3054 | 2.8678 | 3.4648 | 3.5445 | 3.6241 | 2024-08-22 15:00 | 3.7381 | 4.3571 | 4.3571 | 4.3571 | 4.3571
2024-10-22 17:00 | 2.1339 | 2.6545 | 3.2071 | 3.2808 | 3.3545 | 2024-08-22 16:00 | 3.3571 | 3.913 | 3.913 | 3.913 | 3.913
2024-10-22 18:00 | 2.1529 | 2.6782 | 3.2358 | 3.3101 | 3.3845 | 2024-08-22 17:00 | 3.4714 | 4.0462 | 4.0462 | 4.0462 | 4.0462
2024-10-22 19:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2024-08-22 18:00 | 3.3609 | 3.9174 | 3.9174 | 3.9174 | 3.9174
2024-10-22 20:00 | 1.6957 | 2.1094 | 2.5485 | 2.6071 | 2.6656 | 2024-08-22 19:00 | 2.7283 | 3.1801 | 3.1801 | 3.1801 | 3.1801
2024-10-22 21:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2024-08-22 20:00 | 2.8045 | 3.2689 | 3.2689 | 3.2689 | 3.2689
2024-10-22 22:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2024-08-22 21:00 | 2.3892 | 2.7848 | 2.7848 | 2.7848 | 2.7848
2024-10-22 23:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-08-22 22:00 | 1.9091 | 2.2252 | 2.2252 | 2.2252 | 2.2252
2024-10-23 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2024-08-22 23:00 | 1.9205 | 2.2385 | 2.2385 | 2.2385 | 2.2385
2024-10-23 01:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-08-23 | 1.8176 | 2.1186 | 2.1186 | 2.1186 | 2.1186
2024-10-23 02:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-08-23 01:00 | 1.7566 | 2.0475 | 2.0475 | 2.0475 | 2.0475
2024-10-23 03:00 | 1.4099 | 1.7539 | 2.119 | 2.1677 | 2.2164 | 2024-08-23 02:00 | 1.7757 | 2.0697 | 2.0697 | 2.0697 | 2.0697
2024-10-23 04:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-08-23 03:00 | 1.9586 | 2.2829 | 2.2829 | 2.2829 | 2.2829
2024-10-23 05:00 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2024-08-23 04:00 | 2.2863 | 2.6649 | 2.6649 | 2.6649 | 2.6649
2024-10-23 06:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2024-08-23 05:00 | 2.5683 | 2.9936 | 2.9936 | 2.9936 | 2.9936
2024-10-23 07:00 | 1.8862 | 2.3464 | 2.8349 | 2.9 | 2.9651 | 2024-08-23 06:00 | 3.1932 | 3.722 | 3.722 | 3.722 | 3.722
2024-10-23 08:00 | 2.0767 | 2.5834 | 3.1212 | 3.1929 | 3.2646 | 2024-08-23 07:00 | 3.5209 | 4.1039 | 4.1039 | 4.1039 | 4.1039
2024-10-23 09:00 | 2.2101 | 2.7493 | 3.3217 | 3.398 | 3.4743 | 2024-08-23 08:00 | 3.86 | 4.4992 | 4.4992 | 4.4992 | 4.4992
2024-10-23 10:00 | 2.2101 | 2.7493 | 3.3217 | 3.398 | 3.4743 | 2024-08-23 09:00 | 4.043 | 4.7124 | 4.7124 | 4.7124 | 4.7124
2024-10-23 11:00 | 1.9815 | 2.4649 | 2.9781 | 3.0465 | 3.1149 | 2024-08-23 10:00 | 3.6352 | 4.2372 | 4.2372 | 4.2372 | 4.2372
2024-10-23 12:00 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2024-08-23 11:00 | 3.5171 | 4.0995 | 4.0995 | 4.0995 | 4.0995
2024-10-23 13:00 | 2.3054 | 2.8678 | 3.4648 | 3.5445 | 3.6241 | 2024-08-23 12:00 | 3.0713 | 3.5798 | 3.5798 | 3.5798 | 3.5798
2024-10-23 14:00 | 2.191 | 2.7256 | 3.293 | 3.3687 | 3.4444 | 2024-08-23 13:00 | 3.3685 | 3.9263 | 3.9263 | 3.9263 | 3.9263
2024-10-23 15:00 | 2.191 | 2.7256 | 3.293 | 3.3687 | 3.4444 | 2024-08-23 14:00 | 3.6543 | 4.2594 | 4.2594 | 4.2594 | 4.2594
2024-10-23 16:00 | 2.2101 | 2.7493 | 3.3217 | 3.398 | 3.4743 | 2024-08-23 15:00 | 3.3228 | 3.873 | 3.873 | 3.873 | 3.873
2024-10-23 17:00 | 2.2291 | 2.773 | 3.3503 | 3.4273 | 3.5043 | 2024-08-23 16:00 | 3.7381 | 4.3571 | 4.3571 | 4.3571 | 4.3571
2024-10-23 18:00 | 1.8481 | 2.299 | 2.7776 | 2.8414 | 2.9052 | 2024-08-23 17:00 | 3.6695 | 4.2772 | 4.2772 | 4.2772 | 4.2772
2024-10-23 19:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2024-08-23 18:00 | 3.639 | 4.2416 | 4.2416 | 4.2416 | 4.2416
2024-10-23 20:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2024-08-23 19:00 | 3.1589 | 3.682 | 3.682 | 3.682 | 3.682
2024-10-23 21:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2024-08-23 20:00 | 2.8007 | 3.2645 | 3.2645 | 3.2645 | 3.2645
2024-10-23 22:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-08-23 21:00 | 2.3168 | 2.7004 | 2.7004 | 2.7004 | 2.7004
2024-10-23 23:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-08-23 22:00 | 2.0767 | 2.4206 | 2.4206 | 2.4206 | 2.4206
2024-10-24 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-08-23 23:00 | 2.0843 | 2.4295 | 2.4295 | 2.4295 | 2.4295
2024-10-24 01:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-08-24 | 1.871 | 2.1808 | 2.1808 | 2.1808 | 2.1808
2024-10-24 02:00 | 1.4289 | 1.7776 | 2.1476 | 2.197 | 2.2463 | 2024-08-24 01:00 | 1.7414 | 2.0298 | 2.0298 | 2.0298 | 2.0298
2024-10-24 03:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-08-24 02:00 | 1.7948 | 2.0919 | 2.0919 | 2.0919 | 2.0919
2024-10-24 04:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-08-24 03:00 | 1.9014 | 2.2163 | 2.2163 | 2.2163 | 2.2163
2024-10-24 05:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2024-08-24 04:00 | 1.9929 | 2.3229 | 2.3229 | 2.3229 | 2.3229
2024-10-24 06:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2024-08-24 05:00 | 2.191 | 2.5539 | 2.5539 | 2.5539 | 2.5539
2024-10-24 07:00 | 1.4289 | 1.7776 | 2.1476 | 2.197 | 2.2463 | 2024-08-24 06:00 | 2.4463 | 2.8514 | 2.8514 | 2.8514 | 2.8514
2024-10-24 08:00 | 0.89547 | 1.1139 | 1.3458 | 1.3768 | 1.4077 | 2024-08-24 07:00 | 2.5683 | 2.9936 | 2.9936 | 2.9936 | 2.9936
2024-10-24 09:00 | 1.086 | 1.351 | 1.6322 | 1.6697 | 1.7072 | 2024-08-24 08:00 | 2.5073 | 2.9225 | 2.9225 | 2.9225 | 2.9225
2024-10-24 10:00 | 1.2765 | 1.588 | 1.9186 | 1.9626 | 2.0067 | 2024-08-24 09:00 | 2.4616 | 2.8692 | 2.8692 | 2.8692 | 2.8692
2024-10-24 11:00 | 0.80021 | 0.99544 | 1.2027 | 1.2303 | 1.2579 | 2024-08-24 10:00 | 2.3968 | 2.7937 | 2.7937 | 2.7937 | 2.7937
2024-10-24 12:00 | 0.57158 | 0.71103 | 0.85905 | 0.87879 | 0.89853 | 2024-08-24 11:00 | 2.5035 | 2.9181 | 2.9181 | 2.9181 | 2.9181
2024-10-24 13:00 | 0.57158 | 0.71103 | 0.85905 | 0.87879 | 0.89853 | 2024-08-24 12:00 | 2.6369 | 3.0735 | 3.0735 | 3.0735 | 3.0735
2024-10-24 14:00 | 0.57158 | 0.71103 | 0.85905 | 0.87879 | 0.89853 | 2024-08-24 13:00 | 3.0027 | 3.4999 | 3.4999 | 3.4999 | 3.4999
2024-10-24 15:00 | 0.57158 | 0.71103 | 0.85905 | 0.87879 | 0.89853 | 2024-08-24 14:00 | 2.7741 | 3.2334 | 3.2334 | 3.2334 | 3.2334
2024-10-24 16:00 | 0.7621 | 0.94804 | 1.1454 | 1.1717 | 1.198 | 2024-08-24 15:00 | 2.8045 | 3.2689 | 3.2689 | 3.2689 | 3.2689
2024-10-24 17:00 | 1.3527 | 1.6828 | 2.0331 | 2.0798 | 2.1265 | 2024-08-24 16:00 | 3.0789 | 3.5887 | 3.5887 | 3.5887 | 3.5887
2024-10-24 18:00 | 1.8862 | 2.3464 | 2.8349 | 2.9 | 2.9651 | 2024-08-24 17:00 | 3.1284 | 3.6465 | 3.6465 | 3.6465 | 3.6465
2024-10-24 19:00 | 1.7528 | 2.1805 | 2.6344 | 2.695 | 2.7555 | 2024-08-24 18:00 | 2.816 | 3.2823 | 3.2823 | 3.2823 | 3.2823
2024-10-24 20:00 | 1.6957 | 2.1094 | 2.5485 | 2.6071 | 2.6656 | 2024-08-24 19:00 | 2.4121 | 2.8115 | 2.8115 | 2.8115 | 2.8115
2024-10-24 21:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2024-08-24 20:00 | 2.0996 | 2.4473 | 2.4473 | 2.4473 | 2.4473
2024-10-24 22:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2024-08-24 21:00 | 2.1186 | 2.4695 | 2.4695 | 2.4695 | 2.4695
2024-10-24 23:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-08-24 22:00 | 1.9967 | 2.3273 | 2.3273 | 2.3273 | 2.3273
2024-10-25 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-08-24 23:00 | 1.9586 | 2.2829 | 2.2829 | 2.2829 | 2.2829
2024-10-25 01:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-08-25 | 1.8138 | 2.1141 | 2.1141 | 2.1141 | 2.1141
2024-10-25 02:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-08-25 01:00 | 1.7033 | 1.9853 | 1.9853 | 1.9853 | 1.9853
2024-10-25 03:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-08-25 02:00 | 1.7566 | 2.0475 | 2.0475 | 2.0475 | 2.0475
2024-10-25 04:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-08-25 03:00 | 1.871 | 2.1808 | 2.1808 | 2.1808 | 2.1808
2024-10-25 05:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2024-08-25 04:00 | 1.9967 | 2.3273 | 2.3273 | 2.3273 | 2.3273
2024-10-25 06:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2024-08-25 05:00 | 2.3206 | 2.7049 | 2.7049 | 2.7049 | 2.7049
2024-10-25 07:00 | 1.7338 | 2.1568 | 2.6058 | 2.6657 | 2.7255 | 2024-08-25 06:00 | 2.454 | 2.8603 | 2.8603 | 2.8603 | 2.8603
2024-10-25 08:00 | 1.0098 | 1.2561 | 1.5177 | 1.5525 | 1.5874 | 2024-08-25 07:00 | 2.6826 | 3.1268 | 3.1268 | 3.1268 | 3.1268
2024-10-25 09:00 | 0.74305 | 0.92433 | 1.1168 | 1.1424 | 1.1681 | 2024-08-25 08:00 | 2.6635 | 3.1046 | 3.1046 | 3.1046 | 3.1046
2024-10-25 10:00 | 1.0479 | 1.3035 | 1.5749 | 1.6111 | 1.6473 | 2024-08-25 09:00 | 2.8312 | 3.3 | 3.3 | 3.3 | 3.3
2024-10-25 11:00 | 1.7719 | 2.2042 | 2.6631 | 2.7242 | 2.7854 | 2024-08-25 10:00 | 2.9265 | 3.4111 | 3.4111 | 3.4111 | 3.4111
2024-10-25 12:00 | 1.9053 | 2.3701 | 2.8635 | 2.9293 | 2.9951 | 2024-08-25 11:00 | 2.9493 | 3.4377 | 3.4377 | 3.4377 | 3.4377
2024-10-25 13:00 | 1.9815 | 2.4649 | 2.9781 | 3.0465 | 3.1149 | 2024-08-25 12:00 | 3.037 | 3.5399 | 3.5399 | 3.5399 | 3.5399
2024-10-25 14:00 | 1.8481 | 2.299 | 2.7776 | 2.8414 | 2.9052 | 2024-08-25 13:00 | 3.2656 | 3.8064 | 3.8064 | 3.8064 | 3.8064
2024-10-25 15:00 | 1.829 | 2.2753 | 2.749 | 2.8121 | 2.8753 | 2024-08-25 14:00 | 3.3418 | 3.8952 | 3.8952 | 3.8952 | 3.8952
2024-10-25 16:00 | 1.8672 | 2.3227 | 2.8062 | 2.8707 | 2.9352 | 2024-08-25 15:00 | 3.1132 | 3.6287 | 3.6287 | 3.6287 | 3.6287
2024-10-25 17:00 | 1.829 | 2.2753 | 2.749 | 2.8121 | 2.8753 | 2024-08-25 16:00 | 3.0827 | 3.5932 | 3.5932 | 3.5932 | 3.5932
2024-10-25 18:00 | 1.6957 | 2.1094 | 2.5485 | 2.6071 | 2.6656 | 2024-08-25 17:00 | 3.0941 | 3.6065 | 3.6065 | 3.6065 | 3.6065
2024-10-25 19:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2024-08-25 18:00 | 2.6978 | 3.1446 | 3.1446 | 3.1446 | 3.1446
2024-10-25 20:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2024-08-25 19:00 | 2.4502 | 2.8559 | 2.8559 | 2.8559 | 2.8559
2024-10-25 21:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2024-08-25 20:00 | 2.3473 | 2.736 | 2.736 | 2.736 | 2.736
2024-10-25 22:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2024-08-25 21:00 | 2.1796 | 2.5405 | 2.5405 | 2.5405 | 2.5405
2024-10-25 23:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2024-08-25 22:00 | 1.9014 | 2.2163 | 2.2163 | 2.2163 | 2.2163
2024-10-26 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2024-08-25 23:00 | 1.7871 | 2.0831 | 2.0831 | 2.0831 | 2.0831
2024-10-26 01:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-08-26 | 1.7833 | 2.0786 | 2.0786 | 2.0786 | 2.0786
2024-10-26 02:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-08-26 01:00 | 1.7757 | 2.0697 | 2.0697 | 2.0697 | 2.0697
2024-10-26 03:00 | 1.4099 | 1.7539 | 2.119 | 2.1677 | 2.2164 | 2024-08-26 02:00 | 1.829 | 2.1319 | 2.1319 | 2.1319 | 2.1319
2024-10-26 04:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-08-26 03:00 | 1.8976 | 2.2119 | 2.2119 | 2.2119 | 2.2119
2024-10-26 05:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2024-08-26 04:00 | 2.0882 | 2.4339 | 2.4339 | 2.4339 | 2.4339
2024-10-26 06:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2024-08-26 05:00 | 2.3092 | 2.6915 | 2.6915 | 2.6915 | 2.6915
2024-10-26 07:00 | 0.80021 | 0.99544 | 1.2027 | 1.2303 | 1.2579 | 2024-08-26 06:00 | 3.1132 | 3.6287 | 3.6287 | 3.6287 | 3.6287
2024-10-26 08:00 | 0.99073 | 1.2324 | 1.489 | 1.5232 | 1.5574 | 2024-08-26 07:00 | 3.0903 | 3.602 | 3.602 | 3.602 | 3.602
2024-10-26 09:00 | 0.80021 | 0.99544 | 1.2027 | 1.2303 | 1.2579 | 2024-08-26 08:00 | 3.2466 | 3.7841 | 3.7841 | 3.7841 | 3.7841
2024-10-26 10:00 | 1.0288 | 1.2798 | 1.5463 | 1.5818 | 1.6173 | 2024-08-26 09:00 | 3.2389 | 3.7753 | 3.7753 | 3.7753 | 3.7753
2024-10-26 11:00 | 0.87642 | 1.0902 | 1.3172 | 1.3475 | 1.3777 | 2024-08-26 10:00 | 2.915 | 3.3977 | 3.3977 | 3.3977 | 3.3977
2024-10-26 12:00 | 0.80021 | 0.99544 | 1.2027 | 1.2303 | 1.2579 | 2024-08-26 11:00 | 3.1475 | 3.6687 | 3.6687 | 3.6687 | 3.6687
2024-10-26 13:00 | 0.91452 | 1.1376 | 1.3745 | 1.4061 | 1.4376 | 2024-08-26 12:00 | 3.0522 | 3.5576 | 3.5576 | 3.5576 | 3.5576
2024-10-26 14:00 | 1.1432 | 1.4221 | 1.7181 | 1.7576 | 1.7971 | 2024-08-26 13:00 | 2.9913 | 3.4866 | 3.4866 | 3.4866 | 3.4866
2024-10-26 15:00 | 1.1813 | 1.4695 | 1.7754 | 1.8162 | 1.857 | 2024-08-26 14:00 | 2.8541 | 3.3267 | 3.3267 | 3.3267 | 3.3267
2024-10-26 16:00 | 1.0479 | 1.3035 | 1.5749 | 1.6111 | 1.6473 | 2024-08-26 15:00 | 3.2542 | 3.793 | 3.793 | 3.793 | 3.793
2024-10-26 17:00 | 0.64779 | 0.80583 | 0.97359 | 0.99596 | 1.0183 | 2024-08-26 16:00 | 3.4028 | 3.9662 | 3.9662 | 3.9662 | 3.9662
2024-10-26 18:00 | 1.4099 | 1.7539 | 2.119 | 2.1677 | 2.2164 | 2024-08-26 17:00 | 3.62 | 4.2194 | 4.2194 | 4.2194 | 4.2194
2024-10-26 19:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2024-08-26 18:00 | 3.3456 | 3.8996 | 3.8996 | 3.8996 | 3.8996
2024-10-26 20:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2024-08-26 19:00 | 2.7741 | 3.2334 | 3.2334 | 3.2334 | 3.2334
2024-10-26 21:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2024-08-26 20:00 | 2.4692 | 2.8781 | 2.8781 | 2.8781 | 2.8781
2024-10-26 22:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-08-26 21:00 | 2.1415 | 2.4961 | 2.4961 | 2.4961 | 2.4961
2024-10-26 23:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-08-26 22:00 | 1.97 | 2.2962 | 2.2962 | 2.2962 | 2.2962
2024-10-27 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-08-26 23:00 | 2.0615 | 2.4028 | 2.4028 | 2.4028 | 2.4028
2024-10-27 01:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-08-27 | 1.7871 | 2.0831 | 2.0831 | 2.0831 | 2.0831
2024-10-27 02:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-08-27 01:00 | 1.7948 | 2.0919 | 2.0919 | 2.0919 | 2.0919
2024-10-27 03:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-08-27 02:00 | 1.7986 | 2.0964 | 2.0964 | 2.0964 | 2.0964
2024-10-27 04:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-08-27 03:00 | 1.9929 | 2.3229 | 2.3229 | 2.3229 | 2.3229
2024-10-27 05:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-08-27 04:00 | 2.1949 | 2.5583 | 2.5583 | 2.5583 | 2.5583
2024-10-27 06:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-08-27 05:00 | 2.4044 | 2.8026 | 2.8026 | 2.8026 | 2.8026
2024-10-27 07:00 | 1.4289 | 1.7776 | 2.1476 | 2.197 | 2.2463 | 2024-08-27 06:00 | 3.0408 | 3.5443 | 3.5443 | 3.5443 | 3.5443
2024-10-27 08:00 | 1.2575 | 1.5643 | 1.8899 | 1.9333 | 1.9768 | 2024-08-27 07:00 | 3.117 | 3.6331 | 3.6331 | 3.6331 | 3.6331
2024-10-27 09:00 | 0.47631 | 0.59252 | 0.71588 | 0.73232 | 0.74877 | 2024-08-27 08:00 | 3.3571 | 3.913 | 3.913 | 3.913 | 3.913
2024-10-27 10:00 | 0.038105 | 0.047402 | 0.05727 | 0.058586 | 0.059902 | 2024-08-27 09:00 | 3.0522 | 3.5576 | 3.5576 | 3.5576 | 3.5576
2024-10-27 11:00 | 0.62873 | 0.78213 | 0.94496 | 0.96667 | 0.98838 | 2024-08-27 10:00 | 2.9074 | 3.3889 | 3.3889 | 3.3889 | 3.3889
2024-10-27 12:00 | 0.85737 | 1.0665 | 1.2886 | 1.3182 | 1.3478 | 2024-08-27 11:00 | 2.9798 | 3.4732 | 3.4732 | 3.4732 | 3.4732
2024-10-27 13:00 | 0.99073 | 1.2324 | 1.489 | 1.5232 | 1.5574 | 2024-08-27 12:00 | 3.3304 | 3.8819 | 3.8819 | 3.8819 | 3.8819
2024-10-27 14:00 | 0.7621 | 0.94804 | 1.1454 | 1.1717 | 1.198 | 2024-08-27 13:00 | 3.3228 | 3.873 | 3.873 | 3.873 | 3.873
2024-10-27 15:00 | 0.89547 | 1.1139 | 1.3458 | 1.3768 | 1.4077 | 2024-08-27 14:00 | 3.3533 | 3.9085 | 3.9085 | 3.9085 | 3.9085
2024-10-27 16:00 | 0.97168 | 1.2087 | 1.4604 | 1.4939 | 1.5275 | 2024-08-27 15:00 | 3.0332 | 3.5354 | 3.5354 | 3.5354 | 3.5354
2024-10-27 17:00 | 1.1241 | 1.3984 | 1.6895 | 1.7283 | 1.7671 | 2024-08-27 16:00 | 3.2618 | 3.8019 | 3.8019 | 3.8019 | 3.8019
2024-10-27 18:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-08-27 17:00 | 3.3685 | 3.9263 | 3.9263 | 3.9263 | 3.9263
2024-10-27 19:00 | 1.4289 | 1.7776 | 2.1476 | 2.197 | 2.2463 | 2024-08-27 18:00 | 3.1208 | 3.6376 | 3.6376 | 3.6376 | 3.6376
2024-10-27 20:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2024-08-27 19:00 | 2.7436 | 3.1979 | 3.1979 | 3.1979 | 3.1979
2024-10-27 21:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-08-27 20:00 | 2.4578 | 2.8648 | 2.8648 | 2.8648 | 2.8648
2024-10-27 22:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-08-27 21:00 | 2.3968 | 2.7937 | 2.7937 | 2.7937 | 2.7937
2024-10-27 23:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-08-27 22:00 | 2.0691 | 2.4117 | 2.4117 | 2.4117 | 2.4117
2024-10-28 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-08-27 23:00 | 1.8862 | 2.1985 | 2.1985 | 2.1985 | 2.1985
2024-10-28 01:00 | 1.4099 | 1.7539 | 2.119 | 2.1677 | 2.2164 | 2024-08-28 | 1.7719 | 2.0653 | 2.0653 | 2.0653 | 2.0653
2024-10-28 02:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-08-28 01:00 | 1.7948 | 2.0919 | 2.0919 | 2.0919 | 2.0919
2024-10-28 03:00 | 1.3908 | 1.7302 | 2.0904 | 2.1384 | 2.1864 | 2024-08-28 02:00 | 1.7452 | 2.0342 | 2.0342 | 2.0342 | 2.0342
2024-10-28 04:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-08-28 03:00 | 1.9243 | 2.243 | 2.243 | 2.243 | 2.243
2024-10-28 05:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-08-28 04:00 | 2.1301 | 2.4828 | 2.4828 | 2.4828 | 2.4828
2024-10-28 06:00 | 1.6957 | 2.1094 | 2.5485 | 2.6071 | 2.6656 | 2024-08-28 05:00 | 2.2634 | 2.6382 | 2.6382 | 2.6382 | 2.6382
2024-10-28 07:00 | 2.1148 | 2.6308 | 3.1785 | 3.2515 | 3.3245 | 2024-08-28 06:00 | 2.8388 | 3.3089 | 3.3089 | 3.3089 | 3.3089
2024-10-28 08:00 | 2.1529 | 2.6782 | 3.2358 | 3.3101 | 3.3845 | 2024-08-28 07:00 | 3.2732 | 3.8152 | 3.8152 | 3.8152 | 3.8152
2024-10-28 09:00 | 2.0386 | 2.536 | 3.064 | 3.1344 | 3.2047 | 2024-08-28 08:00 | 3.2427 | 3.7797 | 3.7797 | 3.7797 | 3.7797
2024-10-28 10:00 | 1.2003 | 1.4932 | 1.804 | 1.8455 | 1.8869 | 2024-08-28 09:00 | 3.1551 | 3.6776 | 3.6776 | 3.6776 | 3.6776
2024-10-28 11:00 | 0.53347 | 0.66362 | 0.80178 | 0.8202 | 0.83862 | 2024-08-28 10:00 | 3.0675 | 3.5754 | 3.5754 | 3.5754 | 3.5754
2024-10-28 12:00 | 1.9053 | 2.3701 | 2.8635 | 2.9293 | 2.9951 | 2024-08-28 11:00 | 3.0751 | 3.5843 | 3.5843 | 3.5843 | 3.5843
2024-10-28 13:00 | 0.7621 | 0.94804 | 1.1454 | 1.1717 | 1.198 | 2024-08-28 12:00 | 3.4218 | 3.9885 | 3.9885 | 3.9885 | 3.9885
2024-10-28 14:00 | 0.78115 | 0.97174 | 1.174 | 1.201 | 1.228 | 2024-08-28 13:00 | 3.5323 | 4.1173 | 4.1173 | 4.1173 | 4.1173
2024-10-28 15:00 | 0.99073 | 1.2324 | 1.489 | 1.5232 | 1.5574 | 2024-08-28 14:00 | 3.3304 | 3.8819 | 3.8819 | 3.8819 | 3.8819
2024-10-28 16:00 | 1.1622 | 1.4458 | 1.7467 | 1.7869 | 1.827 | 2024-08-28 15:00 | 3.559 | 4.1483 | 4.1483 | 4.1483 | 4.1483
2024-10-28 17:00 | 1.0669 | 1.3272 | 1.6036 | 1.6404 | 1.6772 | 2024-08-28 16:00 | 3.5514 | 4.1395 | 4.1395 | 4.1395 | 4.1395
2024-10-28 18:00 | 1.81 | 2.2516 | 2.7203 | 2.7828 | 2.8453 | 2024-08-28 17:00 | 3.5895 | 4.1839 | 4.1839 | 4.1839 | 4.1839
2024-10-28 19:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2024-08-28 18:00 | 3.1665 | 3.6909 | 3.6909 | 3.6909 | 3.6909
2024-10-28 20:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2024-08-28 19:00 | 2.6712 | 3.1135 | 3.1135 | 3.1135 | 3.1135
2024-10-28 21:00 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2024-08-28 20:00 | 2.7017 | 3.149 | 3.149 | 3.149 | 3.149
2024-10-28 22:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-08-28 21:00 | 2.252 | 2.6249 | 2.6249 | 2.6249 | 2.6249
2024-10-28 23:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-08-28 22:00 | 1.9167 | 2.2341 | 2.2341 | 2.2341 | 2.2341
2024-10-29 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-08-28 23:00 | 1.8633 | 2.1719 | 2.1719 | 2.1719 | 2.1719
2024-10-29 01:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-08-29 | 1.7605 | 2.052 | 2.052 | 2.052 | 2.052
2024-10-29 02:00 | 1.4099 | 1.7539 | 2.119 | 2.1677 | 2.2164 | 2024-08-29 01:00 | 1.7909 | 2.0875 | 2.0875 | 2.0875 | 2.0875
2024-10-29 03:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-08-29 02:00 | 1.7757 | 2.0697 | 2.0697 | 2.0697 | 2.0697
2024-10-29 04:00 | 1.4289 | 1.7776 | 2.1476 | 2.197 | 2.2463 | 2024-08-29 03:00 | 1.8214 | 2.123 | 2.123 | 2.123 | 2.123
2024-10-29 05:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-08-29 04:00 | 2.1415 | 2.4961 | 2.4961 | 2.4961 | 2.4961
2024-10-29 06:00 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2024-08-29 05:00 | 2.5073 | 2.9225 | 2.9225 | 2.9225 | 2.9225
2024-10-29 07:00 | 1.3718 | 1.7065 | 2.0617 | 2.1091 | 2.1565 | 2024-08-29 06:00 | 2.7474 | 3.2023 | 3.2023 | 3.2023 | 3.2023
2024-10-29 08:00 | 0.91452 | 1.1376 | 1.3745 | 1.4061 | 1.4376 | 2024-08-29 07:00 | 3.0675 | 3.5754 | 3.5754 | 3.5754 | 3.5754
2024-10-29 09:00 | 0.64779 | 0.80583 | 0.97359 | 0.99596 | 1.0183 | 2024-08-29 08:00 | 3.3533 | 3.9085 | 3.9085 | 3.9085 | 3.9085
2024-10-29 10:00 | 0.64779 | 0.80583 | 0.97359 | 0.99596 | 1.0183 | 2024-08-29 09:00 | 3.2351 | 3.7708 | 3.7708 | 3.7708 | 3.7708
2024-10-29 11:00 | 0.49537 | 0.61622 | 0.74451 | 0.76162 | 0.77872 | 2024-08-29 10:00 | 3.0637 | 3.571 | 3.571 | 3.571 | 3.571
2024-10-29 12:00 | 0.57158 | 0.71103 | 0.85905 | 0.87879 | 0.89853 | 2024-08-29 11:00 | 2.9608 | 3.451 | 3.451 | 3.451 | 3.451
2024-10-29 13:00 | 0.70494 | 0.87693 | 1.0595 | 1.0838 | 1.1082 | 2024-08-29 12:00 | 2.9989 | 3.4955 | 3.4955 | 3.4955 | 3.4955
2024-10-29 14:00 | 0.68589 | 0.85323 | 1.0309 | 1.0545 | 1.0782 | 2024-08-29 13:00 | 3.0903 | 3.602 | 3.602 | 3.602 | 3.602
2024-10-29 15:00 | 0.70494 | 0.87693 | 1.0595 | 1.0838 | 1.1082 | 2024-08-29 14:00 | 2.9646 | 3.4555 | 3.4555 | 3.4555 | 3.4555
2024-10-29 16:00 | 1.0098 | 1.2561 | 1.5177 | 1.5525 | 1.5874 | 2024-08-29 15:00 | 3.1818 | 3.7086 | 3.7086 | 3.7086 | 3.7086
2024-10-29 17:00 | 1.4289 | 1.7776 | 2.1476 | 2.197 | 2.2463 | 2024-08-29 16:00 | 3.2618 | 3.8019 | 3.8019 | 3.8019 | 3.8019
2024-10-29 18:00 | 1.8862 | 2.3464 | 2.8349 | 2.9 | 2.9651 | 2024-08-29 17:00 | 3.4866 | 4.064 | 4.064 | 4.064 | 4.064
2024-10-29 19:00 | 1.7338 | 2.1568 | 2.6058 | 2.6657 | 2.7255 | 2024-08-29 18:00 | 3.3342 | 3.8863 | 3.8863 | 3.8863 | 3.8863
2024-10-29 20:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2024-08-29 19:00 | 3.1246 | 3.642 | 3.642 | 3.642 | 3.642
2024-10-29 21:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2024-08-29 20:00 | 2.6597 | 3.1002 | 3.1002 | 3.1002 | 3.1002
2024-10-29 22:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2024-08-29 21:00 | 2.2939 | 2.6738 | 2.6738 | 2.6738 | 2.6738
2024-10-29 23:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-08-29 22:00 | 1.8672 | 2.1763 | 2.1763 | 2.1763 | 2.1763
2024-10-30 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-08-29 23:00 | 1.9624 | 2.2874 | 2.2874 | 2.2874 | 2.2874
2024-10-30 01:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-08-30 | 2.0234 | 2.3584 | 2.3584 | 2.3584 | 2.3584
2024-10-30 02:00 | 1.4289 | 1.7776 | 2.1476 | 2.197 | 2.2463 | 2024-08-30 01:00 | 1.8329 | 2.1364 | 2.1364 | 2.1364 | 2.1364
2024-10-30 03:00 | 1.4099 | 1.7539 | 2.119 | 2.1677 | 2.2164 | 2024-08-30 02:00 | 1.8214 | 2.123 | 2.123 | 2.123 | 2.123
2024-10-30 04:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-08-30 03:00 | 1.9396 | 2.2607 | 2.2607 | 2.2607 | 2.2607
2024-10-30 05:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2024-08-30 04:00 | 2.0539 | 2.394 | 2.394 | 2.394 | 2.394
2024-10-30 06:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2024-08-30 05:00 | 2.332 | 2.7182 | 2.7182 | 2.7182 | 2.7182
2024-10-30 07:00 | 1.9243 | 2.3938 | 2.8921 | 2.9586 | 3.025 | 2024-08-30 06:00 | 2.8503 | 3.3222 | 3.3222 | 3.3222 | 3.3222
2024-10-30 08:00 | 0.83831 | 1.0428 | 1.2599 | 1.2889 | 1.3178 | 2024-08-30 07:00 | 3.3228 | 3.873 | 3.873 | 3.873 | 3.873
2024-10-30 09:00 | 0.38105 | 0.47402 | 0.5727 | 0.58586 | 0.59902 | 2024-08-30 08:00 | 3.6962 | 4.3082 | 4.3082 | 4.3082 | 4.3082
2024-10-30 10:00 | 0.53347 | 0.66362 | 0.80178 | 0.8202 | 0.83862 | 2024-08-30 09:00 | 3.6505 | 4.2549 | 4.2549 | 4.2549 | 4.2549
2024-10-30 11:00 | 0.70494 | 0.87693 | 1.0595 | 1.0838 | 1.1082 | 2024-08-30 10:00 | 3.6581 | 4.2638 | 4.2638 | 4.2638 | 4.2638
2024-10-30 12:00 | 0.80021 | 0.99544 | 1.2027 | 1.2303 | 1.2579 | 2024-08-30 11:00 | 3.6047 | 4.2016 | 4.2016 | 4.2016 | 4.2016
2024-10-30 13:00 | 0.97168 | 1.2087 | 1.4604 | 1.4939 | 1.5275 | 2024-08-30 12:00 | 3.62 | 4.2194 | 4.2194 | 4.2194 | 4.2194
2024-10-30 14:00 | 1.2384 | 1.5406 | 1.8613 | 1.904 | 1.9468 | 2024-08-30 13:00 | 3.7648 | 4.3882 | 4.3882 | 4.3882 | 4.3882
2024-10-30 15:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-08-30 14:00 | 3.5819 | 4.175 | 4.175 | 4.175 | 4.175
2024-10-30 16:00 | 1.3146 | 1.6354 | 1.9758 | 2.0212 | 2.0666 | 2024-08-30 15:00 | 3.4561 | 4.0284 | 4.0284 | 4.0284 | 4.0284
2024-10-30 17:00 | 1.3908 | 1.7302 | 2.0904 | 2.1384 | 2.1864 | 2024-08-30 16:00 | 3.4333 | 4.0018 | 4.0018 | 4.0018 | 4.0018
2024-10-30 18:00 | 1.81 | 2.2516 | 2.7203 | 2.7828 | 2.8453 | 2024-08-30 17:00 | 3.5019 | 4.0817 | 4.0817 | 4.0817 | 4.0817
2024-10-30 19:00 | 1.7338 | 2.1568 | 2.6058 | 2.6657 | 2.7255 | 2024-08-30 18:00 | 3.4104 | 3.9751 | 3.9751 | 3.9751 | 3.9751
2024-10-30 20:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2024-08-30 19:00 | 3.0637 | 3.571 | 3.571 | 3.571 | 3.571
2024-10-30 21:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2024-08-30 20:00 | 2.6521 | 3.0913 | 3.0913 | 3.0913 | 3.0913
2024-10-30 22:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2024-08-30 21:00 | 2.2368 | 2.6072 | 2.6072 | 2.6072 | 2.6072
2024-10-30 23:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-08-30 22:00 | 1.8748 | 2.1852 | 2.1852 | 2.1852 | 2.1852
2024-10-31 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-08-30 23:00 | 1.8138 | 2.1141 | 2.1141 | 2.1141 | 2.1141
2024-10-31 01:00 | 1.4289 | 1.7776 | 2.1476 | 2.197 | 2.2463 | 2024-08-31 | 1.8329 | 2.1364 | 2.1364 | 2.1364 | 2.1364
2024-10-31 02:00 | 1.4099 | 1.7539 | 2.119 | 2.1677 | 2.2164 | 2024-08-31 01:00 | 1.7033 | 1.9853 | 1.9853 | 1.9853 | 1.9853
2024-10-31 03:00 | 1.3527 | 1.6828 | 2.0331 | 2.0798 | 2.1265 | 2024-08-31 02:00 | 1.6652 | 1.9409 | 1.9409 | 1.9409 | 1.9409
2024-10-31 04:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-08-31 03:00 | 1.7833 | 2.0786 | 2.0786 | 2.0786 | 2.0786
2024-10-31 05:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-08-31 04:00 | 2.0005 | 2.3318 | 2.3318 | 2.3318 | 2.3318
2024-10-31 06:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2024-08-31 05:00 | 2.2025 | 2.5672 | 2.5672 | 2.5672 | 2.5672
2024-10-31 07:00 | 1.9053 | 2.3701 | 2.8635 | 2.9293 | 2.9951 | 2024-08-31 06:00 | 2.3739 | 2.767 | 2.767 | 2.767 | 2.767
2024-10-31 08:00 | 1.9053 | 2.3701 | 2.8635 | 2.9293 | 2.9951 | 2024-08-31 07:00 | 2.2673 | 2.6427 | 2.6427 | 2.6427 | 2.6427
2024-10-31 09:00 | 2.2101 | 2.7493 | 3.3217 | 3.398 | 3.4743 | 2024-08-31 08:00 | 2.5264 | 2.9447 | 2.9447 | 2.9447 | 2.9447
2024-10-31 10:00 | 2.1148 | 2.6308 | 3.1785 | 3.2515 | 3.3245 | 2024-08-31 09:00 | 2.6864 | 3.1312 | 3.1312 | 3.1312 | 3.1312
2024-10-31 11:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-08-31 10:00 | 2.3816 | 2.7759 | 2.7759 | 2.7759 | 2.7759
2024-10-31 12:00 | 2.2101 | 2.7493 | 3.3217 | 3.398 | 3.4743 | 2024-08-31 11:00 | 2.3435 | 2.7315 | 2.7315 | 2.7315 | 2.7315
2024-10-31 13:00 | 2.0767 | 2.5834 | 3.1212 | 3.1929 | 3.2646 | 2024-08-31 12:00 | 2.8007 | 3.2645 | 3.2645 | 3.2645 | 3.2645
2024-10-31 14:00 | 1.829 | 2.2753 | 2.749 | 2.8121 | 2.8753 | 2024-08-31 13:00 | 2.4425 | 2.847 | 2.847 | 2.847 | 2.847
2024-10-31 15:00 | 1.9815 | 2.4649 | 2.9781 | 3.0465 | 3.1149 | 2024-08-31 14:00 | 2.5111 | 2.9269 | 2.9269 | 2.9269 | 2.9269
2024-10-31 16:00 | 2.0386 | 2.536 | 3.064 | 3.1344 | 3.2047 | 2024-08-31 15:00 | 2.7817 | 3.2423 | 3.2423 | 3.2423 | 3.2423
2024-10-31 17:00 | 2.0767 | 2.5834 | 3.1212 | 3.1929 | 3.2646 | 2024-08-31 16:00 | 3.0675 | 3.5754 | 3.5754 | 3.5754 | 3.5754
2024-10-31 18:00 | 1.7719 | 2.2042 | 2.6631 | 2.7242 | 2.7854 | 2024-08-31 17:00 | 2.9722 | 3.4644 | 3.4644 | 3.4644 | 3.4644
2024-10-31 19:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2024-08-31 18:00 | 2.8083 | 3.2734 | 3.2734 | 3.2734 | 3.2734
2024-10-31 20:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2024-08-31 19:00 | 2.4463 | 2.8514 | 2.8514 | 2.8514 | 2.8514
2024-10-31 21:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2024-08-31 20:00 | 2.2596 | 2.6338 | 2.6338 | 2.6338 | 2.6338
2024-10-31 22:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2024-08-31 21:00 | 2.0958 | 2.4428 | 2.4428 | 2.4428 | 2.4428
2024-10-31 23:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2024-08-31 22:00 | 1.8252 | 2.1275 | 2.1275 | 2.1275 | 2.1275
2024-11-01 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-08-31 23:00 | 1.7871 | 2.0831 | 2.0831 | 2.0831 | 2.0831
2024-11-01 01:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-09-01 | 1.7224 | 2.0076 | 2.0076 | 2.0076 | 2.0076
2024-11-01 02:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-09-01 01:00 | 1.7109 | 1.9942 | 1.9942 | 1.9942 | 1.9942
2024-11-01 03:00 | 1.3908 | 1.7302 | 2.0904 | 2.1384 | 2.1864 | 2024-09-01 02:00 | 1.6919 | 1.972 | 1.972 | 1.972 | 1.972
2024-11-01 04:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-09-01 03:00 | 1.9205 | 2.2385 | 2.2385 | 2.2385 | 2.2385
2024-11-01 05:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-09-01 04:00 | 1.9472 | 2.2696 | 2.2696 | 2.2696 | 2.2696
2024-11-01 06:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2024-09-01 05:00 | 2.2901 | 2.6693 | 2.6693 | 2.6693 | 2.6693
2024-11-01 07:00 | 1.8672 | 2.3227 | 2.8062 | 2.8707 | 2.9352 | 2024-09-01 06:00 | 2.3015 | 2.6827 | 2.6827 | 2.6827 | 2.6827
2024-11-01 08:00 | 1.7909 | 2.2279 | 2.6917 | 2.7535 | 2.8154 | 2024-09-01 07:00 | 2.2558 | 2.6294 | 2.6294 | 2.6294 | 2.6294
2024-11-01 09:00 | 1.9624 | 2.4412 | 2.9494 | 3.0172 | 3.0849 | 2024-09-01 08:00 | 2.2711 | 2.6471 | 2.6471 | 2.6471 | 2.6471
2024-11-01 10:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2024-09-01 09:00 | 2.2063 | 2.5716 | 2.5716 | 2.5716 | 2.5716
2024-11-01 11:00 | 1.8672 | 2.3227 | 2.8062 | 2.8707 | 2.9352 | 2024-09-01 10:00 | 2.4502 | 2.8559 | 2.8559 | 2.8559 | 2.8559
2024-11-01 12:00 | 1.829 | 2.2753 | 2.749 | 2.8121 | 2.8753 | 2024-09-01 11:00 | 2.4387 | 2.8426 | 2.8426 | 2.8426 | 2.8426
2024-11-01 13:00 | 2.0005 | 2.4886 | 3.0067 | 3.0758 | 3.1448 | 2024-09-01 12:00 | 2.5035 | 2.9181 | 2.9181 | 2.9181 | 2.9181
2024-11-01 14:00 | 2.0386 | 2.536 | 3.064 | 3.1344 | 3.2047 | 2024-09-01 13:00 | 2.4121 | 2.8115 | 2.8115 | 2.8115 | 2.8115
2024-11-01 15:00 | 1.9434 | 2.4175 | 2.9208 | 2.9879 | 3.055 | 2024-09-01 14:00 | 2.3739 | 2.767 | 2.767 | 2.767 | 2.767
2024-11-01 16:00 | 1.81 | 2.2516 | 2.7203 | 2.7828 | 2.8453 | 2024-09-01 15:00 | 2.534 | 2.9536 | 2.9536 | 2.9536 | 2.9536
2024-11-01 17:00 | 1.9243 | 2.3938 | 2.8921 | 2.9586 | 3.025 | 2024-09-01 16:00 | 2.7893 | 3.2512 | 3.2512 | 3.2512 | 3.2512
2024-11-01 18:00 | 1.7528 | 2.1805 | 2.6344 | 2.695 | 2.7555 | 2024-09-01 17:00 | 2.8655 | 3.34 | 3.34 | 3.34 | 3.34
2024-11-01 19:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2024-09-01 18:00 | 2.7741 | 3.2334 | 3.2334 | 3.2334 | 3.2334
2024-11-01 20:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2024-09-01 19:00 | 2.4768 | 2.887 | 2.887 | 2.887 | 2.887
2024-11-01 21:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-09-01 20:00 | 2.3054 | 2.6871 | 2.6871 | 2.6871 | 2.6871
2024-11-01 22:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-09-01 21:00 | 2.1606 | 2.5183 | 2.5183 | 2.5183 | 2.5183
2024-11-01 23:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-09-01 22:00 | 1.9434 | 2.2652 | 2.2652 | 2.2652 | 2.2652
2024-11-02 | 1.4289 | 1.7776 | 2.1476 | 2.197 | 2.2463 | 2024-09-01 23:00 | 1.7605 | 2.052 | 2.052 | 2.052 | 2.052
2024-11-02 01:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-09-02 | 1.8443 | 2.1497 | 2.1497 | 2.1497 | 2.1497
2024-11-02 02:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-09-02 01:00 | 1.6919 | 1.972 | 1.972 | 1.972 | 1.972
2024-11-02 03:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-09-02 02:00 | 1.7528 | 2.0431 | 2.0431 | 2.0431 | 2.0431
2024-11-02 04:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-09-02 03:00 | 1.8786 | 2.1897 | 2.1897 | 2.1897 | 2.1897
2024-11-02 05:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-09-02 04:00 | 2.1148 | 2.465 | 2.465 | 2.465 | 2.465
2024-11-02 06:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-09-02 05:00 | 2.3015 | 2.6827 | 2.6827 | 2.6827 | 2.6827
2024-11-02 07:00 | 1.2194 | 1.5169 | 1.8326 | 1.8748 | 1.9169 | 2024-09-02 06:00 | 2.7398 | 3.1934 | 3.1934 | 3.1934 | 3.1934
2024-11-02 08:00 | 1.3337 | 1.6591 | 2.0045 | 2.0505 | 2.0966 | 2024-09-02 07:00 | 2.976 | 3.4688 | 3.4688 | 3.4688 | 3.4688
2024-11-02 09:00 | 1.0288 | 1.2798 | 1.5463 | 1.5818 | 1.6173 | 2024-09-02 08:00 | 3.4828 | 4.0595 | 4.0595 | 4.0595 | 4.0595
2024-11-02 10:00 | 1.2765 | 1.588 | 1.9186 | 1.9626 | 2.0067 | 2024-09-02 09:00 | 3.4523 | 4.024 | 4.024 | 4.024 | 4.024
2024-11-02 11:00 | 1.1813 | 1.4695 | 1.7754 | 1.8162 | 1.857 | 2024-09-02 10:00 | 3.5476 | 4.135 | 4.135 | 4.135 | 4.135
2024-11-02 12:00 | 0.724 | 0.90063 | 1.0881 | 1.1131 | 1.1381 | 2024-09-02 11:00 | 3.761 | 4.3837 | 4.3837 | 4.3837 | 4.3837
2024-11-02 13:00 | 0.66684 | 0.82953 | 1.0022 | 1.0253 | 1.0483 | 2024-09-02 12:00 | 3.5476 | 4.135 | 4.135 | 4.135 | 4.135
2024-11-02 14:00 | 0.81926 | 1.0191 | 1.2313 | 1.2596 | 1.2879 | 2024-09-02 13:00 | 3.6695 | 4.2772 | 4.2772 | 4.2772 | 4.2772
2024-11-02 15:00 | 0.59063 | 0.73473 | 0.88769 | 0.90808 | 0.92848 | 2024-09-02 14:00 | 3.4409 | 4.0107 | 4.0107 | 4.0107 | 4.0107
2024-11-02 16:00 | 0.83831 | 1.0428 | 1.2599 | 1.2889 | 1.3178 | 2024-09-02 15:00 | 3.4638 | 4.0373 | 4.0373 | 4.0373 | 4.0373
2024-11-02 17:00 | 1.1241 | 1.3984 | 1.6895 | 1.7283 | 1.7671 | 2024-09-02 16:00 | 3.7838 | 4.4104 | 4.4104 | 4.4104 | 4.4104
2024-11-02 18:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-09-02 17:00 | 3.7381 | 4.3571 | 4.3571 | 4.3571 | 4.3571
2024-11-02 19:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2024-09-02 18:00 | 3.4142 | 3.9796 | 3.9796 | 3.9796 | 3.9796
2024-11-02 20:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2024-09-02 19:00 | 2.8045 | 3.2689 | 3.2689 | 3.2689 | 3.2689
2024-11-02 21:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2024-09-02 20:00 | 2.5149 | 2.9314 | 2.9314 | 2.9314 | 2.9314
2024-11-02 22:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2024-09-02 21:00 | 2.1644 | 2.5228 | 2.5228 | 2.5228 | 2.5228
2024-11-02 23:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-09-02 22:00 | 2.0539 | 2.394 | 2.394 | 2.394 | 2.394
2024-11-03 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-09-02 23:00 | 1.9548 | 2.2785 | 2.2785 | 2.2785 | 2.2785
2024-11-03 01:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-09-03 | 1.9091 | 2.2252 | 2.2252 | 2.2252 | 2.2252
2024-11-03 02:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-09-03 01:00 | 1.6766 | 1.9543 | 1.9543 | 1.9543 | 1.9543
2024-11-03 03:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-09-03 02:00 | 1.6576 | 1.932 | 1.932 | 1.932 | 1.932
2024-11-03 04:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-09-03 03:00 | 1.8786 | 2.1897 | 2.1897 | 2.1897 | 2.1897
2024-11-03 05:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-09-03 04:00 | 2.1186 | 2.4695 | 2.4695 | 2.4695 | 2.4695
2024-11-03 06:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-09-03 05:00 | 2.4921 | 2.9047 | 2.9047 | 2.9047 | 2.9047
2024-11-03 07:00 | 1.2956 | 1.6117 | 1.9472 | 1.9919 | 2.0367 | 2024-09-03 06:00 | 2.7588 | 3.2156 | 3.2156 | 3.2156 | 3.2156
2024-11-03 08:00 | 1.0669 | 1.3272 | 1.6036 | 1.6404 | 1.6772 | 2024-09-03 07:00 | 3.3799 | 3.9396 | 3.9396 | 3.9396 | 3.9396
2024-11-03 09:00 | 0.66684 | 0.82953 | 1.0022 | 1.0253 | 1.0483 | 2024-09-03 08:00 | 3.2123 | 3.7442 | 3.7442 | 3.7442 | 3.7442
2024-11-03 10:00 | 0.47631 | 0.59252 | 0.71588 | 0.73232 | 0.74877 | 2024-09-03 09:00 | 3.1742 | 3.6998 | 3.6998 | 3.6998 | 3.6998
2024-11-03 11:00 | 0.019053 | 0.023701 | 0.028635 | 0.029293 | 0.029951 | 2024-09-03 10:00 | 3.0827 | 3.5932 | 3.5932 | 3.5932 | 3.5932
2024-11-03 12:00 | 0.43821 | 0.54512 | 0.65861 | 0.67374 | 0.68887 | 2024-09-03 11:00 | 3.0789 | 3.5887 | 3.5887 | 3.5887 | 3.5887
2024-11-03 13:00 | 0.59063 | 0.73473 | 0.88769 | 0.90808 | 0.92848 | 2024-09-03 12:00 | 2.9531 | 3.4422 | 3.4422 | 3.4422 | 3.4422
2024-11-03 14:00 | 0.60968 | 0.75843 | 0.91632 | 0.93738 | 0.95843 | 2024-09-03 13:00 | 2.7893 | 3.2512 | 3.2512 | 3.2512 | 3.2512
2024-11-03 15:00 | 1.2003 | 1.4932 | 1.804 | 1.8455 | 1.8869 | 2024-09-03 14:00 | 2.8769 | 3.3533 | 3.3533 | 3.3533 | 3.3533
2024-11-03 16:00 | 0.038105 | 0.047402 | 0.05727 | 0.058586 | 0.059902 | 2024-09-03 15:00 | 3.1399 | 3.6598 | 3.6598 | 3.6598 | 3.6598
2024-11-03 17:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2024-09-03 16:00 | 3.3875 | 3.9485 | 3.9485 | 3.9485 | 3.9485
2024-11-03 18:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2024-09-03 17:00 | 3.5628 | 4.1528 | 4.1528 | 4.1528 | 4.1528
2024-11-03 19:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2024-09-03 18:00 | 3.0637 | 3.571 | 3.571 | 3.571 | 3.571
2024-11-03 20:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2024-09-03 19:00 | 2.6559 | 3.0957 | 3.0957 | 3.0957 | 3.0957
2024-11-03 21:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2024-09-03 20:00 | 2.4845 | 2.8958 | 2.8958 | 2.8958 | 2.8958
2024-11-03 22:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2024-09-03 21:00 | 2.2101 | 2.5761 | 2.5761 | 2.5761 | 2.5761
2024-11-03 23:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2024-09-03 22:00 | 2.0462 | 2.3851 | 2.3851 | 2.3851 | 2.3851
2024-11-04 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2024-09-03 23:00 | 1.9396 | 2.2607 | 2.2607 | 2.2607 | 2.2607
2024-11-04 01:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-09-04 | 1.7376 | 2.0253 | 2.0253 | 2.0253 | 2.0253
2024-11-04 02:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-09-04 01:00 | 1.7185 | 2.0031 | 2.0031 | 2.0031 | 2.0031
2024-11-04 03:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2024-09-04 02:00 | 1.81 | 2.1097 | 2.1097 | 2.1097 | 2.1097
2024-11-04 04:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2024-09-04 03:00 | 1.9319 | 2.2518 | 2.2518 | 2.2518 | 2.2518
2024-11-04 05:00 | 1.6957 | 2.1094 | 2.5485 | 2.6071 | 2.6656 | 2024-09-04 04:00 | 2.1682 | 2.5272 | 2.5272 | 2.5272 | 2.5272
2024-11-04 06:00 | 1.7909 | 2.2279 | 2.6917 | 2.7535 | 2.8154 | 2024-09-04 05:00 | 2.3473 | 2.736 | 2.736 | 2.736 | 2.736
2024-11-04 07:00 | 2.2291 | 2.773 | 3.3503 | 3.4273 | 3.5043 | 2024-09-04 06:00 | 3.0103 | 3.5088 | 3.5088 | 3.5088 | 3.5088
2024-11-04 08:00 | 2.4197 | 3.01 | 3.6367 | 3.7202 | 3.8038 | 2024-09-04 07:00 | 3.498 | 4.0773 | 4.0773 | 4.0773 | 4.0773
2024-11-04 09:00 | 2.3816 | 2.9626 | 3.5794 | 3.6616 | 3.7439 | 2024-09-04 08:00 | 3.3456 | 3.8996 | 3.8996 | 3.8996 | 3.8996
2024-11-04 10:00 | 2.4578 | 3.0574 | 3.6939 | 3.7788 | 3.8637 | 2024-09-04 09:00 | 3.338 | 3.8907 | 3.8907 | 3.8907 | 3.8907
2024-11-04 11:00 | 2.5911 | 3.2233 | 3.8944 | 3.9838 | 4.0733 | 2024-09-04 10:00 | 3.0941 | 3.6065 | 3.6065 | 3.6065 | 3.6065
2024-11-04 12:00 | 2.2291 | 2.773 | 3.3503 | 3.4273 | 3.5043 | 2024-09-04 11:00 | 3.2008 | 3.7308 | 3.7308 | 3.7308 | 3.7308
2024-11-04 13:00 | 2.2101 | 2.7493 | 3.3217 | 3.398 | 3.4743 | 2024-09-04 12:00 | 3.4028 | 3.9662 | 3.9662 | 3.9662 | 3.9662
2024-11-04 14:00 | 1.8481 | 2.299 | 2.7776 | 2.8414 | 2.9052 | 2024-09-04 13:00 | 3.2123 | 3.7442 | 3.7442 | 3.7442 | 3.7442
2024-11-04 15:00 | 2.0958 | 2.6071 | 3.1499 | 3.2222 | 3.2946 | 2024-09-04 14:00 | 3.2885 | 3.833 | 3.833 | 3.833 | 3.833
2024-11-04 16:00 | 2.2101 | 2.7493 | 3.3217 | 3.398 | 3.4743 | 2024-09-04 15:00 | 3.2504 | 3.7886 | 3.7886 | 3.7886 | 3.7886
2024-11-04 17:00 | 2.6864 | 3.3418 | 4.0375 | 4.1303 | 4.2231 | 2024-09-04 16:00 | 3.6276 | 4.2283 | 4.2283 | 4.2283 | 4.2283
2024-11-04 18:00 | 2.2482 | 2.7967 | 3.3789 | 3.4566 | 3.5342 | 2024-09-04 17:00 | 3.6505 | 4.2549 | 4.2549 | 4.2549 | 4.2549
2024-11-04 19:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2024-09-04 18:00 | 3.2999 | 3.8463 | 3.8463 | 3.8463 | 3.8463
2024-11-04 20:00 | 1.7719 | 2.2042 | 2.6631 | 2.7242 | 2.7854 | 2024-09-04 19:00 | 2.8503 | 3.3222 | 3.3222 | 3.3222 | 3.3222
2024-11-04 21:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2024-09-04 20:00 | 2.614 | 3.0469 | 3.0469 | 3.0469 | 3.0469
2024-11-04 22:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2024-09-04 21:00 | 2.2063 | 2.5716 | 2.5716 | 2.5716 | 2.5716
2024-11-04 23:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2024-09-04 22:00 | 1.9853 | 2.314 | 2.314 | 2.314 | 2.314
2024-11-05 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-09-04 23:00 | 1.9472 | 2.2696 | 2.2696 | 2.2696 | 2.2696
2024-11-05 01:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-09-05 | 1.8367 | 2.1408 | 2.1408 | 2.1408 | 2.1408
2024-11-05 02:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-09-05 01:00 | 1.8329 | 2.1364 | 2.1364 | 2.1364 | 2.1364
2024-11-05 03:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-09-05 02:00 | 1.6728 | 1.9498 | 1.9498 | 1.9498 | 1.9498
2024-11-05 04:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2024-09-05 03:00 | 1.7948 | 2.0919 | 2.0919 | 2.0919 | 2.0919
2024-11-05 05:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2024-09-05 04:00 | 2.0958 | 2.4428 | 2.4428 | 2.4428 | 2.4428
2024-11-05 06:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2024-09-05 05:00 | 2.3015 | 2.6827 | 2.6827 | 2.6827 | 2.6827
2024-11-05 07:00 | 2.2482 | 2.7967 | 3.3789 | 3.4566 | 3.5342 | 2024-09-05 06:00 | 2.8655 | 3.34 | 3.34 | 3.34 | 3.34
2024-11-05 08:00 | 2.0767 | 2.5834 | 3.1212 | 3.1929 | 3.2646 | 2024-09-05 07:00 | 3.1437 | 3.6642 | 3.6642 | 3.6642 | 3.6642
2024-11-05 09:00 | 2.1529 | 2.6782 | 3.2358 | 3.3101 | 3.3845 | 2024-09-05 08:00 | 3.2694 | 3.8108 | 3.8108 | 3.8108 | 3.8108
2024-11-05 10:00 | 1.6957 | 2.1094 | 2.5485 | 2.6071 | 2.6656 | 2024-09-05 09:00 | 3.0979 | 3.6109 | 3.6109 | 3.6109 | 3.6109
2024-11-05 11:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-09-05 10:00 | 2.9722 | 3.4644 | 3.4644 | 3.4644 | 3.4644
2024-11-05 12:00 | 1.7909 | 2.2279 | 2.6917 | 2.7535 | 2.8154 | 2024-09-05 11:00 | 2.957 | 3.4466 | 3.4466 | 3.4466 | 3.4466
2024-11-05 13:00 | 2.3625 | 2.9389 | 3.5508 | 3.6323 | 3.7139 | 2024-09-05 12:00 | 3.4599 | 4.0329 | 4.0329 | 4.0329 | 4.0329
2024-11-05 14:00 | 2.5911 | 3.2233 | 3.8944 | 3.9838 | 4.0733 | 2024-09-05 13:00 | 3.6314 | 4.2327 | 4.2327 | 4.2327 | 4.2327
2024-11-05 15:00 | 2.534 | 3.1522 | 3.8085 | 3.896 | 3.9835 | 2024-09-05 14:00 | 3.3075 | 3.8552 | 3.8552 | 3.8552 | 3.8552
2024-11-05 16:00 | 2.3244 | 2.8915 | 3.4935 | 3.5737 | 3.654 | 2024-09-05 15:00 | 3.5247 | 4.1084 | 4.1084 | 4.1084 | 4.1084
2024-11-05 17:00 | 1.7719 | 2.2042 | 2.6631 | 2.7242 | 2.7854 | 2024-09-05 16:00 | 3.8067 | 4.437 | 4.437 | 4.437 | 4.437
2024-11-05 18:00 | 2.0577 | 2.5597 | 3.0926 | 3.1636 | 3.2347 | 2024-09-05 17:00 | 3.6924 | 4.3038 | 4.3038 | 4.3038 | 4.3038
2024-11-05 19:00 | 1.7719 | 2.2042 | 2.6631 | 2.7242 | 2.7854 | 2024-09-05 18:00 | 3.1856 | 3.7131 | 3.7131 | 3.7131 | 3.7131
2024-11-05 20:00 | 1.7147 | 2.1331 | 2.5772 | 2.6364 | 2.6956 | 2024-09-05 19:00 | 2.7931 | 3.2556 | 3.2556 | 3.2556 | 3.2556
2024-11-05 21:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2024-09-05 20:00 | 2.6674 | 3.109 | 3.109 | 3.109 | 3.109
2024-11-05 22:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2024-09-05 21:00 | 2.1415 | 2.4961 | 2.4961 | 2.4961 | 2.4961
2024-11-05 23:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2024-09-05 22:00 | 2.0348 | 2.3718 | 2.3718 | 2.3718 | 2.3718
2024-11-06 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-09-05 23:00 | 1.8024 | 2.1008 | 2.1008 | 2.1008 | 2.1008
2024-11-06 01:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-09-06 | 1.7071 | 1.9898 | 1.9898 | 1.9898 | 1.9898
2024-11-06 02:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-09-06 01:00 | 1.7224 | 2.0076 | 2.0076 | 2.0076 | 2.0076
2024-11-06 03:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-09-06 02:00 | 1.6766 | 1.9543 | 1.9543 | 1.9543 | 1.9543
2024-11-06 04:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-09-06 03:00 | 1.89 | 2.203 | 2.203 | 2.203 | 2.203
2024-11-06 05:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2024-09-06 04:00 | 2.0158 | 2.3495 | 2.3495 | 2.3495 | 2.3495
2024-11-06 06:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2024-09-06 05:00 | 2.2558 | 2.6294 | 2.6294 | 2.6294 | 2.6294
2024-11-06 07:00 | 1.1241 | 1.3984 | 1.6895 | 1.7283 | 1.7671 | 2024-09-06 06:00 | 2.6902 | 3.1357 | 3.1357 | 3.1357 | 3.1357
2024-11-06 08:00 | 0.7621 | 0.94804 | 1.1454 | 1.1717 | 1.198 | 2024-09-06 07:00 | 3.178 | 3.7042 | 3.7042 | 3.7042 | 3.7042
2024-11-06 09:00 | 0.70494 | 0.87693 | 1.0595 | 1.0838 | 1.1082 | 2024-09-06 08:00 | 3.0865 | 3.5976 | 3.5976 | 3.5976 | 3.5976
2024-11-06 10:00 | 0.78115 | 0.97174 | 1.174 | 1.201 | 1.228 | 2024-09-06 09:00 | 3.1475 | 3.6687 | 3.6687 | 3.6687 | 3.6687
2024-11-06 11:00 | 1.0098 | 1.2561 | 1.5177 | 1.5525 | 1.5874 | 2024-09-06 10:00 | 3.2161 | 3.7486 | 3.7486 | 3.7486 | 3.7486
2024-11-06 12:00 | 2.5911 | 3.2233 | 3.8944 | 3.9838 | 4.0733 | 2024-09-06 11:00 | 3.2313 | 3.7664 | 3.7664 | 3.7664 | 3.7664
2024-11-06 13:00 | 2.7436 | 3.4129 | 4.1235 | 4.2182 | 4.3129 | 2024-09-06 12:00 | 3.0865 | 3.5976 | 3.5976 | 3.5976 | 3.5976
2024-11-06 14:00 | 2.7055 | 3.3655 | 4.0662 | 4.1596 | 4.253 | 2024-09-06 13:00 | 3.3037 | 3.8508 | 3.8508 | 3.8508 | 3.8508
2024-11-06 15:00 | 2.6102 | 3.247 | 3.923 | 4.0131 | 4.1033 | 2024-09-06 14:00 | 3.2999 | 3.8463 | 3.8463 | 3.8463 | 3.8463
2024-11-06 16:00 | 2.6483 | 3.2944 | 3.9803 | 4.0717 | 4.1632 | 2024-09-06 15:00 | 3.5895 | 4.1839 | 4.1839 | 4.1839 | 4.1839
2024-11-06 17:00 | 2.6102 | 3.247 | 3.923 | 4.0131 | 4.1033 | 2024-09-06 16:00 | 3.8219 | 4.4548 | 4.4548 | 4.4548 | 4.4548
2024-11-06 18:00 | 2.0577 | 2.5597 | 3.0926 | 3.1636 | 3.2347 | 2024-09-06 17:00 | 3.8334 | 4.4681 | 4.4681 | 4.4681 | 4.4681
2024-11-06 19:00 | 1.829 | 2.2753 | 2.749 | 2.8121 | 2.8753 | 2024-09-06 18:00 | 3.319 | 3.8685 | 3.8685 | 3.8685 | 3.8685
2024-11-06 20:00 | 1.7909 | 2.2279 | 2.6917 | 2.7535 | 2.8154 | 2024-09-06 19:00 | 2.9531 | 3.4422 | 3.4422 | 3.4422 | 3.4422
2024-11-06 21:00 | 1.7147 | 2.1331 | 2.5772 | 2.6364 | 2.6956 | 2024-09-06 20:00 | 2.8083 | 3.2734 | 3.2734 | 3.2734 | 3.2734
2024-11-06 22:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2024-09-06 21:00 | 2.3701 | 2.7626 | 2.7626 | 2.7626 | 2.7626
2024-11-06 23:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2024-09-06 22:00 | 1.81 | 2.1097 | 2.1097 | 2.1097 | 2.1097
2024-11-07 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-09-06 23:00 | 1.8252 | 2.1275 | 2.1275 | 2.1275 | 2.1275
2024-11-07 01:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-09-07 | 1.7224 | 2.0076 | 2.0076 | 2.0076 | 2.0076
2024-11-07 02:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-09-07 01:00 | 1.7071 | 1.9898 | 1.9898 | 1.9898 | 1.9898
2024-11-07 03:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-09-07 02:00 | 1.6766 | 1.9543 | 1.9543 | 1.9543 | 1.9543
2024-11-07 04:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-09-07 03:00 | 1.7719 | 2.0653 | 2.0653 | 2.0653 | 2.0653
2024-11-07 05:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2024-09-07 04:00 | 1.9738 | 2.3007 | 2.3007 | 2.3007 | 2.3007
2024-11-07 06:00 | 1.7338 | 2.1568 | 2.6058 | 2.6657 | 2.7255 | 2024-09-07 05:00 | 2.092 | 2.4384 | 2.4384 | 2.4384 | 2.4384
2024-11-07 07:00 | 2.2101 | 2.7493 | 3.3217 | 3.398 | 3.4743 | 2024-09-07 06:00 | 2.2558 | 2.6294 | 2.6294 | 2.6294 | 2.6294
2024-11-07 08:00 | 2.4387 | 3.0337 | 3.6653 | 3.7495 | 3.8337 | 2024-09-07 07:00 | 2.5264 | 2.9447 | 2.9447 | 2.9447 | 2.9447
2024-11-07 09:00 | 2.6102 | 3.247 | 3.923 | 4.0131 | 4.1033 | 2024-09-07 08:00 | 2.9189 | 3.4022 | 3.4022 | 3.4022 | 3.4022
2024-11-07 10:00 | 2.4006 | 2.9863 | 3.608 | 3.6909 | 3.7738 | 2024-09-07 09:00 | 2.915 | 3.3977 | 3.3977 | 3.3977 | 3.3977
2024-11-07 11:00 | 2.0005 | 2.4886 | 3.0067 | 3.0758 | 3.1448 | 2024-09-07 10:00 | 2.6864 | 3.1312 | 3.1312 | 3.1312 | 3.1312
2024-11-07 12:00 | 2.3816 | 2.9626 | 3.5794 | 3.6616 | 3.7439 | 2024-09-07 11:00 | 2.8655 | 3.34 | 3.34 | 3.34 | 3.34
2024-11-07 13:00 | 2.4387 | 3.0337 | 3.6653 | 3.7495 | 3.8337 | 2024-09-07 12:00 | 2.9874 | 3.4821 | 3.4821 | 3.4821 | 3.4821
2024-11-07 14:00 | 2.0767 | 2.5834 | 3.1212 | 3.1929 | 3.2646 | 2024-09-07 13:00 | 2.5187 | 2.9358 | 2.9358 | 2.9358 | 2.9358
2024-11-07 15:00 | 2.191 | 2.7256 | 3.293 | 3.3687 | 3.4444 | 2024-09-07 14:00 | 2.5873 | 3.0158 | 3.0158 | 3.0158 | 3.0158
2024-11-07 16:00 | 2.1529 | 2.6782 | 3.2358 | 3.3101 | 3.3845 | 2024-09-07 15:00 | 2.7207 | 3.1712 | 3.1712 | 3.1712 | 3.1712
2024-11-07 17:00 | 2.172 | 2.7019 | 3.2644 | 3.3394 | 3.4144 | 2024-09-07 16:00 | 2.8083 | 3.2734 | 3.2734 | 3.2734 | 3.2734
2024-11-07 18:00 | 1.8481 | 2.299 | 2.7776 | 2.8414 | 2.9052 | 2024-09-07 17:00 | 2.7169 | 3.1668 | 3.1668 | 3.1668 | 3.1668
2024-11-07 19:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2024-09-07 18:00 | 2.7779 | 3.2378 | 3.2378 | 3.2378 | 3.2378
2024-11-07 20:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2024-09-07 19:00 | 2.1872 | 2.5494 | 2.5494 | 2.5494 | 2.5494
2024-11-07 21:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2024-09-07 20:00 | 2.1301 | 2.4828 | 2.4828 | 2.4828 | 2.4828
2024-11-07 22:00 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2024-09-07 21:00 | 1.9472 | 2.2696 | 2.2696 | 2.2696 | 2.2696
2024-11-07 23:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2024-09-07 22:00 | 1.8062 | 2.1053 | 2.1053 | 2.1053 | 2.1053
2024-11-08 | 1.4099 | 1.7539 | 2.119 | 2.1677 | 2.2164 | 2024-09-07 23:00 | 1.6995 | 1.9809 | 1.9809 | 1.9809 | 1.9809
2024-11-08 01:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-09-08 | 1.6385 | 1.9098 | 1.9098 | 1.9098 | 1.9098
2024-11-08 02:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-09-08 01:00 | 1.6538 | 1.9276 | 1.9276 | 1.9276 | 1.9276
2024-11-08 03:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-09-08 02:00 | 1.6195 | 1.8876 | 1.8876 | 1.8876 | 1.8876
2024-11-08 04:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-09-08 03:00 | 1.8786 | 2.1897 | 2.1897 | 2.1897 | 2.1897
2024-11-08 05:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-09-08 04:00 | 1.9319 | 2.2518 | 2.2518 | 2.2518 | 2.2518
2024-11-08 06:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-09-08 05:00 | 2.092 | 2.4384 | 2.4384 | 2.4384 | 2.4384
2024-11-08 07:00 | 0.83831 | 1.0428 | 1.2599 | 1.2889 | 1.3178 | 2024-09-08 06:00 | 2.2444 | 2.616 | 2.616 | 2.616 | 2.616
2024-11-08 08:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2024-09-08 07:00 | 2.3206 | 2.7049 | 2.7049 | 2.7049 | 2.7049
2024-11-08 09:00 | 1.2956 | 1.6117 | 1.9472 | 1.9919 | 2.0367 | 2024-09-08 08:00 | 2.6712 | 3.1135 | 3.1135 | 3.1135 | 3.1135
2024-11-08 10:00 | 0.26674 | 0.33181 | 0.40089 | 0.4101 | 0.41931 | 2024-09-08 09:00 | 2.393 | 2.7893 | 2.7893 | 2.7893 | 2.7893
2024-11-08 11:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2024-09-08 10:00 | 2.9036 | 3.3844 | 3.3844 | 3.3844 | 3.3844
2024-11-08 12:00 | 1.6957 | 2.1094 | 2.5485 | 2.6071 | 2.6656 | 2024-09-08 11:00 | 2.9189 | 3.4022 | 3.4022 | 3.4022 | 3.4022
2024-11-08 13:00 | 2.0577 | 2.5597 | 3.0926 | 3.1636 | 3.2347 | 2024-09-08 12:00 | 2.7207 | 3.1712 | 3.1712 | 3.1712 | 3.1712
2024-11-08 14:00 | 2.0577 | 2.5597 | 3.0926 | 3.1636 | 3.2347 | 2024-09-08 13:00 | 2.6635 | 3.1046 | 3.1046 | 3.1046 | 3.1046
2024-11-08 15:00 | 2.0005 | 2.4886 | 3.0067 | 3.0758 | 3.1448 | 2024-09-08 14:00 | 2.5378 | 2.958 | 2.958 | 2.958 | 2.958
2024-11-08 16:00 | 1.9434 | 2.4175 | 2.9208 | 2.9879 | 3.055 | 2024-09-08 15:00 | 2.8579 | 3.3311 | 3.3311 | 3.3311 | 3.3311
2024-11-08 17:00 | 1.7719 | 2.2042 | 2.6631 | 2.7242 | 2.7854 | 2024-09-08 16:00 | 2.8579 | 3.3311 | 3.3311 | 3.3311 | 3.3311
2024-11-08 18:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2024-09-08 17:00 | 2.8884 | 3.3666 | 3.3666 | 3.3666 | 3.3666
2024-11-08 19:00 | 1.2956 | 1.6117 | 1.9472 | 1.9919 | 2.0367 | 2024-09-08 18:00 | 2.6712 | 3.1135 | 3.1135 | 3.1135 | 3.1135
2024-11-08 20:00 | 1.2956 | 1.6117 | 1.9472 | 1.9919 | 2.0367 | 2024-09-08 19:00 | 2.4845 | 2.8958 | 2.8958 | 2.8958 | 2.8958
2024-11-08 21:00 | 1.2765 | 1.588 | 1.9186 | 1.9626 | 2.0067 | 2024-09-08 20:00 | 2.2787 | 2.656 | 2.656 | 2.656 | 2.656
2024-11-08 22:00 | 1.3718 | 1.7065 | 2.0617 | 2.1091 | 2.1565 | 2024-09-08 21:00 | 2.0462 | 2.3851 | 2.3851 | 2.3851 | 2.3851
2024-11-08 23:00 | 1.3527 | 1.6828 | 2.0331 | 2.0798 | 2.1265 | 2024-09-08 22:00 | 1.8329 | 2.1364 | 2.1364 | 2.1364 | 2.1364
2024-11-09 | 1.3146 | 1.6354 | 1.9758 | 2.0212 | 2.0666 | 2024-09-08 23:00 | 1.8367 | 2.1408 | 2.1408 | 2.1408 | 2.1408
2024-11-09 01:00 | 1.3527 | 1.6828 | 2.0331 | 2.0798 | 2.1265 | 2024-09-09 | 1.7643 | 2.0564 | 2.0564 | 2.0564 | 2.0564
2024-11-09 02:00 | 1.3908 | 1.7302 | 2.0904 | 2.1384 | 2.1864 | 2024-09-09 01:00 | 1.7795 | 2.0742 | 2.0742 | 2.0742 | 2.0742
2024-11-09 03:00 | 1.3337 | 1.6591 | 2.0045 | 2.0505 | 2.0966 | 2024-09-09 02:00 | 1.7795 | 2.0742 | 2.0742 | 2.0742 | 2.0742
2024-11-09 04:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-09-09 03:00 | 1.8633 | 2.1719 | 2.1719 | 2.1719 | 2.1719
2024-11-09 05:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-09-09 04:00 | 2.0386 | 2.3762 | 2.3762 | 2.3762 | 2.3762
2024-11-09 06:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-09-09 05:00 | 2.2596 | 2.6338 | 2.6338 | 2.6338 | 2.6338
2024-11-09 07:00 | 0.97168 | 1.2087 | 1.4604 | 1.4939 | 1.5275 | 2024-09-09 06:00 | 2.614 | 3.0469 | 3.0469 | 3.0469 | 3.0469
2024-11-09 08:00 | 0.81926 | 1.0191 | 1.2313 | 1.2596 | 1.2879 | 2024-09-09 07:00 | 2.8122 | 3.2778 | 3.2778 | 3.2778 | 3.2778
2024-11-09 09:00 | 0.45726 | 0.56882 | 0.68724 | 0.70303 | 0.71882 | 2024-09-09 08:00 | 2.9493 | 3.4377 | 3.4377 | 3.4377 | 3.4377
2024-11-09 10:00 | 0.362 | 0.45032 | 0.54407 | 0.55657 | 0.56907 | 2024-09-09 09:00 | 2.9417 | 3.4288 | 3.4288 | 3.4288 | 3.4288
2024-11-09 11:00 | 0.019053 | 0.023701 | 0.028635 | 0.029293 | 0.029951 | 2024-09-09 10:00 | 2.9303 | 3.4155 | 3.4155 | 3.4155 | 3.4155
2024-11-09 12:00 | 0.30484 | 0.37921 | 0.45816 | 0.46869 | 0.47921 | 2024-09-09 11:00 | 2.9379 | 3.4244 | 3.4244 | 3.4244 | 3.4244
2024-11-09 13:00 | 0.41916 | 0.52142 | 0.62997 | 0.64445 | 0.65892 | 2024-09-09 12:00 | 3.0141 | 3.5132 | 3.5132 | 3.5132 | 3.5132
2024-11-09 14:00 | 0.724 | 0.90063 | 1.0881 | 1.1131 | 1.1381 | 2024-09-09 13:00 | 2.8274 | 3.2956 | 3.2956 | 3.2956 | 3.2956
2024-11-09 15:00 | 0.57158 | 0.71103 | 0.85905 | 0.87879 | 0.89853 | 2024-09-09 14:00 | 2.9646 | 3.4555 | 3.4555 | 3.4555 | 3.4555
2024-11-09 16:00 | 0.87642 | 1.0902 | 1.3172 | 1.3475 | 1.3777 | 2024-09-09 15:00 | 3.056 | 3.5621 | 3.5621 | 3.5621 | 3.5621
2024-11-09 17:00 | 0.97168 | 1.2087 | 1.4604 | 1.4939 | 1.5275 | 2024-09-09 16:00 | 3.399 | 3.9618 | 3.9618 | 3.9618 | 3.9618
2024-11-09 18:00 | 1.2575 | 1.5643 | 1.8899 | 1.9333 | 1.9768 | 2024-09-09 17:00 | 3.5514 | 4.1395 | 4.1395 | 4.1395 | 4.1395
2024-11-09 19:00 | 1.4289 | 1.7776 | 2.1476 | 2.197 | 2.2463 | 2024-09-09 18:00 | 3.1703 | 3.6953 | 3.6953 | 3.6953 | 3.6953
2024-11-09 20:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-09-09 19:00 | 2.6369 | 3.0735 | 3.0735 | 3.0735 | 3.0735
2024-11-09 21:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-09-09 20:00 | 2.5454 | 2.9669 | 2.9669 | 2.9669 | 2.9669
2024-11-09 22:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2024-09-09 21:00 | 2.1834 | 2.545 | 2.545 | 2.545 | 2.545
2024-11-09 23:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-09-09 22:00 | 2.0843 | 2.4295 | 2.4295 | 2.4295 | 2.4295
2024-11-10 | 1.3527 | 1.6828 | 2.0331 | 2.0798 | 2.1265 | 2024-09-09 23:00 | 1.9472 | 2.2696 | 2.2696 | 2.2696 | 2.2696
2024-11-10 01:00 | 1.4289 | 1.7776 | 2.1476 | 2.197 | 2.2463 | 2024-09-10 | 1.7376 | 2.0253 | 2.0253 | 2.0253 | 2.0253
2024-11-10 02:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-09-10 01:00 | 1.6881 | 1.9676 | 1.9676 | 1.9676 | 1.9676
2024-11-10 03:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-09-10 02:00 | 1.6233 | 1.8921 | 1.8921 | 1.8921 | 1.8921
2024-11-10 04:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-09-10 03:00 | 1.8976 | 2.2119 | 2.2119 | 2.2119 | 2.2119
2024-11-10 05:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-09-10 04:00 | 2.1453 | 2.5006 | 2.5006 | 2.5006 | 2.5006
2024-11-10 06:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-09-10 05:00 | 2.4311 | 2.8337 | 2.8337 | 2.8337 | 2.8337
2024-11-10 07:00 | 1.1622 | 1.4458 | 1.7467 | 1.7869 | 1.827 | 2024-09-10 06:00 | 2.9379 | 3.4244 | 3.4244 | 3.4244 | 3.4244
2024-11-10 08:00 | 0.91452 | 1.1376 | 1.3745 | 1.4061 | 1.4376 | 2024-09-10 07:00 | 2.9798 | 3.4732 | 3.4732 | 3.4732 | 3.4732
2024-11-10 09:00 | 0.51442 | 0.63992 | 0.77315 | 0.79091 | 0.80867 | 2024-09-10 08:00 | 3.1018 | 3.6154 | 3.6154 | 3.6154 | 3.6154
2024-11-10 10:00 | 0.362 | 0.45032 | 0.54407 | 0.55657 | 0.56907 | 2024-09-10 09:00 | 3.1894 | 3.7175 | 3.7175 | 3.7175 | 3.7175
2024-11-10 11:00 | 0.019053 | 0.023701 | 0.028635 | 0.029293 | 0.029951 | 2024-09-10 10:00 | 2.8693 | 3.3444 | 3.3444 | 3.3444 | 3.3444
2024-11-10 12:00 | 0.45726 | 0.56882 | 0.68724 | 0.70303 | 0.71882 | 2024-09-10 11:00 | 2.9798 | 3.4732 | 3.4732 | 3.4732 | 3.4732
2024-11-10 13:00 | 0.51442 | 0.63992 | 0.77315 | 0.79091 | 0.80867 | 2024-09-10 12:00 | 3.0865 | 3.5976 | 3.5976 | 3.5976 | 3.5976
2024-11-10 14:00 | 0.362 | 0.45032 | 0.54407 | 0.55657 | 0.56907 | 2024-09-10 13:00 | 2.9227 | 3.4066 | 3.4066 | 3.4066 | 3.4066
2024-11-10 15:00 | 0.93358 | 1.1613 | 1.4031 | 1.4354 | 1.4676 | 2024-09-10 14:00 | 3.1284 | 3.6465 | 3.6465 | 3.6465 | 3.6465
2024-11-10 16:00 | 0.055152 | 0.068608 | 0.082891 | 0.084796 | 0.0867 | 2024-09-10 15:00 | 3.1589 | 3.682 | 3.682 | 3.682 | 3.682
2024-11-10 17:00 | 1.1432 | 1.4221 | 1.7181 | 1.7576 | 1.7971 | 2024-09-10 16:00 | 3.6009 | 4.1972 | 4.1972 | 4.1972 | 4.1972
2024-11-10 18:00 | 1.8672 | 2.3227 | 2.8062 | 2.8707 | 2.9352 | 2024-09-10 17:00 | 3.6009 | 4.1972 | 4.1972 | 4.1972 | 4.1972
2024-11-10 19:00 | 1.9053 | 2.3701 | 2.8635 | 2.9293 | 2.9951 | 2024-09-10 18:00 | 2.9341 | 3.4199 | 3.4199 | 3.4199 | 3.4199
2024-11-10 20:00 | 1.7909 | 2.2279 | 2.6917 | 2.7535 | 2.8154 | 2024-09-10 19:00 | 2.6407 | 3.078 | 3.078 | 3.078 | 3.078
2024-11-10 21:00 | 1.7719 | 2.2042 | 2.6631 | 2.7242 | 2.7854 | 2024-09-10 20:00 | 2.6483 | 3.0868 | 3.0868 | 3.0868 | 3.0868
2024-11-10 22:00 | 1.9434 | 2.4175 | 2.9208 | 2.9879 | 3.055 | 2024-09-10 21:00 | 2.233 | 2.6027 | 2.6027 | 2.6027 | 2.6027
2024-11-10 23:00 | 1.7909 | 2.2279 | 2.6917 | 2.7535 | 2.8154 | 2024-09-10 22:00 | 1.9434 | 2.2652 | 2.2652 | 2.2652 | 2.2652
2024-11-11 | 1.81 | 2.2516 | 2.7203 | 2.7828 | 2.8453 | 2024-09-10 23:00 | 1.9472 | 2.2696 | 2.2696 | 2.2696 | 2.2696
2024-11-11 01:00 | 1.6957 | 2.1094 | 2.5485 | 2.6071 | 2.6656 | 2024-09-11 | 1.7871 | 2.0831 | 2.0831 | 2.0831 | 2.0831
2024-11-11 02:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2024-09-11 01:00 | 1.8214 | 2.123 | 2.123 | 2.123 | 2.123
2024-11-11 03:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2024-09-11 02:00 | 1.8176 | 2.1186 | 2.1186 | 2.1186 | 2.1186
2024-11-11 04:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2024-09-11 03:00 | 1.8595 | 2.1674 | 2.1674 | 2.1674 | 2.1674
2024-11-11 05:00 | 1.7528 | 2.1805 | 2.6344 | 2.695 | 2.7555 | 2024-09-11 04:00 | 2.1377 | 2.4917 | 2.4917 | 2.4917 | 2.4917
2024-11-11 06:00 | 1.8481 | 2.299 | 2.7776 | 2.8414 | 2.9052 | 2024-09-11 05:00 | 2.2406 | 2.6116 | 2.6116 | 2.6116 | 2.6116
2024-11-11 07:00 | 2.191 | 2.7256 | 3.293 | 3.3687 | 3.4444 | 2024-09-11 06:00 | 2.7779 | 3.2378 | 3.2378 | 3.2378 | 3.2378
2024-11-11 08:00 | 2.3816 | 2.9626 | 3.5794 | 3.6616 | 3.7439 | 2024-09-11 07:00 | 2.9646 | 3.4555 | 3.4555 | 3.4555 | 3.4555
2024-11-11 09:00 | 2.3816 | 2.9626 | 3.5794 | 3.6616 | 3.7439 | 2024-09-11 08:00 | 3.3494 | 3.9041 | 3.9041 | 3.9041 | 3.9041
2024-11-11 10:00 | 2.9913 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2024-09-11 09:00 | 3.4257 | 3.9929 | 3.9929 | 3.9929 | 3.9929
2024-11-11 11:00 | 3.3342 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2024-09-11 10:00 | 3.277 | 3.8197 | 3.8197 | 3.8197 | 3.8197
2024-11-11 12:00 | 2.4959 | 3.1048 | 3.7512 | 3.8374 | 3.9236 | 2024-09-11 11:00 | 3.2313 | 3.7664 | 3.7664 | 3.7664 | 3.7664
2024-11-11 13:00 | 1.6957 | 2.1094 | 2.5485 | 2.6071 | 2.6656 | 2024-09-11 12:00 | 3.4218 | 3.9885 | 3.9885 | 3.9885 | 3.9885
2024-11-11 14:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2024-09-11 13:00 | 3.319 | 3.8685 | 3.8685 | 3.8685 | 3.8685
2024-11-11 15:00 | 2.3816 | 2.9626 | 3.5794 | 3.6616 | 3.7439 | 2024-09-11 14:00 | 3.2466 | 3.7841 | 3.7841 | 3.7841 | 3.7841
2024-11-11 16:00 | 2.0958 | 2.6071 | 3.1499 | 3.2222 | 3.2946 | 2024-09-11 15:00 | 3.1742 | 3.6998 | 3.6998 | 3.6998 | 3.6998
2024-11-11 17:00 | 2.3244 | 2.8915 | 3.4935 | 3.5737 | 3.654 | 2024-09-11 16:00 | 3.4676 | 4.0418 | 4.0418 | 4.0418 | 4.0418
2024-11-11 18:00 | 2.4387 | 3.0337 | 3.6653 | 3.7495 | 3.8337 | 2024-09-11 17:00 | 3.2427 | 3.7797 | 3.7797 | 3.7797 | 3.7797
2024-11-11 19:00 | 1.8672 | 2.3227 | 2.8062 | 2.8707 | 2.9352 | 2024-09-11 18:00 | 3.1018 | 3.6154 | 3.6154 | 3.6154 | 3.6154
2024-11-11 20:00 | 1.8481 | 2.299 | 2.7776 | 2.8414 | 2.9052 | 2024-09-11 19:00 | 2.6788 | 3.1224 | 3.1224 | 3.1224 | 3.1224
2024-11-11 21:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2024-09-11 20:00 | 2.4959 | 2.9092 | 2.9092 | 2.9092 | 2.9092
2024-11-11 22:00 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2024-09-11 21:00 | 2.1796 | 2.5405 | 2.5405 | 2.5405 | 2.5405
2024-11-11 23:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2024-09-11 22:00 | 1.9738 | 2.3007 | 2.3007 | 2.3007 | 2.3007
2024-11-12 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-09-11 23:00 | 1.9662 | 2.2918 | 2.2918 | 2.2918 | 2.2918
2024-11-12 01:00 | 1.4289 | 1.7776 | 2.1476 | 2.197 | 2.2463 | 2024-09-12 | 1.7147 | 1.9987 | 1.9987 | 1.9987 | 1.9987
2024-11-12 02:00 | 1.4289 | 1.7776 | 2.1476 | 2.197 | 2.2463 | 2024-09-12 01:00 | 1.6995 | 1.9809 | 1.9809 | 1.9809 | 1.9809
2024-11-12 03:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-09-12 02:00 | 1.7528 | 2.0431 | 2.0431 | 2.0431 | 2.0431
2024-11-12 04:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-09-12 03:00 | 1.81 | 2.1097 | 2.1097 | 2.1097 | 2.1097
2024-11-12 05:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2024-09-12 04:00 | 2.0005 | 2.3318 | 2.3318 | 2.3318 | 2.3318
2024-11-12 06:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2024-09-12 05:00 | 2.332 | 2.7182 | 2.7182 | 2.7182 | 2.7182
2024-11-12 07:00 | 2.2673 | 2.8204 | 3.4076 | 3.4859 | 3.5642 | 2024-09-12 06:00 | 2.7169 | 3.1668 | 3.1668 | 3.1668 | 3.1668
2024-11-12 08:00 | 2.1529 | 2.6782 | 3.2358 | 3.3101 | 3.3845 | 2024-09-12 07:00 | 2.9951 | 3.491 | 3.491 | 3.491 | 3.491
2024-11-12 09:00 | 2.3054 | 2.8678 | 3.4648 | 3.5445 | 3.6241 | 2024-09-12 08:00 | 3.2923 | 3.8374 | 3.8374 | 3.8374 | 3.8374
2024-11-12 10:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2024-09-12 09:00 | 3.5666 | 4.1572 | 4.1572 | 4.1572 | 4.1572
2024-11-12 11:00 | 1.4099 | 1.7539 | 2.119 | 2.1677 | 2.2164 | 2024-09-12 10:00 | 3.8639 | 4.5037 | 4.5037 | 4.5037 | 4.5037
2024-11-12 12:00 | 1.8862 | 2.3464 | 2.8349 | 2.9 | 2.9651 | 2024-09-12 11:00 | 4.062 | 4.7346 | 4.7346 | 4.7346 | 4.7346
2024-11-12 13:00 | 2.3435 | 2.9152 | 3.5221 | 3.603 | 3.684 | 2024-09-12 12:00 | 3.9858 | 4.6458 | 4.6458 | 4.6458 | 4.6458
2024-11-12 14:00 | 2.6102 | 3.247 | 3.923 | 4.0131 | 4.1033 | 2024-09-12 13:00 | 3.8791 | 4.5214 | 4.5214 | 4.5214 | 4.5214
2024-11-12 15:00 | 2.3625 | 2.9389 | 3.5508 | 3.6323 | 3.7139 | 2024-09-12 14:00 | 3.5285 | 4.1128 | 4.1128 | 4.1128 | 4.1128
2024-11-12 16:00 | 2.2482 | 2.7967 | 3.3789 | 3.4566 | 3.5342 | 2024-09-12 15:00 | 3.6886 | 4.2994 | 4.2994 | 4.2994 | 4.2994
2024-11-12 17:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-09-12 16:00 | 3.8143 | 4.4459 | 4.4459 | 4.4459 | 4.4459
2024-11-12 18:00 | 2.0386 | 2.536 | 3.064 | 3.1344 | 3.2047 | 2024-09-12 17:00 | 3.6848 | 4.2949 | 4.2949 | 4.2949 | 4.2949
2024-11-12 19:00 | 1.829 | 2.2753 | 2.749 | 2.8121 | 2.8753 | 2024-09-12 18:00 | 3.4638 | 4.0373 | 4.0373 | 4.0373 | 4.0373
2024-11-12 20:00 | 1.7528 | 2.1805 | 2.6344 | 2.695 | 2.7555 | 2024-09-12 19:00 | 2.7359 | 3.189 | 3.189 | 3.189 | 3.189
2024-11-12 21:00 | 1.7528 | 2.1805 | 2.6344 | 2.695 | 2.7555 | 2024-09-12 20:00 | 2.5683 | 2.9936 | 2.9936 | 2.9936 | 2.9936
2024-11-12 22:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2024-09-12 21:00 | 2.2444 | 2.616 | 2.616 | 2.616 | 2.616
2024-11-12 23:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2024-09-12 22:00 | 1.8786 | 2.1897 | 2.1897 | 2.1897 | 2.1897
2024-11-13 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2024-09-12 23:00 | 1.9548 | 2.2785 | 2.2785 | 2.2785 | 2.2785
2024-11-13 01:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-09-13 | 1.7147 | 1.9987 | 1.9987 | 1.9987 | 1.9987
2024-11-13 02:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2024-09-13 01:00 | 1.7033 | 1.9853 | 1.9853 | 1.9853 | 1.9853
2024-11-13 03:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-09-13 02:00 | 1.7109 | 1.9942 | 1.9942 | 1.9942 | 1.9942
2024-11-13 04:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-09-13 03:00 | 1.9357 | 2.2563 | 2.2563 | 2.2563 | 2.2563
2024-11-13 05:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-09-13 04:00 | 2.1034 | 2.4517 | 2.4517 | 2.4517 | 2.4517
2024-11-13 06:00 | 1.7147 | 2.1331 | 2.5772 | 2.6364 | 2.6956 | 2024-09-13 05:00 | 2.4959 | 2.9092 | 2.9092 | 2.9092 | 2.9092
2024-11-13 07:00 | 0.91452 | 1.1376 | 1.3745 | 1.4061 | 1.4376 | 2024-09-13 06:00 | 2.915 | 3.3977 | 3.3977 | 3.3977 | 3.3977
2024-11-13 08:00 | 0.68589 | 0.85323 | 1.0309 | 1.0545 | 1.0782 | 2024-09-13 07:00 | 3.2618 | 3.8019 | 3.8019 | 3.8019 | 3.8019
2024-11-13 09:00 | 0.66684 | 0.82953 | 1.0022 | 1.0253 | 1.0483 | 2024-09-13 08:00 | 3.3037 | 3.8508 | 3.8508 | 3.8508 | 3.8508
2024-11-13 10:00 | 0.64779 | 0.80583 | 0.97359 | 0.99596 | 1.0183 | 2024-09-13 09:00 | 3.277 | 3.8197 | 3.8197 | 3.8197 | 3.8197
2024-11-13 11:00 | 0.97168 | 1.2087 | 1.4604 | 1.4939 | 1.5275 | 2024-09-13 10:00 | 3.0865 | 3.5976 | 3.5976 | 3.5976 | 3.5976
2024-11-13 12:00 | 2.5149 | 3.1285 | 3.7798 | 3.8667 | 3.9535 | 2024-09-13 11:00 | 3.0484 | 3.5532 | 3.5532 | 3.5532 | 3.5532
2024-11-13 13:00 | 3.0484 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2024-09-13 12:00 | 3.1361 | 3.6553 | 3.6553 | 3.6553 | 3.6553
2024-11-13 14:00 | 3.1437 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2024-09-13 13:00 | 3.0637 | 3.571 | 3.571 | 3.571 | 3.571
2024-11-13 15:00 | 2.5911 | 3.2233 | 3.8944 | 3.9838 | 4.0733 | 2024-09-13 14:00 | 3.1361 | 3.6553 | 3.6553 | 3.6553 | 3.6553
2024-11-13 16:00 | 2.915 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2024-09-13 15:00 | 3.117 | 3.6331 | 3.6331 | 3.6331 | 3.6331
2024-11-13 17:00 | 2.8769 | 3.5788 | 4.3239 | 4.4232 | 4.5226 | 2024-09-13 16:00 | 3.5019 | 4.0817 | 4.0817 | 4.0817 | 4.0817
2024-11-13 18:00 | 2.2673 | 2.8204 | 3.4076 | 3.4859 | 3.5642 | 2024-09-13 17:00 | 3.6086 | 4.2061 | 4.2061 | 4.2061 | 4.2061
2024-11-13 19:00 | 2.1148 | 2.6308 | 3.1785 | 3.2515 | 3.3245 | 2024-09-13 18:00 | 3.4904 | 4.0684 | 4.0684 | 4.0684 | 4.0684
2024-11-13 20:00 | 2.0196 | 2.5123 | 3.0353 | 3.1051 | 3.1748 | 2024-09-13 19:00 | 3.0675 | 3.5754 | 3.5754 | 3.5754 | 3.5754
2024-11-13 21:00 | 1.9624 | 2.4412 | 2.9494 | 3.0172 | 3.0849 | 2024-09-13 20:00 | 2.8884 | 3.3666 | 3.3666 | 3.3666 | 3.3666
2024-11-13 22:00 | 1.8481 | 2.299 | 2.7776 | 2.8414 | 2.9052 | 2024-09-13 21:00 | 2.2634 | 2.6382 | 2.6382 | 2.6382 | 2.6382
2024-11-13 23:00 | 1.829 | 2.2753 | 2.749 | 2.8121 | 2.8753 | 2024-09-13 22:00 | 2.0234 | 2.3584 | 2.3584 | 2.3584 | 2.3584
2024-11-14 | 1.6957 | 2.1094 | 2.5485 | 2.6071 | 2.6656 | 2024-09-13 23:00 | 1.9243 | 2.243 | 2.243 | 2.243 | 2.243
2024-11-14 01:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2024-09-14 | 1.7757 | 2.0697 | 2.0697 | 2.0697 | 2.0697
2024-11-14 02:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2024-09-14 01:00 | 1.7262 | 2.012 | 2.012 | 2.012 | 2.012
2024-11-14 03:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2024-09-14 02:00 | 1.6614 | 1.9365 | 1.9365 | 1.9365 | 1.9365
2024-11-14 04:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2024-09-14 03:00 | 1.8367 | 2.1408 | 2.1408 | 2.1408 | 2.1408
2024-11-14 05:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2024-09-14 04:00 | 2.0005 | 2.3318 | 2.3318 | 2.3318 | 2.3318
2024-11-14 06:00 | 1.7528 | 2.1805 | 2.6344 | 2.695 | 2.7555 | 2024-09-14 05:00 | 2.2863 | 2.6649 | 2.6649 | 2.6649 | 2.6649
2024-11-14 07:00 | 2.4006 | 2.9863 | 3.608 | 3.6909 | 3.7738 | 2024-09-14 06:00 | 2.3435 | 2.7315 | 2.7315 | 2.7315 | 2.7315
2024-11-14 08:00 | 2.553 | 3.1759 | 3.8371 | 3.9253 | 4.0134 | 2024-09-14 07:00 | 2.4883 | 2.9003 | 2.9003 | 2.9003 | 2.9003
2024-11-14 09:00 | 2.8388 | 3.5314 | 4.2666 | 4.3647 | 4.4627 | 2024-09-14 08:00 | 2.7702 | 3.229 | 3.229 | 3.229 | 3.229
2024-11-14 10:00 | 2.7817 | 3.4603 | 4.1807 | 4.2768 | 4.3728 | 2024-09-14 09:00 | 2.8884 | 3.3666 | 3.3666 | 3.3666 | 3.3666
2024-11-14 11:00 | 1.7147 | 2.1331 | 2.5772 | 2.6364 | 2.6956 | 2024-09-14 10:00 | 2.7207 | 3.1712 | 3.1712 | 3.1712 | 3.1712
2024-11-14 12:00 | 2.0767 | 2.5834 | 3.1212 | 3.1929 | 3.2646 | 2024-09-14 11:00 | 2.5073 | 2.9225 | 2.9225 | 2.9225 | 2.9225
2024-11-14 13:00 | 2.0005 | 2.4886 | 3.0067 | 3.0758 | 3.1448 | 2024-09-14 12:00 | 2.5454 | 2.9669 | 2.9669 | 2.9669 | 2.9669
2024-11-14 14:00 | 1.9053 | 2.3701 | 2.8635 | 2.9293 | 2.9951 | 2024-09-14 13:00 | 2.6597 | 3.1002 | 3.1002 | 3.1002 | 3.1002
2024-11-14 15:00 | 2.2291 | 2.773 | 3.3503 | 3.4273 | 3.5043 | 2024-09-14 14:00 | 2.8807 | 3.3578 | 3.3578 | 3.3578 | 3.3578
2024-11-14 16:00 | 2.3054 | 2.8678 | 3.4648 | 3.5445 | 3.6241 | 2024-09-14 15:00 | 2.9608 | 3.451 | 3.451 | 3.451 | 3.451
2024-11-14 17:00 | 2.2863 | 2.8441 | 3.4362 | 3.5152 | 3.5941 | 2024-09-14 16:00 | 3.0217 | 3.5221 | 3.5221 | 3.5221 | 3.5221
2024-11-14 18:00 | 2.0196 | 2.5123 | 3.0353 | 3.1051 | 3.1748 | 2024-09-14 17:00 | 3.0446 | 3.5487 | 3.5487 | 3.5487 | 3.5487
2024-11-14 19:00 | 1.9243 | 2.3938 | 2.8921 | 2.9586 | 3.025 | 2024-09-14 18:00 | 2.9227 | 3.4066 | 3.4066 | 3.4066 | 3.4066
2024-11-14 20:00 | 1.8481 | 2.299 | 2.7776 | 2.8414 | 2.9052 | 2024-09-14 19:00 | 2.252 | 2.6249 | 2.6249 | 2.6249 | 2.6249
2024-11-14 21:00 | 1.7528 | 2.1805 | 2.6344 | 2.695 | 2.7555 | 2024-09-14 20:00 | 2.1072 | 2.4561 | 2.4561 | 2.4561 | 2.4561
2024-11-14 22:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2024-09-14 21:00 | 1.9396 | 2.2607 | 2.2607 | 2.2607 | 2.2607
2024-11-14 23:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2024-09-14 22:00 | 1.9548 | 2.2785 | 2.2785 | 2.2785 | 2.2785
2024-11-15 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-09-14 23:00 | 1.7528 | 2.0431 | 2.0431 | 2.0431 | 2.0431
2024-11-15 01:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-09-15 | 1.6919 | 1.972 | 1.972 | 1.972 | 1.972
2024-11-15 02:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-09-15 01:00 | 1.6614 | 1.9365 | 1.9365 | 1.9365 | 1.9365
2024-11-15 03:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-09-15 02:00 | 1.6804 | 1.9587 | 1.9587 | 1.9587 | 1.9587
2024-11-15 04:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-09-15 03:00 | 1.8557 | 2.163 | 2.163 | 2.163 | 2.163
2024-11-15 05:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2024-09-15 04:00 | 1.9357 | 2.2563 | 2.2563 | 2.2563 | 2.2563
2024-11-15 06:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2024-09-15 05:00 | 2.2863 | 2.6649 | 2.6649 | 2.6649 | 2.6649
2024-11-15 07:00 | 0.59063 | 0.73473 | 0.88769 | 0.90808 | 0.92848 | 2024-09-15 06:00 | 2.3015 | 2.6827 | 2.6827 | 2.6827 | 2.6827
2024-11-15 08:00 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2024-09-15 07:00 | 2.2253 | 2.5938 | 2.5938 | 2.5938 | 2.5938
2024-11-15 09:00 | 1.4099 | 1.7539 | 2.119 | 2.1677 | 2.2164 | 2024-09-15 08:00 | 2.4311 | 2.8337 | 2.8337 | 2.8337 | 2.8337
2024-11-15 10:00 | 0.51442 | 0.63992 | 0.77315 | 0.79091 | 0.80867 | 2024-09-15 09:00 | 2.4806 | 2.8914 | 2.8914 | 2.8914 | 2.8914
2024-11-15 11:00 | 1.7909 | 2.2279 | 2.6917 | 2.7535 | 2.8154 | 2024-09-15 10:00 | 2.5111 | 2.9269 | 2.9269 | 2.9269 | 2.9269
2024-11-15 12:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2024-09-15 11:00 | 2.5378 | 2.958 | 2.958 | 2.958 | 2.958
2024-11-15 13:00 | 1.8862 | 2.3464 | 2.8349 | 2.9 | 2.9651 | 2024-09-15 12:00 | 2.6483 | 3.0868 | 3.0868 | 3.0868 | 3.0868
2024-11-15 14:00 | 2.0196 | 2.5123 | 3.0353 | 3.1051 | 3.1748 | 2024-09-15 13:00 | 2.8617 | 3.3356 | 3.3356 | 3.3356 | 3.3356
2024-11-15 15:00 | 1.9434 | 2.4175 | 2.9208 | 2.9879 | 3.055 | 2024-09-15 14:00 | 3.1665 | 3.6909 | 3.6909 | 3.6909 | 3.6909
2024-11-15 16:00 | 1.9243 | 2.3938 | 2.8921 | 2.9586 | 3.025 | 2024-09-15 15:00 | 3.0484 | 3.5532 | 3.5532 | 3.5532 | 3.5532
2024-11-15 17:00 | 2.0005 | 2.4886 | 3.0067 | 3.0758 | 3.1448 | 2024-09-15 16:00 | 2.9112 | 3.3933 | 3.3933 | 3.3933 | 3.3933
2024-11-15 18:00 | 1.81 | 2.2516 | 2.7203 | 2.7828 | 2.8453 | 2024-09-15 17:00 | 2.9493 | 3.4377 | 3.4377 | 3.4377 | 3.4377
2024-11-15 19:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2024-09-15 18:00 | 2.755 | 3.2112 | 3.2112 | 3.2112 | 3.2112
2024-11-15 20:00 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2024-09-15 19:00 | 2.5187 | 2.9358 | 2.9358 | 2.9358 | 2.9358
2024-11-15 21:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-09-15 20:00 | 2.3054 | 2.6871 | 2.6871 | 2.6871 | 2.6871
2024-11-15 22:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2024-09-15 21:00 | 1.9662 | 2.2918 | 2.2918 | 2.2918 | 2.2918
2024-11-15 23:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-09-15 22:00 | 1.8405 | 2.1452 | 2.1452 | 2.1452 | 2.1452
2024-11-16 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-09-15 23:00 | 1.7643 | 2.0564 | 2.0564 | 2.0564 | 2.0564
2024-11-16 01:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-09-16 | 1.7643 | 2.0564 | 2.0564 | 2.0564 | 2.0564
2024-11-16 02:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-09-16 01:00 | 1.7033 | 1.9853 | 1.9853 | 1.9853 | 1.9853
2024-11-16 03:00 | 1.4289 | 1.7776 | 2.1476 | 2.197 | 2.2463 | 2024-09-16 02:00 | 1.7719 | 2.0653 | 2.0653 | 2.0653 | 2.0653
2024-11-16 04:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-09-16 03:00 | 1.9091 | 2.2252 | 2.2252 | 2.2252 | 2.2252
2024-11-16 05:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-09-16 04:00 | 2.1034 | 2.4517 | 2.4517 | 2.4517 | 2.4517
2024-11-16 06:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2024-09-16 05:00 | 2.3892 | 2.7848 | 2.7848 | 2.7848 | 2.7848
2024-11-16 07:00 | 1.2384 | 1.5406 | 1.8613 | 1.904 | 1.9468 | 2024-09-16 06:00 | 2.8769 | 3.3533 | 3.3533 | 3.3533 | 3.3533
2024-11-16 08:00 | 0.93358 | 1.1613 | 1.4031 | 1.4354 | 1.4676 | 2024-09-16 07:00 | 3.3837 | 3.944 | 3.944 | 3.944 | 3.944
2024-11-16 09:00 | 0.60968 | 0.75843 | 0.91632 | 0.93738 | 0.95843 | 2024-09-16 08:00 | 3.3304 | 3.8819 | 3.8819 | 3.8819 | 3.8819
2024-11-16 10:00 | 0.47631 | 0.59252 | 0.71588 | 0.73232 | 0.74877 | 2024-09-16 09:00 | 3.7534 | 4.3749 | 4.3749 | 4.3749 | 4.3749
2024-11-16 11:00 | 0.30484 | 0.37921 | 0.45816 | 0.46869 | 0.47921 | 2024-09-16 10:00 | 3.4066 | 3.9707 | 3.9707 | 3.9707 | 3.9707
2024-11-16 12:00 | 0.53347 | 0.66362 | 0.80178 | 0.8202 | 0.83862 | 2024-09-16 11:00 | 3.0789 | 3.5887 | 3.5887 | 3.5887 | 3.5887
2024-11-16 13:00 | 0.47631 | 0.59252 | 0.71588 | 0.73232 | 0.74877 | 2024-09-16 12:00 | 3.1551 | 3.6776 | 3.6776 | 3.6776 | 3.6776
2024-11-16 14:00 | 0.80021 | 0.99544 | 1.2027 | 1.2303 | 1.2579 | 2024-09-16 13:00 | 3.1475 | 3.6687 | 3.6687 | 3.6687 | 3.6687
2024-11-16 15:00 | 0.68589 | 0.85323 | 1.0309 | 1.0545 | 1.0782 | 2024-09-16 14:00 | 3.2085 | 3.7397 | 3.7397 | 3.7397 | 3.7397
2024-11-16 16:00 | 0.87642 | 1.0902 | 1.3172 | 1.3475 | 1.3777 | 2024-09-16 15:00 | 3.5514 | 4.1395 | 4.1395 | 4.1395 | 4.1395
2024-11-16 17:00 | 1.1432 | 1.4221 | 1.7181 | 1.7576 | 1.7971 | 2024-09-16 16:00 | 3.559 | 4.1483 | 4.1483 | 4.1483 | 4.1483
2024-11-16 18:00 | 1.3337 | 1.6591 | 2.0045 | 2.0505 | 2.0966 | 2024-09-16 17:00 | 3.6467 | 4.2505 | 4.2505 | 4.2505 | 4.2505
2024-11-16 19:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-09-16 18:00 | 3.1246 | 3.642 | 3.642 | 3.642 | 3.642
2024-11-16 20:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2024-09-16 19:00 | 2.6826 | 3.1268 | 3.1268 | 3.1268 | 3.1268
2024-11-16 21:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2024-09-16 20:00 | 2.3816 | 2.7759 | 2.7759 | 2.7759 | 2.7759
2024-11-16 22:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2024-09-16 21:00 | 2.1148 | 2.465 | 2.465 | 2.465 | 2.465
2024-11-16 23:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2024-09-16 22:00 | 1.9396 | 2.2607 | 2.2607 | 2.2607 | 2.2607
2024-11-17 | 1.4099 | 1.7539 | 2.119 | 2.1677 | 2.2164 | 2024-09-16 23:00 | 1.9357 | 2.2563 | 2.2563 | 2.2563 | 2.2563
2024-11-17 01:00 | 1.4289 | 1.7776 | 2.1476 | 2.197 | 2.2463 | 2024-09-17 | 1.6728 | 1.9498 | 1.9498 | 1.9498 | 1.9498
2024-11-17 02:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-09-17 01:00 | 1.7185 | 2.0031 | 2.0031 | 2.0031 | 2.0031
2024-11-17 03:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-09-17 02:00 | 1.6652 | 1.9409 | 1.9409 | 1.9409 | 1.9409
2024-11-17 04:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-09-17 03:00 | 1.9014 | 2.2163 | 2.2163 | 2.2163 | 2.2163
2024-11-17 05:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-09-17 04:00 | 2.0729 | 2.4162 | 2.4162 | 2.4162 | 2.4162
2024-11-17 06:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2024-09-17 05:00 | 2.4616 | 2.8692 | 2.8692 | 2.8692 | 2.8692
2024-11-17 07:00 | 1.0479 | 1.3035 | 1.5749 | 1.6111 | 1.6473 | 2024-09-17 06:00 | 2.7817 | 3.2423 | 3.2423 | 3.2423 | 3.2423
2024-11-17 08:00 | 0.89547 | 1.1139 | 1.3458 | 1.3768 | 1.4077 | 2024-09-17 07:00 | 3.2199 | 3.7531 | 3.7531 | 3.7531 | 3.7531
2024-11-17 09:00 | 0.41916 | 0.52142 | 0.62997 | 0.64445 | 0.65892 | 2024-09-17 08:00 | 3.1703 | 3.6953 | 3.6953 | 3.6953 | 3.6953
2024-11-17 10:00 | 0.62873 | 0.78213 | 0.94496 | 0.96667 | 0.98838 | 2024-09-17 09:00 | 3.1665 | 3.6909 | 3.6909 | 3.6909 | 3.6909
2024-11-17 11:00 | 0.24768 | 0.30811 | 0.37226 | 0.38081 | 0.38936 | 2024-09-17 10:00 | 3.037 | 3.5399 | 3.5399 | 3.5399 | 3.5399
2024-11-17 12:00 | 0.62873 | 0.78213 | 0.94496 | 0.96667 | 0.98838 | 2024-09-17 11:00 | 3.0141 | 3.5132 | 3.5132 | 3.5132 | 3.5132
2024-11-17 13:00 | 0.22863 | 0.28441 | 0.34362 | 0.35152 | 0.35941 | 2024-09-17 12:00 | 2.9646 | 3.4555 | 3.4555 | 3.4555 | 3.4555
2024-11-17 14:00 | 0.07621 | 0.094804 | 0.11454 | 0.11717 | 0.1198 | 2024-09-17 13:00 | 3.1018 | 3.6154 | 3.6154 | 3.6154 | 3.6154
2024-11-17 15:00 | 0.7621 | 0.94804 | 1.1454 | 1.1717 | 1.198 | 2024-09-17 14:00 | 2.9036 | 3.3844 | 3.3844 | 3.3844 | 3.3844
2024-11-17 16:00 | 0.063174 | 0.078587 | 0.094948 | 0.097129 | 0.099311 | 2024-09-17 15:00 | 3.0255 | 3.5265 | 3.5265 | 3.5265 | 3.5265
2024-11-17 17:00 | 1.105 | 1.3747 | 1.6608 | 1.699 | 1.7372 | 2024-09-17 16:00 | 3.4142 | 3.9796 | 3.9796 | 3.9796 | 3.9796
2024-11-17 18:00 | 1.7338 | 2.1568 | 2.6058 | 2.6657 | 2.7255 | 2024-09-17 17:00 | 3.6238 | 4.2239 | 4.2239 | 4.2239 | 4.2239
2024-11-17 19:00 | 1.81 | 2.2516 | 2.7203 | 2.7828 | 2.8453 | 2024-09-17 18:00 | 3.2313 | 3.7664 | 3.7664 | 3.7664 | 3.7664
2024-11-17 20:00 | 1.7909 | 2.2279 | 2.6917 | 2.7535 | 2.8154 | 2024-09-17 19:00 | 2.9608 | 3.451 | 3.451 | 3.451 | 3.451
2024-11-17 21:00 | 1.7909 | 2.2279 | 2.6917 | 2.7535 | 2.8154 | 2024-09-17 20:00 | 2.4959 | 2.9092 | 2.9092 | 2.9092 | 2.9092
2024-11-17 22:00 | 1.829 | 2.2753 | 2.749 | 2.8121 | 2.8753 | 2024-09-17 21:00 | 2.1682 | 2.5272 | 2.5272 | 2.5272 | 2.5272
2024-11-17 23:00 | 1.7528 | 2.1805 | 2.6344 | 2.695 | 2.7555 | 2024-09-17 22:00 | 1.9777 | 2.3051 | 2.3051 | 2.3051 | 2.3051
2024-11-18 | 1.7528 | 2.1805 | 2.6344 | 2.695 | 2.7555 | 2024-09-17 23:00 | 1.9053 | 2.2207 | 2.2207 | 2.2207 | 2.2207
2024-11-18 01:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2024-09-18 | 1.7033 | 1.9853 | 1.9853 | 1.9853 | 1.9853
2024-11-18 02:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2024-09-18 01:00 | 1.7109 | 1.9942 | 1.9942 | 1.9942 | 1.9942
2024-11-18 03:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2024-09-18 02:00 | 1.7071 | 1.9898 | 1.9898 | 1.9898 | 1.9898
2024-11-18 04:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-09-18 03:00 | 1.8748 | 2.1852 | 2.1852 | 2.1852 | 2.1852
2024-11-18 05:00 | 1.7338 | 2.1568 | 2.6058 | 2.6657 | 2.7255 | 2024-09-18 04:00 | 2.2177 | 2.5849 | 2.5849 | 2.5849 | 2.5849
2024-11-18 06:00 | 1.8481 | 2.299 | 2.7776 | 2.8414 | 2.9052 | 2024-09-18 05:00 | 2.3854 | 2.7804 | 2.7804 | 2.7804 | 2.7804
2024-11-18 07:00 | 2.4006 | 2.9863 | 3.608 | 3.6909 | 3.7738 | 2024-09-18 06:00 | 2.5835 | 3.0113 | 3.0113 | 3.0113 | 3.0113
2024-11-18 08:00 | 2.3625 | 2.9389 | 3.5508 | 3.6323 | 3.7139 | 2024-09-18 07:00 | 2.9913 | 3.4866 | 3.4866 | 3.4866 | 3.4866
2024-11-18 09:00 | 2.0958 | 2.6071 | 3.1499 | 3.2222 | 3.2946 | 2024-09-18 08:00 | 3.1018 | 3.6154 | 3.6154 | 3.6154 | 3.6154
2024-11-18 10:00 | 2.4959 | 3.1048 | 3.7512 | 3.8374 | 3.9236 | 2024-09-18 09:00 | 3.0979 | 3.6109 | 3.6109 | 3.6109 | 3.6109
2024-11-18 11:00 | 2.8579 | 3.5551 | 4.2953 | 4.3939 | 4.4926 | 2024-09-18 10:00 | 2.9913 | 3.4866 | 3.4866 | 3.4866 | 3.4866
2024-11-18 12:00 | 2.4768 | 3.0811 | 3.7226 | 3.8081 | 3.8936 | 2024-09-18 11:00 | 2.8465 | 3.3178 | 3.3178 | 3.3178 | 3.3178
2024-11-18 13:00 | 1.7719 | 2.2042 | 2.6631 | 2.7242 | 2.7854 | 2024-09-18 12:00 | 2.9341 | 3.4199 | 3.4199 | 3.4199 | 3.4199
2024-11-18 14:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-09-18 13:00 | 3.0217 | 3.5221 | 3.5221 | 3.5221 | 3.5221
2024-11-18 15:00 | 1.9434 | 2.4175 | 2.9208 | 2.9879 | 3.055 | 2024-09-18 14:00 | 2.8807 | 3.3578 | 3.3578 | 3.3578 | 3.3578
2024-11-18 16:00 | 2.0577 | 2.5597 | 3.0926 | 3.1636 | 3.2347 | 2024-09-18 15:00 | 3.0789 | 3.5887 | 3.5887 | 3.5887 | 3.5887
2024-11-18 17:00 | 2.4387 | 3.0337 | 3.6653 | 3.7495 | 3.8337 | 2024-09-18 16:00 | 3.5628 | 4.1528 | 4.1528 | 4.1528 | 4.1528
2024-11-18 18:00 | 2.5149 | 3.1285 | 3.7798 | 3.8667 | 3.9535 | 2024-09-18 17:00 | 3.5704 | 4.1617 | 4.1617 | 4.1617 | 4.1617
2024-11-18 19:00 | 1.7909 | 2.2279 | 2.6917 | 2.7535 | 2.8154 | 2024-09-18 18:00 | 3.197 | 3.7264 | 3.7264 | 3.7264 | 3.7264
2024-11-18 20:00 | 1.81 | 2.2516 | 2.7203 | 2.7828 | 2.8453 | 2024-09-18 19:00 | 2.8236 | 3.2911 | 3.2911 | 3.2911 | 3.2911
2024-11-18 21:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2024-09-18 20:00 | 2.5226 | 2.9403 | 2.9403 | 2.9403 | 2.9403
2024-11-18 22:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2024-09-18 21:00 | 2.0767 | 2.4206 | 2.4206 | 2.4206 | 2.4206
2024-11-18 23:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2024-09-18 22:00 | 2.0615 | 2.4028 | 2.4028 | 2.4028 | 2.4028
2024-11-19 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-09-18 23:00 | 1.9091 | 2.2252 | 2.2252 | 2.2252 | 2.2252
2024-11-19 01:00 | 1.4289 | 1.7776 | 2.1476 | 2.197 | 2.2463 | 2024-09-19 | 1.7643 | 2.0564 | 2.0564 | 2.0564 | 2.0564
2024-11-19 02:00 | 1.4289 | 1.7776 | 2.1476 | 2.197 | 2.2463 | 2024-09-19 01:00 | 1.7719 | 2.0653 | 2.0653 | 2.0653 | 2.0653
2024-11-19 03:00 | 1.3908 | 1.7302 | 2.0904 | 2.1384 | 2.1864 | 2024-09-19 02:00 | 1.73 | 2.0164 | 2.0164 | 2.0164 | 2.0164
2024-11-19 04:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-09-19 03:00 | 1.8252 | 2.1275 | 2.1275 | 2.1275 | 2.1275
2024-11-19 05:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2024-09-19 04:00 | 2.0577 | 2.3984 | 2.3984 | 2.3984 | 2.3984
2024-11-19 06:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2024-09-19 05:00 | 2.2253 | 2.5938 | 2.5938 | 2.5938 | 2.5938
2024-11-19 07:00 | 2.3435 | 2.9152 | 3.5221 | 3.603 | 3.684 | 2024-09-19 06:00 | 2.6635 | 3.1046 | 3.1046 | 3.1046 | 3.1046
2024-11-19 08:00 | 2.1339 | 2.6545 | 3.2071 | 3.2808 | 3.3545 | 2024-09-19 07:00 | 3.037 | 3.5399 | 3.5399 | 3.5399 | 3.5399
2024-11-19 09:00 | 2.0577 | 2.5597 | 3.0926 | 3.1636 | 3.2347 | 2024-09-19 08:00 | 3.197 | 3.7264 | 3.7264 | 3.7264 | 3.7264
2024-11-19 10:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-09-19 09:00 | 3.1056 | 3.6198 | 3.6198 | 3.6198 | 3.6198
2024-11-19 11:00 | 1.3718 | 1.7065 | 2.0617 | 2.1091 | 2.1565 | 2024-09-19 10:00 | 3.1094 | 3.6243 | 3.6243 | 3.6243 | 3.6243
2024-11-19 12:00 | 1.6957 | 2.1094 | 2.5485 | 2.6071 | 2.6656 | 2024-09-19 11:00 | 3.2466 | 3.7841 | 3.7841 | 3.7841 | 3.7841
2024-11-19 13:00 | 2.3054 | 2.8678 | 3.4648 | 3.5445 | 3.6241 | 2024-09-19 12:00 | 3.3037 | 3.8508 | 3.8508 | 3.8508 | 3.8508
2024-11-19 14:00 | 2.4578 | 3.0574 | 3.6939 | 3.7788 | 3.8637 | 2024-09-19 13:00 | 2.7169 | 3.1668 | 3.1668 | 3.1668 | 3.1668
2024-11-19 15:00 | 2.1529 | 2.6782 | 3.2358 | 3.3101 | 3.3845 | 2024-09-19 14:00 | 3.0675 | 3.5754 | 3.5754 | 3.5754 | 3.5754
2024-11-19 16:00 | 2.2291 | 2.773 | 3.3503 | 3.4273 | 3.5043 | 2024-09-19 15:00 | 3.3266 | 3.8774 | 3.8774 | 3.8774 | 3.8774
2024-11-19 17:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2024-09-19 16:00 | 3.6086 | 4.2061 | 4.2061 | 4.2061 | 4.2061
2024-11-19 18:00 | 2.3244 | 2.8915 | 3.4935 | 3.5737 | 3.654 | 2024-09-19 17:00 | 3.6581 | 4.2638 | 4.2638 | 4.2638 | 4.2638
2024-11-19 19:00 | 1.8862 | 2.3464 | 2.8349 | 2.9 | 2.9651 | 2024-09-19 18:00 | 3.3037 | 3.8508 | 3.8508 | 3.8508 | 3.8508
2024-11-19 20:00 | 1.8481 | 2.299 | 2.7776 | 2.8414 | 2.9052 | 2024-09-19 19:00 | 2.8045 | 3.2689 | 3.2689 | 3.2689 | 3.2689
2024-11-19 21:00 | 1.7909 | 2.2279 | 2.6917 | 2.7535 | 2.8154 | 2024-09-19 20:00 | 2.4959 | 2.9092 | 2.9092 | 2.9092 | 2.9092
2024-11-19 22:00 | 1.6957 | 2.1094 | 2.5485 | 2.6071 | 2.6656 | 2024-09-19 21:00 | 2.2139 | 2.5805 | 2.5805 | 2.5805 | 2.5805
2024-11-19 23:00 | 1.7147 | 2.1331 | 2.5772 | 2.6364 | 2.6956 | 2024-09-19 22:00 | 2.0958 | 2.4428 | 2.4428 | 2.4428 | 2.4428
2024-11-20 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2024-09-19 23:00 | 1.9281 | 2.2474 | 2.2474 | 2.2474 | 2.2474
2024-11-20 01:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2024-09-20 | 1.81 | 2.1097 | 2.1097 | 2.1097 | 2.1097
2024-11-20 02:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-09-20 01:00 | 1.7147 | 1.9987 | 1.9987 | 1.9987 | 1.9987
2024-11-20 03:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-09-20 02:00 | 1.6881 | 1.9676 | 1.9676 | 1.9676 | 1.9676
2024-11-20 04:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-09-20 03:00 | 1.9548 | 2.2785 | 2.2785 | 2.2785 | 2.2785
2024-11-20 05:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-09-20 04:00 | 2.1225 | 2.4739 | 2.4739 | 2.4739 | 2.4739
2024-11-20 06:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2024-09-20 05:00 | 2.3892 | 2.7848 | 2.7848 | 2.7848 | 2.7848
2024-11-20 07:00 | 0.87642 | 1.0902 | 1.3172 | 1.3475 | 1.3777 | 2024-09-20 06:00 | 2.7017 | 3.149 | 3.149 | 3.149 | 3.149
2024-11-20 08:00 | 0.66684 | 0.82953 | 1.0022 | 1.0253 | 1.0483 | 2024-09-20 07:00 | 3.0294 | 3.531 | 3.531 | 3.531 | 3.531
2024-11-20 09:00 | 0.64779 | 0.80583 | 0.97359 | 0.99596 | 1.0183 | 2024-09-20 08:00 | 2.9036 | 3.3844 | 3.3844 | 3.3844 | 3.3844
2024-11-20 10:00 | 0.66684 | 0.82953 | 1.0022 | 1.0253 | 1.0483 | 2024-09-20 09:00 | 3.1513 | 3.6731 | 3.6731 | 3.6731 | 3.6731
2024-11-20 11:00 | 0.80021 | 0.99544 | 1.2027 | 1.2303 | 1.2579 | 2024-09-20 10:00 | 2.9798 | 3.4732 | 3.4732 | 3.4732 | 3.4732
2024-11-20 12:00 | 2.4006 | 2.9863 | 3.608 | 3.6909 | 3.7738 | 2024-09-20 11:00 | 2.9989 | 3.4955 | 3.4955 | 3.4955 | 3.4955
2024-11-20 13:00 | 3.1056 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2024-09-20 12:00 | 3.178 | 3.7042 | 3.7042 | 3.7042 | 3.7042
2024-11-20 14:00 | 3.1056 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2024-09-20 13:00 | 3.0941 | 3.6065 | 3.6065 | 3.6065 | 3.6065
2024-11-20 15:00 | 2.7055 | 3.3655 | 4.0662 | 4.1596 | 4.253 | 2024-09-20 14:00 | 3.0713 | 3.5798 | 3.5798 | 3.5798 | 3.5798
2024-11-20 16:00 | 2.7817 | 3.4603 | 4.1807 | 4.2768 | 4.3728 | 2024-09-20 15:00 | 3.2008 | 3.7308 | 3.7308 | 3.7308 | 3.7308
2024-11-20 17:00 | 2.8388 | 3.5314 | 4.2666 | 4.3647 | 4.4627 | 2024-09-20 16:00 | 3.6009 | 4.1972 | 4.1972 | 4.1972 | 4.1972
2024-11-20 18:00 | 2.2863 | 2.8441 | 3.4362 | 3.5152 | 3.5941 | 2024-09-20 17:00 | 3.6886 | 4.2994 | 4.2994 | 4.2994 | 4.2994
2024-11-20 19:00 | 2.0386 | 2.536 | 3.064 | 3.1344 | 3.2047 | 2024-09-20 18:00 | 3.6047 | 4.2016 | 4.2016 | 4.2016 | 4.2016
2024-11-20 20:00 | 1.9815 | 2.4649 | 2.9781 | 3.0465 | 3.1149 | 2024-09-20 19:00 | 3.0941 | 3.6065 | 3.6065 | 3.6065 | 3.6065
2024-11-20 21:00 | 1.81 | 2.2516 | 2.7203 | 2.7828 | 2.8453 | 2024-09-20 20:00 | 2.755 | 3.2112 | 3.2112 | 3.2112 | 3.2112
2024-11-20 22:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2024-09-20 21:00 | 2.4502 | 2.8559 | 2.8559 | 2.8559 | 2.8559
2024-11-20 23:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2024-09-20 22:00 | 2.1453 | 2.5006 | 2.5006 | 2.5006 | 2.5006
2024-11-21 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2024-09-20 23:00 | 2.092 | 2.4384 | 2.4384 | 2.4384 | 2.4384
2024-11-21 01:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2024-09-21 | 1.7528 | 2.0431 | 2.0431 | 2.0431 | 2.0431
2024-11-21 02:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-09-21 01:00 | 1.9205 | 2.2385 | 2.2385 | 2.2385 | 2.2385
2024-11-21 03:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-09-21 02:00 | 1.7528 | 2.0431 | 2.0431 | 2.0431 | 2.0431
2024-11-21 04:00 | 1.4289 | 1.7776 | 2.1476 | 2.197 | 2.2463 | 2024-09-21 03:00 | 2.0043 | 2.3362 | 2.3362 | 2.3362 | 2.3362
2024-11-21 05:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2024-09-21 04:00 | 2.0424 | 2.3806 | 2.3806 | 2.3806 | 2.3806
2024-11-21 06:00 | 1.7719 | 2.2042 | 2.6631 | 2.7242 | 2.7854 | 2024-09-21 05:00 | 2.1644 | 2.5228 | 2.5228 | 2.5228 | 2.5228
2024-11-21 07:00 | 2.4768 | 3.0811 | 3.7226 | 3.8081 | 3.8936 | 2024-09-21 06:00 | 2.2444 | 2.616 | 2.616 | 2.616 | 2.616
2024-11-21 08:00 | 2.5721 | 3.1996 | 3.8657 | 3.9546 | 4.0434 | 2024-09-21 07:00 | 2.172 | 2.5316 | 2.5316 | 2.5316 | 2.5316
2024-11-21 09:00 | 2.8198 | 3.5077 | 4.238 | 4.3354 | 4.4327 | 2024-09-21 08:00 | 2.7817 | 3.2423 | 3.2423 | 3.2423 | 3.2423
2024-11-21 10:00 | 2.6102 | 3.247 | 3.923 | 4.0131 | 4.1033 | 2024-09-21 09:00 | 2.9951 | 3.491 | 3.491 | 3.491 | 3.491
2024-11-21 11:00 | 1.7909 | 2.2279 | 2.6917 | 2.7535 | 2.8154 | 2024-09-21 10:00 | 2.8922 | 3.3711 | 3.3711 | 3.3711 | 3.3711
2024-11-21 12:00 | 2.2291 | 2.773 | 3.3503 | 3.4273 | 3.5043 | 2024-09-21 11:00 | 2.9265 | 3.4111 | 3.4111 | 3.4111 | 3.4111
2024-11-21 13:00 | 1.9624 | 2.4412 | 2.9494 | 3.0172 | 3.0849 | 2024-09-21 12:00 | 2.9265 | 3.4111 | 3.4111 | 3.4111 | 3.4111
2024-11-21 14:00 | 1.7338 | 2.1568 | 2.6058 | 2.6657 | 2.7255 | 2024-09-21 13:00 | 3.0789 | 3.5887 | 3.5887 | 3.5887 | 3.5887
2024-11-21 15:00 | 2.1339 | 2.6545 | 3.2071 | 3.2808 | 3.3545 | 2024-09-21 14:00 | 3.0751 | 3.5843 | 3.5843 | 3.5843 | 3.5843
2024-11-21 16:00 | 2.1148 | 2.6308 | 3.1785 | 3.2515 | 3.3245 | 2024-09-21 15:00 | 2.915 | 3.3977 | 3.3977 | 3.3977 | 3.3977
2024-11-21 17:00 | 2.2482 | 2.7967 | 3.3789 | 3.4566 | 3.5342 | 2024-09-21 16:00 | 2.9989 | 3.4955 | 3.4955 | 3.4955 | 3.4955
2024-11-21 18:00 | 1.9243 | 2.3938 | 2.8921 | 2.9586 | 3.025 | 2024-09-21 17:00 | 3.0941 | 3.6065 | 3.6065 | 3.6065 | 3.6065
2024-11-21 19:00 | 1.7909 | 2.2279 | 2.6917 | 2.7535 | 2.8154 | 2024-09-21 18:00 | 2.694 | 3.1401 | 3.1401 | 3.1401 | 3.1401
2024-11-21 20:00 | 1.7338 | 2.1568 | 2.6058 | 2.6657 | 2.7255 | 2024-09-21 19:00 | 2.4159 | 2.8159 | 2.8159 | 2.8159 | 2.8159
2024-11-21 21:00 | 1.7338 | 2.1568 | 2.6058 | 2.6657 | 2.7255 | 2024-09-21 20:00 | 2.1682 | 2.5272 | 2.5272 | 2.5272 | 2.5272
2024-11-21 22:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2024-09-21 21:00 | 1.97 | 2.2962 | 2.2962 | 2.2962 | 2.2962
2024-11-21 23:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2024-09-21 22:00 | 1.9815 | 2.3096 | 2.3096 | 2.3096 | 2.3096
2024-11-22 | 1.4289 | 1.7776 | 2.1476 | 2.197 | 2.2463 | 2024-09-21 23:00 | 1.9891 | 2.3185 | 2.3185 | 2.3185 | 2.3185
2024-11-22 01:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-09-22 | 1.9624 | 2.2874 | 2.2874 | 2.2874 | 2.2874
2024-11-22 02:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-09-22 01:00 | 1.8214 | 2.123 | 2.123 | 2.123 | 2.123
2024-11-22 03:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-09-22 02:00 | 1.8824 | 2.1941 | 2.1941 | 2.1941 | 2.1941
2024-11-22 04:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-09-22 03:00 | 1.9472 | 2.2696 | 2.2696 | 2.2696 | 2.2696
2024-11-22 05:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2024-09-22 04:00 | 1.9472 | 2.2696 | 2.2696 | 2.2696 | 2.2696
2024-11-22 06:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2024-09-22 05:00 | 2.191 | 2.5539 | 2.5539 | 2.5539 | 2.5539
2024-11-22 07:00 | 0.70494 | 0.87693 | 1.0595 | 1.0838 | 1.1082 | 2024-09-22 06:00 | 2.5492 | 2.9714 | 2.9714 | 2.9714 | 2.9714
2024-11-22 08:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2024-09-22 07:00 | 2.4311 | 2.8337 | 2.8337 | 2.8337 | 2.8337
2024-11-22 09:00 | 1.3146 | 1.6354 | 1.9758 | 2.0212 | 2.0666 | 2024-09-22 08:00 | 2.6064 | 3.038 | 3.038 | 3.038 | 3.038
2024-11-22 10:00 | 0.28579 | 0.35551 | 0.42953 | 0.43939 | 0.44926 | 2024-09-22 09:00 | 2.7741 | 3.2334 | 3.2334 | 3.2334 | 3.2334
2024-11-22 11:00 | 1.8481 | 2.299 | 2.7776 | 2.8414 | 2.9052 | 2024-09-22 10:00 | 2.9951 | 3.491 | 3.491 | 3.491 | 3.491
2024-11-22 12:00 | 1.7338 | 2.1568 | 2.6058 | 2.6657 | 2.7255 | 2024-09-22 11:00 | 3.2123 | 3.7442 | 3.7442 | 3.7442 | 3.7442
2024-11-22 13:00 | 1.8862 | 2.3464 | 2.8349 | 2.9 | 2.9651 | 2024-09-22 12:00 | 3.1742 | 3.6998 | 3.6998 | 3.6998 | 3.6998
2024-11-22 14:00 | 2.0958 | 2.6071 | 3.1499 | 3.2222 | 3.2946 | 2024-09-22 13:00 | 3.1703 | 3.6953 | 3.6953 | 3.6953 | 3.6953
2024-11-22 15:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-09-22 14:00 | 3.1094 | 3.6243 | 3.6243 | 3.6243 | 3.6243
2024-11-22 16:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2024-09-22 15:00 | 2.8693 | 3.3444 | 3.3444 | 3.3444 | 3.3444
2024-11-22 17:00 | 1.7147 | 2.1331 | 2.5772 | 2.6364 | 2.6956 | 2024-09-22 16:00 | 2.9874 | 3.4821 | 3.4821 | 3.4821 | 3.4821
2024-11-22 18:00 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2024-09-22 17:00 | 3.1361 | 3.6553 | 3.6553 | 3.6553 | 3.6553
2024-11-22 19:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-09-22 18:00 | 2.7664 | 3.2245 | 3.2245 | 3.2245 | 3.2245
2024-11-22 20:00 | 1.4099 | 1.7539 | 2.119 | 2.1677 | 2.2164 | 2024-09-22 19:00 | 2.3511 | 2.7404 | 2.7404 | 2.7404 | 2.7404
2024-11-22 21:00 | 1.3337 | 1.6591 | 2.0045 | 2.0505 | 2.0966 | 2024-09-22 20:00 | 2.2863 | 2.6649 | 2.6649 | 2.6649 | 2.6649
2024-11-22 22:00 | 1.3908 | 1.7302 | 2.0904 | 2.1384 | 2.1864 | 2024-09-22 21:00 | 2.0005 | 2.3318 | 2.3318 | 2.3318 | 2.3318
2024-11-22 23:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-09-22 22:00 | 2.0005 | 2.3318 | 2.3318 | 2.3318 | 2.3318
2024-11-23 | 1.3908 | 1.7302 | 2.0904 | 2.1384 | 2.1864 | 2024-09-22 23:00 | 1.9243 | 2.243 | 2.243 | 2.243 | 2.243
2024-11-23 01:00 | 1.4289 | 1.7776 | 2.1476 | 2.197 | 2.2463 | 2024-09-23 | 1.8138 | 2.1141 | 2.1141 | 2.1141 | 2.1141
2024-11-23 02:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-09-23 01:00 | 1.8595 | 2.1674 | 2.1674 | 2.1674 | 2.1674
2024-11-23 03:00 | 1.4289 | 1.7776 | 2.1476 | 2.197 | 2.2463 | 2024-09-23 02:00 | 1.81 | 2.1097 | 2.1097 | 2.1097 | 2.1097
2024-11-23 04:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-09-23 03:00 | 1.9396 | 2.2607 | 2.2607 | 2.2607 | 2.2607
2024-11-23 05:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-09-23 04:00 | 2.1263 | 2.4783 | 2.4783 | 2.4783 | 2.4783
2024-11-23 06:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2024-09-23 05:00 | 2.3206 | 2.7049 | 2.7049 | 2.7049 | 2.7049
2024-11-23 07:00 | 1.086 | 1.351 | 1.6322 | 1.6697 | 1.7072 | 2024-09-23 06:00 | 2.755 | 3.2112 | 3.2112 | 3.2112 | 3.2112
2024-11-23 08:00 | 0.93358 | 1.1613 | 1.4031 | 1.4354 | 1.4676 | 2024-09-23 07:00 | 2.6978 | 3.1446 | 3.1446 | 3.1446 | 3.1446
2024-11-23 09:00 | 0.57158 | 0.71103 | 0.85905 | 0.87879 | 0.89853 | 2024-09-23 08:00 | 3.0408 | 3.5443 | 3.5443 | 3.5443 | 3.5443
2024-11-23 10:00 | 0.47631 | 0.59252 | 0.71588 | 0.73232 | 0.74877 | 2024-09-23 09:00 | 3.0522 | 3.5576 | 3.5576 | 3.5576 | 3.5576
2024-11-23 11:00 | 0.32389 | 0.40292 | 0.4868 | 0.49798 | 0.50917 | 2024-09-23 10:00 | 3.0332 | 3.5354 | 3.5354 | 3.5354 | 3.5354
2024-11-23 12:00 | 0.55252 | 0.68733 | 0.83042 | 0.8495 | 0.86858 | 2024-09-23 11:00 | 2.8998 | 3.38 | 3.38 | 3.38 | 3.38
2024-11-23 13:00 | 0.49537 | 0.61622 | 0.74451 | 0.76162 | 0.77872 | 2024-09-23 12:00 | 3.1437 | 3.6642 | 3.6642 | 3.6642 | 3.6642
2024-11-23 14:00 | 0.85737 | 1.0665 | 1.2886 | 1.3182 | 1.3478 | 2024-09-23 13:00 | 3.4257 | 3.9929 | 3.9929 | 3.9929 | 3.9929
2024-11-23 15:00 | 0.80021 | 0.99544 | 1.2027 | 1.2303 | 1.2579 | 2024-09-23 14:00 | 3.0141 | 3.5132 | 3.5132 | 3.5132 | 3.5132
2024-11-23 16:00 | 1.0479 | 1.3035 | 1.5749 | 1.6111 | 1.6473 | 2024-09-23 15:00 | 3.3761 | 3.9352 | 3.9352 | 3.9352 | 3.9352
2024-11-23 17:00 | 1.2765 | 1.588 | 1.9186 | 1.9626 | 2.0067 | 2024-09-23 16:00 | 3.6428 | 4.2461 | 4.2461 | 4.2461 | 4.2461
2024-11-23 18:00 | 1.2956 | 1.6117 | 1.9472 | 1.9919 | 2.0367 | 2024-09-23 17:00 | 3.5666 | 4.1572 | 4.1572 | 4.1572 | 4.1572
2024-11-23 19:00 | 1.3718 | 1.7065 | 2.0617 | 2.1091 | 2.1565 | 2024-09-23 18:00 | 3.0332 | 3.5354 | 3.5354 | 3.5354 | 3.5354
2024-11-23 20:00 | 1.3908 | 1.7302 | 2.0904 | 2.1384 | 2.1864 | 2024-09-23 19:00 | 2.6826 | 3.1268 | 3.1268 | 3.1268 | 3.1268
2024-11-23 21:00 | 1.3718 | 1.7065 | 2.0617 | 2.1091 | 2.1565 | 2024-09-23 20:00 | 2.4997 | 2.9136 | 2.9136 | 2.9136 | 2.9136
2024-11-23 22:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-09-23 21:00 | 2.313 | 2.696 | 2.696 | 2.696 | 2.696
2024-11-23 23:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-09-23 22:00 | 1.8557 | 2.163 | 2.163 | 2.163 | 2.163
2024-11-24 | 1.3908 | 1.7302 | 2.0904 | 2.1384 | 2.1864 | 2024-09-23 23:00 | 1.9396 | 2.2607 | 2.2607 | 2.2607 | 2.2607
2024-11-24 01:00 | 1.4099 | 1.7539 | 2.119 | 2.1677 | 2.2164 | 2024-09-24 | 1.7147 | 1.9987 | 1.9987 | 1.9987 | 1.9987
2024-11-24 02:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-09-24 01:00 | 1.7414 | 2.0298 | 2.0298 | 2.0298 | 2.0298
2024-11-24 03:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2024-09-24 02:00 | 1.7414 | 2.0298 | 2.0298 | 2.0298 | 2.0298
2024-11-24 04:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2024-09-24 03:00 | 1.8633 | 2.1719 | 2.1719 | 2.1719 | 2.1719
2024-11-24 05:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-09-24 04:00 | 2.1415 | 2.4961 | 2.4961 | 2.4961 | 2.4961
2024-11-24 06:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2024-09-24 05:00 | 2.2291 | 2.5983 | 2.5983 | 2.5983 | 2.5983
2024-11-24 07:00 | 1.1432 | 1.4221 | 1.7181 | 1.7576 | 1.7971 | 2024-09-24 06:00 | 2.4654 | 2.8736 | 2.8736 | 2.8736 | 2.8736
2024-11-24 08:00 | 0.80021 | 0.99544 | 1.2027 | 1.2303 | 1.2579 | 2024-09-24 07:00 | 3.2656 | 3.8064 | 3.8064 | 3.8064 | 3.8064
2024-11-24 09:00 | 0.38105 | 0.47402 | 0.5727 | 0.58586 | 0.59902 | 2024-09-24 08:00 | 3.319 | 3.8685 | 3.8685 | 3.8685 | 3.8685
2024-11-24 10:00 | 0.28579 | 0.35551 | 0.42953 | 0.43939 | 0.44926 | 2024-09-24 09:00 | 3.2504 | 3.7886 | 3.7886 | 3.7886 | 3.7886
2024-11-24 11:00 | 0.019053 | 0.023701 | 0.028635 | 0.029293 | 0.029951 | 2024-09-24 10:00 | 3.3761 | 3.9352 | 3.9352 | 3.9352 | 3.9352
2024-11-24 12:00 | 0.49537 | 0.61622 | 0.74451 | 0.76162 | 0.77872 | 2024-09-24 11:00 | 3.2085 | 3.7397 | 3.7397 | 3.7397 | 3.7397
2024-11-24 13:00 | 0.64779 | 0.80583 | 0.97359 | 0.99596 | 1.0183 | 2024-09-24 12:00 | 3.2847 | 3.8286 | 3.8286 | 3.8286 | 3.8286
2024-11-24 14:00 | 0.49537 | 0.61622 | 0.74451 | 0.76162 | 0.77872 | 2024-09-24 13:00 | 3.5895 | 4.1839 | 4.1839 | 4.1839 | 4.1839
2024-11-24 15:00 | 1.1622 | 1.4458 | 1.7467 | 1.7869 | 1.827 | 2024-09-24 14:00 | 3.5971 | 4.1928 | 4.1928 | 4.1928 | 4.1928
2024-11-24 16:00 | 0.043119 | 0.053639 | 0.064806 | 0.066295 | 0.067784 | 2024-09-24 15:00 | 3.4561 | 4.0284 | 4.0284 | 4.0284 | 4.0284
2024-11-24 17:00 | 1.2003 | 1.4932 | 1.804 | 1.8455 | 1.8869 | 2024-09-24 16:00 | 3.5362 | 4.1217 | 4.1217 | 4.1217 | 4.1217
2024-11-24 18:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2024-09-24 17:00 | 3.4676 | 4.0418 | 4.0418 | 4.0418 | 4.0418
2024-11-24 19:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2024-09-24 18:00 | 3.3151 | 3.8641 | 3.8641 | 3.8641 | 3.8641
2024-11-24 20:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2024-09-24 19:00 | 2.5187 | 2.9358 | 2.9358 | 2.9358 | 2.9358
2024-11-24 21:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2024-09-24 20:00 | 2.4578 | 2.8648 | 2.8648 | 2.8648 | 2.8648
2024-11-24 22:00 | 1.7719 | 2.2042 | 2.6631 | 2.7242 | 2.7854 | 2024-09-24 21:00 | 2.3587 | 2.7493 | 2.7493 | 2.7493 | 2.7493
2024-11-24 23:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2024-09-24 22:00 | 1.9777 | 2.3051 | 2.3051 | 2.3051 | 2.3051
2024-11-25 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2024-09-24 23:00 | 1.8138 | 2.1141 | 2.1141 | 2.1141 | 2.1141
2024-11-25 01:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2024-09-25 | 1.7338 | 2.0209 | 2.0209 | 2.0209 | 2.0209
2024-11-25 02:00 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2024-09-25 01:00 | 1.7185 | 2.0031 | 2.0031 | 2.0031 | 2.0031
2024-11-25 03:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2024-09-25 02:00 | 1.7605 | 2.052 | 2.052 | 2.052 | 2.052
2024-11-25 04:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2024-09-25 03:00 | 1.9167 | 2.2341 | 2.2341 | 2.2341 | 2.2341
2024-11-25 05:00 | 1.81 | 2.2516 | 2.7203 | 2.7828 | 2.8453 | 2024-09-25 04:00 | 2.1377 | 2.4917 | 2.4917 | 2.4917 | 2.4917
2024-11-25 06:00 | 1.9243 | 2.3938 | 2.8921 | 2.9586 | 3.025 | 2024-09-25 05:00 | 2.3092 | 2.6915 | 2.6915 | 2.6915 | 2.6915
2024-11-25 07:00 | 2.4197 | 3.01 | 3.6367 | 3.7202 | 3.8038 | 2024-09-25 06:00 | 2.5149 | 2.9314 | 2.9314 | 2.9314 | 2.9314
2024-11-25 08:00 | 2.3244 | 2.8915 | 3.4935 | 3.5737 | 3.654 | 2024-09-25 07:00 | 2.8007 | 3.2645 | 3.2645 | 3.2645 | 3.2645
2024-11-25 09:00 | 2.191 | 2.7256 | 3.293 | 3.3687 | 3.4444 | 2024-09-25 08:00 | 3.4066 | 3.9707 | 3.9707 | 3.9707 | 3.9707
2024-11-25 10:00 | 2.7245 | 3.3892 | 4.0948 | 4.1889 | 4.283 | 2024-09-25 09:00 | 3.3571 | 3.913 | 3.913 | 3.913 | 3.913
2024-11-25 11:00 | 3.0103 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2024-09-25 10:00 | 3.479 | 4.0551 | 4.0551 | 4.0551 | 4.0551
2024-11-25 12:00 | 2.7626 | 3.4366 | 4.1521 | 4.2475 | 4.3429 | 2024-09-25 11:00 | 3.399 | 3.9618 | 3.9618 | 3.9618 | 3.9618
2024-11-25 13:00 | 2.3054 | 2.8678 | 3.4648 | 3.5445 | 3.6241 | 2024-09-25 12:00 | 3.7495 | 4.3704 | 4.3704 | 4.3704 | 4.3704
2024-11-25 14:00 | 1.9434 | 2.4175 | 2.9208 | 2.9879 | 3.055 | 2024-09-25 13:00 | 3.8334 | 4.4681 | 4.4681 | 4.4681 | 4.4681
2024-11-25 15:00 | 2.4197 | 3.01 | 3.6367 | 3.7202 | 3.8038 | 2024-09-25 14:00 | 3.7419 | 4.3615 | 4.3615 | 4.3615 | 4.3615
2024-11-25 16:00 | 2.534 | 3.1522 | 3.8085 | 3.896 | 3.9835 | 2024-09-25 15:00 | 3.4561 | 4.0284 | 4.0284 | 4.0284 | 4.0284
2024-11-25 17:00 | 2.1339 | 2.6545 | 3.2071 | 3.2808 | 3.3545 | 2024-09-25 16:00 | 3.5019 | 4.0817 | 4.0817 | 4.0817 | 4.0817
2024-11-25 18:00 | 2.1148 | 2.6308 | 3.1785 | 3.2515 | 3.3245 | 2024-09-25 17:00 | 3.399 | 3.9618 | 3.9618 | 3.9618 | 3.9618
2024-11-25 19:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2024-09-25 18:00 | 3.1094 | 3.6243 | 3.6243 | 3.6243 | 3.6243
2024-11-25 20:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2024-09-25 19:00 | 2.6369 | 3.0735 | 3.0735 | 3.0735 | 3.0735
2024-11-25 21:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2024-09-25 20:00 | 2.4578 | 2.8648 | 2.8648 | 2.8648 | 2.8648
2024-11-25 22:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-09-25 21:00 | 2.1758 | 2.5361 | 2.5361 | 2.5361 | 2.5361
2024-11-25 23:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-09-25 22:00 | 1.8252 | 2.1275 | 2.1275 | 2.1275 | 2.1275
2024-11-26 | 1.3337 | 1.6591 | 2.0045 | 2.0505 | 2.0966 | 2024-09-25 23:00 | 1.8405 | 2.1452 | 2.1452 | 2.1452 | 2.1452
2024-11-26 01:00 | 1.3337 | 1.6591 | 2.0045 | 2.0505 | 2.0966 | 2024-09-26 | 1.7643 | 2.0564 | 2.0564 | 2.0564 | 2.0564
2024-11-26 02:00 | 1.3527 | 1.6828 | 2.0331 | 2.0798 | 2.1265 | 2024-09-26 01:00 | 1.7262 | 2.012 | 2.012 | 2.012 | 2.012
2024-11-26 03:00 | 1.3146 | 1.6354 | 1.9758 | 2.0212 | 2.0666 | 2024-09-26 02:00 | 1.7757 | 2.0697 | 2.0697 | 2.0697 | 2.0697
2024-11-26 04:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-09-26 03:00 | 1.9053 | 2.2207 | 2.2207 | 2.2207 | 2.2207
2024-11-26 05:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2024-09-26 04:00 | 2.0996 | 2.4473 | 2.4473 | 2.4473 | 2.4473
2024-11-26 06:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2024-09-26 05:00 | 2.3206 | 2.7049 | 2.7049 | 2.7049 | 2.7049
2024-11-26 07:00 | 2.4006 | 2.9863 | 3.608 | 3.6909 | 3.7738 | 2024-09-26 06:00 | 3.2542 | 3.793 | 3.793 | 3.793 | 3.793
2024-11-26 08:00 | 2.1339 | 2.6545 | 3.2071 | 3.2808 | 3.3545 | 2024-09-26 07:00 | 3.1322 | 3.6509 | 3.6509 | 3.6509 | 3.6509
2024-11-26 09:00 | 2.2291 | 2.773 | 3.3503 | 3.4273 | 3.5043 | 2024-09-26 08:00 | 3.6886 | 4.2994 | 4.2994 | 4.2994 | 4.2994
2024-11-26 10:00 | 1.829 | 2.2753 | 2.749 | 2.8121 | 2.8753 | 2024-09-26 09:00 | 3.9515 | 4.6058 | 4.6058 | 4.6058 | 4.6058
2024-11-26 11:00 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2024-09-26 10:00 | 4.0277 | 4.6947 | 4.6947 | 4.6947 | 4.6947
2024-11-26 12:00 | 1.8862 | 2.3464 | 2.8349 | 2.9 | 2.9651 | 2024-09-26 11:00 | 3.8029 | 4.4326 | 4.4326 | 4.4326 | 4.4326
2024-11-26 13:00 | 2.1339 | 2.6545 | 3.2071 | 3.2808 | 3.3545 | 2024-09-26 12:00 | 3.8029 | 4.4326 | 4.4326 | 4.4326 | 4.4326
2024-11-26 14:00 | 2.4197 | 3.01 | 3.6367 | 3.7202 | 3.8038 | 2024-09-26 13:00 | 3.4066 | 3.9707 | 3.9707 | 3.9707 | 3.9707
2024-11-26 15:00 | 1.81 | 2.2516 | 2.7203 | 2.7828 | 2.8453 | 2024-09-26 14:00 | 3.4295 | 3.9973 | 3.9973 | 3.9973 | 3.9973
2024-11-26 16:00 | 1.8481 | 2.299 | 2.7776 | 2.8414 | 2.9052 | 2024-09-26 15:00 | 3.5362 | 4.1217 | 4.1217 | 4.1217 | 4.1217
2024-11-26 17:00 | 1.1622 | 1.4458 | 1.7467 | 1.7869 | 1.827 | 2024-09-26 16:00 | 3.639 | 4.2416 | 4.2416 | 4.2416 | 4.2416
2024-11-26 18:00 | 1.829 | 2.2753 | 2.749 | 2.8121 | 2.8753 | 2024-09-26 17:00 | 3.639 | 4.2416 | 4.2416 | 4.2416 | 4.2416
2024-11-26 19:00 | 1.7338 | 2.1568 | 2.6058 | 2.6657 | 2.7255 | 2024-09-26 18:00 | 3.4142 | 3.9796 | 3.9796 | 3.9796 | 3.9796
2024-11-26 20:00 | 1.6957 | 2.1094 | 2.5485 | 2.6071 | 2.6656 | 2024-09-26 19:00 | 2.835 | 3.3045 | 3.3045 | 3.3045 | 3.3045
2024-11-26 21:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2024-09-26 20:00 | 2.5797 | 3.0069 | 3.0069 | 3.0069 | 3.0069
2024-11-26 22:00 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2024-09-26 21:00 | 2.3473 | 2.736 | 2.736 | 2.736 | 2.736
2024-11-26 23:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2024-09-26 22:00 | 2.1186 | 2.4695 | 2.4695 | 2.4695 | 2.4695
2024-11-27 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-09-26 23:00 | 1.9586 | 2.2829 | 2.2829 | 2.2829 | 2.2829
2024-11-27 01:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-09-27 | 1.7719 | 2.0653 | 2.0653 | 2.0653 | 2.0653
2024-11-27 02:00 | 1.4289 | 1.7776 | 2.1476 | 2.197 | 2.2463 | 2024-09-27 01:00 | 1.8024 | 2.1008 | 2.1008 | 2.1008 | 2.1008
2024-11-27 03:00 | 1.4099 | 1.7539 | 2.119 | 2.1677 | 2.2164 | 2024-09-27 02:00 | 1.7452 | 2.0342 | 2.0342 | 2.0342 | 2.0342
2024-11-27 04:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-09-27 03:00 | 1.9472 | 2.2696 | 2.2696 | 2.2696 | 2.2696
2024-11-27 05:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-09-27 04:00 | 2.3054 | 2.6871 | 2.6871 | 2.6871 | 2.6871
2024-11-27 06:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-09-27 05:00 | 2.3358 | 2.7226 | 2.7226 | 2.7226 | 2.7226
2024-11-27 07:00 | 0.57158 | 0.71103 | 0.85905 | 0.87879 | 0.89853 | 2024-09-27 06:00 | 2.6635 | 3.1046 | 3.1046 | 3.1046 | 3.1046
2024-11-27 08:00 | 0.66684 | 0.82953 | 1.0022 | 1.0253 | 1.0483 | 2024-09-27 07:00 | 2.8312 | 3.3 | 3.3 | 3.3 | 3.3
2024-11-27 09:00 | 0.70494 | 0.87693 | 1.0595 | 1.0838 | 1.1082 | 2024-09-27 08:00 | 3.3723 | 3.9307 | 3.9307 | 3.9307 | 3.9307
2024-11-27 10:00 | 0.91452 | 1.1376 | 1.3745 | 1.4061 | 1.4376 | 2024-09-27 09:00 | 3.4066 | 3.9707 | 3.9707 | 3.9707 | 3.9707
2024-11-27 11:00 | 0.45726 | 0.56882 | 0.68724 | 0.70303 | 0.71882 | 2024-09-27 10:00 | 3.4295 | 3.9973 | 3.9973 | 3.9973 | 3.9973
2024-11-27 12:00 | 1.8862 | 2.3464 | 2.8349 | 2.9 | 2.9651 | 2024-09-27 11:00 | 3.5476 | 4.135 | 4.135 | 4.135 | 4.135
2024-11-27 13:00 | 2.6102 | 3.247 | 3.923 | 4.0131 | 4.1033 | 2024-09-27 12:00 | 3.418 | 3.984 | 3.984 | 3.984 | 3.984
2024-11-27 14:00 | 2.5911 | 3.2233 | 3.8944 | 3.9838 | 4.0733 | 2024-09-27 13:00 | 3.3418 | 3.8952 | 3.8952 | 3.8952 | 3.8952
2024-11-27 15:00 | 2.3244 | 2.8915 | 3.4935 | 3.5737 | 3.654 | 2024-09-27 14:00 | 3.0827 | 3.5932 | 3.5932 | 3.5932 | 3.5932
2024-11-27 16:00 | 2.4387 | 3.0337 | 3.6653 | 3.7495 | 3.8337 | 2024-09-27 15:00 | 3.2313 | 3.7664 | 3.7664 | 3.7664 | 3.7664
2024-11-27 17:00 | 2.4387 | 3.0337 | 3.6653 | 3.7495 | 3.8337 | 2024-09-27 16:00 | 3.639 | 4.2416 | 4.2416 | 4.2416 | 4.2416
2024-11-27 18:00 | 1.8672 | 2.3227 | 2.8062 | 2.8707 | 2.9352 | 2024-09-27 17:00 | 3.6924 | 4.3038 | 4.3038 | 4.3038 | 4.3038
2024-11-27 19:00 | 1.9624 | 2.4412 | 2.9494 | 3.0172 | 3.0849 | 2024-09-27 18:00 | 3.3647 | 3.9218 | 3.9218 | 3.9218 | 3.9218
2024-11-27 20:00 | 1.829 | 2.2753 | 2.749 | 2.8121 | 2.8753 | 2024-09-27 19:00 | 3.2313 | 3.7664 | 3.7664 | 3.7664 | 3.7664
2024-11-27 21:00 | 1.7528 | 2.1805 | 2.6344 | 2.695 | 2.7555 | 2024-09-27 20:00 | 2.8122 | 3.2778 | 3.2778 | 3.2778 | 3.2778
2024-11-27 22:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2024-09-27 21:00 | 2.6102 | 3.0424 | 3.0424 | 3.0424 | 3.0424
2024-11-27 23:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2024-09-27 22:00 | 2.1072 | 2.4561 | 2.4561 | 2.4561 | 2.4561
2024-11-28 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-09-27 23:00 | 2.1301 | 2.4828 | 2.4828 | 2.4828 | 2.4828
2024-11-28 01:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-09-28 | 1.8138 | 2.1141 | 2.1141 | 2.1141 | 2.1141
2024-11-28 02:00 | 1.4289 | 1.7776 | 2.1476 | 2.197 | 2.2463 | 2024-09-28 01:00 | 1.7452 | 2.0342 | 2.0342 | 2.0342 | 2.0342
2024-11-28 03:00 | 1.4099 | 1.7539 | 2.119 | 2.1677 | 2.2164 | 2024-09-28 02:00 | 1.7681 | 2.0609 | 2.0609 | 2.0609 | 2.0609
2024-11-28 04:00 | 1.4099 | 1.7539 | 2.119 | 2.1677 | 2.2164 | 2024-09-28 03:00 | 1.9472 | 2.2696 | 2.2696 | 2.2696 | 2.2696
2024-11-28 05:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-09-28 04:00 | 2.0272 | 2.3629 | 2.3629 | 2.3629 | 2.3629
2024-11-28 06:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2024-09-28 05:00 | 2.3739 | 2.767 | 2.767 | 2.767 | 2.767
2024-11-28 07:00 | 2.1529 | 2.6782 | 3.2358 | 3.3101 | 3.3845 | 2024-09-28 06:00 | 2.2939 | 2.6738 | 2.6738 | 2.6738 | 2.6738
2024-11-28 08:00 | 2.3816 | 2.9626 | 3.5794 | 3.6616 | 3.7439 | 2024-09-28 07:00 | 2.3015 | 2.6827 | 2.6827 | 2.6827 | 2.6827
2024-11-28 09:00 | 2.9341 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2024-09-28 08:00 | 2.7017 | 3.149 | 3.149 | 3.149 | 3.149
2024-11-28 10:00 | 2.5721 | 3.1996 | 3.8657 | 3.9546 | 4.0434 | 2024-09-28 09:00 | 2.7893 | 3.2512 | 3.2512 | 3.2512 | 3.2512
2024-11-28 11:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2024-09-28 10:00 | 2.9417 | 3.4288 | 3.4288 | 3.4288 | 3.4288
2024-11-28 12:00 | 1.8862 | 2.3464 | 2.8349 | 2.9 | 2.9651 | 2024-09-28 11:00 | 2.9874 | 3.4821 | 3.4821 | 3.4821 | 3.4821
2024-11-28 13:00 | 1.4099 | 1.7539 | 2.119 | 2.1677 | 2.2164 | 2024-09-28 12:00 | 2.8426 | 3.3133 | 3.3133 | 3.3133 | 3.3133
2024-11-28 14:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-09-28 13:00 | 3.0027 | 3.4999 | 3.4999 | 3.4999 | 3.4999
2024-11-28 15:00 | 2.0196 | 2.5123 | 3.0353 | 3.1051 | 3.1748 | 2024-09-28 14:00 | 2.9874 | 3.4821 | 3.4821 | 3.4821 | 3.4821
2024-11-28 16:00 | 2.0767 | 2.5834 | 3.1212 | 3.1929 | 3.2646 | 2024-09-28 15:00 | 2.7512 | 3.2068 | 3.2068 | 3.2068 | 3.2068
2024-11-28 17:00 | 1.8672 | 2.3227 | 2.8062 | 2.8707 | 2.9352 | 2024-09-28 16:00 | 2.9951 | 3.491 | 3.491 | 3.491 | 3.491
2024-11-28 18:00 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2024-09-28 17:00 | 3.1056 | 3.6198 | 3.6198 | 3.6198 | 3.6198
2024-11-28 19:00 | 1.81 | 2.2516 | 2.7203 | 2.7828 | 2.8453 | 2024-09-28 18:00 | 2.694 | 3.1401 | 3.1401 | 3.1401 | 3.1401
2024-11-28 20:00 | 1.7338 | 2.1568 | 2.6058 | 2.6657 | 2.7255 | 2024-09-28 19:00 | 2.5378 | 2.958 | 2.958 | 2.958 | 2.958
2024-11-28 21:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2024-09-28 20:00 | 2.3244 | 2.7093 | 2.7093 | 2.7093 | 2.7093
2024-11-28 22:00 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2024-09-28 21:00 | 2.0158 | 2.3495 | 2.3495 | 2.3495 | 2.3495
2024-11-28 23:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2024-09-28 22:00 | 1.8976 | 2.2119 | 2.2119 | 2.2119 | 2.2119
2024-11-29 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-09-28 23:00 | 1.7566 | 2.0475 | 2.0475 | 2.0475 | 2.0475
2024-11-29 01:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-09-29 | 1.6995 | 1.9809 | 1.9809 | 1.9809 | 1.9809
2024-11-29 02:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-09-29 01:00 | 1.7033 | 1.9853 | 1.9853 | 1.9853 | 1.9853
2024-11-29 03:00 | 1.4289 | 1.7776 | 2.1476 | 2.197 | 2.2463 | 2024-09-29 02:00 | 1.7795 | 2.0742 | 2.0742 | 2.0742 | 2.0742
2024-11-29 04:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-09-29 03:00 | 1.8214 | 2.123 | 2.123 | 2.123 | 2.123
2024-11-29 05:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2024-09-29 04:00 | 2.031 | 2.3673 | 2.3673 | 2.3673 | 2.3673
2024-11-29 06:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-09-29 05:00 | 2.172 | 2.5316 | 2.5316 | 2.5316 | 2.5316
2024-11-29 07:00 | 0.57158 | 0.71103 | 0.85905 | 0.87879 | 0.89853 | 2024-09-29 06:00 | 2.2368 | 2.6072 | 2.6072 | 2.6072 | 2.6072
2024-11-29 08:00 | 1.3908 | 1.7302 | 2.0904 | 2.1384 | 2.1864 | 2024-09-29 07:00 | 2.4425 | 2.847 | 2.847 | 2.847 | 2.847
2024-11-29 09:00 | 1.2003 | 1.4932 | 1.804 | 1.8455 | 1.8869 | 2024-09-29 08:00 | 2.5226 | 2.9403 | 2.9403 | 2.9403 | 2.9403
2024-11-29 10:00 | 0.38105 | 0.47402 | 0.5727 | 0.58586 | 0.59902 | 2024-09-29 09:00 | 2.5645 | 2.9891 | 2.9891 | 2.9891 | 2.9891
2024-11-29 11:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2024-09-29 10:00 | 2.6445 | 3.0824 | 3.0824 | 3.0824 | 3.0824
2024-11-29 12:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-09-29 11:00 | 2.7512 | 3.2068 | 3.2068 | 3.2068 | 3.2068
2024-11-29 13:00 | 1.7909 | 2.2279 | 2.6917 | 2.7535 | 2.8154 | 2024-09-29 12:00 | 2.9227 | 3.4066 | 3.4066 | 3.4066 | 3.4066
2024-11-29 14:00 | 1.9243 | 2.3938 | 2.8921 | 2.9586 | 3.025 | 2024-09-29 13:00 | 2.9341 | 3.4199 | 3.4199 | 3.4199 | 3.4199
2024-11-29 15:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2024-09-29 14:00 | 3.0713 | 3.5798 | 3.5798 | 3.5798 | 3.5798
2024-11-29 16:00 | 1.7147 | 2.1331 | 2.5772 | 2.6364 | 2.6956 | 2024-09-29 15:00 | 3.037 | 3.5399 | 3.5399 | 3.5399 | 3.5399
2024-11-29 17:00 | 1.7338 | 2.1568 | 2.6058 | 2.6657 | 2.7255 | 2024-09-29 16:00 | 3.0941 | 3.6065 | 3.6065 | 3.6065 | 3.6065
2024-11-29 18:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2024-09-29 17:00 | 2.976 | 3.4688 | 3.4688 | 3.4688 | 3.4688
2024-11-29 19:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2024-09-29 18:00 | 2.8274 | 3.2956 | 3.2956 | 3.2956 | 3.2956
2024-11-29 20:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-09-29 19:00 | 2.5416 | 2.9625 | 2.9625 | 2.9625 | 2.9625
2024-11-29 21:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-09-29 20:00 | 2.313 | 2.696 | 2.696 | 2.696 | 2.696
2024-11-29 22:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-09-29 21:00 | 2.0882 | 2.4339 | 2.4339 | 2.4339 | 2.4339
2024-11-29 23:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-09-29 22:00 | 1.9243 | 2.243 | 2.243 | 2.243 | 2.243
2024-11-30 | 1.3337 | 1.6591 | 2.0045 | 2.0505 | 2.0966 | 2024-09-29 23:00 | 1.7414 | 2.0298 | 2.0298 | 2.0298 | 2.0298
2024-11-30 01:00 | 1.3718 | 1.7065 | 2.0617 | 2.1091 | 2.1565 | 2024-09-30 | 1.7414 | 2.0298 | 2.0298 | 2.0298 | 2.0298
2024-11-30 02:00 | 1.3718 | 1.7065 | 2.0617 | 2.1091 | 2.1565 | 2024-09-30 01:00 | 1.8519 | 2.1586 | 2.1586 | 2.1586 | 2.1586
2024-11-30 03:00 | 1.3337 | 1.6591 | 2.0045 | 2.0505 | 2.0966 | 2024-09-30 02:00 | 1.8481 | 2.1541 | 2.1541 | 2.1541 | 2.1541
2024-11-30 04:00 | 1.4099 | 1.7539 | 2.119 | 2.1677 | 2.2164 | 2024-09-30 03:00 | 1.8786 | 2.1897 | 2.1897 | 2.1897 | 2.1897
2024-11-30 05:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-09-30 04:00 | 2.0691 | 2.4117 | 2.4117 | 2.4117 | 2.4117
2024-11-30 06:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-09-30 05:00 | 2.2025 | 2.5672 | 2.5672 | 2.5672 | 2.5672
2024-11-30 07:00 | 1.0479 | 1.3035 | 1.5749 | 1.6111 | 1.6473 | 2024-09-30 06:00 | 2.5835 | 3.0113 | 3.0113 | 3.0113 | 3.0113
2024-11-30 08:00 | 0.97168 | 1.2087 | 1.4604 | 1.4939 | 1.5275 | 2024-09-30 07:00 | 2.9036 | 3.3844 | 3.3844 | 3.3844 | 3.3844
2024-11-30 09:00 | 0.60968 | 0.75843 | 0.91632 | 0.93738 | 0.95843 | 2024-09-30 08:00 | 2.9417 | 3.4288 | 3.4288 | 3.4288 | 3.4288
2024-11-30 10:00 | 0.59063 | 0.73473 | 0.88769 | 0.90808 | 0.92848 | 2024-09-30 09:00 | 3.0294 | 3.531 | 3.531 | 3.531 | 3.531
2024-11-30 11:00 | 0.28579 | 0.35551 | 0.42953 | 0.43939 | 0.44926 | 2024-09-30 10:00 | 3.5209 | 4.1039 | 4.1039 | 4.1039 | 4.1039
2024-11-30 12:00 | 0.53347 | 0.66362 | 0.80178 | 0.8202 | 0.83862 | 2024-09-30 11:00 | 3.4561 | 4.0284 | 4.0284 | 4.0284 | 4.0284
2024-11-30 13:00 | 0.4001 | 0.49772 | 0.60134 | 0.61515 | 0.62897 | 2024-09-30 12:00 | 3.4447 | 4.0151 | 4.0151 | 4.0151 | 4.0151
2024-11-30 14:00 | 0.64779 | 0.80583 | 0.97359 | 0.99596 | 1.0183 | 2024-09-30 13:00 | 3.7534 | 4.3749 | 4.3749 | 4.3749 | 4.3749
2024-11-30 15:00 | 0.45726 | 0.56882 | 0.68724 | 0.70303 | 0.71882 | 2024-09-30 14:00 | 3.8448 | 4.4815 | 4.4815 | 4.4815 | 4.4815
2024-11-30 16:00 | 0.68589 | 0.85323 | 1.0309 | 1.0545 | 1.0782 | 2024-09-30 15:00 | 3.6733 | 4.2816 | 4.2816 | 4.2816 | 4.2816
2024-11-30 17:00 | 1.0479 | 1.3035 | 1.5749 | 1.6111 | 1.6473 | 2024-09-30 16:00 | 3.6162 | 4.215 | 4.215 | 4.215 | 4.215
2024-11-30 18:00 | 1.2194 | 1.5169 | 1.8326 | 1.8748 | 1.9169 | 2024-09-30 17:00 | 3.4409 | 4.0107 | 4.0107 | 4.0107 | 4.0107
2024-11-30 19:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2024-09-30 18:00 | 3.2085 | 3.7397 | 3.7397 | 3.7397 | 3.7397
2024-11-30 20:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-09-30 19:00 | 2.755 | 3.2112 | 3.2112 | 3.2112 | 3.2112
2024-11-30 21:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-09-30 20:00 | 2.4273 | 2.8292 | 2.8292 | 2.8292 | 2.8292
2024-11-30 22:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2024-09-30 21:00 | 2.252 | 2.6249 | 2.6249 | 2.6249 | 2.6249
2024-11-30 23:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-09-30 22:00 | 2.0081 | 2.3407 | 2.3407 | 2.3407 | 2.3407
2024-12-01 | 1.3527 | 1.6828 | 2.0331 | 2.0798 | 2.1265 | 2024-09-30 23:00 | 1.9929 | 2.3229 | 2.3229 | 2.3229 | 2.3229
2024-12-01 01:00 | 1.4099 | 1.7539 | 2.119 | 2.1677 | 2.2164 | 2024-10-01 | 1.9167 | 2.2711 | 2.2711 | 2.2711 | 2.2711
2024-12-01 02:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-10-01 01:00 | 1.8062 | 2.1402 | 2.1402 | 2.1402 | 2.1402
2024-12-01 03:00 | 1.3718 | 1.7065 | 2.0617 | 2.1091 | 2.1565 | 2024-10-01 02:00 | 1.8062 | 2.1402 | 2.1402 | 2.1402 | 2.1402
2024-12-01 04:00 | 1.4099 | 1.7539 | 2.119 | 2.1677 | 2.2164 | 2024-10-01 03:00 | 1.9357 | 2.2937 | 2.2937 | 2.2937 | 2.2937
2024-12-01 05:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-10-01 04:00 | 2.1758 | 2.5781 | 2.5781 | 2.5781 | 2.5781
2024-12-01 06:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2024-10-01 05:00 | 2.2139 | 2.6233 | 2.6233 | 2.6233 | 2.6233
2024-12-01 07:00 | 1.3337 | 1.6591 | 2.0045 | 2.0505 | 2.0966 | 2024-10-01 06:00 | 2.5569 | 3.0297 | 3.0297 | 3.0297 | 3.0297
2024-12-01 08:00 | 0.97168 | 1.2087 | 1.4604 | 1.4939 | 1.5275 | 2024-10-01 07:00 | 3.2275 | 3.8243 | 3.8243 | 3.8243 | 3.8243
2024-12-01 09:00 | 0.53347 | 0.66362 | 0.80178 | 0.8202 | 0.83862 | 2024-10-01 08:00 | 3.5362 | 4.19 | 4.19 | 4.19 | 4.19
2024-12-01 10:00 | 0.30484 | 0.37921 | 0.45816 | 0.46869 | 0.47921 | 2024-10-01 09:00 | 3.3837 | 4.0094 | 4.0094 | 4.0094 | 4.0094
2024-12-01 11:00 | 0.095263 | 0.1185 | 0.14318 | 0.14646 | 0.14975 | 2024-10-01 10:00 | 2.9189 | 3.4586 | 3.4586 | 3.4586 | 3.4586
2024-12-01 12:00 | 0.70494 | 0.87693 | 1.0595 | 1.0838 | 1.1082 | 2024-10-01 11:00 | 2.8198 | 3.3412 | 3.3412 | 3.3412 | 3.3412
2024-12-01 13:00 | 0.43821 | 0.54512 | 0.65861 | 0.67374 | 0.68887 | 2024-10-01 12:00 | 2.976 | 3.5263 | 3.5263 | 3.5263 | 3.5263
2024-12-01 14:00 | 0.724 | 0.90063 | 1.0881 | 1.1131 | 1.1381 | 2024-10-01 13:00 | 3.2656 | 3.8695 | 3.8695 | 3.8695 | 3.8695
2024-12-01 15:00 | 1.0669 | 1.3272 | 1.6036 | 1.6404 | 1.6772 | 2024-10-01 14:00 | 3.2427 | 3.8424 | 3.8424 | 3.8424 | 3.8424
2024-12-01 16:00 | 0.19554 | 0.24325 | 0.29389 | 0.30064 | 0.30739 | 2024-10-01 15:00 | 3.4752 | 4.1178 | 4.1178 | 4.1178 | 4.1178
2024-12-01 17:00 | 1.105 | 1.3747 | 1.6608 | 1.699 | 1.7372 | 2024-10-01 16:00 | 3.54 | 4.1946 | 4.1946 | 4.1946 | 4.1946
2024-12-01 18:00 | 1.7147 | 2.1331 | 2.5772 | 2.6364 | 2.6956 | 2024-10-01 17:00 | 3.54 | 4.1946 | 4.1946 | 4.1946 | 4.1946
2024-12-01 19:00 | 1.8481 | 2.299 | 2.7776 | 2.8414 | 2.9052 | 2024-10-01 18:00 | 3.2008 | 3.7927 | 3.7927 | 3.7927 | 3.7927
2024-12-01 20:00 | 1.8672 | 2.3227 | 2.8062 | 2.8707 | 2.9352 | 2024-10-01 19:00 | 2.8312 | 3.3547 | 3.3547 | 3.3547 | 3.3547
2024-12-01 21:00 | 1.8481 | 2.299 | 2.7776 | 2.8414 | 2.9052 | 2024-10-01 20:00 | 2.6864 | 3.1832 | 3.1832 | 3.1832 | 3.1832
2024-12-01 22:00 | 1.9053 | 2.3701 | 2.8635 | 2.9293 | 2.9951 | 2024-10-01 21:00 | 2.233 | 2.6459 | 2.6459 | 2.6459 | 2.6459
2024-12-01 23:00 | 1.7909 | 2.2279 | 2.6917 | 2.7535 | 2.8154 | 2024-10-01 22:00 | 2.1529 | 2.5511 | 2.5511 | 2.5511 | 2.5511
2024-12-02 | 1.7909 | 2.2279 | 2.6917 | 2.7535 | 2.8154 | 2024-10-01 23:00 | 1.9396 | 2.2982 | 2.2982 | 2.2982 | 2.2982
2024-12-02 01:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2024-10-02 | 1.951 | 2.3118 | 2.3118 | 2.3118 | 2.3118
2024-12-02 02:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2024-10-02 01:00 | 1.8214 | 2.1582 | 2.1582 | 2.1582 | 2.1582
2024-12-02 03:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2024-10-02 02:00 | 1.8024 | 2.1357 | 2.1357 | 2.1357 | 2.1357
2024-12-02 04:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2024-10-02 03:00 | 1.8252 | 2.1628 | 2.1628 | 2.1628 | 2.1628
2024-12-02 05:00 | 1.81 | 2.2516 | 2.7203 | 2.7828 | 2.8453 | 2024-10-02 04:00 | 2.0767 | 2.4608 | 2.4608 | 2.4608 | 2.4608
2024-12-02 06:00 | 2.0767 | 2.5834 | 3.1212 | 3.1929 | 3.2646 | 2024-10-02 05:00 | 2.3206 | 2.7497 | 2.7497 | 2.7497 | 2.7497
2024-12-02 07:00 | 2.4387 | 3.0337 | 3.6653 | 3.7495 | 3.8337 | 2024-10-02 06:00 | 2.5416 | 3.0116 | 3.0116 | 3.0116 | 3.0116
2024-12-02 08:00 | 2.3435 | 2.9152 | 3.5221 | 3.603 | 3.684 | 2024-10-02 07:00 | 3.0065 | 3.5624 | 3.5624 | 3.5624 | 3.5624
2024-12-02 09:00 | 2.1339 | 2.6545 | 3.2071 | 3.2808 | 3.3545 | 2024-10-02 08:00 | 3.1703 | 3.7566 | 3.7566 | 3.7566 | 3.7566
2024-12-02 10:00 | 2.5721 | 3.1996 | 3.8657 | 3.9546 | 4.0434 | 2024-10-02 09:00 | 3.1703 | 3.7566 | 3.7566 | 3.7566 | 3.7566
2024-12-02 11:00 | 2.896 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2024-10-02 10:00 | 2.9265 | 3.4676 | 3.4676 | 3.4676 | 3.4676
2024-12-02 12:00 | 2.6864 | 3.3418 | 4.0375 | 4.1303 | 4.2231 | 2024-10-02 11:00 | 3.3494 | 3.9688 | 3.9688 | 3.9688 | 3.9688
2024-12-02 13:00 | 1.9815 | 2.4649 | 2.9781 | 3.0465 | 3.1149 | 2024-10-02 12:00 | 3.3723 | 3.9959 | 3.9959 | 3.9959 | 3.9959
2024-12-02 14:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2024-10-02 13:00 | 3.4409 | 4.0772 | 4.0772 | 4.0772 | 4.0772
2024-12-02 15:00 | 2.1529 | 2.6782 | 3.2358 | 3.3101 | 3.3845 | 2024-10-02 14:00 | 3.1361 | 3.716 | 3.716 | 3.716 | 3.716
2024-12-02 16:00 | 2.0196 | 2.5123 | 3.0353 | 3.1051 | 3.1748 | 2024-10-02 15:00 | 3.4866 | 4.1314 | 4.1314 | 4.1314 | 4.1314
2024-12-02 17:00 | 2.172 | 2.7019 | 3.2644 | 3.3394 | 3.4144 | 2024-10-02 16:00 | 3.7267 | 4.4158 | 4.4158 | 4.4158 | 4.4158
2024-12-02 18:00 | 2.3625 | 2.9389 | 3.5508 | 3.6323 | 3.7139 | 2024-10-02 17:00 | 3.7191 | 4.4068 | 4.4068 | 4.4068 | 4.4068
2024-12-02 19:00 | 1.7338 | 2.1568 | 2.6058 | 2.6657 | 2.7255 | 2024-10-02 18:00 | 3.1284 | 3.7069 | 3.7069 | 3.7069 | 3.7069
2024-12-02 20:00 | 1.8672 | 2.3227 | 2.8062 | 2.8707 | 2.9352 | 2024-10-02 19:00 | 2.7626 | 3.2735 | 3.2735 | 3.2735 | 3.2735
2024-12-02 21:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2024-10-02 20:00 | 2.6902 | 3.1877 | 3.1877 | 3.1877 | 3.1877
2024-12-02 22:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2024-10-02 21:00 | 2.3435 | 2.7768 | 2.7768 | 2.7768 | 2.7768
2024-12-02 23:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2024-10-02 22:00 | 1.9624 | 2.3253 | 2.3253 | 2.3253 | 2.3253
2024-12-03 | 1.4289 | 1.7776 | 2.1476 | 2.197 | 2.2463 | 2024-10-02 23:00 | 1.9662 | 2.3298 | 2.3298 | 2.3298 | 2.3298
2024-12-03 01:00 | 1.4099 | 1.7539 | 2.119 | 2.1677 | 2.2164 | 2024-10-03 | 1.8633 | 2.2079 | 2.2079 | 2.2079 | 2.2079
2024-12-03 02:00 | 1.4289 | 1.7776 | 2.1476 | 2.197 | 2.2463 | 2024-10-03 01:00 | 1.7871 | 2.1176 | 2.1176 | 2.1176 | 2.1176
2024-12-03 03:00 | 1.4099 | 1.7539 | 2.119 | 2.1677 | 2.2164 | 2024-10-03 02:00 | 1.7566 | 2.0815 | 2.0815 | 2.0815 | 2.0815
2024-12-03 04:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-10-03 03:00 | 1.8786 | 2.226 | 2.226 | 2.226 | 2.226
2024-12-03 05:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2024-10-03 04:00 | 2.0653 | 2.4472 | 2.4472 | 2.4472 | 2.4472
2024-12-03 06:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2024-10-03 05:00 | 2.1834 | 2.5872 | 2.5872 | 2.5872 | 2.5872
2024-12-03 07:00 | 2.0958 | 2.6071 | 3.1499 | 3.2222 | 3.2946 | 2024-10-03 06:00 | 2.7474 | 3.2554 | 3.2554 | 3.2554 | 3.2554
2024-12-03 08:00 | 1.829 | 2.2753 | 2.749 | 2.8121 | 2.8753 | 2024-10-03 07:00 | 2.8045 | 3.3231 | 3.3231 | 3.3231 | 3.3231
2024-12-03 09:00 | 1.6957 | 2.1094 | 2.5485 | 2.6071 | 2.6656 | 2024-10-03 08:00 | 3.1856 | 3.7747 | 3.7747 | 3.7747 | 3.7747
2024-12-03 10:00 | 1.4289 | 1.7776 | 2.1476 | 2.197 | 2.2463 | 2024-10-03 09:00 | 3.1665 | 3.7521 | 3.7521 | 3.7521 | 3.7521
2024-12-03 11:00 | 1.2765 | 1.588 | 1.9186 | 1.9626 | 2.0067 | 2024-10-03 10:00 | 3.0675 | 3.6347 | 3.6347 | 3.6347 | 3.6347
2024-12-03 12:00 | 1.2956 | 1.6117 | 1.9472 | 1.9919 | 2.0367 | 2024-10-03 11:00 | 2.957 | 3.5037 | 3.5037 | 3.5037 | 3.5037
2024-12-03 13:00 | 1.8862 | 2.3464 | 2.8349 | 2.9 | 2.9651 | 2024-10-03 12:00 | 3.0598 | 3.6257 | 3.6257 | 3.6257 | 3.6257
2024-12-03 14:00 | 1.9053 | 2.3701 | 2.8635 | 2.9293 | 2.9951 | 2024-10-03 13:00 | 3.2123 | 3.8063 | 3.8063 | 3.8063 | 3.8063
2024-12-03 15:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-10-03 14:00 | 3.1513 | 3.734 | 3.734 | 3.734 | 3.734
2024-12-03 16:00 | 1.9243 | 2.3938 | 2.8921 | 2.9586 | 3.025 | 2024-10-03 15:00 | 3.4409 | 4.0772 | 4.0772 | 4.0772 | 4.0772
2024-12-03 17:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-10-03 16:00 | 3.6505 | 4.3255 | 4.3255 | 4.3255 | 4.3255
2024-12-03 18:00 | 2.0386 | 2.536 | 3.064 | 3.1344 | 3.2047 | 2024-10-03 17:00 | 3.5704 | 4.2307 | 4.2307 | 4.2307 | 4.2307
2024-12-03 19:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2024-10-03 18:00 | 3.4142 | 4.0456 | 4.0456 | 4.0456 | 4.0456
2024-12-03 20:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2024-10-03 19:00 | 2.7398 | 3.2464 | 3.2464 | 3.2464 | 3.2464
2024-12-03 21:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2024-10-03 20:00 | 2.4578 | 2.9123 | 2.9123 | 2.9123 | 2.9123
2024-12-03 22:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-10-03 21:00 | 2.2558 | 2.673 | 2.673 | 2.673 | 2.673
2024-12-03 23:00 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2024-10-03 22:00 | 2.0234 | 2.3975 | 2.3975 | 2.3975 | 2.3975
2024-12-04 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-10-03 23:00 | 1.9815 | 2.3479 | 2.3479 | 2.3479 | 2.3479
2024-12-04 01:00 | 1.4289 | 1.7776 | 2.1476 | 2.197 | 2.2463 | 2024-10-04 | 1.7376 | 2.0589 | 2.0589 | 2.0589 | 2.0589
2024-12-04 02:00 | 1.3908 | 1.7302 | 2.0904 | 2.1384 | 2.1864 | 2024-10-04 01:00 | 1.7071 | 2.0228 | 2.0228 | 2.0228 | 2.0228
2024-12-04 03:00 | 1.3527 | 1.6828 | 2.0331 | 2.0798 | 2.1265 | 2024-10-04 02:00 | 1.7224 | 2.0408 | 2.0408 | 2.0408 | 2.0408
2024-12-04 04:00 | 1.4099 | 1.7539 | 2.119 | 2.1677 | 2.2164 | 2024-10-04 03:00 | 1.8633 | 2.2079 | 2.2079 | 2.2079 | 2.2079
2024-12-04 05:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-10-04 04:00 | 2.172 | 2.5736 | 2.5736 | 2.5736 | 2.5736
2024-12-04 06:00 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2024-10-04 05:00 | 2.2977 | 2.7226 | 2.7226 | 2.7226 | 2.7226
2024-12-04 07:00 | 0.38105 | 0.47402 | 0.5727 | 0.58586 | 0.59902 | 2024-10-04 06:00 | 2.5759 | 3.0522 | 3.0522 | 3.0522 | 3.0522
2024-12-04 08:00 | 0.22863 | 0.28441 | 0.34362 | 0.35152 | 0.35941 | 2024-10-04 07:00 | 2.5988 | 3.0793 | 3.0793 | 3.0793 | 3.0793
2024-12-04 09:00 | 0.30484 | 0.37921 | 0.45816 | 0.46869 | 0.47921 | 2024-10-04 08:00 | 3.1856 | 3.7747 | 3.7747 | 3.7747 | 3.7747
2024-12-04 10:00 | 0.38105 | 0.47402 | 0.5727 | 0.58586 | 0.59902 | 2024-10-04 09:00 | 3.1322 | 3.7114 | 3.7114 | 3.7114 | 3.7114
2024-12-04 11:00 | 0.59063 | 0.73473 | 0.88769 | 0.90808 | 0.92848 | 2024-10-04 10:00 | 3.4066 | 4.0365 | 4.0365 | 4.0365 | 4.0365
2024-12-04 12:00 | 2.191 | 2.7256 | 3.293 | 3.3687 | 3.4444 | 2024-10-04 11:00 | 3.3723 | 3.9959 | 3.9959 | 3.9959 | 3.9959
2024-12-04 13:00 | 2.896 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2024-10-04 12:00 | 3.7915 | 4.4926 | 4.4926 | 4.4926 | 4.4926
2024-12-04 14:00 | 2.7245 | 3.3892 | 4.0948 | 4.1889 | 4.283 | 2024-10-04 13:00 | 3.6428 | 4.3165 | 4.3165 | 4.3165 | 4.3165
2024-12-04 15:00 | 2.3054 | 2.8678 | 3.4648 | 3.5445 | 3.6241 | 2024-10-04 14:00 | 3.7 | 4.3842 | 4.3842 | 4.3842 | 4.3842
2024-12-04 16:00 | 2.5911 | 3.2233 | 3.8944 | 3.9838 | 4.0733 | 2024-10-04 15:00 | 3.8181 | 4.5242 | 4.5242 | 4.5242 | 4.5242
2024-12-04 17:00 | 2.534 | 3.1522 | 3.8085 | 3.896 | 3.9835 | 2024-10-04 16:00 | 3.7191 | 4.4068 | 4.4068 | 4.4068 | 4.4068
2024-12-04 18:00 | 2.0196 | 2.5123 | 3.0353 | 3.1051 | 3.1748 | 2024-10-04 17:00 | 3.5743 | 4.2352 | 4.2352 | 4.2352 | 4.2352
2024-12-04 19:00 | 1.9815 | 2.4649 | 2.9781 | 3.0465 | 3.1149 | 2024-10-04 18:00 | 3.5438 | 4.1991 | 4.1991 | 4.1991 | 4.1991
2024-12-04 20:00 | 1.8481 | 2.299 | 2.7776 | 2.8414 | 2.9052 | 2024-10-04 19:00 | 3.037 | 3.5986 | 3.5986 | 3.5986 | 3.5986
2024-12-04 21:00 | 1.7528 | 2.1805 | 2.6344 | 2.695 | 2.7555 | 2024-10-04 20:00 | 2.7512 | 3.2599 | 3.2599 | 3.2599 | 3.2599
2024-12-04 22:00 | 1.7147 | 2.1331 | 2.5772 | 2.6364 | 2.6956 | 2024-10-04 21:00 | 2.6026 | 3.0838 | 3.0838 | 3.0838 | 3.0838
2024-12-04 23:00 | 1.7147 | 2.1331 | 2.5772 | 2.6364 | 2.6956 | 2024-10-04 22:00 | 1.9929 | 2.3614 | 2.3614 | 2.3614 | 2.3614
2024-12-05 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2024-10-04 23:00 | 2.0996 | 2.4878 | 2.4878 | 2.4878 | 2.4878
2024-12-05 01:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2024-10-05 | 1.8214 | 2.1582 | 2.1582 | 2.1582 | 2.1582
2024-12-05 02:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-10-05 01:00 | 1.7757 | 2.1041 | 2.1041 | 2.1041 | 2.1041
2024-12-05 03:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-10-05 02:00 | 1.7338 | 2.0544 | 2.0544 | 2.0544 | 2.0544
2024-12-05 04:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-10-05 03:00 | 1.8557 | 2.1989 | 2.1989 | 2.1989 | 2.1989
2024-12-05 05:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2024-10-05 04:00 | 1.9815 | 2.3479 | 2.3479 | 2.3479 | 2.3479
2024-12-05 06:00 | 1.81 | 2.2516 | 2.7203 | 2.7828 | 2.8453 | 2024-10-05 05:00 | 2.2977 | 2.7226 | 2.7226 | 2.7226 | 2.7226
2024-12-05 07:00 | 2.3244 | 2.8915 | 3.4935 | 3.5737 | 3.654 | 2024-10-05 06:00 | 2.3282 | 2.7587 | 2.7587 | 2.7587 | 2.7587
2024-12-05 08:00 | 2.6483 | 3.2944 | 3.9803 | 4.0717 | 4.1632 | 2024-10-05 07:00 | 2.1606 | 2.5601 | 2.5601 | 2.5601 | 2.5601
2024-12-05 09:00 | 2.9341 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2024-10-05 08:00 | 2.5569 | 3.0297 | 3.0297 | 3.0297 | 3.0297
2024-12-05 10:00 | 2.7626 | 3.4366 | 4.1521 | 4.2475 | 4.3429 | 2024-10-05 09:00 | 2.8312 | 3.3547 | 3.3547 | 3.3547 | 3.3547
2024-12-05 11:00 | 2.0767 | 2.5834 | 3.1212 | 3.1929 | 3.2646 | 2024-10-05 10:00 | 2.915 | 3.4541 | 3.4541 | 3.4541 | 3.4541
2024-12-05 12:00 | 2.3054 | 2.8678 | 3.4648 | 3.5445 | 3.6241 | 2024-10-05 11:00 | 3.0065 | 3.5624 | 3.5624 | 3.5624 | 3.5624
2024-12-05 13:00 | 1.7909 | 2.2279 | 2.6917 | 2.7535 | 2.8154 | 2024-10-05 12:00 | 3.1208 | 3.6979 | 3.6979 | 3.6979 | 3.6979
2024-12-05 14:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2024-10-05 13:00 | 2.8579 | 3.3864 | 3.3864 | 3.3864 | 3.3864
2024-12-05 15:00 | 2.4197 | 3.01 | 3.6367 | 3.7202 | 3.8038 | 2024-10-05 14:00 | 3.0637 | 3.6302 | 3.6302 | 3.6302 | 3.6302
2024-12-05 16:00 | 2.2482 | 2.7967 | 3.3789 | 3.4566 | 3.5342 | 2024-10-05 15:00 | 2.8426 | 3.3683 | 3.3683 | 3.3683 | 3.3683
2024-12-05 17:00 | 2.2673 | 2.8204 | 3.4076 | 3.4859 | 3.5642 | 2024-10-05 16:00 | 3.037 | 3.5986 | 3.5986 | 3.5986 | 3.5986
2024-12-05 18:00 | 1.9815 | 2.4649 | 2.9781 | 3.0465 | 3.1149 | 2024-10-05 17:00 | 3.0294 | 3.5895 | 3.5895 | 3.5895 | 3.5895
2024-12-05 19:00 | 1.7719 | 2.2042 | 2.6631 | 2.7242 | 2.7854 | 2024-10-05 18:00 | 2.8388 | 3.3638 | 3.3638 | 3.3638 | 3.3638
2024-12-05 20:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2024-10-05 19:00 | 2.5607 | 3.0342 | 3.0342 | 3.0342 | 3.0342
2024-12-05 21:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-10-05 20:00 | 2.3778 | 2.8174 | 2.8174 | 2.8174 | 2.8174
2024-12-05 22:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-10-05 21:00 | 2.1567 | 2.5556 | 2.5556 | 2.5556 | 2.5556
2024-12-05 23:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-10-05 22:00 | 1.9738 | 2.3388 | 2.3388 | 2.3388 | 2.3388
2024-12-06 | 1.2956 | 1.6117 | 1.9472 | 1.9919 | 2.0367 | 2024-10-05 23:00 | 1.7871 | 2.1176 | 2.1176 | 2.1176 | 2.1176
2024-12-06 01:00 | 1.3337 | 1.6591 | 2.0045 | 2.0505 | 2.0966 | 2024-10-06 | 1.8062 | 2.1402 | 2.1402 | 2.1402 | 2.1402
2024-12-06 02:00 | 1.3527 | 1.6828 | 2.0331 | 2.0798 | 2.1265 | 2024-10-06 01:00 | 1.8252 | 2.1628 | 2.1628 | 2.1628 | 2.1628
2024-12-06 03:00 | 1.2956 | 1.6117 | 1.9472 | 1.9919 | 2.0367 | 2024-10-06 03:00 | 1.8595 | 2.2034 | 2.2034 | 2.2034 | 2.2034
2024-12-06 04:00 | 1.3718 | 1.7065 | 2.0617 | 2.1091 | 2.1565 | 2024-10-06 04:00 | 1.9167 | 2.2711 | 2.2711 | 2.2711 | 2.2711
2024-12-06 05:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2024-10-06 05:00 | 2.2673 | 2.6865 | 2.6865 | 2.6865 | 2.6865
2024-12-06 06:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-10-06 06:00 | 2.4082 | 2.8536 | 2.8536 | 2.8536 | 2.8536
2024-12-06 07:00 | 0.57158 | 0.71103 | 0.85905 | 0.87879 | 0.89853 | 2024-10-06 07:00 | 2.5645 | 3.0387 | 3.0387 | 3.0387 | 3.0387
2024-12-06 08:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-10-06 08:00 | 2.5607 | 3.0342 | 3.0342 | 3.0342 | 3.0342
2024-12-06 09:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2024-10-06 09:00 | 2.5797 | 3.0567 | 3.0567 | 3.0567 | 3.0567
2024-12-06 10:00 | 0.019053 | 0.023701 | 0.028635 | 0.029293 | 0.029951 | 2024-10-06 10:00 | 2.915 | 3.4541 | 3.4541 | 3.4541 | 3.4541
2024-12-06 11:00 | 1.2575 | 1.5643 | 1.8899 | 1.9333 | 1.9768 | 2024-10-06 11:00 | 3.1703 | 3.7566 | 3.7566 | 3.7566 | 3.7566
2024-12-06 12:00 | 0.93358 | 1.1613 | 1.4031 | 1.4354 | 1.4676 | 2024-10-06 12:00 | 3.1399 | 3.7205 | 3.7205 | 3.7205 | 3.7205
2024-12-06 13:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2024-10-06 13:00 | 3.117 | 3.6934 | 3.6934 | 3.6934 | 3.6934
2024-12-06 14:00 | 2.2291 | 2.773 | 3.3503 | 3.4273 | 3.5043 | 2024-10-06 14:00 | 3.0522 | 3.6166 | 3.6166 | 3.6166 | 3.6166
2024-12-06 15:00 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2024-10-06 15:00 | 3.0065 | 3.5624 | 3.5624 | 3.5624 | 3.5624
2024-12-06 16:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2024-10-06 16:00 | 2.755 | 3.2644 | 3.2644 | 3.2644 | 3.2644
2024-12-06 17:00 | 1.9815 | 2.4649 | 2.9781 | 3.0465 | 3.1149 | 2024-10-06 17:00 | 2.755 | 3.2644 | 3.2644 | 3.2644 | 3.2644
2024-12-06 18:00 | 1.3718 | 1.7065 | 2.0617 | 2.1091 | 2.1565 | 2024-10-06 18:00 | 2.6369 | 3.1245 | 3.1245 | 3.1245 | 3.1245
2024-12-06 19:00 | 1.3337 | 1.6591 | 2.0045 | 2.0505 | 2.0966 | 2024-10-06 19:00 | 2.3701 | 2.8084 | 2.8084 | 2.8084 | 2.8084
2024-12-06 20:00 | 1.2956 | 1.6117 | 1.9472 | 1.9919 | 2.0367 | 2024-10-06 20:00 | 2.4311 | 2.8807 | 2.8807 | 2.8807 | 2.8807
2024-12-06 21:00 | 1.3146 | 1.6354 | 1.9758 | 2.0212 | 2.0666 | 2024-10-06 21:00 | 2.1491 | 2.5465 | 2.5465 | 2.5465 | 2.5465
2024-12-06 22:00 | 1.2575 | 1.5643 | 1.8899 | 1.9333 | 1.9768 | 2024-10-06 22:00 | 2.0577 | 2.4382 | 2.4382 | 2.4382 | 2.4382
2024-12-06 23:00 | 1.2765 | 1.588 | 1.9186 | 1.9626 | 2.0067 | 2024-10-06 23:00 | 1.8595 | 2.2034 | 2.2034 | 2.2034 | 2.2034
2024-12-07 | 1.2194 | 1.5169 | 1.8326 | 1.8748 | 1.9169 | 2024-10-07 | 1.7376 | 2.0589 | 2.0589 | 2.0589 | 2.0589
2024-12-07 01:00 | 1.2384 | 1.5406 | 1.8613 | 1.904 | 1.9468 | 2024-10-07 01:00 | 1.7528 | 2.077 | 2.077 | 2.077 | 2.077
2024-12-07 02:00 | 1.2575 | 1.5643 | 1.8899 | 1.9333 | 1.9768 | 2024-10-07 02:00 | 1.7528 | 2.077 | 2.077 | 2.077 | 2.077
2024-12-07 03:00 | 1.2384 | 1.5406 | 1.8613 | 1.904 | 1.9468 | 2024-10-07 03:00 | 1.8443 | 2.1853 | 2.1853 | 2.1853 | 2.1853
2024-12-07 04:00 | 1.3337 | 1.6591 | 2.0045 | 2.0505 | 2.0966 | 2024-10-07 04:00 | 1.9091 | 2.2621 | 2.2621 | 2.2621 | 2.2621
2024-12-07 05:00 | 1.3908 | 1.7302 | 2.0904 | 2.1384 | 2.1864 | 2024-10-07 05:00 | 2.2177 | 2.6278 | 2.6278 | 2.6278 | 2.6278
2024-12-07 06:00 | 1.4099 | 1.7539 | 2.119 | 2.1677 | 2.2164 | 2024-10-07 06:00 | 2.4921 | 2.9529 | 2.9529 | 2.9529 | 2.9529
2024-12-07 07:00 | 1.105 | 1.3747 | 1.6608 | 1.699 | 1.7372 | 2024-10-07 07:00 | 2.7931 | 3.3096 | 3.3096 | 3.3096 | 3.3096
2024-12-07 08:00 | 0.95263 | 1.185 | 1.4318 | 1.4646 | 1.4975 | 2024-10-07 08:00 | 2.9417 | 3.4857 | 3.4857 | 3.4857 | 3.4857
2024-12-07 09:00 | 0.68589 | 0.85323 | 1.0309 | 1.0545 | 1.0782 | 2024-10-07 09:00 | 2.755 | 3.2644 | 3.2644 | 3.2644 | 3.2644
2024-12-07 10:00 | 0.724 | 0.90063 | 1.0881 | 1.1131 | 1.1381 | 2024-10-07 10:00 | 2.9189 | 3.4586 | 3.4586 | 3.4586 | 3.4586
2024-12-07 11:00 | 0.57158 | 0.71103 | 0.85905 | 0.87879 | 0.89853 | 2024-10-07 11:00 | 3.3113 | 3.9237 | 3.9237 | 3.9237 | 3.9237
2024-12-07 12:00 | 0.60968 | 0.75843 | 0.91632 | 0.93738 | 0.95843 | 2024-10-07 12:00 | 3.4561 | 4.0952 | 4.0952 | 4.0952 | 4.0952
2024-12-07 13:00 | 0.4001 | 0.49772 | 0.60134 | 0.61515 | 0.62897 | 2024-10-07 13:00 | 3.3418 | 3.9598 | 3.9598 | 3.9598 | 3.9598
2024-12-07 14:00 | 0.87642 | 1.0902 | 1.3172 | 1.3475 | 1.3777 | 2024-10-07 14:00 | 3.2809 | 3.8875 | 3.8875 | 3.8875 | 3.8875
2024-12-07 15:00 | 0.4001 | 0.49772 | 0.60134 | 0.61515 | 0.62897 | 2024-10-07 15:00 | 3.1703 | 3.7566 | 3.7566 | 3.7566 | 3.7566
2024-12-07 16:00 | 0.81926 | 1.0191 | 1.2313 | 1.2596 | 1.2879 | 2024-10-07 16:00 | 3.1703 | 3.7566 | 3.7566 | 3.7566 | 3.7566
2024-12-07 17:00 | 0.62873 | 0.78213 | 0.94496 | 0.96667 | 0.98838 | 2024-10-07 17:00 | 2.9112 | 3.4496 | 3.4496 | 3.4496 | 3.4496
2024-12-07 18:00 | 1.1432 | 1.4221 | 1.7181 | 1.7576 | 1.7971 | 2024-10-07 18:00 | 2.8846 | 3.418 | 3.418 | 3.418 | 3.418
2024-12-07 19:00 | 1.3527 | 1.6828 | 2.0331 | 2.0798 | 2.1265 | 2024-10-07 19:00 | 2.6216 | 3.1064 | 3.1064 | 3.1064 | 3.1064
2024-12-07 20:00 | 1.2575 | 1.5643 | 1.8899 | 1.9333 | 1.9768 | 2024-10-07 20:00 | 2.3587 | 2.7949 | 2.7949 | 2.7949 | 2.7949
2024-12-07 21:00 | 1.3718 | 1.7065 | 2.0617 | 2.1091 | 2.1565 | 2024-10-07 21:00 | 2.0577 | 2.4382 | 2.4382 | 2.4382 | 2.4382
2024-12-07 22:00 | 1.4099 | 1.7539 | 2.119 | 2.1677 | 2.2164 | 2024-10-07 22:00 | 1.8405 | 2.1808 | 2.1808 | 2.1808 | 2.1808
2024-12-07 23:00 | 1.3146 | 1.6354 | 1.9758 | 2.0212 | 2.0666 | 2024-10-07 23:00 | 1.8557 | 2.1989 | 2.1989 | 2.1989 | 2.1989
2024-12-08 | 1.2575 | 1.5643 | 1.8899 | 1.9333 | 1.9768 | 2024-10-08 | 1.7566 | 2.0815 | 2.0815 | 2.0815 | 2.0815
2024-12-08 01:00 | 1.3337 | 1.6591 | 2.0045 | 2.0505 | 2.0966 | 2024-10-08 01:00 | 1.7185 | 2.0363 | 2.0363 | 2.0363 | 2.0363
2024-12-08 02:00 | 1.3337 | 1.6591 | 2.0045 | 2.0505 | 2.0966 | 2024-10-08 02:00 | 1.6957 | 2.0092 | 2.0092 | 2.0092 | 2.0092
2024-12-08 03:00 | 1.3146 | 1.6354 | 1.9758 | 2.0212 | 2.0666 | 2024-10-08 03:00 | 1.9167 | 2.2711 | 2.2711 | 2.2711 | 2.2711
2024-12-08 04:00 | 1.3146 | 1.6354 | 1.9758 | 2.0212 | 2.0666 | 2024-10-08 04:00 | 2.0348 | 2.4111 | 2.4111 | 2.4111 | 2.4111
2024-12-08 05:00 | 1.3527 | 1.6828 | 2.0331 | 2.0798 | 2.1265 | 2024-10-08 05:00 | 2.3358 | 2.7678 | 2.7678 | 2.7678 | 2.7678
2024-12-08 06:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-10-08 06:00 | 2.6445 | 3.1335 | 3.1335 | 3.1335 | 3.1335
2024-12-08 07:00 | 1.3337 | 1.6591 | 2.0045 | 2.0505 | 2.0966 | 2024-10-08 07:00 | 3.1208 | 3.6979 | 3.6979 | 3.6979 | 3.6979
2024-12-08 08:00 | 0.91452 | 1.1376 | 1.3745 | 1.4061 | 1.4376 | 2024-10-08 08:00 | 3.5133 | 4.163 | 4.163 | 4.163 | 4.163
2024-12-08 09:00 | 0.49537 | 0.61622 | 0.74451 | 0.76162 | 0.77872 | 2024-10-08 09:00 | 3.5514 | 4.2081 | 4.2081 | 4.2081 | 4.2081
2024-12-08 10:00 | 0.38105 | 0.47402 | 0.5727 | 0.58586 | 0.59902 | 2024-10-08 10:00 | 3.8867 | 4.6054 | 4.6054 | 4.6054 | 4.6054
2024-12-08 11:00 | 0.057158 | 0.071103 | 0.085905 | 0.087879 | 0.089853 | 2024-10-08 11:00 | 3.7229 | 4.4113 | 4.4113 | 4.4113 | 4.4113
2024-12-08 12:00 | 0.51442 | 0.63992 | 0.77315 | 0.79091 | 0.80867 | 2024-10-08 12:00 | 3.6619 | 4.339 | 4.339 | 4.339 | 4.339
2024-12-08 13:00 | 0.60968 | 0.75843 | 0.91632 | 0.93738 | 0.95843 | 2024-10-08 13:00 | 3.5209 | 4.172 | 4.172 | 4.172 | 4.172
2024-12-08 14:00 | 0.45726 | 0.56882 | 0.68724 | 0.70303 | 0.71882 | 2024-10-08 14:00 | 3.3647 | 3.9869 | 3.9869 | 3.9869 | 3.9869
2024-12-08 15:00 | 1.086 | 1.351 | 1.6322 | 1.6697 | 1.7072 | 2024-10-08 15:00 | 2.9646 | 3.5128 | 3.5128 | 3.5128 | 3.5128
2024-12-08 16:00 | 0.22906 | 0.28495 | 0.34427 | 0.35218 | 0.36009 | 2024-10-08 16:00 | 3.2961 | 3.9056 | 3.9056 | 3.9056 | 3.9056
2024-12-08 17:00 | 1.3146 | 1.6354 | 1.9758 | 2.0212 | 2.0666 | 2024-10-08 17:00 | 3.2237 | 3.8198 | 3.8198 | 3.8198 | 3.8198
2024-12-08 18:00 | 1.9243 | 2.3938 | 2.8921 | 2.9586 | 3.025 | 2024-10-08 18:00 | 2.9074 | 3.4451 | 3.4451 | 3.4451 | 3.4451
2024-12-08 19:00 | 1.7719 | 2.2042 | 2.6631 | 2.7242 | 2.7854 | 2024-10-08 19:00 | 2.7779 | 3.2915 | 3.2915 | 3.2915 | 3.2915
2024-12-08 20:00 | 1.7909 | 2.2279 | 2.6917 | 2.7535 | 2.8154 | 2024-10-08 20:00 | 2.5683 | 3.0432 | 3.0432 | 3.0432 | 3.0432
2024-12-08 21:00 | 1.8481 | 2.299 | 2.7776 | 2.8414 | 2.9052 | 2024-10-08 21:00 | 2.2291 | 2.6414 | 2.6414 | 2.6414 | 2.6414
2024-12-08 22:00 | 1.9434 | 2.4175 | 2.9208 | 2.9879 | 3.055 | 2024-10-08 22:00 | 2.0615 | 2.4427 | 2.4427 | 2.4427 | 2.4427
2024-12-08 23:00 | 1.7909 | 2.2279 | 2.6917 | 2.7535 | 2.8154 | 2024-10-08 23:00 | 1.9357 | 2.2937 | 2.2937 | 2.2937 | 2.2937
2024-12-09 | 1.81 | 2.2516 | 2.7203 | 2.7828 | 2.8453 | 2024-10-09 | 1.7376 | 2.0589 | 2.0589 | 2.0589 | 2.0589
2024-12-09 01:00 | 1.7147 | 2.1331 | 2.5772 | 2.6364 | 2.6956 | 2024-10-09 01:00 | 1.7643 | 2.0905 | 2.0905 | 2.0905 | 2.0905
2024-12-09 02:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2024-10-09 02:00 | 1.7185 | 2.0363 | 2.0363 | 2.0363 | 2.0363
2024-12-09 03:00 | 1.6957 | 2.1094 | 2.5485 | 2.6071 | 2.6656 | 2024-10-09 03:00 | 1.9319 | 2.2892 | 2.2892 | 2.2892 | 2.2892
2024-12-09 04:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2024-10-09 04:00 | 2.1606 | 2.5601 | 2.5601 | 2.5601 | 2.5601
2024-12-09 05:00 | 1.8481 | 2.299 | 2.7776 | 2.8414 | 2.9052 | 2024-10-09 05:00 | 2.3701 | 2.8084 | 2.8084 | 2.8084 | 2.8084
2024-12-09 06:00 | 1.9815 | 2.4649 | 2.9781 | 3.0465 | 3.1149 | 2024-10-09 06:00 | 2.8198 | 3.3412 | 3.3412 | 3.3412 | 3.3412
2024-12-09 07:00 | 2.2863 | 2.8441 | 3.4362 | 3.5152 | 3.5941 | 2024-10-09 07:00 | 3.0789 | 3.6482 | 3.6482 | 3.6482 | 3.6482
2024-12-09 08:00 | 2.3625 | 2.9389 | 3.5508 | 3.6323 | 3.7139 | 2024-10-09 08:00 | 3.3075 | 3.9191 | 3.9191 | 3.9191 | 3.9191
2024-12-09 09:00 | 2.1148 | 2.6308 | 3.1785 | 3.2515 | 3.3245 | 2024-10-09 09:00 | 3.1094 | 3.6844 | 3.6844 | 3.6844 | 3.6844
2024-12-09 10:00 | 2.5149 | 3.1285 | 3.7798 | 3.8667 | 3.9535 | 2024-10-09 10:00 | 3.4942 | 4.1404 | 4.1404 | 4.1404 | 4.1404
2024-12-09 11:00 | 3.2008 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2024-10-09 11:00 | 3.5362 | 4.19 | 4.19 | 4.19 | 4.19
2024-12-09 12:00 | 2.6864 | 3.3418 | 4.0375 | 4.1303 | 4.2231 | 2024-10-09 12:00 | 3.54 | 4.1946 | 4.1946 | 4.1946 | 4.1946
2024-12-09 13:00 | 1.7528 | 2.1805 | 2.6344 | 2.695 | 2.7555 | 2024-10-09 13:00 | 3.5895 | 4.2533 | 4.2533 | 4.2533 | 4.2533
2024-12-09 14:00 | 1.2956 | 1.6117 | 1.9472 | 1.9919 | 2.0367 | 2024-10-09 14:00 | 3.1513 | 3.734 | 3.734 | 3.734 | 3.734
2024-12-09 15:00 | 1.7719 | 2.2042 | 2.6631 | 2.7242 | 2.7854 | 2024-10-09 15:00 | 3.0065 | 3.5624 | 3.5624 | 3.5624 | 3.5624
2024-12-09 16:00 | 2.1339 | 2.6545 | 3.2071 | 3.2808 | 3.3545 | 2024-10-09 16:00 | 3.2542 | 3.8559 | 3.8559 | 3.8559 | 3.8559
2024-12-09 17:00 | 2.3244 | 2.8915 | 3.4935 | 3.5737 | 3.654 | 2024-10-09 17:00 | 3.1208 | 3.6979 | 3.6979 | 3.6979 | 3.6979
2024-12-09 18:00 | 2.3816 | 2.9626 | 3.5794 | 3.6616 | 3.7439 | 2024-10-09 18:00 | 2.9836 | 3.5354 | 3.5354 | 3.5354 | 3.5354
2024-12-09 19:00 | 1.8672 | 2.3227 | 2.8062 | 2.8707 | 2.9352 | 2024-10-09 19:00 | 2.7055 | 3.2057 | 3.2057 | 3.2057 | 3.2057
2024-12-09 20:00 | 1.9053 | 2.3701 | 2.8635 | 2.9293 | 2.9951 | 2024-10-09 20:00 | 2.675 | 3.1696 | 3.1696 | 3.1696 | 3.1696
2024-12-09 21:00 | 1.6957 | 2.1094 | 2.5485 | 2.6071 | 2.6656 | 2024-10-09 21:00 | 2.3397 | 2.7723 | 2.7723 | 2.7723 | 2.7723
2024-12-09 22:00 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2024-10-09 22:00 | 2.0043 | 2.375 | 2.375 | 2.375 | 2.375
2024-12-09 23:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2024-10-09 23:00 | 1.9434 | 2.3027 | 2.3027 | 2.3027 | 2.3027
2024-12-10 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-10-10 | 1.81 | 2.1447 | 2.1447 | 2.1447 | 2.1447
2024-12-10 01:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-10-10 01:00 | 1.7833 | 2.1131 | 2.1131 | 2.1131 | 2.1131
2024-12-10 02:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-10-10 02:00 | 1.7757 | 2.1041 | 2.1041 | 2.1041 | 2.1041
2024-12-10 03:00 | 1.3908 | 1.7302 | 2.0904 | 2.1384 | 2.1864 | 2024-10-10 03:00 | 1.9319 | 2.2892 | 2.2892 | 2.2892 | 2.2892
2024-12-10 04:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-10-10 04:00 | 2.0958 | 2.4833 | 2.4833 | 2.4833 | 2.4833
2024-12-10 05:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2024-10-10 05:00 | 2.5264 | 2.9935 | 2.9935 | 2.9935 | 2.9935
2024-12-10 06:00 | 1.829 | 2.2753 | 2.749 | 2.8121 | 2.8753 | 2024-10-10 06:00 | 2.8122 | 3.3322 | 3.3322 | 3.3322 | 3.3322
2024-12-10 07:00 | 2.3816 | 2.9626 | 3.5794 | 3.6616 | 3.7439 | 2024-10-10 07:00 | 2.9455 | 3.4902 | 3.4902 | 3.4902 | 3.4902
2024-12-10 08:00 | 2.1529 | 2.6782 | 3.2358 | 3.3101 | 3.3845 | 2024-10-10 08:00 | 3.178 | 3.7656 | 3.7656 | 3.7656 | 3.7656
2024-12-10 09:00 | 2.0386 | 2.536 | 3.064 | 3.1344 | 3.2047 | 2024-10-10 09:00 | 3.2123 | 3.8063 | 3.8063 | 3.8063 | 3.8063
2024-12-10 10:00 | 1.7147 | 2.1331 | 2.5772 | 2.6364 | 2.6956 | 2024-10-10 10:00 | 3.0675 | 3.6347 | 3.6347 | 3.6347 | 3.6347
2024-12-10 11:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2024-10-10 11:00 | 3.0332 | 3.5941 | 3.5941 | 3.5941 | 3.5941
2024-12-10 12:00 | 1.7909 | 2.2279 | 2.6917 | 2.7535 | 2.8154 | 2024-10-10 12:00 | 3.1322 | 3.7114 | 3.7114 | 3.7114 | 3.7114
2024-12-10 13:00 | 2.3244 | 2.8915 | 3.4935 | 3.5737 | 3.654 | 2024-10-10 13:00 | 2.9341 | 3.4767 | 3.4767 | 3.4767 | 3.4767
2024-12-10 14:00 | 2.4578 | 3.0574 | 3.6939 | 3.7788 | 3.8637 | 2024-10-10 14:00 | 3.1513 | 3.734 | 3.734 | 3.734 | 3.734
2024-12-10 15:00 | 1.8862 | 2.3464 | 2.8349 | 2.9 | 2.9651 | 2024-10-10 15:00 | 3.4599 | 4.0997 | 4.0997 | 4.0997 | 4.0997
2024-12-10 16:00 | 1.9053 | 2.3701 | 2.8635 | 2.9293 | 2.9951 | 2024-10-10 16:00 | 3.5971 | 4.2623 | 4.2623 | 4.2623 | 4.2623
2024-12-10 17:00 | 1.7338 | 2.1568 | 2.6058 | 2.6657 | 2.7255 | 2024-10-10 17:00 | 3.4714 | 4.1133 | 4.1133 | 4.1133 | 4.1133
2024-12-10 18:00 | 2.3625 | 2.9389 | 3.5508 | 3.6323 | 3.7139 | 2024-10-10 18:00 | 3.0941 | 3.6663 | 3.6663 | 3.6663 | 3.6663
2024-12-10 19:00 | 1.8481 | 2.299 | 2.7776 | 2.8414 | 2.9052 | 2024-10-10 19:00 | 2.7969 | 3.3141 | 3.3141 | 3.3141 | 3.3141
2024-12-10 20:00 | 1.8481 | 2.299 | 2.7776 | 2.8414 | 2.9052 | 2024-10-10 20:00 | 2.7436 | 3.2509 | 3.2509 | 3.2509 | 3.2509
2024-12-10 21:00 | 1.81 | 2.2516 | 2.7203 | 2.7828 | 2.8453 | 2024-10-10 21:00 | 2.3244 | 2.7542 | 2.7542 | 2.7542 | 2.7542
2024-12-10 22:00 | 1.7147 | 2.1331 | 2.5772 | 2.6364 | 2.6956 | 2024-10-10 22:00 | 2.0577 | 2.4382 | 2.4382 | 2.4382 | 2.4382
2024-12-10 23:00 | 1.7147 | 2.1331 | 2.5772 | 2.6364 | 2.6956 | 2024-10-10 23:00 | 1.9815 | 2.3479 | 2.3479 | 2.3479 | 2.3479
2024-12-11 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-10-11 | 1.7986 | 2.1311 | 2.1311 | 2.1311 | 2.1311
2024-12-11 01:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-10-11 01:00 | 1.8672 | 2.2124 | 2.2124 | 2.2124 | 2.2124
2024-12-11 02:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2024-10-11 02:00 | 1.8214 | 2.1582 | 2.1582 | 2.1582 | 2.1582
2024-12-11 03:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-10-11 03:00 | 1.951 | 2.3118 | 2.3118 | 2.3118 | 2.3118
2024-12-11 04:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2024-10-11 04:00 | 2.1301 | 2.524 | 2.524 | 2.524 | 2.524
2024-12-11 05:00 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2024-10-11 05:00 | 2.3435 | 2.7768 | 2.7768 | 2.7768 | 2.7768
2024-12-11 06:00 | 1.7338 | 2.1568 | 2.6058 | 2.6657 | 2.7255 | 2024-10-11 06:00 | 2.6826 | 3.1787 | 3.1787 | 3.1787 | 3.1787
2024-12-11 07:00 | 0.83831 | 1.0428 | 1.2599 | 1.2889 | 1.3178 | 2024-10-11 07:00 | 2.9112 | 3.4496 | 3.4496 | 3.4496 | 3.4496
2024-12-11 08:00 | 0.78115 | 0.97174 | 1.174 | 1.201 | 1.228 | 2024-10-11 08:00 | 3.3266 | 3.9417 | 3.9417 | 3.9417 | 3.9417
2024-12-11 09:00 | 0.70494 | 0.87693 | 1.0595 | 1.0838 | 1.1082 | 2024-10-11 09:00 | 3.2085 | 3.8017 | 3.8017 | 3.8017 | 3.8017
2024-12-11 10:00 | 0.78115 | 0.97174 | 1.174 | 1.201 | 1.228 | 2024-10-11 10:00 | 3.2466 | 3.8469 | 3.8469 | 3.8469 | 3.8469
2024-12-11 11:00 | 0.95263 | 1.185 | 1.4318 | 1.4646 | 1.4975 | 2024-10-11 11:00 | 3.2999 | 3.9101 | 3.9101 | 3.9101 | 3.9101
2024-12-11 12:00 | 2.5149 | 3.1285 | 3.7798 | 3.8667 | 3.9535 | 2024-10-11 12:00 | 3.2656 | 3.8695 | 3.8695 | 3.8695 | 3.8695
2024-12-11 13:00 | 3.258 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2024-10-11 13:00 | 3.6428 | 4.3165 | 4.3165 | 4.3165 | 4.3165
2024-12-11 14:00 | 3.277 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2024-10-11 14:00 | 3.6886 | 4.3707 | 4.3707 | 4.3707 | 4.3707
2024-12-11 15:00 | 2.8579 | 3.5551 | 4.2953 | 4.3939 | 4.4926 | 2024-10-11 15:00 | 3.8334 | 4.5422 | 4.5422 | 4.5422 | 4.5422
2024-12-11 16:00 | 3.1437 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2024-10-11 16:00 | 3.7762 | 4.4745 | 4.4745 | 4.4745 | 4.4745
2024-12-11 17:00 | 3.1056 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2024-10-11 17:00 | 3.7724 | 4.47 | 4.47 | 4.47 | 4.47
2024-12-11 18:00 | 2.5721 | 3.1996 | 3.8657 | 3.9546 | 4.0434 | 2024-10-11 18:00 | 3.1932 | 3.7837 | 3.7837 | 3.7837 | 3.7837
2024-12-11 19:00 | 1.9815 | 2.4649 | 2.9781 | 3.0465 | 3.1149 | 2024-10-11 19:00 | 3.0979 | 3.6708 | 3.6708 | 3.6708 | 3.6708
2024-12-11 20:00 | 1.8481 | 2.299 | 2.7776 | 2.8414 | 2.9052 | 2024-10-11 20:00 | 2.7702 | 3.2825 | 3.2825 | 3.2825 | 3.2825
2024-12-11 21:00 | 1.7338 | 2.1568 | 2.6058 | 2.6657 | 2.7255 | 2024-10-11 21:00 | 2.7169 | 3.2193 | 3.2193 | 3.2193 | 3.2193
2024-12-11 22:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2024-10-11 22:00 | 1.9205 | 2.2756 | 2.2756 | 2.2756 | 2.2756
2024-12-11 23:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2024-10-11 23:00 | 2.0805 | 2.4653 | 2.4653 | 2.4653 | 2.4653
2024-12-12 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2024-10-12 | 1.829 | 2.1673 | 2.1673 | 2.1673 | 2.1673
2024-12-12 01:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-10-12 01:00 | 1.8138 | 2.1492 | 2.1492 | 2.1492 | 2.1492
2024-12-12 02:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-10-12 02:00 | 1.8748 | 2.2214 | 2.2214 | 2.2214 | 2.2214
2024-12-12 03:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-10-12 03:00 | 1.8976 | 2.2485 | 2.2485 | 2.2485 | 2.2485
2024-12-12 04:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-10-12 04:00 | 2.0005 | 2.3704 | 2.3704 | 2.3704 | 2.3704
2024-12-12 05:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2024-10-12 05:00 | 2.3015 | 2.7271 | 2.7271 | 2.7271 | 2.7271
2024-12-12 06:00 | 1.9053 | 2.3701 | 2.8635 | 2.9293 | 2.9951 | 2024-10-12 06:00 | 2.3587 | 2.7949 | 2.7949 | 2.7949 | 2.7949
2024-12-12 07:00 | 2.4578 | 3.0574 | 3.6939 | 3.7788 | 3.8637 | 2024-10-12 07:00 | 2.5073 | 2.971 | 2.971 | 2.971 | 2.971
2024-12-12 08:00 | 2.7245 | 3.3892 | 4.0948 | 4.1889 | 4.283 | 2024-10-12 08:00 | 2.6331 | 3.12 | 3.12 | 3.12 | 3.12
2024-12-12 09:00 | 2.9913 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2024-10-12 09:00 | 2.6445 | 3.1335 | 3.1335 | 3.1335 | 3.1335
2024-12-12 10:00 | 2.7817 | 3.4603 | 4.1807 | 4.2768 | 4.3728 | 2024-10-12 10:00 | 3.0675 | 3.6347 | 3.6347 | 3.6347 | 3.6347
2024-12-12 11:00 | 2.0196 | 2.5123 | 3.0353 | 3.1051 | 3.1748 | 2024-10-12 11:00 | 2.896 | 3.4315 | 3.4315 | 3.4315 | 3.4315
2024-12-12 12:00 | 2.4197 | 3.01 | 3.6367 | 3.7202 | 3.8038 | 2024-10-12 12:00 | 3.0065 | 3.5624 | 3.5624 | 3.5624 | 3.5624
2024-12-12 13:00 | 2.4006 | 2.9863 | 3.608 | 3.6909 | 3.7738 | 2024-10-12 13:00 | 2.7093 | 3.2103 | 3.2103 | 3.2103 | 3.2103
2024-12-12 14:00 | 2.172 | 2.7019 | 3.2644 | 3.3394 | 3.4144 | 2024-10-12 14:00 | 2.7779 | 3.2915 | 3.2915 | 3.2915 | 3.2915
2024-12-12 15:00 | 2.4768 | 3.0811 | 3.7226 | 3.8081 | 3.8936 | 2024-10-12 15:00 | 2.4921 | 2.9529 | 2.9529 | 2.9529 | 2.9529
2024-12-12 16:00 | 2.8579 | 3.5551 | 4.2953 | 4.3939 | 4.4926 | 2024-10-12 16:00 | 2.6978 | 3.1967 | 3.1967 | 3.1967 | 3.1967
2024-12-12 17:00 | 2.8388 | 3.5314 | 4.2666 | 4.3647 | 4.4627 | 2024-10-12 17:00 | 2.5454 | 3.0161 | 3.0161 | 3.0161 | 3.0161
2024-12-12 18:00 | 2.4959 | 3.1048 | 3.7512 | 3.8374 | 3.9236 | 2024-10-12 18:00 | 2.5569 | 3.0297 | 3.0297 | 3.0297 | 3.0297
2024-12-12 19:00 | 1.7528 | 2.1805 | 2.6344 | 2.695 | 2.7555 | 2024-10-12 19:00 | 2.5149 | 2.98 | 2.98 | 2.98 | 2.98
2024-12-12 20:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2024-10-12 20:00 | 2.4654 | 2.9213 | 2.9213 | 2.9213 | 2.9213
2024-12-12 21:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2024-10-12 21:00 | 2.0767 | 2.4608 | 2.4608 | 2.4608 | 2.4608
2024-12-12 22:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-10-12 22:00 | 2.0196 | 2.393 | 2.393 | 2.393 | 2.393
2024-12-12 23:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2024-10-12 23:00 | 1.8938 | 2.244 | 2.244 | 2.244 | 2.244
2024-12-13 | 1.4289 | 1.7776 | 2.1476 | 2.197 | 2.2463 | 2024-10-13 | 1.8252 | 2.1628 | 2.1628 | 2.1628 | 2.1628
2024-12-13 01:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-10-13 01:00 | 1.7376 | 2.0589 | 2.0589 | 2.0589 | 2.0589
2024-12-13 02:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-10-13 02:00 | 1.8176 | 2.1537 | 2.1537 | 2.1537 | 2.1537
2024-12-13 03:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-10-13 03:00 | 1.9662 | 2.3298 | 2.3298 | 2.3298 | 2.3298
2024-12-13 04:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-10-13 04:00 | 1.9777 | 2.3434 | 2.3434 | 2.3434 | 2.3434
2024-12-13 05:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2024-10-13 05:00 | 2.3054 | 2.7317 | 2.7317 | 2.7317 | 2.7317
2024-12-13 06:00 | 1.7147 | 2.1331 | 2.5772 | 2.6364 | 2.6956 | 2024-10-13 06:00 | 2.2406 | 2.6549 | 2.6549 | 2.6549 | 2.6549
2024-12-13 07:00 | 0.81926 | 1.0191 | 1.2313 | 1.2596 | 1.2879 | 2024-10-13 07:00 | 2.2444 | 2.6594 | 2.6594 | 2.6594 | 2.6594
2024-12-13 08:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2024-10-13 08:00 | 2.3854 | 2.8265 | 2.8265 | 2.8265 | 2.8265
2024-12-13 09:00 | 1.4289 | 1.7776 | 2.1476 | 2.197 | 2.2463 | 2024-10-13 09:00 | 2.2596 | 2.6775 | 2.6775 | 2.6775 | 2.6775
2024-12-13 10:00 | 0.47631 | 0.59252 | 0.71588 | 0.73232 | 0.74877 | 2024-10-13 10:00 | 2.4159 | 2.8626 | 2.8626 | 2.8626 | 2.8626
2024-12-13 11:00 | 2.0577 | 2.5597 | 3.0926 | 3.1636 | 3.2347 | 2024-10-13 11:00 | 2.3473 | 2.7813 | 2.7813 | 2.7813 | 2.7813
2024-12-13 12:00 | 2.0196 | 2.5123 | 3.0353 | 3.1051 | 3.1748 | 2024-10-13 12:00 | 2.614 | 3.0974 | 3.0974 | 3.0974 | 3.0974
2024-12-13 13:00 | 2.3054 | 2.8678 | 3.4648 | 3.5445 | 3.6241 | 2024-10-13 13:00 | 2.5416 | 3.0116 | 3.0116 | 3.0116 | 3.0116
2024-12-13 14:00 | 2.3625 | 2.9389 | 3.5508 | 3.6323 | 3.7139 | 2024-10-13 14:00 | 2.5721 | 3.0477 | 3.0477 | 3.0477 | 3.0477
2024-12-13 15:00 | 2.3625 | 2.9389 | 3.5508 | 3.6323 | 3.7139 | 2024-10-13 15:00 | 2.5149 | 2.98 | 2.98 | 2.98 | 2.98
2024-12-13 16:00 | 1.9815 | 2.4649 | 2.9781 | 3.0465 | 3.1149 | 2024-10-13 16:00 | 2.7626 | 3.2735 | 3.2735 | 3.2735 | 3.2735
2024-12-13 17:00 | 2.0005 | 2.4886 | 3.0067 | 3.0758 | 3.1448 | 2024-10-13 17:00 | 2.755 | 3.2644 | 3.2644 | 3.2644 | 3.2644
2024-12-13 18:00 | 1.6957 | 2.1094 | 2.5485 | 2.6071 | 2.6656 | 2024-10-13 18:00 | 2.5035 | 2.9664 | 2.9664 | 2.9664 | 2.9664
2024-12-13 19:00 | 1.3908 | 1.7302 | 2.0904 | 2.1384 | 2.1864 | 2024-10-13 19:00 | 2.2291 | 2.6414 | 2.6414 | 2.6414 | 2.6414
2024-12-13 20:00 | 1.3908 | 1.7302 | 2.0904 | 2.1384 | 2.1864 | 2024-10-13 20:00 | 2.3968 | 2.84 | 2.84 | 2.84 | 2.84
2024-12-13 21:00 | 1.3527 | 1.6828 | 2.0331 | 2.0798 | 2.1265 | 2024-10-13 21:00 | 1.9967 | 2.3659 | 2.3659 | 2.3659 | 2.3659
2024-12-13 22:00 | 1.4289 | 1.7776 | 2.1476 | 2.197 | 2.2463 | 2024-10-13 22:00 | 1.8633 | 2.2079 | 2.2079 | 2.2079 | 2.2079
2024-12-13 23:00 | 1.4289 | 1.7776 | 2.1476 | 2.197 | 2.2463 | 2024-10-13 23:00 | 1.7719 | 2.0995 | 2.0995 | 2.0995 | 2.0995
2024-12-14 | 1.3718 | 1.7065 | 2.0617 | 2.1091 | 2.1565 | 2024-10-14 | 1.7566 | 2.0815 | 2.0815 | 2.0815 | 2.0815
2024-12-14 01:00 | 1.4099 | 1.7539 | 2.119 | 2.1677 | 2.2164 | 2024-10-14 01:00 | 1.7871 | 2.1176 | 2.1176 | 2.1176 | 2.1176
2024-12-14 02:00 | 1.4289 | 1.7776 | 2.1476 | 2.197 | 2.2463 | 2024-10-14 02:00 | 1.8252 | 2.1628 | 2.1628 | 2.1628 | 2.1628
2024-12-14 03:00 | 1.3718 | 1.7065 | 2.0617 | 2.1091 | 2.1565 | 2024-10-14 03:00 | 1.8938 | 2.244 | 2.244 | 2.244 | 2.244
2024-12-14 04:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-10-14 04:00 | 2.0996 | 2.4878 | 2.4878 | 2.4878 | 2.4878
2024-12-14 05:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2024-10-14 05:00 | 2.3549 | 2.7904 | 2.7904 | 2.7904 | 2.7904
2024-12-14 06:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2024-10-14 06:00 | 2.7017 | 3.2012 | 3.2012 | 3.2012 | 3.2012
2024-12-14 07:00 | 1.1432 | 1.4221 | 1.7181 | 1.7576 | 1.7971 | 2024-10-14 07:00 | 3.1056 | 3.6798 | 3.6798 | 3.6798 | 3.6798
2024-12-14 08:00 | 0.97168 | 1.2087 | 1.4604 | 1.4939 | 1.5275 | 2024-10-14 08:00 | 3.2618 | 3.865 | 3.865 | 3.865 | 3.865
2024-12-14 09:00 | 0.74305 | 0.92433 | 1.1168 | 1.1424 | 1.1681 | 2024-10-14 09:00 | 3.1818 | 3.7701 | 3.7701 | 3.7701 | 3.7701
2024-12-14 10:00 | 0.724 | 0.90063 | 1.0881 | 1.1131 | 1.1381 | 2024-10-14 10:00 | 3.3875 | 4.014 | 4.014 | 4.014 | 4.014
2024-12-14 11:00 | 0.49537 | 0.61622 | 0.74451 | 0.76162 | 0.77872 | 2024-10-14 11:00 | 3.6924 | 4.3752 | 4.3752 | 4.3752 | 4.3752
2024-12-14 12:00 | 0.724 | 0.90063 | 1.0881 | 1.1131 | 1.1381 | 2024-10-14 12:00 | 3.5323 | 4.1855 | 4.1855 | 4.1855 | 4.1855
2024-12-14 13:00 | 0.70494 | 0.87693 | 1.0595 | 1.0838 | 1.1082 | 2024-10-14 13:00 | 3.479 | 4.1223 | 4.1223 | 4.1223 | 4.1223
2024-12-14 14:00 | 1.0098 | 1.2561 | 1.5177 | 1.5525 | 1.5874 | 2024-10-14 14:00 | 3.8867 | 4.6054 | 4.6054 | 4.6054 | 4.6054
2024-12-14 15:00 | 1.0288 | 1.2798 | 1.5463 | 1.5818 | 1.6173 | 2024-10-14 15:00 | 3.54 | 4.1946 | 4.1946 | 4.1946 | 4.1946
2024-12-14 16:00 | 1.0098 | 1.2561 | 1.5177 | 1.5525 | 1.5874 | 2024-10-14 16:00 | 4.0163 | 4.759 | 4.759 | 4.759 | 4.759
2024-12-14 17:00 | 1.2003 | 1.4932 | 1.804 | 1.8455 | 1.8869 | 2024-10-14 17:00 | 3.3266 | 3.9417 | 3.9417 | 3.9417 | 3.9417
2024-12-14 18:00 | 1.4099 | 1.7539 | 2.119 | 2.1677 | 2.2164 | 2024-10-14 18:00 | 2.8922 | 3.427 | 3.427 | 3.427 | 3.427
2024-12-14 19:00 | 1.4289 | 1.7776 | 2.1476 | 2.197 | 2.2463 | 2024-10-14 19:00 | 2.7207 | 3.2238 | 3.2238 | 3.2238 | 3.2238
2024-12-14 20:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-10-14 20:00 | 2.4197 | 2.8671 | 2.8671 | 2.8671 | 2.8671
2024-12-14 21:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-10-14 21:00 | 2.2291 | 2.6414 | 2.6414 | 2.6414 | 2.6414
2024-12-14 22:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-10-14 22:00 | 1.9434 | 2.3027 | 2.3027 | 2.3027 | 2.3027
2024-12-14 23:00 | 1.3718 | 1.7065 | 2.0617 | 2.1091 | 2.1565 | 2024-10-14 23:00 | 1.9129 | 2.2666 | 2.2666 | 2.2666 | 2.2666
2024-12-15 | 1.2384 | 1.5406 | 1.8613 | 1.904 | 1.9468 | 2024-10-15 | 1.9091 | 2.2621 | 2.2621 | 2.2621 | 2.2621
2024-12-15 01:00 | 1.2765 | 1.588 | 1.9186 | 1.9626 | 2.0067 | 2024-10-15 01:00 | 1.8862 | 2.235 | 2.235 | 2.235 | 2.235
2024-12-15 02:00 | 1.3718 | 1.7065 | 2.0617 | 2.1091 | 2.1565 | 2024-10-15 02:00 | 1.8633 | 2.2079 | 2.2079 | 2.2079 | 2.2079
2024-12-15 03:00 | 1.4289 | 1.7776 | 2.1476 | 2.197 | 2.2463 | 2024-10-15 03:00 | 1.9662 | 2.3298 | 2.3298 | 2.3298 | 2.3298
2024-12-15 04:00 | 1.4289 | 1.7776 | 2.1476 | 2.197 | 2.2463 | 2024-10-15 04:00 | 2.0996 | 2.4878 | 2.4878 | 2.4878 | 2.4878
2024-12-15 05:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-10-15 05:00 | 2.3816 | 2.822 | 2.822 | 2.822 | 2.822
2024-12-15 06:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2024-10-15 06:00 | 2.6445 | 3.1335 | 3.1335 | 3.1335 | 3.1335
2024-12-15 07:00 | 1.2194 | 1.5169 | 1.8326 | 1.8748 | 1.9169 | 2024-10-15 07:00 | 3.1665 | 3.7521 | 3.7521 | 3.7521 | 3.7521
2024-12-15 08:00 | 0.93358 | 1.1613 | 1.4031 | 1.4354 | 1.4676 | 2024-10-15 08:00 | 3.8181 | 4.5242 | 4.5242 | 4.5242 | 4.5242
2024-12-15 09:00 | 0.57158 | 0.71103 | 0.85905 | 0.87879 | 0.89853 | 2024-10-15 09:00 | 3.7076 | 4.3932 | 4.3932 | 4.3932 | 4.3932
2024-12-15 10:00 | 0.38105 | 0.47402 | 0.5727 | 0.58586 | 0.59902 | 2024-10-15 10:00 | 3.5857 | 4.2487 | 4.2487 | 4.2487 | 4.2487
2024-12-15 11:00 | 0.13337 | 0.16591 | 0.20045 | 0.20505 | 0.20966 | 2024-10-15 11:00 | 3.5933 | 4.2578 | 4.2578 | 4.2578 | 4.2578
2024-12-15 12:00 | 0.59063 | 0.73473 | 0.88769 | 0.90808 | 0.92848 | 2024-10-15 12:00 | 3.5247 | 4.1765 | 4.1765 | 4.1765 | 4.1765
2024-12-15 13:00 | 0.7621 | 0.94804 | 1.1454 | 1.1717 | 1.198 | 2024-10-15 13:00 | 3.6581 | 4.3345 | 4.3345 | 4.3345 | 4.3345
2024-12-15 14:00 | 0.60968 | 0.75843 | 0.91632 | 0.93738 | 0.95843 | 2024-10-15 14:00 | 3.4371 | 4.0727 | 4.0727 | 4.0727 | 4.0727
2024-12-15 15:00 | 1.2003 | 1.4932 | 1.804 | 1.8455 | 1.8869 | 2024-10-15 15:00 | 3.1513 | 3.734 | 3.734 | 3.734 | 3.734
2024-12-15 16:00 | 0.36243 | 0.45085 | 0.54471 | 0.55723 | 0.56974 | 2024-10-15 16:00 | 3.4904 | 4.1359 | 4.1359 | 4.1359 | 4.1359
2024-12-15 17:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-10-15 17:00 | 3.319 | 3.9327 | 3.9327 | 3.9327 | 3.9327
2024-12-15 18:00 | 2.0767 | 2.5834 | 3.1212 | 3.1929 | 3.2646 | 2024-10-15 18:00 | 2.9646 | 3.5128 | 3.5128 | 3.5128 | 3.5128
2024-12-15 19:00 | 1.6957 | 2.1094 | 2.5485 | 2.6071 | 2.6656 | 2024-10-15 19:00 | 2.755 | 3.2644 | 3.2644 | 3.2644 | 3.2644
2024-12-15 20:00 | 1.6957 | 2.1094 | 2.5485 | 2.6071 | 2.6656 | 2024-10-15 20:00 | 2.553 | 3.0251 | 3.0251 | 3.0251 | 3.0251
2024-12-15 21:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2024-10-15 21:00 | 2.2482 | 2.6639 | 2.6639 | 2.6639 | 2.6639
2024-12-15 22:00 | 1.7909 | 2.2279 | 2.6917 | 2.7535 | 2.8154 | 2024-10-15 22:00 | 2.0615 | 2.4427 | 2.4427 | 2.4427 | 2.4427
2024-12-15 23:00 | 1.7147 | 2.1331 | 2.5772 | 2.6364 | 2.6956 | 2024-10-15 23:00 | 1.9548 | 2.3163 | 2.3163 | 2.3163 | 2.3163
2024-12-16 | 1.6957 | 2.1094 | 2.5485 | 2.6071 | 2.6656 | 2024-10-16 | 1.8062 | 2.1402 | 2.1402 | 2.1402 | 2.1402
2024-12-16 01:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2024-10-16 01:00 | 1.8862 | 2.235 | 2.235 | 2.235 | 2.235
2024-12-16 02:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2024-10-16 02:00 | 1.8557 | 2.1989 | 2.1989 | 2.1989 | 2.1989
2024-12-16 03:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2024-10-16 03:00 | 1.9853 | 2.3524 | 2.3524 | 2.3524 | 2.3524
2024-12-16 04:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-10-16 04:00 | 2.1491 | 2.5465 | 2.5465 | 2.5465 | 2.5465
2024-12-16 05:00 | 1.7909 | 2.2279 | 2.6917 | 2.7535 | 2.8154 | 2024-10-16 05:00 | 2.3473 | 2.7813 | 2.7813 | 2.7813 | 2.7813
2024-12-16 06:00 | 1.9243 | 2.3938 | 2.8921 | 2.9586 | 3.025 | 2024-10-16 06:00 | 2.7207 | 3.2238 | 3.2238 | 3.2238 | 3.2238
2024-12-16 07:00 | 2.6674 | 3.3181 | 4.0089 | 4.101 | 4.1931 | 2024-10-16 07:00 | 2.9265 | 3.4676 | 3.4676 | 3.4676 | 3.4676
2024-12-16 08:00 | 2.534 | 3.1522 | 3.8085 | 3.896 | 3.9835 | 2024-10-16 08:00 | 3.5362 | 4.19 | 4.19 | 4.19 | 4.19
2024-12-16 09:00 | 2.4768 | 3.0811 | 3.7226 | 3.8081 | 3.8936 | 2024-10-16 09:00 | 3.2085 | 3.8017 | 3.8017 | 3.8017 | 3.8017
2024-12-16 10:00 | 2.896 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2024-10-16 10:00 | 3.1361 | 3.716 | 3.716 | 3.716 | 3.716
2024-12-16 11:00 | 3.2961 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2024-10-16 11:00 | 3.1742 | 3.7611 | 3.7611 | 3.7611 | 3.7611
2024-12-16 12:00 | 2.8388 | 3.5314 | 4.2666 | 4.3647 | 4.4627 | 2024-10-16 12:00 | 3.0255 | 3.585 | 3.585 | 3.585 | 3.585
2024-12-16 13:00 | 2.1529 | 2.6782 | 3.2358 | 3.3101 | 3.3845 | 2024-10-16 13:00 | 2.9265 | 3.4676 | 3.4676 | 3.4676 | 3.4676
2024-12-16 14:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2024-10-16 14:00 | 3.0027 | 3.5579 | 3.5579 | 3.5579 | 3.5579
2024-12-16 15:00 | 2.0958 | 2.6071 | 3.1499 | 3.2222 | 3.2946 | 2024-10-16 15:00 | 3.4714 | 4.1133 | 4.1133 | 4.1133 | 4.1133
2024-12-16 16:00 | 2.2863 | 2.8441 | 3.4362 | 3.5152 | 3.5941 | 2024-10-16 16:00 | 3.6467 | 4.321 | 4.321 | 4.321 | 4.321
2024-12-16 17:00 | 2.8007 | 3.484 | 4.2094 | 4.3061 | 4.4028 | 2024-10-16 17:00 | 3.5019 | 4.1494 | 4.1494 | 4.1494 | 4.1494
2024-12-16 18:00 | 2.8388 | 3.5314 | 4.2666 | 4.3647 | 4.4627 | 2024-10-16 18:00 | 3.3456 | 3.9643 | 3.9643 | 3.9643 | 3.9643
2024-12-16 19:00 | 1.7147 | 2.1331 | 2.5772 | 2.6364 | 2.6956 | 2024-10-16 19:00 | 2.6978 | 3.1967 | 3.1967 | 3.1967 | 3.1967
2024-12-16 20:00 | 1.7719 | 2.2042 | 2.6631 | 2.7242 | 2.7854 | 2024-10-16 20:00 | 2.5645 | 3.0387 | 3.0387 | 3.0387 | 3.0387
2024-12-16 21:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-10-16 21:00 | 2.2673 | 2.6865 | 2.6865 | 2.6865 | 2.6865
2024-12-16 22:00 | 1.1622 | 1.4458 | 1.7467 | 1.7869 | 1.827 | 2024-10-16 22:00 | 2.1415 | 2.5375 | 2.5375 | 2.5375 | 2.5375
2024-12-16 23:00 | 1.1622 | 1.4458 | 1.7467 | 1.7869 | 1.827 | 2024-10-16 23:00 | 2.0005 | 2.3704 | 2.3704 | 2.3704 | 2.3704
2024-12-17 | 1.2384 | 1.5406 | 1.8613 | 1.904 | 1.9468 | 2024-10-17 | 1.9281 | 2.2847 | 2.2847 | 2.2847 | 2.2847
2024-12-17 01:00 | 1.2194 | 1.5169 | 1.8326 | 1.8748 | 1.9169 | 2024-10-17 01:00 | 1.9738 | 2.3388 | 2.3388 | 2.3388 | 2.3388
2024-12-17 02:00 | 1.2575 | 1.5643 | 1.8899 | 1.9333 | 1.9768 | 2024-10-17 02:00 | 1.8672 | 2.2124 | 2.2124 | 2.2124 | 2.2124
2024-12-17 03:00 | 1.2384 | 1.5406 | 1.8613 | 1.904 | 1.9468 | 2024-10-17 03:00 | 1.9396 | 2.2982 | 2.2982 | 2.2982 | 2.2982
2024-12-17 04:00 | 1.3527 | 1.6828 | 2.0331 | 2.0798 | 2.1265 | 2024-10-17 04:00 | 2.1415 | 2.5375 | 2.5375 | 2.5375 | 2.5375
2024-12-17 05:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2024-10-17 05:00 | 2.4921 | 2.9529 | 2.9529 | 2.9529 | 2.9529
2024-12-17 06:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2024-10-17 06:00 | 2.9074 | 3.4451 | 3.4451 | 3.4451 | 3.4451
2024-12-17 07:00 | 2.172 | 2.7019 | 3.2644 | 3.3394 | 3.4144 | 2024-10-17 07:00 | 3.2885 | 3.8966 | 3.8966 | 3.8966 | 3.8966
2024-12-17 08:00 | 2.172 | 2.7019 | 3.2644 | 3.3394 | 3.4144 | 2024-10-17 08:00 | 3.2466 | 3.8469 | 3.8469 | 3.8469 | 3.8469
2024-12-17 09:00 | 2.2291 | 2.773 | 3.3503 | 3.4273 | 3.5043 | 2024-10-17 09:00 | 3.2732 | 3.8785 | 3.8785 | 3.8785 | 3.8785
2024-12-17 10:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2024-10-17 10:00 | 3.3609 | 3.9824 | 3.9824 | 3.9824 | 3.9824
2024-12-17 11:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2024-10-17 11:00 | 3.0675 | 3.6347 | 3.6347 | 3.6347 | 3.6347
2024-12-17 12:00 | 1.9243 | 2.3938 | 2.8921 | 2.9586 | 3.025 | 2024-10-17 12:00 | 3.4676 | 4.1088 | 4.1088 | 4.1088 | 4.1088
2024-12-17 13:00 | 2.4387 | 3.0337 | 3.6653 | 3.7495 | 3.8337 | 2024-10-17 13:00 | 4.001 | 4.7409 | 4.7409 | 4.7409 | 4.7409
2024-12-17 14:00 | 2.6102 | 3.247 | 3.923 | 4.0131 | 4.1033 | 2024-10-17 14:00 | 3.4333 | 4.0681 | 4.0681 | 4.0681 | 4.0681
2024-12-17 15:00 | 2.1148 | 2.6308 | 3.1785 | 3.2515 | 3.3245 | 2024-10-17 15:00 | 3.7572 | 4.4519 | 4.4519 | 4.4519 | 4.4519
2024-12-17 16:00 | 1.9624 | 2.4412 | 2.9494 | 3.0172 | 3.0849 | 2024-10-17 16:00 | 3.9363 | 4.6641 | 4.6641 | 4.6641 | 4.6641
2024-12-17 17:00 | 1.2003 | 1.4932 | 1.804 | 1.8455 | 1.8869 | 2024-10-17 17:00 | 3.9286 | 4.6551 | 4.6551 | 4.6551 | 4.6551
2024-12-17 18:00 | 1.7719 | 2.2042 | 2.6631 | 2.7242 | 2.7854 | 2024-10-17 18:00 | 3.3456 | 3.9643 | 3.9643 | 3.9643 | 3.9643
2024-12-17 19:00 | 1.7147 | 2.1331 | 2.5772 | 2.6364 | 2.6956 | 2024-10-17 19:00 | 2.6331 | 3.12 | 3.12 | 3.12 | 3.12
2024-12-17 20:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2024-10-17 20:00 | 2.6521 | 3.1425 | 3.1425 | 3.1425 | 3.1425
2024-12-17 21:00 | 1.6957 | 2.1094 | 2.5485 | 2.6071 | 2.6656 | 2024-10-17 21:00 | 2.6559 | 3.1471 | 3.1471 | 3.1471 | 3.1471
2024-12-17 22:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2024-10-17 22:00 | 2.0577 | 2.4382 | 2.4382 | 2.4382 | 2.4382
2024-12-17 23:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2024-10-17 23:00 | 2.0005 | 2.3704 | 2.3704 | 2.3704 | 2.3704
2024-12-18 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2024-10-18 | 1.9205 | 2.2756 | 2.2756 | 2.2756 | 2.2756
2024-12-18 01:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-10-18 01:00 | 1.8176 | 2.1537 | 2.1537 | 2.1537 | 2.1537
2024-12-18 02:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-10-18 02:00 | 1.749 | 2.0724 | 2.0724 | 2.0724 | 2.0724
2024-12-18 03:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-10-18 03:00 | 1.8595 | 2.2034 | 2.2034 | 2.2034 | 2.2034
2024-12-18 04:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-10-18 04:00 | 2.1263 | 2.5194 | 2.5194 | 2.5194 | 2.5194
2024-12-18 05:00 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2024-10-18 05:00 | 2.3625 | 2.7994 | 2.7994 | 2.7994 | 2.7994
2024-12-18 06:00 | 1.7147 | 2.1331 | 2.5772 | 2.6364 | 2.6956 | 2024-10-18 06:00 | 2.5797 | 3.0567 | 3.0567 | 3.0567 | 3.0567
2024-12-18 07:00 | 0.74305 | 0.92433 | 1.1168 | 1.1424 | 1.1681 | 2024-10-18 07:00 | 3.2961 | 3.9056 | 3.9056 | 3.9056 | 3.9056
2024-12-18 08:00 | 0.70494 | 0.87693 | 1.0595 | 1.0838 | 1.1082 | 2024-10-18 08:00 | 3.761 | 4.4564 | 4.4564 | 4.4564 | 4.4564
2024-12-18 09:00 | 0.47631 | 0.59252 | 0.71588 | 0.73232 | 0.74877 | 2024-10-18 09:00 | 4.0163 | 4.759 | 4.759 | 4.759 | 4.759
2024-12-18 10:00 | 0.55252 | 0.68733 | 0.83042 | 0.8495 | 0.86858 | 2024-10-18 10:00 | 4.3859 | 5.1969 | 5.1969 | 5.1969 | 5.1969
2024-12-18 11:00 | 0.70494 | 0.87693 | 1.0595 | 1.0838 | 1.1082 | 2024-10-18 11:00 | 4.1077 | 4.8673 | 4.8673 | 4.8673 | 4.8673
2024-12-18 12:00 | 2.2863 | 2.8441 | 3.4362 | 3.5152 | 3.5941 | 2024-10-18 12:00 | 4.0582 | 4.8086 | 4.8086 | 4.8086 | 4.8086
2024-12-18 13:00 | 3.0103 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2024-10-18 13:00 | 4.0125 | 4.7544 | 4.7544 | 4.7544 | 4.7544
2024-12-18 14:00 | 3.0103 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 2024-10-18 14:00 | 3.9629 | 4.6957 | 4.6957 | 4.6957 | 4.6957
2024-12-18 15:00 | 2.5911 | 3.2233 | 3.8944 | 3.9838 | 4.0733 | 2024-10-18 15:00 | 3.6162 | 4.2849 | 4.2849 | 4.2849 | 4.2849
2024-12-18 16:00 | 2.8579 | 3.5551 | 4.2953 | 4.3939 | 4.4926 | 2024-10-18 16:00 | 3.9667 | 4.7003 | 4.7003 | 4.7003 | 4.7003
2024-12-18 17:00 | 2.8007 | 3.484 | 4.2094 | 4.3061 | 4.4028 | 2024-10-18 17:00 | 3.7534 | 4.4474 | 4.4474 | 4.4474 | 4.4474
2024-12-18 18:00 | 2.3054 | 2.8678 | 3.4648 | 3.5445 | 3.6241 | 2024-10-18 18:00 | 3.3952 | 4.023 | 4.023 | 4.023 | 4.023
2024-12-18 19:00 | 2.0767 | 2.5834 | 3.1212 | 3.1929 | 3.2646 | 2024-10-18 19:00 | 2.9913 | 3.5444 | 3.5444 | 3.5444 | 3.5444
2024-12-18 20:00 | 2.0005 | 2.4886 | 3.0067 | 3.0758 | 3.1448 | 2024-10-18 20:00 | 2.7931 | 3.3096 | 3.3096 | 3.3096 | 3.3096
2024-12-18 21:00 | 1.8672 | 2.3227 | 2.8062 | 2.8707 | 2.9352 | 2024-10-18 21:00 | 2.5035 | 2.9664 | 2.9664 | 2.9664 | 2.9664
2024-12-18 22:00 | 1.7147 | 2.1331 | 2.5772 | 2.6364 | 2.6956 | 2024-10-18 22:00 | 2.2139 | 2.6233 | 2.6233 | 2.6233 | 2.6233
2024-12-18 23:00 | 1.7528 | 2.1805 | 2.6344 | 2.695 | 2.7555 | 2024-10-18 23:00 | 1.9815 | 2.3479 | 2.3479 | 2.3479 | 2.3479
2024-12-19 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2024-10-19 | 1.9624 | 2.3253 | 2.3253 | 2.3253 | 2.3253
2024-12-19 01:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2024-10-19 01:00 | 1.8329 | 2.1718 | 2.1718 | 2.1718 | 2.1718
2024-12-19 02:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-10-19 02:00 | 1.81 | 2.1447 | 2.1447 | 2.1447 | 2.1447
2024-12-19 03:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-10-19 03:00 | 1.9777 | 2.3434 | 2.3434 | 2.3434 | 2.3434
2024-12-19 04:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-10-19 04:00 | 2.0501 | 2.4291 | 2.4291 | 2.4291 | 2.4291
2024-12-19 05:00 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2024-10-19 05:00 | 2.233 | 2.6459 | 2.6459 | 2.6459 | 2.6459
2024-12-19 06:00 | 1.7909 | 2.2279 | 2.6917 | 2.7535 | 2.8154 | 2024-10-19 06:00 | 2.3739 | 2.8129 | 2.8129 | 2.8129 | 2.8129
2024-12-19 07:00 | 2.1529 | 2.6782 | 3.2358 | 3.3101 | 3.3845 | 2024-10-19 07:00 | 2.5683 | 3.0432 | 3.0432 | 3.0432 | 3.0432
2024-12-19 08:00 | 2.4578 | 3.0574 | 3.6939 | 3.7788 | 3.8637 | 2024-10-19 08:00 | 2.6445 | 3.1335 | 3.1335 | 3.1335 | 3.1335
2024-12-19 09:00 | 2.5721 | 3.1996 | 3.8657 | 3.9546 | 4.0434 | 2024-10-19 09:00 | 2.8045 | 3.3231 | 3.3231 | 3.3231 | 3.3231
2024-12-19 10:00 | 2.4006 | 2.9863 | 3.608 | 3.6909 | 3.7738 | 2024-10-19 10:00 | 3.037 | 3.5986 | 3.5986 | 3.5986 | 3.5986
2024-12-19 11:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2024-10-19 11:00 | 3.3418 | 3.9598 | 3.9598 | 3.9598 | 3.9598
2024-12-19 12:00 | 2.0005 | 2.4886 | 3.0067 | 3.0758 | 3.1448 | 2024-10-19 12:00 | 3.3533 | 3.9733 | 3.9733 | 3.9733 | 3.9733
2024-12-19 13:00 | 1.9434 | 2.4175 | 2.9208 | 2.9879 | 3.055 | 2024-10-19 13:00 | 3.4828 | 4.1268 | 4.1268 | 4.1268 | 4.1268
2024-12-19 14:00 | 1.7528 | 2.1805 | 2.6344 | 2.695 | 2.7555 | 2024-10-19 14:00 | 3.418 | 4.0501 | 4.0501 | 4.0501 | 4.0501
2024-12-19 15:00 | 2.0005 | 2.4886 | 3.0067 | 3.0758 | 3.1448 | 2024-10-19 15:00 | 3.4599 | 4.0997 | 4.0997 | 4.0997 | 4.0997
2024-12-19 16:00 | 2.3435 | 2.9152 | 3.5221 | 3.603 | 3.684 | 2024-10-19 16:00 | 3.2389 | 3.8379 | 3.8379 | 3.8379 | 3.8379
2024-12-19 17:00 | 2.4197 | 3.01 | 3.6367 | 3.7202 | 3.8038 | 2024-10-19 17:00 | 2.9036 | 3.4405 | 3.4405 | 3.4405 | 3.4405
2024-12-19 18:00 | 2.2101 | 2.7493 | 3.3217 | 3.398 | 3.4743 | 2024-10-19 18:00 | 2.534 | 3.0026 | 3.0026 | 3.0026 | 3.0026
2024-12-19 19:00 | 1.9243 | 2.3938 | 2.8921 | 2.9586 | 3.025 | 2024-10-19 19:00 | 2.6293 | 3.1154 | 3.1154 | 3.1154 | 3.1154
2024-12-19 20:00 | 1.8672 | 2.3227 | 2.8062 | 2.8707 | 2.9352 | 2024-10-19 20:00 | 2.3739 | 2.8129 | 2.8129 | 2.8129 | 2.8129
2024-12-19 21:00 | 1.7338 | 2.1568 | 2.6058 | 2.6657 | 2.7255 | 2024-10-19 21:00 | 2.233 | 2.6459 | 2.6459 | 2.6459 | 2.6459
2024-12-19 22:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2024-10-19 22:00 | 2.1377 | 2.533 | 2.533 | 2.533 | 2.533
2024-12-19 23:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2024-10-19 23:00 | 1.9891 | 2.3569 | 2.3569 | 2.3569 | 2.3569
2024-12-20 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-10-20 | 1.8176 | 2.1537 | 2.1537 | 2.1537 | 2.1537
2024-12-20 01:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-10-20 01:00 | 1.8329 | 2.1718 | 2.1718 | 2.1718 | 2.1718
2024-12-20 02:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-10-20 02:00 | 1.829 | 2.1673 | 2.1673 | 2.1673 | 2.1673
2024-12-20 03:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-10-20 03:00 | 1.9815 | 2.3479 | 2.3479 | 2.3479 | 2.3479
2024-12-20 04:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-10-20 04:00 | 2.0958 | 2.4833 | 2.4833 | 2.4833 | 2.4833
2024-12-20 05:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2024-10-20 05:00 | 2.3168 | 2.7452 | 2.7452 | 2.7452 | 2.7452
2024-12-20 06:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2024-10-20 06:00 | 2.4845 | 2.9439 | 2.9439 | 2.9439 | 2.9439
2024-12-20 07:00 | 0.95263 | 1.185 | 1.4318 | 1.4646 | 1.4975 | 2024-10-20 07:00 | 2.5073 | 2.971 | 2.971 | 2.971 | 2.971
2024-12-20 08:00 | 1.3908 | 1.7302 | 2.0904 | 2.1384 | 2.1864 | 2024-10-20 08:00 | 2.2482 | 2.6639 | 2.6639 | 2.6639 | 2.6639
2024-12-20 09:00 | 1.0669 | 1.3272 | 1.6036 | 1.6404 | 1.6772 | 2024-10-20 09:00 | 2.5302 | 2.9981 | 2.9981 | 2.9981 | 2.9981
2024-12-20 10:00 | 0.095263 | 0.1185 | 0.14318 | 0.14646 | 0.14975 | 2024-10-20 10:00 | 2.5454 | 3.0161 | 3.0161 | 3.0161 | 3.0161
2024-12-20 11:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2024-10-20 11:00 | 2.5988 | 3.0793 | 3.0793 | 3.0793 | 3.0793
2024-12-20 12:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2024-10-20 12:00 | 2.6788 | 3.1741 | 3.1741 | 3.1741 | 3.1741
2024-12-20 13:00 | 1.8481 | 2.299 | 2.7776 | 2.8414 | 2.9052 | 2024-10-20 13:00 | 2.473 | 2.9303 | 2.9303 | 2.9303 | 2.9303
2024-12-20 14:00 | 1.9815 | 2.4649 | 2.9781 | 3.0465 | 3.1149 | 2024-10-20 14:00 | 2.7398 | 3.2464 | 3.2464 | 3.2464 | 3.2464
2024-12-20 15:00 | 2.0005 | 2.4886 | 3.0067 | 3.0758 | 3.1448 | 2024-10-20 15:00 | 2.8807 | 3.4134 | 3.4134 | 3.4134 | 3.4134
2024-12-20 16:00 | 2.172 | 2.7019 | 3.2644 | 3.3394 | 3.4144 | 2024-10-20 16:00 | 2.7702 | 3.2825 | 3.2825 | 3.2825 | 3.2825
2024-12-20 17:00 | 2.172 | 2.7019 | 3.2644 | 3.3394 | 3.4144 | 2024-10-20 17:00 | 2.6902 | 3.1877 | 3.1877 | 3.1877 | 3.1877
2024-12-20 18:00 | 2.1148 | 2.6308 | 3.1785 | 3.2515 | 3.3245 | 2024-10-20 18:00 | 2.6483 | 3.138 | 3.138 | 3.138 | 3.138
2024-12-20 19:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-10-20 19:00 | 2.4235 | 2.8716 | 2.8716 | 2.8716 | 2.8716
2024-12-20 20:00 | 1.3908 | 1.7302 | 2.0904 | 2.1384 | 2.1864 | 2024-10-20 20:00 | 2.3778 | 2.8174 | 2.8174 | 2.8174 | 2.8174
2024-12-20 21:00 | 1.4099 | 1.7539 | 2.119 | 2.1677 | 2.2164 | 2024-10-20 21:00 | 2.3092 | 2.7362 | 2.7362 | 2.7362 | 2.7362
2024-12-20 22:00 | 1.4289 | 1.7776 | 2.1476 | 2.197 | 2.2463 | 2024-10-20 22:00 | 1.9815 | 2.3479 | 2.3479 | 2.3479 | 2.3479
2024-12-20 23:00 | 1.4289 | 1.7776 | 2.1476 | 2.197 | 2.2463 | 2024-10-20 23:00 | 1.9662 | 2.3298 | 2.3298 | 2.3298 | 2.3298
2024-12-21 | 1.4099 | 1.7539 | 2.119 | 2.1677 | 2.2164 | 2024-10-21 | 1.951 | 2.3118 | 2.3118 | 2.3118 | 2.3118
2024-12-21 01:00 | 1.4289 | 1.7776 | 2.1476 | 2.197 | 2.2463 | 2024-10-21 01:00 | 1.8862 | 2.235 | 2.235 | 2.235 | 2.235
2024-12-21 02:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-10-21 02:00 | 1.8748 | 2.2214 | 2.2214 | 2.2214 | 2.2214
2024-12-21 03:00 | 1.4099 | 1.7539 | 2.119 | 2.1677 | 2.2164 | 2024-10-21 03:00 | 1.9738 | 2.3388 | 2.3388 | 2.3388 | 2.3388
2024-12-21 04:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2024-10-21 04:00 | 2.0958 | 2.4833 | 2.4833 | 2.4833 | 2.4833
2024-12-21 05:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2024-10-21 05:00 | 2.4959 | 2.9574 | 2.9574 | 2.9574 | 2.9574
2024-12-21 06:00 | 1.7528 | 2.1805 | 2.6344 | 2.695 | 2.7555 | 2024-10-21 06:00 | 2.8083 | 3.3277 | 3.3277 | 3.3277 | 3.3277
2024-12-21 07:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2024-10-21 07:00 | 2.8998 | 3.436 | 3.436 | 3.436 | 3.436
2024-12-21 08:00 | 1.1432 | 1.4221 | 1.7181 | 1.7576 | 1.7971 | 2024-10-21 08:00 | 3.0332 | 3.5941 | 3.5941 | 3.5941 | 3.5941
2024-12-21 09:00 | 0.59063 | 0.73473 | 0.88769 | 0.90808 | 0.92848 | 2024-10-21 09:00 | 3.0675 | 3.6347 | 3.6347 | 3.6347 | 3.6347
2024-12-21 10:00 | 0.49537 | 0.61622 | 0.74451 | 0.76162 | 0.77872 | 2024-10-21 10:00 | 3.258 | 3.8604 | 3.8604 | 3.8604 | 3.8604
2024-12-21 11:00 | 0.24768 | 0.30811 | 0.37226 | 0.38081 | 0.38936 | 2024-10-21 11:00 | 3.258 | 3.8604 | 3.8604 | 3.8604 | 3.8604
2024-12-21 12:00 | 0.49537 | 0.61622 | 0.74451 | 0.76162 | 0.77872 | 2024-10-21 12:00 | 3.5095 | 4.1584 | 4.1584 | 4.1584 | 4.1584
2024-12-21 13:00 | 0.45726 | 0.56882 | 0.68724 | 0.70303 | 0.71882 | 2024-10-21 13:00 | 3.3571 | 3.9778 | 3.9778 | 3.9778 | 3.9778
2024-12-21 14:00 | 0.7621 | 0.94804 | 1.1454 | 1.1717 | 1.198 | 2024-10-21 14:00 | 3.2999 | 3.9101 | 3.9101 | 3.9101 | 3.9101
2024-12-21 15:00 | 0.51442 | 0.63992 | 0.77315 | 0.79091 | 0.80867 | 2024-10-21 15:00 | 3.1627 | 3.7476 | 3.7476 | 3.7476 | 3.7476
2024-12-21 16:00 | 0.81926 | 1.0191 | 1.2313 | 1.2596 | 1.2879 | 2024-10-21 16:00 | 3.8296 | 4.5377 | 4.5377 | 4.5377 | 4.5377
2024-12-21 17:00 | 0.87642 | 1.0902 | 1.3172 | 1.3475 | 1.3777 | 2024-10-21 17:00 | 3.5476 | 4.2036 | 4.2036 | 4.2036 | 4.2036
2024-12-21 18:00 | 1.3718 | 1.7065 | 2.0617 | 2.1091 | 2.1565 | 2024-10-21 18:00 | 3.3304 | 3.9462 | 3.9462 | 3.9462 | 3.9462
2024-12-21 19:00 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2024-10-21 19:00 | 2.7817 | 3.2961 | 3.2961 | 3.2961 | 3.2961
2024-12-21 20:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2024-10-21 20:00 | 2.5073 | 2.971 | 2.971 | 2.971 | 2.971
2024-12-21 21:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-10-21 21:00 | 2.1644 | 2.5646 | 2.5646 | 2.5646 | 2.5646
2024-12-21 22:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2024-10-21 22:00 | 1.871 | 2.2169 | 2.2169 | 2.2169 | 2.2169
2024-12-21 23:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-10-21 23:00 | 1.9129 | 2.2666 | 2.2666 | 2.2666 | 2.2666
2024-12-22 | 1.3718 | 1.7065 | 2.0617 | 2.1091 | 2.1565 | 2024-10-22 | 1.829 | 2.1673 | 2.1673 | 2.1673 | 2.1673
2024-12-22 01:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-10-22 01:00 | 1.8405 | 2.1808 | 2.1808 | 2.1808 | 2.1808
2024-12-22 02:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-10-22 02:00 | 1.81 | 2.1447 | 2.1447 | 2.1447 | 2.1447
2024-12-22 03:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-10-22 03:00 | 1.89 | 2.2395 | 2.2395 | 2.2395 | 2.2395
2024-12-22 04:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-10-22 04:00 | 2.0805 | 2.4653 | 2.4653 | 2.4653 | 2.4653
2024-12-22 05:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2024-10-22 05:00 | 2.3054 | 2.7317 | 2.7317 | 2.7317 | 2.7317
2024-12-22 06:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2024-10-22 06:00 | 2.6216 | 3.1064 | 3.1064 | 3.1064 | 3.1064
2024-12-22 07:00 | 1.1241 | 1.3984 | 1.6895 | 1.7283 | 1.7671 | 2024-10-22 07:00 | 3.0941 | 3.6663 | 3.6663 | 3.6663 | 3.6663
2024-12-22 08:00 | 0.7621 | 0.94804 | 1.1454 | 1.1717 | 1.198 | 2024-10-22 08:00 | 3.3571 | 3.9778 | 3.9778 | 3.9778 | 3.9778
2024-12-22 09:00 | 0.43821 | 0.54512 | 0.65861 | 0.67374 | 0.68887 | 2024-10-22 09:00 | 3.3075 | 3.9191 | 3.9191 | 3.9191 | 3.9191
2024-12-22 10:00 | 0.095263 | 0.1185 | 0.14318 | 0.14646 | 0.14975 | 2024-10-22 10:00 | 3.3151 | 3.9282 | 3.9282 | 3.9282 | 3.9282
2024-12-22 11:00 | 0.19096 | 0.23755 | 0.287 | 0.2936 | 0.30019 | 2024-10-22 11:00 | 3.2008 | 3.7927 | 3.7927 | 3.7927 | 3.7927
2024-12-22 12:00 | 0.26674 | 0.33181 | 0.40089 | 0.4101 | 0.41931 | 2024-10-22 12:00 | 3.902 | 4.6235 | 4.6235 | 4.6235 | 4.6235
2024-12-22 13:00 | 0.38105 | 0.47402 | 0.5727 | 0.58586 | 0.59902 | 2024-10-22 13:00 | 3.921 | 4.6461 | 4.6461 | 4.6461 | 4.6461
2024-12-22 14:00 | 0.22863 | 0.28441 | 0.34362 | 0.35152 | 0.35941 | 2024-10-22 14:00 | 3.681 | 4.3616 | 4.3616 | 4.3616 | 4.3616
2024-12-22 15:00 | 0.87642 | 1.0902 | 1.3172 | 1.3475 | 1.3777 | 2024-10-22 15:00 | 4.0734 | 4.8267 | 4.8267 | 4.8267 | 4.8267
2024-12-22 16:00 | 0.56496 | 0.7028 | 0.84911 | 0.86862 | 0.88813 | 2024-10-22 16:00 | 3.9858 | 4.7228 | 4.7228 | 4.7228 | 4.7228
2024-12-22 17:00 | 1.2765 | 1.588 | 1.9186 | 1.9626 | 2.0067 | 2024-10-22 17:00 | 3.8867 | 4.6054 | 4.6054 | 4.6054 | 4.6054
2024-12-22 18:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2024-10-22 18:00 | 3.2999 | 3.9101 | 3.9101 | 3.9101 | 3.9101
2024-12-22 19:00 | 1.6957 | 2.1094 | 2.5485 | 2.6071 | 2.6656 | 2024-10-22 19:00 | 2.816 | 3.3367 | 3.3367 | 3.3367 | 3.3367
2024-12-22 20:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2024-10-22 20:00 | 2.6178 | 3.1019 | 3.1019 | 3.1019 | 3.1019
2024-12-22 21:00 | 1.6195 | 2.0146 | 2.434 | 2.4899 | 2.5458 | 2024-10-22 21:00 | 2.3968 | 2.84 | 2.84 | 2.84 | 2.84
2024-12-22 22:00 | 1.6957 | 2.1094 | 2.5485 | 2.6071 | 2.6656 | 2024-10-22 22:00 | 2.0577 | 2.4382 | 2.4382 | 2.4382 | 2.4382
2024-12-22 23:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2024-10-22 23:00 | 1.9777 | 2.3434 | 2.3434 | 2.3434 | 2.3434
2024-12-23 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2024-10-23 | 1.8329 | 2.1718 | 2.1718 | 2.1718 | 2.1718
2024-12-23 01:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-10-23 01:00 | 1.8252 | 2.1628 | 2.1628 | 2.1628 | 2.1628
2024-12-23 02:00 | 1.4099 | 1.7539 | 2.119 | 2.1677 | 2.2164 | 2024-10-23 02:00 | 1.7909 | 2.1221 | 2.1221 | 2.1221 | 2.1221
2024-12-23 03:00 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-10-23 03:00 | 1.9129 | 2.2666 | 2.2666 | 2.2666 | 2.2666
2024-12-23 04:00 | 1.4289 | 1.7776 | 2.1476 | 2.197 | 2.2463 | 2024-10-23 04:00 | 2.1301 | 2.524 | 2.524 | 2.524 | 2.524
2024-12-23 05:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2024-10-23 05:00 | 2.3473 | 2.7813 | 2.7813 | 2.7813 | 2.7813
2024-12-23 06:00 | 1.7909 | 2.2279 | 2.6917 | 2.7535 | 2.8154 | 2024-10-23 06:00 | 2.5721 | 3.0477 | 3.0477 | 3.0477 | 3.0477
2024-12-23 07:00 | 2.3244 | 2.8915 | 3.4935 | 3.5737 | 3.654 | 2024-10-23 07:00 | 3.2123 | 3.8063 | 3.8063 | 3.8063 | 3.8063
2024-12-23 08:00 | 2.191 | 2.7256 | 3.293 | 3.3687 | 3.4444 | 2024-10-23 08:00 | 3.3723 | 3.9959 | 3.9959 | 3.9959 | 3.9959
2024-12-23 09:00 | 1.9243 | 2.3938 | 2.8921 | 2.9586 | 3.025 | 2024-10-23 09:00 | 3.4866 | 4.1314 | 4.1314 | 4.1314 | 4.1314
2024-12-23 10:00 | 2.3244 | 2.8915 | 3.4935 | 3.5737 | 3.654 | 2024-10-23 10:00 | 3.4142 | 4.0456 | 4.0456 | 4.0456 | 4.0456
2024-12-23 11:00 | 2.553 | 3.1759 | 3.8371 | 3.9253 | 4.0134 | 2024-10-23 11:00 | 3.7419 | 4.4339 | 4.4339 | 4.4339 | 4.4339
2024-12-23 12:00 | 2.2101 | 2.7493 | 3.3217 | 3.398 | 3.4743 | 2024-10-23 12:00 | 3.78 | 4.479 | 4.479 | 4.479 | 4.479
2024-12-23 13:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2024-10-23 13:00 | 4.0087 | 4.7499 | 4.7499 | 4.7499 | 4.7499
2024-12-23 14:00 | 1.1813 | 1.4695 | 1.7754 | 1.8162 | 1.857 | 2024-10-23 14:00 | 3.9782 | 4.7138 | 4.7138 | 4.7138 | 4.7138
2024-12-23 15:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2024-10-23 15:00 | 3.9972 | 4.7364 | 4.7364 | 4.7364 | 4.7364
2024-12-23 16:00 | 1.81 | 2.2516 | 2.7203 | 2.7828 | 2.8453 | 2024-10-23 16:00 | 3.8829 | 4.6009 | 4.6009 | 4.6009 | 4.6009
2024-12-23 17:00 | 2.2863 | 2.8441 | 3.4362 | 3.5152 | 3.5941 | 2024-10-23 17:00 | 3.5819 | 4.2442 | 4.2442 | 4.2442 | 4.2442
2024-12-23 18:00 | 2.3244 | 2.8915 | 3.4935 | 3.5737 | 3.654 | 2024-10-23 18:00 | 3.1932 | 3.7837 | 3.7837 | 3.7837 | 3.7837
2024-12-23 19:00 | 1.81 | 2.2516 | 2.7203 | 2.7828 | 2.8453 | 2024-10-23 19:00 | 2.8617 | 3.3909 | 3.3909 | 3.3909 | 3.3909
2024-12-23 20:00 | 1.7528 | 2.1805 | 2.6344 | 2.695 | 2.7555 | 2024-10-23 20:00 | 2.6826 | 3.1787 | 3.1787 | 3.1787 | 3.1787
2024-12-23 21:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-10-23 21:00 | 2.4845 | 2.9439 | 2.9439 | 2.9439 | 2.9439
2024-12-23 22:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-10-23 22:00 | 2.0234 | 2.3975 | 2.3975 | 2.3975 | 2.3975
2024-12-23 23:00 | 1.4099 | 1.7539 | 2.119 | 2.1677 | 2.2164 | 2024-10-23 23:00 | 1.9243 | 2.2801 | 2.2801 | 2.2801 | 2.2801
2024-12-24 | 1.2575 | 1.5643 | 1.8899 | 1.9333 | 1.9768 | 2024-10-24 | 1.8672 | 2.2124 | 2.2124 | 2.2124 | 2.2124
2024-12-24 01:00 | 1.2575 | 1.5643 | 1.8899 | 1.9333 | 1.9768 | 2024-10-24 01:00 | 1.8443 | 2.1853 | 2.1853 | 2.1853 | 2.1853
2024-12-24 02:00 | 1.2956 | 1.6117 | 1.9472 | 1.9919 | 2.0367 | 2024-10-24 02:00 | 1.8252 | 2.1628 | 2.1628 | 2.1628 | 2.1628
2024-12-24 03:00 | 1.2765 | 1.588 | 1.9186 | 1.9626 | 2.0067 | 2024-10-24 03:00 | 1.9662 | 2.3298 | 2.3298 | 2.3298 | 2.3298
2024-12-24 04:00 | 1.3527 | 1.6828 | 2.0331 | 2.0798 | 2.1265 | 2024-10-24 04:00 | 2.0196 | 2.393 | 2.393 | 2.393 | 2.393
2024-12-24 05:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-10-24 05:00 | 2.3358 | 2.7678 | 2.7678 | 2.7678 | 2.7678
2024-12-24 06:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2024-10-24 06:00 | 2.4159 | 2.8626 | 2.8626 | 2.8626 | 2.8626
2024-12-24 07:00 | 2.3244 | 2.8915 | 3.4935 | 3.5737 | 3.654 | 2024-10-24 07:00 | 2.6178 | 3.1019 | 3.1019 | 3.1019 | 3.1019
2024-12-24 08:00 | 2.0577 | 2.5597 | 3.0926 | 3.1636 | 3.2347 | 2024-10-24 08:00 | 2.915 | 3.4541 | 3.4541 | 3.4541 | 3.4541
2024-12-24 09:00 | 1.8481 | 2.299 | 2.7776 | 2.8414 | 2.9052 | 2024-10-24 09:00 | 3.1094 | 3.6844 | 3.6844 | 3.6844 | 3.6844
2024-12-24 10:00 | 1.3718 | 1.7065 | 2.0617 | 2.1091 | 2.1565 | 2024-10-24 10:00 | 3.0675 | 3.6347 | 3.6347 | 3.6347 | 3.6347
2024-12-24 11:00 | 1.1241 | 1.3984 | 1.6895 | 1.7283 | 1.7671 | 2024-10-24 11:00 | 3.0255 | 3.585 | 3.585 | 3.585 | 3.585
2024-12-24 12:00 | 1.4099 | 1.7539 | 2.119 | 2.1677 | 2.2164 | 2024-10-24 12:00 | 3.0484 | 3.6121 | 3.6121 | 3.6121 | 3.6121
2024-12-24 13:00 | 1.9815 | 2.4649 | 2.9781 | 3.0465 | 3.1149 | 2024-10-24 13:00 | 3.2313 | 3.8288 | 3.8288 | 3.8288 | 3.8288
2024-12-24 14:00 | 2.1148 | 2.6308 | 3.1785 | 3.2515 | 3.3245 | 2024-10-24 14:00 | 3.0789 | 3.6482 | 3.6482 | 3.6482 | 3.6482
2024-12-24 15:00 | 1.9053 | 2.3701 | 2.8635 | 2.9293 | 2.9951 | 2024-10-24 15:00 | 3.0979 | 3.6708 | 3.6708 | 3.6708 | 3.6708
2024-12-24 16:00 | 1.9434 | 2.4175 | 2.9208 | 2.9879 | 3.055 | 2024-10-24 16:00 | 3.3456 | 3.9643 | 3.9643 | 3.9643 | 3.9643
2024-12-24 17:00 | 1.4099 | 1.7539 | 2.119 | 2.1677 | 2.2164 | 2024-10-24 17:00 | 3.3723 | 3.9959 | 3.9959 | 3.9959 | 3.9959
2024-12-24 18:00 | 2.1148 | 2.6308 | 3.1785 | 3.2515 | 3.3245 | 2024-10-24 18:00 | 3.277 | 3.883 | 3.883 | 3.883 | 3.883
2024-12-24 19:00 | 1.829 | 2.2753 | 2.749 | 2.8121 | 2.8753 | 2024-10-24 19:00 | 2.8922 | 3.427 | 3.427 | 3.427 | 3.427
2024-12-24 20:00 | 1.7909 | 2.2279 | 2.6917 | 2.7535 | 2.8154 | 2024-10-24 20:00 | 2.5873 | 3.0658 | 3.0658 | 3.0658 | 3.0658
2024-12-24 21:00 | 1.7528 | 2.1805 | 2.6344 | 2.695 | 2.7555 | 2024-10-24 21:00 | 2.3511 | 2.7858 | 2.7858 | 2.7858 | 2.7858
2024-12-24 22:00 | 1.7338 | 2.1568 | 2.6058 | 2.6657 | 2.7255 | 2024-10-24 22:00 | 2.1453 | 2.542 | 2.542 | 2.542 | 2.542
2024-12-24 23:00 | 1.6957 | 2.1094 | 2.5485 | 2.6071 | 2.6656 | 2024-10-24 23:00 | 1.8786 | 2.226 | 2.226 | 2.226 | 2.226
2024-12-25 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2024-10-25 | 1.8519 | 2.1944 | 2.1944 | 2.1944 | 2.1944
2024-12-25 01:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2024-10-25 01:00 | 1.7909 | 2.1221 | 2.1221 | 2.1221 | 2.1221
2024-12-25 02:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2024-10-25 02:00 | 1.7605 | 2.086 | 2.086 | 2.086 | 2.086
2024-12-25 03:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2024-10-25 03:00 | 1.9929 | 2.3614 | 2.3614 | 2.3614 | 2.3614
2024-12-25 04:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2024-10-25 04:00 | 2.1415 | 2.5375 | 2.5375 | 2.5375 | 2.5375
2024-12-25 05:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2024-10-25 05:00 | 2.3968 | 2.84 | 2.84 | 2.84 | 2.84
2024-12-25 06:00 | 1.9434 | 2.4175 | 2.9208 | 2.9879 | 3.055 | 2024-10-25 06:00 | 2.6331 | 3.12 | 3.12 | 3.12 | 3.12
2024-12-25 07:00 | 0.55252 | 0.68733 | 0.83042 | 0.8495 | 0.86858 | 2024-10-25 07:00 | 2.8122 | 3.3322 | 3.3322 | 3.3322 | 3.3322
2024-12-25 08:00 | 0.28579 | 0.35551 | 0.42953 | 0.43939 | 0.44926 | 2024-10-25 08:00 | 3.0903 | 3.6618 | 3.6618 | 3.6618 | 3.6618
2024-12-25 09:00 | 0.22863 | 0.28441 | 0.34362 | 0.35152 | 0.35941 | 2024-10-25 09:00 | 3.2046 | 3.7972 | 3.7972 | 3.7972 | 3.7972
2024-12-25 10:00 | 0.30484 | 0.37921 | 0.45816 | 0.46869 | 0.47921 | 2024-10-25 10:00 | 3.1818 | 3.7701 | 3.7701 | 3.7701 | 3.7701
2024-12-25 11:00 | 0.45726 | 0.56882 | 0.68724 | 0.70303 | 0.71882 | 2024-10-25 11:00 | 3.338 | 3.9553 | 3.9553 | 3.9553 | 3.9553
2024-12-25 12:00 | 2.0767 | 2.5834 | 3.1212 | 3.1929 | 3.2646 | 2024-10-25 12:00 | 3.6505 | 4.3255 | 4.3255 | 4.3255 | 4.3255
2024-12-25 13:00 | 2.7436 | 3.4129 | 4.1235 | 4.2182 | 4.3129 | 2024-10-25 13:00 | 3.6543 | 4.33 | 4.33 | 4.33 | 4.33
2024-12-25 14:00 | 2.7245 | 3.3892 | 4.0948 | 4.1889 | 4.283 | 2024-10-25 14:00 | 3.559 | 4.2171 | 4.2171 | 4.2171 | 4.2171
2024-12-25 15:00 | 2.3054 | 2.8678 | 3.4648 | 3.5445 | 3.6241 | 2024-10-25 15:00 | 3.6047 | 4.2713 | 4.2713 | 4.2713 | 4.2713
2024-12-25 16:00 | 2.6293 | 3.2707 | 3.9516 | 4.0424 | 4.1332 | 2024-10-25 16:00 | 3.3685 | 3.9914 | 3.9914 | 3.9914 | 3.9914
2024-12-25 17:00 | 2.7055 | 3.3655 | 4.0662 | 4.1596 | 4.253 | 2024-10-25 17:00 | 3.2809 | 3.8875 | 3.8875 | 3.8875 | 3.8875
2024-12-25 18:00 | 2.2863 | 2.8441 | 3.4362 | 3.5152 | 3.5941 | 2024-10-25 18:00 | 3.1665 | 3.7521 | 3.7521 | 3.7521 | 3.7521
2024-12-25 19:00 | 2.0767 | 2.5834 | 3.1212 | 3.1929 | 3.2646 | 2024-10-25 19:00 | 2.9608 | 3.5083 | 3.5083 | 3.5083 | 3.5083
2024-12-25 20:00 | 2.0005 | 2.4886 | 3.0067 | 3.0758 | 3.1448 | 2024-10-25 20:00 | 2.915 | 3.4541 | 3.4541 | 3.4541 | 3.4541
2024-12-25 21:00 | 1.8862 | 2.3464 | 2.8349 | 2.9 | 2.9651 | 2024-10-25 21:00 | 2.4997 | 2.9619 | 2.9619 | 2.9619 | 2.9619
2024-12-25 22:00 | 1.7528 | 2.1805 | 2.6344 | 2.695 | 2.7555 | 2024-10-25 22:00 | 2.0653 | 2.4472 | 2.4472 | 2.4472 | 2.4472
2024-12-25 23:00 | 1.7147 | 2.1331 | 2.5772 | 2.6364 | 2.6956 | 2024-10-25 23:00 | 1.97 | 2.3343 | 2.3343 | 2.3343 | 2.3343
2024-12-26 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2024-10-26 | 1.9167 | 2.2711 | 2.2711 | 2.2711 | 2.2711
2024-12-26 01:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-10-26 01:00 | 1.8938 | 2.244 | 2.244 | 2.244 | 2.244
2024-12-26 02:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-10-26 02:00 | 1.8405 | 2.1808 | 2.1808 | 2.1808 | 2.1808
2024-12-26 03:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2024-10-26 03:00 | 1.97 | 2.3343 | 2.3343 | 2.3343 | 2.3343
2024-12-26 04:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-10-26 04:00 | 2.0386 | 2.4156 | 2.4156 | 2.4156 | 2.4156
2024-12-26 05:00 | 1.7338 | 2.1568 | 2.6058 | 2.6657 | 2.7255 | 2024-10-26 05:00 | 2.3054 | 2.7317 | 2.7317 | 2.7317 | 2.7317
2024-12-26 06:00 | 2.0386 | 2.536 | 3.064 | 3.1344 | 3.2047 | 2024-10-26 06:00 | 2.4463 | 2.8987 | 2.8987 | 2.8987 | 2.8987
2024-12-26 07:00 | 2.2863 | 2.8441 | 3.4362 | 3.5152 | 3.5941 | 2024-10-26 07:00 | 2.3625 | 2.7994 | 2.7994 | 2.7994 | 2.7994
2024-12-26 08:00 | 2.3435 | 2.9152 | 3.5221 | 3.603 | 3.684 | 2024-10-26 08:00 | 2.6369 | 3.1245 | 3.1245 | 3.1245 | 3.1245
2024-12-26 09:00 | 2.5721 | 3.1996 | 3.8657 | 3.9546 | 4.0434 | 2024-10-26 09:00 | 2.7664 | 3.278 | 3.278 | 3.278 | 3.278
2024-12-26 10:00 | 2.3816 | 2.9626 | 3.5794 | 3.6616 | 3.7439 | 2024-10-26 10:00 | 2.5226 | 2.989 | 2.989 | 2.989 | 2.989
2024-12-26 11:00 | 1.5814 | 1.9672 | 2.3767 | 2.4313 | 2.4859 | 2024-10-26 11:00 | 2.5416 | 3.0116 | 3.0116 | 3.0116 | 3.0116
2024-12-26 12:00 | 1.9815 | 2.4649 | 2.9781 | 3.0465 | 3.1149 | 2024-10-26 12:00 | 2.5988 | 3.0793 | 3.0793 | 3.0793 | 3.0793
2024-12-26 13:00 | 1.8481 | 2.299 | 2.7776 | 2.8414 | 2.9052 | 2024-10-26 13:00 | 2.5187 | 2.9845 | 2.9845 | 2.9845 | 2.9845
2024-12-26 14:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2024-10-26 14:00 | 2.4425 | 2.8942 | 2.8942 | 2.8942 | 2.8942
2024-12-26 15:00 | 2.0196 | 2.5123 | 3.0353 | 3.1051 | 3.1748 | 2024-10-26 15:00 | 2.3701 | 2.8084 | 2.8084 | 2.8084 | 2.8084
2024-12-26 16:00 | 2.3816 | 2.9626 | 3.5794 | 3.6616 | 3.7439 | 2024-10-26 16:00 | 2.6788 | 3.1741 | 3.1741 | 3.1741 | 3.1741
2024-12-26 17:00 | 2.4768 | 3.0811 | 3.7226 | 3.8081 | 3.8936 | 2024-10-26 17:00 | 2.5988 | 3.0793 | 3.0793 | 3.0793 | 3.0793
2024-12-26 18:00 | 2.3625 | 2.9389 | 3.5508 | 3.6323 | 3.7139 | 2024-10-26 18:00 | 2.6826 | 3.1787 | 3.1787 | 3.1787 | 3.1787
2024-12-26 19:00 | 1.7719 | 2.2042 | 2.6631 | 2.7242 | 2.7854 | 2024-10-26 19:00 | 2.3816 | 2.822 | 2.822 | 2.822 | 2.822
2024-12-26 20:00 | 1.7338 | 2.1568 | 2.6058 | 2.6657 | 2.7255 | 2024-10-26 20:00 | 2.2977 | 2.7226 | 2.7226 | 2.7226 | 2.7226
2024-12-26 21:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2024-10-26 21:00 | 2.2025 | 2.6097 | 2.6097 | 2.6097 | 2.6097
2024-12-26 22:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2024-10-26 22:00 | 2.2253 | 2.6368 | 2.6368 | 2.6368 | 2.6368
2024-12-26 23:00 | 1.6004 | 1.9909 | 2.4053 | 2.4606 | 2.5159 | 2024-10-26 23:00 | 2.012 | 2.384 | 2.384 | 2.384 | 2.384
2024-12-27 | 1.467 | 1.825 | 2.2049 | 2.2556 | 2.3062 | 2024-10-27 | 1.7643 | 2.0905 | 2.0905 | 2.0905 | 2.0905
2024-12-27 01:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-10-27 01:00 | 1.8176 | 2.1537 | 2.1537 | 2.1537 | 2.1537
2024-12-27 02:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-10-27 02:00 | 1.749 | 2.0724 | 2.0724 | 2.0724 | 2.0724
2024-12-27 03:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-10-27 03:00 | 1.8329 | 2.1718 | 2.1718 | 2.1718 | 2.1718
2024-12-27 04:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-10-27 04:00 | 1.9624 | 2.3253 | 2.3253 | 2.3253 | 2.3253
2024-12-27 05:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2024-10-27 05:00 | 2.233 | 2.6459 | 2.6459 | 2.6459 | 2.6459
2024-12-27 06:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2024-10-27 06:00 | 2.2977 | 2.7226 | 2.7226 | 2.7226 | 2.7226
2024-12-27 07:00 | 0.55252 | 0.68733 | 0.83042 | 0.8495 | 0.86858 | 2024-10-27 07:00 | 2.1872 | 2.5917 | 2.5917 | 2.5917 | 2.5917
2024-12-27 08:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-10-27 08:00 | 2.4425 | 2.8942 | 2.8942 | 2.8942 | 2.8942
2024-12-27 09:00 | 1.105 | 1.3747 | 1.6608 | 1.699 | 1.7372 | 2024-10-27 09:00 | 2.4349 | 2.8852 | 2.8852 | 2.8852 | 2.8852
2024-12-27 10:00 | 0.13337 | 0.16591 | 0.20045 | 0.20505 | 0.20966 | 2024-10-27 10:00 | 2.4768 | 2.9348 | 2.9348 | 2.9348 | 2.9348
2024-12-27 11:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2024-10-27 11:00 | 2.9036 | 3.4405 | 3.4405 | 3.4405 | 3.4405
2024-12-27 12:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-10-27 12:00 | 2.6483 | 3.138 | 3.138 | 3.138 | 3.138
2024-12-27 13:00 | 1.8481 | 2.299 | 2.7776 | 2.8414 | 2.9052 | 2024-10-27 13:00 | 2.5797 | 3.0567 | 3.0567 | 3.0567 | 3.0567
2024-12-27 14:00 | 1.81 | 2.2516 | 2.7203 | 2.7828 | 2.8453 | 2024-10-27 14:00 | 3.1665 | 3.7521 | 3.7521 | 3.7521 | 3.7521
2024-12-27 15:00 | 1.8862 | 2.3464 | 2.8349 | 2.9 | 2.9651 | 2024-10-27 15:00 | 3.2123 | 3.8063 | 3.8063 | 3.8063 | 3.8063
2024-12-27 16:00 | 1.9624 | 2.4412 | 2.9494 | 3.0172 | 3.0849 | 2024-10-27 16:00 | 3.1284 | 3.7069 | 3.7069 | 3.7069 | 3.7069
2024-12-27 17:00 | 1.9624 | 2.4412 | 2.9494 | 3.0172 | 3.0849 | 2024-10-27 17:00 | 2.7664 | 3.278 | 3.278 | 3.278 | 3.278
2024-12-27 18:00 | 1.9243 | 2.3938 | 2.8921 | 2.9586 | 3.025 | 2024-10-27 18:00 | 2.7245 | 3.2283 | 3.2283 | 3.2283 | 3.2283
2024-12-27 19:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-10-27 19:00 | 2.4463 | 2.8987 | 2.8987 | 2.8987 | 2.8987
2024-12-27 20:00 | 1.4289 | 1.7776 | 2.1476 | 2.197 | 2.2463 | 2024-10-27 20:00 | 2.1644 | 2.5646 | 2.5646 | 2.5646 | 2.5646
2024-12-27 21:00 | 1.3908 | 1.7302 | 2.0904 | 2.1384 | 2.1864 | 2024-10-27 21:00 | 2.1301 | 2.524 | 2.524 | 2.524 | 2.524
2024-12-27 22:00 | 1.3718 | 1.7065 | 2.0617 | 2.1091 | 2.1565 | 2024-10-27 22:00 | 1.8748 | 2.2214 | 2.2214 | 2.2214 | 2.2214
2024-12-27 23:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2024-10-27 23:00 | 1.8024 | 2.1357 | 2.1357 | 2.1357 | 2.1357
2024-12-28 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-10-28 | 1.7948 | 2.1266 | 2.1266 | 2.1266 | 2.1266
2024-12-28 01:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-10-28 01:00 | 1.7605 | 2.086 | 2.086 | 2.086 | 2.086
2024-12-28 02:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-10-28 02:00 | 1.8329 | 2.1718 | 2.1718 | 2.1718 | 2.1718
2024-12-28 03:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-10-28 03:00 | 1.8824 | 2.2305 | 2.2305 | 2.2305 | 2.2305
2024-12-28 04:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-10-28 04:00 | 2.0462 | 2.4246 | 2.4246 | 2.4246 | 2.4246
2024-12-28 05:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2024-10-28 05:00 | 2.3739 | 2.8129 | 2.8129 | 2.8129 | 2.8129
2024-12-28 06:00 | 1.7528 | 2.1805 | 2.6344 | 2.695 | 2.7555 | 2024-10-28 06:00 | 2.7664 | 3.278 | 3.278 | 3.278 | 3.278
2024-12-28 07:00 | 0.81926 | 1.0191 | 1.2313 | 1.2596 | 1.2879 | 2024-10-28 07:00 | 3.056 | 3.6211 | 3.6211 | 3.6211 | 3.6211
2024-12-28 08:00 | 1.1622 | 1.4458 | 1.7467 | 1.7869 | 1.827 | 2024-10-28 08:00 | 3.5019 | 4.1494 | 4.1494 | 4.1494 | 4.1494
2024-12-28 09:00 | 0.38105 | 0.47402 | 0.5727 | 0.58586 | 0.59902 | 2024-10-28 09:00 | 3.4333 | 4.0681 | 4.0681 | 4.0681 | 4.0681
2024-12-28 10:00 | 0.26674 | 0.33181 | 0.40089 | 0.4101 | 0.41931 | 2024-10-28 10:00 | 3.6276 | 4.2984 | 4.2984 | 4.2984 | 4.2984
2024-12-28 11:00 | 0.07621 | 0.094804 | 0.11454 | 0.11717 | 0.1198 | 2024-10-28 11:00 | 3.6009 | 4.2668 | 4.2668 | 4.2668 | 4.2668
2024-12-28 12:00 | 0.26674 | 0.33181 | 0.40089 | 0.4101 | 0.41931 | 2024-10-28 12:00 | 3.3723 | 3.9959 | 3.9959 | 3.9959 | 3.9959
2024-12-28 13:00 | 0.22863 | 0.28441 | 0.34362 | 0.35152 | 0.35941 | 2024-10-28 13:00 | 3.2961 | 3.9056 | 3.9056 | 3.9056 | 3.9056
2024-12-28 14:00 | 0.55252 | 0.68733 | 0.83042 | 0.8495 | 0.86858 | 2024-10-28 14:00 | 3.1322 | 3.7114 | 3.7114 | 3.7114 | 3.7114
2024-12-28 15:00 | 0.38105 | 0.47402 | 0.5727 | 0.58586 | 0.59902 | 2024-10-28 15:00 | 3.3685 | 3.9914 | 3.9914 | 3.9914 | 3.9914
2024-12-28 16:00 | 0.64779 | 0.80583 | 0.97359 | 0.99596 | 1.0183 | 2024-10-28 16:00 | 3.7915 | 4.4926 | 4.4926 | 4.4926 | 4.4926
2024-12-28 17:00 | 0.89547 | 1.1139 | 1.3458 | 1.3768 | 1.4077 | 2024-10-28 17:00 | 3.7305 | 4.4203 | 4.4203 | 4.4203 | 4.4203
2024-12-28 18:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-10-28 18:00 | 3.1284 | 3.7069 | 3.7069 | 3.7069 | 3.7069
2024-12-28 19:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2024-10-28 19:00 | 2.6369 | 3.1245 | 3.1245 | 3.1245 | 3.1245
2024-12-28 20:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-10-28 20:00 | 2.614 | 3.0974 | 3.0974 | 3.0974 | 3.0974
2024-12-28 21:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-10-28 21:00 | 2.1758 | 2.5781 | 2.5781 | 2.5781 | 2.5781
2024-12-28 22:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-10-28 22:00 | 1.9891 | 2.3569 | 2.3569 | 2.3569 | 2.3569
2024-12-28 23:00 | 1.3718 | 1.7065 | 2.0617 | 2.1091 | 2.1565 | 2024-10-28 23:00 | 1.9319 | 2.2892 | 2.2892 | 2.2892 | 2.2892
2024-12-29 | 1.2956 | 1.6117 | 1.9472 | 1.9919 | 2.0367 | 2024-10-29 | 1.9624 | 2.3253 | 2.3253 | 2.3253 | 2.3253
2024-12-29 01:00 | 1.3527 | 1.6828 | 2.0331 | 2.0798 | 2.1265 | 2024-10-29 01:00 | 1.829 | 2.1673 | 2.1673 | 2.1673 | 2.1673
2024-12-29 02:00 | 1.4289 | 1.7776 | 2.1476 | 2.197 | 2.2463 | 2024-10-29 02:00 | 1.7376 | 2.0589 | 2.0589 | 2.0589 | 2.0589
2024-12-29 03:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-10-29 03:00 | 1.8938 | 2.244 | 2.244 | 2.244 | 2.244
2024-12-29 04:00 | 1.4099 | 1.7539 | 2.119 | 2.1677 | 2.2164 | 2024-10-29 04:00 | 2.0386 | 2.4156 | 2.4156 | 2.4156 | 2.4156
2024-12-29 05:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-10-29 05:00 | 2.3968 | 2.84 | 2.84 | 2.84 | 2.84
2024-12-29 06:00 | 1.5433 | 1.9198 | 2.3194 | 2.3727 | 2.426 | 2024-10-29 06:00 | 2.4463 | 2.8987 | 2.8987 | 2.8987 | 2.8987
2024-12-29 07:00 | 1.0288 | 1.2798 | 1.5463 | 1.5818 | 1.6173 | 2024-10-29 07:00 | 2.6902 | 3.1877 | 3.1877 | 3.1877 | 3.1877
2024-12-29 08:00 | 0.64779 | 0.80583 | 0.97359 | 0.99596 | 1.0183 | 2024-10-29 08:00 | 3.0637 | 3.6302 | 3.6302 | 3.6302 | 3.6302
2024-12-29 09:00 | 0.19053 | 0.23701 | 0.28635 | 0.29293 | 0.29951 | 2024-10-29 09:00 | 3.0141 | 3.5715 | 3.5715 | 3.5715 | 3.5715
2024-12-29 10:00 | 0.019053 | 0.023701 | 0.028635 | 0.029293 | 0.029951 | 2024-10-29 10:00 | 2.957 | 3.5037 | 3.5037 | 3.5037 | 3.5037
2024-12-29 11:00 | 0.20005 | 0.24886 | 0.30067 | 0.30758 | 0.31448 | 2024-10-29 11:00 | 3.2313 | 3.8288 | 3.8288 | 3.8288 | 3.8288
2024-12-29 12:00 | 0.20958 | 0.26071 | 0.31499 | 0.32222 | 0.32946 | 2024-10-29 12:00 | 3.1665 | 3.7521 | 3.7521 | 3.7521 | 3.7521
2024-12-29 13:00 | 0.30484 | 0.37921 | 0.45816 | 0.46869 | 0.47921 | 2024-10-29 13:00 | 3.3151 | 3.9282 | 3.9282 | 3.9282 | 3.9282
2024-12-29 14:00 | 0.19053 | 0.23701 | 0.28635 | 0.29293 | 0.29951 | 2024-10-29 14:00 | 3.2008 | 3.7927 | 3.7927 | 3.7927 | 3.7927
2024-12-29 15:00 | 0.81926 | 1.0191 | 1.2313 | 1.2596 | 1.2879 | 2024-10-29 15:00 | 3.3456 | 3.9643 | 3.9643 | 3.9643 | 3.9643
2024-12-29 16:00 | 0.6076 | 0.75584 | 0.9132 | 0.93418 | 0.95516 | 2024-10-29 16:00 | 3.639 | 4.312 | 4.312 | 4.312 | 4.312
2024-12-29 17:00 | 1.1432 | 1.4221 | 1.7181 | 1.7576 | 1.7971 | 2024-10-29 17:00 | 3.7724 | 4.47 | 4.47 | 4.47 | 4.47
2024-12-29 18:00 | 1.9053 | 2.3701 | 2.8635 | 2.9293 | 2.9951 | 2024-10-29 18:00 | 3.5743 | 4.2352 | 4.2352 | 4.2352 | 4.2352
2024-12-29 19:00 | 1.9624 | 2.4412 | 2.9494 | 3.0172 | 3.0849 | 2024-10-29 19:00 | 2.7283 | 3.2328 | 3.2328 | 3.2328 | 3.2328
2024-12-29 20:00 | 1.9434 | 2.4175 | 2.9208 | 2.9879 | 3.055 | 2024-10-29 20:00 | 2.694 | 3.1922 | 3.1922 | 3.1922 | 3.1922
2024-12-29 21:00 | 1.8862 | 2.3464 | 2.8349 | 2.9 | 2.9651 | 2024-10-29 21:00 | 2.313 | 2.7407 | 2.7407 | 2.7407 | 2.7407
2024-12-29 22:00 | 1.9624 | 2.4412 | 2.9494 | 3.0172 | 3.0849 | 2024-10-29 22:00 | 1.9891 | 2.3569 | 2.3569 | 2.3569 | 2.3569
2024-12-29 23:00 | 1.829 | 2.2753 | 2.749 | 2.8121 | 2.8753 | 2024-10-29 23:00 | 1.9472 | 2.3072 | 2.3072 | 2.3072 | 2.3072
2024-12-30 | 1.81 | 2.2516 | 2.7203 | 2.7828 | 2.8453 | 2024-10-30 | 1.9167 | 2.2711 | 2.2711 | 2.2711 | 2.2711
2024-12-30 01:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2024-10-30 01:00 | 1.9053 | 2.2576 | 2.2576 | 2.2576 | 2.2576
2024-12-30 02:00 | 1.6385 | 2.0383 | 2.4626 | 2.5192 | 2.5758 | 2024-10-30 02:00 | 1.7795 | 2.1086 | 2.1086 | 2.1086 | 2.1086
2024-12-30 03:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2024-10-30 03:00 | 1.9319 | 2.2892 | 2.2892 | 2.2892 | 2.2892
2024-12-30 04:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2024-10-30 04:00 | 2.0272 | 2.4021 | 2.4021 | 2.4021 | 2.4021
2024-12-30 05:00 | 1.8672 | 2.3227 | 2.8062 | 2.8707 | 2.9352 | 2024-10-30 05:00 | 2.3244 | 2.7542 | 2.7542 | 2.7542 | 2.7542
2024-12-30 06:00 | 2.0386 | 2.536 | 3.064 | 3.1344 | 3.2047 | 2024-10-30 06:00 | 2.5797 | 3.0567 | 3.0567 | 3.0567 | 3.0567
2024-12-30 07:00 | 2.2291 | 2.773 | 3.3503 | 3.4273 | 3.5043 | 2024-10-30 07:00 | 2.9874 | 3.5399 | 3.5399 | 3.5399 | 3.5399
2024-12-30 08:00 | 2.0958 | 2.6071 | 3.1499 | 3.2222 | 3.2946 | 2024-10-30 08:00 | 3.1094 | 3.6844 | 3.6844 | 3.6844 | 3.6844
2024-12-30 09:00 | 1.8862 | 2.3464 | 2.8349 | 2.9 | 2.9651 | 2024-10-30 09:00 | 3.2199 | 3.8153 | 3.8153 | 3.8153 | 3.8153
2024-12-30 10:00 | 2.3054 | 2.8678 | 3.4648 | 3.5445 | 3.6241 | 2024-10-30 10:00 | 3.2504 | 3.8514 | 3.8514 | 3.8514 | 3.8514
2024-12-30 11:00 | 2.6483 | 3.2944 | 3.9803 | 4.0717 | 4.1632 | 2024-10-30 11:00 | 3.338 | 3.9553 | 3.9553 | 3.9553 | 3.9553
2024-12-30 12:00 | 2.3816 | 2.9626 | 3.5794 | 3.6616 | 3.7439 | 2024-10-30 12:00 | 3.4066 | 4.0365 | 4.0365 | 4.0365 | 4.0365
2024-12-30 13:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2024-10-30 13:00 | 3.3952 | 4.023 | 4.023 | 4.023 | 4.023
2024-12-30 14:00 | 1.3337 | 1.6591 | 2.0045 | 2.0505 | 2.0966 | 2024-10-30 14:00 | 3.3266 | 3.9417 | 3.9417 | 3.9417 | 3.9417
2024-12-30 15:00 | 1.8481 | 2.299 | 2.7776 | 2.8414 | 2.9052 | 2024-10-30 15:00 | 3.4218 | 4.0546 | 4.0546 | 4.0546 | 4.0546
2024-12-30 16:00 | 2.0386 | 2.536 | 3.064 | 3.1344 | 3.2047 | 2024-10-30 16:00 | 3.6238 | 4.2939 | 4.2939 | 4.2939 | 4.2939
2024-12-30 17:00 | 2.1529 | 2.6782 | 3.2358 | 3.3101 | 3.3845 | 2024-10-30 17:00 | 3.6619 | 4.339 | 4.339 | 4.339 | 4.339
2024-12-30 18:00 | 2.4959 | 3.1048 | 3.7512 | 3.8374 | 3.9236 | 2024-10-30 18:00 | 3.4828 | 4.1268 | 4.1268 | 4.1268 | 4.1268
2024-12-30 19:00 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 2024-10-30 19:00 | 2.9608 | 3.5083 | 3.5083 | 3.5083 | 3.5083
2024-12-30 20:00 | 1.7338 | 2.1568 | 2.6058 | 2.6657 | 2.7255 | 2024-10-30 20:00 | 2.896 | 3.4315 | 3.4315 | 3.4315 | 3.4315
2024-12-30 21:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2024-10-30 21:00 | 2.3701 | 2.8084 | 2.8084 | 2.8084 | 2.8084
2024-12-30 22:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2024-10-30 22:00 | 2.0462 | 2.4246 | 2.4246 | 2.4246 | 2.4246
2024-12-30 23:00 | 1.5242 | 1.8961 | 2.2908 | 2.3434 | 2.3961 | 2024-10-30 23:00 | 1.9167 | 2.2711 | 2.2711 | 2.2711 | 2.2711
2024-12-31 | 1.3908 | 1.7302 | 2.0904 | 2.1384 | 2.1864 | 2024-10-31 | 1.9472 | 2.3072 | 2.3072 | 2.3072 | 2.3072
2024-12-31 01:00 | 1.3337 | 1.6591 | 2.0045 | 2.0505 | 2.0966 | 2024-10-31 01:00 | 1.8481 | 2.1898 | 2.1898 | 2.1898 | 2.1898
2024-12-31 02:00 | 1.448 | 1.8013 | 2.1763 | 2.2263 | 2.2763 | 2024-10-31 02:00 | 1.7719 | 2.0995 | 2.0995 | 2.0995 | 2.0995
2024-12-31 03:00 | 1.3908 | 1.7302 | 2.0904 | 2.1384 | 2.1864 | 2024-10-31 03:00 | 1.9281 | 2.2847 | 2.2847 | 2.2847 | 2.2847
2024-12-31 04:00 | 1.5052 | 1.8724 | 2.2622 | 2.3141 | 2.3661 | 2024-10-31 04:00 | 2.0882 | 2.4743 | 2.4743 | 2.4743 | 2.4743
2024-12-31 05:00 | 1.7147 | 2.1331 | 2.5772 | 2.6364 | 2.6956 | 2024-10-31 05:00 | 2.3282 | 2.7587 | 2.7587 | 2.7587 | 2.7587
2024-12-31 06:00 | 1.7909 | 2.2279 | 2.6917 | 2.7535 | 2.8154 | 2024-10-31 06:00 | 2.5759 | 3.0522 | 3.0522 | 3.0522 | 3.0522
2024-12-31 07:00 | 2.3625 | 2.9389 | 3.5508 | 3.6323 | 3.7139 | 2024-10-31 07:00 | 2.816 | 3.3367 | 3.3367 | 3.3367 | 3.3367
2024-12-31 08:00 | 2.0958 | 2.6071 | 3.1499 | 3.2222 | 3.2946 | 2024-10-31 08:00 | 3.2504 | 3.8514 | 3.8514 | 3.8514 | 3.8514
2024-12-31 09:00 | 2.0005 | 2.4886 | 3.0067 | 3.0758 | 3.1448 | 2024-10-31 09:00 | 3.3494 | 3.9688 | 3.9688 | 3.9688 | 3.9688
2024-12-31 10:00 | 1.4861 | 1.8487 | 2.2335 | 2.2849 | 2.3362 | 2024-10-31 10:00 | 3.4714 | 4.1133 | 4.1133 | 4.1133 | 4.1133
2024-12-31 11:00 | 1.3527 | 1.6828 | 2.0331 | 2.0798 | 2.1265 | 2024-10-31 11:00 | 3.4752 | 4.1178 | 4.1178 | 4.1178 | 4.1178
2024-12-31 12:00 | 1.5623 | 1.9435 | 2.3481 | 2.402 | 2.456 | 2024-10-31 12:00 | 3.6238 | 4.2939 | 4.2939 | 4.2939 | 4.2939
2024-12-31 13:00 | 2.172 | 2.7019 | 3.2644 | 3.3394 | 3.4144 | 2024-10-31 13:00 | 3.7229 | 4.4113 | 4.4113 | 4.4113 | 4.4113
2024-12-31 14:00 | 2.3435 | 2.9152 | 3.5221 | 3.603 | 3.684 | 2024-10-31 14:00 | 3.6962 | 4.3797 | 4.3797 | 4.3797 | 4.3797
2024-12-31 15:00 | 2.0577 | 2.5597 | 3.0926 | 3.1636 | 3.2347 | 2024-10-31 15:00 | 3.5057 | 4.1539 | 4.1539 | 4.1539 | 4.1539
2024-12-31 16:00 | 1.9624 | 2.4412 | 2.9494 | 3.0172 | 3.0849 | 2024-10-31 16:00 | 3.8296 | 4.5377 | 4.5377 | 4.5377 | 4.5377
2024-12-31 17:00 | 1.2765 | 1.588 | 1.9186 | 1.9626 | 2.0067 | 2024-10-31 17:00 | 3.5933 | 4.2578 | 4.2578 | 4.2578 | 4.2578
2024-12-31 18:00 | 2.2101 | 2.7493 | 3.3217 | 3.398 | 3.4743 | 2024-10-31 18:00 | 2.9074 | 3.4451 | 3.4451 | 3.4451 | 3.4451
2024-12-31 19:00 | 1.9243 | 2.3938 | 2.8921 | 2.9586 | 3.025 | 2024-10-31 19:00 | 2.7436 | 3.2509 | 3.2509 | 3.2509 | 3.2509
2024-12-31 20:00 | 1.81 | 2.2516 | 2.7203 | 2.7828 | 2.8453 | 2024-10-31 20:00 | 2.5721 | 3.0477 | 3.0477 | 3.0477 | 3.0477
2024-12-31 21:00 | 1.7528 | 2.1805 | 2.6344 | 2.695 | 2.7555 | 2024-10-31 21:00 | 2.3778 | 2.8174 | 2.8174 | 2.8174 | 2.8174
2024-12-31 22:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2024-10-31 22:00 | 2.0081 | 2.3795 | 2.3795 | 2.3795 | 2.3795
2024-12-31 23:00 | 1.6576 | 2.062 | 2.4913 | 2.5485 | 2.6057 | 2024-10-31 23:00 | 1.9777 | 2.3434 | 2.3434 | 2.3434 | 2.3434
2025-01-01 | 0 | 0 | 0 | 0 | 0 | 2024-11-01 | 1.9777 | 2.3434 | 2.3434 | 2.3434 | 2.3434

## Daily Load - Winter
| Dairy North | [9 empty] | Aero Park
| Average Winter Day Load (MW/MVA) |  |  |  |  | Peak Winter Day Load (MW/MVA) |  |  |  |  | Average Winter Day Load (MW/MVA) |  |  |  |  | Peak Winter Day Load (MW/MVA)
Time | 2024 | 2026 | 2027 | 2028 | 2029 | 2024 | 2026 | 2027 | 2028 | 2029 | 2024 | 2026 | 2027 | 2028 | 2029 | 2024 | 2026 | 2027 | 2028 | 2029
0:00 | 1.5376 | 1.6498 | 2.048 | 2.1542 | 2.2604 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 1.7889 | 2.0851 | 2.0851 | 2.0851 | 2.0851 | 2.3397 | 2.7271 | 2.7271 | 2.7271 | 2.7271
1:00 | 1.5159 | 1.6264 | 2.019 | 2.1237 | 2.2284 | 1.7528 | 1.8807 | 2.3346 | 2.4557 | 2.5767 | 1.7596 | 2.051 | 2.051 | 2.051 | 2.051 | 2.3092 | 2.6915 | 2.6915 | 2.6915 | 2.6915
2:00 | 1.5084 | 1.6184 | 2.009 | 2.1132 | 2.2174 | 1.81 | 1.942 | 2.4107 | 2.5357 | 2.6607 | 1.7576 | 2.0487 | 2.0487 | 2.0487 | 2.0487 | 2.3739 | 2.767 | 2.767 | 2.767 | 2.767
3:00 | 1.5048 | 1.6146 | 2.0043 | 2.1082 | 2.2121 | 1.7147 | 1.8398 | 2.2839 | 2.4023 | 2.5207 | 1.8867 | 2.1991 | 2.1991 | 2.1991 | 2.1991 | 2.393 | 2.7893 | 2.7893 | 2.7893 | 2.7893
4:00 | 1.5571 | 1.6707 | 2.0739 | 2.1814 | 2.289 | 1.7528 | 1.8807 | 2.3346 | 2.4557 | 2.5767 | 2.1007 | 2.4485 | 2.4485 | 2.4485 | 2.4485 | 2.7779 | 3.2378 | 3.2378 | 3.2378 | 3.2378
5:00 | 1.6967 | 1.8204 | 2.2599 | 2.377 | 2.4942 | 2.0196 | 2.1668 | 2.6899 | 2.8293 | 2.9688 | 2.3635 | 2.7548 | 2.7548 | 2.7548 | 2.7548 | 3.0903 | 3.602 | 3.602 | 3.602 | 3.602
6:00 | 1.8507 | 1.9857 | 2.4649 | 2.5928 | 2.7206 | 2.4197 | 2.5961 | 3.2228 | 3.3899 | 3.557 | 2.7328 | 3.1853 | 3.1853 | 3.1853 | 3.1853 | 3.6543 | 4.2594 | 4.2594 | 4.2594 | 4.2594
7:00 | 2.0904 | 2.2428 | 2.7842 | 2.9285 | 3.0729 | 2.8388 | 3.0458 | 3.781 | 3.9771 | 4.1731 | 3.0601 | 3.5668 | 3.5668 | 3.5668 | 3.5668 | 3.9972 | 4.6591 | 4.6591 | 4.6591 | 4.6591
8:00 | 2.0204 | 2.1677 | 2.691 | 2.8305 | 2.97 | 2.8579 | 3.0663 | 3.8064 | 4.0038 | 4.2012 | 3.3398 | 3.8928 | 3.8928 | 3.8928 | 3.8928 | 4.3707 | 5.0944 | 5.0944 | 5.0944 | 5.0944
9:00 | 1.8641 | 2.0001 | 2.4828 | 2.6116 | 2.7403 | 2.896 | 3.1072 | 3.8572 | 4.0572 | 4.2572 | 3.4052 | 3.9691 | 3.9691 | 3.9691 | 3.9691 | 4.6641 | 5.4364 | 5.4364 | 5.4364 | 5.4364
10:00 | 1.7568 | 1.8849 | 2.3399 | 2.4612 | 2.5825 | 2.7436 | 2.9436 | 3.6542 | 3.8436 | 4.0331 | 3.3266 | 3.8774 | 3.8774 | 3.8774 | 3.8774 | 5.9787 | 6.9687 | 6.9687 | 6.9687 | 6.9687
11:00 | 1.6908 | 1.8141 | 2.252 | 2.3687 | 2.4855 | 2.5911 | 2.7801 | 3.4512 | 3.6301 | 3.809 | 3.3197 | 3.8695 | 3.8695 | 3.8695 | 3.8695 | 5.9444 | 6.9287 | 6.9287 | 6.9287 | 6.9287
12:00 | 1.7082 | 1.8327 | 2.2751 | 2.3931 | 2.5111 | 2.5911 | 2.7801 | 3.4512 | 3.6301 | 3.809 | 3.3661 | 3.9235 | 3.9235 | 3.9235 | 3.9235 | 5.7691 | 6.7244 | 6.7244 | 6.7244 | 6.7244
13:00 | 1.6771 | 1.7994 | 2.2338 | 2.3496 | 2.4654 | 2.5911 | 2.7801 | 3.4512 | 3.6301 | 3.809 | 3.3489 | 3.9035 | 3.9035 | 3.9035 | 3.9035 | 5.1861 | 6.0449 | 6.0449 | 6.0449 | 6.0449
14:00 | 1.6724 | 1.7943 | 2.2274 | 2.3429 | 2.4584 | 2.5911 | 2.7801 | 3.4512 | 3.6301 | 3.809 | 3.3571 | 3.913 | 3.913 | 3.913 | 3.913 | 5.1366 | 5.9871 | 5.9871 | 5.9871 | 5.9871
15:00 | 1.7213 | 1.8468 | 2.2926 | 2.4115 | 2.5303 | 2.4959 | 2.6779 | 3.3243 | 3.4966 | 3.669 | 3.3964 | 3.9588 | 3.9588 | 3.9588 | 3.9588 | 4.4964 | 5.241 | 5.241 | 5.241 | 5.241
16:00 | 1.9227 | 2.063 | 2.5609 | 2.6937 | 2.8265 | 2.6293 | 2.821 | 3.5019 | 3.6835 | 3.8651 | 3.5299 | 4.1144 | 4.1144 | 4.1144 | 4.1144 | 4.4964 | 5.241 | 5.241 | 5.241 | 5.241
17:00 | 1.9886 | 2.1337 | 2.6487 | 2.786 | 2.9234 | 2.4578 | 2.637 | 3.2735 | 3.4433 | 3.613 | 3.5167 | 4.099 | 4.099 | 4.099 | 4.099 | 4.5536 | 5.3076 | 5.3076 | 5.3076 | 5.3076
18:00 | 1.97 | 2.1137 | 2.6239 | 2.7599 | 2.896 | 2.553 | 2.7392 | 3.4004 | 3.5767 | 3.753 | 3.1945 | 3.7234 | 3.7234 | 3.7234 | 3.7234 | 4.1763 | 4.8679 | 4.8679 | 4.8679 | 4.8679
19:00 | 1.7753 | 1.9048 | 2.3646 | 2.4872 | 2.6098 | 2.0577 | 2.2077 | 2.7406 | 2.8827 | 3.0248 | 2.8 | 3.2636 | 3.2636 | 3.2636 | 3.2636 | 3.9058 | 4.5525 | 4.5525 | 4.5525 | 4.5525
20:00 | 1.7037 | 1.8279 | 2.2692 | 2.3868 | 2.5045 | 1.9624 | 2.1055 | 2.6137 | 2.7493 | 2.8848 | 2.5795 | 3.0066 | 3.0066 | 3.0066 | 3.0066 | 3.4523 | 4.024 | 4.024 | 4.024 | 4.024
21:00 | 1.6639 | 1.7853 | 2.2162 | 2.3311 | 2.446 | 1.829 | 1.9624 | 2.4361 | 2.5624 | 2.6887 | 2.3244 | 2.7093 | 2.7093 | 2.7093 | 2.7093 | 2.9608 | 3.451 | 3.451 | 3.451 | 3.451
22:00 | 1.6309 | 1.7498 | 2.1722 | 2.2849 | 2.3975 | 1.7528 | 1.8807 | 2.3346 | 2.4557 | 2.5767 | 2.0123 | 2.3455 | 2.3455 | 2.3455 | 2.3455 | 2.6674 | 3.109 | 3.109 | 3.109 | 3.109
23:00 | 1.6035 | 1.7205 | 2.1358 | 2.2465 | 2.3572 | 1.7909 | 1.9215 | 2.3854 | 2.509 | 2.6327 | 1.9231 | 2.2415 | 2.2415 | 2.2415 | 2.2415 | 2.4425 | 2.847 | 2.847 | 2.847 | 2.847

## Daily Load - Summer
| Dairy North | [9 empty] | Aero Park
| Average Summer Day Load (MW/MVA) |  |  |  |  | Peak Summer Day Load (MW/MVA) |  |  |  |  | Average Summer Day Load (MW/MVA) |  |  |  |  | Peak Summer Day Load (MW/MVA)
Time | 2021 | 2026 | 2027 | 2028 | 2029 | 2021 | 2026 | 2027 | 2028 | 2029 | 2021 | 2026 | 2027 | 2028 | 2029 | 2021 | 2026 | 2027 | 2028 | 2029
0:00 | 1.5195 | 1.8903 | 2.2838 | 2.3363 | 2.3887 | 1.81 | 2.2516 | 2.7203 | 2.7828 | 2.8453 | 1.6965 | 2.0103 | 2.0103 | 2.0103 | 2.0103 | 2.2063 | 2.6143 | 2.6143 | 2.6143 | 2.6143
1:00 | 1.5047 | 1.8719 | 2.2615 | 2.3135 | 2.3655 | 1.7338 | 2.1568 | 2.6058 | 2.6657 | 2.7255 | 1.6998 | 2.0141 | 2.0141 | 2.0141 | 2.0141 | 2.1949 | 2.6007 | 2.6007 | 2.6007 | 2.6007
2:00 | 1.4982 | 1.8638 | 2.2518 | 2.3035 | 2.3553 | 1.6766 | 2.0857 | 2.5199 | 2.5778 | 2.6357 | 1.6796 | 1.9902 | 1.9902 | 1.9902 | 1.9902 | 2.1682 | 2.5691 | 2.5691 | 2.5691 | 2.5691
3:00 | 1.4858 | 1.8483 | 2.2331 | 2.2844 | 2.3357 | 1.6957 | 2.1094 | 2.5485 | 2.6071 | 2.6656 | 1.8058 | 2.1397 | 2.1397 | 2.1397 | 2.1397 | 2.3854 | 2.8265 | 2.8265 | 2.8265 | 2.8265
4:00 | 1.5134 | 1.8826 | 2.2745 | 2.3268 | 2.3791 | 1.6957 | 2.1094 | 2.5485 | 2.6071 | 2.6656 | 1.969 | 2.3331 | 2.3331 | 2.3331 | 2.3331 | 2.4654 | 2.9213 | 2.9213 | 2.9213 | 2.9213
5:00 | 1.613 | 2.0065 | 2.4243 | 2.48 | 2.5357 | 2.0767 | 2.5834 | 3.1212 | 3.1929 | 3.2646 | 2.2361 | 2.6496 | 2.6496 | 2.6496 | 2.6496 | 2.8884 | 3.4225 | 3.4225 | 3.4225 | 3.4225
6:00 | 1.7295 | 2.1515 | 2.5994 | 2.6591 | 2.7188 | 2.534 | 3.1522 | 3.8085 | 3.896 | 3.9835 | 2.4128 | 2.859 | 2.859 | 2.859 | 2.859 | 3.3456 | 3.9643 | 3.9643 | 3.9643 | 3.9643
7:00 | 1.8131 | 2.2555 | 2.725 | 2.7876 | 2.8502 | 2.7626 | 3.4366 | 4.1521 | 4.2475 | 4.3429 | 2.6656 | 3.1585 | 3.1585 | 3.1585 | 3.1585 | 3.7191 | 4.4068 | 4.4068 | 4.4068 | 4.4068
8:00 | 1.7437 | 2.167 | 2.6182 | 2.6783 | 2.7385 | 3.1627 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 3.037 | 3.5986 | 3.5986 | 3.5986 | 3.5986 | 4.3249 | 5.1247 | 5.1247 | 5.1247 | 5.1247
9:00 | 1.6053 | 1.9913 | 2.4058 | 2.4611 | 2.5164 | 3.1818 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 3.1641 | 3.7492 | 3.7492 | 3.7492 | 3.7492 | 4.5345 | 5.373 | 5.373 | 5.373 | 5.373
10:00 | 1.5344 | 1.9037 | 2.3 | 2.3529 | 2.4057 | 3.1246 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 3.2504 | 3.8515 | 3.8515 | 3.8515 | 3.8515 | 4.7327 | 5.6078 | 5.6078 | 5.6078 | 5.6078
11:00 | 1.5796 | 1.9525 | 2.359 | 2.4132 | 2.4674 | 3.3342 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 3.3541 | 3.9744 | 3.9744 | 3.9744 | 3.9744 | 4.5879 | 5.4362 | 5.4362 | 5.4362 | 5.4362
12:00 | 1.6917 | 2.0931 | 2.5288 | 2.5869 | 2.645 | 3.2199 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 3.4767 | 4.1196 | 4.1196 | 4.1196 | 4.1196 | 5.1366 | 6.0864 | 6.0864 | 6.0864 | 6.0864
13:00 | 1.751 | 2.1556 | 2.6044 | 2.6642 | 2.7241 | 3.3723 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 3.5584 | 4.2164 | 4.2164 | 4.2164 | 4.2164 | 4.9994 | 5.9239 | 5.9239 | 5.9239 | 5.9239
14:00 | 1.7666 | 2.1726 | 2.6249 | 2.6852 | 2.7455 | 3.3914 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 3.5792 | 4.241 | 4.241 | 4.241 | 4.241 | 5.3538 | 6.3438 | 6.3438 | 6.3438 | 6.3438
15:00 | 1.7951 | 2.2219 | 2.6845 | 2.7462 | 2.8079 | 3.258 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 3.5769 | 4.2383 | 4.2383 | 4.2383 | 4.2383 | 5.0032 | 5.9284 | 5.9284 | 5.9284 | 5.9284
16:00 | 1.8058 | 2.2382 | 2.7041 | 2.7662 | 2.8284 | 3.2389 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 3.6008 | 4.2667 | 4.2667 | 4.2667 | 4.2667 | 4.847 | 5.7433 | 5.7433 | 5.7433 | 5.7433
17:00 | 1.8675 | 2.3206 | 2.8037 | 2.8682 | 2.9326 | 3.1056 | 3.6025 | 4.3525 | 4.4525 | 4.5525 | 3.4404 | 4.0765 | 4.0765 | 4.0765 | 4.0765 | 4.5993 | 5.4498 | 5.4498 | 5.4498 | 5.4498
18:00 | 1.928 | 2.3983 | 2.8976 | 2.9642 | 3.0308 | 2.8388 | 3.5314 | 4.2666 | 4.3647 | 4.4627 | 3.102 | 3.6756 | 3.6756 | 3.6756 | 3.6756 | 4.3554 | 5.1608 | 5.1608 | 5.1608 | 5.1608
19:00 | 1.7547 | 2.1828 | 2.6372 | 2.6978 | 2.7584 | 2.3435 | 2.9152 | 3.5221 | 3.603 | 3.684 | 2.7853 | 3.3003 | 3.3003 | 3.3003 | 3.3003 | 3.902 | 4.6235 | 4.6235 | 4.6235 | 4.6235
20:00 | 1.7019 | 2.1172 | 2.5579 | 2.6167 | 2.6754 | 2.0196 | 2.5123 | 3.0353 | 3.1051 | 3.1748 | 2.5356 | 3.0045 | 3.0045 | 3.0045 | 3.0045 | 3.4638 | 4.1043 | 4.1043 | 4.1043 | 4.1043
21:00 | 1.6684 | 2.0754 | 2.5075 | 2.5651 | 2.6227 | 1.9624 | 2.4412 | 2.9494 | 3.0172 | 3.0849 | 2.3069 | 2.7335 | 2.7335 | 2.7335 | 2.7335 | 2.7169 | 3.2193 | 3.2193 | 3.2193 | 3.2193
22:00 | 1.6375 | 2.037 | 2.4611 | 2.5176 | 2.5741 | 1.9624 | 2.4412 | 2.9494 | 3.0172 | 3.0849 | 2.0279 | 2.4029 | 2.4029 | 2.4029 | 2.4029 | 2.5111 | 2.9755 | 2.9755 | 2.9755 | 2.9755
23:00 | 1.5996 | 1.9898 | 2.4041 | 2.4593 | 2.5146 | 1.8862 | 2.3464 | 2.8349 | 2.9 | 2.9651 | 1.8454 | 2.1866 | 2.1866 | 2.1866 | 2.1866 | 2.3663 | 2.8039 | 2.8039 | 2.8039 | 2.8039

## Feeder Loading
Feeder | Summer |  | Winter |  | 2026 |  | 2027 |  | 2028 |  | 2029
| Firm | Thermal | Firm | Thermal | Summer | Winter | Summer | Winter | Summer | Winter | Summer | Winter
Dairy North | 2.6 | 3.5 | 2.6 | 3.5 | 3.6 | 3.1 | 4.4 | 3.9 | 4.5 | 4.1 | 4.6 | 4.3
Aero Park | 5 | 6.7 | 5.6 | 7.5 | 6.3 | 7 | 6.3 | 7 | 6.3 | 7 | 6.3 | 7
Above Firm
Above Thermal
Units: MVA/MW

## Methodology
Tab | Description
Annual Load | Hourly historical demand of relevant feeders and their hourly forecasts. These forecasts preserve relative percentage of seasonal peak demand in any given hour across a year, and scale the peak demand itself based on addition of point loads as described in the business case
Daily Load | Average Summer / Winter Day load: Calculated by averaging the demand at the same hour throughtout the year. Peak Summer / Winter Day load: The daily load profile on the day when the peak summer/winter demand occurs.
Feeder Loadings | Forecast peak seasonal loadings of relevant feeders in winter and summer.