## Annual Load
|  | Peak Demand | 4.6107 | 2020-02-10 12:00 |  | Summer |  | Peak Demand | 3.2866 | 2020-02-10 12:00 |  | Summer |  | Peak Demand | 4.9918 | 2020-01-31 12:00 |  | Summer |  | Peak Demand | 1.9014 | 2020-10-13 12:00 |  | Summer |  | Peak Demand | 4.9537 | 2020-02-18 13:00 |  | Summer
|  | Hobart Short | [5 empty] | Electricity House | [5 empty] | Edinburgh | [5 empty] | Edmund Barton | [5 empty] | Hobart Long
Timestamp | Season | Historical Load (MVA/MW) | Forecast Load (MVA/MW) |  |  |  |  | Historical Load (MVA/MW) | Forecast Load (MVA/MW) |  |  |  |  | Historical Load (MVA/MW) | Forecast Load (MVA/MW) |  |  |  |  | Historical Load (MVA/MW) | Forecast Load (MVA/MW) |  |  |  |  | Historical Load (MVA/MW) | Forecast Load (MVA/MW)
|  | 2020 | 2025 | 2026 | 2027 | 2028 | 2029 | 2020 | 2025 | 2026 | 2027 | 2028 | 2029 | 2020 | 2025 | 2026 | 2027 | 2028 | 2029 | 2020 | 2025 | 2026 | 2027 | 2028 | 2029 | 2020 | 2025 | 2026 | 2027 | 2028 | 2029
2020-01-08 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.46583 | 0.9213 | 0.9213 | 0.9213 | 0.9213 | 0.9213 | 2.0474 | 2.6422 | 3.0318 | 3.2369 | 3.6471 | 4.0572 | 0.73543 | 1.4515 | 1.7418 | 1.7418 | 1.7418 | 1.7418 | 0.97168 | 1.1303 | 1.1303 | 1.1303 | 1.1303 | 1.1303
2020-01-08 01:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.50584 | 1.0004 | 1.0004 | 1.0004 | 1.0004 | 1.0004 | 1.9624 | 2.5325 | 2.9059 | 3.1025 | 3.4956 | 3.8887 | 0.70875 | 1.3989 | 1.6786 | 1.6786 | 1.6786 | 1.6786 | 1.0669 | 1.2411 | 1.2411 | 1.2411 | 1.2411 | 1.2411
2020-01-08 02:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.49727 | 0.98347 | 0.98347 | 0.98347 | 0.98347 | 0.98347 | 1.9434 | 2.5079 | 2.8777 | 3.0724 | 3.4617 | 3.851 | 0.73162 | 1.444 | 1.7328 | 1.7328 | 1.7328 | 1.7328 | 1.0098 | 1.1746 | 1.1746 | 1.1746 | 1.1746 | 1.1746
2020-01-08 03:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.4544 | 0.89869 | 0.89869 | 0.89869 | 0.89869 | 0.89869 | 1.9243 | 2.4833 | 2.8495 | 3.0422 | 3.4277 | 3.8132 | 0.71256 | 1.4064 | 1.6877 | 1.6877 | 1.6877 | 1.6877 | 1.0098 | 1.1746 | 1.1746 | 1.1746 | 1.1746 | 1.1746
2020-01-08 04:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.46869 | 0.92695 | 0.92695 | 0.92695 | 0.92695 | 0.92695 | 1.9624 | 2.5325 | 2.9059 | 3.1025 | 3.4956 | 3.8887 | 0.69351 | 1.3688 | 1.6425 | 1.6425 | 1.6425 | 1.6425 | 1.2381 | 1.4402 | 1.4402 | 1.4402 | 1.4402 | 1.4402
2020-01-08 05:00 | Summer | 0.59038 | 0.84492 | 1.2193 | 1.2193 | 1.2193 | 1.2193 | 0.55518 | 1.098 | 1.098 | 1.098 | 1.098 | 1.098 | 2.0005 | 2.5816 | 2.9624 | 3.1627 | 3.5635 | 3.9643 | 0.97549 | 1.9253 | 2.3104 | 2.3104 | 2.3104 | 2.3104 | 1.304 | 1.5169 | 1.5169 | 1.5169 | 1.5169 | 1.5169
2020-01-08 06:00 | Summer | 0.68552 | 0.98109 | 1.4157 | 1.4157 | 1.4157 | 1.4157 | 0.81781 | 1.6174 | 1.6174 | 1.6174 | 1.6174 | 1.6174 | 2.2915 | 2.9571 | 3.3932 | 3.6227 | 4.0818 | 4.5408 | 1.0441 | 2.0607 | 2.4728 | 2.4728 | 2.4728 | 2.4728 | 1.6576 | 1.9282 | 1.9282 | 1.9282 | 1.9282 | 1.9282
2020-01-08 07:00 | Summer | 2.0341 | 2.9111 | 4.2008 | 4.2008 | 4.2008 | 4.2008 | 1.0517 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.896 | 3.7372 | 4.2884 | 4.5784 | 5.1586 | 5.7387 | 1.3832 | 2.73 | 3.276 | 3.276 | 3.276 | 3.276 | 2.191 | 2.5488 | 2.5488 | 2.5488 | 2.5488 | 2.5488
2020-01-08 08:00 | Summer | 2.172 | 3.1085 | 4.4856 | 4.4856 | 4.4856 | 4.4856 | 1.0717 | 2.1196 | 2.1196 | 2.1196 | 2.1196 | 2.1196 | 3.2199 | 4.1552 | 4.768 | 5.0905 | 5.7355 | 6.3806 | 1.4442 | 2.8504 | 3.4204 | 3.4204 | 3.4204 | 3.4204 | 2.5149 | 2.9255 | 2.9255 | 2.9255 | 2.9255 | 2.9255
2020-01-08 09:00 | Summer | 1.9624 | 2.8085 | 4.0528 | 4.0528 | 4.0528 | 4.0528 | 1.3289 | 2.6283 | 2.6283 | 2.6283 | 2.6283 | 2.6283 | 3.3747 | 4.3549 | 4.9972 | 5.3352 | 6.0112 | 6.6873 | 1.3451 | 2.6548 | 3.1858 | 3.1858 | 3.1858 | 3.1858 | 2.7244 | 3.1691 | 3.1691 | 3.1691 | 3.1691 | 3.1691
2020-01-08 10:00 | Summer | 2.1339 | 3.0539 | 4.4069 | 4.4069 | 4.4069 | 4.4069 | 1.4689 | 2.9052 | 2.9052 | 2.9052 | 2.9052 | 2.9052 | 3.5819 | 4.6223 | 5.304 | 5.6628 | 6.3804 | 7.0979 | 1.3222 | 2.6097 | 3.1316 | 3.1316 | 3.1316 | 3.1316 | 2.9913 | 3.4796 | 3.4796 | 3.4796 | 3.4796 | 3.4796
2020-01-08 11:00 | Summer | 2.2482 | 3.2175 | 4.643 | 4.643 | 4.643 | 4.643 | 1.4575 | 2.8826 | 2.8826 | 2.8826 | 2.8826 | 2.8826 | 3.7915 | 4.8928 | 5.6144 | 5.9941 | 6.7537 | 7.5132 | 1.3413 | 2.6473 | 3.1768 | 3.1768 | 3.1768 | 3.1768 | 3.1056 | 3.6126 | 3.6126 | 3.6126 | 3.6126 | 3.6126
2020-01-08 12:00 | Summer | 2.3054 | 3.2993 | 4.7611 | 4.7611 | 4.7611 | 4.7611 | 1.689 | 3.3404 | 3.3404 | 3.3404 | 3.3404 | 3.3404 | 3.8867 | 5.0157 | 5.7554 | 6.1447 | 6.9234 | 7.702 | 1.368 | 2.6999 | 3.2399 | 3.2399 | 3.2399 | 3.2399 | 3.1627 | 3.6791 | 3.6791 | 3.6791 | 3.6791 | 3.6791
2020-01-08 13:00 | Summer | 2.4197 | 3.4629 | 4.9972 | 4.9972 | 4.9972 | 4.9972 | 1.7576 | 3.4761 | 3.4761 | 3.4761 | 3.4761 | 3.4761 | 4.001 | 5.1633 | 5.9247 | 6.3255 | 7.127 | 7.9285 | 1.4023 | 2.7676 | 3.3212 | 3.3212 | 3.3212 | 3.3212 | 3.2389 | 3.7677 | 3.7677 | 3.7677 | 3.7677 | 3.7677
2020-01-08 14:00 | Summer | 2.4116 | 3.4514 | 4.9805 | 4.9805 | 4.9805 | 4.9805 | 1.7605 | 3.4817 | 3.4817 | 3.4817 | 3.4817 | 3.4817 | 4.1535 | 5.3599 | 6.1504 | 6.5664 | 7.3985 | 8.2306 | 1.3985 | 2.7601 | 3.3121 | 3.3121 | 3.3121 | 3.3121 | 3.2206 | 3.7464 | 3.7464 | 3.7464 | 3.7464 | 3.7464
2020-01-08 15:00 | Summer | 2.2291 | 3.1903 | 4.6037 | 4.6037 | 4.6037 | 4.6037 | 1.6261 | 3.2161 | 3.2161 | 3.2161 | 3.2161 | 3.2161 | 4.1344 | 5.3354 | 6.1222 | 6.5363 | 7.3646 | 8.1928 | 1.4175 | 2.7977 | 3.3573 | 3.3573 | 3.3573 | 3.3573 | 3.277 | 3.8121 | 3.8121 | 3.8121 | 3.8121 | 3.8121
2020-01-08 16:00 | Summer | 2.2101 | 3.163 | 4.5643 | 4.5643 | 4.5643 | 4.5643 | 1.7376 | 3.4365 | 3.4365 | 3.4365 | 3.4365 | 3.4365 | 4.2487 | 5.4829 | 6.2915 | 6.717 | 7.5682 | 8.4193 | 1.4137 | 2.7902 | 3.3482 | 3.3482 | 3.3482 | 3.3482 | 3.2008 | 3.7234 | 3.7234 | 3.7234 | 3.7234 | 3.7234
2020-01-08 17:00 | Summer | 1.9995 | 2.8616 | 4.1293 | 4.1293 | 4.1293 | 4.1293 | 1.569 | 3.103 | 3.103 | 3.103 | 3.103 | 3.103 | 3.7915 | 4.8928 | 5.6144 | 5.9941 | 6.7537 | 7.5132 | 1.3794 | 2.7225 | 3.267 | 3.267 | 3.267 | 3.267 | 2.7626 | 3.2137 | 3.2137 | 3.2137 | 3.2137 | 3.2137
2020-01-08 18:00 | Summer | 1.4756 | 2.1119 | 3.0475 | 3.0475 | 3.0475 | 3.0475 | 1.1603 | 2.2948 | 2.2948 | 2.2948 | 2.2948 | 2.2948 | 3.5754 | 4.6139 | 5.2944 | 5.6525 | 6.3687 | 7.085 | 1.0593 | 2.0908 | 2.5089 | 2.5089 | 2.5089 | 2.5089 | 2.0397 | 2.3727 | 2.3727 | 2.3727 | 2.3727 | 2.3727
2020-01-08 19:00 | Summer | 0.74305 | 1.0634 | 1.5346 | 1.5346 | 1.5346 | 1.5346 | 0.644 | 1.2737 | 1.2737 | 1.2737 | 1.2737 | 1.2737 | 2.9205 | 3.7689 | 4.3247 | 4.6172 | 5.2023 | 5.7873 | 1.0212 | 2.0156 | 2.4187 | 2.4187 | 2.4187 | 2.4187 | 1.2956 | 1.5071 | 1.5071 | 1.5071 | 1.5071 | 1.5071
2020-01-08 20:00 | Summer | 0.724 | 1.0362 | 1.4952 | 1.4952 | 1.4952 | 1.4952 | 0.57729 | 1.1417 | 1.1417 | 1.1417 | 1.1417 | 1.1417 | 2.6293 | 3.393 | 3.8934 | 4.1567 | 4.6835 | 5.2102 | 1.0326 | 2.0381 | 2.4457 | 2.4457 | 2.4457 | 2.4457 | 1.2194 | 1.4184 | 1.4184 | 1.4184 | 1.4184 | 1.4184
2020-01-08 21:00 | Summer | 0.62026 | 0.88769 | 1.281 | 1.281 | 1.281 | 1.281 | 0.49727 | 0.98347 | 0.98347 | 0.98347 | 0.98347 | 0.98347 | 2.4383 | 3.1465 | 3.6106 | 3.8548 | 4.3433 | 4.8317 | 1.0365 | 2.0456 | 2.4548 | 2.4548 | 2.4548 | 2.4548 | 1.1241 | 1.3076 | 1.3076 | 1.3076 | 1.3076 | 1.3076
2020-01-08 22:00 | Summer | 0.59054 | 0.84516 | 1.2196 | 1.2196 | 1.2196 | 1.2196 | 0.50584 | 1.0004 | 1.0004 | 1.0004 | 1.0004 | 1.0004 | 2.3054 | 2.975 | 3.4138 | 3.6447 | 4.1065 | 4.5683 | 0.98692 | 1.9479 | 2.3374 | 2.3374 | 2.3374 | 2.3374 | 0.99073 | 1.1525 | 1.1525 | 1.1525 | 1.1525 | 1.1525
2020-01-08 23:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.46012 | 0.90999 | 0.90999 | 0.90999 | 0.90999 | 0.90999 | 2.2101 | 2.8521 | 3.2727 | 3.4941 | 3.9368 | 4.3796 | 0.91071 | 1.7975 | 2.1569 | 2.1569 | 2.1569 | 2.1569 | 0.99073 | 1.1525 | 1.1525 | 1.1525 | 1.1525 | 1.1525
2020-01-09 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.41439 | 0.81956 | 0.81956 | 0.81956 | 0.81956 | 0.81956 | 1.9815 | 2.557 | 2.9341 | 3.1326 | 3.5296 | 3.9265 | 0.68589 | 1.3537 | 1.6245 | 1.6245 | 1.6245 | 1.6245 | 0.97168 | 1.1303 | 1.1303 | 1.1303 | 1.1303 | 1.1303
2020-01-09 01:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.45154 | 0.89304 | 0.89304 | 0.89304 | 0.89304 | 0.89304 | 1.9053 | 2.4587 | 2.8213 | 3.0121 | 3.3938 | 3.7755 | 0.67827 | 1.3387 | 1.6064 | 1.6064 | 1.6064 | 1.6064 | 0.97168 | 1.1303 | 1.1303 | 1.1303 | 1.1303 | 1.1303
2020-01-09 02:00 | Summer | 0.55198 | 0.78997 | 1.14 | 1.14 | 1.14 | 1.14 | 0.44011 | 0.87043 | 0.87043 | 0.87043 | 0.87043 | 0.87043 | 1.8862 | 2.4341 | 2.7931 | 2.982 | 3.3599 | 3.7377 | 0.65204 | 1.2869 | 1.5443 | 1.5443 | 1.5443 | 1.5443 | 0.93358 | 1.086 | 1.086 | 1.086 | 1.086 | 1.086
2020-01-09 03:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.583 | 1.153 | 1.153 | 1.153 | 1.153 | 1.153 | 1.8481 | 2.3849 | 2.7366 | 2.9218 | 3.292 | 3.6622 | 0.65541 | 1.2936 | 1.5523 | 1.5523 | 1.5523 | 1.5523 | 0.91452 | 1.0638 | 1.0638 | 1.0638 | 1.0638 | 1.0638
2020-01-09 04:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.49101 | 0.97109 | 0.97109 | 0.97109 | 0.97109 | 0.97109 | 1.9281 | 2.4882 | 2.8551 | 3.0483 | 3.4345 | 3.8208 | 0.74686 | 1.4741 | 1.7689 | 1.7689 | 1.7689 | 1.7689 | 1.105 | 1.2855 | 1.2855 | 1.2855 | 1.2855 | 1.2855
2020-01-09 05:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.49727 | 0.98347 | 0.98347 | 0.98347 | 0.98347 | 0.98347 | 1.9815 | 2.557 | 2.9341 | 3.1326 | 3.5296 | 3.9265 | 0.88023 | 1.7373 | 2.0847 | 2.0847 | 2.0847 | 2.0847 | 1.3146 | 1.5293 | 1.5293 | 1.5293 | 1.5293 | 1.5293
2020-01-09 06:00 | Summer | 0.91367 | 1.3076 | 1.8869 | 1.8869 | 1.8869 | 1.8869 | 0.88308 | 1.7465 | 1.7465 | 1.7465 | 1.7465 | 1.7465 | 2.1344 | 2.7544 | 3.1606 | 3.3744 | 3.802 | 4.2296 | 1.0403 | 2.0532 | 2.4638 | 2.4638 | 2.4638 | 2.4638 | 1.5074 | 1.7535 | 1.7535 | 1.7535 | 1.7535 | 1.7535
2020-01-09 07:00 | Summer | 1.829 | 2.6177 | 3.7774 | 3.7774 | 3.7774 | 3.7774 | 0.97453 | 1.9274 | 1.9274 | 1.9274 | 1.9274 | 1.9274 | 2.8579 | 3.688 | 4.2319 | 4.5182 | 5.0907 | 5.6632 | 1.2041 | 2.3766 | 2.8519 | 2.8519 | 2.8519 | 2.8519 | 2.0005 | 2.3271 | 2.3271 | 2.3271 | 2.3271 | 2.3271
2020-01-09 08:00 | Summer | 1.8672 | 2.6722 | 3.8561 | 3.8561 | 3.8561 | 3.8561 | 1.1031 | 2.1817 | 2.1817 | 2.1817 | 2.1817 | 2.1817 | 3.1142 | 4.0188 | 4.6115 | 4.9234 | 5.5473 | 6.1712 | 1.166 | 2.3013 | 2.7616 | 2.7616 | 2.7616 | 2.7616 | 2.4006 | 2.7926 | 2.7926 | 2.7926 | 2.7926 | 2.7926
2020-01-09 09:00 | Summer | 1.7909 | 2.5631 | 3.6987 | 3.6987 | 3.6987 | 3.6987 | 1.3403 | 2.6509 | 2.6509 | 2.6509 | 2.6509 | 2.6509 | 3.1246 | 4.0323 | 4.6269 | 4.9399 | 5.5658 | 6.1918 | 1.1584 | 2.2863 | 2.7436 | 2.7436 | 2.7436 | 2.7436 | 2.4768 | 2.8812 | 2.8812 | 2.8812 | 2.8812 | 2.8812
2020-01-09 10:00 | Summer | 1.7909 | 2.5631 | 3.6987 | 3.6987 | 3.6987 | 3.6987 | 1.2918 | 2.5548 | 2.5548 | 2.5548 | 2.5548 | 2.5548 | 3.1246 | 4.0323 | 4.6269 | 4.9399 | 5.5658 | 6.1918 | 1.1393 | 2.2487 | 2.6984 | 2.6984 | 2.6984 | 2.6984 | 2.5911 | 3.0142 | 3.0142 | 3.0142 | 3.0142 | 3.0142
2020-01-09 11:00 | Summer | 1.7719 | 2.5359 | 3.6593 | 3.6593 | 3.6593 | 3.6593 | 1.1917 | 2.357 | 2.357 | 2.357 | 2.357 | 2.357 | 3.3151 | 4.2781 | 4.909 | 5.2411 | 5.9052 | 6.5693 | 1.1089 | 2.1885 | 2.6262 | 2.6262 | 2.6262 | 2.6262 | 2.6674 | 3.1028 | 3.1028 | 3.1028 | 3.1028 | 3.1028
2020-01-09 12:00 | Summer | 1.7909 | 2.5631 | 3.6987 | 3.6987 | 3.6987 | 3.6987 | 1.3232 | 2.617 | 2.617 | 2.617 | 2.617 | 2.617 | 3.2961 | 4.2535 | 4.8808 | 5.211 | 5.8713 | 6.5316 | 1.1127 | 2.1961 | 2.6353 | 2.6353 | 2.6353 | 2.6353 | 2.7055 | 3.1472 | 3.1472 | 3.1472 | 3.1472 | 3.1472
2020-01-09 13:00 | Summer | 1.81 | 2.5904 | 3.738 | 3.738 | 3.738 | 3.738 | 1.3918 | 2.7526 | 2.7526 | 2.7526 | 2.7526 | 2.7526 | 3.258 | 4.2044 | 4.8244 | 5.1507 | 5.8034 | 6.4561 | 1.0974 | 2.166 | 2.5992 | 2.5992 | 2.5992 | 2.5992 | 2.7626 | 3.2137 | 3.2137 | 3.2137 | 3.2137 | 3.2137
2020-01-09 14:00 | Summer | 1.829 | 2.6177 | 3.7774 | 3.7774 | 3.7774 | 3.7774 | 1.2775 | 2.5265 | 2.5265 | 2.5265 | 2.5265 | 2.5265 | 3.3533 | 4.3273 | 4.9655 | 5.3013 | 5.9731 | 6.6449 | 1.1279 | 2.2261 | 2.6714 | 2.6714 | 2.6714 | 2.6714 | 2.8198 | 3.2802 | 3.2802 | 3.2802 | 3.2802 | 3.2802
2020-01-09 15:00 | Summer | 1.8481 | 2.6449 | 3.8167 | 3.8167 | 3.8167 | 3.8167 | 1.3203 | 2.6113 | 2.6113 | 2.6113 | 2.6113 | 2.6113 | 3.3723 | 4.3519 | 4.9937 | 5.3315 | 6.007 | 6.6826 | 1.1241 | 2.2186 | 2.6623 | 2.6623 | 2.6623 | 2.6623 | 2.6864 | 3.125 | 3.125 | 3.125 | 3.125 | 3.125
2020-01-09 16:00 | Summer | 1.829 | 2.6177 | 3.7774 | 3.7774 | 3.7774 | 3.7774 | 1.4175 | 2.8035 | 2.8035 | 2.8035 | 2.8035 | 2.8035 | 3.3533 | 4.3273 | 4.9655 | 5.3013 | 5.9731 | 6.6449 | 1.1317 | 2.2337 | 2.6804 | 2.6804 | 2.6804 | 2.6804 | 2.6674 | 3.1028 | 3.1028 | 3.1028 | 3.1028 | 3.1028
2020-01-09 17:00 | Summer | 1.6269 | 2.3284 | 3.3599 | 3.3599 | 3.3599 | 3.3599 | 1.2832 | 2.5378 | 2.5378 | 2.5378 | 2.5378 | 2.5378 | 3.2389 | 4.1798 | 4.7962 | 5.1206 | 5.7695 | 6.4183 | 1.0793 | 2.1301 | 2.5562 | 2.5562 | 2.5562 | 2.5562 | 2.3625 | 2.7482 | 2.7482 | 2.7482 | 2.7482 | 2.7482
2020-01-09 18:00 | Summer | 1.1102 | 1.5888 | 2.2927 | 2.2927 | 2.2927 | 2.2927 | 1.012 | 2.0015 | 2.0015 | 2.0015 | 2.0015 | 2.0015 | 2.9722 | 3.8356 | 4.4012 | 4.6989 | 5.2943 | 5.8898 | 1.0479 | 2.0682 | 2.4818 | 2.4818 | 2.4818 | 2.4818 | 1.865 | 2.1695 | 2.1695 | 2.1695 | 2.1695 | 2.1695
2020-01-09 19:00 | Summer | 0.89547 | 1.2816 | 1.8493 | 1.8493 | 1.8493 | 1.8493 | 0.78306 | 1.5487 | 1.5487 | 1.5487 | 1.5487 | 1.5487 | 2.661 | 3.434 | 3.9404 | 4.207 | 4.7401 | 5.2731 | 1.0669 | 2.1058 | 2.527 | 2.527 | 2.527 | 2.527 | 1.2956 | 1.5071 | 1.5071 | 1.5071 | 1.5071 | 1.5071
2020-01-09 20:00 | Summer | 0.81926 | 1.1725 | 1.692 | 1.692 | 1.692 | 1.692 | 0.6716 | 1.3283 | 1.3283 | 1.3283 | 1.3283 | 1.3283 | 2.4006 | 3.098 | 3.5548 | 3.7953 | 4.2762 | 4.7571 | 1.1127 | 2.1961 | 2.6353 | 2.6353 | 2.6353 | 2.6353 | 1.1241 | 1.3076 | 1.3076 | 1.3076 | 1.3076 | 1.3076
2020-01-09 21:00 | Summer | 0.71718 | 1.0264 | 1.4811 | 1.4811 | 1.4811 | 1.4811 | 0.583 | 1.153 | 1.153 | 1.153 | 1.153 | 1.153 | 2.3816 | 3.0734 | 3.5266 | 3.7652 | 4.2423 | 4.7194 | 1.0403 | 2.0532 | 2.4638 | 2.4638 | 2.4638 | 2.4638 | 1.086 | 1.2633 | 1.2633 | 1.2633 | 1.2633 | 1.2633
2020-01-09 22:00 | Summer | 0.60958 | 0.87241 | 1.2589 | 1.2589 | 1.2589 | 1.2589 | 0.46297 | 0.91565 | 0.91565 | 0.91565 | 0.91565 | 0.91565 | 2.3054 | 2.975 | 3.4138 | 3.6447 | 4.1065 | 4.5683 | 0.99073 | 1.9554 | 2.3465 | 2.3465 | 2.3465 | 2.3465 | 0.99073 | 1.1525 | 1.1525 | 1.1525 | 1.1525 | 1.1525
2020-01-09 23:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.46012 | 0.90999 | 0.90999 | 0.90999 | 0.90999 | 0.90999 | 2.1148 | 2.7291 | 3.1316 | 3.3435 | 3.7671 | 4.1908 | 0.95644 | 1.8877 | 2.2652 | 2.2652 | 2.2652 | 2.2652 | 0.99073 | 1.1525 | 1.1525 | 1.1525 | 1.1525 | 1.1525
2020-01-10 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.42296 | 0.83652 | 0.83652 | 0.83652 | 0.83652 | 0.83652 | 1.9053 | 2.4587 | 2.8213 | 3.0121 | 3.3938 | 3.7755 | 0.70494 | 1.3913 | 1.6696 | 1.6696 | 1.6696 | 1.6696 | 0.99073 | 1.1525 | 1.1525 | 1.1525 | 1.1525 | 1.1525
2020-01-10 01:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.44297 | 0.87608 | 0.87608 | 0.87608 | 0.87608 | 0.87608 | 1.9243 | 2.4833 | 2.8495 | 3.0422 | 3.4277 | 3.8132 | 0.67446 | 1.3312 | 1.5974 | 1.5974 | 1.5974 | 1.5974 | 0.95263 | 1.1082 | 1.1082 | 1.1082 | 1.1082 | 1.1082
2020-01-10 02:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.46012 | 0.90999 | 0.90999 | 0.90999 | 0.90999 | 0.90999 | 1.8852 | 2.4328 | 2.7915 | 2.9804 | 3.358 | 3.7357 | 0.64779 | 1.2785 | 1.5342 | 1.5342 | 1.5342 | 1.5342 | 0.97168 | 1.1303 | 1.1303 | 1.1303 | 1.1303 | 1.1303
2020-01-10 03:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.45154 | 0.89304 | 0.89304 | 0.89304 | 0.89304 | 0.89304 | 1.8481 | 2.3849 | 2.7366 | 2.9218 | 3.292 | 3.6622 | 0.64779 | 1.2785 | 1.5342 | 1.5342 | 1.5342 | 1.5342 | 0.97168 | 1.1303 | 1.1303 | 1.1303 | 1.1303 | 1.1303
2020-01-10 04:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.48869 | 0.96652 | 0.96652 | 0.96652 | 0.96652 | 0.96652 | 1.8672 | 2.4095 | 2.7649 | 2.9519 | 3.3259 | 3.7 | 0.67827 | 1.3387 | 1.6064 | 1.6064 | 1.6064 | 1.6064 | 1.1432 | 1.3298 | 1.3298 | 1.3298 | 1.3298 | 1.3298
2020-01-10 05:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.51442 | 1.0174 | 1.0174 | 1.0174 | 1.0174 | 1.0174 | 1.9624 | 2.5325 | 2.9059 | 3.1025 | 3.4956 | 3.8887 | 0.86498 | 1.7072 | 2.0486 | 2.0486 | 2.0486 | 2.0486 | 1.2502 | 1.4544 | 1.4544 | 1.4544 | 1.4544 | 1.4544
2020-01-10 06:00 | Summer | 0.91452 | 1.3088 | 1.8887 | 1.8887 | 1.8887 | 1.8887 | 0.803 | 1.5881 | 1.5881 | 1.5881 | 1.5881 | 1.5881 | 2.1942 | 2.8316 | 3.2492 | 3.4689 | 3.9085 | 4.3481 | 1.0136 | 2.0005 | 2.4006 | 2.4006 | 2.4006 | 2.4006 | 1.4933 | 1.7371 | 1.7371 | 1.7371 | 1.7371 | 1.7371
2020-01-10 07:00 | Summer | 1.7909 | 2.5631 | 3.6987 | 3.6987 | 3.6987 | 3.6987 | 1.0003 | 1.9783 | 1.9783 | 1.9783 | 1.9783 | 1.9783 | 2.9813 | 3.8473 | 4.4147 | 4.7134 | 5.3106 | 5.9079 | 1.3413 | 2.6473 | 3.1768 | 3.1768 | 3.1768 | 3.1768 | 2.0767 | 2.4158 | 2.4158 | 2.4158 | 2.4158 | 2.4158
2020-01-10 08:00 | Summer | 1.9434 | 2.7813 | 4.0135 | 4.0135 | 4.0135 | 4.0135 | 1.1289 | 2.2326 | 2.2326 | 2.2326 | 2.2326 | 2.2326 | 3.2389 | 4.1798 | 4.7962 | 5.1206 | 5.7695 | 6.4183 | 1.3946 | 2.7526 | 3.3031 | 3.3031 | 3.3031 | 3.3031 | 2.4959 | 2.9034 | 2.9034 | 2.9034 | 2.9034 | 2.9034
2020-01-10 09:00 | Summer | 2.0767 | 2.9721 | 4.2889 | 4.2889 | 4.2889 | 4.2889 | 1.3661 | 2.7017 | 2.7017 | 2.7017 | 2.7017 | 2.7017 | 3.3723 | 4.3519 | 4.9937 | 5.3315 | 6.007 | 6.6826 | 1.2994 | 2.5646 | 3.0775 | 3.0775 | 3.0775 | 3.0775 | 2.7245 | 3.1693 | 3.1693 | 3.1693 | 3.1693 | 3.1693
2020-01-10 10:00 | Summer | 2.0958 | 2.9994 | 4.3282 | 4.3282 | 4.3282 | 4.3282 | 1.5918 | 3.1483 | 3.1483 | 3.1483 | 3.1483 | 3.1483 | 3.62 | 4.6715 | 5.3604 | 5.723 | 6.4482 | 7.1734 | 1.3375 | 2.6398 | 3.1677 | 3.1677 | 3.1677 | 3.1677 | 3.0484 | 3.5461 | 3.5461 | 3.5461 | 3.5461 | 3.5461
2020-01-10 11:00 | Summer | 2.0958 | 2.9994 | 4.3282 | 4.3282 | 4.3282 | 4.3282 | 1.489 | 2.9448 | 2.9448 | 2.9448 | 2.9448 | 2.9448 | 3.8198 | 4.9293 | 5.6563 | 6.0389 | 6.8041 | 7.5693 | 1.3642 | 2.6924 | 3.2309 | 3.2309 | 3.2309 | 3.2309 | 3.0649 | 3.5653 | 3.5653 | 3.5653 | 3.5653 | 3.5653
2020-01-10 12:00 | Summer | 2.1148 | 3.0267 | 4.3676 | 4.3676 | 4.3676 | 4.3676 | 1.6204 | 3.2048 | 3.2048 | 3.2048 | 3.2048 | 3.2048 | 3.9439 | 5.0895 | 5.8401 | 6.2351 | 7.0252 | 7.8153 | 1.4328 | 2.8278 | 3.3934 | 3.3934 | 3.3934 | 3.3934 | 3.2008 | 3.7234 | 3.7234 | 3.7234 | 3.7234 | 3.7234
2020-01-10 13:00 | Summer | 2.0958 | 2.9994 | 4.3282 | 4.3282 | 4.3282 | 4.3282 | 1.8062 | 3.5722 | 3.5722 | 3.5722 | 3.5722 | 3.5722 | 4.0582 | 5.237 | 6.0093 | 6.4158 | 7.2288 | 8.0418 | 1.4251 | 2.8128 | 3.3753 | 3.3753 | 3.3753 | 3.3753 | 3.258 | 3.7899 | 3.7899 | 3.7899 | 3.7899 | 3.7899
2020-01-10 14:00 | Summer | 2.1339 | 3.0539 | 4.4069 | 4.4069 | 4.4069 | 4.4069 | 1.7017 | 3.3656 | 3.3656 | 3.3656 | 3.3656 | 3.3656 | 4.1344 | 5.3354 | 6.1222 | 6.5363 | 7.3646 | 8.1928 | 1.4137 | 2.7902 | 3.3482 | 3.3482 | 3.3482 | 3.3482 | 3.2961 | 3.8342 | 3.8342 | 3.8342 | 3.8342 | 3.8342
2020-01-10 15:00 | Summer | 2.1148 | 3.0267 | 4.3676 | 4.3676 | 4.3676 | 4.3676 | 1.9805 | 3.917 | 3.917 | 3.917 | 3.917 | 3.917 | 4.3821 | 5.655 | 6.489 | 6.9279 | 7.8058 | 8.6836 | 1.4137 | 2.7902 | 3.3482 | 3.3482 | 3.3482 | 3.3482 | 3.4104 | 3.9672 | 3.9672 | 3.9672 | 3.9672 | 3.9672
2020-01-10 16:00 | Summer | 2.1148 | 3.0267 | 4.3676 | 4.3676 | 4.3676 | 4.3676 | 2.0091 | 3.9735 | 3.9735 | 3.9735 | 3.9735 | 3.9735 | 4.4202 | 5.7042 | 6.5454 | 6.9881 | 7.8736 | 8.7591 | 1.4518 | 2.8654 | 3.4385 | 3.4385 | 3.4385 | 3.4385 | 3.4485 | 4.0115 | 4.0115 | 4.0115 | 4.0115 | 4.0115
2020-01-10 17:00 | Summer | 1.9815 | 2.8358 | 4.0922 | 4.0922 | 4.0922 | 4.0922 | 1.9548 | 3.8661 | 3.8661 | 3.8661 | 3.8661 | 3.8661 | 4.3249 | 5.5812 | 6.4043 | 6.8375 | 7.7039 | 8.5704 | 1.2841 | 2.5345 | 3.0414 | 3.0414 | 3.0414 | 3.0414 | 3.1037 | 3.6104 | 3.6104 | 3.6104 | 3.6104 | 3.6104
2020-01-10 18:00 | Summer | 1.5967 | 2.2852 | 3.2976 | 3.2976 | 3.2976 | 3.2976 | 1.3937 | 2.7565 | 2.7565 | 2.7565 | 2.7565 | 2.7565 | 3.9558 | 5.1049 | 5.8577 | 6.254 | 7.0464 | 7.8389 | 1.1089 | 2.1885 | 2.6262 | 2.6262 | 2.6262 | 2.6262 | 2.2321 | 2.5965 | 2.5965 | 2.5965 | 2.5965 | 2.5965
2020-01-10 19:00 | Summer | 0.85737 | 1.227 | 1.7706 | 1.7706 | 1.7706 | 1.7706 | 0.92881 | 1.837 | 1.837 | 1.837 | 1.837 | 1.837 | 3.6513 | 4.712 | 5.4069 | 5.7726 | 6.5041 | 7.2356 | 1.1127 | 2.1961 | 2.6353 | 2.6353 | 2.6353 | 2.6353 | 1.4099 | 1.6401 | 1.6401 | 1.6401 | 1.6401 | 1.6401
2020-01-10 20:00 | Summer | 0.81926 | 1.1725 | 1.692 | 1.692 | 1.692 | 1.692 | 0.82021 | 1.6222 | 1.6222 | 1.6222 | 1.6222 | 1.6222 | 3.0486 | 3.9341 | 4.5143 | 4.8197 | 5.4304 | 6.0411 | 1.0708 | 2.1133 | 2.536 | 2.536 | 2.536 | 2.536 | 1.3527 | 1.5736 | 1.5736 | 1.5736 | 1.5736 | 1.5736
2020-01-10 21:00 | Summer | 0.68589 | 0.98162 | 1.4165 | 1.4165 | 1.4165 | 1.4165 | 0.68017 | 1.3452 | 1.3452 | 1.3452 | 1.3452 | 1.3452 | 2.9722 | 3.8356 | 4.4012 | 4.6989 | 5.2943 | 5.8898 | 1.0479 | 2.0682 | 2.4818 | 2.4818 | 2.4818 | 2.4818 | 1.2578 | 1.4632 | 1.4632 | 1.4632 | 1.4632 | 1.4632
2020-01-10 22:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.69446 | 1.3735 | 1.3735 | 1.3735 | 1.3735 | 1.3735 | 2.915 | 3.7618 | 4.3166 | 4.6086 | 5.1925 | 5.7765 | 1.0479 | 2.0682 | 2.4818 | 2.4818 | 2.4818 | 2.4818 | 1.1432 | 1.3298 | 1.3298 | 1.3298 | 1.3298 | 1.3298
2020-01-10 23:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.64302 | 1.2717 | 1.2717 | 1.2717 | 1.2717 | 1.2717 | 2.6984 | 3.4822 | 3.9957 | 4.266 | 4.8066 | 5.3472 | 1.0441 | 2.0607 | 2.4728 | 2.4728 | 2.4728 | 2.4728 | 1.1241 | 1.3076 | 1.3076 | 1.3076 | 1.3076 | 1.3076
2020-01-11 | Summer | 0.57615 | 0.82457 | 1.1899 | 1.1899 | 1.1899 | 1.1899 | 0.54871 | 1.0852 | 1.0852 | 1.0852 | 1.0852 | 1.0852 | 2.3625 | 3.0488 | 3.4984 | 3.735 | 4.2083 | 4.6816 | 0.84593 | 1.6696 | 2.0035 | 2.0035 | 2.0035 | 2.0035 | 1.067 | 1.2413 | 1.2413 | 1.2413 | 1.2413 | 1.2413
2020-01-11 01:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.47441 | 0.93825 | 0.93825 | 0.93825 | 0.93825 | 0.93825 | 2.191 | 2.8275 | 3.2445 | 3.4639 | 3.9029 | 4.3418 | 0.81545 | 1.6094 | 1.9313 | 1.9313 | 1.9313 | 1.9313 | 1.105 | 1.2855 | 1.2855 | 1.2855 | 1.2855 | 1.2855
2020-01-11 02:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.48298 | 0.95521 | 0.95521 | 0.95521 | 0.95521 | 0.95521 | 2.1148 | 2.7291 | 3.1316 | 3.3435 | 3.7671 | 4.1908 | 0.76591 | 1.5117 | 1.814 | 1.814 | 1.814 | 1.814 | 1.105 | 1.2855 | 1.2855 | 1.2855 | 1.2855 | 1.2855
2020-01-11 03:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.49155 | 0.97217 | 0.97217 | 0.97217 | 0.97217 | 0.97217 | 2.0577 | 2.6554 | 3.047 | 3.2531 | 3.6653 | 4.0775 | 0.73075 | 1.4423 | 1.7307 | 1.7307 | 1.7307 | 1.7307 | 1.086 | 1.2633 | 1.2633 | 1.2633 | 1.2633 | 1.2633
2020-01-11 04:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.46012 | 0.90999 | 0.90999 | 0.90999 | 0.90999 | 0.90999 | 2.1148 | 2.7291 | 3.1316 | 3.3435 | 3.7671 | 4.1908 | 0.78115 | 1.5417 | 1.8501 | 1.8501 | 1.8501 | 1.8501 | 1.086 | 1.2633 | 1.2633 | 1.2633 | 1.2633 | 1.2633
2020-01-11 05:00 | Summer | 2.2482 | 3.2175 | 4.643 | 4.643 | 4.643 | 4.643 | 1.3031 | 2.5772 | 2.5772 | 2.5772 | 2.5772 | 2.5772 | 2.1108 | 2.724 | 3.1257 | 3.3371 | 3.76 | 4.1828 | 0.82688 | 1.632 | 1.9584 | 1.9584 | 1.9584 | 1.9584 | 1.086 | 1.2633 | 1.2633 | 1.2633 | 1.2633 | 1.2633
2020-01-11 06:00 | Summer | 2.1257 | 3.0423 | 4.3901 | 4.3901 | 4.3901 | 4.3901 | 1.306 | 2.583 | 2.583 | 2.583 | 2.583 | 2.583 | 2.1676 | 2.7972 | 3.2097 | 3.4268 | 3.8611 | 4.2953 | 0.96787 | 1.9103 | 2.2923 | 2.2923 | 2.2923 | 2.2923 | 1.0669 | 1.2411 | 1.2411 | 1.2411 | 1.2411 | 1.2411
2020-01-11 07:00 | Summer | 0.30906 | 0.44232 | 0.63828 | 0.63828 | 0.63828 | 0.63828 | 1.4061 | 2.7809 | 2.7809 | 2.7809 | 2.7809 | 2.7809 | 2.3504 | 3.0332 | 3.4805 | 3.7159 | 4.1868 | 4.6576 | 0.93357 | 1.8426 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 1.2003 | 1.3963 | 1.3963 | 1.3963 | 1.3963 | 1.3963
2020-01-11 08:00 | Summer | 0.51011 | 0.73004 | 1.0535 | 1.0535 | 1.0535 | 1.0535 | 1.4146 | 2.7978 | 2.7978 | 2.7978 | 2.7978 | 2.7978 | 2.4959 | 3.2209 | 3.6959 | 3.9459 | 4.4459 | 4.9459 | 0.96787 | 1.9103 | 2.2923 | 2.2923 | 2.2923 | 2.2923 | 1.2003 | 1.3963 | 1.3963 | 1.3963 | 1.3963 | 1.3963
2020-01-11 09:00 | Summer | 0.71115 | 1.0178 | 1.4687 | 1.4687 | 1.4687 | 1.4687 | 1.609 | 3.1822 | 3.1822 | 3.1822 | 3.1822 | 3.1822 | 2.4387 | 3.1471 | 3.6112 | 3.8555 | 4.3441 | 4.8326 | 0.94501 | 1.8651 | 2.2382 | 2.2382 | 2.2382 | 2.2382 | 1.1813 | 1.3741 | 1.3741 | 1.3741 | 1.3741 | 1.3741
2020-01-11 10:00 | Summer | 0.91219 | 1.3055 | 1.8839 | 1.8839 | 1.8839 | 1.8839 | 1.5204 | 3.007 | 3.007 | 3.007 | 3.007 | 3.007 | 2.534 | 3.2701 | 3.7523 | 4.0061 | 4.5138 | 5.0214 | 0.97966 | 1.9335 | 2.3203 | 2.3203 | 2.3203 | 2.3203 | 1.2765 | 1.4849 | 1.4849 | 1.4849 | 1.4849 | 1.4849
2020-01-11 11:00 | Summer | 1.1132 | 1.5932 | 2.2991 | 2.2991 | 2.2991 | 2.2991 | 1.5518 | 3.0691 | 3.0691 | 3.0691 | 3.0691 | 3.0691 | 2.6909 | 3.4725 | 3.9846 | 4.2541 | 4.7932 | 5.3323 | 0.98311 | 1.9403 | 2.3284 | 2.3284 | 2.3284 | 2.3284 | 1.3086 | 1.5222 | 1.5222 | 1.5222 | 1.5222 | 1.5222
2020-01-11 12:00 | Summer | 1.3143 | 1.8809 | 2.7143 | 2.7143 | 2.7143 | 2.7143 | 1.4775 | 2.9222 | 2.9222 | 2.9222 | 2.9222 | 2.9222 | 2.7817 | 3.5897 | 4.1191 | 4.3977 | 4.955 | 5.5122 | 0.95644 | 1.8877 | 2.2652 | 2.2652 | 2.2652 | 2.2652 | 1.3527 | 1.5736 | 1.5736 | 1.5736 | 1.5736 | 1.5736
2020-01-11 13:00 | Summer | 1.5153 | 2.1687 | 3.1295 | 3.1295 | 3.1295 | 3.1295 | 1.3089 | 2.5887 | 2.5887 | 2.5887 | 2.5887 | 2.5887 | 2.8198 | 3.6389 | 4.1755 | 4.4579 | 5.0228 | 5.5877 | 0.93357 | 1.8426 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 1.3146 | 1.5293 | 1.5293 | 1.5293 | 1.5293 | 1.5293
2020-01-11 14:00 | Summer | 1.7164 | 2.4564 | 3.5447 | 3.5447 | 3.5447 | 3.5447 | 1.5604 | 3.0861 | 3.0861 | 3.0861 | 3.0861 | 3.0861 | 2.8579 | 3.688 | 4.2319 | 4.5182 | 5.0907 | 5.6632 | 0.98311 | 1.9403 | 2.3284 | 2.3284 | 2.3284 | 2.3284 | 1.2956 | 1.5071 | 1.5071 | 1.5071 | 1.5071 | 1.5071
2020-01-11 15:00 | Summer | 1.9174 | 2.7441 | 3.9599 | 3.9599 | 3.9599 | 3.9599 | 1.4918 | 2.9504 | 2.9504 | 2.9504 | 2.9504 | 2.9504 | 2.9531 | 3.811 | 4.373 | 4.6688 | 5.2604 | 5.852 | 0.97168 | 1.9178 | 2.3013 | 2.3013 | 2.3013 | 2.3013 | 1.3337 | 1.5514 | 1.5514 | 1.5514 | 1.5514 | 1.5514
2020-01-11 16:00 | Summer | 2.1185 | 3.0318 | 4.3751 | 4.3751 | 4.3751 | 4.3751 | 1.5547 | 3.0748 | 3.0748 | 3.0748 | 3.0748 | 3.0748 | 2.915 | 3.7618 | 4.3166 | 4.6086 | 5.1925 | 5.7765 | 0.99073 | 1.9554 | 2.3465 | 2.3465 | 2.3465 | 2.3465 | 1.3146 | 1.5293 | 1.5293 | 1.5293 | 1.5293 | 1.5293
2020-01-11 17:00 | Summer | 2.3195 | 3.3196 | 4.7903 | 4.7903 | 4.7903 | 4.7903 | 1.4461 | 2.86 | 2.86 | 2.86 | 2.86 | 2.86 | 2.915 | 3.7618 | 4.3166 | 4.6086 | 5.1925 | 5.7765 | 1.0212 | 2.0156 | 2.4187 | 2.4187 | 2.4187 | 2.4187 | 1.2765 | 1.4849 | 1.4849 | 1.4849 | 1.4849 | 1.4849
2020-01-11 18:00 | Summer | 2.5205 | 3.6073 | 5.2055 | 5.2055 | 5.2055 | 5.2055 | 1.3032 | 2.5774 | 2.5774 | 2.5774 | 2.5774 | 2.5774 | 2.8769 | 3.7126 | 4.2601 | 4.5483 | 5.1246 | 5.701 | 1.0288 | 2.0306 | 2.4367 | 2.4367 | 2.4367 | 2.4367 | 1.1622 | 1.352 | 1.352 | 1.352 | 1.352 | 1.352
2020-01-11 19:00 | Summer | 2.7216 | 3.895 | 5.6207 | 5.6207 | 5.6207 | 5.6207 | 1.1746 | 2.323 | 2.323 | 2.323 | 2.323 | 2.323 | 2.6483 | 3.4176 | 3.9216 | 4.1869 | 4.7174 | 5.2479 | 0.96406 | 1.9027 | 2.2833 | 2.2833 | 2.2833 | 2.2833 | 1.1241 | 1.3076 | 1.3076 | 1.3076 | 1.3076 | 1.3076
2020-01-11 20:00 | Summer | 2.915 | 4.1719 | 6.0202 | 6.0202 | 6.0202 | 6.0202 | 2.0405 | 4.0356 | 4.0356 | 4.0356 | 4.0356 | 4.0356 | 2.5149 | 3.2455 | 3.7241 | 3.976 | 4.4798 | 4.9836 | 0.93738 | 1.8501 | 2.2201 | 2.2201 | 2.2201 | 2.2201 | 1.086 | 1.2633 | 1.2633 | 1.2633 | 1.2633 | 1.2633
2020-01-11 21:00 | Summer | 0.56932 | 0.81479 | 1.1758 | 1.1758 | 1.1758 | 1.1758 | 0.55443 | 1.0965 | 1.0965 | 1.0965 | 1.0965 | 1.0965 | 2.4387 | 3.1471 | 3.6112 | 3.8555 | 4.3441 | 4.8326 | 0.99073 | 1.9554 | 2.3465 | 2.3465 | 2.3465 | 2.3465 | 1.086 | 1.2633 | 1.2633 | 1.2633 | 1.2633 | 1.2633
2020-01-11 22:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.50298 | 0.99478 | 0.99478 | 0.99478 | 0.99478 | 0.99478 | 2.2863 | 2.9504 | 3.3855 | 3.6146 | 4.0726 | 4.5306 | 0.91071 | 1.7975 | 2.1569 | 2.1569 | 2.1569 | 2.1569 | 0.97168 | 1.1303 | 1.1303 | 1.1303 | 1.1303 | 1.1303
2020-01-11 23:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.5087 | 1.0061 | 1.0061 | 1.0061 | 1.0061 | 1.0061 | 2.191 | 2.8275 | 3.2445 | 3.4639 | 3.9029 | 4.3418 | 0.85736 | 1.6922 | 2.0306 | 2.0306 | 2.0306 | 2.0306 | 0.97168 | 1.1303 | 1.1303 | 1.1303 | 1.1303 | 1.1303
2020-01-12 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.47441 | 0.93825 | 0.93825 | 0.93825 | 0.93825 | 0.93825 | 1.9816 | 2.5573 | 2.9344 | 3.1329 | 3.5299 | 3.9268 | 0.74305 | 1.4665 | 1.7599 | 1.7599 | 1.7599 | 1.7599 | 0.95263 | 1.1082 | 1.1082 | 1.1082 | 1.1082 | 1.1082
2020-01-12 01:00 | Summer | 0.55252 | 0.79075 | 1.1411 | 1.1411 | 1.1411 | 1.1411 | 0.46012 | 0.90999 | 0.90999 | 0.90999 | 0.90999 | 0.90999 | 1.9243 | 2.4833 | 2.8495 | 3.0422 | 3.4277 | 3.8132 | 0.6516 | 1.286 | 1.5433 | 1.5433 | 1.5433 | 1.5433 | 0.90601 | 1.0539 | 1.0539 | 1.0539 | 1.0539 | 1.0539
2020-01-12 02:00 | Summer | 0.54136 | 0.77477 | 1.118 | 1.118 | 1.118 | 1.118 | 0.50584 | 1.0004 | 1.0004 | 1.0004 | 1.0004 | 1.0004 | 1.8481 | 2.3849 | 2.7366 | 2.9218 | 3.292 | 3.6622 | 0.62873 | 1.2409 | 1.4891 | 1.4891 | 1.4891 | 1.4891 | 0.91452 | 1.0638 | 1.0638 | 1.0638 | 1.0638 | 1.0638
2020-01-12 03:00 | Summer | 0.55251 | 0.79073 | 1.1411 | 1.1411 | 1.1411 | 1.1411 | 0.50013 | 0.98912 | 0.98912 | 0.98912 | 0.98912 | 0.98912 | 1.7909 | 2.3112 | 2.652 | 2.8314 | 3.1902 | 3.549 | 0.63635 | 1.256 | 1.5072 | 1.5072 | 1.5072 | 1.5072 | 0.91452 | 1.0638 | 1.0638 | 1.0638 | 1.0638 | 1.0638
2020-01-12 04:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.48584 | 0.96086 | 0.96086 | 0.96086 | 0.96086 | 0.96086 | 1.8672 | 2.4095 | 2.7649 | 2.9519 | 3.3259 | 3.7 | 0.65541 | 1.2936 | 1.5523 | 1.5523 | 1.5523 | 1.5523 | 0.91452 | 1.0638 | 1.0638 | 1.0638 | 1.0638 | 1.0638
2020-01-12 05:00 | Summer | 0.55279 | 0.79113 | 1.1416 | 1.1416 | 1.1416 | 1.1416 | 0.51156 | 1.0117 | 1.0117 | 1.0117 | 1.0117 | 1.0117 | 1.9624 | 2.5325 | 2.9059 | 3.1025 | 3.4956 | 3.8887 | 0.80783 | 1.5944 | 1.9133 | 1.9133 | 1.9133 | 1.9133 | 0.91452 | 1.0638 | 1.0638 | 1.0638 | 1.0638 | 1.0638
2020-01-12 06:00 | Summer | 1.2765 | 1.8269 | 2.6363 | 2.6363 | 2.6363 | 2.6363 | 0.49441 | 0.97782 | 0.97782 | 0.97782 | 0.97782 | 0.97782 | 2.0196 | 2.6062 | 2.9906 | 3.1929 | 3.5974 | 4.002 | 1.5661 | 3.091 | 3.7092 | 3.7092 | 3.7092 | 3.7092 | 0.97168 | 1.1303 | 1.1303 | 1.1303 | 1.1303 | 1.1303
2020-01-12 07:00 | Summer | 0.020681 | 0.029598 | 0.042711 | 0.042711 | 0.042711 | 0.042711 | 0.56872 | 1.1248 | 1.1248 | 1.1248 | 1.1248 | 1.1248 | 2.0577 | 2.6554 | 3.047 | 3.2531 | 3.6653 | 4.0775 | 1.5814 | 3.1211 | 3.7453 | 3.7453 | 3.7453 | 3.7453 | 0.93358 | 1.086 | 1.086 | 1.086 | 1.086 | 1.086
2020-01-12 08:00 | Summer | 0.036492 | 0.052226 | 0.075364 | 0.075364 | 0.075364 | 0.075364 | 0.46869 | 0.92695 | 0.92695 | 0.92695 | 0.92695 | 0.92695 | 2.2961 | 2.9631 | 3.4001 | 3.6301 | 4.0901 | 4.5501 | 1.5509 | 3.0609 | 3.6731 | 3.6731 | 3.6731 | 3.6731 | 0.95263 | 1.1082 | 1.1082 | 1.1082 | 1.1082 | 1.1082
2020-01-12 09:00 | Summer | 0.052303 | 0.074854 | 0.10802 | 0.10802 | 0.10802 | 0.10802 | 0.53728 | 1.0626 | 1.0626 | 1.0626 | 1.0626 | 1.0626 | 2.3054 | 2.975 | 3.4138 | 3.6447 | 4.1065 | 4.5683 | 1.5204 | 3.0008 | 3.6009 | 3.6009 | 3.6009 | 3.6009 | 0.95263 | 1.1082 | 1.1082 | 1.1082 | 1.1082 | 1.1082
2020-01-12 10:00 | Summer | 0.16382 | 0.23445 | 0.33832 | 0.33832 | 0.33832 | 0.33832 | 0.54299 | 1.0739 | 1.0739 | 1.0739 | 1.0739 | 1.0739 | 2.3816 | 3.0734 | 3.5266 | 3.7652 | 4.2423 | 4.7194 | 1.6423 | 3.2414 | 3.8897 | 3.8897 | 3.8897 | 3.8897 | 0.97168 | 1.1303 | 1.1303 | 1.1303 | 1.1303 | 1.1303
2020-01-12 11:00 | Summer | 0.41534 | 0.59441 | 0.85776 | 0.85776 | 0.85776 | 0.85776 | 0.52585 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 2.4578 | 3.1717 | 3.6395 | 3.8856 | 4.378 | 4.8704 | 1.6385 | 3.2339 | 3.8807 | 3.8807 | 3.8807 | 3.8807 | 0.95347 | 1.1091 | 1.1091 | 1.1091 | 1.1091 | 1.1091
2020-01-12 12:00 | Summer | 0.68589 | 0.98162 | 1.4165 | 1.4165 | 1.4165 | 1.4165 | 0.46869 | 0.92695 | 0.92695 | 0.92695 | 0.92695 | 0.92695 | 2.4768 | 3.1963 | 3.6677 | 3.9158 | 4.4119 | 4.9081 | 1.5318 | 3.0233 | 3.628 | 3.628 | 3.628 | 3.628 | 1.0288 | 1.1968 | 1.1968 | 1.1968 | 1.1968 | 1.1968
2020-01-12 13:00 | Summer | 0.70494 | 1.0089 | 1.4559 | 1.4559 | 1.4559 | 1.4559 | 0.48012 | 0.94956 | 0.94956 | 0.94956 | 0.94956 | 0.94956 | 2.4578 | 3.1717 | 3.6395 | 3.8856 | 4.378 | 4.8704 | 0.84974 | 1.6771 | 2.0125 | 2.0125 | 2.0125 | 2.0125 | 0.97168 | 1.1303 | 1.1303 | 1.1303 | 1.1303 | 1.1303
2020-01-12 14:00 | Summer | 0.64779 | 0.92709 | 1.3378 | 1.3378 | 1.3378 | 1.3378 | 0.52013 | 1.0287 | 1.0287 | 1.0287 | 1.0287 | 1.0287 | 2.4197 | 3.1225 | 3.583 | 3.8254 | 4.3101 | 4.7949 | 0.86117 | 1.6997 | 2.0396 | 2.0396 | 2.0396 | 2.0396 | 0.97168 | 1.1303 | 1.1303 | 1.1303 | 1.1303 | 1.1303
2020-01-12 15:00 | Summer | 0.68589 | 0.98162 | 1.4165 | 1.4165 | 1.4165 | 1.4165 | 0.54014 | 1.0683 | 1.0683 | 1.0683 | 1.0683 | 1.0683 | 2.4578 | 3.1717 | 3.6395 | 3.8856 | 4.378 | 4.8704 | 0.88785 | 1.7523 | 2.1028 | 2.1028 | 2.1028 | 2.1028 | 0.97168 | 1.1303 | 1.1303 | 1.1303 | 1.1303 | 1.1303
2020-01-12 16:00 | Summer | 0.72242 | 1.0339 | 1.492 | 1.492 | 1.492 | 1.492 | 0.54299 | 1.0739 | 1.0739 | 1.0739 | 1.0739 | 1.0739 | 2.4959 | 3.2209 | 3.6959 | 3.9459 | 4.4459 | 4.9459 | 0.88023 | 1.7373 | 2.0847 | 2.0847 | 2.0847 | 2.0847 | 0.95263 | 1.1082 | 1.1082 | 1.1082 | 1.1082 | 1.1082
2020-01-12 17:00 | Summer | 0.74305 | 1.0634 | 1.5346 | 1.5346 | 1.5346 | 1.5346 | 0.55157 | 1.0909 | 1.0909 | 1.0909 | 1.0909 | 1.0909 | 2.534 | 3.2701 | 3.7523 | 4.0061 | 4.5138 | 5.0214 | 0.86498 | 1.7072 | 2.0486 | 2.0486 | 2.0486 | 2.0486 | 0.99073 | 1.1525 | 1.1525 | 1.1525 | 1.1525 | 1.1525
2020-01-12 18:00 | Summer | 0.55252 | 0.79075 | 1.1411 | 1.1411 | 1.1411 | 1.1411 | 0.53442 | 1.057 | 1.057 | 1.057 | 1.057 | 1.057 | 2.4768 | 3.1963 | 3.6677 | 3.9158 | 4.4119 | 4.9081 | 0.93738 | 1.8501 | 2.2201 | 2.2201 | 2.2201 | 2.2201 | 0.97168 | 1.1303 | 1.1303 | 1.1303 | 1.1303 | 1.1303
2020-01-12 19:00 | Summer | 0.55252 | 0.79075 | 1.1411 | 1.1411 | 1.1411 | 1.1411 | 0.54585 | 1.0796 | 1.0796 | 1.0796 | 1.0796 | 1.0796 | 2.3816 | 3.0734 | 3.5266 | 3.7652 | 4.2423 | 4.7194 | 0.85736 | 1.6922 | 2.0306 | 2.0306 | 2.0306 | 2.0306 | 0.97168 | 1.1303 | 1.1303 | 1.1303 | 1.1303 | 1.1303
2020-01-12 20:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.46583 | 0.9213 | 0.9213 | 0.9213 | 0.9213 | 0.9213 | 2.3244 | 2.9996 | 3.442 | 3.6748 | 4.1404 | 4.6061 | 0.86879 | 1.7147 | 2.0577 | 2.0577 | 2.0577 | 2.0577 | 0.95263 | 1.1082 | 1.1082 | 1.1082 | 1.1082 | 1.1082
2020-01-12 21:00 | Summer | 0.55252 | 0.79075 | 1.1411 | 1.1411 | 1.1411 | 1.1411 | 0.48869 | 0.96652 | 0.96652 | 0.96652 | 0.96652 | 0.96652 | 2.2291 | 2.8767 | 3.3009 | 3.5242 | 3.9708 | 4.4173 | 0.88404 | 1.7448 | 2.0938 | 2.0938 | 2.0938 | 2.0938 | 0.91452 | 1.0638 | 1.0638 | 1.0638 | 1.0638 | 1.0638
2020-01-12 22:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.49727 | 0.98347 | 0.98347 | 0.98347 | 0.98347 | 0.98347 | 2.1529 | 2.7783 | 3.1881 | 3.4037 | 3.835 | 4.2663 | 0.74686 | 1.4741 | 1.7689 | 1.7689 | 1.7689 | 1.7689 | 0.89547 | 1.0417 | 1.0417 | 1.0417 | 1.0417 | 1.0417
2020-01-12 23:00 | Summer | 0.56722 | 0.81179 | 1.1714 | 1.1714 | 1.1714 | 1.1714 | 0.49155 | 0.97217 | 0.97217 | 0.97217 | 0.97217 | 0.97217 | 2.0147 | 2.5999 | 2.9833 | 3.1851 | 3.5887 | 3.9923 | 0.64779 | 1.2785 | 1.5342 | 1.5342 | 1.5342 | 1.5342 | 0.87642 | 1.0195 | 1.0195 | 1.0195 | 1.0195 | 1.0195
2020-01-13 | Summer | 0.55208 | 0.79012 | 1.1402 | 1.1402 | 1.1402 | 1.1402 | 0.46012 | 0.90999 | 0.90999 | 0.90999 | 0.90999 | 0.90999 | 1.8481 | 2.3849 | 2.7366 | 2.9218 | 3.292 | 3.6622 | 0.5792 | 1.1431 | 1.3718 | 1.3718 | 1.3718 | 1.3718 | 0.8565 | 0.99634 | 0.99634 | 0.99634 | 0.99634 | 0.99634
2020-01-13 01:00 | Summer | 0.55252 | 0.79075 | 1.1411 | 1.1411 | 1.1411 | 1.1411 | 0.45726 | 0.90434 | 0.90434 | 0.90434 | 0.90434 | 0.90434 | 1.6929 | 2.1847 | 2.5068 | 2.6764 | 3.0155 | 3.3547 | 0.5449 | 1.0755 | 1.2906 | 1.2906 | 1.2906 | 1.2906 | 0.85737 | 0.99734 | 0.99734 | 0.99734 | 0.99734 | 0.99734
2020-01-13 02:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.58015 | 1.1474 | 1.1474 | 1.1474 | 1.1474 | 1.1474 | 1.6385 | 2.1145 | 2.4263 | 2.5904 | 2.9187 | 3.2469 | 0.52585 | 1.0379 | 1.2454 | 1.2454 | 1.2454 | 1.2454 | 0.85737 | 0.99734 | 0.99734 | 0.99734 | 0.99734 | 0.99734
2020-01-13 03:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.48298 | 0.95521 | 0.95521 | 0.95521 | 0.95521 | 0.95521 | 1.6261 | 2.0985 | 2.408 | 2.5709 | 2.8966 | 3.2224 | 0.54871 | 1.083 | 1.2996 | 1.2996 | 1.2996 | 1.2996 | 0.91412 | 1.0634 | 1.0634 | 1.0634 | 1.0634 | 1.0634
2020-01-13 04:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.47726 | 0.94391 | 0.94391 | 0.94391 | 0.94391 | 0.94391 | 1.6957 | 2.1882 | 2.5109 | 2.6808 | 3.0205 | 3.3602 | 0.60206 | 1.1883 | 1.4259 | 1.4259 | 1.4259 | 1.4259 | 1.0669 | 1.2411 | 1.2411 | 1.2411 | 1.2411 | 1.2411
2020-01-13 05:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.54014 | 1.0683 | 1.0683 | 1.0683 | 1.0683 | 1.0683 | 1.7338 | 2.2374 | 2.5674 | 2.741 | 3.0884 | 3.4357 | 0.8345 | 1.647 | 1.9764 | 1.9764 | 1.9764 | 1.9764 | 1.1614 | 1.351 | 1.351 | 1.351 | 1.351 | 1.351
2020-01-13 06:00 | Summer | 1.505 | 2.1538 | 3.1081 | 3.1081 | 3.1081 | 3.1081 | 0.70018 | 1.3848 | 1.3848 | 1.3848 | 1.3848 | 1.3848 | 2.0196 | 2.6062 | 2.9906 | 3.1929 | 3.5974 | 4.002 | 0.88023 | 1.7373 | 2.0847 | 2.0847 | 2.0847 | 2.0847 | 1.2956 | 1.5071 | 1.5071 | 1.5071 | 1.5071 | 1.5071
2020-01-13 07:00 | Summer | 1.5052 | 2.1541 | 3.1085 | 3.1085 | 3.1085 | 3.1085 | 0.94881 | 1.8765 | 1.8765 | 1.8765 | 1.8765 | 1.8765 | 2.4959 | 3.2209 | 3.6959 | 3.9459 | 4.4459 | 4.9459 | 1.2003 | 2.369 | 2.8428 | 2.8428 | 2.8428 | 2.8428 | 1.9053 | 2.2163 | 2.2163 | 2.2163 | 2.2163 | 2.2163
2020-01-13 08:00 | Summer | 1.7528 | 2.5086 | 3.62 | 3.62 | 3.62 | 3.62 | 0.9631 | 1.9048 | 1.9048 | 1.9048 | 1.9048 | 1.9048 | 2.915 | 3.7618 | 4.3166 | 4.6086 | 5.1925 | 5.7765 | 1.1774 | 2.3239 | 2.7887 | 2.7887 | 2.7887 | 2.7887 | 2.2673 | 2.6374 | 2.6374 | 2.6374 | 2.6374 | 2.6374
2020-01-13 09:00 | Summer | 1.7819 | 2.5501 | 3.6799 | 3.6799 | 3.6799 | 3.6799 | 1.0946 | 2.1648 | 2.1648 | 2.1648 | 2.1648 | 2.1648 | 2.9531 | 3.811 | 4.373 | 4.6688 | 5.2604 | 5.852 | 1.1203 | 2.2111 | 2.6533 | 2.6533 | 2.6533 | 2.6533 | 2.4578 | 2.8591 | 2.8591 | 2.8591 | 2.8591 | 2.8591
2020-01-13 10:00 | Summer | 1.829 | 2.6177 | 3.7774 | 3.7774 | 3.7774 | 3.7774 | 1.1917 | 2.357 | 2.357 | 2.357 | 2.357 | 2.357 | 3.1056 | 4.0077 | 4.5987 | 4.9098 | 5.5319 | 6.154 | 1.1432 | 2.2562 | 2.7075 | 2.7075 | 2.7075 | 2.7075 | 2.553 | 2.9699 | 2.9699 | 2.9699 | 2.9699 | 2.9699
2020-01-13 11:00 | Summer | 1.829 | 2.6177 | 3.7774 | 3.7774 | 3.7774 | 3.7774 | 1.0917 | 2.1591 | 2.1591 | 2.1591 | 2.1591 | 2.1591 | 3.2282 | 4.166 | 4.7803 | 5.1037 | 5.7504 | 6.3971 | 1.1432 | 2.2562 | 2.7075 | 2.7075 | 2.7075 | 2.7075 | 2.6102 | 3.0364 | 3.0364 | 3.0364 | 3.0364 | 3.0364
2020-01-13 12:00 | Summer | 1.829 | 2.6177 | 3.7774 | 3.7774 | 3.7774 | 3.7774 | 1.4832 | 2.9335 | 2.9335 | 2.9335 | 2.9335 | 2.9335 | 3.3672 | 4.3453 | 4.9861 | 5.3234 | 5.9979 | 6.6725 | 1.0365 | 2.0456 | 2.4548 | 2.4548 | 2.4548 | 2.4548 | 2.6293 | 3.0585 | 3.0585 | 3.0585 | 3.0585 | 3.0585
2020-01-13 13:00 | Summer | 1.81 | 2.5904 | 3.738 | 3.738 | 3.738 | 3.738 | 1.3232 | 2.617 | 2.617 | 2.617 | 2.617 | 2.617 | 3.3723 | 4.3519 | 4.9937 | 5.3315 | 6.007 | 6.6826 | 1.0784 | 2.1284 | 2.554 | 2.554 | 2.554 | 2.554 | 2.7245 | 3.1693 | 3.1693 | 3.1693 | 3.1693 | 3.1693
2020-01-13 14:00 | Summer | 1.7909 | 2.5631 | 3.6987 | 3.6987 | 3.6987 | 3.6987 | 1.4289 | 2.8261 | 2.8261 | 2.8261 | 2.8261 | 2.8261 | 3.5247 | 4.5486 | 5.2194 | 5.5724 | 6.2785 | 6.9846 | 1.025 | 2.0231 | 2.4277 | 2.4277 | 2.4277 | 2.4277 | 2.6864 | 3.125 | 3.125 | 3.125 | 3.125 | 3.125
2020-01-13 15:00 | Summer | 1.829 | 2.6177 | 3.7774 | 3.7774 | 3.7774 | 3.7774 | 1.5004 | 2.9674 | 2.9674 | 2.9674 | 2.9674 | 2.9674 | 3.4676 | 4.4748 | 5.1347 | 5.4821 | 6.1767 | 6.8714 | 1.0403 | 2.0532 | 2.4638 | 2.4638 | 2.4638 | 2.4638 | 2.7626 | 3.2137 | 3.2137 | 3.2137 | 3.2137 | 3.2137
2020-01-13 16:00 | Summer | 1.81 | 2.5904 | 3.738 | 3.738 | 3.738 | 3.738 | 1.3203 | 2.6113 | 2.6113 | 2.6113 | 2.6113 | 2.6113 | 3.7343 | 4.819 | 5.5297 | 5.9038 | 6.6519 | 7.4 | 1.0555 | 2.0832 | 2.4999 | 2.4999 | 2.4999 | 2.4999 | 2.7817 | 3.2358 | 3.2358 | 3.2358 | 3.2358 | 3.2358
2020-01-13 17:00 | Summer | 1.7189 | 2.46 | 3.5499 | 3.5499 | 3.5499 | 3.5499 | 1.3461 | 2.6622 | 2.6622 | 2.6622 | 2.6622 | 2.6622 | 3.4485 | 4.4502 | 5.1065 | 5.4519 | 6.1428 | 6.8336 | 1.0479 | 2.0682 | 2.4818 | 2.4818 | 2.4818 | 2.4818 | 2.6674 | 3.1028 | 3.1028 | 3.1028 | 3.1028 | 3.1028
2020-01-13 18:00 | Summer | 1.2948 | 1.8531 | 2.6741 | 2.6741 | 2.6741 | 2.6741 | 1.0524 | 2.0814 | 2.0814 | 2.0814 | 2.0814 | 2.0814 | 3.1982 | 4.1273 | 4.7359 | 5.0563 | 5.697 | 6.3377 | 0.95644 | 1.8877 | 2.2652 | 2.2652 | 2.2652 | 2.2652 | 2.0203 | 2.3501 | 2.3501 | 2.3501 | 2.3501 | 2.3501
2020-01-13 19:00 | Summer | 0.7621 | 1.0907 | 1.5739 | 1.5739 | 1.5739 | 1.5739 | 0.75856 | 1.5002 | 1.5002 | 1.5002 | 1.5002 | 1.5002 | 3.0169 | 3.8932 | 4.4673 | 4.7695 | 5.3739 | 5.9783 | 0.96699 | 1.9085 | 2.2902 | 2.2902 | 2.2902 | 2.2902 | 1.2003 | 1.3963 | 1.3963 | 1.3963 | 1.3963 | 1.3963
2020-01-13 20:00 | Summer | 0.73119 | 1.0464 | 1.5101 | 1.5101 | 1.5101 | 1.5101 | 0.53156 | 1.0513 | 1.0513 | 1.0513 | 1.0513 | 1.0513 | 2.5721 | 3.3192 | 3.8087 | 4.0664 | 4.5816 | 5.0969 | 1.0517 | 2.0757 | 2.4909 | 2.4909 | 2.4909 | 2.4909 | 1.1813 | 1.3741 | 1.3741 | 1.3741 | 1.3741 | 1.3741
2020-01-13 21:00 | Summer | 0.60988 | 0.87284 | 1.2595 | 1.2595 | 1.2595 | 1.2595 | 0.46583 | 0.9213 | 0.9213 | 0.9213 | 0.9213 | 0.9213 | 2.553 | 3.2946 | 3.7805 | 4.0362 | 4.5477 | 5.0591 | 0.9069 | 1.7899 | 2.1479 | 2.1479 | 2.1479 | 2.1479 | 1.1015 | 1.2814 | 1.2814 | 1.2814 | 1.2814 | 1.2814
2020-01-13 22:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.40582 | 0.8026 | 0.8026 | 0.8026 | 0.8026 | 0.8026 | 2.2297 | 2.8774 | 3.3018 | 3.5251 | 3.9718 | 4.4185 | 0.94119 | 1.8576 | 2.2291 | 2.2291 | 2.2291 | 2.2291 | 0.97168 | 1.1303 | 1.1303 | 1.1303 | 1.1303 | 1.1303
2020-01-13 23:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.38295 | 0.75738 | 0.75738 | 0.75738 | 0.75738 | 0.75738 | 2.1148 | 2.7291 | 3.1316 | 3.3435 | 3.7671 | 4.1908 | 0.81164 | 1.6019 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 0.93358 | 1.086 | 1.086 | 1.086 | 1.086 | 1.086
2020-01-14 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.46012 | 0.90999 | 0.90999 | 0.90999 | 0.90999 | 0.90999 | 1.9053 | 2.4587 | 2.8213 | 3.0121 | 3.3938 | 3.7755 | 0.60206 | 1.1883 | 1.4259 | 1.4259 | 1.4259 | 1.4259 | 0.93358 | 1.086 | 1.086 | 1.086 | 1.086 | 1.086
2020-01-14 01:00 | Summer | 0.55292 | 0.79131 | 1.1419 | 1.1419 | 1.1419 | 1.1419 | 0.42011 | 0.83086 | 0.83086 | 0.83086 | 0.83086 | 0.83086 | 1.829 | 2.3603 | 2.7084 | 2.8916 | 3.2581 | 3.6245 | 0.5792 | 1.1431 | 1.3718 | 1.3718 | 1.3718 | 1.3718 | 0.95263 | 1.1082 | 1.1082 | 1.1082 | 1.1082 | 1.1082
2020-01-14 02:00 | Summer | 0.55252 | 0.79075 | 1.1411 | 1.1411 | 1.1411 | 1.1411 | 0.48869 | 0.96652 | 0.96652 | 0.96652 | 0.96652 | 0.96652 | 1.7909 | 2.3112 | 2.652 | 2.8314 | 3.1902 | 3.549 | 0.56395 | 1.1131 | 1.3357 | 1.3357 | 1.3357 | 1.3357 | 0.87642 | 1.0195 | 1.0195 | 1.0195 | 1.0195 | 1.0195
2020-01-14 03:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.40296 | 0.79695 | 0.79695 | 0.79695 | 0.79695 | 0.79695 | 1.7488 | 2.2568 | 2.5897 | 2.7648 | 3.1152 | 3.4655 | 0.59825 | 1.1808 | 1.4169 | 1.4169 | 1.4169 | 1.4169 | 0.87642 | 1.0195 | 1.0195 | 1.0195 | 1.0195 | 1.0195
2020-01-14 04:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.51807 | 1.0246 | 1.0246 | 1.0246 | 1.0246 | 1.0246 | 1.7909 | 2.3112 | 2.652 | 2.8314 | 3.1902 | 3.549 | 0.57157 | 1.1281 | 1.3537 | 1.3537 | 1.3537 | 1.3537 | 0.99073 | 1.1525 | 1.1525 | 1.1525 | 1.1525 | 1.1525
2020-01-14 05:00 | Summer | 0.60124 | 0.86047 | 1.2417 | 1.2417 | 1.2417 | 1.2417 | 0.54585 | 1.0796 | 1.0796 | 1.0796 | 1.0796 | 1.0796 | 1.8862 | 2.4341 | 2.7931 | 2.982 | 3.3599 | 3.7377 | 0.91833 | 1.8125 | 2.175 | 2.175 | 2.175 | 2.175 | 1.1241 | 1.3076 | 1.3076 | 1.3076 | 1.3076 | 1.3076
2020-01-14 06:00 | Summer | 0.91452 | 1.3088 | 1.8887 | 1.8887 | 1.8887 | 1.8887 | 0.81404 | 1.61 | 1.61 | 1.61 | 1.61 | 1.61 | 2.0767 | 2.68 | 3.0752 | 3.2832 | 3.6992 | 4.1153 | 0.91452 | 1.805 | 2.166 | 2.166 | 2.166 | 2.166 | 1.3337 | 1.5514 | 1.5514 | 1.5514 | 1.5514 | 1.5514
2020-01-14 07:00 | Summer | 1.7528 | 2.5086 | 3.62 | 3.62 | 3.62 | 3.62 | 0.90023 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 2.7436 | 3.5405 | 4.0627 | 4.3375 | 4.8871 | 5.4367 | 1.1889 | 2.3465 | 2.8158 | 2.8158 | 2.8158 | 2.8158 | 1.9243 | 2.2385 | 2.2385 | 2.2385 | 2.2385 | 2.2385
2020-01-14 08:00 | Summer | 1.7909 | 2.5631 | 3.6987 | 3.6987 | 3.6987 | 3.6987 | 1.1231 | 2.2213 | 2.2213 | 2.2213 | 2.2213 | 2.2213 | 3.1437 | 4.0568 | 4.6551 | 4.97 | 5.5998 | 6.2296 | 1.2498 | 2.4668 | 2.9602 | 2.9602 | 2.9602 | 2.9602 | 2.2863 | 2.6596 | 2.6596 | 2.6596 | 2.6596 | 2.6596
2020-01-14 09:00 | Summer | 1.8481 | 2.6449 | 3.8167 | 3.8167 | 3.8167 | 3.8167 | 1.2203 | 2.4135 | 2.4135 | 2.4135 | 2.4135 | 2.4135 | 3.1709 | 4.092 | 4.6955 | 5.0131 | 5.6484 | 6.2836 | 1.2384 | 2.4442 | 2.9331 | 2.9331 | 2.9331 | 2.9331 | 2.553 | 2.9699 | 2.9699 | 2.9699 | 2.9699 | 2.9699
2020-01-14 10:00 | Summer | 1.9053 | 2.7267 | 3.9348 | 3.9348 | 3.9348 | 3.9348 | 1.3232 | 2.617 | 2.617 | 2.617 | 2.617 | 2.617 | 3.3533 | 4.3273 | 4.9655 | 5.3013 | 5.9731 | 6.6449 | 1.0822 | 2.1359 | 2.5631 | 2.5631 | 2.5631 | 2.5631 | 2.7436 | 3.1915 | 3.1915 | 3.1915 | 3.1915 | 3.1915
2020-01-14 11:00 | Summer | 1.8862 | 2.6995 | 3.8954 | 3.8954 | 3.8954 | 3.8954 | 1.2689 | 2.5096 | 2.5096 | 2.5096 | 2.5096 | 2.5096 | 3.6962 | 4.7699 | 5.4733 | 5.8435 | 6.584 | 7.3244 | 1.1089 | 2.1885 | 2.6262 | 2.6262 | 2.6262 | 2.6262 | 2.823 | 3.2839 | 3.2839 | 3.2839 | 3.2839 | 3.2839
2020-01-14 12:00 | Summer | 1.9243 | 2.754 | 3.9741 | 3.9741 | 3.9741 | 3.9741 | 1.3718 | 2.713 | 2.713 | 2.713 | 2.713 | 2.713 | 3.6962 | 4.7699 | 5.4733 | 5.8435 | 6.584 | 7.3244 | 1.1317 | 2.2337 | 2.6804 | 2.6804 | 2.6804 | 2.6804 | 2.8769 | 3.3466 | 3.3466 | 3.3466 | 3.3466 | 3.3466
2020-01-14 13:00 | Summer | 2.0958 | 2.9994 | 4.3282 | 4.3282 | 4.3282 | 4.3282 | 1.4375 | 2.843 | 2.843 | 2.843 | 2.843 | 2.843 | 3.8105 | 4.9174 | 5.6426 | 6.0243 | 6.7876 | 7.551 | 1.1698 | 2.3089 | 2.7706 | 2.7706 | 2.7706 | 2.7706 | 3.0484 | 3.5461 | 3.5461 | 3.5461 | 3.5461 | 3.5461
2020-01-14 14:00 | Summer | 2.1529 | 3.0812 | 4.4463 | 4.4463 | 4.4463 | 4.4463 | 1.3318 | 2.6339 | 2.6339 | 2.6339 | 2.6339 | 2.6339 | 3.8867 | 5.0157 | 5.7554 | 6.1447 | 6.9234 | 7.702 | 1.1851 | 2.3389 | 2.8067 | 2.8067 | 2.8067 | 2.8067 | 3.0675 | 3.5683 | 3.5683 | 3.5683 | 3.5683 | 3.5683
2020-01-14 15:00 | Summer | 2.0958 | 2.9994 | 4.3282 | 4.3282 | 4.3282 | 4.3282 | 1.3764 | 2.7221 | 2.7221 | 2.7221 | 2.7221 | 2.7221 | 3.8867 | 5.0157 | 5.7554 | 6.1447 | 6.9234 | 7.702 | 1.1546 | 2.2788 | 2.7345 | 2.7345 | 2.7345 | 2.7345 | 3.2008 | 3.7234 | 3.7234 | 3.7234 | 3.7234 | 3.7234
2020-01-14 16:00 | Summer | 1.9624 | 2.8085 | 4.0528 | 4.0528 | 4.0528 | 4.0528 | 1.4375 | 2.843 | 2.843 | 2.843 | 2.843 | 2.843 | 3.9248 | 5.0649 | 5.8119 | 6.205 | 6.9912 | 7.7775 | 1.2346 | 2.4367 | 2.9241 | 2.9241 | 2.9241 | 2.9241 | 2.9531 | 3.4353 | 3.4353 | 3.4353 | 3.4353 | 3.4353
2020-01-14 17:00 | Summer | 1.7909 | 2.5631 | 3.6987 | 3.6987 | 3.6987 | 3.6987 | 1.306 | 2.583 | 2.583 | 2.583 | 2.583 | 2.583 | 3.7915 | 4.8928 | 5.6144 | 5.9941 | 6.7537 | 7.5132 | 1.1965 | 2.3615 | 2.8338 | 2.8338 | 2.8338 | 2.8338 | 2.8209 | 3.2815 | 3.2815 | 3.2815 | 3.2815 | 3.2815
2020-01-14 18:00 | Summer | 1.2006 | 1.7183 | 2.4795 | 2.4795 | 2.4795 | 2.4795 | 0.91738 | 1.8143 | 1.8143 | 1.8143 | 1.8143 | 1.8143 | 3.4104 | 4.4011 | 5.0501 | 5.3917 | 6.0749 | 6.7581 | 1.1355 | 2.2412 | 2.6894 | 2.6894 | 2.6894 | 2.6894 | 2.1339 | 2.4823 | 2.4823 | 2.4823 | 2.4823 | 2.4823
2020-01-14 19:00 | Summer | 0.7621 | 1.0907 | 1.5739 | 1.5739 | 1.5739 | 1.5739 | 0.66303 | 1.3113 | 1.3113 | 1.3113 | 1.3113 | 1.3113 | 2.9988 | 3.8698 | 4.4406 | 4.7409 | 5.3417 | 5.9424 | 1.1546 | 2.2788 | 2.7345 | 2.7345 | 2.7345 | 2.7345 | 1.2108 | 1.4085 | 1.4085 | 1.4085 | 1.4085 | 1.4085
2020-01-14 20:00 | Summer | 0.70494 | 1.0089 | 1.4559 | 1.4559 | 1.4559 | 1.4559 | 0.60587 | 1.1983 | 1.1983 | 1.1983 | 1.1983 | 1.1983 | 2.6293 | 3.393 | 3.8934 | 4.1567 | 4.6835 | 5.2102 | 1.0936 | 2.1585 | 2.5901 | 2.5901 | 2.5901 | 2.5901 | 1.1432 | 1.3298 | 1.3298 | 1.3298 | 1.3298 | 1.3298
2020-01-14 21:00 | Summer | 0.64337 | 0.92076 | 1.3287 | 1.3287 | 1.3287 | 1.3287 | 0.54585 | 1.0796 | 1.0796 | 1.0796 | 1.0796 | 1.0796 | 2.5335 | 3.2694 | 3.7515 | 4.0053 | 4.5128 | 5.0203 | 1.0593 | 2.0908 | 2.5089 | 2.5089 | 2.5089 | 2.5089 | 1.1622 | 1.352 | 1.352 | 1.352 | 1.352 | 1.352
2020-01-14 22:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.563 | 1.1135 | 1.1135 | 1.1135 | 1.1135 | 1.1135 | 2.3625 | 3.0488 | 3.4984 | 3.735 | 4.2083 | 4.6816 | 0.99454 | 1.9629 | 2.3555 | 2.3555 | 2.3555 | 2.3555 | 1.105 | 1.2855 | 1.2855 | 1.2855 | 1.2855 | 1.2855
2020-01-14 23:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.52585 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 2.2101 | 2.8521 | 3.2727 | 3.4941 | 3.9368 | 4.3796 | 0.92753 | 1.8306 | 2.1968 | 2.1968 | 2.1968 | 2.1968 | 1.0098 | 1.1746 | 1.1746 | 1.1746 | 1.1746 | 1.1746
2020-01-15 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.59158 | 1.17 | 1.17 | 1.17 | 1.17 | 1.17 | 1.9434 | 2.5079 | 2.8777 | 3.0724 | 3.4617 | 3.851 | 0.84974 | 1.6771 | 2.0125 | 2.0125 | 2.0125 | 2.0125 | 0.99073 | 1.1525 | 1.1525 | 1.1525 | 1.1525 | 1.1525
2020-01-15 01:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.52013 | 1.0287 | 1.0287 | 1.0287 | 1.0287 | 1.0287 | 1.9053 | 2.4587 | 2.8213 | 3.0121 | 3.3938 | 3.7755 | 0.70875 | 1.3989 | 1.6786 | 1.6786 | 1.6786 | 1.6786 | 0.97168 | 1.1303 | 1.1303 | 1.1303 | 1.1303 | 1.1303
2020-01-15 02:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.53442 | 1.057 | 1.057 | 1.057 | 1.057 | 1.057 | 1.8862 | 2.4341 | 2.7931 | 2.982 | 3.3599 | 3.7377 | 0.64016 | 1.2635 | 1.5162 | 1.5162 | 1.5162 | 1.5162 | 0.99073 | 1.1525 | 1.1525 | 1.1525 | 1.1525 | 1.1525
2020-01-15 03:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.51442 | 1.0174 | 1.0174 | 1.0174 | 1.0174 | 1.0174 | 1.8672 | 2.4095 | 2.7649 | 2.9519 | 3.3259 | 3.7 | 0.64016 | 1.2635 | 1.5162 | 1.5162 | 1.5162 | 1.5162 | 0.99073 | 1.1525 | 1.1525 | 1.1525 | 1.1525 | 1.1525
2020-01-15 04:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.50298 | 0.99478 | 0.99478 | 0.99478 | 0.99478 | 0.99478 | 1.8862 | 2.4341 | 2.7931 | 2.982 | 3.3599 | 3.7377 | 0.65541 | 1.2936 | 1.5523 | 1.5523 | 1.5523 | 1.5523 | 1.1432 | 1.3298 | 1.3298 | 1.3298 | 1.3298 | 1.3298
2020-01-15 05:00 | Summer | 0.62839 | 0.89933 | 1.2978 | 1.2978 | 1.2978 | 1.2978 | 0.61158 | 1.2096 | 1.2096 | 1.2096 | 1.2096 | 1.2096 | 1.9815 | 2.557 | 2.9341 | 3.1326 | 3.5296 | 3.9265 | 1.0746 | 2.1208 | 2.545 | 2.545 | 2.545 | 2.545 | 1.2564 | 1.4616 | 1.4616 | 1.4616 | 1.4616 | 1.4616
2020-01-15 06:00 | Summer | 0.89437 | 1.28 | 1.8471 | 1.8471 | 1.8471 | 1.8471 | 0.83736 | 1.6561 | 1.6561 | 1.6561 | 1.6561 | 1.6561 | 2.1219 | 2.7383 | 3.1422 | 3.3547 | 3.7798 | 4.2049 | 1.0136 | 2.0005 | 2.4006 | 2.4006 | 2.4006 | 2.4006 | 1.4877 | 1.7306 | 1.7306 | 1.7306 | 1.7306 | 1.7306
2020-01-15 07:00 | Summer | 1.5125 | 2.1647 | 3.1237 | 3.1237 | 3.1237 | 3.1237 | 1.1117 | 2.1987 | 2.1987 | 2.1987 | 2.1987 | 2.1987 | 2.8198 | 3.6389 | 4.1755 | 4.4579 | 5.0228 | 5.5877 | 1.2308 | 2.4292 | 2.915 | 2.915 | 2.915 | 2.915 | 1.9624 | 2.2828 | 2.2828 | 2.2828 | 2.2828 | 2.2828
2020-01-15 08:00 | Summer | 1.7719 | 2.5359 | 3.6593 | 3.6593 | 3.6593 | 3.6593 | 1.2119 | 2.3968 | 2.3968 | 2.3968 | 2.3968 | 2.3968 | 3.1437 | 4.0568 | 4.6551 | 4.97 | 5.5998 | 6.2296 | 1.1584 | 2.2863 | 2.7436 | 2.7436 | 2.7436 | 2.7436 | 2.3054 | 2.6817 | 2.6817 | 2.6817 | 2.6817 | 2.6817
2020-01-15 09:00 | Summer | 1.829 | 2.6177 | 3.7774 | 3.7774 | 3.7774 | 3.7774 | 1.3346 | 2.6396 | 2.6396 | 2.6396 | 2.6396 | 2.6396 | 3.1413 | 4.0538 | 4.6516 | 4.9662 | 5.5955 | 6.2248 | 1.2537 | 2.4743 | 2.9692 | 2.9692 | 2.9692 | 2.9692 | 2.5727 | 2.9928 | 2.9928 | 2.9928 | 2.9928 | 2.9928
2020-01-15 10:00 | Summer | 2.1404 | 3.0633 | 4.4205 | 4.4205 | 4.4205 | 4.4205 | 1.3946 | 2.7583 | 2.7583 | 2.7583 | 2.7583 | 2.7583 | 3.62 | 4.6715 | 5.3604 | 5.723 | 6.4482 | 7.1734 | 1.2651 | 2.4969 | 2.9963 | 2.9963 | 2.9963 | 2.9963 | 2.7436 | 3.1915 | 3.1915 | 3.1915 | 3.1915 | 3.1915
2020-01-15 11:00 | Summer | 2.3054 | 3.2993 | 4.7611 | 4.7611 | 4.7611 | 4.7611 | 1.3346 | 2.6396 | 2.6396 | 2.6396 | 2.6396 | 2.6396 | 3.62 | 4.6715 | 5.3604 | 5.723 | 6.4482 | 7.1734 | 1.1279 | 2.2261 | 2.6714 | 2.6714 | 2.6714 | 2.6714 | 2.727 | 3.1723 | 3.1723 | 3.1723 | 3.1723 | 3.1723
2020-01-15 12:00 | Summer | 2.0931 | 2.9955 | 4.3227 | 4.3227 | 4.3227 | 4.3227 | 1.3946 | 2.7583 | 2.7583 | 2.7583 | 2.7583 | 2.7583 | 3.7343 | 4.819 | 5.5297 | 5.9038 | 6.6519 | 7.4 | 1.1165 | 2.2036 | 2.6443 | 2.6443 | 2.6443 | 2.6443 | 2.8769 | 3.3466 | 3.3466 | 3.3466 | 3.3466 | 3.3466
2020-01-15 13:00 | Summer | 2.191 | 3.1357 | 4.525 | 4.525 | 4.525 | 4.525 | 1.4518 | 2.8713 | 2.8713 | 2.8713 | 2.8713 | 2.8713 | 3.8296 | 4.942 | 5.6708 | 6.0544 | 6.8215 | 7.5887 | 1.1127 | 2.1961 | 2.6353 | 2.6353 | 2.6353 | 2.6353 | 3.1627 | 3.6791 | 3.6791 | 3.6791 | 3.6791 | 3.6791
2020-01-15 14:00 | Summer | 2.4197 | 3.4629 | 4.9972 | 4.9972 | 4.9972 | 4.9972 | 1.5404 | 3.0465 | 3.0465 | 3.0465 | 3.0465 | 3.0465 | 3.982 | 5.1387 | 5.8965 | 6.2953 | 7.0931 | 7.8908 | 1.1584 | 2.2863 | 2.7436 | 2.7436 | 2.7436 | 2.7436 | 3.1056 | 3.6126 | 3.6126 | 3.6126 | 3.6126 | 3.6126
2020-01-15 15:00 | Summer | 2.2572 | 3.2305 | 4.6617 | 4.6617 | 4.6617 | 4.6617 | 1.5547 | 3.0748 | 3.0748 | 3.0748 | 3.0748 | 3.0748 | 4.0391 | 5.2124 | 5.9811 | 6.3857 | 7.1949 | 8.004 | 1.1736 | 2.3164 | 2.7797 | 2.7797 | 2.7797 | 2.7797 | 3.0484 | 3.5461 | 3.5461 | 3.5461 | 3.5461 | 3.5461
2020-01-15 16:00 | Summer | 2.1529 | 3.0812 | 4.4463 | 4.4463 | 4.4463 | 4.4463 | 1.5718 | 3.1087 | 3.1087 | 3.1087 | 3.1087 | 3.1087 | 3.9641 | 5.1155 | 5.87 | 6.267 | 7.0611 | 7.8553 | 1.1355 | 2.2412 | 2.6894 | 2.6894 | 2.6894 | 2.6894 | 2.9722 | 3.4575 | 3.4575 | 3.4575 | 3.4575 | 3.4575
2020-01-15 17:00 | Summer | 1.7806 | 2.5484 | 3.6774 | 3.6774 | 3.6774 | 3.6774 | 1.4146 | 2.7978 | 2.7978 | 2.7978 | 2.7978 | 2.7978 | 4.0963 | 5.2862 | 6.0658 | 6.4761 | 7.2967 | 8.1173 | 1.1165 | 2.2036 | 2.6443 | 2.6443 | 2.6443 | 2.6443 | 2.7589 | 3.2094 | 3.2094 | 3.2094 | 3.2094 | 3.2094
2020-01-15 18:00 | Summer | 1.4677 | 2.1005 | 3.0311 | 3.0311 | 3.0311 | 3.0311 | 1.0946 | 2.1648 | 2.1648 | 2.1648 | 2.1648 | 2.1648 | 3.5582 | 4.5918 | 5.2689 | 5.6253 | 6.3381 | 7.051 | 1.1432 | 2.2562 | 2.7075 | 2.7075 | 2.7075 | 2.7075 | 1.8885 | 2.1968 | 2.1968 | 2.1968 | 2.1968 | 2.1968
2020-01-15 19:00 | Summer | 0.78115 | 1.118 | 1.6133 | 1.6133 | 1.6133 | 1.6133 | 0.88809 | 1.7564 | 1.7564 | 1.7564 | 1.7564 | 1.7564 | 3.1271 | 4.0355 | 4.6306 | 4.9438 | 5.5703 | 6.1967 | 1.1017 | 2.1743 | 2.6092 | 2.6092 | 2.6092 | 2.6092 | 1.2765 | 1.4849 | 1.4849 | 1.4849 | 1.4849 | 1.4849
2020-01-15 20:00 | Summer | 0.724 | 1.0362 | 1.4952 | 1.4952 | 1.4952 | 1.4952 | 0.84307 | 1.6674 | 1.6674 | 1.6674 | 1.6674 | 1.6674 | 2.8007 | 3.6143 | 4.1473 | 4.4278 | 4.9889 | 5.55 | 1.1089 | 2.1885 | 2.6262 | 2.6262 | 2.6262 | 2.6262 | 1.2194 | 1.4184 | 1.4184 | 1.4184 | 1.4184 | 1.4184
2020-01-15 21:00 | Summer | 0.66684 | 0.95435 | 1.3772 | 1.3772 | 1.3772 | 1.3772 | 0.68303 | 1.3509 | 1.3509 | 1.3509 | 1.3509 | 1.3509 | 2.7436 | 3.5405 | 4.0627 | 4.3375 | 4.8871 | 5.4367 | 1.1012 | 2.1735 | 2.6082 | 2.6082 | 2.6082 | 2.6082 | 1.1355 | 1.3209 | 1.3209 | 1.3209 | 1.3209 | 1.3209
2020-01-15 22:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.60913 | 1.2047 | 1.2047 | 1.2047 | 1.2047 | 1.2047 | 2.534 | 3.2701 | 3.7523 | 4.0061 | 4.5138 | 5.0214 | 1.1012 | 2.1735 | 2.6082 | 2.6082 | 2.6082 | 2.6082 | 1.0288 | 1.1968 | 1.1968 | 1.1968 | 1.1968 | 1.1968
2020-01-15 23:00 | Summer | 0.62777 | 0.89844 | 1.2965 | 1.2965 | 1.2965 | 1.2965 | 0.65159 | 1.2887 | 1.2887 | 1.2887 | 1.2887 | 1.2887 | 2.3435 | 3.0242 | 3.4702 | 3.7049 | 4.1744 | 4.6438 | 1.0326 | 2.0381 | 2.4457 | 2.4457 | 2.4457 | 2.4457 | 1.0288 | 1.1968 | 1.1968 | 1.1968 | 1.1968 | 1.1968
2020-01-16 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.56014 | 1.1078 | 1.1078 | 1.1078 | 1.1078 | 1.1078 | 2.1295 | 2.748 | 3.1533 | 3.3666 | 3.7932 | 4.2198 | 0.81164 | 1.6019 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 0.99073 | 1.1525 | 1.1525 | 1.1525 | 1.1525 | 1.1525
2020-01-16 01:00 | Summer | 0.59699 | 0.85438 | 1.2329 | 1.2329 | 1.2329 | 1.2329 | 0.57729 | 1.1417 | 1.1417 | 1.1417 | 1.1417 | 1.1417 | 2.0577 | 2.6554 | 3.047 | 3.2531 | 3.6653 | 4.0775 | 0.71637 | 1.4139 | 1.6967 | 1.6967 | 1.6967 | 1.6967 | 1.0288 | 1.1968 | 1.1968 | 1.1968 | 1.1968 | 1.1968
2020-01-16 02:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.59444 | 1.1756 | 1.1756 | 1.1756 | 1.1756 | 1.1756 | 2.0386 | 2.6308 | 3.0188 | 3.223 | 3.6314 | 4.0398 | 0.724 | 1.4289 | 1.7147 | 1.7147 | 1.7147 | 1.7147 | 0.97168 | 1.1303 | 1.1303 | 1.1303 | 1.1303 | 1.1303
2020-01-16 03:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.57157 | 1.1304 | 1.1304 | 1.1304 | 1.1304 | 1.1304 | 1.9815 | 2.557 | 2.9341 | 3.1326 | 3.5296 | 3.9265 | 0.67065 | 1.3236 | 1.5884 | 1.5884 | 1.5884 | 1.5884 | 0.99073 | 1.1525 | 1.1525 | 1.1525 | 1.1525 | 1.1525
2020-01-16 04:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.68017 | 1.3452 | 1.3452 | 1.3452 | 1.3452 | 1.3452 | 2.0386 | 2.6308 | 3.0188 | 3.223 | 3.6314 | 4.0398 | 0.67827 | 1.3387 | 1.6064 | 1.6064 | 1.6064 | 1.6064 | 1.105 | 1.2855 | 1.2855 | 1.2855 | 1.2855 | 1.2855
2020-01-16 05:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.67446 | 1.3339 | 1.3339 | 1.3339 | 1.3339 | 1.3339 | 2.1339 | 2.7537 | 3.1598 | 3.3736 | 3.8011 | 4.2285 | 0.99073 | 1.9554 | 2.3465 | 2.3465 | 2.3465 | 2.3465 | 1.2644 | 1.4708 | 1.4708 | 1.4708 | 1.4708 | 1.4708
2020-01-16 06:00 | Summer | 1.105 | 1.5815 | 2.2822 | 2.2822 | 2.2822 | 2.2822 | 0.92309 | 1.8256 | 1.8256 | 1.8256 | 1.8256 | 1.8256 | 2.2673 | 2.9258 | 3.3573 | 3.5844 | 4.0386 | 4.4928 | 1.1089 | 2.1885 | 2.6262 | 2.6262 | 2.6262 | 2.6262 | 1.4099 | 1.6401 | 1.6401 | 1.6401 | 1.6401 | 1.6401
2020-01-16 07:00 | Summer | 1.9243 | 2.754 | 3.9741 | 3.9741 | 3.9741 | 3.9741 | 1.1889 | 2.3513 | 2.3513 | 2.3513 | 2.3513 | 2.3513 | 3.2389 | 4.1798 | 4.7962 | 5.1206 | 5.7695 | 6.4183 | 1.2956 | 2.5571 | 3.0685 | 3.0685 | 3.0685 | 3.0685 | 2.0382 | 2.3709 | 2.3709 | 2.3709 | 2.3709 | 2.3709
2020-01-16 08:00 | Summer | 2.1529 | 3.0812 | 4.4463 | 4.4463 | 4.4463 | 4.4463 | 1.4547 | 2.877 | 2.877 | 2.877 | 2.877 | 2.877 | 3.4095 | 4.3999 | 5.0487 | 5.3902 | 6.0732 | 6.7563 | 1.2575 | 2.4818 | 2.9782 | 2.9782 | 2.9782 | 2.9782 | 2.7436 | 3.1915 | 3.1915 | 3.1915 | 3.1915 | 3.1915
2020-01-16 09:00 | Summer | 2.1148 | 3.0267 | 4.3676 | 4.3676 | 4.3676 | 4.3676 | 1.6376 | 3.2387 | 3.2387 | 3.2387 | 3.2387 | 3.2387 | 3.5628 | 4.5978 | 5.2758 | 5.6327 | 6.3464 | 7.0602 | 1.1927 | 2.354 | 2.8248 | 2.8248 | 2.8248 | 2.8248 | 2.8198 | 3.2802 | 3.2802 | 3.2802 | 3.2802 | 3.2802
2020-01-16 10:00 | Summer | 2.2863 | 3.2721 | 4.7217 | 4.7217 | 4.7217 | 4.7217 | 1.6719 | 3.3065 | 3.3065 | 3.3065 | 3.3065 | 3.3065 | 3.6962 | 4.7699 | 5.4733 | 5.8435 | 6.584 | 7.3244 | 1.2194 | 2.4066 | 2.888 | 2.888 | 2.888 | 2.888 | 2.9341 | 3.4131 | 3.4131 | 3.4131 | 3.4131 | 3.4131
2020-01-16 11:00 | Summer | 2.2244 | 3.1835 | 4.5938 | 4.5938 | 4.5938 | 4.5938 | 1.5375 | 3.0409 | 3.0409 | 3.0409 | 3.0409 | 3.0409 | 3.8677 | 4.9911 | 5.7272 | 6.1146 | 6.8894 | 7.6642 | 1.1927 | 2.354 | 2.8248 | 2.8248 | 2.8248 | 2.8248 | 3.0103 | 3.5018 | 3.5018 | 3.5018 | 3.5018 | 3.5018
2020-01-16 12:00 | Summer | 2.172 | 3.1085 | 4.4856 | 4.4856 | 4.4856 | 4.4856 | 1.5261 | 3.0183 | 3.0183 | 3.0183 | 3.0183 | 3.0183 | 3.9439 | 5.0895 | 5.8401 | 6.2351 | 7.0252 | 7.8153 | 1.1892 | 2.3471 | 2.8165 | 2.8165 | 2.8165 | 2.8165 | 3.0103 | 3.5018 | 3.5018 | 3.5018 | 3.5018 | 3.5018
2020-01-16 13:00 | Summer | 2.1532 | 3.0815 | 4.4468 | 4.4468 | 4.4468 | 4.4468 | 1.6261 | 3.2161 | 3.2161 | 3.2161 | 3.2161 | 3.2161 | 3.982 | 5.1387 | 5.8965 | 6.2953 | 7.0931 | 7.8908 | 1.2232 | 2.4142 | 2.897 | 2.897 | 2.897 | 2.897 | 2.9341 | 3.4131 | 3.4131 | 3.4131 | 3.4131 | 3.4131
2020-01-16 14:00 | Summer | 1.829 | 2.6177 | 3.7774 | 3.7774 | 3.7774 | 3.7774 | 1.4518 | 2.8713 | 2.8713 | 2.8713 | 2.8713 | 2.8713 | 3.6506 | 4.711 | 5.4058 | 5.7714 | 6.5028 | 7.2341 | 1.1622 | 2.2938 | 2.7526 | 2.7526 | 2.7526 | 2.7526 | 2.896 | 3.3688 | 3.3688 | 3.3688 | 3.3688 | 3.3688
2020-01-16 15:00 | Summer | 1.9434 | 2.7813 | 4.0135 | 4.0135 | 4.0135 | 4.0135 | 1.6061 | 3.1765 | 3.1765 | 3.1765 | 3.1765 | 3.1765 | 3.7534 | 4.8436 | 5.5579 | 5.9339 | 6.6858 | 7.4377 | 1.1622 | 2.2938 | 2.7526 | 2.7526 | 2.7526 | 2.7526 | 2.9341 | 3.4131 | 3.4131 | 3.4131 | 3.4131 | 3.4131
2020-01-16 16:00 | Summer | 1.9624 | 2.8085 | 4.0528 | 4.0528 | 4.0528 | 4.0528 | 1.4834 | 2.9338 | 2.9338 | 2.9338 | 2.9338 | 2.9338 | 3.7271 | 4.8097 | 5.5191 | 5.8924 | 6.639 | 7.3857 | 1.227 | 2.4217 | 2.906 | 2.906 | 2.906 | 2.906 | 2.8198 | 3.2802 | 3.2802 | 3.2802 | 3.2802 | 3.2802
2020-01-16 17:00 | Summer | 1.7147 | 2.4541 | 3.5413 | 3.5413 | 3.5413 | 3.5413 | 1.246 | 2.4643 | 2.4643 | 2.4643 | 2.4643 | 2.4643 | 3.5819 | 4.6223 | 5.304 | 5.6628 | 6.3804 | 7.0979 | 1.2003 | 2.369 | 2.8428 | 2.8428 | 2.8428 | 2.8428 | 2.6111 | 3.0374 | 3.0374 | 3.0374 | 3.0374 | 3.0374
2020-01-16 18:00 | Summer | 1.1185 | 1.6007 | 2.3099 | 2.3099 | 2.3099 | 2.3099 | 0.89465 | 1.7694 | 1.7694 | 1.7694 | 1.7694 | 1.7694 | 3.0094 | 3.8835 | 4.4563 | 4.7577 | 5.3606 | 5.9634 | 1.1173 | 2.2052 | 2.6462 | 2.6462 | 2.6462 | 2.6462 | 1.7336 | 2.0166 | 2.0166 | 2.0166 | 2.0166 | 2.0166
2020-01-16 19:00 | Summer | 0.87642 | 1.2543 | 1.81 | 1.81 | 1.81 | 1.81 | 0.65204 | 1.2896 | 1.2896 | 1.2896 | 1.2896 | 1.2896 | 2.7626 | 3.5651 | 4.0909 | 4.3676 | 4.921 | 5.4745 | 0.99454 | 1.9629 | 2.3555 | 2.3555 | 2.3555 | 2.3555 | 1.2003 | 1.3963 | 1.3963 | 1.3963 | 1.3963 | 1.3963
2020-01-16 20:00 | Summer | 0.80021 | 1.1452 | 1.6526 | 1.6526 | 1.6526 | 1.6526 | 0.59729 | 1.1813 | 1.1813 | 1.1813 | 1.1813 | 1.1813 | 2.5149 | 3.2455 | 3.7241 | 3.976 | 4.4798 | 4.9836 | 1.0288 | 2.0306 | 2.4367 | 2.4367 | 2.4367 | 2.4367 | 1.2384 | 1.4406 | 1.4406 | 1.4406 | 1.4406 | 1.4406
2020-01-16 21:00 | Summer | 0.74305 | 1.0634 | 1.5346 | 1.5346 | 1.5346 | 1.5346 | 0.6373 | 1.2604 | 1.2604 | 1.2604 | 1.2604 | 1.2604 | 2.3919 | 3.0867 | 3.5419 | 3.7815 | 4.2607 | 4.7399 | 1.0669 | 2.1058 | 2.527 | 2.527 | 2.527 | 2.527 | 1.0479 | 1.219 | 1.219 | 1.219 | 1.219 | 1.219
2020-01-16 22:00 | Summer | 0.59078 | 0.84551 | 1.2201 | 1.2201 | 1.2201 | 1.2201 | 0.55728 | 1.1022 | 1.1022 | 1.1022 | 1.1022 | 1.1022 | 2.3244 | 2.9996 | 3.442 | 3.6748 | 4.1404 | 4.6061 | 0.98692 | 1.9479 | 2.3374 | 2.3374 | 2.3374 | 2.3374 | 1.0098 | 1.1746 | 1.1746 | 1.1746 | 1.1746 | 1.1746
2020-01-16 23:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.49155 | 0.97217 | 0.97217 | 0.97217 | 0.97217 | 0.97217 | 2.197 | 2.8351 | 3.2533 | 3.4733 | 3.9134 | 4.3535 | 0.89547 | 1.7674 | 2.1208 | 2.1208 | 2.1208 | 2.1208 | 0.97168 | 1.1303 | 1.1303 | 1.1303 | 1.1303 | 1.1303
2020-01-17 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.48012 | 0.94956 | 0.94956 | 0.94956 | 0.94956 | 0.94956 | 2.0386 | 2.6308 | 3.0188 | 3.223 | 3.6314 | 4.0398 | 0.66684 | 1.3161 | 1.5794 | 1.5794 | 1.5794 | 1.5794 | 0.97168 | 1.1303 | 1.1303 | 1.1303 | 1.1303 | 1.1303
2020-01-17 01:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.49362 | 0.97626 | 0.97626 | 0.97626 | 0.97626 | 0.97626 | 1.9323 | 2.4936 | 2.8613 | 3.0549 | 3.442 | 3.8291 | 0.66303 | 1.3086 | 1.5703 | 1.5703 | 1.5703 | 1.5703 | 0.95263 | 1.1082 | 1.1082 | 1.1082 | 1.1082 | 1.1082
2020-01-17 02:00 | Summer | 0.59014 | 0.84459 | 1.2188 | 1.2188 | 1.2188 | 1.2188 | 0.50013 | 0.98912 | 0.98912 | 0.98912 | 0.98912 | 0.98912 | 1.9243 | 2.4833 | 2.8495 | 3.0422 | 3.4277 | 3.8132 | 0.6173 | 1.2184 | 1.462 | 1.462 | 1.462 | 1.462 | 0.95263 | 1.1082 | 1.1082 | 1.1082 | 1.1082 | 1.1082
2020-01-17 03:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.54299 | 1.0739 | 1.0739 | 1.0739 | 1.0739 | 1.0739 | 1.9053 | 2.4587 | 2.8213 | 3.0121 | 3.3938 | 3.7755 | 0.59444 | 1.1732 | 1.4079 | 1.4079 | 1.4079 | 1.4079 | 0.95263 | 1.1082 | 1.1082 | 1.1082 | 1.1082 | 1.1082
2020-01-17 04:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.5087 | 1.0061 | 1.0061 | 1.0061 | 1.0061 | 1.0061 | 2.0005 | 2.5816 | 2.9624 | 3.1627 | 3.5635 | 3.9643 | 0.6173 | 1.2184 | 1.462 | 1.462 | 1.462 | 1.462 | 1.0672 | 1.2414 | 1.2414 | 1.2414 | 1.2414 | 1.2414
2020-01-17 05:00 | Summer | 0.72391 | 1.036 | 1.495 | 1.495 | 1.495 | 1.495 | 0.57157 | 1.1304 | 1.1304 | 1.1304 | 1.1304 | 1.1304 | 2.0571 | 2.6546 | 3.0461 | 3.2522 | 3.6643 | 4.0764 | 0.89166 | 1.7599 | 2.1118 | 2.1118 | 2.1118 | 2.1118 | 1.2575 | 1.4628 | 1.4628 | 1.4628 | 1.4628 | 1.4628
2020-01-17 06:00 | Summer | 0.88145 | 1.2615 | 1.8204 | 1.8204 | 1.8204 | 1.8204 | 0.78591 | 1.5543 | 1.5543 | 1.5543 | 1.5543 | 1.5543 | 2.172 | 2.8029 | 3.2163 | 3.4338 | 3.8689 | 4.3041 | 1.025 | 2.0231 | 2.4277 | 2.4277 | 2.4277 | 2.4277 | 1.4323 | 1.6661 | 1.6661 | 1.6661 | 1.6661 | 1.6661
2020-01-17 07:00 | Summer | 1.5542 | 2.2243 | 3.2098 | 3.2098 | 3.2098 | 3.2098 | 0.92595 | 1.8313 | 1.8313 | 1.8313 | 1.8313 | 1.8313 | 2.7436 | 3.5405 | 4.0627 | 4.3375 | 4.8871 | 5.4367 | 1.2346 | 2.4367 | 2.9241 | 2.9241 | 2.9241 | 2.9241 | 1.9253 | 2.2396 | 2.2396 | 2.2396 | 2.2396 | 2.2396
2020-01-17 08:00 | Summer | 1.6521 | 2.3645 | 3.412 | 3.412 | 3.412 | 3.412 | 1.0803 | 2.1365 | 2.1365 | 2.1365 | 2.1365 | 2.1365 | 3.3151 | 4.2781 | 4.909 | 5.2411 | 5.9052 | 6.5693 | 1.147 | 2.2637 | 2.7165 | 2.7165 | 2.7165 | 2.7165 | 2.4006 | 2.7926 | 2.7926 | 2.7926 | 2.7926 | 2.7926
2020-01-17 09:00 | Summer | 1.7338 | 2.4813 | 3.5806 | 3.5806 | 3.5806 | 3.5806 | 1.1117 | 2.1987 | 2.1987 | 2.1987 | 2.1987 | 2.1987 | 3.1056 | 4.0077 | 4.5987 | 4.9098 | 5.5319 | 6.154 | 1.1165 | 2.2036 | 2.6443 | 2.6443 | 2.6443 | 2.6443 | 2.3435 | 2.7261 | 2.7261 | 2.7261 | 2.7261 | 2.7261
2020-01-17 10:00 | Summer | 1.7719 | 2.5359 | 3.6593 | 3.6593 | 3.6593 | 3.6593 | 1.1717 | 2.3174 | 2.3174 | 2.3174 | 2.3174 | 2.3174 | 3.277 | 4.2289 | 4.8526 | 5.1809 | 5.8373 | 6.4938 | 1.1012 | 2.1735 | 2.6082 | 2.6082 | 2.6082 | 2.6082 | 2.5149 | 2.9255 | 2.9255 | 2.9255 | 2.9255 | 2.9255
2020-01-17 11:00 | Summer | 1.7532 | 2.5091 | 3.6208 | 3.6208 | 3.6208 | 3.6208 | 1.1403 | 2.2552 | 2.2552 | 2.2552 | 2.2552 | 2.2552 | 3.277 | 4.2289 | 4.8526 | 5.1809 | 5.8373 | 6.4938 | 1.1355 | 2.2412 | 2.6894 | 2.6894 | 2.6894 | 2.6894 | 2.553 | 2.9699 | 2.9699 | 2.9699 | 2.9699 | 2.9699
2020-01-17 12:00 | Summer | 1.6766 | 2.3995 | 3.4626 | 3.4626 | 3.4626 | 3.4626 | 1.1832 | 2.34 | 2.34 | 2.34 | 2.34 | 2.34 | 3.2389 | 4.1798 | 4.7962 | 5.1206 | 5.7695 | 6.4183 | 1.1355 | 2.2412 | 2.6894 | 2.6894 | 2.6894 | 2.6894 | 2.5911 | 3.0142 | 3.0142 | 3.0142 | 3.0142 | 3.0142
2020-01-17 13:00 | Summer | 1.7338 | 2.4813 | 3.5806 | 3.5806 | 3.5806 | 3.5806 | 1.2346 | 2.4417 | 2.4417 | 2.4417 | 2.4417 | 2.4417 | 3.5438 | 4.5732 | 5.2476 | 5.6026 | 6.3125 | 7.0224 | 1.1203 | 2.2111 | 2.6533 | 2.6533 | 2.6533 | 2.6533 | 2.534 | 2.9477 | 2.9477 | 2.9477 | 2.9477 | 2.9477
2020-01-17 14:00 | Summer | 1.6957 | 2.4268 | 3.5019 | 3.5019 | 3.5019 | 3.5019 | 1.2718 | 2.5152 | 2.5152 | 2.5152 | 2.5152 | 2.5152 | 3.391 | 4.376 | 5.0213 | 5.361 | 6.0403 | 6.7196 | 1.1241 | 2.2186 | 2.6623 | 2.6623 | 2.6623 | 2.6623 | 2.6102 | 3.0364 | 3.0364 | 3.0364 | 3.0364 | 3.0364
2020-01-17 15:00 | Summer | 1.7147 | 2.4541 | 3.5413 | 3.5413 | 3.5413 | 3.5413 | 1.375 | 2.7194 | 2.7194 | 2.7194 | 2.7194 | 2.7194 | 3.4676 | 4.4748 | 5.1347 | 5.4821 | 6.1767 | 6.8714 | 1.0936 | 2.1585 | 2.5901 | 2.5901 | 2.5901 | 2.5901 | 2.5911 | 3.0142 | 3.0142 | 3.0142 | 3.0142 | 3.0142
2020-01-17 16:00 | Summer | 1.6766 | 2.3995 | 3.4626 | 3.4626 | 3.4626 | 3.4626 | 1.3775 | 2.7243 | 2.7243 | 2.7243 | 2.7243 | 2.7243 | 3.4295 | 4.4256 | 5.0783 | 5.4218 | 6.1088 | 6.7959 | 1.0784 | 2.1284 | 2.554 | 2.554 | 2.554 | 2.554 | 2.553 | 2.9699 | 2.9699 | 2.9699 | 2.9699 | 2.9699
2020-01-17 17:00 | Summer | 1.5433 | 2.2086 | 3.1872 | 3.1872 | 3.1872 | 3.1872 | 1.3118 | 2.5943 | 2.5943 | 2.5943 | 2.5943 | 2.5943 | 3.2961 | 4.2535 | 4.8808 | 5.211 | 5.8713 | 6.5316 | 1.0974 | 2.166 | 2.5992 | 2.5992 | 2.5992 | 2.5992 | 2.2974 | 2.6725 | 2.6725 | 2.6725 | 2.6725 | 2.6725
2020-01-17 18:00 | Summer | 1.0108 | 1.4466 | 2.0874 | 2.0874 | 2.0874 | 2.0874 | 0.98628 | 1.9506 | 1.9506 | 1.9506 | 1.9506 | 1.9506 | 3.176 | 4.0986 | 4.703 | 5.0212 | 5.6574 | 6.2937 | 0.97549 | 1.9253 | 2.3104 | 2.3104 | 2.3104 | 2.3104 | 1.7423 | 2.0268 | 2.0268 | 2.0268 | 2.0268 | 2.0268
2020-01-17 19:00 | Summer | 0.70494 | 1.0089 | 1.4559 | 1.4559 | 1.4559 | 1.4559 | 0.70323 | 1.3908 | 1.3908 | 1.3908 | 1.3908 | 1.3908 | 2.7006 | 3.4851 | 3.9991 | 4.2696 | 4.8106 | 5.3516 | 1.0212 | 2.0156 | 2.4187 | 2.4187 | 2.4187 | 2.4187 | 1.2003 | 1.3963 | 1.3963 | 1.3963 | 1.3963 | 1.3963
2020-01-17 20:00 | Summer | 0.66684 | 0.95435 | 1.3772 | 1.3772 | 1.3772 | 1.3772 | 0.59493 | 1.1766 | 1.1766 | 1.1766 | 1.1766 | 1.1766 | 2.4197 | 3.1225 | 3.583 | 3.8254 | 4.3101 | 4.7949 | 1.0174 | 2.008 | 2.4096 | 2.4096 | 2.4096 | 2.4096 | 1.1241 | 1.3076 | 1.3076 | 1.3076 | 1.3076 | 1.3076
2020-01-17 21:00 | Summer | 0.59067 | 0.84534 | 1.2199 | 1.2199 | 1.2199 | 1.2199 | 0.48584 | 0.96086 | 0.96086 | 0.96086 | 0.96086 | 0.96086 | 2.4138 | 3.115 | 3.5744 | 3.8162 | 4.2997 | 4.7833 | 0.95644 | 1.8877 | 2.2652 | 2.2652 | 2.2652 | 2.2652 | 1.0479 | 1.219 | 1.219 | 1.219 | 1.219 | 1.219
2020-01-17 22:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.563 | 1.1135 | 1.1135 | 1.1135 | 1.1135 | 1.1135 | 2.2673 | 2.9258 | 3.3573 | 3.5844 | 4.0386 | 4.4928 | 0.91452 | 1.805 | 2.166 | 2.166 | 2.166 | 2.166 | 1.0098 | 1.1746 | 1.1746 | 1.1746 | 1.1746 | 1.1746
2020-01-17 23:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.47155 | 0.9326 | 0.9326 | 0.9326 | 0.9326 | 0.9326 | 2.1148 | 2.7291 | 3.1316 | 3.3435 | 3.7671 | 4.1908 | 0.87642 | 1.7298 | 2.0757 | 2.0757 | 2.0757 | 2.0757 | 0.93358 | 1.086 | 1.086 | 1.086 | 1.086 | 1.086
2020-01-18 | Summer | 0.58786 | 0.84133 | 1.2141 | 1.2141 | 1.2141 | 1.2141 | 0.44011 | 0.87043 | 0.87043 | 0.87043 | 0.87043 | 0.87043 | 1.8877 | 2.436 | 2.7953 | 2.9844 | 3.3625 | 3.7407 | 0.60587 | 1.1958 | 1.435 | 1.435 | 1.435 | 1.435 | 0.91452 | 1.0638 | 1.0638 | 1.0638 | 1.0638 | 1.0638
2020-01-18 01:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.42011 | 0.83086 | 0.83086 | 0.83086 | 0.83086 | 0.83086 | 1.9053 | 2.4587 | 2.8213 | 3.0121 | 3.3938 | 3.7755 | 0.60968 | 1.2033 | 1.444 | 1.444 | 1.444 | 1.444 | 0.93358 | 1.086 | 1.086 | 1.086 | 1.086 | 1.086
2020-01-18 02:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.47726 | 0.94391 | 0.94391 | 0.94391 | 0.94391 | 0.94391 | 1.8559 | 2.395 | 2.7482 | 2.9341 | 3.3058 | 3.6776 | 0.63635 | 1.256 | 1.5072 | 1.5072 | 1.5072 | 1.5072 | 0.89547 | 1.0417 | 1.0417 | 1.0417 | 1.0417 | 1.0417
2020-01-18 03:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.41439 | 0.81956 | 0.81956 | 0.81956 | 0.81956 | 0.81956 | 1.8672 | 2.4095 | 2.7649 | 2.9519 | 3.3259 | 3.7 | 0.5792 | 1.1431 | 1.3718 | 1.3718 | 1.3718 | 1.3718 | 0.87642 | 1.0195 | 1.0195 | 1.0195 | 1.0195 | 1.0195
2020-01-18 04:00 | Summer | 0.55252 | 0.79075 | 1.1411 | 1.1411 | 1.1411 | 1.1411 | 0.41697 | 0.82467 | 0.82467 | 0.82467 | 0.82467 | 0.82467 | 1.829 | 2.3603 | 2.7084 | 2.8916 | 3.2581 | 3.6245 | 0.57157 | 1.1281 | 1.3537 | 1.3537 | 1.3537 | 1.3537 | 0.89547 | 1.0417 | 1.0417 | 1.0417 | 1.0417 | 1.0417
2020-01-18 05:00 | Summer | 0.55252 | 0.79075 | 1.1411 | 1.1411 | 1.1411 | 1.1411 | 0.43154 | 0.85347 | 0.85347 | 0.85347 | 0.85347 | 0.85347 | 1.8481 | 2.3849 | 2.7366 | 2.9218 | 3.292 | 3.6622 | 0.85277 | 1.6831 | 2.0197 | 2.0197 | 2.0197 | 2.0197 | 0.89547 | 1.0417 | 1.0417 | 1.0417 | 1.0417 | 1.0417
2020-01-18 06:00 | Summer | 0.724 | 1.0362 | 1.4952 | 1.4952 | 1.4952 | 1.4952 | 0.53652 | 1.0611 | 1.0611 | 1.0611 | 1.0611 | 1.0611 | 1.8862 | 2.4341 | 2.7931 | 2.982 | 3.3599 | 3.7377 | 0.94119 | 1.8576 | 2.2291 | 2.2291 | 2.2291 | 2.2291 | 0.95263 | 1.1082 | 1.1082 | 1.1082 | 1.1082 | 1.1082
2020-01-18 07:00 | Summer | 0.72028 | 1.0308 | 1.4875 | 1.4875 | 1.4875 | 1.4875 | 0.68303 | 1.3509 | 1.3509 | 1.3509 | 1.3509 | 1.3509 | 2.1612 | 2.789 | 3.2003 | 3.4167 | 3.8497 | 4.2826 | 0.89928 | 1.7749 | 2.1299 | 2.1299 | 2.1299 | 2.1299 | 1.086 | 1.2633 | 1.2633 | 1.2633 | 1.2633 | 1.2633
2020-01-18 08:00 | Summer | 0.74305 | 1.0634 | 1.5346 | 1.5346 | 1.5346 | 1.5346 | 0.65445 | 1.2943 | 1.2943 | 1.2943 | 1.2943 | 1.2943 | 2.2863 | 2.9504 | 3.3855 | 3.6146 | 4.0726 | 4.5306 | 0.86498 | 1.7072 | 2.0486 | 2.0486 | 2.0486 | 2.0486 | 1.1174 | 1.2999 | 1.2999 | 1.2999 | 1.2999 | 1.2999
2020-01-18 09:00 | Summer | 0.724 | 1.0362 | 1.4952 | 1.4952 | 1.4952 | 1.4952 | 0.71733 | 1.4187 | 1.4187 | 1.4187 | 1.4187 | 1.4187 | 2.3625 | 3.0488 | 3.4984 | 3.735 | 4.2083 | 4.6816 | 0.91833 | 1.8125 | 2.175 | 2.175 | 2.175 | 2.175 | 1.1622 | 1.352 | 1.352 | 1.352 | 1.352 | 1.352
2020-01-18 10:00 | Summer | 0.55252 | 0.79075 | 1.1411 | 1.1411 | 1.1411 | 1.1411 | 0.73733 | 1.4583 | 1.4583 | 1.4583 | 1.4583 | 1.4583 | 2.4387 | 3.1471 | 3.6112 | 3.8555 | 4.3441 | 4.8326 | 0.9793 | 1.9328 | 2.3194 | 2.3194 | 2.3194 | 2.3194 | 1.2003 | 1.3963 | 1.3963 | 1.3963 | 1.3963 | 1.3963
2020-01-18 11:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.7459 | 1.4752 | 1.4752 | 1.4752 | 1.4752 | 1.4752 | 2.4578 | 3.1717 | 3.6395 | 3.8856 | 4.378 | 4.8704 | 0.88404 | 1.7448 | 2.0938 | 2.0938 | 2.0938 | 2.0938 | 1.2194 | 1.4184 | 1.4184 | 1.4184 | 1.4184 | 1.4184
2020-01-18 12:00 | Summer | 0.49537 | 0.70895 | 1.023 | 1.023 | 1.023 | 1.023 | 0.83164 | 1.6448 | 1.6448 | 1.6448 | 1.6448 | 1.6448 | 2.7055 | 3.4913 | 4.0062 | 4.2772 | 4.8192 | 5.3612 | 0.93738 | 1.8501 | 2.2201 | 2.2201 | 2.2201 | 2.2201 | 1.2575 | 1.4628 | 1.4628 | 1.4628 | 1.4628 | 1.4628
2020-01-18 13:00 | Summer | 0.51442 | 0.73622 | 1.0624 | 1.0624 | 1.0624 | 1.0624 | 0.84879 | 1.6787 | 1.6787 | 1.6787 | 1.6787 | 1.6787 | 2.6711 | 3.447 | 3.9554 | 4.223 | 4.7581 | 5.2932 | 0.91833 | 1.8125 | 2.175 | 2.175 | 2.175 | 2.175 | 1.1813 | 1.3741 | 1.3741 | 1.3741 | 1.3741 | 1.3741
2020-01-18 14:00 | Summer | 0.45699 | 0.65403 | 0.94379 | 0.94379 | 0.94379 | 0.94379 | 0.87165 | 1.7239 | 1.7239 | 1.7239 | 1.7239 | 1.7239 | 2.7245 | 3.5159 | 4.0344 | 4.3073 | 4.8531 | 5.3989 | 0.96406 | 1.9027 | 2.2833 | 2.2833 | 2.2833 | 2.2833 | 1.1432 | 1.3298 | 1.3298 | 1.3298 | 1.3298 | 1.3298
2020-01-18 15:00 | Summer | 0.48015 | 0.68717 | 0.99161 | 0.99161 | 0.99161 | 0.99161 | 0.78306 | 1.5487 | 1.5487 | 1.5487 | 1.5487 | 1.5487 | 2.7436 | 3.5405 | 4.0627 | 4.3375 | 4.8871 | 5.4367 | 0.96406 | 1.9027 | 2.2833 | 2.2833 | 2.2833 | 2.2833 | 1.1622 | 1.352 | 1.352 | 1.352 | 1.352 | 1.352
2020-01-18 16:00 | Summer | 0.66684 | 0.95435 | 1.3772 | 1.3772 | 1.3772 | 1.3772 | 0.75734 | 1.4978 | 1.4978 | 1.4978 | 1.4978 | 1.4978 | 2.7245 | 3.5159 | 4.0344 | 4.3073 | 4.8531 | 5.3989 | 0.95263 | 1.8802 | 2.2562 | 2.2562 | 2.2562 | 2.2562 | 1.1622 | 1.352 | 1.352 | 1.352 | 1.352 | 1.352
2020-01-18 17:00 | Summer | 0.66684 | 0.95435 | 1.3772 | 1.3772 | 1.3772 | 1.3772 | 0.76877 | 1.5204 | 1.5204 | 1.5204 | 1.5204 | 1.5204 | 2.5721 | 3.3192 | 3.8087 | 4.0664 | 4.5816 | 5.0969 | 1.0212 | 2.0156 | 2.4187 | 2.4187 | 2.4187 | 2.4187 | 1.1622 | 1.352 | 1.352 | 1.352 | 1.352 | 1.352
2020-01-18 18:00 | Summer | 0.59468 | 0.85109 | 1.2282 | 1.2282 | 1.2282 | 1.2282 | 0.78877 | 1.56 | 1.56 | 1.56 | 1.56 | 1.56 | 2.6293 | 3.393 | 3.8934 | 4.1567 | 4.6835 | 5.2102 | 0.97549 | 1.9253 | 2.3104 | 2.3104 | 2.3104 | 2.3104 | 1.1432 | 1.3298 | 1.3298 | 1.3298 | 1.3298 | 1.3298
2020-01-18 19:00 | Summer | 0.56679 | 0.81117 | 1.1706 | 1.1706 | 1.1706 | 1.1706 | 0.62016 | 1.2265 | 1.2265 | 1.2265 | 1.2265 | 1.2265 | 2.4387 | 3.1471 | 3.6112 | 3.8555 | 4.3441 | 4.8326 | 0.98311 | 1.9403 | 2.3284 | 2.3284 | 2.3284 | 2.3284 | 1.1432 | 1.3298 | 1.3298 | 1.3298 | 1.3298 | 1.3298
2020-01-18 20:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.60873 | 1.2039 | 1.2039 | 1.2039 | 1.2039 | 1.2039 | 2.3435 | 3.0242 | 3.4702 | 3.7049 | 4.1744 | 4.6438 | 0.94882 | 1.8727 | 2.2472 | 2.2472 | 2.2472 | 2.2472 | 1.086 | 1.2633 | 1.2633 | 1.2633 | 1.2633 | 1.2633
2020-01-18 21:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.563 | 1.1135 | 1.1135 | 1.1135 | 1.1135 | 1.1135 | 2.3625 | 3.0488 | 3.4984 | 3.735 | 4.2083 | 4.6816 | 0.97168 | 1.9178 | 2.3013 | 2.3013 | 2.3013 | 2.3013 | 1.0288 | 1.1968 | 1.1968 | 1.1968 | 1.1968 | 1.1968
2020-01-18 22:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.49441 | 0.97782 | 0.97782 | 0.97782 | 0.97782 | 0.97782 | 2.191 | 2.8275 | 3.2445 | 3.4639 | 3.9029 | 4.3418 | 0.92214 | 1.82 | 2.184 | 2.184 | 2.184 | 2.184 | 0.97168 | 1.1303 | 1.1303 | 1.1303 | 1.1303 | 1.1303
2020-01-18 23:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.43154 | 0.85347 | 0.85347 | 0.85347 | 0.85347 | 0.85347 | 2.1178 | 2.733 | 3.136 | 3.3481 | 3.7724 | 4.1967 | 0.92595 | 1.8275 | 2.193 | 2.193 | 2.193 | 2.193 | 0.93358 | 1.086 | 1.086 | 1.086 | 1.086 | 1.086
2020-01-19 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.53156 | 1.0513 | 1.0513 | 1.0513 | 1.0513 | 1.0513 | 1.8862 | 2.4341 | 2.7931 | 2.982 | 3.3599 | 3.7377 | 0.70875 | 1.3989 | 1.6786 | 1.6786 | 1.6786 | 1.6786 | 0.9691 | 1.1273 | 1.1273 | 1.1273 | 1.1273 | 1.1273
2020-01-19 01:00 | Summer | 0.57154 | 0.81797 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.48298 | 0.95521 | 0.95521 | 0.95521 | 0.95521 | 0.95521 | 1.8481 | 2.3849 | 2.7366 | 2.9218 | 3.292 | 3.6622 | 0.63254 | 1.2484 | 1.4981 | 1.4981 | 1.4981 | 1.4981 | 0.97168 | 1.1303 | 1.1303 | 1.1303 | 1.1303 | 1.1303
2020-01-19 02:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.40296 | 0.79695 | 0.79695 | 0.79695 | 0.79695 | 0.79695 | 1.81 | 2.3358 | 2.6802 | 2.8615 | 3.2241 | 3.5867 | 0.62111 | 1.2259 | 1.4711 | 1.4711 | 1.4711 | 1.4711 | 0.85737 | 0.99734 | 0.99734 | 0.99734 | 0.99734 | 0.99734
2020-01-19 03:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.37724 | 0.74608 | 0.74608 | 0.74608 | 0.74608 | 0.74608 | 1.7338 | 2.2374 | 2.5674 | 2.741 | 3.0884 | 3.4357 | 0.59444 | 1.1732 | 1.4079 | 1.4079 | 1.4079 | 1.4079 | 0.85737 | 0.99734 | 0.99734 | 0.99734 | 0.99734 | 0.99734
2020-01-19 04:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.39153 | 0.77434 | 0.77434 | 0.77434 | 0.77434 | 0.77434 | 1.7719 | 2.2866 | 2.6238 | 2.8013 | 3.1562 | 3.5112 | 0.62111 | 1.2259 | 1.4711 | 1.4711 | 1.4711 | 1.4711 | 0.83821 | 0.97506 | 0.97506 | 0.97506 | 0.97506 | 0.97506
2020-01-19 05:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.41725 | 0.82521 | 0.82521 | 0.82521 | 0.82521 | 0.82521 | 1.8481 | 2.3849 | 2.7366 | 2.9218 | 3.292 | 3.6622 | 0.81926 | 1.617 | 1.9403 | 1.9403 | 1.9403 | 1.9403 | 0.87642 | 1.0195 | 1.0195 | 1.0195 | 1.0195 | 1.0195
2020-01-19 06:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.50013 | 0.98912 | 0.98912 | 0.98912 | 0.98912 | 0.98912 | 1.8862 | 2.4341 | 2.7931 | 2.982 | 3.3599 | 3.7377 | 0.92976 | 1.8351 | 2.2021 | 2.2021 | 2.2021 | 2.2021 | 0.87642 | 1.0195 | 1.0195 | 1.0195 | 1.0195 | 1.0195
2020-01-19 07:00 | Summer | 0.55252 | 0.79075 | 1.1411 | 1.1411 | 1.1411 | 1.1411 | 0.5087 | 1.0061 | 1.0061 | 1.0061 | 1.0061 | 1.0061 | 2.1339 | 2.7537 | 3.1598 | 3.3736 | 3.8011 | 4.2285 | 0.92214 | 1.82 | 2.184 | 2.184 | 2.184 | 2.184 | 0.85737 | 0.99734 | 0.99734 | 0.99734 | 0.99734 | 0.99734
2020-01-19 08:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.5287 | 1.0456 | 1.0456 | 1.0456 | 1.0456 | 1.0456 | 2.4006 | 3.098 | 3.5548 | 3.7953 | 4.2762 | 4.7571 | 0.91071 | 1.7975 | 2.1569 | 2.1569 | 2.1569 | 2.1569 | 0.93358 | 1.086 | 1.086 | 1.086 | 1.086 | 1.086
2020-01-19 09:00 | Summer | 0.53347 | 0.76348 | 1.1017 | 1.1017 | 1.1017 | 1.1017 | 0.563 | 1.1135 | 1.1135 | 1.1135 | 1.1135 | 1.1135 | 2.4387 | 3.1471 | 3.6112 | 3.8555 | 4.3441 | 4.8326 | 0.94501 | 1.8651 | 2.2382 | 2.2382 | 2.2382 | 2.2382 | 1.0098 | 1.1746 | 1.1746 | 1.1746 | 1.1746 | 1.1746
2020-01-19 10:00 | Summer | 0.55252 | 0.79075 | 1.1411 | 1.1411 | 1.1411 | 1.1411 | 0.65731 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 2.6293 | 3.393 | 3.8934 | 4.1567 | 4.6835 | 5.2102 | 0.91071 | 1.7975 | 2.1569 | 2.1569 | 2.1569 | 2.1569 | 1.0288 | 1.1968 | 1.1968 | 1.1968 | 1.1968 | 1.1968
2020-01-19 11:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.66874 | 1.3226 | 1.3226 | 1.3226 | 1.3226 | 1.3226 | 2.7817 | 3.5897 | 4.1191 | 4.3977 | 4.955 | 5.5122 | 0.96406 | 1.9027 | 2.2833 | 2.2833 | 2.2833 | 2.2833 | 0.99073 | 1.1525 | 1.1525 | 1.1525 | 1.1525 | 1.1525
2020-01-19 12:00 | Summer | 0.53347 | 0.76348 | 1.1017 | 1.1017 | 1.1017 | 1.1017 | 0.67446 | 1.3339 | 1.3339 | 1.3339 | 1.3339 | 1.3339 | 2.7055 | 3.4913 | 4.0062 | 4.2772 | 4.8192 | 5.3612 | 0.97549 | 1.9253 | 2.3104 | 2.3104 | 2.3104 | 2.3104 | 1.0479 | 1.219 | 1.219 | 1.219 | 1.219 | 1.219
2020-01-19 13:00 | Summer | 0.51442 | 0.73622 | 1.0624 | 1.0624 | 1.0624 | 1.0624 | 0.66303 | 1.3113 | 1.3113 | 1.3113 | 1.3113 | 1.3113 | 2.7055 | 3.4913 | 4.0062 | 4.2772 | 4.8192 | 5.3612 | 0.99454 | 1.9629 | 2.3555 | 2.3555 | 2.3555 | 2.3555 | 1.0098 | 1.1746 | 1.1746 | 1.1746 | 1.1746 | 1.1746
2020-01-19 14:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.65445 | 1.2943 | 1.2943 | 1.2943 | 1.2943 | 1.2943 | 2.8579 | 3.688 | 4.2319 | 4.5182 | 5.0907 | 5.6632 | 1.0441 | 2.0607 | 2.4728 | 2.4728 | 2.4728 | 2.4728 | 1.1432 | 1.3298 | 1.3298 | 1.3298 | 1.3298 | 1.3298
2020-01-19 15:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.70304 | 1.3904 | 1.3904 | 1.3904 | 1.3904 | 1.3904 | 2.9531 | 3.811 | 4.373 | 4.6688 | 5.2604 | 5.852 | 1.0288 | 2.0306 | 2.4367 | 2.4367 | 2.4367 | 2.4367 | 1.105 | 1.2855 | 1.2855 | 1.2855 | 1.2855 | 1.2855
2020-01-19 16:00 | Summer | 0.64779 | 0.92709 | 1.3378 | 1.3378 | 1.3378 | 1.3378 | 0.81449 | 1.6109 | 1.6109 | 1.6109 | 1.6109 | 1.6109 | 2.9341 | 3.7864 | 4.3448 | 4.6387 | 5.2265 | 5.8142 | 1.0098 | 1.993 | 2.3916 | 2.3916 | 2.3916 | 2.3916 | 1.105 | 1.2855 | 1.2855 | 1.2855 | 1.2855 | 1.2855
2020-01-19 17:00 | Summer | 0.57178 | 0.81831 | 1.1808 | 1.1808 | 1.1808 | 1.1808 | 0.81164 | 1.6052 | 1.6052 | 1.6052 | 1.6052 | 1.6052 | 2.8417 | 3.6671 | 4.2079 | 4.4926 | 5.0619 | 5.6311 | 1.0326 | 2.0381 | 2.4457 | 2.4457 | 2.4457 | 2.4457 | 1.067 | 1.2412 | 1.2412 | 1.2412 | 1.2412 | 1.2412
2020-01-19 18:00 | Summer | 0.59742 | 0.855 | 1.2338 | 1.2338 | 1.2338 | 1.2338 | 0.80878 | 1.5996 | 1.5996 | 1.5996 | 1.5996 | 1.5996 | 2.8579 | 3.688 | 4.2319 | 4.5182 | 5.0907 | 5.6632 | 1.006 | 1.9855 | 2.3826 | 2.3826 | 2.3826 | 2.3826 | 1.0669 | 1.2411 | 1.2411 | 1.2411 | 1.2411 | 1.2411
2020-01-19 19:00 | Summer | 0.64779 | 0.92709 | 1.3378 | 1.3378 | 1.3378 | 1.3378 | 0.85165 | 1.6843 | 1.6843 | 1.6843 | 1.6843 | 1.6843 | 2.7245 | 3.5159 | 4.0344 | 4.3073 | 4.8531 | 5.3989 | 1.0288 | 2.0306 | 2.4367 | 2.4367 | 2.4367 | 2.4367 | 1.0479 | 1.219 | 1.219 | 1.219 | 1.219 | 1.219
2020-01-19 20:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.78877 | 1.56 | 1.56 | 1.56 | 1.56 | 1.56 | 2.5721 | 3.3192 | 3.8087 | 4.0664 | 4.5816 | 5.0969 | 1.0326 | 2.0381 | 2.4457 | 2.4457 | 2.4457 | 2.4457 | 1.0098 | 1.1746 | 1.1746 | 1.1746 | 1.1746 | 1.1746
2020-01-19 21:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.76019 | 1.5035 | 1.5035 | 1.5035 | 1.5035 | 1.5035 | 2.553 | 3.2946 | 3.7805 | 4.0362 | 4.5477 | 5.0591 | 1.0288 | 2.0306 | 2.4367 | 2.4367 | 2.4367 | 2.4367 | 1.0098 | 1.1746 | 1.1746 | 1.1746 | 1.1746 | 1.1746
2020-01-19 22:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.66017 | 1.3056 | 1.3056 | 1.3056 | 1.3056 | 1.3056 | 2.3625 | 3.0488 | 3.4984 | 3.735 | 4.2083 | 4.6816 | 1.0212 | 2.0156 | 2.4187 | 2.4187 | 2.4187 | 2.4187 | 1.0098 | 1.1746 | 1.1746 | 1.1746 | 1.1746 | 1.1746
2020-01-19 23:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.64302 | 1.2717 | 1.2717 | 1.2717 | 1.2717 | 1.2717 | 2.2673 | 2.9258 | 3.3573 | 3.5844 | 4.0386 | 4.4928 | 0.89928 | 1.7749 | 2.1299 | 2.1299 | 2.1299 | 2.1299 | 0.93358 | 1.086 | 1.086 | 1.086 | 1.086 | 1.086
2020-01-20 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.51742 | 1.0233 | 1.0233 | 1.0233 | 1.0233 | 1.0233 | 2.044 | 2.6377 | 3.0267 | 3.2314 | 3.6409 | 4.0504 | 0.67446 | 1.3312 | 1.5974 | 1.5974 | 1.5974 | 1.5974 | 0.93358 | 1.086 | 1.086 | 1.086 | 1.086 | 1.086
2020-01-20 01:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.51442 | 1.0174 | 1.0174 | 1.0174 | 1.0174 | 1.0174 | 1.9624 | 2.5325 | 2.9059 | 3.1025 | 3.4956 | 3.8887 | 0.65541 | 1.2936 | 1.5523 | 1.5523 | 1.5523 | 1.5523 | 0.93358 | 1.086 | 1.086 | 1.086 | 1.086 | 1.086
2020-01-20 02:00 | Summer | 0.57154 | 0.81796 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.62873 | 1.2435 | 1.2435 | 1.2435 | 1.2435 | 1.2435 | 1.9243 | 2.4833 | 2.8495 | 3.0422 | 3.4277 | 3.8132 | 0.62111 | 1.2259 | 1.4711 | 1.4711 | 1.4711 | 1.4711 | 0.92109 | 1.0715 | 1.0715 | 1.0715 | 1.0715 | 1.0715
2020-01-20 03:00 | Summer | 0.59461 | 0.85099 | 1.228 | 1.228 | 1.228 | 1.228 | 0.6716 | 1.3283 | 1.3283 | 1.3283 | 1.3283 | 1.3283 | 1.9243 | 2.4833 | 2.8495 | 3.0422 | 3.4277 | 3.8132 | 0.63254 | 1.2484 | 1.4981 | 1.4981 | 1.4981 | 1.4981 | 0.99073 | 1.1525 | 1.1525 | 1.1525 | 1.1525 | 1.1525
2020-01-20 04:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.76877 | 1.5204 | 1.5204 | 1.5204 | 1.5204 | 1.5204 | 1.9065 | 2.4603 | 2.8232 | 3.0141 | 3.396 | 3.778 | 0.64016 | 1.2635 | 1.5162 | 1.5162 | 1.5162 | 1.5162 | 1.1241 | 1.3076 | 1.3076 | 1.3076 | 1.3076 | 1.3076
2020-01-20 05:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.78877 | 1.56 | 1.56 | 1.56 | 1.56 | 1.56 | 2.0577 | 2.6554 | 3.047 | 3.2531 | 3.6653 | 4.0775 | 0.92214 | 1.82 | 2.184 | 2.184 | 2.184 | 2.184 | 1.3671 | 1.5903 | 1.5903 | 1.5903 | 1.5903 | 1.5903
2020-01-20 06:00 | Summer | 1.4351 | 2.0539 | 2.9638 | 2.9638 | 2.9638 | 2.9638 | 0.9631 | 1.9048 | 1.9048 | 1.9048 | 1.9048 | 1.9048 | 2.4959 | 3.2209 | 3.6959 | 3.9459 | 4.4459 | 4.9459 | 0.98692 | 1.9479 | 2.3374 | 2.3374 | 2.3374 | 2.3374 | 1.4875 | 1.7304 | 1.7304 | 1.7304 | 1.7304 | 1.7304
2020-01-20 07:00 | Summer | 2.0005 | 2.8631 | 4.1315 | 4.1315 | 4.1315 | 4.1315 | 1.2317 | 2.4361 | 2.4361 | 2.4361 | 2.4361 | 2.4361 | 3.1019 | 4.0029 | 4.5932 | 4.9039 | 5.5253 | 6.1467 | 1.1965 | 2.3615 | 2.8338 | 2.8338 | 2.8338 | 2.8338 | 2.0393 | 2.3722 | 2.3722 | 2.3722 | 2.3722 | 2.3722
2020-01-20 08:00 | Summer | 2.1148 | 3.0267 | 4.3676 | 4.3676 | 4.3676 | 4.3676 | 1.2317 | 2.4361 | 2.4361 | 2.4361 | 2.4361 | 2.4361 | 3.4104 | 4.4011 | 5.0501 | 5.3917 | 6.0749 | 6.7581 | 1.227 | 2.4217 | 2.906 | 2.906 | 2.906 | 2.906 | 2.6864 | 3.125 | 3.125 | 3.125 | 3.125 | 3.125
2020-01-20 09:00 | Summer | 2.2101 | 3.163 | 4.5643 | 4.5643 | 4.5643 | 4.5643 | 1.4461 | 2.86 | 2.86 | 2.86 | 2.86 | 2.86 | 3.639 | 4.6961 | 5.3887 | 5.7532 | 6.4822 | 7.2112 | 1.147 | 2.2637 | 2.7165 | 2.7165 | 2.7165 | 2.7165 | 2.8388 | 3.3023 | 3.3023 | 3.3023 | 3.3023 | 3.3023
2020-01-20 10:00 | Summer | 2.4387 | 3.4902 | 5.0365 | 5.0365 | 5.0365 | 5.0365 | 1.6261 | 3.2161 | 3.2161 | 3.2161 | 3.2161 | 3.2161 | 3.8105 | 4.9174 | 5.6426 | 6.0243 | 6.7876 | 7.551 | 1.1127 | 2.1961 | 2.6353 | 2.6353 | 2.6353 | 2.6353 | 2.9722 | 3.4575 | 3.4575 | 3.4575 | 3.4575 | 3.4575
2020-01-20 11:00 | Summer | 2.2863 | 3.2721 | 4.7217 | 4.7217 | 4.7217 | 4.7217 | 1.5833 | 3.1313 | 3.1313 | 3.1313 | 3.1313 | 3.1313 | 3.8486 | 4.9666 | 5.699 | 6.0845 | 6.8555 | 7.6265 | 1.3375 | 2.6398 | 3.1677 | 3.1677 | 3.1677 | 3.1677 | 3.0294 | 3.5239 | 3.5239 | 3.5239 | 3.5239 | 3.5239
2020-01-20 12:00 | Summer | 2.3625 | 3.3811 | 4.8791 | 4.8791 | 4.8791 | 4.8791 | 1.5833 | 3.1313 | 3.1313 | 3.1313 | 3.1313 | 3.1313 | 4.0772 | 5.2616 | 6.0376 | 6.4459 | 7.2627 | 8.0795 | 1.3261 | 2.6172 | 3.1407 | 3.1407 | 3.1407 | 3.1407 | 3.1437 | 3.6569 | 3.6569 | 3.6569 | 3.6569 | 3.6569
2020-01-20 13:00 | Summer | 1.6957 | 2.4268 | 3.5019 | 3.5019 | 3.5019 | 3.5019 | 1.3689 | 2.7074 | 2.7074 | 2.7074 | 2.7074 | 2.7074 | 3.2389 | 4.1798 | 4.7962 | 5.1206 | 5.7695 | 6.4183 | 1.2498 | 2.4668 | 2.9602 | 2.9602 | 2.9602 | 2.9602 | 2.4578 | 2.8591 | 2.8591 | 2.8591 | 2.8591 | 2.8591
2020-01-20 14:00 | Summer | 1.81 | 2.5904 | 3.738 | 3.738 | 3.738 | 3.738 | 1.3032 | 2.5774 | 2.5774 | 2.5774 | 2.5774 | 2.5774 | 3.1437 | 4.0568 | 4.6551 | 4.97 | 5.5998 | 6.2296 | 1.288 | 2.542 | 3.0504 | 3.0504 | 3.0504 | 3.0504 | 2.534 | 2.9477 | 2.9477 | 2.9477 | 2.9477 | 2.9477
2020-01-20 15:00 | Summer | 2.172 | 3.1085 | 4.4856 | 4.4856 | 4.4856 | 4.4856 | 1.3456 | 2.6612 | 2.6612 | 2.6612 | 2.6612 | 2.6612 | 3.4866 | 4.4994 | 5.163 | 5.5122 | 6.2107 | 6.9091 | 1.2117 | 2.3916 | 2.8699 | 2.8699 | 2.8699 | 2.8699 | 2.6483 | 3.0807 | 3.0807 | 3.0807 | 3.0807 | 3.0807
2020-01-20 16:00 | Summer | 1.9053 | 2.7267 | 3.9348 | 3.9348 | 3.9348 | 3.9348 | 1.4432 | 2.8543 | 2.8543 | 2.8543 | 2.8543 | 2.8543 | 3.3342 | 4.3027 | 4.9373 | 5.2712 | 5.9392 | 6.6071 | 1.0631 | 2.0983 | 2.5179 | 2.5179 | 2.5179 | 2.5179 | 2.6483 | 3.0807 | 3.0807 | 3.0807 | 3.0807 | 3.0807
2020-01-20 17:00 | Summer | 1.7909 | 2.5631 | 3.6987 | 3.6987 | 3.6987 | 3.6987 | 1.3435 | 2.6571 | 2.6571 | 2.6571 | 2.6571 | 2.6571 | 3.3342 | 4.3027 | 4.9373 | 5.2712 | 5.9392 | 6.6071 | 1.1012 | 2.1735 | 2.6082 | 2.6082 | 2.6082 | 2.6082 | 2.5304 | 2.9435 | 2.9435 | 2.9435 | 2.9435 | 2.9435
2020-01-20 18:00 | Summer | 1.3162 | 1.8837 | 2.7182 | 2.7182 | 2.7182 | 2.7182 | 0.95448 | 1.8877 | 1.8877 | 1.8877 | 1.8877 | 1.8877 | 3.1381 | 4.0497 | 4.6469 | 4.9612 | 5.5899 | 6.2185 | 1.0479 | 2.0682 | 2.4818 | 2.4818 | 2.4818 | 2.4818 | 1.8479 | 2.1496 | 2.1496 | 2.1496 | 2.1496 | 2.1496
2020-01-20 19:00 | Summer | 0.7621 | 1.0907 | 1.5739 | 1.5739 | 1.5739 | 1.5739 | 0.83164 | 1.6448 | 1.6448 | 1.6448 | 1.6448 | 1.6448 | 2.6149 | 3.3745 | 3.8722 | 4.1341 | 4.6579 | 5.1818 | 1.0365 | 2.0456 | 2.4548 | 2.4548 | 2.4548 | 2.4548 | 1.2003 | 1.3963 | 1.3963 | 1.3963 | 1.3963 | 1.3963
2020-01-20 20:00 | Summer | 0.68601 | 0.98179 | 1.4168 | 1.4168 | 1.4168 | 1.4168 | 0.81735 | 1.6165 | 1.6165 | 1.6165 | 1.6165 | 1.6165 | 2.553 | 3.2946 | 3.7805 | 4.0362 | 4.5477 | 5.0591 | 0.98311 | 1.9403 | 2.3284 | 2.3284 | 2.3284 | 2.3284 | 1.1631 | 1.353 | 1.353 | 1.353 | 1.353 | 1.353
2020-01-20 21:00 | Summer | 0.60816 | 0.87037 | 1.256 | 1.256 | 1.256 | 1.256 | 0.66303 | 1.3113 | 1.3113 | 1.3113 | 1.3113 | 1.3113 | 2.3435 | 3.0242 | 3.4702 | 3.7049 | 4.1744 | 4.6438 | 0.96025 | 1.8952 | 2.2743 | 2.2743 | 2.2743 | 2.2743 | 1.0479 | 1.219 | 1.219 | 1.219 | 1.219 | 1.219
2020-01-20 22:00 | Summer | 0.62714 | 0.89754 | 1.2952 | 1.2952 | 1.2952 | 1.2952 | 0.66303 | 1.3113 | 1.3113 | 1.3113 | 1.3113 | 1.3113 | 2.2416 | 2.8927 | 3.3193 | 3.5438 | 3.9929 | 4.4419 | 0.88023 | 1.7373 | 2.0847 | 2.0847 | 2.0847 | 2.0847 | 0.99073 | 1.1525 | 1.1525 | 1.1525 | 1.1525 | 1.1525
2020-01-20 23:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.62016 | 1.2265 | 1.2265 | 1.2265 | 1.2265 | 1.2265 | 2.0196 | 2.6062 | 2.9906 | 3.1929 | 3.5974 | 4.002 | 0.82307 | 1.6245 | 1.9494 | 1.9494 | 1.9494 | 1.9494 | 0.95263 | 1.1082 | 1.1082 | 1.1082 | 1.1082 | 1.1082
2020-01-21 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.54014 | 1.0683 | 1.0683 | 1.0683 | 1.0683 | 1.0683 | 1.8481 | 2.3849 | 2.7366 | 2.9218 | 3.292 | 3.6622 | 0.59825 | 1.1808 | 1.4169 | 1.4169 | 1.4169 | 1.4169 | 0.91452 | 1.0638 | 1.0638 | 1.0638 | 1.0638 | 1.0638
2020-01-21 01:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.54299 | 1.0739 | 1.0739 | 1.0739 | 1.0739 | 1.0739 | 1.7719 | 2.2866 | 2.6238 | 2.8013 | 3.1562 | 3.5112 | 0.62111 | 1.2259 | 1.4711 | 1.4711 | 1.4711 | 1.4711 | 0.91452 | 1.0638 | 1.0638 | 1.0638 | 1.0638 | 1.0638
2020-01-21 02:00 | Summer | 0.57214 | 0.81882 | 1.1816 | 1.1816 | 1.1816 | 1.1816 | 0.52585 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.7528 | 2.262 | 2.5956 | 2.7712 | 3.1223 | 3.4734 | 0.58301 | 1.1507 | 1.3808 | 1.3808 | 1.3808 | 1.3808 | 0.89547 | 1.0417 | 1.0417 | 1.0417 | 1.0417 | 1.0417
2020-01-21 03:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.52299 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.6957 | 2.1882 | 2.5109 | 2.6808 | 3.0205 | 3.3602 | 0.56395 | 1.1131 | 1.3357 | 1.3357 | 1.3357 | 1.3357 | 0.87642 | 1.0195 | 1.0195 | 1.0195 | 1.0195 | 1.0195
2020-01-21 04:00 | Summer | 0.63658 | 0.91105 | 1.3147 | 1.3147 | 1.3147 | 1.3147 | 0.58872 | 1.1643 | 1.1643 | 1.1643 | 1.1643 | 1.1643 | 1.7528 | 2.262 | 2.5956 | 2.7712 | 3.1223 | 3.4734 | 0.56395 | 1.1131 | 1.3357 | 1.3357 | 1.3357 | 1.3357 | 0.99073 | 1.1525 | 1.1525 | 1.1525 | 1.1525 | 1.1525
2020-01-21 05:00 | Summer | 0.64779 | 0.92709 | 1.3378 | 1.3378 | 1.3378 | 1.3378 | 0.63159 | 1.2491 | 1.2491 | 1.2491 | 1.2491 | 1.2491 | 1.81 | 2.3358 | 2.6802 | 2.8615 | 3.2241 | 3.5867 | 0.81164 | 1.6019 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 1.1137 | 1.2955 | 1.2955 | 1.2955 | 1.2955 | 1.2955
2020-01-21 06:00 | Summer | 0.99002 | 1.4169 | 2.0446 | 2.0446 | 2.0446 | 2.0446 | 0.76305 | 1.5091 | 1.5091 | 1.5091 | 1.5091 | 1.5091 | 2.0386 | 2.6308 | 3.0188 | 3.223 | 3.6314 | 4.0398 | 0.9793 | 1.9328 | 2.3194 | 2.3194 | 2.3194 | 2.3194 | 1.3143 | 1.5289 | 1.5289 | 1.5289 | 1.5289 | 1.5289
2020-01-21 07:00 | Summer | 1.8178 | 2.6016 | 3.7542 | 3.7542 | 3.7542 | 3.7542 | 0.93738 | 1.8539 | 1.8539 | 1.8539 | 1.8539 | 1.8539 | 2.8384 | 3.6629 | 4.2031 | 4.4874 | 5.056 | 5.6246 | 1.2194 | 2.4066 | 2.888 | 2.888 | 2.888 | 2.888 | 1.9049 | 2.2159 | 2.2159 | 2.2159 | 2.2159 | 2.2159
2020-01-21 08:00 | Summer | 1.9624 | 2.8085 | 4.0528 | 4.0528 | 4.0528 | 4.0528 | 1.0774 | 2.1309 | 2.1309 | 2.1309 | 2.1309 | 2.1309 | 2.9913 | 3.8601 | 4.4294 | 4.729 | 5.3283 | 5.9275 | 1.2537 | 2.4743 | 2.9692 | 2.9692 | 2.9692 | 2.9692 | 2.3816 | 2.7704 | 2.7704 | 2.7704 | 2.7704 | 2.7704
2020-01-21 09:00 | Summer | 1.9815 | 2.8358 | 4.0922 | 4.0922 | 4.0922 | 4.0922 | 1.2032 | 2.3796 | 2.3796 | 2.3796 | 2.3796 | 2.3796 | 3.0484 | 3.9339 | 4.5141 | 4.8194 | 5.4301 | 6.0408 | 1.1736 | 2.3164 | 2.7797 | 2.7797 | 2.7797 | 2.7797 | 2.5149 | 2.9255 | 2.9255 | 2.9255 | 2.9255 | 2.9255
2020-01-21 10:00 | Summer | 2.0386 | 2.9176 | 4.2102 | 4.2102 | 4.2102 | 4.2102 | 1.3603 | 2.6904 | 2.6904 | 2.6904 | 2.6904 | 2.6904 | 3.1437 | 4.0568 | 4.6551 | 4.97 | 5.5998 | 6.2296 | 1.0365 | 2.0456 | 2.4548 | 2.4548 | 2.4548 | 2.4548 | 2.6102 | 3.0364 | 3.0364 | 3.0364 | 3.0364 | 3.0364
2020-01-21 11:00 | Summer | 2.0196 | 2.8903 | 4.1709 | 4.1709 | 4.1709 | 4.1709 | 1.4004 | 2.7696 | 2.7696 | 2.7696 | 2.7696 | 2.7696 | 3.258 | 4.2044 | 4.8244 | 5.1507 | 5.8034 | 6.4561 | 0.99073 | 1.9554 | 2.3465 | 2.3465 | 2.3465 | 2.3465 | 2.7436 | 3.1915 | 3.1915 | 3.1915 | 3.1915 | 3.1915
2020-01-21 12:00 | Summer | 1.9624 | 2.8085 | 4.0528 | 4.0528 | 4.0528 | 4.0528 | 1.3832 | 2.7356 | 2.7356 | 2.7356 | 2.7356 | 2.7356 | 3.4485 | 4.4502 | 5.1065 | 5.4519 | 6.1428 | 6.8336 | 0.96406 | 1.9027 | 2.2833 | 2.2833 | 2.2833 | 2.2833 | 2.6864 | 3.125 | 3.125 | 3.125 | 3.125 | 3.125
2020-01-21 13:00 | Summer | 1.9624 | 2.8085 | 4.0528 | 4.0528 | 4.0528 | 4.0528 | 1.5575 | 3.0804 | 3.0804 | 3.0804 | 3.0804 | 3.0804 | 3.3914 | 4.3765 | 5.0219 | 5.3616 | 6.041 | 6.7204 | 0.9793 | 1.9328 | 2.3194 | 2.3194 | 2.3194 | 2.3194 | 2.7626 | 3.2137 | 3.2137 | 3.2137 | 3.2137 | 3.2137
2020-01-21 14:00 | Summer | 1.9053 | 2.7267 | 3.9348 | 3.9348 | 3.9348 | 3.9348 | 1.5318 | 3.0296 | 3.0296 | 3.0296 | 3.0296 | 3.0296 | 3.4866 | 4.4994 | 5.163 | 5.5122 | 6.2107 | 6.9091 | 0.99454 | 1.9629 | 2.3555 | 2.3555 | 2.3555 | 2.3555 | 2.7436 | 3.1915 | 3.1915 | 3.1915 | 3.1915 | 3.1915
2020-01-21 15:00 | Summer | 1.8672 | 2.6722 | 3.8561 | 3.8561 | 3.8561 | 3.8561 | 1.4947 | 2.9561 | 2.9561 | 2.9561 | 2.9561 | 2.9561 | 3.4295 | 4.4256 | 5.0783 | 5.4218 | 6.1088 | 6.7959 | 0.98692 | 1.9479 | 2.3374 | 2.3374 | 2.3374 | 2.3374 | 2.7626 | 3.2137 | 3.2137 | 3.2137 | 3.2137 | 3.2137
2020-01-21 16:00 | Summer | 1.829 | 2.6177 | 3.7774 | 3.7774 | 3.7774 | 3.7774 | 1.5918 | 3.1483 | 3.1483 | 3.1483 | 3.1483 | 3.1483 | 3.4485 | 4.4502 | 5.1065 | 5.4519 | 6.1428 | 6.8336 | 0.99454 | 1.9629 | 2.3555 | 2.3555 | 2.3555 | 2.3555 | 2.7245 | 3.1693 | 3.1693 | 3.1693 | 3.1693 | 3.1693
2020-01-21 17:00 | Summer | 1.7338 | 2.4813 | 3.5806 | 3.5806 | 3.5806 | 3.5806 | 1.3889 | 2.747 | 2.747 | 2.747 | 2.747 | 2.747 | 3.3533 | 4.3273 | 4.9655 | 5.3013 | 5.9731 | 6.6449 | 0.92595 | 1.8275 | 2.193 | 2.193 | 2.193 | 2.193 | 2.6775 | 3.1147 | 3.1147 | 3.1147 | 3.1147 | 3.1147
2020-01-21 18:00 | Summer | 1.2489 | 1.7874 | 2.5793 | 2.5793 | 2.5793 | 2.5793 | 1.1095 | 2.1943 | 2.1943 | 2.1943 | 2.1943 | 2.1943 | 3.0675 | 3.9585 | 4.5423 | 4.8495 | 5.464 | 6.0785 | 0.94882 | 1.8727 | 2.2472 | 2.2472 | 2.2472 | 2.2472 | 2.0395 | 2.3725 | 2.3725 | 2.3725 | 2.3725 | 2.3725
2020-01-21 19:00 | Summer | 0.74305 | 1.0634 | 1.5346 | 1.5346 | 1.5346 | 1.5346 | 0.90023 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 2.8447 | 3.6711 | 4.2125 | 4.4974 | 5.0673 | 5.6372 | 0.93357 | 1.8426 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 1.2956 | 1.5071 | 1.5071 | 1.5071 | 1.5071 | 1.5071
2020-01-21 20:00 | Summer | 0.74305 | 1.0634 | 1.5346 | 1.5346 | 1.5346 | 1.5346 | 0.80592 | 1.5939 | 1.5939 | 1.5939 | 1.5939 | 1.5939 | 2.534 | 3.2701 | 3.7523 | 4.0061 | 4.5138 | 5.0214 | 0.91833 | 1.8125 | 2.175 | 2.175 | 2.175 | 2.175 | 1.1813 | 1.3741 | 1.3741 | 1.3741 | 1.3741 | 1.3741
2020-01-21 21:00 | Summer | 0.66684 | 0.95435 | 1.3772 | 1.3772 | 1.3772 | 1.3772 | 0.76877 | 1.5204 | 1.5204 | 1.5204 | 1.5204 | 1.5204 | 2.4006 | 3.098 | 3.5548 | 3.7953 | 4.2762 | 4.7571 | 0.89547 | 1.7674 | 2.1208 | 2.1208 | 2.1208 | 2.1208 | 1.1432 | 1.3298 | 1.3298 | 1.3298 | 1.3298 | 1.3298
2020-01-21 22:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.76305 | 1.5091 | 1.5091 | 1.5091 | 1.5091 | 1.5091 | 2.2101 | 2.8521 | 3.2727 | 3.4941 | 3.9368 | 4.3796 | 0.77734 | 1.5342 | 1.8411 | 1.8411 | 1.8411 | 1.8411 | 1.0455 | 1.2162 | 1.2162 | 1.2162 | 1.2162 | 1.2162
2020-01-21 23:00 | Summer | 0.62577 | 0.89558 | 1.2924 | 1.2924 | 1.2924 | 1.2924 | 0.67446 | 1.3339 | 1.3339 | 1.3339 | 1.3339 | 1.3339 | 2.115 | 2.7293 | 3.1318 | 3.3437 | 3.7674 | 4.1911 | 0.80402 | 1.5869 | 1.9042 | 1.9042 | 1.9042 | 1.9042 | 1.0098 | 1.1746 | 1.1746 | 1.1746 | 1.1746 | 1.1746
2020-01-22 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.56014 | 1.1078 | 1.1078 | 1.1078 | 1.1078 | 1.1078 | 1.9048 | 2.4581 | 2.8206 | 3.0114 | 3.393 | 3.7746 | 0.55633 | 1.098 | 1.3176 | 1.3176 | 1.3176 | 1.3176 | 0.99926 | 1.1624 | 1.1624 | 1.1624 | 1.1624 | 1.1624
2020-01-22 01:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.51727 | 1.023 | 1.023 | 1.023 | 1.023 | 1.023 | 1.81 | 2.3358 | 2.6802 | 2.8615 | 3.2241 | 3.5867 | 0.54109 | 1.0679 | 1.2815 | 1.2815 | 1.2815 | 1.2815 | 0.91452 | 1.0638 | 1.0638 | 1.0638 | 1.0638 | 1.0638
2020-01-22 02:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.57157 | 1.1304 | 1.1304 | 1.1304 | 1.1304 | 1.1304 | 1.7919 | 2.3124 | 2.6535 | 2.833 | 3.1919 | 3.5509 | 0.5068 | 1.0003 | 1.2003 | 1.2003 | 1.2003 | 1.2003 | 0.95263 | 1.1082 | 1.1082 | 1.1082 | 1.1082 | 1.1082
2020-01-22 03:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.54299 | 1.0739 | 1.0739 | 1.0739 | 1.0739 | 1.0739 | 1.7528 | 2.262 | 2.5956 | 2.7712 | 3.1223 | 3.4734 | 0.56014 | 1.1055 | 1.3267 | 1.3267 | 1.3267 | 1.3267 | 0.95263 | 1.1082 | 1.1082 | 1.1082 | 1.1082 | 1.1082
2020-01-22 04:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.64016 | 1.2661 | 1.2661 | 1.2661 | 1.2661 | 1.2661 | 1.7719 | 2.2866 | 2.6238 | 2.8013 | 3.1562 | 3.5112 | 0.5068 | 1.0003 | 1.2003 | 1.2003 | 1.2003 | 1.2003 | 1.0797 | 1.256 | 1.256 | 1.256 | 1.256 | 1.256
2020-01-22 05:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.63159 | 1.2491 | 1.2491 | 1.2491 | 1.2491 | 1.2491 | 1.8479 | 2.3846 | 2.7363 | 2.9214 | 3.2916 | 3.6618 | 0.80402 | 1.5869 | 1.9042 | 1.9042 | 1.9042 | 1.9042 | 1.1813 | 1.3741 | 1.3741 | 1.3741 | 1.3741 | 1.3741
2020-01-22 06:00 | Summer | 0.98868 | 1.415 | 2.0418 | 2.0418 | 2.0418 | 2.0418 | 0.74019 | 1.4639 | 1.4639 | 1.4639 | 1.4639 | 1.4639 | 2.0721 | 2.6741 | 3.0684 | 3.276 | 3.6911 | 4.1062 | 0.84593 | 1.6696 | 2.0035 | 2.0035 | 2.0035 | 2.0035 | 1.3695 | 1.5931 | 1.5931 | 1.5931 | 1.5931 | 1.5931
2020-01-22 07:00 | Summer | 1.829 | 2.6177 | 3.7774 | 3.7774 | 3.7774 | 3.7774 | 0.95739 | 1.8935 | 1.8935 | 1.8935 | 1.8935 | 1.8935 | 2.7055 | 3.4913 | 4.0062 | 4.2772 | 4.8192 | 5.3612 | 1.0898 | 2.1509 | 2.5811 | 2.5811 | 2.5811 | 2.5811 | 1.9053 | 2.2163 | 2.2163 | 2.2163 | 2.2163 | 2.2163
2020-01-22 08:00 | Summer | 1.9815 | 2.8358 | 4.0922 | 4.0922 | 4.0922 | 4.0922 | 1.0603 | 2.097 | 2.097 | 2.097 | 2.097 | 2.097 | 3.0103 | 3.8847 | 4.4576 | 4.7592 | 5.3622 | 5.9653 | 1.1508 | 2.2713 | 2.7255 | 2.7255 | 2.7255 | 2.7255 | 2.5911 | 3.0142 | 3.0142 | 3.0142 | 3.0142 | 3.0142
2020-01-22 09:00 | Summer | 2.0577 | 2.9449 | 4.2495 | 4.2495 | 4.2495 | 4.2495 | 1.266 | 2.5039 | 2.5039 | 2.5039 | 2.5039 | 2.5039 | 3.3914 | 4.3765 | 5.0219 | 5.3616 | 6.041 | 6.7204 | 1.1279 | 2.2261 | 2.6714 | 2.6714 | 2.6714 | 2.6714 | 2.6682 | 3.1038 | 3.1038 | 3.1038 | 3.1038 | 3.1038
2020-01-22 10:00 | Summer | 2.0808 | 2.9779 | 4.2973 | 4.2973 | 4.2973 | 4.2973 | 1.266 | 2.5039 | 2.5039 | 2.5039 | 2.5039 | 2.5039 | 3.5438 | 4.5732 | 5.2476 | 5.6026 | 6.3125 | 7.0224 | 1.0326 | 2.0381 | 2.4457 | 2.4457 | 2.4457 | 2.4457 | 2.8388 | 3.3023 | 3.3023 | 3.3023 | 3.3023 | 3.3023
2020-01-22 11:00 | Summer | 2.191 | 3.1357 | 4.525 | 4.525 | 4.525 | 4.525 | 1.1946 | 2.3626 | 2.3626 | 2.3626 | 2.3626 | 2.3626 | 3.5247 | 4.5486 | 5.2194 | 5.5724 | 6.2785 | 6.9846 | 1.0365 | 2.0456 | 2.4548 | 2.4548 | 2.4548 | 2.4548 | 2.8579 | 3.3245 | 3.3245 | 3.3245 | 3.3245 | 3.3245
2020-01-22 12:00 | Summer | 2.0958 | 2.9994 | 4.3282 | 4.3282 | 4.3282 | 4.3282 | 1.3603 | 2.6904 | 2.6904 | 2.6904 | 2.6904 | 2.6904 | 3.5059 | 4.5242 | 5.1915 | 5.5426 | 6.245 | 6.9473 | 1.0326 | 2.0381 | 2.4457 | 2.4457 | 2.4457 | 2.4457 | 2.915 | 3.391 | 3.391 | 3.391 | 3.391 | 3.391
2020-01-22 13:00 | Summer | 1.9243 | 2.754 | 3.9741 | 3.9741 | 3.9741 | 3.9741 | 1.3118 | 2.5943 | 2.5943 | 2.5943 | 2.5943 | 2.5943 | 3.5057 | 4.524 | 5.1912 | 5.5423 | 6.2446 | 6.9469 | 1.0212 | 2.0156 | 2.4187 | 2.4187 | 2.4187 | 2.4187 | 2.915 | 3.391 | 3.391 | 3.391 | 3.391 | 3.391
2020-01-22 14:00 | Summer | 1.9434 | 2.7813 | 4.0135 | 4.0135 | 4.0135 | 4.0135 | 1.3775 | 2.7243 | 2.7243 | 2.7243 | 2.7243 | 2.7243 | 3.7152 | 4.7944 | 5.5015 | 5.8736 | 6.6179 | 7.3622 | 1.0479 | 2.0682 | 2.4818 | 2.4818 | 2.4818 | 2.4818 | 3.1246 | 3.6348 | 3.6348 | 3.6348 | 3.6348 | 3.6348
2020-01-22 15:00 | Summer | 2.0386 | 2.9176 | 4.2102 | 4.2102 | 4.2102 | 4.2102 | 1.5061 | 2.9787 | 2.9787 | 2.9787 | 2.9787 | 2.9787 | 3.6962 | 4.7699 | 5.4733 | 5.8435 | 6.584 | 7.3244 | 1.0898 | 2.1509 | 2.5811 | 2.5811 | 2.5811 | 2.5811 | 3.0103 | 3.5018 | 3.5018 | 3.5018 | 3.5018 | 3.5018
2020-01-22 16:00 | Summer | 1.9925 | 2.8516 | 4.115 | 4.115 | 4.115 | 4.115 | 1.3775 | 2.7243 | 2.7243 | 2.7243 | 2.7243 | 2.7243 | 3.7534 | 4.8436 | 5.5579 | 5.9339 | 6.6858 | 7.4377 | 1.0174 | 2.008 | 2.4096 | 2.4096 | 2.4096 | 2.4096 | 3.0675 | 3.5683 | 3.5683 | 3.5683 | 3.5683 | 3.5683
2020-01-22 17:00 | Summer | 1.83 | 2.619 | 3.7793 | 3.7793 | 3.7793 | 3.7793 | 1.2718 | 2.5152 | 2.5152 | 2.5152 | 2.5152 | 2.5152 | 3.7724 | 4.8682 | 5.5861 | 5.964 | 6.7197 | 7.4755 | 0.95644 | 1.8877 | 2.2652 | 2.2652 | 2.2652 | 2.2652 | 2.9221 | 3.3991 | 3.3991 | 3.3991 | 3.3991 | 3.3991
2020-01-22 18:00 | Summer | 1.456 | 2.0838 | 3.007 | 3.007 | 3.007 | 3.007 | 1.166 | 2.3061 | 2.3061 | 2.3061 | 2.3061 | 2.3061 | 3.4941 | 4.5091 | 5.174 | 5.524 | 6.224 | 6.924 | 1.0022 | 1.978 | 2.3735 | 2.3735 | 2.3735 | 2.3735 | 2.2537 | 2.6216 | 2.6216 | 2.6216 | 2.6216 | 2.6216
2020-01-22 19:00 | Summer | 0.81822 | 1.171 | 1.6898 | 1.6898 | 1.6898 | 1.6898 | 0.69446 | 1.3735 | 1.3735 | 1.3735 | 1.3735 | 1.3735 | 3.1905 | 4.1172 | 4.7244 | 5.044 | 5.6831 | 6.3223 | 0.96406 | 1.9027 | 2.2833 | 2.2833 | 2.2833 | 2.2833 | 1.3908 | 1.6179 | 1.6179 | 1.6179 | 1.6179 | 1.6179
2020-01-22 20:00 | Summer | 0.724 | 1.0362 | 1.4952 | 1.4952 | 1.4952 | 1.4952 | 0.66303 | 1.3113 | 1.3113 | 1.3113 | 1.3113 | 1.3113 | 2.7325 | 3.5262 | 4.0463 | 4.32 | 4.8674 | 5.4148 | 0.86879 | 1.7147 | 2.0577 | 2.0577 | 2.0577 | 2.0577 | 1.2956 | 1.5071 | 1.5071 | 1.5071 | 1.5071 | 1.5071
2020-01-22 21:00 | Summer | 0.65912 | 0.9433 | 1.3612 | 1.3612 | 1.3612 | 1.3612 | 0.51468 | 1.0179 | 1.0179 | 1.0179 | 1.0179 | 1.0179 | 2.7245 | 3.5159 | 4.0344 | 4.3073 | 4.8531 | 5.3989 | 0.88404 | 1.7448 | 2.0938 | 2.0938 | 2.0938 | 2.0938 | 1.1432 | 1.3298 | 1.3298 | 1.3298 | 1.3298 | 1.3298
2020-01-22 22:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.51727 | 1.023 | 1.023 | 1.023 | 1.023 | 1.023 | 2.4768 | 3.1963 | 3.6677 | 3.9158 | 4.4119 | 4.9081 | 0.88023 | 1.7373 | 2.0847 | 2.0847 | 2.0847 | 2.0847 | 1.0098 | 1.1746 | 1.1746 | 1.1746 | 1.1746 | 1.1746
2020-01-22 23:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.48584 | 0.96086 | 0.96086 | 0.96086 | 0.96086 | 0.96086 | 2.3054 | 2.975 | 3.4138 | 3.6447 | 4.1065 | 4.5683 | 0.7621 | 1.5041 | 1.805 | 1.805 | 1.805 | 1.805 | 1.0098 | 1.1746 | 1.1746 | 1.1746 | 1.1746 | 1.1746
2020-01-23 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.47155 | 0.9326 | 0.9326 | 0.9326 | 0.9326 | 0.9326 | 2.0577 | 2.6554 | 3.047 | 3.2531 | 3.6653 | 4.0775 | 0.54871 | 1.083 | 1.2996 | 1.2996 | 1.2996 | 1.2996 | 1.0098 | 1.1746 | 1.1746 | 1.1746 | 1.1746 | 1.1746
2020-01-23 01:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.46869 | 0.92695 | 0.92695 | 0.92695 | 0.92695 | 0.92695 | 1.9815 | 2.557 | 2.9341 | 3.1326 | 3.5296 | 3.9265 | 0.52585 | 1.0379 | 1.2454 | 1.2454 | 1.2454 | 1.2454 | 0.99073 | 1.1525 | 1.1525 | 1.1525 | 1.1525 | 1.1525
2020-01-23 02:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.45726 | 0.90434 | 0.90434 | 0.90434 | 0.90434 | 0.90434 | 1.8862 | 2.4341 | 2.7931 | 2.982 | 3.3599 | 3.7377 | 0.5068 | 1.0003 | 1.2003 | 1.2003 | 1.2003 | 1.2003 | 0.99073 | 1.1525 | 1.1525 | 1.1525 | 1.1525 | 1.1525
2020-01-23 03:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.47155 | 0.9326 | 0.9326 | 0.9326 | 0.9326 | 0.9326 | 1.8862 | 2.4341 | 2.7931 | 2.982 | 3.3599 | 3.7377 | 0.51061 | 1.0078 | 1.2093 | 1.2093 | 1.2093 | 1.2093 | 1.0098 | 1.1746 | 1.1746 | 1.1746 | 1.1746 | 1.1746
2020-01-23 04:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.49404 | 0.97709 | 0.97709 | 0.97709 | 0.97709 | 0.97709 | 1.9243 | 2.4833 | 2.8495 | 3.0422 | 3.4277 | 3.8132 | 0.5068 | 1.0003 | 1.2003 | 1.2003 | 1.2003 | 1.2003 | 1.1432 | 1.3298 | 1.3298 | 1.3298 | 1.3298 | 1.3298
2020-01-23 05:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.64016 | 1.2661 | 1.2661 | 1.2661 | 1.2661 | 1.2661 | 1.9815 | 2.557 | 2.9341 | 3.1326 | 3.5296 | 3.9265 | 0.7964 | 1.5718 | 1.8862 | 1.8862 | 1.8862 | 1.8862 | 1.2765 | 1.4849 | 1.4849 | 1.4849 | 1.4849 | 1.4849
2020-01-23 06:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.91738 | 1.8143 | 1.8143 | 1.8143 | 1.8143 | 1.8143 | 2.2291 | 2.8767 | 3.3009 | 3.5242 | 3.9708 | 4.4173 | 0.95644 | 1.8877 | 2.2652 | 2.2652 | 2.2652 | 2.2652 | 1.5433 | 1.7952 | 1.7952 | 1.7952 | 1.7952 | 1.7952
2020-01-23 07:00 | Summer | 1.9999 | 2.8622 | 4.1303 | 4.1303 | 4.1303 | 4.1303 | 1.1031 | 2.1817 | 2.1817 | 2.1817 | 2.1817 | 2.1817 | 3.1056 | 4.0077 | 4.5987 | 4.9098 | 5.5319 | 6.154 | 1.147 | 2.2637 | 2.7165 | 2.7165 | 2.7165 | 2.7165 | 2.2915 | 2.6656 | 2.6656 | 2.6656 | 2.6656 | 2.6656
2020-01-23 08:00 | Summer | 2.3054 | 3.2993 | 4.7611 | 4.7611 | 4.7611 | 4.7611 | 1.4975 | 2.9617 | 2.9617 | 2.9617 | 2.9617 | 2.9617 | 3.5819 | 4.6223 | 5.304 | 5.6628 | 6.3804 | 7.0979 | 1.0936 | 2.1585 | 2.5901 | 2.5901 | 2.5901 | 2.5901 | 2.9562 | 3.4388 | 3.4388 | 3.4388 | 3.4388 | 3.4388
2020-01-23 09:00 | Summer | 2.3054 | 3.2993 | 4.7611 | 4.7611 | 4.7611 | 4.7611 | 1.5118 | 2.99 | 2.99 | 2.99 | 2.99 | 2.99 | 3.6771 | 4.7453 | 5.4451 | 5.8134 | 6.55 | 7.2867 | 1.0517 | 2.0757 | 2.4909 | 2.4909 | 2.4909 | 2.4909 | 3.1056 | 3.6126 | 3.6126 | 3.6126 | 3.6126 | 3.6126
2020-01-23 10:00 | Summer | 2.2863 | 3.2721 | 4.7217 | 4.7217 | 4.7217 | 4.7217 | 1.7119 | 3.3856 | 3.3856 | 3.3856 | 3.3856 | 3.3856 | 3.9305 | 5.0723 | 5.8203 | 6.214 | 7.0014 | 7.7888 | 1.0365 | 2.0456 | 2.4548 | 2.4548 | 2.4548 | 2.4548 | 3.1818 | 3.7013 | 3.7013 | 3.7013 | 3.7013 | 3.7013
2020-01-23 11:00 | Summer | 2.2863 | 3.2721 | 4.7217 | 4.7217 | 4.7217 | 4.7217 | 1.6919 | 3.3461 | 3.3461 | 3.3461 | 3.3461 | 3.3461 | 4.0391 | 5.2124 | 5.9811 | 6.3857 | 7.1949 | 8.004 | 1.0479 | 2.0682 | 2.4818 | 2.4818 | 2.4818 | 2.4818 | 3.3723 | 3.9229 | 3.9229 | 3.9229 | 3.9229 | 3.9229
2020-01-23 12:00 | Summer | 2.4387 | 3.4902 | 5.0365 | 5.0365 | 5.0365 | 5.0365 | 1.6633 | 3.2896 | 3.2896 | 3.2896 | 3.2896 | 3.2896 | 4.6298 | 5.9746 | 6.8557 | 7.3195 | 8.2469 | 9.1744 | 1.4175 | 2.7977 | 3.3573 | 3.3573 | 3.3573 | 3.3573 | 3.3723 | 3.9229 | 3.9229 | 3.9229 | 3.9229 | 3.9229
2020-01-23 13:00 | Summer | 2.3054 | 3.2993 | 4.7611 | 4.7611 | 4.7611 | 4.7611 | 1.5861 | 3.137 | 3.137 | 3.137 | 3.137 | 3.137 | 4.0201 | 5.1878 | 5.9529 | 6.3556 | 7.1609 | 7.9663 | 1.307 | 2.5796 | 3.0955 | 3.0955 | 3.0955 | 3.0955 | 3.2961 | 3.8342 | 3.8342 | 3.8342 | 3.8342 | 3.8342
2020-01-23 14:00 | Summer | 1.9815 | 2.8358 | 4.0922 | 4.0922 | 4.0922 | 4.0922 | 1.7119 | 3.3856 | 3.3856 | 3.3856 | 3.3856 | 3.3856 | 4.1916 | 5.4091 | 6.2068 | 6.6267 | 7.4664 | 8.3061 | 1.1889 | 2.3465 | 2.8158 | 2.8158 | 2.8158 | 2.8158 | 3.2389 | 3.7677 | 3.7677 | 3.7677 | 3.7677 | 3.7677
2020-01-23 15:00 | Summer | 1.9435 | 2.7815 | 4.0138 | 4.0138 | 4.0138 | 4.0138 | 1.4461 | 2.86 | 2.86 | 2.86 | 2.86 | 2.86 | 3.8867 | 5.0157 | 5.7554 | 6.1447 | 6.9234 | 7.702 | 1.086 | 2.1434 | 2.5721 | 2.5721 | 2.5721 | 2.5721 | 3.1246 | 3.6348 | 3.6348 | 3.6348 | 3.6348 | 3.6348
2020-01-23 16:00 | Summer | 1.8197 | 2.6043 | 3.7581 | 3.7581 | 3.7581 | 3.7581 | 1.549 | 3.0635 | 3.0635 | 3.0635 | 3.0635 | 3.0635 | 3.982 | 5.1387 | 5.8965 | 6.2953 | 7.0931 | 7.8908 | 1.1241 | 2.2186 | 2.6623 | 2.6623 | 2.6623 | 2.6623 | 3.0675 | 3.5683 | 3.5683 | 3.5683 | 3.5683 | 3.5683
2020-01-23 17:00 | Summer | 1.7147 | 2.4541 | 3.5413 | 3.5413 | 3.5413 | 3.5413 | 1.5204 | 3.007 | 3.007 | 3.007 | 3.007 | 3.007 | 3.9058 | 5.0403 | 5.7836 | 6.1749 | 6.9573 | 7.7397 | 1.1241 | 2.2186 | 2.6623 | 2.6623 | 2.6623 | 2.6623 | 2.9774 | 3.4635 | 3.4635 | 3.4635 | 3.4635 | 3.4635
2020-01-23 18:00 | Summer | 1.3722 | 1.9638 | 2.8339 | 2.8339 | 2.8339 | 2.8339 | 1.0717 | 2.1196 | 2.1196 | 2.1196 | 2.1196 | 2.1196 | 3.4792 | 4.4899 | 5.152 | 5.5005 | 6.1975 | 6.8945 | 0.98311 | 1.9403 | 2.3284 | 2.3284 | 2.3284 | 2.3284 | 2.0774 | 2.4166 | 2.4166 | 2.4166 | 2.4166 | 2.4166
2020-01-23 19:00 | Summer | 0.89569 | 1.2819 | 1.8498 | 1.8498 | 1.8498 | 1.8498 | 0.86022 | 1.7013 | 1.7013 | 1.7013 | 1.7013 | 1.7013 | 3.0103 | 3.8847 | 4.4576 | 4.7592 | 5.3622 | 5.9653 | 0.85984 | 1.697 | 2.0365 | 2.0365 | 2.0365 | 2.0365 | 1.3337 | 1.5514 | 1.5514 | 1.5514 | 1.5514 | 1.5514
2020-01-23 20:00 | Summer | 0.87642 | 1.2543 | 1.81 | 1.81 | 1.81 | 1.81 | 0.7802 | 1.543 | 1.543 | 1.543 | 1.543 | 1.543 | 2.6102 | 3.3684 | 3.8652 | 4.1266 | 4.6495 | 5.1724 | 1.0326 | 2.0381 | 2.4457 | 2.4457 | 2.4457 | 2.4457 | 1.2956 | 1.5071 | 1.5071 | 1.5071 | 1.5071 | 1.5071
2020-01-23 21:00 | Summer | 0.79702 | 1.1407 | 1.646 | 1.646 | 1.646 | 1.646 | 0.70018 | 1.3848 | 1.3848 | 1.3848 | 1.3848 | 1.3848 | 2.553 | 3.2946 | 3.7805 | 4.0362 | 4.5477 | 5.0591 | 1.0136 | 2.0005 | 2.4006 | 2.4006 | 2.4006 | 2.4006 | 1.1432 | 1.3298 | 1.3298 | 1.3298 | 1.3298 | 1.3298
2020-01-23 22:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.64016 | 1.2661 | 1.2661 | 1.2661 | 1.2661 | 1.2661 | 2.4006 | 3.098 | 3.5548 | 3.7953 | 4.2762 | 4.7571 | 0.86498 | 1.7072 | 2.0486 | 2.0486 | 2.0486 | 2.0486 | 1.0288 | 1.1968 | 1.1968 | 1.1968 | 1.1968 | 1.1968
2020-01-23 23:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.60587 | 1.1983 | 1.1983 | 1.1983 | 1.1983 | 1.1983 | 2.2103 | 2.8524 | 3.273 | 3.4944 | 3.9372 | 4.38 | 0.80402 | 1.5869 | 1.9042 | 1.9042 | 1.9042 | 1.9042 | 0.95221 | 1.1077 | 1.1077 | 1.1077 | 1.1077 | 1.1077
2020-01-24 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.59444 | 1.1756 | 1.1756 | 1.1756 | 1.1756 | 1.1756 | 2.0005 | 2.5816 | 2.9624 | 3.1627 | 3.5635 | 3.9643 | 0.5792 | 1.1431 | 1.3718 | 1.3718 | 1.3718 | 1.3718 | 0.99073 | 1.1525 | 1.1525 | 1.1525 | 1.1525 | 1.1525
2020-01-24 01:00 | Summer | 0.57187 | 0.81844 | 1.181 | 1.181 | 1.181 | 1.181 | 0.64588 | 1.2774 | 1.2774 | 1.2774 | 1.2774 | 1.2774 | 1.9243 | 2.4833 | 2.8495 | 3.0422 | 3.4277 | 3.8132 | 0.49918 | 0.98521 | 1.1823 | 1.1823 | 1.1823 | 1.1823 | 0.97168 | 1.1303 | 1.1303 | 1.1303 | 1.1303 | 1.1303
2020-01-24 02:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.57157 | 1.1304 | 1.1304 | 1.1304 | 1.1304 | 1.1304 | 1.8672 | 2.4095 | 2.7649 | 2.9519 | 3.3259 | 3.7 | 0.49155 | 0.97017 | 1.1642 | 1.1642 | 1.1642 | 1.1642 | 0.97168 | 1.1303 | 1.1303 | 1.1303 | 1.1303 | 1.1303
2020-01-24 03:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.59729 | 1.1813 | 1.1813 | 1.1813 | 1.1813 | 1.1813 | 1.9624 | 2.5325 | 2.9059 | 3.1025 | 3.4956 | 3.8887 | 0.49536 | 0.97769 | 1.1732 | 1.1732 | 1.1732 | 1.1732 | 0.95263 | 1.1082 | 1.1082 | 1.1082 | 1.1082 | 1.1082
2020-01-24 04:00 | Summer | 0.6698 | 0.95859 | 1.3833 | 1.3833 | 1.3833 | 1.3833 | 0.563 | 1.1135 | 1.1135 | 1.1135 | 1.1135 | 1.1135 | 1.9624 | 2.5325 | 2.9059 | 3.1025 | 3.4956 | 3.8887 | 0.54109 | 1.0679 | 1.2815 | 1.2815 | 1.2815 | 1.2815 | 1.0096 | 1.1744 | 1.1744 | 1.1744 | 1.1744 | 1.1744
2020-01-24 05:00 | Summer | 0.83831 | 1.1998 | 1.7313 | 1.7313 | 1.7313 | 1.7313 | 0.58015 | 1.1474 | 1.1474 | 1.1474 | 1.1474 | 1.1474 | 2.0005 | 2.5816 | 2.9624 | 3.1627 | 3.5635 | 3.9643 | 0.73924 | 1.459 | 1.7508 | 1.7508 | 1.7508 | 1.7508 | 1.2894 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
2020-01-24 06:00 | Summer | 1.1622 | 1.6633 | 2.4002 | 2.4002 | 2.4002 | 2.4002 | 0.84468 | 1.6706 | 1.6706 | 1.6706 | 1.6706 | 1.6706 | 2.1148 | 2.7291 | 3.1316 | 3.3435 | 3.7671 | 4.1908 | 0.86117 | 1.6997 | 2.0396 | 2.0396 | 2.0396 | 2.0396 | 1.3527 | 1.5736 | 1.5736 | 1.5736 | 1.5736 | 1.5736
2020-01-24 07:00 | Summer | 1.5242 | 2.1814 | 3.1478 | 3.1478 | 3.1478 | 3.1478 | 0.97453 | 1.9274 | 1.9274 | 1.9274 | 1.9274 | 1.9274 | 2.8906 | 3.7303 | 4.2804 | 4.57 | 5.149 | 5.7281 | 1.1203 | 2.2111 | 2.6533 | 2.6533 | 2.6533 | 2.6533 | 1.8672 | 2.172 | 2.172 | 2.172 | 2.172 | 2.172
2020-01-24 08:00 | Summer | 1.9897 | 2.8476 | 4.1092 | 4.1092 | 4.1092 | 4.1092 | 1.1146 | 2.2043 | 2.2043 | 2.2043 | 2.2043 | 2.2043 | 3.1437 | 4.0568 | 4.6551 | 4.97 | 5.5998 | 6.2296 | 1.0136 | 2.0005 | 2.4006 | 2.4006 | 2.4006 | 2.4006 | 2.4768 | 2.8812 | 2.8812 | 2.8812 | 2.8812 | 2.8812
2020-01-24 09:00 | Summer | 2.2482 | 3.2175 | 4.643 | 4.643 | 4.643 | 4.643 | 1.0546 | 2.0856 | 2.0856 | 2.0856 | 2.0856 | 2.0856 | 3.3342 | 4.3027 | 4.9373 | 5.2712 | 5.9392 | 6.6071 | 1.0403 | 2.0532 | 2.4638 | 2.4638 | 2.4638 | 2.4638 | 2.6483 | 3.0807 | 3.0807 | 3.0807 | 3.0807 | 3.0807
2020-01-24 10:00 | Summer | 2.0767 | 2.9721 | 4.2889 | 4.2889 | 4.2889 | 4.2889 | 1.2032 | 2.3796 | 2.3796 | 2.3796 | 2.3796 | 2.3796 | 3.2961 | 4.2535 | 4.8808 | 5.211 | 5.8713 | 6.5316 | 0.98692 | 1.9479 | 2.3374 | 2.3374 | 2.3374 | 2.3374 | 2.61 | 3.0361 | 3.0361 | 3.0361 | 3.0361 | 3.0361
2020-01-24 11:00 | Summer | 2.0958 | 2.9994 | 4.3282 | 4.3282 | 4.3282 | 4.3282 | 1.3003 | 2.5717 | 2.5717 | 2.5717 | 2.5717 | 2.5717 | 3.4866 | 4.4994 | 5.163 | 5.5122 | 6.2107 | 6.9091 | 1.0022 | 1.978 | 2.3735 | 2.3735 | 2.3735 | 2.3735 | 2.8007 | 3.258 | 3.258 | 3.258 | 3.258 | 3.258
2020-01-24 12:00 | Summer | 2.0196 | 2.8903 | 4.1709 | 4.1709 | 4.1709 | 4.1709 | 1.2403 | 2.453 | 2.453 | 2.453 | 2.453 | 2.453 | 3.3342 | 4.3027 | 4.9373 | 5.2712 | 5.9392 | 6.6071 | 1.0288 | 2.0306 | 2.4367 | 2.4367 | 2.4367 | 2.4367 | 2.8388 | 3.3023 | 3.3023 | 3.3023 | 3.3023 | 3.3023
2020-01-24 13:00 | Summer | 1.9053 | 2.7267 | 3.9348 | 3.9348 | 3.9348 | 3.9348 | 1.3403 | 2.6509 | 2.6509 | 2.6509 | 2.6509 | 2.6509 | 3.4104 | 4.4011 | 5.0501 | 5.3917 | 6.0749 | 6.7581 | 1.0174 | 2.008 | 2.4096 | 2.4096 | 2.4096 | 2.4096 | 2.8435 | 3.3078 | 3.3078 | 3.3078 | 3.3078 | 3.3078
2020-01-24 14:00 | Summer | 1.81 | 2.5904 | 3.738 | 3.738 | 3.738 | 3.738 | 1.2632 | 2.4983 | 2.4983 | 2.4983 | 2.4983 | 2.4983 | 3.3723 | 4.3519 | 4.9937 | 5.3315 | 6.007 | 6.6826 | 0.98692 | 1.9479 | 2.3374 | 2.3374 | 2.3374 | 2.3374 | 2.8769 | 3.3466 | 3.3466 | 3.3466 | 3.3466 | 3.3466
2020-01-24 15:00 | Summer | 1.7909 | 2.5631 | 3.6987 | 3.6987 | 3.6987 | 3.6987 | 1.3518 | 2.6735 | 2.6735 | 2.6735 | 2.6735 | 2.6735 | 3.4485 | 4.4502 | 5.1065 | 5.4519 | 6.1428 | 6.8336 | 0.98692 | 1.9479 | 2.3374 | 2.3374 | 2.3374 | 2.3374 | 2.896 | 3.3688 | 3.3688 | 3.3688 | 3.3688 | 3.3688
2020-01-24 16:00 | Summer | 1.7719 | 2.5359 | 3.6593 | 3.6593 | 3.6593 | 3.6593 | 1.2517 | 2.4756 | 2.4756 | 2.4756 | 2.4756 | 2.4756 | 3.5247 | 4.5486 | 5.2194 | 5.5724 | 6.2785 | 6.9846 | 0.98311 | 1.9403 | 2.3284 | 2.3284 | 2.3284 | 2.3284 | 2.7817 | 3.2358 | 3.2358 | 3.2358 | 3.2358 | 3.2358
2020-01-24 17:00 | Summer | 1.6768 | 2.3998 | 3.463 | 3.463 | 3.463 | 3.463 | 1.2546 | 2.4813 | 2.4813 | 2.4813 | 2.4813 | 2.4813 | 3.3914 | 4.3765 | 5.0219 | 5.3616 | 6.041 | 6.7204 | 1.0288 | 2.0306 | 2.4367 | 2.4367 | 2.4367 | 2.4367 | 2.5866 | 3.0089 | 3.0089 | 3.0089 | 3.0089 | 3.0089
2020-01-24 18:00 | Summer | 1.1362 | 1.6261 | 2.3465 | 2.3465 | 2.3465 | 2.3465 | 1.0989 | 2.1733 | 2.1733 | 2.1733 | 2.1733 | 2.1733 | 3.2776 | 4.2297 | 4.8535 | 5.1818 | 5.8384 | 6.495 | 0.91071 | 1.7975 | 2.1569 | 2.1569 | 2.1569 | 2.1569 | 1.974 | 2.2963 | 2.2963 | 2.2963 | 2.2963 | 2.2963
2020-01-24 19:00 | Summer | 0.74305 | 1.0634 | 1.5346 | 1.5346 | 1.5346 | 1.5346 | 0.68875 | 1.3622 | 1.3622 | 1.3622 | 1.3622 | 1.3622 | 2.8968 | 3.7383 | 4.2896 | 4.5798 | 5.1601 | 5.7404 | 0.95263 | 1.8802 | 2.2562 | 2.2562 | 2.2562 | 2.2562 | 1.2956 | 1.5071 | 1.5071 | 1.5071 | 1.5071 | 1.5071
2020-01-24 20:00 | Summer | 0.66684 | 0.95435 | 1.3772 | 1.3772 | 1.3772 | 1.3772 | 0.6716 | 1.3283 | 1.3283 | 1.3283 | 1.3283 | 1.3283 | 2.6483 | 3.4176 | 3.9216 | 4.1869 | 4.7174 | 5.2479 | 0.95263 | 1.8802 | 2.2562 | 2.2562 | 2.2562 | 2.2562 | 1.1981 | 1.3937 | 1.3937 | 1.3937 | 1.3937 | 1.3937
2020-01-24 21:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.62587 | 1.2378 | 1.2378 | 1.2378 | 1.2378 | 1.2378 | 2.4387 | 3.1471 | 3.6112 | 3.8555 | 4.3441 | 4.8326 | 0.91833 | 1.8125 | 2.175 | 2.175 | 2.175 | 2.175 | 1.1432 | 1.3298 | 1.3298 | 1.3298 | 1.3298 | 1.3298
2020-01-24 22:00 | Summer | 0.56827 | 0.81329 | 1.1736 | 1.1736 | 1.1736 | 1.1736 | 0.58015 | 1.1474 | 1.1474 | 1.1474 | 1.1474 | 1.1474 | 2.3625 | 3.0488 | 3.4984 | 3.735 | 4.2083 | 4.6816 | 0.92214 | 1.82 | 2.184 | 2.184 | 2.184 | 2.184 | 1.105 | 1.2855 | 1.2855 | 1.2855 | 1.2855 | 1.2855
2020-01-24 23:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.56872 | 1.1248 | 1.1248 | 1.1248 | 1.1248 | 1.1248 | 2.172 | 2.8029 | 3.2163 | 3.4338 | 3.8689 | 4.3041 | 0.84593 | 1.6696 | 2.0035 | 2.0035 | 2.0035 | 2.0035 | 1.0479 | 1.219 | 1.219 | 1.219 | 1.219 | 1.219
2020-01-25 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.62587 | 1.2378 | 1.2378 | 1.2378 | 1.2378 | 1.2378 | 2.0958 | 2.7046 | 3.1034 | 3.3133 | 3.7332 | 4.153 | 0.58682 | 1.1582 | 1.3898 | 1.3898 | 1.3898 | 1.3898 | 1.0479 | 1.219 | 1.219 | 1.219 | 1.219 | 1.219
2020-01-25 01:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.53442 | 1.057 | 1.057 | 1.057 | 1.057 | 1.057 | 1.9624 | 2.5325 | 2.9059 | 3.1025 | 3.4956 | 3.8887 | 0.5068 | 1.0003 | 1.2003 | 1.2003 | 1.2003 | 1.2003 | 0.97168 | 1.1303 | 1.1303 | 1.1303 | 1.1303 | 1.1303
2020-01-25 02:00 | Summer | 0.57027 | 0.81615 | 1.1777 | 1.1777 | 1.1777 | 1.1777 | 0.53728 | 1.0626 | 1.0626 | 1.0626 | 1.0626 | 1.0626 | 1.9434 | 2.5079 | 2.8777 | 3.0724 | 3.4617 | 3.851 | 0.51442 | 1.0153 | 1.2184 | 1.2184 | 1.2184 | 1.2184 | 0.97168 | 1.1303 | 1.1303 | 1.1303 | 1.1303 | 1.1303
2020-01-25 03:00 | Summer | 0.56677 | 0.81114 | 1.1705 | 1.1705 | 1.1705 | 1.1705 | 0.56586 | 1.1191 | 1.1191 | 1.1191 | 1.1191 | 1.1191 | 1.8481 | 2.3849 | 2.7366 | 2.9218 | 3.292 | 3.6622 | 0.54109 | 1.0679 | 1.2815 | 1.2815 | 1.2815 | 1.2815 | 0.95263 | 1.1082 | 1.1082 | 1.1082 | 1.1082 | 1.1082
2020-01-25 04:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.53728 | 1.0626 | 1.0626 | 1.0626 | 1.0626 | 1.0626 | 2.0005 | 2.5816 | 2.9624 | 3.1627 | 3.5635 | 3.9643 | 0.51823 | 1.0228 | 1.2274 | 1.2274 | 1.2274 | 1.2274 | 0.95263 | 1.1082 | 1.1082 | 1.1082 | 1.1082 | 1.1082
2020-01-25 05:00 | Summer | 0.57184 | 0.8184 | 1.181 | 1.181 | 1.181 | 1.181 | 0.51442 | 1.0174 | 1.0174 | 1.0174 | 1.0174 | 1.0174 | 1.9624 | 2.5325 | 2.9059 | 3.1025 | 3.4956 | 3.8887 | 0.68593 | 1.3538 | 1.6246 | 1.6246 | 1.6246 | 1.6246 | 1.0098 | 1.1746 | 1.1746 | 1.1746 | 1.1746 | 1.1746
2020-01-25 06:00 | Summer | 0.58183 | 0.83269 | 1.2016 | 1.2016 | 1.2016 | 1.2016 | 0.57729 | 1.1417 | 1.1417 | 1.1417 | 1.1417 | 1.1417 | 2.0577 | 2.6554 | 3.047 | 3.2531 | 3.6653 | 4.0775 | 0.89166 | 1.7599 | 2.1118 | 2.1118 | 2.1118 | 2.1118 | 1.0288 | 1.1968 | 1.1968 | 1.1968 | 1.1968 | 1.1968
2020-01-25 07:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.66874 | 1.3226 | 1.3226 | 1.3226 | 1.3226 | 1.3226 | 2.2835 | 2.9468 | 3.3814 | 3.6101 | 4.0676 | 4.525 | 0.86498 | 1.7072 | 2.0486 | 2.0486 | 2.0486 | 2.0486 | 1.1241 | 1.3076 | 1.3076 | 1.3076 | 1.3076 | 1.3076
2020-01-25 08:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.68017 | 1.3452 | 1.3452 | 1.3452 | 1.3452 | 1.3452 | 2.4609 | 3.1757 | 3.644 | 3.8905 | 4.3835 | 4.8765 | 0.94882 | 1.8727 | 2.2472 | 2.2472 | 2.2472 | 2.2472 | 1.2384 | 1.4406 | 1.4406 | 1.4406 | 1.4406 | 1.4406
2020-01-25 09:00 | Summer | 0.64779 | 0.92709 | 1.3378 | 1.3378 | 1.3378 | 1.3378 | 0.75734 | 1.4978 | 1.4978 | 1.4978 | 1.4978 | 1.4978 | 2.6483 | 3.4176 | 3.9216 | 4.1869 | 4.7174 | 5.2479 | 0.93738 | 1.8501 | 2.2201 | 2.2201 | 2.2201 | 2.2201 | 1.2956 | 1.5071 | 1.5071 | 1.5071 | 1.5071 | 1.5071
2020-01-25 10:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.75734 | 1.4978 | 1.4978 | 1.4978 | 1.4978 | 1.4978 | 2.7817 | 3.5897 | 4.1191 | 4.3977 | 4.955 | 5.5122 | 0.9793 | 1.9328 | 2.3194 | 2.3194 | 2.3194 | 2.3194 | 1.3146 | 1.5293 | 1.5293 | 1.5293 | 1.5293 | 1.5293
2020-01-25 11:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.7259 | 1.4356 | 1.4356 | 1.4356 | 1.4356 | 1.4356 | 2.7817 | 3.5897 | 4.1191 | 4.3977 | 4.955 | 5.5122 | 0.89166 | 1.7599 | 2.1118 | 2.1118 | 2.1118 | 2.1118 | 1.4861 | 1.7287 | 1.7287 | 1.7287 | 1.7287 | 1.7287
2020-01-25 12:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.73161 | 1.447 | 1.447 | 1.447 | 1.447 | 1.447 | 2.7817 | 3.5897 | 4.1191 | 4.3977 | 4.955 | 5.5122 | 0.88023 | 1.7373 | 2.0847 | 2.0847 | 2.0847 | 2.0847 | 1.3718 | 1.5957 | 1.5957 | 1.5957 | 1.5957 | 1.5957
2020-01-25 13:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.7259 | 1.4356 | 1.4356 | 1.4356 | 1.4356 | 1.4356 | 2.7436 | 3.5405 | 4.0627 | 4.3375 | 4.8871 | 5.4367 | 0.89547 | 1.7674 | 2.1208 | 2.1208 | 2.1208 | 2.1208 | 1.295 | 1.5065 | 1.5065 | 1.5065 | 1.5065 | 1.5065
2020-01-25 14:00 | Summer | 0.57173 | 0.81824 | 1.1807 | 1.1807 | 1.1807 | 1.1807 | 0.74305 | 1.4696 | 1.4696 | 1.4696 | 1.4696 | 1.4696 | 2.7817 | 3.5897 | 4.1191 | 4.3977 | 4.955 | 5.5122 | 0.89928 | 1.7749 | 2.1299 | 2.1299 | 2.1299 | 2.1299 | 1.2956 | 1.5071 | 1.5071 | 1.5071 | 1.5071 | 1.5071
2020-01-25 15:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.7259 | 1.4356 | 1.4356 | 1.4356 | 1.4356 | 1.4356 | 2.8198 | 3.6389 | 4.1755 | 4.4579 | 5.0228 | 5.5877 | 0.94501 | 1.8651 | 2.2382 | 2.2382 | 2.2382 | 2.2382 | 1.2575 | 1.4628 | 1.4628 | 1.4628 | 1.4628 | 1.4628
2020-01-25 16:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.69446 | 1.3735 | 1.3735 | 1.3735 | 1.3735 | 1.3735 | 2.896 | 3.7372 | 4.2884 | 4.5784 | 5.1586 | 5.7387 | 0.88023 | 1.7373 | 2.0847 | 2.0847 | 2.0847 | 2.0847 | 1.2194 | 1.4184 | 1.4184 | 1.4184 | 1.4184 | 1.4184
2020-01-25 17:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.71447 | 1.413 | 1.413 | 1.413 | 1.413 | 1.413 | 3.0865 | 3.9831 | 4.5705 | 4.8796 | 5.498 | 6.1163 | 0.98311 | 1.9403 | 2.3284 | 2.3284 | 2.3284 | 2.3284 | 1.3146 | 1.5293 | 1.5293 | 1.5293 | 1.5293 | 1.5293
2020-01-25 18:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.81449 | 1.6109 | 1.6109 | 1.6109 | 1.6109 | 1.6109 | 2.8579 | 3.688 | 4.2319 | 4.5182 | 5.0907 | 5.6632 | 0.99073 | 1.9554 | 2.3465 | 2.3465 | 2.3465 | 2.3465 | 1.2003 | 1.3963 | 1.3963 | 1.3963 | 1.3963 | 1.3963
2020-01-25 19:00 | Summer | 0.66684 | 0.95435 | 1.3772 | 1.3772 | 1.3772 | 1.3772 | 0.7259 | 1.4356 | 1.4356 | 1.4356 | 1.4356 | 1.4356 | 2.915 | 3.7618 | 4.3166 | 4.6086 | 5.1925 | 5.7765 | 0.97549 | 1.9253 | 2.3104 | 2.3104 | 2.3104 | 2.3104 | 1.1813 | 1.3741 | 1.3741 | 1.3741 | 1.3741 | 1.3741
2020-01-25 20:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.70304 | 1.3904 | 1.3904 | 1.3904 | 1.3904 | 1.3904 | 2.7626 | 3.5651 | 4.0909 | 4.3676 | 4.921 | 5.4745 | 0.96025 | 1.8952 | 2.2743 | 2.2743 | 2.2743 | 2.2743 | 1.1432 | 1.3298 | 1.3298 | 1.3298 | 1.3298 | 1.3298
2020-01-25 21:00 | Summer | 0.60961 | 0.87246 | 1.259 | 1.259 | 1.259 | 1.259 | 0.6373 | 1.2604 | 1.2604 | 1.2604 | 1.2604 | 1.2604 | 2.7245 | 3.5159 | 4.0344 | 4.3073 | 4.8531 | 5.3989 | 0.98692 | 1.9479 | 2.3374 | 2.3374 | 2.3374 | 2.3374 | 1.1432 | 1.3298 | 1.3298 | 1.3298 | 1.3298 | 1.3298
2020-01-25 22:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.59444 | 1.1756 | 1.1756 | 1.1756 | 1.1756 | 1.1756 | 2.6674 | 3.4422 | 3.9498 | 4.217 | 4.7513 | 5.2857 | 0.91452 | 1.805 | 2.166 | 2.166 | 2.166 | 2.166 | 1.105 | 1.2855 | 1.2855 | 1.2855 | 1.2855 | 1.2855
2020-01-25 23:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.62587 | 1.2378 | 1.2378 | 1.2378 | 1.2378 | 1.2378 | 2.534 | 3.2701 | 3.7523 | 4.0061 | 4.5138 | 5.0214 | 0.86879 | 1.7147 | 2.0577 | 2.0577 | 2.0577 | 2.0577 | 1.0669 | 1.2411 | 1.2411 | 1.2411 | 1.2411 | 1.2411
2020-01-26 | Summer | 0.60933 | 0.87205 | 1.2584 | 1.2584 | 1.2584 | 1.2584 | 0.60873 | 1.2039 | 1.2039 | 1.2039 | 1.2039 | 1.2039 | 2.2673 | 2.9258 | 3.3573 | 3.5844 | 4.0386 | 4.4928 | 0.71637 | 1.4139 | 1.6967 | 1.6967 | 1.6967 | 1.6967 | 1.0669 | 1.2411 | 1.2411 | 1.2411 | 1.2411 | 1.2411
2020-01-26 01:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.61444 | 1.2152 | 1.2152 | 1.2152 | 1.2152 | 1.2152 | 2.1532 | 2.7787 | 3.1885 | 3.4041 | 3.8355 | 4.2668 | 0.68589 | 1.3537 | 1.6245 | 1.6245 | 1.6245 | 1.6245 | 1.0288 | 1.1968 | 1.1968 | 1.1968 | 1.1968 | 1.1968
2020-01-26 02:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.59729 | 1.1813 | 1.1813 | 1.1813 | 1.1813 | 1.1813 | 2.1148 | 2.7291 | 3.1316 | 3.3435 | 3.7671 | 4.1908 | 0.62492 | 1.2334 | 1.4801 | 1.4801 | 1.4801 | 1.4801 | 1.0669 | 1.2411 | 1.2411 | 1.2411 | 1.2411 | 1.2411
2020-01-26 03:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.563 | 1.1135 | 1.1135 | 1.1135 | 1.1135 | 1.1135 | 2.0767 | 2.68 | 3.0752 | 3.2832 | 3.6992 | 4.1153 | 0.51061 | 1.0078 | 1.2093 | 1.2093 | 1.2093 | 1.2093 | 1.0288 | 1.1968 | 1.1968 | 1.1968 | 1.1968 | 1.1968
2020-01-26 04:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.54299 | 1.0739 | 1.0739 | 1.0739 | 1.0739 | 1.0739 | 2.1148 | 2.7291 | 3.1316 | 3.3435 | 3.7671 | 4.1908 | 0.52204 | 1.0303 | 1.2364 | 1.2364 | 1.2364 | 1.2364 | 1.0098 | 1.1746 | 1.1746 | 1.1746 | 1.1746 | 1.1746
2020-01-26 05:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.6173 | 1.2209 | 1.2209 | 1.2209 | 1.2209 | 1.2209 | 2.1182 | 2.7335 | 3.1366 | 3.3488 | 3.7732 | 4.1975 | 0.6897 | 1.3613 | 1.6335 | 1.6335 | 1.6335 | 1.6335 | 1.0479 | 1.219 | 1.219 | 1.219 | 1.219 | 1.219
2020-01-26 06:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.62587 | 1.2378 | 1.2378 | 1.2378 | 1.2378 | 1.2378 | 2.2101 | 2.8521 | 3.2727 | 3.4941 | 3.9368 | 4.3796 | 0.87261 | 1.7222 | 2.0667 | 2.0667 | 2.0667 | 2.0667 | 1.0098 | 1.1746 | 1.1746 | 1.1746 | 1.1746 | 1.1746
2020-01-26 07:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.64016 | 1.2661 | 1.2661 | 1.2661 | 1.2661 | 1.2661 | 2.4059 | 3.1047 | 3.5626 | 3.8036 | 4.2855 | 4.7675 | 0.89547 | 1.7674 | 2.1208 | 2.1208 | 2.1208 | 2.1208 | 1.0479 | 1.219 | 1.219 | 1.219 | 1.219 | 1.219
2020-01-26 08:00 | Summer | 0.57898 | 0.82861 | 1.1957 | 1.1957 | 1.1957 | 1.1957 | 0.62016 | 1.2265 | 1.2265 | 1.2265 | 1.2265 | 1.2265 | 2.7055 | 3.4913 | 4.0062 | 4.2772 | 4.8192 | 5.3612 | 0.95263 | 1.8802 | 2.2562 | 2.2562 | 2.2562 | 2.2562 | 1.0669 | 1.2411 | 1.2411 | 1.2411 | 1.2411 | 1.2411
2020-01-26 09:00 | Summer | 0.56511 | 0.80876 | 1.1671 | 1.1671 | 1.1671 | 1.1671 | 0.65159 | 1.2887 | 1.2887 | 1.2887 | 1.2887 | 1.2887 | 2.8579 | 3.688 | 4.2319 | 4.5182 | 5.0907 | 5.6632 | 1.0403 | 2.0532 | 2.4638 | 2.4638 | 2.4638 | 2.4638 | 1.086 | 1.2633 | 1.2633 | 1.2633 | 1.2633 | 1.2633
2020-01-26 10:00 | Summer | 0.5888 | 0.84267 | 1.216 | 1.216 | 1.216 | 1.216 | 0.60587 | 1.1983 | 1.1983 | 1.1983 | 1.1983 | 1.1983 | 2.9913 | 3.8601 | 4.4294 | 4.729 | 5.3283 | 5.9275 | 0.89928 | 1.7749 | 2.1299 | 2.1299 | 2.1299 | 2.1299 | 1.1241 | 1.3076 | 1.3076 | 1.3076 | 1.3076 | 1.3076
2020-01-26 11:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.60301 | 1.1926 | 1.1926 | 1.1926 | 1.1926 | 1.1926 | 2.9531 | 3.811 | 4.373 | 4.6688 | 5.2604 | 5.852 | 0.94501 | 1.8651 | 2.2382 | 2.2382 | 2.2382 | 2.2382 | 1.105 | 1.2855 | 1.2855 | 1.2855 | 1.2855 | 1.2855
2020-01-26 12:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.59729 | 1.1813 | 1.1813 | 1.1813 | 1.1813 | 1.1813 | 3.1246 | 4.0323 | 4.6269 | 4.9399 | 5.5658 | 6.1918 | 0.9069 | 1.7899 | 2.1479 | 2.1479 | 2.1479 | 2.1479 | 1.1813 | 1.3741 | 1.3741 | 1.3741 | 1.3741 | 1.3741
2020-01-26 13:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.60587 | 1.1983 | 1.1983 | 1.1983 | 1.1983 | 1.1983 | 3.0103 | 3.8847 | 4.4576 | 4.7592 | 5.3622 | 5.9653 | 0.92214 | 1.82 | 2.184 | 2.184 | 2.184 | 2.184 | 1.1432 | 1.3298 | 1.3298 | 1.3298 | 1.3298 | 1.3298
2020-01-26 14:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.6173 | 1.2209 | 1.2209 | 1.2209 | 1.2209 | 1.2209 | 2.9532 | 3.8111 | 4.3731 | 4.6689 | 5.2606 | 5.8522 | 0.95644 | 1.8877 | 2.2652 | 2.2652 | 2.2652 | 2.2652 | 1.1432 | 1.3298 | 1.3298 | 1.3298 | 1.3298 | 1.3298
2020-01-26 15:00 | Summer | 0.59717 | 0.85465 | 1.2333 | 1.2333 | 1.2333 | 1.2333 | 0.58586 | 1.1587 | 1.1587 | 1.1587 | 1.1587 | 1.1587 | 3.1818 | 4.106 | 4.7115 | 5.0303 | 5.6677 | 6.3051 | 0.9793 | 1.9328 | 2.3194 | 2.3194 | 2.3194 | 2.3194 | 1.1622 | 1.352 | 1.352 | 1.352 | 1.352 | 1.352
2020-01-26 16:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.56872 | 1.1248 | 1.1248 | 1.1248 | 1.1248 | 1.1248 | 2.9913 | 3.8601 | 4.4294 | 4.729 | 5.3283 | 5.9275 | 0.9793 | 1.9328 | 2.3194 | 2.3194 | 2.3194 | 2.3194 | 1.2194 | 1.4184 | 1.4184 | 1.4184 | 1.4184 | 1.4184
2020-01-26 17:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.61444 | 1.2152 | 1.2152 | 1.2152 | 1.2152 | 1.2152 | 3.0484 | 3.9339 | 4.5141 | 4.8194 | 5.4301 | 6.0408 | 0.99454 | 1.9629 | 2.3555 | 2.3555 | 2.3555 | 2.3555 | 1.2384 | 1.4406 | 1.4406 | 1.4406 | 1.4406 | 1.4406
2020-01-26 18:00 | Summer | 0.60987 | 0.87282 | 1.2595 | 1.2595 | 1.2595 | 1.2595 | 0.61444 | 1.2152 | 1.2152 | 1.2152 | 1.2152 | 1.2152 | 2.9993 | 3.8706 | 4.4414 | 4.7418 | 5.3427 | 5.9435 | 0.97168 | 1.9178 | 2.3013 | 2.3013 | 2.3013 | 2.3013 | 1.2575 | 1.4628 | 1.4628 | 1.4628 | 1.4628 | 1.4628
2020-01-26 19:00 | Summer | 0.64779 | 0.92709 | 1.3378 | 1.3378 | 1.3378 | 1.3378 | 0.65159 | 1.2887 | 1.2887 | 1.2887 | 1.2887 | 1.2887 | 2.9722 | 3.8356 | 4.4012 | 4.6989 | 5.2943 | 5.8898 | 0.96406 | 1.9027 | 2.2833 | 2.2833 | 2.2833 | 2.2833 | 1.1241 | 1.3076 | 1.3076 | 1.3076 | 1.3076 | 1.3076
2020-01-26 20:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.62016 | 1.2265 | 1.2265 | 1.2265 | 1.2265 | 1.2265 | 2.8198 | 3.6389 | 4.1755 | 4.4579 | 5.0228 | 5.5877 | 0.99454 | 1.9629 | 2.3555 | 2.3555 | 2.3555 | 2.3555 | 1.105 | 1.2855 | 1.2855 | 1.2855 | 1.2855 | 1.2855
2020-01-26 21:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.61158 | 1.2096 | 1.2096 | 1.2096 | 1.2096 | 1.2096 | 2.8198 | 3.6389 | 4.1755 | 4.4579 | 5.0228 | 5.5877 | 1.006 | 1.9855 | 2.3826 | 2.3826 | 2.3826 | 2.3826 | 1.1241 | 1.3076 | 1.3076 | 1.3076 | 1.3076 | 1.3076
2020-01-26 22:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.54014 | 1.0683 | 1.0683 | 1.0683 | 1.0683 | 1.0683 | 2.7055 | 3.4913 | 4.0062 | 4.2772 | 4.8192 | 5.3612 | 0.95263 | 1.8802 | 2.2562 | 2.2562 | 2.2562 | 2.2562 | 1.086 | 1.2633 | 1.2633 | 1.2633 | 1.2633 | 1.2633
2020-01-26 23:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.56586 | 1.1191 | 1.1191 | 1.1191 | 1.1191 | 1.1191 | 2.5149 | 3.2455 | 3.7241 | 3.976 | 4.4798 | 4.9836 | 0.88404 | 1.7448 | 2.0938 | 2.0938 | 2.0938 | 2.0938 | 1.086 | 1.2633 | 1.2633 | 1.2633 | 1.2633 | 1.2633
2020-01-27 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.56014 | 1.1078 | 1.1078 | 1.1078 | 1.1078 | 1.1078 | 2.1529 | 2.7783 | 3.1881 | 3.4037 | 3.835 | 4.2663 | 0.58006 | 1.1449 | 1.3738 | 1.3738 | 1.3738 | 1.3738 | 1.0098 | 1.1746 | 1.1746 | 1.1746 | 1.1746 | 1.1746
2020-01-27 01:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.54299 | 1.0739 | 1.0739 | 1.0739 | 1.0739 | 1.0739 | 2.0196 | 2.6062 | 2.9906 | 3.1929 | 3.5974 | 4.002 | 0.55633 | 1.098 | 1.3176 | 1.3176 | 1.3176 | 1.3176 | 1.0098 | 1.1746 | 1.1746 | 1.1746 | 1.1746 | 1.1746
2020-01-27 02:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.54585 | 1.0796 | 1.0796 | 1.0796 | 1.0796 | 1.0796 | 2.0094 | 2.593 | 2.9754 | 3.1767 | 3.5792 | 3.9818 | 0.52585 | 1.0379 | 1.2454 | 1.2454 | 1.2454 | 1.2454 | 1.0558 | 1.2282 | 1.2282 | 1.2282 | 1.2282 | 1.2282
2020-01-27 03:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.53156 | 1.0513 | 1.0513 | 1.0513 | 1.0513 | 1.0513 | 2.0005 | 2.5816 | 2.9624 | 3.1627 | 3.5635 | 3.9643 | 0.60968 | 1.2033 | 1.444 | 1.444 | 1.444 | 1.444 | 1.2003 | 1.3963 | 1.3963 | 1.3963 | 1.3963 | 1.3963
2020-01-27 04:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.60587 | 1.1983 | 1.1983 | 1.1983 | 1.1983 | 1.1983 | 2.0005 | 2.5816 | 2.9624 | 3.1627 | 3.5635 | 3.9643 | 0.60206 | 1.1883 | 1.4259 | 1.4259 | 1.4259 | 1.4259 | 1.1432 | 1.3298 | 1.3298 | 1.3298 | 1.3298 | 1.3298
2020-01-27 05:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.7259 | 1.4356 | 1.4356 | 1.4356 | 1.4356 | 1.4356 | 2.0386 | 2.6308 | 3.0188 | 3.223 | 3.6314 | 4.0398 | 0.80337 | 1.5856 | 1.9027 | 1.9027 | 1.9027 | 1.9027 | 1.3476 | 1.5676 | 1.5676 | 1.5676 | 1.5676 | 1.5676
2020-01-27 06:00 | Summer | 0.60272 | 0.86259 | 1.2447 | 1.2447 | 1.2447 | 1.2447 | 0.90023 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 2.2291 | 2.8767 | 3.3009 | 3.5242 | 3.9708 | 4.4173 | 0.80402 | 1.5869 | 1.9042 | 1.9042 | 1.9042 | 1.9042 | 1.5433 | 1.7952 | 1.7952 | 1.7952 | 1.7952 | 1.7952
2020-01-27 07:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.87165 | 1.7239 | 1.7239 | 1.7239 | 1.7239 | 1.7239 | 2.3816 | 3.0734 | 3.5266 | 3.7652 | 4.2423 | 4.7194 | 0.84593 | 1.6696 | 2.0035 | 2.0035 | 2.0035 | 2.0035 | 1.9434 | 2.2606 | 2.2606 | 2.2606 | 2.2606 | 2.2606
2020-01-27 08:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.91452 | 1.8087 | 1.8087 | 1.8087 | 1.8087 | 1.8087 | 2.6864 | 3.4668 | 3.978 | 4.2471 | 4.7853 | 5.3234 | 0.85355 | 1.6846 | 2.0216 | 2.0216 | 2.0216 | 2.0216 | 2.0958 | 2.4379 | 2.4379 | 2.4379 | 2.4379 | 2.4379
2020-01-27 09:00 | Summer | 0.57176 | 0.81828 | 1.1808 | 1.1808 | 1.1808 | 1.1808 | 0.83164 | 1.6448 | 1.6448 | 1.6448 | 1.6448 | 1.6448 | 2.7436 | 3.5405 | 4.0627 | 4.3375 | 4.8871 | 5.4367 | 0.98692 | 1.9479 | 2.3374 | 2.3374 | 2.3374 | 2.3374 | 2.2101 | 2.5709 | 2.5709 | 2.5709 | 2.5709 | 2.5709
2020-01-27 10:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.97739 | 1.933 | 1.933 | 1.933 | 1.933 | 1.933 | 2.9531 | 3.811 | 4.373 | 4.6688 | 5.2604 | 5.852 | 0.99835 | 1.9704 | 2.3645 | 2.3645 | 2.3645 | 2.3645 | 2.3064 | 2.6829 | 2.6829 | 2.6829 | 2.6829 | 2.6829
2020-01-27 11:00 | Summer | 0.61005 | 0.87308 | 1.2599 | 1.2599 | 1.2599 | 1.2599 | 0.96596 | 1.9104 | 1.9104 | 1.9104 | 1.9104 | 1.9104 | 3.3533 | 4.3273 | 4.9655 | 5.3013 | 5.9731 | 6.6449 | 0.94882 | 1.8727 | 2.2472 | 2.2472 | 2.2472 | 2.2472 | 2.4387 | 2.8369 | 2.8369 | 2.8369 | 2.8369 | 2.8369
2020-01-27 12:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.96882 | 1.9161 | 1.9161 | 1.9161 | 1.9161 | 1.9161 | 3.3723 | 4.3519 | 4.9937 | 5.3315 | 6.007 | 6.6826 | 0.94882 | 1.8727 | 2.2472 | 2.2472 | 2.2472 | 2.2472 | 2.6483 | 3.0807 | 3.0807 | 3.0807 | 3.0807 | 3.0807
2020-01-27 13:00 | Summer | 0.64779 | 0.92709 | 1.3378 | 1.3378 | 1.3378 | 1.3378 | 1.0174 | 2.0122 | 2.0122 | 2.0122 | 2.0122 | 2.0122 | 3.5057 | 4.524 | 5.1912 | 5.5423 | 6.2446 | 6.9469 | 0.93357 | 1.8426 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.553 | 2.9699 | 2.9699 | 2.9699 | 2.9699 | 2.9699
2020-01-27 14:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.94596 | 1.8709 | 1.8709 | 1.8709 | 1.8709 | 1.8709 | 3.2961 | 4.2535 | 4.8808 | 5.211 | 5.8713 | 6.5316 | 0.97549 | 1.9253 | 2.3104 | 2.3104 | 2.3104 | 2.3104 | 2.5911 | 3.0142 | 3.0142 | 3.0142 | 3.0142 | 3.0142
2020-01-27 15:00 | Summer | 0.59074 | 0.84544 | 1.22 | 1.22 | 1.22 | 1.22 | 1.0888 | 2.1535 | 2.1535 | 2.1535 | 2.1535 | 2.1535 | 3.3533 | 4.3273 | 4.9655 | 5.3013 | 5.9731 | 6.6449 | 0.94119 | 1.8576 | 2.2291 | 2.2291 | 2.2291 | 2.2291 | 2.5721 | 2.992 | 2.992 | 2.992 | 2.992 | 2.992
2020-01-27 16:00 | Summer | 0.62823 | 0.89909 | 1.2974 | 1.2974 | 1.2974 | 1.2974 | 1.1546 | 2.2835 | 2.2835 | 2.2835 | 2.2835 | 2.2835 | 3.8677 | 4.9911 | 5.7272 | 6.1146 | 6.8894 | 7.6642 | 0.97549 | 1.9253 | 2.3104 | 2.3104 | 2.3104 | 2.3104 | 2.5911 | 3.0142 | 3.0142 | 3.0142 | 3.0142 | 3.0142
2020-01-27 17:00 | Summer | 0.64779 | 0.92709 | 1.3378 | 1.3378 | 1.3378 | 1.3378 | 1.1403 | 2.2552 | 2.2552 | 2.2552 | 2.2552 | 2.2552 | 3.4866 | 4.4994 | 5.163 | 5.5122 | 6.2107 | 6.9091 | 0.96406 | 1.9027 | 2.2833 | 2.2833 | 2.2833 | 2.2833 | 2.4628 | 2.8649 | 2.8649 | 2.8649 | 2.8649 | 2.8649
2020-01-27 18:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 1.0774 | 2.1309 | 2.1309 | 2.1309 | 2.1309 | 2.1309 | 3.3723 | 4.3519 | 4.9937 | 5.3315 | 6.007 | 6.6826 | 1.0212 | 2.0156 | 2.4187 | 2.4187 | 2.4187 | 2.4187 | 2.0185 | 2.3481 | 2.3481 | 2.3481 | 2.3481 | 2.3481
2020-01-27 19:00 | Summer | 0.64779 | 0.92709 | 1.3378 | 1.3378 | 1.3378 | 1.3378 | 0.86671 | 1.7141 | 1.7141 | 1.7141 | 1.7141 | 1.7141 | 3.183 | 4.1076 | 4.7133 | 5.0322 | 5.6698 | 6.3075 | 0.94882 | 1.8727 | 2.2472 | 2.2472 | 2.2472 | 2.2472 | 1.2956 | 1.5071 | 1.5071 | 1.5071 | 1.5071 | 1.5071
2020-01-27 20:00 | Summer | 0.59075 | 0.84545 | 1.22 | 1.22 | 1.22 | 1.22 | 0.71161 | 1.4074 | 1.4074 | 1.4074 | 1.4074 | 1.4074 | 2.9286 | 3.7793 | 4.3367 | 4.63 | 5.2167 | 5.8034 | 0.99073 | 1.9554 | 2.3465 | 2.3465 | 2.3465 | 2.3465 | 1.2003 | 1.3963 | 1.3963 | 1.3963 | 1.3963 | 1.3963
2020-01-27 21:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.55728 | 1.1022 | 1.1022 | 1.1022 | 1.1022 | 1.1022 | 2.8388 | 3.6634 | 4.2037 | 4.4881 | 5.0568 | 5.6255 | 0.96025 | 1.8952 | 2.2743 | 2.2743 | 2.2743 | 2.2743 | 1.1813 | 1.3741 | 1.3741 | 1.3741 | 1.3741 | 1.3741
2020-01-27 22:00 | Summer | 0.59443 | 0.85072 | 1.2276 | 1.2276 | 1.2276 | 1.2276 | 0.54299 | 1.0739 | 1.0739 | 1.0739 | 1.0739 | 1.0739 | 2.7247 | 3.5162 | 4.0348 | 4.3077 | 4.8536 | 5.3994 | 0.89547 | 1.7674 | 2.1208 | 2.1208 | 2.1208 | 2.1208 | 1.1241 | 1.3076 | 1.3076 | 1.3076 | 1.3076 | 1.3076
2020-01-27 23:00 | Summer | 0.64779 | 0.92709 | 1.3378 | 1.3378 | 1.3378 | 1.3378 | 0.55728 | 1.1022 | 1.1022 | 1.1022 | 1.1022 | 1.1022 | 2.5721 | 3.3192 | 3.8087 | 4.0664 | 4.5816 | 5.0969 | 0.8345 | 1.647 | 1.9764 | 1.9764 | 1.9764 | 1.9764 | 1.0479 | 1.219 | 1.219 | 1.219 | 1.219 | 1.219
2020-01-28 | Summer | 0.62646 | 0.89657 | 1.2938 | 1.2938 | 1.2938 | 1.2938 | 0.54585 | 1.0796 | 1.0796 | 1.0796 | 1.0796 | 1.0796 | 2.3435 | 3.0242 | 3.4702 | 3.7049 | 4.1744 | 4.6438 | 0.57157 | 1.1281 | 1.3537 | 1.3537 | 1.3537 | 1.3537 | 1.0479 | 1.219 | 1.219 | 1.219 | 1.219 | 1.219
2020-01-28 01:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.54871 | 1.0852 | 1.0852 | 1.0852 | 1.0852 | 1.0852 | 2.2101 | 2.8521 | 3.2727 | 3.4941 | 3.9368 | 4.3796 | 0.62873 | 1.2409 | 1.4891 | 1.4891 | 1.4891 | 1.4891 | 1.0479 | 1.219 | 1.219 | 1.219 | 1.219 | 1.219
2020-01-28 02:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.54014 | 1.0683 | 1.0683 | 1.0683 | 1.0683 | 1.0683 | 2.2101 | 2.8521 | 3.2727 | 3.4941 | 3.9368 | 4.3796 | 0.60587 | 1.1958 | 1.435 | 1.435 | 1.435 | 1.435 | 1.0288 | 1.1968 | 1.1968 | 1.1968 | 1.1968 | 1.1968
2020-01-28 03:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.58872 | 1.1643 | 1.1643 | 1.1643 | 1.1643 | 1.1643 | 2.1529 | 2.7783 | 3.1881 | 3.4037 | 3.835 | 4.2663 | 0.60968 | 1.2033 | 1.444 | 1.444 | 1.444 | 1.444 | 1.1241 | 1.3076 | 1.3076 | 1.3076 | 1.3076 | 1.3076
2020-01-28 04:00 | Summer | 0.60654 | 0.86806 | 1.2526 | 1.2526 | 1.2526 | 1.2526 | 0.60015 | 1.187 | 1.187 | 1.187 | 1.187 | 1.187 | 2.172 | 2.8029 | 3.2163 | 3.4338 | 3.8689 | 4.3041 | 0.56395 | 1.1131 | 1.3357 | 1.3357 | 1.3357 | 1.3357 | 1.3527 | 1.5736 | 1.5736 | 1.5736 | 1.5736 | 1.5736
2020-01-28 05:00 | Summer | 0.64779 | 0.92709 | 1.3378 | 1.3378 | 1.3378 | 1.3378 | 0.67239 | 1.3298 | 1.3298 | 1.3298 | 1.3298 | 1.3298 | 2.5911 | 3.3438 | 3.8369 | 4.0965 | 4.6156 | 5.1347 | 0.80783 | 1.5944 | 1.9133 | 1.9133 | 1.9133 | 1.9133 | 1.4512 | 1.6881 | 1.6881 | 1.6881 | 1.6881 | 1.6881
2020-01-28 06:00 | Summer | 1.0413 | 1.4903 | 2.1505 | 2.1505 | 2.1505 | 2.1505 | 1.0574 | 2.0913 | 2.0913 | 2.0913 | 2.0913 | 2.0913 | 3.1056 | 4.0077 | 4.5987 | 4.9098 | 5.5319 | 6.154 | 0.94501 | 1.8651 | 2.2382 | 2.2382 | 2.2382 | 2.2382 | 1.9091 | 2.2208 | 2.2208 | 2.2208 | 2.2208 | 2.2208
2020-01-28 07:00 | Summer | 2.0767 | 2.9721 | 4.2889 | 4.2889 | 4.2889 | 4.2889 | 1.3461 | 2.6622 | 2.6622 | 2.6622 | 2.6622 | 2.6622 | 3.5628 | 4.5978 | 5.2758 | 5.6327 | 6.3464 | 7.0602 | 1.4255 | 2.8134 | 3.3761 | 3.3761 | 3.3761 | 3.3761 | 2.8007 | 3.258 | 3.258 | 3.258 | 3.258 | 3.258
2020-01-28 08:00 | Summer | 2.8579 | 4.0901 | 5.9022 | 5.9022 | 5.9022 | 5.9022 | 1.5004 | 2.9674 | 2.9674 | 2.9674 | 2.9674 | 2.9674 | 4.0225 | 5.191 | 5.9565 | 6.3594 | 7.1653 | 7.9711 | 1.509 | 2.9782 | 3.5739 | 3.5739 | 3.5739 | 3.5739 | 3.2389 | 3.7677 | 3.7677 | 3.7677 | 3.7677 | 3.7677
2020-01-28 09:00 | Summer | 2.915 | 4.1719 | 6.0202 | 6.0202 | 6.0202 | 6.0202 | 1.6916 | 3.3455 | 3.3455 | 3.3455 | 3.3455 | 3.3455 | 4.3059 | 5.5566 | 6.3761 | 6.8074 | 7.67 | 8.5326 | 1.5776 | 3.1136 | 3.7363 | 3.7363 | 3.7363 | 3.7363 | 3.4485 | 4.0115 | 4.0115 | 4.0115 | 4.0115 | 4.0115
2020-01-28 10:00 | Summer | 2.915 | 4.1719 | 6.0202 | 6.0202 | 6.0202 | 6.0202 | 1.7605 | 3.4817 | 3.4817 | 3.4817 | 3.4817 | 3.4817 | 4.4207 | 5.7049 | 6.5462 | 6.989 | 7.8746 | 8.7602 | 1.6842 | 3.3242 | 3.989 | 3.989 | 3.989 | 3.989 | 3.639 | 4.2332 | 4.2332 | 4.2332 | 4.2332 | 4.2332
2020-01-28 11:00 | Summer | 2.8198 | 4.0356 | 5.8235 | 5.8235 | 5.8235 | 5.8235 | 1.6377 | 3.239 | 3.239 | 3.239 | 3.239 | 3.239 | 4.4774 | 5.7779 | 6.63 | 7.0785 | 7.9754 | 8.8724 | 1.5776 | 3.1136 | 3.7363 | 3.7363 | 3.7363 | 3.7363 | 3.5057 | 4.078 | 4.078 | 4.078 | 4.078 | 4.078
2020-01-28 12:00 | Summer | 2.7436 | 3.9265 | 5.6661 | 5.6661 | 5.6661 | 5.6661 | 1.529 | 3.0239 | 3.0239 | 3.0239 | 3.0239 | 3.0239 | 4.706 | 6.073 | 6.9686 | 7.44 | 8.3827 | 9.3254 | 1.4747 | 2.9105 | 3.4926 | 3.4926 | 3.4926 | 3.4926 | 3.3723 | 3.9229 | 3.9229 | 3.9229 | 3.9229 | 3.9229
2020-01-28 13:00 | Summer | 2.6671 | 3.817 | 5.5081 | 5.5081 | 5.5081 | 5.5081 | 1.6061 | 3.1765 | 3.1765 | 3.1765 | 3.1765 | 3.1765 | 4.5155 | 5.8271 | 6.6864 | 7.1387 | 8.0433 | 8.9479 | 1.4937 | 2.9481 | 3.5378 | 3.5378 | 3.5378 | 3.5378 | 3.3533 | 3.9007 | 3.9007 | 3.9007 | 3.9007 | 3.9007
2020-01-28 14:00 | Summer | 2.5149 | 3.5993 | 5.1939 | 5.1939 | 5.1939 | 5.1939 | 1.549 | 3.0635 | 3.0635 | 3.0635 | 3.0635 | 3.0635 | 4.5536 | 5.8763 | 6.7429 | 7.199 | 8.1112 | 9.0234 | 1.5052 | 2.9707 | 3.5648 | 3.5648 | 3.5648 | 3.5648 | 3.3914 | 3.945 | 3.945 | 3.945 | 3.945 | 3.945
2020-01-28 15:00 | Summer | 2.4197 | 3.4629 | 4.9972 | 4.9972 | 4.9972 | 4.9972 | 1.5204 | 3.007 | 3.007 | 3.007 | 3.007 | 3.007 | 4.4202 | 5.7042 | 6.5454 | 6.9881 | 7.8736 | 8.7591 | 1.5013 | 2.9632 | 3.5558 | 3.5558 | 3.5558 | 3.5558 | 3.4283 | 3.988 | 3.988 | 3.988 | 3.988 | 3.988
2020-01-28 16:00 | Summer | 2.4197 | 3.4629 | 4.9972 | 4.9972 | 4.9972 | 4.9972 | 1.5004 | 2.9674 | 2.9674 | 2.9674 | 2.9674 | 2.9674 | 4.4964 | 5.8025 | 6.6582 | 7.1086 | 8.0094 | 8.9101 | 1.4899 | 2.9406 | 3.5287 | 3.5287 | 3.5287 | 3.5287 | 3.4295 | 3.9894 | 3.9894 | 3.9894 | 3.9894 | 3.9894
2020-01-28 17:00 | Summer | 2.1978 | 3.1454 | 4.5389 | 4.5389 | 4.5389 | 4.5389 | 1.5404 | 3.0465 | 3.0465 | 3.0465 | 3.0465 | 3.0465 | 4.706 | 6.073 | 6.9686 | 7.44 | 8.3827 | 9.3254 | 1.4404 | 2.8428 | 3.4114 | 3.4114 | 3.4114 | 3.4114 | 3.3151 | 3.8564 | 3.8564 | 3.8564 | 3.8564 | 3.8564
2020-01-28 18:00 | Summer | 1.567 | 2.2427 | 3.2363 | 3.2363 | 3.2363 | 3.2363 | 1.2288 | 2.4302 | 2.4302 | 2.4302 | 2.4302 | 2.4302 | 4.0951 | 5.2846 | 6.0639 | 6.4741 | 7.2945 | 8.1148 | 1.1774 | 2.3239 | 2.7887 | 2.7887 | 2.7887 | 2.7887 | 2.3102 | 2.6874 | 2.6874 | 2.6874 | 2.6874 | 2.6874
2020-01-28 19:00 | Summer | 0.81926 | 1.1725 | 1.692 | 1.692 | 1.692 | 1.692 | 0.84021 | 1.6617 | 1.6617 | 1.6617 | 1.6617 | 1.6617 | 3.6175 | 4.6683 | 5.3568 | 5.7191 | 6.4438 | 7.1685 | 1.1622 | 2.2938 | 2.7526 | 2.7526 | 2.7526 | 2.7526 | 1.467 | 1.7066 | 1.7066 | 1.7066 | 1.7066 | 1.7066
2020-01-28 20:00 | Summer | 0.87642 | 1.2543 | 1.81 | 1.81 | 1.81 | 1.81 | 0.71161 | 1.4074 | 1.4074 | 1.4074 | 1.4074 | 1.4074 | 3.1056 | 4.0077 | 4.5987 | 4.9098 | 5.5319 | 6.154 | 1.0822 | 2.1359 | 2.5631 | 2.5631 | 2.5631 | 2.5631 | 1.3527 | 1.5736 | 1.5736 | 1.5736 | 1.5736 | 1.5736
2020-01-28 21:00 | Summer | 0.83712 | 1.1981 | 1.7288 | 1.7288 | 1.7288 | 1.7288 | 0.65445 | 1.2943 | 1.2943 | 1.2943 | 1.2943 | 1.2943 | 2.896 | 3.7372 | 4.2884 | 4.5784 | 5.1586 | 5.7387 | 1.1241 | 2.2186 | 2.6623 | 2.6623 | 2.6623 | 2.6623 | 1.2003 | 1.3963 | 1.3963 | 1.3963 | 1.3963 | 1.3963
2020-01-28 22:00 | Summer | 0.66567 | 0.95269 | 1.3748 | 1.3748 | 1.3748 | 1.3748 | 0.64588 | 1.2774 | 1.2774 | 1.2774 | 1.2774 | 1.2774 | 2.6483 | 3.4176 | 3.9216 | 4.1869 | 4.7174 | 5.2479 | 1.0288 | 2.0306 | 2.4367 | 2.4367 | 2.4367 | 2.4367 | 1.105 | 1.2855 | 1.2855 | 1.2855 | 1.2855 | 1.2855
2020-01-28 23:00 | Summer | 0.58247 | 0.8336 | 1.2029 | 1.2029 | 1.2029 | 1.2029 | 0.67731 | 1.3396 | 1.3396 | 1.3396 | 1.3396 | 1.3396 | 2.5668 | 3.3124 | 3.8009 | 4.058 | 4.5722 | 5.0864 | 0.99073 | 1.9554 | 2.3465 | 2.3465 | 2.3465 | 2.3465 | 1.0669 | 1.2411 | 1.2411 | 1.2411 | 1.2411 | 1.2411
2020-01-29 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.6173 | 1.2209 | 1.2209 | 1.2209 | 1.2209 | 1.2209 | 2.2482 | 2.9013 | 3.3291 | 3.5543 | 4.0047 | 4.4551 | 0.724 | 1.4289 | 1.7147 | 1.7147 | 1.7147 | 1.7147 | 1.0669 | 1.2411 | 1.2411 | 1.2411 | 1.2411 | 1.2411
2020-01-29 01:00 | Summer | 0.58188 | 0.83276 | 1.2017 | 1.2017 | 1.2017 | 1.2017 | 0.57729 | 1.1417 | 1.1417 | 1.1417 | 1.1417 | 1.1417 | 2.0767 | 2.68 | 3.0752 | 3.2832 | 3.6992 | 4.1153 | 0.68589 | 1.3537 | 1.6245 | 1.6245 | 1.6245 | 1.6245 | 1.0098 | 1.1746 | 1.1746 | 1.1746 | 1.1746 | 1.1746
2020-01-29 02:00 | Summer | 0.59485 | 0.85133 | 1.2285 | 1.2285 | 1.2285 | 1.2285 | 0.57443 | 1.1361 | 1.1361 | 1.1361 | 1.1361 | 1.1361 | 2.0958 | 2.7046 | 3.1034 | 3.3133 | 3.7332 | 4.153 | 0.68589 | 1.3537 | 1.6245 | 1.6245 | 1.6245 | 1.6245 | 1.0288 | 1.1968 | 1.1968 | 1.1968 | 1.1968 | 1.1968
2020-01-29 03:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.66874 | 1.3226 | 1.3226 | 1.3226 | 1.3226 | 1.3226 | 2.0312 | 2.6213 | 3.0078 | 3.2113 | 3.6182 | 4.0251 | 0.64779 | 1.2785 | 1.5342 | 1.5342 | 1.5342 | 1.5342 | 0.99073 | 1.1525 | 1.1525 | 1.1525 | 1.1525 | 1.1525
2020-01-29 04:00 | Summer | 0.59089 | 0.84565 | 1.2203 | 1.2203 | 1.2203 | 1.2203 | 0.60301 | 1.1926 | 1.1926 | 1.1926 | 1.1926 | 1.1926 | 2.0577 | 2.6554 | 3.047 | 3.2531 | 3.6653 | 4.0775 | 0.73543 | 1.4515 | 1.7418 | 1.7418 | 1.7418 | 1.7418 | 1.086 | 1.2633 | 1.2633 | 1.2633 | 1.2633 | 1.2633
2020-01-29 05:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.64874 | 1.283 | 1.283 | 1.283 | 1.283 | 1.283 | 2.191 | 2.8275 | 3.2445 | 3.4639 | 3.9029 | 4.3418 | 0.94824 | 1.8715 | 2.2458 | 2.2458 | 2.2458 | 2.2458 | 1.2765 | 1.4849 | 1.4849 | 1.4849 | 1.4849 | 1.4849
2020-01-29 06:00 | Summer | 0.98587 | 1.4109 | 2.036 | 2.036 | 2.036 | 2.036 | 0.9088 | 1.7974 | 1.7974 | 1.7974 | 1.7974 | 1.7974 | 2.3625 | 3.0488 | 3.4984 | 3.735 | 4.2083 | 4.6816 | 1.0593 | 2.0908 | 2.5089 | 2.5089 | 2.5089 | 2.5089 | 1.6382 | 1.9056 | 1.9056 | 1.9056 | 1.9056 | 1.9056
2020-01-29 07:00 | Summer | 2.0386 | 2.9176 | 4.2102 | 4.2102 | 4.2102 | 4.2102 | 1.1374 | 2.2496 | 2.2496 | 2.2496 | 2.2496 | 2.2496 | 3.2199 | 4.1552 | 4.768 | 5.0905 | 5.7355 | 6.3806 | 1.2651 | 2.4969 | 2.9963 | 2.9963 | 2.9963 | 2.9963 | 2.2863 | 2.6596 | 2.6596 | 2.6596 | 2.6596 | 2.6596
2020-01-29 08:00 | Summer | 2.4197 | 3.4629 | 4.9972 | 4.9972 | 4.9972 | 4.9972 | 1.3089 | 2.5887 | 2.5887 | 2.5887 | 2.5887 | 2.5887 | 3.6771 | 4.7453 | 5.4451 | 5.8134 | 6.55 | 7.2867 | 1.2194 | 2.4066 | 2.888 | 2.888 | 2.888 | 2.888 | 2.8388 | 3.3023 | 3.3023 | 3.3023 | 3.3023 | 3.3023
2020-01-29 09:00 | Summer | 2.4578 | 3.5175 | 5.0759 | 5.0759 | 5.0759 | 5.0759 | 1.3518 | 2.6735 | 2.6735 | 2.6735 | 2.6735 | 2.6735 | 4.1303 | 5.3301 | 6.1161 | 6.5298 | 7.3573 | 8.1847 | 1.1813 | 2.3314 | 2.7977 | 2.7977 | 2.7977 | 2.7977 | 2.9722 | 3.4575 | 3.4575 | 3.4575 | 3.4575 | 3.4575
2020-01-29 10:00 | Summer | 2.3816 | 3.4084 | 4.9185 | 4.9185 | 4.9185 | 4.9185 | 1.4718 | 2.9109 | 2.9109 | 2.9109 | 2.9109 | 2.9109 | 4.1916 | 5.4091 | 6.2068 | 6.6267 | 7.4664 | 8.3061 | 1.1774 | 2.3239 | 2.7887 | 2.7887 | 2.7887 | 2.7887 | 3.0865 | 3.5904 | 3.5904 | 3.5904 | 3.5904 | 3.5904
2020-01-29 11:00 | Summer | 2.4006 | 3.4357 | 4.9578 | 4.9578 | 4.9578 | 4.9578 | 1.4205 | 2.8093 | 2.8093 | 2.8093 | 2.8093 | 2.8093 | 4.5345 | 5.8517 | 6.7147 | 7.1689 | 8.0773 | 8.9857 | 1.1774 | 2.3239 | 2.7887 | 2.7887 | 2.7887 | 2.7887 | 3.2389 | 3.7677 | 3.7677 | 3.7677 | 3.7677 | 3.7677
2020-01-29 12:00 | Summer | 2.4006 | 3.4357 | 4.9578 | 4.9578 | 4.9578 | 4.9578 | 1.4547 | 2.877 | 2.877 | 2.877 | 2.877 | 2.877 | 4.4964 | 5.8025 | 6.6582 | 7.1086 | 8.0094 | 8.9101 | 1.1965 | 2.3615 | 2.8338 | 2.8338 | 2.8338 | 2.8338 | 3.3533 | 3.9007 | 3.9007 | 3.9007 | 3.9007 | 3.9007
2020-01-29 13:00 | Summer | 2.3625 | 3.3811 | 4.8791 | 4.8791 | 4.8791 | 4.8791 | 1.5547 | 3.0748 | 3.0748 | 3.0748 | 3.0748 | 3.0748 | 4.5917 | 5.9254 | 6.7993 | 7.2592 | 8.1791 | 9.0989 | 1.2156 | 2.3991 | 2.8789 | 2.8789 | 2.8789 | 2.8789 | 3.3151 | 3.8564 | 3.8564 | 3.8564 | 3.8564 | 3.8564
2020-01-29 14:00 | Summer | 2.3435 | 3.3539 | 4.8398 | 4.8398 | 4.8398 | 4.8398 | 1.749 | 3.4591 | 3.4591 | 3.4591 | 3.4591 | 3.4591 | 4.5345 | 5.8517 | 6.7147 | 7.1689 | 8.0773 | 8.9857 | 1.2232 | 2.4142 | 2.897 | 2.897 | 2.897 | 2.897 | 3.3151 | 3.8564 | 3.8564 | 3.8564 | 3.8564 | 3.8564
2020-01-29 15:00 | Summer | 2.4197 | 3.4629 | 4.9972 | 4.9972 | 4.9972 | 4.9972 | 1.6604 | 3.2839 | 3.2839 | 3.2839 | 3.2839 | 3.2839 | 4.3821 | 5.655 | 6.489 | 6.9279 | 7.8058 | 8.6836 | 1.1965 | 2.3615 | 2.8338 | 2.8338 | 2.8338 | 2.8338 | 3.1437 | 3.6569 | 3.6569 | 3.6569 | 3.6569 | 3.6569
2020-01-29 16:00 | Summer | 2.2485 | 3.2179 | 4.6435 | 4.6435 | 4.6435 | 4.6435 | 1.6576 | 3.2783 | 3.2783 | 3.2783 | 3.2783 | 3.2783 | 4.344 | 5.6058 | 6.4325 | 6.8676 | 7.7379 | 8.6081 | 1.1927 | 2.354 | 2.8248 | 2.8248 | 2.8248 | 2.8248 | 3.1437 | 3.6569 | 3.6569 | 3.6569 | 3.6569 | 3.6569
2020-01-29 17:00 | Summer | 2.2482 | 3.2175 | 4.643 | 4.643 | 4.643 | 4.643 | 1.669 | 3.3009 | 3.3009 | 3.3009 | 3.3009 | 3.3009 | 4.3821 | 5.655 | 6.489 | 6.9279 | 7.8058 | 8.6836 | 1.1584 | 2.2863 | 2.7436 | 2.7436 | 2.7436 | 2.7436 | 3.1254 | 3.6357 | 3.6357 | 3.6357 | 3.6357 | 3.6357
2020-01-29 18:00 | Summer | 1.6127 | 2.308 | 3.3305 | 3.3305 | 3.3305 | 3.3305 | 1.286 | 2.5435 | 2.5435 | 2.5435 | 2.5435 | 2.5435 | 4.0847 | 5.2712 | 6.0486 | 6.4578 | 7.2761 | 8.0944 | 1.1203 | 2.2111 | 2.6533 | 2.6533 | 2.6533 | 2.6533 | 2.5537 | 2.9706 | 2.9706 | 2.9706 | 2.9706 | 2.9706
2020-01-29 19:00 | Summer | 0.81926 | 1.1725 | 1.692 | 1.692 | 1.692 | 1.692 | 0.88759 | 1.7554 | 1.7554 | 1.7554 | 1.7554 | 1.7554 | 3.6125 | 4.6619 | 5.3494 | 5.7112 | 6.4349 | 7.1586 | 1.1622 | 2.2938 | 2.7526 | 2.7526 | 2.7526 | 2.7526 | 1.467 | 1.7066 | 1.7066 | 1.7066 | 1.7066 | 1.7066
2020-01-29 20:00 | Summer | 0.70494 | 1.0089 | 1.4559 | 1.4559 | 1.4559 | 1.4559 | 0.83736 | 1.6561 | 1.6561 | 1.6561 | 1.6561 | 1.6561 | 3.0865 | 3.9831 | 4.5705 | 4.8796 | 5.498 | 6.1163 | 1.1279 | 2.2261 | 2.6714 | 2.6714 | 2.6714 | 2.6714 | 1.3527 | 1.5736 | 1.5736 | 1.5736 | 1.5736 | 1.5736
2020-01-29 21:00 | Summer | 0.66807 | 0.95612 | 1.3797 | 1.3797 | 1.3797 | 1.3797 | 0.63445 | 1.2548 | 1.2548 | 1.2548 | 1.2548 | 1.2548 | 2.954 | 3.812 | 4.3742 | 4.6701 | 5.2619 | 5.8536 | 1.0593 | 2.0908 | 2.5089 | 2.5089 | 2.5089 | 2.5089 | 1.2765 | 1.4849 | 1.4849 | 1.4849 | 1.4849 | 1.4849
2020-01-29 22:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.62587 | 1.2378 | 1.2378 | 1.2378 | 1.2378 | 1.2378 | 2.8007 | 3.6143 | 4.1473 | 4.4278 | 4.9889 | 5.55 | 0.98311 | 1.9403 | 2.3284 | 2.3284 | 2.3284 | 2.3284 | 1.1432 | 1.3298 | 1.3298 | 1.3298 | 1.3298 | 1.3298
2020-01-29 23:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.55728 | 1.1022 | 1.1022 | 1.1022 | 1.1022 | 1.1022 | 2.4768 | 3.1963 | 3.6677 | 3.9158 | 4.4119 | 4.9081 | 0.97168 | 1.9178 | 2.3013 | 2.3013 | 2.3013 | 2.3013 | 1.0288 | 1.1968 | 1.1968 | 1.1968 | 1.1968 | 1.1968
2020-01-30 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.58872 | 1.1643 | 1.1643 | 1.1643 | 1.1643 | 1.1643 | 2.2658 | 2.924 | 3.3552 | 3.5822 | 4.0361 | 4.49 | 0.75829 | 1.4966 | 1.796 | 1.796 | 1.796 | 1.796 | 1.0479 | 1.219 | 1.219 | 1.219 | 1.219 | 1.219
2020-01-30 01:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.58015 | 1.1474 | 1.1474 | 1.1474 | 1.1474 | 1.1474 | 2.3244 | 2.9996 | 3.442 | 3.6748 | 4.1404 | 4.6061 | 0.724 | 1.4289 | 1.7147 | 1.7147 | 1.7147 | 1.7147 | 1.0098 | 1.1746 | 1.1746 | 1.1746 | 1.1746 | 1.1746
2020-01-30 02:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.55157 | 1.0909 | 1.0909 | 1.0909 | 1.0909 | 1.0909 | 2.1339 | 2.7537 | 3.1598 | 3.3736 | 3.8011 | 4.2285 | 0.62492 | 1.2334 | 1.4801 | 1.4801 | 1.4801 | 1.4801 | 1.0098 | 1.1746 | 1.1746 | 1.1746 | 1.1746 | 1.1746
2020-01-30 03:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.55728 | 1.1022 | 1.1022 | 1.1022 | 1.1022 | 1.1022 | 2.2101 | 2.8521 | 3.2727 | 3.4941 | 3.9368 | 4.3796 | 0.6516 | 1.286 | 1.5433 | 1.5433 | 1.5433 | 1.5433 | 0.99073 | 1.1525 | 1.1525 | 1.1525 | 1.1525 | 1.1525
2020-01-30 04:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.58872 | 1.1643 | 1.1643 | 1.1643 | 1.1643 | 1.1643 | 2.191 | 2.8275 | 3.2445 | 3.4639 | 3.9029 | 4.3418 | 0.6173 | 1.2184 | 1.462 | 1.462 | 1.462 | 1.462 | 1.086 | 1.2633 | 1.2633 | 1.2633 | 1.2633 | 1.2633
2020-01-30 05:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.62873 | 1.2435 | 1.2435 | 1.2435 | 1.2435 | 1.2435 | 2.172 | 2.8029 | 3.2163 | 3.4338 | 3.8689 | 4.3041 | 0.89928 | 1.7749 | 2.1299 | 2.1299 | 2.1299 | 2.1299 | 1.3337 | 1.5514 | 1.5514 | 1.5514 | 1.5514 | 1.5514
2020-01-30 06:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.84879 | 1.6787 | 1.6787 | 1.6787 | 1.6787 | 1.6787 | 2.4197 | 3.1225 | 3.583 | 3.8254 | 4.3101 | 4.7949 | 1.0022 | 1.978 | 2.3735 | 2.3735 | 2.3735 | 2.3735 | 1.5417 | 1.7934 | 1.7934 | 1.7934 | 1.7934 | 1.7934
2020-01-30 07:00 | Summer | 2.0369 | 2.9151 | 4.2066 | 4.2066 | 4.2066 | 4.2066 | 1.0746 | 2.1252 | 2.1252 | 2.1252 | 2.1252 | 2.1252 | 3.4295 | 4.4256 | 5.0783 | 5.4218 | 6.1088 | 6.7959 | 1.2651 | 2.4969 | 2.9963 | 2.9963 | 2.9963 | 2.9963 | 2.0577 | 2.3936 | 2.3936 | 2.3936 | 2.3936 | 2.3936
2020-01-30 08:00 | Summer | 2.2673 | 3.2448 | 4.6824 | 4.6824 | 4.6824 | 4.6824 | 1.206 | 2.3852 | 2.3852 | 2.3852 | 2.3852 | 2.3852 | 3.4878 | 4.5009 | 5.1647 | 5.514 | 6.2127 | 6.9114 | 1.1508 | 2.2713 | 2.7255 | 2.7255 | 2.7255 | 2.7255 | 2.5827 | 3.0043 | 3.0043 | 3.0043 | 3.0043 | 3.0043
2020-01-30 09:00 | Summer | 2.0577 | 2.9449 | 4.2495 | 4.2495 | 4.2495 | 4.2495 | 1.3832 | 2.7356 | 2.7356 | 2.7356 | 2.7356 | 2.7356 | 3.7343 | 4.819 | 5.5297 | 5.9038 | 6.6519 | 7.4 | 1.1736 | 2.3164 | 2.7797 | 2.7797 | 2.7797 | 2.7797 | 2.7522 | 3.2016 | 3.2016 | 3.2016 | 3.2016 | 3.2016
2020-01-30 10:00 | Summer | 2.0196 | 2.8903 | 4.1709 | 4.1709 | 4.1709 | 4.1709 | 1.4918 | 2.9504 | 2.9504 | 2.9504 | 2.9504 | 2.9504 | 3.7724 | 4.8682 | 5.5861 | 5.964 | 6.7197 | 7.4755 | 1.1965 | 2.3615 | 2.8338 | 2.8338 | 2.8338 | 2.8338 | 3.0294 | 3.5239 | 3.5239 | 3.5239 | 3.5239 | 3.5239
2020-01-30 11:00 | Summer | 2.0767 | 2.9721 | 4.2889 | 4.2889 | 4.2889 | 4.2889 | 1.4461 | 2.86 | 2.86 | 2.86 | 2.86 | 2.86 | 4.0201 | 5.1878 | 5.9529 | 6.3556 | 7.1609 | 7.9663 | 1.2117 | 2.3916 | 2.8699 | 2.8699 | 2.8699 | 2.8699 | 2.9722 | 3.4575 | 3.4575 | 3.4575 | 3.4575 | 3.4575
2020-01-30 12:00 | Summer | 2.2673 | 3.2448 | 4.6824 | 4.6824 | 4.6824 | 4.6824 | 1.5633 | 3.0917 | 3.0917 | 3.0917 | 3.0917 | 3.0917 | 4.2487 | 5.4829 | 6.2915 | 6.717 | 7.5682 | 8.4193 | 1.2117 | 2.3916 | 2.8699 | 2.8699 | 2.8699 | 2.8699 | 3.2008 | 3.7234 | 3.7234 | 3.7234 | 3.7234 | 3.7234
2020-01-30 13:00 | Summer | 2.3625 | 3.3811 | 4.8791 | 4.8791 | 4.8791 | 4.8791 | 1.6004 | 3.1652 | 3.1652 | 3.1652 | 3.1652 | 3.1652 | 4.4392 | 5.7288 | 6.5736 | 7.0183 | 7.9076 | 8.7969 | 1.246 | 2.4593 | 2.9511 | 2.9511 | 2.9511 | 2.9511 | 3.2961 | 3.8342 | 3.8342 | 3.8342 | 3.8342 | 3.8342
2020-01-30 14:00 | Summer | 2.3625 | 3.3811 | 4.8791 | 4.8791 | 4.8791 | 4.8791 | 1.649 | 3.2613 | 3.2613 | 3.2613 | 3.2613 | 3.2613 | 4.652 | 6.0032 | 6.8886 | 7.3545 | 8.2865 | 9.2184 | 1.5204 | 3.0008 | 3.6009 | 3.6009 | 3.6009 | 3.6009 | 3.3723 | 3.9229 | 3.9229 | 3.9229 | 3.9229 | 3.9229
2020-01-30 15:00 | Summer | 2.4699 | 3.5349 | 5.1009 | 5.1009 | 5.1009 | 5.1009 | 1.9148 | 3.787 | 3.787 | 3.787 | 3.787 | 3.787 | 4.7631 | 6.1467 | 7.0532 | 7.5303 | 8.4845 | 9.4387 | 1.5166 | 2.9933 | 3.5919 | 3.5919 | 3.5919 | 3.5919 | 3.3914 | 3.945 | 3.945 | 3.945 | 3.945 | 3.945
2020-01-30 16:00 | Summer | 2.4768 | 3.5447 | 5.1152 | 5.1152 | 5.1152 | 5.1152 | 1.9033 | 3.7643 | 3.7643 | 3.7643 | 3.7643 | 3.7643 | 4.7298 | 6.1037 | 7.0038 | 7.4775 | 8.4251 | 9.3726 | 1.5318 | 3.0233 | 3.628 | 3.628 | 3.628 | 3.628 | 3.4295 | 3.9894 | 3.9894 | 3.9894 | 3.9894 | 3.9894
2020-01-30 17:00 | Summer | 2.0958 | 2.9994 | 4.3282 | 4.3282 | 4.3282 | 4.3282 | 1.8748 | 3.7078 | 3.7078 | 3.7078 | 3.7078 | 3.7078 | 4.5672 | 5.8938 | 6.763 | 7.2205 | 8.1354 | 9.0504 | 1.4518 | 2.8654 | 3.4385 | 3.4385 | 3.4385 | 3.4385 | 3.2961 | 3.8342 | 3.8342 | 3.8342 | 3.8342 | 3.8342
2020-01-30 18:00 | Summer | 1.6865 | 2.4136 | 3.483 | 3.483 | 3.483 | 3.483 | 1.5461 | 3.0578 | 3.0578 | 3.0578 | 3.0578 | 3.0578 | 4.4021 | 5.6808 | 6.5186 | 6.9595 | 7.8414 | 8.7232 | 1.2651 | 2.4969 | 2.9963 | 2.9963 | 2.9963 | 2.9963 | 2.3528 | 2.7369 | 2.7369 | 2.7369 | 2.7369 | 2.7369
2020-01-30 19:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 1.0003 | 1.9783 | 1.9783 | 1.9783 | 1.9783 | 1.9783 | 3.963 | 5.1141 | 5.8683 | 6.2653 | 7.0592 | 7.8531 | 1.2194 | 2.4066 | 2.888 | 2.888 | 2.888 | 2.888 | 1.4099 | 1.6401 | 1.6401 | 1.6401 | 1.6401 | 1.6401
2020-01-30 20:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.81449 | 1.6109 | 1.6109 | 1.6109 | 1.6109 | 1.6109 | 3.3883 | 4.3725 | 5.0173 | 5.3567 | 6.0355 | 6.7143 | 1.1508 | 2.2713 | 2.7255 | 2.7255 | 2.7255 | 2.7255 | 1.3337 | 1.5514 | 1.5514 | 1.5514 | 1.5514 | 1.5514
2020-01-30 21:00 | Summer | 0.85737 | 1.227 | 1.7706 | 1.7706 | 1.7706 | 1.7706 | 0.64874 | 1.283 | 1.283 | 1.283 | 1.283 | 1.283 | 3.0675 | 3.9585 | 4.5423 | 4.8495 | 5.464 | 6.0785 | 1.1432 | 2.2562 | 2.7075 | 2.7075 | 2.7075 | 2.7075 | 1.2296 | 1.4303 | 1.4303 | 1.4303 | 1.4303 | 1.4303
2020-01-30 22:00 | Summer | 0.724 | 1.0362 | 1.4952 | 1.4952 | 1.4952 | 1.4952 | 0.65731 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 2.915 | 3.7618 | 4.3166 | 4.6086 | 5.1925 | 5.7765 | 1.1012 | 2.1735 | 2.6082 | 2.6082 | 2.6082 | 2.6082 | 1.0669 | 1.2411 | 1.2411 | 1.2411 | 1.2411 | 1.2411
2020-01-30 23:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.58586 | 1.1587 | 1.1587 | 1.1587 | 1.1587 | 1.1587 | 2.6102 | 3.3684 | 3.8652 | 4.1266 | 4.6495 | 5.1724 | 1.025 | 2.0231 | 2.4277 | 2.4277 | 2.4277 | 2.4277 | 1.0479 | 1.219 | 1.219 | 1.219 | 1.219 | 1.219
2020-01-31 | Summer | 0.5692 | 0.81461 | 1.1755 | 1.1755 | 1.1755 | 1.1755 | 0.563 | 1.1135 | 1.1135 | 1.1135 | 1.1135 | 1.1135 | 2.4183 | 3.1207 | 3.5809 | 3.8232 | 4.3076 | 4.7921 | 0.82686 | 1.632 | 1.9583 | 1.9583 | 1.9583 | 1.9583 | 1.0479 | 1.219 | 1.219 | 1.219 | 1.219 | 1.219
2020-01-31 01:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.54299 | 1.0739 | 1.0739 | 1.0739 | 1.0739 | 1.0739 | 2.191 | 2.8275 | 3.2445 | 3.4639 | 3.9029 | 4.3418 | 0.8345 | 1.647 | 1.9764 | 1.9764 | 1.9764 | 1.9764 | 1.0479 | 1.219 | 1.219 | 1.219 | 1.219 | 1.219
2020-01-31 02:00 | Summer | 0.59052 | 0.84512 | 1.2195 | 1.2195 | 1.2195 | 1.2195 | 0.56014 | 1.1078 | 1.1078 | 1.1078 | 1.1078 | 1.1078 | 2.1529 | 2.7783 | 3.1881 | 3.4037 | 3.835 | 4.2663 | 0.7621 | 1.5041 | 1.805 | 1.805 | 1.805 | 1.805 | 0.99073 | 1.1525 | 1.1525 | 1.1525 | 1.1525 | 1.1525
2020-01-31 03:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.54585 | 1.0796 | 1.0796 | 1.0796 | 1.0796 | 1.0796 | 2.0577 | 2.6554 | 3.047 | 3.2531 | 3.6653 | 4.0775 | 0.71637 | 1.4139 | 1.6967 | 1.6967 | 1.6967 | 1.6967 | 1.1241 | 1.3076 | 1.3076 | 1.3076 | 1.3076 | 1.3076
2020-01-31 04:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.62587 | 1.2378 | 1.2378 | 1.2378 | 1.2378 | 1.2378 | 2.0958 | 2.7046 | 3.1034 | 3.3133 | 3.7332 | 4.153 | 0.69351 | 1.3688 | 1.6425 | 1.6425 | 1.6425 | 1.6425 | 1.2765 | 1.4849 | 1.4849 | 1.4849 | 1.4849 | 1.4849
2020-01-31 05:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.73447 | 1.4526 | 1.4526 | 1.4526 | 1.4526 | 1.4526 | 2.1339 | 2.7537 | 3.1598 | 3.3736 | 3.8011 | 4.2285 | 1.0441 | 2.0607 | 2.4728 | 2.4728 | 2.4728 | 2.4728 | 1.4289 | 1.6622 | 1.6622 | 1.6622 | 1.6622 | 1.6622
2020-01-31 06:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.92823 | 1.8358 | 1.8358 | 1.8358 | 1.8358 | 1.8358 | 2.3625 | 3.0488 | 3.4984 | 3.735 | 4.2083 | 4.6816 | 1.086 | 2.1434 | 2.5721 | 2.5721 | 2.5721 | 2.5721 | 1.6611 | 1.9323 | 1.9323 | 1.9323 | 1.9323 | 1.9323
2020-01-31 07:00 | Summer | 2.0196 | 2.8903 | 4.1709 | 4.1709 | 4.1709 | 4.1709 | 1.2346 | 2.4417 | 2.4417 | 2.4417 | 2.4417 | 2.4417 | 3.4485 | 4.4502 | 5.1065 | 5.4519 | 6.1428 | 6.8336 | 1.3832 | 2.73 | 3.276 | 3.276 | 3.276 | 3.276 | 2.4578 | 2.8591 | 2.8591 | 2.8591 | 2.8591 | 2.8591
2020-01-31 08:00 | Summer | 2.4006 | 3.4357 | 4.9578 | 4.9578 | 4.9578 | 4.9578 | 1.3489 | 2.6678 | 2.6678 | 2.6678 | 2.6678 | 2.6678 | 3.9248 | 5.0649 | 5.8119 | 6.205 | 6.9912 | 7.7775 | 1.4556 | 2.8729 | 3.4475 | 3.4475 | 3.4475 | 3.4475 | 3.0484 | 3.5461 | 3.5461 | 3.5461 | 3.5461 | 3.5461
2020-01-31 09:00 | Summer | 2.3625 | 3.3811 | 4.8791 | 4.8791 | 4.8791 | 4.8791 | 1.5976 | 3.1596 | 3.1596 | 3.1596 | 3.1596 | 3.1596 | 4.001 | 5.1633 | 5.9247 | 6.3255 | 7.127 | 7.9285 | 1.4442 | 2.8504 | 3.4204 | 3.4204 | 3.4204 | 3.4204 | 3.1437 | 3.6569 | 3.6569 | 3.6569 | 3.6569 | 3.6569
2020-01-31 10:00 | Summer | 2.4006 | 3.4357 | 4.9578 | 4.9578 | 4.9578 | 4.9578 | 1.709 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 4.3818 | 5.6546 | 6.4885 | 6.9274 | 7.8052 | 8.683 | 1.4937 | 2.9481 | 3.5378 | 3.5378 | 3.5378 | 3.5378 | 3.5127 | 4.0862 | 4.0862 | 4.0862 | 4.0862 | 4.0862
2020-01-31 11:00 | Summer | 2.3816 | 3.4084 | 4.9185 | 4.9185 | 4.9185 | 4.9185 | 1.7223 | 3.4063 | 3.4063 | 3.4063 | 3.4063 | 3.4063 | 4.6388 | 5.9863 | 6.8691 | 7.3338 | 8.2631 | 9.1924 | 1.5928 | 3.1437 | 3.7724 | 3.7724 | 3.7724 | 3.7724 | 3.6771 | 4.2775 | 4.2775 | 4.2775 | 4.2775 | 4.2775
2020-01-31 12:00 | Summer | 2.4768 | 3.5447 | 5.1152 | 5.1152 | 5.1152 | 5.1152 | 2.112 | 4.177 | 4.177 | 4.177 | 4.177 | 4.177 | 4.9918 | 6.4418 | 7.3918 | 7.8918 | 8.8918 | 9.8918 | 1.5699 | 3.0985 | 3.7183 | 3.7183 | 3.7183 | 3.7183 | 3.8296 | 4.4548 | 4.4548 | 4.4548 | 4.4548 | 4.4548
2020-01-31 13:00 | Summer | 2.4197 | 3.4629 | 4.9972 | 4.9972 | 4.9972 | 4.9972 | 2.1577 | 4.2674 | 4.2674 | 4.2674 | 4.2674 | 4.2674 | 4.9918 | 6.4418 | 7.3918 | 7.8918 | 8.8918 | 9.8918 | 1.6995 | 3.3542 | 4.0251 | 4.0251 | 4.0251 | 4.0251 | 3.9439 | 4.5878 | 4.5878 | 4.5878 | 4.5878 | 4.5878
2020-01-31 14:00 | Summer | 2.4578 | 3.5175 | 5.0759 | 5.0759 | 5.0759 | 5.0759 | 2.032 | 4.0187 | 4.0187 | 4.0187 | 4.0187 | 4.0187 | 4.9918 | 6.4418 | 7.3918 | 7.8918 | 8.8918 | 9.8918 | 1.6461 | 3.249 | 3.8988 | 3.8988 | 3.8988 | 3.8988 | 3.9629 | 4.6099 | 4.6099 | 4.6099 | 4.6099 | 4.6099
2020-01-31 15:00 | Summer | 2.4029 | 3.4389 | 4.9625 | 4.9625 | 4.9625 | 4.9625 | 2.172 | 4.2956 | 4.2956 | 4.2956 | 4.2956 | 4.2956 | 4.9918 | 6.4418 | 7.3918 | 7.8918 | 8.8918 | 9.8918 | 1.6652 | 3.2866 | 3.9439 | 3.9439 | 3.9439 | 3.9439 | 3.9439 | 4.5878 | 4.5878 | 4.5878 | 4.5878 | 4.5878
2020-01-31 16:00 | Summer | 2.2673 | 3.2448 | 4.6824 | 4.6824 | 4.6824 | 4.6824 | 2.1063 | 4.1656 | 4.1656 | 4.1656 | 4.1656 | 4.1656 | 4.9918 | 6.4418 | 7.3918 | 7.8918 | 8.8918 | 9.8918 | 1.6766 | 3.3091 | 3.9709 | 3.9709 | 3.9709 | 3.9709 | 3.8677 | 4.4991 | 4.4991 | 4.4991 | 4.4991 | 4.4991
2020-01-31 17:00 | Summer | 2.1642 | 3.0973 | 4.4695 | 4.4695 | 4.4695 | 4.4695 | 2.1634 | 4.2787 | 4.2787 | 4.2787 | 4.2787 | 4.2787 | 4.9918 | 6.4418 | 7.3918 | 7.8918 | 8.8918 | 9.8918 | 1.5814 | 3.1211 | 3.7453 | 3.7453 | 3.7453 | 3.7453 | 3.8105 | 4.4326 | 4.4326 | 4.4326 | 4.4326 | 4.4326
2020-01-31 18:00 | Summer | 1.5936 | 2.2808 | 3.2912 | 3.2912 | 3.2912 | 3.2912 | 1.8605 | 3.6796 | 3.6796 | 3.6796 | 3.6796 | 3.6796 | 4.9156 | 6.3434 | 7.2789 | 7.7713 | 8.756 | 9.7408 | 1.3337 | 2.6323 | 3.1587 | 3.1587 | 3.1587 | 3.1587 | 2.9547 | 3.4371 | 3.4371 | 3.4371 | 3.4371 | 3.4371
2020-01-31 19:00 | Summer | 0.78136 | 1.1183 | 1.6137 | 1.6137 | 1.6137 | 1.6137 | 1.246 | 2.4643 | 2.4643 | 2.4643 | 2.4643 | 2.4643 | 4.4392 | 5.7288 | 6.5736 | 7.0183 | 7.9076 | 8.7969 | 1.2727 | 2.5119 | 3.0143 | 3.0143 | 3.0143 | 3.0143 | 1.5052 | 1.7509 | 1.7509 | 1.7509 | 1.7509 | 1.7509
2020-01-31 20:00 | Summer | 0.724 | 1.0362 | 1.4952 | 1.4952 | 1.4952 | 1.4952 | 1.066 | 2.1083 | 2.1083 | 2.1083 | 2.1083 | 2.1083 | 3.8867 | 5.0157 | 5.7554 | 6.1447 | 6.9234 | 7.702 | 1.2575 | 2.4818 | 2.9782 | 2.9782 | 2.9782 | 2.9782 | 1.5052 | 1.7509 | 1.7509 | 1.7509 | 1.7509 | 1.7509
2020-01-31 21:00 | Summer | 0.80021 | 1.1452 | 1.6526 | 1.6526 | 1.6526 | 1.6526 | 1.0546 | 2.0856 | 2.0856 | 2.0856 | 2.0856 | 2.0856 | 3.639 | 4.6961 | 5.3887 | 5.7532 | 6.4822 | 7.2112 | 1.3222 | 2.6097 | 3.1316 | 3.1316 | 3.1316 | 3.1316 | 1.3337 | 1.5514 | 1.5514 | 1.5514 | 1.5514 | 1.5514
2020-01-31 22:00 | Summer | 0.78115 | 1.118 | 1.6133 | 1.6133 | 1.6133 | 1.6133 | 0.97739 | 1.933 | 1.933 | 1.933 | 1.933 | 1.933 | 3.4297 | 4.426 | 5.0787 | 5.4223 | 6.1094 | 6.7964 | 1.227 | 2.4217 | 2.906 | 2.906 | 2.906 | 2.906 | 1.2384 | 1.4406 | 1.4406 | 1.4406 | 1.4406 | 1.4406
2020-01-31 23:00 | Summer | 0.70508 | 1.0091 | 1.4561 | 1.4561 | 1.4561 | 1.4561 | 0.9631 | 1.9048 | 1.9048 | 1.9048 | 1.9048 | 1.9048 | 3.2584 | 4.2049 | 4.825 | 5.1514 | 5.8041 | 6.4569 | 1.105 | 2.181 | 2.6172 | 2.6172 | 2.6172 | 2.6172 | 1.1432 | 1.3298 | 1.3298 | 1.3298 | 1.3298 | 1.3298
2020-02-01 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.83164 | 1.6448 | 1.6448 | 1.6448 | 1.6448 | 1.6448 | 2.8811 | 3.718 | 4.2663 | 4.5548 | 5.132 | 5.7092 | 0.94501 | 1.8651 | 2.2382 | 2.2382 | 2.2382 | 2.2382 | 1.1241 | 1.3076 | 1.3076 | 1.3076 | 1.3076 | 1.3076
2020-02-01 01:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.65731 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 2.6102 | 3.3684 | 3.8652 | 4.1266 | 4.6495 | 5.1724 | 0.83069 | 1.6395 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 1.086 | 1.2633 | 1.2633 | 1.2633 | 1.2633 | 1.2633
2020-02-01 02:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.62873 | 1.2435 | 1.2435 | 1.2435 | 1.2435 | 1.2435 | 2.5149 | 3.2455 | 3.7241 | 3.976 | 4.4798 | 4.9836 | 0.81545 | 1.6094 | 1.9313 | 1.9313 | 1.9313 | 1.9313 | 1.028 | 1.1958 | 1.1958 | 1.1958 | 1.1958 | 1.1958
2020-02-01 03:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.6173 | 1.2209 | 1.2209 | 1.2209 | 1.2209 | 1.2209 | 2.534 | 3.2701 | 3.7523 | 4.0061 | 4.5138 | 5.0214 | 0.89547 | 1.7674 | 2.1208 | 2.1208 | 2.1208 | 2.1208 | 1.0479 | 1.219 | 1.219 | 1.219 | 1.219 | 1.219
2020-02-01 04:00 | Summer | 0.57699 | 0.82577 | 1.1916 | 1.1916 | 1.1916 | 1.1916 | 0.58586 | 1.1587 | 1.1587 | 1.1587 | 1.1587 | 1.1587 | 2.5529 | 3.2944 | 3.7803 | 4.036 | 4.5474 | 5.0588 | 0.95235 | 1.8796 | 2.2556 | 2.2556 | 2.2556 | 2.2556 | 1.0669 | 1.2411 | 1.2411 | 1.2411 | 1.2411 | 1.2411
2020-02-01 05:00 | Summer | 0.58296 | 0.83431 | 1.2039 | 1.2039 | 1.2039 | 1.2039 | 0.66017 | 1.3056 | 1.3056 | 1.3056 | 1.3056 | 1.3056 | 2.5721 | 3.3192 | 3.8087 | 4.0664 | 4.5816 | 5.0969 | 0.97168 | 1.9178 | 2.3013 | 2.3013 | 2.3013 | 2.3013 | 1.1141 | 1.296 | 1.296 | 1.296 | 1.296 | 1.296
2020-02-01 06:00 | Summer | 0.58892 | 0.84284 | 1.2163 | 1.2163 | 1.2163 | 1.2163 | 0.68589 | 1.3565 | 1.3565 | 1.3565 | 1.3565 | 1.3565 | 2.6674 | 3.4422 | 3.9498 | 4.217 | 4.7513 | 5.2857 | 1.105 | 2.181 | 2.6172 | 2.6172 | 2.6172 | 2.6172 | 1.1622 | 1.352 | 1.352 | 1.352 | 1.352 | 1.352
2020-02-01 07:00 | Summer | 0.66516 | 0.95194 | 1.3737 | 1.3737 | 1.3737 | 1.3737 | 0.91738 | 1.8143 | 1.8143 | 1.8143 | 1.8143 | 1.8143 | 3.3209 | 4.2856 | 4.9176 | 5.2502 | 5.9155 | 6.5808 | 1.1546 | 2.2788 | 2.7345 | 2.7345 | 2.7345 | 2.7345 | 1.4254 | 1.6581 | 1.6581 | 1.6581 | 1.6581 | 1.6581
2020-02-01 08:00 | Summer | 0.91452 | 1.3088 | 1.8887 | 1.8887 | 1.8887 | 1.8887 | 0.99168 | 1.9613 | 1.9613 | 1.9613 | 1.9613 | 1.9613 | 3.7152 | 4.7944 | 5.5015 | 5.8736 | 6.6179 | 7.3622 | 1.1813 | 2.3314 | 2.7977 | 2.7977 | 2.7977 | 2.7977 | 1.6957 | 1.9725 | 1.9725 | 1.9725 | 1.9725 | 1.9725
2020-02-01 09:00 | Summer | 0.87629 | 1.2541 | 1.8097 | 1.8097 | 1.8097 | 1.8097 | 1.0517 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 3.7915 | 4.8928 | 5.6144 | 5.9941 | 6.7537 | 7.5132 | 1.1813 | 2.3314 | 2.7977 | 2.7977 | 2.7977 | 2.7977 | 1.9053 | 2.2163 | 2.2163 | 2.2163 | 2.2163 | 2.2163
2020-02-01 10:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 1.0374 | 2.0517 | 2.0517 | 2.0517 | 2.0517 | 2.0517 | 3.9058 | 5.0403 | 5.7836 | 6.1749 | 6.9573 | 7.7397 | 1.1622 | 2.2938 | 2.7526 | 2.7526 | 2.7526 | 2.7526 | 2.0577 | 2.3936 | 2.3936 | 2.3936 | 2.3936 | 2.3936
2020-02-01 11:00 | Summer | 0.95267 | 1.3634 | 1.9675 | 1.9675 | 1.9675 | 1.9675 | 1.0031 | 1.9839 | 1.9839 | 1.9839 | 1.9839 | 1.9839 | 4.0391 | 5.2124 | 5.9811 | 6.3857 | 7.1949 | 8.004 | 1.2117 | 2.3916 | 2.8699 | 2.8699 | 2.8699 | 2.8699 | 1.9434 | 2.2606 | 2.2606 | 2.2606 | 2.2606 | 2.2606
2020-02-01 12:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 1.1289 | 2.2326 | 2.2326 | 2.2326 | 2.2326 | 2.2326 | 4.2106 | 5.4337 | 6.235 | 6.6568 | 7.5003 | 8.3438 | 1.1889 | 2.3465 | 2.8158 | 2.8158 | 2.8158 | 2.8158 | 2.172 | 2.5266 | 2.5266 | 2.5266 | 2.5266 | 2.5266
2020-02-01 13:00 | Summer | 0.89636 | 1.2828 | 1.8512 | 1.8512 | 1.8512 | 1.8512 | 1.3489 | 2.6678 | 2.6678 | 2.6678 | 2.6678 | 2.6678 | 4.5917 | 5.9254 | 6.7993 | 7.2592 | 8.1791 | 9.0989 | 1.2498 | 2.4668 | 2.9602 | 2.9602 | 2.9602 | 2.9602 | 1.9815 | 2.305 | 2.305 | 2.305 | 2.305 | 2.305
2020-02-01 14:00 | Summer | 0.96332 | 1.3787 | 1.9895 | 1.9895 | 1.9895 | 1.9895 | 1.3118 | 2.5943 | 2.5943 | 2.5943 | 2.5943 | 2.5943 | 4.2678 | 5.5075 | 6.3197 | 6.7472 | 7.6021 | 8.4571 | 1.2346 | 2.4367 | 2.9241 | 2.9241 | 2.9241 | 2.9241 | 1.9187 | 2.2319 | 2.2319 | 2.2319 | 2.2319 | 2.2319
2020-02-01 15:00 | Summer | 1.1241 | 1.6088 | 2.3215 | 2.3215 | 2.3215 | 2.3215 | 1.266 | 2.5039 | 2.5039 | 2.5039 | 2.5039 | 2.5039 | 4.3821 | 5.655 | 6.489 | 6.9279 | 7.8058 | 8.6836 | 1.2156 | 2.3991 | 2.8789 | 2.8789 | 2.8789 | 2.8789 | 2.0005 | 2.3271 | 2.3271 | 2.3271 | 2.3271 | 2.3271
2020-02-01 16:00 | Summer | 1.2003 | 1.7178 | 2.4789 | 2.4789 | 2.4789 | 2.4789 | 1.3403 | 2.6509 | 2.6509 | 2.6509 | 2.6509 | 2.6509 | 4.5726 | 5.9009 | 6.7711 | 7.2291 | 8.1451 | 9.0612 | 1.2651 | 2.4969 | 2.9963 | 2.9963 | 2.9963 | 2.9963 | 1.7719 | 2.0612 | 2.0612 | 2.0612 | 2.0612 | 2.0612
2020-02-01 17:00 | Summer | 1.0669 | 1.527 | 2.2035 | 2.2035 | 2.2035 | 2.2035 | 1.0603 | 2.097 | 2.097 | 2.097 | 2.097 | 2.097 | 4.344 | 5.6058 | 6.4325 | 6.8676 | 7.7379 | 8.6081 | 1.2918 | 2.5495 | 3.0594 | 3.0594 | 3.0594 | 3.0594 | 1.8095 | 2.1049 | 2.1049 | 2.1049 | 2.1049 | 2.1049
2020-02-01 18:00 | Summer | 1.0099 | 1.4453 | 2.0856 | 2.0856 | 2.0856 | 2.0856 | 1.1146 | 2.2043 | 2.2043 | 2.2043 | 2.2043 | 2.2043 | 4.1916 | 5.4091 | 6.2068 | 6.6267 | 7.4664 | 8.3061 | 1.4328 | 2.8278 | 3.3934 | 3.3934 | 3.3934 | 3.3934 | 1.81 | 2.1055 | 2.1055 | 2.1055 | 2.1055 | 2.1055
2020-02-01 19:00 | Summer | 0.8498 | 1.2162 | 1.755 | 1.755 | 1.755 | 1.755 | 1.0917 | 2.1591 | 2.1591 | 2.1591 | 2.1591 | 2.1591 | 4.0772 | 5.2616 | 6.0376 | 6.4459 | 7.2627 | 8.0795 | 1.3642 | 2.6924 | 3.2309 | 3.2309 | 3.2309 | 3.2309 | 1.5814 | 1.8395 | 1.8395 | 1.8395 | 1.8395 | 1.8395
2020-02-01 20:00 | Summer | 0.85737 | 1.227 | 1.7706 | 1.7706 | 1.7706 | 1.7706 | 0.96596 | 1.9104 | 1.9104 | 1.9104 | 1.9104 | 1.9104 | 3.9061 | 5.0407 | 5.7841 | 6.1754 | 6.9579 | 7.7404 | 1.2079 | 2.3841 | 2.8609 | 2.8609 | 2.8609 | 2.8609 | 1.5623 | 1.8174 | 1.8174 | 1.8174 | 1.8174 | 1.8174
2020-02-01 21:00 | Summer | 0.64779 | 0.92709 | 1.3378 | 1.3378 | 1.3378 | 1.3378 | 0.86594 | 1.7126 | 1.7126 | 1.7126 | 1.7126 | 1.7126 | 3.8843 | 5.0127 | 5.7519 | 6.141 | 6.9191 | 7.6973 | 1.2308 | 2.4292 | 2.915 | 2.915 | 2.915 | 2.915 | 1.5242 | 1.7731 | 1.7731 | 1.7731 | 1.7731 | 1.7731
2020-02-01 22:00 | Summer | 0.91452 | 1.3088 | 1.8887 | 1.8887 | 1.8887 | 1.8887 | 0.82307 | 1.6278 | 1.6278 | 1.6278 | 1.6278 | 1.6278 | 3.62 | 4.6715 | 5.3604 | 5.723 | 6.4482 | 7.1734 | 1.227 | 2.4217 | 2.906 | 2.906 | 2.906 | 2.906 | 1.3917 | 1.6189 | 1.6189 | 1.6189 | 1.6189 | 1.6189
2020-02-01 23:00 | Summer | 0.81926 | 1.1725 | 1.692 | 1.692 | 1.692 | 1.692 | 0.79449 | 1.5713 | 1.5713 | 1.5713 | 1.5713 | 1.5713 | 3.4485 | 4.4502 | 5.1065 | 5.4519 | 6.1428 | 6.8336 | 1.2079 | 2.3841 | 2.8609 | 2.8609 | 2.8609 | 2.8609 | 1.3146 | 1.5293 | 1.5293 | 1.5293 | 1.5293 | 1.5293
2020-02-02 | Summer | 0.80094 | 1.1463 | 1.6541 | 1.6541 | 1.6541 | 1.6541 | 0.79735 | 1.577 | 1.577 | 1.577 | 1.577 | 1.577 | 3.1419 | 4.0545 | 4.6525 | 4.9672 | 5.5966 | 6.226 | 1.2308 | 2.4292 | 2.915 | 2.915 | 2.915 | 2.915 | 1.2384 | 1.4406 | 1.4406 | 1.4406 | 1.4406 | 1.4406
2020-02-02 01:00 | Summer | 0.85737 | 1.227 | 1.7706 | 1.7706 | 1.7706 | 1.7706 | 0.75448 | 1.4922 | 1.4922 | 1.4922 | 1.4922 | 1.4922 | 2.8388 | 3.6634 | 4.2037 | 4.4881 | 5.0568 | 5.6255 | 1.0441 | 2.0607 | 2.4728 | 2.4728 | 2.4728 | 2.4728 | 1.2575 | 1.4628 | 1.4628 | 1.4628 | 1.4628 | 1.4628
2020-02-02 02:00 | Summer | 0.80021 | 1.1452 | 1.6526 | 1.6526 | 1.6526 | 1.6526 | 0.69732 | 1.3791 | 1.3791 | 1.3791 | 1.3791 | 1.3791 | 2.7436 | 3.5405 | 4.0627 | 4.3375 | 4.8871 | 5.4367 | 1.0365 | 2.0456 | 2.4548 | 2.4548 | 2.4548 | 2.4548 | 1.2194 | 1.4184 | 1.4184 | 1.4184 | 1.4184 | 1.4184
2020-02-02 03:00 | Summer | 0.79942 | 1.1441 | 1.651 | 1.651 | 1.651 | 1.651 | 0.70875 | 1.4017 | 1.4017 | 1.4017 | 1.4017 | 1.4017 | 2.6483 | 3.4176 | 3.9216 | 4.1869 | 4.7174 | 5.2479 | 1.0212 | 2.0156 | 2.4187 | 2.4187 | 2.4187 | 2.4187 | 1.1813 | 1.3741 | 1.3741 | 1.3741 | 1.3741 | 1.3741
2020-02-02 04:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.76877 | 1.5204 | 1.5204 | 1.5204 | 1.5204 | 1.5204 | 2.6672 | 3.4419 | 3.9495 | 4.2167 | 4.751 | 5.2853 | 1.0136 | 2.0005 | 2.4006 | 2.4006 | 2.4006 | 2.4006 | 1.1622 | 1.352 | 1.352 | 1.352 | 1.352 | 1.352
2020-02-02 05:00 | Summer | 0.66684 | 0.95435 | 1.3772 | 1.3772 | 1.3772 | 1.3772 | 0.74305 | 1.4696 | 1.4696 | 1.4696 | 1.4696 | 1.4696 | 2.783 | 3.5914 | 4.121 | 4.3998 | 4.9573 | 5.5148 | 0.97168 | 1.9178 | 2.3013 | 2.3013 | 2.3013 | 2.3013 | 1.1432 | 1.3298 | 1.3298 | 1.3298 | 1.3298 | 1.3298
2020-02-02 06:00 | Summer | 0.66684 | 0.95435 | 1.3772 | 1.3772 | 1.3772 | 1.3772 | 0.86308 | 1.707 | 1.707 | 1.707 | 1.707 | 1.707 | 2.8388 | 3.6634 | 4.2037 | 4.4881 | 5.0568 | 5.6255 | 1.0936 | 2.1585 | 2.5901 | 2.5901 | 2.5901 | 2.5901 | 1.1813 | 1.3741 | 1.3741 | 1.3741 | 1.3741 | 1.3741
2020-02-02 07:00 | Summer | 0.64779 | 0.92709 | 1.3378 | 1.3378 | 1.3378 | 1.3378 | 0.95739 | 1.8935 | 1.8935 | 1.8935 | 1.8935 | 1.8935 | 3.1056 | 4.0077 | 4.5987 | 4.9098 | 5.5319 | 6.154 | 1.1927 | 2.354 | 2.8248 | 2.8248 | 2.8248 | 2.8248 | 1.3337 | 1.5514 | 1.5514 | 1.5514 | 1.5514 | 1.5514
2020-02-02 08:00 | Summer | 0.61183 | 0.87562 | 1.2636 | 1.2636 | 1.2636 | 1.2636 | 0.92023 | 1.82 | 1.82 | 1.82 | 1.82 | 1.82 | 3.5819 | 4.6223 | 5.304 | 5.6628 | 6.3804 | 7.0979 | 1.307 | 2.5796 | 3.0955 | 3.0955 | 3.0955 | 3.0955 | 1.448 | 1.6844 | 1.6844 | 1.6844 | 1.6844 | 1.6844
2020-02-02 09:00 | Summer | 0.64779 | 0.92709 | 1.3378 | 1.3378 | 1.3378 | 1.3378 | 0.95453 | 1.8878 | 1.8878 | 1.8878 | 1.8878 | 1.8878 | 3.8096 | 4.9162 | 5.6413 | 6.0229 | 6.786 | 7.5492 | 1.6157 | 3.1888 | 3.8266 | 3.8266 | 3.8266 | 3.8266 | 1.5623 | 1.8174 | 1.8174 | 1.8174 | 1.8174 | 1.8174
2020-02-02 10:00 | Summer | 0.64779 | 0.92709 | 1.3378 | 1.3378 | 1.3378 | 1.3378 | 0.97453 | 1.9274 | 1.9274 | 1.9274 | 1.9274 | 1.9274 | 4.0772 | 5.2616 | 6.0376 | 6.4459 | 7.2627 | 8.0795 | 1.6652 | 3.2866 | 3.9439 | 3.9439 | 3.9439 | 3.9439 | 1.6004 | 1.8617 | 1.8617 | 1.8617 | 1.8617 | 1.8617
2020-02-02 11:00 | Summer | 0.93624 | 1.3399 | 1.9335 | 1.9335 | 1.9335 | 1.9335 | 0.91738 | 1.8143 | 1.8143 | 1.8143 | 1.8143 | 1.8143 | 4.1916 | 5.4091 | 6.2068 | 6.6267 | 7.4664 | 8.3061 | 1.6042 | 3.1662 | 3.7995 | 3.7995 | 3.7995 | 3.7995 | 1.6576 | 1.9282 | 1.9282 | 1.9282 | 1.9282 | 1.9282
2020-02-02 12:00 | Summer | 1.105 | 1.5815 | 2.2822 | 2.2822 | 2.2822 | 2.2822 | 0.92881 | 1.837 | 1.837 | 1.837 | 1.837 | 1.837 | 3.982 | 5.1387 | 5.8965 | 6.2953 | 7.0931 | 7.8908 | 1.5318 | 3.0233 | 3.628 | 3.628 | 3.628 | 3.628 | 1.5623 | 1.8174 | 1.8174 | 1.8174 | 1.8174 | 1.8174
2020-02-02 13:00 | Summer | 1.01 | 1.4455 | 2.0859 | 2.0859 | 2.0859 | 2.0859 | 0.8888 | 1.7578 | 1.7578 | 1.7578 | 1.7578 | 1.7578 | 4.2423 | 5.4746 | 6.282 | 6.707 | 7.5568 | 8.4067 | 1.5585 | 3.076 | 3.6912 | 3.6912 | 3.6912 | 3.6912 | 1.448 | 1.6844 | 1.6844 | 1.6844 | 1.6844 | 1.6844
2020-02-02 14:00 | Summer | 0.70494 | 1.0089 | 1.4559 | 1.4559 | 1.4559 | 1.4559 | 0.96596 | 1.9104 | 1.9104 | 1.9104 | 1.9104 | 1.9104 | 4.344 | 5.6058 | 6.4325 | 6.8676 | 7.7379 | 8.6081 | 1.4442 | 2.8504 | 3.4204 | 3.4204 | 3.4204 | 3.4204 | 1.448 | 1.6844 | 1.6844 | 1.6844 | 1.6844 | 1.6844
2020-02-02 15:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.94135 | 1.8617 | 1.8617 | 1.8617 | 1.8617 | 1.8617 | 4.1331 | 5.3337 | 6.1203 | 6.5343 | 7.3623 | 8.1903 | 1.4023 | 2.7676 | 3.3212 | 3.3212 | 3.3212 | 3.3212 | 1.3381 | 1.5566 | 1.5566 | 1.5566 | 1.5566 | 1.5566
2020-02-02 16:00 | Summer | 0.78115 | 1.118 | 1.6133 | 1.6133 | 1.6133 | 1.6133 | 0.89166 | 1.7635 | 1.7635 | 1.7635 | 1.7635 | 1.7635 | 3.9058 | 5.0403 | 5.7836 | 6.1749 | 6.9573 | 7.7397 | 1.3032 | 2.5721 | 3.0865 | 3.0865 | 3.0865 | 3.0865 | 1.3337 | 1.5514 | 1.5514 | 1.5514 | 1.5514 | 1.5514
2020-02-02 17:00 | Summer | 0.68589 | 0.98162 | 1.4165 | 1.4165 | 1.4165 | 1.4165 | 0.86879 | 1.7183 | 1.7183 | 1.7183 | 1.7183 | 1.7183 | 3.6581 | 4.7207 | 5.4169 | 5.7833 | 6.5161 | 7.2489 | 1.2384 | 2.4442 | 2.9331 | 2.9331 | 2.9331 | 2.9331 | 1.3337 | 1.5514 | 1.5514 | 1.5514 | 1.5514 | 1.5514
2020-02-02 18:00 | Summer | 0.83831 | 1.1998 | 1.7313 | 1.7313 | 1.7313 | 1.7313 | 0.86308 | 1.707 | 1.707 | 1.707 | 1.707 | 1.707 | 3.3533 | 4.3273 | 4.9655 | 5.3013 | 5.9731 | 6.6449 | 1.1851 | 2.3389 | 2.8067 | 2.8067 | 2.8067 | 2.8067 | 1.2256 | 1.4257 | 1.4257 | 1.4257 | 1.4257 | 1.4257
2020-02-02 19:00 | Summer | 0.7621 | 1.0907 | 1.5739 | 1.5739 | 1.5739 | 1.5739 | 0.79735 | 1.577 | 1.577 | 1.577 | 1.577 | 1.577 | 3.3342 | 4.3027 | 4.9373 | 5.2712 | 5.9392 | 6.6071 | 1.0784 | 2.1284 | 2.554 | 2.554 | 2.554 | 2.554 | 1.2194 | 1.4184 | 1.4184 | 1.4184 | 1.4184 | 1.4184
2020-02-02 20:00 | Summer | 0.81926 | 1.1725 | 1.692 | 1.692 | 1.692 | 1.692 | 0.79449 | 1.5713 | 1.5713 | 1.5713 | 1.5713 | 1.5713 | 3.1437 | 4.0568 | 4.6551 | 4.97 | 5.5998 | 6.2296 | 1.1813 | 2.3314 | 2.7977 | 2.7977 | 2.7977 | 2.7977 | 1.1813 | 1.3741 | 1.3741 | 1.3741 | 1.3741 | 1.3741
2020-02-02 21:00 | Summer | 0.7621 | 1.0907 | 1.5739 | 1.5739 | 1.5739 | 1.5739 | 0.68875 | 1.3622 | 1.3622 | 1.3622 | 1.3622 | 1.3622 | 2.9722 | 3.8356 | 4.4012 | 4.6989 | 5.2943 | 5.8898 | 1.1546 | 2.2788 | 2.7345 | 2.7345 | 2.7345 | 2.7345 | 1.1432 | 1.3298 | 1.3298 | 1.3298 | 1.3298 | 1.3298
2020-02-02 22:00 | Summer | 0.83831 | 1.1998 | 1.7313 | 1.7313 | 1.7313 | 1.7313 | 0.64874 | 1.283 | 1.283 | 1.283 | 1.283 | 1.283 | 2.8388 | 3.6634 | 4.2037 | 4.4881 | 5.0568 | 5.6255 | 1.0867 | 2.1448 | 2.5738 | 2.5738 | 2.5738 | 2.5738 | 1.105 | 1.2855 | 1.2855 | 1.2855 | 1.2855 | 1.2855
2020-02-02 23:00 | Summer | 0.7621 | 1.0907 | 1.5739 | 1.5739 | 1.5739 | 1.5739 | 0.60301 | 1.1926 | 1.1926 | 1.1926 | 1.1926 | 1.1926 | 2.5721 | 3.3192 | 3.8087 | 4.0664 | 4.5816 | 5.0969 | 1.0026 | 1.9789 | 2.3746 | 2.3746 | 2.3746 | 2.3746 | 1.086 | 1.2633 | 1.2633 | 1.2633 | 1.2633 | 1.2633
2020-02-03 | Summer | 0.70494 | 1.0089 | 1.4559 | 1.4559 | 1.4559 | 1.4559 | 0.59444 | 1.1756 | 1.1756 | 1.1756 | 1.1756 | 1.1756 | 2.2673 | 2.9258 | 3.3573 | 3.5844 | 4.0386 | 4.4928 | 0.92214 | 1.82 | 2.184 | 2.184 | 2.184 | 2.184 | 1.105 | 1.2855 | 1.2855 | 1.2855 | 1.2855 | 1.2855
2020-02-03 01:00 | Summer | 0.5909 | 0.84568 | 1.2203 | 1.2203 | 1.2203 | 1.2203 | 0.62016 | 1.2265 | 1.2265 | 1.2265 | 1.2265 | 1.2265 | 2.0958 | 2.7046 | 3.1034 | 3.3133 | 3.7332 | 4.153 | 0.79258 | 1.5643 | 1.8772 | 1.8772 | 1.8772 | 1.8772 | 1.0669 | 1.2411 | 1.2411 | 1.2411 | 1.2411 | 1.2411
2020-02-03 02:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.56586 | 1.1191 | 1.1191 | 1.1191 | 1.1191 | 1.1191 | 2.0958 | 2.7046 | 3.1034 | 3.3133 | 3.7332 | 4.153 | 0.83831 | 1.6546 | 1.9855 | 1.9855 | 1.9855 | 1.9855 | 1.1043 | 1.2846 | 1.2846 | 1.2846 | 1.2846 | 1.2846
2020-02-03 03:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.56014 | 1.1078 | 1.1078 | 1.1078 | 1.1078 | 1.1078 | 2.0577 | 2.6554 | 3.047 | 3.2531 | 3.6653 | 4.0775 | 0.84212 | 1.6621 | 1.9945 | 1.9945 | 1.9945 | 1.9945 | 1.3146 | 1.5293 | 1.5293 | 1.5293 | 1.5293 | 1.5293
2020-02-03 04:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.6173 | 1.2209 | 1.2209 | 1.2209 | 1.2209 | 1.2209 | 2.0577 | 2.6554 | 3.047 | 3.2531 | 3.6653 | 4.0775 | 0.82688 | 1.632 | 1.9584 | 1.9584 | 1.9584 | 1.9584 | 1.3337 | 1.5514 | 1.5514 | 1.5514 | 1.5514 | 1.5514
2020-02-03 05:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.76877 | 1.5204 | 1.5204 | 1.5204 | 1.5204 | 1.5204 | 2.3052 | 2.9748 | 3.4135 | 3.6444 | 4.1062 | 4.568 | 0.9069 | 1.7899 | 2.1479 | 2.1479 | 2.1479 | 2.1479 | 1.4289 | 1.6622 | 1.6622 | 1.6622 | 1.6622 | 1.6622
2020-02-03 06:00 | Summer | 1.5623 | 2.2359 | 3.2265 | 3.2265 | 3.2265 | 3.2265 | 0.95453 | 1.8878 | 1.8878 | 1.8878 | 1.8878 | 1.8878 | 2.6787 | 3.4568 | 3.9666 | 4.2349 | 4.7715 | 5.3081 | 1.0174 | 2.008 | 2.4096 | 2.4096 | 2.4096 | 2.4096 | 1.6934 | 1.9699 | 1.9699 | 1.9699 | 1.9699 | 1.9699
2020-02-03 07:00 | Summer | 2.0386 | 2.9176 | 4.2102 | 4.2102 | 4.2102 | 4.2102 | 1.2746 | 2.5209 | 2.5209 | 2.5209 | 2.5209 | 2.5209 | 3.1574 | 4.0745 | 4.6754 | 4.9917 | 5.6242 | 6.2567 | 1.1736 | 2.3164 | 2.7797 | 2.7797 | 2.7797 | 2.7797 | 2.534 | 2.9477 | 2.9477 | 2.9477 | 2.9477 | 2.9477
2020-02-03 08:00 | Summer | 2.3625 | 3.3811 | 4.8791 | 4.8791 | 4.8791 | 4.8791 | 1.3918 | 2.7526 | 2.7526 | 2.7526 | 2.7526 | 2.7526 | 3.4485 | 4.4502 | 5.1065 | 5.4519 | 6.1428 | 6.8336 | 1.1927 | 2.354 | 2.8248 | 2.8248 | 2.8248 | 2.8248 | 2.9341 | 3.4131 | 3.4131 | 3.4131 | 3.4131 | 3.4131
2020-02-03 09:00 | Summer | 2.4006 | 3.4357 | 4.9578 | 4.9578 | 4.9578 | 4.9578 | 1.5918 | 3.1483 | 3.1483 | 3.1483 | 3.1483 | 3.1483 | 3.7915 | 4.8928 | 5.6144 | 5.9941 | 6.7537 | 7.5132 | 1.227 | 2.4217 | 2.906 | 2.906 | 2.906 | 2.906 | 3.1246 | 3.6348 | 3.6348 | 3.6348 | 3.6348 | 3.6348
2020-02-03 10:00 | Summer | 2.3816 | 3.4084 | 4.9185 | 4.9185 | 4.9185 | 4.9185 | 1.6519 | 3.267 | 3.267 | 3.267 | 3.267 | 3.267 | 4.1154 | 5.3108 | 6.094 | 6.5062 | 7.3306 | 8.155 | 1.2156 | 2.3991 | 2.8789 | 2.8789 | 2.8789 | 2.8789 | 3.1627 | 3.6791 | 3.6791 | 3.6791 | 3.6791 | 3.6791
2020-02-03 11:00 | Summer | 2.3625 | 3.3811 | 4.8791 | 4.8791 | 4.8791 | 4.8791 | 1.5318 | 3.0296 | 3.0296 | 3.0296 | 3.0296 | 3.0296 | 4.1535 | 5.3599 | 6.1504 | 6.5664 | 7.3985 | 8.2306 | 1.2117 | 2.3916 | 2.8699 | 2.8699 | 2.8699 | 2.8699 | 3.2199 | 3.7456 | 3.7456 | 3.7456 | 3.7456 | 3.7456
2020-02-03 12:00 | Summer | 2.3054 | 3.2993 | 4.7611 | 4.7611 | 4.7611 | 4.7611 | 1.5833 | 3.1313 | 3.1313 | 3.1313 | 3.1313 | 3.1313 | 4.1725 | 5.3845 | 6.1786 | 6.5966 | 7.4324 | 8.2683 | 1.2384 | 2.4442 | 2.9331 | 2.9331 | 2.9331 | 2.9331 | 3.258 | 3.7899 | 3.7899 | 3.7899 | 3.7899 | 3.7899
2020-02-03 13:00 | Summer | 2.2291 | 3.1903 | 4.6037 | 4.6037 | 4.6037 | 4.6037 | 1.5318 | 3.0296 | 3.0296 | 3.0296 | 3.0296 | 3.0296 | 4.0963 | 5.2862 | 6.0658 | 6.4761 | 7.2967 | 8.1173 | 1.227 | 2.4217 | 2.906 | 2.906 | 2.906 | 2.906 | 3.1818 | 3.7013 | 3.7013 | 3.7013 | 3.7013 | 3.7013
2020-02-03 14:00 | Summer | 2.2291 | 3.1903 | 4.6037 | 4.6037 | 4.6037 | 4.6037 | 1.5175 | 3.0013 | 3.0013 | 3.0013 | 3.0013 | 3.0013 | 4.1194 | 5.316 | 6.0999 | 6.5125 | 7.3378 | 8.163 | 1.1965 | 2.3615 | 2.8338 | 2.8338 | 2.8338 | 2.8338 | 3.3151 | 3.8564 | 3.8564 | 3.8564 | 3.8564 | 3.8564
2020-02-03 15:00 | Summer | 2.2482 | 3.2175 | 4.643 | 4.643 | 4.643 | 4.643 | 1.5004 | 2.9674 | 2.9674 | 2.9674 | 2.9674 | 2.9674 | 4.1721 | 5.3839 | 6.1779 | 6.5958 | 7.4316 | 8.2674 | 1.2079 | 2.3841 | 2.8609 | 2.8609 | 2.8609 | 2.8609 | 3.2389 | 3.7677 | 3.7677 | 3.7677 | 3.7677 | 3.7677
2020-02-03 16:00 | Summer | 2.172 | 3.1085 | 4.4856 | 4.4856 | 4.4856 | 4.4856 | 1.5804 | 3.1256 | 3.1256 | 3.1256 | 3.1256 | 3.1256 | 4.2106 | 5.4337 | 6.235 | 6.6568 | 7.5003 | 8.3438 | 1.1736 | 2.3164 | 2.7797 | 2.7797 | 2.7797 | 2.7797 | 3.1818 | 3.7013 | 3.7013 | 3.7013 | 3.7013 | 3.7013
2020-02-03 17:00 | Summer | 2.0577 | 2.9449 | 4.2495 | 4.2495 | 4.2495 | 4.2495 | 1.5004 | 2.9674 | 2.9674 | 2.9674 | 2.9674 | 2.9674 | 3.982 | 5.1387 | 5.8965 | 6.2953 | 7.0931 | 7.8908 | 1.1851 | 2.3389 | 2.8067 | 2.8067 | 2.8067 | 2.8067 | 2.9544 | 3.4367 | 3.4367 | 3.4367 | 3.4367 | 3.4367
2020-02-03 18:00 | Summer | 1.5492 | 2.2172 | 3.1995 | 3.1995 | 3.1995 | 3.1995 | 1.3019 | 2.5749 | 2.5749 | 2.5749 | 2.5749 | 2.5749 | 3.7886 | 4.8891 | 5.6101 | 5.9896 | 6.7486 | 7.5075 | 1.1546 | 2.2788 | 2.7345 | 2.7345 | 2.7345 | 2.7345 | 2.1234 | 2.4701 | 2.4701 | 2.4701 | 2.4701 | 2.4701
2020-02-03 19:00 | Summer | 0.76169 | 1.0901 | 1.5731 | 1.5731 | 1.5731 | 1.5731 | 0.84919 | 1.6795 | 1.6795 | 1.6795 | 1.6795 | 1.6795 | 3.2015 | 4.1315 | 4.7408 | 5.0615 | 5.7029 | 6.3442 | 1.105 | 2.181 | 2.6172 | 2.6172 | 2.6172 | 2.6172 | 1.3146 | 1.5293 | 1.5293 | 1.5293 | 1.5293 | 1.5293
2020-02-03 20:00 | Summer | 0.7621 | 1.0907 | 1.5739 | 1.5739 | 1.5739 | 1.5739 | 0.75162 | 1.4865 | 1.4865 | 1.4865 | 1.4865 | 1.4865 | 2.6483 | 3.4176 | 3.9216 | 4.1869 | 4.7174 | 5.2479 | 1.0822 | 2.1359 | 2.5631 | 2.5631 | 2.5631 | 2.5631 | 1.3337 | 1.5514 | 1.5514 | 1.5514 | 1.5514 | 1.5514
2020-02-03 21:00 | Summer | 0.64779 | 0.92709 | 1.3378 | 1.3378 | 1.3378 | 1.3378 | 0.60587 | 1.1983 | 1.1983 | 1.1983 | 1.1983 | 1.1983 | 2.5585 | 3.3017 | 3.7887 | 4.0449 | 4.5575 | 5.07 | 1.0746 | 2.1208 | 2.545 | 2.545 | 2.545 | 2.545 | 1.2577 | 1.4631 | 1.4631 | 1.4631 | 1.4631 | 1.4631
2020-02-03 22:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.59729 | 1.1813 | 1.1813 | 1.1813 | 1.1813 | 1.1813 | 2.4197 | 3.1225 | 3.583 | 3.8254 | 4.3101 | 4.7949 | 0.92976 | 1.8351 | 2.2021 | 2.2021 | 2.2021 | 2.2021 | 1.1241 | 1.3076 | 1.3076 | 1.3076 | 1.3076 | 1.3076
2020-02-03 23:00 | Summer | 0.57194 | 0.81854 | 1.1812 | 1.1812 | 1.1812 | 1.1812 | 0.61158 | 1.2096 | 1.2096 | 1.2096 | 1.2096 | 1.2096 | 2.2482 | 2.9013 | 3.3291 | 3.5543 | 4.0047 | 4.4551 | 0.84593 | 1.6696 | 2.0035 | 2.0035 | 2.0035 | 2.0035 | 1.0098 | 1.1746 | 1.1746 | 1.1746 | 1.1746 | 1.1746
2020-02-04 | Summer | 0.59024 | 0.84473 | 1.219 | 1.219 | 1.219 | 1.219 | 0.53442 | 1.057 | 1.057 | 1.057 | 1.057 | 1.057 | 2.001 | 2.5822 | 2.963 | 3.1634 | 3.5643 | 3.9651 | 0.77734 | 1.5342 | 1.8411 | 1.8411 | 1.8411 | 1.8411 | 0.95263 | 1.1082 | 1.1082 | 1.1082 | 1.1082 | 1.1082
2020-02-04 01:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.52585 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.9243 | 2.4833 | 2.8495 | 3.0422 | 3.4277 | 3.8132 | 0.59825 | 1.1808 | 1.4169 | 1.4169 | 1.4169 | 1.4169 | 0.91452 | 1.0638 | 1.0638 | 1.0638 | 1.0638 | 1.0638
2020-02-04 02:00 | Summer | 0.56442 | 0.80778 | 1.1657 | 1.1657 | 1.1657 | 1.1657 | 0.56586 | 1.1191 | 1.1191 | 1.1191 | 1.1191 | 1.1191 | 1.7719 | 2.2866 | 2.6238 | 2.8013 | 3.1562 | 3.5112 | 0.56395 | 1.1131 | 1.3357 | 1.3357 | 1.3357 | 1.3357 | 0.93358 | 1.086 | 1.086 | 1.086 | 1.086 | 1.086
2020-02-04 03:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.48584 | 0.96086 | 0.96086 | 0.96086 | 0.96086 | 0.96086 | 1.81 | 2.3358 | 2.6802 | 2.8615 | 3.2241 | 3.5867 | 0.62111 | 1.2259 | 1.4711 | 1.4711 | 1.4711 | 1.4711 | 0.89547 | 1.0417 | 1.0417 | 1.0417 | 1.0417 | 1.0417
2020-02-04 04:00 | Summer | 0.60948 | 0.87226 | 1.2587 | 1.2587 | 1.2587 | 1.2587 | 0.52585 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.7909 | 2.3112 | 2.652 | 2.8314 | 3.1902 | 3.549 | 0.60206 | 1.1883 | 1.4259 | 1.4259 | 1.4259 | 1.4259 | 0.97168 | 1.1303 | 1.1303 | 1.1303 | 1.1303 | 1.1303
2020-02-04 05:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.50584 | 1.0004 | 1.0004 | 1.0004 | 1.0004 | 1.0004 | 1.8481 | 2.3849 | 2.7366 | 2.9218 | 3.292 | 3.6622 | 0.83069 | 1.6395 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 1.2088 | 1.4061 | 1.4061 | 1.4061 | 1.4061 | 1.4061
2020-02-04 06:00 | Summer | 0.70474 | 1.0086 | 1.4554 | 1.4554 | 1.4554 | 1.4554 | 0.83736 | 1.6561 | 1.6561 | 1.6561 | 1.6561 | 1.6561 | 1.9815 | 2.557 | 2.9341 | 3.1326 | 3.5296 | 3.9265 | 1.0212 | 2.0156 | 2.4187 | 2.4187 | 2.4187 | 2.4187 | 1.4011 | 1.6298 | 1.6298 | 1.6298 | 1.6298 | 1.6298
2020-02-04 07:00 | Summer | 1.4322 | 2.0497 | 2.9579 | 2.9579 | 2.9579 | 2.9579 | 0.9431 | 1.8652 | 1.8652 | 1.8652 | 1.8652 | 1.8652 | 2.5603 | 3.304 | 3.7912 | 4.0477 | 4.5606 | 5.0735 | 1.1851 | 2.3389 | 2.8067 | 2.8067 | 2.8067 | 2.8067 | 1.8479 | 2.1496 | 2.1496 | 2.1496 | 2.1496 | 2.1496
2020-02-04 08:00 | Summer | 2.1525 | 3.0805 | 4.4453 | 4.4453 | 4.4453 | 4.4453 | 1.1374 | 2.2496 | 2.2496 | 2.2496 | 2.2496 | 2.2496 | 2.8198 | 3.6389 | 4.1755 | 4.4579 | 5.0228 | 5.5877 | 1.1622 | 2.2938 | 2.7526 | 2.7526 | 2.7526 | 2.7526 | 2.191 | 2.5488 | 2.5488 | 2.5488 | 2.5488 | 2.5488
2020-02-04 09:00 | Summer | 2.2101 | 3.163 | 4.5643 | 4.5643 | 4.5643 | 4.5643 | 1.1889 | 2.3513 | 2.3513 | 2.3513 | 2.3513 | 2.3513 | 2.9341 | 3.7864 | 4.3448 | 4.6387 | 5.2265 | 5.8142 | 1.3451 | 2.6548 | 3.1858 | 3.1858 | 3.1858 | 3.1858 | 2.4185 | 2.8134 | 2.8134 | 2.8134 | 2.8134 | 2.8134
2020-02-04 10:00 | Summer | 2.0386 | 2.9176 | 4.2102 | 4.2102 | 4.2102 | 4.2102 | 1.266 | 2.5039 | 2.5039 | 2.5039 | 2.5039 | 2.5039 | 3.3151 | 4.2781 | 4.909 | 5.2411 | 5.9052 | 6.5693 | 1.3375 | 2.6398 | 3.1677 | 3.1677 | 3.1677 | 3.1677 | 2.6864 | 3.125 | 3.125 | 3.125 | 3.125 | 3.125
2020-02-04 11:00 | Summer | 2.1339 | 3.0539 | 4.4069 | 4.4069 | 4.4069 | 4.4069 | 1.2403 | 2.453 | 2.453 | 2.453 | 2.453 | 2.453 | 3.3533 | 4.3273 | 4.9655 | 5.3013 | 5.9731 | 6.6449 | 1.1622 | 2.2938 | 2.7526 | 2.7526 | 2.7526 | 2.7526 | 2.6528 | 3.0859 | 3.0859 | 3.0859 | 3.0859 | 3.0859
2020-02-04 12:00 | Summer | 1.9629 | 2.8092 | 4.0538 | 4.0538 | 4.0538 | 4.0538 | 1.2975 | 2.5661 | 2.5661 | 2.5661 | 2.5661 | 2.5661 | 3.5057 | 4.524 | 5.1912 | 5.5423 | 6.2446 | 6.9469 | 1.1317 | 2.2337 | 2.6804 | 2.6804 | 2.6804 | 2.6804 | 2.7501 | 3.1991 | 3.1991 | 3.1991 | 3.1991 | 3.1991
2020-02-04 13:00 | Summer | 2.0196 | 2.8903 | 4.1709 | 4.1709 | 4.1709 | 4.1709 | 1.3946 | 2.7583 | 2.7583 | 2.7583 | 2.7583 | 2.7583 | 3.4999 | 4.5166 | 5.1826 | 5.5332 | 6.2343 | 6.9355 | 1.1508 | 2.2713 | 2.7255 | 2.7255 | 2.7255 | 2.7255 | 2.8388 | 3.3023 | 3.3023 | 3.3023 | 3.3023 | 3.3023
2020-02-04 14:00 | Summer | 1.9714 | 2.8214 | 4.0714 | 4.0714 | 4.0714 | 4.0714 | 1.2642 | 2.5003 | 2.5003 | 2.5003 | 2.5003 | 2.5003 | 3.5438 | 4.5732 | 5.2476 | 5.6026 | 6.3125 | 7.0224 | 1.1546 | 2.2788 | 2.7345 | 2.7345 | 2.7345 | 2.7345 | 2.8769 | 3.3466 | 3.3466 | 3.3466 | 3.3466 | 3.3466
2020-02-04 15:00 | Summer | 1.9434 | 2.7813 | 4.0135 | 4.0135 | 4.0135 | 4.0135 | 1.286 | 2.5435 | 2.5435 | 2.5435 | 2.5435 | 2.5435 | 3.6009 | 4.6469 | 5.3322 | 5.6929 | 6.4143 | 7.1357 | 1.1736 | 2.3164 | 2.7797 | 2.7797 | 2.7797 | 2.7797 | 2.9531 | 3.4353 | 3.4353 | 3.4353 | 3.4353 | 3.4353
2020-02-04 16:00 | Summer | 1.9053 | 2.7267 | 3.9348 | 3.9348 | 3.9348 | 3.9348 | 1.2975 | 2.5661 | 2.5661 | 2.5661 | 2.5661 | 2.5661 | 3.5628 | 4.5978 | 5.2758 | 5.6327 | 6.3464 | 7.0602 | 1.1584 | 2.2863 | 2.7436 | 2.7436 | 2.7436 | 2.7436 | 2.8198 | 3.2802 | 3.2802 | 3.2802 | 3.2802 | 3.2802
2020-02-04 17:00 | Summer | 1.81 | 2.5904 | 3.738 | 3.738 | 3.738 | 3.738 | 1.266 | 2.5039 | 2.5039 | 2.5039 | 2.5039 | 2.5039 | 3.4485 | 4.4502 | 5.1065 | 5.4519 | 6.1428 | 6.8336 | 1.1355 | 2.2412 | 2.6894 | 2.6894 | 2.6894 | 2.6894 | 2.7436 | 3.1915 | 3.1915 | 3.1915 | 3.1915 | 3.1915
2020-02-04 18:00 | Summer | 1.3032 | 1.865 | 2.6913 | 2.6913 | 2.6913 | 2.6913 | 0.9295 | 1.8383 | 1.8383 | 1.8383 | 1.8383 | 1.8383 | 3.258 | 4.2044 | 4.8244 | 5.1507 | 5.8034 | 6.4561 | 1.1355 | 2.2412 | 2.6894 | 2.6894 | 2.6894 | 2.6894 | 2.1529 | 2.5044 | 2.5044 | 2.5044 | 2.5044 | 2.5044
2020-02-04 19:00 | Summer | 0.7621 | 1.0907 | 1.5739 | 1.5739 | 1.5739 | 1.5739 | 0.66588 | 1.317 | 1.317 | 1.317 | 1.317 | 1.317 | 2.9917 | 3.8607 | 4.43 | 4.7297 | 5.329 | 5.9283 | 1.1012 | 2.1735 | 2.6082 | 2.6082 | 2.6082 | 2.6082 | 1.2575 | 1.4628 | 1.4628 | 1.4628 | 1.4628 | 1.4628
2020-02-04 20:00 | Summer | 0.724 | 1.0362 | 1.4952 | 1.4952 | 1.4952 | 1.4952 | 0.6716 | 1.3283 | 1.3283 | 1.3283 | 1.3283 | 1.3283 | 2.553 | 3.2946 | 3.7805 | 4.0362 | 4.5477 | 5.0591 | 1.0593 | 2.0908 | 2.5089 | 2.5089 | 2.5089 | 2.5089 | 1.1432 | 1.3298 | 1.3298 | 1.3298 | 1.3298 | 1.3298
2020-02-04 21:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.52013 | 1.0287 | 1.0287 | 1.0287 | 1.0287 | 1.0287 | 2.4959 | 3.2209 | 3.6959 | 3.9459 | 4.4459 | 4.9459 | 1.0441 | 2.0607 | 2.4728 | 2.4728 | 2.4728 | 2.4728 | 1.086 | 1.2633 | 1.2633 | 1.2633 | 1.2633 | 1.2633
2020-02-04 22:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.52013 | 1.0287 | 1.0287 | 1.0287 | 1.0287 | 1.0287 | 2.3054 | 2.975 | 3.4138 | 3.6447 | 4.1065 | 4.5683 | 0.95644 | 1.8877 | 2.2652 | 2.2652 | 2.2652 | 2.2652 | 0.95263 | 1.1082 | 1.1082 | 1.1082 | 1.1082 | 1.1082
2020-02-04 23:00 | Summer | 0.58529 | 0.83764 | 1.2087 | 1.2087 | 1.2087 | 1.2087 | 0.46297 | 0.91565 | 0.91565 | 0.91565 | 0.91565 | 0.91565 | 2.0434 | 2.6369 | 3.0258 | 3.2305 | 3.6398 | 4.0492 | 0.87261 | 1.7222 | 2.0667 | 2.0667 | 2.0667 | 2.0667 | 0.93358 | 1.086 | 1.086 | 1.086 | 1.086 | 1.086
2020-02-05 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.50013 | 0.98912 | 0.98912 | 0.98912 | 0.98912 | 0.98912 | 1.9243 | 2.4833 | 2.8495 | 3.0422 | 3.4277 | 3.8132 | 0.79258 | 1.5643 | 1.8772 | 1.8772 | 1.8772 | 1.8772 | 0.89547 | 1.0417 | 1.0417 | 1.0417 | 1.0417 | 1.0417
2020-02-05 01:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.47726 | 0.94391 | 0.94391 | 0.94391 | 0.94391 | 0.94391 | 1.7909 | 2.3112 | 2.652 | 2.8314 | 3.1902 | 3.549 | 0.79258 | 1.5643 | 1.8772 | 1.8772 | 1.8772 | 1.8772 | 0.93358 | 1.086 | 1.086 | 1.086 | 1.086 | 1.086
2020-02-05 02:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.47441 | 0.93825 | 0.93825 | 0.93825 | 0.93825 | 0.93825 | 1.7719 | 2.2866 | 2.6238 | 2.8013 | 3.1562 | 3.5112 | 0.97549 | 1.9253 | 2.3104 | 2.3104 | 2.3104 | 2.3104 | 0.89547 | 1.0417 | 1.0417 | 1.0417 | 1.0417 | 1.0417
2020-02-05 03:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.51156 | 1.0117 | 1.0117 | 1.0117 | 1.0117 | 1.0117 | 1.7528 | 2.262 | 2.5956 | 2.7712 | 3.1223 | 3.4734 | 0.78115 | 1.5417 | 1.8501 | 1.8501 | 1.8501 | 1.8501 | 0.91452 | 1.0638 | 1.0638 | 1.0638 | 1.0638 | 1.0638
2020-02-05 04:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.53156 | 1.0513 | 1.0513 | 1.0513 | 1.0513 | 1.0513 | 1.7338 | 2.2374 | 2.5674 | 2.741 | 3.0884 | 3.4357 | 0.73924 | 1.459 | 1.7508 | 1.7508 | 1.7508 | 1.7508 | 1.0018 | 1.1653 | 1.1653 | 1.1653 | 1.1653 | 1.1653
2020-02-05 05:00 | Summer | 0.59477 | 0.85121 | 1.2283 | 1.2283 | 1.2283 | 1.2283 | 0.56872 | 1.1248 | 1.1248 | 1.1248 | 1.1248 | 1.1248 | 1.8672 | 2.4095 | 2.7649 | 2.9519 | 3.3259 | 3.7 | 0.92595 | 1.8275 | 2.193 | 2.193 | 2.193 | 2.193 | 1.2194 | 1.4184 | 1.4184 | 1.4184 | 1.4184 | 1.4184
2020-02-05 06:00 | Summer | 0.72884 | 1.0431 | 1.5052 | 1.5052 | 1.5052 | 1.5052 | 0.84593 | 1.673 | 1.673 | 1.673 | 1.673 | 1.673 | 2.0724 | 2.6743 | 3.0687 | 3.2763 | 3.6915 | 4.1066 | 1.0098 | 1.993 | 2.3916 | 2.3916 | 2.3916 | 2.3916 | 1.3086 | 1.5223 | 1.5223 | 1.5223 | 1.5223 | 1.5223
2020-02-05 07:00 | Summer | 1.8208 | 2.6058 | 3.7603 | 3.7603 | 3.7603 | 3.7603 | 0.8888 | 1.7578 | 1.7578 | 1.7578 | 1.7578 | 1.7578 | 2.6102 | 3.3684 | 3.8652 | 4.1266 | 4.6495 | 5.1724 | 1.3299 | 2.6247 | 3.1497 | 3.1497 | 3.1497 | 3.1497 | 1.9243 | 2.2385 | 2.2385 | 2.2385 | 2.2385 | 2.2385
2020-02-05 08:00 | Summer | 1.8862 | 2.6995 | 3.8954 | 3.8954 | 3.8954 | 3.8954 | 0.98025 | 1.9387 | 1.9387 | 1.9387 | 1.9387 | 1.9387 | 2.8769 | 3.7126 | 4.2601 | 4.5483 | 5.1246 | 5.701 | 1.2994 | 2.5646 | 3.0775 | 3.0775 | 3.0775 | 3.0775 | 2.3816 | 2.7704 | 2.7704 | 2.7704 | 2.7704 | 2.7704
2020-02-05 09:00 | Summer | 1.9243 | 2.754 | 3.9741 | 3.9741 | 3.9741 | 3.9741 | 1.1517 | 2.2778 | 2.2778 | 2.2778 | 2.2778 | 2.2778 | 3.1437 | 4.0568 | 4.6551 | 4.97 | 5.5998 | 6.2296 | 1.2651 | 2.4969 | 2.9963 | 2.9963 | 2.9963 | 2.9963 | 2.4387 | 2.8369 | 2.8369 | 2.8369 | 2.8369 | 2.8369
2020-02-05 10:00 | Summer | 2.0577 | 2.9449 | 4.2495 | 4.2495 | 4.2495 | 4.2495 | 1.1374 | 2.2496 | 2.2496 | 2.2496 | 2.2496 | 2.2496 | 3.2008 | 4.1306 | 4.7398 | 5.0604 | 5.7016 | 6.3428 | 1.2651 | 2.4969 | 2.9963 | 2.9963 | 2.9963 | 2.9963 | 2.6864 | 3.125 | 3.125 | 3.125 | 3.125 | 3.125
2020-02-05 11:00 | Summer | 1.9815 | 2.8358 | 4.0922 | 4.0922 | 4.0922 | 4.0922 | 1.0956 | 2.1669 | 2.1669 | 2.1669 | 2.1669 | 2.1669 | 3.277 | 4.2289 | 4.8526 | 5.1809 | 5.8373 | 6.4938 | 1.1889 | 2.3465 | 2.8158 | 2.8158 | 2.8158 | 2.8158 | 2.7436 | 3.1915 | 3.1915 | 3.1915 | 3.1915 | 3.1915
2020-02-05 12:00 | Summer | 2.0386 | 2.9176 | 4.2102 | 4.2102 | 4.2102 | 4.2102 | 1.2489 | 2.47 | 2.47 | 2.47 | 2.47 | 2.47 | 3.4676 | 4.4748 | 5.1347 | 5.4821 | 6.1767 | 6.8714 | 1.1965 | 2.3615 | 2.8338 | 2.8338 | 2.8338 | 2.8338 | 2.8198 | 3.2802 | 3.2802 | 3.2802 | 3.2802 | 3.2802
2020-02-05 13:00 | Summer | 1.9479 | 2.7877 | 4.0228 | 4.0228 | 4.0228 | 4.0228 | 1.2718 | 2.5152 | 2.5152 | 2.5152 | 2.5152 | 2.5152 | 3.7724 | 4.8682 | 5.5861 | 5.964 | 6.7197 | 7.4755 | 1.1774 | 2.3239 | 2.7887 | 2.7887 | 2.7887 | 2.7887 | 2.9341 | 3.4131 | 3.4131 | 3.4131 | 3.4131 | 3.4131
2020-02-05 14:00 | Summer | 2.0196 | 2.8903 | 4.1709 | 4.1709 | 4.1709 | 4.1709 | 1.2832 | 2.5378 | 2.5378 | 2.5378 | 2.5378 | 2.5378 | 3.8486 | 4.9666 | 5.699 | 6.0845 | 6.8555 | 7.6265 | 1.1774 | 2.3239 | 2.7887 | 2.7887 | 2.7887 | 2.7887 | 3.1056 | 3.6126 | 3.6126 | 3.6126 | 3.6126 | 3.6126
2020-02-05 15:00 | Summer | 2.0005 | 2.8631 | 4.1315 | 4.1315 | 4.1315 | 4.1315 | 1.3232 | 2.617 | 2.617 | 2.617 | 2.617 | 2.617 | 3.7534 | 4.8436 | 5.5579 | 5.9339 | 6.6858 | 7.4377 | 1.1508 | 2.2713 | 2.7255 | 2.7255 | 2.7255 | 2.7255 | 3.0675 | 3.5683 | 3.5683 | 3.5683 | 3.5683 | 3.5683
2020-02-05 16:00 | Summer | 1.9624 | 2.8085 | 4.0528 | 4.0528 | 4.0528 | 4.0528 | 1.3146 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 3.62 | 4.6715 | 5.3604 | 5.723 | 6.4482 | 7.1734 | 1.1622 | 2.2938 | 2.7526 | 2.7526 | 2.7526 | 2.7526 | 2.8908 | 3.3628 | 3.3628 | 3.3628 | 3.3628 | 3.3628
2020-02-05 17:00 | Summer | 1.7338 | 2.4813 | 3.5806 | 3.5806 | 3.5806 | 3.5806 | 1.1974 | 2.3683 | 2.3683 | 2.3683 | 2.3683 | 2.3683 | 3.6009 | 4.6469 | 5.3322 | 5.6929 | 6.4143 | 7.1357 | 1.1393 | 2.2487 | 2.6984 | 2.6984 | 2.6984 | 2.6984 | 2.7436 | 3.1915 | 3.1915 | 3.1915 | 3.1915 | 3.1915
2020-02-05 18:00 | Summer | 1.467 | 2.0996 | 3.0298 | 3.0298 | 3.0298 | 3.0298 | 0.9279 | 1.8352 | 1.8352 | 1.8352 | 1.8352 | 1.8352 | 3.3927 | 4.3782 | 5.0238 | 5.3637 | 6.0433 | 6.723 | 1.0974 | 2.166 | 2.5992 | 2.5992 | 2.5992 | 2.5992 | 2.1691 | 2.5232 | 2.5232 | 2.5232 | 2.5232 | 2.5232
2020-02-05 19:00 | Summer | 0.7621 | 1.0907 | 1.5739 | 1.5739 | 1.5739 | 1.5739 | 0.70304 | 1.3904 | 1.3904 | 1.3904 | 1.3904 | 1.3904 | 2.9535 | 3.8115 | 4.3736 | 4.6694 | 5.2611 | 5.8527 | 1.1089 | 2.1885 | 2.6262 | 2.6262 | 2.6262 | 2.6262 | 1.2956 | 1.5071 | 1.5071 | 1.5071 | 1.5071 | 1.5071
2020-02-05 20:00 | Summer | 0.7046 | 1.0084 | 1.4552 | 1.4552 | 1.4552 | 1.4552 | 0.57443 | 1.1361 | 1.1361 | 1.1361 | 1.1361 | 1.1361 | 2.6293 | 3.393 | 3.8934 | 4.1567 | 4.6835 | 5.2102 | 1.0517 | 2.0757 | 2.4909 | 2.4909 | 2.4909 | 2.4909 | 1.2818 | 1.4911 | 1.4911 | 1.4911 | 1.4911 | 1.4911
2020-02-05 21:00 | Summer | 0.64779 | 0.92709 | 1.3378 | 1.3378 | 1.3378 | 1.3378 | 0.56586 | 1.1191 | 1.1191 | 1.1191 | 1.1191 | 1.1191 | 2.6864 | 3.4668 | 3.978 | 4.2471 | 4.7853 | 5.3234 | 1.0365 | 2.0456 | 2.4548 | 2.4548 | 2.4548 | 2.4548 | 1.1622 | 1.352 | 1.352 | 1.352 | 1.352 | 1.352
2020-02-05 22:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.60873 | 1.2039 | 1.2039 | 1.2039 | 1.2039 | 1.2039 | 2.3468 | 3.0285 | 3.4752 | 3.7102 | 4.1804 | 4.6505 | 1.0593 | 2.0908 | 2.5089 | 2.5089 | 2.5089 | 2.5089 | 1.1241 | 1.3076 | 1.3076 | 1.3076 | 1.3076 | 1.3076
2020-02-05 23:00 | Summer | 0.59059 | 0.84523 | 1.2197 | 1.2197 | 1.2197 | 1.2197 | 0.56586 | 1.1191 | 1.1191 | 1.1191 | 1.1191 | 1.1191 | 2.3625 | 3.0488 | 3.4984 | 3.735 | 4.2083 | 4.6816 | 1.0174 | 2.008 | 2.4096 | 2.4096 | 2.4096 | 2.4096 | 1.0479 | 1.219 | 1.219 | 1.219 | 1.219 | 1.219
2020-02-06 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.52101 | 1.0304 | 1.0304 | 1.0304 | 1.0304 | 1.0304 | 2.0005 | 2.5816 | 2.9624 | 3.1627 | 3.5635 | 3.9643 | 0.82307 | 1.6245 | 1.9494 | 1.9494 | 1.9494 | 1.9494 | 1.0288 | 1.1968 | 1.1968 | 1.1968 | 1.1968 | 1.1968
2020-02-06 01:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.54585 | 1.0796 | 1.0796 | 1.0796 | 1.0796 | 1.0796 | 1.9243 | 2.4833 | 2.8495 | 3.0422 | 3.4277 | 3.8132 | 0.68589 | 1.3537 | 1.6245 | 1.6245 | 1.6245 | 1.6245 | 1.0098 | 1.1746 | 1.1746 | 1.1746 | 1.1746 | 1.1746
2020-02-06 02:00 | Summer | 0.57157 | 0.818 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.49155 | 0.97217 | 0.97217 | 0.97217 | 0.97217 | 0.97217 | 1.9053 | 2.4587 | 2.8213 | 3.0121 | 3.3938 | 3.7755 | 0.64397 | 1.271 | 1.5252 | 1.5252 | 1.5252 | 1.5252 | 0.99073 | 1.1525 | 1.1525 | 1.1525 | 1.1525 | 1.1525
2020-02-06 03:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.44297 | 0.87608 | 0.87608 | 0.87608 | 0.87608 | 0.87608 | 1.829 | 2.3603 | 2.7084 | 2.8916 | 3.2581 | 3.6245 | 0.64016 | 1.2635 | 1.5162 | 1.5162 | 1.5162 | 1.5162 | 0.99073 | 1.1525 | 1.1525 | 1.1525 | 1.1525 | 1.1525
2020-02-06 04:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.53728 | 1.0626 | 1.0626 | 1.0626 | 1.0626 | 1.0626 | 1.829 | 2.3603 | 2.7084 | 2.8916 | 3.2581 | 3.6245 | 0.67065 | 1.3236 | 1.5884 | 1.5884 | 1.5884 | 1.5884 | 1.1813 | 1.3741 | 1.3741 | 1.3741 | 1.3741 | 1.3741
2020-02-06 05:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.55443 | 1.0965 | 1.0965 | 1.0965 | 1.0965 | 1.0965 | 1.9434 | 2.5079 | 2.8777 | 3.0724 | 3.4617 | 3.851 | 1.1317 | 2.2337 | 2.6804 | 2.6804 | 2.6804 | 2.6804 | 1.3337 | 1.5514 | 1.5514 | 1.5514 | 1.5514 | 1.5514
2020-02-06 06:00 | Summer | 0.78018 | 1.1166 | 1.6112 | 1.6112 | 1.6112 | 1.6112 | 0.82018 | 1.6221 | 1.6221 | 1.6221 | 1.6221 | 1.6221 | 2.0956 | 2.7043 | 3.1031 | 3.313 | 3.7328 | 4.1526 | 1.0822 | 2.1359 | 2.5631 | 2.5631 | 2.5631 | 2.5631 | 1.5272 | 1.7765 | 1.7765 | 1.7765 | 1.7765 | 1.7765
2020-02-06 07:00 | Summer | 1.8862 | 2.6995 | 3.8954 | 3.8954 | 3.8954 | 3.8954 | 1.0231 | 2.0235 | 2.0235 | 2.0235 | 2.0235 | 2.0235 | 2.915 | 3.7618 | 4.3166 | 4.6086 | 5.1925 | 5.7765 | 1.2765 | 2.5194 | 3.0233 | 3.0233 | 3.0233 | 3.0233 | 2.0005 | 2.3271 | 2.3271 | 2.3271 | 2.3271 | 2.3271
2020-02-06 08:00 | Summer | 1.9053 | 2.7267 | 3.9348 | 3.9348 | 3.9348 | 3.9348 | 1.1917 | 2.357 | 2.357 | 2.357 | 2.357 | 2.357 | 3.0294 | 3.9093 | 4.4858 | 4.7893 | 5.3962 | 6.003 | 1.1889 | 2.3465 | 2.8158 | 2.8158 | 2.8158 | 2.8158 | 2.4197 | 2.8147 | 2.8147 | 2.8147 | 2.8147 | 2.8147
2020-02-06 09:00 | Summer | 1.7909 | 2.5631 | 3.6987 | 3.6987 | 3.6987 | 3.6987 | 1.2689 | 2.5096 | 2.5096 | 2.5096 | 2.5096 | 2.5096 | 3.1056 | 4.0077 | 4.5987 | 4.9098 | 5.5319 | 6.154 | 1.1698 | 2.3089 | 2.7706 | 2.7706 | 2.7706 | 2.7706 | 2.553 | 2.9699 | 2.9699 | 2.9699 | 2.9699 | 2.9699
2020-02-06 10:00 | Summer | 1.8672 | 2.6722 | 3.8561 | 3.8561 | 3.8561 | 3.8561 | 1.4032 | 2.7752 | 2.7752 | 2.7752 | 2.7752 | 2.7752 | 3.2389 | 4.1798 | 4.7962 | 5.1206 | 5.7695 | 6.4183 | 1.166 | 2.3013 | 2.7616 | 2.7616 | 2.7616 | 2.7616 | 2.7055 | 3.1472 | 3.1472 | 3.1472 | 3.1472 | 3.1472
2020-02-06 11:00 | Summer | 1.8445 | 2.6397 | 3.8092 | 3.8092 | 3.8092 | 3.8092 | 1.3832 | 2.7356 | 2.7356 | 2.7356 | 2.7356 | 2.7356 | 3.5057 | 4.524 | 5.1912 | 5.5423 | 6.2446 | 6.9469 | 1.1393 | 2.2487 | 2.6984 | 2.6984 | 2.6984 | 2.6984 | 2.8378 | 3.3012 | 3.3012 | 3.3012 | 3.3012 | 3.3012
2020-02-06 12:00 | Summer | 1.8862 | 2.6995 | 3.8954 | 3.8954 | 3.8954 | 3.8954 | 1.4204 | 2.8091 | 2.8091 | 2.8091 | 2.8091 | 2.8091 | 3.5628 | 4.5978 | 5.2758 | 5.6327 | 6.3464 | 7.0602 | 1.1508 | 2.2713 | 2.7255 | 2.7255 | 2.7255 | 2.7255 | 2.8579 | 3.3245 | 3.3245 | 3.3245 | 3.3245 | 3.3245
2020-02-06 13:00 | Summer | 1.9053 | 2.7267 | 3.9348 | 3.9348 | 3.9348 | 3.9348 | 1.4747 | 2.9165 | 2.9165 | 2.9165 | 2.9165 | 2.9165 | 3.5247 | 4.5486 | 5.2194 | 5.5724 | 6.2785 | 6.9846 | 1.166 | 2.3013 | 2.7616 | 2.7616 | 2.7616 | 2.7616 | 2.896 | 3.3688 | 3.3688 | 3.3688 | 3.3688 | 3.3688
2020-02-06 14:00 | Summer | 1.8672 | 2.6722 | 3.8561 | 3.8561 | 3.8561 | 3.8561 | 1.4461 | 2.86 | 2.86 | 2.86 | 2.86 | 2.86 | 3.5057 | 4.524 | 5.1912 | 5.5423 | 6.2446 | 6.9469 | 1.1508 | 2.2713 | 2.7255 | 2.7255 | 2.7255 | 2.7255 | 2.8769 | 3.3466 | 3.3466 | 3.3466 | 3.3466 | 3.3466
2020-02-06 15:00 | Summer | 1.8862 | 2.6995 | 3.8954 | 3.8954 | 3.8954 | 3.8954 | 1.5384 | 3.0425 | 3.0425 | 3.0425 | 3.0425 | 3.0425 | 3.5628 | 4.5978 | 5.2758 | 5.6327 | 6.3464 | 7.0602 | 1.1584 | 2.2863 | 2.7436 | 2.7436 | 2.7436 | 2.7436 | 2.8579 | 3.3245 | 3.3245 | 3.3245 | 3.3245 | 3.3245
2020-02-06 16:00 | Summer | 1.8481 | 2.6449 | 3.8167 | 3.8167 | 3.8167 | 3.8167 | 1.5404 | 3.0465 | 3.0465 | 3.0465 | 3.0465 | 3.0465 | 3.5628 | 4.5978 | 5.2758 | 5.6327 | 6.3464 | 7.0602 | 1.1508 | 2.2713 | 2.7255 | 2.7255 | 2.7255 | 2.7255 | 2.7626 | 3.2137 | 3.2137 | 3.2137 | 3.2137 | 3.2137
2020-02-06 17:00 | Summer | 1.6385 | 2.345 | 3.3839 | 3.3839 | 3.3839 | 3.3839 | 1.267 | 2.5059 | 2.5059 | 2.5059 | 2.5059 | 2.5059 | 3.4485 | 4.4502 | 5.1065 | 5.4519 | 6.1428 | 6.8336 | 1.1393 | 2.2487 | 2.6984 | 2.6984 | 2.6984 | 2.6984 | 2.5559 | 2.9732 | 2.9732 | 2.9732 | 2.9732 | 2.9732
2020-02-06 18:00 | Summer | 1.1645 | 1.6666 | 2.405 | 2.405 | 2.405 | 2.405 | 1.0313 | 2.0397 | 2.0397 | 2.0397 | 2.0397 | 2.0397 | 3.0865 | 3.9831 | 4.5705 | 4.8796 | 5.498 | 6.1163 | 1.1165 | 2.2036 | 2.6443 | 2.6443 | 2.6443 | 2.6443 | 1.9101 | 2.222 | 2.222 | 2.222 | 2.222 | 2.222
2020-02-06 19:00 | Summer | 0.75943 | 1.0869 | 1.5684 | 1.5684 | 1.5684 | 1.5684 | 0.86308 | 1.707 | 1.707 | 1.707 | 1.707 | 1.707 | 2.9341 | 3.7864 | 4.3448 | 4.6387 | 5.2265 | 5.8142 | 1.0555 | 2.0832 | 2.4999 | 2.4999 | 2.4999 | 2.4999 | 1.2575 | 1.4628 | 1.4628 | 1.4628 | 1.4628 | 1.4628
2020-02-06 20:00 | Summer | 0.7139 | 1.0217 | 1.4744 | 1.4744 | 1.4744 | 1.4744 | 0.76019 | 1.5035 | 1.5035 | 1.5035 | 1.5035 | 1.5035 | 2.6293 | 3.393 | 3.8934 | 4.1567 | 4.6835 | 5.2102 | 0.99835 | 1.9704 | 2.3645 | 2.3645 | 2.3645 | 2.3645 | 1.2003 | 1.3963 | 1.3963 | 1.3963 | 1.3963 | 1.3963
2020-02-06 21:00 | Summer | 0.64779 | 0.92709 | 1.3378 | 1.3378 | 1.3378 | 1.3378 | 0.66832 | 1.3218 | 1.3218 | 1.3218 | 1.3218 | 1.3218 | 2.4959 | 3.2209 | 3.6959 | 3.9459 | 4.4459 | 4.9459 | 1.086 | 2.1434 | 2.5721 | 2.5721 | 2.5721 | 2.5721 | 1.086 | 1.2633 | 1.2633 | 1.2633 | 1.2633 | 1.2633
2020-02-06 22:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.6916 | 1.3678 | 1.3678 | 1.3678 | 1.3678 | 1.3678 | 2.3435 | 3.0242 | 3.4702 | 3.7049 | 4.1744 | 4.6438 | 0.98311 | 1.9403 | 2.3284 | 2.3284 | 2.3284 | 2.3284 | 1.0479 | 1.219 | 1.219 | 1.219 | 1.219 | 1.219
2020-02-06 23:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.62016 | 1.2265 | 1.2265 | 1.2265 | 1.2265 | 1.2265 | 2.3435 | 3.0242 | 3.4702 | 3.7049 | 4.1744 | 4.6438 | 0.94882 | 1.8727 | 2.2472 | 2.2472 | 2.2472 | 2.2472 | 1.0098 | 1.1746 | 1.1746 | 1.1746 | 1.1746 | 1.1746
2020-02-07 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.52585 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.9974 | 2.5775 | 2.9577 | 3.1577 | 3.5579 | 3.958 | 0.71256 | 1.4064 | 1.6877 | 1.6877 | 1.6877 | 1.6877 | 0.99073 | 1.1525 | 1.1525 | 1.1525 | 1.1525 | 1.1525
2020-02-07 01:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.52299 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.8862 | 2.4341 | 2.7931 | 2.982 | 3.3599 | 3.7377 | 0.68208 | 1.3462 | 1.6155 | 1.6155 | 1.6155 | 1.6155 | 0.97168 | 1.1303 | 1.1303 | 1.1303 | 1.1303 | 1.1303
2020-02-07 02:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.5287 | 1.0456 | 1.0456 | 1.0456 | 1.0456 | 1.0456 | 1.8862 | 2.4341 | 2.7931 | 2.982 | 3.3599 | 3.7377 | 0.67446 | 1.3312 | 1.5974 | 1.5974 | 1.5974 | 1.5974 | 0.95263 | 1.1082 | 1.1082 | 1.1082 | 1.1082 | 1.1082
2020-02-07 03:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.52013 | 1.0287 | 1.0287 | 1.0287 | 1.0287 | 1.0287 | 1.8409 | 2.3756 | 2.7259 | 2.9103 | 3.2791 | 3.6479 | 0.64682 | 1.2766 | 1.5319 | 1.5319 | 1.5319 | 1.5319 | 0.95263 | 1.1082 | 1.1082 | 1.1082 | 1.1082 | 1.1082
2020-02-07 04:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.58015 | 1.1474 | 1.1474 | 1.1474 | 1.1474 | 1.1474 | 1.9624 | 2.5325 | 2.9059 | 3.1025 | 3.4956 | 3.8887 | 0.69732 | 1.3763 | 1.6516 | 1.6516 | 1.6516 | 1.6516 | 1.132 | 1.3168 | 1.3168 | 1.3168 | 1.3168 | 1.3168
2020-02-07 05:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.60873 | 1.2039 | 1.2039 | 1.2039 | 1.2039 | 1.2039 | 1.9434 | 2.5079 | 2.8777 | 3.0724 | 3.4617 | 3.851 | 0.89692 | 1.7702 | 2.1243 | 2.1243 | 2.1243 | 2.1243 | 1.2575 | 1.4628 | 1.4628 | 1.4628 | 1.4628 | 1.4628
2020-02-07 06:00 | Summer | 0.78115 | 1.118 | 1.6133 | 1.6133 | 1.6133 | 1.6133 | 0.8266 | 1.6348 | 1.6348 | 1.6348 | 1.6348 | 1.6348 | 2.2182 | 2.8626 | 3.2847 | 3.5069 | 3.9513 | 4.3957 | 1.0136 | 2.0005 | 2.4006 | 2.4006 | 2.4006 | 2.4006 | 1.4759 | 1.7168 | 1.7168 | 1.7168 | 1.7168 | 1.7168
2020-02-07 07:00 | Summer | 1.7528 | 2.5086 | 3.62 | 3.62 | 3.62 | 3.62 | 0.9088 | 1.7974 | 1.7974 | 1.7974 | 1.7974 | 1.7974 | 2.896 | 3.7372 | 4.2884 | 4.5784 | 5.1586 | 5.7387 | 1.2498 | 2.4668 | 2.9602 | 2.9602 | 2.9602 | 2.9602 | 1.8361 | 2.1358 | 2.1358 | 2.1358 | 2.1358 | 2.1358
2020-02-07 08:00 | Summer | 1.8862 | 2.6995 | 3.8954 | 3.8954 | 3.8954 | 3.8954 | 1.0288 | 2.0348 | 2.0348 | 2.0348 | 2.0348 | 2.0348 | 3.0484 | 3.9339 | 4.5141 | 4.8194 | 5.4301 | 6.0408 | 1.1965 | 2.3615 | 2.8338 | 2.8338 | 2.8338 | 2.8338 | 2.409 | 2.8023 | 2.8023 | 2.8023 | 2.8023 | 2.8023
2020-02-07 09:00 | Summer | 1.7909 | 2.5631 | 3.6987 | 3.6987 | 3.6987 | 3.6987 | 1.1031 | 2.1817 | 2.1817 | 2.1817 | 2.1817 | 2.1817 | 3.2199 | 4.1552 | 4.768 | 5.0905 | 5.7355 | 6.3806 | 1.147 | 2.2637 | 2.7165 | 2.7165 | 2.7165 | 2.7165 | 2.5721 | 2.992 | 2.992 | 2.992 | 2.992 | 2.992
2020-02-07 10:00 | Summer | 1.7719 | 2.5359 | 3.6593 | 3.6593 | 3.6593 | 3.6593 | 1.2146 | 2.4022 | 2.4022 | 2.4022 | 2.4022 | 2.4022 | 3.3723 | 4.3519 | 4.9937 | 5.3315 | 6.007 | 6.6826 | 1.1698 | 2.3089 | 2.7706 | 2.7706 | 2.7706 | 2.7706 | 2.7055 | 3.1472 | 3.1472 | 3.1472 | 3.1472 | 3.1472
2020-02-07 11:00 | Summer | 1.7528 | 2.5086 | 3.62 | 3.62 | 3.62 | 3.62 | 1.1717 | 2.3174 | 2.3174 | 2.3174 | 2.3174 | 2.3174 | 3.4866 | 4.4994 | 5.163 | 5.5122 | 6.2107 | 6.9091 | 1.166 | 2.3013 | 2.7616 | 2.7616 | 2.7616 | 2.7616 | 2.7436 | 3.1915 | 3.1915 | 3.1915 | 3.1915 | 3.1915
2020-02-07 12:00 | Summer | 1.7909 | 2.5631 | 3.6987 | 3.6987 | 3.6987 | 3.6987 | 1.3003 | 2.5717 | 2.5717 | 2.5717 | 2.5717 | 2.5717 | 3.4676 | 4.4748 | 5.1347 | 5.4821 | 6.1767 | 6.8714 | 1.166 | 2.3013 | 2.7616 | 2.7616 | 2.7616 | 2.7616 | 2.7436 | 3.1915 | 3.1915 | 3.1915 | 3.1915 | 3.1915
2020-02-07 13:00 | Summer | 1.7528 | 2.5086 | 3.62 | 3.62 | 3.62 | 3.62 | 1.3089 | 2.5887 | 2.5887 | 2.5887 | 2.5887 | 2.5887 | 3.3924 | 4.3779 | 5.0235 | 5.3633 | 6.0429 | 6.7225 | 1.166 | 2.3013 | 2.7616 | 2.7616 | 2.7616 | 2.7616 | 2.7626 | 3.2137 | 3.2137 | 3.2137 | 3.2137 | 3.2137
2020-02-07 14:00 | Summer | 1.7528 | 2.5086 | 3.62 | 3.62 | 3.62 | 3.62 | 1.2232 | 2.4191 | 2.4191 | 2.4191 | 2.4191 | 2.4191 | 3.3533 | 4.3273 | 4.9655 | 5.3013 | 5.9731 | 6.6449 | 1.166 | 2.3013 | 2.7616 | 2.7616 | 2.7616 | 2.7616 | 2.6293 | 3.0585 | 3.0585 | 3.0585 | 3.0585 | 3.0585
2020-02-07 15:00 | Summer | 1.7719 | 2.5359 | 3.6593 | 3.6593 | 3.6593 | 3.6593 | 1.2432 | 2.4587 | 2.4587 | 2.4587 | 2.4587 | 2.4587 | 3.4866 | 4.4994 | 5.163 | 5.5122 | 6.2107 | 6.9091 | 1.1355 | 2.2412 | 2.6894 | 2.6894 | 2.6894 | 2.6894 | 2.6864 | 3.125 | 3.125 | 3.125 | 3.125 | 3.125
2020-02-07 16:00 | Summer | 1.6291 | 2.3315 | 3.3645 | 3.3645 | 3.3645 | 3.3645 | 1.3146 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 3.4866 | 4.4994 | 5.163 | 5.5122 | 6.2107 | 6.9091 | 1.1241 | 2.2186 | 2.6623 | 2.6623 | 2.6623 | 2.6623 | 2.6674 | 3.1028 | 3.1028 | 3.1028 | 3.1028 | 3.1028
2020-02-07 17:00 | Summer | 1.5433 | 2.2086 | 3.1872 | 3.1872 | 3.1872 | 3.1872 | 1.2546 | 2.4813 | 2.4813 | 2.4813 | 2.4813 | 2.4813 | 3.2961 | 4.2535 | 4.8808 | 5.211 | 5.8713 | 6.5316 | 1.1432 | 2.2562 | 2.7075 | 2.7075 | 2.7075 | 2.7075 | 2.6041 | 3.0293 | 3.0293 | 3.0293 | 3.0293 | 3.0293
2020-02-07 18:00 | Summer | 0.97263 | 1.392 | 2.0087 | 2.0087 | 2.0087 | 2.0087 | 0.82661 | 1.6348 | 1.6348 | 1.6348 | 1.6348 | 1.6348 | 3.1013 | 4.0021 | 4.5924 | 4.903 | 5.5243 | 6.1456 | 1.1317 | 2.2337 | 2.6804 | 2.6804 | 2.6804 | 2.6804 | 2.0392 | 2.3722 | 2.3722 | 2.3722 | 2.3722 | 2.3722
2020-02-07 19:00 | Summer | 0.70494 | 1.0089 | 1.4559 | 1.4559 | 1.4559 | 1.4559 | 0.76305 | 1.5091 | 1.5091 | 1.5091 | 1.5091 | 1.5091 | 2.5883 | 3.3401 | 3.8327 | 4.092 | 4.6105 | 5.129 | 1.0136 | 2.0005 | 2.4006 | 2.4006 | 2.4006 | 2.4006 | 1.2003 | 1.3963 | 1.3963 | 1.3963 | 1.3963 | 1.3963
2020-02-07 20:00 | Summer | 0.68589 | 0.98162 | 1.4165 | 1.4165 | 1.4165 | 1.4165 | 0.73733 | 1.4583 | 1.4583 | 1.4583 | 1.4583 | 1.4583 | 2.534 | 3.2701 | 3.7523 | 4.0061 | 4.5138 | 5.0214 | 1.0708 | 2.1133 | 2.536 | 2.536 | 2.536 | 2.536 | 1.1622 | 1.352 | 1.352 | 1.352 | 1.352 | 1.352
2020-02-07 21:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.63159 | 1.2491 | 1.2491 | 1.2491 | 1.2491 | 1.2491 | 2.3625 | 3.0488 | 3.4984 | 3.735 | 4.2083 | 4.6816 | 1.006 | 1.9855 | 2.3826 | 2.3826 | 2.3826 | 2.3826 | 1.0288 | 1.1968 | 1.1968 | 1.1968 | 1.1968 | 1.1968
2020-02-07 22:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.63159 | 1.2491 | 1.2491 | 1.2491 | 1.2491 | 1.2491 | 2.3244 | 2.9996 | 3.442 | 3.6748 | 4.1404 | 4.6061 | 1.0365 | 2.0456 | 2.4548 | 2.4548 | 2.4548 | 2.4548 | 0.95263 | 1.1082 | 1.1082 | 1.1082 | 1.1082 | 1.1082
2020-02-07 23:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.58015 | 1.1474 | 1.1474 | 1.1474 | 1.1474 | 1.1474 | 2.191 | 2.8275 | 3.2445 | 3.4639 | 3.9029 | 4.3418 | 0.91071 | 1.7975 | 2.1569 | 2.1569 | 2.1569 | 2.1569 | 0.95263 | 1.1082 | 1.1082 | 1.1082 | 1.1082 | 1.1082
2020-02-08 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.50584 | 1.0004 | 1.0004 | 1.0004 | 1.0004 | 1.0004 | 1.9339 | 2.4957 | 2.8638 | 3.0575 | 3.4449 | 3.8323 | 0.9069 | 1.7899 | 2.1479 | 2.1479 | 2.1479 | 2.1479 | 0.97168 | 1.1303 | 1.1303 | 1.1303 | 1.1303 | 1.1303
2020-02-08 01:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.42582 | 0.84217 | 0.84217 | 0.84217 | 0.84217 | 0.84217 | 1.8292 | 2.3605 | 2.7086 | 2.8918 | 3.2583 | 3.6247 | 0.80021 | 1.5794 | 1.8952 | 1.8952 | 1.8952 | 1.8952 | 0.93358 | 1.086 | 1.086 | 1.086 | 1.086 | 1.086
2020-02-08 02:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.50584 | 1.0004 | 1.0004 | 1.0004 | 1.0004 | 1.0004 | 1.829 | 2.3603 | 2.7084 | 2.8916 | 3.2581 | 3.6245 | 0.75067 | 1.4816 | 1.7779 | 1.7779 | 1.7779 | 1.7779 | 0.93358 | 1.086 | 1.086 | 1.086 | 1.086 | 1.086
2020-02-08 03:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.44297 | 0.87608 | 0.87608 | 0.87608 | 0.87608 | 0.87608 | 1.81 | 2.3358 | 2.6802 | 2.8615 | 3.2241 | 3.5867 | 0.84593 | 1.6696 | 2.0035 | 2.0035 | 2.0035 | 2.0035 | 0.91452 | 1.0638 | 1.0638 | 1.0638 | 1.0638 | 1.0638
2020-02-08 04:00 | Summer | 0.59143 | 0.84643 | 1.2214 | 1.2214 | 1.2214 | 1.2214 | 0.40268 | 0.79641 | 0.79641 | 0.79641 | 0.79641 | 0.79641 | 1.8862 | 2.4341 | 2.7931 | 2.982 | 3.3599 | 3.7377 | 0.84974 | 1.6771 | 2.0125 | 2.0125 | 2.0125 | 2.0125 | 0.95263 | 1.1082 | 1.1082 | 1.1082 | 1.1082 | 1.1082
2020-02-08 05:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.49727 | 0.98347 | 0.98347 | 0.98347 | 0.98347 | 0.98347 | 1.9053 | 2.4587 | 2.8213 | 3.0121 | 3.3938 | 3.7755 | 0.84974 | 1.6771 | 2.0125 | 2.0125 | 2.0125 | 2.0125 | 0.97168 | 1.1303 | 1.1303 | 1.1303 | 1.1303 | 1.1303
2020-02-08 06:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.51156 | 1.0117 | 1.0117 | 1.0117 | 1.0117 | 1.0117 | 1.9434 | 2.5079 | 2.8777 | 3.0724 | 3.4617 | 3.851 | 0.95263 | 1.8802 | 2.2562 | 2.2562 | 2.2562 | 2.2562 | 1.0098 | 1.1746 | 1.1746 | 1.1746 | 1.1746 | 1.1746
2020-02-08 07:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.58586 | 1.1587 | 1.1587 | 1.1587 | 1.1587 | 1.1587 | 2.1529 | 2.7783 | 3.1881 | 3.4037 | 3.835 | 4.2663 | 0.93357 | 1.8426 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 1.1432 | 1.3298 | 1.3298 | 1.3298 | 1.3298 | 1.3298
2020-02-08 08:00 | Summer | 0.64779 | 0.92709 | 1.3378 | 1.3378 | 1.3378 | 1.3378 | 0.59729 | 1.1813 | 1.1813 | 1.1813 | 1.1813 | 1.1813 | 2.3816 | 3.0734 | 3.5266 | 3.7652 | 4.2423 | 4.7194 | 1.0708 | 2.1133 | 2.536 | 2.536 | 2.536 | 2.536 | 1.1813 | 1.3741 | 1.3741 | 1.3741 | 1.3741 | 1.3741
2020-02-08 09:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.6173 | 1.2209 | 1.2209 | 1.2209 | 1.2209 | 1.2209 | 2.4959 | 3.2209 | 3.6959 | 3.9459 | 4.4459 | 4.9459 | 1.0669 | 2.1058 | 2.527 | 2.527 | 2.527 | 2.527 | 1.2194 | 1.4184 | 1.4184 | 1.4184 | 1.4184 | 1.4184
2020-02-08 10:00 | Summer | 0.64779 | 0.92709 | 1.3378 | 1.3378 | 1.3378 | 1.3378 | 0.60301 | 1.1926 | 1.1926 | 1.1926 | 1.1926 | 1.1926 | 2.534 | 3.2701 | 3.7523 | 4.0061 | 4.5138 | 5.0214 | 1.0365 | 2.0456 | 2.4548 | 2.4548 | 2.4548 | 2.4548 | 1.2956 | 1.5071 | 1.5071 | 1.5071 | 1.5071 | 1.5071
2020-02-08 11:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.70018 | 1.3848 | 1.3848 | 1.3848 | 1.3848 | 1.3848 | 2.6293 | 3.393 | 3.8934 | 4.1567 | 4.6835 | 5.2102 | 1.0669 | 2.1058 | 2.527 | 2.527 | 2.527 | 2.527 | 1.2765 | 1.4849 | 1.4849 | 1.4849 | 1.4849 | 1.4849
2020-02-08 12:00 | Summer | 0.7621 | 1.0907 | 1.5739 | 1.5739 | 1.5739 | 1.5739 | 0.66303 | 1.3113 | 1.3113 | 1.3113 | 1.3113 | 1.3113 | 2.8388 | 3.6634 | 4.2037 | 4.4881 | 5.0568 | 5.6255 | 1.0746 | 2.1208 | 2.545 | 2.545 | 2.545 | 2.545 | 1.3146 | 1.5293 | 1.5293 | 1.5293 | 1.5293 | 1.5293
2020-02-08 13:00 | Summer | 0.70494 | 1.0089 | 1.4559 | 1.4559 | 1.4559 | 1.4559 | 0.76877 | 1.5204 | 1.5204 | 1.5204 | 1.5204 | 1.5204 | 2.7569 | 3.5577 | 4.0824 | 4.3586 | 4.9108 | 5.4631 | 1.0441 | 2.0607 | 2.4728 | 2.4728 | 2.4728 | 2.4728 | 1.2575 | 1.4628 | 1.4628 | 1.4628 | 1.4628 | 1.4628
2020-02-08 14:00 | Summer | 0.68589 | 0.98162 | 1.4165 | 1.4165 | 1.4165 | 1.4165 | 0.74305 | 1.4696 | 1.4696 | 1.4696 | 1.4696 | 1.4696 | 2.7245 | 3.5159 | 4.0344 | 4.3073 | 4.8531 | 5.3989 | 1.0136 | 2.0005 | 2.4006 | 2.4006 | 2.4006 | 2.4006 | 1.1904 | 1.3848 | 1.3848 | 1.3848 | 1.3848 | 1.3848
2020-02-08 15:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.73733 | 1.4583 | 1.4583 | 1.4583 | 1.4583 | 1.4583 | 2.7245 | 3.5159 | 4.0344 | 4.3073 | 4.8531 | 5.3989 | 1.0441 | 2.0607 | 2.4728 | 2.4728 | 2.4728 | 2.4728 | 1.1813 | 1.3741 | 1.3741 | 1.3741 | 1.3741 | 1.3741
2020-02-08 16:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.80592 | 1.5939 | 1.5939 | 1.5939 | 1.5939 | 1.5939 | 2.7245 | 3.5159 | 4.0344 | 4.3073 | 4.8531 | 5.3989 | 1.0174 | 2.008 | 2.4096 | 2.4096 | 2.4096 | 2.4096 | 1.0669 | 1.2411 | 1.2411 | 1.2411 | 1.2411 | 1.2411
2020-02-08 17:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.82878 | 1.6391 | 1.6391 | 1.6391 | 1.6391 | 1.6391 | 2.7817 | 3.5897 | 4.1191 | 4.3977 | 4.955 | 5.5122 | 1.0441 | 2.0607 | 2.4728 | 2.4728 | 2.4728 | 2.4728 | 1.0669 | 1.2411 | 1.2411 | 1.2411 | 1.2411 | 1.2411
2020-02-08 18:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.65731 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 2.5149 | 3.2455 | 3.7241 | 3.976 | 4.4798 | 4.9836 | 1.0746 | 2.1208 | 2.545 | 2.545 | 2.545 | 2.545 | 1.0098 | 1.1746 | 1.1746 | 1.1746 | 1.1746 | 1.1746
2020-02-08 19:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.74305 | 1.4696 | 1.4696 | 1.4696 | 1.4696 | 1.4696 | 2.4578 | 3.1717 | 3.6395 | 3.8856 | 4.378 | 4.8704 | 1.0669 | 2.1058 | 2.527 | 2.527 | 2.527 | 2.527 | 1.0098 | 1.1746 | 1.1746 | 1.1746 | 1.1746 | 1.1746
2020-02-08 20:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.71733 | 1.4187 | 1.4187 | 1.4187 | 1.4187 | 1.4187 | 2.5721 | 3.3192 | 3.8087 | 4.0664 | 4.5816 | 5.0969 | 1.0669 | 2.1058 | 2.527 | 2.527 | 2.527 | 2.527 | 1.0098 | 1.1746 | 1.1746 | 1.1746 | 1.1746 | 1.1746
2020-02-08 21:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.63159 | 1.2491 | 1.2491 | 1.2491 | 1.2491 | 1.2491 | 2.4443 | 3.1543 | 3.6195 | 3.8643 | 4.354 | 4.8436 | 1.0403 | 2.0532 | 2.4638 | 2.4638 | 2.4638 | 2.4638 | 1.0098 | 1.1746 | 1.1746 | 1.1746 | 1.1746 | 1.1746
2020-02-08 22:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.61444 | 1.2152 | 1.2152 | 1.2152 | 1.2152 | 1.2152 | 2.3437 | 3.0245 | 3.4706 | 3.7053 | 4.1749 | 4.6444 | 1.025 | 2.0231 | 2.4277 | 2.4277 | 2.4277 | 2.4277 | 0.97168 | 1.1303 | 1.1303 | 1.1303 | 1.1303 | 1.1303
2020-02-08 23:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.53442 | 1.057 | 1.057 | 1.057 | 1.057 | 1.057 | 2.2676 | 2.9263 | 3.3579 | 3.585 | 4.0393 | 4.4936 | 0.97549 | 1.9253 | 2.3104 | 2.3104 | 2.3104 | 2.3104 | 0.95263 | 1.1082 | 1.1082 | 1.1082 | 1.1082 | 1.1082
2020-02-09 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.43439 | 0.85912 | 0.85912 | 0.85912 | 0.85912 | 0.85912 | 1.9434 | 2.5079 | 2.8777 | 3.0724 | 3.4617 | 3.851 | 0.88785 | 1.7523 | 2.1028 | 2.1028 | 2.1028 | 2.1028 | 0.91452 | 1.0638 | 1.0638 | 1.0638 | 1.0638 | 1.0638
2020-02-09 01:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.39728 | 0.78571 | 0.78571 | 0.78571 | 0.78571 | 0.78571 | 1.8862 | 2.4341 | 2.7931 | 2.982 | 3.3599 | 3.7377 | 0.69351 | 1.3688 | 1.6425 | 1.6425 | 1.6425 | 1.6425 | 0.91452 | 1.0638 | 1.0638 | 1.0638 | 1.0638 | 1.0638
2020-02-09 02:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.42582 | 0.84217 | 0.84217 | 0.84217 | 0.84217 | 0.84217 | 1.829 | 2.3603 | 2.7084 | 2.8916 | 3.2581 | 3.6245 | 0.67065 | 1.3236 | 1.5884 | 1.5884 | 1.5884 | 1.5884 | 0.91452 | 1.0638 | 1.0638 | 1.0638 | 1.0638 | 1.0638
2020-02-09 03:00 | Summer | 0.55332 | 0.79189 | 1.1427 | 1.1427 | 1.1427 | 1.1427 | 0.41149 | 0.81381 | 0.81381 | 0.81381 | 0.81381 | 0.81381 | 1.829 | 2.3603 | 2.7084 | 2.8916 | 3.2581 | 3.6245 | 0.68589 | 1.3537 | 1.6245 | 1.6245 | 1.6245 | 1.6245 | 0.89547 | 1.0417 | 1.0417 | 1.0417 | 1.0417 | 1.0417
2020-02-09 04:00 | Summer | 0.53755 | 0.76932 | 1.1102 | 1.1102 | 1.1102 | 1.1102 | 0.41153 | 0.81391 | 0.81391 | 0.81391 | 0.81391 | 0.81391 | 1.829 | 2.3603 | 2.7084 | 2.8916 | 3.2581 | 3.6245 | 0.69732 | 1.3763 | 1.6516 | 1.6516 | 1.6516 | 1.6516 | 0.87642 | 1.0195 | 1.0195 | 1.0195 | 1.0195 | 1.0195
2020-02-09 05:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.46583 | 0.9213 | 0.9213 | 0.9213 | 0.9213 | 0.9213 | 1.9243 | 2.4833 | 2.8495 | 3.0422 | 3.4277 | 3.8132 | 1.0098 | 1.993 | 2.3916 | 2.3916 | 2.3916 | 2.3916 | 0.85737 | 0.99734 | 0.99734 | 0.99734 | 0.99734 | 0.99734
2020-02-09 06:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.47726 | 0.94391 | 0.94391 | 0.94391 | 0.94391 | 0.94391 | 1.9053 | 2.4587 | 2.8213 | 3.0121 | 3.3938 | 3.7755 | 0.96025 | 1.8952 | 2.2743 | 2.2743 | 2.2743 | 2.2743 | 0.91452 | 1.0638 | 1.0638 | 1.0638 | 1.0638 | 1.0638
2020-02-09 07:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.48584 | 0.96086 | 0.96086 | 0.96086 | 0.96086 | 0.96086 | 2.1339 | 2.7537 | 3.1598 | 3.3736 | 3.8011 | 4.2285 | 0.96025 | 1.8952 | 2.2743 | 2.2743 | 2.2743 | 2.2743 | 0.91711 | 1.0668 | 1.0668 | 1.0668 | 1.0668 | 1.0668
2020-02-09 08:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.53156 | 1.0513 | 1.0513 | 1.0513 | 1.0513 | 1.0513 | 2.3244 | 2.9996 | 3.442 | 3.6748 | 4.1404 | 4.6061 | 1.0669 | 2.1058 | 2.527 | 2.527 | 2.527 | 2.527 | 0.95263 | 1.1082 | 1.1082 | 1.1082 | 1.1082 | 1.1082
2020-02-09 09:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.51156 | 1.0117 | 1.0117 | 1.0117 | 1.0117 | 1.0117 | 2.3625 | 3.0488 | 3.4984 | 3.735 | 4.2083 | 4.6816 | 1.0669 | 2.1058 | 2.527 | 2.527 | 2.527 | 2.527 | 0.95263 | 1.1082 | 1.1082 | 1.1082 | 1.1082 | 1.1082
2020-02-09 10:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.54299 | 1.0739 | 1.0739 | 1.0739 | 1.0739 | 1.0739 | 2.4197 | 3.1225 | 3.583 | 3.8254 | 4.3101 | 4.7949 | 1.0479 | 2.0682 | 2.4818 | 2.4818 | 2.4818 | 2.4818 | 0.95263 | 1.1082 | 1.1082 | 1.1082 | 1.1082 | 1.1082
2020-02-09 11:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.50584 | 1.0004 | 1.0004 | 1.0004 | 1.0004 | 1.0004 | 2.4333 | 3.1401 | 3.6032 | 3.847 | 4.3344 | 4.8219 | 1.0441 | 2.0607 | 2.4728 | 2.4728 | 2.4728 | 2.4728 | 0.95263 | 1.1082 | 1.1082 | 1.1082 | 1.1082 | 1.1082
2020-02-09 12:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.53728 | 1.0626 | 1.0626 | 1.0626 | 1.0626 | 1.0626 | 2.4578 | 3.1717 | 3.6395 | 3.8856 | 4.378 | 4.8704 | 1.0212 | 2.0156 | 2.4187 | 2.4187 | 2.4187 | 2.4187 | 0.95263 | 1.1082 | 1.1082 | 1.1082 | 1.1082 | 1.1082
2020-02-09 13:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.53442 | 1.057 | 1.057 | 1.057 | 1.057 | 1.057 | 2.4197 | 3.1225 | 3.583 | 3.8254 | 4.3101 | 4.7949 | 0.9793 | 1.9328 | 2.3194 | 2.3194 | 2.3194 | 2.3194 | 0.93358 | 1.086 | 1.086 | 1.086 | 1.086 | 1.086
2020-02-09 14:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.60301 | 1.1926 | 1.1926 | 1.1926 | 1.1926 | 1.1926 | 2.4768 | 3.1963 | 3.6677 | 3.9158 | 4.4119 | 4.9081 | 1.025 | 2.0231 | 2.4277 | 2.4277 | 2.4277 | 2.4277 | 1.0288 | 1.1968 | 1.1968 | 1.1968 | 1.1968 | 1.1968
2020-02-09 15:00 | Summer | 0.58666 | 0.83961 | 1.2116 | 1.2116 | 1.2116 | 1.2116 | 0.51727 | 1.023 | 1.023 | 1.023 | 1.023 | 1.023 | 2.4006 | 3.098 | 3.5548 | 3.7953 | 4.2762 | 4.7571 | 0.99454 | 1.9629 | 2.3555 | 2.3555 | 2.3555 | 2.3555 | 1.0098 | 1.1746 | 1.1746 | 1.1746 | 1.1746 | 1.1746
2020-02-09 16:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.51442 | 1.0174 | 1.0174 | 1.0174 | 1.0174 | 1.0174 | 2.3816 | 3.0734 | 3.5266 | 3.7652 | 4.2423 | 4.7194 | 0.92976 | 1.8351 | 2.2021 | 2.2021 | 2.2021 | 2.2021 | 0.95263 | 1.1082 | 1.1082 | 1.1082 | 1.1082 | 1.1082
2020-02-09 17:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.5087 | 1.0061 | 1.0061 | 1.0061 | 1.0061 | 1.0061 | 2.4006 | 3.098 | 3.5548 | 3.7953 | 4.2762 | 4.7571 | 1.0098 | 1.993 | 2.3916 | 2.3916 | 2.3916 | 2.3916 | 0.87642 | 1.0195 | 1.0195 | 1.0195 | 1.0195 | 1.0195
2020-02-09 18:00 | Summer | 0.57149 | 0.8179 | 1.1803 | 1.1803 | 1.1803 | 1.1803 | 0.53442 | 1.057 | 1.057 | 1.057 | 1.057 | 1.057 | 2.3244 | 2.9996 | 3.442 | 3.6748 | 4.1404 | 4.6061 | 1.0555 | 2.0832 | 2.4999 | 2.4999 | 2.4999 | 2.4999 | 0.87642 | 1.0195 | 1.0195 | 1.0195 | 1.0195 | 1.0195
2020-02-09 19:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.51442 | 1.0174 | 1.0174 | 1.0174 | 1.0174 | 1.0174 | 2.2673 | 2.9258 | 3.3573 | 3.5844 | 4.0386 | 4.4928 | 1.0022 | 1.978 | 2.3735 | 2.3735 | 2.3735 | 2.3735 | 0.87642 | 1.0195 | 1.0195 | 1.0195 | 1.0195 | 1.0195
2020-02-09 20:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.57443 | 1.1361 | 1.1361 | 1.1361 | 1.1361 | 1.1361 | 2.2863 | 2.9504 | 3.3855 | 3.6146 | 4.0726 | 4.5306 | 1.0441 | 2.0607 | 2.4728 | 2.4728 | 2.4728 | 2.4728 | 0.89547 | 1.0417 | 1.0417 | 1.0417 | 1.0417 | 1.0417
2020-02-09 21:00 | Summer | 0.60923 | 0.8719 | 1.2582 | 1.2582 | 1.2582 | 1.2582 | 0.42868 | 0.84782 | 0.84782 | 0.84782 | 0.84782 | 0.84782 | 2.2291 | 2.8767 | 3.3009 | 3.5242 | 3.9708 | 4.4173 | 1.0441 | 2.0607 | 2.4728 | 2.4728 | 2.4728 | 2.4728 | 0.89547 | 1.0417 | 1.0417 | 1.0417 | 1.0417 | 1.0417
2020-02-09 22:00 | Summer | 0.5715 | 0.8179 | 1.1803 | 1.1803 | 1.1803 | 1.1803 | 0.39156 | 0.7744 | 0.7744 | 0.7744 | 0.7744 | 0.7744 | 2.191 | 2.8275 | 3.2445 | 3.4639 | 3.9029 | 4.3418 | 1.006 | 1.9855 | 2.3826 | 2.3826 | 2.3826 | 2.3826 | 0.89547 | 1.0417 | 1.0417 | 1.0417 | 1.0417 | 1.0417
2020-02-09 23:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.45154 | 0.89304 | 0.89304 | 0.89304 | 0.89304 | 0.89304 | 2.0767 | 2.68 | 3.0752 | 3.2832 | 3.6992 | 4.1153 | 0.95644 | 1.8877 | 2.2652 | 2.2652 | 2.2652 | 2.2652 | 0.89547 | 1.0417 | 1.0417 | 1.0417 | 1.0417 | 1.0417
2020-02-10 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.39724 | 0.78565 | 0.78565 | 0.78565 | 0.78565 | 0.78565 | 1.8672 | 2.4095 | 2.7649 | 2.9519 | 3.3259 | 3.7 | 0.71637 | 1.4139 | 1.6967 | 1.6967 | 1.6967 | 1.6967 | 0.87642 | 1.0195 | 1.0195 | 1.0195 | 1.0195 | 1.0195
2020-02-10 01:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.40582 | 0.8026 | 0.8026 | 0.8026 | 0.8026 | 0.8026 | 1.81 | 2.3358 | 2.6802 | 2.8615 | 3.2241 | 3.5867 | 0.6516 | 1.286 | 1.5433 | 1.5433 | 1.5433 | 1.5433 | 0.89547 | 1.0417 | 1.0417 | 1.0417 | 1.0417 | 1.0417
2020-02-10 02:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.45726 | 0.90434 | 0.90434 | 0.90434 | 0.90434 | 0.90434 | 1.829 | 2.3603 | 2.7084 | 2.8916 | 3.2581 | 3.6245 | 0.78115 | 1.5417 | 1.8501 | 1.8501 | 1.8501 | 1.8501 | 0.87642 | 1.0195 | 1.0195 | 1.0195 | 1.0195 | 1.0195
2020-02-10 03:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.39153 | 0.77434 | 0.77434 | 0.77434 | 0.77434 | 0.77434 | 1.7528 | 2.262 | 2.5956 | 2.7712 | 3.1223 | 3.4734 | 0.77353 | 1.5267 | 1.832 | 1.832 | 1.832 | 1.832 | 0.91452 | 1.0638 | 1.0638 | 1.0638 | 1.0638 | 1.0638
2020-02-10 04:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.48298 | 0.95521 | 0.95521 | 0.95521 | 0.95521 | 0.95521 | 1.835 | 2.3681 | 2.7173 | 2.9011 | 3.2687 | 3.6363 | 0.69351 | 1.3688 | 1.6425 | 1.6425 | 1.6425 | 1.6425 | 1.0288 | 1.1968 | 1.1968 | 1.1968 | 1.1968 | 1.1968
2020-02-10 05:00 | Summer | 0.60937 | 0.87211 | 1.2585 | 1.2585 | 1.2585 | 1.2585 | 0.65159 | 1.2887 | 1.2887 | 1.2887 | 1.2887 | 1.2887 | 1.9243 | 2.4833 | 2.8495 | 3.0422 | 3.4277 | 3.8132 | 0.93331 | 1.8421 | 2.2105 | 2.2105 | 2.2105 | 2.2105 | 1.2099 | 1.4074 | 1.4074 | 1.4074 | 1.4074 | 1.4074
2020-02-10 06:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.73161 | 1.447 | 1.447 | 1.447 | 1.447 | 1.447 | 2.2863 | 2.9504 | 3.3855 | 3.6146 | 4.0726 | 4.5306 | 1.0174 | 2.008 | 2.4096 | 2.4096 | 2.4096 | 2.4096 | 1.3527 | 1.5736 | 1.5736 | 1.5736 | 1.5736 | 1.5736
2020-02-10 07:00 | Summer | 1.4289 | 2.045 | 2.9511 | 2.9511 | 2.9511 | 2.9511 | 0.86022 | 1.7013 | 1.7013 | 1.7013 | 1.7013 | 1.7013 | 2.5911 | 3.3438 | 3.8369 | 4.0965 | 4.6156 | 5.1347 | 1.2041 | 2.3766 | 2.8519 | 2.8519 | 2.8519 | 2.8519 | 1.7719 | 2.0612 | 2.0612 | 2.0612 | 2.0612 | 2.0612
2020-02-10 08:00 | Summer | 1.5814 | 2.2632 | 3.2659 | 3.2659 | 3.2659 | 3.2659 | 1.0003 | 1.9783 | 1.9783 | 1.9783 | 1.9783 | 1.9783 | 2.9722 | 3.8356 | 4.4012 | 4.6989 | 5.2943 | 5.8898 | 1.1927 | 2.354 | 2.8248 | 2.8248 | 2.8248 | 2.8248 | 2.1339 | 2.4823 | 2.4823 | 2.4823 | 2.4823 | 2.4823
2020-02-10 09:00 | Summer | 1.8862 | 2.6995 | 3.8954 | 3.8954 | 3.8954 | 3.8954 | 1.1117 | 2.1987 | 2.1987 | 2.1987 | 2.1987 | 2.1987 | 2.915 | 3.7618 | 4.3166 | 4.6086 | 5.1925 | 5.7765 | 1.1432 | 2.2562 | 2.7075 | 2.7075 | 2.7075 | 2.7075 | 2.3625 | 2.7482 | 2.7482 | 2.7482 | 2.7482 | 2.7482
2020-02-10 10:00 | Summer | 2.0196 | 2.8903 | 4.1709 | 4.1709 | 4.1709 | 4.1709 | 1.0803 | 2.1365 | 2.1365 | 2.1365 | 2.1365 | 2.1365 | 3.2389 | 4.1798 | 4.7962 | 5.1206 | 5.7695 | 6.4183 | 1.1698 | 2.3089 | 2.7706 | 2.7706 | 2.7706 | 2.7706 | 2.6102 | 3.0364 | 3.0364 | 3.0364 | 3.0364 | 3.0364
2020-02-10 11:00 | Summer | 2.7395 | 3.9206 | 5.6576 | 5.6576 | 5.6576 | 5.6576 | 1.3832 | 2.7356 | 2.7356 | 2.7356 | 2.7356 | 2.7356 | 3.3151 | 4.2781 | 4.909 | 5.2411 | 5.9052 | 6.5693 | 1.166 | 2.3013 | 2.7616 | 2.7616 | 2.7616 | 2.7616 | 2.6864 | 3.125 | 3.125 | 3.125 | 3.125 | 3.125
2020-02-10 12:00 | Summer | 4.6107 | 6.5833 | 9.5 | 9.5 | 9.5 | 9.5 | 3.2866 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 3.5057 | 4.524 | 5.1912 | 5.5423 | 6.2446 | 6.9469 | 1.2041 | 2.3766 | 2.8519 | 2.8519 | 2.8519 | 2.8519 | 2.9341 | 3.4131 | 3.4131 | 3.4131 | 3.4131 | 3.4131
2020-02-10 13:00 | Summer | 3.9789 | 5.6945 | 8.2174 | 8.2174 | 8.2174 | 8.2174 | 3.2694 | 6.4661 | 6.4661 | 6.4661 | 6.4661 | 6.4661 | 3.982 | 5.1387 | 5.8965 | 6.2953 | 7.0931 | 7.8908 | 1.2651 | 2.4969 | 2.9963 | 2.9963 | 2.9963 | 2.9963 | 2.8769 | 3.3466 | 3.3466 | 3.3466 | 3.3466 | 3.3466
2020-02-10 14:00 | Summer | 4.4774 | 6.4078 | 9.2467 | 9.2467 | 9.2467 | 9.2467 | 3.2065 | 6.3417 | 6.3417 | 6.3417 | 6.3417 | 6.3417 | 3.9544 | 5.103 | 5.8556 | 6.2517 | 7.0439 | 7.836 | 1.2498 | 2.4668 | 2.9602 | 2.9602 | 2.9602 | 2.9602 | 2.896 | 3.3688 | 3.3688 | 3.3688 | 3.3688 | 3.3688
2020-02-10 15:00 | Summer | 1.9243 | 2.754 | 3.9741 | 3.9741 | 3.9741 | 3.9741 | 1.2947 | 2.5606 | 2.5606 | 2.5606 | 2.5606 | 2.5606 | 3.7724 | 4.8682 | 5.5861 | 5.964 | 6.7197 | 7.4755 | 1.1927 | 2.354 | 2.8248 | 2.8248 | 2.8248 | 2.8248 | 2.9531 | 3.4353 | 3.4353 | 3.4353 | 3.4353 | 3.4353
2020-02-10 16:00 | Summer | 1.81 | 2.5904 | 3.738 | 3.738 | 3.738 | 3.738 | 1.2775 | 2.5265 | 2.5265 | 2.5265 | 2.5265 | 2.5265 | 3.3914 | 4.3765 | 5.0219 | 5.3616 | 6.041 | 6.7204 | 1.1927 | 2.354 | 2.8248 | 2.8248 | 2.8248 | 2.8248 | 2.6674 | 3.1028 | 3.1028 | 3.1028 | 3.1028 | 3.1028
2020-02-10 17:00 | Summer | 1.6766 | 2.3995 | 3.4626 | 3.4626 | 3.4626 | 3.4626 | 1.2517 | 2.4756 | 2.4756 | 2.4756 | 2.4756 | 2.4756 | 3.3533 | 4.3273 | 4.9655 | 5.3013 | 5.9731 | 6.6449 | 1.166 | 2.3013 | 2.7616 | 2.7616 | 2.7616 | 2.7616 | 2.4959 | 2.9034 | 2.9034 | 2.9034 | 2.9034 | 2.9034
2020-02-10 18:00 | Summer | 1.2244 | 1.7523 | 2.5286 | 2.5286 | 2.5286 | 2.5286 | 0.91246 | 1.8046 | 1.8046 | 1.8046 | 1.8046 | 1.8046 | 3.2098 | 4.1422 | 4.7531 | 5.0746 | 5.7176 | 6.3607 | 1.1432 | 2.2562 | 2.7075 | 2.7075 | 2.7075 | 2.7075 | 1.9738 | 2.296 | 2.296 | 2.296 | 2.296 | 2.296
2020-02-10 19:00 | Summer | 0.80021 | 1.1452 | 1.6526 | 1.6526 | 1.6526 | 1.6526 | 0.68303 | 1.3509 | 1.3509 | 1.3509 | 1.3509 | 1.3509 | 3.0103 | 3.8847 | 4.4576 | 4.7592 | 5.3622 | 5.9653 | 1.0669 | 2.1058 | 2.527 | 2.527 | 2.527 | 2.527 | 1.2585 | 1.4639 | 1.4639 | 1.4639 | 1.4639 | 1.4639
2020-02-10 20:00 | Summer | 0.74305 | 1.0634 | 1.5346 | 1.5346 | 1.5346 | 1.5346 | 0.66017 | 1.3056 | 1.3056 | 1.3056 | 1.3056 | 1.3056 | 2.6102 | 3.3684 | 3.8652 | 4.1266 | 4.6495 | 5.1724 | 1.0784 | 2.1284 | 2.554 | 2.554 | 2.554 | 2.554 | 1.2003 | 1.3963 | 1.3963 | 1.3963 | 1.3963 | 1.3963
2020-02-10 21:00 | Summer | 0.66684 | 0.95435 | 1.3772 | 1.3772 | 1.3772 | 1.3772 | 0.54871 | 1.0852 | 1.0852 | 1.0852 | 1.0852 | 1.0852 | 2.534 | 3.2701 | 3.7523 | 4.0061 | 4.5138 | 5.0214 | 1.1355 | 2.2412 | 2.6894 | 2.6894 | 2.6894 | 2.6894 | 1.105 | 1.2855 | 1.2855 | 1.2855 | 1.2855 | 1.2855
2020-02-10 22:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.55443 | 1.0965 | 1.0965 | 1.0965 | 1.0965 | 1.0965 | 2.4387 | 3.1471 | 3.6112 | 3.8555 | 4.3441 | 4.8326 | 1.0288 | 2.0306 | 2.4367 | 2.4367 | 2.4367 | 2.4367 | 1.0669 | 1.2411 | 1.2411 | 1.2411 | 1.2411 | 1.2411
2020-02-10 23:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.52585 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 2.2863 | 2.9504 | 3.3855 | 3.6146 | 4.0726 | 4.5306 | 1.0403 | 2.0532 | 2.4638 | 2.4638 | 2.4638 | 2.4638 | 1.0288 | 1.1968 | 1.1968 | 1.1968 | 1.1968 | 1.1968
2020-02-11 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.48298 | 0.95521 | 0.95521 | 0.95521 | 0.95521 | 0.95521 | 2.0962 | 2.705 | 3.104 | 3.3139 | 3.7338 | 4.1538 | 0.67827 | 1.3387 | 1.6064 | 1.6064 | 1.6064 | 1.6064 | 0.99073 | 1.1525 | 1.1525 | 1.1525 | 1.1525 | 1.1525
2020-02-11 01:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.52299 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.9815 | 2.557 | 2.9341 | 3.1326 | 3.5296 | 3.9265 | 0.71256 | 1.4064 | 1.6877 | 1.6877 | 1.6877 | 1.6877 | 0.99073 | 1.1525 | 1.1525 | 1.1525 | 1.1525 | 1.1525
2020-02-11 02:00 | Summer | 0.59155 | 0.8466 | 1.2217 | 1.2217 | 1.2217 | 1.2217 | 0.54299 | 1.0739 | 1.0739 | 1.0739 | 1.0739 | 1.0739 | 1.9243 | 2.4833 | 2.8495 | 3.0422 | 3.4277 | 3.8132 | 0.64016 | 1.2635 | 1.5162 | 1.5162 | 1.5162 | 1.5162 | 0.95286 | 1.1084 | 1.1084 | 1.1084 | 1.1084 | 1.1084
2020-02-11 03:00 | Summer | 0.60965 | 0.87251 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.5087 | 1.0061 | 1.0061 | 1.0061 | 1.0061 | 1.0061 | 1.9053 | 2.4587 | 2.8213 | 3.0121 | 3.3938 | 3.7755 | 0.64016 | 1.2635 | 1.5162 | 1.5162 | 1.5162 | 1.5162 | 0.97168 | 1.1303 | 1.1303 | 1.1303 | 1.1303 | 1.1303
2020-02-11 04:00 | Summer | 0.63386 | 0.90716 | 1.3091 | 1.3091 | 1.3091 | 1.3091 | 0.50298 | 0.99478 | 0.99478 | 0.99478 | 0.99478 | 0.99478 | 2.0005 | 2.5816 | 2.9624 | 3.1627 | 3.5635 | 3.9643 | 0.64397 | 1.271 | 1.5252 | 1.5252 | 1.5252 | 1.5252 | 1.0288 | 1.1968 | 1.1968 | 1.1968 | 1.1968 | 1.1968
2020-02-11 05:00 | Summer | 0.85737 | 1.227 | 1.7706 | 1.7706 | 1.7706 | 1.7706 | 0.6973 | 1.3791 | 1.3791 | 1.3791 | 1.3791 | 1.3791 | 2.0958 | 2.7046 | 3.1034 | 3.3133 | 3.7332 | 4.153 | 1.0136 | 2.0005 | 2.4006 | 2.4006 | 2.4006 | 2.4006 | 1.1432 | 1.3298 | 1.3298 | 1.3298 | 1.3298 | 1.3298
2020-02-11 06:00 | Summer | 0.8169 | 1.1691 | 1.6871 | 1.6871 | 1.6871 | 1.6871 | 1.1117 | 2.1987 | 2.1987 | 2.1987 | 2.1987 | 2.1987 | 2.2766 | 2.938 | 3.3712 | 3.5993 | 4.0553 | 4.5114 | 1.0631 | 2.0983 | 2.5179 | 2.5179 | 2.5179 | 2.5179 | 1.5408 | 1.7923 | 1.7923 | 1.7923 | 1.7923 | 1.7923
2020-02-11 07:00 | Summer | 1.5827 | 2.2652 | 3.2687 | 3.2687 | 3.2687 | 3.2687 | 1.0431 | 2.063 | 2.063 | 2.063 | 2.063 | 2.063 | 2.915 | 3.7618 | 4.3166 | 4.6086 | 5.1925 | 5.7765 | 1.1774 | 2.3239 | 2.7887 | 2.7887 | 2.7887 | 2.7887 | 1.9243 | 2.2385 | 2.2385 | 2.2385 | 2.2385 | 2.2385
2020-02-11 08:00 | Summer | 2.172 | 3.1085 | 4.4856 | 4.4856 | 4.4856 | 4.4856 | 1.0917 | 2.1591 | 2.1591 | 2.1591 | 2.1591 | 2.1591 | 3.6962 | 4.7699 | 5.4733 | 5.8435 | 6.584 | 7.3244 | 1.2079 | 2.3841 | 2.8609 | 2.8609 | 2.8609 | 2.8609 | 2.4959 | 2.9034 | 2.9034 | 2.9034 | 2.9034 | 2.9034
2020-02-11 09:00 | Summer | 1.4861 | 2.1268 | 3.0691 | 3.0691 | 3.0691 | 3.0691 | 1.2146 | 2.4022 | 2.4022 | 2.4022 | 2.4022 | 2.4022 | 4.0772 | 5.2616 | 6.0376 | 6.4459 | 7.2627 | 8.0795 | 1.227 | 2.4217 | 2.906 | 2.906 | 2.906 | 2.906 | 2.8388 | 3.3023 | 3.3023 | 3.3023 | 3.3023 | 3.3023
2020-02-11 10:00 | Summer | 1.829 | 2.6177 | 3.7774 | 3.7774 | 3.7774 | 3.7774 | 1.4632 | 2.8939 | 2.8939 | 2.8939 | 2.8939 | 2.8939 | 4.1344 | 5.3354 | 6.1222 | 6.5363 | 7.3646 | 8.1928 | 1.1221 | 2.2147 | 2.6577 | 2.6577 | 2.6577 | 2.6577 | 2.896 | 3.3688 | 3.3688 | 3.3688 | 3.3688 | 3.3688
2020-02-11 11:00 | Summer | 1.7964 | 2.571 | 3.71 | 3.71 | 3.71 | 3.71 | 1.3918 | 2.7526 | 2.7526 | 2.7526 | 2.7526 | 2.7526 | 4.0391 | 5.2124 | 5.9811 | 6.3857 | 7.1949 | 8.004 | 1.1012 | 2.1735 | 2.6082 | 2.6082 | 2.6082 | 2.6082 | 2.9722 | 3.4575 | 3.4575 | 3.4575 | 3.4575 | 3.4575
2020-02-11 12:00 | Summer | 2.8769 | 4.1174 | 5.9415 | 5.9415 | 5.9415 | 5.9415 | 1.3918 | 2.7526 | 2.7526 | 2.7526 | 2.7526 | 2.7526 | 4.9918 | 6.4418 | 7.3918 | 7.8918 | 8.8918 | 9.8918 | 1.1241 | 2.2186 | 2.6623 | 2.6623 | 2.6623 | 2.6623 | 3.0675 | 3.5683 | 3.5683 | 3.5683 | 3.5683 | 3.5683
2020-02-11 13:00 | Summer | 1.0669 | 1.527 | 2.2035 | 2.2035 | 2.2035 | 2.2035 | 1.4975 | 2.9617 | 2.9617 | 2.9617 | 2.9617 | 2.9617 | 4.9918 | 6.4418 | 7.3918 | 7.8918 | 8.8918 | 9.8918 | 1.0746 | 2.1208 | 2.545 | 2.545 | 2.545 | 2.545 | 3.1056 | 3.6126 | 3.6126 | 3.6126 | 3.6126 | 3.6126
2020-02-11 14:00 | Summer | 1.0007 | 1.4322 | 2.0667 | 2.0667 | 2.0667 | 2.0667 | 1.3775 | 2.7243 | 2.7243 | 2.7243 | 2.7243 | 2.7243 | 4.9918 | 6.4418 | 7.3918 | 7.8918 | 8.8918 | 9.8918 | 1.0898 | 2.1509 | 2.5811 | 2.5811 | 2.5811 | 2.5811 | 3.0865 | 3.5904 | 3.5904 | 3.5904 | 3.5904 | 3.5904
2020-02-11 15:00 | Summer | 1.2275 | 1.7568 | 2.5351 | 2.5351 | 2.5351 | 2.5351 | 1.529 | 3.0239 | 3.0239 | 3.0239 | 3.0239 | 3.0239 | 4.9918 | 6.4418 | 7.3918 | 7.8918 | 8.8918 | 9.8918 | 1.1127 | 2.1961 | 2.6353 | 2.6353 | 2.6353 | 2.6353 | 2.9913 | 3.4796 | 3.4796 | 3.4796 | 3.4796 | 3.4796
2020-02-11 16:00 | Summer | 2.5721 | 3.6811 | 5.3119 | 5.3119 | 5.3119 | 5.3119 | 1.504 | 2.9744 | 2.9744 | 2.9744 | 2.9744 | 2.9744 | 3.9528 | 5.101 | 5.8532 | 6.2492 | 7.041 | 7.8329 | 1.1089 | 2.1885 | 2.6262 | 2.6262 | 2.6262 | 2.6262 | 2.8198 | 3.2802 | 3.2802 | 3.2802 | 3.2802 | 3.2802
2020-02-11 17:00 | Summer | 2.0577 | 2.9449 | 4.2495 | 4.2495 | 4.2495 | 4.2495 | 1.3489 | 2.6678 | 2.6678 | 2.6678 | 2.6678 | 2.6678 | 3.8486 | 4.9666 | 5.699 | 6.0845 | 6.8555 | 7.6265 | 1.0746 | 2.1208 | 2.545 | 2.545 | 2.545 | 2.545 | 2.7245 | 3.1693 | 3.1693 | 3.1693 | 3.1693 | 3.1693
2020-02-11 18:00 | Summer | 1.596 | 2.2841 | 3.2961 | 3.2961 | 3.2961 | 3.2961 | 1.2289 | 2.4304 | 2.4304 | 2.4304 | 2.4304 | 2.4304 | 3.5247 | 4.5486 | 5.2194 | 5.5724 | 6.2785 | 6.9846 | 1.0593 | 2.0908 | 2.5089 | 2.5089 | 2.5089 | 2.5089 | 2.0287 | 2.3599 | 2.3599 | 2.3599 | 2.3599 | 2.3599
2020-02-11 19:00 | Summer | 0.83831 | 1.1998 | 1.7313 | 1.7313 | 1.7313 | 1.7313 | 0.83474 | 1.6509 | 1.6509 | 1.6509 | 1.6509 | 1.6509 | 3.2812 | 4.2343 | 4.8587 | 5.1874 | 5.8447 | 6.502 | 1.0669 | 2.1058 | 2.527 | 2.527 | 2.527 | 2.527 | 1.4289 | 1.6622 | 1.6622 | 1.6622 | 1.6622 | 1.6622
2020-02-11 20:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.76591 | 1.5148 | 1.5148 | 1.5148 | 1.5148 | 1.5148 | 2.8769 | 3.7126 | 4.2601 | 4.5483 | 5.1246 | 5.701 | 1.0326 | 2.0381 | 2.4457 | 2.4457 | 2.4457 | 2.4457 | 1.2003 | 1.3963 | 1.3963 | 1.3963 | 1.3963 | 1.3963
2020-02-11 21:00 | Summer | 0.87642 | 1.2543 | 1.81 | 1.81 | 1.81 | 1.81 | 0.76305 | 1.5091 | 1.5091 | 1.5091 | 1.5091 | 1.5091 | 2.8198 | 3.6389 | 4.1755 | 4.4579 | 5.0228 | 5.5877 | 1.0326 | 2.0381 | 2.4457 | 2.4457 | 2.4457 | 2.4457 | 1.1432 | 1.3298 | 1.3298 | 1.3298 | 1.3298 | 1.3298
2020-02-11 22:00 | Summer | 0.75839 | 1.0854 | 1.5662 | 1.5662 | 1.5662 | 1.5662 | 0.70589 | 1.3961 | 1.3961 | 1.3961 | 1.3961 | 1.3961 | 2.5541 | 3.296 | 3.7821 | 4.0379 | 4.5496 | 5.0612 | 0.94882 | 1.8727 | 2.2472 | 2.2472 | 2.2472 | 2.2472 | 1.0669 | 1.2411 | 1.2411 | 1.2411 | 1.2411 | 1.2411
2020-02-11 23:00 | Summer | 0.64779 | 0.92709 | 1.3378 | 1.3378 | 1.3378 | 1.3378 | 0.59158 | 1.17 | 1.17 | 1.17 | 1.17 | 1.17 | 2.4578 | 3.1717 | 3.6395 | 3.8856 | 4.378 | 4.8704 | 0.88785 | 1.7523 | 2.1028 | 2.1028 | 2.1028 | 2.1028 | 1.0288 | 1.1968 | 1.1968 | 1.1968 | 1.1968 | 1.1968
2020-02-12 | Summer | 0.6474 | 0.92653 | 1.337 | 1.337 | 1.337 | 1.337 | 0.53442 | 1.057 | 1.057 | 1.057 | 1.057 | 1.057 | 2.1325 | 2.752 | 3.1579 | 3.3715 | 3.7987 | 4.2259 | 0.68208 | 1.3462 | 1.6155 | 1.6155 | 1.6155 | 1.6155 | 1.0479 | 1.219 | 1.219 | 1.219 | 1.219 | 1.219
2020-02-12 01:00 | Summer | 0.64779 | 0.92709 | 1.3378 | 1.3378 | 1.3378 | 1.3378 | 0.54871 | 1.0852 | 1.0852 | 1.0852 | 1.0852 | 1.0852 | 2.0386 | 2.6308 | 3.0188 | 3.223 | 3.6314 | 4.0398 | 0.55252 | 1.0905 | 1.3086 | 1.3086 | 1.3086 | 1.3086 | 1.0098 | 1.1746 | 1.1746 | 1.1746 | 1.1746 | 1.1746
2020-02-12 02:00 | Summer | 0.60964 | 0.87249 | 1.259 | 1.259 | 1.259 | 1.259 | 0.55443 | 1.0965 | 1.0965 | 1.0965 | 1.0965 | 1.0965 | 1.9815 | 2.557 | 2.9341 | 3.1326 | 3.5296 | 3.9265 | 0.55633 | 1.098 | 1.3176 | 1.3176 | 1.3176 | 1.3176 | 0.99073 | 1.1525 | 1.1525 | 1.1525 | 1.1525 | 1.1525
2020-02-12 03:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.55728 | 1.1022 | 1.1022 | 1.1022 | 1.1022 | 1.1022 | 1.9815 | 2.557 | 2.9341 | 3.1326 | 3.5296 | 3.9265 | 0.53347 | 1.0529 | 1.2635 | 1.2635 | 1.2635 | 1.2635 | 1.0288 | 1.1968 | 1.1968 | 1.1968 | 1.1968 | 1.1968
2020-02-12 04:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.58586 | 1.1587 | 1.1587 | 1.1587 | 1.1587 | 1.1587 | 2.0196 | 2.6062 | 2.9906 | 3.1929 | 3.5974 | 4.002 | 0.5449 | 1.0755 | 1.2906 | 1.2906 | 1.2906 | 1.2906 | 1.1241 | 1.3076 | 1.3076 | 1.3076 | 1.3076 | 1.3076
2020-02-12 05:00 | Summer | 0.68589 | 0.98162 | 1.4165 | 1.4165 | 1.4165 | 1.4165 | 0.63151 | 1.249 | 1.249 | 1.249 | 1.249 | 1.249 | 2.0577 | 2.6554 | 3.047 | 3.2531 | 3.6653 | 4.0775 | 0.83069 | 1.6395 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 1.2948 | 1.5062 | 1.5062 | 1.5062 | 1.5062 | 1.5062
2020-02-12 06:00 | Summer | 0.84182 | 1.2048 | 1.7385 | 1.7385 | 1.7385 | 1.7385 | 0.7459 | 1.4752 | 1.4752 | 1.4752 | 1.4752 | 1.4752 | 2.3398 | 3.0195 | 3.4648 | 3.6992 | 4.1679 | 4.6366 | 1.0593 | 2.0908 | 2.5089 | 2.5089 | 2.5089 | 2.5089 | 1.5898 | 1.8494 | 1.8494 | 1.8494 | 1.8494 | 1.8494
2020-02-12 07:00 | Summer | 1.6957 | 2.4268 | 3.5019 | 3.5019 | 3.5019 | 3.5019 | 1.0831 | 2.1422 | 2.1422 | 2.1422 | 2.1422 | 2.1422 | 3.0103 | 3.8847 | 4.4576 | 4.7592 | 5.3622 | 5.9653 | 1.1622 | 2.2938 | 2.7526 | 2.7526 | 2.7526 | 2.7526 | 2.0263 | 2.3572 | 2.3572 | 2.3572 | 2.3572 | 2.3572
2020-02-12 08:00 | Summer | 1.9624 | 2.8085 | 4.0528 | 4.0528 | 4.0528 | 4.0528 | 1.1574 | 2.2891 | 2.2891 | 2.2891 | 2.2891 | 2.2891 | 3.3342 | 4.3027 | 4.9373 | 5.2712 | 5.9392 | 6.6071 | 1.1127 | 2.1961 | 2.6353 | 2.6353 | 2.6353 | 2.6353 | 2.534 | 2.9477 | 2.9477 | 2.9477 | 2.9477 | 2.9477
2020-02-12 09:00 | Summer | 2.3054 | 3.2993 | 4.7611 | 4.7611 | 4.7611 | 4.7611 | 1.3261 | 2.6226 | 2.6226 | 2.6226 | 2.6226 | 2.6226 | 3.5247 | 4.5486 | 5.2194 | 5.5724 | 6.2785 | 6.9846 | 1.105 | 2.181 | 2.6172 | 2.6172 | 2.6172 | 2.6172 | 2.7817 | 3.2358 | 3.2358 | 3.2358 | 3.2358 | 3.2358
2020-02-12 10:00 | Summer | 2.2673 | 3.2448 | 4.6824 | 4.6824 | 4.6824 | 4.6824 | 1.2775 | 2.5265 | 2.5265 | 2.5265 | 2.5265 | 2.5265 | 3.6392 | 4.6963 | 5.3889 | 5.7534 | 6.4825 | 7.2115 | 1.0212 | 2.0156 | 2.4187 | 2.4187 | 2.4187 | 2.4187 | 2.8579 | 3.3245 | 3.3245 | 3.3245 | 3.3245 | 3.3245
2020-02-12 11:00 | Summer | 2.2482 | 3.2175 | 4.643 | 4.643 | 4.643 | 4.643 | 1.286 | 2.5435 | 2.5435 | 2.5435 | 2.5435 | 2.5435 | 3.8102 | 4.917 | 5.6421 | 6.0237 | 6.787 | 7.5503 | 1.0898 | 2.1509 | 2.5811 | 2.5811 | 2.5811 | 2.5811 | 2.915 | 3.391 | 3.391 | 3.391 | 3.391 | 3.391
2020-02-12 12:00 | Summer | 2.2101 | 3.163 | 4.5643 | 4.5643 | 4.5643 | 4.5643 | 1.4261 | 2.8204 | 2.8204 | 2.8204 | 2.8204 | 2.8204 | 3.8486 | 4.9666 | 5.699 | 6.0845 | 6.8555 | 7.6265 | 1.1508 | 2.2713 | 2.7255 | 2.7255 | 2.7255 | 2.7255 | 2.9531 | 3.4353 | 3.4353 | 3.4353 | 3.4353 | 3.4353
2020-02-12 13:00 | Summer | 2.1529 | 3.0812 | 4.4463 | 4.4463 | 4.4463 | 4.4463 | 1.4175 | 2.8035 | 2.8035 | 2.8035 | 2.8035 | 2.8035 | 3.8677 | 4.9911 | 5.7272 | 6.1146 | 6.8894 | 7.6642 | 1.1774 | 2.3239 | 2.7887 | 2.7887 | 2.7887 | 2.7887 | 3.0294 | 3.5239 | 3.5239 | 3.5239 | 3.5239 | 3.5239
2020-02-12 14:00 | Summer | 2.172 | 3.1085 | 4.4856 | 4.4856 | 4.4856 | 4.4856 | 1.489 | 2.9448 | 2.9448 | 2.9448 | 2.9448 | 2.9448 | 4.0582 | 5.237 | 6.0093 | 6.4158 | 7.2288 | 8.0418 | 1.3565 | 2.6774 | 3.2129 | 3.2129 | 3.2129 | 3.2129 | 3.1818 | 3.7013 | 3.7013 | 3.7013 | 3.7013 | 3.7013
2020-02-12 15:00 | Summer | 2.0767 | 2.9721 | 4.2889 | 4.2889 | 4.2889 | 4.2889 | 1.4804 | 2.9278 | 2.9278 | 2.9278 | 2.9278 | 2.9278 | 3.8703 | 4.9945 | 5.7311 | 6.1188 | 6.8941 | 7.6695 | 1.3604 | 2.6849 | 3.2219 | 3.2219 | 3.2219 | 3.2219 | 2.9913 | 3.4796 | 3.4796 | 3.4796 | 3.4796 | 3.4796
2020-02-12 16:00 | Summer | 2.0577 | 2.9449 | 4.2495 | 4.2495 | 4.2495 | 4.2495 | 1.3146 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 3.8486 | 4.9666 | 5.699 | 6.0845 | 6.8555 | 7.6265 | 1.307 | 2.5796 | 3.0955 | 3.0955 | 3.0955 | 3.0955 | 2.8769 | 3.3466 | 3.3466 | 3.3466 | 3.3466 | 3.3466
2020-02-12 17:00 | Summer | 1.8774 | 2.6869 | 3.8773 | 3.8773 | 3.8773 | 3.8773 | 1.4204 | 2.8091 | 2.8091 | 2.8091 | 2.8091 | 2.8091 | 3.8296 | 4.942 | 5.6708 | 6.0544 | 6.8215 | 7.5887 | 1.1851 | 2.3389 | 2.8067 | 2.8067 | 2.8067 | 2.8067 | 2.7817 | 3.2358 | 3.2358 | 3.2358 | 3.2358 | 3.2358
2020-02-12 18:00 | Summer | 1.4987 | 2.1449 | 3.0951 | 3.0951 | 3.0951 | 3.0951 | 1.3496 | 2.6691 | 2.6691 | 2.6691 | 2.6691 | 2.6691 | 3.5438 | 4.5732 | 5.2476 | 5.6026 | 6.3125 | 7.0224 | 1.0479 | 2.0682 | 2.4818 | 2.4818 | 2.4818 | 2.4818 | 1.933 | 2.2486 | 2.2486 | 2.2486 | 2.2486 | 2.2486
2020-02-12 19:00 | Summer | 0.89547 | 1.2816 | 1.8493 | 1.8493 | 1.8493 | 1.8493 | 0.86308 | 1.707 | 1.707 | 1.707 | 1.707 | 1.707 | 3.277 | 4.2289 | 4.8526 | 5.1809 | 5.8373 | 6.4938 | 1.0326 | 2.0381 | 2.4457 | 2.4457 | 2.4457 | 2.4457 | 1.3337 | 1.5514 | 1.5514 | 1.5514 | 1.5514 | 1.5514
2020-02-12 20:00 | Summer | 0.87642 | 1.2543 | 1.81 | 1.81 | 1.81 | 1.81 | 0.82307 | 1.6278 | 1.6278 | 1.6278 | 1.6278 | 1.6278 | 2.8388 | 3.6634 | 4.2037 | 4.4881 | 5.0568 | 5.6255 | 0.99454 | 1.9629 | 2.3555 | 2.3555 | 2.3555 | 2.3555 | 1.2956 | 1.5071 | 1.5071 | 1.5071 | 1.5071 | 1.5071
2020-02-12 21:00 | Summer | 0.78139 | 1.1183 | 1.6137 | 1.6137 | 1.6137 | 1.6137 | 0.74019 | 1.4639 | 1.4639 | 1.4639 | 1.4639 | 1.4639 | 2.7055 | 3.4913 | 4.0062 | 4.2772 | 4.8192 | 5.3612 | 0.96025 | 1.8952 | 2.2743 | 2.2743 | 2.2743 | 2.2743 | 1.1622 | 1.352 | 1.352 | 1.352 | 1.352 | 1.352
2020-02-12 22:00 | Summer | 0.66684 | 0.95435 | 1.3772 | 1.3772 | 1.3772 | 1.3772 | 0.67446 | 1.3339 | 1.3339 | 1.3339 | 1.3339 | 1.3339 | 2.6102 | 3.3684 | 3.8652 | 4.1266 | 4.6495 | 5.1724 | 0.94501 | 1.8651 | 2.2382 | 2.2382 | 2.2382 | 2.2382 | 1.0669 | 1.2411 | 1.2411 | 1.2411 | 1.2411 | 1.2411
2020-02-12 23:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.62301 | 1.2322 | 1.2322 | 1.2322 | 1.2322 | 1.2322 | 2.359 | 3.0442 | 3.4931 | 3.7294 | 4.202 | 4.6746 | 0.91071 | 1.7975 | 2.1569 | 2.1569 | 2.1569 | 2.1569 | 1.0669 | 1.2411 | 1.2411 | 1.2411 | 1.2411 | 1.2411
2020-02-13 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.56872 | 1.1248 | 1.1248 | 1.1248 | 1.1248 | 1.1248 | 2.191 | 2.8275 | 3.2445 | 3.4639 | 3.9029 | 4.3418 | 0.62111 | 1.2259 | 1.4711 | 1.4711 | 1.4711 | 1.4711 | 1.0098 | 1.1746 | 1.1746 | 1.1746 | 1.1746 | 1.1746
2020-02-13 01:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.66303 | 1.3113 | 1.3113 | 1.3113 | 1.3113 | 1.3113 | 2.0767 | 2.68 | 3.0752 | 3.2832 | 3.6992 | 4.1153 | 0.63254 | 1.2484 | 1.4981 | 1.4981 | 1.4981 | 1.4981 | 0.99073 | 1.1525 | 1.1525 | 1.1525 | 1.1525 | 1.1525
2020-02-13 02:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.74876 | 1.4809 | 1.4809 | 1.4809 | 1.4809 | 1.4809 | 2.0196 | 2.6062 | 2.9906 | 3.1929 | 3.5974 | 4.002 | 0.53347 | 1.0529 | 1.2635 | 1.2635 | 1.2635 | 1.2635 | 1.0098 | 1.1746 | 1.1746 | 1.1746 | 1.1746 | 1.1746
2020-02-13 03:00 | Summer | 0.64779 | 0.92709 | 1.3378 | 1.3378 | 1.3378 | 1.3378 | 0.66303 | 1.3113 | 1.3113 | 1.3113 | 1.3113 | 1.3113 | 2.0005 | 2.5816 | 2.9624 | 3.1627 | 3.5635 | 3.9643 | 0.60206 | 1.1883 | 1.4259 | 1.4259 | 1.4259 | 1.4259 | 1.0098 | 1.1746 | 1.1746 | 1.1746 | 1.1746 | 1.1746
2020-02-13 04:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.7459 | 1.4752 | 1.4752 | 1.4752 | 1.4752 | 1.4752 | 2.048 | 2.6429 | 3.0327 | 3.2378 | 3.6481 | 4.0583 | 0.52966 | 1.0454 | 1.2545 | 1.2545 | 1.2545 | 1.2545 | 1.105 | 1.2855 | 1.2855 | 1.2855 | 1.2855 | 1.2855
2020-02-13 05:00 | Summer | 0.64779 | 0.92709 | 1.3378 | 1.3378 | 1.3378 | 1.3378 | 0.82307 | 1.6278 | 1.6278 | 1.6278 | 1.6278 | 1.6278 | 2.0767 | 2.68 | 3.0752 | 3.2832 | 3.6992 | 4.1153 | 0.82647 | 1.6312 | 1.9574 | 1.9574 | 1.9574 | 1.9574 | 1.3429 | 1.5621 | 1.5621 | 1.5621 | 1.5621 | 1.5621
2020-02-13 06:00 | Summer | 0.82658 | 1.183 | 1.7071 | 1.7071 | 1.7071 | 1.7071 | 0.9431 | 1.8652 | 1.8652 | 1.8652 | 1.8652 | 1.8652 | 2.3054 | 2.975 | 3.4138 | 3.6447 | 4.1065 | 4.5683 | 0.98692 | 1.9479 | 2.3374 | 2.3374 | 2.3374 | 2.3374 | 1.5269 | 1.7761 | 1.7761 | 1.7761 | 1.7761 | 1.7761
2020-02-13 07:00 | Summer | 2.0005 | 2.8631 | 4.1315 | 4.1315 | 4.1315 | 4.1315 | 1.226 | 2.4248 | 2.4248 | 2.4248 | 2.4248 | 2.4248 | 3.1437 | 4.0568 | 4.6551 | 4.97 | 5.5998 | 6.2296 | 1.3832 | 2.73 | 3.276 | 3.276 | 3.276 | 3.276 | 2.1988 | 2.5578 | 2.5578 | 2.5578 | 2.5578 | 2.5578
2020-02-13 08:00 | Summer | 1.8481 | 2.6449 | 3.8167 | 3.8167 | 3.8167 | 3.8167 | 1.2689 | 2.5096 | 2.5096 | 2.5096 | 2.5096 | 2.5096 | 3.4295 | 4.4256 | 5.0783 | 5.4218 | 6.1088 | 6.7959 | 1.3375 | 2.6398 | 3.1677 | 3.1677 | 3.1677 | 3.1677 | 2.6674 | 3.1028 | 3.1028 | 3.1028 | 3.1028 | 3.1028
2020-02-13 09:00 | Summer | 3.3013 | 4.7247 | 6.8179 | 6.8179 | 6.8179 | 6.8179 | 1.3203 | 2.6113 | 2.6113 | 2.6113 | 2.6113 | 2.6113 | 3.6009 | 4.6469 | 5.3322 | 5.6929 | 6.4143 | 7.1357 | 1.3451 | 2.6548 | 3.1858 | 3.1858 | 3.1858 | 3.1858 | 2.7817 | 3.2358 | 3.2358 | 3.2358 | 3.2358 | 3.2358
2020-02-13 10:00 | Summer | 3.6771 | 5.2626 | 7.5941 | 7.5941 | 7.5941 | 7.5941 | 1.529 | 3.0239 | 3.0239 | 3.0239 | 3.0239 | 3.0239 | 3.6581 | 4.7207 | 5.4169 | 5.7833 | 6.5161 | 7.2489 | 1.2956 | 2.5571 | 3.0685 | 3.0685 | 3.0685 | 3.0685 | 2.106 | 2.4498 | 2.4498 | 2.4498 | 2.4498 | 2.4498
2020-02-13 11:00 | Summer | 3.7915 | 5.4262 | 7.8302 | 7.8302 | 7.8302 | 7.8302 | 1.4089 | 2.7865 | 2.7865 | 2.7865 | 2.7865 | 2.7865 | 3.7915 | 4.8928 | 5.6144 | 5.9941 | 6.7537 | 7.5132 | 1.3794 | 2.7225 | 3.267 | 3.267 | 3.267 | 3.267 | 2.4959 | 2.9034 | 2.9034 | 2.9034 | 2.9034 | 2.9034
2020-02-13 12:00 | Summer | 3.7915 | 5.4262 | 7.8302 | 7.8302 | 7.8302 | 7.8302 | 1.5404 | 3.0465 | 3.0465 | 3.0465 | 3.0465 | 3.0465 | 3.9439 | 5.0895 | 5.8401 | 6.2351 | 7.0252 | 7.8153 | 1.3261 | 2.6172 | 3.1407 | 3.1407 | 3.1407 | 3.1407 | 2.9722 | 3.4575 | 3.4575 | 3.4575 | 3.4575 | 3.4575
2020-02-13 13:00 | Summer | 2.1238 | 3.0394 | 4.386 | 4.386 | 4.386 | 4.386 | 1.569 | 3.103 | 3.103 | 3.103 | 3.103 | 3.103 | 4.0391 | 5.2124 | 5.9811 | 6.3857 | 7.1949 | 8.004 | 1.3565 | 2.6774 | 3.2129 | 3.2129 | 3.2129 | 3.2129 | 2.9722 | 3.4575 | 3.4575 | 3.4575 | 3.4575 | 3.4575
2020-02-13 14:00 | Summer | 2.1529 | 3.0812 | 4.4463 | 4.4463 | 4.4463 | 4.4463 | 1.5061 | 2.9787 | 2.9787 | 2.9787 | 2.9787 | 2.9787 | 3.8396 | 4.9549 | 5.6856 | 6.0702 | 6.8394 | 7.6086 | 1.4137 | 2.7902 | 3.3482 | 3.3482 | 3.3482 | 3.3482 | 3.0484 | 3.5461 | 3.5461 | 3.5461 | 3.5461 | 3.5461
2020-02-13 15:00 | Summer | 2.1339 | 3.0539 | 4.4069 | 4.4069 | 4.4069 | 4.4069 | 1.4575 | 2.8826 | 2.8826 | 2.8826 | 2.8826 | 2.8826 | 3.8677 | 4.9911 | 5.7272 | 6.1146 | 6.8894 | 7.6642 | 1.3604 | 2.6849 | 3.2219 | 3.2219 | 3.2219 | 3.2219 | 2.9913 | 3.4796 | 3.4796 | 3.4796 | 3.4796 | 3.4796
2020-02-13 16:00 | Summer | 2.0196 | 2.8903 | 4.1709 | 4.1709 | 4.1709 | 4.1709 | 1.4146 | 2.7978 | 2.7978 | 2.7978 | 2.7978 | 2.7978 | 3.6099 | 4.6585 | 5.3455 | 5.7071 | 6.4303 | 7.1535 | 1.2498 | 2.4668 | 2.9602 | 2.9602 | 2.9602 | 2.9602 | 2.8007 | 3.258 | 3.258 | 3.258 | 3.258 | 3.258
2020-02-13 17:00 | Summer | 1.7147 | 2.4541 | 3.5413 | 3.5413 | 3.5413 | 3.5413 | 1.3603 | 2.6904 | 2.6904 | 2.6904 | 2.6904 | 2.6904 | 3.2961 | 4.2535 | 4.8808 | 5.211 | 5.8713 | 6.5316 | 1.2384 | 2.4442 | 2.9331 | 2.9331 | 2.9331 | 2.9331 | 2.5149 | 2.9255 | 2.9255 | 2.9255 | 2.9255 | 2.9255
2020-02-13 18:00 | Summer | 1.2877 | 1.8429 | 2.6593 | 2.6593 | 2.6593 | 2.6593 | 1.1374 | 2.2496 | 2.2496 | 2.2496 | 2.2496 | 2.2496 | 3.0675 | 3.9585 | 4.5423 | 4.8495 | 5.464 | 6.0785 | 0.95263 | 1.8802 | 2.2562 | 2.2562 | 2.2562 | 2.2562 | 1.8595 | 2.1631 | 2.1631 | 2.1631 | 2.1631 | 2.1631
2020-02-13 19:00 | Summer | 0.83831 | 1.1998 | 1.7313 | 1.7313 | 1.7313 | 1.7313 | 0.81164 | 1.6052 | 1.6052 | 1.6052 | 1.6052 | 1.6052 | 2.9531 | 3.811 | 4.373 | 4.6688 | 5.2604 | 5.852 | 0.96025 | 1.8952 | 2.2743 | 2.2743 | 2.2743 | 2.2743 | 1.2765 | 1.4849 | 1.4849 | 1.4849 | 1.4849 | 1.4849
2020-02-13 20:00 | Summer | 0.7621 | 1.0907 | 1.5739 | 1.5739 | 1.5739 | 1.5739 | 0.72304 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 2.8007 | 3.6143 | 4.1473 | 4.4278 | 4.9889 | 5.55 | 0.95263 | 1.8802 | 2.2562 | 2.2562 | 2.2562 | 2.2562 | 1.2956 | 1.5071 | 1.5071 | 1.5071 | 1.5071 | 1.5071
2020-02-13 21:00 | Summer | 0.70494 | 1.0089 | 1.4559 | 1.4559 | 1.4559 | 1.4559 | 0.63159 | 1.2491 | 1.2491 | 1.2491 | 1.2491 | 1.2491 | 2.7626 | 3.5651 | 4.0909 | 4.3676 | 4.921 | 5.4745 | 0.9069 | 1.7899 | 2.1479 | 2.1479 | 2.1479 | 2.1479 | 1.1241 | 1.3076 | 1.3076 | 1.3076 | 1.3076 | 1.3076
2020-02-13 22:00 | Summer | 0.6287 | 0.89977 | 1.2984 | 1.2984 | 1.2984 | 1.2984 | 0.65159 | 1.2887 | 1.2887 | 1.2887 | 1.2887 | 1.2887 | 2.5721 | 3.3192 | 3.8087 | 4.0664 | 4.5816 | 5.0969 | 0.91833 | 1.8125 | 2.175 | 2.175 | 2.175 | 2.175 | 1.0479 | 1.219 | 1.219 | 1.219 | 1.219 | 1.219
2020-02-13 23:00 | Summer | 0.64764 | 0.92688 | 1.3375 | 1.3375 | 1.3375 | 1.3375 | 0.66874 | 1.3226 | 1.3226 | 1.3226 | 1.3226 | 1.3226 | 2.4387 | 3.1471 | 3.6112 | 3.8555 | 4.3441 | 4.8326 | 0.88404 | 1.7448 | 2.0938 | 2.0938 | 2.0938 | 2.0938 | 1.0288 | 1.1968 | 1.1968 | 1.1968 | 1.1968 | 1.1968
2020-02-14 | Summer | 0.64779 | 0.92709 | 1.3378 | 1.3378 | 1.3378 | 1.3378 | 0.63445 | 1.2548 | 1.2548 | 1.2548 | 1.2548 | 1.2548 | 2.1148 | 2.7291 | 3.1316 | 3.3435 | 3.7671 | 4.1908 | 0.60968 | 1.2033 | 1.444 | 1.444 | 1.444 | 1.444 | 1.0097 | 1.1746 | 1.1746 | 1.1746 | 1.1746 | 1.1746
2020-02-14 01:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.70589 | 1.3961 | 1.3961 | 1.3961 | 1.3961 | 1.3961 | 1.9815 | 2.557 | 2.9341 | 3.1326 | 3.5296 | 3.9265 | 0.59063 | 1.1657 | 1.3989 | 1.3989 | 1.3989 | 1.3989 | 1.0098 | 1.1746 | 1.1746 | 1.1746 | 1.1746 | 1.1746
2020-02-14 02:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.66303 | 1.3113 | 1.3113 | 1.3113 | 1.3113 | 1.3113 | 2.0005 | 2.5816 | 2.9624 | 3.1627 | 3.5635 | 3.9643 | 0.56776 | 1.1206 | 1.3447 | 1.3447 | 1.3447 | 1.3447 | 0.95263 | 1.1082 | 1.1082 | 1.1082 | 1.1082 | 1.1082
2020-02-14 03:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.54585 | 1.0796 | 1.0796 | 1.0796 | 1.0796 | 1.0796 | 1.9815 | 2.557 | 2.9341 | 3.1326 | 3.5296 | 3.9265 | 0.62492 | 1.2334 | 1.4801 | 1.4801 | 1.4801 | 1.4801 | 0.97168 | 1.1303 | 1.1303 | 1.1303 | 1.1303 | 1.1303
2020-02-14 04:00 | Summer | 0.64779 | 0.92709 | 1.3378 | 1.3378 | 1.3378 | 1.3378 | 0.51714 | 1.0228 | 1.0228 | 1.0228 | 1.0228 | 1.0228 | 1.9815 | 2.557 | 2.9341 | 3.1326 | 3.5296 | 3.9265 | 0.59444 | 1.1732 | 1.4079 | 1.4079 | 1.4079 | 1.4079 | 1.04 | 1.2098 | 1.2098 | 1.2098 | 1.2098 | 1.2098
2020-02-14 05:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.56586 | 1.1191 | 1.1191 | 1.1191 | 1.1191 | 1.1191 | 2.04 | 2.6326 | 3.0209 | 3.2252 | 3.6339 | 4.0426 | 0.73924 | 1.459 | 1.7508 | 1.7508 | 1.7508 | 1.7508 | 1.2384 | 1.4406 | 1.4406 | 1.4406 | 1.4406 | 1.4406
2020-02-14 06:00 | Summer | 0.78115 | 1.118 | 1.6133 | 1.6133 | 1.6133 | 1.6133 | 0.88973 | 1.7597 | 1.7597 | 1.7597 | 1.7597 | 1.7597 | 2.2539 | 2.9086 | 3.3375 | 3.5633 | 4.0148 | 4.4663 | 0.89928 | 1.7749 | 2.1299 | 2.1299 | 2.1299 | 2.1299 | 1.3321 | 1.5495 | 1.5495 | 1.5495 | 1.5495 | 1.5495
2020-02-14 07:00 | Summer | 1.8277 | 2.6157 | 3.7746 | 3.7746 | 3.7746 | 3.7746 | 0.97453 | 1.9274 | 1.9274 | 1.9274 | 1.9274 | 1.9274 | 2.6864 | 3.4668 | 3.978 | 4.2471 | 4.7853 | 5.3234 | 1.4175 | 2.7977 | 3.3573 | 3.3573 | 3.3573 | 3.3573 | 1.9132 | 2.2255 | 2.2255 | 2.2255 | 2.2255 | 2.2255
2020-02-14 08:00 | Summer | 1.9624 | 2.8085 | 4.0528 | 4.0528 | 4.0528 | 4.0528 | 1.0403 | 2.0574 | 2.0574 | 2.0574 | 2.0574 | 2.0574 | 3.1627 | 4.0814 | 4.6833 | 5.0001 | 5.6337 | 6.2673 | 1.2727 | 2.5119 | 3.0143 | 3.0143 | 3.0143 | 3.0143 | 2.4006 | 2.7926 | 2.7926 | 2.7926 | 2.7926 | 2.7926
2020-02-14 09:00 | Summer | 1.8672 | 2.6722 | 3.8561 | 3.8561 | 3.8561 | 3.8561 | 1.2117 | 2.3965 | 2.3965 | 2.3965 | 2.3965 | 2.3965 | 3.3533 | 4.3273 | 4.9655 | 5.3013 | 5.9731 | 6.6449 | 1.2194 | 2.4066 | 2.888 | 2.888 | 2.888 | 2.888 | 2.4768 | 2.8812 | 2.8812 | 2.8812 | 2.8812 | 2.8812
2020-02-14 10:00 | Summer | 1.829 | 2.6177 | 3.7774 | 3.7774 | 3.7774 | 3.7774 | 1.206 | 2.3852 | 2.3852 | 2.3852 | 2.3852 | 2.3852 | 3.5247 | 4.5486 | 5.2194 | 5.5724 | 6.2785 | 6.9846 | 1.3946 | 2.7526 | 3.3031 | 3.3031 | 3.3031 | 3.3031 | 2.5906 | 3.0135 | 3.0135 | 3.0135 | 3.0135 | 3.0135
2020-02-14 11:00 | Summer | 1.9434 | 2.7813 | 4.0135 | 4.0135 | 4.0135 | 4.0135 | 1.1917 | 2.357 | 2.357 | 2.357 | 2.357 | 2.357 | 3.4977 | 4.5137 | 5.1794 | 5.5298 | 6.2305 | 6.9312 | 1.3718 | 2.7075 | 3.249 | 3.249 | 3.249 | 3.249 | 2.7817 | 3.2358 | 3.2358 | 3.2358 | 3.2358 | 3.2358
2020-02-14 12:00 | Summer | 2.122 | 3.037 | 4.3825 | 4.3825 | 4.3825 | 4.3825 | 1.3232 | 2.617 | 2.617 | 2.617 | 2.617 | 2.617 | 3.62 | 4.6715 | 5.3604 | 5.723 | 6.4482 | 7.1734 | 1.3604 | 2.6849 | 3.2219 | 3.2219 | 3.2219 | 3.2219 | 2.8365 | 3.2996 | 3.2996 | 3.2996 | 3.2996 | 3.2996
2020-02-14 13:00 | Summer | 2.1529 | 3.0812 | 4.4463 | 4.4463 | 4.4463 | 4.4463 | 1.246 | 2.4643 | 2.4643 | 2.4643 | 2.4643 | 2.4643 | 3.639 | 4.6961 | 5.3887 | 5.7532 | 6.4822 | 7.2112 | 1.3489 | 2.6623 | 3.1948 | 3.1948 | 3.1948 | 3.1948 | 2.8388 | 3.3023 | 3.3023 | 3.3023 | 3.3023 | 3.3023
2020-02-14 14:00 | Summer | 2.0767 | 2.9721 | 4.2889 | 4.2889 | 4.2889 | 4.2889 | 1.3889 | 2.747 | 2.747 | 2.747 | 2.747 | 2.747 | 3.8296 | 4.942 | 5.6708 | 6.0544 | 6.8215 | 7.5887 | 1.3946 | 2.7526 | 3.3031 | 3.3031 | 3.3031 | 3.3031 | 2.8769 | 3.3466 | 3.3466 | 3.3466 | 3.3466 | 3.3466
2020-02-14 15:00 | Summer | 2.172 | 3.1085 | 4.4856 | 4.4856 | 4.4856 | 4.4856 | 1.5461 | 3.0578 | 3.0578 | 3.0578 | 3.0578 | 3.0578 | 3.8867 | 5.0157 | 5.7554 | 6.1447 | 6.9234 | 7.702 | 1.3908 | 2.7451 | 3.2941 | 3.2941 | 3.2941 | 3.2941 | 2.9722 | 3.4575 | 3.4575 | 3.4575 | 3.4575 | 3.4575
2020-02-14 16:00 | Summer | 2.0958 | 2.9994 | 4.3282 | 4.3282 | 4.3282 | 4.3282 | 1.4689 | 2.9052 | 2.9052 | 2.9052 | 2.9052 | 2.9052 | 4.0772 | 5.2616 | 6.0376 | 6.4459 | 7.2627 | 8.0795 | 1.3489 | 2.6623 | 3.1948 | 3.1948 | 3.1948 | 3.1948 | 2.8388 | 3.3023 | 3.3023 | 3.3023 | 3.3023 | 3.3023
2020-02-14 17:00 | Summer | 1.9455 | 2.7844 | 4.0179 | 4.0179 | 4.0179 | 4.0179 | 1.4318 | 2.8317 | 2.8317 | 2.8317 | 2.8317 | 2.8317 | 3.9864 | 5.1443 | 5.903 | 6.3023 | 7.1008 | 7.8994 | 1.2918 | 2.5495 | 3.0594 | 3.0594 | 3.0594 | 3.0594 | 2.5911 | 3.0142 | 3.0142 | 3.0142 | 3.0142 | 3.0142
2020-02-14 18:00 | Summer | 1.3966 | 1.9988 | 2.8844 | 2.8844 | 2.8844 | 2.8844 | 1.1495 | 2.2734 | 2.2734 | 2.2734 | 2.2734 | 2.2734 | 3.6009 | 4.6469 | 5.3322 | 5.6929 | 6.4143 | 7.1357 | 1.0098 | 1.993 | 2.3916 | 2.3916 | 2.3916 | 2.3916 | 2.1044 | 2.448 | 2.448 | 2.448 | 2.448 | 2.448
2020-02-14 19:00 | Summer | 0.87642 | 1.2543 | 1.81 | 1.81 | 1.81 | 1.81 | 0.90595 | 1.7917 | 1.7917 | 1.7917 | 1.7917 | 1.7917 | 3.1823 | 4.1066 | 4.7123 | 5.031 | 5.6685 | 6.306 | 0.92595 | 1.8275 | 2.193 | 2.193 | 2.193 | 2.193 | 1.3527 | 1.5736 | 1.5736 | 1.5736 | 1.5736 | 1.5736
2020-02-14 20:00 | Summer | 0.83831 | 1.1998 | 1.7313 | 1.7313 | 1.7313 | 1.7313 | 0.88594 | 1.7522 | 1.7522 | 1.7522 | 1.7522 | 1.7522 | 2.8769 | 3.7126 | 4.2601 | 4.5483 | 5.1246 | 5.701 | 1.0022 | 1.978 | 2.3735 | 2.3735 | 2.3735 | 2.3735 | 1.3146 | 1.5293 | 1.5293 | 1.5293 | 1.5293 | 1.5293
2020-02-14 21:00 | Summer | 0.77809 | 1.1136 | 1.6069 | 1.6069 | 1.6069 | 1.6069 | 0.84879 | 1.6787 | 1.6787 | 1.6787 | 1.6787 | 1.6787 | 2.7436 | 3.5405 | 4.0627 | 4.3375 | 4.8871 | 5.4367 | 0.95644 | 1.8877 | 2.2652 | 2.2652 | 2.2652 | 2.2652 | 1.2332 | 1.4345 | 1.4345 | 1.4345 | 1.4345 | 1.4345
2020-02-14 22:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.7259 | 1.4356 | 1.4356 | 1.4356 | 1.4356 | 1.4356 | 2.6293 | 3.393 | 3.8934 | 4.1567 | 4.6835 | 5.2102 | 0.92214 | 1.82 | 2.184 | 2.184 | 2.184 | 2.184 | 1.0669 | 1.2411 | 1.2411 | 1.2411 | 1.2411 | 1.2411
2020-02-14 23:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.63159 | 1.2491 | 1.2491 | 1.2491 | 1.2491 | 1.2491 | 2.4959 | 3.2209 | 3.6959 | 3.9459 | 4.4459 | 4.9459 | 0.89547 | 1.7674 | 2.1208 | 2.1208 | 2.1208 | 2.1208 | 1 | 1.1633 | 1.1633 | 1.1633 | 1.1633 | 1.1633
2020-02-15 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.54014 | 1.0683 | 1.0683 | 1.0683 | 1.0683 | 1.0683 | 2.2233 | 2.8692 | 3.2923 | 3.515 | 3.9604 | 4.4058 | 0.59063 | 1.1657 | 1.3989 | 1.3989 | 1.3989 | 1.3989 | 0.95263 | 1.1082 | 1.1082 | 1.1082 | 1.1082 | 1.1082
2020-02-15 01:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.52585 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 2.0386 | 2.6308 | 3.0188 | 3.223 | 3.6314 | 4.0398 | 0.54109 | 1.0679 | 1.2815 | 1.2815 | 1.2815 | 1.2815 | 0.95237 | 1.1079 | 1.1079 | 1.1079 | 1.1079 | 1.1079
2020-02-15 02:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.54299 | 1.0739 | 1.0739 | 1.0739 | 1.0739 | 1.0739 | 2.0196 | 2.6062 | 2.9906 | 3.1929 | 3.5974 | 4.002 | 0.5449 | 1.0755 | 1.2906 | 1.2906 | 1.2906 | 1.2906 | 0.97717 | 1.1367 | 1.1367 | 1.1367 | 1.1367 | 1.1367
2020-02-15 03:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.51156 | 1.0117 | 1.0117 | 1.0117 | 1.0117 | 1.0117 | 1.9624 | 2.5325 | 2.9059 | 3.1025 | 3.4956 | 3.8887 | 0.53347 | 1.0529 | 1.2635 | 1.2635 | 1.2635 | 1.2635 | 1.0098 | 1.1746 | 1.1746 | 1.1746 | 1.1746 | 1.1746
2020-02-15 04:00 | Summer | 0.62861 | 0.89964 | 1.2982 | 1.2982 | 1.2982 | 1.2982 | 0.46012 | 0.90999 | 0.90999 | 0.90999 | 0.90999 | 0.90999 | 2.0386 | 2.6308 | 3.0188 | 3.223 | 3.6314 | 4.0398 | 0.51823 | 1.0228 | 1.2274 | 1.2274 | 1.2274 | 1.2274 | 0.93358 | 1.086 | 1.086 | 1.086 | 1.086 | 1.086
2020-02-15 05:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.50584 | 1.0004 | 1.0004 | 1.0004 | 1.0004 | 1.0004 | 2.0577 | 2.6554 | 3.047 | 3.2531 | 3.6653 | 4.0775 | 0.8345 | 1.647 | 1.9764 | 1.9764 | 1.9764 | 1.9764 | 0.97168 | 1.1303 | 1.1303 | 1.1303 | 1.1303 | 1.1303
2020-02-15 06:00 | Summer | 0.61102 | 0.87447 | 1.2619 | 1.2619 | 1.2619 | 1.2619 | 0.54299 | 1.0739 | 1.0739 | 1.0739 | 1.0739 | 1.0739 | 2.0958 | 2.7046 | 3.1034 | 3.3133 | 3.7332 | 4.153 | 0.9069 | 1.7899 | 2.1479 | 2.1479 | 2.1479 | 2.1479 | 1.0669 | 1.2411 | 1.2411 | 1.2411 | 1.2411 | 1.2411
2020-02-15 07:00 | Summer | 0.64779 | 0.92709 | 1.3378 | 1.3378 | 1.3378 | 1.3378 | 0.6716 | 1.3283 | 1.3283 | 1.3283 | 1.3283 | 1.3283 | 2.3051 | 2.9747 | 3.4134 | 3.6443 | 4.106 | 4.5678 | 0.81164 | 1.6019 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 1.1622 | 1.352 | 1.352 | 1.352 | 1.352 | 1.352
2020-02-15 08:00 | Summer | 0.64779 | 0.92709 | 1.3378 | 1.3378 | 1.3378 | 1.3378 | 0.7459 | 1.4752 | 1.4752 | 1.4752 | 1.4752 | 1.4752 | 2.4578 | 3.1717 | 3.6395 | 3.8856 | 4.378 | 4.8704 | 0.86498 | 1.7072 | 2.0486 | 2.0486 | 2.0486 | 2.0486 | 1.1813 | 1.3741 | 1.3741 | 1.3741 | 1.3741 | 1.3741
2020-02-15 09:00 | Summer | 0.66684 | 0.95435 | 1.3772 | 1.3772 | 1.3772 | 1.3772 | 0.75734 | 1.4978 | 1.4978 | 1.4978 | 1.4978 | 1.4978 | 2.6293 | 3.393 | 3.8934 | 4.1567 | 4.6835 | 5.2102 | 0.89864 | 1.7736 | 2.1283 | 2.1283 | 2.1283 | 2.1283 | 1.2956 | 1.5071 | 1.5071 | 1.5071 | 1.5071 | 1.5071
2020-02-15 10:00 | Summer | 0.66684 | 0.95435 | 1.3772 | 1.3772 | 1.3772 | 1.3772 | 0.78306 | 1.5487 | 1.5487 | 1.5487 | 1.5487 | 1.5487 | 2.9531 | 3.811 | 4.373 | 4.6688 | 5.2604 | 5.852 | 1.0403 | 2.0532 | 2.4638 | 2.4638 | 2.4638 | 2.4638 | 1.3146 | 1.5293 | 1.5293 | 1.5293 | 1.5293 | 1.5293
2020-02-15 11:00 | Summer | 0.66684 | 0.95435 | 1.3772 | 1.3772 | 1.3772 | 1.3772 | 0.773 | 1.5288 | 1.5288 | 1.5288 | 1.5288 | 1.5288 | 2.9913 | 3.8601 | 4.4294 | 4.729 | 5.3283 | 5.9275 | 1.1203 | 2.2111 | 2.6533 | 2.6533 | 2.6533 | 2.6533 | 1.3337 | 1.5514 | 1.5514 | 1.5514 | 1.5514 | 1.5514
2020-02-15 12:00 | Summer | 0.66684 | 0.95435 | 1.3772 | 1.3772 | 1.3772 | 1.3772 | 0.78591 | 1.5543 | 1.5543 | 1.5543 | 1.5543 | 1.5543 | 3.1246 | 4.0323 | 4.6269 | 4.9399 | 5.5658 | 6.1918 | 1.1127 | 2.1961 | 2.6353 | 2.6353 | 2.6353 | 2.6353 | 1.3718 | 1.5957 | 1.5957 | 1.5957 | 1.5957 | 1.5957
2020-02-15 13:00 | Summer | 0.60947 | 0.87225 | 1.2587 | 1.2587 | 1.2587 | 1.2587 | 0.8002 | 1.5826 | 1.5826 | 1.5826 | 1.5826 | 1.5826 | 3.0865 | 3.9831 | 4.5705 | 4.8796 | 5.498 | 6.1163 | 1.086 | 2.1434 | 2.5721 | 2.5721 | 2.5721 | 2.5721 | 1.3718 | 1.5957 | 1.5957 | 1.5957 | 1.5957 | 1.5957
2020-02-15 14:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.77734 | 1.5374 | 1.5374 | 1.5374 | 1.5374 | 1.5374 | 2.9546 | 3.8128 | 4.3751 | 4.6711 | 5.263 | 5.8548 | 1.0974 | 2.166 | 2.5992 | 2.5992 | 2.5992 | 2.5992 | 1.2765 | 1.4849 | 1.4849 | 1.4849 | 1.4849 | 1.4849
2020-02-15 15:00 | Summer | 0.7621 | 1.0907 | 1.5739 | 1.5739 | 1.5739 | 1.5739 | 0.73161 | 1.447 | 1.447 | 1.447 | 1.447 | 1.447 | 2.7817 | 3.5897 | 4.1191 | 4.3977 | 4.955 | 5.5122 | 0.96787 | 1.9103 | 2.2923 | 2.2923 | 2.2923 | 2.2923 | 1.2384 | 1.4406 | 1.4406 | 1.4406 | 1.4406 | 1.4406
2020-02-15 16:00 | Summer | 0.7621 | 1.0907 | 1.5739 | 1.5739 | 1.5739 | 1.5739 | 0.68933 | 1.3633 | 1.3633 | 1.3633 | 1.3633 | 1.3633 | 2.7817 | 3.5897 | 4.1191 | 4.3977 | 4.955 | 5.5122 | 0.89166 | 1.7599 | 2.1118 | 2.1118 | 2.1118 | 2.1118 | 1.1622 | 1.352 | 1.352 | 1.352 | 1.352 | 1.352
2020-02-15 17:00 | Summer | 0.74152 | 1.0612 | 1.5314 | 1.5314 | 1.5314 | 1.5314 | 0.80592 | 1.5939 | 1.5939 | 1.5939 | 1.5939 | 1.5939 | 2.8007 | 3.6143 | 4.1473 | 4.4278 | 4.9889 | 5.55 | 0.93738 | 1.8501 | 2.2201 | 2.2201 | 2.2201 | 2.2201 | 1.1241 | 1.3076 | 1.3076 | 1.3076 | 1.3076 | 1.3076
2020-02-15 18:00 | Summer | 0.64779 | 0.92709 | 1.3378 | 1.3378 | 1.3378 | 1.3378 | 0.8888 | 1.7578 | 1.7578 | 1.7578 | 1.7578 | 1.7578 | 2.6483 | 3.4176 | 3.9216 | 4.1869 | 4.7174 | 5.2479 | 0.92976 | 1.8351 | 2.2021 | 2.2021 | 2.2021 | 2.2021 | 1.0483 | 1.2194 | 1.2194 | 1.2194 | 1.2194 | 1.2194
2020-02-15 19:00 | Summer | 0.64779 | 0.92709 | 1.3378 | 1.3378 | 1.3378 | 1.3378 | 0.87165 | 1.7239 | 1.7239 | 1.7239 | 1.7239 | 1.7239 | 2.6864 | 3.4668 | 3.978 | 4.2471 | 4.7853 | 5.3234 | 0.94119 | 1.8576 | 2.2291 | 2.2291 | 2.2291 | 2.2291 | 1.086 | 1.2633 | 1.2633 | 1.2633 | 1.2633 | 1.2633
2020-02-15 20:00 | Summer | 0.64779 | 0.92709 | 1.3378 | 1.3378 | 1.3378 | 1.3378 | 0.85165 | 1.6843 | 1.6843 | 1.6843 | 1.6843 | 1.6843 | 2.6418 | 3.4092 | 3.912 | 4.1766 | 4.7059 | 5.2351 | 0.90309 | 1.7824 | 2.1389 | 2.1389 | 2.1389 | 2.1389 | 1.086 | 1.2633 | 1.2633 | 1.2633 | 1.2633 | 1.2633
2020-02-15 21:00 | Summer | 0.62132 | 0.88921 | 1.2832 | 1.2832 | 1.2832 | 1.2832 | 0.8002 | 1.5826 | 1.5826 | 1.5826 | 1.5826 | 1.5826 | 2.6102 | 3.3684 | 3.8652 | 4.1266 | 4.6495 | 5.1724 | 0.95644 | 1.8877 | 2.2652 | 2.2652 | 2.2652 | 2.2652 | 1.086 | 1.2633 | 1.2633 | 1.2633 | 1.2633 | 1.2633
2020-02-15 22:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.75162 | 1.4865 | 1.4865 | 1.4865 | 1.4865 | 1.4865 | 2.5721 | 3.3192 | 3.8087 | 4.0664 | 4.5816 | 5.0969 | 0.87642 | 1.7298 | 2.0757 | 2.0757 | 2.0757 | 2.0757 | 1.9815 | 2.305 | 2.305 | 2.305 | 2.305 | 2.305
2020-02-15 23:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.52013 | 1.0287 | 1.0287 | 1.0287 | 1.0287 | 1.0287 | 2.338 | 3.0171 | 3.4621 | 3.6963 | 4.1646 | 4.633 | 0.89166 | 1.7599 | 2.1118 | 2.1118 | 2.1118 | 2.1118 | 1.8196 | 2.1166 | 2.1166 | 2.1166 | 2.1166 | 2.1166
2020-02-16 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.42868 | 0.84782 | 0.84782 | 0.84782 | 0.84782 | 0.84782 | 2.0581 | 2.6559 | 3.0476 | 3.2537 | 3.666 | 4.0783 | 0.60587 | 1.1958 | 1.435 | 1.435 | 1.435 | 1.435 | 1.7338 | 2.0168 | 2.0168 | 2.0168 | 2.0168 | 2.0168
2020-02-16 01:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.48298 | 0.95521 | 0.95521 | 0.95521 | 0.95521 | 0.95521 | 2.0005 | 2.5816 | 2.9624 | 3.1627 | 3.5635 | 3.9643 | 0.55633 | 1.098 | 1.3176 | 1.3176 | 1.3176 | 1.3176 | 1.6195 | 1.8839 | 1.8839 | 1.8839 | 1.8839 | 1.8839
2020-02-16 02:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.50298 | 0.99478 | 0.99478 | 0.99478 | 0.99478 | 0.99478 | 1.8862 | 2.4341 | 2.7931 | 2.982 | 3.3599 | 3.7377 | 0.53728 | 1.0604 | 1.2725 | 1.2725 | 1.2725 | 1.2725 | 1.6004 | 1.8617 | 1.8617 | 1.8617 | 1.8617 | 1.8617
2020-02-16 03:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.52299 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.8862 | 2.4341 | 2.7931 | 2.982 | 3.3599 | 3.7377 | 0.52966 | 1.0454 | 1.2545 | 1.2545 | 1.2545 | 1.2545 | 1.5433 | 1.7952 | 1.7952 | 1.7952 | 1.7952 | 1.7952
2020-02-16 04:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.46297 | 0.91565 | 0.91565 | 0.91565 | 0.91565 | 0.91565 | 1.8862 | 2.4341 | 2.7931 | 2.982 | 3.3599 | 3.7377 | 0.52966 | 1.0454 | 1.2545 | 1.2545 | 1.2545 | 1.2545 | 1.5433 | 1.7952 | 1.7952 | 1.7952 | 1.7952 | 1.7952
2020-02-16 05:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.48575 | 0.96069 | 0.96069 | 0.96069 | 0.96069 | 0.96069 | 1.9243 | 2.4833 | 2.8495 | 3.0422 | 3.4277 | 3.8132 | 0.70494 | 1.3913 | 1.6696 | 1.6696 | 1.6696 | 1.6696 | 1.5433 | 1.7952 | 1.7952 | 1.7952 | 1.7952 | 1.7952
2020-02-16 06:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.54014 | 1.0683 | 1.0683 | 1.0683 | 1.0683 | 1.0683 | 2.0196 | 2.6062 | 2.9906 | 3.1929 | 3.5974 | 4.002 | 0.78115 | 1.5417 | 1.8501 | 1.8501 | 1.8501 | 1.8501 | 1.6576 | 1.9282 | 1.9282 | 1.9282 | 1.9282 | 1.9282
2020-02-16 07:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.68017 | 1.3452 | 1.3452 | 1.3452 | 1.3452 | 1.3452 | 2.2291 | 2.8767 | 3.3009 | 3.5242 | 3.9708 | 4.4173 | 0.77734 | 1.5342 | 1.8411 | 1.8411 | 1.8411 | 1.8411 | 1.7147 | 1.9947 | 1.9947 | 1.9947 | 1.9947 | 1.9947
2020-02-16 08:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.6716 | 1.3283 | 1.3283 | 1.3283 | 1.3283 | 1.3283 | 2.5149 | 3.2455 | 3.7241 | 3.976 | 4.4798 | 4.9836 | 0.82526 | 1.6288 | 1.9546 | 1.9546 | 1.9546 | 1.9546 | 1.7719 | 2.0612 | 2.0612 | 2.0612 | 2.0612 | 2.0612
2020-02-16 09:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.6716 | 1.3283 | 1.3283 | 1.3283 | 1.3283 | 1.3283 | 2.534 | 3.2701 | 3.7523 | 4.0061 | 4.5138 | 5.0214 | 0.88404 | 1.7448 | 2.0938 | 2.0938 | 2.0938 | 2.0938 | 1.7528 | 2.039 | 2.039 | 2.039 | 2.039 | 2.039
2020-02-16 10:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.59729 | 1.1813 | 1.1813 | 1.1813 | 1.1813 | 1.1813 | 2.6674 | 3.4422 | 3.9498 | 4.217 | 4.7513 | 5.2857 | 0.9069 | 1.7899 | 2.1479 | 2.1479 | 2.1479 | 2.1479 | 1.8313 | 2.1303 | 2.1303 | 2.1303 | 2.1303 | 2.1303
2020-02-16 11:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.61444 | 1.2152 | 1.2152 | 1.2152 | 1.2152 | 1.2152 | 2.821 | 3.6404 | 4.1773 | 4.4598 | 5.025 | 5.5901 | 0.88023 | 1.7373 | 2.0847 | 2.0847 | 2.0847 | 2.0847 | 1.9815 | 2.305 | 2.305 | 2.305 | 2.305 | 2.305
2020-02-16 12:00 | Summer | 0.64779 | 0.92709 | 1.3378 | 1.3378 | 1.3378 | 1.3378 | 0.70875 | 1.4017 | 1.4017 | 1.4017 | 1.4017 | 1.4017 | 2.896 | 3.7372 | 4.2884 | 4.5784 | 5.1586 | 5.7387 | 0.81164 | 1.6019 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 2.0005 | 2.3271 | 2.3271 | 2.3271 | 2.3271 | 2.3271
2020-02-16 13:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.56586 | 1.1191 | 1.1191 | 1.1191 | 1.1191 | 1.1191 | 2.915 | 3.7618 | 4.3166 | 4.6086 | 5.1925 | 5.7765 | 0.84593 | 1.6696 | 2.0035 | 2.0035 | 2.0035 | 2.0035 | 1.9243 | 2.2385 | 2.2385 | 2.2385 | 2.2385 | 2.2385
2020-02-16 14:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.57729 | 1.1417 | 1.1417 | 1.1417 | 1.1417 | 1.1417 | 2.9913 | 3.8601 | 4.4294 | 4.729 | 5.3283 | 5.9275 | 0.87642 | 1.7298 | 2.0757 | 2.0757 | 2.0757 | 2.0757 | 1.8672 | 2.172 | 2.172 | 2.172 | 2.172 | 2.172
2020-02-16 15:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.64302 | 1.2717 | 1.2717 | 1.2717 | 1.2717 | 1.2717 | 2.9341 | 3.7864 | 4.3448 | 4.6387 | 5.2265 | 5.8142 | 0.90309 | 1.7824 | 2.1389 | 2.1389 | 2.1389 | 2.1389 | 1.829 | 2.1277 | 2.1277 | 2.1277 | 2.1277 | 2.1277
2020-02-16 16:00 | Summer | 0.74305 | 1.0634 | 1.5346 | 1.5346 | 1.5346 | 1.5346 | 0.60301 | 1.1926 | 1.1926 | 1.1926 | 1.1926 | 1.1926 | 2.896 | 3.7372 | 4.2884 | 4.5784 | 5.1586 | 5.7387 | 0.94119 | 1.8576 | 2.2291 | 2.2291 | 2.2291 | 2.2291 | 1.7528 | 2.039 | 2.039 | 2.039 | 2.039 | 2.039
2020-02-16 17:00 | Summer | 0.74305 | 1.0634 | 1.5346 | 1.5346 | 1.5346 | 1.5346 | 0.79332 | 1.569 | 1.569 | 1.569 | 1.569 | 1.569 | 2.8388 | 3.6634 | 4.2037 | 4.4881 | 5.0568 | 5.6255 | 0.92976 | 1.8351 | 2.2021 | 2.2021 | 2.2021 | 2.2021 | 1.8481 | 2.1498 | 2.1498 | 2.1498 | 2.1498 | 2.1498
2020-02-16 18:00 | Summer | 0.64779 | 0.92709 | 1.3378 | 1.3378 | 1.3378 | 1.3378 | 0.79449 | 1.5713 | 1.5713 | 1.5713 | 1.5713 | 1.5713 | 2.6377 | 3.4039 | 3.9058 | 4.17 | 4.6984 | 5.2269 | 0.92595 | 1.8275 | 2.193 | 2.193 | 2.193 | 2.193 | 1.7909 | 2.0833 | 2.0833 | 2.0833 | 2.0833 | 2.0833
2020-02-16 19:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.82021 | 1.6222 | 1.6222 | 1.6222 | 1.6222 | 1.6222 | 2.534 | 3.2701 | 3.7523 | 4.0061 | 4.5138 | 5.0214 | 0.87642 | 1.7298 | 2.0757 | 2.0757 | 2.0757 | 2.0757 | 1.7338 | 2.0168 | 2.0168 | 2.0168 | 2.0168 | 2.0168
2020-02-16 20:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.83164 | 1.6448 | 1.6448 | 1.6448 | 1.6448 | 1.6448 | 2.4387 | 3.1471 | 3.6112 | 3.8555 | 4.3441 | 4.8326 | 0.86879 | 1.7147 | 2.0577 | 2.0577 | 2.0577 | 2.0577 | 1.7909 | 2.0833 | 2.0833 | 2.0833 | 2.0833 | 2.0833
2020-02-16 21:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.64016 | 1.2661 | 1.2661 | 1.2661 | 1.2661 | 1.2661 | 2.3816 | 3.0734 | 3.5266 | 3.7652 | 4.2423 | 4.7194 | 0.89547 | 1.7674 | 2.1208 | 2.1208 | 2.1208 | 2.1208 | 1.7528 | 2.039 | 2.039 | 2.039 | 2.039 | 2.039
2020-02-16 22:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.57729 | 1.1417 | 1.1417 | 1.1417 | 1.1417 | 1.1417 | 2.3444 | 3.0254 | 3.4715 | 3.7064 | 4.176 | 4.6456 | 0.80402 | 1.5869 | 1.9042 | 1.9042 | 1.9042 | 1.9042 | 1.6957 | 1.9725 | 1.9725 | 1.9725 | 1.9725 | 1.9725
2020-02-16 23:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.5287 | 1.0456 | 1.0456 | 1.0456 | 1.0456 | 1.0456 | 2.191 | 2.8275 | 3.2445 | 3.4639 | 3.9029 | 4.3418 | 0.7621 | 1.5041 | 1.805 | 1.805 | 1.805 | 1.805 | 1.6766 | 1.9504 | 1.9504 | 1.9504 | 1.9504 | 1.9504
2020-02-17 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.48012 | 0.94956 | 0.94956 | 0.94956 | 0.94956 | 0.94956 | 1.9815 | 2.557 | 2.9341 | 3.1326 | 3.5296 | 3.9265 | 0.62873 | 1.2409 | 1.4891 | 1.4891 | 1.4891 | 1.4891 | 1.6576 | 1.9282 | 1.9282 | 1.9282 | 1.9282 | 1.9282
2020-02-17 01:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.44297 | 0.87608 | 0.87608 | 0.87608 | 0.87608 | 0.87608 | 1.829 | 2.3603 | 2.7084 | 2.8916 | 3.2581 | 3.6245 | 0.53347 | 1.0529 | 1.2635 | 1.2635 | 1.2635 | 1.2635 | 1.5052 | 1.7509 | 1.7509 | 1.7509 | 1.7509 | 1.7509
2020-02-17 02:00 | Summer | 0.5719 | 0.81847 | 1.1811 | 1.1811 | 1.1811 | 1.1811 | 0.55443 | 1.0965 | 1.0965 | 1.0965 | 1.0965 | 1.0965 | 1.8672 | 2.4095 | 2.7649 | 2.9519 | 3.3259 | 3.7 | 0.51061 | 1.0078 | 1.2093 | 1.2093 | 1.2093 | 1.2093 | 1.5242 | 1.7731 | 1.7731 | 1.7731 | 1.7731 | 1.7731
2020-02-17 03:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.49441 | 0.97782 | 0.97782 | 0.97782 | 0.97782 | 0.97782 | 1.8894 | 2.4382 | 2.7977 | 2.987 | 3.3655 | 3.744 | 0.52204 | 1.0303 | 1.2364 | 1.2364 | 1.2364 | 1.2364 | 1.5814 | 1.8395 | 1.8395 | 1.8395 | 1.8395 | 1.8395
2020-02-17 04:00 | Summer | 0.81926 | 1.1725 | 1.692 | 1.692 | 1.692 | 1.692 | 0.583 | 1.153 | 1.153 | 1.153 | 1.153 | 1.153 | 1.9434 | 2.5079 | 2.8777 | 3.0724 | 3.4617 | 3.851 | 0.54871 | 1.083 | 1.2996 | 1.2996 | 1.2996 | 1.2996 | 1.6957 | 1.9725 | 1.9725 | 1.9725 | 1.9725 | 1.9725
2020-02-17 05:00 | Summer | 0.91452 | 1.3088 | 1.8887 | 1.8887 | 1.8887 | 1.8887 | 0.70304 | 1.3904 | 1.3904 | 1.3904 | 1.3904 | 1.3904 | 2.1363 | 2.7568 | 3.1634 | 3.3773 | 3.8053 | 4.2333 | 0.82307 | 1.6245 | 1.9494 | 1.9494 | 1.9494 | 1.9494 | 2.0962 | 2.4384 | 2.4384 | 2.4384 | 2.4384 | 2.4384
2020-02-17 06:00 | Summer | 1.0479 | 1.4997 | 2.1641 | 2.1641 | 2.1641 | 2.1641 | 0.85165 | 1.6843 | 1.6843 | 1.6843 | 1.6843 | 1.6843 | 2.3344 | 3.0125 | 3.4568 | 3.6906 | 4.1583 | 4.6259 | 0.96787 | 1.9103 | 2.2923 | 2.2923 | 2.2923 | 2.2923 | 2.5149 | 2.9255 | 2.9255 | 2.9255 | 2.9255 | 2.9255
2020-02-17 07:00 | Summer | 1.5623 | 2.2359 | 3.2265 | 3.2265 | 3.2265 | 3.2265 | 1.0374 | 2.0517 | 2.0517 | 2.0517 | 2.0517 | 2.0517 | 2.8579 | 3.688 | 4.2319 | 4.5182 | 5.0907 | 5.6632 | 1.307 | 2.5796 | 3.0955 | 3.0955 | 3.0955 | 3.0955 | 3.0836 | 3.5871 | 3.5871 | 3.5871 | 3.5871 | 3.5871
2020-02-17 08:00 | Summer | 1.7719 | 2.5359 | 3.6593 | 3.6593 | 3.6593 | 3.6593 | 1.1031 | 2.1817 | 2.1817 | 2.1817 | 2.1817 | 2.1817 | 3.1056 | 4.0077 | 4.5987 | 4.9098 | 5.5319 | 6.154 | 1.2384 | 2.4442 | 2.9331 | 2.9331 | 2.9331 | 2.9331 | 3.6009 | 4.1888 | 4.1888 | 4.1888 | 4.1888 | 4.1888
2020-02-17 09:00 | Summer | 1.9243 | 2.754 | 3.9741 | 3.9741 | 3.9741 | 3.9741 | 1.266 | 2.5039 | 2.5039 | 2.5039 | 2.5039 | 2.5039 | 3.258 | 4.2044 | 4.8244 | 5.1507 | 5.8034 | 6.4561 | 1.3108 | 2.5871 | 3.1046 | 3.1046 | 3.1046 | 3.1046 | 3.8867 | 4.5213 | 4.5213 | 4.5213 | 4.5213 | 4.5213
2020-02-17 10:00 | Summer | 1.8895 | 2.7042 | 3.9023 | 3.9023 | 3.9023 | 3.9023 | 1.2489 | 2.47 | 2.47 | 2.47 | 2.47 | 2.47 | 3.4676 | 4.4748 | 5.1347 | 5.4821 | 6.1767 | 6.8714 | 1.3032 | 2.5721 | 3.0865 | 3.0865 | 3.0865 | 3.0865 | 4.0772 | 4.7429 | 4.7429 | 4.7429 | 4.7429 | 4.7429
2020-02-17 11:00 | Summer | 2.1538 | 3.0824 | 4.448 | 4.448 | 4.448 | 4.448 | 1.3346 | 2.6396 | 2.6396 | 2.6396 | 2.6396 | 2.6396 | 3.6962 | 4.7699 | 5.4733 | 5.8435 | 6.584 | 7.3244 | 1.2384 | 2.4442 | 2.9331 | 2.9331 | 2.9331 | 2.9331 | 4.1916 | 4.8759 | 4.8759 | 4.8759 | 4.8759 | 4.8759
2020-02-17 12:00 | Summer | 2.3054 | 3.2993 | 4.7611 | 4.7611 | 4.7611 | 4.7611 | 1.3718 | 2.713 | 2.713 | 2.713 | 2.713 | 2.713 | 3.7724 | 4.8682 | 5.5861 | 5.964 | 6.7197 | 7.4755 | 1.3108 | 2.5871 | 3.1046 | 3.1046 | 3.1046 | 3.1046 | 4.5536 | 5.297 | 5.297 | 5.297 | 5.297 | 5.297
2020-02-17 13:00 | Summer | 2.3054 | 3.2993 | 4.7611 | 4.7611 | 4.7611 | 4.7611 | 1.3918 | 2.7526 | 2.7526 | 2.7526 | 2.7526 | 2.7526 | 3.8105 | 4.9174 | 5.6426 | 6.0243 | 6.7876 | 7.551 | 1.3337 | 2.6323 | 3.1587 | 3.1587 | 3.1587 | 3.1587 | 4.4774 | 5.2083 | 5.2083 | 5.2083 | 5.2083 | 5.2083
2020-02-17 14:00 | Summer | 2.2291 | 3.1903 | 4.6037 | 4.6037 | 4.6037 | 4.6037 | 1.3403 | 2.6509 | 2.6509 | 2.6509 | 2.6509 | 2.6509 | 3.8296 | 4.942 | 5.6708 | 6.0544 | 6.8215 | 7.5887 | 1.3337 | 2.6323 | 3.1587 | 3.1587 | 3.1587 | 3.1587 | 4.5562 | 5.3001 | 5.3001 | 5.3001 | 5.3001 | 5.3001
2020-02-17 15:00 | Summer | 2.2482 | 3.2175 | 4.643 | 4.643 | 4.643 | 4.643 | 1.4432 | 2.8543 | 2.8543 | 2.8543 | 2.8543 | 2.8543 | 3.8867 | 5.0157 | 5.7554 | 6.1447 | 6.9234 | 7.702 | 1.3489 | 2.6623 | 3.1948 | 3.1948 | 3.1948 | 3.1948 | 4.5917 | 5.3413 | 5.3413 | 5.3413 | 5.3413 | 5.3413
2020-02-17 16:00 | Summer | 2.1339 | 3.0539 | 4.4069 | 4.4069 | 4.4069 | 4.4069 | 1.4347 | 2.8374 | 2.8374 | 2.8374 | 2.8374 | 2.8374 | 3.8341 | 4.9478 | 5.6775 | 6.0616 | 6.8297 | 7.5977 | 1.2308 | 2.4292 | 2.915 | 2.915 | 2.915 | 2.915 | 4.5731 | 5.3197 | 5.3197 | 5.3197 | 5.3197 | 5.3197
2020-02-17 17:00 | Summer | 2.0386 | 2.9176 | 4.2102 | 4.2102 | 4.2102 | 4.2102 | 1.3546 | 2.6791 | 2.6791 | 2.6791 | 2.6791 | 2.6791 | 3.8296 | 4.942 | 5.6708 | 6.0544 | 6.8215 | 7.5887 | 1.1889 | 2.3465 | 2.8158 | 2.8158 | 2.8158 | 2.8158 | 4.449 | 5.1754 | 5.1754 | 5.1754 | 5.1754 | 5.1754
2020-02-17 18:00 | Summer | 1.6503 | 2.3619 | 3.4083 | 3.4083 | 3.4083 | 3.4083 | 1.3775 | 2.7243 | 2.7243 | 2.7243 | 2.7243 | 2.7243 | 3.53 | 4.5554 | 5.2272 | 5.5807 | 6.2879 | 6.9951 | 1.0098 | 1.993 | 2.3916 | 2.3916 | 2.3916 | 2.3916 | 3.4833 | 4.0521 | 4.0521 | 4.0521 | 4.0521 | 4.0521
2020-02-17 19:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.8345 | 1.6504 | 1.6504 | 1.6504 | 1.6504 | 1.6504 | 3.0884 | 3.9855 | 4.5733 | 4.8826 | 5.5013 | 6.12 | 0.9793 | 1.9328 | 2.3194 | 2.3194 | 2.3194 | 2.3194 | 2.3435 | 2.7261 | 2.7261 | 2.7261 | 2.7261 | 2.7261
2020-02-17 20:00 | Summer | 0.83831 | 1.1998 | 1.7313 | 1.7313 | 1.7313 | 1.7313 | 0.62301 | 1.2322 | 1.2322 | 1.2322 | 1.2322 | 1.2322 | 2.7055 | 3.4913 | 4.0062 | 4.2772 | 4.8192 | 5.3612 | 0.94882 | 1.8727 | 2.2472 | 2.2472 | 2.2472 | 2.2472 | 2.191 | 2.5488 | 2.5488 | 2.5488 | 2.5488 | 2.5488
2020-02-17 21:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.50298 | 0.99478 | 0.99478 | 0.99478 | 0.99478 | 0.99478 | 2.6483 | 3.4176 | 3.9216 | 4.1869 | 4.7174 | 5.2479 | 0.95263 | 1.8802 | 2.2562 | 2.2562 | 2.2562 | 2.2562 | 2.0958 | 2.4379 | 2.4379 | 2.4379 | 2.4379 | 2.4379
2020-02-17 22:00 | Summer | 0.60923 | 0.87191 | 1.2582 | 1.2582 | 1.2582 | 1.2582 | 0.54299 | 1.0739 | 1.0739 | 1.0739 | 1.0739 | 1.0739 | 2.4959 | 3.2209 | 3.6959 | 3.9459 | 4.4459 | 4.9459 | 0.88785 | 1.7523 | 2.1028 | 2.1028 | 2.1028 | 2.1028 | 1.8672 | 2.172 | 2.172 | 2.172 | 2.172 | 2.172
2020-02-17 23:00 | Summer | 0.62848 | 0.89946 | 1.298 | 1.298 | 1.298 | 1.298 | 0.54014 | 1.0683 | 1.0683 | 1.0683 | 1.0683 | 1.0683 | 2.3625 | 3.0488 | 3.4984 | 3.735 | 4.2083 | 4.6816 | 0.84974 | 1.6771 | 2.0125 | 2.0125 | 2.0125 | 2.0125 | 1.7528 | 2.039 | 2.039 | 2.039 | 2.039 | 2.039
2020-02-18 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.53728 | 1.0626 | 1.0626 | 1.0626 | 1.0626 | 1.0626 | 2.2087 | 2.8503 | 3.2706 | 3.4919 | 3.9343 | 4.3768 | 0.63254 | 1.2484 | 1.4981 | 1.4981 | 1.4981 | 1.4981 | 1.7147 | 1.9947 | 1.9947 | 1.9947 | 1.9947 | 1.9947
2020-02-18 01:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.57729 | 1.1417 | 1.1417 | 1.1417 | 1.1417 | 1.1417 | 2.0196 | 2.6062 | 2.9906 | 3.1929 | 3.5974 | 4.002 | 0.60587 | 1.1958 | 1.435 | 1.435 | 1.435 | 1.435 | 1.6004 | 1.8617 | 1.8617 | 1.8617 | 1.8617 | 1.8617
2020-02-18 02:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.57157 | 1.1304 | 1.1304 | 1.1304 | 1.1304 | 1.1304 | 2.001 | 2.5822 | 2.963 | 3.1634 | 3.5643 | 3.9651 | 0.53347 | 1.0529 | 1.2635 | 1.2635 | 1.2635 | 1.2635 | 1.5623 | 1.8174 | 1.8174 | 1.8174 | 1.8174 | 1.8174
2020-02-18 03:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.49441 | 0.97782 | 0.97782 | 0.97782 | 0.97782 | 0.97782 | 1.9815 | 2.557 | 2.9341 | 3.1326 | 3.5296 | 3.9265 | 0.54109 | 1.0679 | 1.2815 | 1.2815 | 1.2815 | 1.2815 | 1.5814 | 1.8395 | 1.8395 | 1.8395 | 1.8395 | 1.8395
2020-02-18 04:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.52585 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 2.0005 | 2.5816 | 2.9624 | 3.1627 | 3.5635 | 3.9643 | 0.56395 | 1.1131 | 1.3357 | 1.3357 | 1.3357 | 1.3357 | 1.6957 | 1.9725 | 1.9725 | 1.9725 | 1.9725 | 1.9725
2020-02-18 05:00 | Summer | 0.85737 | 1.227 | 1.7706 | 1.7706 | 1.7706 | 1.7706 | 0.66542 | 1.316 | 1.316 | 1.316 | 1.316 | 1.316 | 2.0767 | 2.68 | 3.0752 | 3.2832 | 3.6992 | 4.1153 | 0.80021 | 1.5794 | 1.8952 | 1.8952 | 1.8952 | 1.8952 | 2.0395 | 2.3725 | 2.3725 | 2.3725 | 2.3725 | 2.3725
2020-02-18 06:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.86308 | 1.707 | 1.707 | 1.707 | 1.707 | 1.707 | 2.3617 | 3.0477 | 3.4972 | 3.7337 | 4.2068 | 4.6799 | 1.1012 | 2.1735 | 2.6082 | 2.6082 | 2.6082 | 2.6082 | 2.6293 | 3.0585 | 3.0585 | 3.0585 | 3.0585 | 3.0585
2020-02-18 07:00 | Summer | 1.9624 | 2.8085 | 4.0528 | 4.0528 | 4.0528 | 4.0528 | 1.1089 | 2.193 | 2.193 | 2.193 | 2.193 | 2.193 | 3.2199 | 4.1552 | 4.768 | 5.0905 | 5.7355 | 6.3806 | 1.3222 | 2.6097 | 3.1316 | 3.1316 | 3.1316 | 3.1316 | 3.4198 | 3.9781 | 3.9781 | 3.9781 | 3.9781 | 3.9781
2020-02-18 08:00 | Summer | 2.0767 | 2.9721 | 4.2889 | 4.2889 | 4.2889 | 4.2889 | 1.126 | 2.227 | 2.227 | 2.227 | 2.227 | 2.227 | 3.3914 | 4.3765 | 5.0219 | 5.3616 | 6.041 | 6.7204 | 1.3337 | 2.6323 | 3.1587 | 3.1587 | 3.1587 | 3.1587 | 3.9629 | 4.6099 | 4.6099 | 4.6099 | 4.6099 | 4.6099
2020-02-18 09:00 | Summer | 2.0767 | 2.9721 | 4.2889 | 4.2889 | 4.2889 | 4.2889 | 1.3146 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 3.5247 | 4.5486 | 5.2194 | 5.5724 | 6.2785 | 6.9846 | 1.3299 | 2.6247 | 3.1497 | 3.1497 | 3.1497 | 3.1497 | 4.0772 | 4.7429 | 4.7429 | 4.7429 | 4.7429 | 4.7429
2020-02-18 10:00 | Summer | 2.1138 | 3.0252 | 4.3655 | 4.3655 | 4.3655 | 4.3655 | 1.3203 | 2.6113 | 2.6113 | 2.6113 | 2.6113 | 2.6113 | 3.7724 | 4.8682 | 5.5861 | 5.964 | 6.7197 | 7.4755 | 1.4366 | 2.8353 | 3.4024 | 3.4024 | 3.4024 | 3.4024 | 4.3059 | 5.0089 | 5.0089 | 5.0089 | 5.0089 | 5.0089
2020-02-18 11:00 | Summer | 2.3435 | 3.3539 | 4.8398 | 4.8398 | 4.8398 | 4.8398 | 1.3146 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 4.0201 | 5.1878 | 5.9529 | 6.3556 | 7.1609 | 7.9663 | 1.4251 | 2.8128 | 3.3753 | 3.3753 | 3.3753 | 3.3753 | 4.6128 | 5.3659 | 5.3659 | 5.3659 | 5.3659 | 5.3659
2020-02-18 12:00 | Summer | 2.2291 | 3.1903 | 4.6037 | 4.6037 | 4.6037 | 4.6037 | 1.5775 | 3.12 | 3.12 | 3.12 | 3.12 | 3.12 | 4.187 | 5.4032 | 6.2001 | 6.6195 | 7.4583 | 8.297 | 1.4518 | 2.8654 | 3.4385 | 3.4385 | 3.4385 | 3.4385 | 4.8393 | 5.6294 | 5.6294 | 5.6294 | 5.6294 | 5.6294
2020-02-18 13:00 | Summer | 2.2673 | 3.2448 | 4.6824 | 4.6824 | 4.6824 | 4.6824 | 1.5833 | 3.1313 | 3.1313 | 3.1313 | 3.1313 | 3.1313 | 4.344 | 5.6058 | 6.4325 | 6.8676 | 7.7379 | 8.6081 | 1.5547 | 3.0685 | 3.6822 | 3.6822 | 3.6822 | 3.6822 | 4.9537 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7
2020-02-18 14:00 | Summer | 2.4768 | 3.5447 | 5.1152 | 5.1152 | 5.1152 | 5.1152 | 2.0234 | 4.0017 | 4.0017 | 4.0017 | 4.0017 | 4.0017 | 4.3059 | 5.5566 | 6.3761 | 6.8074 | 7.67 | 8.5326 | 1.528 | 3.0158 | 3.619 | 3.619 | 3.619 | 3.619 | 4.9156 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7
2020-02-18 15:00 | Summer | 2.4959 | 3.572 | 5.1545 | 5.1545 | 5.1545 | 5.1545 | 1.7719 | 3.5043 | 3.5043 | 3.5043 | 3.5043 | 3.5043 | 4.2297 | 5.4583 | 6.2633 | 6.6869 | 7.5342 | 8.3816 | 1.4975 | 2.9556 | 3.5468 | 3.5468 | 3.5468 | 3.5468 | 4.7822 | 5.563 | 5.563 | 5.563 | 5.563 | 5.563
2020-02-18 16:00 | Summer | 2.4387 | 3.4902 | 5.0365 | 5.0365 | 5.0365 | 5.0365 | 1.6719 | 3.3065 | 3.3065 | 3.3065 | 3.3065 | 3.3065 | 4.1344 | 5.3354 | 6.1222 | 6.5363 | 7.3646 | 8.1928 | 1.467 | 2.8955 | 3.4746 | 3.4746 | 3.4746 | 3.4746 | 4.8012 | 5.5851 | 5.5851 | 5.5851 | 5.5851 | 5.5851
2020-02-18 17:00 | Summer | 1.9305 | 2.7629 | 3.987 | 3.987 | 3.987 | 3.987 | 1.6061 | 3.1765 | 3.1765 | 3.1765 | 3.1765 | 3.1765 | 4.2868 | 5.5321 | 6.3479 | 6.7773 | 7.6361 | 8.4948 | 1.368 | 2.6999 | 3.2399 | 3.2399 | 3.2399 | 3.2399 | 4.362 | 5.0742 | 5.0742 | 5.0742 | 5.0742 | 5.0742
2020-02-18 18:00 | Summer | 1.5056 | 2.1548 | 3.1094 | 3.1094 | 3.1094 | 3.1094 | 1.3118 | 2.5943 | 2.5943 | 2.5943 | 2.5943 | 2.5943 | 3.8677 | 4.9911 | 5.7272 | 6.1146 | 6.8894 | 7.6642 | 1.1927 | 2.354 | 2.8248 | 2.8248 | 2.8248 | 2.8248 | 3.5122 | 4.0856 | 4.0856 | 4.0856 | 4.0856 | 4.0856
2020-02-18 19:00 | Summer | 0.85737 | 1.227 | 1.7706 | 1.7706 | 1.7706 | 1.7706 | 0.84387 | 1.669 | 1.669 | 1.669 | 1.669 | 1.669 | 3.364 | 4.3411 | 4.9813 | 5.3183 | 5.9922 | 6.6661 | 1.1851 | 2.3389 | 2.8067 | 2.8067 | 2.8067 | 2.8067 | 2.3237 | 2.7031 | 2.7031 | 2.7031 | 2.7031 | 2.7031
2020-02-18 20:00 | Summer | 0.80021 | 1.1452 | 1.6526 | 1.6526 | 1.6526 | 1.6526 | 0.61158 | 1.2096 | 1.2096 | 1.2096 | 1.2096 | 1.2096 | 2.9341 | 3.7864 | 4.3448 | 4.6387 | 5.2265 | 5.8142 | 1.1089 | 2.1885 | 2.6262 | 2.6262 | 2.6262 | 2.6262 | 2.0577 | 2.3936 | 2.3936 | 2.3936 | 2.3936 | 2.3936
2020-02-18 21:00 | Summer | 0.80021 | 1.1452 | 1.6526 | 1.6526 | 1.6526 | 1.6526 | 0.55443 | 1.0965 | 1.0965 | 1.0965 | 1.0965 | 1.0965 | 2.7055 | 3.4913 | 4.0062 | 4.2772 | 4.8192 | 5.3612 | 1.0593 | 2.0908 | 2.5089 | 2.5089 | 2.5089 | 2.5089 | 1.9053 | 2.2163 | 2.2163 | 2.2163 | 2.2163 | 2.2163
2020-02-18 22:00 | Summer | 0.724 | 1.0362 | 1.4952 | 1.4952 | 1.4952 | 1.4952 | 0.54299 | 1.0739 | 1.0739 | 1.0739 | 1.0739 | 1.0739 | 2.5721 | 3.3192 | 3.8087 | 4.0664 | 4.5816 | 5.0969 | 1.0098 | 1.993 | 2.3916 | 2.3916 | 2.3916 | 2.3916 | 1.81 | 2.1055 | 2.1055 | 2.1055 | 2.1055 | 2.1055
2020-02-18 23:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.57729 | 1.1417 | 1.1417 | 1.1417 | 1.1417 | 1.1417 | 2.3625 | 3.0488 | 3.4984 | 3.735 | 4.2083 | 4.6816 | 0.94501 | 1.8651 | 2.2382 | 2.2382 | 2.2382 | 2.2382 | 1.7338 | 2.0168 | 2.0168 | 2.0168 | 2.0168 | 2.0168
2020-02-19 | Summer | 0.60881 | 0.8713 | 1.2573 | 1.2573 | 1.2573 | 1.2573 | 0.54299 | 1.0739 | 1.0739 | 1.0739 | 1.0739 | 1.0739 | 2.0476 | 2.6423 | 3.032 | 3.2371 | 3.6473 | 4.0575 | 0.71637 | 1.4139 | 1.6967 | 1.6967 | 1.6967 | 1.6967 | 1.6957 | 1.9725 | 1.9725 | 1.9725 | 1.9725 | 1.9725
2020-02-19 01:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.53442 | 1.057 | 1.057 | 1.057 | 1.057 | 1.057 | 1.9243 | 2.4833 | 2.8495 | 3.0422 | 3.4277 | 3.8132 | 0.68589 | 1.3537 | 1.6245 | 1.6245 | 1.6245 | 1.6245 | 1.5363 | 1.7872 | 1.7872 | 1.7872 | 1.7872 | 1.7872
2020-02-19 02:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.5087 | 1.0061 | 1.0061 | 1.0061 | 1.0061 | 1.0061 | 1.8862 | 2.4341 | 2.7931 | 2.982 | 3.3599 | 3.7377 | 0.60206 | 1.1883 | 1.4259 | 1.4259 | 1.4259 | 1.4259 | 1.4861 | 1.7287 | 1.7287 | 1.7287 | 1.7287 | 1.7287
2020-02-19 03:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.563 | 1.1135 | 1.1135 | 1.1135 | 1.1135 | 1.1135 | 1.829 | 2.3603 | 2.7084 | 2.8916 | 3.2581 | 3.6245 | 0.61349 | 1.2108 | 1.453 | 1.453 | 1.453 | 1.453 | 1.467 | 1.7066 | 1.7066 | 1.7066 | 1.7066 | 1.7066
2020-02-19 04:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.64302 | 1.2717 | 1.2717 | 1.2717 | 1.2717 | 1.2717 | 1.7909 | 2.3112 | 2.652 | 2.8314 | 3.1902 | 3.549 | 0.6173 | 1.2184 | 1.462 | 1.462 | 1.462 | 1.462 | 1.5433 | 1.7952 | 1.7952 | 1.7952 | 1.7952 | 1.7952
2020-02-19 05:00 | Summer | 0.78115 | 1.118 | 1.6133 | 1.6133 | 1.6133 | 1.6133 | 0.60015 | 1.187 | 1.187 | 1.187 | 1.187 | 1.187 | 1.8672 | 2.4095 | 2.7649 | 2.9519 | 3.3259 | 3.7 | 0.9069 | 1.7899 | 2.1479 | 2.1479 | 2.1479 | 2.1479 | 1.8146 | 2.1109 | 2.1109 | 2.1109 | 2.1109 | 2.1109
2020-02-19 06:00 | Summer | 0.78115 | 1.118 | 1.6133 | 1.6133 | 1.6133 | 1.6133 | 0.8545 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 2.0926 | 2.7005 | 3.0987 | 3.3083 | 3.7275 | 4.1467 | 0.96406 | 1.9027 | 2.2833 | 2.2833 | 2.2833 | 2.2833 | 2.0577 | 2.3936 | 2.3936 | 2.3936 | 2.3936 | 2.3936
2020-02-19 07:00 | Summer | 1.81 | 2.5904 | 3.738 | 3.738 | 3.738 | 3.738 | 1.1289 | 2.2326 | 2.2326 | 2.2326 | 2.2326 | 2.2326 | 2.5907 | 3.3432 | 3.8363 | 4.0958 | 4.6147 | 5.1337 | 1.2232 | 2.4142 | 2.897 | 2.897 | 2.897 | 2.897 | 2.8867 | 3.358 | 3.358 | 3.358 | 3.358 | 3.358
2020-02-19 08:00 | Summer | 1.9243 | 2.754 | 3.9741 | 3.9741 | 3.9741 | 3.9741 | 1.1517 | 2.2778 | 2.2778 | 2.2778 | 2.2778 | 2.2778 | 2.9531 | 3.811 | 4.373 | 4.6688 | 5.2604 | 5.852 | 1.2841 | 2.5345 | 3.0414 | 3.0414 | 3.0414 | 3.0414 | 3.3533 | 3.9007 | 3.9007 | 3.9007 | 3.9007 | 3.9007
2020-02-19 09:00 | Summer | 1.829 | 2.6177 | 3.7774 | 3.7774 | 3.7774 | 3.7774 | 1.1431 | 2.2609 | 2.2609 | 2.2609 | 2.2609 | 2.2609 | 3.1056 | 4.0077 | 4.5987 | 4.9098 | 5.5319 | 6.154 | 1.2003 | 2.369 | 2.8428 | 2.8428 | 2.8428 | 2.8428 | 3.6581 | 4.2553 | 4.2553 | 4.2553 | 4.2553 | 4.2553
2020-02-19 10:00 | Summer | 1.8481 | 2.6449 | 3.8167 | 3.8167 | 3.8167 | 3.8167 | 1.2089 | 2.3909 | 2.3909 | 2.3909 | 2.3909 | 2.3909 | 3.1818 | 4.106 | 4.7115 | 5.0303 | 5.6677 | 6.3051 | 1.1851 | 2.3389 | 2.8067 | 2.8067 | 2.8067 | 2.8067 | 3.7534 | 4.3661 | 4.3661 | 4.3661 | 4.3661 | 4.3661
2020-02-19 11:00 | Summer | 1.8672 | 2.6722 | 3.8561 | 3.8561 | 3.8561 | 3.8561 | 1.1403 | 2.2552 | 2.2552 | 2.2552 | 2.2552 | 2.2552 | 3.1627 | 4.0814 | 4.6833 | 5.0001 | 5.6337 | 6.2673 | 1.2041 | 2.3766 | 2.8519 | 2.8519 | 2.8519 | 2.8519 | 3.7915 | 4.4105 | 4.4105 | 4.4105 | 4.4105 | 4.4105
2020-02-19 12:00 | Summer | 1.8481 | 2.6449 | 3.8167 | 3.8167 | 3.8167 | 3.8167 | 1.1717 | 2.3174 | 2.3174 | 2.3174 | 2.3174 | 2.3174 | 3.1818 | 4.106 | 4.7115 | 5.0303 | 5.6677 | 6.3051 | 1.307 | 2.5796 | 3.0955 | 3.0955 | 3.0955 | 3.0955 | 4.0201 | 4.6764 | 4.6764 | 4.6764 | 4.6764 | 4.6764
2020-02-19 13:00 | Summer | 1.7909 | 2.5631 | 3.6987 | 3.6987 | 3.6987 | 3.6987 | 1.1774 | 2.3287 | 2.3287 | 2.3287 | 2.3287 | 2.3287 | 3.1246 | 4.0323 | 4.6269 | 4.9399 | 5.5658 | 6.1918 | 1.2422 | 2.4518 | 2.9421 | 2.9421 | 2.9421 | 2.9421 | 3.8296 | 4.4548 | 4.4548 | 4.4548 | 4.4548 | 4.4548
2020-02-19 14:00 | Summer | 1.81 | 2.5904 | 3.738 | 3.738 | 3.738 | 3.738 | 1.2489 | 2.47 | 2.47 | 2.47 | 2.47 | 2.47 | 3.2008 | 4.1306 | 4.7398 | 5.0604 | 5.7016 | 6.3428 | 1.2232 | 2.4142 | 2.897 | 2.897 | 2.897 | 2.897 | 3.7915 | 4.4105 | 4.4105 | 4.4105 | 4.4105 | 4.4105
2020-02-19 15:00 | Summer | 1.7719 | 2.5359 | 3.6593 | 3.6593 | 3.6593 | 3.6593 | 1.2346 | 2.4417 | 2.4417 | 2.4417 | 2.4417 | 2.4417 | 3.1818 | 4.106 | 4.7115 | 5.0303 | 5.6677 | 6.3051 | 1.2003 | 2.369 | 2.8428 | 2.8428 | 2.8428 | 2.8428 | 3.7724 | 4.3883 | 4.3883 | 4.3883 | 4.3883 | 4.3883
2020-02-19 16:00 | Summer | 1.7338 | 2.4813 | 3.5806 | 3.5806 | 3.5806 | 3.5806 | 1.3261 | 2.6226 | 2.6226 | 2.6226 | 2.6226 | 2.6226 | 3.1246 | 4.0323 | 4.6269 | 4.9399 | 5.5658 | 6.1918 | 1.2117 | 2.3916 | 2.8699 | 2.8699 | 2.8699 | 2.8699 | 3.6771 | 4.2775 | 4.2775 | 4.2775 | 4.2775 | 4.2775
2020-02-19 17:00 | Summer | 1.5242 | 2.1814 | 3.1478 | 3.1478 | 3.1478 | 3.1478 | 1.0603 | 2.097 | 2.097 | 2.097 | 2.097 | 2.097 | 3.0361 | 3.918 | 4.4958 | 4.7999 | 5.4082 | 6.0164 | 1.1698 | 2.3089 | 2.7706 | 2.7706 | 2.7706 | 2.7706 | 3.4104 | 3.9672 | 3.9672 | 3.9672 | 3.9672 | 3.9672
2020-02-19 18:00 | Summer | 1.2767 | 1.8272 | 2.6367 | 2.6367 | 2.6367 | 2.6367 | 0.91311 | 1.8059 | 1.8059 | 1.8059 | 1.8059 | 1.8059 | 2.9341 | 3.7864 | 4.3448 | 4.6387 | 5.2265 | 5.8142 | 1.0708 | 2.1133 | 2.536 | 2.536 | 2.536 | 2.536 | 2.983 | 3.47 | 3.47 | 3.47 | 3.47 | 3.47
2020-02-19 19:00 | Summer | 0.81926 | 1.1725 | 1.692 | 1.692 | 1.692 | 1.692 | 0.68875 | 1.3622 | 1.3622 | 1.3622 | 1.3622 | 1.3622 | 2.4588 | 3.173 | 3.641 | 3.8872 | 4.3798 | 4.8724 | 1.0479 | 2.0682 | 2.4818 | 2.4818 | 2.4818 | 2.4818 | 2.1529 | 2.5044 | 2.5044 | 2.5044 | 2.5044 | 2.5044
2020-02-19 20:00 | Summer | 0.724 | 1.0362 | 1.4952 | 1.4952 | 1.4952 | 1.4952 | 0.70018 | 1.3848 | 1.3848 | 1.3848 | 1.3848 | 1.3848 | 2.4006 | 3.098 | 3.5548 | 3.7953 | 4.2762 | 4.7571 | 1.0746 | 2.1208 | 2.545 | 2.545 | 2.545 | 2.545 | 2.0386 | 2.3715 | 2.3715 | 2.3715 | 2.3715 | 2.3715
2020-02-19 21:00 | Summer | 0.64541 | 0.92368 | 1.3329 | 1.3329 | 1.3329 | 1.3329 | 0.62587 | 1.2378 | 1.2378 | 1.2378 | 1.2378 | 1.2378 | 2.3244 | 2.9996 | 3.442 | 3.6748 | 4.1404 | 4.6061 | 0.98311 | 1.9403 | 2.3284 | 2.3284 | 2.3284 | 2.3284 | 1.9243 | 2.2385 | 2.2385 | 2.2385 | 2.2385 | 2.2385
2020-02-19 22:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.49727 | 0.98347 | 0.98347 | 0.98347 | 0.98347 | 0.98347 | 2.1649 | 2.7938 | 3.2058 | 3.4226 | 3.8563 | 4.29 | 0.97168 | 1.9178 | 2.3013 | 2.3013 | 2.3013 | 2.3013 | 1.7528 | 2.039 | 2.039 | 2.039 | 2.039 | 2.039
2020-02-19 23:00 | Summer | 0.59097 | 0.84577 | 1.2205 | 1.2205 | 1.2205 | 1.2205 | 0.44868 | 0.88738 | 0.88738 | 0.88738 | 0.88738 | 0.88738 | 2.0577 | 2.6554 | 3.047 | 3.2531 | 3.6653 | 4.0775 | 0.88404 | 1.7448 | 2.0938 | 2.0938 | 2.0938 | 2.0938 | 1.6576 | 1.9282 | 1.9282 | 1.9282 | 1.9282 | 1.9282
2020-02-20 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.42868 | 0.84782 | 0.84782 | 0.84782 | 0.84782 | 0.84782 | 1.8564 | 2.3957 | 2.749 | 2.9349 | 3.3068 | 3.6787 | 0.65541 | 1.2936 | 1.5523 | 1.5523 | 1.5523 | 1.5523 | 1.5242 | 1.7731 | 1.7731 | 1.7731 | 1.7731 | 1.7731
2020-02-20 01:00 | Summer | 0.57313 | 0.82024 | 1.1836 | 1.1836 | 1.1836 | 1.1836 | 0.40582 | 0.8026 | 0.8026 | 0.8026 | 0.8026 | 0.8026 | 1.81 | 2.3358 | 2.6802 | 2.8615 | 3.2241 | 3.5867 | 0.63635 | 1.256 | 1.5072 | 1.5072 | 1.5072 | 1.5072 | 1.448 | 1.6844 | 1.6844 | 1.6844 | 1.6844 | 1.6844
2020-02-20 02:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.50013 | 0.98912 | 0.98912 | 0.98912 | 0.98912 | 0.98912 | 1.7719 | 2.2866 | 2.6238 | 2.8013 | 3.1562 | 3.5112 | 0.60587 | 1.1958 | 1.435 | 1.435 | 1.435 | 1.435 | 1.448 | 1.6844 | 1.6844 | 1.6844 | 1.6844 | 1.6844
2020-02-20 03:00 | Summer | 0.58115 | 0.83173 | 1.2002 | 1.2002 | 1.2002 | 1.2002 | 0.47441 | 0.93825 | 0.93825 | 0.93825 | 0.93825 | 0.93825 | 1.7528 | 2.262 | 2.5956 | 2.7712 | 3.1223 | 3.4734 | 0.60587 | 1.1958 | 1.435 | 1.435 | 1.435 | 1.435 | 1.4289 | 1.6622 | 1.6622 | 1.6622 | 1.6622 | 1.6622
2020-02-20 04:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.44297 | 0.87608 | 0.87608 | 0.87608 | 0.87608 | 0.87608 | 1.7583 | 2.269 | 2.6036 | 2.7797 | 3.132 | 3.4842 | 0.60587 | 1.1958 | 1.435 | 1.435 | 1.435 | 1.435 | 1.4616 | 1.7002 | 1.7002 | 1.7002 | 1.7002 | 1.7002
2020-02-20 05:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.56701 | 1.1214 | 1.1214 | 1.1214 | 1.1214 | 1.1214 | 1.8487 | 2.3856 | 2.7375 | 2.9226 | 3.293 | 3.6633 | 0.8075 | 1.5938 | 1.9125 | 1.9125 | 1.9125 | 1.9125 | 1.7338 | 2.0168 | 2.0168 | 2.0168 | 2.0168 | 2.0168
2020-02-20 06:00 | Summer | 0.74244 | 1.0625 | 1.5333 | 1.5333 | 1.5333 | 1.5333 | 0.69446 | 1.3735 | 1.3735 | 1.3735 | 1.3735 | 1.3735 | 2.1148 | 2.7291 | 3.1316 | 3.3435 | 3.7671 | 4.1908 | 0.94882 | 1.8727 | 2.2472 | 2.2472 | 2.2472 | 2.2472 | 2.1094 | 2.4538 | 2.4538 | 2.4538 | 2.4538 | 2.4538
2020-02-20 07:00 | Summer | 1.3908 | 1.9905 | 2.8724 | 2.8724 | 2.8724 | 2.8724 | 0.82021 | 1.6222 | 1.6222 | 1.6222 | 1.6222 | 1.6222 | 2.5911 | 3.3438 | 3.8369 | 4.0965 | 4.6156 | 5.1347 | 1.0746 | 2.1208 | 2.545 | 2.545 | 2.545 | 2.545 | 2.644 | 3.0757 | 3.0757 | 3.0757 | 3.0757 | 3.0757
2020-02-20 08:00 | Summer | 1.7147 | 2.4541 | 3.5413 | 3.5413 | 3.5413 | 3.5413 | 0.8888 | 1.7578 | 1.7578 | 1.7578 | 1.7578 | 1.7578 | 2.8198 | 3.6389 | 4.1755 | 4.4579 | 5.0228 | 5.5877 | 1.2537 | 2.4743 | 2.9692 | 2.9692 | 2.9692 | 2.9692 | 3.4295 | 3.9894 | 3.9894 | 3.9894 | 3.9894 | 3.9894
2020-02-20 09:00 | Summer | 1.7528 | 2.5086 | 3.62 | 3.62 | 3.62 | 3.62 | 1.0231 | 2.0235 | 2.0235 | 2.0235 | 2.0235 | 2.0235 | 2.9722 | 3.8356 | 4.4012 | 4.6989 | 5.2943 | 5.8898 | 1.166 | 2.3013 | 2.7616 | 2.7616 | 2.7616 | 2.7616 | 3.5438 | 4.1224 | 4.1224 | 4.1224 | 4.1224 | 4.1224
2020-02-20 10:00 | Summer | 1.7909 | 2.5631 | 3.6987 | 3.6987 | 3.6987 | 3.6987 | 1.0688 | 2.1139 | 2.1139 | 2.1139 | 2.1139 | 2.1139 | 3.1056 | 4.0077 | 4.5987 | 4.9098 | 5.5319 | 6.154 | 1.1736 | 2.3164 | 2.7797 | 2.7797 | 2.7797 | 2.7797 | 3.7152 | 4.3218 | 4.3218 | 4.3218 | 4.3218 | 4.3218
2020-02-20 11:00 | Summer | 1.9624 | 2.8085 | 4.0528 | 4.0528 | 4.0528 | 4.0528 | 1.0346 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 3.277 | 4.2289 | 4.8526 | 5.1809 | 5.8373 | 6.4938 | 1.1813 | 2.3314 | 2.7977 | 2.7977 | 2.7977 | 2.7977 | 3.8105 | 4.4326 | 4.4326 | 4.4326 | 4.4326 | 4.4326
2020-02-20 12:00 | Summer | 1.8481 | 2.6449 | 3.8167 | 3.8167 | 3.8167 | 3.8167 | 1.1374 | 2.2496 | 2.2496 | 2.2496 | 2.2496 | 2.2496 | 3.3437 | 4.315 | 4.9513 | 5.2862 | 5.9561 | 6.6259 | 1.2079 | 2.3841 | 2.8609 | 2.8609 | 2.8609 | 2.8609 | 3.9248 | 4.5656 | 4.5656 | 4.5656 | 4.5656 | 4.5656
2020-02-20 13:00 | Summer | 1.8672 | 2.6722 | 3.8561 | 3.8561 | 3.8561 | 3.8561 | 1.2146 | 2.4022 | 2.4022 | 2.4022 | 2.4022 | 2.4022 | 3.4104 | 4.4011 | 5.0501 | 5.3917 | 6.0749 | 6.7581 | 1.0936 | 2.1585 | 2.5901 | 2.5901 | 2.5901 | 2.5901 | 4.0772 | 4.7429 | 4.7429 | 4.7429 | 4.7429 | 4.7429
2020-02-20 14:00 | Summer | 1.81 | 2.5904 | 3.738 | 3.738 | 3.738 | 3.738 | 1.3203 | 2.6113 | 2.6113 | 2.6113 | 2.6113 | 2.6113 | 3.3723 | 4.3519 | 4.9937 | 5.3315 | 6.007 | 6.6826 | 1.1012 | 2.1735 | 2.6082 | 2.6082 | 2.6082 | 2.6082 | 4.0963 | 4.7651 | 4.7651 | 4.7651 | 4.7651 | 4.7651
2020-02-20 15:00 | Summer | 1.8481 | 2.6449 | 3.8167 | 3.8167 | 3.8167 | 3.8167 | 1.3918 | 2.7526 | 2.7526 | 2.7526 | 2.7526 | 2.7526 | 3.3723 | 4.3519 | 4.9937 | 5.3315 | 6.007 | 6.6826 | 1.086 | 2.1434 | 2.5721 | 2.5721 | 2.5721 | 2.5721 | 4.0201 | 4.6764 | 4.6764 | 4.6764 | 4.6764 | 4.6764
2020-02-20 16:00 | Summer | 1.81 | 2.5904 | 3.738 | 3.738 | 3.738 | 3.738 | 1.549 | 3.0635 | 3.0635 | 3.0635 | 3.0635 | 3.0635 | 3.3914 | 4.3765 | 5.0219 | 5.3616 | 6.041 | 6.7204 | 1.0974 | 2.166 | 2.5992 | 2.5992 | 2.5992 | 2.5992 | 4.0391 | 4.6986 | 4.6986 | 4.6986 | 4.6986 | 4.6986
2020-02-20 17:00 | Summer | 1.7147 | 2.4541 | 3.5413 | 3.5413 | 3.5413 | 3.5413 | 1.3489 | 2.6678 | 2.6678 | 2.6678 | 2.6678 | 2.6678 | 3.3151 | 4.2781 | 4.909 | 5.2411 | 5.9052 | 6.5693 | 1.0708 | 2.1133 | 2.536 | 2.536 | 2.536 | 2.536 | 3.8566 | 4.4863 | 4.4863 | 4.4863 | 4.4863 | 4.4863
2020-02-20 18:00 | Summer | 1.2968 | 1.856 | 2.6782 | 2.6782 | 2.6782 | 2.6782 | 1.0058 | 1.9893 | 1.9893 | 1.9893 | 1.9893 | 1.9893 | 3.277 | 4.2289 | 4.8526 | 5.1809 | 5.8373 | 6.4938 | 1.0441 | 2.0607 | 2.4728 | 2.4728 | 2.4728 | 2.4728 | 3.2497 | 3.7803 | 3.7803 | 3.7803 | 3.7803 | 3.7803
2020-02-20 19:00 | Summer | 0.80097 | 1.1463 | 1.6542 | 1.6542 | 1.6542 | 1.6542 | 0.95453 | 1.8878 | 1.8878 | 1.8878 | 1.8878 | 1.8878 | 2.9169 | 3.7642 | 4.3194 | 4.6115 | 5.1959 | 5.7802 | 1.0288 | 2.0306 | 2.4367 | 2.4367 | 2.4367 | 2.4367 | 2.172 | 2.5266 | 2.5266 | 2.5266 | 2.5266 | 2.5266
2020-02-20 20:00 | Summer | 0.7621 | 1.0907 | 1.5739 | 1.5739 | 1.5739 | 1.5739 | 0.90595 | 1.7917 | 1.7917 | 1.7917 | 1.7917 | 1.7917 | 2.5911 | 3.3438 | 3.8369 | 4.0965 | 4.6156 | 5.1347 | 0.96406 | 1.9027 | 2.2833 | 2.2833 | 2.2833 | 2.2833 | 2.1339 | 2.4823 | 2.4823 | 2.4823 | 2.4823 | 2.4823
2020-02-20 21:00 | Summer | 0.83331 | 1.1926 | 1.721 | 1.721 | 1.721 | 1.721 | 0.79765 | 1.5776 | 1.5776 | 1.5776 | 1.5776 | 1.5776 | 2.534 | 3.2701 | 3.7523 | 4.0061 | 4.5138 | 5.0214 | 0.95263 | 1.8802 | 2.2562 | 2.2562 | 2.2562 | 2.2562 | 1.2003 | 1.3963 | 1.3963 | 1.3963 | 1.3963 | 1.3963
2020-02-20 22:00 | Summer | 0.83831 | 1.1998 | 1.7313 | 1.7313 | 1.7313 | 1.7313 | 0.64016 | 1.2661 | 1.2661 | 1.2661 | 1.2661 | 1.2661 | 2.3625 | 3.0488 | 3.4984 | 3.735 | 4.2083 | 4.6816 | 0.96787 | 1.9103 | 2.2923 | 2.2923 | 2.2923 | 2.2923 | 1.0288 | 1.1968 | 1.1968 | 1.1968 | 1.1968 | 1.1968
2020-02-20 23:00 | Summer | 0.724 | 1.0362 | 1.4952 | 1.4952 | 1.4952 | 1.4952 | 0.52013 | 1.0287 | 1.0287 | 1.0287 | 1.0287 | 1.0287 | 2.191 | 2.8275 | 3.2445 | 3.4639 | 3.9029 | 4.3418 | 0.86117 | 1.6997 | 2.0396 | 2.0396 | 2.0396 | 2.0396 | 0.91452 | 1.0638 | 1.0638 | 1.0638 | 1.0638 | 1.0638
2020-02-21 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.42868 | 0.84782 | 0.84782 | 0.84782 | 0.84782 | 0.84782 | 1.961 | 2.5306 | 2.9038 | 3.1003 | 3.4931 | 3.8859 | 0.69732 | 1.3763 | 1.6516 | 1.6516 | 1.6516 | 1.6516 | 0.87642 | 1.0195 | 1.0195 | 1.0195 | 1.0195 | 1.0195
2020-02-21 01:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.53156 | 1.0513 | 1.0513 | 1.0513 | 1.0513 | 1.0513 | 1.829 | 2.3603 | 2.7084 | 2.8916 | 3.2581 | 3.6245 | 0.66684 | 1.3161 | 1.5794 | 1.5794 | 1.5794 | 1.5794 | 0.85737 | 0.99734 | 0.99734 | 0.99734 | 0.99734 | 0.99734
2020-02-21 02:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.48584 | 0.96086 | 0.96086 | 0.96086 | 0.96086 | 0.96086 | 1.8481 | 2.3849 | 2.7366 | 2.9218 | 3.292 | 3.6622 | 0.60587 | 1.1958 | 1.435 | 1.435 | 1.435 | 1.435 | 0.85737 | 0.99734 | 0.99734 | 0.99734 | 0.99734 | 0.99734
2020-02-21 03:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.4544 | 0.89869 | 0.89869 | 0.89869 | 0.89869 | 0.89869 | 1.81 | 2.3358 | 2.6802 | 2.8615 | 3.2241 | 3.5867 | 0.62111 | 1.2259 | 1.4711 | 1.4711 | 1.4711 | 1.4711 | 0.85737 | 0.99734 | 0.99734 | 0.99734 | 0.99734 | 0.99734
2020-02-21 04:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.46297 | 0.91565 | 0.91565 | 0.91565 | 0.91565 | 0.91565 | 1.8455 | 2.3815 | 2.7327 | 2.9176 | 3.2873 | 3.657 | 0.6173 | 1.2184 | 1.462 | 1.462 | 1.462 | 1.462 | 0.97168 | 1.1303 | 1.1303 | 1.1303 | 1.1303 | 1.1303
2020-02-21 05:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.55728 | 1.1022 | 1.1022 | 1.1022 | 1.1022 | 1.1022 | 1.8672 | 2.4095 | 2.7649 | 2.9519 | 3.3259 | 3.7 | 0.83396 | 1.646 | 1.9752 | 1.9752 | 1.9752 | 1.9752 | 1.1197 | 1.3025 | 1.3025 | 1.3025 | 1.3025 | 1.3025
2020-02-21 06:00 | Summer | 0.76541 | 1.0954 | 1.5807 | 1.5807 | 1.5807 | 1.5807 | 0.79163 | 1.5656 | 1.5656 | 1.5656 | 1.5656 | 1.5656 | 2.0816 | 2.6862 | 3.0824 | 3.2909 | 3.7079 | 4.1249 | 0.96025 | 1.8952 | 2.2743 | 2.2743 | 2.2743 | 2.2743 | 1.2756 | 1.4839 | 1.4839 | 1.4839 | 1.4839 | 1.4839
2020-02-21 07:00 | Summer | 1.6766 | 2.3995 | 3.4626 | 3.4626 | 3.4626 | 3.4626 | 0.87451 | 1.7296 | 1.7296 | 1.7296 | 1.7296 | 1.7296 | 2.553 | 3.2946 | 3.7805 | 4.0362 | 4.5477 | 5.0591 | 1.1584 | 2.2863 | 2.7436 | 2.7436 | 2.7436 | 2.7436 | 1.7573 | 2.0442 | 2.0442 | 2.0442 | 2.0442 | 2.0442
2020-02-21 08:00 | Summer | 1.6385 | 2.345 | 3.3839 | 3.3839 | 3.3839 | 3.3839 | 1.1374 | 2.2496 | 2.2496 | 2.2496 | 2.2496 | 2.2496 | 2.915 | 3.7618 | 4.3166 | 4.6086 | 5.1925 | 5.7765 | 1.1165 | 2.2036 | 2.6443 | 2.6443 | 2.6443 | 2.6443 | 2.1148 | 2.4601 | 2.4601 | 2.4601 | 2.4601 | 2.4601
2020-02-21 09:00 | Summer | 1.6957 | 2.4268 | 3.5019 | 3.5019 | 3.5019 | 3.5019 | 1.2146 | 2.4022 | 2.4022 | 2.4022 | 2.4022 | 2.4022 | 3.0294 | 3.9093 | 4.4858 | 4.7893 | 5.3962 | 6.003 | 1.1355 | 2.2412 | 2.6894 | 2.6894 | 2.6894 | 2.6894 | 2.3054 | 2.6817 | 2.6817 | 2.6817 | 2.6817 | 2.6817
2020-02-21 10:00 | Summer | 1.7338 | 2.4813 | 3.5806 | 3.5806 | 3.5806 | 3.5806 | 1.1889 | 2.3513 | 2.3513 | 2.3513 | 2.3513 | 2.3513 | 3.1056 | 4.0077 | 4.5987 | 4.9098 | 5.5319 | 6.154 | 1.1889 | 2.3465 | 2.8158 | 2.8158 | 2.8158 | 2.8158 | 2.4578 | 2.8591 | 2.8591 | 2.8591 | 2.8591 | 2.8591
2020-02-21 11:00 | Summer | 1.7528 | 2.5086 | 3.62 | 3.62 | 3.62 | 3.62 | 1.2689 | 2.5096 | 2.5096 | 2.5096 | 2.5096 | 2.5096 | 3.2008 | 4.1306 | 4.7398 | 5.0604 | 5.7016 | 6.3428 | 1.2384 | 2.4442 | 2.9331 | 2.9331 | 2.9331 | 2.9331 | 2.5721 | 2.992 | 2.992 | 2.992 | 2.992 | 2.992
2020-02-21 12:00 | Summer | 1.7528 | 2.5086 | 3.62 | 3.62 | 3.62 | 3.62 | 1.2546 | 2.4813 | 2.4813 | 2.4813 | 2.4813 | 2.4813 | 3.5247 | 4.5486 | 5.2194 | 5.5724 | 6.2785 | 6.9846 | 1.2537 | 2.4743 | 2.9692 | 2.9692 | 2.9692 | 2.9692 | 2.7055 | 3.1472 | 3.1472 | 3.1472 | 3.1472 | 3.1472
2020-02-21 13:00 | Summer | 1.7909 | 2.5631 | 3.6987 | 3.6987 | 3.6987 | 3.6987 | 1.4261 | 2.8204 | 2.8204 | 2.8204 | 2.8204 | 2.8204 | 3.4104 | 4.4011 | 5.0501 | 5.3917 | 6.0749 | 6.7581 | 1.1432 | 2.2562 | 2.7075 | 2.7075 | 2.7075 | 2.7075 | 2.6102 | 3.0364 | 3.0364 | 3.0364 | 3.0364 | 3.0364
2020-02-21 14:00 | Summer | 1.7719 | 2.5359 | 3.6593 | 3.6593 | 3.6593 | 3.6593 | 1.3175 | 2.6056 | 2.6056 | 2.6056 | 2.6056 | 2.6056 | 3.4485 | 4.4502 | 5.1065 | 5.4519 | 6.1428 | 6.8336 | 1.1393 | 2.2487 | 2.6984 | 2.6984 | 2.6984 | 2.6984 | 2.7055 | 3.1472 | 3.1472 | 3.1472 | 3.1472 | 3.1472
2020-02-21 15:00 | Summer | 1.789 | 2.5604 | 3.6947 | 3.6947 | 3.6947 | 3.6947 | 1.4575 | 2.8826 | 2.8826 | 2.8826 | 2.8826 | 2.8826 | 3.5628 | 4.5978 | 5.2758 | 5.6327 | 6.3464 | 7.0602 | 1.1584 | 2.2863 | 2.7436 | 2.7436 | 2.7436 | 2.7436 | 2.7436 | 3.1915 | 3.1915 | 3.1915 | 3.1915 | 3.1915
2020-02-21 16:00 | Summer | 1.7909 | 2.5631 | 3.6987 | 3.6987 | 3.6987 | 3.6987 | 1.6204 | 3.2048 | 3.2048 | 3.2048 | 3.2048 | 3.2048 | 3.5247 | 4.5486 | 5.2194 | 5.5724 | 6.2785 | 6.9846 | 1.2003 | 2.369 | 2.8428 | 2.8428 | 2.8428 | 2.8428 | 2.7245 | 3.1693 | 3.1693 | 3.1693 | 3.1693 | 3.1693
2020-02-21 17:00 | Summer | 1.6151 | 2.3115 | 3.3356 | 3.3356 | 3.3356 | 3.3356 | 1.509 | 2.9843 | 2.9843 | 2.9843 | 2.9843 | 2.9843 | 3.4485 | 4.4502 | 5.1065 | 5.4519 | 6.1428 | 6.8336 | 1.1584 | 2.2863 | 2.7436 | 2.7436 | 2.7436 | 2.7436 | 2.6468 | 3.079 | 3.079 | 3.079 | 3.079 | 3.079
2020-02-21 18:00 | Summer | 1.2262 | 1.7548 | 2.5323 | 2.5323 | 2.5323 | 2.5323 | 1.2889 | 2.5491 | 2.5491 | 2.5491 | 2.5491 | 2.5491 | 3.3342 | 4.3027 | 4.9373 | 5.2712 | 5.9392 | 6.6071 | 1.0669 | 2.1058 | 2.527 | 2.527 | 2.527 | 2.527 | 1.8756 | 2.1818 | 2.1818 | 2.1818 | 2.1818 | 2.1818
2020-02-21 19:00 | Summer | 0.70494 | 1.0089 | 1.4559 | 1.4559 | 1.4559 | 1.4559 | 0.87165 | 1.7239 | 1.7239 | 1.7239 | 1.7239 | 1.7239 | 2.7114 | 3.499 | 4.0151 | 4.2866 | 4.8298 | 5.373 | 1.0555 | 2.0832 | 2.4999 | 2.4999 | 2.4999 | 2.4999 | 1.2384 | 1.4406 | 1.4406 | 1.4406 | 1.4406 | 1.4406
2020-02-21 20:00 | Summer | 0.66884 | 0.95721 | 1.3813 | 1.3813 | 1.3813 | 1.3813 | 0.92023 | 1.82 | 1.82 | 1.82 | 1.82 | 1.82 | 2.4197 | 3.1225 | 3.583 | 3.8254 | 4.3101 | 4.7949 | 1.0403 | 2.0532 | 2.4638 | 2.4638 | 2.4638 | 2.4638 | 1.2003 | 1.3963 | 1.3963 | 1.3963 | 1.3963 | 1.3963
2020-02-21 21:00 | Summer | 0.60153 | 0.86089 | 1.2423 | 1.2423 | 1.2423 | 1.2423 | 0.78877 | 1.56 | 1.56 | 1.56 | 1.56 | 1.56 | 2.4387 | 3.1471 | 3.6112 | 3.8555 | 4.3441 | 4.8326 | 1.0098 | 1.993 | 2.3916 | 2.3916 | 2.3916 | 2.3916 | 1.086 | 1.2633 | 1.2633 | 1.2633 | 1.2633 | 1.2633
2020-02-21 22:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.67731 | 1.3396 | 1.3396 | 1.3396 | 1.3396 | 1.3396 | 2.2482 | 2.9013 | 3.3291 | 3.5543 | 4.0047 | 4.4551 | 0.97168 | 1.9178 | 2.3013 | 2.3013 | 2.3013 | 2.3013 | 0.97168 | 1.1303 | 1.1303 | 1.1303 | 1.1303 | 1.1303
2020-02-21 23:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.66874 | 1.3226 | 1.3226 | 1.3226 | 1.3226 | 1.3226 | 2.0767 | 2.68 | 3.0752 | 3.2832 | 3.6992 | 4.1153 | 0.9069 | 1.7899 | 2.1479 | 2.1479 | 2.1479 | 2.1479 | 0.91452 | 1.0638 | 1.0638 | 1.0638 | 1.0638 | 1.0638
2020-02-22 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.50298 | 0.99478 | 0.99478 | 0.99478 | 0.99478 | 0.99478 | 1.909 | 2.4635 | 2.8268 | 3.018 | 3.4005 | 3.7829 | 0.75829 | 1.4966 | 1.796 | 1.796 | 1.796 | 1.796 | 0.89547 | 1.0417 | 1.0417 | 1.0417 | 1.0417 | 1.0417
2020-02-22 01:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.43154 | 0.85347 | 0.85347 | 0.85347 | 0.85347 | 0.85347 | 1.8672 | 2.4095 | 2.7649 | 2.9519 | 3.3259 | 3.7 | 0.66303 | 1.3086 | 1.5703 | 1.5703 | 1.5703 | 1.5703 | 0.87642 | 1.0195 | 1.0195 | 1.0195 | 1.0195 | 1.0195
2020-02-22 02:00 | Summer | 0.5509 | 0.78843 | 1.1377 | 1.1377 | 1.1377 | 1.1377 | 0.38867 | 0.76869 | 0.76869 | 0.76869 | 0.76869 | 0.76869 | 1.81 | 2.3358 | 2.6802 | 2.8615 | 3.2241 | 3.5867 | 0.59825 | 1.1808 | 1.4169 | 1.4169 | 1.4169 | 1.4169 | 0.87642 | 1.0195 | 1.0195 | 1.0195 | 1.0195 | 1.0195
2020-02-22 03:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.40582 | 0.8026 | 0.8026 | 0.8026 | 0.8026 | 0.8026 | 1.7528 | 2.262 | 2.5956 | 2.7712 | 3.1223 | 3.4734 | 0.59444 | 1.1732 | 1.4079 | 1.4079 | 1.4079 | 1.4079 | 0.87642 | 1.0195 | 1.0195 | 1.0195 | 1.0195 | 1.0195
2020-02-22 04:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.45154 | 0.89304 | 0.89304 | 0.89304 | 0.89304 | 0.89304 | 1.8481 | 2.3849 | 2.7366 | 2.9218 | 3.292 | 3.6622 | 0.59063 | 1.1657 | 1.3989 | 1.3989 | 1.3989 | 1.3989 | 0.87642 | 1.0195 | 1.0195 | 1.0195 | 1.0195 | 1.0195
2020-02-22 05:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.40296 | 0.79695 | 0.79695 | 0.79695 | 0.79695 | 0.79695 | 1.7909 | 2.3112 | 2.652 | 2.8314 | 3.1902 | 3.549 | 0.67827 | 1.3387 | 1.6064 | 1.6064 | 1.6064 | 1.6064 | 0.85737 | 0.99734 | 0.99734 | 0.99734 | 0.99734 | 0.99734
2020-02-22 06:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.53156 | 1.0513 | 1.0513 | 1.0513 | 1.0513 | 1.0513 | 1.829 | 2.3603 | 2.7084 | 2.8916 | 3.2581 | 3.6245 | 0.84974 | 1.6771 | 2.0125 | 2.0125 | 2.0125 | 2.0125 | 0.93551 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-02-22 07:00 | Summer | 0.80021 | 1.1452 | 1.6526 | 1.6526 | 1.6526 | 1.6526 | 0.59729 | 1.1813 | 1.1813 | 1.1813 | 1.1813 | 1.1813 | 2.0577 | 2.6554 | 3.047 | 3.2531 | 3.6653 | 4.0775 | 0.81545 | 1.6094 | 1.9313 | 1.9313 | 1.9313 | 1.9313 | 1.0479 | 1.219 | 1.219 | 1.219 | 1.219 | 1.219
2020-02-22 08:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.64016 | 1.2661 | 1.2661 | 1.2661 | 1.2661 | 1.2661 | 2.3164 | 2.9893 | 3.4302 | 3.6622 | 4.1262 | 4.5903 | 0.88404 | 1.7448 | 2.0938 | 2.0938 | 2.0938 | 2.0938 | 1.1622 | 1.352 | 1.352 | 1.352 | 1.352 | 1.352
2020-02-22 09:00 | Summer | 0.83831 | 1.1998 | 1.7313 | 1.7313 | 1.7313 | 1.7313 | 0.61444 | 1.2152 | 1.2152 | 1.2152 | 1.2152 | 1.2152 | 2.4578 | 3.1717 | 3.6395 | 3.8856 | 4.378 | 4.8704 | 1.0403 | 2.0532 | 2.4638 | 2.4638 | 2.4638 | 2.4638 | 1.2504 | 1.4546 | 1.4546 | 1.4546 | 1.4546 | 1.4546
2020-02-22 10:00 | Summer | 0.67165 | 0.96123 | 1.3871 | 1.3871 | 1.3871 | 1.3871 | 0.75734 | 1.4978 | 1.4978 | 1.4978 | 1.4978 | 1.4978 | 2.4768 | 3.1963 | 3.6677 | 3.9158 | 4.4119 | 4.9081 | 0.99813 | 1.97 | 2.364 | 2.364 | 2.364 | 2.364 | 1.2956 | 1.5071 | 1.5071 | 1.5071 | 1.5071 | 1.5071
2020-02-22 11:00 | Summer | 0.80021 | 1.1452 | 1.6526 | 1.6526 | 1.6526 | 1.6526 | 0.78079 | 1.5442 | 1.5442 | 1.5442 | 1.5442 | 1.5442 | 2.553 | 3.2946 | 3.7805 | 4.0362 | 4.5477 | 5.0591 | 0.92976 | 1.8351 | 2.2021 | 2.2021 | 2.2021 | 2.2021 | 1.3379 | 1.5563 | 1.5563 | 1.5563 | 1.5563 | 1.5563
2020-02-22 12:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 1.046 | 2.0687 | 2.0687 | 2.0687 | 2.0687 | 2.0687 | 2.6151 | 3.3747 | 3.8724 | 4.1344 | 4.6583 | 5.1821 | 0.94119 | 1.8576 | 2.2291 | 2.2291 | 2.2291 | 2.2291 | 1.3908 | 1.6179 | 1.6179 | 1.6179 | 1.6179 | 1.6179
2020-02-22 13:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.98882 | 1.9556 | 1.9556 | 1.9556 | 1.9556 | 1.9556 | 2.6483 | 3.4176 | 3.9216 | 4.1869 | 4.7174 | 5.2479 | 0.95644 | 1.8877 | 2.2652 | 2.2652 | 2.2652 | 2.2652 | 1.2137 | 1.4119 | 1.4119 | 1.4119 | 1.4119 | 1.4119
2020-02-22 14:00 | Summer | 0.55267 | 0.79097 | 1.1414 | 1.1414 | 1.1414 | 1.1414 | 0.98597 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 2.6293 | 3.393 | 3.8934 | 4.1567 | 4.6835 | 5.2102 | 0.94882 | 1.8727 | 2.2472 | 2.2472 | 2.2472 | 2.2472 | 1.1622 | 1.352 | 1.352 | 1.352 | 1.352 | 1.352
2020-02-22 15:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.9431 | 1.8652 | 1.8652 | 1.8652 | 1.8652 | 1.8652 | 2.7055 | 3.4913 | 4.0062 | 4.2772 | 4.8192 | 5.3612 | 0.94119 | 1.8576 | 2.2291 | 2.2291 | 2.2291 | 2.2291 | 1.1813 | 1.3741 | 1.3741 | 1.3741 | 1.3741 | 1.3741
2020-02-22 16:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.98025 | 1.9387 | 1.9387 | 1.9387 | 1.9387 | 1.9387 | 2.6293 | 3.393 | 3.8934 | 4.1567 | 4.6835 | 5.2102 | 1.0288 | 2.0306 | 2.4367 | 2.4367 | 2.4367 | 2.4367 | 1.2003 | 1.3963 | 1.3963 | 1.3963 | 1.3963 | 1.3963
2020-02-22 17:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.97168 | 1.9217 | 1.9217 | 1.9217 | 1.9217 | 1.9217 | 2.6483 | 3.4176 | 3.9216 | 4.1869 | 4.7174 | 5.2479 | 1.0822 | 2.1359 | 2.5631 | 2.5631 | 2.5631 | 2.5631 | 1.086 | 1.2633 | 1.2633 | 1.2633 | 1.2633 | 1.2633
2020-02-22 18:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 1.0145 | 2.0065 | 2.0065 | 2.0065 | 2.0065 | 2.0065 | 2.5372 | 3.2742 | 3.7571 | 4.0112 | 4.5195 | 5.0278 | 1.0669 | 2.1058 | 2.527 | 2.527 | 2.527 | 2.527 | 1.0479 | 1.219 | 1.219 | 1.219 | 1.219 | 1.219
2020-02-22 19:00 | Summer | 0.57331 | 0.8205 | 1.184 | 1.184 | 1.184 | 1.184 | 1.0003 | 1.9783 | 1.9783 | 1.9783 | 1.9783 | 1.9783 | 2.4578 | 3.1717 | 3.6395 | 3.8856 | 4.378 | 4.8704 | 1.0555 | 2.0832 | 2.4999 | 2.4999 | 2.4999 | 2.4999 | 1.0288 | 1.1968 | 1.1968 | 1.1968 | 1.1968 | 1.1968
2020-02-22 20:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.88594 | 1.7522 | 1.7522 | 1.7522 | 1.7522 | 1.7522 | 2.4006 | 3.098 | 3.5548 | 3.7953 | 4.2762 | 4.7571 | 1.0403 | 2.0532 | 2.4638 | 2.4638 | 2.4638 | 2.4638 | 1.0669 | 1.2411 | 1.2411 | 1.2411 | 1.2411 | 1.2411
2020-02-22 21:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.78877 | 1.56 | 1.56 | 1.56 | 1.56 | 1.56 | 2.4006 | 3.098 | 3.5548 | 3.7953 | 4.2762 | 4.7571 | 0.99073 | 1.9554 | 2.3465 | 2.3465 | 2.3465 | 2.3465 | 1.0669 | 1.2411 | 1.2411 | 1.2411 | 1.2411 | 1.2411
2020-02-22 22:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.7459 | 1.4752 | 1.4752 | 1.4752 | 1.4752 | 1.4752 | 2.3054 | 2.975 | 3.4138 | 3.6447 | 4.1065 | 4.5683 | 0.96406 | 1.9027 | 2.2833 | 2.2833 | 2.2833 | 2.2833 | 0.97168 | 1.1303 | 1.1303 | 1.1303 | 1.1303 | 1.1303
2020-02-22 23:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.594 | 1.1748 | 1.1748 | 1.1748 | 1.1748 | 1.1748 | 2.2291 | 2.8767 | 3.3009 | 3.5242 | 3.9708 | 4.4173 | 0.89928 | 1.7749 | 2.1299 | 2.1299 | 2.1299 | 2.1299 | 0.95263 | 1.1082 | 1.1082 | 1.1082 | 1.1082 | 1.1082
2020-02-23 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.48012 | 0.94956 | 0.94956 | 0.94956 | 0.94956 | 0.94956 | 2.0386 | 2.6308 | 3.0188 | 3.223 | 3.6314 | 4.0398 | 0.77353 | 1.5267 | 1.832 | 1.832 | 1.832 | 1.832 | 0.95263 | 1.1082 | 1.1082 | 1.1082 | 1.1082 | 1.1082
2020-02-23 01:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.48584 | 0.96086 | 0.96086 | 0.96086 | 0.96086 | 0.96086 | 1.9053 | 2.4587 | 2.8213 | 3.0121 | 3.3938 | 3.7755 | 0.66303 | 1.3086 | 1.5703 | 1.5703 | 1.5703 | 1.5703 | 0.93358 | 1.086 | 1.086 | 1.086 | 1.086 | 1.086
2020-02-23 02:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.41725 | 0.82521 | 0.82521 | 0.82521 | 0.82521 | 0.82521 | 1.7909 | 2.3112 | 2.652 | 2.8314 | 3.1902 | 3.549 | 0.65541 | 1.2936 | 1.5523 | 1.5523 | 1.5523 | 1.5523 | 0.97168 | 1.1303 | 1.1303 | 1.1303 | 1.1303 | 1.1303
2020-02-23 03:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.39738 | 0.78591 | 0.78591 | 0.78591 | 0.78591 | 0.78591 | 1.7909 | 2.3112 | 2.652 | 2.8314 | 3.1902 | 3.549 | 0.63635 | 1.256 | 1.5072 | 1.5072 | 1.5072 | 1.5072 | 0.89547 | 1.0417 | 1.0417 | 1.0417 | 1.0417 | 1.0417
2020-02-23 04:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.43725 | 0.86478 | 0.86478 | 0.86478 | 0.86478 | 0.86478 | 1.829 | 2.3603 | 2.7084 | 2.8916 | 3.2581 | 3.6245 | 0.64397 | 1.271 | 1.5252 | 1.5252 | 1.5252 | 1.5252 | 0.87642 | 1.0195 | 1.0195 | 1.0195 | 1.0195 | 1.0195
2020-02-23 05:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.42296 | 0.83652 | 0.83652 | 0.83652 | 0.83652 | 0.83652 | 1.8481 | 2.3849 | 2.7366 | 2.9218 | 3.292 | 3.6622 | 0.73543 | 1.4515 | 1.7418 | 1.7418 | 1.7418 | 1.7418 | 0.87642 | 1.0195 | 1.0195 | 1.0195 | 1.0195 | 1.0195
2020-02-23 06:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.53442 | 1.057 | 1.057 | 1.057 | 1.057 | 1.057 | 1.8862 | 2.4341 | 2.7931 | 2.982 | 3.3599 | 3.7377 | 0.78496 | 1.5493 | 1.8591 | 1.8591 | 1.8591 | 1.8591 | 0.87642 | 1.0195 | 1.0195 | 1.0195 | 1.0195 | 1.0195
2020-02-23 07:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.57157 | 1.1304 | 1.1304 | 1.1304 | 1.1304 | 1.1304 | 2.1148 | 2.7291 | 3.1316 | 3.3435 | 3.7671 | 4.1908 | 0.81926 | 1.617 | 1.9403 | 1.9403 | 1.9403 | 1.9403 | 0.89547 | 1.0417 | 1.0417 | 1.0417 | 1.0417 | 1.0417
2020-02-23 08:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.53442 | 1.057 | 1.057 | 1.057 | 1.057 | 1.057 | 2.3435 | 3.0242 | 3.4702 | 3.7049 | 4.1744 | 4.6438 | 0.89547 | 1.7674 | 2.1208 | 2.1208 | 2.1208 | 2.1208 | 0.95263 | 1.1082 | 1.1082 | 1.1082 | 1.1082 | 1.1082
2020-02-23 09:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.58586 | 1.1587 | 1.1587 | 1.1587 | 1.1587 | 1.1587 | 2.3625 | 3.0488 | 3.4984 | 3.735 | 4.2083 | 4.6816 | 0.98311 | 1.9403 | 2.3284 | 2.3284 | 2.3284 | 2.3284 | 1.0098 | 1.1746 | 1.1746 | 1.1746 | 1.1746 | 1.1746
2020-02-23 10:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.87165 | 1.7239 | 1.7239 | 1.7239 | 1.7239 | 1.7239 | 2.534 | 3.2701 | 3.7523 | 4.0061 | 4.5138 | 5.0214 | 0.94501 | 1.8651 | 2.2382 | 2.2382 | 2.2382 | 2.2382 | 0.97168 | 1.1303 | 1.1303 | 1.1303 | 1.1303 | 1.1303
2020-02-23 11:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.91738 | 1.8143 | 1.8143 | 1.8143 | 1.8143 | 1.8143 | 2.7245 | 3.5159 | 4.0344 | 4.3073 | 4.8531 | 5.3989 | 0.95263 | 1.8802 | 2.2562 | 2.2562 | 2.2562 | 2.2562 | 0.97168 | 1.1303 | 1.1303 | 1.1303 | 1.1303 | 1.1303
2020-02-23 12:00 | Summer | 0.57179 | 0.81832 | 1.1809 | 1.1809 | 1.1809 | 1.1809 | 0.83164 | 1.6448 | 1.6448 | 1.6448 | 1.6448 | 1.6448 | 2.6598 | 3.4324 | 3.9386 | 4.205 | 4.7379 | 5.2707 | 0.92595 | 1.8275 | 2.193 | 2.193 | 2.193 | 2.193 | 1.0098 | 1.1746 | 1.1746 | 1.1746 | 1.1746 | 1.1746
2020-02-23 13:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.79163 | 1.5656 | 1.5656 | 1.5656 | 1.5656 | 1.5656 | 2.8007 | 3.6143 | 4.1473 | 4.4278 | 4.9889 | 5.55 | 0.96787 | 1.9103 | 2.2923 | 2.2923 | 2.2923 | 2.2923 | 1.0098 | 1.1746 | 1.1746 | 1.1746 | 1.1746 | 1.1746
2020-02-23 14:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.92595 | 1.8313 | 1.8313 | 1.8313 | 1.8313 | 1.8313 | 2.7245 | 3.5159 | 4.0344 | 4.3073 | 4.8531 | 5.3989 | 0.95644 | 1.8877 | 2.2652 | 2.2652 | 2.2652 | 2.2652 | 1.0098 | 1.1746 | 1.1746 | 1.1746 | 1.1746 | 1.1746
2020-02-23 15:00 | Summer | 0.57643 | 0.82496 | 1.1905 | 1.1905 | 1.1905 | 1.1905 | 0.8545 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 2.7245 | 3.5159 | 4.0344 | 4.3073 | 4.8531 | 5.3989 | 0.93357 | 1.8426 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 1.0288 | 1.1968 | 1.1968 | 1.1968 | 1.1968 | 1.1968
2020-02-23 16:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.80592 | 1.5939 | 1.5939 | 1.5939 | 1.5939 | 1.5939 | 2.7245 | 3.5159 | 4.0344 | 4.3073 | 4.8531 | 5.3989 | 0.97549 | 1.9253 | 2.3104 | 2.3104 | 2.3104 | 2.3104 | 1.0098 | 1.1746 | 1.1746 | 1.1746 | 1.1746 | 1.1746
2020-02-23 17:00 | Summer | 0.66684 | 0.95435 | 1.3772 | 1.3772 | 1.3772 | 1.3772 | 0.77448 | 1.5317 | 1.5317 | 1.5317 | 1.5317 | 1.5317 | 2.6863 | 3.4666 | 3.9778 | 4.2469 | 4.785 | 5.3232 | 1.006 | 1.9855 | 2.3826 | 2.3826 | 2.3826 | 2.3826 | 1.0669 | 1.2411 | 1.2411 | 1.2411 | 1.2411 | 1.2411
2020-02-23 18:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.81735 | 1.6165 | 1.6165 | 1.6165 | 1.6165 | 1.6165 | 2.7626 | 3.5651 | 4.0909 | 4.3676 | 4.921 | 5.4745 | 0.93738 | 1.8501 | 2.2201 | 2.2201 | 2.2201 | 2.2201 | 1.086 | 1.2633 | 1.2633 | 1.2633 | 1.2633 | 1.2633
2020-02-23 19:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.76019 | 1.5035 | 1.5035 | 1.5035 | 1.5035 | 1.5035 | 2.5721 | 3.3192 | 3.8087 | 4.0664 | 4.5816 | 5.0969 | 0.93738 | 1.8501 | 2.2201 | 2.2201 | 2.2201 | 2.2201 | 1.0098 | 1.1746 | 1.1746 | 1.1746 | 1.1746 | 1.1746
2020-02-23 20:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.73447 | 1.4526 | 1.4526 | 1.4526 | 1.4526 | 1.4526 | 2.4768 | 3.1963 | 3.6677 | 3.9158 | 4.4119 | 4.9081 | 0.95263 | 1.8802 | 2.2562 | 2.2562 | 2.2562 | 2.2562 | 1.0669 | 1.2411 | 1.2411 | 1.2411 | 1.2411 | 1.2411
2020-02-23 21:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.68017 | 1.3452 | 1.3452 | 1.3452 | 1.3452 | 1.3452 | 2.4427 | 3.1522 | 3.6171 | 3.8618 | 4.3511 | 4.8405 | 1.0174 | 2.008 | 2.4096 | 2.4096 | 2.4096 | 2.4096 | 1.086 | 1.2633 | 1.2633 | 1.2633 | 1.2633 | 1.2633
2020-02-23 22:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.61444 | 1.2152 | 1.2152 | 1.2152 | 1.2152 | 1.2152 | 2.2482 | 2.9013 | 3.3291 | 3.5543 | 4.0047 | 4.4551 | 0.9793 | 1.9328 | 2.3194 | 2.3194 | 2.3194 | 2.3194 | 0.97168 | 1.1303 | 1.1303 | 1.1303 | 1.1303 | 1.1303
2020-02-23 23:00 | Summer | 0.58233 | 0.8334 | 1.2026 | 1.2026 | 1.2026 | 1.2026 | 0.71733 | 1.4187 | 1.4187 | 1.4187 | 1.4187 | 1.4187 | 2.1529 | 2.7783 | 3.1881 | 3.4037 | 3.835 | 4.2663 | 0.9069 | 1.7899 | 2.1479 | 2.1479 | 2.1479 | 2.1479 | 0.97168 | 1.1303 | 1.1303 | 1.1303 | 1.1303 | 1.1303
2020-02-24 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.56586 | 1.1191 | 1.1191 | 1.1191 | 1.1191 | 1.1191 | 1.9627 | 2.5328 | 2.9064 | 3.103 | 3.4962 | 3.8893 | 0.70113 | 1.3838 | 1.6606 | 1.6606 | 1.6606 | 1.6606 | 0.92684 | 1.0782 | 1.0782 | 1.0782 | 1.0782 | 1.0782
2020-02-24 01:00 | Summer | 0.54809 | 0.7844 | 1.1319 | 1.1319 | 1.1319 | 1.1319 | 0.49441 | 0.97782 | 0.97782 | 0.97782 | 0.97782 | 0.97782 | 1.8862 | 2.4341 | 2.7931 | 2.982 | 3.3599 | 3.7377 | 0.6897 | 1.3613 | 1.6335 | 1.6335 | 1.6335 | 1.6335 | 0.95263 | 1.1082 | 1.1082 | 1.1082 | 1.1082 | 1.1082
2020-02-24 02:00 | Summer | 0.57264 | 0.81955 | 1.1826 | 1.1826 | 1.1826 | 1.1826 | 0.47155 | 0.9326 | 0.9326 | 0.9326 | 0.9326 | 0.9326 | 1.8481 | 2.3849 | 2.7366 | 2.9218 | 3.292 | 3.6622 | 0.62873 | 1.2409 | 1.4891 | 1.4891 | 1.4891 | 1.4891 | 0.89547 | 1.0417 | 1.0417 | 1.0417 | 1.0417 | 1.0417
2020-02-24 03:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.46297 | 0.91565 | 0.91565 | 0.91565 | 0.91565 | 0.91565 | 1.8387 | 2.3728 | 2.7227 | 2.9069 | 3.2752 | 3.6435 | 0.63254 | 1.2484 | 1.4981 | 1.4981 | 1.4981 | 1.4981 | 0.94499 | 1.0993 | 1.0993 | 1.0993 | 1.0993 | 1.0993
2020-02-24 04:00 | Summer | 0.78115 | 1.118 | 1.6133 | 1.6133 | 1.6133 | 1.6133 | 0.55443 | 1.0965 | 1.0965 | 1.0965 | 1.0965 | 1.0965 | 1.8394 | 2.3737 | 2.7238 | 2.908 | 3.2765 | 3.645 | 0.65166 | 1.2862 | 1.5434 | 1.5434 | 1.5434 | 1.5434 | 1.0098 | 1.1746 | 1.1746 | 1.1746 | 1.1746 | 1.1746
2020-02-24 05:00 | Summer | 0.89547 | 1.2816 | 1.8493 | 1.8493 | 1.8493 | 1.8493 | 0.6256 | 1.2373 | 1.2373 | 1.2373 | 1.2373 | 1.2373 | 2.022 | 2.6093 | 2.9942 | 3.1967 | 3.6018 | 4.0068 | 0.90325 | 1.7827 | 2.1393 | 2.1393 | 2.1393 | 2.1393 | 1.1862 | 1.3798 | 1.3798 | 1.3798 | 1.3798 | 1.3798
2020-02-24 06:00 | Summer | 1.1127 | 1.5924 | 2.2979 | 2.2979 | 2.2979 | 2.2979 | 0.75734 | 1.4978 | 1.4978 | 1.4978 | 1.4978 | 1.4978 | 2.2863 | 2.9504 | 3.3855 | 3.6146 | 4.0726 | 4.5306 | 0.92595 | 1.8275 | 2.193 | 2.193 | 2.193 | 2.193 | 1.3337 | 1.5514 | 1.5514 | 1.5514 | 1.5514 | 1.5514
2020-02-24 07:00 | Summer | 1.9624 | 2.8085 | 4.0528 | 4.0528 | 4.0528 | 4.0528 | 1.1117 | 2.1987 | 2.1987 | 2.1987 | 2.1987 | 2.1987 | 2.8334 | 3.6564 | 4.1956 | 4.4794 | 5.047 | 5.6146 | 1.1584 | 2.2863 | 2.7436 | 2.7436 | 2.7436 | 2.7436 | 1.988 | 2.3126 | 2.3126 | 2.3126 | 2.3126 | 2.3126
2020-02-24 08:00 | Summer | 2.0005 | 2.8631 | 4.1315 | 4.1315 | 4.1315 | 4.1315 | 1.1489 | 2.2722 | 2.2722 | 2.2722 | 2.2722 | 2.2722 | 3.2008 | 4.1306 | 4.7398 | 5.0604 | 5.7016 | 6.3428 | 1.1698 | 2.3089 | 2.7706 | 2.7706 | 2.7706 | 2.7706 | 2.4197 | 2.8147 | 2.8147 | 2.8147 | 2.8147 | 2.8147
2020-02-24 09:00 | Summer | 2.1705 | 3.1063 | 4.4825 | 4.4825 | 4.4825 | 4.4825 | 1.3432 | 2.6565 | 2.6565 | 2.6565 | 2.6565 | 2.6565 | 3.4295 | 4.4256 | 5.0783 | 5.4218 | 6.1088 | 6.7959 | 1.1774 | 2.3239 | 2.7887 | 2.7887 | 2.7887 | 2.7887 | 2.7626 | 3.2137 | 3.2137 | 3.2137 | 3.2137 | 3.2137
2020-02-24 10:00 | Summer | 2.2101 | 3.163 | 4.5643 | 4.5643 | 4.5643 | 4.5643 | 1.4004 | 2.7696 | 2.7696 | 2.7696 | 2.7696 | 2.7696 | 3.7724 | 4.8682 | 5.5861 | 5.964 | 6.7197 | 7.4755 | 1.1622 | 2.2938 | 2.7526 | 2.7526 | 2.7526 | 2.7526 | 2.8579 | 3.3245 | 3.3245 | 3.3245 | 3.3245 | 3.3245
2020-02-24 11:00 | Summer | 2.2482 | 3.2175 | 4.643 | 4.643 | 4.643 | 4.643 | 1.4118 | 2.7922 | 2.7922 | 2.7922 | 2.7922 | 2.7922 | 3.7534 | 4.8436 | 5.5579 | 5.9339 | 6.6858 | 7.4377 | 1.1889 | 2.3465 | 2.8158 | 2.8158 | 2.8158 | 2.8158 | 2.9913 | 3.4796 | 3.4796 | 3.4796 | 3.4796 | 3.4796
2020-02-24 12:00 | Summer | 2.4387 | 3.4902 | 5.0365 | 5.0365 | 5.0365 | 5.0365 | 1.5433 | 3.0522 | 3.0522 | 3.0522 | 3.0522 | 3.0522 | 3.9629 | 5.1141 | 5.8683 | 6.2652 | 7.0591 | 7.853 | 1.1851 | 2.3389 | 2.8067 | 2.8067 | 2.8067 | 2.8067 | 3.1056 | 3.6126 | 3.6126 | 3.6126 | 3.6126 | 3.6126
2020-02-24 13:00 | Summer | 2.277 | 3.2587 | 4.7025 | 4.7025 | 4.7025 | 4.7025 | 1.5604 | 3.0861 | 3.0861 | 3.0861 | 3.0861 | 3.0861 | 3.9629 | 5.1141 | 5.8683 | 6.2652 | 7.0591 | 7.853 | 1.2003 | 2.369 | 2.8428 | 2.8428 | 2.8428 | 2.8428 | 3.1246 | 3.6348 | 3.6348 | 3.6348 | 3.6348 | 3.6348
2020-02-24 14:00 | Summer | 2.3244 | 3.3266 | 4.8004 | 4.8004 | 4.8004 | 4.8004 | 1.4975 | 2.9617 | 2.9617 | 2.9617 | 2.9617 | 2.9617 | 3.9058 | 5.0403 | 5.7836 | 6.1749 | 6.9573 | 7.7397 | 1.2232 | 2.4142 | 2.897 | 2.897 | 2.897 | 2.897 | 3.0619 | 3.5618 | 3.5618 | 3.5618 | 3.5618 | 3.5618
2020-02-24 15:00 | Summer | 2.2863 | 3.2721 | 4.7217 | 4.7217 | 4.7217 | 4.7217 | 1.5204 | 3.007 | 3.007 | 3.007 | 3.007 | 3.007 | 3.8486 | 4.9666 | 5.699 | 6.0845 | 6.8555 | 7.6265 | 1.2156 | 2.3991 | 2.8789 | 2.8789 | 2.8789 | 2.8789 | 2.8579 | 3.3245 | 3.3245 | 3.3245 | 3.3245 | 3.3245
2020-02-24 16:00 | Summer | 2.2101 | 3.163 | 4.5643 | 4.5643 | 4.5643 | 4.5643 | 1.549 | 3.0635 | 3.0635 | 3.0635 | 3.0635 | 3.0635 | 3.9248 | 5.0649 | 5.8119 | 6.205 | 6.9912 | 7.7775 | 1.2308 | 2.4292 | 2.915 | 2.915 | 2.915 | 2.915 | 2.915 | 3.391 | 3.391 | 3.391 | 3.391 | 3.391
2020-02-24 17:00 | Summer | 1.9815 | 2.8358 | 4.0922 | 4.0922 | 4.0922 | 4.0922 | 1.5271 | 3.0203 | 3.0203 | 3.0203 | 3.0203 | 3.0203 | 3.8867 | 5.0157 | 5.7554 | 6.1447 | 6.9234 | 7.702 | 1.1889 | 2.3465 | 2.8158 | 2.8158 | 2.8158 | 2.8158 | 2.8075 | 3.2659 | 3.2659 | 3.2659 | 3.2659 | 3.2659
2020-02-24 18:00 | Summer | 1.3155 | 1.8827 | 2.7169 | 2.7169 | 2.7169 | 2.7169 | 1.106 | 2.1874 | 2.1874 | 2.1874 | 2.1874 | 2.1874 | 3.62 | 4.6715 | 5.3604 | 5.723 | 6.4482 | 7.1734 | 1.1508 | 2.2713 | 2.7255 | 2.7255 | 2.7255 | 2.7255 | 1.9714 | 2.2933 | 2.2933 | 2.2933 | 2.2933 | 2.2933
2020-02-24 19:00 | Summer | 0.7621 | 1.0907 | 1.5739 | 1.5739 | 1.5739 | 1.5739 | 0.83736 | 1.6561 | 1.6561 | 1.6561 | 1.6561 | 1.6561 | 2.9808 | 3.8467 | 4.414 | 4.7126 | 5.3097 | 5.9069 | 1.1089 | 2.1885 | 2.6262 | 2.6262 | 2.6262 | 2.6262 | 1.3146 | 1.5293 | 1.5293 | 1.5293 | 1.5293 | 1.5293
2020-02-24 20:00 | Summer | 0.70494 | 1.0089 | 1.4559 | 1.4559 | 1.4559 | 1.4559 | 0.70589 | 1.3961 | 1.3961 | 1.3961 | 1.3961 | 1.3961 | 2.6864 | 3.4668 | 3.978 | 4.2471 | 4.7853 | 5.3234 | 1.0936 | 2.1585 | 2.5901 | 2.5901 | 2.5901 | 2.5901 | 1.2194 | 1.4184 | 1.4184 | 1.4184 | 1.4184 | 1.4184
2020-02-24 21:00 | Summer | 0.61534 | 0.88065 | 1.2708 | 1.2708 | 1.2708 | 1.2708 | 0.69446 | 1.3735 | 1.3735 | 1.3735 | 1.3735 | 1.3735 | 2.553 | 3.2946 | 3.7805 | 4.0362 | 4.5477 | 5.0591 | 1.0441 | 2.0607 | 2.4728 | 2.4728 | 2.4728 | 2.4728 | 1.086 | 1.2633 | 1.2633 | 1.2633 | 1.2633 | 1.2633
2020-02-24 22:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.66588 | 1.317 | 1.317 | 1.317 | 1.317 | 1.317 | 2.4768 | 3.1963 | 3.6677 | 3.9158 | 4.4119 | 4.9081 | 1.0136 | 2.0005 | 2.4006 | 2.4006 | 2.4006 | 2.4006 | 1.0098 | 1.1746 | 1.1746 | 1.1746 | 1.1746 | 1.1746
2020-02-24 23:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.53156 | 1.0513 | 1.0513 | 1.0513 | 1.0513 | 1.0513 | 2.2291 | 2.8767 | 3.3009 | 3.5242 | 3.9708 | 4.4173 | 0.91833 | 1.8125 | 2.175 | 2.175 | 2.175 | 2.175 | 0.99073 | 1.1525 | 1.1525 | 1.1525 | 1.1525 | 1.1525
2020-02-25 | Summer | 0.57197 | 0.81858 | 1.1812 | 1.1812 | 1.1812 | 1.1812 | 0.52299 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 2.0005 | 2.5816 | 2.9624 | 3.1627 | 3.5635 | 3.9643 | 0.71637 | 1.4139 | 1.6967 | 1.6967 | 1.6967 | 1.6967 | 0.99073 | 1.1525 | 1.1525 | 1.1525 | 1.1525 | 1.1525
2020-02-25 01:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.54585 | 1.0796 | 1.0796 | 1.0796 | 1.0796 | 1.0796 | 1.9434 | 2.5079 | 2.8777 | 3.0724 | 3.4617 | 3.851 | 0.67446 | 1.3312 | 1.5974 | 1.5974 | 1.5974 | 1.5974 | 0.97168 | 1.1303 | 1.1303 | 1.1303 | 1.1303 | 1.1303
2020-02-25 02:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.47441 | 0.93825 | 0.93825 | 0.93825 | 0.93825 | 0.93825 | 1.8862 | 2.4341 | 2.7931 | 2.982 | 3.3599 | 3.7377 | 0.6516 | 1.286 | 1.5433 | 1.5433 | 1.5433 | 1.5433 | 0.95263 | 1.1082 | 1.1082 | 1.1082 | 1.1082 | 1.1082
2020-02-25 03:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.49441 | 0.97782 | 0.97782 | 0.97782 | 0.97782 | 0.97782 | 1.8481 | 2.3849 | 2.7366 | 2.9218 | 3.292 | 3.6622 | 0.64016 | 1.2635 | 1.5162 | 1.5162 | 1.5162 | 1.5162 | 0.89547 | 1.0417 | 1.0417 | 1.0417 | 1.0417 | 1.0417
2020-02-25 04:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.55443 | 1.0965 | 1.0965 | 1.0965 | 1.0965 | 1.0965 | 1.9053 | 2.4587 | 2.8213 | 3.0121 | 3.3938 | 3.7755 | 0.68589 | 1.3537 | 1.6245 | 1.6245 | 1.6245 | 1.6245 | 0.99073 | 1.1525 | 1.1525 | 1.1525 | 1.1525 | 1.1525
2020-02-25 05:00 | Summer | 0.89547 | 1.2816 | 1.8493 | 1.8493 | 1.8493 | 1.8493 | 0.58015 | 1.1474 | 1.1474 | 1.1474 | 1.1474 | 1.1474 | 1.9243 | 2.4833 | 2.8495 | 3.0422 | 3.4277 | 3.8132 | 0.89166 | 1.7599 | 2.1118 | 2.1118 | 2.1118 | 2.1118 | 1.1813 | 1.3741 | 1.3741 | 1.3741 | 1.3741 | 1.3741
2020-02-25 06:00 | Summer | 0.84368 | 1.2074 | 1.7424 | 1.7424 | 1.7424 | 1.7424 | 0.79449 | 1.5713 | 1.5713 | 1.5713 | 1.5713 | 1.5713 | 2.2451 | 2.8973 | 3.3245 | 3.5494 | 3.9992 | 4.4489 | 0.96657 | 1.9077 | 2.2892 | 2.2892 | 2.2892 | 2.2892 | 1.2568 | 1.4619 | 1.4619 | 1.4619 | 1.4619 | 1.4619
2020-02-25 07:00 | Summer | 1.5814 | 2.2632 | 3.2659 | 3.2659 | 3.2659 | 3.2659 | 0.99168 | 1.9613 | 1.9613 | 1.9613 | 1.9613 | 1.9613 | 2.8388 | 3.6634 | 4.2037 | 4.4881 | 5.0568 | 5.6255 | 1.2918 | 2.5495 | 3.0594 | 3.0594 | 3.0594 | 3.0594 | 1.8832 | 2.1906 | 2.1906 | 2.1906 | 2.1906 | 2.1906
2020-02-25 08:00 | Summer | 1.9624 | 2.8085 | 4.0528 | 4.0528 | 4.0528 | 4.0528 | 0.99168 | 1.9613 | 1.9613 | 1.9613 | 1.9613 | 1.9613 | 3.1056 | 4.0077 | 4.5987 | 4.9098 | 5.5319 | 6.154 | 1.2918 | 2.5495 | 3.0594 | 3.0594 | 3.0594 | 3.0594 | 2.4578 | 2.8591 | 2.8591 | 2.8591 | 2.8591 | 2.8591
2020-02-25 09:00 | Summer | 2.0832 | 2.9813 | 4.3022 | 4.3022 | 4.3022 | 4.3022 | 1.3232 | 2.617 | 2.617 | 2.617 | 2.617 | 2.617 | 3.4104 | 4.4011 | 5.0501 | 5.3917 | 6.0749 | 6.7581 | 1.2994 | 2.5646 | 3.0775 | 3.0775 | 3.0775 | 3.0775 | 2.7626 | 3.2137 | 3.2137 | 3.2137 | 3.2137 | 3.2137
2020-02-25 10:00 | Summer | 2.2101 | 3.163 | 4.5643 | 4.5643 | 4.5643 | 4.5643 | 1.3775 | 2.7243 | 2.7243 | 2.7243 | 2.7243 | 2.7243 | 3.7534 | 4.8436 | 5.5579 | 5.9339 | 6.6858 | 7.4377 | 1.1927 | 2.354 | 2.8248 | 2.8248 | 2.8248 | 2.8248 | 2.8579 | 3.3245 | 3.3245 | 3.3245 | 3.3245 | 3.3245
2020-02-25 11:00 | Summer | 2.2101 | 3.163 | 4.5643 | 4.5643 | 4.5643 | 4.5643 | 1.3861 | 2.7413 | 2.7413 | 2.7413 | 2.7413 | 2.7413 | 3.7915 | 4.8928 | 5.6144 | 5.9941 | 6.7537 | 7.5132 | 1.1393 | 2.2487 | 2.6984 | 2.6984 | 2.6984 | 2.6984 | 2.915 | 3.391 | 3.391 | 3.391 | 3.391 | 3.391
2020-02-25 12:00 | Summer | 2.1728 | 3.1097 | 4.4874 | 4.4874 | 4.4874 | 4.4874 | 1.4661 | 2.8996 | 2.8996 | 2.8996 | 2.8996 | 2.8996 | 3.9439 | 5.0895 | 5.8401 | 6.2351 | 7.0252 | 7.8153 | 1.2041 | 2.3766 | 2.8519 | 2.8519 | 2.8519 | 2.8519 | 3.0865 | 3.5904 | 3.5904 | 3.5904 | 3.5904 | 3.5904
2020-02-25 13:00 | Summer | 2.2101 | 3.163 | 4.5643 | 4.5643 | 4.5643 | 4.5643 | 1.5404 | 3.0465 | 3.0465 | 3.0465 | 3.0465 | 3.0465 | 4.2106 | 5.4337 | 6.235 | 6.6568 | 7.5003 | 8.3438 | 1.2079 | 2.3841 | 2.8609 | 2.8609 | 2.8609 | 2.8609 | 3.1818 | 3.7013 | 3.7013 | 3.7013 | 3.7013 | 3.7013
2020-02-25 14:00 | Summer | 2.3244 | 3.3266 | 4.8004 | 4.8004 | 4.8004 | 4.8004 | 1.7062 | 3.3743 | 3.3743 | 3.3743 | 3.3743 | 3.3743 | 3.9929 | 5.1528 | 5.9127 | 6.3126 | 7.1125 | 7.9124 | 1.2079 | 2.3841 | 2.8609 | 2.8609 | 2.8609 | 2.8609 | 3.2008 | 3.7234 | 3.7234 | 3.7234 | 3.7234 | 3.7234
2020-02-25 15:00 | Summer | 2.3054 | 3.2993 | 4.7611 | 4.7611 | 4.7611 | 4.7611 | 1.6633 | 3.2896 | 3.2896 | 3.2896 | 3.2896 | 3.2896 | 4.1337 | 5.3344 | 6.1211 | 6.5352 | 7.3633 | 8.1914 | 1.227 | 2.4217 | 2.906 | 2.906 | 2.906 | 2.906 | 3.1246 | 3.6348 | 3.6348 | 3.6348 | 3.6348 | 3.6348
2020-02-25 16:00 | Summer | 2.172 | 3.1085 | 4.4856 | 4.4856 | 4.4856 | 4.4856 | 1.7633 | 3.4874 | 3.4874 | 3.4874 | 3.4874 | 3.4874 | 4.1344 | 5.3354 | 6.1222 | 6.5363 | 7.3646 | 8.1928 | 1.2041 | 2.3766 | 2.8519 | 2.8519 | 2.8519 | 2.8519 | 3.0675 | 3.5683 | 3.5683 | 3.5683 | 3.5683 | 3.5683
2020-02-25 17:00 | Summer | 1.9053 | 2.7267 | 3.9348 | 3.9348 | 3.9348 | 3.9348 | 1.4632 | 2.8939 | 2.8939 | 2.8939 | 2.8939 | 2.8939 | 3.8867 | 5.0157 | 5.7554 | 6.1447 | 6.9234 | 7.702 | 1.1393 | 2.2487 | 2.6984 | 2.6984 | 2.6984 | 2.6984 | 2.9155 | 3.3915 | 3.3915 | 3.3915 | 3.3915 | 3.3915
2020-02-25 18:00 | Summer | 1.4094 | 2.017 | 2.9106 | 2.9106 | 2.9106 | 2.9106 | 1.2024 | 2.3781 | 2.3781 | 2.3781 | 2.3781 | 2.3781 | 3.639 | 4.6961 | 5.3887 | 5.7532 | 6.4822 | 7.2112 | 1.1183 | 2.2072 | 2.6486 | 2.6486 | 2.6486 | 2.6486 | 2.0432 | 2.3767 | 2.3767 | 2.3767 | 2.3767 | 2.3767
2020-02-25 19:00 | Summer | 0.89547 | 1.2816 | 1.8493 | 1.8493 | 1.8493 | 1.8493 | 0.89058 | 1.7613 | 1.7613 | 1.7613 | 1.7613 | 1.7613 | 3.1036 | 4.0051 | 4.5957 | 4.9066 | 5.5283 | 6.15 | 1.1089 | 2.1885 | 2.6262 | 2.6262 | 2.6262 | 2.6262 | 1.2773 | 1.4858 | 1.4858 | 1.4858 | 1.4858 | 1.4858
2020-02-25 20:00 | Summer | 0.85737 | 1.227 | 1.7706 | 1.7706 | 1.7706 | 1.7706 | 0.89166 | 1.7635 | 1.7635 | 1.7635 | 1.7635 | 1.7635 | 2.8198 | 3.6389 | 4.1755 | 4.4579 | 5.0228 | 5.5877 | 1.1317 | 2.2337 | 2.6804 | 2.6804 | 2.6804 | 2.6804 | 1.2194 | 1.4184 | 1.4184 | 1.4184 | 1.4184 | 1.4184
2020-02-25 21:00 | Summer | 0.76311 | 1.0921 | 1.576 | 1.576 | 1.576 | 1.576 | 0.75448 | 1.4922 | 1.4922 | 1.4922 | 1.4922 | 1.4922 | 2.7436 | 3.5405 | 4.0627 | 4.3375 | 4.8871 | 5.4367 | 1.0974 | 2.166 | 2.5992 | 2.5992 | 2.5992 | 2.5992 | 1.0654 | 1.2393 | 1.2393 | 1.2393 | 1.2393 | 1.2393
2020-02-25 22:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.71447 | 1.413 | 1.413 | 1.413 | 1.413 | 1.413 | 2.5476 | 3.2876 | 3.7724 | 4.0276 | 4.538 | 5.0483 | 1.0365 | 2.0456 | 2.4548 | 2.4548 | 2.4548 | 2.4548 | 0.99073 | 1.1525 | 1.1525 | 1.1525 | 1.1525 | 1.1525
2020-02-25 23:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.67731 | 1.3396 | 1.3396 | 1.3396 | 1.3396 | 1.3396 | 2.2863 | 2.9504 | 3.3855 | 3.6146 | 4.0726 | 4.5306 | 0.94501 | 1.8651 | 2.2382 | 2.2382 | 2.2382 | 2.2382 | 0.97168 | 1.1303 | 1.1303 | 1.1303 | 1.1303 | 1.1303
2020-02-26 | Summer | 0.57192 | 0.81851 | 1.1811 | 1.1811 | 1.1811 | 1.1811 | 0.51727 | 1.023 | 1.023 | 1.023 | 1.023 | 1.023 | 2.1133 | 2.7272 | 3.1294 | 3.341 | 3.7644 | 4.1878 | 0.74763 | 1.4756 | 1.7707 | 1.7707 | 1.7707 | 1.7707 | 0.95263 | 1.1082 | 1.1082 | 1.1082 | 1.1082 | 1.1082
2020-02-26 01:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.50584 | 1.0004 | 1.0004 | 1.0004 | 1.0004 | 1.0004 | 2.0196 | 2.6062 | 2.9906 | 3.1929 | 3.5974 | 4.002 | 0.66684 | 1.3161 | 1.5794 | 1.5794 | 1.5794 | 1.5794 | 0.95263 | 1.1082 | 1.1082 | 1.1082 | 1.1082 | 1.1082
2020-02-26 02:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.53156 | 1.0513 | 1.0513 | 1.0513 | 1.0513 | 1.0513 | 1.9815 | 2.557 | 2.9341 | 3.1326 | 3.5296 | 3.9265 | 0.67827 | 1.3387 | 1.6064 | 1.6064 | 1.6064 | 1.6064 | 0.91452 | 1.0638 | 1.0638 | 1.0638 | 1.0638 | 1.0638
2020-02-26 03:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.52016 | 1.0287 | 1.0287 | 1.0287 | 1.0287 | 1.0287 | 1.9624 | 2.5325 | 2.9059 | 3.1025 | 3.4956 | 3.8887 | 0.63635 | 1.256 | 1.5072 | 1.5072 | 1.5072 | 1.5072 | 0.93358 | 1.086 | 1.086 | 1.086 | 1.086 | 1.086
2020-02-26 04:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.62016 | 1.2265 | 1.2265 | 1.2265 | 1.2265 | 1.2265 | 1.9624 | 2.5325 | 2.9059 | 3.1025 | 3.4956 | 3.8887 | 0.6516 | 1.286 | 1.5433 | 1.5433 | 1.5433 | 1.5433 | 1.0288 | 1.1968 | 1.1968 | 1.1968 | 1.1968 | 1.1968
2020-02-26 05:00 | Summer | 0.74278 | 1.063 | 1.534 | 1.534 | 1.534 | 1.534 | 0.69732 | 1.3791 | 1.3791 | 1.3791 | 1.3791 | 1.3791 | 2.0468 | 2.6413 | 3.0308 | 3.2358 | 3.6459 | 4.0559 | 1.0098 | 1.993 | 2.3916 | 2.3916 | 2.3916 | 2.3916 | 1.2572 | 1.4624 | 1.4624 | 1.4624 | 1.4624 | 1.4624
2020-02-26 06:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.99888 | 1.9755 | 1.9755 | 1.9755 | 1.9755 | 1.9755 | 2.3405 | 3.0203 | 3.4657 | 3.7002 | 4.169 | 4.6379 | 1.1279 | 2.2261 | 2.6714 | 2.6714 | 2.6714 | 2.6714 | 1.5518 | 1.8052 | 1.8052 | 1.8052 | 1.8052 | 1.8052
2020-02-26 07:00 | Summer | 1.9779 | 2.8307 | 4.0848 | 4.0848 | 4.0848 | 4.0848 | 1.0688 | 2.1139 | 2.1139 | 2.1139 | 2.1139 | 2.1139 | 2.9913 | 3.8601 | 4.4294 | 4.729 | 5.3283 | 5.9275 | 1.2384 | 2.4442 | 2.9331 | 2.9331 | 2.9331 | 2.9331 | 2.1299 | 2.4776 | 2.4776 | 2.4776 | 2.4776 | 2.4776
2020-02-26 08:00 | Summer | 2.172 | 3.1085 | 4.4856 | 4.4856 | 4.4856 | 4.4856 | 1.2734 | 2.5186 | 2.5186 | 2.5186 | 2.5186 | 2.5186 | 3.4295 | 4.4256 | 5.0783 | 5.4218 | 6.1088 | 6.7959 | 1.1508 | 2.2713 | 2.7255 | 2.7255 | 2.7255 | 2.7255 | 2.6915 | 3.1309 | 3.1309 | 3.1309 | 3.1309 | 3.1309
2020-02-26 09:00 | Summer | 1.9053 | 2.7267 | 3.9348 | 3.9348 | 3.9348 | 3.9348 | 1.3346 | 2.6396 | 2.6396 | 2.6396 | 2.6396 | 2.6396 | 3.4866 | 4.4994 | 5.163 | 5.5122 | 6.2107 | 6.9091 | 1.1851 | 2.3389 | 2.8067 | 2.8067 | 2.8067 | 2.8067 | 2.7055 | 3.1472 | 3.1472 | 3.1472 | 3.1472 | 3.1472
2020-02-26 10:00 | Summer | 2.0215 | 2.8931 | 4.1748 | 4.1748 | 4.1748 | 4.1748 | 1.3575 | 2.6848 | 2.6848 | 2.6848 | 2.6848 | 2.6848 | 3.8105 | 4.9174 | 5.6426 | 6.0243 | 6.7876 | 7.551 | 1.1584 | 2.2863 | 2.7436 | 2.7436 | 2.7436 | 2.7436 | 3.0675 | 3.5683 | 3.5683 | 3.5683 | 3.5683 | 3.5683
2020-02-26 11:00 | Summer | 2.0958 | 2.9994 | 4.3282 | 4.3282 | 4.3282 | 4.3282 | 1.3489 | 2.6678 | 2.6678 | 2.6678 | 2.6678 | 2.6678 | 3.9058 | 5.0403 | 5.7836 | 6.1749 | 6.9573 | 7.7397 | 1.2194 | 2.4066 | 2.888 | 2.888 | 2.888 | 2.888 | 3.3342 | 3.8786 | 3.8786 | 3.8786 | 3.8786 | 3.8786
2020-02-26 12:00 | Summer | 2.0767 | 2.9721 | 4.2889 | 4.2889 | 4.2889 | 4.2889 | 1.4232 | 2.8148 | 2.8148 | 2.8148 | 2.8148 | 2.8148 | 3.8677 | 4.9911 | 5.7272 | 6.1146 | 6.8894 | 7.6642 | 1.1927 | 2.354 | 2.8248 | 2.8248 | 2.8248 | 2.8248 | 3.1246 | 3.6348 | 3.6348 | 3.6348 | 3.6348 | 3.6348
2020-02-26 13:00 | Summer | 1.9787 | 2.8318 | 4.0864 | 4.0864 | 4.0864 | 4.0864 | 1.4375 | 2.843 | 2.843 | 2.843 | 2.843 | 2.843 | 3.9248 | 5.0649 | 5.8119 | 6.205 | 6.9912 | 7.7775 | 1.1813 | 2.3314 | 2.7977 | 2.7977 | 2.7977 | 2.7977 | 3.0484 | 3.5461 | 3.5461 | 3.5461 | 3.5461 | 3.5461
2020-02-26 14:00 | Summer | 1.9053 | 2.7267 | 3.9348 | 3.9348 | 3.9348 | 3.9348 | 1.549 | 3.0635 | 3.0635 | 3.0635 | 3.0635 | 3.0635 | 3.8105 | 4.9174 | 5.6426 | 6.0243 | 6.7876 | 7.551 | 1.1736 | 2.3164 | 2.7797 | 2.7797 | 2.7797 | 2.7797 | 3.0484 | 3.5461 | 3.5461 | 3.5461 | 3.5461 | 3.5461
2020-02-26 15:00 | Summer | 1.8862 | 2.6995 | 3.8954 | 3.8954 | 3.8954 | 3.8954 | 1.5375 | 3.0409 | 3.0409 | 3.0409 | 3.0409 | 3.0409 | 3.7534 | 4.8436 | 5.5579 | 5.9339 | 6.6858 | 7.4377 | 1.147 | 2.2637 | 2.7165 | 2.7165 | 2.7165 | 2.7165 | 3.0294 | 3.5239 | 3.5239 | 3.5239 | 3.5239 | 3.5239
2020-02-26 16:00 | Summer | 1.81 | 2.5904 | 3.738 | 3.738 | 3.738 | 3.738 | 1.4661 | 2.8996 | 2.8996 | 2.8996 | 2.8996 | 2.8996 | 3.7343 | 4.819 | 5.5297 | 5.9038 | 6.6519 | 7.4 | 1.1317 | 2.2337 | 2.6804 | 2.6804 | 2.6804 | 2.6804 | 2.9722 | 3.4575 | 3.4575 | 3.4575 | 3.4575 | 3.4575
2020-02-26 17:00 | Summer | 1.6766 | 2.3995 | 3.4626 | 3.4626 | 3.4626 | 3.4626 | 1.4347 | 2.8374 | 2.8374 | 2.8374 | 2.8374 | 2.8374 | 3.6398 | 4.6971 | 5.3898 | 5.7543 | 6.4835 | 7.2126 | 1.147 | 2.2637 | 2.7165 | 2.7165 | 2.7165 | 2.7165 | 2.7762 | 3.2295 | 3.2295 | 3.2295 | 3.2295 | 3.2295
2020-02-26 18:00 | Summer | 1.2333 | 1.7651 | 2.5471 | 2.5471 | 2.5471 | 2.5471 | 1.1348 | 2.2444 | 2.2444 | 2.2444 | 2.2444 | 2.2444 | 3.3731 | 4.3529 | 4.9949 | 5.3327 | 6.0085 | 6.6842 | 1.147 | 2.2637 | 2.7165 | 2.7165 | 2.7165 | 2.7165 | 2.2863 | 2.6596 | 2.6596 | 2.6596 | 2.6596 | 2.6596
2020-02-26 19:00 | Summer | 0.91452 | 1.3088 | 1.8887 | 1.8887 | 1.8887 | 1.8887 | 0.89166 | 1.7635 | 1.7635 | 1.7635 | 1.7635 | 1.7635 | 3.1437 | 4.0568 | 4.6551 | 4.97 | 5.5998 | 6.2296 | 1.147 | 2.2637 | 2.7165 | 2.7165 | 2.7165 | 2.7165 | 1.4099 | 1.6401 | 1.6401 | 1.6401 | 1.6401 | 1.6401
2020-02-26 20:00 | Summer | 0.7817 | 1.1187 | 1.6144 | 1.6144 | 1.6144 | 1.6144 | 0.75734 | 1.4978 | 1.4978 | 1.4978 | 1.4978 | 1.4978 | 2.6864 | 3.4668 | 3.978 | 4.2471 | 4.7853 | 5.3234 | 1.0555 | 2.0832 | 2.4999 | 2.4999 | 2.4999 | 2.4999 | 1.3718 | 1.5957 | 1.5957 | 1.5957 | 1.5957 | 1.5957
2020-02-26 21:00 | Summer | 0.6099 | 0.87287 | 1.2596 | 1.2596 | 1.2596 | 1.2596 | 0.66874 | 1.3226 | 1.3226 | 1.3226 | 1.3226 | 1.3226 | 2.5911 | 3.3438 | 3.8369 | 4.0965 | 4.6156 | 5.1347 | 1.0784 | 2.1284 | 2.554 | 2.554 | 2.554 | 2.554 | 1.1813 | 1.3741 | 1.3741 | 1.3741 | 1.3741 | 1.3741
2020-02-26 22:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.62016 | 1.2265 | 1.2265 | 1.2265 | 1.2265 | 1.2265 | 2.3625 | 3.0488 | 3.4984 | 3.735 | 4.2083 | 4.6816 | 0.99454 | 1.9629 | 2.3555 | 2.3555 | 2.3555 | 2.3555 | 1.0669 | 1.2411 | 1.2411 | 1.2411 | 1.2411 | 1.2411
2020-02-26 23:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.48869 | 0.96652 | 0.96652 | 0.96652 | 0.96652 | 0.96652 | 2.2482 | 2.9013 | 3.3291 | 3.5543 | 4.0047 | 4.4551 | 0.94501 | 1.8651 | 2.2382 | 2.2382 | 2.2382 | 2.2382 | 0.99073 | 1.1525 | 1.1525 | 1.1525 | 1.1525 | 1.1525
2020-02-27 | Summer | 0.55252 | 0.79075 | 1.1411 | 1.1411 | 1.1411 | 1.1411 | 0.43154 | 0.85347 | 0.85347 | 0.85347 | 0.85347 | 0.85347 | 1.9624 | 2.5325 | 2.9059 | 3.1025 | 3.4956 | 3.8887 | 0.75067 | 1.4816 | 1.7779 | 1.7779 | 1.7779 | 1.7779 | 0.91452 | 1.0638 | 1.0638 | 1.0638 | 1.0638 | 1.0638
2020-02-27 01:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.47441 | 0.93825 | 0.93825 | 0.93825 | 0.93825 | 0.93825 | 1.8672 | 2.4095 | 2.7649 | 2.9519 | 3.3259 | 3.7 | 0.70113 | 1.3838 | 1.6606 | 1.6606 | 1.6606 | 1.6606 | 0.90927 | 1.0577 | 1.0577 | 1.0577 | 1.0577 | 1.0577
2020-02-27 02:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.385 | 0.76144 | 0.76144 | 0.76144 | 0.76144 | 0.76144 | 1.9624 | 2.5325 | 2.9059 | 3.1025 | 3.4956 | 3.8887 | 0.63635 | 1.256 | 1.5072 | 1.5072 | 1.5072 | 1.5072 | 0.91452 | 1.0638 | 1.0638 | 1.0638 | 1.0638 | 1.0638
2020-02-27 03:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.38771 | 0.76679 | 0.76679 | 0.76679 | 0.76679 | 0.76679 | 1.8481 | 2.3849 | 2.7366 | 2.9218 | 3.292 | 3.6622 | 0.64397 | 1.271 | 1.5252 | 1.5252 | 1.5252 | 1.5252 | 0.89547 | 1.0417 | 1.0417 | 1.0417 | 1.0417 | 1.0417
2020-02-27 04:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.55408 | 1.0958 | 1.0958 | 1.0958 | 1.0958 | 1.0958 | 1.8862 | 2.4341 | 2.7931 | 2.982 | 3.3599 | 3.7377 | 0.64016 | 1.2635 | 1.5162 | 1.5162 | 1.5162 | 1.5162 | 0.97168 | 1.1303 | 1.1303 | 1.1303 | 1.1303 | 1.1303
2020-02-27 05:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.56586 | 1.1191 | 1.1191 | 1.1191 | 1.1191 | 1.1191 | 1.9624 | 2.5325 | 2.9059 | 3.1025 | 3.4956 | 3.8887 | 0.86498 | 1.7072 | 2.0486 | 2.0486 | 2.0486 | 2.0486 | 1.109 | 1.2901 | 1.2901 | 1.2901 | 1.2901 | 1.2901
2020-02-27 06:00 | Summer | 0.70494 | 1.0089 | 1.4559 | 1.4559 | 1.4559 | 1.4559 | 0.7802 | 1.543 | 1.543 | 1.543 | 1.543 | 1.543 | 2.0577 | 2.6554 | 3.047 | 3.2531 | 3.6653 | 4.0775 | 1.0174 | 2.008 | 2.4096 | 2.4096 | 2.4096 | 2.4096 | 1.3338 | 1.5516 | 1.5516 | 1.5516 | 1.5516 | 1.5516
2020-02-27 07:00 | Summer | 1.6385 | 2.345 | 3.3839 | 3.3839 | 3.3839 | 3.3839 | 0.78877 | 1.56 | 1.56 | 1.56 | 1.56 | 1.56 | 2.6864 | 3.4668 | 3.978 | 4.2471 | 4.7853 | 5.3234 | 1.246 | 2.4593 | 2.9511 | 2.9511 | 2.9511 | 2.9511 | 1.7528 | 2.039 | 2.039 | 2.039 | 2.039 | 2.039
2020-02-27 08:00 | Summer | 1.7305 | 2.4766 | 3.5739 | 3.5739 | 3.5739 | 3.5739 | 1.0631 | 2.1026 | 2.1026 | 2.1026 | 2.1026 | 2.1026 | 3.0103 | 3.8847 | 4.4576 | 4.7592 | 5.3622 | 5.9653 | 1.2384 | 2.4442 | 2.9331 | 2.9331 | 2.9331 | 2.9331 | 2.3054 | 2.6817 | 2.6817 | 2.6817 | 2.6817 | 2.6817
2020-02-27 09:00 | Summer | 1.7909 | 2.5631 | 3.6987 | 3.6987 | 3.6987 | 3.6987 | 1.1746 | 2.323 | 2.323 | 2.323 | 2.323 | 2.323 | 3.1818 | 4.106 | 4.7115 | 5.0303 | 5.6677 | 6.3051 | 1.227 | 2.4217 | 2.906 | 2.906 | 2.906 | 2.906 | 2.4006 | 2.7926 | 2.7926 | 2.7926 | 2.7926 | 2.7926
2020-02-27 10:00 | Summer | 1.829 | 2.6177 | 3.7774 | 3.7774 | 3.7774 | 3.7774 | 1.1689 | 2.3117 | 2.3117 | 2.3117 | 2.3117 | 2.3117 | 3.2199 | 4.1552 | 4.768 | 5.0905 | 5.7355 | 6.3806 | 1.2689 | 2.5044 | 3.0053 | 3.0053 | 3.0053 | 3.0053 | 2.5149 | 2.9255 | 2.9255 | 2.9255 | 2.9255 | 2.9255
2020-02-27 11:00 | Summer | 1.7909 | 2.5631 | 3.6987 | 3.6987 | 3.6987 | 3.6987 | 1.166 | 2.3061 | 2.3061 | 2.3061 | 2.3061 | 2.3061 | 3.258 | 4.2044 | 4.8244 | 5.1507 | 5.8034 | 6.4561 | 1.4213 | 2.8052 | 3.3663 | 3.3663 | 3.3663 | 3.3663 | 2.6102 | 3.0364 | 3.0364 | 3.0364 | 3.0364 | 3.0364
2020-02-27 12:00 | Summer | 1.7909 | 2.5631 | 3.6987 | 3.6987 | 3.6987 | 3.6987 | 1.3146 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 3.258 | 4.2044 | 4.8244 | 5.1507 | 5.8034 | 6.4561 | 1.3413 | 2.6473 | 3.1768 | 3.1768 | 3.1768 | 3.1768 | 2.7055 | 3.1472 | 3.1472 | 3.1472 | 3.1472 | 3.1472
2020-02-27 13:00 | Summer | 1.7719 | 2.5359 | 3.6593 | 3.6593 | 3.6593 | 3.6593 | 1.3146 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 3.3914 | 4.3765 | 5.0219 | 5.3616 | 6.041 | 6.7204 | 1.2727 | 2.5119 | 3.0143 | 3.0143 | 3.0143 | 3.0143 | 2.8007 | 3.258 | 3.258 | 3.258 | 3.258 | 3.258
2020-02-27 14:00 | Summer | 1.829 | 2.6177 | 3.7774 | 3.7774 | 3.7774 | 3.7774 | 1.3375 | 2.6452 | 2.6452 | 2.6452 | 2.6452 | 2.6452 | 3.5057 | 4.524 | 5.1912 | 5.5423 | 6.2446 | 6.9469 | 1.3946 | 2.7526 | 3.3031 | 3.3031 | 3.3031 | 3.3031 | 2.7436 | 3.1915 | 3.1915 | 3.1915 | 3.1915 | 3.1915
2020-02-27 15:00 | Summer | 1.81 | 2.5904 | 3.738 | 3.738 | 3.738 | 3.738 | 1.4661 | 2.8996 | 2.8996 | 2.8996 | 2.8996 | 2.8996 | 3.4485 | 4.4502 | 5.1065 | 5.4519 | 6.1428 | 6.8336 | 1.3946 | 2.7526 | 3.3031 | 3.3031 | 3.3031 | 3.3031 | 2.8007 | 3.258 | 3.258 | 3.258 | 3.258 | 3.258
2020-02-27 16:00 | Summer | 1.7338 | 2.4813 | 3.5806 | 3.5806 | 3.5806 | 3.5806 | 1.4089 | 2.7865 | 2.7865 | 2.7865 | 2.7865 | 2.7865 | 3.4866 | 4.4994 | 5.163 | 5.5122 | 6.2107 | 6.9091 | 1.307 | 2.5796 | 3.0955 | 3.0955 | 3.0955 | 3.0955 | 2.7436 | 3.1915 | 3.1915 | 3.1915 | 3.1915 | 3.1915
2020-02-27 17:00 | Summer | 1.6385 | 2.345 | 3.3839 | 3.3839 | 3.3839 | 3.3839 | 1.3089 | 2.5887 | 2.5887 | 2.5887 | 2.5887 | 2.5887 | 3.4676 | 4.4748 | 5.1347 | 5.4821 | 6.1767 | 6.8714 | 1.3375 | 2.6398 | 3.1677 | 3.1677 | 3.1677 | 3.1677 | 2.6293 | 3.0585 | 3.0585 | 3.0585 | 3.0585 | 3.0585
2020-02-27 18:00 | Summer | 1.3349 | 1.9105 | 2.7569 | 2.7569 | 2.7569 | 2.7569 | 1.1174 | 2.21 | 2.21 | 2.21 | 2.21 | 2.21 | 3.0273 | 3.9067 | 4.4828 | 4.7861 | 5.3925 | 5.999 | 0.99454 | 1.9629 | 2.3555 | 2.3555 | 2.3555 | 2.3555 | 1.9742 | 2.2966 | 2.2966 | 2.2966 | 2.2966 | 2.2966
2020-02-27 19:00 | Summer | 0.89547 | 1.2816 | 1.8493 | 1.8493 | 1.8493 | 1.8493 | 0.8462 | 1.6736 | 1.6736 | 1.6736 | 1.6736 | 1.6736 | 2.9153 | 3.7622 | 4.317 | 4.609 | 5.1931 | 5.7771 | 0.93357 | 1.8426 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 1.3337 | 1.5514 | 1.5514 | 1.5514 | 1.5514 | 1.5514
2020-02-27 20:00 | Summer | 0.83174 | 1.1904 | 1.7177 | 1.7177 | 1.7177 | 1.7177 | 0.8345 | 1.6504 | 1.6504 | 1.6504 | 1.6504 | 1.6504 | 2.6864 | 3.4668 | 3.978 | 4.2471 | 4.7853 | 5.3234 | 0.99835 | 1.9704 | 2.3645 | 2.3645 | 2.3645 | 2.3645 | 1.2194 | 1.4184 | 1.4184 | 1.4184 | 1.4184 | 1.4184
2020-02-27 21:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.74305 | 1.4696 | 1.4696 | 1.4696 | 1.4696 | 1.4696 | 2.534 | 3.2701 | 3.7523 | 4.0061 | 4.5138 | 5.0214 | 0.9793 | 1.9328 | 2.3194 | 2.3194 | 2.3194 | 2.3194 | 1.2003 | 1.3963 | 1.3963 | 1.3963 | 1.3963 | 1.3963
2020-02-27 22:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.59444 | 1.1756 | 1.1756 | 1.1756 | 1.1756 | 1.1756 | 2.4197 | 3.1225 | 3.583 | 3.8254 | 4.3101 | 4.7949 | 0.92214 | 1.82 | 2.184 | 2.184 | 2.184 | 2.184 | 1.0098 | 1.1746 | 1.1746 | 1.1746 | 1.1746 | 1.1746
2020-02-27 23:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.52585 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 2.0767 | 2.68 | 3.0752 | 3.2832 | 3.6992 | 4.1153 | 0.78496 | 1.5493 | 1.8591 | 1.8591 | 1.8591 | 1.8591 | 0.97168 | 1.1303 | 1.1303 | 1.1303 | 1.1303 | 1.1303
2020-02-28 | Summer | 0.55252 | 0.79075 | 1.1411 | 1.1411 | 1.1411 | 1.1411 | 0.40582 | 0.8026 | 0.8026 | 0.8026 | 0.8026 | 0.8026 | 1.8862 | 2.4341 | 2.7931 | 2.982 | 3.3599 | 3.7377 | 0.66303 | 1.3086 | 1.5703 | 1.5703 | 1.5703 | 1.5703 | 0.93358 | 1.086 | 1.086 | 1.086 | 1.086 | 1.086
2020-02-28 01:00 | Summer | 0.55252 | 0.79075 | 1.1411 | 1.1411 | 1.1411 | 1.1411 | 0.40867 | 0.80825 | 0.80825 | 0.80825 | 0.80825 | 0.80825 | 1.7909 | 2.3112 | 2.652 | 2.8314 | 3.1902 | 3.549 | 0.87642 | 1.7298 | 2.0757 | 2.0757 | 2.0757 | 2.0757 | 0.89547 | 1.0417 | 1.0417 | 1.0417 | 1.0417 | 1.0417
2020-02-28 02:00 | Summer | 0.55244 | 0.79062 | 1.1409 | 1.1409 | 1.1409 | 1.1409 | 0.40582 | 0.8026 | 0.8026 | 0.8026 | 0.8026 | 0.8026 | 1.7528 | 2.262 | 2.5956 | 2.7712 | 3.1223 | 3.4734 | 0.68208 | 1.3462 | 1.6155 | 1.6155 | 1.6155 | 1.6155 | 0.89547 | 1.0417 | 1.0417 | 1.0417 | 1.0417 | 1.0417
2020-02-28 03:00 | Summer | 0.55252 | 0.79075 | 1.1411 | 1.1411 | 1.1411 | 1.1411 | 0.36296 | 0.71785 | 0.71785 | 0.71785 | 0.71785 | 0.71785 | 1.7147 | 2.2128 | 2.5392 | 2.7109 | 3.0544 | 3.3979 | 0.70494 | 1.3913 | 1.6696 | 1.6696 | 1.6696 | 1.6696 | 0.89547 | 1.0417 | 1.0417 | 1.0417 | 1.0417 | 1.0417
2020-02-28 04:00 | Summer | 0.60867 | 0.87111 | 1.257 | 1.257 | 1.257 | 1.257 | 0.44583 | 0.88173 | 0.88173 | 0.88173 | 0.88173 | 0.88173 | 1.81 | 2.3358 | 2.6802 | 2.8615 | 3.2241 | 3.5867 | 0.69732 | 1.3763 | 1.6516 | 1.6516 | 1.6516 | 1.6516 | 0.93358 | 1.086 | 1.086 | 1.086 | 1.086 | 1.086
2020-02-28 05:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.54585 | 1.0796 | 1.0796 | 1.0796 | 1.0796 | 1.0796 | 1.8374 | 2.3711 | 2.7208 | 2.9049 | 3.2729 | 3.641 | 0.74686 | 1.4741 | 1.7689 | 1.7689 | 1.7689 | 1.7689 | 1.0472 | 1.2181 | 1.2181 | 1.2181 | 1.2181 | 1.2181
2020-02-28 06:00 | Summer | 0.70494 | 1.0089 | 1.4559 | 1.4559 | 1.4559 | 1.4559 | 0.75448 | 1.4922 | 1.4922 | 1.4922 | 1.4922 | 1.4922 | 1.8853 | 2.433 | 2.7918 | 2.9806 | 3.3583 | 3.736 | 0.84593 | 1.6696 | 2.0035 | 2.0035 | 2.0035 | 2.0035 | 1.3947 | 1.6224 | 1.6224 | 1.6224 | 1.6224 | 1.6224
2020-02-28 07:00 | Summer | 1.3908 | 1.9905 | 2.8724 | 2.8724 | 2.8724 | 2.8724 | 0.82307 | 1.6278 | 1.6278 | 1.6278 | 1.6278 | 1.6278 | 2.4959 | 3.2209 | 3.6959 | 3.9459 | 4.4459 | 4.9459 | 1.1432 | 2.2562 | 2.7075 | 2.7075 | 2.7075 | 2.7075 | 1.7528 | 2.039 | 2.039 | 2.039 | 2.039 | 2.039
2020-02-28 08:00 | Summer | 1.7338 | 2.4813 | 3.5806 | 3.5806 | 3.5806 | 3.5806 | 0.88594 | 1.7522 | 1.7522 | 1.7522 | 1.7522 | 1.7522 | 2.7245 | 3.5159 | 4.0344 | 4.3073 | 4.8531 | 5.3989 | 1.1127 | 2.1961 | 2.6353 | 2.6353 | 2.6353 | 2.6353 | 2.0958 | 2.4379 | 2.4379 | 2.4379 | 2.4379 | 2.4379
2020-02-28 09:00 | Summer | 1.7338 | 2.4813 | 3.5806 | 3.5806 | 3.5806 | 3.5806 | 0.98882 | 1.9556 | 1.9556 | 1.9556 | 1.9556 | 1.9556 | 2.9341 | 3.7864 | 4.3448 | 4.6387 | 5.2265 | 5.8142 | 1.1355 | 2.2412 | 2.6894 | 2.6894 | 2.6894 | 2.6894 | 2.2863 | 2.6596 | 2.6596 | 2.6596 | 2.6596 | 2.6596
2020-02-28 10:00 | Summer | 1.7719 | 2.5359 | 3.6593 | 3.6593 | 3.6593 | 3.6593 | 1.046 | 2.0687 | 2.0687 | 2.0687 | 2.0687 | 2.0687 | 3.1818 | 4.106 | 4.7115 | 5.0303 | 5.6677 | 6.3051 | 1.1203 | 2.2111 | 2.6533 | 2.6533 | 2.6533 | 2.6533 | 2.534 | 2.9477 | 2.9477 | 2.9477 | 2.9477 | 2.9477
2020-02-28 11:00 | Summer | 1.7909 | 2.5631 | 3.6987 | 3.6987 | 3.6987 | 3.6987 | 1.0631 | 2.1026 | 2.1026 | 2.1026 | 2.1026 | 2.1026 | 3.277 | 4.2289 | 4.8526 | 5.1809 | 5.8373 | 6.4938 | 1.1992 | 2.3669 | 2.8402 | 2.8402 | 2.8402 | 2.8402 | 2.7055 | 3.1472 | 3.1472 | 3.1472 | 3.1472 | 3.1472
2020-02-28 12:00 | Summer | 1.829 | 2.6177 | 3.7774 | 3.7774 | 3.7774 | 3.7774 | 1.166 | 2.3061 | 2.3061 | 2.3061 | 2.3061 | 2.3061 | 3.3723 | 4.3519 | 4.9937 | 5.3315 | 6.007 | 6.6826 | 1.3184 | 2.6022 | 3.1226 | 3.1226 | 3.1226 | 3.1226 | 2.8007 | 3.258 | 3.258 | 3.258 | 3.258 | 3.258
2020-02-28 13:00 | Summer | 1.8481 | 2.6449 | 3.8167 | 3.8167 | 3.8167 | 3.8167 | 1.2975 | 2.5661 | 2.5661 | 2.5661 | 2.5661 | 2.5661 | 3.5057 | 4.524 | 5.1912 | 5.5423 | 6.2446 | 6.9469 | 1.2918 | 2.5495 | 3.0594 | 3.0594 | 3.0594 | 3.0594 | 2.7626 | 3.2137 | 3.2137 | 3.2137 | 3.2137 | 3.2137
2020-02-28 14:00 | Summer | 1.8481 | 2.6449 | 3.8167 | 3.8167 | 3.8167 | 3.8167 | 1.2746 | 2.5209 | 2.5209 | 2.5209 | 2.5209 | 2.5209 | 3.4866 | 4.4994 | 5.163 | 5.5122 | 6.2107 | 6.9091 | 1.3527 | 2.6699 | 3.2038 | 3.2038 | 3.2038 | 3.2038 | 2.8007 | 3.258 | 3.258 | 3.258 | 3.258 | 3.258
2020-02-28 15:00 | Summer | 1.9434 | 2.7813 | 4.0135 | 4.0135 | 4.0135 | 4.0135 | 1.3432 | 2.6565 | 2.6565 | 2.6565 | 2.6565 | 2.6565 | 3.5438 | 4.5732 | 5.2476 | 5.6026 | 6.3125 | 7.0224 | 1.4518 | 2.8654 | 3.4385 | 3.4385 | 3.4385 | 3.4385 | 2.8388 | 3.3023 | 3.3023 | 3.3023 | 3.3023 | 3.3023
2020-02-28 16:00 | Summer | 2.0196 | 2.8903 | 4.1709 | 4.1709 | 4.1709 | 4.1709 | 1.5147 | 2.9956 | 2.9956 | 2.9956 | 2.9956 | 2.9956 | 3.639 | 4.6961 | 5.3887 | 5.7532 | 6.4822 | 7.2112 | 1.4518 | 2.8654 | 3.4385 | 3.4385 | 3.4385 | 3.4385 | 2.7626 | 3.2137 | 3.2137 | 3.2137 | 3.2137 | 3.2137
2020-02-28 17:00 | Summer | 1.786 | 2.556 | 3.6884 | 3.6884 | 3.6884 | 3.6884 | 1.4232 | 2.8148 | 2.8148 | 2.8148 | 2.8148 | 2.8148 | 3.6331 | 4.6884 | 5.3798 | 5.7437 | 6.4716 | 7.1994 | 1.3946 | 2.7526 | 3.3031 | 3.3031 | 3.3031 | 3.3031 | 2.6873 | 3.1261 | 3.1261 | 3.1261 | 3.1261 | 3.1261
2020-02-28 18:00 | Summer | 1.2246 | 1.7525 | 2.529 | 2.529 | 2.529 | 2.529 | 1.1632 | 2.3004 | 2.3004 | 2.3004 | 2.3004 | 2.3004 | 3.3507 | 4.324 | 4.9617 | 5.2973 | 5.9685 | 6.6398 | 1.1393 | 2.2487 | 2.6984 | 2.6984 | 2.6984 | 2.6984 | 2.0577 | 2.3937 | 2.3937 | 2.3937 | 2.3937 | 2.3937
2020-02-28 19:00 | Summer | 0.78115 | 1.118 | 1.6133 | 1.6133 | 1.6133 | 1.6133 | 0.82737 | 1.6363 | 1.6363 | 1.6363 | 1.6363 | 1.6363 | 3.0685 | 3.9598 | 4.5438 | 4.8512 | 5.4659 | 6.0806 | 1.0555 | 2.0832 | 2.4999 | 2.4999 | 2.4999 | 2.4999 | 1.2956 | 1.5071 | 1.5071 | 1.5071 | 1.5071 | 1.5071
2020-02-28 20:00 | Summer | 0.78115 | 1.118 | 1.6133 | 1.6133 | 1.6133 | 1.6133 | 0.80592 | 1.5939 | 1.5939 | 1.5939 | 1.5939 | 1.5939 | 2.6293 | 3.393 | 3.8934 | 4.1567 | 4.6835 | 5.2102 | 1.0936 | 2.1585 | 2.5901 | 2.5901 | 2.5901 | 2.5901 | 1.2384 | 1.4406 | 1.4406 | 1.4406 | 1.4406 | 1.4406
2020-02-28 21:00 | Summer | 0.66684 | 0.95435 | 1.3772 | 1.3772 | 1.3772 | 1.3772 | 0.73447 | 1.4526 | 1.4526 | 1.4526 | 1.4526 | 1.4526 | 2.6674 | 3.4422 | 3.9498 | 4.217 | 4.7513 | 5.2857 | 1.0212 | 2.0156 | 2.4187 | 2.4187 | 2.4187 | 2.4187 | 1.0861 | 1.2634 | 1.2634 | 1.2634 | 1.2634 | 1.2634
2020-02-28 22:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.72018 | 1.4243 | 1.4243 | 1.4243 | 1.4243 | 1.4243 | 2.3625 | 3.0488 | 3.4984 | 3.735 | 4.2083 | 4.6816 | 1.0288 | 2.0306 | 2.4367 | 2.4367 | 2.4367 | 2.4367 | 1.0669 | 1.2411 | 1.2411 | 1.2411 | 1.2411 | 1.2411
2020-02-28 23:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.65159 | 1.2887 | 1.2887 | 1.2887 | 1.2887 | 1.2887 | 2.1339 | 2.7537 | 3.1598 | 3.3736 | 3.8011 | 4.2285 | 0.96787 | 1.9103 | 2.2923 | 2.2923 | 2.2923 | 2.2923 | 0.9721 | 1.1308 | 1.1308 | 1.1308 | 1.1308 | 1.1308
2020-02-29 | Summer | 0.55252 | 0.79075 | 1.1411 | 1.1411 | 1.1411 | 1.1411 | 0.46012 | 0.90999 | 0.90999 | 0.90999 | 0.90999 | 0.90999 | 1.9053 | 2.4587 | 2.8213 | 3.0121 | 3.3938 | 3.7755 | 0.87261 | 1.7222 | 2.0667 | 2.0667 | 2.0667 | 2.0667 | 0.89547 | 1.0417 | 1.0417 | 1.0417 | 1.0417 | 1.0417
2020-02-29 01:00 | Summer | 0.55252 | 0.79075 | 1.1411 | 1.1411 | 1.1411 | 1.1411 | 0.41725 | 0.82521 | 0.82521 | 0.82521 | 0.82521 | 0.82521 | 1.8672 | 2.4095 | 2.7649 | 2.9519 | 3.3259 | 3.7 | 0.70558 | 1.3926 | 1.6711 | 1.6711 | 1.6711 | 1.6711 | 0.87642 | 1.0195 | 1.0195 | 1.0195 | 1.0195 | 1.0195
2020-02-29 02:00 | Summer | 0.55252 | 0.79075 | 1.1411 | 1.1411 | 1.1411 | 1.1411 | 0.44868 | 0.88738 | 0.88738 | 0.88738 | 0.88738 | 0.88738 | 1.8481 | 2.3849 | 2.7366 | 2.9218 | 3.292 | 3.6622 | 0.67065 | 1.3236 | 1.5884 | 1.5884 | 1.5884 | 1.5884 | 0.87642 | 1.0195 | 1.0195 | 1.0195 | 1.0195 | 1.0195
2020-02-29 03:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.39153 | 0.77434 | 0.77434 | 0.77434 | 0.77434 | 0.77434 | 1.7909 | 2.3112 | 2.652 | 2.8314 | 3.1902 | 3.549 | 0.66303 | 1.3086 | 1.5703 | 1.5703 | 1.5703 | 1.5703 | 0.89547 | 1.0417 | 1.0417 | 1.0417 | 1.0417 | 1.0417
2020-02-29 04:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.42011 | 0.83086 | 0.83086 | 0.83086 | 0.83086 | 0.83086 | 1.81 | 2.3358 | 2.6802 | 2.8615 | 3.2241 | 3.5867 | 0.6516 | 1.286 | 1.5433 | 1.5433 | 1.5433 | 1.5433 | 0.87642 | 1.0195 | 1.0195 | 1.0195 | 1.0195 | 1.0195
2020-02-29 05:00 | Summer | 0.57085 | 0.81697 | 1.1789 | 1.1789 | 1.1789 | 1.1789 | 0.38581 | 0.76304 | 0.76304 | 0.76304 | 0.76304 | 0.76304 | 1.8233 | 2.353 | 2.7 | 2.8826 | 3.2479 | 3.6132 | 0.79258 | 1.5643 | 1.8772 | 1.8772 | 1.8772 | 1.8772 | 0.87636 | 1.0194 | 1.0194 | 1.0194 | 1.0194 | 1.0194
2020-02-29 06:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.46012 | 0.90999 | 0.90999 | 0.90999 | 0.90999 | 0.90999 | 1.8862 | 2.4341 | 2.7931 | 2.982 | 3.3599 | 3.7377 | 0.9793 | 1.9328 | 2.3194 | 2.3194 | 2.3194 | 2.3194 | 0.96336 | 1.1206 | 1.1206 | 1.1206 | 1.1206 | 1.1206
2020-02-29 07:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.58586 | 1.1587 | 1.1587 | 1.1587 | 1.1587 | 1.1587 | 2.2482 | 2.9013 | 3.3291 | 3.5543 | 4.0047 | 4.4551 | 1.0441 | 2.0607 | 2.4728 | 2.4728 | 2.4728 | 2.4728 | 1.086 | 1.2633 | 1.2633 | 1.2633 | 1.2633 | 1.2633
2020-02-29 08:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.56014 | 1.1078 | 1.1078 | 1.1078 | 1.1078 | 1.1078 | 2.4578 | 3.1717 | 3.6395 | 3.8856 | 4.378 | 4.8704 | 1.0555 | 2.0832 | 2.4999 | 2.4999 | 2.4999 | 2.4999 | 1.0479 | 1.219 | 1.219 | 1.219 | 1.219 | 1.219
2020-02-29 09:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.68303 | 1.3509 | 1.3509 | 1.3509 | 1.3509 | 1.3509 | 2.5149 | 3.2455 | 3.7241 | 3.976 | 4.4798 | 4.9836 | 1.0403 | 2.0532 | 2.4638 | 2.4638 | 2.4638 | 2.4638 | 1.1241 | 1.3076 | 1.3076 | 1.3076 | 1.3076 | 1.3076
2020-02-29 10:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.67731 | 1.3396 | 1.3396 | 1.3396 | 1.3396 | 1.3396 | 2.5721 | 3.3192 | 3.8087 | 4.0664 | 4.5816 | 5.0969 | 1.0098 | 1.993 | 2.3916 | 2.3916 | 2.3916 | 2.3916 | 1.1328 | 1.3178 | 1.3178 | 1.3178 | 1.3178 | 1.3178
2020-02-29 11:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.86022 | 1.7013 | 1.7013 | 1.7013 | 1.7013 | 1.7013 | 2.6674 | 3.4422 | 3.9498 | 4.217 | 4.7513 | 5.2857 | 0.99454 | 1.9629 | 2.3555 | 2.3555 | 2.3555 | 2.3555 | 1.2194 | 1.4184 | 1.4184 | 1.4184 | 1.4184 | 1.4184
2020-02-29 12:00 | Summer | 0.61588 | 0.88143 | 1.2719 | 1.2719 | 1.2719 | 1.2719 | 0.98311 | 1.9443 | 1.9443 | 1.9443 | 1.9443 | 1.9443 | 2.7055 | 3.4913 | 4.0062 | 4.2772 | 4.8192 | 5.3612 | 0.98692 | 1.9479 | 2.3374 | 2.3374 | 2.3374 | 2.3374 | 1.1813 | 1.3741 | 1.3741 | 1.3741 | 1.3741 | 1.3741
2020-02-29 13:00 | Summer | 0.724 | 1.0362 | 1.4952 | 1.4952 | 1.4952 | 1.4952 | 0.88022 | 1.7409 | 1.7409 | 1.7409 | 1.7409 | 1.7409 | 2.6674 | 3.4422 | 3.9498 | 4.217 | 4.7513 | 5.2857 | 1.006 | 1.9855 | 2.3826 | 2.3826 | 2.3826 | 2.3826 | 1.1622 | 1.352 | 1.352 | 1.352 | 1.352 | 1.352
2020-02-29 14:00 | Summer | 0.70494 | 1.0089 | 1.4559 | 1.4559 | 1.4559 | 1.4559 | 0.86308 | 1.707 | 1.707 | 1.707 | 1.707 | 1.707 | 2.7245 | 3.5159 | 4.0344 | 4.3073 | 4.8531 | 5.3989 | 1.025 | 2.0231 | 2.4277 | 2.4277 | 2.4277 | 2.4277 | 1.1432 | 1.3298 | 1.3298 | 1.3298 | 1.3298 | 1.3298
2020-02-29 15:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.89451 | 1.7691 | 1.7691 | 1.7691 | 1.7691 | 1.7691 | 2.7817 | 3.5897 | 4.1191 | 4.3977 | 4.955 | 5.5122 | 1.0669 | 2.1058 | 2.527 | 2.527 | 2.527 | 2.527 | 1.086 | 1.2633 | 1.2633 | 1.2633 | 1.2633 | 1.2633
2020-02-29 16:00 | Summer | 0.68589 | 0.98162 | 1.4165 | 1.4165 | 1.4165 | 1.4165 | 0.8545 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 2.7436 | 3.5405 | 4.0627 | 4.3375 | 4.8871 | 5.4367 | 1.0136 | 2.0005 | 2.4006 | 2.4006 | 2.4006 | 2.4006 | 1.0807 | 1.2572 | 1.2572 | 1.2572 | 1.2572 | 1.2572
2020-02-29 17:00 | Summer | 0.68589 | 0.98162 | 1.4165 | 1.4165 | 1.4165 | 1.4165 | 0.84021 | 1.6617 | 1.6617 | 1.6617 | 1.6617 | 1.6617 | 2.6933 | 3.4757 | 3.9882 | 4.258 | 4.7976 | 5.3371 | 1.0708 | 2.1133 | 2.536 | 2.536 | 2.536 | 2.536 | 1.105 | 1.2855 | 1.2855 | 1.2855 | 1.2855 | 1.2855
2020-02-29 18:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.9088 | 1.7974 | 1.7974 | 1.7974 | 1.7974 | 1.7974 | 2.6483 | 3.4176 | 3.9216 | 4.1869 | 4.7174 | 5.2479 | 1.0326 | 2.0381 | 2.4457 | 2.4457 | 2.4457 | 2.4457 | 1.1432 | 1.3298 | 1.3298 | 1.3298 | 1.3298 | 1.3298
2020-02-29 19:00 | Summer | 0.5678 | 0.81261 | 1.1726 | 1.1726 | 1.1726 | 1.1726 | 0.92595 | 1.8313 | 1.8313 | 1.8313 | 1.8313 | 1.8313 | 2.5149 | 3.2455 | 3.7241 | 3.976 | 4.4798 | 4.9836 | 1.105 | 2.181 | 2.6172 | 2.6172 | 2.6172 | 2.6172 | 1.1242 | 1.3078 | 1.3078 | 1.3078 | 1.3078 | 1.3078
2020-02-29 20:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.84879 | 1.6787 | 1.6787 | 1.6787 | 1.6787 | 1.6787 | 2.4578 | 3.1717 | 3.6395 | 3.8856 | 4.378 | 4.8704 | 0.98311 | 1.9403 | 2.3284 | 2.3284 | 2.3284 | 2.3284 | 1.0669 | 1.2411 | 1.2411 | 1.2411 | 1.2411 | 1.2411
2020-02-29 21:00 | Summer | 0.57182 | 0.81837 | 1.1809 | 1.1809 | 1.1809 | 1.1809 | 0.84593 | 1.673 | 1.673 | 1.673 | 1.673 | 1.673 | 2.3816 | 3.0734 | 3.5266 | 3.7652 | 4.2423 | 4.7194 | 0.98692 | 1.9479 | 2.3374 | 2.3374 | 2.3374 | 2.3374 | 1.0098 | 1.1746 | 1.1746 | 1.1746 | 1.1746 | 1.1746
2020-02-29 22:00 | Summer | 0.55252 | 0.79075 | 1.1411 | 1.1411 | 1.1411 | 1.1411 | 0.77734 | 1.5374 | 1.5374 | 1.5374 | 1.5374 | 1.5374 | 2.2863 | 2.9504 | 3.3855 | 3.6146 | 4.0726 | 4.5306 | 0.92976 | 1.8351 | 2.2021 | 2.2021 | 2.2021 | 2.2021 | 0.95263 | 1.1082 | 1.1082 | 1.1082 | 1.1082 | 1.1082
2020-02-29 23:00 | Summer | 0.55252 | 0.79075 | 1.1411 | 1.1411 | 1.1411 | 1.1411 | 0.66874 | 1.3226 | 1.3226 | 1.3226 | 1.3226 | 1.3226 | 2.1339 | 2.7537 | 3.1598 | 3.3736 | 3.8011 | 4.2285 | 0.88785 | 1.7523 | 2.1028 | 2.1028 | 2.1028 | 2.1028 | 0.97168 | 1.1303 | 1.1303 | 1.1303 | 1.1303 | 1.1303
2020-03-01 | Summer | 0.57138 | 0.81773 | 1.18 | 1.18 | 1.18 | 1.18 | 0.48298 | 0.95521 | 0.95521 | 0.95521 | 0.95521 | 0.95521 | 1.9434 | 2.5079 | 2.8777 | 3.0724 | 3.4617 | 3.851 | 0.70875 | 1.3989 | 1.6786 | 1.6786 | 1.6786 | 1.6786 | 0.95263 | 1.1082 | 1.1082 | 1.1082 | 1.1082 | 1.1082
2020-03-01 01:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.42868 | 0.84782 | 0.84782 | 0.84782 | 0.84782 | 0.84782 | 1.8862 | 2.4341 | 2.7931 | 2.982 | 3.3599 | 3.7377 | 0.74686 | 1.4741 | 1.7689 | 1.7689 | 1.7689 | 1.7689 | 0.93358 | 1.086 | 1.086 | 1.086 | 1.086 | 1.086
2020-03-01 02:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.4544 | 0.89869 | 0.89869 | 0.89869 | 0.89869 | 0.89869 | 1.829 | 2.3603 | 2.7084 | 2.8916 | 3.2581 | 3.6245 | 0.73543 | 1.4515 | 1.7418 | 1.7418 | 1.7418 | 1.7418 | 0.91452 | 1.0638 | 1.0638 | 1.0638 | 1.0638 | 1.0638
2020-03-01 03:00 | Summer | 0.55252 | 0.79075 | 1.1411 | 1.1411 | 1.1411 | 1.1411 | 0.4001 | 0.7913 | 0.7913 | 0.7913 | 0.7913 | 0.7913 | 1.9243 | 2.4833 | 2.8495 | 3.0422 | 3.4277 | 3.8132 | 0.69732 | 1.3763 | 1.6516 | 1.6516 | 1.6516 | 1.6516 | 0.93358 | 1.086 | 1.086 | 1.086 | 1.086 | 1.086
2020-03-01 04:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.40578 | 0.80254 | 0.80254 | 0.80254 | 0.80254 | 0.80254 | 1.8481 | 2.3849 | 2.7366 | 2.9218 | 3.292 | 3.6622 | 0.67446 | 1.3312 | 1.5974 | 1.5974 | 1.5974 | 1.5974 | 0.89547 | 1.0417 | 1.0417 | 1.0417 | 1.0417 | 1.0417
2020-03-01 05:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.40582 | 0.8026 | 0.8026 | 0.8026 | 0.8026 | 0.8026 | 1.829 | 2.3603 | 2.7084 | 2.8916 | 3.2581 | 3.6245 | 0.79258 | 1.5643 | 1.8772 | 1.8772 | 1.8772 | 1.8772 | 0.85737 | 0.99734 | 0.99734 | 0.99734 | 0.99734 | 0.99734
2020-03-01 06:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.47441 | 0.93825 | 0.93825 | 0.93825 | 0.93825 | 0.93825 | 1.9053 | 2.4587 | 2.8213 | 3.0121 | 3.3938 | 3.7755 | 0.88785 | 1.7523 | 2.1028 | 2.1028 | 2.1028 | 2.1028 | 0.93358 | 1.086 | 1.086 | 1.086 | 1.086 | 1.086
2020-03-01 07:00 | Summer | 0.56926 | 0.81471 | 1.1757 | 1.1757 | 1.1757 | 1.1757 | 0.46869 | 0.92695 | 0.92695 | 0.92695 | 0.92695 | 0.92695 | 2.0858 | 2.6917 | 3.0887 | 3.2976 | 3.7155 | 4.1333 | 1.0136 | 2.0005 | 2.4006 | 2.4006 | 2.4006 | 2.4006 | 0.89547 | 1.0417 | 1.0417 | 1.0417 | 1.0417 | 1.0417
2020-03-01 08:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.55728 | 1.1022 | 1.1022 | 1.1022 | 1.1022 | 1.1022 | 2.3244 | 2.9996 | 3.442 | 3.6748 | 4.1404 | 4.6061 | 1.105 | 2.181 | 2.6172 | 2.6172 | 2.6172 | 2.6172 | 0.93358 | 1.086 | 1.086 | 1.086 | 1.086 | 1.086
2020-03-01 09:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.61158 | 1.2096 | 1.2096 | 1.2096 | 1.2096 | 1.2096 | 2.4578 | 3.1717 | 3.6395 | 3.8856 | 4.378 | 4.8704 | 1.0746 | 2.1208 | 2.545 | 2.545 | 2.545 | 2.545 | 1.1432 | 1.3298 | 1.3298 | 1.3298 | 1.3298 | 1.3298
2020-03-01 10:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.56014 | 1.1078 | 1.1078 | 1.1078 | 1.1078 | 1.1078 | 2.6102 | 3.3684 | 3.8652 | 4.1266 | 4.6495 | 5.1724 | 0.99454 | 1.9629 | 2.3555 | 2.3555 | 2.3555 | 2.3555 | 1.1241 | 1.3076 | 1.3076 | 1.3076 | 1.3076 | 1.3076
2020-03-01 11:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.54014 | 1.0683 | 1.0683 | 1.0683 | 1.0683 | 1.0683 | 2.8388 | 3.6634 | 4.2037 | 4.4881 | 5.0568 | 5.6255 | 1.0669 | 2.1058 | 2.527 | 2.527 | 2.527 | 2.527 | 1.105 | 1.2855 | 1.2855 | 1.2855 | 1.2855 | 1.2855
2020-03-01 12:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.86879 | 1.7183 | 1.7183 | 1.7183 | 1.7183 | 1.7183 | 2.8007 | 3.6143 | 4.1473 | 4.4278 | 4.9889 | 5.55 | 1.0326 | 2.0381 | 2.4457 | 2.4457 | 2.4457 | 2.4457 | 1.105 | 1.2855 | 1.2855 | 1.2855 | 1.2855 | 1.2855
2020-03-01 13:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.68589 | 1.3565 | 1.3565 | 1.3565 | 1.3565 | 1.3565 | 2.915 | 3.7618 | 4.3166 | 4.6086 | 5.1925 | 5.7765 | 1.0974 | 2.166 | 2.5992 | 2.5992 | 2.5992 | 2.5992 | 1.1241 | 1.3076 | 1.3076 | 1.3076 | 1.3076 | 1.3076
2020-03-01 14:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.69446 | 1.3735 | 1.3735 | 1.3735 | 1.3735 | 1.3735 | 2.896 | 3.7372 | 4.2884 | 4.5784 | 5.1586 | 5.7387 | 1.0631 | 2.0983 | 2.5179 | 2.5179 | 2.5179 | 2.5179 | 1.1432 | 1.3298 | 1.3298 | 1.3298 | 1.3298 | 1.3298
2020-03-01 15:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.76591 | 1.5148 | 1.5148 | 1.5148 | 1.5148 | 1.5148 | 2.9531 | 3.811 | 4.373 | 4.6688 | 5.2604 | 5.852 | 1.0593 | 2.0908 | 2.5089 | 2.5089 | 2.5089 | 2.5089 | 1.0669 | 1.2411 | 1.2411 | 1.2411 | 1.2411 | 1.2411
2020-03-01 16:00 | Summer | 0.59057 | 0.8452 | 1.2197 | 1.2197 | 1.2197 | 1.2197 | 0.8545 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 3.0675 | 3.9585 | 4.5423 | 4.8495 | 5.464 | 6.0785 | 1.0517 | 2.0757 | 2.4909 | 2.4909 | 2.4909 | 2.4909 | 1.1241 | 1.3076 | 1.3076 | 1.3076 | 1.3076 | 1.3076
2020-03-01 17:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.86594 | 1.7126 | 1.7126 | 1.7126 | 1.7126 | 1.7126 | 2.9711 | 3.8341 | 4.3995 | 4.6971 | 5.2923 | 5.8875 | 1.086 | 2.1434 | 2.5721 | 2.5721 | 2.5721 | 2.5721 | 1.1622 | 1.352 | 1.352 | 1.352 | 1.352 | 1.352
2020-03-01 18:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.75448 | 1.4922 | 1.4922 | 1.4922 | 1.4922 | 1.4922 | 2.9722 | 3.8356 | 4.4012 | 4.6989 | 5.2943 | 5.8898 | 1.0669 | 2.1058 | 2.527 | 2.527 | 2.527 | 2.527 | 1.1432 | 1.3298 | 1.3298 | 1.3298 | 1.3298 | 1.3298
2020-03-01 19:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.84879 | 1.6787 | 1.6787 | 1.6787 | 1.6787 | 1.6787 | 2.7245 | 3.5159 | 4.0344 | 4.3073 | 4.8531 | 5.3989 | 1.0098 | 1.993 | 2.3916 | 2.3916 | 2.3916 | 2.3916 | 1.086 | 1.2633 | 1.2633 | 1.2633 | 1.2633 | 1.2633
2020-03-01 20:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.68875 | 1.3622 | 1.3622 | 1.3622 | 1.3622 | 1.3622 | 2.6864 | 3.4668 | 3.978 | 4.2471 | 4.7853 | 5.3234 | 0.98311 | 1.9403 | 2.3284 | 2.3284 | 2.3284 | 2.3284 | 1.105 | 1.2855 | 1.2855 | 1.2855 | 1.2855 | 1.2855
2020-03-01 21:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.6716 | 1.3283 | 1.3283 | 1.3283 | 1.3283 | 1.3283 | 2.6293 | 3.393 | 3.8934 | 4.1567 | 4.6835 | 5.2102 | 0.97549 | 1.9253 | 2.3104 | 2.3104 | 2.3104 | 2.3104 | 1.0288 | 1.1968 | 1.1968 | 1.1968 | 1.1968 | 1.1968
2020-03-01 22:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.64874 | 1.283 | 1.283 | 1.283 | 1.283 | 1.283 | 2.4387 | 3.1471 | 3.6112 | 3.8555 | 4.3441 | 4.8326 | 0.91452 | 1.805 | 2.166 | 2.166 | 2.166 | 2.166 | 1.0098 | 1.1746 | 1.1746 | 1.1746 | 1.1746 | 1.1746
2020-03-01 23:00 | Summer | 0.55241 | 0.79058 | 1.1408 | 1.1408 | 1.1408 | 1.1408 | 0.56872 | 1.1248 | 1.1248 | 1.1248 | 1.1248 | 1.1248 | 2.172 | 2.8029 | 3.2163 | 3.4338 | 3.8689 | 4.3041 | 0.89547 | 1.7674 | 2.1208 | 2.1208 | 2.1208 | 2.1208 | 0.99073 | 1.1525 | 1.1525 | 1.1525 | 1.1525 | 1.1525
2020-03-02 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.53442 | 1.057 | 1.057 | 1.057 | 1.057 | 1.057 | 2.004 | 2.5861 | 2.9675 | 3.1683 | 3.5697 | 3.9712 | 0.86117 | 1.6997 | 2.0396 | 2.0396 | 2.0396 | 2.0396 | 1.0098 | 1.1746 | 1.1746 | 1.1746 | 1.1746 | 1.1746
2020-03-02 01:00 | Summer | 0.56643 | 0.81066 | 1.1698 | 1.1698 | 1.1698 | 1.1698 | 0.48869 | 0.96652 | 0.96652 | 0.96652 | 0.96652 | 0.96652 | 1.9434 | 2.5079 | 2.8777 | 3.0724 | 3.4617 | 3.851 | 0.71637 | 1.4139 | 1.6967 | 1.6967 | 1.6967 | 1.6967 | 0.97168 | 1.1303 | 1.1303 | 1.1303 | 1.1303 | 1.1303
2020-03-02 02:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.49441 | 0.97782 | 0.97782 | 0.97782 | 0.97782 | 0.97782 | 1.8862 | 2.4341 | 2.7931 | 2.982 | 3.3599 | 3.7377 | 0.65922 | 1.3011 | 1.5613 | 1.5613 | 1.5613 | 1.5613 | 1.0479 | 1.219 | 1.219 | 1.219 | 1.219 | 1.219
2020-03-02 03:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.44297 | 0.87608 | 0.87608 | 0.87608 | 0.87608 | 0.87608 | 1.8672 | 2.4095 | 2.7649 | 2.9519 | 3.3259 | 3.7 | 0.62873 | 1.2409 | 1.4891 | 1.4891 | 1.4891 | 1.4891 | 1.105 | 1.2855 | 1.2855 | 1.2855 | 1.2855 | 1.2855
2020-03-02 04:00 | Summer | 0.80021 | 1.1452 | 1.6526 | 1.6526 | 1.6526 | 1.6526 | 0.60873 | 1.2039 | 1.2039 | 1.2039 | 1.2039 | 1.2039 | 1.8862 | 2.4341 | 2.7931 | 2.982 | 3.3599 | 3.7377 | 0.67446 | 1.3312 | 1.5974 | 1.5974 | 1.5974 | 1.5974 | 1.1622 | 1.352 | 1.352 | 1.352 | 1.352 | 1.352
2020-03-02 05:00 | Summer | 0.81926 | 1.1725 | 1.692 | 1.692 | 1.692 | 1.692 | 0.60378 | 1.1941 | 1.1941 | 1.1941 | 1.1941 | 1.1941 | 2.0594 | 2.6577 | 3.0496 | 3.2559 | 3.6684 | 4.081 | 0.94119 | 1.8576 | 2.2291 | 2.2291 | 2.2291 | 2.2291 | 1.1621 | 1.3518 | 1.3518 | 1.3518 | 1.3518 | 1.3518
2020-03-02 06:00 | Summer | 1.1813 | 1.6906 | 2.4396 | 2.4396 | 2.4396 | 2.4396 | 0.80805 | 1.5981 | 1.5981 | 1.5981 | 1.5981 | 1.5981 | 2.3054 | 2.975 | 3.4138 | 3.6447 | 4.1065 | 4.5683 | 1.0326 | 2.0381 | 2.4457 | 2.4457 | 2.4457 | 2.4457 | 1.5583 | 1.8128 | 1.8128 | 1.8128 | 1.8128 | 1.8128
2020-03-02 07:00 | Summer | 2.0005 | 2.8631 | 4.1315 | 4.1315 | 4.1315 | 4.1315 | 0.96596 | 1.9104 | 1.9104 | 1.9104 | 1.9104 | 1.9104 | 2.7817 | 3.5897 | 4.1191 | 4.3977 | 4.955 | 5.5122 | 1.3718 | 2.7075 | 3.249 | 3.249 | 3.249 | 3.249 | 2.191 | 2.5488 | 2.5488 | 2.5488 | 2.5488 | 2.5488
2020-03-02 08:00 | Summer | 2.2291 | 3.1903 | 4.6037 | 4.6037 | 4.6037 | 4.6037 | 1.0346 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 3.0865 | 3.9831 | 4.5705 | 4.8796 | 5.498 | 6.1163 | 1.2994 | 2.5646 | 3.0775 | 3.0775 | 3.0775 | 3.0775 | 2.534 | 2.9477 | 2.9477 | 2.9477 | 2.9477 | 2.9477
2020-03-02 09:00 | Summer | 2.2291 | 3.1903 | 4.6037 | 4.6037 | 4.6037 | 4.6037 | 1.3403 | 2.6509 | 2.6509 | 2.6509 | 2.6509 | 2.6509 | 3.3622 | 4.3388 | 4.9787 | 5.3154 | 5.989 | 6.6625 | 1.3222 | 2.6097 | 3.1316 | 3.1316 | 3.1316 | 3.1316 | 2.8404 | 3.3042 | 3.3042 | 3.3042 | 3.3042 | 3.3042
2020-03-02 10:00 | Summer | 2.2673 | 3.2448 | 4.6824 | 4.6824 | 4.6824 | 4.6824 | 1.306 | 2.583 | 2.583 | 2.583 | 2.583 | 2.583 | 3.6553 | 4.7171 | 5.4128 | 5.7789 | 6.5112 | 7.2434 | 1.3908 | 2.7451 | 3.2941 | 3.2941 | 3.2941 | 3.2941 | 3.0865 | 3.5904 | 3.5904 | 3.5904 | 3.5904 | 3.5904
2020-03-02 11:00 | Summer | 2.3244 | 3.3266 | 4.8004 | 4.8004 | 4.8004 | 4.8004 | 1.306 | 2.583 | 2.583 | 2.583 | 2.583 | 2.583 | 3.9248 | 5.0649 | 5.8119 | 6.205 | 6.9912 | 7.7775 | 1.4937 | 2.9481 | 3.5378 | 3.5378 | 3.5378 | 3.5378 | 3.1627 | 3.6791 | 3.6791 | 3.6791 | 3.6791 | 3.6791
2020-03-02 12:00 | Summer | 2.4197 | 3.4629 | 4.9972 | 4.9972 | 4.9972 | 4.9972 | 1.3746 | 2.7187 | 2.7187 | 2.7187 | 2.7187 | 2.7187 | 3.9629 | 5.1141 | 5.8683 | 6.2652 | 7.0591 | 7.853 | 1.4899 | 2.9406 | 3.5287 | 3.5287 | 3.5287 | 3.5287 | 3.3981 | 3.9529 | 3.9529 | 3.9529 | 3.9529 | 3.9529
2020-03-02 13:00 | Summer | 2.3625 | 3.3811 | 4.8791 | 4.8791 | 4.8791 | 4.8791 | 1.4032 | 2.7752 | 2.7752 | 2.7752 | 2.7752 | 2.7752 | 4.2106 | 5.4337 | 6.235 | 6.6568 | 7.5003 | 8.3438 | 1.5356 | 3.0309 | 3.637 | 3.637 | 3.637 | 3.637 | 3.4295 | 3.9894 | 3.9894 | 3.9894 | 3.9894 | 3.9894
2020-03-02 14:00 | Summer | 2.3435 | 3.3539 | 4.8398 | 4.8398 | 4.8398 | 4.8398 | 1.4032 | 2.7752 | 2.7752 | 2.7752 | 2.7752 | 2.7752 | 4.0865 | 5.2736 | 6.0513 | 6.4606 | 7.2793 | 8.098 | 1.4899 | 2.9406 | 3.5287 | 3.5287 | 3.5287 | 3.5287 | 3.1818 | 3.7013 | 3.7013 | 3.7013 | 3.7013 | 3.7013
2020-03-02 15:00 | Summer | 2.3054 | 3.2993 | 4.7611 | 4.7611 | 4.7611 | 4.7611 | 1.3318 | 2.6339 | 2.6339 | 2.6339 | 2.6339 | 2.6339 | 4.0582 | 5.237 | 6.0093 | 6.4158 | 7.2288 | 8.0418 | 1.4937 | 2.9481 | 3.5378 | 3.5378 | 3.5378 | 3.5378 | 3.1056 | 3.6126 | 3.6126 | 3.6126 | 3.6126 | 3.6126
2020-03-02 16:00 | Summer | 2.1798 | 3.1197 | 4.5019 | 4.5019 | 4.5019 | 4.5019 | 1.4032 | 2.7752 | 2.7752 | 2.7752 | 2.7752 | 2.7752 | 4.0772 | 5.2616 | 6.0376 | 6.4459 | 7.2627 | 8.0795 | 1.467 | 2.8955 | 3.4746 | 3.4746 | 3.4746 | 3.4746 | 3.1437 | 3.6569 | 3.6569 | 3.6569 | 3.6569 | 3.6569
2020-03-02 17:00 | Summer | 2.0386 | 2.9176 | 4.2102 | 4.2102 | 4.2102 | 4.2102 | 1.3575 | 2.6848 | 2.6848 | 2.6848 | 2.6848 | 2.6848 | 4.001 | 5.1633 | 5.9247 | 6.3255 | 7.127 | 7.9285 | 1.4556 | 2.8729 | 3.4475 | 3.4475 | 3.4475 | 3.4475 | 3.0484 | 3.5461 | 3.5461 | 3.5461 | 3.5461 | 3.5461
2020-03-02 18:00 | Summer | 1.3215 | 1.8912 | 2.7291 | 2.7291 | 2.7291 | 2.7291 | 0.98025 | 1.9387 | 1.9387 | 1.9387 | 1.9387 | 1.9387 | 3.6511 | 4.7117 | 5.4065 | 5.7723 | 6.5037 | 7.2351 | 1.1203 | 2.2111 | 2.6533 | 2.6533 | 2.6533 | 2.6533 | 2.0388 | 2.3717 | 2.3717 | 2.3717 | 2.3717 | 2.3717
2020-03-02 19:00 | Summer | 0.85737 | 1.227 | 1.7706 | 1.7706 | 1.7706 | 1.7706 | 0.65731 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 3.241 | 4.1824 | 4.7992 | 5.1238 | 5.7731 | 6.4224 | 1.0517 | 2.0757 | 2.4909 | 2.4909 | 2.4909 | 2.4909 | 1.3337 | 1.5514 | 1.5514 | 1.5514 | 1.5514 | 1.5514
2020-03-02 20:00 | Summer | 0.78115 | 1.118 | 1.6133 | 1.6133 | 1.6133 | 1.6133 | 0.60635 | 1.1992 | 1.1992 | 1.1992 | 1.1992 | 1.1992 | 2.7245 | 3.5159 | 4.0344 | 4.3073 | 4.8531 | 5.3989 | 1.0669 | 2.1058 | 2.527 | 2.527 | 2.527 | 2.527 | 1.2547 | 1.4595 | 1.4595 | 1.4595 | 1.4595 | 1.4595
2020-03-02 21:00 | Summer | 0.70494 | 1.0089 | 1.4559 | 1.4559 | 1.4559 | 1.4559 | 0.63159 | 1.2491 | 1.2491 | 1.2491 | 1.2491 | 1.2491 | 2.6256 | 3.3882 | 3.8879 | 4.1509 | 4.6769 | 5.2029 | 1.0098 | 1.993 | 2.3916 | 2.3916 | 2.3916 | 2.3916 | 1.1813 | 1.3741 | 1.3741 | 1.3741 | 1.3741 | 1.3741
2020-03-02 22:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.50584 | 1.0004 | 1.0004 | 1.0004 | 1.0004 | 1.0004 | 2.4199 | 3.1228 | 3.5833 | 3.8257 | 4.3105 | 4.7952 | 0.96406 | 1.9027 | 2.2833 | 2.2833 | 2.2833 | 2.2833 | 1.1813 | 1.3741 | 1.3741 | 1.3741 | 1.3741 | 1.3741
2020-03-02 23:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.46751 | 0.92462 | 0.92462 | 0.92462 | 0.92462 | 0.92462 | 2.2775 | 2.939 | 3.3725 | 3.6006 | 4.0568 | 4.5131 | 0.92595 | 1.8275 | 2.193 | 2.193 | 2.193 | 2.193 | 1.0387 | 1.2083 | 1.2083 | 1.2083 | 1.2083 | 1.2083
2020-03-03 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.4544 | 0.89869 | 0.89869 | 0.89869 | 0.89869 | 0.89869 | 2.0196 | 2.6062 | 2.9906 | 3.1929 | 3.5974 | 4.002 | 0.68589 | 1.3537 | 1.6245 | 1.6245 | 1.6245 | 1.6245 | 0.99073 | 1.1525 | 1.1525 | 1.1525 | 1.1525 | 1.1525
2020-03-03 01:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.56586 | 1.1191 | 1.1191 | 1.1191 | 1.1191 | 1.1191 | 1.9624 | 2.5325 | 2.9059 | 3.1025 | 3.4956 | 3.8887 | 0.69351 | 1.3688 | 1.6425 | 1.6425 | 1.6425 | 1.6425 | 1.0098 | 1.1746 | 1.1746 | 1.1746 | 1.1746 | 1.1746
2020-03-03 02:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.54585 | 1.0796 | 1.0796 | 1.0796 | 1.0796 | 1.0796 | 1.9053 | 2.4587 | 2.8213 | 3.0121 | 3.3938 | 3.7755 | 0.67827 | 1.3387 | 1.6064 | 1.6064 | 1.6064 | 1.6064 | 0.91452 | 1.0638 | 1.0638 | 1.0638 | 1.0638 | 1.0638
2020-03-03 03:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.47726 | 0.94391 | 0.94391 | 0.94391 | 0.94391 | 0.94391 | 1.8672 | 2.4095 | 2.7649 | 2.9519 | 3.3259 | 3.7 | 0.67065 | 1.3236 | 1.5884 | 1.5884 | 1.5884 | 1.5884 | 0.89547 | 1.0417 | 1.0417 | 1.0417 | 1.0417 | 1.0417
2020-03-03 04:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.51442 | 1.0174 | 1.0174 | 1.0174 | 1.0174 | 1.0174 | 1.8862 | 2.4341 | 2.7931 | 2.982 | 3.3599 | 3.7377 | 0.64779 | 1.2785 | 1.5342 | 1.5342 | 1.5342 | 1.5342 | 0.99073 | 1.1525 | 1.1525 | 1.1525 | 1.1525 | 1.1525
2020-03-03 05:00 | Summer | 0.83831 | 1.1998 | 1.7313 | 1.7313 | 1.7313 | 1.7313 | 0.62587 | 1.2378 | 1.2378 | 1.2378 | 1.2378 | 1.2378 | 2.0005 | 2.5816 | 2.9624 | 3.1627 | 3.5635 | 3.9643 | 0.89433 | 1.7651 | 2.1181 | 2.1181 | 2.1181 | 2.1181 | 1.2765 | 1.4849 | 1.4849 | 1.4849 | 1.4849 | 1.4849
2020-03-03 06:00 | Summer | 0.91452 | 1.3088 | 1.8887 | 1.8887 | 1.8887 | 1.8887 | 0.90595 | 1.7917 | 1.7917 | 1.7917 | 1.7917 | 1.7917 | 2.1497 | 2.7742 | 3.1833 | 3.3986 | 3.8293 | 4.2599 | 1.0974 | 2.166 | 2.5992 | 2.5992 | 2.5992 | 2.5992 | 1.4347 | 1.6689 | 1.6689 | 1.6689 | 1.6689 | 1.6689
2020-03-03 07:00 | Summer | 1.5209 | 2.1766 | 3.1409 | 3.1409 | 3.1409 | 3.1409 | 0.95453 | 1.8878 | 1.8878 | 1.8878 | 1.8878 | 1.8878 | 2.6293 | 3.393 | 3.8934 | 4.1567 | 4.6835 | 5.2102 | 1.2727 | 2.5119 | 3.0143 | 3.0143 | 3.0143 | 3.0143 | 1.9815 | 2.305 | 2.305 | 2.305 | 2.305 | 2.305
2020-03-03 08:00 | Summer | 1.829 | 2.6177 | 3.7774 | 3.7774 | 3.7774 | 3.7774 | 1.0746 | 2.1252 | 2.1252 | 2.1252 | 2.1252 | 2.1252 | 3.0103 | 3.8847 | 4.4576 | 4.7592 | 5.3622 | 5.9653 | 1.2384 | 2.4442 | 2.9331 | 2.9331 | 2.9331 | 2.9331 | 2.3625 | 2.7482 | 2.7482 | 2.7482 | 2.7482 | 2.7482
2020-03-03 09:00 | Summer | 1.829 | 2.6177 | 3.7774 | 3.7774 | 3.7774 | 3.7774 | 1.1689 | 2.3117 | 2.3117 | 2.3117 | 2.3117 | 2.3117 | 3.0675 | 3.9585 | 4.5423 | 4.8495 | 5.464 | 6.0785 | 1.1813 | 2.3314 | 2.7977 | 2.7977 | 2.7977 | 2.7977 | 2.4006 | 2.7926 | 2.7926 | 2.7926 | 2.7926 | 2.7926
2020-03-03 10:00 | Summer | 1.7719 | 2.5359 | 3.6593 | 3.6593 | 3.6593 | 3.6593 | 1.106 | 2.1874 | 2.1874 | 2.1874 | 2.1874 | 2.1874 | 3.0484 | 3.9339 | 4.5141 | 4.8194 | 5.4301 | 6.0408 | 1.1282 | 2.2267 | 2.6721 | 2.6721 | 2.6721 | 2.6721 | 2.4768 | 2.8812 | 2.8812 | 2.8812 | 2.8812 | 2.8812
2020-03-03 11:00 | Summer | 1.7528 | 2.5086 | 3.62 | 3.62 | 3.62 | 3.62 | 1.0974 | 2.1704 | 2.1704 | 2.1704 | 2.1704 | 2.1704 | 3.1056 | 4.0077 | 4.5987 | 4.9098 | 5.5319 | 6.154 | 1.0593 | 2.0908 | 2.5089 | 2.5089 | 2.5089 | 2.5089 | 2.4578 | 2.8591 | 2.8591 | 2.8591 | 2.8591 | 2.8591
2020-03-03 12:00 | Summer | 1.81 | 2.5904 | 3.738 | 3.738 | 3.738 | 3.738 | 1.1574 | 2.2891 | 2.2891 | 2.2891 | 2.2891 | 2.2891 | 3.3342 | 4.3027 | 4.9373 | 5.2712 | 5.9392 | 6.6071 | 1.0974 | 2.166 | 2.5992 | 2.5992 | 2.5992 | 2.5992 | 2.5305 | 2.9436 | 2.9436 | 2.9436 | 2.9436 | 2.9436
2020-03-03 13:00 | Summer | 1.9053 | 2.7267 | 3.9348 | 3.9348 | 3.9348 | 3.9348 | 1.126 | 2.227 | 2.227 | 2.227 | 2.227 | 2.227 | 3.258 | 4.2044 | 4.8244 | 5.1507 | 5.8034 | 6.4561 | 1.1127 | 2.1961 | 2.6353 | 2.6353 | 2.6353 | 2.6353 | 2.553 | 2.9699 | 2.9699 | 2.9699 | 2.9699 | 2.9699
2020-03-03 14:00 | Summer | 1.7909 | 2.5631 | 3.6987 | 3.6987 | 3.6987 | 3.6987 | 1.0917 | 2.1591 | 2.1591 | 2.1591 | 2.1591 | 2.1591 | 3.2199 | 4.1552 | 4.768 | 5.0905 | 5.7355 | 6.3806 | 1.1089 | 2.1885 | 2.6262 | 2.6262 | 2.6262 | 2.6262 | 2.4959 | 2.9034 | 2.9034 | 2.9034 | 2.9034 | 2.9034
2020-03-03 15:00 | Summer | 1.7338 | 2.4813 | 3.5806 | 3.5806 | 3.5806 | 3.5806 | 1.106 | 2.1874 | 2.1874 | 2.1874 | 2.1874 | 2.1874 | 3.1056 | 4.0077 | 4.5987 | 4.9098 | 5.5319 | 6.154 | 1.086 | 2.1434 | 2.5721 | 2.5721 | 2.5721 | 2.5721 | 2.3625 | 2.7482 | 2.7482 | 2.7482 | 2.7482 | 2.7482
2020-03-03 16:00 | Summer | 1.6385 | 2.345 | 3.3839 | 3.3839 | 3.3839 | 3.3839 | 1.006 | 1.9896 | 1.9896 | 1.9896 | 1.9896 | 1.9896 | 3.1246 | 4.0323 | 4.6269 | 4.9399 | 5.5658 | 6.1918 | 1.0746 | 2.1208 | 2.545 | 2.545 | 2.545 | 2.545 | 2.3625 | 2.7482 | 2.7482 | 2.7482 | 2.7482 | 2.7482
2020-03-03 17:00 | Summer | 1.5242 | 2.1814 | 3.1478 | 3.1478 | 3.1478 | 3.1478 | 0.93738 | 1.8539 | 1.8539 | 1.8539 | 1.8539 | 1.8539 | 3.0865 | 3.9831 | 4.5705 | 4.8796 | 5.498 | 6.1163 | 1.0669 | 2.1058 | 2.527 | 2.527 | 2.527 | 2.527 | 2.2673 | 2.6374 | 2.6374 | 2.6374 | 2.6374 | 2.6374
2020-03-03 18:00 | Summer | 0.98266 | 1.4063 | 2.0294 | 2.0294 | 2.0294 | 2.0294 | 0.93167 | 1.8426 | 1.8426 | 1.8426 | 1.8426 | 1.8426 | 2.858 | 3.6882 | 4.2322 | 4.5184 | 5.091 | 5.6635 | 0.91071 | 1.7975 | 2.1569 | 2.1569 | 2.1569 | 2.1569 | 1.7276 | 2.0096 | 2.0096 | 2.0096 | 2.0096 | 2.0096
2020-03-03 19:00 | Summer | 0.73293 | 1.0489 | 1.5137 | 1.5137 | 1.5137 | 1.5137 | 0.66017 | 1.3056 | 1.3056 | 1.3056 | 1.3056 | 1.3056 | 2.5369 | 3.2739 | 3.7567 | 4.0108 | 4.519 | 5.0272 | 0.93357 | 1.8426 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 1.3146 | 1.5293 | 1.5293 | 1.5293 | 1.5293 | 1.5293
2020-03-03 20:00 | Summer | 0.80021 | 1.1452 | 1.6526 | 1.6526 | 1.6526 | 1.6526 | 0.57157 | 1.1304 | 1.1304 | 1.1304 | 1.1304 | 1.1304 | 2.4768 | 3.1963 | 3.6677 | 3.9158 | 4.4119 | 4.9081 | 0.9069 | 1.7899 | 2.1479 | 2.1479 | 2.1479 | 2.1479 | 1.1241 | 1.3076 | 1.3076 | 1.3076 | 1.3076 | 1.3076
2020-03-03 21:00 | Summer | 0.68589 | 0.98162 | 1.4165 | 1.4165 | 1.4165 | 1.4165 | 0.48012 | 0.94956 | 0.94956 | 0.94956 | 0.94956 | 0.94956 | 2.3816 | 3.0734 | 3.5266 | 3.7652 | 4.2423 | 4.7194 | 0.88785 | 1.7523 | 2.1028 | 2.1028 | 2.1028 | 2.1028 | 1.0288 | 1.1968 | 1.1968 | 1.1968 | 1.1968 | 1.1968
2020-03-03 22:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.42296 | 0.83652 | 0.83652 | 0.83652 | 0.83652 | 0.83652 | 2.1721 | 2.803 | 3.2164 | 3.434 | 3.8691 | 4.3042 | 0.86879 | 1.7147 | 2.0577 | 2.0577 | 2.0577 | 2.0577 | 0.91452 | 1.0638 | 1.0638 | 1.0638 | 1.0638 | 1.0638
2020-03-03 23:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.40882 | 0.80854 | 0.80854 | 0.80854 | 0.80854 | 0.80854 | 2.1148 | 2.7291 | 3.1316 | 3.3435 | 3.7671 | 4.1908 | 0.84119 | 1.6603 | 1.9923 | 1.9923 | 1.9923 | 1.9923 | 0.89547 | 1.0417 | 1.0417 | 1.0417 | 1.0417 | 1.0417
2020-03-04 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.39153 | 0.77434 | 0.77434 | 0.77434 | 0.77434 | 0.77434 | 1.9053 | 2.4587 | 2.8213 | 3.0121 | 3.3938 | 3.7755 | 0.59825 | 1.1808 | 1.4169 | 1.4169 | 1.4169 | 1.4169 | 0.89547 | 1.0417 | 1.0417 | 1.0417 | 1.0417 | 1.0417
2020-03-04 01:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.39957 | 0.79025 | 0.79025 | 0.79025 | 0.79025 | 0.79025 | 1.829 | 2.3603 | 2.7084 | 2.8916 | 3.2581 | 3.6245 | 0.56776 | 1.1206 | 1.3447 | 1.3447 | 1.3447 | 1.3447 | 0.89547 | 1.0417 | 1.0417 | 1.0417 | 1.0417 | 1.0417
2020-03-04 02:00 | Summer | 0.5526 | 0.79086 | 1.1412 | 1.1412 | 1.1412 | 1.1412 | 0.41439 | 0.81956 | 0.81956 | 0.81956 | 0.81956 | 0.81956 | 1.81 | 2.3358 | 2.6802 | 2.8615 | 3.2241 | 3.5867 | 0.52585 | 1.0379 | 1.2454 | 1.2454 | 1.2454 | 1.2454 | 0.87642 | 1.0195 | 1.0195 | 1.0195 | 1.0195 | 1.0195
2020-03-04 03:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.40867 | 0.80825 | 0.80825 | 0.80825 | 0.80825 | 0.80825 | 1.829 | 2.3603 | 2.7084 | 2.8916 | 3.2581 | 3.6245 | 0.55633 | 1.098 | 1.3176 | 1.3176 | 1.3176 | 1.3176 | 0.87642 | 1.0195 | 1.0195 | 1.0195 | 1.0195 | 1.0195
2020-03-04 04:00 | Summer | 0.62663 | 0.89681 | 1.2941 | 1.2941 | 1.2941 | 1.2941 | 0.42008 | 0.83081 | 0.83081 | 0.83081 | 0.83081 | 0.83081 | 1.8672 | 2.4095 | 2.7649 | 2.9519 | 3.3259 | 3.7 | 0.54109 | 1.0679 | 1.2815 | 1.2815 | 1.2815 | 1.2815 | 0.93358 | 1.086 | 1.086 | 1.086 | 1.086 | 1.086
2020-03-04 05:00 | Summer | 0.7621 | 1.0907 | 1.5739 | 1.5739 | 1.5739 | 1.5739 | 0.55443 | 1.0965 | 1.0965 | 1.0965 | 1.0965 | 1.0965 | 1.8853 | 2.433 | 2.7918 | 2.9807 | 3.3583 | 3.736 | 0.84854 | 1.6748 | 2.0097 | 2.0097 | 2.0097 | 2.0097 | 1.1432 | 1.3298 | 1.3298 | 1.3298 | 1.3298 | 1.3298
2020-03-04 06:00 | Summer | 0.87669 | 1.2547 | 1.8106 | 1.8106 | 1.8106 | 1.8106 | 0.75734 | 1.4978 | 1.4978 | 1.4978 | 1.4978 | 1.4978 | 2.1529 | 2.7783 | 3.1881 | 3.4037 | 3.835 | 4.2663 | 1.0441 | 2.0607 | 2.4728 | 2.4728 | 2.4728 | 2.4728 | 1.5373 | 1.7883 | 1.7883 | 1.7883 | 1.7883 | 1.7883
2020-03-04 07:00 | Summer | 1.1805 | 1.6894 | 2.4379 | 2.4379 | 2.4379 | 2.4379 | 0.90595 | 1.7917 | 1.7917 | 1.7917 | 1.7917 | 1.7917 | 2.6102 | 3.3684 | 3.8652 | 4.1266 | 4.6495 | 5.1724 | 1.1546 | 2.2788 | 2.7345 | 2.7345 | 2.7345 | 2.7345 | 1.9145 | 2.2271 | 2.2271 | 2.2271 | 2.2271 | 2.2271
2020-03-04 08:00 | Summer | 1.7338 | 2.4813 | 3.5806 | 3.5806 | 3.5806 | 3.5806 | 0.94024 | 1.8596 | 1.8596 | 1.8596 | 1.8596 | 1.8596 | 2.896 | 3.7372 | 4.2884 | 4.5784 | 5.1586 | 5.7387 | 1.1584 | 2.2863 | 2.7436 | 2.7436 | 2.7436 | 2.7436 | 2.2863 | 2.6596 | 2.6596 | 2.6596 | 2.6596 | 2.6596
2020-03-04 09:00 | Summer | 1.6385 | 2.345 | 3.3839 | 3.3839 | 3.3839 | 3.3839 | 1.0117 | 2.0009 | 2.0009 | 2.0009 | 2.0009 | 2.0009 | 3.0103 | 3.8847 | 4.4576 | 4.7592 | 5.3622 | 5.9653 | 1.1584 | 2.2863 | 2.7436 | 2.7436 | 2.7436 | 2.7436 | 2.3435 | 2.7261 | 2.7261 | 2.7261 | 2.7261 | 2.7261
2020-03-04 10:00 | Summer | 1.6385 | 2.345 | 3.3839 | 3.3839 | 3.3839 | 3.3839 | 1.1146 | 2.2043 | 2.2043 | 2.2043 | 2.2043 | 2.2043 | 2.9913 | 3.8601 | 4.4294 | 4.729 | 5.3283 | 5.9275 | 1.2765 | 2.5194 | 3.0233 | 3.0233 | 3.0233 | 3.0233 | 2.4578 | 2.8591 | 2.8591 | 2.8591 | 2.8591 | 2.8591
2020-03-04 11:00 | Summer | 1.6385 | 2.345 | 3.3839 | 3.3839 | 3.3839 | 3.3839 | 1.1146 | 2.2043 | 2.2043 | 2.2043 | 2.2043 | 2.2043 | 3.0865 | 3.9831 | 4.5705 | 4.8796 | 5.498 | 6.1163 | 1.2117 | 2.3916 | 2.8699 | 2.8699 | 2.8699 | 2.8699 | 2.4006 | 2.7926 | 2.7926 | 2.7926 | 2.7926 | 2.7926
2020-03-04 12:00 | Summer | 1.7528 | 2.5086 | 3.62 | 3.62 | 3.62 | 3.62 | 1.0888 | 2.1535 | 2.1535 | 2.1535 | 2.1535 | 2.1535 | 3.258 | 4.2044 | 4.8244 | 5.1507 | 5.8034 | 6.4561 | 1.2117 | 2.3916 | 2.8699 | 2.8699 | 2.8699 | 2.8699 | 2.4578 | 2.8591 | 2.8591 | 2.8591 | 2.8591 | 2.8591
2020-03-04 13:00 | Summer | 1.7528 | 2.5086 | 3.62 | 3.62 | 3.62 | 3.62 | 1.226 | 2.4248 | 2.4248 | 2.4248 | 2.4248 | 2.4248 | 3.2199 | 4.1552 | 4.768 | 5.0905 | 5.7355 | 6.3806 | 1.1813 | 2.3314 | 2.7977 | 2.7977 | 2.7977 | 2.7977 | 2.4197 | 2.8147 | 2.8147 | 2.8147 | 2.8147 | 2.8147
2020-03-04 14:00 | Summer | 1.6957 | 2.4268 | 3.5019 | 3.5019 | 3.5019 | 3.5019 | 1.1403 | 2.2552 | 2.2552 | 2.2552 | 2.2552 | 2.2552 | 3.1437 | 4.0568 | 4.6551 | 4.97 | 5.5998 | 6.2296 | 1.2232 | 2.4142 | 2.897 | 2.897 | 2.897 | 2.897 | 2.3625 | 2.7482 | 2.7482 | 2.7482 | 2.7482 | 2.7482
2020-03-04 15:00 | Summer | 1.6385 | 2.345 | 3.3839 | 3.3839 | 3.3839 | 3.3839 | 1.2575 | 2.487 | 2.487 | 2.487 | 2.487 | 2.487 | 3.1056 | 4.0077 | 4.5987 | 4.9098 | 5.5319 | 6.154 | 1.2117 | 2.3916 | 2.8699 | 2.8699 | 2.8699 | 2.8699 | 2.3054 | 2.6817 | 2.6817 | 2.6817 | 2.6817 | 2.6817
2020-03-04 16:00 | Summer | 1.5814 | 2.2632 | 3.2659 | 3.2659 | 3.2659 | 3.2659 | 1.1603 | 2.2948 | 2.2948 | 2.2948 | 2.2948 | 2.2948 | 3.1437 | 4.0568 | 4.6551 | 4.97 | 5.5998 | 6.2296 | 1.2156 | 2.3991 | 2.8789 | 2.8789 | 2.8789 | 2.8789 | 2.3435 | 2.7261 | 2.7261 | 2.7261 | 2.7261 | 2.7261
2020-03-04 17:00 | Summer | 1.5242 | 2.1814 | 3.1478 | 3.1478 | 3.1478 | 3.1478 | 1.1231 | 2.2213 | 2.2213 | 2.2213 | 2.2213 | 2.2213 | 3.1627 | 4.0814 | 4.6833 | 5.0001 | 5.6337 | 6.2673 | 1.2117 | 2.3916 | 2.8699 | 2.8699 | 2.8699 | 2.8699 | 2.2839 | 2.6568 | 2.6568 | 2.6568 | 2.6568 | 2.6568
2020-03-04 18:00 | Summer | 1.0504 | 1.5034 | 2.1694 | 2.1694 | 2.1694 | 2.1694 | 0.95205 | 1.8829 | 1.8829 | 1.8829 | 1.8829 | 1.8829 | 3.0103 | 3.8847 | 4.4576 | 4.7592 | 5.3622 | 5.9653 | 1.0098 | 1.993 | 2.3916 | 2.3916 | 2.3916 | 2.3916 | 1.6698 | 1.9424 | 1.9424 | 1.9424 | 1.9424 | 1.9424
2020-03-04 19:00 | Summer | 0.724 | 1.0362 | 1.4952 | 1.4952 | 1.4952 | 1.4952 | 0.72483 | 1.4335 | 1.4335 | 1.4335 | 1.4335 | 1.4335 | 2.8122 | 3.6291 | 4.1643 | 4.446 | 5.0093 | 5.5727 | 1.006 | 1.9855 | 2.3826 | 2.3826 | 2.3826 | 2.3826 | 1.2575 | 1.4628 | 1.4628 | 1.4628 | 1.4628 | 1.4628
2020-03-04 20:00 | Summer | 0.724 | 1.0362 | 1.4952 | 1.4952 | 1.4952 | 1.4952 | 0.78877 | 1.56 | 1.56 | 1.56 | 1.56 | 1.56 | 2.5911 | 3.3438 | 3.8369 | 4.0965 | 4.6156 | 5.1347 | 0.96406 | 1.9027 | 2.2833 | 2.2833 | 2.2833 | 2.2833 | 1.2003 | 1.3963 | 1.3963 | 1.3963 | 1.3963 | 1.3963
2020-03-04 21:00 | Summer | 0.64779 | 0.92709 | 1.3378 | 1.3378 | 1.3378 | 1.3378 | 0.62873 | 1.2435 | 1.2435 | 1.2435 | 1.2435 | 1.2435 | 2.4959 | 3.2209 | 3.6959 | 3.9459 | 4.4459 | 4.9459 | 0.91452 | 1.805 | 2.166 | 2.166 | 2.166 | 2.166 | 1.1241 | 1.3076 | 1.3076 | 1.3076 | 1.3076 | 1.3076
2020-03-04 22:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.58872 | 1.1643 | 1.1643 | 1.1643 | 1.1643 | 1.1643 | 2.3244 | 2.9996 | 3.442 | 3.6748 | 4.1404 | 4.6061 | 0.92976 | 1.8351 | 2.2021 | 2.2021 | 2.2021 | 2.2021 | 1.0098 | 1.1746 | 1.1746 | 1.1746 | 1.1746 | 1.1746
2020-03-04 23:00 | Summer | 0.60539 | 0.86641 | 1.2503 | 1.2503 | 1.2503 | 1.2503 | 0.58586 | 1.1587 | 1.1587 | 1.1587 | 1.1587 | 1.1587 | 2.172 | 2.8029 | 3.2163 | 3.4338 | 3.8689 | 4.3041 | 0.80021 | 1.5794 | 1.8952 | 1.8952 | 1.8952 | 1.8952 | 0.89547 | 1.0417 | 1.0417 | 1.0417 | 1.0417 | 1.0417
2020-03-05 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.44011 | 0.87043 | 0.87043 | 0.87043 | 0.87043 | 0.87043 | 1.9423 | 2.5065 | 2.8762 | 3.0707 | 3.4599 | 3.849 | 0.58682 | 1.1582 | 1.3898 | 1.3898 | 1.3898 | 1.3898 | 0.87642 | 1.0195 | 1.0195 | 1.0195 | 1.0195 | 1.0195
2020-03-05 01:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.42582 | 0.84217 | 0.84217 | 0.84217 | 0.84217 | 0.84217 | 1.9243 | 2.4833 | 2.8495 | 3.0422 | 3.4277 | 3.8132 | 0.6173 | 1.2184 | 1.462 | 1.462 | 1.462 | 1.462 | 0.85737 | 0.99734 | 0.99734 | 0.99734 | 0.99734 | 0.99734
2020-03-05 02:00 | Summer | 0.56887 | 0.81414 | 1.1748 | 1.1748 | 1.1748 | 1.1748 | 0.42868 | 0.84782 | 0.84782 | 0.84782 | 0.84782 | 0.84782 | 1.8672 | 2.4095 | 2.7649 | 2.9519 | 3.3259 | 3.7 | 0.57157 | 1.1281 | 1.3537 | 1.3537 | 1.3537 | 1.3537 | 0.87642 | 1.0195 | 1.0195 | 1.0195 | 1.0195 | 1.0195
2020-03-05 03:00 | Summer | 0.60489 | 0.8657 | 1.2492 | 1.2492 | 1.2492 | 1.2492 | 0.4001 | 0.7913 | 0.7913 | 0.7913 | 0.7913 | 0.7913 | 1.81 | 2.3358 | 2.6802 | 2.8615 | 3.2241 | 3.5867 | 0.57539 | 1.1356 | 1.3628 | 1.3628 | 1.3628 | 1.3628 | 0.91452 | 1.0638 | 1.0638 | 1.0638 | 1.0638 | 1.0638
2020-03-05 04:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.54573 | 1.0793 | 1.0793 | 1.0793 | 1.0793 | 1.0793 | 1.8672 | 2.4095 | 2.7649 | 2.9519 | 3.3259 | 3.7 | 0.5792 | 1.1431 | 1.3718 | 1.3718 | 1.3718 | 1.3718 | 0.99073 | 1.1525 | 1.1525 | 1.1525 | 1.1525 | 1.1525
2020-03-05 05:00 | Summer | 0.724 | 1.0362 | 1.4952 | 1.4952 | 1.4952 | 1.4952 | 0.59729 | 1.1813 | 1.1813 | 1.1813 | 1.1813 | 1.1813 | 2.0492 | 2.6444 | 3.0344 | 3.2397 | 3.6502 | 4.0607 | 0.75053 | 1.4813 | 1.7776 | 1.7776 | 1.7776 | 1.7776 | 1.1383 | 1.3241 | 1.3241 | 1.3241 | 1.3241 | 1.3241
2020-03-05 06:00 | Summer | 0.86938 | 1.2442 | 1.7955 | 1.7955 | 1.7955 | 1.7955 | 0.85376 | 1.6885 | 1.6885 | 1.6885 | 1.6885 | 1.6885 | 2.2101 | 2.8521 | 3.2727 | 3.4941 | 3.9368 | 4.3796 | 0.97168 | 1.9178 | 2.3013 | 2.3013 | 2.3013 | 2.3013 | 1.4871 | 1.7299 | 1.7299 | 1.7299 | 1.7299 | 1.7299
2020-03-05 07:00 | Summer | 1.2631 | 1.8077 | 2.6085 | 2.6085 | 2.6085 | 2.6085 | 0.93738 | 1.8539 | 1.8539 | 1.8539 | 1.8539 | 1.8539 | 2.8579 | 3.688 | 4.2319 | 4.5182 | 5.0907 | 5.6632 | 1.105 | 2.181 | 2.6172 | 2.6172 | 2.6172 | 2.6172 | 1.829 | 2.1277 | 2.1277 | 2.1277 | 2.1277 | 2.1277
2020-03-05 08:00 | Summer | 1.7719 | 2.5359 | 3.6593 | 3.6593 | 3.6593 | 3.6593 | 1.0288 | 2.0348 | 2.0348 | 2.0348 | 2.0348 | 2.0348 | 3.0675 | 3.9585 | 4.5423 | 4.8495 | 5.464 | 6.0785 | 1.0974 | 2.166 | 2.5992 | 2.5992 | 2.5992 | 2.5992 | 2.2291 | 2.5931 | 2.5931 | 2.5931 | 2.5931 | 2.5931
2020-03-05 09:00 | Summer | 1.7338 | 2.4813 | 3.5806 | 3.5806 | 3.5806 | 3.5806 | 1.246 | 2.4643 | 2.4643 | 2.4643 | 2.4643 | 2.4643 | 3.1246 | 4.0323 | 4.6269 | 4.9399 | 5.5658 | 6.1918 | 1.0593 | 2.0908 | 2.5089 | 2.5089 | 2.5089 | 2.5089 | 2.4006 | 2.7926 | 2.7926 | 2.7926 | 2.7926 | 2.7926
2020-03-05 10:00 | Summer | 1.7528 | 2.5086 | 3.62 | 3.62 | 3.62 | 3.62 | 1.0774 | 2.1309 | 2.1309 | 2.1309 | 2.1309 | 2.1309 | 3.2008 | 4.1306 | 4.7398 | 5.0604 | 5.7016 | 6.3428 | 1.086 | 2.1434 | 2.5721 | 2.5721 | 2.5721 | 2.5721 | 2.4006 | 2.7926 | 2.7926 | 2.7926 | 2.7926 | 2.7926
2020-03-05 11:00 | Summer | 1.7338 | 2.4813 | 3.5806 | 3.5806 | 3.5806 | 3.5806 | 1.1917 | 2.357 | 2.357 | 2.357 | 2.357 | 2.357 | 3.2961 | 4.2535 | 4.8808 | 5.211 | 5.8713 | 6.5316 | 1.0669 | 2.1058 | 2.527 | 2.527 | 2.527 | 2.527 | 2.4578 | 2.8591 | 2.8591 | 2.8591 | 2.8591 | 2.8591
2020-03-05 12:00 | Summer | 1.7147 | 2.4541 | 3.5413 | 3.5413 | 3.5413 | 3.5413 | 1.1717 | 2.3174 | 2.3174 | 2.3174 | 2.3174 | 2.3174 | 3.3533 | 4.3273 | 4.9655 | 5.3013 | 5.9731 | 6.6449 | 1.0288 | 2.0306 | 2.4367 | 2.4367 | 2.4367 | 2.4367 | 2.4959 | 2.9034 | 2.9034 | 2.9034 | 2.9034 | 2.9034
2020-03-05 13:00 | Summer | 1.6957 | 2.4268 | 3.5019 | 3.5019 | 3.5019 | 3.5019 | 1.0917 | 2.1591 | 2.1591 | 2.1591 | 2.1591 | 2.1591 | 3.3342 | 4.3027 | 4.9373 | 5.2712 | 5.9392 | 6.6071 | 1.0631 | 2.0983 | 2.5179 | 2.5179 | 2.5179 | 2.5179 | 2.5149 | 2.9255 | 2.9255 | 2.9255 | 2.9255 | 2.9255
2020-03-05 14:00 | Summer | 1.6766 | 2.3995 | 3.4626 | 3.4626 | 3.4626 | 3.4626 | 1.0746 | 2.1252 | 2.1252 | 2.1252 | 2.1252 | 2.1252 | 3.1818 | 4.106 | 4.7115 | 5.0303 | 5.6677 | 6.3051 | 1.0288 | 2.0306 | 2.4367 | 2.4367 | 2.4367 | 2.4367 | 2.3816 | 2.7704 | 2.7704 | 2.7704 | 2.7704 | 2.7704
2020-03-05 15:00 | Summer | 1.6735 | 2.395 | 3.4561 | 3.4561 | 3.4561 | 3.4561 | 1.2546 | 2.4813 | 2.4813 | 2.4813 | 2.4813 | 2.4813 | 3.1627 | 4.0814 | 4.6833 | 5.0001 | 5.6337 | 6.2673 | 1.0669 | 2.1058 | 2.527 | 2.527 | 2.527 | 2.527 | 2.4006 | 2.7926 | 2.7926 | 2.7926 | 2.7926 | 2.7926
2020-03-05 16:00 | Summer | 1.6385 | 2.345 | 3.3839 | 3.3839 | 3.3839 | 3.3839 | 1.0774 | 2.1309 | 2.1309 | 2.1309 | 2.1309 | 2.1309 | 3.1437 | 4.0568 | 4.6551 | 4.97 | 5.5998 | 6.2296 | 0.99454 | 1.9629 | 2.3555 | 2.3555 | 2.3555 | 2.3555 | 2.4006 | 2.7926 | 2.7926 | 2.7926 | 2.7926 | 2.7926
2020-03-05 17:00 | Summer | 1.5242 | 2.1814 | 3.1478 | 3.1478 | 3.1478 | 3.1478 | 0.98311 | 1.9443 | 1.9443 | 1.9443 | 1.9443 | 1.9443 | 3.0484 | 3.9339 | 4.5141 | 4.8194 | 5.4301 | 6.0408 | 1.025 | 2.0231 | 2.4277 | 2.4277 | 2.4277 | 2.4277 | 2.3572 | 2.7421 | 2.7421 | 2.7421 | 2.7421 | 2.7421
2020-03-05 18:00 | Summer | 1.0727 | 1.5352 | 2.2153 | 2.2153 | 2.2153 | 2.2153 | 0.83472 | 1.6509 | 1.6509 | 1.6509 | 1.6509 | 1.6509 | 2.896 | 3.7372 | 4.2884 | 4.5784 | 5.1586 | 5.7387 | 1.0022 | 1.978 | 2.3735 | 2.3735 | 2.3735 | 2.3735 | 1.7003 | 1.9779 | 1.9779 | 1.9779 | 1.9779 | 1.9779
2020-03-05 19:00 | Summer | 0.89547 | 1.2816 | 1.8493 | 1.8493 | 1.8493 | 1.8493 | 0.79163 | 1.5656 | 1.5656 | 1.5656 | 1.5656 | 1.5656 | 2.7453 | 3.5427 | 4.0652 | 4.3401 | 4.8901 | 5.4401 | 1.0288 | 2.0306 | 2.4367 | 2.4367 | 2.4367 | 2.4367 | 1.3527 | 1.5736 | 1.5736 | 1.5736 | 1.5736 | 1.5736
2020-03-05 20:00 | Summer | 0.87642 | 1.2543 | 1.81 | 1.81 | 1.81 | 1.81 | 0.6373 | 1.2604 | 1.2604 | 1.2604 | 1.2604 | 1.2604 | 2.6293 | 3.393 | 3.8934 | 4.1567 | 4.6835 | 5.2102 | 0.98692 | 1.9479 | 2.3374 | 2.3374 | 2.3374 | 2.3374 | 1.3337 | 1.5514 | 1.5514 | 1.5514 | 1.5514 | 1.5514
2020-03-05 21:00 | Summer | 0.724 | 1.0362 | 1.4952 | 1.4952 | 1.4952 | 1.4952 | 0.55728 | 1.1022 | 1.1022 | 1.1022 | 1.1022 | 1.1022 | 2.4387 | 3.1471 | 3.6112 | 3.8555 | 4.3441 | 4.8326 | 0.89547 | 1.7674 | 2.1208 | 2.1208 | 2.1208 | 2.1208 | 1.2003 | 1.3963 | 1.3963 | 1.3963 | 1.3963 | 1.3963
2020-03-05 22:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.57157 | 1.1304 | 1.1304 | 1.1304 | 1.1304 | 1.1304 | 2.3716 | 3.0604 | 3.5118 | 3.7493 | 4.2244 | 4.6995 | 0.9069 | 1.7899 | 2.1479 | 2.1479 | 2.1479 | 2.1479 | 1.0288 | 1.1968 | 1.1968 | 1.1968 | 1.1968 | 1.1968
2020-03-05 23:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.57729 | 1.1417 | 1.1417 | 1.1417 | 1.1417 | 1.1417 | 2.2101 | 2.8521 | 3.2727 | 3.4941 | 3.9368 | 4.3796 | 0.84212 | 1.6621 | 1.9945 | 1.9945 | 1.9945 | 1.9945 | 1.0256 | 1.193 | 1.193 | 1.193 | 1.193 | 1.193
2020-03-06 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.53442 | 1.057 | 1.057 | 1.057 | 1.057 | 1.057 | 2.0577 | 2.6554 | 3.047 | 3.2531 | 3.6653 | 4.0775 | 0.67827 | 1.3387 | 1.6064 | 1.6064 | 1.6064 | 1.6064 | 1.0098 | 1.1746 | 1.1746 | 1.1746 | 1.1746 | 1.1746
2020-03-06 01:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.58872 | 1.1643 | 1.1643 | 1.1643 | 1.1643 | 1.1643 | 1.9434 | 2.5079 | 2.8777 | 3.0724 | 3.4617 | 3.851 | 0.64397 | 1.271 | 1.5252 | 1.5252 | 1.5252 | 1.5252 | 0.93358 | 1.086 | 1.086 | 1.086 | 1.086 | 1.086
2020-03-06 02:00 | Summer | 0.59049 | 0.84508 | 1.2195 | 1.2195 | 1.2195 | 1.2195 | 0.55443 | 1.0965 | 1.0965 | 1.0965 | 1.0965 | 1.0965 | 1.9434 | 2.5079 | 2.8777 | 3.0724 | 3.4617 | 3.851 | 0.53347 | 1.0529 | 1.2635 | 1.2635 | 1.2635 | 1.2635 | 0.95263 | 1.1082 | 1.1082 | 1.1082 | 1.1082 | 1.1082
2020-03-06 03:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.50298 | 0.99478 | 0.99478 | 0.99478 | 0.99478 | 0.99478 | 1.9008 | 2.4529 | 2.8147 | 3.0051 | 3.3859 | 3.7666 | 0.55252 | 1.0905 | 1.3086 | 1.3086 | 1.3086 | 1.3086 | 0.95263 | 1.1082 | 1.1082 | 1.1082 | 1.1082 | 1.1082
2020-03-06 04:00 | Summer | 0.62869 | 0.89975 | 1.2984 | 1.2984 | 1.2984 | 1.2984 | 0.52013 | 1.0287 | 1.0287 | 1.0287 | 1.0287 | 1.0287 | 1.9434 | 2.5079 | 2.8777 | 3.0724 | 3.4617 | 3.851 | 0.54871 | 1.083 | 1.2996 | 1.2996 | 1.2996 | 1.2996 | 1.0288 | 1.1968 | 1.1968 | 1.1968 | 1.1968 | 1.1968
2020-03-06 05:00 | Summer | 0.7621 | 1.0907 | 1.5739 | 1.5739 | 1.5739 | 1.5739 | 0.54014 | 1.0683 | 1.0683 | 1.0683 | 1.0683 | 1.0683 | 2.0767 | 2.68 | 3.0752 | 3.2832 | 3.6992 | 4.1153 | 0.83069 | 1.6395 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 1.2123 | 1.4103 | 1.4103 | 1.4103 | 1.4103 | 1.4103
2020-03-06 06:00 | Summer | 0.87585 | 1.2535 | 1.8088 | 1.8088 | 1.8088 | 1.8088 | 0.83736 | 1.6561 | 1.6561 | 1.6561 | 1.6561 | 1.6561 | 2.1715 | 2.8023 | 3.2156 | 3.4331 | 3.8681 | 4.3032 | 0.85355 | 1.6846 | 2.0216 | 2.0216 | 2.0216 | 2.0216 | 1.3854 | 1.6116 | 1.6116 | 1.6116 | 1.6116 | 1.6116
2020-03-06 07:00 | Summer | 1.3176 | 1.8857 | 2.7212 | 2.7212 | 2.7212 | 2.7212 | 0.95167 | 1.8822 | 1.8822 | 1.8822 | 1.8822 | 1.8822 | 2.7626 | 3.5651 | 4.0909 | 4.3676 | 4.921 | 5.4745 | 1.0784 | 2.1284 | 2.554 | 2.554 | 2.554 | 2.554 | 1.9049 | 2.2159 | 2.2159 | 2.2159 | 2.2159 | 2.2159
2020-03-06 08:00 | Summer | 1.7909 | 2.5631 | 3.6987 | 3.6987 | 3.6987 | 3.6987 | 1.0574 | 2.0913 | 2.0913 | 2.0913 | 2.0913 | 2.0913 | 3.1437 | 4.0568 | 4.6551 | 4.97 | 5.5998 | 6.2296 | 0.99835 | 1.9704 | 2.3645 | 2.3645 | 2.3645 | 2.3645 | 2.4768 | 2.8812 | 2.8812 | 2.8812 | 2.8812 | 2.8812
2020-03-06 09:00 | Summer | 1.7528 | 2.5086 | 3.62 | 3.62 | 3.62 | 3.62 | 1.0917 | 2.1591 | 2.1591 | 2.1591 | 2.1591 | 2.1591 | 3.3342 | 4.3027 | 4.9373 | 5.2712 | 5.9392 | 6.6071 | 1.0136 | 2.0005 | 2.4006 | 2.4006 | 2.4006 | 2.4006 | 2.5149 | 2.9255 | 2.9255 | 2.9255 | 2.9255 | 2.9255
2020-03-06 10:00 | Summer | 1.829 | 2.6177 | 3.7774 | 3.7774 | 3.7774 | 3.7774 | 1.1231 | 2.2213 | 2.2213 | 2.2213 | 2.2213 | 2.2213 | 3.3562 | 4.3311 | 4.9698 | 5.306 | 5.9784 | 6.6507 | 1.0365 | 2.0456 | 2.4548 | 2.4548 | 2.4548 | 2.4548 | 2.6263 | 3.0551 | 3.0551 | 3.0551 | 3.0551 | 3.0551
2020-03-06 11:00 | Summer | 1.7909 | 2.5631 | 3.6987 | 3.6987 | 3.6987 | 3.6987 | 1.1803 | 2.3343 | 2.3343 | 2.3343 | 2.3343 | 2.3343 | 3.6009 | 4.6469 | 5.3322 | 5.6929 | 6.4143 | 7.1357 | 1.0403 | 2.0532 | 2.4638 | 2.4638 | 2.4638 | 2.4638 | 2.8007 | 3.258 | 3.258 | 3.258 | 3.258 | 3.258
2020-03-06 12:00 | Summer | 1.829 | 2.6177 | 3.7774 | 3.7774 | 3.7774 | 3.7774 | 1.186 | 2.3456 | 2.3456 | 2.3456 | 2.3456 | 2.3456 | 3.639 | 4.6961 | 5.3887 | 5.7532 | 6.4822 | 7.2112 | 1.1012 | 2.1735 | 2.6082 | 2.6082 | 2.6082 | 2.6082 | 2.7245 | 3.1693 | 3.1693 | 3.1693 | 3.1693 | 3.1693
2020-03-06 13:00 | Summer | 1.8481 | 2.6449 | 3.8167 | 3.8167 | 3.8167 | 3.8167 | 1.2232 | 2.4191 | 2.4191 | 2.4191 | 2.4191 | 2.4191 | 3.7534 | 4.8436 | 5.5579 | 5.9339 | 6.6858 | 7.4377 | 1.0669 | 2.1058 | 2.527 | 2.527 | 2.527 | 2.527 | 2.7626 | 3.2137 | 3.2137 | 3.2137 | 3.2137 | 3.2137
2020-03-06 14:00 | Summer | 1.829 | 2.6177 | 3.7774 | 3.7774 | 3.7774 | 3.7774 | 1.4204 | 2.8091 | 2.8091 | 2.8091 | 2.8091 | 2.8091 | 3.7152 | 4.7944 | 5.5015 | 5.8736 | 6.6179 | 7.3622 | 1.0746 | 2.1208 | 2.545 | 2.545 | 2.545 | 2.545 | 2.7626 | 3.2137 | 3.2137 | 3.2137 | 3.2137 | 3.2137
2020-03-06 15:00 | Summer | 1.829 | 2.6177 | 3.7774 | 3.7774 | 3.7774 | 3.7774 | 1.3032 | 2.5774 | 2.5774 | 2.5774 | 2.5774 | 2.5774 | 3.639 | 4.6961 | 5.3887 | 5.7532 | 6.4822 | 7.2112 | 1.3718 | 2.7075 | 3.249 | 3.249 | 3.249 | 3.249 | 2.7436 | 3.1915 | 3.1915 | 3.1915 | 3.1915 | 3.1915
2020-03-06 16:00 | Summer | 1.6576 | 2.3723 | 3.4232 | 3.4232 | 3.4232 | 3.4232 | 1.2432 | 2.4587 | 2.4587 | 2.4587 | 2.4587 | 2.4587 | 3.4485 | 4.4502 | 5.1065 | 5.4519 | 6.1428 | 6.8336 | 1.288 | 2.542 | 3.0504 | 3.0504 | 3.0504 | 3.0504 | 2.5721 | 2.992 | 2.992 | 2.992 | 2.992 | 2.992
2020-03-06 17:00 | Summer | 1.5052 | 2.1541 | 3.1085 | 3.1085 | 3.1085 | 3.1085 | 1.3403 | 2.6509 | 2.6509 | 2.6509 | 2.6509 | 2.6509 | 3.3723 | 4.3519 | 4.9937 | 5.3315 | 6.007 | 6.6826 | 1.1432 | 2.2562 | 2.7075 | 2.7075 | 2.7075 | 2.7075 | 2.3863 | 2.7758 | 2.7758 | 2.7758 | 2.7758 | 2.7758
2020-03-06 18:00 | Summer | 0.95519 | 1.367 | 1.9727 | 1.9727 | 1.9727 | 1.9727 | 1.0778 | 2.1316 | 2.1316 | 2.1316 | 2.1316 | 2.1316 | 3.0413 | 3.9248 | 4.5036 | 4.8082 | 5.4175 | 6.0268 | 0.98311 | 1.9403 | 2.3284 | 2.3284 | 2.3284 | 2.3284 | 1.7403 | 2.0244 | 2.0244 | 2.0244 | 2.0244 | 2.0244
2020-03-06 19:00 | Summer | 0.724 | 1.0362 | 1.4952 | 1.4952 | 1.4952 | 1.4952 | 0.83736 | 1.6561 | 1.6561 | 1.6561 | 1.6561 | 1.6561 | 2.6568 | 3.4286 | 3.9342 | 4.2004 | 4.7326 | 5.2648 | 0.91833 | 1.8125 | 2.175 | 2.175 | 2.175 | 2.175 | 1.2956 | 1.5071 | 1.5071 | 1.5071 | 1.5071 | 1.5071
2020-03-06 20:00 | Summer | 0.70144 | 1.0039 | 1.4486 | 1.4486 | 1.4486 | 1.4486 | 0.84021 | 1.6617 | 1.6617 | 1.6617 | 1.6617 | 1.6617 | 2.4927 | 3.2168 | 3.6912 | 3.9409 | 4.4403 | 4.9397 | 0.94119 | 1.8576 | 2.2291 | 2.2291 | 2.2291 | 2.2291 | 1.2194 | 1.4184 | 1.4184 | 1.4184 | 1.4184 | 1.4184
2020-03-06 21:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.76877 | 1.5204 | 1.5204 | 1.5204 | 1.5204 | 1.5204 | 2.5149 | 3.2455 | 3.7241 | 3.976 | 4.4798 | 4.9836 | 0.89547 | 1.7674 | 2.1208 | 2.1208 | 2.1208 | 2.1208 | 1.2003 | 1.3963 | 1.3963 | 1.3963 | 1.3963 | 1.3963
2020-03-06 22:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.73733 | 1.4583 | 1.4583 | 1.4583 | 1.4583 | 1.4583 | 2.3435 | 3.0242 | 3.4702 | 3.7049 | 4.1744 | 4.6438 | 0.91071 | 1.7975 | 2.1569 | 2.1569 | 2.1569 | 2.1569 | 1.0479 | 1.219 | 1.219 | 1.219 | 1.219 | 1.219
2020-03-06 23:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.70875 | 1.4017 | 1.4017 | 1.4017 | 1.4017 | 1.4017 | 2.1423 | 2.7646 | 3.1724 | 3.3869 | 3.8161 | 4.2453 | 0.83831 | 1.6546 | 1.9855 | 1.9855 | 1.9855 | 1.9855 | 0.97168 | 1.1303 | 1.1303 | 1.1303 | 1.1303 | 1.1303
2020-03-07 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.55728 | 1.1022 | 1.1022 | 1.1022 | 1.1022 | 1.1022 | 2.0196 | 2.6062 | 2.9906 | 3.1929 | 3.5974 | 4.002 | 0.57394 | 1.1328 | 1.3593 | 1.3593 | 1.3593 | 1.3593 | 0.95263 | 1.1082 | 1.1082 | 1.1082 | 1.1082 | 1.1082
2020-03-07 01:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.46587 | 0.92137 | 0.92137 | 0.92137 | 0.92137 | 0.92137 | 1.9143 | 2.4703 | 2.8346 | 3.0264 | 3.4099 | 3.7933 | 0.54871 | 1.083 | 1.2996 | 1.2996 | 1.2996 | 1.2996 | 0.95263 | 1.1082 | 1.1082 | 1.1082 | 1.1082 | 1.1082
2020-03-07 02:00 | Summer | 0.59056 | 0.84518 | 1.2196 | 1.2196 | 1.2196 | 1.2196 | 0.46583 | 0.9213 | 0.9213 | 0.9213 | 0.9213 | 0.9213 | 1.9053 | 2.4587 | 2.8213 | 3.0121 | 3.3938 | 3.7755 | 0.53728 | 1.0604 | 1.2725 | 1.2725 | 1.2725 | 1.2725 | 0.91452 | 1.0638 | 1.0638 | 1.0638 | 1.0638 | 1.0638
2020-03-07 03:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.47726 | 0.94391 | 0.94391 | 0.94391 | 0.94391 | 0.94391 | 1.9053 | 2.4587 | 2.8213 | 3.0121 | 3.3938 | 3.7755 | 0.63635 | 1.256 | 1.5072 | 1.5072 | 1.5072 | 1.5072 | 0.87642 | 1.0195 | 1.0195 | 1.0195 | 1.0195 | 1.0195
2020-03-07 04:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.47155 | 0.9326 | 0.9326 | 0.9326 | 0.9326 | 0.9326 | 1.829 | 2.3603 | 2.7084 | 2.8916 | 3.2581 | 3.6245 | 0.63635 | 1.256 | 1.5072 | 1.5072 | 1.5072 | 1.5072 | 0.89547 | 1.0417 | 1.0417 | 1.0417 | 1.0417 | 1.0417
2020-03-07 05:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.48298 | 0.95521 | 0.95521 | 0.95521 | 0.95521 | 0.95521 | 1.897 | 2.448 | 2.809 | 2.999 | 3.379 | 3.759 | 0.69732 | 1.3763 | 1.6516 | 1.6516 | 1.6516 | 1.6516 | 0.91452 | 1.0638 | 1.0638 | 1.0638 | 1.0638 | 1.0638
2020-03-07 06:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.50298 | 0.99478 | 0.99478 | 0.99478 | 0.99478 | 0.99478 | 1.9243 | 2.4833 | 2.8495 | 3.0422 | 3.4277 | 3.8132 | 0.73543 | 1.4515 | 1.7418 | 1.7418 | 1.7418 | 1.7418 | 1.0349 | 1.2038 | 1.2038 | 1.2038 | 1.2038 | 1.2038
2020-03-07 07:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.59158 | 1.17 | 1.17 | 1.17 | 1.17 | 1.17 | 2.0767 | 2.68 | 3.0752 | 3.2832 | 3.6992 | 4.1153 | 0.77353 | 1.5267 | 1.832 | 1.832 | 1.832 | 1.832 | 1.1432 | 1.3298 | 1.3298 | 1.3298 | 1.3298 | 1.3298
2020-03-07 08:00 | Summer | 0.64779 | 0.92709 | 1.3378 | 1.3378 | 1.3378 | 1.3378 | 0.60587 | 1.1983 | 1.1983 | 1.1983 | 1.1983 | 1.1983 | 2.3244 | 2.9996 | 3.442 | 3.6748 | 4.1404 | 4.6061 | 0.86117 | 1.6997 | 2.0396 | 2.0396 | 2.0396 | 2.0396 | 1.105 | 1.2855 | 1.2855 | 1.2855 | 1.2855 | 1.2855
2020-03-07 09:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.66659 | 1.3184 | 1.3184 | 1.3184 | 1.3184 | 1.3184 | 2.3435 | 3.0242 | 3.4702 | 3.7049 | 4.1744 | 4.6438 | 0.86498 | 1.7072 | 2.0486 | 2.0486 | 2.0486 | 2.0486 | 1.1813 | 1.3741 | 1.3741 | 1.3741 | 1.3741 | 1.3741
2020-03-07 10:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.77162 | 1.5261 | 1.5261 | 1.5261 | 1.5261 | 1.5261 | 2.4189 | 3.1216 | 3.5819 | 3.8242 | 4.3088 | 4.7934 | 0.84212 | 1.6621 | 1.9945 | 1.9945 | 1.9945 | 1.9945 | 1.2575 | 1.4628 | 1.4628 | 1.4628 | 1.4628 | 1.4628
2020-03-07 11:00 | Summer | 0.64779 | 0.92709 | 1.3378 | 1.3378 | 1.3378 | 1.3378 | 0.75095 | 1.4852 | 1.4852 | 1.4852 | 1.4852 | 1.4852 | 2.4959 | 3.2209 | 3.6959 | 3.9459 | 4.4459 | 4.9459 | 0.9069 | 1.7899 | 2.1479 | 2.1479 | 2.1479 | 2.1479 | 1.1813 | 1.3741 | 1.3741 | 1.3741 | 1.3741 | 1.3741
2020-03-07 12:00 | Summer | 0.61034 | 0.8735 | 1.2605 | 1.2605 | 1.2605 | 1.2605 | 0.76877 | 1.5204 | 1.5204 | 1.5204 | 1.5204 | 1.5204 | 2.4959 | 3.2209 | 3.6959 | 3.9459 | 4.4459 | 4.9459 | 0.82307 | 1.6245 | 1.9494 | 1.9494 | 1.9494 | 1.9494 | 1.2194 | 1.4184 | 1.4184 | 1.4184 | 1.4184 | 1.4184
2020-03-07 13:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.82021 | 1.6222 | 1.6222 | 1.6222 | 1.6222 | 1.6222 | 2.5911 | 3.3438 | 3.8369 | 4.0965 | 4.6156 | 5.1347 | 0.86498 | 1.7072 | 2.0486 | 2.0486 | 2.0486 | 2.0486 | 1.1793 | 1.3718 | 1.3718 | 1.3718 | 1.3718 | 1.3718
2020-03-07 14:00 | Summer | 0.5581 | 0.79873 | 1.1526 | 1.1526 | 1.1526 | 1.1526 | 0.82021 | 1.6222 | 1.6222 | 1.6222 | 1.6222 | 1.6222 | 2.5911 | 3.3438 | 3.8369 | 4.0965 | 4.6156 | 5.1347 | 0.89166 | 1.7599 | 2.1118 | 2.1118 | 2.1118 | 2.1118 | 1.1622 | 1.352 | 1.352 | 1.352 | 1.352 | 1.352
2020-03-07 15:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.85165 | 1.6843 | 1.6843 | 1.6843 | 1.6843 | 1.6843 | 2.6102 | 3.3684 | 3.8652 | 4.1266 | 4.6495 | 5.1724 | 0.92595 | 1.8275 | 2.193 | 2.193 | 2.193 | 2.193 | 1.1407 | 1.327 | 1.327 | 1.327 | 1.327 | 1.327
2020-03-07 16:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.8002 | 1.5826 | 1.5826 | 1.5826 | 1.5826 | 1.5826 | 2.5721 | 3.3192 | 3.8087 | 4.0664 | 4.5816 | 5.0969 | 0.97168 | 1.9178 | 2.3013 | 2.3013 | 2.3013 | 2.3013 | 1.105 | 1.2855 | 1.2855 | 1.2855 | 1.2855 | 1.2855
2020-03-07 17:00 | Summer | 0.7621 | 1.0907 | 1.5739 | 1.5739 | 1.5739 | 1.5739 | 0.84307 | 1.6674 | 1.6674 | 1.6674 | 1.6674 | 1.6674 | 2.6102 | 3.3684 | 3.8652 | 4.1266 | 4.6495 | 5.1724 | 0.96406 | 1.9027 | 2.2833 | 2.2833 | 2.2833 | 2.2833 | 1.086 | 1.2633 | 1.2633 | 1.2633 | 1.2633 | 1.2633
2020-03-07 18:00 | Summer | 0.74305 | 1.0634 | 1.5346 | 1.5346 | 1.5346 | 1.5346 | 0.75448 | 1.4922 | 1.4922 | 1.4922 | 1.4922 | 1.4922 | 2.5327 | 3.2684 | 3.7504 | 4.004 | 4.5114 | 5.0188 | 0.9069 | 1.7899 | 2.1479 | 2.1479 | 2.1479 | 2.1479 | 1.0534 | 1.2254 | 1.2254 | 1.2254 | 1.2254 | 1.2254
2020-03-07 19:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.72876 | 1.4413 | 1.4413 | 1.4413 | 1.4413 | 1.4413 | 2.3816 | 3.0734 | 3.5266 | 3.7652 | 4.2423 | 4.7194 | 0.97168 | 1.9178 | 2.3013 | 2.3013 | 2.3013 | 2.3013 | 1.0669 | 1.2411 | 1.2411 | 1.2411 | 1.2411 | 1.2411
2020-03-07 20:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.62301 | 1.2322 | 1.2322 | 1.2322 | 1.2322 | 1.2322 | 2.3625 | 3.0488 | 3.4984 | 3.735 | 4.2083 | 4.6816 | 0.94119 | 1.8576 | 2.2291 | 2.2291 | 2.2291 | 2.2291 | 1.0479 | 1.219 | 1.219 | 1.219 | 1.219 | 1.219
2020-03-07 21:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.6373 | 1.2604 | 1.2604 | 1.2604 | 1.2604 | 1.2604 | 2.2863 | 2.9504 | 3.3855 | 3.6146 | 4.0726 | 4.5306 | 0.93738 | 1.8501 | 2.2201 | 2.2201 | 2.2201 | 2.2201 | 1.0118 | 1.177 | 1.177 | 1.177 | 1.177 | 1.177
2020-03-07 22:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.64588 | 1.2774 | 1.2774 | 1.2774 | 1.2774 | 1.2774 | 2.2291 | 2.8767 | 3.3009 | 3.5242 | 3.9708 | 4.4173 | 0.84593 | 1.6696 | 2.0035 | 2.0035 | 2.0035 | 2.0035 | 0.95263 | 1.1082 | 1.1082 | 1.1082 | 1.1082 | 1.1082
2020-03-07 23:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.56014 | 1.1078 | 1.1078 | 1.1078 | 1.1078 | 1.1078 | 2.1148 | 2.7291 | 3.1316 | 3.3435 | 3.7671 | 4.1908 | 0.87642 | 1.7298 | 2.0757 | 2.0757 | 2.0757 | 2.0757 | 0.89547 | 1.0417 | 1.0417 | 1.0417 | 1.0417 | 1.0417
2020-03-08 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.48298 | 0.95521 | 0.95521 | 0.95521 | 0.95521 | 0.95521 | 1.9053 | 2.4587 | 2.8213 | 3.0121 | 3.3938 | 3.7755 | 0.63254 | 1.2484 | 1.4981 | 1.4981 | 1.4981 | 1.4981 | 0.89547 | 1.0417 | 1.0417 | 1.0417 | 1.0417 | 1.0417
2020-03-08 01:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.43439 | 0.85912 | 0.85912 | 0.85912 | 0.85912 | 0.85912 | 1.7719 | 2.2866 | 2.6238 | 2.8013 | 3.1562 | 3.5112 | 0.56014 | 1.1055 | 1.3267 | 1.3267 | 1.3267 | 1.3267 | 0.87642 | 1.0195 | 1.0195 | 1.0195 | 1.0195 | 1.0195
2020-03-08 02:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.46414 | 0.91796 | 0.91796 | 0.91796 | 0.91796 | 0.91796 | 1.7909 | 2.3112 | 2.652 | 2.8314 | 3.1902 | 3.549 | 0.53728 | 1.0604 | 1.2725 | 1.2725 | 1.2725 | 1.2725 | 0.87642 | 1.0195 | 1.0195 | 1.0195 | 1.0195 | 1.0195
2020-03-08 03:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.46583 | 0.9213 | 0.9213 | 0.9213 | 0.9213 | 0.9213 | 1.6957 | 2.1882 | 2.5109 | 2.6808 | 3.0205 | 3.3602 | 0.54871 | 1.083 | 1.2996 | 1.2996 | 1.2996 | 1.2996 | 0.85737 | 0.99734 | 0.99734 | 0.99734 | 0.99734 | 0.99734
2020-03-08 04:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.46583 | 0.9213 | 0.9213 | 0.9213 | 0.9213 | 0.9213 | 1.6957 | 2.1882 | 2.5109 | 2.6808 | 3.0205 | 3.3602 | 0.5449 | 1.0755 | 1.2906 | 1.2906 | 1.2906 | 1.2906 | 0.85737 | 0.99734 | 0.99734 | 0.99734 | 0.99734 | 0.99734
2020-03-08 05:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.44583 | 0.88173 | 0.88173 | 0.88173 | 0.88173 | 0.88173 | 1.7719 | 2.2866 | 2.6238 | 2.8013 | 3.1562 | 3.5112 | 0.84974 | 1.6771 | 2.0125 | 2.0125 | 2.0125 | 2.0125 | 0.85737 | 0.99734 | 0.99734 | 0.99734 | 0.99734 | 0.99734
2020-03-08 06:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.49155 | 0.97217 | 0.97217 | 0.97217 | 0.97217 | 0.97217 | 1.829 | 2.3603 | 2.7084 | 2.8916 | 3.2581 | 3.6245 | 0.84593 | 1.6696 | 2.0035 | 2.0035 | 2.0035 | 2.0035 | 0.89547 | 1.0417 | 1.0417 | 1.0417 | 1.0417 | 1.0417
2020-03-08 07:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.58872 | 1.1643 | 1.1643 | 1.1643 | 1.1643 | 1.1643 | 2.0196 | 2.6062 | 2.9906 | 3.1929 | 3.5974 | 4.002 | 0.82307 | 1.6245 | 1.9494 | 1.9494 | 1.9494 | 1.9494 | 0.85903 | 0.99928 | 0.99928 | 0.99928 | 0.99928 | 0.99928
2020-03-08 08:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.60015 | 1.187 | 1.187 | 1.187 | 1.187 | 1.187 | 2.1339 | 2.7537 | 3.1598 | 3.3736 | 3.8011 | 4.2285 | 0.8345 | 1.647 | 1.9764 | 1.9764 | 1.9764 | 1.9764 | 0.93358 | 1.086 | 1.086 | 1.086 | 1.086 | 1.086
2020-03-08 09:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.60587 | 1.1983 | 1.1983 | 1.1983 | 1.1983 | 1.1983 | 2.2291 | 2.8767 | 3.3009 | 3.5242 | 3.9708 | 4.4173 | 0.88785 | 1.7523 | 2.1028 | 2.1028 | 2.1028 | 2.1028 | 0.93358 | 1.086 | 1.086 | 1.086 | 1.086 | 1.086
2020-03-08 10:00 | Summer | 0.59649 | 0.85367 | 1.2319 | 1.2319 | 1.2319 | 1.2319 | 0.5287 | 1.0456 | 1.0456 | 1.0456 | 1.0456 | 1.0456 | 2.2673 | 2.9258 | 3.3573 | 3.5844 | 4.0386 | 4.4928 | 0.7964 | 1.5718 | 1.8862 | 1.8862 | 1.8862 | 1.8862 | 1.0098 | 1.1746 | 1.1746 | 1.1746 | 1.1746 | 1.1746
2020-03-08 11:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.45726 | 0.90434 | 0.90434 | 0.90434 | 0.90434 | 0.90434 | 2.3244 | 2.9996 | 3.442 | 3.6748 | 4.1404 | 4.6061 | 0.80783 | 1.5944 | 1.9133 | 1.9133 | 1.9133 | 1.9133 | 1.0098 | 1.1746 | 1.1746 | 1.1746 | 1.1746 | 1.1746
2020-03-08 12:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.63445 | 1.2548 | 1.2548 | 1.2548 | 1.2548 | 1.2548 | 2.4006 | 3.098 | 3.5548 | 3.7953 | 4.2762 | 4.7571 | 0.83831 | 1.6546 | 1.9855 | 1.9855 | 1.9855 | 1.9855 | 0.9948 | 1.1572 | 1.1572 | 1.1572 | 1.1572 | 1.1572
2020-03-08 13:00 | Summer | 0.7621 | 1.0907 | 1.5739 | 1.5739 | 1.5739 | 1.5739 | 0.59158 | 1.17 | 1.17 | 1.17 | 1.17 | 1.17 | 2.4006 | 3.098 | 3.5548 | 3.7953 | 4.2762 | 4.7571 | 0.81545 | 1.6094 | 1.9313 | 1.9313 | 1.9313 | 1.9313 | 1.0479 | 1.219 | 1.219 | 1.219 | 1.219 | 1.219
2020-03-08 14:00 | Summer | 0.75228 | 1.0766 | 1.5536 | 1.5536 | 1.5536 | 1.5536 | 0.61029 | 1.207 | 1.207 | 1.207 | 1.207 | 1.207 | 2.4197 | 3.1225 | 3.583 | 3.8254 | 4.3101 | 4.7949 | 0.79258 | 1.5643 | 1.8772 | 1.8772 | 1.8772 | 1.8772 | 1.1241 | 1.3076 | 1.3076 | 1.3076 | 1.3076 | 1.3076
2020-03-08 15:00 | Summer | 0.70494 | 1.0089 | 1.4559 | 1.4559 | 1.4559 | 1.4559 | 0.65159 | 1.2887 | 1.2887 | 1.2887 | 1.2887 | 1.2887 | 2.2673 | 2.9258 | 3.3573 | 3.5844 | 4.0386 | 4.4928 | 0.80021 | 1.5794 | 1.8952 | 1.8952 | 1.8952 | 1.8952 | 1.0669 | 1.2411 | 1.2411 | 1.2411 | 1.2411 | 1.2411
2020-03-08 16:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.64016 | 1.2661 | 1.2661 | 1.2661 | 1.2661 | 1.2661 | 2.3435 | 3.0242 | 3.4702 | 3.7049 | 4.1744 | 4.6438 | 0.76591 | 1.5117 | 1.814 | 1.814 | 1.814 | 1.814 | 1.0479 | 1.219 | 1.219 | 1.219 | 1.219 | 1.219
2020-03-08 17:00 | Summer | 0.64779 | 0.92709 | 1.3378 | 1.3378 | 1.3378 | 1.3378 | 0.6373 | 1.2604 | 1.2604 | 1.2604 | 1.2604 | 1.2604 | 2.3054 | 2.975 | 3.4138 | 3.6447 | 4.1065 | 4.5683 | 0.82307 | 1.6245 | 1.9494 | 1.9494 | 1.9494 | 1.9494 | 0.99073 | 1.1525 | 1.1525 | 1.1525 | 1.1525 | 1.1525
2020-03-08 18:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.60301 | 1.1926 | 1.1926 | 1.1926 | 1.1926 | 1.1926 | 2.2673 | 2.9258 | 3.3573 | 3.5844 | 4.0386 | 4.4928 | 0.80021 | 1.5794 | 1.8952 | 1.8952 | 1.8952 | 1.8952 | 0.90289 | 1.0503 | 1.0503 | 1.0503 | 1.0503 | 1.0503
2020-03-08 19:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.59158 | 1.17 | 1.17 | 1.17 | 1.17 | 1.17 | 2.2101 | 2.8521 | 3.2727 | 3.4941 | 3.9368 | 4.3796 | 0.86117 | 1.6997 | 2.0396 | 2.0396 | 2.0396 | 2.0396 | 0.91452 | 1.0638 | 1.0638 | 1.0638 | 1.0638 | 1.0638
2020-03-08 20:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.63445 | 1.2548 | 1.2548 | 1.2548 | 1.2548 | 1.2548 | 2.2101 | 2.8521 | 3.2727 | 3.4941 | 3.9368 | 4.3796 | 0.85736 | 1.6922 | 2.0306 | 2.0306 | 2.0306 | 2.0306 | 0.93358 | 1.086 | 1.086 | 1.086 | 1.086 | 1.086
2020-03-08 21:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.55443 | 1.0965 | 1.0965 | 1.0965 | 1.0965 | 1.0965 | 2.1339 | 2.7537 | 3.1598 | 3.3736 | 3.8011 | 4.2285 | 0.89928 | 1.7749 | 2.1299 | 2.1299 | 2.1299 | 2.1299 | 0.91452 | 1.0638 | 1.0638 | 1.0638 | 1.0638 | 1.0638
2020-03-08 22:00 | Summer | 0.61601 | 0.88161 | 1.2722 | 1.2722 | 1.2722 | 1.2722 | 0.59729 | 1.1813 | 1.1813 | 1.1813 | 1.1813 | 1.1813 | 2.0767 | 2.68 | 3.0752 | 3.2832 | 3.6992 | 4.1153 | 0.91071 | 1.7975 | 2.1569 | 2.1569 | 2.1569 | 2.1569 | 0.93358 | 1.086 | 1.086 | 1.086 | 1.086 | 1.086
2020-03-08 23:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.583 | 1.153 | 1.153 | 1.153 | 1.153 | 1.153 | 2.0005 | 2.5816 | 2.9624 | 3.1627 | 3.5635 | 3.9643 | 0.65164 | 1.2861 | 1.5434 | 1.5434 | 1.5434 | 1.5434 | 0.87642 | 1.0195 | 1.0195 | 1.0195 | 1.0195 | 1.0195
2020-03-09 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.57157 | 1.1304 | 1.1304 | 1.1304 | 1.1304 | 1.1304 | 1.8672 | 2.4095 | 2.7649 | 2.9519 | 3.3259 | 3.7 | 0.58301 | 1.1507 | 1.3808 | 1.3808 | 1.3808 | 1.3808 | 0.87642 | 1.0195 | 1.0195 | 1.0195 | 1.0195 | 1.0195
2020-03-09 01:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.55157 | 1.0909 | 1.0909 | 1.0909 | 1.0909 | 1.0909 | 1.7909 | 2.3112 | 2.652 | 2.8314 | 3.1902 | 3.549 | 0.56776 | 1.1206 | 1.3447 | 1.3447 | 1.3447 | 1.3447 | 0.87642 | 1.0195 | 1.0195 | 1.0195 | 1.0195 | 1.0195
2020-03-09 02:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.52299 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.829 | 2.3603 | 2.7084 | 2.8916 | 3.2581 | 3.6245 | 0.56395 | 1.1131 | 1.3357 | 1.3357 | 1.3357 | 1.3357 | 0.85737 | 0.99734 | 0.99734 | 0.99734 | 0.99734 | 0.99734
2020-03-09 03:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.52585 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.7386 | 2.2436 | 2.5745 | 2.7487 | 3.097 | 3.4453 | 0.54109 | 1.0679 | 1.2815 | 1.2815 | 1.2815 | 1.2815 | 0.91452 | 1.0638 | 1.0638 | 1.0638 | 1.0638 | 1.0638
2020-03-09 04:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.51727 | 1.023 | 1.023 | 1.023 | 1.023 | 1.023 | 1.7719 | 2.2866 | 2.6238 | 2.8013 | 3.1562 | 3.5112 | 0.59825 | 1.1808 | 1.4169 | 1.4169 | 1.4169 | 1.4169 | 0.9197 | 1.0699 | 1.0699 | 1.0699 | 1.0699 | 1.0699
2020-03-09 05:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.48869 | 0.96652 | 0.96652 | 0.96652 | 0.96652 | 0.96652 | 1.7909 | 2.3112 | 2.652 | 2.8314 | 3.1902 | 3.549 | 0.83831 | 1.6546 | 1.9855 | 1.9855 | 1.9855 | 1.9855 | 1.1432 | 1.3298 | 1.3298 | 1.3298 | 1.3298 | 1.3298
2020-03-09 06:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.563 | 1.1135 | 1.1135 | 1.1135 | 1.1135 | 1.1135 | 1.9434 | 2.5079 | 2.8777 | 3.0724 | 3.4617 | 3.851 | 0.83069 | 1.6395 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 1.4166 | 1.6479 | 1.6479 | 1.6479 | 1.6479 | 1.6479
2020-03-09 07:00 | Summer | 0.64779 | 0.92709 | 1.3378 | 1.3378 | 1.3378 | 1.3378 | 0.51156 | 1.0117 | 1.0117 | 1.0117 | 1.0117 | 1.0117 | 2.0145 | 2.5996 | 2.983 | 3.1848 | 3.5884 | 3.9919 | 0.86879 | 1.7147 | 2.0577 | 2.0577 | 2.0577 | 2.0577 | 1.5433 | 1.7952 | 1.7952 | 1.7952 | 1.7952 | 1.7952
2020-03-09 08:00 | Summer | 0.64779 | 0.92709 | 1.3378 | 1.3378 | 1.3378 | 1.3378 | 0.57157 | 1.1304 | 1.1304 | 1.1304 | 1.1304 | 1.1304 | 2.2482 | 2.9013 | 3.3291 | 3.5543 | 4.0047 | 4.4551 | 0.88785 | 1.7523 | 2.1028 | 2.1028 | 2.1028 | 2.1028 | 1.5623 | 1.8174 | 1.8174 | 1.8174 | 1.8174 | 1.8174
2020-03-09 09:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.63159 | 1.2491 | 1.2491 | 1.2491 | 1.2491 | 1.2491 | 2.3244 | 2.9996 | 3.442 | 3.6748 | 4.1404 | 4.6061 | 0.94119 | 1.8576 | 2.2291 | 2.2291 | 2.2291 | 2.2291 | 1.5814 | 1.8395 | 1.8395 | 1.8395 | 1.8395 | 1.8395
2020-03-09 10:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.68589 | 1.3565 | 1.3565 | 1.3565 | 1.3565 | 1.3565 | 2.3244 | 2.9996 | 3.442 | 3.6748 | 4.1404 | 4.6061 | 0.92214 | 1.82 | 2.184 | 2.184 | 2.184 | 2.184 | 1.6004 | 1.8617 | 1.8617 | 1.8617 | 1.8617 | 1.8617
2020-03-09 11:00 | Summer | 0.66684 | 0.95435 | 1.3772 | 1.3772 | 1.3772 | 1.3772 | 0.53728 | 1.0626 | 1.0626 | 1.0626 | 1.0626 | 1.0626 | 2.4578 | 3.1717 | 3.6395 | 3.8856 | 4.378 | 4.8704 | 0.92214 | 1.82 | 2.184 | 2.184 | 2.184 | 2.184 | 1.6385 | 1.906 | 1.906 | 1.906 | 1.906 | 1.906
2020-03-09 12:00 | Summer | 0.64779 | 0.92709 | 1.3378 | 1.3378 | 1.3378 | 1.3378 | 0.60873 | 1.2039 | 1.2039 | 1.2039 | 1.2039 | 1.2039 | 2.4197 | 3.1225 | 3.583 | 3.8254 | 4.3101 | 4.7949 | 0.86498 | 1.7072 | 2.0486 | 2.0486 | 2.0486 | 2.0486 | 1.5814 | 1.8395 | 1.8395 | 1.8395 | 1.8395 | 1.8395
2020-03-09 13:00 | Summer | 0.65167 | 0.93265 | 1.3458 | 1.3458 | 1.3458 | 1.3458 | 0.583 | 1.153 | 1.153 | 1.153 | 1.153 | 1.153 | 2.4959 | 3.2209 | 3.6959 | 3.9459 | 4.4459 | 4.9459 | 0.88785 | 1.7523 | 2.1028 | 2.1028 | 2.1028 | 2.1028 | 1.6385 | 1.906 | 1.906 | 1.906 | 1.906 | 1.906
2020-03-09 14:00 | Summer | 0.66684 | 0.95435 | 1.3772 | 1.3772 | 1.3772 | 1.3772 | 0.60873 | 1.2039 | 1.2039 | 1.2039 | 1.2039 | 1.2039 | 2.4768 | 3.1963 | 3.6677 | 3.9158 | 4.4119 | 4.9081 | 0.88023 | 1.7373 | 2.0847 | 2.0847 | 2.0847 | 2.0847 | 1.6195 | 1.8839 | 1.8839 | 1.8839 | 1.8839 | 1.8839
2020-03-09 15:00 | Summer | 0.68589 | 0.98162 | 1.4165 | 1.4165 | 1.4165 | 1.4165 | 0.58015 | 1.1474 | 1.1474 | 1.1474 | 1.1474 | 1.1474 | 2.5149 | 3.2455 | 3.7241 | 3.976 | 4.4798 | 4.9836 | 0.90309 | 1.7824 | 2.1389 | 2.1389 | 2.1389 | 2.1389 | 1.6957 | 1.9725 | 1.9725 | 1.9725 | 1.9725 | 1.9725
2020-03-09 16:00 | Summer | 0.724 | 1.0362 | 1.4952 | 1.4952 | 1.4952 | 1.4952 | 0.54014 | 1.0683 | 1.0683 | 1.0683 | 1.0683 | 1.0683 | 2.534 | 3.2701 | 3.7523 | 4.0061 | 4.5138 | 5.0214 | 0.95263 | 1.8802 | 2.2562 | 2.2562 | 2.2562 | 2.2562 | 1.6385 | 1.906 | 1.906 | 1.906 | 1.906 | 1.906
2020-03-09 17:00 | Summer | 0.64779 | 0.92709 | 1.3378 | 1.3378 | 1.3378 | 1.3378 | 0.52585 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 2.6293 | 3.393 | 3.8934 | 4.1567 | 4.6835 | 5.2102 | 0.94119 | 1.8576 | 2.2291 | 2.2291 | 2.2291 | 2.2291 | 1.5628 | 1.818 | 1.818 | 1.818 | 1.818 | 1.818
2020-03-09 18:00 | Summer | 0.62992 | 0.90151 | 1.3009 | 1.3009 | 1.3009 | 1.3009 | 0.58015 | 1.1474 | 1.1474 | 1.1474 | 1.1474 | 1.1474 | 2.4578 | 3.1717 | 3.6395 | 3.8856 | 4.378 | 4.8704 | 0.81545 | 1.6094 | 1.9313 | 1.9313 | 1.9313 | 1.9313 | 1.2635 | 1.4698 | 1.4698 | 1.4698 | 1.4698 | 1.4698
2020-03-09 19:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.50584 | 1.0004 | 1.0004 | 1.0004 | 1.0004 | 1.0004 | 2.2863 | 2.9504 | 3.3855 | 3.6146 | 4.0726 | 4.5306 | 0.83069 | 1.6395 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 1.0288 | 1.1968 | 1.1968 | 1.1968 | 1.1968 | 1.1968
2020-03-09 20:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.48298 | 0.95521 | 0.95521 | 0.95521 | 0.95521 | 0.95521 | 2.2482 | 2.9013 | 3.3291 | 3.5543 | 4.0047 | 4.4551 | 0.79258 | 1.5643 | 1.8772 | 1.8772 | 1.8772 | 1.8772 | 0.99073 | 1.1525 | 1.1525 | 1.1525 | 1.1525 | 1.1525
2020-03-09 21:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.43725 | 0.86478 | 0.86478 | 0.86478 | 0.86478 | 0.86478 | 2.172 | 2.8029 | 3.2163 | 3.4338 | 3.8689 | 4.3041 | 0.84974 | 1.6771 | 2.0125 | 2.0125 | 2.0125 | 2.0125 | 0.93902 | 1.0923 | 1.0923 | 1.0923 | 1.0923 | 1.0923
2020-03-09 22:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.43439 | 0.85912 | 0.85912 | 0.85912 | 0.85912 | 0.85912 | 2.0196 | 2.6062 | 2.9906 | 3.1929 | 3.5974 | 4.002 | 0.82688 | 1.632 | 1.9584 | 1.9584 | 1.9584 | 1.9584 | 0.91452 | 1.0638 | 1.0638 | 1.0638 | 1.0638 | 1.0638
2020-03-09 23:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.38581 | 0.76304 | 0.76304 | 0.76304 | 0.76304 | 0.76304 | 2.0196 | 2.6062 | 2.9906 | 3.1929 | 3.5974 | 4.002 | 0.72018 | 1.4214 | 1.7057 | 1.7057 | 1.7057 | 1.7057 | 0.85737 | 0.99734 | 0.99734 | 0.99734 | 0.99734 | 0.99734
2020-03-10 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.39724 | 0.78565 | 0.78565 | 0.78565 | 0.78565 | 0.78565 | 1.7719 | 2.2866 | 2.6238 | 2.8013 | 3.1562 | 3.5112 | 0.56776 | 1.1206 | 1.3447 | 1.3447 | 1.3447 | 1.3447 | 0.85737 | 0.99734 | 0.99734 | 0.99734 | 0.99734 | 0.99734
2020-03-10 01:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.35553 | 0.70316 | 0.70316 | 0.70316 | 0.70316 | 0.70316 | 1.7614 | 2.273 | 2.6082 | 2.7847 | 3.1375 | 3.4904 | 0.52585 | 1.0379 | 1.2454 | 1.2454 | 1.2454 | 1.2454 | 0.85737 | 0.99734 | 0.99734 | 0.99734 | 0.99734 | 0.99734
2020-03-10 02:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.33151 | 0.65565 | 0.65565 | 0.65565 | 0.65565 | 0.65565 | 1.6901 | 2.181 | 2.5026 | 2.6719 | 3.0105 | 3.3491 | 0.54871 | 1.083 | 1.2996 | 1.2996 | 1.2996 | 1.2996 | 0.89547 | 1.0417 | 1.0417 | 1.0417 | 1.0417 | 1.0417
2020-03-10 03:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.3143 | 0.62161 | 0.62161 | 0.62161 | 0.62161 | 0.62161 | 1.7528 | 2.262 | 2.5956 | 2.7712 | 3.1223 | 3.4734 | 0.54871 | 1.083 | 1.2996 | 1.2996 | 1.2996 | 1.2996 | 0.85737 | 0.99734 | 0.99734 | 0.99734 | 0.99734 | 0.99734
2020-03-10 04:00 | Summer | 0.68954 | 0.98685 | 1.4241 | 1.4241 | 1.4241 | 1.4241 | 0.33997 | 0.67238 | 0.67238 | 0.67238 | 0.67238 | 0.67238 | 1.6576 | 2.1391 | 2.4545 | 2.6205 | 2.9526 | 3.2847 | 0.53728 | 1.0604 | 1.2725 | 1.2725 | 1.2725 | 1.2725 | 0.91452 | 1.0638 | 1.0638 | 1.0638 | 1.0638 | 1.0638
2020-03-10 05:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.5287 | 1.0456 | 1.0456 | 1.0456 | 1.0456 | 1.0456 | 1.7909 | 2.3112 | 2.652 | 2.8314 | 3.1902 | 3.549 | 0.72989 | 1.4406 | 1.7287 | 1.7287 | 1.7287 | 1.7287 | 1.1425 | 1.329 | 1.329 | 1.329 | 1.329 | 1.329
2020-03-10 06:00 | Summer | 0.97113 | 1.3898 | 2.0056 | 2.0056 | 2.0056 | 2.0056 | 0.75114 | 1.4856 | 1.4856 | 1.4856 | 1.4856 | 1.4856 | 1.9217 | 2.4799 | 2.8456 | 3.0381 | 3.4231 | 3.808 | 0.78877 | 1.5568 | 1.8681 | 1.8681 | 1.8681 | 1.8681 | 1.4903 | 1.7337 | 1.7337 | 1.7337 | 1.7337 | 1.7337
2020-03-10 07:00 | Summer | 1.3794 | 1.9742 | 2.8488 | 2.8488 | 2.8488 | 2.8488 | 0.81449 | 1.6109 | 1.6109 | 1.6109 | 1.6109 | 1.6109 | 2.4768 | 3.1963 | 3.6677 | 3.9158 | 4.4119 | 4.9081 | 0.96025 | 1.8952 | 2.2743 | 2.2743 | 2.2743 | 2.2743 | 1.8338 | 2.1331 | 2.1331 | 2.1331 | 2.1331 | 2.1331
2020-03-10 08:00 | Summer | 1.7338 | 2.4813 | 3.5806 | 3.5806 | 3.5806 | 3.5806 | 0.88594 | 1.7522 | 1.7522 | 1.7522 | 1.7522 | 1.7522 | 2.7055 | 3.4913 | 4.0062 | 4.2772 | 4.8192 | 5.3612 | 1.0936 | 2.1585 | 2.5901 | 2.5901 | 2.5901 | 2.5901 | 2.1231 | 2.4698 | 2.4698 | 2.4698 | 2.4698 | 2.4698
2020-03-10 09:00 | Summer | 1.7909 | 2.5631 | 3.6987 | 3.6987 | 3.6987 | 3.6987 | 1.0317 | 2.0404 | 2.0404 | 2.0404 | 2.0404 | 2.0404 | 2.7245 | 3.5159 | 4.0344 | 4.3073 | 4.8531 | 5.3989 | 1.0746 | 2.1208 | 2.545 | 2.545 | 2.545 | 2.545 | 2.2746 | 2.646 | 2.646 | 2.646 | 2.646 | 2.646
2020-03-10 10:00 | Summer | 1.7719 | 2.5359 | 3.6593 | 3.6593 | 3.6593 | 3.6593 | 1.0003 | 1.9783 | 1.9783 | 1.9783 | 1.9783 | 1.9783 | 2.9145 | 3.7611 | 4.3157 | 4.6077 | 5.1915 | 5.7754 | 1.1241 | 2.2186 | 2.6623 | 2.6623 | 2.6623 | 2.6623 | 2.3244 | 2.7039 | 2.7039 | 2.7039 | 2.7039 | 2.7039
2020-03-10 11:00 | Summer | 1.7909 | 2.5631 | 3.6987 | 3.6987 | 3.6987 | 3.6987 | 1.0517 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 3.0675 | 3.9585 | 4.5423 | 4.8495 | 5.464 | 6.0785 | 1.1279 | 2.2261 | 2.6714 | 2.6714 | 2.6714 | 2.6714 | 2.3816 | 2.7704 | 2.7704 | 2.7704 | 2.7704 | 2.7704
2020-03-10 12:00 | Summer | 1.81 | 2.5904 | 3.738 | 3.738 | 3.738 | 3.738 | 1.0831 | 2.1422 | 2.1422 | 2.1422 | 2.1422 | 2.1422 | 3.1818 | 4.106 | 4.7115 | 5.0303 | 5.6677 | 6.3051 | 1.1584 | 2.2863 | 2.7436 | 2.7436 | 2.7436 | 2.7436 | 2.534 | 2.9477 | 2.9477 | 2.9477 | 2.9477 | 2.9477
2020-03-10 13:00 | Summer | 1.8481 | 2.6449 | 3.8167 | 3.8167 | 3.8167 | 3.8167 | 1.1231 | 2.2213 | 2.2213 | 2.2213 | 2.2213 | 2.2213 | 3.277 | 4.2289 | 4.8526 | 5.1809 | 5.8373 | 6.4938 | 1.166 | 2.3013 | 2.7616 | 2.7616 | 2.7616 | 2.7616 | 2.5149 | 2.9255 | 2.9255 | 2.9255 | 2.9255 | 2.9255
2020-03-10 14:00 | Summer | 1.8672 | 2.6722 | 3.8561 | 3.8561 | 3.8561 | 3.8561 | 1.1146 | 2.2043 | 2.2043 | 2.2043 | 2.2043 | 2.2043 | 3.1992 | 4.1285 | 4.7373 | 5.0578 | 5.6987 | 6.3396 | 1.2232 | 2.4142 | 2.897 | 2.897 | 2.897 | 2.897 | 2.5911 | 3.0142 | 3.0142 | 3.0142 | 3.0142 | 3.0142
2020-03-10 15:00 | Summer | 1.7719 | 2.5359 | 3.6593 | 3.6593 | 3.6593 | 3.6593 | 1.226 | 2.4248 | 2.4248 | 2.4248 | 2.4248 | 2.4248 | 3.258 | 4.2044 | 4.8244 | 5.1507 | 5.8034 | 6.4561 | 1.0822 | 2.1359 | 2.5631 | 2.5631 | 2.5631 | 2.5631 | 2.534 | 2.9477 | 2.9477 | 2.9477 | 2.9477 | 2.9477
2020-03-10 16:00 | Summer | 1.7719 | 2.5359 | 3.6593 | 3.6593 | 3.6593 | 3.6593 | 1.2117 | 2.3965 | 2.3965 | 2.3965 | 2.3965 | 2.3965 | 3.277 | 4.2289 | 4.8526 | 5.1809 | 5.8373 | 6.4938 | 1.0593 | 2.0908 | 2.5089 | 2.5089 | 2.5089 | 2.5089 | 2.534 | 2.9477 | 2.9477 | 2.9477 | 2.9477 | 2.9477
2020-03-10 17:00 | Summer | 1.6004 | 2.2904 | 3.3052 | 3.3052 | 3.3052 | 3.3052 | 1.1803 | 2.3343 | 2.3343 | 2.3343 | 2.3343 | 2.3343 | 3.0056 | 3.8786 | 4.4506 | 4.7517 | 5.3538 | 5.9559 | 1.0174 | 2.008 | 2.4096 | 2.4096 | 2.4096 | 2.4096 | 2.4006 | 2.7926 | 2.7926 | 2.7926 | 2.7926 | 2.7926
2020-03-10 18:00 | Summer | 1.3146 | 1.8814 | 2.715 | 2.715 | 2.715 | 2.715 | 0.89451 | 1.7691 | 1.7691 | 1.7691 | 1.7691 | 1.7691 | 2.7993 | 3.6124 | 4.1451 | 4.4255 | 4.9863 | 5.5471 | 0.97168 | 1.9178 | 2.3013 | 2.3013 | 2.3013 | 2.3013 | 1.7427 | 2.0272 | 2.0272 | 2.0272 | 2.0272 | 2.0272
2020-03-10 19:00 | Summer | 0.74305 | 1.0634 | 1.5346 | 1.5346 | 1.5346 | 1.5346 | 0.74305 | 1.4696 | 1.4696 | 1.4696 | 1.4696 | 1.4696 | 2.4953 | 3.2201 | 3.695 | 3.9449 | 4.4448 | 4.9447 | 0.99073 | 1.9554 | 2.3465 | 2.3465 | 2.3465 | 2.3465 | 1.2003 | 1.3963 | 1.3963 | 1.3963 | 1.3963 | 1.3963
2020-03-10 20:00 | Summer | 0.68589 | 0.98162 | 1.4165 | 1.4165 | 1.4165 | 1.4165 | 0.75162 | 1.4865 | 1.4865 | 1.4865 | 1.4865 | 1.4865 | 2.3625 | 3.0488 | 3.4984 | 3.735 | 4.2083 | 4.6816 | 0.94882 | 1.8727 | 2.2472 | 2.2472 | 2.2472 | 2.2472 | 1.2003 | 1.3963 | 1.3963 | 1.3963 | 1.3963 | 1.3963
2020-03-10 21:00 | Summer | 0.66684 | 0.95435 | 1.3772 | 1.3772 | 1.3772 | 1.3772 | 0.63159 | 1.2491 | 1.2491 | 1.2491 | 1.2491 | 1.2491 | 2.2101 | 2.8521 | 3.2727 | 3.4941 | 3.9368 | 4.3796 | 0.94501 | 1.8651 | 2.2382 | 2.2382 | 2.2382 | 2.2382 | 1.086 | 1.2633 | 1.2633 | 1.2633 | 1.2633 | 1.2633
2020-03-10 22:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.62301 | 1.2322 | 1.2322 | 1.2322 | 1.2322 | 1.2322 | 2.1339 | 2.7537 | 3.1598 | 3.3736 | 3.8011 | 4.2285 | 0.86879 | 1.7147 | 2.0577 | 2.0577 | 2.0577 | 2.0577 | 0.95263 | 1.1082 | 1.1082 | 1.1082 | 1.1082 | 1.1082
2020-03-10 23:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.50013 | 0.98912 | 0.98912 | 0.98912 | 0.98912 | 0.98912 | 1.9815 | 2.557 | 2.9341 | 3.1326 | 3.5296 | 3.9265 | 0.86879 | 1.7147 | 2.0577 | 2.0577 | 2.0577 | 2.0577 | 0.89564 | 1.0419 | 1.0419 | 1.0419 | 1.0419 | 1.0419
2020-03-11 | Summer | 0.59188 | 0.84708 | 1.2224 | 1.2224 | 1.2224 | 1.2224 | 0.43154 | 0.85347 | 0.85347 | 0.85347 | 0.85347 | 0.85347 | 1.8862 | 2.4341 | 2.7931 | 2.982 | 3.3599 | 3.7377 | 0.64397 | 1.271 | 1.5252 | 1.5252 | 1.5252 | 1.5252 | 0.87831 | 1.0217 | 1.0217 | 1.0217 | 1.0217 | 1.0217
2020-03-11 01:00 | Summer | 0.64779 | 0.92709 | 1.3378 | 1.3378 | 1.3378 | 1.3378 | 0.4001 | 0.7913 | 0.7913 | 0.7913 | 0.7913 | 0.7913 | 1.7719 | 2.2866 | 2.6238 | 2.8013 | 3.1562 | 3.5112 | 0.63635 | 1.256 | 1.5072 | 1.5072 | 1.5072 | 1.5072 | 0.89547 | 1.0417 | 1.0417 | 1.0417 | 1.0417 | 1.0417
2020-03-11 02:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.40867 | 0.80825 | 0.80825 | 0.80825 | 0.80825 | 0.80825 | 1.7338 | 2.2374 | 2.5674 | 2.741 | 3.0884 | 3.4357 | 0.59444 | 1.1732 | 1.4079 | 1.4079 | 1.4079 | 1.4079 | 0.87642 | 1.0195 | 1.0195 | 1.0195 | 1.0195 | 1.0195
2020-03-11 03:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.38295 | 0.75738 | 0.75738 | 0.75738 | 0.75738 | 0.75738 | 1.7528 | 2.262 | 2.5956 | 2.7712 | 3.1223 | 3.4734 | 0.59063 | 1.1657 | 1.3989 | 1.3989 | 1.3989 | 1.3989 | 0.89547 | 1.0417 | 1.0417 | 1.0417 | 1.0417 | 1.0417
2020-03-11 04:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.40582 | 0.8026 | 0.8026 | 0.8026 | 0.8026 | 0.8026 | 1.7338 | 2.2374 | 2.5674 | 2.741 | 3.0884 | 3.4357 | 0.6173 | 1.2184 | 1.462 | 1.462 | 1.462 | 1.462 | 0.91389 | 1.0631 | 1.0631 | 1.0631 | 1.0631 | 1.0631
2020-03-11 05:00 | Summer | 0.85737 | 1.227 | 1.7706 | 1.7706 | 1.7706 | 1.7706 | 0.49155 | 0.97217 | 0.97217 | 0.97217 | 0.97217 | 0.97217 | 1.7909 | 2.3112 | 2.652 | 2.8314 | 3.1902 | 3.549 | 0.83831 | 1.6546 | 1.9855 | 1.9855 | 1.9855 | 1.9855 | 1.1807 | 1.3734 | 1.3734 | 1.3734 | 1.3734 | 1.3734
2020-03-11 06:00 | Summer | 0.91452 | 1.3088 | 1.8887 | 1.8887 | 1.8887 | 1.8887 | 0.66874 | 1.3226 | 1.3226 | 1.3226 | 1.3226 | 1.3226 | 2.0386 | 2.6308 | 3.0188 | 3.223 | 3.6314 | 4.0398 | 0.96025 | 1.8952 | 2.2743 | 2.2743 | 2.2743 | 2.2743 | 1.4455 | 1.6815 | 1.6815 | 1.6815 | 1.6815 | 1.6815
2020-03-11 07:00 | Summer | 1.297 | 1.8563 | 2.6787 | 2.6787 | 2.6787 | 2.6787 | 0.83736 | 1.6561 | 1.6561 | 1.6561 | 1.6561 | 1.6561 | 2.4768 | 3.1963 | 3.6677 | 3.9158 | 4.4119 | 4.9081 | 1.1736 | 2.3164 | 2.7797 | 2.7797 | 2.7797 | 2.7797 | 1.9434 | 2.2606 | 2.2606 | 2.2606 | 2.2606 | 2.2606
2020-03-11 08:00 | Summer | 1.7719 | 2.5359 | 3.6593 | 3.6593 | 3.6593 | 3.6593 | 0.99454 | 1.967 | 1.967 | 1.967 | 1.967 | 1.967 | 2.7817 | 3.5897 | 4.1191 | 4.3977 | 4.955 | 5.5122 | 1.1279 | 2.2261 | 2.6714 | 2.6714 | 2.6714 | 2.6714 | 2.2102 | 2.5711 | 2.5711 | 2.5711 | 2.5711 | 2.5711
2020-03-11 09:00 | Summer | 1.7528 | 2.5086 | 3.62 | 3.62 | 3.62 | 3.62 | 1.0688 | 2.1139 | 2.1139 | 2.1139 | 2.1139 | 2.1139 | 2.8769 | 3.7126 | 4.2601 | 4.5483 | 5.1246 | 5.701 | 1.1355 | 2.2412 | 2.6894 | 2.6894 | 2.6894 | 2.6894 | 2.3435 | 2.7261 | 2.7261 | 2.7261 | 2.7261 | 2.7261
2020-03-11 10:00 | Summer | 1.7909 | 2.5631 | 3.6987 | 3.6987 | 3.6987 | 3.6987 | 1.0431 | 2.063 | 2.063 | 2.063 | 2.063 | 2.063 | 3.0484 | 3.9339 | 4.5141 | 4.8194 | 5.4301 | 6.0408 | 1.1165 | 2.2036 | 2.6443 | 2.6443 | 2.6443 | 2.6443 | 2.4732 | 2.877 | 2.877 | 2.877 | 2.877 | 2.877
2020-03-11 11:00 | Summer | 1.7909 | 2.5631 | 3.6987 | 3.6987 | 3.6987 | 3.6987 | 1.1374 | 2.2496 | 2.2496 | 2.2496 | 2.2496 | 2.2496 | 3.277 | 4.2289 | 4.8526 | 5.1809 | 5.8373 | 6.4938 | 1.227 | 2.4217 | 2.906 | 2.906 | 2.906 | 2.906 | 2.5149 | 2.9255 | 2.9255 | 2.9255 | 2.9255 | 2.9255
2020-03-11 12:00 | Summer | 1.829 | 2.6177 | 3.7774 | 3.7774 | 3.7774 | 3.7774 | 1.2146 | 2.4022 | 2.4022 | 2.4022 | 2.4022 | 2.4022 | 3.277 | 4.2289 | 4.8526 | 5.1809 | 5.8373 | 6.4938 | 1.1965 | 2.3615 | 2.8338 | 2.8338 | 2.8338 | 2.8338 | 2.553 | 2.9699 | 2.9699 | 2.9699 | 2.9699 | 2.9699
2020-03-11 13:00 | Summer | 1.8161 | 2.5992 | 3.7507 | 3.7507 | 3.7507 | 3.7507 | 1.2975 | 2.5661 | 2.5661 | 2.5661 | 2.5661 | 2.5661 | 3.277 | 4.2289 | 4.8526 | 5.1809 | 5.8373 | 6.4938 | 1.1622 | 2.2938 | 2.7526 | 2.7526 | 2.7526 | 2.7526 | 2.8007 | 3.258 | 3.258 | 3.258 | 3.258 | 3.258
2020-03-11 14:00 | Summer | 1.81 | 2.5904 | 3.738 | 3.738 | 3.738 | 3.738 | 1.4804 | 2.9278 | 2.9278 | 2.9278 | 2.9278 | 2.9278 | 3.2389 | 4.1798 | 4.7962 | 5.1206 | 5.7695 | 6.4183 | 1.0669 | 2.1058 | 2.527 | 2.527 | 2.527 | 2.527 | 2.6293 | 3.0585 | 3.0585 | 3.0585 | 3.0585 | 3.0585
2020-03-11 15:00 | Summer | 1.7528 | 2.5086 | 3.62 | 3.62 | 3.62 | 3.62 | 1.414 | 2.7965 | 2.7965 | 2.7965 | 2.7965 | 2.7965 | 3.2389 | 4.1798 | 4.7962 | 5.1206 | 5.7695 | 6.4183 | 1.0403 | 2.0532 | 2.4638 | 2.4638 | 2.4638 | 2.4638 | 2.6102 | 3.0364 | 3.0364 | 3.0364 | 3.0364 | 3.0364
2020-03-11 16:00 | Summer | 1.6957 | 2.4268 | 3.5019 | 3.5019 | 3.5019 | 3.5019 | 1.2517 | 2.4756 | 2.4756 | 2.4756 | 2.4756 | 2.4756 | 3.2199 | 4.1552 | 4.768 | 5.0905 | 5.7355 | 6.3806 | 1.0555 | 2.0832 | 2.4999 | 2.4999 | 2.4999 | 2.4999 | 2.553 | 2.9699 | 2.9699 | 2.9699 | 2.9699 | 2.9699
2020-03-11 17:00 | Summer | 1.5242 | 2.1814 | 3.1478 | 3.1478 | 3.1478 | 3.1478 | 1.206 | 2.3852 | 2.3852 | 2.3852 | 2.3852 | 2.3852 | 2.9726 | 3.836 | 4.4017 | 4.6995 | 5.295 | 5.8905 | 1.0365 | 2.0456 | 2.4548 | 2.4548 | 2.4548 | 2.4548 | 2.2491 | 2.6162 | 2.6162 | 2.6162 | 2.6162 | 2.6162
2020-03-11 18:00 | Summer | 1.101 | 1.5757 | 2.2737 | 2.2737 | 2.2737 | 2.2737 | 0.91452 | 1.8087 | 1.8087 | 1.8087 | 1.8087 | 1.8087 | 2.8388 | 3.6634 | 4.2037 | 4.4881 | 5.0568 | 5.6255 | 0.9793 | 1.9328 | 2.3194 | 2.3194 | 2.3194 | 2.3194 | 1.6857 | 1.9609 | 1.9609 | 1.9609 | 1.9609 | 1.9609
2020-03-11 19:00 | Summer | 0.78121 | 1.118 | 1.6134 | 1.6134 | 1.6134 | 1.6134 | 0.74305 | 1.4696 | 1.4696 | 1.4696 | 1.4696 | 1.4696 | 2.446 | 3.1564 | 3.6219 | 3.8669 | 4.3569 | 4.8469 | 0.93738 | 1.8501 | 2.2201 | 2.2201 | 2.2201 | 2.2201 | 1.2693 | 1.4765 | 1.4765 | 1.4765 | 1.4765 | 1.4765
2020-03-11 20:00 | Summer | 0.7621 | 1.0907 | 1.5739 | 1.5739 | 1.5739 | 1.5739 | 0.77448 | 1.5317 | 1.5317 | 1.5317 | 1.5317 | 1.5317 | 2.3625 | 3.0488 | 3.4984 | 3.735 | 4.2083 | 4.6816 | 0.98692 | 1.9479 | 2.3374 | 2.3374 | 2.3374 | 2.3374 | 1.1813 | 1.3741 | 1.3741 | 1.3741 | 1.3741 | 1.3741
2020-03-11 21:00 | Summer | 0.62881 | 0.89993 | 1.2986 | 1.2986 | 1.2986 | 1.2986 | 0.72304 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 2.2482 | 2.9013 | 3.3291 | 3.5543 | 4.0047 | 4.4551 | 0.93357 | 1.8426 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 1.1241 | 1.3076 | 1.3076 | 1.3076 | 1.3076 | 1.3076
2020-03-11 22:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.63159 | 1.2491 | 1.2491 | 1.2491 | 1.2491 | 1.2491 | 2.1148 | 2.7291 | 3.1316 | 3.3435 | 3.7671 | 4.1908 | 0.91833 | 1.8125 | 2.175 | 2.175 | 2.175 | 2.175 | 0.98785 | 1.1491 | 1.1491 | 1.1491 | 1.1491 | 1.1491
2020-03-11 23:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.56014 | 1.1078 | 1.1078 | 1.1078 | 1.1078 | 1.1078 | 1.9195 | 2.4771 | 2.8424 | 3.0346 | 3.4191 | 3.8037 | 0.83069 | 1.6395 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.95263 | 1.1082 | 1.1082 | 1.1082 | 1.1082 | 1.1082
2020-03-12 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.46641 | 0.92244 | 0.92244 | 0.92244 | 0.92244 | 0.92244 | 1.829 | 2.3603 | 2.7084 | 2.8916 | 3.2581 | 3.6245 | 0.66684 | 1.3161 | 1.5794 | 1.5794 | 1.5794 | 1.5794 | 0.89547 | 1.0417 | 1.0417 | 1.0417 | 1.0417 | 1.0417
2020-03-12 01:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.43439 | 0.85912 | 0.85912 | 0.85912 | 0.85912 | 0.85912 | 1.7195 | 2.219 | 2.5463 | 2.7185 | 3.063 | 3.4075 | 0.61349 | 1.2108 | 1.453 | 1.453 | 1.453 | 1.453 | 0.89547 | 1.0417 | 1.0417 | 1.0417 | 1.0417 | 1.0417
2020-03-12 02:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.49441 | 0.97782 | 0.97782 | 0.97782 | 0.97782 | 0.97782 | 1.7528 | 2.262 | 2.5956 | 2.7712 | 3.1223 | 3.4734 | 0.62492 | 1.2334 | 1.4801 | 1.4801 | 1.4801 | 1.4801 | 0.89547 | 1.0417 | 1.0417 | 1.0417 | 1.0417 | 1.0417
2020-03-12 03:00 | Summer | 0.63748 | 0.91234 | 1.3165 | 1.3165 | 1.3165 | 1.3165 | 0.37724 | 0.74608 | 0.74608 | 0.74608 | 0.74608 | 0.74608 | 1.7437 | 2.2502 | 2.582 | 2.7567 | 3.106 | 3.4553 | 0.59825 | 1.1808 | 1.4169 | 1.4169 | 1.4169 | 1.4169 | 0.91452 | 1.0638 | 1.0638 | 1.0638 | 1.0638 | 1.0638
2020-03-12 04:00 | Summer | 0.64779 | 0.92709 | 1.3378 | 1.3378 | 1.3378 | 1.3378 | 0.43154 | 0.85347 | 0.85347 | 0.85347 | 0.85347 | 0.85347 | 1.7338 | 2.2374 | 2.5674 | 2.741 | 3.0884 | 3.4357 | 0.62492 | 1.2334 | 1.4801 | 1.4801 | 1.4801 | 1.4801 | 0.95263 | 1.1082 | 1.1082 | 1.1082 | 1.1082 | 1.1082
2020-03-12 05:00 | Summer | 0.74305 | 1.0634 | 1.5346 | 1.5346 | 1.5346 | 1.5346 | 0.5087 | 1.0061 | 1.0061 | 1.0061 | 1.0061 | 1.0061 | 1.8672 | 2.4095 | 2.7649 | 2.9519 | 3.3259 | 3.7 | 0.8365 | 1.651 | 1.9812 | 1.9812 | 1.9812 | 1.9812 | 1.1104 | 1.2917 | 1.2917 | 1.2917 | 1.2917 | 1.2917
2020-03-12 06:00 | Summer | 0.83776 | 1.199 | 1.7302 | 1.7302 | 1.7302 | 1.7302 | 0.69732 | 1.3791 | 1.3791 | 1.3791 | 1.3791 | 1.3791 | 2.0023 | 2.584 | 2.965 | 3.1656 | 3.5667 | 3.9679 | 1.0555 | 2.0832 | 2.4999 | 2.4999 | 2.4999 | 2.4999 | 1.3938 | 1.6214 | 1.6214 | 1.6214 | 1.6214 | 1.6214
2020-03-12 07:00 | Summer | 1.2003 | 1.7178 | 2.4789 | 2.4789 | 2.4789 | 2.4789 | 0.79449 | 1.5713 | 1.5713 | 1.5713 | 1.5713 | 1.5713 | 2.4959 | 3.2209 | 3.6959 | 3.9459 | 4.4459 | 4.9459 | 1.1393 | 2.2487 | 2.6984 | 2.6984 | 2.6984 | 2.6984 | 1.774 | 2.0637 | 2.0637 | 2.0637 | 2.0637 | 2.0637
2020-03-12 08:00 | Summer | 1.7147 | 2.4541 | 3.5413 | 3.5413 | 3.5413 | 3.5413 | 0.90595 | 1.7917 | 1.7917 | 1.7917 | 1.7917 | 1.7917 | 2.6674 | 3.4422 | 3.9498 | 4.217 | 4.7513 | 5.2857 | 1.1736 | 2.3164 | 2.7797 | 2.7797 | 2.7797 | 2.7797 | 2.1148 | 2.4601 | 2.4601 | 2.4601 | 2.4601 | 2.4601
2020-03-12 09:00 | Summer | 1.7338 | 2.4813 | 3.5806 | 3.5806 | 3.5806 | 3.5806 | 0.93452 | 1.8483 | 1.8483 | 1.8483 | 1.8483 | 1.8483 | 2.8769 | 3.7126 | 4.2601 | 4.5483 | 5.1246 | 5.701 | 1.2156 | 2.3991 | 2.8789 | 2.8789 | 2.8789 | 2.8789 | 2.2482 | 2.6153 | 2.6153 | 2.6153 | 2.6153 | 2.6153
2020-03-12 10:00 | Summer | 1.829 | 2.6177 | 3.7774 | 3.7774 | 3.7774 | 3.7774 | 0.96882 | 1.9161 | 1.9161 | 1.9161 | 1.9161 | 1.9161 | 2.9722 | 3.8356 | 4.4012 | 4.6989 | 5.2943 | 5.8898 | 1.1965 | 2.3615 | 2.8338 | 2.8338 | 2.8338 | 2.8338 | 2.362 | 2.7476 | 2.7476 | 2.7476 | 2.7476 | 2.7476
2020-03-12 11:00 | Summer | 1.7719 | 2.5359 | 3.6593 | 3.6593 | 3.6593 | 3.6593 | 0.98597 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 3.0294 | 3.9093 | 4.4858 | 4.7893 | 5.3962 | 6.003 | 1.1393 | 2.2487 | 2.6984 | 2.6984 | 2.6984 | 2.6984 | 2.4006 | 2.7926 | 2.7926 | 2.7926 | 2.7926 | 2.7926
2020-03-12 12:00 | Summer | 1.7719 | 2.5359 | 3.6593 | 3.6593 | 3.6593 | 3.6593 | 0.98882 | 1.9556 | 1.9556 | 1.9556 | 1.9556 | 1.9556 | 3.0484 | 3.9339 | 4.5141 | 4.8194 | 5.4301 | 6.0408 | 1.1774 | 2.3239 | 2.7887 | 2.7887 | 2.7887 | 2.7887 | 2.534 | 2.9477 | 2.9477 | 2.9477 | 2.9477 | 2.9477
2020-03-12 13:00 | Summer | 1.7719 | 2.5359 | 3.6593 | 3.6593 | 3.6593 | 3.6593 | 0.96882 | 1.9161 | 1.9161 | 1.9161 | 1.9161 | 1.9161 | 3.0484 | 3.9339 | 4.5141 | 4.8194 | 5.4301 | 6.0408 | 1.2156 | 2.3991 | 2.8789 | 2.8789 | 2.8789 | 2.8789 | 2.5149 | 2.9255 | 2.9255 | 2.9255 | 2.9255 | 2.9255
2020-03-12 14:00 | Summer | 1.7528 | 2.5086 | 3.62 | 3.62 | 3.62 | 3.62 | 1.1089 | 2.193 | 2.193 | 2.193 | 2.193 | 2.193 | 3.1056 | 4.0077 | 4.5987 | 4.9098 | 5.5319 | 6.154 | 1.1813 | 2.3314 | 2.7977 | 2.7977 | 2.7977 | 2.7977 | 2.4578 | 2.8591 | 2.8591 | 2.8591 | 2.8591 | 2.8591
2020-03-12 15:00 | Summer | 1.7147 | 2.4541 | 3.5413 | 3.5413 | 3.5413 | 3.5413 | 1.0746 | 2.1252 | 2.1252 | 2.1252 | 2.1252 | 2.1252 | 3.1246 | 4.0323 | 4.6269 | 4.9399 | 5.5658 | 6.1918 | 1.1622 | 2.2938 | 2.7526 | 2.7526 | 2.7526 | 2.7526 | 2.3816 | 2.7704 | 2.7704 | 2.7704 | 2.7704 | 2.7704
2020-03-12 16:00 | Summer | 1.6518 | 2.364 | 3.4114 | 3.4114 | 3.4114 | 3.4114 | 1.0892 | 2.1542 | 2.1542 | 2.1542 | 2.1542 | 2.1542 | 3.1056 | 4.0077 | 4.5987 | 4.9098 | 5.5319 | 6.154 | 1.0669 | 2.1058 | 2.527 | 2.527 | 2.527 | 2.527 | 2.4006 | 2.7926 | 2.7926 | 2.7926 | 2.7926 | 2.7926
2020-03-12 17:00 | Summer | 1.563 | 2.2369 | 3.2279 | 3.2279 | 3.2279 | 3.2279 | 1.3289 | 2.6283 | 2.6283 | 2.6283 | 2.6283 | 2.6283 | 3.0294 | 3.9093 | 4.4858 | 4.7893 | 5.3962 | 6.003 | 1.025 | 2.0231 | 2.4277 | 2.4277 | 2.4277 | 2.4277 | 2.4006 | 2.7926 | 2.7926 | 2.7926 | 2.7926 | 2.7926
2020-03-12 18:00 | Summer | 1.0801 | 1.5459 | 2.2307 | 2.2307 | 2.2307 | 2.2307 | 1.1165 | 2.2082 | 2.2082 | 2.2082 | 2.2082 | 2.2082 | 2.9531 | 3.811 | 4.373 | 4.6688 | 5.2604 | 5.852 | 0.97168 | 1.9178 | 2.3013 | 2.3013 | 2.3013 | 2.3013 | 1.7268 | 2.0087 | 2.0087 | 2.0087 | 2.0087 | 2.0087
2020-03-12 19:00 | Summer | 0.724 | 1.0362 | 1.4952 | 1.4952 | 1.4952 | 1.4952 | 0.74876 | 1.4809 | 1.4809 | 1.4809 | 1.4809 | 1.4809 | 2.5721 | 3.3192 | 3.8087 | 4.0664 | 4.5816 | 5.0969 | 0.96025 | 1.8952 | 2.2743 | 2.2743 | 2.2743 | 2.2743 | 1.2575 | 1.4628 | 1.4628 | 1.4628 | 1.4628 | 1.4628
2020-03-12 20:00 | Summer | 0.724 | 1.0362 | 1.4952 | 1.4952 | 1.4952 | 1.4952 | 0.75448 | 1.4922 | 1.4922 | 1.4922 | 1.4922 | 1.4922 | 2.4578 | 3.1717 | 3.6395 | 3.8856 | 4.378 | 4.8704 | 0.94882 | 1.8727 | 2.2472 | 2.2472 | 2.2472 | 2.2472 | 1.1813 | 1.3741 | 1.3741 | 1.3741 | 1.3741 | 1.3741
2020-03-12 21:00 | Summer | 0.62896 | 0.90014 | 1.2989 | 1.2989 | 1.2989 | 1.2989 | 0.65731 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 2.2673 | 2.9258 | 3.3573 | 3.5844 | 4.0386 | 4.4928 | 0.93738 | 1.8501 | 2.2201 | 2.2201 | 2.2201 | 2.2201 | 1.086 | 1.2633 | 1.2633 | 1.2633 | 1.2633 | 1.2633
2020-03-12 22:00 | Summer | 0.59054 | 0.84516 | 1.2196 | 1.2196 | 1.2196 | 1.2196 | 0.583 | 1.153 | 1.153 | 1.153 | 1.153 | 1.153 | 2.1148 | 2.7291 | 3.1316 | 3.3435 | 3.7671 | 4.1908 | 0.94501 | 1.8651 | 2.2382 | 2.2382 | 2.2382 | 2.2382 | 0.95263 | 1.1082 | 1.1082 | 1.1082 | 1.1082 | 1.1082
2020-03-12 23:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.46583 | 0.9213 | 0.9213 | 0.9213 | 0.9213 | 0.9213 | 1.9624 | 2.5325 | 2.9059 | 3.1025 | 3.4956 | 3.8887 | 0.9069 | 1.7899 | 2.1479 | 2.1479 | 2.1479 | 2.1479 | 0.91452 | 1.0638 | 1.0638 | 1.0638 | 1.0638 | 1.0638
2020-03-13 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.50013 | 0.98912 | 0.98912 | 0.98912 | 0.98912 | 0.98912 | 1.7909 | 2.3112 | 2.652 | 2.8314 | 3.1902 | 3.549 | 0.62873 | 1.2409 | 1.4891 | 1.4891 | 1.4891 | 1.4891 | 0.87645 | 1.0195 | 1.0195 | 1.0195 | 1.0195 | 1.0195
2020-03-13 01:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.46583 | 0.9213 | 0.9213 | 0.9213 | 0.9213 | 0.9213 | 1.7528 | 2.262 | 2.5956 | 2.7712 | 3.1223 | 3.4734 | 0.65541 | 1.2936 | 1.5523 | 1.5523 | 1.5523 | 1.5523 | 0.87642 | 1.0195 | 1.0195 | 1.0195 | 1.0195 | 1.0195
2020-03-13 02:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.48584 | 0.96086 | 0.96086 | 0.96086 | 0.96086 | 0.96086 | 1.7147 | 2.2128 | 2.5392 | 2.7109 | 3.0544 | 3.3979 | 0.62886 | 1.2412 | 1.4894 | 1.4894 | 1.4894 | 1.4894 | 0.85737 | 0.99734 | 0.99734 | 0.99734 | 0.99734 | 0.99734
2020-03-13 03:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.46012 | 0.90999 | 0.90999 | 0.90999 | 0.90999 | 0.90999 | 1.7147 | 2.2128 | 2.5392 | 2.7109 | 3.0544 | 3.3979 | 0.69351 | 1.3688 | 1.6425 | 1.6425 | 1.6425 | 1.6425 | 0.87642 | 1.0195 | 1.0195 | 1.0195 | 1.0195 | 1.0195
2020-03-13 04:00 | Summer | 0.63513 | 0.90897 | 1.3117 | 1.3117 | 1.3117 | 1.3117 | 0.44011 | 0.87043 | 0.87043 | 0.87043 | 0.87043 | 0.87043 | 1.7338 | 2.2374 | 2.5674 | 2.741 | 3.0884 | 3.4357 | 0.64779 | 1.2785 | 1.5342 | 1.5342 | 1.5342 | 1.5342 | 0.93291 | 1.0852 | 1.0852 | 1.0852 | 1.0852 | 1.0852
2020-03-13 05:00 | Summer | 0.724 | 1.0362 | 1.4952 | 1.4952 | 1.4952 | 1.4952 | 0.57443 | 1.1361 | 1.1361 | 1.1361 | 1.1361 | 1.1361 | 1.8239 | 2.3537 | 2.7009 | 2.8836 | 3.2489 | 3.6143 | 1.0784 | 2.1284 | 2.554 | 2.554 | 2.554 | 2.554 | 1.106 | 1.2866 | 1.2866 | 1.2866 | 1.2866 | 1.2866
2020-03-13 06:00 | Summer | 0.78108 | 1.1178 | 1.6131 | 1.6131 | 1.6131 | 1.6131 | 0.69446 | 1.3735 | 1.3735 | 1.3735 | 1.3735 | 1.3735 | 1.991 | 2.5693 | 2.9482 | 3.1476 | 3.5465 | 3.9453 | 0.97168 | 1.9178 | 2.3013 | 2.3013 | 2.3013 | 2.3013 | 1.4086 | 1.6386 | 1.6386 | 1.6386 | 1.6386 | 1.6386
2020-03-13 07:00 | Summer | 1.1622 | 1.6633 | 2.4002 | 2.4002 | 2.4002 | 2.4002 | 0.82245 | 1.6266 | 1.6266 | 1.6266 | 1.6266 | 1.6266 | 2.3698 | 3.0582 | 3.5092 | 3.7466 | 4.2213 | 4.6961 | 1.1317 | 2.2337 | 2.6804 | 2.6804 | 2.6804 | 2.6804 | 1.7528 | 2.039 | 2.039 | 2.039 | 2.039 | 2.039
2020-03-13 08:00 | Summer | 1.6195 | 2.3177 | 3.3446 | 3.3446 | 3.3446 | 3.3446 | 0.91452 | 1.8087 | 1.8087 | 1.8087 | 1.8087 | 1.8087 | 2.6483 | 3.4176 | 3.9216 | 4.1869 | 4.7174 | 5.2479 | 1.1279 | 2.2261 | 2.6714 | 2.6714 | 2.6714 | 2.6714 | 2.0449 | 2.3787 | 2.3787 | 2.3787 | 2.3787 | 2.3787
2020-03-13 09:00 | Summer | 1.7338 | 2.4813 | 3.5806 | 3.5806 | 3.5806 | 3.5806 | 0.89166 | 1.7635 | 1.7635 | 1.7635 | 1.7635 | 1.7635 | 2.7817 | 3.5897 | 4.1191 | 4.3977 | 4.955 | 5.5122 | 1.1813 | 2.3314 | 2.7977 | 2.7977 | 2.7977 | 2.7977 | 2.2863 | 2.6596 | 2.6596 | 2.6596 | 2.6596 | 2.6596
2020-03-13 10:00 | Summer | 1.7147 | 2.4541 | 3.5413 | 3.5413 | 3.5413 | 3.5413 | 1.0231 | 2.0235 | 2.0235 | 2.0235 | 2.0235 | 2.0235 | 3.0294 | 3.9093 | 4.4858 | 4.7893 | 5.3962 | 6.003 | 1.1851 | 2.3389 | 2.8067 | 2.8067 | 2.8067 | 2.8067 | 2.4568 | 2.8579 | 2.8579 | 2.8579 | 2.8579 | 2.8579
2020-03-13 11:00 | Summer | 1.6957 | 2.4268 | 3.5019 | 3.5019 | 3.5019 | 3.5019 | 0.96944 | 1.9173 | 1.9173 | 1.9173 | 1.9173 | 1.9173 | 3.0865 | 3.9831 | 4.5705 | 4.8796 | 5.498 | 6.1163 | 1.1889 | 2.3465 | 2.8158 | 2.8158 | 2.8158 | 2.8158 | 2.4578 | 2.8591 | 2.8591 | 2.8591 | 2.8591 | 2.8591
2020-03-13 12:00 | Summer | 1.6766 | 2.3995 | 3.4626 | 3.4626 | 3.4626 | 3.4626 | 1.0374 | 2.0517 | 2.0517 | 2.0517 | 2.0517 | 2.0517 | 3.1056 | 4.0077 | 4.5987 | 4.9098 | 5.5319 | 6.154 | 1.2041 | 2.3766 | 2.8519 | 2.8519 | 2.8519 | 2.8519 | 2.534 | 2.9477 | 2.9477 | 2.9477 | 2.9477 | 2.9477
2020-03-13 13:00 | Summer | 1.6766 | 2.3995 | 3.4626 | 3.4626 | 3.4626 | 3.4626 | 1.1803 | 2.3343 | 2.3343 | 2.3343 | 2.3343 | 2.3343 | 3.258 | 4.2044 | 4.8244 | 5.1507 | 5.8034 | 6.4561 | 1.1165 | 2.2036 | 2.6443 | 2.6443 | 2.6443 | 2.6443 | 2.4959 | 2.9034 | 2.9034 | 2.9034 | 2.9034 | 2.9034
2020-03-13 14:00 | Summer | 1.6957 | 2.4268 | 3.5019 | 3.5019 | 3.5019 | 3.5019 | 1.1689 | 2.3117 | 2.3117 | 2.3117 | 2.3117 | 2.3117 | 3.258 | 4.2044 | 4.8244 | 5.1507 | 5.8034 | 6.4561 | 1.0365 | 2.0456 | 2.4548 | 2.4548 | 2.4548 | 2.4548 | 2.5721 | 2.992 | 2.992 | 2.992 | 2.992 | 2.992
2020-03-13 15:00 | Summer | 1.6957 | 2.4268 | 3.5019 | 3.5019 | 3.5019 | 3.5019 | 1.2803 | 2.5322 | 2.5322 | 2.5322 | 2.5322 | 2.5322 | 3.277 | 4.2289 | 4.8526 | 5.1809 | 5.8373 | 6.4938 | 1.1127 | 2.1961 | 2.6353 | 2.6353 | 2.6353 | 2.6353 | 2.5149 | 2.9255 | 2.9255 | 2.9255 | 2.9255 | 2.9255
2020-03-13 16:00 | Summer | 1.6004 | 2.2904 | 3.3052 | 3.3052 | 3.3052 | 3.3052 | 1.3232 | 2.617 | 2.617 | 2.617 | 2.617 | 2.617 | 3.277 | 4.2289 | 4.8526 | 5.1809 | 5.8373 | 6.4938 | 1.0784 | 2.1284 | 2.554 | 2.554 | 2.554 | 2.554 | 2.534 | 2.9477 | 2.9477 | 2.9477 | 2.9477 | 2.9477
2020-03-13 17:00 | Summer | 1.5242 | 2.1814 | 3.1478 | 3.1478 | 3.1478 | 3.1478 | 1.3575 | 2.6848 | 2.6848 | 2.6848 | 2.6848 | 2.6848 | 3.0865 | 3.9831 | 4.5705 | 4.8796 | 5.498 | 6.1163 | 1.0326 | 2.0381 | 2.4457 | 2.4457 | 2.4457 | 2.4457 | 2.3816 | 2.7704 | 2.7704 | 2.7704 | 2.7704 | 2.7704
2020-03-13 18:00 | Summer | 1.1287 | 1.6154 | 2.3311 | 2.3311 | 2.3311 | 2.3311 | 0.97593 | 1.9301 | 1.9301 | 1.9301 | 1.9301 | 1.9301 | 2.971 | 3.834 | 4.3994 | 4.697 | 5.2922 | 5.8874 | 1.025 | 2.0231 | 2.4277 | 2.4277 | 2.4277 | 2.4277 | 1.9006 | 2.2109 | 2.2109 | 2.2109 | 2.2109 | 2.2109
2020-03-13 19:00 | Summer | 0.89547 | 1.2816 | 1.8493 | 1.8493 | 1.8493 | 1.8493 | 0.80306 | 1.5883 | 1.5883 | 1.5883 | 1.5883 | 1.5883 | 2.6345 | 3.3998 | 3.9012 | 4.1651 | 4.6928 | 5.2206 | 0.95263 | 1.8802 | 2.2562 | 2.2562 | 2.2562 | 2.2562 | 1.2956 | 1.5071 | 1.5071 | 1.5071 | 1.5071 | 1.5071
2020-03-13 20:00 | Summer | 0.7056 | 1.0098 | 1.4572 | 1.4572 | 1.4572 | 1.4572 | 0.8002 | 1.5826 | 1.5826 | 1.5826 | 1.5826 | 1.5826 | 2.3816 | 3.0734 | 3.5266 | 3.7652 | 4.2423 | 4.7194 | 1.0022 | 1.978 | 2.3735 | 2.3735 | 2.3735 | 2.3735 | 1.2384 | 1.4406 | 1.4406 | 1.4406 | 1.4406 | 1.4406
2020-03-13 21:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.64874 | 1.283 | 1.283 | 1.283 | 1.283 | 1.283 | 2.2863 | 2.9504 | 3.3855 | 3.6146 | 4.0726 | 4.5306 | 0.94882 | 1.8727 | 2.2472 | 2.2472 | 2.2472 | 2.2472 | 1.1432 | 1.3298 | 1.3298 | 1.3298 | 1.3298 | 1.3298
2020-03-13 22:00 | Summer | 0.64779 | 0.92709 | 1.3378 | 1.3378 | 1.3378 | 1.3378 | 0.62873 | 1.2435 | 1.2435 | 1.2435 | 1.2435 | 1.2435 | 2.2101 | 2.8521 | 3.2727 | 3.4941 | 3.9368 | 4.3796 | 0.94882 | 1.8727 | 2.2472 | 2.2472 | 2.2472 | 2.2472 | 1.0479 | 1.219 | 1.219 | 1.219 | 1.219 | 1.219
2020-03-13 23:00 | Summer | 0.59115 | 0.84603 | 1.2208 | 1.2208 | 1.2208 | 1.2208 | 0.563 | 1.1135 | 1.1135 | 1.1135 | 1.1135 | 1.1135 | 2.0767 | 2.68 | 3.0752 | 3.2832 | 3.6992 | 4.1153 | 0.90309 | 1.7824 | 2.1389 | 2.1389 | 2.1389 | 2.1389 | 0.99246 | 1.1545 | 1.1545 | 1.1545 | 1.1545 | 1.1545
2020-03-14 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.5089 | 1.0065 | 1.0065 | 1.0065 | 1.0065 | 1.0065 | 1.9243 | 2.4833 | 2.8495 | 3.0422 | 3.4277 | 3.8132 | 0.67627 | 1.3347 | 1.6017 | 1.6017 | 1.6017 | 1.6017 | 0.99073 | 1.1525 | 1.1525 | 1.1525 | 1.1525 | 1.1525
2020-03-14 01:00 | Summer | 0.57221 | 0.81892 | 1.1817 | 1.1817 | 1.1817 | 1.1817 | 0.5287 | 1.0456 | 1.0456 | 1.0456 | 1.0456 | 1.0456 | 1.9243 | 2.4833 | 2.8495 | 3.0422 | 3.4277 | 3.8132 | 0.62492 | 1.2334 | 1.4801 | 1.4801 | 1.4801 | 1.4801 | 0.97168 | 1.1303 | 1.1303 | 1.1303 | 1.1303 | 1.1303
2020-03-14 02:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.53156 | 1.0513 | 1.0513 | 1.0513 | 1.0513 | 1.0513 | 1.8862 | 2.4341 | 2.7931 | 2.982 | 3.3599 | 3.7377 | 0.62492 | 1.2334 | 1.4801 | 1.4801 | 1.4801 | 1.4801 | 0.97168 | 1.1303 | 1.1303 | 1.1303 | 1.1303 | 1.1303
2020-03-14 03:00 | Summer | 0.59044 | 0.84502 | 1.2194 | 1.2194 | 1.2194 | 1.2194 | 0.50013 | 0.98912 | 0.98912 | 0.98912 | 0.98912 | 0.98912 | 1.7718 | 2.2865 | 2.6237 | 2.8012 | 3.1561 | 3.5111 | 0.60587 | 1.1958 | 1.435 | 1.435 | 1.435 | 1.435 | 0.97168 | 1.1303 | 1.1303 | 1.1303 | 1.1303 | 1.1303
2020-03-14 04:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.43356 | 0.85747 | 0.85747 | 0.85747 | 0.85747 | 0.85747 | 1.8481 | 2.3849 | 2.7366 | 2.9218 | 3.292 | 3.6622 | 0.59825 | 1.1808 | 1.4169 | 1.4169 | 1.4169 | 1.4169 | 0.93358 | 1.086 | 1.086 | 1.086 | 1.086 | 1.086
2020-03-14 05:00 | Summer | 0.59003 | 0.84443 | 1.2186 | 1.2186 | 1.2186 | 1.2186 | 0.44011 | 0.87043 | 0.87043 | 0.87043 | 0.87043 | 0.87043 | 1.7909 | 2.3112 | 2.652 | 2.8314 | 3.1902 | 3.549 | 0.78058 | 1.5406 | 1.8487 | 1.8487 | 1.8487 | 1.8487 | 0.86206 | 1.0028 | 1.0028 | 1.0028 | 1.0028 | 1.0028
2020-03-14 06:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.41725 | 0.82521 | 0.82521 | 0.82521 | 0.82521 | 0.82521 | 1.8481 | 2.3849 | 2.7366 | 2.9218 | 3.292 | 3.6622 | 0.85355 | 1.6846 | 2.0216 | 2.0216 | 2.0216 | 2.0216 | 0.95032 | 1.1055 | 1.1055 | 1.1055 | 1.1055 | 1.1055
2020-03-14 07:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.54585 | 1.0796 | 1.0796 | 1.0796 | 1.0796 | 1.0796 | 1.9821 | 2.5579 | 2.9351 | 3.1336 | 3.5307 | 3.9278 | 0.85736 | 1.6922 | 2.0306 | 2.0306 | 2.0306 | 2.0306 | 1.0479 | 1.219 | 1.219 | 1.219 | 1.219 | 1.219
2020-03-14 08:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.64874 | 1.283 | 1.283 | 1.283 | 1.283 | 1.283 | 2.0386 | 2.6308 | 3.0188 | 3.223 | 3.6314 | 4.0398 | 0.85355 | 1.6846 | 2.0216 | 2.0216 | 2.0216 | 2.0216 | 1.1227 | 1.306 | 1.306 | 1.306 | 1.306 | 1.306
2020-03-14 09:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.70018 | 1.3848 | 1.3848 | 1.3848 | 1.3848 | 1.3848 | 2.191 | 2.8275 | 3.2445 | 3.4639 | 3.9029 | 4.3418 | 0.88785 | 1.7523 | 2.1028 | 2.1028 | 2.1028 | 2.1028 | 1.1432 | 1.3298 | 1.3298 | 1.3298 | 1.3298 | 1.3298
2020-03-14 10:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.6916 | 1.3678 | 1.3678 | 1.3678 | 1.3678 | 1.3678 | 2.2673 | 2.9258 | 3.3573 | 3.5844 | 4.0386 | 4.4928 | 0.88757 | 1.7518 | 2.1021 | 2.1021 | 2.1021 | 2.1021 | 1.1622 | 1.352 | 1.352 | 1.352 | 1.352 | 1.352
2020-03-14 11:00 | Summer | 0.62683 | 0.8971 | 1.2945 | 1.2945 | 1.2945 | 1.2945 | 0.61444 | 1.2152 | 1.2152 | 1.2152 | 1.2152 | 1.2152 | 2.2673 | 2.9258 | 3.3573 | 3.5844 | 4.0386 | 4.4928 | 0.91071 | 1.7975 | 2.1569 | 2.1569 | 2.1569 | 2.1569 | 1.1622 | 1.352 | 1.352 | 1.352 | 1.352 | 1.352
2020-03-14 12:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.60587 | 1.1983 | 1.1983 | 1.1983 | 1.1983 | 1.1983 | 2.3294 | 3.0061 | 3.4494 | 3.6828 | 4.1494 | 4.6161 | 0.86498 | 1.7072 | 2.0486 | 2.0486 | 2.0486 | 2.0486 | 1.0479 | 1.219 | 1.219 | 1.219 | 1.219 | 1.219
2020-03-14 13:00 | Summer | 0.60672 | 0.86831 | 1.253 | 1.253 | 1.253 | 1.253 | 0.62016 | 1.2265 | 1.2265 | 1.2265 | 1.2265 | 1.2265 | 2.3625 | 3.0488 | 3.4984 | 3.735 | 4.2083 | 4.6816 | 0.87261 | 1.7222 | 2.0667 | 2.0667 | 2.0667 | 2.0667 | 1.0098 | 1.1746 | 1.1746 | 1.1746 | 1.1746 | 1.1746
2020-03-14 14:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.7459 | 1.4752 | 1.4752 | 1.4752 | 1.4752 | 1.4752 | 2.3625 | 3.0488 | 3.4984 | 3.735 | 4.2083 | 4.6816 | 0.72018 | 1.4214 | 1.7057 | 1.7057 | 1.7057 | 1.7057 | 0.99073 | 1.1525 | 1.1525 | 1.1525 | 1.1525 | 1.1525
2020-03-14 15:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.67446 | 1.3339 | 1.3339 | 1.3339 | 1.3339 | 1.3339 | 2.3625 | 3.0488 | 3.4984 | 3.735 | 4.2083 | 4.6816 | 0.83069 | 1.6395 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.91452 | 1.0638 | 1.0638 | 1.0638 | 1.0638 | 1.0638
2020-03-14 16:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.54585 | 1.0796 | 1.0796 | 1.0796 | 1.0796 | 1.0796 | 2.4578 | 3.1717 | 3.6395 | 3.8856 | 4.378 | 4.8704 | 0.93357 | 1.8426 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 0.89547 | 1.0417 | 1.0417 | 1.0417 | 1.0417 | 1.0417
2020-03-14 17:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.58872 | 1.1643 | 1.1643 | 1.1643 | 1.1643 | 1.1643 | 2.4006 | 3.098 | 3.5548 | 3.7953 | 4.2762 | 4.7571 | 0.94119 | 1.8576 | 2.2291 | 2.2291 | 2.2291 | 2.2291 | 0.89547 | 1.0417 | 1.0417 | 1.0417 | 1.0417 | 1.0417
2020-03-14 18:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.55157 | 1.0909 | 1.0909 | 1.0909 | 1.0909 | 1.0909 | 2.4197 | 3.1225 | 3.583 | 3.8254 | 4.3101 | 4.7949 | 0.94501 | 1.8651 | 2.2382 | 2.2382 | 2.2382 | 2.2382 | 0.91452 | 1.0638 | 1.0638 | 1.0638 | 1.0638 | 1.0638
2020-03-14 19:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.62016 | 1.2265 | 1.2265 | 1.2265 | 1.2265 | 1.2265 | 2.4768 | 3.1963 | 3.6677 | 3.9158 | 4.4119 | 4.9081 | 0.86879 | 1.7147 | 2.0577 | 2.0577 | 2.0577 | 2.0577 | 0.97168 | 1.1303 | 1.1303 | 1.1303 | 1.1303 | 1.1303
2020-03-14 20:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.72876 | 1.4413 | 1.4413 | 1.4413 | 1.4413 | 1.4413 | 2.3625 | 3.0488 | 3.4984 | 3.735 | 4.2083 | 4.6816 | 1.0136 | 2.0005 | 2.4006 | 2.4006 | 2.4006 | 2.4006 | 0.99073 | 1.1525 | 1.1525 | 1.1525 | 1.1525 | 1.1525
2020-03-14 21:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.59444 | 1.1756 | 1.1756 | 1.1756 | 1.1756 | 1.1756 | 2.2103 | 2.8523 | 3.273 | 3.4944 | 3.9371 | 4.3799 | 0.97168 | 1.9178 | 2.3013 | 2.3013 | 2.3013 | 2.3013 | 0.99073 | 1.1525 | 1.1525 | 1.1525 | 1.1525 | 1.1525
2020-03-14 22:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.51264 | 1.0139 | 1.0139 | 1.0139 | 1.0139 | 1.0139 | 2.191 | 2.8275 | 3.2445 | 3.4639 | 3.9029 | 4.3418 | 0.93738 | 1.8501 | 2.2201 | 2.2201 | 2.2201 | 2.2201 | 0.95263 | 1.1082 | 1.1082 | 1.1082 | 1.1082 | 1.1082
2020-03-14 23:00 | Summer | 0.55045 | 0.78778 | 1.1368 | 1.1368 | 1.1368 | 1.1368 | 0.4544 | 0.89869 | 0.89869 | 0.89869 | 0.89869 | 0.89869 | 1.9817 | 2.5574 | 2.9345 | 3.133 | 3.53 | 3.927 | 0.78115 | 1.5417 | 1.8501 | 1.8501 | 1.8501 | 1.8501 | 0.91452 | 1.0638 | 1.0638 | 1.0638 | 1.0638 | 1.0638
2020-03-15 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.45726 | 0.90434 | 0.90434 | 0.90434 | 0.90434 | 0.90434 | 1.81 | 2.3358 | 2.6802 | 2.8615 | 3.2241 | 3.5867 | 0.6897 | 1.3613 | 1.6335 | 1.6335 | 1.6335 | 1.6335 | 0.89547 | 1.0417 | 1.0417 | 1.0417 | 1.0417 | 1.0417
2020-03-15 01:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.49727 | 0.98347 | 0.98347 | 0.98347 | 0.98347 | 0.98347 | 1.7909 | 2.3112 | 2.652 | 2.8314 | 3.1902 | 3.549 | 0.60587 | 1.1958 | 1.435 | 1.435 | 1.435 | 1.435 | 1.105 | 1.2855 | 1.2855 | 1.2855 | 1.2855 | 1.2855
2020-03-15 02:00 | Summer | 0.55252 | 0.79075 | 1.1411 | 1.1411 | 1.1411 | 1.1411 | 0.44297 | 0.87608 | 0.87608 | 0.87608 | 0.87608 | 0.87608 | 1.6957 | 2.1882 | 2.5109 | 2.6808 | 3.0205 | 3.3602 | 0.60206 | 1.1883 | 1.4259 | 1.4259 | 1.4259 | 1.4259 | 0.91489 | 1.0643 | 1.0643 | 1.0643 | 1.0643 | 1.0643
2020-03-15 03:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.33723 | 0.66695 | 0.66695 | 0.66695 | 0.66695 | 0.66695 | 1.6385 | 2.1145 | 2.4263 | 2.5904 | 2.9187 | 3.2469 | 0.55252 | 1.0905 | 1.3086 | 1.3086 | 1.3086 | 1.3086 | 0.89547 | 1.0417 | 1.0417 | 1.0417 | 1.0417 | 1.0417
2020-03-15 04:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.32864 | 0.64998 | 0.64998 | 0.64998 | 0.64998 | 0.64998 | 1.6576 | 2.1391 | 2.4545 | 2.6205 | 2.9526 | 3.2847 | 0.60968 | 1.2033 | 1.444 | 1.444 | 1.444 | 1.444 | 0.87642 | 1.0195 | 1.0195 | 1.0195 | 1.0195 | 1.0195
2020-03-15 05:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.49441 | 0.97782 | 0.97782 | 0.97782 | 0.97782 | 0.97782 | 1.6957 | 2.1882 | 2.5109 | 2.6808 | 3.0205 | 3.3602 | 0.63254 | 1.2484 | 1.4981 | 1.4981 | 1.4981 | 1.4981 | 0.91452 | 1.0638 | 1.0638 | 1.0638 | 1.0638 | 1.0638
2020-03-15 06:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.5087 | 1.0061 | 1.0061 | 1.0061 | 1.0061 | 1.0061 | 1.6957 | 2.1882 | 2.5109 | 2.6808 | 3.0205 | 3.3602 | 0.68589 | 1.3537 | 1.6245 | 1.6245 | 1.6245 | 1.6245 | 0.91452 | 1.0638 | 1.0638 | 1.0638 | 1.0638 | 1.0638
2020-03-15 07:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.60587 | 1.1983 | 1.1983 | 1.1983 | 1.1983 | 1.1983 | 1.9624 | 2.5325 | 2.9059 | 3.1025 | 3.4956 | 3.8887 | 0.724 | 1.4289 | 1.7147 | 1.7147 | 1.7147 | 1.7147 | 0.91452 | 1.0638 | 1.0638 | 1.0638 | 1.0638 | 1.0638
2020-03-15 08:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.50298 | 0.99478 | 0.99478 | 0.99478 | 0.99478 | 0.99478 | 2.0577 | 2.6554 | 3.047 | 3.2531 | 3.6653 | 4.0775 | 0.94119 | 1.8576 | 2.2291 | 2.2291 | 2.2291 | 2.2291 | 0.95263 | 1.1082 | 1.1082 | 1.1082 | 1.1082 | 1.1082
2020-03-15 09:00 | Summer | 0.5505 | 0.78786 | 1.1369 | 1.1369 | 1.1369 | 1.1369 | 0.55443 | 1.0965 | 1.0965 | 1.0965 | 1.0965 | 1.0965 | 2.1529 | 2.7783 | 3.1881 | 3.4037 | 3.835 | 4.2663 | 0.94501 | 1.8651 | 2.2382 | 2.2382 | 2.2382 | 2.2382 | 0.97168 | 1.1303 | 1.1303 | 1.1303 | 1.1303 | 1.1303
2020-03-15 10:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.55157 | 1.0909 | 1.0909 | 1.0909 | 1.0909 | 1.0909 | 2.2291 | 2.8767 | 3.3009 | 3.5242 | 3.9708 | 4.4173 | 0.91071 | 1.7975 | 2.1569 | 2.1569 | 2.1569 | 2.1569 | 1.0098 | 1.1746 | 1.1746 | 1.1746 | 1.1746 | 1.1746
2020-03-15 11:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.42011 | 0.83086 | 0.83086 | 0.83086 | 0.83086 | 0.83086 | 2.3244 | 2.9996 | 3.442 | 3.6748 | 4.1404 | 4.6061 | 0.93738 | 1.8501 | 2.2201 | 2.2201 | 2.2201 | 2.2201 | 1.0479 | 1.219 | 1.219 | 1.219 | 1.219 | 1.219
2020-03-15 12:00 | Summer | 0.57668 | 0.82532 | 1.191 | 1.191 | 1.191 | 1.191 | 0.38867 | 0.76869 | 0.76869 | 0.76869 | 0.76869 | 0.76869 | 2.3058 | 2.9755 | 3.4144 | 3.6453 | 4.1072 | 4.5691 | 0.87642 | 1.7298 | 2.0757 | 2.0757 | 2.0757 | 2.0757 | 1.1241 | 1.3076 | 1.3076 | 1.3076 | 1.3076 | 1.3076
2020-03-15 13:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.44868 | 0.88738 | 0.88738 | 0.88738 | 0.88738 | 0.88738 | 2.3244 | 2.9996 | 3.442 | 3.6748 | 4.1404 | 4.6061 | 0.7188 | 1.4187 | 1.7024 | 1.7024 | 1.7024 | 1.7024 | 1.0288 | 1.1968 | 1.1968 | 1.1968 | 1.1968 | 1.1968
2020-03-15 14:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.43154 | 0.85347 | 0.85347 | 0.85347 | 0.85347 | 0.85347 | 2.2673 | 2.9258 | 3.3573 | 3.5844 | 4.0386 | 4.4928 | 0.78877 | 1.5568 | 1.8681 | 1.8681 | 1.8681 | 1.8681 | 1.0479 | 1.219 | 1.219 | 1.219 | 1.219 | 1.219
2020-03-15 15:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.43725 | 0.86478 | 0.86478 | 0.86478 | 0.86478 | 0.86478 | 2.3054 | 2.975 | 3.4138 | 3.6447 | 4.1065 | 4.5683 | 0.86117 | 1.6997 | 2.0396 | 2.0396 | 2.0396 | 2.0396 | 1.0098 | 1.1746 | 1.1746 | 1.1746 | 1.1746 | 1.1746
2020-03-15 16:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.45154 | 0.89304 | 0.89304 | 0.89304 | 0.89304 | 0.89304 | 2.3054 | 2.975 | 3.4138 | 3.6447 | 4.1065 | 4.5683 | 0.81926 | 1.617 | 1.9403 | 1.9403 | 1.9403 | 1.9403 | 0.97168 | 1.1303 | 1.1303 | 1.1303 | 1.1303 | 1.1303
2020-03-15 17:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.38867 | 0.76869 | 0.76869 | 0.76869 | 0.76869 | 0.76869 | 2.3054 | 2.975 | 3.4138 | 3.6447 | 4.1065 | 4.5683 | 0.86117 | 1.6997 | 2.0396 | 2.0396 | 2.0396 | 2.0396 | 0.95263 | 1.1082 | 1.1082 | 1.1082 | 1.1082 | 1.1082
2020-03-15 18:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.46012 | 0.90999 | 0.90999 | 0.90999 | 0.90999 | 0.90999 | 2.2863 | 2.9504 | 3.3855 | 3.6146 | 4.0726 | 4.5306 | 0.90309 | 1.7824 | 2.1389 | 2.1389 | 2.1389 | 2.1389 | 0.95263 | 1.1082 | 1.1082 | 1.1082 | 1.1082 | 1.1082
2020-03-15 19:00 | Summer | 0.60296 | 0.86293 | 1.2452 | 1.2452 | 1.2452 | 1.2452 | 0.39724 | 0.78565 | 0.78565 | 0.78565 | 0.78565 | 0.78565 | 2.2101 | 2.8521 | 3.2727 | 3.4941 | 3.9368 | 4.3796 | 0.81545 | 1.6094 | 1.9313 | 1.9313 | 1.9313 | 1.9313 | 0.91452 | 1.0638 | 1.0638 | 1.0638 | 1.0638 | 1.0638
2020-03-15 20:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.47155 | 0.9326 | 0.9326 | 0.9326 | 0.9326 | 0.9326 | 2.2291 | 2.8767 | 3.3009 | 3.5242 | 3.9708 | 4.4173 | 0.82307 | 1.6245 | 1.9494 | 1.9494 | 1.9494 | 1.9494 | 0.95263 | 1.1082 | 1.1082 | 1.1082 | 1.1082 | 1.1082
2020-03-15 21:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.44011 | 0.87043 | 0.87043 | 0.87043 | 0.87043 | 0.87043 | 2.0584 | 2.6563 | 3.048 | 3.2542 | 3.6666 | 4.0789 | 0.92214 | 1.82 | 2.184 | 2.184 | 2.184 | 2.184 | 0.91452 | 1.0638 | 1.0638 | 1.0638 | 1.0638 | 1.0638
2020-03-15 22:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.30007 | 0.59347 | 0.59347 | 0.59347 | 0.59347 | 0.59347 | 2.0577 | 2.6554 | 3.047 | 3.2531 | 3.6653 | 4.0775 | 0.7621 | 1.5041 | 1.805 | 1.805 | 1.805 | 1.805 | 0.89547 | 1.0417 | 1.0417 | 1.0417 | 1.0417 | 1.0417
2020-03-15 23:00 | Summer | 0.57284 | 0.81982 | 1.183 | 1.183 | 1.183 | 1.183 | 0.31151 | 0.61608 | 0.61608 | 0.61608 | 0.61608 | 0.61608 | 1.8862 | 2.4341 | 2.7931 | 2.982 | 3.3599 | 3.7377 | 0.71116 | 1.4036 | 1.6843 | 1.6843 | 1.6843 | 1.6843 | 0.85737 | 0.99734 | 0.99734 | 0.99734 | 0.99734 | 0.99734
2020-03-16 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.32865 | 0.64999 | 0.64999 | 0.64999 | 0.64999 | 0.64999 | 1.7338 | 2.2374 | 2.5674 | 2.741 | 3.0884 | 3.4357 | 0.61349 | 1.2108 | 1.453 | 1.453 | 1.453 | 1.453 | 0.83831 | 0.97518 | 0.97518 | 0.97518 | 0.97518 | 0.97518
2020-03-16 01:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.32008 | 0.63304 | 0.63304 | 0.63304 | 0.63304 | 0.63304 | 1.6896 | 2.1804 | 2.502 | 2.6712 | 3.0097 | 3.3482 | 0.59061 | 1.1657 | 1.3988 | 1.3988 | 1.3988 | 1.3988 | 0.83831 | 0.97518 | 0.97518 | 0.97518 | 0.97518 | 0.97518
2020-03-16 02:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.46297 | 0.91565 | 0.91565 | 0.91565 | 0.91565 | 0.91565 | 1.6385 | 2.1145 | 2.4263 | 2.5904 | 2.9187 | 3.2469 | 0.60206 | 1.1883 | 1.4259 | 1.4259 | 1.4259 | 1.4259 | 0.87642 | 1.0195 | 1.0195 | 1.0195 | 1.0195 | 1.0195
2020-03-16 03:00 | Summer | 0.60213 | 0.86175 | 1.2435 | 1.2435 | 1.2435 | 1.2435 | 0.42582 | 0.84217 | 0.84217 | 0.84217 | 0.84217 | 0.84217 | 1.6385 | 2.1145 | 2.4263 | 2.5904 | 2.9187 | 3.2469 | 0.5792 | 1.1431 | 1.3718 | 1.3718 | 1.3718 | 1.3718 | 0.90089 | 1.048 | 1.048 | 1.048 | 1.048 | 1.048
2020-03-16 04:00 | Summer | 0.70494 | 1.0089 | 1.4559 | 1.4559 | 1.4559 | 1.4559 | 0.38551 | 0.76244 | 0.76244 | 0.76244 | 0.76244 | 0.76244 | 1.6576 | 2.1391 | 2.4545 | 2.6205 | 2.9526 | 3.2847 | 0.5792 | 1.1431 | 1.3718 | 1.3718 | 1.3718 | 1.3718 | 0.93336 | 1.0857 | 1.0857 | 1.0857 | 1.0857 | 1.0857
2020-03-16 05:00 | Summer | 0.78115 | 1.118 | 1.6133 | 1.6133 | 1.6133 | 1.6133 | 0.55443 | 1.0965 | 1.0965 | 1.0965 | 1.0965 | 1.0965 | 1.7719 | 2.2866 | 2.6238 | 2.8013 | 3.1562 | 3.5112 | 0.78115 | 1.5417 | 1.8501 | 1.8501 | 1.8501 | 1.8501 | 1.2392 | 1.4416 | 1.4416 | 1.4416 | 1.4416 | 1.4416
2020-03-16 06:00 | Summer | 0.87642 | 1.2543 | 1.81 | 1.81 | 1.81 | 1.81 | 0.72304 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 2.0618 | 2.6607 | 3.0531 | 3.2596 | 3.6726 | 4.0856 | 0.78496 | 1.5493 | 1.8591 | 1.8591 | 1.8591 | 1.8591 | 1.5242 | 1.7731 | 1.7731 | 1.7731 | 1.7731 | 1.7731
2020-03-16 07:00 | Summer | 1.1847 | 1.6955 | 2.4466 | 2.4466 | 2.4466 | 2.4466 | 0.82307 | 1.6278 | 1.6278 | 1.6278 | 1.6278 | 1.6278 | 2.428 | 3.1332 | 3.5953 | 3.8385 | 4.3249 | 4.8113 | 0.93357 | 1.8426 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 1.9434 | 2.2606 | 2.2606 | 2.2606 | 2.2606 | 2.2606
2020-03-16 08:00 | Summer | 1.448 | 2.0723 | 2.9904 | 2.9904 | 2.9904 | 2.9904 | 0.95739 | 1.8935 | 1.8935 | 1.8935 | 1.8935 | 1.8935 | 2.6102 | 3.3684 | 3.8652 | 4.1266 | 4.6495 | 5.1724 | 0.96787 | 1.9103 | 2.2923 | 2.2923 | 2.2923 | 2.2923 | 2.2101 | 2.5709 | 2.5709 | 2.5709 | 2.5709 | 2.5709
2020-03-16 09:00 | Summer | 1.7528 | 2.5086 | 3.62 | 3.62 | 3.62 | 3.62 | 0.88022 | 1.7409 | 1.7409 | 1.7409 | 1.7409 | 1.7409 | 2.6864 | 3.4668 | 3.978 | 4.2471 | 4.7853 | 5.3234 | 1.2003 | 2.369 | 2.8428 | 2.8428 | 2.8428 | 2.8428 | 2.2291 | 2.5931 | 2.5931 | 2.5931 | 2.5931 | 2.5931
2020-03-16 10:00 | Summer | 1.7528 | 2.5086 | 3.62 | 3.62 | 3.62 | 3.62 | 0.93452 | 1.8483 | 1.8483 | 1.8483 | 1.8483 | 1.8483 | 2.9913 | 3.8601 | 4.4294 | 4.729 | 5.3283 | 5.9275 | 1.1241 | 2.2186 | 2.6623 | 2.6623 | 2.6623 | 2.6623 | 2.3244 | 2.7039 | 2.7039 | 2.7039 | 2.7039 | 2.7039
2020-03-16 11:00 | Summer | 1.6766 | 2.3995 | 3.4626 | 3.4626 | 3.4626 | 3.4626 | 0.95739 | 1.8935 | 1.8935 | 1.8935 | 1.8935 | 1.8935 | 2.9341 | 3.7864 | 4.3448 | 4.6387 | 5.2265 | 5.8142 | 1.0708 | 2.1133 | 2.536 | 2.536 | 2.536 | 2.536 | 2.4006 | 2.7926 | 2.7926 | 2.7926 | 2.7926 | 2.7926
2020-03-16 12:00 | Summer | 1.7719 | 2.5359 | 3.6593 | 3.6593 | 3.6593 | 3.6593 | 0.89451 | 1.7691 | 1.7691 | 1.7691 | 1.7691 | 1.7691 | 2.9341 | 3.7864 | 4.3448 | 4.6387 | 5.2265 | 5.8142 | 1.086 | 2.1434 | 2.5721 | 2.5721 | 2.5721 | 2.5721 | 2.4006 | 2.7926 | 2.7926 | 2.7926 | 2.7926 | 2.7926
2020-03-16 13:00 | Summer | 1.7338 | 2.4813 | 3.5806 | 3.5806 | 3.5806 | 3.5806 | 1.0603 | 2.097 | 2.097 | 2.097 | 2.097 | 2.097 | 2.9722 | 3.8356 | 4.4012 | 4.6989 | 5.2943 | 5.8898 | 1.1355 | 2.2412 | 2.6894 | 2.6894 | 2.6894 | 2.6894 | 2.3816 | 2.7704 | 2.7704 | 2.7704 | 2.7704 | 2.7704
2020-03-16 14:00 | Summer | 1.7528 | 2.5086 | 3.62 | 3.62 | 3.62 | 3.62 | 1.066 | 2.1083 | 2.1083 | 2.1083 | 2.1083 | 2.1083 | 2.9722 | 3.8356 | 4.4012 | 4.6989 | 5.2943 | 5.8898 | 1.1241 | 2.2186 | 2.6623 | 2.6623 | 2.6623 | 2.6623 | 2.3625 | 2.7482 | 2.7482 | 2.7482 | 2.7482 | 2.7482
2020-03-16 15:00 | Summer | 1.7528 | 2.5086 | 3.62 | 3.62 | 3.62 | 3.62 | 0.93738 | 1.8539 | 1.8539 | 1.8539 | 1.8539 | 1.8539 | 2.915 | 3.7618 | 4.3166 | 4.6086 | 5.1925 | 5.7765 | 1.0898 | 2.1509 | 2.5811 | 2.5811 | 2.5811 | 2.5811 | 2.3054 | 2.6817 | 2.6817 | 2.6817 | 2.6817 | 2.6817
2020-03-16 16:00 | Summer | 1.6766 | 2.3995 | 3.4626 | 3.4626 | 3.4626 | 3.4626 | 1.0374 | 2.0517 | 2.0517 | 2.0517 | 2.0517 | 2.0517 | 2.915 | 3.7618 | 4.3166 | 4.6086 | 5.1925 | 5.7765 | 1.1355 | 2.2412 | 2.6894 | 2.6894 | 2.6894 | 2.6894 | 2.3054 | 2.6817 | 2.6817 | 2.6817 | 2.6817 | 2.6817
2020-03-16 17:00 | Summer | 1.6576 | 2.3723 | 3.4232 | 3.4232 | 3.4232 | 3.4232 | 1.0117 | 2.0009 | 2.0009 | 2.0009 | 2.0009 | 2.0009 | 2.8579 | 3.688 | 4.2319 | 4.5182 | 5.0907 | 5.6632 | 1.006 | 1.9855 | 2.3826 | 2.3826 | 2.3826 | 2.3826 | 2.2101 | 2.5709 | 2.5709 | 2.5709 | 2.5709 | 2.5709
2020-03-16 18:00 | Summer | 1.1924 | 1.7065 | 2.4625 | 2.4625 | 2.4625 | 2.4625 | 0.7271 | 1.438 | 1.438 | 1.438 | 1.438 | 1.438 | 2.7245 | 3.5159 | 4.0344 | 4.3073 | 4.8531 | 5.3989 | 0.92595 | 1.8275 | 2.193 | 2.193 | 2.193 | 2.193 | 1.6318 | 1.8982 | 1.8982 | 1.8982 | 1.8982 | 1.8982
2020-03-16 19:00 | Summer | 0.78195 | 1.1191 | 1.6149 | 1.6149 | 1.6149 | 1.6149 | 0.53728 | 1.0626 | 1.0626 | 1.0626 | 1.0626 | 1.0626 | 2.4197 | 3.1225 | 3.583 | 3.8254 | 4.3101 | 4.7949 | 1.0936 | 2.1585 | 2.5901 | 2.5901 | 2.5901 | 2.5901 | 1.1813 | 1.3741 | 1.3741 | 1.3741 | 1.3741 | 1.3741
2020-03-16 20:00 | Summer | 0.68575 | 0.98142 | 1.4162 | 1.4162 | 1.4162 | 1.4162 | 0.54014 | 1.0683 | 1.0683 | 1.0683 | 1.0683 | 1.0683 | 2.3241 | 2.9992 | 3.4415 | 3.6743 | 4.1399 | 4.6055 | 0.91452 | 1.805 | 2.166 | 2.166 | 2.166 | 2.166 | 1.105 | 1.2855 | 1.2855 | 1.2855 | 1.2855 | 1.2855
2020-03-16 21:00 | Summer | 0.64779 | 0.92709 | 1.3378 | 1.3378 | 1.3378 | 1.3378 | 0.46012 | 0.90999 | 0.90999 | 0.90999 | 0.90999 | 0.90999 | 2.1148 | 2.7291 | 3.1316 | 3.3435 | 3.7671 | 4.1908 | 0.87261 | 1.7222 | 2.0667 | 2.0667 | 2.0667 | 2.0667 | 0.99091 | 1.1527 | 1.1527 | 1.1527 | 1.1527 | 1.1527
2020-03-16 22:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.41153 | 0.81391 | 0.81391 | 0.81391 | 0.81391 | 0.81391 | 1.9272 | 2.487 | 2.8537 | 3.0467 | 3.4328 | 3.8189 | 0.85736 | 1.6922 | 2.0306 | 2.0306 | 2.0306 | 2.0306 | 0.91452 | 1.0638 | 1.0638 | 1.0638 | 1.0638 | 1.0638
2020-03-16 23:00 | Summer | 0.60982 | 0.87274 | 1.2594 | 1.2594 | 1.2594 | 1.2594 | 0.45154 | 0.89304 | 0.89304 | 0.89304 | 0.89304 | 0.89304 | 1.8862 | 2.4341 | 2.7931 | 2.982 | 3.3599 | 3.7377 | 0.7621 | 1.5041 | 1.805 | 1.805 | 1.805 | 1.805 | 0.85737 | 0.99734 | 0.99734 | 0.99734 | 0.99734 | 0.99734
2020-03-17 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.41725 | 0.82521 | 0.82521 | 0.82521 | 0.82521 | 0.82521 | 1.7338 | 2.2374 | 2.5674 | 2.741 | 3.0884 | 3.4357 | 0.63635 | 1.256 | 1.5072 | 1.5072 | 1.5072 | 1.5072 | 0.85737 | 0.99734 | 0.99734 | 0.99734 | 0.99734 | 0.99734
2020-03-17 01:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.40582 | 0.8026 | 0.8026 | 0.8026 | 0.8026 | 0.8026 | 1.6957 | 2.1882 | 2.5109 | 2.6808 | 3.0205 | 3.3602 | 0.58301 | 1.1507 | 1.3808 | 1.3808 | 1.3808 | 1.3808 | 0.81926 | 0.95302 | 0.95302 | 0.95302 | 0.95302 | 0.95302
2020-03-17 02:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.3258 | 0.64434 | 0.64434 | 0.64434 | 0.64434 | 0.64434 | 1.6576 | 2.1391 | 2.4545 | 2.6205 | 2.9526 | 3.2847 | 0.57539 | 1.1356 | 1.3628 | 1.3628 | 1.3628 | 1.3628 | 0.83831 | 0.97518 | 0.97518 | 0.97518 | 0.97518 | 0.97518
2020-03-17 03:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.42341 | 0.83739 | 0.83739 | 0.83739 | 0.83739 | 0.83739 | 1.6385 | 2.1145 | 2.4263 | 2.5904 | 2.9187 | 3.2469 | 0.58301 | 1.1507 | 1.3808 | 1.3808 | 1.3808 | 1.3808 | 0.81926 | 0.95302 | 0.95302 | 0.95302 | 0.95302 | 0.95302
2020-03-17 04:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.55443 | 1.0965 | 1.0965 | 1.0965 | 1.0965 | 1.0965 | 1.6576 | 2.1391 | 2.4545 | 2.6205 | 2.9526 | 3.2847 | 0.60968 | 1.2033 | 1.444 | 1.444 | 1.444 | 1.444 | 0.91373 | 1.0629 | 1.0629 | 1.0629 | 1.0629 | 1.0629
2020-03-17 05:00 | Summer | 0.724 | 1.0362 | 1.4952 | 1.4952 | 1.4952 | 1.4952 | 0.53728 | 1.0626 | 1.0626 | 1.0626 | 1.0626 | 1.0626 | 1.7824 | 2.3002 | 2.6394 | 2.818 | 3.175 | 3.5321 | 0.65922 | 1.3011 | 1.5613 | 1.5613 | 1.5613 | 1.5613 | 1.2059 | 1.4028 | 1.4028 | 1.4028 | 1.4028 | 1.4028
2020-03-17 06:00 | Summer | 0.7621 | 1.0907 | 1.5739 | 1.5739 | 1.5739 | 1.5739 | 0.70018 | 1.3848 | 1.3848 | 1.3848 | 1.3848 | 1.3848 | 1.9683 | 2.5401 | 2.9147 | 3.1118 | 3.5062 | 3.9005 | 0.75829 | 1.4966 | 1.796 | 1.796 | 1.796 | 1.796 | 1.4648 | 1.704 | 1.704 | 1.704 | 1.704 | 1.704
2020-03-17 07:00 | Summer | 1.2263 | 1.755 | 2.5325 | 2.5325 | 2.5325 | 2.5325 | 0.84307 | 1.6674 | 1.6674 | 1.6674 | 1.6674 | 1.6674 | 2.4006 | 3.098 | 3.5548 | 3.7953 | 4.2762 | 4.7571 | 0.88785 | 1.7523 | 2.1028 | 2.1028 | 2.1028 | 2.1028 | 1.8559 | 2.159 | 2.159 | 2.159 | 2.159 | 2.159
2020-03-17 08:00 | Summer | 1.7338 | 2.4813 | 3.5806 | 3.5806 | 3.5806 | 3.5806 | 0.97168 | 1.9217 | 1.9217 | 1.9217 | 1.9217 | 1.9217 | 2.6496 | 3.4192 | 3.9235 | 4.1889 | 4.7197 | 5.2505 | 0.95644 | 1.8877 | 2.2652 | 2.2652 | 2.2652 | 2.2652 | 2.4768 | 2.8812 | 2.8812 | 2.8812 | 2.8812 | 2.8812
2020-03-17 09:00 | Summer | 1.6766 | 2.3995 | 3.4626 | 3.4626 | 3.4626 | 3.4626 | 0.9088 | 1.7974 | 1.7974 | 1.7974 | 1.7974 | 1.7974 | 2.7436 | 3.5405 | 4.0627 | 4.3375 | 4.8871 | 5.4367 | 1.1317 | 2.2337 | 2.6804 | 2.6804 | 2.6804 | 2.6804 | 2.287 | 2.6604 | 2.6604 | 2.6604 | 2.6604 | 2.6604
2020-03-17 10:00 | Summer | 1.7909 | 2.5631 | 3.6987 | 3.6987 | 3.6987 | 3.6987 | 0.87737 | 1.7352 | 1.7352 | 1.7352 | 1.7352 | 1.7352 | 2.7363 | 3.5312 | 4.0519 | 4.326 | 4.8742 | 5.4223 | 1.1165 | 2.2036 | 2.6443 | 2.6443 | 2.6443 | 2.6443 | 2.3625 | 2.7482 | 2.7482 | 2.7482 | 2.7482 | 2.7482
2020-03-17 11:00 | Summer | 1.6957 | 2.4268 | 3.5019 | 3.5019 | 3.5019 | 3.5019 | 0.92595 | 1.8313 | 1.8313 | 1.8313 | 1.8313 | 1.8313 | 2.8388 | 3.6634 | 4.2037 | 4.4881 | 5.0568 | 5.6255 | 1.086 | 2.1434 | 2.5721 | 2.5721 | 2.5721 | 2.5721 | 2.4006 | 2.7926 | 2.7926 | 2.7926 | 2.7926 | 2.7926
2020-03-17 12:00 | Summer | 1.7719 | 2.5359 | 3.6593 | 3.6593 | 3.6593 | 3.6593 | 0.94596 | 1.8709 | 1.8709 | 1.8709 | 1.8709 | 1.8709 | 2.9722 | 3.8356 | 4.4012 | 4.6989 | 5.2943 | 5.8898 | 1.0822 | 2.1359 | 2.5631 | 2.5631 | 2.5631 | 2.5631 | 2.4006 | 2.7926 | 2.7926 | 2.7926 | 2.7926 | 2.7926
2020-03-17 13:00 | Summer | 1.7338 | 2.4813 | 3.5806 | 3.5806 | 3.5806 | 3.5806 | 1.0203 | 2.0178 | 2.0178 | 2.0178 | 2.0178 | 2.0178 | 2.9341 | 3.7864 | 4.3448 | 4.6387 | 5.2265 | 5.8142 | 1.0974 | 2.166 | 2.5992 | 2.5992 | 2.5992 | 2.5992 | 2.553 | 2.9699 | 2.9699 | 2.9699 | 2.9699 | 2.9699
2020-03-17 14:00 | Summer | 1.7338 | 2.4813 | 3.5806 | 3.5806 | 3.5806 | 3.5806 | 1.0546 | 2.0856 | 2.0856 | 2.0856 | 2.0856 | 2.0856 | 2.9531 | 3.811 | 4.373 | 4.6688 | 5.2604 | 5.852 | 1.1317 | 2.2337 | 2.6804 | 2.6804 | 2.6804 | 2.6804 | 2.6483 | 3.0807 | 3.0807 | 3.0807 | 3.0807 | 3.0807
2020-03-17 15:00 | Summer | 1.7132 | 2.4519 | 3.5382 | 3.5382 | 3.5382 | 3.5382 | 1.0231 | 2.0235 | 2.0235 | 2.0235 | 2.0235 | 2.0235 | 3.0484 | 3.9339 | 4.5141 | 4.8194 | 5.4301 | 6.0408 | 1.1393 | 2.2487 | 2.6984 | 2.6984 | 2.6984 | 2.6984 | 2.4197 | 2.8147 | 2.8147 | 2.8147 | 2.8147 | 2.8147
2020-03-17 16:00 | Summer | 1.6393 | 2.3461 | 3.3855 | 3.3855 | 3.3855 | 3.3855 | 1.106 | 2.1874 | 2.1874 | 2.1874 | 2.1874 | 2.1874 | 3.0484 | 3.9339 | 4.5141 | 4.8194 | 5.4301 | 6.0408 | 1.147 | 2.2637 | 2.7165 | 2.7165 | 2.7165 | 2.7165 | 2.4387 | 2.8369 | 2.8369 | 2.8369 | 2.8369 | 2.8369
2020-03-17 17:00 | Summer | 1.5814 | 2.2632 | 3.2659 | 3.2659 | 3.2659 | 3.2659 | 1.0831 | 2.1422 | 2.1422 | 2.1422 | 2.1422 | 2.1422 | 3.0209 | 3.8984 | 4.4734 | 4.7759 | 5.3811 | 5.9863 | 1.0174 | 2.008 | 2.4096 | 2.4096 | 2.4096 | 2.4096 | 2.4197 | 2.8147 | 2.8147 | 2.8147 | 2.8147 | 2.8147
2020-03-17 18:00 | Summer | 1.123 | 1.6073 | 2.3193 | 2.3193 | 2.3193 | 2.3193 | 0.78162 | 1.5458 | 1.5458 | 1.5458 | 1.5458 | 1.5458 | 2.7245 | 3.5159 | 4.0344 | 4.3073 | 4.8531 | 5.3989 | 0.97168 | 1.9178 | 2.3013 | 2.3013 | 2.3013 | 2.3013 | 1.7771 | 2.0672 | 2.0672 | 2.0672 | 2.0672 | 2.0672
2020-03-17 19:00 | Summer | 0.81926 | 1.1725 | 1.692 | 1.692 | 1.692 | 1.692 | 0.55792 | 1.1034 | 1.1034 | 1.1034 | 1.1034 | 1.1034 | 2.3538 | 3.0376 | 3.4855 | 3.7213 | 4.1929 | 4.6644 | 0.91452 | 1.805 | 2.166 | 2.166 | 2.166 | 2.166 | 1.3527 | 1.5736 | 1.5736 | 1.5736 | 1.5736 | 1.5736
2020-03-17 20:00 | Summer | 0.74305 | 1.0634 | 1.5346 | 1.5346 | 1.5346 | 1.5346 | 0.44356 | 0.87726 | 0.87726 | 0.87726 | 0.87726 | 0.87726 | 2.2863 | 2.9504 | 3.3855 | 3.6146 | 4.0726 | 4.5306 | 0.92976 | 1.8351 | 2.2021 | 2.2021 | 2.2021 | 2.2021 | 1.2587 | 1.4642 | 1.4642 | 1.4642 | 1.4642 | 1.4642
2020-03-17 21:00 | Summer | 0.64779 | 0.92709 | 1.3378 | 1.3378 | 1.3378 | 1.3378 | 0.39809 | 0.78731 | 0.78731 | 0.78731 | 0.78731 | 0.78731 | 2.0767 | 2.68 | 3.0752 | 3.2832 | 3.6992 | 4.1153 | 0.94119 | 1.8576 | 2.2291 | 2.2291 | 2.2291 | 2.2291 | 1.0669 | 1.2411 | 1.2411 | 1.2411 | 1.2411 | 1.2411
2020-03-17 22:00 | Summer | 0.66684 | 0.95435 | 1.3772 | 1.3772 | 1.3772 | 1.3772 | 0.4001 | 0.7913 | 0.7913 | 0.7913 | 0.7913 | 0.7913 | 2.0171 | 2.603 | 2.9869 | 3.1889 | 3.593 | 3.9971 | 0.89547 | 1.7674 | 2.1208 | 2.1208 | 2.1208 | 2.1208 | 0.96126 | 1.1182 | 1.1182 | 1.1182 | 1.1182 | 1.1182
2020-03-17 23:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.37724 | 0.74608 | 0.74608 | 0.74608 | 0.74608 | 0.74608 | 1.9243 | 2.4833 | 2.8495 | 3.0422 | 3.4277 | 3.8132 | 0.79269 | 1.5645 | 1.8774 | 1.8774 | 1.8774 | 1.8774 | 0.95263 | 1.1082 | 1.1082 | 1.1082 | 1.1082 | 1.1082
2020-03-18 | Summer | 0.59055 | 0.84518 | 1.2196 | 1.2196 | 1.2196 | 1.2196 | 0.35437 | 0.70086 | 0.70086 | 0.70086 | 0.70086 | 0.70086 | 1.7528 | 2.262 | 2.5956 | 2.7712 | 3.1223 | 3.4734 | 0.65541 | 1.2936 | 1.5523 | 1.5523 | 1.5523 | 1.5523 | 0.91452 | 1.0638 | 1.0638 | 1.0638 | 1.0638 | 1.0638
2020-03-18 01:00 | Summer | 0.59836 | 0.85634 | 1.2357 | 1.2357 | 1.2357 | 1.2357 | 0.29994 | 0.59321 | 0.59321 | 0.59321 | 0.59321 | 0.59321 | 1.6766 | 2.1636 | 2.4827 | 2.6507 | 2.9865 | 3.3224 | 0.5792 | 1.1431 | 1.3718 | 1.3718 | 1.3718 | 1.3718 | 0.89547 | 1.0417 | 1.0417 | 1.0417 | 1.0417 | 1.0417
2020-03-18 02:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.30577 | 0.60473 | 0.60473 | 0.60473 | 0.60473 | 0.60473 | 1.6687 | 2.1534 | 2.471 | 2.6381 | 2.9724 | 3.3067 | 0.58682 | 1.1582 | 1.3898 | 1.3898 | 1.3898 | 1.3898 | 0.89547 | 1.0417 | 1.0417 | 1.0417 | 1.0417 | 1.0417
2020-03-18 03:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.43439 | 0.85912 | 0.85912 | 0.85912 | 0.85912 | 0.85912 | 1.7719 | 2.2866 | 2.6238 | 2.8013 | 3.1562 | 3.5112 | 0.5792 | 1.1431 | 1.3718 | 1.3718 | 1.3718 | 1.3718 | 0.89547 | 1.0417 | 1.0417 | 1.0417 | 1.0417 | 1.0417
2020-03-18 04:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.44583 | 0.88173 | 0.88173 | 0.88173 | 0.88173 | 0.88173 | 1.6957 | 2.1882 | 2.5109 | 2.6808 | 3.0205 | 3.3602 | 0.56776 | 1.1206 | 1.3447 | 1.3447 | 1.3447 | 1.3447 | 0.87642 | 1.0195 | 1.0195 | 1.0195 | 1.0195 | 1.0195
2020-03-18 05:00 | Summer | 0.64269 | 0.91979 | 1.3273 | 1.3273 | 1.3273 | 1.3273 | 0.45726 | 0.90434 | 0.90434 | 0.90434 | 0.90434 | 0.90434 | 1.7909 | 2.3112 | 2.652 | 2.8314 | 3.1902 | 3.549 | 0.68208 | 1.3462 | 1.6155 | 1.6155 | 1.6155 | 1.6155 | 1.2015 | 1.3977 | 1.3977 | 1.3977 | 1.3977 | 1.3977
2020-03-18 06:00 | Summer | 0.7235 | 1.0354 | 1.4942 | 1.4942 | 1.4942 | 1.4942 | 0.76019 | 1.5035 | 1.5035 | 1.5035 | 1.5035 | 1.5035 | 1.9309 | 2.4918 | 2.8592 | 3.0527 | 3.4395 | 3.8263 | 0.73924 | 1.459 | 1.7508 | 1.7508 | 1.7508 | 1.7508 | 1.4966 | 1.7409 | 1.7409 | 1.7409 | 1.7409 | 1.7409
2020-03-18 07:00 | Summer | 1.2607 | 1.8042 | 2.6036 | 2.6036 | 2.6036 | 2.6036 | 0.89737 | 1.7748 | 1.7748 | 1.7748 | 1.7748 | 1.7748 | 2.4197 | 3.1225 | 3.583 | 3.8254 | 4.3101 | 4.7949 | 1.0708 | 2.1133 | 2.536 | 2.536 | 2.536 | 2.536 | 1.8257 | 2.1238 | 2.1238 | 2.1238 | 2.1238 | 2.1238
2020-03-18 08:00 | Summer | 1.5688 | 2.2453 | 3.24 | 3.24 | 3.24 | 3.24 | 0.9088 | 1.7974 | 1.7974 | 1.7974 | 1.7974 | 1.7974 | 2.5149 | 3.2455 | 3.7241 | 3.976 | 4.4798 | 4.9836 | 1.105 | 2.181 | 2.6172 | 2.6172 | 2.6172 | 2.6172 | 2.172 | 2.5266 | 2.5266 | 2.5266 | 2.5266 | 2.5266
2020-03-18 09:00 | Summer | 1.6957 | 2.4268 | 3.5019 | 3.5019 | 3.5019 | 3.5019 | 0.93738 | 1.8539 | 1.8539 | 1.8539 | 1.8539 | 1.8539 | 2.5911 | 3.3438 | 3.8369 | 4.0965 | 4.6156 | 5.1347 | 1.105 | 2.181 | 2.6172 | 2.6172 | 2.6172 | 2.6172 | 2.2291 | 2.5931 | 2.5931 | 2.5931 | 2.5931 | 2.5931
2020-03-18 10:00 | Summer | 1.7338 | 2.4813 | 3.5806 | 3.5806 | 3.5806 | 3.5806 | 0.92881 | 1.837 | 1.837 | 1.837 | 1.837 | 1.837 | 2.915 | 3.7618 | 4.3166 | 4.6086 | 5.1925 | 5.7765 | 1.1241 | 2.2186 | 2.6623 | 2.6623 | 2.6623 | 2.6623 | 2.3571 | 2.742 | 2.742 | 2.742 | 2.742 | 2.742
2020-03-18 11:00 | Summer | 1.6957 | 2.4268 | 3.5019 | 3.5019 | 3.5019 | 3.5019 | 0.93452 | 1.8483 | 1.8483 | 1.8483 | 1.8483 | 1.8483 | 2.9531 | 3.811 | 4.373 | 4.6688 | 5.2604 | 5.852 | 1.1927 | 2.354 | 2.8248 | 2.8248 | 2.8248 | 2.8248 | 2.4959 | 2.9034 | 2.9034 | 2.9034 | 2.9034 | 2.9034
2020-03-18 12:00 | Summer | 1.7571 | 2.5148 | 3.6289 | 3.6289 | 3.6289 | 3.6289 | 1.0288 | 2.0348 | 2.0348 | 2.0348 | 2.0348 | 2.0348 | 2.9722 | 3.8356 | 4.4012 | 4.6989 | 5.2943 | 5.8898 | 1.1698 | 2.3089 | 2.7706 | 2.7706 | 2.7706 | 2.7706 | 2.5149 | 2.9255 | 2.9255 | 2.9255 | 2.9255 | 2.9255
2020-03-18 13:00 | Summer | 1.81 | 2.5904 | 3.738 | 3.738 | 3.738 | 3.738 | 1.1117 | 2.1987 | 2.1987 | 2.1987 | 2.1987 | 2.1987 | 3.0484 | 3.9339 | 4.5141 | 4.8194 | 5.4301 | 6.0408 | 1.0441 | 2.0607 | 2.4728 | 2.4728 | 2.4728 | 2.4728 | 2.4387 | 2.8369 | 2.8369 | 2.8369 | 2.8369 | 2.8369
2020-03-18 14:00 | Summer | 1.81 | 2.5904 | 3.738 | 3.738 | 3.738 | 3.738 | 1.0974 | 2.1704 | 2.1704 | 2.1704 | 2.1704 | 2.1704 | 3.1627 | 4.0814 | 4.6833 | 5.0001 | 5.6337 | 6.2673 | 1.0708 | 2.1133 | 2.536 | 2.536 | 2.536 | 2.536 | 2.4768 | 2.8812 | 2.8812 | 2.8812 | 2.8812 | 2.8812
2020-03-18 15:00 | Summer | 1.6957 | 2.4268 | 3.5019 | 3.5019 | 3.5019 | 3.5019 | 1.166 | 2.3061 | 2.3061 | 2.3061 | 2.3061 | 2.3061 | 3.0294 | 3.9093 | 4.4858 | 4.7893 | 5.3962 | 6.003 | 1.006 | 1.9855 | 2.3826 | 2.3826 | 2.3826 | 2.3826 | 2.4387 | 2.8369 | 2.8369 | 2.8369 | 2.8369 | 2.8369
2020-03-18 16:00 | Summer | 1.6576 | 2.3723 | 3.4232 | 3.4232 | 3.4232 | 3.4232 | 1.2032 | 2.3796 | 2.3796 | 2.3796 | 2.3796 | 2.3796 | 3.1056 | 4.0077 | 4.5987 | 4.9098 | 5.5319 | 6.154 | 1.0326 | 2.0381 | 2.4457 | 2.4457 | 2.4457 | 2.4457 | 2.5911 | 3.0142 | 3.0142 | 3.0142 | 3.0142 | 3.0142
2020-03-18 17:00 | Summer | 1.5814 | 2.2632 | 3.2659 | 3.2659 | 3.2659 | 3.2659 | 1.1603 | 2.2948 | 2.2948 | 2.2948 | 2.2948 | 2.2948 | 2.9531 | 3.811 | 4.373 | 4.6688 | 5.2604 | 5.852 | 1.006 | 1.9855 | 2.3826 | 2.3826 | 2.3826 | 2.3826 | 2.4527 | 2.8532 | 2.8532 | 2.8532 | 2.8532 | 2.8532
2020-03-18 18:00 | Summer | 1.1497 | 1.6454 | 2.3744 | 2.3744 | 2.3744 | 2.3744 | 0.99232 | 1.9626 | 1.9626 | 1.9626 | 1.9626 | 1.9626 | 2.8398 | 3.6647 | 4.2051 | 4.4896 | 5.0585 | 5.6274 | 1.0326 | 2.0381 | 2.4457 | 2.4457 | 2.4457 | 2.4457 | 1.9043 | 2.2152 | 2.2152 | 2.2152 | 2.2152 | 2.2152
2020-03-18 19:00 | Summer | 0.81926 | 1.1725 | 1.692 | 1.692 | 1.692 | 1.692 | 0.6378 | 1.2614 | 1.2614 | 1.2614 | 1.2614 | 1.2614 | 2.5541 | 3.2961 | 3.7821 | 4.038 | 4.5496 | 5.0613 | 0.97168 | 1.9178 | 2.3013 | 2.3013 | 2.3013 | 2.3013 | 1.2575 | 1.4628 | 1.4628 | 1.4628 | 1.4628 | 1.4628
2020-03-18 20:00 | Summer | 0.74305 | 1.0634 | 1.5346 | 1.5346 | 1.5346 | 1.5346 | 0.50298 | 0.99478 | 0.99478 | 0.99478 | 0.99478 | 0.99478 | 2.3244 | 2.9996 | 3.442 | 3.6748 | 4.1404 | 4.6061 | 0.92214 | 1.82 | 2.184 | 2.184 | 2.184 | 2.184 | 1.2194 | 1.4184 | 1.4184 | 1.4184 | 1.4184 | 1.4184
2020-03-18 21:00 | Summer | 0.66 | 0.94456 | 1.363 | 1.363 | 1.363 | 1.363 | 0.41725 | 0.82521 | 0.82521 | 0.82521 | 0.82521 | 0.82521 | 2.1529 | 2.7783 | 3.1881 | 3.4037 | 3.835 | 4.2663 | 0.91071 | 1.7975 | 2.1569 | 2.1569 | 2.1569 | 2.1569 | 1.105 | 1.2855 | 1.2855 | 1.2855 | 1.2855 | 1.2855
2020-03-18 22:00 | Summer | 0.61579 | 0.88129 | 1.2717 | 1.2717 | 1.2717 | 1.2717 | 0.42011 | 0.83086 | 0.83086 | 0.83086 | 0.83086 | 0.83086 | 2.0005 | 2.5816 | 2.9624 | 3.1627 | 3.5635 | 3.9643 | 0.83831 | 1.6546 | 1.9855 | 1.9855 | 1.9855 | 1.9855 | 1.0098 | 1.1746 | 1.1746 | 1.1746 | 1.1746 | 1.1746
2020-03-18 23:00 | Summer | 0.64779 | 0.92709 | 1.3378 | 1.3378 | 1.3378 | 1.3378 | 0.41439 | 0.81956 | 0.81956 | 0.81956 | 0.81956 | 0.81956 | 1.9434 | 2.5079 | 2.8777 | 3.0724 | 3.4617 | 3.851 | 0.86498 | 1.7072 | 2.0486 | 2.0486 | 2.0486 | 2.0486 | 0.97192 | 1.1306 | 1.1306 | 1.1306 | 1.1306 | 1.1306
2020-03-19 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.40867 | 0.80825 | 0.80825 | 0.80825 | 0.80825 | 0.80825 | 1.7719 | 2.2866 | 2.6238 | 2.8013 | 3.1562 | 3.5112 | 0.59444 | 1.1732 | 1.4079 | 1.4079 | 1.4079 | 1.4079 | 0.93358 | 1.086 | 1.086 | 1.086 | 1.086 | 1.086
2020-03-19 01:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.40296 | 0.79695 | 0.79695 | 0.79695 | 0.79695 | 0.79695 | 1.7147 | 2.2128 | 2.5392 | 2.7109 | 3.0544 | 3.3979 | 0.58682 | 1.1582 | 1.3898 | 1.3898 | 1.3898 | 1.3898 | 0.89547 | 1.0417 | 1.0417 | 1.0417 | 1.0417 | 1.0417
2020-03-19 02:00 | Summer | 0.59086 | 0.84562 | 1.2203 | 1.2203 | 1.2203 | 1.2203 | 0.43439 | 0.85912 | 0.85912 | 0.85912 | 0.85912 | 0.85912 | 1.7338 | 2.2374 | 2.5674 | 2.741 | 3.0884 | 3.4357 | 0.57157 | 1.1281 | 1.3537 | 1.3537 | 1.3537 | 1.3537 | 0.85737 | 0.99734 | 0.99734 | 0.99734 | 0.99734 | 0.99734
2020-03-19 03:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.48869 | 0.96652 | 0.96652 | 0.96652 | 0.96652 | 0.96652 | 1.6957 | 2.1882 | 2.5109 | 2.6808 | 3.0205 | 3.3602 | 0.57157 | 1.1281 | 1.3537 | 1.3537 | 1.3537 | 1.3537 | 0.83831 | 0.97518 | 0.97518 | 0.97518 | 0.97518 | 0.97518
2020-03-19 04:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.41153 | 0.81391 | 0.81391 | 0.81391 | 0.81391 | 0.81391 | 1.6957 | 2.1882 | 2.5109 | 2.6808 | 3.0205 | 3.3602 | 0.56776 | 1.1206 | 1.3447 | 1.3447 | 1.3447 | 1.3447 | 0.89547 | 1.0417 | 1.0417 | 1.0417 | 1.0417 | 1.0417
2020-03-19 05:00 | Summer | 0.74305 | 1.0634 | 1.5346 | 1.5346 | 1.5346 | 1.5346 | 0.44297 | 0.87608 | 0.87608 | 0.87608 | 0.87608 | 0.87608 | 1.7623 | 2.2742 | 2.6096 | 2.7861 | 3.1391 | 3.4922 | 0.79412 | 1.5674 | 1.8808 | 1.8808 | 1.8808 | 1.8808 | 1.122 | 1.3052 | 1.3052 | 1.3052 | 1.3052 | 1.3052
2020-03-19 06:00 | Summer | 0.83831 | 1.1998 | 1.7313 | 1.7313 | 1.7313 | 1.7313 | 0.75734 | 1.4978 | 1.4978 | 1.4978 | 1.4978 | 1.4978 | 1.9424 | 2.5066 | 2.8763 | 3.0708 | 3.4599 | 3.8491 | 0.81545 | 1.6094 | 1.9313 | 1.9313 | 1.9313 | 1.9313 | 1.3683 | 1.5917 | 1.5917 | 1.5917 | 1.5917 | 1.5917
2020-03-19 07:00 | Summer | 1.0479 | 1.4997 | 2.1641 | 2.1641 | 2.1641 | 2.1641 | 0.82021 | 1.6222 | 1.6222 | 1.6222 | 1.6222 | 1.6222 | 2.3739 | 3.0634 | 3.5152 | 3.753 | 4.2285 | 4.7041 | 1.1241 | 2.2186 | 2.6623 | 2.6623 | 2.6623 | 2.6623 | 1.7435 | 2.0282 | 2.0282 | 2.0282 | 2.0282 | 2.0282
2020-03-19 08:00 | Summer | 1.5433 | 2.2086 | 3.1872 | 3.1872 | 3.1872 | 3.1872 | 0.89451 | 1.7691 | 1.7691 | 1.7691 | 1.7691 | 1.7691 | 2.5942 | 3.3477 | 3.8414 | 4.1013 | 4.6209 | 5.1406 | 1.0936 | 2.1585 | 2.5901 | 2.5901 | 2.5901 | 2.5901 | 2.1529 | 2.5044 | 2.5044 | 2.5044 | 2.5044 | 2.5044
2020-03-19 09:00 | Summer | 1.6385 | 2.345 | 3.3839 | 3.3839 | 3.3839 | 3.3839 | 0.90023 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 2.7817 | 3.5897 | 4.1191 | 4.3977 | 4.955 | 5.5122 | 1.1508 | 2.2713 | 2.7255 | 2.7255 | 2.7255 | 2.7255 | 2.4006 | 2.7926 | 2.7926 | 2.7926 | 2.7926 | 2.7926
2020-03-19 10:00 | Summer | 1.6957 | 2.4268 | 3.5019 | 3.5019 | 3.5019 | 3.5019 | 1.0145 | 2.0065 | 2.0065 | 2.0065 | 2.0065 | 2.0065 | 2.915 | 3.7618 | 4.3166 | 4.6086 | 5.1925 | 5.7765 | 1.1813 | 2.3314 | 2.7977 | 2.7977 | 2.7977 | 2.7977 | 2.534 | 2.9477 | 2.9477 | 2.9477 | 2.9477 | 2.9477
2020-03-19 11:00 | Summer | 1.8481 | 2.6449 | 3.8167 | 3.8167 | 3.8167 | 3.8167 | 1.1089 | 2.193 | 2.193 | 2.193 | 2.193 | 2.193 | 3.0484 | 3.9339 | 4.5141 | 4.8194 | 5.4301 | 6.0408 | 1.3222 | 2.6097 | 3.1316 | 3.1316 | 3.1316 | 3.1316 | 2.7055 | 3.1472 | 3.1472 | 3.1472 | 3.1472 | 3.1472
2020-03-19 12:00 | Summer | 1.8481 | 2.6449 | 3.8167 | 3.8167 | 3.8167 | 3.8167 | 1.0803 | 2.1365 | 2.1365 | 2.1365 | 2.1365 | 2.1365 | 3.0675 | 3.9585 | 4.5423 | 4.8495 | 5.464 | 6.0785 | 1.288 | 2.542 | 3.0504 | 3.0504 | 3.0504 | 3.0504 | 2.6483 | 3.0807 | 3.0807 | 3.0807 | 3.0807 | 3.0807
2020-03-19 13:00 | Summer | 1.7909 | 2.5631 | 3.6987 | 3.6987 | 3.6987 | 3.6987 | 1.2032 | 2.3796 | 2.3796 | 2.3796 | 2.3796 | 2.3796 | 3.277 | 4.2289 | 4.8526 | 5.1809 | 5.8373 | 6.4938 | 1.2651 | 2.4969 | 2.9963 | 2.9963 | 2.9963 | 2.9963 | 2.7817 | 3.2358 | 3.2358 | 3.2358 | 3.2358 | 3.2358
2020-03-19 14:00 | Summer | 1.81 | 2.5904 | 3.738 | 3.738 | 3.738 | 3.738 | 1.2975 | 2.5661 | 2.5661 | 2.5661 | 2.5661 | 2.5661 | 3.277 | 4.2289 | 4.8526 | 5.1809 | 5.8373 | 6.4938 | 1.2956 | 2.5571 | 3.0685 | 3.0685 | 3.0685 | 3.0685 | 2.7245 | 3.1693 | 3.1693 | 3.1693 | 3.1693 | 3.1693
2020-03-19 15:00 | Summer | 1.7719 | 2.5359 | 3.6593 | 3.6593 | 3.6593 | 3.6593 | 1.2137 | 2.4004 | 2.4004 | 2.4004 | 2.4004 | 2.4004 | 3.277 | 4.2289 | 4.8526 | 5.1809 | 5.8373 | 6.4938 | 1.3222 | 2.6097 | 3.1316 | 3.1316 | 3.1316 | 3.1316 | 2.7626 | 3.2137 | 3.2137 | 3.2137 | 3.2137 | 3.2137
2020-03-19 16:00 | Summer | 1.7909 | 2.5631 | 3.6987 | 3.6987 | 3.6987 | 3.6987 | 1.3118 | 2.5943 | 2.5943 | 2.5943 | 2.5943 | 2.5943 | 3.277 | 4.2289 | 4.8526 | 5.1809 | 5.8373 | 6.4938 | 1.3032 | 2.5721 | 3.0865 | 3.0865 | 3.0865 | 3.0865 | 2.7626 | 3.2137 | 3.2137 | 3.2137 | 3.2137 | 3.2137
2020-03-19 17:00 | Summer | 1.7147 | 2.4541 | 3.5413 | 3.5413 | 3.5413 | 3.5413 | 1.2975 | 2.5661 | 2.5661 | 2.5661 | 2.5661 | 2.5661 | 3.277 | 4.2289 | 4.8526 | 5.1809 | 5.8373 | 6.4938 | 1.2613 | 2.4894 | 2.9872 | 2.9872 | 2.9872 | 2.9872 | 2.6674 | 3.1028 | 3.1028 | 3.1028 | 3.1028 | 3.1028
2020-03-19 18:00 | Summer | 1.2301 | 1.7605 | 2.5405 | 2.5405 | 2.5405 | 2.5405 | 0.99168 | 1.9613 | 1.9613 | 1.9613 | 1.9613 | 1.9613 | 3.0675 | 3.9585 | 4.5423 | 4.8495 | 5.464 | 6.0785 | 1.0326 | 2.0381 | 2.4457 | 2.4457 | 2.4457 | 2.4457 | 1.915 | 2.2276 | 2.2276 | 2.2276 | 2.2276 | 2.2276
2020-03-19 19:00 | Summer | 0.85737 | 1.227 | 1.7706 | 1.7706 | 1.7706 | 1.7706 | 0.70875 | 1.4017 | 1.4017 | 1.4017 | 1.4017 | 1.4017 | 2.7509 | 3.55 | 4.0735 | 4.3491 | 4.9001 | 5.4512 | 0.99835 | 1.9704 | 2.3645 | 2.3645 | 2.3645 | 2.3645 | 1.2956 | 1.5071 | 1.5071 | 1.5071 | 1.5071 | 1.5071
2020-03-19 20:00 | Summer | 0.74305 | 1.0634 | 1.5346 | 1.5346 | 1.5346 | 1.5346 | 0.57729 | 1.1417 | 1.1417 | 1.1417 | 1.1417 | 1.1417 | 2.4387 | 3.1471 | 3.6112 | 3.8555 | 4.3441 | 4.8326 | 0.99073 | 1.9554 | 2.3465 | 2.3465 | 2.3465 | 2.3465 | 1.2765 | 1.4849 | 1.4849 | 1.4849 | 1.4849 | 1.4849
2020-03-19 21:00 | Summer | 0.66726 | 0.95496 | 1.378 | 1.378 | 1.378 | 1.378 | 0.42582 | 0.84217 | 0.84217 | 0.84217 | 0.84217 | 0.84217 | 2.3054 | 2.975 | 3.4138 | 3.6447 | 4.1065 | 4.5683 | 0.95644 | 1.8877 | 2.2652 | 2.2652 | 2.2652 | 2.2652 | 1.1434 | 1.3301 | 1.3301 | 1.3301 | 1.3301 | 1.3301
2020-03-19 22:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.44297 | 0.87608 | 0.87608 | 0.87608 | 0.87608 | 0.87608 | 2.0546 | 2.6514 | 3.0424 | 3.2482 | 3.6598 | 4.0714 | 0.87261 | 1.7222 | 2.0667 | 2.0667 | 2.0667 | 2.0667 | 1.0288 | 1.1968 | 1.1968 | 1.1968 | 1.1968 | 1.1968
2020-03-19 23:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.46297 | 0.91565 | 0.91565 | 0.91565 | 0.91565 | 0.91565 | 1.9815 | 2.557 | 2.9341 | 3.1326 | 3.5296 | 3.9265 | 0.85736 | 1.6922 | 2.0306 | 2.0306 | 2.0306 | 2.0306 | 0.99073 | 1.1525 | 1.1525 | 1.1525 | 1.1525 | 1.1525
2020-03-20 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.38581 | 0.76304 | 0.76304 | 0.76304 | 0.76304 | 0.76304 | 1.8481 | 2.3849 | 2.7366 | 2.9218 | 3.292 | 3.6622 | 0.62681 | 1.2371 | 1.4846 | 1.4846 | 1.4846 | 1.4846 | 0.97168 | 1.1303 | 1.1303 | 1.1303 | 1.1303 | 1.1303
2020-03-20 01:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.41153 | 0.81391 | 0.81391 | 0.81391 | 0.81391 | 0.81391 | 1.7528 | 2.262 | 2.5956 | 2.7712 | 3.1223 | 3.4734 | 0.74305 | 1.4665 | 1.7599 | 1.7599 | 1.7599 | 1.7599 | 0.97168 | 1.1303 | 1.1303 | 1.1303 | 1.1303 | 1.1303
2020-03-20 02:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.5087 | 1.0061 | 1.0061 | 1.0061 | 1.0061 | 1.0061 | 1.7528 | 2.262 | 2.5956 | 2.7712 | 3.1223 | 3.4734 | 0.7621 | 1.5041 | 1.805 | 1.805 | 1.805 | 1.805 | 0.97168 | 1.1303 | 1.1303 | 1.1303 | 1.1303 | 1.1303
2020-03-20 03:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.42296 | 0.83652 | 0.83652 | 0.83652 | 0.83652 | 0.83652 | 1.7147 | 2.2128 | 2.5392 | 2.7109 | 3.0544 | 3.3979 | 0.6516 | 1.286 | 1.5433 | 1.5433 | 1.5433 | 1.5433 | 0.97168 | 1.1303 | 1.1303 | 1.1303 | 1.1303 | 1.1303
2020-03-20 04:00 | Summer | 0.65546 | 0.93807 | 1.3537 | 1.3537 | 1.3537 | 1.3537 | 0.48487 | 0.95894 | 0.95894 | 0.95894 | 0.95894 | 0.95894 | 1.7338 | 2.2374 | 2.5674 | 2.741 | 3.0884 | 3.4357 | 0.67446 | 1.3312 | 1.5974 | 1.5974 | 1.5974 | 1.5974 | 1.0288 | 1.1968 | 1.1968 | 1.1968 | 1.1968 | 1.1968
2020-03-20 05:00 | Summer | 0.78115 | 1.118 | 1.6133 | 1.6133 | 1.6133 | 1.6133 | 0.54585 | 1.0796 | 1.0796 | 1.0796 | 1.0796 | 1.0796 | 1.829 | 2.3603 | 2.7084 | 2.8916 | 3.2581 | 3.6245 | 0.98692 | 1.9479 | 2.3374 | 2.3374 | 2.3374 | 2.3374 | 1.1432 | 1.3298 | 1.3298 | 1.3298 | 1.3298 | 1.3298
2020-03-20 06:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.87451 | 1.7296 | 1.7296 | 1.7296 | 1.7296 | 1.7296 | 1.9815 | 2.557 | 2.9341 | 3.1326 | 3.5296 | 3.9265 | 0.93738 | 1.8501 | 2.2201 | 2.2201 | 2.2201 | 2.2201 | 1.3978 | 1.626 | 1.626 | 1.626 | 1.626 | 1.626
2020-03-20 07:00 | Summer | 1.1783 | 1.6864 | 2.4335 | 2.4335 | 2.4335 | 2.4335 | 0.93452 | 1.8483 | 1.8483 | 1.8483 | 1.8483 | 1.8483 | 2.4578 | 3.1717 | 3.6395 | 3.8856 | 4.378 | 4.8704 | 1.3413 | 2.6473 | 3.1768 | 3.1768 | 3.1768 | 3.1768 | 1.829 | 2.1277 | 2.1277 | 2.1277 | 2.1277 | 2.1277
2020-03-20 08:00 | Summer | 1.7338 | 2.4813 | 3.5806 | 3.5806 | 3.5806 | 3.5806 | 0.94881 | 1.8765 | 1.8765 | 1.8765 | 1.8765 | 1.8765 | 2.8007 | 3.6143 | 4.1473 | 4.4278 | 4.9889 | 5.55 | 1.2156 | 2.3991 | 2.8789 | 2.8789 | 2.8789 | 2.8789 | 2.3625 | 2.7482 | 2.7482 | 2.7482 | 2.7482 | 2.7482
2020-03-20 09:00 | Summer | 1.9053 | 2.7267 | 3.9348 | 3.9348 | 3.9348 | 3.9348 | 1.0145 | 2.0065 | 2.0065 | 2.0065 | 2.0065 | 2.0065 | 2.9318 | 3.7834 | 4.3414 | 4.6351 | 5.2224 | 5.8097 | 1.227 | 2.4217 | 2.906 | 2.906 | 2.906 | 2.906 | 2.6674 | 3.1028 | 3.1028 | 3.1028 | 3.1028 | 3.1028
2020-03-20 10:00 | Summer | 1.829 | 2.6177 | 3.7774 | 3.7774 | 3.7774 | 3.7774 | 1.1574 | 2.2891 | 2.2891 | 2.2891 | 2.2891 | 2.2891 | 3.277 | 4.2289 | 4.8526 | 5.1809 | 5.8373 | 6.4938 | 1.2308 | 2.4292 | 2.915 | 2.915 | 2.915 | 2.915 | 2.7626 | 3.2137 | 3.2137 | 3.2137 | 3.2137 | 3.2137
2020-03-20 11:00 | Summer | 1.8862 | 2.6995 | 3.8954 | 3.8954 | 3.8954 | 3.8954 | 1.1489 | 2.2722 | 2.2722 | 2.2722 | 2.2722 | 2.2722 | 3.2002 | 4.1298 | 4.7388 | 5.0594 | 5.7005 | 6.3416 | 1.307 | 2.5796 | 3.0955 | 3.0955 | 3.0955 | 3.0955 | 2.7817 | 3.2358 | 3.2358 | 3.2358 | 3.2358 | 3.2358
2020-03-20 12:00 | Summer | 1.8672 | 2.6722 | 3.8561 | 3.8561 | 3.8561 | 3.8561 | 1.3432 | 2.6565 | 2.6565 | 2.6565 | 2.6565 | 2.6565 | 3.277 | 4.2289 | 4.8526 | 5.1809 | 5.8373 | 6.4938 | 1.3032 | 2.5721 | 3.0865 | 3.0865 | 3.0865 | 3.0865 | 2.7817 | 3.2358 | 3.2358 | 3.2358 | 3.2358 | 3.2358
2020-03-20 13:00 | Summer | 1.8672 | 2.6722 | 3.8561 | 3.8561 | 3.8561 | 3.8561 | 1.3632 | 2.6961 | 2.6961 | 2.6961 | 2.6961 | 2.6961 | 3.277 | 4.2289 | 4.8526 | 5.1809 | 5.8373 | 6.4938 | 1.2956 | 2.5571 | 3.0685 | 3.0685 | 3.0685 | 3.0685 | 2.8007 | 3.258 | 3.258 | 3.258 | 3.258 | 3.258
2020-03-20 14:00 | Summer | 1.7909 | 2.5631 | 3.6987 | 3.6987 | 3.6987 | 3.6987 | 1.3775 | 2.7243 | 2.7243 | 2.7243 | 2.7243 | 2.7243 | 3.277 | 4.2289 | 4.8526 | 5.1809 | 5.8373 | 6.4938 | 1.2384 | 2.4442 | 2.9331 | 2.9331 | 2.9331 | 2.9331 | 2.8579 | 3.3245 | 3.3245 | 3.3245 | 3.3245 | 3.3245
2020-03-20 15:00 | Summer | 1.7719 | 2.5359 | 3.6593 | 3.6593 | 3.6593 | 3.6593 | 1.3489 | 2.6678 | 2.6678 | 2.6678 | 2.6678 | 2.6678 | 3.277 | 4.2289 | 4.8526 | 5.1809 | 5.8373 | 6.4938 | 1.2803 | 2.527 | 3.0324 | 3.0324 | 3.0324 | 3.0324 | 2.7436 | 3.1915 | 3.1915 | 3.1915 | 3.1915 | 3.1915
2020-03-20 16:00 | Summer | 1.6957 | 2.4268 | 3.5019 | 3.5019 | 3.5019 | 3.5019 | 1.2375 | 2.4474 | 2.4474 | 2.4474 | 2.4474 | 2.4474 | 3.1627 | 4.0814 | 4.6833 | 5.0001 | 5.6337 | 6.2673 | 1.2498 | 2.4668 | 2.9602 | 2.9602 | 2.9602 | 2.9602 | 2.6674 | 3.1028 | 3.1028 | 3.1028 | 3.1028 | 3.1028
2020-03-20 17:00 | Summer | 1.6004 | 2.2904 | 3.3052 | 3.3052 | 3.3052 | 3.3052 | 1.266 | 2.5039 | 2.5039 | 2.5039 | 2.5039 | 2.5039 | 3.0675 | 3.9585 | 4.5423 | 4.8495 | 5.464 | 6.0785 | 1.166 | 2.3013 | 2.7616 | 2.7616 | 2.7616 | 2.7616 | 2.534 | 2.9477 | 2.9477 | 2.9477 | 2.9477 | 2.9477
2020-03-20 18:00 | Summer | 1.2949 | 1.8533 | 2.6743 | 2.6743 | 2.6743 | 2.6743 | 0.8625 | 1.7058 | 1.7058 | 1.7058 | 1.7058 | 1.7058 | 2.915 | 3.7618 | 4.3166 | 4.6086 | 5.1925 | 5.7765 | 0.94119 | 1.8576 | 2.2291 | 2.2291 | 2.2291 | 2.2291 | 1.8782 | 2.1848 | 2.1848 | 2.1848 | 2.1848 | 2.1848
2020-03-20 19:00 | Summer | 0.724 | 1.0362 | 1.4952 | 1.4952 | 1.4952 | 1.4952 | 0.59158 | 1.17 | 1.17 | 1.17 | 1.17 | 1.17 | 2.4537 | 3.1665 | 3.6335 | 3.8792 | 4.3708 | 4.8623 | 0.92595 | 1.8275 | 2.193 | 2.193 | 2.193 | 2.193 | 1.2765 | 1.4849 | 1.4849 | 1.4849 | 1.4849 | 1.4849
2020-03-20 20:00 | Summer | 0.66684 | 0.95435 | 1.3772 | 1.3772 | 1.3772 | 1.3772 | 0.49727 | 0.98347 | 0.98347 | 0.98347 | 0.98347 | 0.98347 | 2.1529 | 2.7783 | 3.1881 | 3.4037 | 3.835 | 4.2663 | 0.93738 | 1.8501 | 2.2201 | 2.2201 | 2.2201 | 2.2201 | 1.2384 | 1.4406 | 1.4406 | 1.4406 | 1.4406 | 1.4406
2020-03-20 21:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.43439 | 0.85912 | 0.85912 | 0.85912 | 0.85912 | 0.85912 | 2.1339 | 2.7537 | 3.1598 | 3.3736 | 3.8011 | 4.2285 | 0.85736 | 1.6922 | 2.0306 | 2.0306 | 2.0306 | 2.0306 | 1.086 | 1.2633 | 1.2633 | 1.2633 | 1.2633 | 1.2633
2020-03-20 22:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.45726 | 0.90434 | 0.90434 | 0.90434 | 0.90434 | 0.90434 | 2.0005 | 2.5816 | 2.9624 | 3.1627 | 3.5635 | 3.9643 | 0.85355 | 1.6846 | 2.0216 | 2.0216 | 2.0216 | 2.0216 | 0.95263 | 1.1082 | 1.1082 | 1.1082 | 1.1082 | 1.1082
2020-03-20 23:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.41439 | 0.81956 | 0.81956 | 0.81956 | 0.81956 | 0.81956 | 1.8862 | 2.4341 | 2.7931 | 2.982 | 3.3599 | 3.7377 | 0.64779 | 1.2785 | 1.5342 | 1.5342 | 1.5342 | 1.5342 | 1.0288 | 1.1968 | 1.1968 | 1.1968 | 1.1968 | 1.1968
2020-03-21 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.40582 | 0.8026 | 0.8026 | 0.8026 | 0.8026 | 0.8026 | 1.7909 | 2.3112 | 2.652 | 2.8314 | 3.1902 | 3.549 | 0.59063 | 1.1657 | 1.3989 | 1.3989 | 1.3989 | 1.3989 | 0.95263 | 1.1082 | 1.1082 | 1.1082 | 1.1082 | 1.1082
2020-03-21 01:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.4001 | 0.7913 | 0.7913 | 0.7913 | 0.7913 | 0.7913 | 1.7528 | 2.262 | 2.5956 | 2.7712 | 3.1223 | 3.4734 | 0.56395 | 1.1131 | 1.3357 | 1.3357 | 1.3357 | 1.3357 | 0.93358 | 1.086 | 1.086 | 1.086 | 1.086 | 1.086
2020-03-21 02:00 | Summer | 0.57182 | 0.81836 | 1.1809 | 1.1809 | 1.1809 | 1.1809 | 0.35437 | 0.70086 | 0.70086 | 0.70086 | 0.70086 | 0.70086 | 1.6576 | 2.1391 | 2.4545 | 2.6205 | 2.9526 | 3.2847 | 0.53347 | 1.0529 | 1.2635 | 1.2635 | 1.2635 | 1.2635 | 0.87642 | 1.0195 | 1.0195 | 1.0195 | 1.0195 | 1.0195
2020-03-21 03:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.36295 | 0.71782 | 0.71782 | 0.71782 | 0.71782 | 0.71782 | 1.6576 | 2.1391 | 2.4545 | 2.6205 | 2.9526 | 3.2847 | 0.57539 | 1.1356 | 1.3628 | 1.3628 | 1.3628 | 1.3628 | 0.85727 | 0.99724 | 0.99724 | 0.99724 | 0.99724 | 0.99724
2020-03-21 04:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.46012 | 0.90999 | 0.90999 | 0.90999 | 0.90999 | 0.90999 | 1.6195 | 2.0899 | 2.3981 | 2.5603 | 2.8847 | 3.2092 | 0.54109 | 1.0679 | 1.2815 | 1.2815 | 1.2815 | 1.2815 | 0.85737 | 0.99734 | 0.99734 | 0.99734 | 0.99734 | 0.99734
2020-03-21 05:00 | Summer | 0.56465 | 0.8081 | 1.1661 | 1.1661 | 1.1661 | 1.1661 | 0.44297 | 0.87608 | 0.87608 | 0.87608 | 0.87608 | 0.87608 | 1.7338 | 2.2374 | 2.5674 | 2.741 | 3.0884 | 3.4357 | 0.71637 | 1.4139 | 1.6967 | 1.6967 | 1.6967 | 1.6967 | 0.86606 | 1.0075 | 1.0075 | 1.0075 | 1.0075 | 1.0075
2020-03-21 06:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.44868 | 0.88738 | 0.88738 | 0.88738 | 0.88738 | 0.88738 | 1.7719 | 2.2866 | 2.6238 | 2.8013 | 3.1562 | 3.5112 | 0.79258 | 1.5643 | 1.8772 | 1.8772 | 1.8772 | 1.8772 | 0.95686 | 1.1131 | 1.1131 | 1.1131 | 1.1131 | 1.1131
2020-03-21 07:00 | Summer | 0.59755 | 0.8552 | 1.2341 | 1.2341 | 1.2341 | 1.2341 | 0.53442 | 1.057 | 1.057 | 1.057 | 1.057 | 1.057 | 1.9053 | 2.4587 | 2.8213 | 3.0121 | 3.3938 | 3.7755 | 0.6173 | 1.2184 | 1.462 | 1.462 | 1.462 | 1.462 | 1.0479 | 1.219 | 1.219 | 1.219 | 1.219 | 1.219
2020-03-21 08:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.51727 | 1.023 | 1.023 | 1.023 | 1.023 | 1.023 | 2.003 | 2.5848 | 2.966 | 3.1666 | 3.5679 | 3.9691 | 0.82688 | 1.632 | 1.9584 | 1.9584 | 1.9584 | 1.9584 | 1.0288 | 1.1968 | 1.1968 | 1.1968 | 1.1968 | 1.1968
2020-03-21 09:00 | Summer | 0.60251 | 0.86228 | 1.2443 | 1.2443 | 1.2443 | 1.2443 | 0.52299 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 2.172 | 2.8029 | 3.2163 | 3.4338 | 3.8689 | 4.3041 | 0.94882 | 1.8727 | 2.2472 | 2.2472 | 2.2472 | 2.2472 | 1.105 | 1.2855 | 1.2855 | 1.2855 | 1.2855 | 1.2855
2020-03-21 10:00 | Summer | 0.6193 | 0.88632 | 1.279 | 1.279 | 1.279 | 1.279 | 0.5087 | 1.0061 | 1.0061 | 1.0061 | 1.0061 | 1.0061 | 2.2101 | 2.8521 | 3.2727 | 3.4941 | 3.9368 | 4.3796 | 0.93738 | 1.8501 | 2.2201 | 2.2201 | 2.2201 | 2.2201 | 1.1432 | 1.3298 | 1.3298 | 1.3298 | 1.3298 | 1.3298
2020-03-21 11:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.5287 | 1.0456 | 1.0456 | 1.0456 | 1.0456 | 1.0456 | 2.2673 | 2.9258 | 3.3573 | 3.5844 | 4.0386 | 4.4928 | 0.92976 | 1.8351 | 2.2021 | 2.2021 | 2.2021 | 2.2021 | 1.1622 | 1.352 | 1.352 | 1.352 | 1.352 | 1.352
2020-03-21 12:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.51442 | 1.0174 | 1.0174 | 1.0174 | 1.0174 | 1.0174 | 2.302 | 2.9706 | 3.4087 | 3.6393 | 4.1005 | 4.5616 | 0.88023 | 1.7373 | 2.0847 | 2.0847 | 2.0847 | 2.0847 | 1.2194 | 1.4184 | 1.4184 | 1.4184 | 1.4184 | 1.4184
2020-03-21 13:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.56586 | 1.1191 | 1.1191 | 1.1191 | 1.1191 | 1.1191 | 2.3244 | 2.9996 | 3.442 | 3.6748 | 4.1404 | 4.6061 | 0.79258 | 1.5643 | 1.8772 | 1.8772 | 1.8772 | 1.8772 | 1.1622 | 1.352 | 1.352 | 1.352 | 1.352 | 1.352
2020-03-21 14:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.54585 | 1.0796 | 1.0796 | 1.0796 | 1.0796 | 1.0796 | 2.4006 | 3.098 | 3.5548 | 3.7953 | 4.2762 | 4.7571 | 0.92976 | 1.8351 | 2.2021 | 2.2021 | 2.2021 | 2.2021 | 1.1432 | 1.3298 | 1.3298 | 1.3298 | 1.3298 | 1.3298
2020-03-21 15:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.53442 | 1.057 | 1.057 | 1.057 | 1.057 | 1.057 | 2.4959 | 3.2209 | 3.6959 | 3.9459 | 4.4459 | 4.9459 | 0.92214 | 1.82 | 2.184 | 2.184 | 2.184 | 2.184 | 1.0479 | 1.219 | 1.219 | 1.219 | 1.219 | 1.219
2020-03-21 16:00 | Summer | 0.60632 | 0.86774 | 1.2522 | 1.2522 | 1.2522 | 1.2522 | 0.52013 | 1.0287 | 1.0287 | 1.0287 | 1.0287 | 1.0287 | 2.4699 | 3.1874 | 3.6574 | 3.9048 | 4.3996 | 4.8944 | 0.89928 | 1.7749 | 2.1299 | 2.1299 | 2.1299 | 2.1299 | 1.0668 | 1.2409 | 1.2409 | 1.2409 | 1.2409 | 1.2409
2020-03-21 17:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.563 | 1.1135 | 1.1135 | 1.1135 | 1.1135 | 1.1135 | 2.4398 | 3.1485 | 3.6128 | 3.8572 | 4.346 | 4.8348 | 0.99454 | 1.9629 | 2.3555 | 2.3555 | 2.3555 | 2.3555 | 1.0669 | 1.2411 | 1.2411 | 1.2411 | 1.2411 | 1.2411
2020-03-21 18:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.43439 | 0.85912 | 0.85912 | 0.85912 | 0.85912 | 0.85912 | 2.4578 | 3.1717 | 3.6395 | 3.8856 | 4.378 | 4.8704 | 0.94119 | 1.8576 | 2.2291 | 2.2291 | 2.2291 | 2.2291 | 1.0486 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 1.2198
2020-03-21 19:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.45154 | 0.89304 | 0.89304 | 0.89304 | 0.89304 | 0.89304 | 2.3625 | 3.0488 | 3.4984 | 3.735 | 4.2083 | 4.6816 | 0.93357 | 1.8426 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 1.0479 | 1.219 | 1.219 | 1.219 | 1.219 | 1.219
2020-03-21 20:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.44297 | 0.87608 | 0.87608 | 0.87608 | 0.87608 | 0.87608 | 2.3054 | 2.975 | 3.4138 | 3.6447 | 4.1065 | 4.5683 | 1.0022 | 1.978 | 2.3735 | 2.3735 | 2.3735 | 2.3735 | 1.0098 | 1.1746 | 1.1746 | 1.1746 | 1.1746 | 1.1746
2020-03-21 21:00 | Summer | 0.5918 | 0.84696 | 1.2222 | 1.2222 | 1.2222 | 1.2222 | 0.34008 | 0.6726 | 0.6726 | 0.6726 | 0.6726 | 0.6726 | 2.191 | 2.8275 | 3.2445 | 3.4639 | 3.9029 | 4.3418 | 0.91452 | 1.805 | 2.166 | 2.166 | 2.166 | 2.166 | 0.99073 | 1.1525 | 1.1525 | 1.1525 | 1.1525 | 1.1525
2020-03-21 22:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.34294 | 0.67825 | 0.67825 | 0.67825 | 0.67825 | 0.67825 | 2.1339 | 2.7537 | 3.1598 | 3.3736 | 3.8011 | 4.2285 | 0.81164 | 1.6019 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 0.93358 | 1.086 | 1.086 | 1.086 | 1.086 | 1.086
2020-03-21 23:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.3458 | 0.68391 | 0.68391 | 0.68391 | 0.68391 | 0.68391 | 1.9624 | 2.5325 | 2.9059 | 3.1025 | 3.4956 | 3.8887 | 0.6516 | 1.286 | 1.5433 | 1.5433 | 1.5433 | 1.5433 | 0.93358 | 1.086 | 1.086 | 1.086 | 1.086 | 1.086
2020-03-22 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.33151 | 0.65565 | 0.65565 | 0.65565 | 0.65565 | 0.65565 | 1.8672 | 2.4095 | 2.7649 | 2.9519 | 3.3259 | 3.7 | 0.56776 | 1.1206 | 1.3447 | 1.3447 | 1.3447 | 1.3447 | 0.87642 | 1.0195 | 1.0195 | 1.0195 | 1.0195 | 1.0195
2020-03-22 01:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.39724 | 0.78565 | 0.78565 | 0.78565 | 0.78565 | 0.78565 | 1.7163 | 2.2148 | 2.5415 | 2.7134 | 3.0572 | 3.401 | 0.56014 | 1.1055 | 1.3267 | 1.3267 | 1.3267 | 1.3267 | 0.87642 | 1.0195 | 1.0195 | 1.0195 | 1.0195 | 1.0195
2020-03-22 02:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.34008 | 0.6726 | 0.6726 | 0.6726 | 0.6726 | 0.6726 | 1.7338 | 2.2374 | 2.5674 | 2.741 | 3.0884 | 3.4357 | 0.56395 | 1.1131 | 1.3357 | 1.3357 | 1.3357 | 1.3357 | 0.87642 | 1.0195 | 1.0195 | 1.0195 | 1.0195 | 1.0195
2020-03-22 03:00 | Summer | 0.57328 | 0.82045 | 1.1839 | 1.1839 | 1.1839 | 1.1839 | 0.4001 | 0.7913 | 0.7913 | 0.7913 | 0.7913 | 0.7913 | 1.6385 | 2.1145 | 2.4263 | 2.5904 | 2.9187 | 3.2469 | 0.56776 | 1.1206 | 1.3447 | 1.3447 | 1.3447 | 1.3447 | 0.85737 | 0.99734 | 0.99734 | 0.99734 | 0.99734 | 0.99734
2020-03-22 04:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.38581 | 0.76304 | 0.76304 | 0.76304 | 0.76304 | 0.76304 | 1.6957 | 2.1882 | 2.5109 | 2.6808 | 3.0205 | 3.3602 | 0.55633 | 1.098 | 1.3176 | 1.3176 | 1.3176 | 1.3176 | 0.85737 | 0.99734 | 0.99734 | 0.99734 | 0.99734 | 0.99734
2020-03-22 05:00 | Summer | 0.57234 | 0.81912 | 1.182 | 1.182 | 1.182 | 1.182 | 0.39438 | 0.77999 | 0.77999 | 0.77999 | 0.77999 | 0.77999 | 1.6766 | 2.1636 | 2.4827 | 2.6507 | 2.9865 | 3.3224 | 0.68558 | 1.3531 | 1.6238 | 1.6238 | 1.6238 | 1.6238 | 0.85737 | 0.99734 | 0.99734 | 0.99734 | 0.99734 | 0.99734
2020-03-22 06:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.45154 | 0.89304 | 0.89304 | 0.89304 | 0.89304 | 0.89304 | 1.7719 | 2.2866 | 2.6238 | 2.8013 | 3.1562 | 3.5112 | 0.77734 | 1.5342 | 1.8411 | 1.8411 | 1.8411 | 1.8411 | 0.91452 | 1.0638 | 1.0638 | 1.0638 | 1.0638 | 1.0638
2020-03-22 07:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.5087 | 1.0061 | 1.0061 | 1.0061 | 1.0061 | 1.0061 | 1.8672 | 2.4095 | 2.7649 | 2.9519 | 3.3259 | 3.7 | 0.76591 | 1.5117 | 1.814 | 1.814 | 1.814 | 1.814 | 0.85737 | 0.99734 | 0.99734 | 0.99734 | 0.99734 | 0.99734
2020-03-22 08:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.41725 | 0.82521 | 0.82521 | 0.82521 | 0.82521 | 0.82521 | 2.0386 | 2.6308 | 3.0188 | 3.223 | 3.6314 | 4.0398 | 0.8345 | 1.647 | 1.9764 | 1.9764 | 1.9764 | 1.9764 | 0.89547 | 1.0417 | 1.0417 | 1.0417 | 1.0417 | 1.0417
2020-03-22 09:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.42296 | 0.83652 | 0.83652 | 0.83652 | 0.83652 | 0.83652 | 2.0767 | 2.68 | 3.0752 | 3.2832 | 3.6992 | 4.1153 | 0.92595 | 1.8275 | 2.193 | 2.193 | 2.193 | 2.193 | 0.91452 | 1.0638 | 1.0638 | 1.0638 | 1.0638 | 1.0638
2020-03-22 10:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.4544 | 0.89869 | 0.89869 | 0.89869 | 0.89869 | 0.89869 | 2.2291 | 2.8767 | 3.3009 | 3.5242 | 3.9708 | 4.4173 | 0.93738 | 1.8501 | 2.2201 | 2.2201 | 2.2201 | 2.2201 | 0.93358 | 1.086 | 1.086 | 1.086 | 1.086 | 1.086
2020-03-22 11:00 | Summer | 0.57175 | 0.81827 | 1.1808 | 1.1808 | 1.1808 | 1.1808 | 0.46869 | 0.92695 | 0.92695 | 0.92695 | 0.92695 | 0.92695 | 2.2863 | 2.9504 | 3.3855 | 3.6146 | 4.0726 | 4.5306 | 0.92595 | 1.8275 | 2.193 | 2.193 | 2.193 | 2.193 | 1.0098 | 1.1746 | 1.1746 | 1.1746 | 1.1746 | 1.1746
2020-03-22 12:00 | Summer | 0.55252 | 0.79075 | 1.1411 | 1.1411 | 1.1411 | 1.1411 | 0.46583 | 0.9213 | 0.9213 | 0.9213 | 0.9213 | 0.9213 | 2.3435 | 3.0242 | 3.4702 | 3.7049 | 4.1744 | 4.6438 | 0.83069 | 1.6395 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 1.0479 | 1.219 | 1.219 | 1.219 | 1.219 | 1.219
2020-03-22 13:00 | Summer | 0.55252 | 0.79075 | 1.1411 | 1.1411 | 1.1411 | 1.1411 | 0.41725 | 0.82521 | 0.82521 | 0.82521 | 0.82521 | 0.82521 | 2.3244 | 2.9996 | 3.442 | 3.6748 | 4.1404 | 4.6061 | 0.89547 | 1.7674 | 2.1208 | 2.1208 | 2.1208 | 2.1208 | 1.0098 | 1.1746 | 1.1746 | 1.1746 | 1.1746 | 1.1746
2020-03-22 14:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.48584 | 0.96086 | 0.96086 | 0.96086 | 0.96086 | 0.96086 | 2.2863 | 2.9504 | 3.3855 | 3.6146 | 4.0726 | 4.5306 | 0.91452 | 1.805 | 2.166 | 2.166 | 2.166 | 2.166 | 1.0479 | 1.219 | 1.219 | 1.219 | 1.219 | 1.219
2020-03-22 15:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.42296 | 0.83652 | 0.83652 | 0.83652 | 0.83652 | 0.83652 | 2.2673 | 2.9258 | 3.3573 | 3.5844 | 4.0386 | 4.4928 | 0.86879 | 1.7147 | 2.0577 | 2.0577 | 2.0577 | 2.0577 | 0.97168 | 1.1303 | 1.1303 | 1.1303 | 1.1303 | 1.1303
2020-03-22 16:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.42868 | 0.84782 | 0.84782 | 0.84782 | 0.84782 | 0.84782 | 2.4006 | 3.098 | 3.5548 | 3.7953 | 4.2762 | 4.7571 | 0.89547 | 1.7674 | 2.1208 | 2.1208 | 2.1208 | 2.1208 | 0.95263 | 1.1082 | 1.1082 | 1.1082 | 1.1082 | 1.1082
2020-03-22 17:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.55157 | 1.0909 | 1.0909 | 1.0909 | 1.0909 | 1.0909 | 2.3244 | 2.9996 | 3.442 | 3.6748 | 4.1404 | 4.6061 | 0.89166 | 1.7599 | 2.1118 | 2.1118 | 2.1118 | 2.1118 | 0.95263 | 1.1082 | 1.1082 | 1.1082 | 1.1082 | 1.1082
2020-03-22 18:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.44011 | 0.87043 | 0.87043 | 0.87043 | 0.87043 | 0.87043 | 2.2482 | 2.9013 | 3.3291 | 3.5543 | 4.0047 | 4.4551 | 0.9069 | 1.7899 | 2.1479 | 2.1479 | 2.1479 | 2.1479 | 0.95263 | 1.1082 | 1.1082 | 1.1082 | 1.1082 | 1.1082
2020-03-22 19:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.41667 | 0.82406 | 0.82406 | 0.82406 | 0.82406 | 0.82406 | 2.1339 | 2.7537 | 3.1598 | 3.3736 | 3.8011 | 4.2285 | 0.91452 | 1.805 | 2.166 | 2.166 | 2.166 | 2.166 | 0.97168 | 1.1303 | 1.1303 | 1.1303 | 1.1303 | 1.1303
2020-03-22 20:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.47441 | 0.93825 | 0.93825 | 0.93825 | 0.93825 | 0.93825 | 2.2291 | 2.8767 | 3.3009 | 3.5242 | 3.9708 | 4.4173 | 0.92214 | 1.82 | 2.184 | 2.184 | 2.184 | 2.184 | 0.97168 | 1.1303 | 1.1303 | 1.1303 | 1.1303 | 1.1303
2020-03-22 21:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.42582 | 0.84217 | 0.84217 | 0.84217 | 0.84217 | 0.84217 | 2.0628 | 2.662 | 3.0546 | 3.2612 | 3.6745 | 4.0877 | 0.82307 | 1.6245 | 1.9494 | 1.9494 | 1.9494 | 1.9494 | 0.97168 | 1.1303 | 1.1303 | 1.1303 | 1.1303 | 1.1303
2020-03-22 22:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.35152 | 0.69521 | 0.69521 | 0.69521 | 0.69521 | 0.69521 | 1.9624 | 2.5325 | 2.9059 | 3.1025 | 3.4956 | 3.8887 | 0.86117 | 1.6997 | 2.0396 | 2.0396 | 2.0396 | 2.0396 | 0.87636 | 1.0194 | 1.0194 | 1.0194 | 1.0194 | 1.0194
2020-03-22 23:00 | Summer | 0.58811 | 0.84168 | 1.2146 | 1.2146 | 1.2146 | 1.2146 | 0.39438 | 0.77999 | 0.77999 | 0.77999 | 0.77999 | 0.77999 | 1.8474 | 2.3841 | 2.7356 | 2.9207 | 3.2908 | 3.6609 | 0.62111 | 1.2259 | 1.4711 | 1.4711 | 1.4711 | 1.4711 | 0.87642 | 1.0195 | 1.0195 | 1.0195 | 1.0195 | 1.0195
2020-03-23 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.37438 | 0.74043 | 0.74043 | 0.74043 | 0.74043 | 0.74043 | 1.7338 | 2.2374 | 2.5674 | 2.741 | 3.0884 | 3.4357 | 0.55252 | 1.0905 | 1.3086 | 1.3086 | 1.3086 | 1.3086 | 0.87642 | 1.0195 | 1.0195 | 1.0195 | 1.0195 | 1.0195
2020-03-23 01:00 | Summer | 0.57148 | 0.81788 | 1.1802 | 1.1802 | 1.1802 | 1.1802 | 0.2915 | 0.57652 | 0.57652 | 0.57652 | 0.57652 | 0.57652 | 1.6576 | 2.1391 | 2.4545 | 2.6205 | 2.9526 | 3.2847 | 0.59825 | 1.1808 | 1.4169 | 1.4169 | 1.4169 | 1.4169 | 0.87642 | 1.0195 | 1.0195 | 1.0195 | 1.0195 | 1.0195
2020-03-23 02:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.30018 | 0.59367 | 0.59367 | 0.59367 | 0.59367 | 0.59367 | 1.6195 | 2.0899 | 2.3981 | 2.5603 | 2.8847 | 3.2092 | 0.55633 | 1.098 | 1.3176 | 1.3176 | 1.3176 | 1.3176 | 0.85737 | 0.99734 | 0.99734 | 0.99734 | 0.99734 | 0.99734
2020-03-23 03:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.38009 | 0.75173 | 0.75173 | 0.75173 | 0.75173 | 0.75173 | 1.6004 | 2.0653 | 2.3699 | 2.5302 | 2.8508 | 3.1714 | 0.54871 | 1.083 | 1.2996 | 1.2996 | 1.2996 | 1.2996 | 0.89547 | 1.0417 | 1.0417 | 1.0417 | 1.0417 | 1.0417
2020-03-23 04:00 | Summer | 0.85737 | 1.227 | 1.7706 | 1.7706 | 1.7706 | 1.7706 | 0.43154 | 0.85347 | 0.85347 | 0.85347 | 0.85347 | 0.85347 | 1.6385 | 2.1145 | 2.4263 | 2.5904 | 2.9187 | 3.2469 | 0.52585 | 1.0379 | 1.2454 | 1.2454 | 1.2454 | 1.2454 | 0.97168 | 1.1303 | 1.1303 | 1.1303 | 1.1303 | 1.1303
2020-03-23 05:00 | Summer | 0.91452 | 1.3088 | 1.8887 | 1.8887 | 1.8887 | 1.8887 | 0.53442 | 1.057 | 1.057 | 1.057 | 1.057 | 1.057 | 1.6576 | 2.1391 | 2.4545 | 2.6205 | 2.9526 | 3.2847 | 0.80021 | 1.5794 | 1.8952 | 1.8952 | 1.8952 | 1.8952 | 1.1429 | 1.3295 | 1.3295 | 1.3295 | 1.3295 | 1.3295
2020-03-23 06:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.76877 | 1.5204 | 1.5204 | 1.5204 | 1.5204 | 1.5204 | 1.9624 | 2.5325 | 2.9059 | 3.1025 | 3.4956 | 3.8887 | 0.87261 | 1.7222 | 2.0667 | 2.0667 | 2.0667 | 2.0667 | 1.4168 | 1.6482 | 1.6482 | 1.6482 | 1.6482 | 1.6482
2020-03-23 07:00 | Summer | 1.2194 | 1.7451 | 2.5183 | 2.5183 | 2.5183 | 2.5183 | 0.79449 | 1.5713 | 1.5713 | 1.5713 | 1.5713 | 1.5713 | 2.2291 | 2.8767 | 3.3009 | 3.5242 | 3.9708 | 4.4173 | 1.0365 | 2.0456 | 2.4548 | 2.4548 | 2.4548 | 2.4548 | 1.7297 | 2.0121 | 2.0121 | 2.0121 | 2.0121 | 2.0121
2020-03-23 08:00 | Summer | 1.5808 | 2.2623 | 3.2646 | 3.2646 | 3.2646 | 3.2646 | 0.92595 | 1.8313 | 1.8313 | 1.8313 | 1.8313 | 1.8313 | 2.4387 | 3.1471 | 3.6112 | 3.8555 | 4.3441 | 4.8326 | 1.0479 | 2.0682 | 2.4818 | 2.4818 | 2.4818 | 2.4818 | 2.1339 | 2.4823 | 2.4823 | 2.4823 | 2.4823 | 2.4823
2020-03-23 09:00 | Summer | 1.6195 | 2.3177 | 3.3446 | 3.3446 | 3.3446 | 3.3446 | 0.98311 | 1.9443 | 1.9443 | 1.9443 | 1.9443 | 1.9443 | 2.4768 | 3.1963 | 3.6677 | 3.9158 | 4.4119 | 4.9081 | 1.0441 | 2.0607 | 2.4728 | 2.4728 | 2.4728 | 2.4728 | 2.172 | 2.5266 | 2.5266 | 2.5266 | 2.5266 | 2.5266
2020-03-23 10:00 | Summer | 1.6004 | 2.2904 | 3.3052 | 3.3052 | 3.3052 | 3.3052 | 0.95453 | 1.8878 | 1.8878 | 1.8878 | 1.8878 | 1.8878 | 2.6293 | 3.393 | 3.8934 | 4.1567 | 4.6835 | 5.2102 | 0.93738 | 1.8501 | 2.2201 | 2.2201 | 2.2201 | 2.2201 | 2.2482 | 2.6153 | 2.6153 | 2.6153 | 2.6153 | 2.6153
2020-03-23 11:00 | Summer | 1.6016 | 2.2922 | 3.3077 | 3.3077 | 3.3077 | 3.3077 | 0.97453 | 1.9274 | 1.9274 | 1.9274 | 1.9274 | 1.9274 | 2.7122 | 3.5 | 4.0162 | 4.2878 | 4.8312 | 5.3745 | 0.99073 | 1.9554 | 2.3465 | 2.3465 | 2.3465 | 2.3465 | 2.3244 | 2.7039 | 2.7039 | 2.7039 | 2.7039 | 2.7039
2020-03-23 12:00 | Summer | 1.6766 | 2.3995 | 3.4626 | 3.4626 | 3.4626 | 3.4626 | 1.126 | 2.227 | 2.227 | 2.227 | 2.227 | 2.227 | 2.8388 | 3.6634 | 4.2037 | 4.4881 | 5.0568 | 5.6255 | 0.99073 | 1.9554 | 2.3465 | 2.3465 | 2.3465 | 2.3465 | 2.3816 | 2.7704 | 2.7704 | 2.7704 | 2.7704 | 2.7704
2020-03-23 13:00 | Summer | 1.8862 | 2.6995 | 3.8954 | 3.8954 | 3.8954 | 3.8954 | 1.086 | 2.1478 | 2.1478 | 2.1478 | 2.1478 | 2.1478 | 2.8007 | 3.6143 | 4.1473 | 4.4278 | 4.9889 | 5.55 | 1.0326 | 2.0381 | 2.4457 | 2.4457 | 2.4457 | 2.4457 | 2.3816 | 2.7704 | 2.7704 | 2.7704 | 2.7704 | 2.7704
2020-03-23 14:00 | Summer | 1.81 | 2.5904 | 3.738 | 3.738 | 3.738 | 3.738 | 1.106 | 2.1874 | 2.1874 | 2.1874 | 2.1874 | 2.1874 | 2.7817 | 3.5897 | 4.1191 | 4.3977 | 4.955 | 5.5122 | 1.2232 | 2.4142 | 2.897 | 2.897 | 2.897 | 2.897 | 2.4006 | 2.7926 | 2.7926 | 2.7926 | 2.7926 | 2.7926
2020-03-23 15:00 | Summer | 1.7909 | 2.5631 | 3.6987 | 3.6987 | 3.6987 | 3.6987 | 1.1231 | 2.2213 | 2.2213 | 2.2213 | 2.2213 | 2.2213 | 2.7817 | 3.5897 | 4.1191 | 4.3977 | 4.955 | 5.5122 | 1.0669 | 2.1058 | 2.527 | 2.527 | 2.527 | 2.527 | 2.4387 | 2.8369 | 2.8369 | 2.8369 | 2.8369 | 2.8369
2020-03-23 16:00 | Summer | 1.6766 | 2.3995 | 3.4626 | 3.4626 | 3.4626 | 3.4626 | 1.0088 | 1.9952 | 1.9952 | 1.9952 | 1.9952 | 1.9952 | 2.6729 | 3.4493 | 3.958 | 4.2257 | 4.7612 | 5.2966 | 1.0593 | 2.0908 | 2.5089 | 2.5089 | 2.5089 | 2.5089 | 2.2863 | 2.6596 | 2.6596 | 2.6596 | 2.6596 | 2.6596
2020-03-23 17:00 | Summer | 1.557 | 2.2284 | 3.2156 | 3.2156 | 3.2156 | 3.2156 | 0.92595 | 1.8313 | 1.8313 | 1.8313 | 1.8313 | 1.8313 | 2.534 | 3.2701 | 3.7523 | 4.0061 | 4.5138 | 5.0214 | 0.97168 | 1.9178 | 2.3013 | 2.3013 | 2.3013 | 2.3013 | 2.0853 | 2.4257 | 2.4257 | 2.4257 | 2.4257 | 2.4257
2020-03-23 18:00 | Summer | 1.0584 | 1.5147 | 2.1858 | 2.1858 | 2.1858 | 2.1858 | 0.67203 | 1.3291 | 1.3291 | 1.3291 | 1.3291 | 1.3291 | 2.5149 | 3.2455 | 3.7241 | 3.976 | 4.4798 | 4.9836 | 0.83069 | 1.6395 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 1.5523 | 1.8058 | 1.8058 | 1.8058 | 1.8058 | 1.8058
2020-03-23 19:00 | Summer | 0.78115 | 1.118 | 1.6133 | 1.6133 | 1.6133 | 1.6133 | 0.50013 | 0.98912 | 0.98912 | 0.98912 | 0.98912 | 0.98912 | 2.2673 | 2.9258 | 3.3573 | 3.5844 | 4.0386 | 4.4928 | 0.68589 | 1.3537 | 1.6245 | 1.6245 | 1.6245 | 1.6245 | 1.1241 | 1.3076 | 1.3076 | 1.3076 | 1.3076 | 1.3076
2020-03-23 20:00 | Summer | 0.64797 | 0.92734 | 1.3382 | 1.3382 | 1.3382 | 1.3382 | 0.39438 | 0.77999 | 0.77999 | 0.77999 | 0.77999 | 0.77999 | 2.1148 | 2.7291 | 3.1316 | 3.3435 | 3.7671 | 4.1908 | 0.67065 | 1.3236 | 1.5884 | 1.5884 | 1.5884 | 1.5884 | 1.086 | 1.2633 | 1.2633 | 1.2633 | 1.2633 | 1.2633
2020-03-23 21:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.38009 | 0.75173 | 0.75173 | 0.75173 | 0.75173 | 0.75173 | 1.9815 | 2.557 | 2.9341 | 3.1326 | 3.5296 | 3.9265 | 0.67065 | 1.3236 | 1.5884 | 1.5884 | 1.5884 | 1.5884 | 0.95338 | 1.109 | 1.109 | 1.109 | 1.109 | 1.109
2020-03-23 22:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.37724 | 0.74608 | 0.74608 | 0.74608 | 0.74608 | 0.74608 | 1.9243 | 2.4833 | 2.8495 | 3.0422 | 3.4277 | 3.8132 | 0.64397 | 1.271 | 1.5252 | 1.5252 | 1.5252 | 1.5252 | 0.89656 | 1.0429 | 1.0429 | 1.0429 | 1.0429 | 1.0429
2020-03-23 23:00 | Summer | 0.58691 | 0.83997 | 1.2121 | 1.2121 | 1.2121 | 1.2121 | 0.27453 | 0.54295 | 0.54295 | 0.54295 | 0.54295 | 0.54295 | 1.829 | 2.3603 | 2.7084 | 2.8916 | 3.2581 | 3.6245 | 0.58304 | 1.1507 | 1.3809 | 1.3809 | 1.3809 | 1.3809 | 0.87642 | 1.0195 | 1.0195 | 1.0195 | 1.0195 | 1.0195
2020-03-24 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.33151 | 0.65565 | 0.65565 | 0.65565 | 0.65565 | 0.65565 | 1.7338 | 2.2374 | 2.5674 | 2.741 | 3.0884 | 3.4357 | 0.55252 | 1.0905 | 1.3086 | 1.3086 | 1.3086 | 1.3086 | 0.85737 | 0.99734 | 0.99734 | 0.99734 | 0.99734 | 0.99734
2020-03-24 01:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.37438 | 0.74043 | 0.74043 | 0.74043 | 0.74043 | 0.74043 | 1.7147 | 2.2128 | 2.5392 | 2.7109 | 3.0544 | 3.3979 | 0.5449 | 1.0755 | 1.2906 | 1.2906 | 1.2906 | 1.2906 | 0.83831 | 0.97518 | 0.97518 | 0.97518 | 0.97518 | 0.97518
2020-03-24 02:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.40867 | 0.80825 | 0.80825 | 0.80825 | 0.80825 | 0.80825 | 1.6004 | 2.0653 | 2.3699 | 2.5302 | 2.8508 | 3.1714 | 0.52966 | 1.0454 | 1.2545 | 1.2545 | 1.2545 | 1.2545 | 0.85737 | 0.99734 | 0.99734 | 0.99734 | 0.99734 | 0.99734
2020-03-24 03:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.37152 | 0.73478 | 0.73478 | 0.73478 | 0.73478 | 0.73478 | 1.6004 | 2.0653 | 2.3699 | 2.5302 | 2.8508 | 3.1714 | 0.55633 | 1.098 | 1.3176 | 1.3176 | 1.3176 | 1.3176 | 0.85737 | 0.99734 | 0.99734 | 0.99734 | 0.99734 | 0.99734
2020-03-24 04:00 | Summer | 0.62836 | 0.89929 | 1.2977 | 1.2977 | 1.2977 | 1.2977 | 0.2915 | 0.57652 | 0.57652 | 0.57652 | 0.57652 | 0.57652 | 1.6193 | 2.0897 | 2.3978 | 2.56 | 2.8844 | 3.2088 | 0.56776 | 1.1206 | 1.3447 | 1.3447 | 1.3447 | 1.3447 | 0.90021 | 1.0472 | 1.0472 | 1.0472 | 1.0472 | 1.0472
2020-03-24 05:00 | Summer | 0.80021 | 1.1452 | 1.6526 | 1.6526 | 1.6526 | 1.6526 | 0.49441 | 0.97782 | 0.97782 | 0.97782 | 0.97782 | 0.97782 | 1.6735 | 2.1597 | 2.4782 | 2.6458 | 2.981 | 3.3163 | 0.59825 | 1.1808 | 1.4169 | 1.4169 | 1.4169 | 1.4169 | 1.0969 | 1.2759 | 1.2759 | 1.2759 | 1.2759 | 1.2759
2020-03-24 06:00 | Summer | 0.83775 | 1.199 | 1.7301 | 1.7301 | 1.7301 | 1.7301 | 0.70018 | 1.3848 | 1.3848 | 1.3848 | 1.3848 | 1.3848 | 1.8564 | 2.3956 | 2.7489 | 2.9349 | 3.3068 | 3.6786 | 0.73924 | 1.459 | 1.7508 | 1.7508 | 1.7508 | 1.7508 | 1.3704 | 1.5942 | 1.5942 | 1.5942 | 1.5942 | 1.5942
2020-03-24 07:00 | Summer | 1.0776 | 1.5422 | 2.2254 | 2.2254 | 2.2254 | 2.2254 | 0.8002 | 1.5826 | 1.5826 | 1.5826 | 1.5826 | 1.5826 | 2.2101 | 2.8521 | 3.2727 | 3.4941 | 3.9368 | 4.3796 | 0.9793 | 1.9328 | 2.3194 | 2.3194 | 2.3194 | 2.3194 | 1.7334 | 2.0165 | 2.0165 | 2.0165 | 2.0165 | 2.0165
2020-03-24 08:00 | Summer | 1.5052 | 2.1541 | 3.1085 | 3.1085 | 3.1085 | 3.1085 | 0.90023 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 2.4006 | 3.098 | 3.5548 | 3.7953 | 4.2762 | 4.7571 | 0.87539 | 1.7277 | 2.0733 | 2.0733 | 2.0733 | 2.0733 | 2.0386 | 2.3715 | 2.3715 | 2.3715 | 2.3715 | 2.3715
2020-03-24 09:00 | Summer | 1.5623 | 2.2359 | 3.2265 | 3.2265 | 3.2265 | 3.2265 | 0.8545 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 2.4006 | 3.098 | 3.5548 | 3.7953 | 4.2762 | 4.7571 | 0.81164 | 1.6019 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 2.1339 | 2.4823 | 2.4823 | 2.4823 | 2.4823 | 2.4823
2020-03-24 10:00 | Summer | 1.4861 | 2.1268 | 3.0691 | 3.0691 | 3.0691 | 3.0691 | 0.95739 | 1.8935 | 1.8935 | 1.8935 | 1.8935 | 1.8935 | 2.553 | 3.2946 | 3.7805 | 4.0362 | 4.5477 | 5.0591 | 0.91452 | 1.805 | 2.166 | 2.166 | 2.166 | 2.166 | 2.1339 | 2.4823 | 2.4823 | 2.4823 | 2.4823 | 2.4823
2020-03-24 11:00 | Summer | 1.6195 | 2.3177 | 3.3446 | 3.3446 | 3.3446 | 3.3446 | 0.94596 | 1.8709 | 1.8709 | 1.8709 | 1.8709 | 1.8709 | 2.6835 | 3.463 | 3.9737 | 4.2425 | 4.7801 | 5.3177 | 0.89166 | 1.7599 | 2.1118 | 2.1118 | 2.1118 | 2.1118 | 2.2673 | 2.6374 | 2.6374 | 2.6374 | 2.6374 | 2.6374
2020-03-24 12:00 | Summer | 1.7338 | 2.4813 | 3.5806 | 3.5806 | 3.5806 | 3.5806 | 1.0431 | 2.063 | 2.063 | 2.063 | 2.063 | 2.063 | 2.7436 | 3.5405 | 4.0627 | 4.3375 | 4.8871 | 5.4367 | 0.91833 | 1.8125 | 2.175 | 2.175 | 2.175 | 2.175 | 2.3625 | 2.7482 | 2.7482 | 2.7482 | 2.7482 | 2.7482
2020-03-24 13:00 | Summer | 1.7338 | 2.4813 | 3.5806 | 3.5806 | 3.5806 | 3.5806 | 0.98025 | 1.9387 | 1.9387 | 1.9387 | 1.9387 | 1.9387 | 2.6865 | 3.4669 | 3.9781 | 4.2472 | 4.7854 | 5.3236 | 0.81545 | 1.6094 | 1.9313 | 1.9313 | 1.9313 | 1.9313 | 2.3625 | 2.7482 | 2.7482 | 2.7482 | 2.7482 | 2.7482
2020-03-24 14:00 | Summer | 1.7338 | 2.4813 | 3.5806 | 3.5806 | 3.5806 | 3.5806 | 0.99168 | 1.9613 | 1.9613 | 1.9613 | 1.9613 | 1.9613 | 2.7817 | 3.5897 | 4.1191 | 4.3977 | 4.955 | 5.5122 | 0.82307 | 1.6245 | 1.9494 | 1.9494 | 1.9494 | 1.9494 | 2.3816 | 2.7704 | 2.7704 | 2.7704 | 2.7704 | 2.7704
2020-03-24 15:00 | Summer | 1.6766 | 2.3995 | 3.4626 | 3.4626 | 3.4626 | 3.4626 | 1.106 | 2.1874 | 2.1874 | 2.1874 | 2.1874 | 2.1874 | 2.6864 | 3.4668 | 3.978 | 4.2471 | 4.7853 | 5.3234 | 0.94119 | 1.8576 | 2.2291 | 2.2291 | 2.2291 | 2.2291 | 2.3244 | 2.7039 | 2.7039 | 2.7039 | 2.7039 | 2.7039
2020-03-24 16:00 | Summer | 1.5814 | 2.2632 | 3.2659 | 3.2659 | 3.2659 | 3.2659 | 1.0231 | 2.0235 | 2.0235 | 2.0235 | 2.0235 | 2.0235 | 2.6864 | 3.4668 | 3.978 | 4.2471 | 4.7853 | 5.3234 | 0.83831 | 1.6546 | 1.9855 | 1.9855 | 1.9855 | 1.9855 | 2.2673 | 2.6374 | 2.6374 | 2.6374 | 2.6374 | 2.6374
2020-03-24 17:00 | Summer | 1.5242 | 2.1814 | 3.1478 | 3.1478 | 3.1478 | 3.1478 | 0.91738 | 1.8143 | 1.8143 | 1.8143 | 1.8143 | 1.8143 | 2.7055 | 3.4913 | 4.0062 | 4.2772 | 4.8192 | 5.3612 | 0.81545 | 1.6094 | 1.9313 | 1.9313 | 1.9313 | 1.9313 | 2.2482 | 2.6153 | 2.6153 | 2.6153 | 2.6153 | 2.6153
2020-03-24 18:00 | Summer | 1.0823 | 1.5489 | 2.2351 | 2.2351 | 2.2351 | 2.2351 | 0.72438 | 1.4326 | 1.4326 | 1.4326 | 1.4326 | 1.4326 | 2.4293 | 3.1349 | 3.5973 | 3.8406 | 4.3273 | 4.8139 | 0.62111 | 1.2259 | 1.4711 | 1.4711 | 1.4711 | 1.4711 | 1.5702 | 1.8265 | 1.8265 | 1.8265 | 1.8265 | 1.8265
2020-03-24 19:00 | Summer | 0.724 | 1.0362 | 1.4952 | 1.4952 | 1.4952 | 1.4952 | 0.47155 | 0.9326 | 0.9326 | 0.9326 | 0.9326 | 0.9326 | 2.2514 | 2.9054 | 3.3339 | 3.5594 | 4.0104 | 4.4615 | 0.62111 | 1.2259 | 1.4711 | 1.4711 | 1.4711 | 1.4711 | 1.1622 | 1.352 | 1.352 | 1.352 | 1.352 | 1.352
2020-03-24 20:00 | Summer | 0.68589 | 0.98162 | 1.4165 | 1.4165 | 1.4165 | 1.4165 | 0.41439 | 0.81956 | 0.81956 | 0.81956 | 0.81956 | 0.81956 | 2.1148 | 2.7291 | 3.1316 | 3.3435 | 3.7671 | 4.1908 | 0.65922 | 1.3011 | 1.5613 | 1.5613 | 1.5613 | 1.5613 | 1.1241 | 1.3076 | 1.3076 | 1.3076 | 1.3076 | 1.3076
2020-03-24 21:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.40296 | 0.79695 | 0.79695 | 0.79695 | 0.79695 | 0.79695 | 1.9815 | 2.557 | 2.9341 | 3.1326 | 3.5296 | 3.9265 | 0.62873 | 1.2409 | 1.4891 | 1.4891 | 1.4891 | 1.4891 | 1.0288 | 1.1968 | 1.1968 | 1.1968 | 1.1968 | 1.1968
2020-03-24 22:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.41725 | 0.82521 | 0.82521 | 0.82521 | 0.82521 | 0.82521 | 1.9434 | 2.5079 | 2.8777 | 3.0724 | 3.4617 | 3.851 | 0.53728 | 1.0604 | 1.2725 | 1.2725 | 1.2725 | 1.2725 | 0.99102 | 1.1528 | 1.1528 | 1.1528 | 1.1528 | 1.1528
2020-03-24 23:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.37438 | 0.74043 | 0.74043 | 0.74043 | 0.74043 | 0.74043 | 1.8292 | 2.3605 | 2.7086 | 2.8919 | 3.2583 | 3.6248 | 0.51442 | 1.0153 | 1.2184 | 1.2184 | 1.2184 | 1.2184 | 0.93358 | 1.086 | 1.086 | 1.086 | 1.086 | 1.086
2020-03-25 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.41725 | 0.82521 | 0.82521 | 0.82521 | 0.82521 | 0.82521 | 1.81 | 2.3358 | 2.6802 | 2.8615 | 3.2241 | 3.5867 | 0.49155 | 0.97017 | 1.1642 | 1.1642 | 1.1642 | 1.1642 | 0.89547 | 1.0417 | 1.0417 | 1.0417 | 1.0417 | 1.0417
2020-03-25 01:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.41439 | 0.81956 | 0.81956 | 0.81956 | 0.81956 | 0.81956 | 1.6576 | 2.1391 | 2.4545 | 2.6205 | 2.9526 | 3.2847 | 0.46869 | 0.92505 | 1.1101 | 1.1101 | 1.1101 | 1.1101 | 0.85737 | 0.99734 | 0.99734 | 0.99734 | 0.99734 | 0.99734
2020-03-25 02:00 | Summer | 0.60087 | 0.85994 | 1.2409 | 1.2409 | 1.2409 | 1.2409 | 0.37724 | 0.74608 | 0.74608 | 0.74608 | 0.74608 | 0.74608 | 1.7528 | 2.262 | 2.5956 | 2.7712 | 3.1223 | 3.4734 | 0.45345 | 0.89497 | 1.074 | 1.074 | 1.074 | 1.074 | 0.83831 | 0.97518 | 0.97518 | 0.97518 | 0.97518 | 0.97518
2020-03-25 03:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.47155 | 0.9326 | 0.9326 | 0.9326 | 0.9326 | 0.9326 | 1.6766 | 2.1636 | 2.4827 | 2.6507 | 2.9865 | 3.3224 | 0.44964 | 0.88744 | 1.0649 | 1.0649 | 1.0649 | 1.0649 | 0.83831 | 0.97518 | 0.97518 | 0.97518 | 0.97518 | 0.97518
2020-03-25 04:00 | Summer | 0.63238 | 0.90503 | 1.306 | 1.306 | 1.306 | 1.306 | 0.44011 | 0.87043 | 0.87043 | 0.87043 | 0.87043 | 0.87043 | 1.7147 | 2.2128 | 2.5392 | 2.7109 | 3.0544 | 3.3979 | 0.46107 | 0.91001 | 1.092 | 1.092 | 1.092 | 1.092 | 0.91439 | 1.0637 | 1.0637 | 1.0637 | 1.0637 | 1.0637
2020-03-25 05:00 | Summer | 0.70494 | 1.0089 | 1.4559 | 1.4559 | 1.4559 | 1.4559 | 0.47155 | 0.9326 | 0.9326 | 0.9326 | 0.9326 | 0.9326 | 1.7338 | 2.2374 | 2.5674 | 2.741 | 3.0884 | 3.4357 | 0.53273 | 1.0514 | 1.2617 | 1.2617 | 1.2617 | 1.2617 | 1.0288 | 1.1968 | 1.1968 | 1.1968 | 1.1968 | 1.1968
2020-03-25 06:00 | Summer | 0.83466 | 1.1945 | 1.7238 | 1.7238 | 1.7238 | 1.7238 | 0.66017 | 1.3056 | 1.3056 | 1.3056 | 1.3056 | 1.3056 | 1.9311 | 2.492 | 2.8595 | 3.0529 | 3.4398 | 3.8266 | 0.64397 | 1.271 | 1.5252 | 1.5252 | 1.5252 | 1.5252 | 1.3779 | 1.6028 | 1.6028 | 1.6028 | 1.6028 | 1.6028
2020-03-25 07:00 | Summer | 1.0346 | 1.4807 | 2.1367 | 2.1367 | 2.1367 | 2.1367 | 0.73785 | 1.4593 | 1.4593 | 1.4593 | 1.4593 | 1.4593 | 2.2271 | 2.8741 | 3.2979 | 3.521 | 3.9672 | 4.4134 | 0.72018 | 1.4214 | 1.7057 | 1.7057 | 1.7057 | 1.7057 | 1.6485 | 1.9176 | 1.9176 | 1.9176 | 1.9176 | 1.9176
2020-03-25 08:00 | Summer | 1.467 | 2.0996 | 3.0298 | 3.0298 | 3.0298 | 3.0298 | 0.89375 | 1.7676 | 1.7676 | 1.7676 | 1.7676 | 1.7676 | 2.5149 | 3.2455 | 3.7241 | 3.976 | 4.4798 | 4.9836 | 0.7621 | 1.5041 | 1.805 | 1.805 | 1.805 | 1.805 | 2.0196 | 2.3493 | 2.3493 | 2.3493 | 2.3493 | 2.3493
2020-03-25 09:00 | Summer | 1.6576 | 2.3723 | 3.4232 | 3.4232 | 3.4232 | 3.4232 | 1.1946 | 2.3626 | 2.3626 | 2.3626 | 2.3626 | 2.3626 | 2.6102 | 3.3684 | 3.8652 | 4.1266 | 4.6495 | 5.1724 | 0.94501 | 1.8651 | 2.2382 | 2.2382 | 2.2382 | 2.2382 | 2.1339 | 2.4823 | 2.4823 | 2.4823 | 2.4823 | 2.4823
2020-03-25 10:00 | Summer | 1.6576 | 2.3723 | 3.4232 | 3.4232 | 3.4232 | 3.4232 | 1.1317 | 2.2383 | 2.2383 | 2.2383 | 2.2383 | 2.2383 | 2.6483 | 3.4176 | 3.9216 | 4.1869 | 4.7174 | 5.2479 | 0.92976 | 1.8351 | 2.2021 | 2.2021 | 2.2021 | 2.2021 | 2.2673 | 2.6374 | 2.6374 | 2.6374 | 2.6374 | 2.6374
2020-03-25 11:00 | Summer | 1.695 | 2.4258 | 3.5005 | 3.5005 | 3.5005 | 3.5005 | 1.1003 | 2.1761 | 2.1761 | 2.1761 | 2.1761 | 2.1761 | 2.7436 | 3.5405 | 4.0627 | 4.3375 | 4.8871 | 5.4367 | 0.97168 | 1.9178 | 2.3013 | 2.3013 | 2.3013 | 2.3013 | 2.3816 | 2.7704 | 2.7704 | 2.7704 | 2.7704 | 2.7704
2020-03-25 12:00 | Summer | 1.6957 | 2.4268 | 3.5019 | 3.5019 | 3.5019 | 3.5019 | 1.1803 | 2.3343 | 2.3343 | 2.3343 | 2.3343 | 2.3343 | 2.7055 | 3.4913 | 4.0062 | 4.2772 | 4.8192 | 5.3612 | 1.1241 | 2.2186 | 2.6623 | 2.6623 | 2.6623 | 2.6623 | 2.3816 | 2.7704 | 2.7704 | 2.7704 | 2.7704 | 2.7704
2020-03-25 13:00 | Summer | 1.6385 | 2.345 | 3.3839 | 3.3839 | 3.3839 | 3.3839 | 1.3203 | 2.6113 | 2.6113 | 2.6113 | 2.6113 | 2.6113 | 2.7626 | 3.5651 | 4.0909 | 4.3676 | 4.921 | 5.4745 | 0.99073 | 1.9554 | 2.3465 | 2.3465 | 2.3465 | 2.3465 | 2.534 | 2.9477 | 2.9477 | 2.9477 | 2.9477 | 2.9477
2020-03-25 14:00 | Summer | 1.6385 | 2.345 | 3.3839 | 3.3839 | 3.3839 | 3.3839 | 1.1605 | 2.2953 | 2.2953 | 2.2953 | 2.2953 | 2.2953 | 2.7436 | 3.5405 | 4.0627 | 4.3375 | 4.8871 | 5.4367 | 1.0212 | 2.0156 | 2.4187 | 2.4187 | 2.4187 | 2.4187 | 2.4387 | 2.8369 | 2.8369 | 2.8369 | 2.8369 | 2.8369
2020-03-25 15:00 | Summer | 1.6195 | 2.3177 | 3.3446 | 3.3446 | 3.3446 | 3.3446 | 1.1489 | 2.2722 | 2.2722 | 2.2722 | 2.2722 | 2.2722 | 2.8007 | 3.6143 | 4.1473 | 4.4278 | 4.9889 | 5.55 | 1.1736 | 2.3164 | 2.7797 | 2.7797 | 2.7797 | 2.7797 | 2.3816 | 2.7704 | 2.7704 | 2.7704 | 2.7704 | 2.7704
2020-03-25 16:00 | Summer | 1.5814 | 2.2632 | 3.2659 | 3.2659 | 3.2659 | 3.2659 | 1.2689 | 2.5096 | 2.5096 | 2.5096 | 2.5096 | 2.5096 | 2.7055 | 3.4913 | 4.0062 | 4.2772 | 4.8192 | 5.3612 | 0.93738 | 1.8501 | 2.2201 | 2.2201 | 2.2201 | 2.2201 | 2.3244 | 2.7039 | 2.7039 | 2.7039 | 2.7039 | 2.7039
2020-03-25 17:00 | Summer | 1.5237 | 2.1806 | 3.1467 | 3.1467 | 3.1467 | 3.1467 | 1.0974 | 2.1704 | 2.1704 | 2.1704 | 2.1704 | 2.1704 | 2.6293 | 3.393 | 3.8934 | 4.1567 | 4.6835 | 5.2102 | 0.80021 | 1.5794 | 1.8952 | 1.8952 | 1.8952 | 1.8952 | 2.172 | 2.5266 | 2.5266 | 2.5266 | 2.5266 | 2.5266
2020-03-25 18:00 | Summer | 1.1293 | 1.6162 | 2.3322 | 2.3322 | 2.3322 | 2.3322 | 0.73447 | 1.4526 | 1.4526 | 1.4526 | 1.4526 | 1.4526 | 2.4278 | 3.133 | 3.5951 | 3.8383 | 4.3246 | 4.811 | 0.78496 | 1.5493 | 1.8591 | 1.8591 | 1.8591 | 1.8591 | 1.4668 | 1.7063 | 1.7063 | 1.7063 | 1.7063 | 1.7063
2020-03-25 19:00 | Summer | 0.78115 | 1.118 | 1.6133 | 1.6133 | 1.6133 | 1.6133 | 0.57443 | 1.1361 | 1.1361 | 1.1361 | 1.1361 | 1.1361 | 2.2291 | 2.8767 | 3.3009 | 3.5242 | 3.9708 | 4.4173 | 0.64779 | 1.2785 | 1.5342 | 1.5342 | 1.5342 | 1.5342 | 1.1813 | 1.3741 | 1.3741 | 1.3741 | 1.3741 | 1.3741
2020-03-25 20:00 | Summer | 0.68589 | 0.98162 | 1.4165 | 1.4165 | 1.4165 | 1.4165 | 0.51727 | 1.023 | 1.023 | 1.023 | 1.023 | 1.023 | 2.1148 | 2.7291 | 3.1316 | 3.3435 | 3.7671 | 4.1908 | 0.63635 | 1.256 | 1.5072 | 1.5072 | 1.5072 | 1.5072 | 1.0479 | 1.219 | 1.219 | 1.219 | 1.219 | 1.219
2020-03-25 21:00 | Summer | 0.60986 | 0.87281 | 1.2595 | 1.2595 | 1.2595 | 1.2595 | 0.46012 | 0.90999 | 0.90999 | 0.90999 | 0.90999 | 0.90999 | 2.0005 | 2.5816 | 2.9624 | 3.1627 | 3.5635 | 3.9643 | 0.56776 | 1.1206 | 1.3447 | 1.3447 | 1.3447 | 1.3447 | 0.97168 | 1.1303 | 1.1303 | 1.1303 | 1.1303 | 1.1303
2020-03-25 22:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.4544 | 0.89869 | 0.89869 | 0.89869 | 0.89869 | 0.89869 | 1.9624 | 2.5325 | 2.9059 | 3.1025 | 3.4956 | 3.8887 | 0.53347 | 1.0529 | 1.2635 | 1.2635 | 1.2635 | 1.2635 | 0.89547 | 1.0417 | 1.0417 | 1.0417 | 1.0417 | 1.0417
2020-03-25 23:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.41153 | 0.81391 | 0.81391 | 0.81391 | 0.81391 | 0.81391 | 1.8862 | 2.4341 | 2.7931 | 2.982 | 3.3599 | 3.7377 | 0.47631 | 0.94009 | 1.1281 | 1.1281 | 1.1281 | 1.1281 | 0.87642 | 1.0195 | 1.0195 | 1.0195 | 1.0195 | 1.0195
2020-03-26 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.37438 | 0.74043 | 0.74043 | 0.74043 | 0.74043 | 0.74043 | 1.7147 | 2.2128 | 2.5392 | 2.7109 | 3.0544 | 3.3979 | 0.54109 | 1.0679 | 1.2815 | 1.2815 | 1.2815 | 1.2815 | 0.87642 | 1.0195 | 1.0195 | 1.0195 | 1.0195 | 1.0195
2020-03-26 01:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.42582 | 0.84217 | 0.84217 | 0.84217 | 0.84217 | 0.84217 | 1.6576 | 2.1391 | 2.4545 | 2.6205 | 2.9526 | 3.2847 | 0.48774 | 0.96265 | 1.1552 | 1.1552 | 1.1552 | 1.1552 | 0.83915 | 0.97615 | 0.97615 | 0.97615 | 0.97615 | 0.97615
2020-03-26 02:00 | Summer | 0.57245 | 0.81927 | 1.1822 | 1.1822 | 1.1822 | 1.1822 | 0.40582 | 0.8026 | 0.8026 | 0.8026 | 0.8026 | 0.8026 | 1.6014 | 2.0665 | 2.3713 | 2.5317 | 2.8525 | 3.1733 | 0.49155 | 0.97017 | 1.1642 | 1.1642 | 1.1642 | 1.1642 | 0.87642 | 1.0195 | 1.0195 | 1.0195 | 1.0195 | 1.0195
2020-03-26 03:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.4001 | 0.7913 | 0.7913 | 0.7913 | 0.7913 | 0.7913 | 1.5814 | 2.0407 | 2.3417 | 2.5001 | 2.8169 | 3.1337 | 0.48012 | 0.94761 | 1.1371 | 1.1371 | 1.1371 | 1.1371 | 0.85737 | 0.99734 | 0.99734 | 0.99734 | 0.99734 | 0.99734
2020-03-26 04:00 | Summer | 0.63127 | 0.90345 | 1.3037 | 1.3037 | 1.3037 | 1.3037 | 0.31432 | 0.62165 | 0.62165 | 0.62165 | 0.62165 | 0.62165 | 1.6195 | 2.0899 | 2.3981 | 2.5603 | 2.8847 | 3.2092 | 0.46869 | 0.92505 | 1.1101 | 1.1101 | 1.1101 | 1.1101 | 0.91452 | 1.0638 | 1.0638 | 1.0638 | 1.0638 | 1.0638
2020-03-26 05:00 | Summer | 0.70494 | 1.0089 | 1.4559 | 1.4559 | 1.4559 | 1.4559 | 0.51156 | 1.0117 | 1.0117 | 1.0117 | 1.0117 | 1.0117 | 1.6004 | 2.0653 | 2.3699 | 2.5302 | 2.8508 | 3.1714 | 0.51061 | 1.0078 | 1.2093 | 1.2093 | 1.2093 | 1.2093 | 1.1236 | 1.307 | 1.307 | 1.307 | 1.307 | 1.307
2020-03-26 06:00 | Summer | 0.724 | 1.0362 | 1.4952 | 1.4952 | 1.4952 | 1.4952 | 0.65731 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.7287 | 2.2309 | 2.5599 | 2.7331 | 3.0794 | 3.4257 | 0.62873 | 1.2409 | 1.4891 | 1.4891 | 1.4891 | 1.4891 | 1.4078 | 1.6376 | 1.6376 | 1.6376 | 1.6376 | 1.6376
2020-03-26 07:00 | Summer | 0.9836 | 1.4077 | 2.0313 | 2.0313 | 2.0313 | 2.0313 | 0.81449 | 1.6109 | 1.6109 | 1.6109 | 1.6109 | 1.6109 | 2.0577 | 2.6554 | 3.047 | 3.2531 | 3.6653 | 4.0775 | 0.64779 | 1.2785 | 1.5342 | 1.5342 | 1.5342 | 1.5342 | 1.7719 | 2.0612 | 2.0612 | 2.0612 | 2.0612 | 2.0612
2020-03-26 08:00 | Summer | 1.2194 | 1.7451 | 2.5183 | 2.5183 | 2.5183 | 2.5183 | 0.88308 | 1.7465 | 1.7465 | 1.7465 | 1.7465 | 1.7465 | 2.172 | 2.8029 | 3.2163 | 3.4338 | 3.8689 | 4.3041 | 0.6897 | 1.3613 | 1.6335 | 1.6335 | 1.6335 | 1.6335 | 2.0005 | 2.3271 | 2.3271 | 2.3271 | 2.3271 | 2.3271
2020-03-26 09:00 | Summer | 1.2956 | 1.8542 | 2.6756 | 2.6756 | 2.6756 | 2.6756 | 0.83736 | 1.6561 | 1.6561 | 1.6561 | 1.6561 | 1.6561 | 2.1849 | 2.8195 | 3.2353 | 3.4542 | 3.8919 | 4.3296 | 0.83878 | 1.6555 | 1.9866 | 1.9866 | 1.9866 | 1.9866 | 2.0386 | 2.3715 | 2.3715 | 2.3715 | 2.3715 | 2.3715
2020-03-26 10:00 | Summer | 1.2765 | 1.8269 | 2.6363 | 2.6363 | 2.6363 | 2.6363 | 0.96373 | 1.906 | 1.906 | 1.906 | 1.906 | 1.906 | 2.3244 | 2.9996 | 3.442 | 3.6748 | 4.1404 | 4.6061 | 0.89166 | 1.7599 | 2.1118 | 2.1118 | 2.1118 | 2.1118 | 2.0386 | 2.3715 | 2.3715 | 2.3715 | 2.3715 | 2.3715
2020-03-26 11:00 | Summer | 1.5242 | 2.1814 | 3.1478 | 3.1478 | 3.1478 | 3.1478 | 0.97168 | 1.9217 | 1.9217 | 1.9217 | 1.9217 | 1.9217 | 2.4578 | 3.1717 | 3.6395 | 3.8856 | 4.378 | 4.8704 | 0.7621 | 1.5041 | 1.805 | 1.805 | 1.805 | 1.805 | 2.1339 | 2.4823 | 2.4823 | 2.4823 | 2.4823 | 2.4823
2020-03-26 12:00 | Summer | 1.5814 | 2.2632 | 3.2659 | 3.2659 | 3.2659 | 3.2659 | 0.90309 | 1.7861 | 1.7861 | 1.7861 | 1.7861 | 1.7861 | 2.3625 | 3.0488 | 3.4984 | 3.735 | 4.2083 | 4.6816 | 0.86498 | 1.7072 | 2.0486 | 2.0486 | 2.0486 | 2.0486 | 2.191 | 2.5488 | 2.5488 | 2.5488 | 2.5488 | 2.5488
2020-03-26 13:00 | Summer | 1.6004 | 2.2904 | 3.3052 | 3.3052 | 3.3052 | 3.3052 | 1.0774 | 2.1309 | 2.1309 | 2.1309 | 2.1309 | 2.1309 | 2.5149 | 3.2455 | 3.7241 | 3.976 | 4.4798 | 4.9836 | 0.76972 | 1.5192 | 1.823 | 1.823 | 1.823 | 1.823 | 2.2673 | 2.6374 | 2.6374 | 2.6374 | 2.6374 | 2.6374
2020-03-26 14:00 | Summer | 1.5623 | 2.2359 | 3.2265 | 3.2265 | 3.2265 | 3.2265 | 0.99168 | 1.9613 | 1.9613 | 1.9613 | 1.9613 | 1.9613 | 2.4197 | 3.1225 | 3.583 | 3.8254 | 4.3101 | 4.7949 | 0.73162 | 1.444 | 1.7328 | 1.7328 | 1.7328 | 1.7328 | 2.2101 | 2.5709 | 2.5709 | 2.5709 | 2.5709 | 2.5709
2020-03-26 15:00 | Summer | 1.5433 | 2.2086 | 3.1872 | 3.1872 | 3.1872 | 3.1872 | 1.0374 | 2.0517 | 2.0517 | 2.0517 | 2.0517 | 2.0517 | 2.4197 | 3.1225 | 3.583 | 3.8254 | 4.3101 | 4.7949 | 0.87261 | 1.7222 | 2.0667 | 2.0667 | 2.0667 | 2.0667 | 2.2291 | 2.5931 | 2.5931 | 2.5931 | 2.5931 | 2.5931
2020-03-26 16:00 | Summer | 1.5242 | 2.1814 | 3.1478 | 3.1478 | 3.1478 | 3.1478 | 1.0203 | 2.0178 | 2.0178 | 2.0178 | 2.0178 | 2.0178 | 2.4006 | 3.098 | 3.5548 | 3.7953 | 4.2762 | 4.7571 | 0.76972 | 1.5192 | 1.823 | 1.823 | 1.823 | 1.823 | 2.1148 | 2.4601 | 2.4601 | 2.4601 | 2.4601 | 2.4601
2020-03-26 17:00 | Summer | 1.467 | 2.0996 | 3.0298 | 3.0298 | 3.0298 | 3.0298 | 0.91166 | 1.803 | 1.803 | 1.803 | 1.803 | 1.803 | 2.4959 | 3.2209 | 3.6959 | 3.9459 | 4.4459 | 4.9459 | 0.73543 | 1.4515 | 1.7418 | 1.7418 | 1.7418 | 1.7418 | 1.9734 | 2.2955 | 2.2955 | 2.2955 | 2.2955 | 2.2955
2020-03-26 18:00 | Summer | 1.2003 | 1.7178 | 2.4789 | 2.4789 | 2.4789 | 2.4789 | 0.70535 | 1.395 | 1.395 | 1.395 | 1.395 | 1.395 | 2.2835 | 2.9468 | 3.3814 | 3.6101 | 4.0676 | 4.525 | 0.64779 | 1.2785 | 1.5342 | 1.5342 | 1.5342 | 1.5342 | 1.5378 | 1.7889 | 1.7889 | 1.7889 | 1.7889 | 1.7889
2020-03-26 19:00 | Summer | 0.724 | 1.0362 | 1.4952 | 1.4952 | 1.4952 | 1.4952 | 0.51156 | 1.0117 | 1.0117 | 1.0117 | 1.0117 | 1.0117 | 2.0789 | 2.6828 | 3.0784 | 3.2866 | 3.7031 | 4.1195 | 0.62873 | 1.2409 | 1.4891 | 1.4891 | 1.4891 | 1.4891 | 1.105 | 1.2855 | 1.2855 | 1.2855 | 1.2855 | 1.2855
2020-03-26 20:00 | Summer | 0.68589 | 0.98162 | 1.4165 | 1.4165 | 1.4165 | 1.4165 | 0.56872 | 1.1248 | 1.1248 | 1.1248 | 1.1248 | 1.1248 | 1.9624 | 2.5325 | 2.9059 | 3.1025 | 3.4956 | 3.8887 | 0.56395 | 1.1131 | 1.3357 | 1.3357 | 1.3357 | 1.3357 | 1.0669 | 1.2411 | 1.2411 | 1.2411 | 1.2411 | 1.2411
2020-03-26 21:00 | Summer | 0.64779 | 0.92709 | 1.3378 | 1.3378 | 1.3378 | 1.3378 | 0.42296 | 0.83652 | 0.83652 | 0.83652 | 0.83652 | 0.83652 | 1.8862 | 2.4341 | 2.7931 | 2.982 | 3.3599 | 3.7377 | 0.53728 | 1.0604 | 1.2725 | 1.2725 | 1.2725 | 1.2725 | 0.95314 | 1.1088 | 1.1088 | 1.1088 | 1.1088 | 1.1088
2020-03-26 22:00 | Summer | 0.62853 | 0.89952 | 1.298 | 1.298 | 1.298 | 1.298 | 0.46297 | 0.91565 | 0.91565 | 0.91565 | 0.91565 | 0.91565 | 1.8672 | 2.4095 | 2.7649 | 2.9519 | 3.3259 | 3.7 | 0.52966 | 1.0454 | 1.2545 | 1.2545 | 1.2545 | 1.2545 | 0.89547 | 1.0417 | 1.0417 | 1.0417 | 1.0417 | 1.0417
2020-03-26 23:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.33151 | 0.65565 | 0.65565 | 0.65565 | 0.65565 | 0.65565 | 1.7338 | 2.2374 | 2.5674 | 2.741 | 3.0884 | 3.4357 | 0.49918 | 0.98521 | 1.1823 | 1.1823 | 1.1823 | 1.1823 | 0.85737 | 0.99734 | 0.99734 | 0.99734 | 0.99734 | 0.99734
2020-03-27 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.33437 | 0.6613 | 0.6613 | 0.6613 | 0.6613 | 0.6613 | 1.6576 | 2.1391 | 2.4545 | 2.6205 | 2.9526 | 3.2847 | 0.49155 | 0.97017 | 1.1642 | 1.1642 | 1.1642 | 1.1642 | 0.83831 | 0.97518 | 0.97518 | 0.97518 | 0.97518 | 0.97518
2020-03-27 01:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.31151 | 0.61608 | 0.61608 | 0.61608 | 0.61608 | 0.61608 | 1.5433 | 1.9915 | 2.2852 | 2.4398 | 2.749 | 3.0581 | 0.4725 | 0.93257 | 1.1191 | 1.1191 | 1.1191 | 1.1191 | 0.81926 | 0.95302 | 0.95302 | 0.95302 | 0.95302 | 0.95302
2020-03-27 02:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.51442 | 1.0174 | 1.0174 | 1.0174 | 1.0174 | 1.0174 | 1.5242 | 1.967 | 2.257 | 2.4097 | 2.715 | 3.0204 | 0.5068 | 1.0003 | 1.2003 | 1.2003 | 1.2003 | 1.2003 | 0.83831 | 0.97518 | 0.97518 | 0.97518 | 0.97518 | 0.97518
2020-03-27 03:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.42868 | 0.84782 | 0.84782 | 0.84782 | 0.84782 | 0.84782 | 1.5433 | 1.9915 | 2.2852 | 2.4398 | 2.749 | 3.0581 | 0.49536 | 0.97769 | 1.1732 | 1.1732 | 1.1732 | 1.1732 | 0.81926 | 0.95302 | 0.95302 | 0.95302 | 0.95302 | 0.95302
2020-03-27 04:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.43439 | 0.85912 | 0.85912 | 0.85912 | 0.85912 | 0.85912 | 1.5402 | 1.9876 | 2.2807 | 2.435 | 2.7436 | 3.0521 | 0.6173 | 1.2184 | 1.462 | 1.462 | 1.462 | 1.462 | 0.8951 | 1.0412 | 1.0412 | 1.0412 | 1.0412 | 1.0412
2020-03-27 05:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.48012 | 0.94956 | 0.94956 | 0.94956 | 0.94956 | 0.94956 | 1.5814 | 2.0407 | 2.3417 | 2.5001 | 2.8169 | 3.1337 | 0.51442 | 1.0153 | 1.2184 | 1.2184 | 1.2184 | 1.2184 | 1.061 | 1.2343 | 1.2343 | 1.2343 | 1.2343 | 1.2343
2020-03-27 06:00 | Summer | 0.71368 | 1.0214 | 1.4739 | 1.4739 | 1.4739 | 1.4739 | 0.58015 | 1.1474 | 1.1474 | 1.1474 | 1.1474 | 1.1474 | 1.7528 | 2.262 | 2.5956 | 2.7712 | 3.1223 | 3.4734 | 0.71256 | 1.4064 | 1.6877 | 1.6877 | 1.6877 | 1.6877 | 1.4384 | 1.6733 | 1.6733 | 1.6733 | 1.6733 | 1.6733
2020-03-27 07:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.74019 | 1.4639 | 1.4639 | 1.4639 | 1.4639 | 1.4639 | 2.0001 | 2.5811 | 2.9618 | 3.1621 | 3.5628 | 3.9635 | 0.71256 | 1.4064 | 1.6877 | 1.6877 | 1.6877 | 1.6877 | 1.6536 | 1.9236 | 1.9236 | 1.9236 | 1.9236 | 1.9236
2020-03-27 08:00 | Summer | 1.3908 | 1.9905 | 2.8724 | 2.8724 | 2.8724 | 2.8724 | 0.79449 | 1.5713 | 1.5713 | 1.5713 | 1.5713 | 1.5713 | 2.0767 | 2.68 | 3.0752 | 3.2832 | 3.6992 | 4.1153 | 0.74305 | 1.4665 | 1.7599 | 1.7599 | 1.7599 | 1.7599 | 1.8669 | 2.1717 | 2.1717 | 2.1717 | 2.1717 | 2.1717
2020-03-27 09:00 | Summer | 1.3978 | 2.0005 | 2.8868 | 2.8868 | 2.8868 | 2.8868 | 0.88594 | 1.7522 | 1.7522 | 1.7522 | 1.7522 | 1.7522 | 2.2291 | 2.8767 | 3.3009 | 3.5242 | 3.9708 | 4.4173 | 0.75829 | 1.4966 | 1.796 | 1.796 | 1.796 | 1.796 | 1.9053 | 2.2163 | 2.2163 | 2.2163 | 2.2163 | 2.2163
2020-03-27 10:00 | Summer | 1.448 | 2.0723 | 2.9904 | 2.9904 | 2.9904 | 2.9904 | 0.85736 | 1.6956 | 1.6956 | 1.6956 | 1.6956 | 1.6956 | 2.2673 | 2.9258 | 3.3573 | 3.5844 | 4.0386 | 4.4928 | 0.86879 | 1.7147 | 2.0577 | 2.0577 | 2.0577 | 2.0577 | 1.9624 | 2.2828 | 2.2828 | 2.2828 | 2.2828 | 2.2828
2020-03-27 11:00 | Summer | 1.5433 | 2.2086 | 3.1872 | 3.1872 | 3.1872 | 3.1872 | 0.86308 | 1.707 | 1.707 | 1.707 | 1.707 | 1.707 | 2.3435 | 3.0242 | 3.4702 | 3.7049 | 4.1744 | 4.6438 | 0.88023 | 1.7373 | 2.0847 | 2.0847 | 2.0847 | 2.0847 | 1.9624 | 2.2828 | 2.2828 | 2.2828 | 2.2828 | 2.2828
2020-03-27 12:00 | Summer | 1.5242 | 2.1814 | 3.1478 | 3.1478 | 3.1478 | 3.1478 | 0.95453 | 1.8878 | 1.8878 | 1.8878 | 1.8878 | 1.8878 | 2.4006 | 3.098 | 3.5548 | 3.7953 | 4.2762 | 4.7571 | 0.73924 | 1.459 | 1.7508 | 1.7508 | 1.7508 | 1.7508 | 2.1529 | 2.5044 | 2.5044 | 2.5044 | 2.5044 | 2.5044
2020-03-27 13:00 | Summer | 1.5242 | 2.1814 | 3.1478 | 3.1478 | 3.1478 | 3.1478 | 0.9631 | 1.9048 | 1.9048 | 1.9048 | 1.9048 | 1.9048 | 2.4006 | 3.098 | 3.5548 | 3.7953 | 4.2762 | 4.7571 | 0.79258 | 1.5643 | 1.8772 | 1.8772 | 1.8772 | 1.8772 | 2.0958 | 2.4379 | 2.4379 | 2.4379 | 2.4379 | 2.4379
2020-03-27 14:00 | Summer | 1.5052 | 2.1541 | 3.1085 | 3.1085 | 3.1085 | 3.1085 | 0.98025 | 1.9387 | 1.9387 | 1.9387 | 1.9387 | 1.9387 | 2.3625 | 3.0488 | 3.4984 | 3.735 | 4.2083 | 4.6816 | 0.86498 | 1.7072 | 2.0486 | 2.0486 | 2.0486 | 2.0486 | 2.1529 | 2.5044 | 2.5044 | 2.5044 | 2.5044 | 2.5044
2020-03-27 15:00 | Summer | 1.5052 | 2.1541 | 3.1085 | 3.1085 | 3.1085 | 3.1085 | 0.91738 | 1.8143 | 1.8143 | 1.8143 | 1.8143 | 1.8143 | 2.3625 | 3.0488 | 3.4984 | 3.735 | 4.2083 | 4.6816 | 0.89166 | 1.7599 | 2.1118 | 2.1118 | 2.1118 | 2.1118 | 2.1339 | 2.4823 | 2.4823 | 2.4823 | 2.4823 | 2.4823
2020-03-27 16:00 | Summer | 1.448 | 2.0723 | 2.9904 | 2.9904 | 2.9904 | 2.9904 | 0.89451 | 1.7691 | 1.7691 | 1.7691 | 1.7691 | 1.7691 | 2.2456 | 2.8979 | 3.3253 | 3.5502 | 4.0001 | 4.45 | 0.85736 | 1.6922 | 2.0306 | 2.0306 | 2.0306 | 2.0306 | 2.0386 | 2.3715 | 2.3715 | 2.3715 | 2.3715 | 2.3715
2020-03-27 17:00 | Summer | 1.3718 | 1.9632 | 2.833 | 2.833 | 2.833 | 2.833 | 0.75448 | 1.4922 | 1.4922 | 1.4922 | 1.4922 | 1.4922 | 2.2101 | 2.8521 | 3.2727 | 3.4941 | 3.9368 | 4.3796 | 0.76591 | 1.5117 | 1.814 | 1.814 | 1.814 | 1.814 | 1.8969 | 2.2066 | 2.2066 | 2.2066 | 2.2066 | 2.2066
2020-03-27 18:00 | Summer | 0.98533 | 1.4102 | 2.0349 | 2.0349 | 2.0349 | 2.0349 | 0.70304 | 1.3904 | 1.3904 | 1.3904 | 1.3904 | 1.3904 | 2.1341 | 2.754 | 3.1602 | 3.3739 | 3.8014 | 4.229 | 0.65541 | 1.2936 | 1.5523 | 1.5523 | 1.5523 | 1.5523 | 1.5069 | 1.7529 | 1.7529 | 1.7529 | 1.7529 | 1.7529
2020-03-27 19:00 | Summer | 0.70494 | 1.0089 | 1.4559 | 1.4559 | 1.4559 | 1.4559 | 0.48298 | 0.95521 | 0.95521 | 0.95521 | 0.95521 | 0.95521 | 1.9768 | 2.5511 | 2.9273 | 3.1253 | 3.5213 | 3.9173 | 0.62111 | 1.2259 | 1.4711 | 1.4711 | 1.4711 | 1.4711 | 1.086 | 1.2633 | 1.2633 | 1.2633 | 1.2633 | 1.2633
2020-03-27 20:00 | Summer | 0.66415 | 0.9505 | 1.3716 | 1.3716 | 1.3716 | 1.3716 | 0.46583 | 0.9213 | 0.9213 | 0.9213 | 0.9213 | 0.9213 | 1.9243 | 2.4833 | 2.8495 | 3.0422 | 3.4277 | 3.8132 | 0.59716 | 1.1786 | 1.4143 | 1.4143 | 1.4143 | 1.4143 | 1.0669 | 1.2411 | 1.2411 | 1.2411 | 1.2411 | 1.2411
2020-03-27 21:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.44868 | 0.88738 | 0.88738 | 0.88738 | 0.88738 | 0.88738 | 1.8862 | 2.4341 | 2.7931 | 2.982 | 3.3599 | 3.7377 | 0.53347 | 1.0529 | 1.2635 | 1.2635 | 1.2635 | 1.2635 | 0.95263 | 1.1082 | 1.1082 | 1.1082 | 1.1082 | 1.1082
2020-03-27 22:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.43725 | 0.86478 | 0.86478 | 0.86478 | 0.86478 | 0.86478 | 1.8862 | 2.4341 | 2.7931 | 2.982 | 3.3599 | 3.7377 | 0.56395 | 1.1131 | 1.3357 | 1.3357 | 1.3357 | 1.3357 | 0.91452 | 1.0638 | 1.0638 | 1.0638 | 1.0638 | 1.0638
2020-03-27 23:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.43439 | 0.85912 | 0.85912 | 0.85912 | 0.85912 | 0.85912 | 1.7909 | 2.3112 | 2.652 | 2.8314 | 3.1902 | 3.549 | 0.52204 | 1.0303 | 1.2364 | 1.2364 | 1.2364 | 1.2364 | 0.83831 | 0.97518 | 0.97518 | 0.97518 | 0.97518 | 0.97518
2020-03-28 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.42868 | 0.84782 | 0.84782 | 0.84782 | 0.84782 | 0.84782 | 1.6385 | 2.1145 | 2.4263 | 2.5904 | 2.9187 | 3.2469 | 0.51061 | 1.0078 | 1.2093 | 1.2093 | 1.2093 | 1.2093 | 0.8198 | 0.95365 | 0.95365 | 0.95365 | 0.95365 | 0.95365
2020-03-28 01:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.39153 | 0.77434 | 0.77434 | 0.77434 | 0.77434 | 0.77434 | 1.5623 | 2.0161 | 2.3135 | 2.4699 | 2.7829 | 3.0959 | 0.53728 | 1.0604 | 1.2725 | 1.2725 | 1.2725 | 1.2725 | 0.81926 | 0.95302 | 0.95302 | 0.95302 | 0.95302 | 0.95302
2020-03-28 02:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.40582 | 0.8026 | 0.8026 | 0.8026 | 0.8026 | 0.8026 | 1.5814 | 2.0407 | 2.3417 | 2.5001 | 2.8169 | 3.1337 | 0.45345 | 0.89497 | 1.074 | 1.074 | 1.074 | 1.074 | 0.81926 | 0.95302 | 0.95302 | 0.95302 | 0.95302 | 0.95302
2020-03-28 03:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.46583 | 0.9213 | 0.9213 | 0.9213 | 0.9213 | 0.9213 | 1.5249 | 1.9678 | 2.258 | 2.4108 | 2.7162 | 3.0217 | 0.44583 | 0.87992 | 1.0559 | 1.0559 | 1.0559 | 1.0559 | 0.78703 | 0.91553 | 0.91553 | 0.91553 | 0.91553 | 0.91553
2020-03-28 04:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.39724 | 0.78565 | 0.78565 | 0.78565 | 0.78565 | 0.78565 | 1.6004 | 2.0653 | 2.3699 | 2.5302 | 2.8508 | 3.1714 | 0.46107 | 0.91001 | 1.092 | 1.092 | 1.092 | 1.092 | 0.81926 | 0.95302 | 0.95302 | 0.95302 | 0.95302 | 0.95302
2020-03-28 05:00 | Summer | 0.55252 | 0.79075 | 1.1411 | 1.1411 | 1.1411 | 1.1411 | 0.40296 | 0.79695 | 0.79695 | 0.79695 | 0.79695 | 0.79695 | 1.6004 | 2.0653 | 2.3699 | 2.5302 | 2.8508 | 3.1714 | 0.52204 | 1.0303 | 1.2364 | 1.2364 | 1.2364 | 1.2364 | 0.83425 | 0.97045 | 0.97045 | 0.97045 | 0.97045 | 0.97045
2020-03-28 06:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.45154 | 0.89304 | 0.89304 | 0.89304 | 0.89304 | 0.89304 | 1.6195 | 2.0899 | 2.3981 | 2.5603 | 2.8847 | 3.2092 | 0.52966 | 1.0454 | 1.2545 | 1.2545 | 1.2545 | 1.2545 | 0.88993 | 1.0352 | 1.0352 | 1.0352 | 1.0352 | 1.0352
2020-03-28 07:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.50298 | 0.99478 | 0.99478 | 0.99478 | 0.99478 | 0.99478 | 1.6766 | 2.1636 | 2.4827 | 2.6507 | 2.9865 | 3.3224 | 0.49918 | 0.98521 | 1.1823 | 1.1823 | 1.1823 | 1.1823 | 0.99073 | 1.1525 | 1.1525 | 1.1525 | 1.1525 | 1.1525
2020-03-28 08:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.55707 | 1.1017 | 1.1017 | 1.1017 | 1.1017 | 1.1017 | 1.7528 | 2.262 | 2.5956 | 2.7712 | 3.1223 | 3.4734 | 0.51061 | 1.0078 | 1.2093 | 1.2093 | 1.2093 | 1.2093 | 0.97168 | 1.1303 | 1.1303 | 1.1303 | 1.1303 | 1.1303
2020-03-28 09:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.6373 | 1.2604 | 1.2604 | 1.2604 | 1.2604 | 1.2604 | 1.7909 | 2.3112 | 2.652 | 2.8314 | 3.1902 | 3.549 | 0.70875 | 1.3989 | 1.6786 | 1.6786 | 1.6786 | 1.6786 | 0.99973 | 1.1629 | 1.1629 | 1.1629 | 1.1629 | 1.1629
2020-03-28 10:00 | Summer | 0.68589 | 0.98162 | 1.4165 | 1.4165 | 1.4165 | 1.4165 | 0.51156 | 1.0117 | 1.0117 | 1.0117 | 1.0117 | 1.0117 | 1.9053 | 2.4587 | 2.8213 | 3.0121 | 3.3938 | 3.7755 | 0.66684 | 1.3161 | 1.5794 | 1.5794 | 1.5794 | 1.5794 | 1.0288 | 1.1968 | 1.1968 | 1.1968 | 1.1968 | 1.1968
2020-03-28 11:00 | Summer | 0.64779 | 0.92709 | 1.3378 | 1.3378 | 1.3378 | 1.3378 | 0.44297 | 0.87608 | 0.87608 | 0.87608 | 0.87608 | 0.87608 | 1.9226 | 2.4811 | 2.847 | 3.0395 | 3.4247 | 3.8098 | 0.78496 | 1.5493 | 1.8591 | 1.8591 | 1.8591 | 1.8591 | 1.086 | 1.2633 | 1.2633 | 1.2633 | 1.2633 | 1.2633
2020-03-28 12:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.42868 | 0.84782 | 0.84782 | 0.84782 | 0.84782 | 0.84782 | 1.9243 | 2.4833 | 2.8495 | 3.0422 | 3.4277 | 3.8132 | 0.67065 | 1.3236 | 1.5884 | 1.5884 | 1.5884 | 1.5884 | 1.0479 | 1.219 | 1.219 | 1.219 | 1.219 | 1.219
2020-03-28 13:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.41725 | 0.82521 | 0.82521 | 0.82521 | 0.82521 | 0.82521 | 1.9053 | 2.4587 | 2.8213 | 3.0121 | 3.3938 | 3.7755 | 0.75448 | 1.4891 | 1.7869 | 1.7869 | 1.7869 | 1.7869 | 0.97168 | 1.1303 | 1.1303 | 1.1303 | 1.1303 | 1.1303
2020-03-28 14:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.41725 | 0.82521 | 0.82521 | 0.82521 | 0.82521 | 0.82521 | 1.8481 | 2.3849 | 2.7366 | 2.9218 | 3.292 | 3.6622 | 0.70113 | 1.3838 | 1.6606 | 1.6606 | 1.6606 | 1.6606 | 0.99073 | 1.1525 | 1.1525 | 1.1525 | 1.1525 | 1.1525
2020-03-28 15:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.43725 | 0.86478 | 0.86478 | 0.86478 | 0.86478 | 0.86478 | 1.9053 | 2.4587 | 2.8213 | 3.0121 | 3.3938 | 3.7755 | 0.72018 | 1.4214 | 1.7057 | 1.7057 | 1.7057 | 1.7057 | 0.97168 | 1.1303 | 1.1303 | 1.1303 | 1.1303 | 1.1303
2020-03-28 16:00 | Summer | 0.64779 | 0.92709 | 1.3378 | 1.3378 | 1.3378 | 1.3378 | 0.44011 | 0.87043 | 0.87043 | 0.87043 | 0.87043 | 0.87043 | 1.9239 | 2.4828 | 2.8489 | 3.0416 | 3.427 | 3.8125 | 0.63635 | 1.256 | 1.5072 | 1.5072 | 1.5072 | 1.5072 | 0.93358 | 1.086 | 1.086 | 1.086 | 1.086 | 1.086
2020-03-28 17:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.47726 | 0.94391 | 0.94391 | 0.94391 | 0.94391 | 0.94391 | 1.9624 | 2.5325 | 2.9059 | 3.1025 | 3.4956 | 3.8887 | 0.6516 | 1.286 | 1.5433 | 1.5433 | 1.5433 | 1.5433 | 0.89547 | 1.0417 | 1.0417 | 1.0417 | 1.0417 | 1.0417
2020-03-28 18:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.40867 | 0.80825 | 0.80825 | 0.80825 | 0.80825 | 0.80825 | 1.8672 | 2.4095 | 2.7649 | 2.9519 | 3.3259 | 3.7 | 0.67446 | 1.3312 | 1.5974 | 1.5974 | 1.5974 | 1.5974 | 0.85737 | 0.99734 | 0.99734 | 0.99734 | 0.99734 | 0.99734
2020-03-28 19:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.36866 | 0.72912 | 0.72912 | 0.72912 | 0.72912 | 0.72912 | 1.9053 | 2.4587 | 2.8213 | 3.0121 | 3.3938 | 3.7755 | 0.60206 | 1.1883 | 1.4259 | 1.4259 | 1.4259 | 1.4259 | 0.91452 | 1.0638 | 1.0638 | 1.0638 | 1.0638 | 1.0638
2020-03-28 20:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.35723 | 0.70652 | 0.70652 | 0.70652 | 0.70652 | 0.70652 | 1.9053 | 2.4587 | 2.8213 | 3.0121 | 3.3938 | 3.7755 | 0.62111 | 1.2259 | 1.4711 | 1.4711 | 1.4711 | 1.4711 | 0.87642 | 1.0195 | 1.0195 | 1.0195 | 1.0195 | 1.0195
2020-03-28 21:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.41725 | 0.82521 | 0.82521 | 0.82521 | 0.82521 | 0.82521 | 1.9053 | 2.4587 | 2.8213 | 3.0121 | 3.3938 | 3.7755 | 0.54109 | 1.0679 | 1.2815 | 1.2815 | 1.2815 | 1.2815 | 0.83831 | 0.97518 | 0.97518 | 0.97518 | 0.97518 | 0.97518
2020-03-28 22:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.39153 | 0.77434 | 0.77434 | 0.77434 | 0.77434 | 0.77434 | 1.8672 | 2.4095 | 2.7649 | 2.9519 | 3.3259 | 3.7 | 0.55633 | 1.098 | 1.3176 | 1.3176 | 1.3176 | 1.3176 | 0.81926 | 0.95302 | 0.95302 | 0.95302 | 0.95302 | 0.95302
2020-03-28 23:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.34008 | 0.6726 | 0.6726 | 0.6726 | 0.6726 | 0.6726 | 1.7528 | 2.262 | 2.5956 | 2.7712 | 3.1223 | 3.4734 | 0.5068 | 1.0003 | 1.2003 | 1.2003 | 1.2003 | 1.2003 | 0.80021 | 0.93085 | 0.93085 | 0.93085 | 0.93085 | 0.93085
2020-03-29 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.37152 | 0.73478 | 0.73478 | 0.73478 | 0.73478 | 0.73478 | 1.6385 | 2.1145 | 2.4263 | 2.5904 | 2.9187 | 3.2469 | 0.46869 | 0.92505 | 1.1101 | 1.1101 | 1.1101 | 1.1101 | 0.80021 | 0.93085 | 0.93085 | 0.93085 | 0.93085 | 0.93085
2020-03-29 01:00 | Summer | 0.57757 | 0.82659 | 1.1928 | 1.1928 | 1.1928 | 1.1928 | 0.37724 | 0.74608 | 0.74608 | 0.74608 | 0.74608 | 0.74608 | 1.5623 | 2.0161 | 2.3135 | 2.4699 | 2.7829 | 3.0959 | 0.46869 | 0.92505 | 1.1101 | 1.1101 | 1.1101 | 1.1101 | 0.80021 | 0.93085 | 0.93085 | 0.93085 | 0.93085 | 0.93085
2020-03-29 02:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.37724 | 0.74608 | 0.74608 | 0.74608 | 0.74608 | 0.74608 | 1.6385 | 2.1145 | 2.4263 | 2.5904 | 2.9187 | 3.2469 | 0.52966 | 1.0454 | 1.2545 | 1.2545 | 1.2545 | 1.2545 | 0.81926 | 0.95302 | 0.95302 | 0.95302 | 0.95302 | 0.95302
2020-03-29 03:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.37724 | 0.74608 | 0.74608 | 0.74608 | 0.74608 | 0.74608 | 1.5623 | 2.0161 | 2.3135 | 2.4699 | 2.7829 | 3.0959 | 0.45345 | 0.89497 | 1.074 | 1.074 | 1.074 | 1.074 | 0.80021 | 0.93085 | 0.93085 | 0.93085 | 0.93085 | 0.93085
2020-03-29 04:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.38295 | 0.75738 | 0.75738 | 0.75738 | 0.75738 | 0.75738 | 1.5623 | 2.0161 | 2.3135 | 2.4699 | 2.7829 | 3.0959 | 0.49155 | 0.97017 | 1.1642 | 1.1642 | 1.1642 | 1.1642 | 0.81926 | 0.95302 | 0.95302 | 0.95302 | 0.95302 | 0.95302
2020-03-29 05:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.34008 | 0.6726 | 0.6726 | 0.6726 | 0.6726 | 0.6726 | 1.6004 | 2.0653 | 2.3699 | 2.5302 | 2.8508 | 3.1714 | 0.46107 | 0.91001 | 1.092 | 1.092 | 1.092 | 1.092 | 0.80021 | 0.93085 | 0.93085 | 0.93085 | 0.93085 | 0.93085
2020-03-29 06:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.38867 | 0.76869 | 0.76869 | 0.76869 | 0.76869 | 0.76869 | 1.6004 | 2.0653 | 2.3699 | 2.5302 | 2.8508 | 3.1714 | 0.53347 | 1.0529 | 1.2635 | 1.2635 | 1.2635 | 1.2635 | 0.82702 | 0.96205 | 0.96205 | 0.96205 | 0.96205 | 0.96205
2020-03-29 07:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.47441 | 0.93825 | 0.93825 | 0.93825 | 0.93825 | 0.93825 | 1.7325 | 2.2358 | 2.5655 | 2.739 | 3.0861 | 3.4332 | 0.54871 | 1.083 | 1.2996 | 1.2996 | 1.2996 | 1.2996 | 0.83831 | 0.97518 | 0.97518 | 0.97518 | 0.97518 | 0.97518
2020-03-29 08:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.40582 | 0.8026 | 0.8026 | 0.8026 | 0.8026 | 0.8026 | 1.7528 | 2.262 | 2.5956 | 2.7712 | 3.1223 | 3.4734 | 0.56014 | 1.1055 | 1.3267 | 1.3267 | 1.3267 | 1.3267 | 0.83831 | 0.97518 | 0.97518 | 0.97518 | 0.97518 | 0.97518
2020-03-29 09:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.44868 | 0.88738 | 0.88738 | 0.88738 | 0.88738 | 0.88738 | 1.8481 | 2.3849 | 2.7366 | 2.9218 | 3.292 | 3.6622 | 0.66303 | 1.3086 | 1.5703 | 1.5703 | 1.5703 | 1.5703 | 0.83831 | 0.97518 | 0.97518 | 0.97518 | 0.97518 | 0.97518
2020-03-29 10:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.38581 | 0.76304 | 0.76304 | 0.76304 | 0.76304 | 0.76304 | 1.8862 | 2.4341 | 2.7931 | 2.982 | 3.3599 | 3.7377 | 0.73162 | 1.444 | 1.7328 | 1.7328 | 1.7328 | 1.7328 | 0.85737 | 0.99734 | 0.99734 | 0.99734 | 0.99734 | 0.99734
2020-03-29 11:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.38867 | 0.76869 | 0.76869 | 0.76869 | 0.76869 | 0.76869 | 1.8862 | 2.4341 | 2.7931 | 2.982 | 3.3599 | 3.7377 | 0.724 | 1.4289 | 1.7147 | 1.7147 | 1.7147 | 1.7147 | 0.83831 | 0.97518 | 0.97518 | 0.97518 | 0.97518 | 0.97518
2020-03-29 12:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.40582 | 0.8026 | 0.8026 | 0.8026 | 0.8026 | 0.8026 | 1.9434 | 2.5079 | 2.8777 | 3.0724 | 3.4617 | 3.851 | 0.71637 | 1.4139 | 1.6967 | 1.6967 | 1.6967 | 1.6967 | 0.95263 | 1.1082 | 1.1082 | 1.1082 | 1.1082 | 1.1082
2020-03-29 13:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.38867 | 0.76869 | 0.76869 | 0.76869 | 0.76869 | 0.76869 | 1.9815 | 2.557 | 2.9341 | 3.1326 | 3.5296 | 3.9265 | 0.69732 | 1.3763 | 1.6516 | 1.6516 | 1.6516 | 1.6516 | 0.95263 | 1.1082 | 1.1082 | 1.1082 | 1.1082 | 1.1082
2020-03-29 14:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.46012 | 0.90999 | 0.90999 | 0.90999 | 0.90999 | 0.90999 | 1.9815 | 2.557 | 2.9341 | 3.1326 | 3.5296 | 3.9265 | 0.70113 | 1.3838 | 1.6606 | 1.6606 | 1.6606 | 1.6606 | 0.91452 | 1.0638 | 1.0638 | 1.0638 | 1.0638 | 1.0638
2020-03-29 15:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.49441 | 0.97782 | 0.97782 | 0.97782 | 0.97782 | 0.97782 | 2.0767 | 2.68 | 3.0752 | 3.2832 | 3.6992 | 4.1153 | 0.74686 | 1.4741 | 1.7689 | 1.7689 | 1.7689 | 1.7689 | 0.85737 | 0.99734 | 0.99734 | 0.99734 | 0.99734 | 0.99734
2020-03-29 16:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.42011 | 0.83086 | 0.83086 | 0.83086 | 0.83086 | 0.83086 | 2.0386 | 2.6308 | 3.0188 | 3.223 | 3.6314 | 4.0398 | 0.69732 | 1.3763 | 1.6516 | 1.6516 | 1.6516 | 1.6516 | 0.91452 | 1.0638 | 1.0638 | 1.0638 | 1.0638 | 1.0638
2020-03-29 17:00 | Summer | 0.62639 | 0.89646 | 1.2936 | 1.2936 | 1.2936 | 1.2936 | 0.40346 | 0.79795 | 0.79795 | 0.79795 | 0.79795 | 0.79795 | 2.0016 | 2.583 | 2.9639 | 3.1644 | 3.5654 | 3.9663 | 0.73487 | 1.4504 | 1.7405 | 1.7405 | 1.7405 | 1.7405 | 0.87642 | 1.0195 | 1.0195 | 1.0195 | 1.0195 | 1.0195
2020-03-29 18:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.48298 | 0.95521 | 0.95521 | 0.95521 | 0.95521 | 0.95521 | 1.9624 | 2.5325 | 2.9059 | 3.1025 | 3.4956 | 3.8887 | 0.75829 | 1.4966 | 1.796 | 1.796 | 1.796 | 1.796 | 0.89547 | 1.0417 | 1.0417 | 1.0417 | 1.0417 | 1.0417
2020-03-29 19:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.40296 | 0.79695 | 0.79695 | 0.79695 | 0.79695 | 0.79695 | 1.9624 | 2.5325 | 2.9059 | 3.1025 | 3.4956 | 3.8887 | 0.6516 | 1.286 | 1.5433 | 1.5433 | 1.5433 | 1.5433 | 0.91452 | 1.0638 | 1.0638 | 1.0638 | 1.0638 | 1.0638
2020-03-29 20:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.39438 | 0.77999 | 0.77999 | 0.77999 | 0.77999 | 0.77999 | 1.9053 | 2.4587 | 2.8213 | 3.0121 | 3.3938 | 3.7755 | 0.6516 | 1.286 | 1.5433 | 1.5433 | 1.5433 | 1.5433 | 0.91452 | 1.0638 | 1.0638 | 1.0638 | 1.0638 | 1.0638
2020-03-29 21:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.39438 | 0.77999 | 0.77999 | 0.77999 | 0.77999 | 0.77999 | 1.8672 | 2.4095 | 2.7649 | 2.9519 | 3.3259 | 3.7 | 0.60206 | 1.1883 | 1.4259 | 1.4259 | 1.4259 | 1.4259 | 0.86416 | 1.0052 | 1.0052 | 1.0052 | 1.0052 | 1.0052
2020-03-29 22:00 | Summer | 0.64779 | 0.92709 | 1.3378 | 1.3378 | 1.3378 | 1.3378 | 0.40582 | 0.8026 | 0.8026 | 0.8026 | 0.8026 | 0.8026 | 1.81 | 2.3358 | 2.6802 | 2.8615 | 3.2241 | 3.5867 | 0.63254 | 1.2484 | 1.4981 | 1.4981 | 1.4981 | 1.4981 | 0.83831 | 0.97518 | 0.97518 | 0.97518 | 0.97518 | 0.97518
2020-03-29 23:00 | Summer | 0.59147 | 0.84649 | 1.2215 | 1.2215 | 1.2215 | 1.2215 | 0.37438 | 0.74043 | 0.74043 | 0.74043 | 0.74043 | 0.74043 | 1.7909 | 2.3112 | 2.652 | 2.8314 | 3.1902 | 3.549 | 0.59444 | 1.1732 | 1.4079 | 1.4079 | 1.4079 | 1.4079 | 0.81926 | 0.95302 | 0.95302 | 0.95302 | 0.95302 | 0.95302
2020-03-30 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.38581 | 0.76304 | 0.76304 | 0.76304 | 0.76304 | 0.76304 | 1.6576 | 2.1391 | 2.4545 | 2.6205 | 2.9526 | 3.2847 | 0.49155 | 0.97017 | 1.1642 | 1.1642 | 1.1642 | 1.1642 | 0.78115 | 0.90869 | 0.90869 | 0.90869 | 0.90869 | 0.90869
2020-03-30 01:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.36581 | 0.72347 | 0.72347 | 0.72347 | 0.72347 | 0.72347 | 1.6004 | 2.0653 | 2.3699 | 2.5302 | 2.8508 | 3.1714 | 0.46869 | 0.92505 | 1.1101 | 1.1101 | 1.1101 | 1.1101 | 0.80021 | 0.93085 | 0.93085 | 0.93085 | 0.93085 | 0.93085
2020-03-30 02:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.46012 | 0.90999 | 0.90999 | 0.90999 | 0.90999 | 0.90999 | 1.6385 | 2.1145 | 2.4263 | 2.5904 | 2.9187 | 3.2469 | 0.49663 | 0.98019 | 1.1762 | 1.1762 | 1.1762 | 1.1762 | 0.78115 | 0.90869 | 0.90869 | 0.90869 | 0.90869 | 0.90869
2020-03-30 03:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.42296 | 0.83652 | 0.83652 | 0.83652 | 0.83652 | 0.83652 | 1.6385 | 2.1145 | 2.4263 | 2.5904 | 2.9187 | 3.2469 | 0.50299 | 0.99273 | 1.1913 | 1.1913 | 1.1913 | 1.1913 | 0.83831 | 0.97518 | 0.97518 | 0.97518 | 0.97518 | 0.97518
2020-03-30 04:00 | Summer | 0.78115 | 1.118 | 1.6133 | 1.6133 | 1.6133 | 1.6133 | 0.42868 | 0.84782 | 0.84782 | 0.84782 | 0.84782 | 0.84782 | 1.6576 | 2.1391 | 2.4545 | 2.6205 | 2.9526 | 3.2847 | 0.48393 | 0.95513 | 1.1462 | 1.1462 | 1.1462 | 1.1462 | 0.87201 | 1.0144 | 1.0144 | 1.0144 | 1.0144 | 1.0144
2020-03-30 05:00 | Summer | 0.87642 | 1.2543 | 1.81 | 1.81 | 1.81 | 1.81 | 0.55157 | 1.0909 | 1.0909 | 1.0909 | 1.0909 | 1.0909 | 1.6957 | 2.1882 | 2.5109 | 2.6808 | 3.0205 | 3.3602 | 0.54109 | 1.0679 | 1.2815 | 1.2815 | 1.2815 | 1.2815 | 1.105 | 1.2855 | 1.2855 | 1.2855 | 1.2855 | 1.2855
2020-03-30 06:00 | Summer | 0.85737 | 1.227 | 1.7706 | 1.7706 | 1.7706 | 1.7706 | 0.6716 | 1.3283 | 1.3283 | 1.3283 | 1.3283 | 1.3283 | 1.8481 | 2.3849 | 2.7366 | 2.9218 | 3.292 | 3.6622 | 0.57539 | 1.1356 | 1.3628 | 1.3628 | 1.3628 | 1.3628 | 1.2946 | 1.5059 | 1.5059 | 1.5059 | 1.5059 | 1.5059
2020-03-30 07:00 | Summer | 1.4861 | 2.1268 | 3.0691 | 3.0691 | 3.0691 | 3.0691 | 0.73447 | 1.4526 | 1.4526 | 1.4526 | 1.4526 | 1.4526 | 2.0767 | 2.68 | 3.0752 | 3.2832 | 3.6992 | 4.1153 | 0.61349 | 1.2108 | 1.453 | 1.453 | 1.453 | 1.453 | 1.6957 | 1.9725 | 1.9725 | 1.9725 | 1.9725 | 1.9725
2020-03-30 08:00 | Summer | 1.4861 | 2.1268 | 3.0691 | 3.0691 | 3.0691 | 3.0691 | 0.87165 | 1.7239 | 1.7239 | 1.7239 | 1.7239 | 1.7239 | 2.1539 | 2.7795 | 3.1894 | 3.4051 | 3.8366 | 4.2681 | 0.6516 | 1.286 | 1.5433 | 1.5433 | 1.5433 | 1.5433 | 2.0196 | 2.3493 | 2.3493 | 2.3493 | 2.3493 | 2.3493
2020-03-30 09:00 | Summer | 1.467 | 2.0996 | 3.0298 | 3.0298 | 3.0298 | 3.0298 | 0.98211 | 1.9424 | 1.9424 | 1.9424 | 1.9424 | 1.9424 | 2.2291 | 2.8767 | 3.3009 | 3.5242 | 3.9708 | 4.4173 | 0.80749 | 1.5937 | 1.9125 | 1.9125 | 1.9125 | 1.9125 | 1.9815 | 2.305 | 2.305 | 2.305 | 2.305 | 2.305
2020-03-30 10:00 | Summer | 1.467 | 2.0996 | 3.0298 | 3.0298 | 3.0298 | 3.0298 | 0.99168 | 1.9613 | 1.9613 | 1.9613 | 1.9613 | 1.9613 | 2.3435 | 3.0242 | 3.4702 | 3.7049 | 4.1744 | 4.6438 | 0.82688 | 1.632 | 1.9584 | 1.9584 | 1.9584 | 1.9584 | 1.9611 | 2.2813 | 2.2813 | 2.2813 | 2.2813 | 2.2813
2020-03-30 11:00 | Summer | 1.5052 | 2.1541 | 3.1085 | 3.1085 | 3.1085 | 3.1085 | 1.1746 | 2.323 | 2.323 | 2.323 | 2.323 | 2.323 | 2.3625 | 3.0488 | 3.4984 | 3.735 | 4.2083 | 4.6816 | 0.80021 | 1.5794 | 1.8952 | 1.8952 | 1.8952 | 1.8952 | 2.0005 | 2.3271 | 2.3271 | 2.3271 | 2.3271 | 2.3271
2020-03-30 12:00 | Summer | 1.467 | 2.0996 | 3.0298 | 3.0298 | 3.0298 | 3.0298 | 0.99168 | 1.9613 | 1.9613 | 1.9613 | 1.9613 | 1.9613 | 2.4387 | 3.1471 | 3.6112 | 3.8555 | 4.3441 | 4.8326 | 0.79258 | 1.5643 | 1.8772 | 1.8772 | 1.8772 | 1.8772 | 2.1529 | 2.5044 | 2.5044 | 2.5044 | 2.5044 | 2.5044
2020-03-30 13:00 | Summer | 1.5052 | 2.1541 | 3.1085 | 3.1085 | 3.1085 | 3.1085 | 1.0517 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.5149 | 3.2455 | 3.7241 | 3.976 | 4.4798 | 4.9836 | 0.74305 | 1.4665 | 1.7599 | 1.7599 | 1.7599 | 1.7599 | 2.1307 | 2.4786 | 2.4786 | 2.4786 | 2.4786 | 2.4786
2020-03-30 14:00 | Summer | 1.6957 | 2.4268 | 3.5019 | 3.5019 | 3.5019 | 3.5019 | 1.066 | 2.1083 | 2.1083 | 2.1083 | 2.1083 | 2.1083 | 2.5911 | 3.3438 | 3.8369 | 4.0965 | 4.6156 | 5.1347 | 0.75067 | 1.4816 | 1.7779 | 1.7779 | 1.7779 | 1.7779 | 2.3054 | 2.6817 | 2.6817 | 2.6817 | 2.6817 | 2.6817
2020-03-30 15:00 | Summer | 1.5814 | 2.2632 | 3.2659 | 3.2659 | 3.2659 | 3.2659 | 1.0031 | 1.9839 | 1.9839 | 1.9839 | 1.9839 | 1.9839 | 2.5911 | 3.3438 | 3.8369 | 4.0965 | 4.6156 | 5.1347 | 0.72018 | 1.4214 | 1.7057 | 1.7057 | 1.7057 | 1.7057 | 2.2482 | 2.6153 | 2.6153 | 2.6153 | 2.6153 | 2.6153
2020-03-30 16:00 | Summer | 1.5814 | 2.2632 | 3.2659 | 3.2659 | 3.2659 | 3.2659 | 0.99454 | 1.967 | 1.967 | 1.967 | 1.967 | 1.967 | 2.6483 | 3.4176 | 3.9216 | 4.1869 | 4.7174 | 5.2479 | 0.70494 | 1.3913 | 1.6696 | 1.6696 | 1.6696 | 1.6696 | 2.2482 | 2.6153 | 2.6153 | 2.6153 | 2.6153 | 2.6153
2020-03-30 17:00 | Summer | 1.5242 | 2.1814 | 3.1478 | 3.1478 | 3.1478 | 3.1478 | 0.9631 | 1.9048 | 1.9048 | 1.9048 | 1.9048 | 1.9048 | 2.7245 | 3.5159 | 4.0344 | 4.3073 | 4.8531 | 5.3989 | 0.64016 | 1.2635 | 1.5162 | 1.5162 | 1.5162 | 1.5162 | 2.1031 | 2.4464 | 2.4464 | 2.4464 | 2.4464 | 2.4464
2020-03-30 18:00 | Summer | 1.1623 | 1.6635 | 2.4005 | 2.4005 | 2.4005 | 2.4005 | 0.7259 | 1.4356 | 1.4356 | 1.4356 | 1.4356 | 1.4356 | 2.5263 | 3.2602 | 3.741 | 3.994 | 4.5001 | 5.0062 | 0.64397 | 1.271 | 1.5252 | 1.5252 | 1.5252 | 1.5252 | 1.668 | 1.9404 | 1.9404 | 1.9404 | 1.9404 | 1.9404
2020-03-30 19:00 | Summer | 0.74305 | 1.0634 | 1.5346 | 1.5346 | 1.5346 | 1.5346 | 0.58417 | 1.1554 | 1.1554 | 1.1554 | 1.1554 | 1.1554 | 2.1757 | 2.8078 | 3.2218 | 3.4398 | 3.8756 | 4.3115 | 0.62492 | 1.2334 | 1.4801 | 1.4801 | 1.4801 | 1.4801 | 1.1622 | 1.352 | 1.352 | 1.352 | 1.352 | 1.352
2020-03-30 20:00 | Summer | 0.63313 | 0.9061 | 1.3075 | 1.3075 | 1.3075 | 1.3075 | 0.44011 | 0.87043 | 0.87043 | 0.87043 | 0.87043 | 0.87043 | 2.1148 | 2.7291 | 3.1316 | 3.3435 | 3.7671 | 4.1908 | 0.57157 | 1.1281 | 1.3537 | 1.3537 | 1.3537 | 1.3537 | 1.0927 | 1.2711 | 1.2711 | 1.2711 | 1.2711 | 1.2711
2020-03-30 21:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.42296 | 0.83652 | 0.83652 | 0.83652 | 0.83652 | 0.83652 | 1.9434 | 2.5079 | 2.8777 | 3.0724 | 3.4617 | 3.851 | 0.52966 | 1.0454 | 1.2545 | 1.2545 | 1.2545 | 1.2545 | 1.0068 | 1.1712 | 1.1712 | 1.1712 | 1.1712 | 1.1712
2020-03-30 22:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.44868 | 0.88738 | 0.88738 | 0.88738 | 0.88738 | 0.88738 | 1.8492 | 2.3864 | 2.7383 | 2.9236 | 3.294 | 3.6645 | 0.53347 | 1.0529 | 1.2635 | 1.2635 | 1.2635 | 1.2635 | 0.91452 | 1.0638 | 1.0638 | 1.0638 | 1.0638 | 1.0638
2020-03-30 23:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.40296 | 0.79695 | 0.79695 | 0.79695 | 0.79695 | 0.79695 | 1.7909 | 2.3112 | 2.652 | 2.8314 | 3.1902 | 3.549 | 0.5068 | 1.0003 | 1.2003 | 1.2003 | 1.2003 | 1.2003 | 0.91452 | 1.0638 | 1.0638 | 1.0638 | 1.0638 | 1.0638
2020-03-31 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.41725 | 0.82521 | 0.82521 | 0.82521 | 0.82521 | 0.82521 | 1.7147 | 2.2128 | 2.5392 | 2.7109 | 3.0544 | 3.3979 | 0.44583 | 0.87992 | 1.0559 | 1.0559 | 1.0559 | 1.0559 | 0.87642 | 1.0195 | 1.0195 | 1.0195 | 1.0195 | 1.0195
2020-03-31 01:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.41725 | 0.82521 | 0.82521 | 0.82521 | 0.82521 | 0.82521 | 1.6195 | 2.0899 | 2.3981 | 2.5603 | 2.8847 | 3.2092 | 0.46107 | 0.91001 | 1.092 | 1.092 | 1.092 | 1.092 | 0.83831 | 0.97518 | 0.97518 | 0.97518 | 0.97518 | 0.97518
2020-03-31 02:00 | Summer | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.43439 | 0.85912 | 0.85912 | 0.85912 | 0.85912 | 0.85912 | 1.5623 | 2.0161 | 2.3135 | 2.4699 | 2.7829 | 3.0959 | 0.45345 | 0.89497 | 1.074 | 1.074 | 1.074 | 1.074 | 0.85737 | 0.99734 | 0.99734 | 0.99734 | 0.99734 | 0.99734
2020-03-31 03:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.43439 | 0.85912 | 0.85912 | 0.85912 | 0.85912 | 0.85912 | 1.5623 | 2.0161 | 2.3135 | 2.4699 | 2.7829 | 3.0959 | 0.44964 | 0.88744 | 1.0649 | 1.0649 | 1.0649 | 1.0649 | 0.81477 | 0.94779 | 0.94779 | 0.94779 | 0.94779 | 0.94779
2020-03-31 04:00 | Summer | 0.6089 | 0.87143 | 1.2575 | 1.2575 | 1.2575 | 1.2575 | 0.38867 | 0.76869 | 0.76869 | 0.76869 | 0.76869 | 0.76869 | 1.6004 | 2.0653 | 2.3699 | 2.5302 | 2.8508 | 3.1714 | 0.44583 | 0.87992 | 1.0559 | 1.0559 | 1.0559 | 1.0559 | 0.87642 | 1.0195 | 1.0195 | 1.0195 | 1.0195 | 1.0195
2020-03-31 05:00 | Summer | 0.68589 | 0.98162 | 1.4165 | 1.4165 | 1.4165 | 1.4165 | 0.46583 | 0.9213 | 0.9213 | 0.9213 | 0.9213 | 0.9213 | 1.6003 | 2.0652 | 2.3698 | 2.5301 | 2.8507 | 3.1713 | 0.5449 | 1.0755 | 1.2906 | 1.2906 | 1.2906 | 1.2906 | 0.95263 | 1.1082 | 1.1082 | 1.1082 | 1.1082 | 1.1082
2020-03-31 06:00 | Summer | 0.74305 | 1.0634 | 1.5346 | 1.5346 | 1.5346 | 1.5346 | 0.56872 | 1.1248 | 1.1248 | 1.1248 | 1.1248 | 1.1248 | 1.788 | 2.3074 | 2.6477 | 2.8268 | 3.185 | 3.5432 | 0.53347 | 1.0529 | 1.2635 | 1.2635 | 1.2635 | 1.2635 | 1.3755 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6
2020-03-31 07:00 | Summer | 0.85737 | 1.227 | 1.7706 | 1.7706 | 1.7706 | 1.7706 | 0.79449 | 1.5713 | 1.5713 | 1.5713 | 1.5713 | 1.5713 | 2.0627 | 2.6618 | 3.0544 | 3.261 | 3.6742 | 4.0874 | 0.74305 | 1.4665 | 1.7599 | 1.7599 | 1.7599 | 1.7599 | 1.594 | 1.8543 | 1.8543 | 1.8543 | 1.8543 | 1.8543
2020-03-31 08:00 | Summer | 1.3527 | 1.936 | 2.7937 | 2.7937 | 2.7937 | 2.7937 | 0.90595 | 1.7917 | 1.7917 | 1.7917 | 1.7917 | 1.7917 | 2.191 | 2.8275 | 3.2445 | 3.4639 | 3.9029 | 4.3418 | 0.65541 | 1.2936 | 1.5523 | 1.5523 | 1.5523 | 1.5523 | 1.8481 | 2.1498 | 2.1498 | 2.1498 | 2.1498 | 2.1498
2020-03-31 09:00 | Summer | 1.3908 | 1.9905 | 2.8724 | 2.8724 | 2.8724 | 2.8724 | 1.026 | 2.0291 | 2.0291 | 2.0291 | 2.0291 | 2.0291 | 2.3435 | 3.0242 | 3.4702 | 3.7049 | 4.1744 | 4.6438 | 0.82355 | 1.6254 | 1.9505 | 1.9505 | 1.9505 | 1.9505 | 1.9815 | 2.305 | 2.305 | 2.305 | 2.305 | 2.305
2020-03-31 10:00 | Summer | 1.3908 | 1.9905 | 2.8724 | 2.8724 | 2.8724 | 2.8724 | 1.0546 | 2.0856 | 2.0856 | 2.0856 | 2.0856 | 2.0856 | 2.4387 | 3.1471 | 3.6112 | 3.8555 | 4.3441 | 4.8326 | 0.9793 | 1.9328 | 2.3194 | 2.3194 | 2.3194 | 2.3194 | 2.1529 | 2.5044 | 2.5044 | 2.5044 | 2.5044 | 2.5044
2020-03-31 11:00 | Summer | 1.4289 | 2.045 | 2.9511 | 2.9511 | 2.9511 | 2.9511 | 0.98311 | 1.9443 | 1.9443 | 1.9443 | 1.9443 | 1.9443 | 2.4281 | 3.1334 | 3.5955 | 3.8388 | 4.3252 | 4.8116 | 0.82688 | 1.632 | 1.9584 | 1.9584 | 1.9584 | 1.9584 | 2.1529 | 2.5044 | 2.5044 | 2.5044 | 2.5044 | 2.5044
2020-03-31 12:00 | Summer | 1.5433 | 2.2086 | 3.1872 | 3.1872 | 3.1872 | 3.1872 | 0.92881 | 1.837 | 1.837 | 1.837 | 1.837 | 1.837 | 2.5149 | 3.2455 | 3.7241 | 3.976 | 4.4798 | 4.9836 | 0.95644 | 1.8877 | 2.2652 | 2.2652 | 2.2652 | 2.2652 | 2.1339 | 2.4823 | 2.4823 | 2.4823 | 2.4823 | 2.4823
2020-03-31 13:00 | Summer | 1.4861 | 2.1268 | 3.0691 | 3.0691 | 3.0691 | 3.0691 | 0.94024 | 1.8596 | 1.8596 | 1.8596 | 1.8596 | 1.8596 | 2.534 | 3.2701 | 3.7523 | 4.0061 | 4.5138 | 5.0214 | 0.89255 | 1.7616 | 2.1139 | 2.1139 | 2.1139 | 2.1139 | 2.2482 | 2.6153 | 2.6153 | 2.6153 | 2.6153 | 2.6153
2020-03-31 14:00 | Summer | 1.4289 | 2.045 | 2.9511 | 2.9511 | 2.9511 | 2.9511 | 1.1031 | 2.1817 | 2.1817 | 2.1817 | 2.1817 | 2.1817 | 2.5721 | 3.3192 | 3.8087 | 4.0664 | 4.5816 | 5.0969 | 0.90309 | 1.7824 | 2.1389 | 2.1389 | 2.1389 | 2.1389 | 2.172 | 2.5266 | 2.5266 | 2.5266 | 2.5266 | 2.5266
2020-03-31 15:00 | Summer | 1.4099 | 2.0178 | 2.9117 | 2.9117 | 2.9117 | 2.9117 | 0.9431 | 1.8652 | 1.8652 | 1.8652 | 1.8652 | 1.8652 | 2.553 | 3.2946 | 3.7805 | 4.0362 | 4.5477 | 5.0591 | 0.75448 | 1.4891 | 1.7869 | 1.7869 | 1.7869 | 1.7869 | 2.2101 | 2.5709 | 2.5709 | 2.5709 | 2.5709 | 2.5709
2020-03-31 16:00 | Summer | 1.4289 | 2.045 | 2.9511 | 2.9511 | 2.9511 | 2.9511 | 1.026 | 2.0291 | 2.0291 | 2.0291 | 2.0291 | 2.0291 | 2.588 | 3.3398 | 3.8323 | 4.0916 | 4.61 | 5.1285 | 0.76591 | 1.5117 | 1.814 | 1.814 | 1.814 | 1.814 | 2.2291 | 2.5931 | 2.5931 | 2.5931 | 2.5931 | 2.5931
2020-03-31 17:00 | Summer | 1.3718 | 1.9632 | 2.833 | 2.833 | 2.833 | 2.833 | 1.0631 | 2.1026 | 2.1026 | 2.1026 | 2.1026 | 2.1026 | 2.6293 | 3.393 | 3.8934 | 4.1567 | 4.6835 | 5.2102 | 0.724 | 1.4289 | 1.7147 | 1.7147 | 1.7147 | 1.7147 | 2.1148 | 2.4601 | 2.4601 | 2.4601 | 2.4601 | 2.4601
2020-03-31 18:00 | Summer | 0.95422 | 1.3656 | 1.9707 | 1.9707 | 1.9707 | 1.9707 | 0.75734 | 1.4978 | 1.4978 | 1.4978 | 1.4978 | 1.4978 | 2.4293 | 3.135 | 3.5973 | 3.8407 | 4.3273 | 4.814 | 0.84593 | 1.6696 | 2.0035 | 2.0035 | 2.0035 | 2.0035 | 1.6254 | 1.8908 | 1.8908 | 1.8908 | 1.8908 | 1.8908
2020-03-31 19:00 | Summer | 0.724 | 1.0362 | 1.4952 | 1.4952 | 1.4952 | 1.4952 | 0.59444 | 1.1756 | 1.1756 | 1.1756 | 1.1756 | 1.1756 | 2.18 | 2.8133 | 3.2281 | 3.4465 | 3.8832 | 4.3199 | 0.67065 | 1.3236 | 1.5884 | 1.5884 | 1.5884 | 1.5884 | 1.1622 | 1.352 | 1.352 | 1.352 | 1.352 | 1.352
2020-03-31 20:00 | Summer | 0.64779 | 0.92709 | 1.3378 | 1.3378 | 1.3378 | 1.3378 | 0.55728 | 1.1022 | 1.1022 | 1.1022 | 1.1022 | 1.1022 | 2.0005 | 2.5816 | 2.9624 | 3.1627 | 3.5635 | 3.9643 | 0.6516 | 1.286 | 1.5433 | 1.5433 | 1.5433 | 1.5433 | 1.0669 | 1.2411 | 1.2411 | 1.2411 | 1.2411 | 1.2411
2020-03-31 21:00 | Summer | 0.62873 | 0.89982 | 1.2985 | 1.2985 | 1.2985 | 1.2985 | 0.42868 | 0.84782 | 0.84782 | 0.84782 | 0.84782 | 0.84782 | 1.8699 | 2.4131 | 2.769 | 2.9563 | 3.3309 | 3.7055 | 0.61349 | 1.2108 | 1.453 | 1.453 | 1.453 | 1.453 | 1.0288 | 1.1968 | 1.1968 | 1.1968 | 1.1968 | 1.1968
2020-03-31 22:00 | Summer | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.43439 | 0.85912 | 0.85912 | 0.85912 | 0.85912 | 0.85912 | 1.8672 | 2.4095 | 2.7649 | 2.9519 | 3.3259 | 3.7 | 0.62111 | 1.2259 | 1.4711 | 1.4711 | 1.4711 | 1.4711 | 0.87727 | 1.0205 | 1.0205 | 1.0205 | 1.0205 | 1.0205
2020-03-31 23:00 | Summer | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.39438 | 0.77999 | 0.77999 | 0.77999 | 0.77999 | 0.77999 | 1.7719 | 2.2866 | 2.6238 | 2.8013 | 3.1562 | 3.5112 | 0.56842 | 1.1219 | 1.3462 | 1.3462 | 1.3462 | 1.3462 | 0.91452 | 1.0638 | 1.0638 | 1.0638 | 1.0638 | 1.0638
2020-04-01 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.35297 | 0.35297 | 0.35297 | 0.35297 | 0.35297 | 0.35297 | 1.6576 | 2.391 | 2.8715 | 3.1244 | 3.6302 | 4.1361 | 0.57157 | 1.5526 | 1.9474 | 1.9474 | 1.9474 | 1.9474 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-04-01 01:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.38581 | 0.38581 | 0.38581 | 0.38581 | 0.38581 | 0.38581 | 1.6004 | 2.3086 | 2.7725 | 3.0167 | 3.5051 | 3.9934 | 0.53728 | 1.4595 | 1.8305 | 1.8305 | 1.8305 | 1.8305 | 0.80021 | 1.0157 | 1.0157 | 1.0157 | 1.0157 | 1.0157
2020-04-01 02:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 1.5814 | 2.2811 | 2.7395 | 2.9808 | 3.4633 | 3.9459 | 0.55252 | 1.5009 | 1.8825 | 1.8825 | 1.8825 | 1.8825 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-04-01 03:00 | Winter | 0.57187 | 0.87931 | 1.3306 | 1.3306 | 1.3306 | 1.3306 | 0.47726 | 0.47726 | 0.47726 | 0.47726 | 0.47726 | 0.47726 | 1.5433 | 2.2261 | 2.6735 | 2.909 | 3.3799 | 3.8508 | 0.5449 | 1.4802 | 1.8565 | 1.8565 | 1.8565 | 1.8565 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-04-01 04:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 1.5814 | 2.2811 | 2.7395 | 2.9808 | 3.4633 | 3.9459 | 0.5449 | 1.4802 | 1.8565 | 1.8565 | 1.8565 | 1.8565 | 0.91434 | 1.1606 | 1.1606 | 1.1606 | 1.1606 | 1.1606
2020-04-01 05:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.42296 | 0.42296 | 0.42296 | 0.42296 | 0.42296 | 0.42296 | 1.6222 | 2.34 | 2.8102 | 3.0578 | 3.5528 | 4.0478 | 0.60587 | 1.6458 | 2.0642 | 2.0642 | 2.0642 | 2.0642 | 0.97307 | 1.2351 | 1.2351 | 1.2351 | 1.2351 | 1.2351
2020-04-01 06:00 | Winter | 0.66684 | 1.0253 | 1.5515 | 1.5515 | 1.5515 | 1.5515 | 0.59729 | 0.59729 | 0.59729 | 0.59729 | 0.59729 | 0.59729 | 1.7147 | 2.4735 | 2.9705 | 3.2322 | 3.7554 | 4.2787 | 0.63635 | 1.7286 | 2.1681 | 2.1681 | 2.1681 | 2.1681 | 1.3275 | 1.6849 | 1.6849 | 1.6849 | 1.6849 | 1.6849
2020-04-01 07:00 | Winter | 0.87617 | 1.3472 | 2.0386 | 2.0386 | 2.0386 | 2.0386 | 0.71306 | 0.71306 | 0.71306 | 0.71306 | 0.71306 | 0.71306 | 2.061 | 2.9729 | 3.5704 | 3.8849 | 4.5138 | 5.1427 | 0.82688 | 2.2461 | 2.8172 | 2.8172 | 2.8172 | 2.8172 | 1.5408 | 1.9556 | 1.9556 | 1.9556 | 1.9556 | 1.9556
2020-04-01 08:00 | Winter | 1.4328 | 2.203 | 3.3336 | 3.3336 | 3.3336 | 3.3336 | 0.75734 | 0.75734 | 0.75734 | 0.75734 | 0.75734 | 0.75734 | 2.1529 | 3.1056 | 3.7297 | 4.0582 | 4.7151 | 5.3721 | 0.80211 | 2.1789 | 2.7328 | 2.7328 | 2.7328 | 2.7328 | 1.8672 | 2.3699 | 2.3699 | 2.3699 | 2.3699 | 2.3699
2020-04-01 09:00 | Winter | 1.448 | 2.2265 | 3.3691 | 3.3691 | 3.3691 | 3.3691 | 0.86879 | 0.86879 | 0.86879 | 0.86879 | 0.86879 | 0.86879 | 2.3244 | 3.3529 | 4.0267 | 4.3814 | 5.0907 | 5.8 | 1.0098 | 2.743 | 3.4404 | 3.4404 | 3.4404 | 3.4404 | 2.0005 | 2.5392 | 2.5392 | 2.5392 | 2.5392 | 2.5392
2020-04-01 10:00 | Winter | 1.4289 | 2.1972 | 3.3247 | 3.3247 | 3.3247 | 3.3247 | 0.93738 | 0.93738 | 0.93738 | 0.93738 | 0.93738 | 0.93738 | 2.4959 | 3.6002 | 4.3238 | 4.7046 | 5.4662 | 6.2279 | 0.96199 | 2.6132 | 3.2775 | 3.2775 | 3.2775 | 3.2775 | 2.2101 | 2.8052 | 2.8052 | 2.8052 | 2.8052 | 2.8052
2020-04-01 11:00 | Winter | 1.5433 | 2.3729 | 3.5907 | 3.5907 | 3.5907 | 3.5907 | 1.1031 | 1.1031 | 1.1031 | 1.1031 | 1.1031 | 1.1031 | 2.422 | 3.4937 | 4.1958 | 4.5653 | 5.3044 | 6.0435 | 0.86879 | 2.36 | 2.96 | 2.96 | 2.96 | 2.96 | 2.2286 | 2.8287 | 2.8287 | 2.8287 | 2.8287 | 2.8287
2020-04-01 12:00 | Winter | 1.467 | 2.2558 | 3.4134 | 3.4134 | 3.4134 | 3.4134 | 1.0917 | 1.0917 | 1.0917 | 1.0917 | 1.0917 | 1.0917 | 2.553 | 3.6827 | 4.4228 | 4.8123 | 5.5914 | 6.3705 | 0.74686 | 2.0288 | 2.5446 | 2.5446 | 2.5446 | 2.5446 | 2.3244 | 2.9503 | 2.9503 | 2.9503 | 2.9503 | 2.9503
2020-04-01 13:00 | Winter | 1.3718 | 2.1093 | 3.1918 | 3.1918 | 3.1918 | 3.1918 | 1.0517 | 1.0517 | 1.0517 | 1.0517 | 1.0517 | 1.0517 | 2.5149 | 3.6277 | 4.3568 | 4.7405 | 5.508 | 6.2754 | 0.85355 | 2.3186 | 2.9081 | 2.9081 | 2.9081 | 2.9081 | 2.4578 | 3.1196 | 3.1196 | 3.1196 | 3.1196 | 3.1196
2020-04-01 14:00 | Winter | 1.3908 | 2.1386 | 3.2361 | 3.2361 | 3.2361 | 3.2361 | 1.0631 | 1.0631 | 1.0631 | 1.0631 | 1.0631 | 1.0631 | 2.5721 | 3.7102 | 4.4558 | 4.8483 | 5.6331 | 6.418 | 0.9069 | 2.4635 | 3.0898 | 3.0898 | 3.0898 | 3.0898 | 2.4578 | 3.1196 | 3.1196 | 3.1196 | 3.1196 | 3.1196
2020-04-01 15:00 | Winter | 1.3908 | 2.1386 | 3.2361 | 3.2361 | 3.2361 | 3.2361 | 1.0974 | 1.0974 | 1.0974 | 1.0974 | 1.0974 | 1.0974 | 2.5911 | 3.7377 | 4.4888 | 4.8842 | 5.6749 | 6.4656 | 0.71637 | 1.946 | 2.4407 | 2.4407 | 2.4407 | 2.4407 | 2.4768 | 3.1438 | 3.1438 | 3.1438 | 3.1438 | 3.1438
2020-04-01 16:00 | Winter | 1.3908 | 2.1386 | 3.2361 | 3.2361 | 3.2361 | 3.2361 | 1.0317 | 1.0317 | 1.0317 | 1.0317 | 1.0317 | 1.0317 | 2.6293 | 3.7926 | 4.5548 | 4.956 | 5.7583 | 6.5606 | 0.74305 | 2.0184 | 2.5316 | 2.5316 | 2.5316 | 2.5316 | 2.2101 | 2.8052 | 2.8052 | 2.8052 | 2.8052 | 2.8052
2020-04-01 17:00 | Winter | 1.2956 | 1.9921 | 3.0144 | 3.0144 | 3.0144 | 3.0144 | 0.96882 | 0.96882 | 0.96882 | 0.96882 | 0.96882 | 0.96882 | 2.5162 | 3.6295 | 4.359 | 4.7429 | 5.5107 | 6.2785 | 0.6516 | 1.77 | 2.22 | 2.22 | 2.22 | 2.22 | 2.0839 | 2.645 | 2.645 | 2.645 | 2.645 | 2.645
2020-04-01 18:00 | Winter | 0.98237 | 1.5105 | 2.2857 | 2.2857 | 2.2857 | 2.2857 | 0.78992 | 0.78992 | 0.78992 | 0.78992 | 0.78992 | 0.78992 | 2.4471 | 3.5299 | 4.2393 | 4.6126 | 5.3594 | 6.1061 | 0.6516 | 1.77 | 2.22 | 2.22 | 2.22 | 2.22 | 1.4974 | 1.9006 | 1.9006 | 1.9006 | 1.9006 | 1.9006
2020-04-01 19:00 | Winter | 0.66684 | 1.0253 | 1.5515 | 1.5515 | 1.5515 | 1.5515 | 0.63445 | 0.63445 | 0.63445 | 0.63445 | 0.63445 | 0.63445 | 2.1863 | 3.1537 | 3.7874 | 4.121 | 4.7882 | 5.4553 | 0.6516 | 1.77 | 2.22 | 2.22 | 2.22 | 2.22 | 1.1606 | 1.4731 | 1.4731 | 1.4731 | 1.4731 | 1.4731
2020-04-01 20:00 | Winter | 0.66684 | 1.0253 | 1.5515 | 1.5515 | 1.5515 | 1.5515 | 0.51442 | 0.51442 | 0.51442 | 0.51442 | 0.51442 | 0.51442 | 2.0196 | 2.9132 | 3.4986 | 3.8068 | 4.4231 | 5.0393 | 0.67446 | 1.8321 | 2.2979 | 2.2979 | 2.2979 | 2.2979 | 1.1241 | 1.4268 | 1.4268 | 1.4268 | 1.4268 | 1.4268
2020-04-01 21:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.42582 | 0.42582 | 0.42582 | 0.42582 | 0.42582 | 0.42582 | 1.9815 | 2.8582 | 3.4326 | 3.735 | 4.3396 | 4.9443 | 0.66303 | 1.8011 | 2.2589 | 2.2589 | 2.2589 | 2.2589 | 1.0098 | 1.2817 | 1.2817 | 1.2817 | 1.2817 | 1.2817
2020-04-01 22:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.40582 | 0.40582 | 0.40582 | 0.40582 | 0.40582 | 0.40582 | 1.8767 | 2.7071 | 3.2511 | 3.5374 | 4.1101 | 4.6828 | 0.6173 | 1.6768 | 2.1032 | 2.1032 | 2.1032 | 2.1032 | 0.93358 | 1.185 | 1.185 | 1.185 | 1.185 | 1.185
2020-04-01 23:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.4001 | 0.4001 | 0.4001 | 0.4001 | 0.4001 | 0.4001 | 1.81 | 2.6109 | 3.1356 | 3.4117 | 3.9641 | 4.5164 | 0.6173 | 1.6768 | 2.1032 | 2.1032 | 2.1032 | 2.1032 | 0.91452 | 1.1608 | 1.1608 | 1.1608 | 1.1608 | 1.1608
2020-04-02 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.43439 | 0.43439 | 0.43439 | 0.43439 | 0.43439 | 0.43439 | 1.6766 | 2.4185 | 2.9045 | 3.1603 | 3.672 | 4.1836 | 0.57539 | 1.563 | 1.9603 | 1.9603 | 1.9603 | 1.9603 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-04-02 01:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 1.6004 | 2.3086 | 2.7725 | 3.0167 | 3.5051 | 3.9934 | 0.58301 | 1.5837 | 1.9863 | 1.9863 | 1.9863 | 1.9863 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-04-02 02:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 1.5814 | 2.2811 | 2.7395 | 2.9808 | 3.4633 | 3.9459 | 0.53218 | 1.4456 | 1.8131 | 1.8131 | 1.8131 | 1.8131 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-04-02 03:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 1.5814 | 2.2811 | 2.7395 | 2.9808 | 3.4633 | 3.9459 | 0.52966 | 1.4388 | 1.8046 | 1.8046 | 1.8046 | 1.8046 | 0.82308 | 1.0447 | 1.0447 | 1.0447 | 1.0447 | 1.0447
2020-04-02 04:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 1.5623 | 2.2536 | 2.7065 | 2.9449 | 3.4216 | 3.8984 | 0.52204 | 1.4181 | 1.7786 | 1.7786 | 1.7786 | 1.7786 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-04-02 05:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 1.6038 | 2.3134 | 2.7783 | 3.023 | 3.5124 | 4.0018 | 0.56776 | 1.5423 | 1.9344 | 1.9344 | 1.9344 | 1.9344 | 0.95686 | 1.2145 | 1.2145 | 1.2145 | 1.2145 | 1.2145
2020-04-02 06:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.59158 | 0.59158 | 0.59158 | 0.59158 | 0.59158 | 0.59158 | 1.7528 | 2.5284 | 3.0366 | 3.304 | 3.8389 | 4.3738 | 0.64779 | 1.7596 | 2.207 | 2.207 | 2.207 | 2.207 | 1.2793 | 1.6238 | 1.6238 | 1.6238 | 1.6238 | 1.6238
2020-04-02 07:00 | Winter | 0.88926 | 1.3673 | 2.0691 | 2.0691 | 2.0691 | 2.0691 | 0.69446 | 0.69446 | 0.69446 | 0.69446 | 0.69446 | 0.69446 | 2.0386 | 2.9407 | 3.5316 | 3.8427 | 4.4648 | 5.0869 | 0.86879 | 2.36 | 2.96 | 2.96 | 2.96 | 2.96 | 1.6195 | 2.0556 | 2.0556 | 2.0556 | 2.0556 | 2.0556
2020-04-02 08:00 | Winter | 1.2765 | 1.9628 | 2.9701 | 2.9701 | 2.9701 | 2.9701 | 0.8345 | 0.8345 | 0.8345 | 0.8345 | 0.8345 | 0.8345 | 2.172 | 3.133 | 3.7627 | 4.0941 | 4.7569 | 5.4197 | 0.87261 | 2.3704 | 2.973 | 2.973 | 2.973 | 2.973 | 1.8862 | 2.3941 | 2.3941 | 2.3941 | 2.3941 | 2.3941
2020-04-02 09:00 | Winter | 1.3527 | 2.08 | 3.1474 | 3.1474 | 3.1474 | 3.1474 | 0.89737 | 0.89737 | 0.89737 | 0.89737 | 0.89737 | 0.89737 | 2.191 | 3.1605 | 3.7957 | 4.13 | 4.7986 | 5.4672 | 0.75473 | 2.0502 | 2.5714 | 2.5714 | 2.5714 | 2.5714 | 1.8481 | 2.3458 | 2.3458 | 2.3458 | 2.3458 | 2.3458
2020-04-02 10:00 | Winter | 1.3146 | 2.0214 | 3.0588 | 3.0588 | 3.0588 | 3.0588 | 1.0145 | 1.0145 | 1.0145 | 1.0145 | 1.0145 | 1.0145 | 2.3244 | 3.3529 | 4.0267 | 4.3814 | 5.0907 | 5.8 | 0.86498 | 2.3496 | 2.947 | 2.947 | 2.947 | 2.947 | 1.9815 | 2.515 | 2.515 | 2.515 | 2.515 | 2.515
2020-04-02 11:00 | Winter | 1.3146 | 2.0214 | 3.0588 | 3.0588 | 3.0588 | 3.0588 | 0.93738 | 0.93738 | 0.93738 | 0.93738 | 0.93738 | 0.93738 | 2.2673 | 3.2705 | 3.9277 | 4.2736 | 4.9655 | 5.6574 | 0.82307 | 2.2358 | 2.8042 | 2.8042 | 2.8042 | 2.8042 | 1.9815 | 2.515 | 2.515 | 2.515 | 2.515 | 2.515
2020-04-02 12:00 | Winter | 1.3527 | 2.08 | 3.1474 | 3.1474 | 3.1474 | 3.1474 | 0.95739 | 0.95739 | 0.95739 | 0.95739 | 0.95739 | 0.95739 | 2.3054 | 3.3254 | 3.9937 | 4.3455 | 5.049 | 5.7525 | 0.85736 | 2.3289 | 2.9211 | 2.9211 | 2.9211 | 2.9211 | 1.9815 | 2.515 | 2.515 | 2.515 | 2.515 | 2.515
2020-04-02 13:00 | Winter | 1.3527 | 2.08 | 3.1474 | 3.1474 | 3.1474 | 3.1474 | 0.91738 | 0.91738 | 0.91738 | 0.91738 | 0.91738 | 0.91738 | 2.2863 | 3.2979 | 3.9607 | 4.3096 | 5.0072 | 5.7049 | 0.73543 | 1.9977 | 2.5056 | 2.5056 | 2.5056 | 2.5056 | 2.0196 | 2.5634 | 2.5634 | 2.5634 | 2.5634 | 2.5634
2020-04-02 14:00 | Winter | 1.3527 | 2.08 | 3.1474 | 3.1474 | 3.1474 | 3.1474 | 0.92309 | 0.92309 | 0.92309 | 0.92309 | 0.92309 | 0.92309 | 2.2863 | 3.2979 | 3.9607 | 4.3096 | 5.0072 | 5.7049 | 0.73543 | 1.9977 | 2.5056 | 2.5056 | 2.5056 | 2.5056 | 1.8481 | 2.3458 | 2.3458 | 2.3458 | 2.3458 | 2.3458
2020-04-02 15:00 | Winter | 1.2792 | 1.967 | 2.9764 | 2.9764 | 2.9764 | 2.9764 | 0.86022 | 0.86022 | 0.86022 | 0.86022 | 0.86022 | 0.86022 | 2.2863 | 3.2979 | 3.9607 | 4.3096 | 5.0072 | 5.7049 | 0.68589 | 1.8632 | 2.3368 | 2.3368 | 2.3368 | 2.3368 | 1.9243 | 2.4425 | 2.4425 | 2.4425 | 2.4425 | 2.4425
2020-04-02 16:00 | Winter | 1.2575 | 1.9335 | 2.9258 | 2.9258 | 2.9258 | 2.9258 | 0.8345 | 0.8345 | 0.8345 | 0.8345 | 0.8345 | 0.8345 | 2.4387 | 3.5178 | 4.2248 | 4.5969 | 5.3411 | 6.0852 | 0.71256 | 1.9356 | 2.4277 | 2.4277 | 2.4277 | 2.4277 | 1.9624 | 2.4908 | 2.4908 | 2.4908 | 2.4908 | 2.4908
2020-04-02 17:00 | Winter | 1.2575 | 1.9335 | 2.9258 | 2.9258 | 2.9258 | 2.9258 | 0.86022 | 0.86022 | 0.86022 | 0.86022 | 0.86022 | 0.86022 | 2.4197 | 3.4903 | 4.1918 | 4.561 | 5.2993 | 6.0377 | 0.70875 | 1.9253 | 2.4147 | 2.4147 | 2.4147 | 2.4147 | 1.8292 | 2.3217 | 2.3217 | 2.3217 | 2.3217 | 2.3217
2020-04-02 18:00 | Winter | 0.83351 | 1.2816 | 1.9393 | 1.9393 | 1.9393 | 1.9393 | 0.61269 | 0.61269 | 0.61269 | 0.61269 | 0.61269 | 0.61269 | 2.2482 | 3.243 | 3.8947 | 4.2377 | 4.9238 | 5.6098 | 0.66303 | 1.8011 | 2.2589 | 2.2589 | 2.2589 | 2.2589 | 1.3191 | 1.6743 | 1.6743 | 1.6743 | 1.6743 | 1.6743
2020-04-02 19:00 | Winter | 0.66684 | 1.0253 | 1.5515 | 1.5515 | 1.5515 | 1.5515 | 0.50883 | 0.50883 | 0.50883 | 0.50883 | 0.50883 | 0.50883 | 2.1529 | 3.1056 | 3.7297 | 4.0582 | 4.7151 | 5.3721 | 0.72781 | 1.977 | 2.4796 | 2.4796 | 2.4796 | 2.4796 | 1.086 | 1.3784 | 1.3784 | 1.3784 | 1.3784 | 1.3784
2020-04-02 20:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 2.0196 | 2.9132 | 3.4986 | 3.8068 | 4.4231 | 5.0393 | 0.66684 | 1.8114 | 2.2719 | 2.2719 | 2.2719 | 2.2719 | 1.0288 | 1.3059 | 1.3059 | 1.3059 | 1.3059 | 1.3059
2020-04-02 21:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.43154 | 0.43154 | 0.43154 | 0.43154 | 0.43154 | 0.43154 | 1.9434 | 2.8032 | 3.3666 | 3.6631 | 4.2562 | 4.8492 | 0.65541 | 1.7803 | 2.233 | 2.233 | 2.233 | 2.233 | 0.93364 | 1.1851 | 1.1851 | 1.1851 | 1.1851 | 1.1851
2020-04-02 22:00 | Winter | 0.59022 | 0.90753 | 1.3733 | 1.3733 | 1.3733 | 1.3733 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 1.9434 | 2.8032 | 3.3666 | 3.6631 | 4.2562 | 4.8492 | 0.6173 | 1.6768 | 2.1032 | 2.1032 | 2.1032 | 2.1032 | 0.83851 | 1.0643 | 1.0643 | 1.0643 | 1.0643 | 1.0643
2020-04-02 23:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.4001 | 0.4001 | 0.4001 | 0.4001 | 0.4001 | 0.4001 | 1.7719 | 2.5559 | 3.0696 | 3.3399 | 3.8806 | 4.4213 | 0.59444 | 1.6147 | 2.0253 | 2.0253 | 2.0253 | 2.0253 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-04-03 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.37724 | 0.37724 | 0.37724 | 0.37724 | 0.37724 | 0.37724 | 1.6768 | 2.4188 | 2.9049 | 3.1607 | 3.6724 | 4.1841 | 0.56395 | 1.5319 | 1.9214 | 1.9214 | 1.9214 | 1.9214 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-04-03 01:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.38581 | 0.38581 | 0.38581 | 0.38581 | 0.38581 | 0.38581 | 1.6576 | 2.391 | 2.8715 | 3.1244 | 3.6302 | 4.1361 | 0.59444 | 1.6147 | 2.0253 | 2.0253 | 2.0253 | 2.0253 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-04-03 02:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.4001 | 0.4001 | 0.4001 | 0.4001 | 0.4001 | 0.4001 | 1.6006 | 2.3088 | 2.7728 | 3.017 | 3.5055 | 3.9939 | 0.54109 | 1.4698 | 1.8435 | 1.8435 | 1.8435 | 1.8435 | 0.80021 | 1.0157 | 1.0157 | 1.0157 | 1.0157 | 1.0157
2020-04-03 03:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.39724 | 0.39724 | 0.39724 | 0.39724 | 0.39724 | 0.39724 | 1.5817 | 2.2816 | 2.7402 | 2.9815 | 3.4642 | 3.9469 | 0.54109 | 1.4698 | 1.8435 | 1.8435 | 1.8435 | 1.8435 | 0.80021 | 1.0157 | 1.0157 | 1.0157 | 1.0157 | 1.0157
2020-04-03 04:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.35152 | 0.35152 | 0.35152 | 0.35152 | 0.35152 | 0.35152 | 1.5623 | 2.2536 | 2.7065 | 2.9449 | 3.4216 | 3.8984 | 0.52204 | 1.4181 | 1.7786 | 1.7786 | 1.7786 | 1.7786 | 0.85684 | 1.0876 | 1.0876 | 1.0876 | 1.0876 | 1.0876
2020-04-03 05:00 | Winter | 0.58007 | 0.89192 | 1.3497 | 1.3497 | 1.3497 | 1.3497 | 0.39438 | 0.39438 | 0.39438 | 0.39438 | 0.39438 | 0.39438 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.56395 | 1.5319 | 1.9214 | 1.9214 | 1.9214 | 1.9214 | 0.98979 | 1.2563 | 1.2563 | 1.2563 | 1.2563 | 1.2563
2020-04-03 06:00 | Winter | 0.61821 | 0.95056 | 1.4384 | 1.4384 | 1.4384 | 1.4384 | 0.58872 | 0.58872 | 0.58872 | 0.58872 | 0.58872 | 0.58872 | 1.7713 | 2.555 | 3.0685 | 3.3387 | 3.8793 | 4.4198 | 0.60968 | 1.6561 | 2.0772 | 2.0772 | 2.0772 | 2.0772 | 1.2514 | 1.5884 | 1.5884 | 1.5884 | 1.5884 | 1.5884
2020-04-03 07:00 | Winter | 0.81926 | 1.2597 | 1.9062 | 1.9062 | 1.9062 | 1.9062 | 0.80878 | 0.80878 | 0.80878 | 0.80878 | 0.80878 | 0.80878 | 1.9812 | 2.8578 | 3.4322 | 3.7344 | 4.339 | 4.9436 | 0.74305 | 2.0184 | 2.5316 | 2.5316 | 2.5316 | 2.5316 | 1.5392 | 1.9537 | 1.9537 | 1.9537 | 1.9537 | 1.9537
2020-04-03 08:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 0.80878 | 0.80878 | 0.80878 | 0.80878 | 0.80878 | 0.80878 | 2.0767 | 2.9956 | 3.5977 | 3.9145 | 4.5482 | 5.182 | 0.72018 | 1.9563 | 2.4537 | 2.4537 | 2.4537 | 2.4537 | 1.7732 | 2.2507 | 2.2507 | 2.2507 | 2.2507 | 2.2507
2020-04-03 09:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 0.77162 | 0.77162 | 0.77162 | 0.77162 | 0.77162 | 0.77162 | 2.1339 | 3.0781 | 3.6967 | 4.0223 | 4.6734 | 5.3246 | 0.69351 | 1.8839 | 2.3628 | 2.3628 | 2.3628 | 2.3628 | 1.829 | 2.3216 | 2.3216 | 2.3216 | 2.3216 | 2.3216
2020-04-03 10:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.86308 | 0.86308 | 0.86308 | 0.86308 | 0.86308 | 0.86308 | 2.172 | 3.133 | 3.7627 | 4.0941 | 4.7569 | 5.4197 | 0.69351 | 1.8839 | 2.3628 | 2.3628 | 2.3628 | 2.3628 | 1.9243 | 2.4425 | 2.4425 | 2.4425 | 2.4425 | 2.4425
2020-04-03 11:00 | Winter | 1.2285 | 1.889 | 2.8584 | 2.8584 | 2.8584 | 2.8584 | 0.86022 | 0.86022 | 0.86022 | 0.86022 | 0.86022 | 0.86022 | 2.3427 | 3.3793 | 4.0585 | 4.4159 | 5.1308 | 5.8457 | 0.6516 | 1.77 | 2.22 | 2.22 | 2.22 | 2.22 | 1.8672 | 2.3699 | 2.3699 | 2.3699 | 2.3699 | 2.3699
2020-04-03 12:00 | Winter | 1.2384 | 1.9042 | 2.8814 | 2.8814 | 2.8814 | 2.8814 | 0.80592 | 0.80592 | 0.80592 | 0.80592 | 0.80592 | 0.80592 | 2.3625 | 3.4079 | 4.0927 | 4.4532 | 5.1741 | 5.8951 | 0.73543 | 1.9977 | 2.5056 | 2.5056 | 2.5056 | 2.5056 | 1.8672 | 2.3699 | 2.3699 | 2.3699 | 2.3699 | 2.3699
2020-04-03 13:00 | Winter | 1.2575 | 1.9335 | 2.9258 | 2.9258 | 2.9258 | 2.9258 | 0.79163 | 0.79163 | 0.79163 | 0.79163 | 0.79163 | 0.79163 | 2.2673 | 3.2705 | 3.9277 | 4.2736 | 4.9655 | 5.6574 | 0.73162 | 1.9874 | 2.4926 | 2.4926 | 2.4926 | 2.4926 | 1.8672 | 2.3699 | 2.3699 | 2.3699 | 2.3699 | 2.3699
2020-04-03 14:00 | Winter | 1.2384 | 1.9042 | 2.8814 | 2.8814 | 2.8814 | 2.8814 | 0.77734 | 0.77734 | 0.77734 | 0.77734 | 0.77734 | 0.77734 | 2.2291 | 3.2155 | 3.8617 | 4.2018 | 4.8821 | 5.5623 | 0.69732 | 1.8942 | 2.3758 | 2.3758 | 2.3758 | 2.3758 | 1.81 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974
2020-04-03 15:00 | Winter | 1.2003 | 1.8456 | 2.7928 | 2.7928 | 2.7928 | 2.7928 | 0.73161 | 0.73161 | 0.73161 | 0.73161 | 0.73161 | 0.73161 | 2.2101 | 3.188 | 3.8287 | 4.1659 | 4.8403 | 5.5147 | 0.724 | 1.9667 | 2.4667 | 2.4667 | 2.4667 | 2.4667 | 1.7909 | 2.2732 | 2.2732 | 2.2732 | 2.2732 | 2.2732
2020-04-03 16:00 | Winter | 1.2194 | 1.8749 | 2.8371 | 2.8371 | 2.8371 | 2.8371 | 0.75734 | 0.75734 | 0.75734 | 0.75734 | 0.75734 | 0.75734 | 2.3435 | 3.3804 | 4.0597 | 4.4173 | 5.1324 | 5.8475 | 0.73543 | 1.9977 | 2.5056 | 2.5056 | 2.5056 | 2.5056 | 1.7338 | 2.2007 | 2.2007 | 2.2007 | 2.2007 | 2.2007
2020-04-03 17:00 | Winter | 1.086 | 1.6698 | 2.5268 | 2.5268 | 2.5268 | 2.5268 | 0.75448 | 0.75448 | 0.75448 | 0.75448 | 0.75448 | 0.75448 | 2.2863 | 3.2979 | 3.9607 | 4.3096 | 5.0072 | 5.7049 | 0.70875 | 1.9253 | 2.4147 | 2.4147 | 2.4147 | 2.4147 | 1.715 | 2.1768 | 2.1768 | 2.1768 | 2.1768 | 2.1768
2020-04-03 18:00 | Winter | 0.9022 | 1.3872 | 2.0992 | 2.0992 | 2.0992 | 2.0992 | 0.64302 | 0.64302 | 0.64302 | 0.64302 | 0.64302 | 0.64302 | 2.1316 | 3.0748 | 3.6928 | 4.018 | 4.6685 | 5.319 | 0.60587 | 1.6458 | 2.0642 | 2.0642 | 2.0642 | 2.0642 | 1.388 | 1.7618 | 1.7618 | 1.7618 | 1.7618 | 1.7618
2020-04-03 19:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.47441 | 0.47441 | 0.47441 | 0.47441 | 0.47441 | 0.47441 | 2.0577 | 2.9681 | 3.5647 | 3.8786 | 4.5065 | 5.1344 | 0.6516 | 1.77 | 2.22 | 2.22 | 2.22 | 2.22 | 1.0421 | 1.3228 | 1.3228 | 1.3228 | 1.3228 | 1.3228
2020-04-03 20:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 1.9624 | 2.8307 | 3.3996 | 3.699 | 4.2979 | 4.8967 | 0.62492 | 1.6975 | 2.1291 | 2.1291 | 2.1291 | 2.1291 | 0.97168 | 1.2333 | 1.2333 | 1.2333 | 1.2333 | 1.2333
2020-04-03 21:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 1.8672 | 2.6933 | 3.2346 | 3.5195 | 4.0892 | 4.659 | 0.62111 | 1.6872 | 2.1161 | 2.1161 | 2.1161 | 2.1161 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-04-03 22:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 1.8481 | 2.6658 | 3.2016 | 3.4836 | 4.0475 | 4.6115 | 0.60587 | 1.6458 | 2.0642 | 2.0642 | 2.0642 | 2.0642 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-04-03 23:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.43439 | 0.43439 | 0.43439 | 0.43439 | 0.43439 | 0.43439 | 1.7719 | 2.5559 | 3.0696 | 3.3399 | 3.8806 | 4.4213 | 0.54109 | 1.4698 | 1.8435 | 1.8435 | 1.8435 | 1.8435 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-04-04 | Winter | 0.53354 | 0.82038 | 1.2414 | 1.2414 | 1.2414 | 1.2414 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.55633 | 1.5112 | 1.8954 | 1.8954 | 1.8954 | 1.8954 | 0.79642 | 1.0109 | 1.0109 | 1.0109 | 1.0109 | 1.0109
2020-04-04 01:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.41668 | 0.41668 | 0.41668 | 0.41668 | 0.41668 | 0.41668 | 1.5814 | 2.2811 | 2.7395 | 2.9808 | 3.4633 | 3.9459 | 0.54109 | 1.4698 | 1.8435 | 1.8435 | 1.8435 | 1.8435 | 0.78115 | 0.9915 | 0.9915 | 0.9915 | 0.9915 | 0.9915
2020-04-04 02:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 1.5489 | 2.2342 | 2.6832 | 2.9195 | 3.3922 | 3.8648 | 0.52204 | 1.4181 | 1.7786 | 1.7786 | 1.7786 | 1.7786 | 0.78115 | 0.9915 | 0.9915 | 0.9915 | 0.9915 | 0.9915
2020-04-04 03:00 | Winter | 0.57251 | 0.88031 | 1.3321 | 1.3321 | 1.3321 | 1.3321 | 0.42582 | 0.42582 | 0.42582 | 0.42582 | 0.42582 | 0.42582 | 1.5433 | 2.2261 | 2.6735 | 2.909 | 3.3799 | 3.8508 | 0.51061 | 1.387 | 1.7396 | 1.7396 | 1.7396 | 1.7396 | 0.78115 | 0.9915 | 0.9915 | 0.9915 | 0.9915 | 0.9915
2020-04-04 04:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 1.5814 | 2.2811 | 2.7395 | 2.9808 | 3.4633 | 3.9459 | 0.52585 | 1.4284 | 1.7916 | 1.7916 | 1.7916 | 1.7916 | 0.78115 | 0.9915 | 0.9915 | 0.9915 | 0.9915 | 0.9915
2020-04-04 05:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.41153 | 0.41153 | 0.41153 | 0.41153 | 0.41153 | 0.41153 | 1.6195 | 2.336 | 2.8055 | 3.0526 | 3.5468 | 4.041 | 0.52204 | 1.4181 | 1.7786 | 1.7786 | 1.7786 | 1.7786 | 0.80021 | 1.0157 | 1.0157 | 1.0157 | 1.0157 | 1.0157
2020-04-04 06:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 1.6576 | 2.391 | 2.8715 | 3.1244 | 3.6302 | 4.1361 | 0.53728 | 1.4595 | 1.8305 | 1.8305 | 1.8305 | 1.8305 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-04-04 07:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.52013 | 0.52013 | 0.52013 | 0.52013 | 0.52013 | 0.52013 | 1.7147 | 2.4735 | 2.9705 | 3.2322 | 3.7554 | 4.2787 | 0.57539 | 1.563 | 1.9603 | 1.9603 | 1.9603 | 1.9603 | 0.88929 | 1.1288 | 1.1288 | 1.1288 | 1.1288 | 1.1288
2020-04-04 08:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.49727 | 0.49727 | 0.49727 | 0.49727 | 0.49727 | 0.49727 | 1.7719 | 2.5559 | 3.0696 | 3.3399 | 3.8806 | 4.4213 | 0.5449 | 1.4802 | 1.8565 | 1.8565 | 1.8565 | 1.8565 | 0.93358 | 1.185 | 1.185 | 1.185 | 1.185 | 1.185
2020-04-04 09:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.58015 | 0.58015 | 0.58015 | 0.58015 | 0.58015 | 0.58015 | 1.7909 | 2.5834 | 3.1026 | 3.3758 | 3.9223 | 4.4688 | 0.59825 | 1.6251 | 2.0382 | 2.0382 | 2.0382 | 2.0382 | 0.95263 | 1.2092 | 1.2092 | 1.2092 | 1.2092 | 1.2092
2020-04-04 10:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.49441 | 0.49441 | 0.49441 | 0.49441 | 0.49441 | 0.49441 | 1.9053 | 2.7483 | 3.3006 | 3.5913 | 4.1727 | 4.7541 | 0.6516 | 1.77 | 2.22 | 2.22 | 2.22 | 2.22 | 1.0098 | 1.2817 | 1.2817 | 1.2817 | 1.2817 | 1.2817
2020-04-04 11:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.50298 | 0.50298 | 0.50298 | 0.50298 | 0.50298 | 0.50298 | 1.8862 | 2.7208 | 3.2676 | 3.5554 | 4.131 | 4.7066 | 0.62111 | 1.6872 | 2.1161 | 2.1161 | 2.1161 | 2.1161 | 0.99073 | 1.2575 | 1.2575 | 1.2575 | 1.2575 | 1.2575
2020-04-04 12:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.48012 | 0.48012 | 0.48012 | 0.48012 | 0.48012 | 0.48012 | 1.9053 | 2.7483 | 3.3006 | 3.5913 | 4.1727 | 4.7541 | 0.54109 | 1.4698 | 1.8435 | 1.8435 | 1.8435 | 1.8435 | 0.99073 | 1.2575 | 1.2575 | 1.2575 | 1.2575 | 1.2575
2020-04-04 13:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.55157 | 0.55157 | 0.55157 | 0.55157 | 0.55157 | 0.55157 | 1.9434 | 2.8032 | 3.3666 | 3.6631 | 4.2562 | 4.8492 | 0.54871 | 1.4905 | 1.8695 | 1.8695 | 1.8695 | 1.8695 | 0.99073 | 1.2575 | 1.2575 | 1.2575 | 1.2575 | 1.2575
2020-04-04 14:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 1.9053 | 2.7483 | 3.3006 | 3.5913 | 4.1727 | 4.7541 | 0.56014 | 1.5216 | 1.9084 | 1.9084 | 1.9084 | 1.9084 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-04-04 15:00 | Winter | 0.6096 | 0.93733 | 1.4184 | 1.4184 | 1.4184 | 1.4184 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 1.8377 | 2.6508 | 3.1835 | 3.4639 | 4.0247 | 4.5854 | 0.52585 | 1.4284 | 1.7916 | 1.7916 | 1.7916 | 1.7916 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-04-04 16:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.44206 | 0.44206 | 0.44206 | 0.44206 | 0.44206 | 0.44206 | 1.8672 | 2.6933 | 3.2346 | 3.5195 | 4.0892 | 4.659 | 0.53347 | 1.4491 | 1.8175 | 1.8175 | 1.8175 | 1.8175 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-04-04 17:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.46869 | 0.46869 | 0.46869 | 0.46869 | 0.46869 | 0.46869 | 1.9434 | 2.8032 | 3.3666 | 3.6631 | 4.2562 | 4.8492 | 0.52966 | 1.4388 | 1.8046 | 1.8046 | 1.8046 | 1.8046 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-04-04 18:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 1.9434 | 2.8032 | 3.3666 | 3.6631 | 4.2562 | 4.8492 | 0.60206 | 1.6354 | 2.0512 | 2.0512 | 2.0512 | 2.0512 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-04-04 19:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 1.9624 | 2.8307 | 3.3996 | 3.699 | 4.2979 | 4.8967 | 0.61349 | 1.6665 | 2.0902 | 2.0902 | 2.0902 | 2.0902 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-04-04 20:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 1.9434 | 2.8032 | 3.3666 | 3.6631 | 4.2562 | 4.8492 | 0.59444 | 1.6147 | 2.0253 | 2.0253 | 2.0253 | 2.0253 | 0.87745 | 1.1137 | 1.1137 | 1.1137 | 1.1137 | 1.1137
2020-04-04 21:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.39153 | 0.39153 | 0.39153 | 0.39153 | 0.39153 | 0.39153 | 1.8862 | 2.7208 | 3.2676 | 3.5554 | 4.131 | 4.7066 | 0.57157 | 1.5526 | 1.9474 | 1.9474 | 1.9474 | 1.9474 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-04-04 22:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.30007 | 0.30007 | 0.30007 | 0.30007 | 0.30007 | 0.30007 | 1.7909 | 2.5834 | 3.1026 | 3.3758 | 3.9223 | 4.4688 | 0.5449 | 1.4802 | 1.8565 | 1.8565 | 1.8565 | 1.8565 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-04-04 23:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.28578 | 0.28578 | 0.28578 | 0.28578 | 0.28578 | 0.28578 | 1.7528 | 2.5284 | 3.0366 | 3.304 | 3.8389 | 4.3738 | 0.54124 | 1.4702 | 1.844 | 1.844 | 1.844 | 1.844 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-04-05 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.38295 | 0.38295 | 0.38295 | 0.38295 | 0.38295 | 0.38295 | 1.618 | 2.334 | 2.803 | 3.0499 | 3.5437 | 4.0374 | 0.49536 | 1.3456 | 1.6877 | 1.6877 | 1.6877 | 1.6877 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-04-05 01:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.42296 | 0.42296 | 0.42296 | 0.42296 | 0.42296 | 0.42296 | 1.5814 | 2.2811 | 2.7395 | 2.9808 | 3.4633 | 3.9459 | 0.48844 | 1.3268 | 1.6641 | 1.6641 | 1.6641 | 1.6641 | 0.80021 | 1.0157 | 1.0157 | 1.0157 | 1.0157 | 1.0157
2020-04-05 02:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.3458 | 0.3458 | 0.3458 | 0.3458 | 0.3458 | 0.3458 | 1.5814 | 2.2811 | 2.7395 | 2.9808 | 3.4633 | 3.9459 | 0.49918 | 1.356 | 1.7007 | 1.7007 | 1.7007 | 1.7007 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-04-05 02:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.28012 | 0.28012 | 0.28012 | 0.28012 | 0.28012 | 0.28012 | 1.5814 | 2.2811 | 2.7395 | 2.9808 | 3.4633 | 3.9459 | 0.48393 | 1.3146 | 1.6488 | 1.6488 | 1.6488 | 1.6488 | 0.80021 | 1.0157 | 1.0157 | 1.0157 | 1.0157 | 1.0157
2020-04-05 03:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 1.4944 | 2.1556 | 2.5889 | 2.8169 | 3.2729 | 3.7289 | 0.48012 | 1.3042 | 1.6358 | 1.6358 | 1.6358 | 1.6358 | 0.80021 | 1.0157 | 1.0157 | 1.0157 | 1.0157 | 1.0157
2020-04-05 04:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.42582 | 0.42582 | 0.42582 | 0.42582 | 0.42582 | 0.42582 | 1.5433 | 2.2261 | 2.6735 | 2.909 | 3.3799 | 3.8508 | 0.48012 | 1.3042 | 1.6358 | 1.6358 | 1.6358 | 1.6358 | 0.80021 | 1.0157 | 1.0157 | 1.0157 | 1.0157 | 1.0157
2020-04-05 05:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.41153 | 0.41153 | 0.41153 | 0.41153 | 0.41153 | 0.41153 | 1.5623 | 2.2536 | 2.7065 | 2.9449 | 3.4216 | 3.8984 | 0.50299 | 1.3663 | 1.7137 | 1.7137 | 1.7137 | 1.7137 | 0.80017 | 1.0156 | 1.0156 | 1.0156 | 1.0156 | 1.0156
2020-04-05 06:00 | Winter | 0.57271 | 0.88061 | 1.3325 | 1.3325 | 1.3325 | 1.3325 | 0.39438 | 0.39438 | 0.39438 | 0.39438 | 0.39438 | 0.39438 | 1.5575 | 2.2466 | 2.6981 | 2.9358 | 3.4111 | 3.8863 | 0.46869 | 1.2732 | 1.5968 | 1.5968 | 1.5968 | 1.5968 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-04-05 07:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 1.6955 | 2.4457 | 2.9372 | 3.1959 | 3.7133 | 4.2307 | 0.52585 | 1.4284 | 1.7916 | 1.7916 | 1.7916 | 1.7916 | 0.8864 | 1.1251 | 1.1251 | 1.1251 | 1.1251 | 1.1251
2020-04-05 08:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.52013 | 0.52013 | 0.52013 | 0.52013 | 0.52013 | 0.52013 | 1.7909 | 2.5834 | 3.1026 | 3.3758 | 3.9223 | 4.4688 | 0.53728 | 1.4595 | 1.8305 | 1.8305 | 1.8305 | 1.8305 | 0.91452 | 1.1608 | 1.1608 | 1.1608 | 1.1608 | 1.1608
2020-04-05 09:00 | Winter | 0.55757 | 0.85733 | 1.2973 | 1.2973 | 1.2973 | 1.2973 | 0.6716 | 0.6716 | 0.6716 | 0.6716 | 0.6716 | 0.6716 | 1.8481 | 2.6658 | 3.2016 | 3.4836 | 4.0475 | 4.6115 | 0.5449 | 1.4802 | 1.8565 | 1.8565 | 1.8565 | 1.8565 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-04-05 10:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.60301 | 0.60301 | 0.60301 | 0.60301 | 0.60301 | 0.60301 | 1.9243 | 2.7758 | 3.3336 | 3.6272 | 4.2144 | 4.8016 | 0.56395 | 1.5319 | 1.9214 | 1.9214 | 1.9214 | 1.9214 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-04-05 11:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 1.8481 | 2.6658 | 3.2016 | 3.4836 | 4.0475 | 4.6115 | 0.52966 | 1.4388 | 1.8046 | 1.8046 | 1.8046 | 1.8046 | 0.78115 | 0.9915 | 0.9915 | 0.9915 | 0.9915 | 0.9915
2020-04-05 12:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.42296 | 0.42296 | 0.42296 | 0.42296 | 0.42296 | 0.42296 | 1.9053 | 2.7483 | 3.3006 | 3.5913 | 4.1727 | 4.7541 | 0.52204 | 1.4181 | 1.7786 | 1.7786 | 1.7786 | 1.7786 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-04-05 13:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 1.9434 | 2.8032 | 3.3666 | 3.6631 | 4.2562 | 4.8492 | 0.52204 | 1.4181 | 1.7786 | 1.7786 | 1.7786 | 1.7786 | 0.80021 | 1.0157 | 1.0157 | 1.0157 | 1.0157 | 1.0157
2020-04-05 14:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 1.9053 | 2.7483 | 3.3006 | 3.5913 | 4.1727 | 4.7541 | 0.53347 | 1.4491 | 1.8175 | 1.8175 | 1.8175 | 1.8175 | 0.80021 | 1.0157 | 1.0157 | 1.0157 | 1.0157 | 1.0157
2020-04-05 15:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.42296 | 0.42296 | 0.42296 | 0.42296 | 0.42296 | 0.42296 | 2.0386 | 2.9407 | 3.5316 | 3.8427 | 4.4648 | 5.0869 | 0.53347 | 1.4491 | 1.8175 | 1.8175 | 1.8175 | 1.8175 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-04-05 16:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 1.9243 | 2.7758 | 3.3336 | 3.6272 | 4.2144 | 4.8016 | 0.56776 | 1.5423 | 1.9344 | 1.9344 | 1.9344 | 1.9344 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-04-05 17:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.43154 | 0.43154 | 0.43154 | 0.43154 | 0.43154 | 0.43154 | 2.0386 | 2.9407 | 3.5316 | 3.8427 | 4.4648 | 5.0869 | 0.57539 | 1.563 | 1.9603 | 1.9603 | 1.9603 | 1.9603 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-04-05 18:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 2.0577 | 2.9681 | 3.5647 | 3.8786 | 4.5065 | 5.1344 | 0.62492 | 1.6975 | 2.1291 | 2.1291 | 2.1291 | 2.1291 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-04-05 19:00 | Winter | 0.55947 | 0.86025 | 1.3017 | 1.3017 | 1.3017 | 1.3017 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 1.9598 | 2.8269 | 3.3951 | 3.6941 | 4.2921 | 4.8901 | 0.58301 | 1.5837 | 1.9863 | 1.9863 | 1.9863 | 1.9863 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-04-05 20:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 1.9815 | 2.8582 | 3.4326 | 3.735 | 4.3396 | 4.9443 | 0.59444 | 1.6147 | 2.0253 | 2.0253 | 2.0253 | 2.0253 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-04-05 21:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.42582 | 0.42582 | 0.42582 | 0.42582 | 0.42582 | 0.42582 | 1.9053 | 2.7483 | 3.3006 | 3.5913 | 4.1727 | 4.7541 | 0.58301 | 1.5837 | 1.9863 | 1.9863 | 1.9863 | 1.9863 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-04-05 22:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.27996 | 0.27996 | 0.27996 | 0.27996 | 0.27996 | 0.27996 | 1.7294 | 2.4947 | 2.996 | 3.2599 | 3.7876 | 4.3154 | 0.55252 | 1.5009 | 1.8825 | 1.8825 | 1.8825 | 1.8825 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-04-05 23:00 | Winter | 0.55617 | 0.85517 | 1.294 | 1.294 | 1.294 | 1.294 | 0.28007 | 0.28007 | 0.28007 | 0.28007 | 0.28007 | 0.28007 | 1.6766 | 2.4185 | 2.9045 | 3.1603 | 3.672 | 4.1836 | 0.51061 | 1.387 | 1.7396 | 1.7396 | 1.7396 | 1.7396 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-04-06 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.38581 | 0.38581 | 0.38581 | 0.38581 | 0.38581 | 0.38581 | 1.5814 | 2.2811 | 2.7395 | 2.9808 | 3.4633 | 3.9459 | 0.52204 | 1.4181 | 1.7786 | 1.7786 | 1.7786 | 1.7786 | 0.80021 | 1.0157 | 1.0157 | 1.0157 | 1.0157 | 1.0157
2020-04-06 01:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.42296 | 0.42296 | 0.42296 | 0.42296 | 0.42296 | 0.42296 | 1.5482 | 2.2333 | 2.6821 | 2.9183 | 3.3908 | 3.8632 | 0.48012 | 1.3042 | 1.6358 | 1.6358 | 1.6358 | 1.6358 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-04-06 02:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.31151 | 0.31151 | 0.31151 | 0.31151 | 0.31151 | 0.31151 | 1.5814 | 2.2811 | 2.7395 | 2.9808 | 3.4633 | 3.9459 | 0.48012 | 1.3042 | 1.6358 | 1.6358 | 1.6358 | 1.6358 | 0.81533 | 1.0349 | 1.0349 | 1.0349 | 1.0349 | 1.0349
2020-04-06 03:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.38009 | 0.38009 | 0.38009 | 0.38009 | 0.38009 | 0.38009 | 1.5433 | 2.2261 | 2.6735 | 2.909 | 3.3799 | 3.8508 | 0.48774 | 1.3249 | 1.6618 | 1.6618 | 1.6618 | 1.6618 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-04-06 04:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.39153 | 0.39153 | 0.39153 | 0.39153 | 0.39153 | 0.39153 | 1.5623 | 2.2536 | 2.7065 | 2.9449 | 3.4216 | 3.8984 | 0.49081 | 1.3332 | 1.6722 | 1.6722 | 1.6722 | 1.6722 | 1.086 | 1.3784 | 1.3784 | 1.3784 | 1.3784 | 1.3784
2020-04-06 05:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.50013 | 0.50013 | 0.50013 | 0.50013 | 0.50013 | 0.50013 | 1.5999 | 2.3078 | 2.7715 | 3.0156 | 3.5038 | 3.992 | 0.51061 | 1.387 | 1.7396 | 1.7396 | 1.7396 | 1.7396 | 1.3546 | 1.7193 | 1.7193 | 1.7193 | 1.7193 | 1.7193
2020-04-06 06:00 | Winter | 0.69432 | 1.0676 | 1.6155 | 1.6155 | 1.6155 | 1.6155 | 0.71447 | 0.71447 | 0.71447 | 0.71447 | 0.71447 | 0.71447 | 1.8915 | 2.7284 | 3.2767 | 3.5653 | 4.1425 | 4.7197 | 0.54399 | 1.4777 | 1.8534 | 1.8534 | 1.8534 | 1.8534 | 1.4289 | 1.8137 | 1.8137 | 1.8137 | 1.8137 | 1.8137
2020-04-06 07:00 | Winter | 1.0174 | 1.5644 | 2.3672 | 2.3672 | 2.3672 | 2.3672 | 0.79449 | 0.79449 | 0.79449 | 0.79449 | 0.79449 | 0.79449 | 2.0084 | 2.897 | 3.4792 | 3.7856 | 4.3985 | 5.0114 | 0.7621 | 2.0702 | 2.5965 | 2.5965 | 2.5965 | 2.5965 | 1.9053 | 2.4183 | 2.4183 | 2.4183 | 2.4183 | 2.4183
2020-04-06 08:00 | Winter | 1.1241 | 1.7284 | 2.6155 | 2.6155 | 2.6155 | 2.6155 | 0.89737 | 0.89737 | 0.89737 | 0.89737 | 0.89737 | 0.89737 | 2.1529 | 3.1056 | 3.7297 | 4.0582 | 4.7151 | 5.3721 | 0.73162 | 1.9874 | 2.4926 | 2.4926 | 2.4926 | 2.4926 | 2.0436 | 2.5939 | 2.5939 | 2.5939 | 2.5939 | 2.5939
2020-04-06 09:00 | Winter | 1.1432 | 1.7577 | 2.6598 | 2.6598 | 2.6598 | 2.6598 | 0.92595 | 0.92595 | 0.92595 | 0.92595 | 0.92595 | 0.92595 | 2.1339 | 3.0781 | 3.6967 | 4.0223 | 4.6734 | 5.3246 | 0.73924 | 2.0081 | 2.5186 | 2.5186 | 2.5186 | 2.5186 | 2.3816 | 3.0229 | 3.0229 | 3.0229 | 3.0229 | 3.0229
2020-04-06 10:00 | Winter | 1.1622 | 1.787 | 2.7041 | 2.7041 | 2.7041 | 2.7041 | 0.81449 | 0.81449 | 0.81449 | 0.81449 | 0.81449 | 0.81449 | 2.191 | 3.1605 | 3.7957 | 4.13 | 4.7986 | 5.4672 | 0.75067 | 2.0391 | 2.5575 | 2.5575 | 2.5575 | 2.5575 | 2.3425 | 2.9733 | 2.9733 | 2.9733 | 2.9733 | 2.9733
2020-04-06 11:00 | Winter | 1.3146 | 2.0214 | 3.0588 | 3.0588 | 3.0588 | 3.0588 | 0.80306 | 0.80306 | 0.80306 | 0.80306 | 0.80306 | 0.80306 | 2.172 | 3.133 | 3.7627 | 4.0941 | 4.7569 | 5.4197 | 0.71256 | 1.9356 | 2.4277 | 2.4277 | 2.4277 | 2.4277 | 1.9624 | 2.4908 | 2.4908 | 2.4908 | 2.4908 | 2.4908
2020-04-06 12:00 | Winter | 1.3146 | 2.0214 | 3.0588 | 3.0588 | 3.0588 | 3.0588 | 0.73447 | 0.73447 | 0.73447 | 0.73447 | 0.73447 | 0.73447 | 2.2863 | 3.2979 | 3.9607 | 4.3096 | 5.0072 | 5.7049 | 0.724 | 1.9667 | 2.4667 | 2.4667 | 2.4667 | 2.4667 | 1.9243 | 2.4425 | 2.4425 | 2.4425 | 2.4425 | 2.4425
2020-04-06 13:00 | Winter | 1.2956 | 1.9921 | 3.0144 | 3.0144 | 3.0144 | 3.0144 | 0.78591 | 0.78591 | 0.78591 | 0.78591 | 0.78591 | 0.78591 | 2.3244 | 3.3529 | 4.0267 | 4.3814 | 5.0907 | 5.8 | 0.6897 | 1.8735 | 2.3498 | 2.3498 | 2.3498 | 2.3498 | 1.9053 | 2.4183 | 2.4183 | 2.4183 | 2.4183 | 2.4183
2020-04-06 14:00 | Winter | 1.3527 | 2.08 | 3.1474 | 3.1474 | 3.1474 | 3.1474 | 0.81164 | 0.81164 | 0.81164 | 0.81164 | 0.81164 | 0.81164 | 2.2101 | 3.188 | 3.8287 | 4.1659 | 4.8403 | 5.5147 | 0.65922 | 1.7907 | 2.246 | 2.246 | 2.246 | 2.246 | 1.8481 | 2.3458 | 2.3458 | 2.3458 | 2.3458 | 2.3458
2020-04-06 15:00 | Winter | 1.2384 | 1.9042 | 2.8814 | 2.8814 | 2.8814 | 2.8814 | 0.79163 | 0.79163 | 0.79163 | 0.79163 | 0.79163 | 0.79163 | 2.1339 | 3.0781 | 3.6967 | 4.0223 | 4.6734 | 5.3246 | 0.63635 | 1.7286 | 2.1681 | 2.1681 | 2.1681 | 2.1681 | 1.8672 | 2.3699 | 2.3699 | 2.3699 | 2.3699 | 2.3699
2020-04-06 16:00 | Winter | 1.086 | 1.6698 | 2.5268 | 2.5268 | 2.5268 | 2.5268 | 0.78306 | 0.78306 | 0.78306 | 0.78306 | 0.78306 | 0.78306 | 2.1148 | 3.0506 | 3.6637 | 3.9863 | 4.6317 | 5.277 | 0.66303 | 1.8011 | 2.2589 | 2.2589 | 2.2589 | 2.2589 | 1.7896 | 2.2715 | 2.2715 | 2.2715 | 2.2715 | 2.2715
2020-04-06 17:00 | Winter | 0.98563 | 1.5155 | 2.2933 | 2.2933 | 2.2933 | 2.2933 | 0.67668 | 0.67668 | 0.67668 | 0.67668 | 0.67668 | 0.67668 | 2.0686 | 2.9839 | 3.5836 | 3.8992 | 4.5304 | 5.1616 | 0.57423 | 1.5598 | 1.9564 | 1.9564 | 1.9564 | 1.9564 | 1.5675 | 1.9896 | 1.9896 | 1.9896 | 1.9896 | 1.9896
2020-04-06 18:00 | Winter | 0.87614 | 1.3472 | 2.0385 | 2.0385 | 2.0385 | 2.0385 | 0.55632 | 0.55632 | 0.55632 | 0.55632 | 0.55632 | 0.55632 | 2.0174 | 2.9101 | 3.4949 | 3.8027 | 4.4184 | 5.034 | 0.56028 | 1.5219 | 1.9089 | 1.9089 | 1.9089 | 1.9089 | 1.3576 | 1.7232 | 1.7232 | 1.7232 | 1.7232 | 1.7232
2020-04-06 19:00 | Winter | 0.76664 | 1.1788 | 1.7838 | 1.7838 | 1.7838 | 1.7838 | 0.43596 | 0.43596 | 0.43596 | 0.43596 | 0.43596 | 0.43596 | 1.9663 | 2.8363 | 3.4063 | 3.7063 | 4.3063 | 4.9064 | 0.54632 | 1.484 | 1.8613 | 1.8613 | 1.8613 | 1.8613 | 1.1478 | 1.4568 | 1.4568 | 1.4568 | 1.4568 | 1.4568
2020-04-06 20:00 | Winter | 0.65715 | 1.0104 | 1.529 | 1.529 | 1.529 | 1.529 | 0.31722 | 0.31722 | 0.31722 | 0.31722 | 0.31722 | 0.31722 | 1.9151 | 2.7625 | 3.3177 | 3.6099 | 4.1943 | 4.7787 | 0.60587 | 1.6458 | 2.0642 | 2.0642 | 2.0642 | 2.0642 | 0.93792 | 1.1905 | 1.1905 | 1.1905 | 1.1905 | 1.1905
2020-04-06 21:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 1.8672 | 2.6933 | 3.2346 | 3.5195 | 4.0892 | 4.659 | 0.58301 | 1.5837 | 1.9863 | 1.9863 | 1.9863 | 1.9863 | 0.84008 | 1.0663 | 1.0663 | 1.0663 | 1.0663 | 1.0663
2020-04-06 22:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.33723 | 0.33723 | 0.33723 | 0.33723 | 0.33723 | 0.33723 | 1.7909 | 2.5834 | 3.1026 | 3.3758 | 3.9223 | 4.4688 | 0.53347 | 1.4491 | 1.8175 | 1.8175 | 1.8175 | 1.8175 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-04-06 23:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.3258 | 0.3258 | 0.3258 | 0.3258 | 0.3258 | 0.3258 | 1.677 | 2.4191 | 2.9053 | 3.1611 | 3.6729 | 4.1847 | 0.51061 | 1.387 | 1.7396 | 1.7396 | 1.7396 | 1.7396 | 0.7621 | 0.96732 | 0.96732 | 0.96732 | 0.96732 | 0.96732
2020-04-07 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 1.6004 | 2.3086 | 2.7725 | 3.0167 | 3.5051 | 3.9934 | 0.50299 | 1.3663 | 1.7137 | 1.7137 | 1.7137 | 1.7137 | 0.78115 | 0.9915 | 0.9915 | 0.9915 | 0.9915 | 0.9915
2020-04-07 01:00 | Winter | 0.55287 | 0.8501 | 1.2864 | 1.2864 | 1.2864 | 1.2864 | 0.38581 | 0.38581 | 0.38581 | 0.38581 | 0.38581 | 0.38581 | 1.5242 | 2.1986 | 2.6405 | 2.873 | 3.3382 | 3.8033 | 0.49155 | 1.3353 | 1.6747 | 1.6747 | 1.6747 | 1.6747 | 0.7621 | 0.96732 | 0.96732 | 0.96732 | 0.96732 | 0.96732
2020-04-07 02:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.33151 | 0.33151 | 0.33151 | 0.33151 | 0.33151 | 0.33151 | 1.5433 | 2.2261 | 2.6735 | 2.909 | 3.3799 | 3.8508 | 0.4725 | 1.2835 | 1.6098 | 1.6098 | 1.6098 | 1.6098 | 0.78115 | 0.9915 | 0.9915 | 0.9915 | 0.9915 | 0.9915
2020-04-07 03:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.28582 | 0.28582 | 0.28582 | 0.28582 | 0.28582 | 0.28582 | 1.5433 | 2.2261 | 2.6735 | 2.909 | 3.3799 | 3.8508 | 0.48393 | 1.3146 | 1.6488 | 1.6488 | 1.6488 | 1.6488 | 0.78115 | 0.9915 | 0.9915 | 0.9915 | 0.9915 | 0.9915
2020-04-07 04:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.47726 | 0.47726 | 0.47726 | 0.47726 | 0.47726 | 0.47726 | 1.5623 | 2.2536 | 2.7065 | 2.9449 | 3.4216 | 3.8984 | 0.48012 | 1.3042 | 1.6358 | 1.6358 | 1.6358 | 1.6358 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-04-07 05:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.47726 | 0.47726 | 0.47726 | 0.47726 | 0.47726 | 0.47726 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.50299 | 1.3663 | 1.7137 | 1.7137 | 1.7137 | 1.7137 | 1.1527 | 1.4631 | 1.4631 | 1.4631 | 1.4631 | 1.4631
2020-04-07 06:00 | Winter | 0.68589 | 1.0546 | 1.5959 | 1.5959 | 1.5959 | 1.5959 | 0.60015 | 0.60015 | 0.60015 | 0.60015 | 0.60015 | 0.60015 | 1.7909 | 2.5834 | 3.1026 | 3.3758 | 3.9223 | 4.4688 | 0.51061 | 1.387 | 1.7396 | 1.7396 | 1.7396 | 1.7396 | 1.4091 | 1.7886 | 1.7886 | 1.7886 | 1.7886 | 1.7886
2020-04-07 07:00 | Winter | 0.79995 | 1.23 | 1.8613 | 1.8613 | 1.8613 | 1.8613 | 0.78591 | 0.78591 | 0.78591 | 0.78591 | 0.78591 | 0.78591 | 2.0577 | 2.9681 | 3.5647 | 3.8786 | 4.5065 | 5.1344 | 0.73543 | 1.9977 | 2.5056 | 2.5056 | 2.5056 | 2.5056 | 1.7909 | 2.2732 | 2.2732 | 2.2732 | 2.2732 | 2.2732
2020-04-07 08:00 | Winter | 1.105 | 1.6991 | 2.5711 | 2.5711 | 2.5711 | 2.5711 | 0.81735 | 0.81735 | 0.81735 | 0.81735 | 0.81735 | 0.81735 | 2.172 | 3.133 | 3.7627 | 4.0941 | 4.7569 | 5.4197 | 0.70875 | 1.9253 | 2.4147 | 2.4147 | 2.4147 | 2.4147 | 1.9624 | 2.4908 | 2.4908 | 2.4908 | 2.4908 | 2.4908
2020-04-07 09:00 | Winter | 1.1432 | 1.7577 | 2.6598 | 2.6598 | 2.6598 | 2.6598 | 0.82592 | 0.82592 | 0.82592 | 0.82592 | 0.82592 | 0.82592 | 2.1148 | 3.0506 | 3.6637 | 3.9863 | 4.6317 | 5.277 | 0.71256 | 1.9356 | 2.4277 | 2.4277 | 2.4277 | 2.4277 | 1.9815 | 2.515 | 2.515 | 2.515 | 2.515 | 2.515
2020-04-07 10:00 | Winter | 1.1432 | 1.7577 | 2.6598 | 2.6598 | 2.6598 | 2.6598 | 0.79449 | 0.79449 | 0.79449 | 0.79449 | 0.79449 | 0.79449 | 2.191 | 3.1605 | 3.7957 | 4.13 | 4.7986 | 5.4672 | 0.724 | 1.9667 | 2.4667 | 2.4667 | 2.4667 | 2.4667 | 1.9434 | 2.4667 | 2.4667 | 2.4667 | 2.4667 | 2.4667
2020-04-07 11:00 | Winter | 1.3908 | 2.1386 | 3.2361 | 3.2361 | 3.2361 | 3.2361 | 0.76877 | 0.76877 | 0.76877 | 0.76877 | 0.76877 | 0.76877 | 2.2101 | 3.188 | 3.8287 | 4.1659 | 4.8403 | 5.5147 | 0.69732 | 1.8942 | 2.3758 | 2.3758 | 2.3758 | 2.3758 | 1.9053 | 2.4183 | 2.4183 | 2.4183 | 2.4183 | 2.4183
2020-04-07 12:00 | Winter | 1.2765 | 1.9628 | 2.9701 | 2.9701 | 2.9701 | 2.9701 | 0.76019 | 0.76019 | 0.76019 | 0.76019 | 0.76019 | 0.76019 | 2.3054 | 3.3254 | 3.9937 | 4.3455 | 5.049 | 5.7525 | 0.67827 | 1.8425 | 2.3109 | 2.3109 | 2.3109 | 2.3109 | 1.9053 | 2.4183 | 2.4183 | 2.4183 | 2.4183 | 2.4183
2020-04-07 13:00 | Winter | 1.2003 | 1.8456 | 2.7928 | 2.7928 | 2.7928 | 2.7928 | 0.72304 | 0.72304 | 0.72304 | 0.72304 | 0.72304 | 0.72304 | 2.2101 | 3.188 | 3.8287 | 4.1659 | 4.8403 | 5.5147 | 0.69351 | 1.8839 | 2.3628 | 2.3628 | 2.3628 | 2.3628 | 1.9053 | 2.4183 | 2.4183 | 2.4183 | 2.4183 | 2.4183
2020-04-07 14:00 | Winter | 1.1791 | 1.8131 | 2.7435 | 2.7435 | 2.7435 | 2.7435 | 0.76305 | 0.76305 | 0.76305 | 0.76305 | 0.76305 | 0.76305 | 2.1529 | 3.1056 | 3.7297 | 4.0582 | 4.7151 | 5.3721 | 0.73162 | 1.9874 | 2.4926 | 2.4926 | 2.4926 | 2.4926 | 1.829 | 2.3216 | 2.3216 | 2.3216 | 2.3216 | 2.3216
2020-04-07 15:00 | Winter | 1.1622 | 1.787 | 2.7041 | 2.7041 | 2.7041 | 2.7041 | 0.76019 | 0.76019 | 0.76019 | 0.76019 | 0.76019 | 0.76019 | 2.1339 | 3.0781 | 3.6967 | 4.0223 | 4.6734 | 5.3246 | 0.73924 | 2.0081 | 2.5186 | 2.5186 | 2.5186 | 2.5186 | 1.7909 | 2.2732 | 2.2732 | 2.2732 | 2.2732 | 2.2732
2020-04-07 16:00 | Winter | 1.1622 | 1.787 | 2.7041 | 2.7041 | 2.7041 | 2.7041 | 0.78306 | 0.78306 | 0.78306 | 0.78306 | 0.78306 | 0.78306 | 2.0958 | 3.0231 | 3.6307 | 3.9504 | 4.59 | 5.2295 | 0.70494 | 1.9149 | 2.4018 | 2.4018 | 2.4018 | 2.4018 | 1.7528 | 2.2248 | 2.2248 | 2.2248 | 2.2248 | 2.2248
2020-04-07 17:00 | Winter | 1.086 | 1.6698 | 2.5268 | 2.5268 | 2.5268 | 2.5268 | 0.70018 | 0.70018 | 0.70018 | 0.70018 | 0.70018 | 0.70018 | 2.1148 | 3.0506 | 3.6637 | 3.9863 | 4.6317 | 5.277 | 0.63635 | 1.7286 | 2.1681 | 2.1681 | 2.1681 | 2.1681 | 1.6969 | 2.1538 | 2.1538 | 2.1538 | 2.1538 | 2.1538
2020-04-07 18:00 | Winter | 0.80144 | 1.2323 | 1.8647 | 1.8647 | 1.8647 | 1.8647 | 0.60094 | 0.60094 | 0.60094 | 0.60094 | 0.60094 | 0.60094 | 2.172 | 3.133 | 3.7627 | 4.0941 | 4.7569 | 5.4197 | 0.69351 | 1.8839 | 2.3628 | 2.3628 | 2.3628 | 2.3628 | 1.3516 | 1.7156 | 1.7156 | 1.7156 | 1.7156 | 1.7156
2020-04-07 19:00 | Winter | 0.68589 | 1.0546 | 1.5959 | 1.5959 | 1.5959 | 1.5959 | 0.37137 | 0.37137 | 0.37137 | 0.37137 | 0.37137 | 0.37137 | 2.0579 | 2.9685 | 3.5651 | 3.8791 | 4.5071 | 5.1351 | 0.63254 | 1.7182 | 2.1551 | 2.1551 | 2.1551 | 2.1551 | 1.0098 | 1.2817 | 1.2817 | 1.2817 | 1.2817 | 1.2817
2020-04-07 20:00 | Winter | 0.58574 | 0.90064 | 1.3628 | 1.3628 | 1.3628 | 1.3628 | 0.32008 | 0.32008 | 0.32008 | 0.32008 | 0.32008 | 0.32008 | 1.8672 | 2.6933 | 3.2346 | 3.5195 | 4.0892 | 4.659 | 0.60968 | 1.6561 | 2.0772 | 2.0772 | 2.0772 | 2.0772 | 0.97168 | 1.2333 | 1.2333 | 1.2333 | 1.2333 | 1.2333
2020-04-07 21:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 1.829 | 2.6383 | 3.1686 | 3.4477 | 4.0058 | 4.5639 | 0.59825 | 1.6251 | 2.0382 | 2.0382 | 2.0382 | 2.0382 | 0.8575 | 1.0884 | 1.0884 | 1.0884 | 1.0884 | 1.0884
2020-04-07 22:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 1.7528 | 2.5284 | 3.0366 | 3.304 | 3.8389 | 4.3738 | 0.5792 | 1.5733 | 1.9733 | 1.9733 | 1.9733 | 1.9733 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-04-07 23:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.39153 | 0.39153 | 0.39153 | 0.39153 | 0.39153 | 0.39153 | 1.6576 | 2.391 | 2.8715 | 3.1244 | 3.6302 | 4.1361 | 0.52204 | 1.4181 | 1.7786 | 1.7786 | 1.7786 | 1.7786 | 0.7621 | 0.96732 | 0.96732 | 0.96732 | 0.96732 | 0.96732
2020-04-08 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.41153 | 0.41153 | 0.41153 | 0.41153 | 0.41153 | 0.41153 | 1.6195 | 2.336 | 2.8055 | 3.0526 | 3.5468 | 4.041 | 0.47631 | 1.2939 | 1.6228 | 1.6228 | 1.6228 | 1.6228 | 0.78115 | 0.9915 | 0.9915 | 0.9915 | 0.9915 | 0.9915
2020-04-08 01:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.38009 | 0.38009 | 0.38009 | 0.38009 | 0.38009 | 0.38009 | 1.5242 | 2.1986 | 2.6405 | 2.873 | 3.3382 | 3.8033 | 0.49918 | 1.356 | 1.7007 | 1.7007 | 1.7007 | 1.7007 | 0.7621 | 0.96732 | 0.96732 | 0.96732 | 0.96732 | 0.96732
2020-04-08 02:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.38295 | 0.38295 | 0.38295 | 0.38295 | 0.38295 | 0.38295 | 1.5242 | 2.1986 | 2.6405 | 2.873 | 3.3382 | 3.8033 | 0.48012 | 1.3042 | 1.6358 | 1.6358 | 1.6358 | 1.6358 | 0.78115 | 0.9915 | 0.9915 | 0.9915 | 0.9915 | 0.9915
2020-04-08 03:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.41153 | 0.41153 | 0.41153 | 0.41153 | 0.41153 | 0.41153 | 1.5242 | 2.1986 | 2.6405 | 2.873 | 3.3382 | 3.8033 | 0.50299 | 1.3663 | 1.7137 | 1.7137 | 1.7137 | 1.7137 | 0.78115 | 0.9915 | 0.9915 | 0.9915 | 0.9915 | 0.9915
2020-04-08 04:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.36295 | 0.36295 | 0.36295 | 0.36295 | 0.36295 | 0.36295 | 1.5623 | 2.2536 | 2.7065 | 2.9449 | 3.4216 | 3.8984 | 0.46107 | 1.2525 | 1.5709 | 1.5709 | 1.5709 | 1.5709 | 0.83794 | 1.0636 | 1.0636 | 1.0636 | 1.0636 | 1.0636
2020-04-08 05:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 1.5623 | 2.2536 | 2.7065 | 2.9449 | 3.4216 | 3.8984 | 0.54871 | 1.4905 | 1.8695 | 1.8695 | 1.8695 | 1.8695 | 1.1075 | 1.4057 | 1.4057 | 1.4057 | 1.4057 | 1.4057
2020-04-08 06:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.65731 | 0.65731 | 0.65731 | 0.65731 | 0.65731 | 0.65731 | 1.7057 | 2.4604 | 2.9549 | 3.2151 | 3.7356 | 4.2561 | 0.56395 | 1.5319 | 1.9214 | 1.9214 | 1.9214 | 1.9214 | 1.333 | 1.692 | 1.692 | 1.692 | 1.692 | 1.692
2020-04-08 07:00 | Winter | 0.84206 | 1.2948 | 1.9592 | 1.9592 | 1.9592 | 1.9592 | 0.6918 | 0.6918 | 0.6918 | 0.6918 | 0.6918 | 0.6918 | 1.8481 | 2.6658 | 3.2016 | 3.4836 | 4.0475 | 4.6115 | 0.65541 | 1.7803 | 2.233 | 2.233 | 2.233 | 2.233 | 1.7036 | 2.1624 | 2.1624 | 2.1624 | 2.1624 | 2.1624
2020-04-08 08:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.74019 | 0.74019 | 0.74019 | 0.74019 | 0.74019 | 0.74019 | 2.0958 | 3.0231 | 3.6307 | 3.9504 | 4.59 | 5.2295 | 0.68208 | 1.8528 | 2.3239 | 2.3239 | 2.3239 | 2.3239 | 1.9243 | 2.4425 | 2.4425 | 2.4425 | 2.4425 | 2.4425
2020-04-08 09:00 | Winter | 1.0669 | 1.6405 | 2.4825 | 2.4825 | 2.4825 | 2.4825 | 0.71694 | 0.71694 | 0.71694 | 0.71694 | 0.71694 | 0.71694 | 2.1148 | 3.0506 | 3.6637 | 3.9863 | 4.6317 | 5.277 | 0.68208 | 1.8528 | 2.3239 | 2.3239 | 2.3239 | 2.3239 | 1.9195 | 2.4363 | 2.4363 | 2.4363 | 2.4363 | 2.4363
2020-04-08 10:00 | Winter | 1.0288 | 1.582 | 2.3938 | 2.3938 | 2.3938 | 2.3938 | 0.71733 | 0.71733 | 0.71733 | 0.71733 | 0.71733 | 0.71733 | 2.2593 | 3.259 | 3.914 | 4.2587 | 4.9482 | 5.6376 | 0.68589 | 1.8632 | 2.3368 | 2.3368 | 2.3368 | 2.3368 | 1.9053 | 2.4183 | 2.4183 | 2.4183 | 2.4183 | 2.4183
2020-04-08 11:00 | Winter | 1.1813 | 1.8163 | 2.7485 | 2.7485 | 2.7485 | 2.7485 | 0.70875 | 0.70875 | 0.70875 | 0.70875 | 0.70875 | 0.70875 | 2.2863 | 3.2979 | 3.9607 | 4.3096 | 5.0072 | 5.7049 | 0.79258 | 2.153 | 2.7003 | 2.7003 | 2.7003 | 2.7003 | 1.8672 | 2.3699 | 2.3699 | 2.3699 | 2.3699 | 2.3699
2020-04-08 12:00 | Winter | 1.2194 | 1.8749 | 2.8371 | 2.8371 | 2.8371 | 2.8371 | 0.73733 | 0.73733 | 0.73733 | 0.73733 | 0.73733 | 0.73733 | 2.2863 | 3.2979 | 3.9607 | 4.3096 | 5.0072 | 5.7049 | 0.724 | 1.9667 | 2.4667 | 2.4667 | 2.4667 | 2.4667 | 1.8862 | 2.3941 | 2.3941 | 2.3941 | 2.3941 | 2.3941
2020-04-08 13:00 | Winter | 1.2194 | 1.8749 | 2.8371 | 2.8371 | 2.8371 | 2.8371 | 0.72018 | 0.72018 | 0.72018 | 0.72018 | 0.72018 | 0.72018 | 2.172 | 3.133 | 3.7627 | 4.0941 | 4.7569 | 5.4197 | 0.73162 | 1.9874 | 2.4926 | 2.4926 | 2.4926 | 2.4926 | 1.9434 | 2.4667 | 2.4667 | 2.4667 | 2.4667 | 2.4667
2020-04-08 14:00 | Winter | 1.2194 | 1.8749 | 2.8371 | 2.8371 | 2.8371 | 2.8371 | 0.7459 | 0.7459 | 0.7459 | 0.7459 | 0.7459 | 0.7459 | 2.191 | 3.1605 | 3.7957 | 4.13 | 4.7986 | 5.4672 | 0.67446 | 1.8321 | 2.2979 | 2.2979 | 2.2979 | 2.2979 | 1.8481 | 2.3458 | 2.3458 | 2.3458 | 2.3458 | 2.3458
2020-04-08 15:00 | Winter | 1.2194 | 1.8749 | 2.8371 | 2.8371 | 2.8371 | 2.8371 | 0.8002 | 0.8002 | 0.8002 | 0.8002 | 0.8002 | 0.8002 | 2.1529 | 3.1056 | 3.7297 | 4.0582 | 4.7151 | 5.3721 | 0.68589 | 1.8632 | 2.3368 | 2.3368 | 2.3368 | 2.3368 | 1.81 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974
2020-04-08 16:00 | Winter | 1.1432 | 1.7577 | 2.6598 | 2.6598 | 2.6598 | 2.6598 | 0.78306 | 0.78306 | 0.78306 | 0.78306 | 0.78306 | 0.78306 | 2.1214 | 3.0601 | 3.6751 | 3.9987 | 4.6461 | 5.2935 | 0.68208 | 1.8528 | 2.3239 | 2.3239 | 2.3239 | 2.3239 | 1.829 | 2.3216 | 2.3216 | 2.3216 | 2.3216 | 2.3216
2020-04-08 17:00 | Winter | 0.97064 | 1.4925 | 2.2584 | 2.2584 | 2.2584 | 2.2584 | 0.68589 | 0.68589 | 0.68589 | 0.68589 | 0.68589 | 0.68589 | 2.1906 | 3.1599 | 3.7949 | 4.1291 | 4.7976 | 5.4661 | 0.68589 | 1.8632 | 2.3368 | 2.3368 | 2.3368 | 2.3368 | 1.7074 | 2.1671 | 2.1671 | 2.1671 | 2.1671 | 2.1671
2020-04-08 18:00 | Winter | 0.8287 | 1.2742 | 1.9282 | 1.9282 | 1.9282 | 1.9282 | 0.55828 | 0.55828 | 0.55828 | 0.55828 | 0.55828 | 0.55828 | 2.2291 | 3.2155 | 3.8617 | 4.2018 | 4.8821 | 5.5623 | 0.68208 | 1.8528 | 2.3239 | 2.3239 | 2.3239 | 2.3239 | 1.3918 | 1.7666 | 1.7666 | 1.7666 | 1.7666 | 1.7666
2020-04-08 19:00 | Winter | 0.66684 | 1.0253 | 1.5515 | 1.5515 | 1.5515 | 1.5515 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 2.1034 | 3.0342 | 3.6439 | 3.9649 | 4.6067 | 5.2486 | 0.62492 | 1.6975 | 2.1291 | 2.1291 | 2.1291 | 2.1291 | 1.0479 | 1.3301 | 1.3301 | 1.3301 | 1.3301 | 1.3301
2020-04-08 20:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.33151 | 0.33151 | 0.33151 | 0.33151 | 0.33151 | 0.33151 | 2.0005 | 2.8857 | 3.4656 | 3.7709 | 4.3813 | 4.9918 | 0.62111 | 1.6872 | 2.1161 | 2.1161 | 2.1161 | 2.1161 | 0.93358 | 1.185 | 1.185 | 1.185 | 1.185 | 1.185
2020-04-08 21:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.31151 | 0.31151 | 0.31151 | 0.31151 | 0.31151 | 0.31151 | 1.9104 | 2.7557 | 3.3096 | 3.6011 | 4.184 | 4.767 | 0.60968 | 1.6561 | 2.0772 | 2.0772 | 2.0772 | 2.0772 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-04-08 22:00 | Winter | 0.59043 | 0.90786 | 1.3738 | 1.3738 | 1.3738 | 1.3738 | 0.52299 | 0.52299 | 0.52299 | 0.52299 | 0.52299 | 0.52299 | 1.8672 | 2.6933 | 3.2346 | 3.5195 | 4.0892 | 4.659 | 0.58301 | 1.5837 | 1.9863 | 1.9863 | 1.9863 | 1.9863 | 0.81317 | 1.0321 | 1.0321 | 1.0321 | 1.0321 | 1.0321
2020-04-08 23:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.31304 | 0.31304 | 0.31304 | 0.31304 | 0.31304 | 0.31304 | 1.7338 | 2.5009 | 3.0036 | 3.2681 | 3.7972 | 4.3262 | 0.52204 | 1.4181 | 1.7786 | 1.7786 | 1.7786 | 1.7786 | 0.80021 | 1.0157 | 1.0157 | 1.0157 | 1.0157 | 1.0157
2020-04-09 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.30152 | 0.30152 | 0.30152 | 0.30152 | 0.30152 | 0.30152 | 1.6004 | 2.3086 | 2.7725 | 3.0167 | 3.5051 | 3.9934 | 0.51823 | 1.4077 | 1.7656 | 1.7656 | 1.7656 | 1.7656 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-04-09 01:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.40296 | 0.40296 | 0.40296 | 0.40296 | 0.40296 | 0.40296 | 1.5433 | 2.2261 | 2.6735 | 2.909 | 3.3799 | 3.8508 | 0.53728 | 1.4595 | 1.8305 | 1.8305 | 1.8305 | 1.8305 | 0.78115 | 0.9915 | 0.9915 | 0.9915 | 0.9915 | 0.9915
2020-04-09 02:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.51442 | 0.51442 | 0.51442 | 0.51442 | 0.51442 | 0.51442 | 1.5433 | 2.2261 | 2.6735 | 2.909 | 3.3799 | 3.8508 | 0.50912 | 1.383 | 1.7346 | 1.7346 | 1.7346 | 1.7346 | 0.78115 | 0.9915 | 0.9915 | 0.9915 | 0.9915 | 0.9915
2020-04-09 03:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.30579 | 0.30579 | 0.30579 | 0.30579 | 0.30579 | 0.30579 | 1.5623 | 2.2536 | 2.7065 | 2.9449 | 3.4216 | 3.8984 | 0.51061 | 1.387 | 1.7396 | 1.7396 | 1.7396 | 1.7396 | 0.7621 | 0.96732 | 0.96732 | 0.96732 | 0.96732 | 0.96732
2020-04-09 04:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.31436 | 0.31436 | 0.31436 | 0.31436 | 0.31436 | 0.31436 | 1.6004 | 2.3086 | 2.7725 | 3.0167 | 3.5051 | 3.9934 | 0.49155 | 1.3353 | 1.6747 | 1.6747 | 1.6747 | 1.6747 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-04-09 05:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 1.6766 | 2.4185 | 2.9045 | 3.1603 | 3.672 | 4.1836 | 0.52204 | 1.4181 | 1.7786 | 1.7786 | 1.7786 | 1.7786 | 1.1175 | 1.4184 | 1.4184 | 1.4184 | 1.4184 | 1.4184
2020-04-09 06:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.64302 | 0.64302 | 0.64302 | 0.64302 | 0.64302 | 0.64302 | 1.7719 | 2.5559 | 3.0696 | 3.3399 | 3.8806 | 4.4213 | 0.53347 | 1.4491 | 1.8175 | 1.8175 | 1.8175 | 1.8175 | 1.3329 | 1.6919 | 1.6919 | 1.6919 | 1.6919 | 1.6919
2020-04-09 07:00 | Winter | 0.89782 | 1.3805 | 2.089 | 2.089 | 2.089 | 2.089 | 1.006 | 1.006 | 1.006 | 1.006 | 1.006 | 1.006 | 2.0386 | 2.9407 | 3.5316 | 3.8427 | 4.4648 | 5.0869 | 0.64397 | 1.7493 | 2.194 | 2.194 | 2.194 | 2.194 | 1.6957 | 2.1523 | 2.1523 | 2.1523 | 2.1523 | 2.1523
2020-04-09 08:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.90595 | 0.90595 | 0.90595 | 0.90595 | 0.90595 | 0.90595 | 2.0767 | 2.9956 | 3.5977 | 3.9145 | 4.5482 | 5.182 | 0.72781 | 1.977 | 2.4796 | 2.4796 | 2.4796 | 2.4796 | 1.9053 | 2.4183 | 2.4183 | 2.4183 | 2.4183 | 2.4183
2020-04-09 09:00 | Winter | 1.0669 | 1.6405 | 2.4825 | 2.4825 | 2.4825 | 2.4825 | 0.87737 | 0.87737 | 0.87737 | 0.87737 | 0.87737 | 0.87737 | 2.172 | 3.133 | 3.7627 | 4.0941 | 4.7569 | 5.4197 | 0.73162 | 1.9874 | 2.4926 | 2.4926 | 2.4926 | 2.4926 | 1.9243 | 2.4425 | 2.4425 | 2.4425 | 2.4425 | 2.4425
2020-04-09 10:00 | Winter | 1.2384 | 1.9042 | 2.8814 | 2.8814 | 2.8814 | 2.8814 | 0.82592 | 0.82592 | 0.82592 | 0.82592 | 0.82592 | 0.82592 | 2.1529 | 3.1056 | 3.7297 | 4.0582 | 4.7151 | 5.3721 | 0.6897 | 1.8735 | 2.3498 | 2.3498 | 2.3498 | 2.3498 | 1.9243 | 2.4425 | 2.4425 | 2.4425 | 2.4425 | 2.4425
2020-04-09 11:00 | Winter | 1.2765 | 1.9628 | 2.9701 | 2.9701 | 2.9701 | 2.9701 | 0.83164 | 0.83164 | 0.83164 | 0.83164 | 0.83164 | 0.83164 | 2.1529 | 3.1056 | 3.7297 | 4.0582 | 4.7151 | 5.3721 | 0.6516 | 1.77 | 2.22 | 2.22 | 2.22 | 2.22 | 1.8862 | 2.3941 | 2.3941 | 2.3941 | 2.3941 | 2.3941
2020-04-09 12:00 | Winter | 1.2575 | 1.9335 | 2.9258 | 2.9258 | 2.9258 | 2.9258 | 0.8345 | 0.8345 | 0.8345 | 0.8345 | 0.8345 | 0.8345 | 2.172 | 3.133 | 3.7627 | 4.0941 | 4.7569 | 5.4197 | 0.79258 | 2.153 | 2.7003 | 2.7003 | 2.7003 | 2.7003 | 1.8481 | 2.3458 | 2.3458 | 2.3458 | 2.3458 | 2.3458
2020-04-09 13:00 | Winter | 1.2956 | 1.9921 | 3.0144 | 3.0144 | 3.0144 | 3.0144 | 0.85736 | 0.85736 | 0.85736 | 0.85736 | 0.85736 | 0.85736 | 2.2863 | 3.2979 | 3.9607 | 4.3096 | 5.0072 | 5.7049 | 0.70113 | 1.9046 | 2.3888 | 2.3888 | 2.3888 | 2.3888 | 1.8862 | 2.3941 | 2.3941 | 2.3941 | 2.3941 | 2.3941
2020-04-09 14:00 | Winter | 1.3337 | 2.0507 | 3.1031 | 3.1031 | 3.1031 | 3.1031 | 0.82878 | 0.82878 | 0.82878 | 0.82878 | 0.82878 | 0.82878 | 2.191 | 3.1605 | 3.7957 | 4.13 | 4.7986 | 5.4672 | 0.73162 | 1.9874 | 2.4926 | 2.4926 | 2.4926 | 2.4926 | 1.9053 | 2.4183 | 2.4183 | 2.4183 | 2.4183 | 2.4183
2020-04-09 15:00 | Winter | 1.3146 | 2.0214 | 3.0588 | 3.0588 | 3.0588 | 3.0588 | 0.87451 | 0.87451 | 0.87451 | 0.87451 | 0.87451 | 0.87451 | 2.2101 | 3.188 | 3.8287 | 4.1659 | 4.8403 | 5.5147 | 0.71637 | 1.946 | 2.4407 | 2.4407 | 2.4407 | 2.4407 | 1.9243 | 2.4425 | 2.4425 | 2.4425 | 2.4425 | 2.4425
2020-04-09 16:00 | Winter | 1.232 | 1.8943 | 2.8665 | 2.8665 | 2.8665 | 2.8665 | 0.80306 | 0.80306 | 0.80306 | 0.80306 | 0.80306 | 0.80306 | 2.1148 | 3.0506 | 3.6637 | 3.9863 | 4.6317 | 5.277 | 0.69732 | 1.8942 | 2.3758 | 2.3758 | 2.3758 | 2.3758 | 1.7528 | 2.2248 | 2.2248 | 2.2248 | 2.2248 | 2.2248
2020-04-09 17:00 | Winter | 1.1432 | 1.7577 | 2.6598 | 2.6598 | 2.6598 | 2.6598 | 0.7802 | 0.7802 | 0.7802 | 0.7802 | 0.7802 | 0.7802 | 2.1529 | 3.1056 | 3.7297 | 4.0582 | 4.7151 | 5.3721 | 0.70875 | 1.9253 | 2.4147 | 2.4147 | 2.4147 | 2.4147 | 1.6633 | 2.1111 | 2.1111 | 2.1111 | 2.1111 | 2.1111
2020-04-09 18:00 | Winter | 0.79593 | 1.2238 | 1.8519 | 1.8519 | 1.8519 | 1.8519 | 0.63445 | 0.63445 | 0.63445 | 0.63445 | 0.63445 | 0.63445 | 2.191 | 3.1605 | 3.7957 | 4.13 | 4.7986 | 5.4672 | 0.70494 | 1.9149 | 2.4018 | 2.4018 | 2.4018 | 2.4018 | 1.3104 | 1.6632 | 1.6632 | 1.6632 | 1.6632 | 1.6632
2020-04-09 19:00 | Winter | 0.64947 | 0.99863 | 1.5111 | 1.5111 | 1.5111 | 1.5111 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 2.1148 | 3.0506 | 3.6637 | 3.9863 | 4.6317 | 5.277 | 0.65541 | 1.7803 | 2.233 | 2.233 | 2.233 | 2.233 | 0.97168 | 1.2333 | 1.2333 | 1.2333 | 1.2333 | 1.2333
2020-04-09 20:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.48869 | 0.48869 | 0.48869 | 0.48869 | 0.48869 | 0.48869 | 2.0767 | 2.9956 | 3.5977 | 3.9145 | 4.5482 | 5.182 | 0.59063 | 1.6044 | 2.0123 | 2.0123 | 2.0123 | 2.0123 | 0.95263 | 1.2092 | 1.2092 | 1.2092 | 1.2092 | 1.2092
2020-04-09 21:00 | Winter | 0.5909 | 0.90858 | 1.3749 | 1.3749 | 1.3749 | 1.3749 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 1.8862 | 2.7208 | 3.2676 | 3.5554 | 4.131 | 4.7066 | 0.60587 | 1.6458 | 2.0642 | 2.0642 | 2.0642 | 2.0642 | 0.87329 | 1.1085 | 1.1085 | 1.1085 | 1.1085 | 1.1085
2020-04-09 22:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.42582 | 0.42582 | 0.42582 | 0.42582 | 0.42582 | 0.42582 | 1.829 | 2.6383 | 3.1686 | 3.4477 | 4.0058 | 4.5639 | 0.55633 | 1.5112 | 1.8954 | 1.8954 | 1.8954 | 1.8954 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-04-09 23:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 1.7147 | 2.4735 | 2.9705 | 3.2322 | 3.7554 | 4.2787 | 0.5449 | 1.4802 | 1.8565 | 1.8565 | 1.8565 | 1.8565 | 0.80021 | 1.0157 | 1.0157 | 1.0157 | 1.0157 | 1.0157
2020-04-10 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.41439 | 0.41439 | 0.41439 | 0.41439 | 0.41439 | 0.41439 | 1.6004 | 2.3086 | 2.7725 | 3.0167 | 3.5051 | 3.9934 | 0.56395 | 1.5319 | 1.9214 | 1.9214 | 1.9214 | 1.9214 | 0.78115 | 0.9915 | 0.9915 | 0.9915 | 0.9915 | 0.9915
2020-04-10 01:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.38867 | 0.38867 | 0.38867 | 0.38867 | 0.38867 | 0.38867 | 1.5814 | 2.2811 | 2.7395 | 2.9808 | 3.4633 | 3.9459 | 0.56395 | 1.5319 | 1.9214 | 1.9214 | 1.9214 | 1.9214 | 0.7621 | 0.96732 | 0.96732 | 0.96732 | 0.96732 | 0.96732
2020-04-10 02:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.38295 | 0.38295 | 0.38295 | 0.38295 | 0.38295 | 0.38295 | 1.5433 | 2.2261 | 2.6735 | 2.909 | 3.3799 | 3.8508 | 0.53728 | 1.4595 | 1.8305 | 1.8305 | 1.8305 | 1.8305 | 0.7621 | 0.96732 | 0.96732 | 0.96732 | 0.96732 | 0.96732
2020-04-10 03:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 1.5433 | 2.2261 | 2.6735 | 2.909 | 3.3799 | 3.8508 | 0.53347 | 1.4491 | 1.8175 | 1.8175 | 1.8175 | 1.8175 | 0.78115 | 0.9915 | 0.9915 | 0.9915 | 0.9915 | 0.9915
2020-04-10 04:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 1.5242 | 2.1986 | 2.6405 | 2.873 | 3.3382 | 3.8033 | 0.53728 | 1.4595 | 1.8305 | 1.8305 | 1.8305 | 1.8305 | 0.7621 | 0.96732 | 0.96732 | 0.96732 | 0.96732 | 0.96732
2020-04-10 05:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 1.5814 | 2.2811 | 2.7395 | 2.9808 | 3.4633 | 3.9459 | 0.53347 | 1.4491 | 1.8175 | 1.8175 | 1.8175 | 1.8175 | 1.017 | 1.2909 | 1.2909 | 1.2909 | 1.2909 | 1.2909
2020-04-10 06:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.47441 | 0.47441 | 0.47441 | 0.47441 | 0.47441 | 0.47441 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.5449 | 1.4802 | 1.8565 | 1.8565 | 1.8565 | 1.8565 | 1.2708 | 1.613 | 1.613 | 1.613 | 1.613 | 1.613
2020-04-10 07:00 | Winter | 0.60812 | 0.93505 | 1.4149 | 1.4149 | 1.4149 | 1.4149 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 1.718 | 2.4781 | 2.9761 | 3.2383 | 3.7625 | 4.2867 | 0.54109 | 1.4698 | 1.8435 | 1.8435 | 1.8435 | 1.8435 | 1.4289 | 1.8137 | 1.8137 | 1.8137 | 1.8137 | 1.8137
2020-04-10 08:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.43439 | 0.43439 | 0.43439 | 0.43439 | 0.43439 | 0.43439 | 1.8672 | 2.6933 | 3.2346 | 3.5195 | 4.0892 | 4.659 | 0.60206 | 1.6354 | 2.0512 | 2.0512 | 2.0512 | 2.0512 | 1.467 | 1.8621 | 1.8621 | 1.8621 | 1.8621 | 1.8621
2020-04-10 09:00 | Winter | 0.5919 | 0.91012 | 1.3772 | 1.3772 | 1.3772 | 1.3772 | 0.48869 | 0.48869 | 0.48869 | 0.48869 | 0.48869 | 0.48869 | 1.9243 | 2.7758 | 3.3336 | 3.6272 | 4.2144 | 4.8016 | 0.5792 | 1.5733 | 1.9733 | 1.9733 | 1.9733 | 1.9733 | 1.4099 | 1.7895 | 1.7895 | 1.7895 | 1.7895 | 1.7895
2020-04-10 10:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.43154 | 0.43154 | 0.43154 | 0.43154 | 0.43154 | 0.43154 | 2.0386 | 2.9407 | 3.5316 | 3.8427 | 4.4648 | 5.0869 | 0.64779 | 1.7596 | 2.207 | 2.207 | 2.207 | 2.207 | 1.3908 | 1.7654 | 1.7654 | 1.7654 | 1.7654 | 1.7654
2020-04-10 11:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.43439 | 0.43439 | 0.43439 | 0.43439 | 0.43439 | 0.43439 | 2.0005 | 2.8857 | 3.4656 | 3.7709 | 4.3813 | 4.9918 | 0.61349 | 1.6665 | 2.0902 | 2.0902 | 2.0902 | 2.0902 | 1.4289 | 1.8137 | 1.8137 | 1.8137 | 1.8137 | 1.8137
2020-04-10 12:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.4544 | 0.4544 | 0.4544 | 0.4544 | 0.4544 | 0.4544 | 2.0577 | 2.9681 | 3.5647 | 3.8786 | 4.5065 | 5.1344 | 0.56014 | 1.5216 | 1.9084 | 1.9084 | 1.9084 | 1.9084 | 1.3527 | 1.717 | 1.717 | 1.717 | 1.717 | 1.717
2020-04-10 13:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.43879 | 0.43879 | 0.43879 | 0.43879 | 0.43879 | 0.43879 | 2.0577 | 2.9681 | 3.5647 | 3.8786 | 4.5065 | 5.1344 | 0.62873 | 1.7079 | 2.1421 | 2.1421 | 2.1421 | 2.1421 | 1.3146 | 1.6686 | 1.6686 | 1.6686 | 1.6686 | 1.6686
2020-04-10 14:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 2.0005 | 2.8857 | 3.4656 | 3.7709 | 4.3813 | 4.9918 | 0.56776 | 1.5423 | 1.9344 | 1.9344 | 1.9344 | 1.9344 | 1.3908 | 1.7654 | 1.7654 | 1.7654 | 1.7654 | 1.7654
2020-04-10 15:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 1.9434 | 2.8032 | 3.3666 | 3.6631 | 4.2562 | 4.8492 | 0.5449 | 1.4802 | 1.8565 | 1.8565 | 1.8565 | 1.8565 | 1.4099 | 1.7895 | 1.7895 | 1.7895 | 1.7895 | 1.7895
2020-04-10 16:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 1.9385 | 2.7962 | 3.3582 | 3.654 | 4.2455 | 4.8371 | 0.56395 | 1.5319 | 1.9214 | 1.9214 | 1.9214 | 1.9214 | 1.3718 | 1.7412 | 1.7412 | 1.7412 | 1.7412 | 1.7412
2020-04-10 17:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.51156 | 0.51156 | 0.51156 | 0.51156 | 0.51156 | 0.51156 | 1.9815 | 2.8582 | 3.4326 | 3.735 | 4.3396 | 4.9443 | 0.58682 | 1.594 | 1.9993 | 1.9993 | 1.9993 | 1.9993 | 1.3718 | 1.7412 | 1.7412 | 1.7412 | 1.7412 | 1.7412
2020-04-10 18:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.49441 | 0.49441 | 0.49441 | 0.49441 | 0.49441 | 0.49441 | 2.0767 | 2.9956 | 3.5977 | 3.9145 | 4.5482 | 5.182 | 0.62873 | 1.7079 | 2.1421 | 2.1421 | 2.1421 | 2.1421 | 1.1253 | 1.4283 | 1.4283 | 1.4283 | 1.4283 | 1.4283
2020-04-10 19:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.46869 | 0.46869 | 0.46869 | 0.46869 | 0.46869 | 0.46869 | 1.9815 | 2.8582 | 3.4326 | 3.735 | 4.3396 | 4.9443 | 0.61349 | 1.6665 | 2.0902 | 2.0902 | 2.0902 | 2.0902 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-04-10 20:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 1.8862 | 2.7208 | 3.2676 | 3.5554 | 4.131 | 4.7066 | 0.60206 | 1.6354 | 2.0512 | 2.0512 | 2.0512 | 2.0512 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-04-10 21:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.39153 | 0.39153 | 0.39153 | 0.39153 | 0.39153 | 0.39153 | 1.9434 | 2.8032 | 3.3666 | 3.6631 | 4.2562 | 4.8492 | 0.58301 | 1.5837 | 1.9863 | 1.9863 | 1.9863 | 1.9863 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-04-10 22:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.40296 | 0.40296 | 0.40296 | 0.40296 | 0.40296 | 0.40296 | 1.81 | 2.6109 | 3.1356 | 3.4117 | 3.9641 | 4.5164 | 0.54871 | 1.4905 | 1.8695 | 1.8695 | 1.8695 | 1.8695 | 0.80021 | 1.0157 | 1.0157 | 1.0157 | 1.0157 | 1.0157
2020-04-10 23:00 | Winter | 0.57244 | 0.88019 | 1.3319 | 1.3319 | 1.3319 | 1.3319 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 1.7338 | 2.5009 | 3.0036 | 3.2681 | 3.7972 | 4.3262 | 0.53728 | 1.4595 | 1.8305 | 1.8305 | 1.8305 | 1.8305 | 0.80021 | 1.0157 | 1.0157 | 1.0157 | 1.0157 | 1.0157
2020-04-11 | Winter | 0.55201 | 0.84879 | 1.2844 | 1.2844 | 1.2844 | 1.2844 | 0.38009 | 0.38009 | 0.38009 | 0.38009 | 0.38009 | 0.38009 | 1.6576 | 2.391 | 2.8715 | 3.1244 | 3.6302 | 4.1361 | 0.52585 | 1.4284 | 1.7916 | 1.7916 | 1.7916 | 1.7916 | 0.78115 | 0.9915 | 0.9915 | 0.9915 | 0.9915 | 0.9915
2020-04-11 01:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.38349 | 0.38349 | 0.38349 | 0.38349 | 0.38349 | 0.38349 | 1.6004 | 2.3086 | 2.7725 | 3.0167 | 3.5051 | 3.9934 | 0.56395 | 1.5319 | 1.9214 | 1.9214 | 1.9214 | 1.9214 | 0.78115 | 0.9915 | 0.9915 | 0.9915 | 0.9915 | 0.9915
2020-04-11 02:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 1.5914 | 2.2955 | 2.7568 | 2.9996 | 3.4852 | 3.9709 | 0.51442 | 1.3974 | 1.7526 | 1.7526 | 1.7526 | 1.7526 | 0.7621 | 0.96732 | 0.96732 | 0.96732 | 0.96732 | 0.96732
2020-04-11 03:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.38867 | 0.38867 | 0.38867 | 0.38867 | 0.38867 | 0.38867 | 1.6004 | 2.3086 | 2.7725 | 3.0167 | 3.5051 | 3.9934 | 0.51442 | 1.3974 | 1.7526 | 1.7526 | 1.7526 | 1.7526 | 0.78115 | 0.9915 | 0.9915 | 0.9915 | 0.9915 | 0.9915
2020-04-11 04:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.50299 | 1.3663 | 1.7137 | 1.7137 | 1.7137 | 1.7137 | 0.76273 | 0.96812 | 0.96812 | 0.96812 | 0.96812 | 0.96812
2020-04-11 05:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 1.5814 | 2.2811 | 2.7395 | 2.9808 | 3.4633 | 3.9459 | 0.52204 | 1.4181 | 1.7786 | 1.7786 | 1.7786 | 1.7786 | 0.80021 | 1.0157 | 1.0157 | 1.0157 | 1.0157 | 1.0157
2020-04-11 06:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.43154 | 0.43154 | 0.43154 | 0.43154 | 0.43154 | 0.43154 | 1.6004 | 2.3086 | 2.7725 | 3.0167 | 3.5051 | 3.9934 | 0.50709 | 1.3775 | 1.7277 | 1.7277 | 1.7277 | 1.7277 | 0.8513 | 1.0805 | 1.0805 | 1.0805 | 1.0805 | 1.0805
2020-04-11 07:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 1.6957 | 2.446 | 2.9375 | 3.1963 | 3.7137 | 4.2311 | 0.52585 | 1.4284 | 1.7916 | 1.7916 | 1.7916 | 1.7916 | 0.91452 | 1.1608 | 1.1608 | 1.1608 | 1.1608 | 1.1608
2020-04-11 08:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 1.81 | 2.6109 | 3.1356 | 3.4117 | 3.9641 | 4.5164 | 0.51442 | 1.3974 | 1.7526 | 1.7526 | 1.7526 | 1.7526 | 0.91452 | 1.1608 | 1.1608 | 1.1608 | 1.1608 | 1.1608
2020-04-11 09:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.52013 | 0.52013 | 0.52013 | 0.52013 | 0.52013 | 0.52013 | 1.829 | 2.6383 | 3.1686 | 3.4477 | 4.0058 | 4.5639 | 0.71256 | 1.9356 | 2.4277 | 2.4277 | 2.4277 | 2.4277 | 0.95263 | 1.2092 | 1.2092 | 1.2092 | 1.2092 | 1.2092
2020-04-11 10:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 1.8672 | 2.6933 | 3.2346 | 3.5195 | 4.0892 | 4.659 | 0.60968 | 1.6561 | 2.0772 | 2.0772 | 2.0772 | 2.0772 | 0.93358 | 1.185 | 1.185 | 1.185 | 1.185 | 1.185
2020-04-11 11:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 1.8481 | 2.6658 | 3.2016 | 3.4836 | 4.0475 | 4.6115 | 0.55633 | 1.5112 | 1.8954 | 1.8954 | 1.8954 | 1.8954 | 0.95263 | 1.2092 | 1.2092 | 1.2092 | 1.2092 | 1.2092
2020-04-11 12:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.38581 | 0.38581 | 0.38581 | 0.38581 | 0.38581 | 0.38581 | 1.829 | 2.6383 | 3.1686 | 3.4477 | 4.0058 | 4.5639 | 0.54871 | 1.4905 | 1.8695 | 1.8695 | 1.8695 | 1.8695 | 0.93358 | 1.185 | 1.185 | 1.185 | 1.185 | 1.185
2020-04-11 13:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.41439 | 0.41439 | 0.41439 | 0.41439 | 0.41439 | 0.41439 | 1.9053 | 2.7483 | 3.3006 | 3.5913 | 4.1727 | 4.7541 | 0.52204 | 1.4181 | 1.7786 | 1.7786 | 1.7786 | 1.7786 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-04-11 14:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 1.8672 | 2.6933 | 3.2346 | 3.5195 | 4.0892 | 4.659 | 0.52585 | 1.4284 | 1.7916 | 1.7916 | 1.7916 | 1.7916 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-04-11 15:00 | Winter | 0.57307 | 0.88116 | 1.3334 | 1.3334 | 1.3334 | 1.3334 | 0.41439 | 0.41439 | 0.41439 | 0.41439 | 0.41439 | 0.41439 | 1.8481 | 2.6658 | 3.2016 | 3.4836 | 4.0475 | 4.6115 | 0.51823 | 1.4077 | 1.7656 | 1.7656 | 1.7656 | 1.7656 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-04-11 16:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.49727 | 0.49727 | 0.49727 | 0.49727 | 0.49727 | 0.49727 | 1.8672 | 2.6933 | 3.2346 | 3.5195 | 4.0892 | 4.659 | 0.52204 | 1.4181 | 1.7786 | 1.7786 | 1.7786 | 1.7786 | 0.81923 | 1.0398 | 1.0398 | 1.0398 | 1.0398 | 1.0398
2020-04-11 17:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 1.9793 | 2.855 | 3.4288 | 3.7308 | 4.3348 | 4.9387 | 0.56014 | 1.5216 | 1.9084 | 1.9084 | 1.9084 | 1.9084 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-04-11 18:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 2.1339 | 3.0781 | 3.6967 | 4.0223 | 4.6734 | 5.3246 | 0.59825 | 1.6251 | 2.0382 | 2.0382 | 2.0382 | 2.0382 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-04-11 19:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 2.0196 | 2.9132 | 3.4986 | 3.8068 | 4.4231 | 5.0393 | 0.62873 | 1.7079 | 2.1421 | 2.1421 | 2.1421 | 2.1421 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-04-11 20:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.39153 | 0.39153 | 0.39153 | 0.39153 | 0.39153 | 0.39153 | 1.9243 | 2.7758 | 3.3336 | 3.6272 | 4.2144 | 4.8016 | 0.60587 | 1.6458 | 2.0642 | 2.0642 | 2.0642 | 2.0642 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-04-11 21:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.35437 | 0.35437 | 0.35437 | 0.35437 | 0.35437 | 0.35437 | 1.8862 | 2.7208 | 3.2676 | 3.5554 | 4.131 | 4.7066 | 0.5449 | 1.4802 | 1.8565 | 1.8565 | 1.8565 | 1.8565 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-04-11 22:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.30293 | 0.30293 | 0.30293 | 0.30293 | 0.30293 | 0.30293 | 1.829 | 2.6383 | 3.1686 | 3.4477 | 4.0058 | 4.5639 | 0.56395 | 1.5319 | 1.9214 | 1.9214 | 1.9214 | 1.9214 | 0.78115 | 0.9915 | 0.9915 | 0.9915 | 0.9915 | 0.9915
2020-04-11 23:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.38867 | 0.38867 | 0.38867 | 0.38867 | 0.38867 | 0.38867 | 1.7147 | 2.4735 | 2.9705 | 3.2322 | 3.7554 | 4.2787 | 0.56776 | 1.5423 | 1.9344 | 1.9344 | 1.9344 | 1.9344 | 0.7621 | 0.96732 | 0.96732 | 0.96732 | 0.96732 | 0.96732
2020-04-12 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.34866 | 0.34866 | 0.34866 | 0.34866 | 0.34866 | 0.34866 | 1.5623 | 2.2536 | 2.7065 | 2.9449 | 3.4216 | 3.8984 | 0.54871 | 1.4905 | 1.8695 | 1.8695 | 1.8695 | 1.8695 | 0.78115 | 0.9915 | 0.9915 | 0.9915 | 0.9915 | 0.9915
2020-04-12 01:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 1.5623 | 2.2536 | 2.7065 | 2.9449 | 3.4216 | 3.8984 | 0.52204 | 1.4181 | 1.7786 | 1.7786 | 1.7786 | 1.7786 | 0.78115 | 0.9915 | 0.9915 | 0.9915 | 0.9915 | 0.9915
2020-04-12 02:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.55728 | 0.55728 | 0.55728 | 0.55728 | 0.55728 | 0.55728 | 1.5433 | 2.2261 | 2.6735 | 2.909 | 3.3799 | 3.8508 | 0.56014 | 1.5216 | 1.9084 | 1.9084 | 1.9084 | 1.9084 | 0.78115 | 0.9915 | 0.9915 | 0.9915 | 0.9915 | 0.9915
2020-04-12 03:00 | Winter | 0.57148 | 0.87872 | 1.3297 | 1.3297 | 1.3297 | 1.3297 | 0.39153 | 0.39153 | 0.39153 | 0.39153 | 0.39153 | 0.39153 | 1.4861 | 2.1437 | 2.5745 | 2.8012 | 3.2547 | 3.7082 | 0.51245 | 1.392 | 1.7459 | 1.7459 | 1.7459 | 1.7459 | 0.78115 | 0.9915 | 0.9915 | 0.9915 | 0.9915 | 0.9915
2020-04-12 04:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 1.5484 | 2.2335 | 2.6824 | 2.9186 | 3.3911 | 3.8636 | 0.59444 | 1.6147 | 2.0253 | 2.0253 | 2.0253 | 2.0253 | 0.78115 | 0.9915 | 0.9915 | 0.9915 | 0.9915 | 0.9915
2020-04-12 05:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.46869 | 0.46869 | 0.46869 | 0.46869 | 0.46869 | 0.46869 | 1.5814 | 2.2811 | 2.7395 | 2.9808 | 3.4633 | 3.9459 | 0.51442 | 1.3974 | 1.7526 | 1.7526 | 1.7526 | 1.7526 | 0.79033 | 1.0031 | 1.0031 | 1.0031 | 1.0031 | 1.0031
2020-04-12 06:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 1.5609 | 2.2515 | 2.704 | 2.9422 | 3.4185 | 3.8948 | 0.53347 | 1.4491 | 1.8175 | 1.8175 | 1.8175 | 1.8175 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-04-12 07:00 | Winter | 0.5713 | 0.87844 | 1.3293 | 1.3293 | 1.3293 | 1.3293 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 1.6646 | 2.4011 | 2.8837 | 3.1376 | 3.6456 | 4.1536 | 0.56395 | 1.5319 | 1.9214 | 1.9214 | 1.9214 | 1.9214 | 0.7621 | 0.96732 | 0.96732 | 0.96732 | 0.96732 | 0.96732
2020-04-12 08:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 1.7909 | 2.5834 | 3.1026 | 3.3758 | 3.9223 | 4.4688 | 0.55633 | 1.5112 | 1.8954 | 1.8954 | 1.8954 | 1.8954 | 0.70494 | 0.89477 | 0.89477 | 0.89477 | 0.89477 | 0.89477
2020-04-12 09:00 | Winter | 0.51442 | 0.79098 | 1.1969 | 1.1969 | 1.1969 | 1.1969 | 0.38867 | 0.38867 | 0.38867 | 0.38867 | 0.38867 | 0.38867 | 1.81 | 2.6109 | 3.1356 | 3.4117 | 3.9641 | 4.5164 | 0.5792 | 1.5733 | 1.9733 | 1.9733 | 1.9733 | 1.9733 | 0.78115 | 0.9915 | 0.9915 | 0.9915 | 0.9915 | 0.9915
2020-04-12 10:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.33437 | 0.33437 | 0.33437 | 0.33437 | 0.33437 | 0.33437 | 1.8672 | 2.6933 | 3.2346 | 3.5195 | 4.0892 | 4.659 | 0.5792 | 1.5733 | 1.9733 | 1.9733 | 1.9733 | 1.9733 | 0.80021 | 1.0157 | 1.0157 | 1.0157 | 1.0157 | 1.0157
2020-04-12 11:00 | Winter | 0.53347 | 0.82027 | 1.2412 | 1.2412 | 1.2412 | 1.2412 | 0.41153 | 0.41153 | 0.41153 | 0.41153 | 0.41153 | 0.41153 | 1.8862 | 2.7208 | 3.2676 | 3.5554 | 4.131 | 4.7066 | 0.65541 | 1.7803 | 2.233 | 2.233 | 2.233 | 2.233 | 0.74305 | 0.94314 | 0.94314 | 0.94314 | 0.94314 | 0.94314
2020-04-12 12:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.35152 | 0.35152 | 0.35152 | 0.35152 | 0.35152 | 0.35152 | 1.8672 | 2.6933 | 3.2346 | 3.5195 | 4.0892 | 4.659 | 0.57157 | 1.5526 | 1.9474 | 1.9474 | 1.9474 | 1.9474 | 0.724 | 0.91895 | 0.91895 | 0.91895 | 0.91895 | 0.91895
2020-04-12 13:00 | Winter | 0.53347 | 0.82027 | 1.2412 | 1.2412 | 1.2412 | 1.2412 | 0.35723 | 0.35723 | 0.35723 | 0.35723 | 0.35723 | 0.35723 | 1.8481 | 2.6658 | 3.2016 | 3.4836 | 4.0475 | 4.6115 | 0.52204 | 1.4181 | 1.7786 | 1.7786 | 1.7786 | 1.7786 | 0.724 | 0.91895 | 0.91895 | 0.91895 | 0.91895 | 0.91895
2020-04-12 14:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.36581 | 0.36581 | 0.36581 | 0.36581 | 0.36581 | 0.36581 | 1.8481 | 2.6658 | 3.2016 | 3.4836 | 4.0475 | 4.6115 | 0.53728 | 1.4595 | 1.8305 | 1.8305 | 1.8305 | 1.8305 | 0.76043 | 0.9652 | 0.9652 | 0.9652 | 0.9652 | 0.9652
2020-04-12 15:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.35437 | 0.35437 | 0.35437 | 0.35437 | 0.35437 | 0.35437 | 1.8481 | 2.6658 | 3.2016 | 3.4836 | 4.0475 | 4.6115 | 0.48774 | 1.3249 | 1.6618 | 1.6618 | 1.6618 | 1.6618 | 0.80021 | 1.0157 | 1.0157 | 1.0157 | 1.0157 | 1.0157
2020-04-12 16:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.38295 | 0.38295 | 0.38295 | 0.38295 | 0.38295 | 0.38295 | 1.8481 | 2.6658 | 3.2016 | 3.4836 | 4.0475 | 4.6115 | 0.62508 | 1.698 | 2.1296 | 2.1296 | 2.1296 | 2.1296 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-04-12 17:00 | Winter | 0.57994 | 0.89172 | 1.3493 | 1.3493 | 1.3493 | 1.3493 | 0.39438 | 0.39438 | 0.39438 | 0.39438 | 0.39438 | 0.39438 | 1.8862 | 2.7208 | 3.2676 | 3.5554 | 4.131 | 4.7066 | 0.64016 | 1.7389 | 2.1811 | 2.1811 | 2.1811 | 2.1811 | 0.80021 | 1.0157 | 1.0157 | 1.0157 | 1.0157 | 1.0157
2020-04-12 18:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 2.0005 | 2.8857 | 3.4656 | 3.7709 | 4.3813 | 4.9918 | 0.56395 | 1.5319 | 1.9214 | 1.9214 | 1.9214 | 1.9214 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-04-12 19:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 1.9361 | 2.7928 | 3.3541 | 3.6495 | 4.2403 | 4.8311 | 0.60968 | 1.6561 | 2.0772 | 2.0772 | 2.0772 | 2.0772 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-04-12 20:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.37152 | 0.37152 | 0.37152 | 0.37152 | 0.37152 | 0.37152 | 2.0005 | 2.8857 | 3.4656 | 3.7709 | 4.3813 | 4.9918 | 0.56395 | 1.5319 | 1.9214 | 1.9214 | 1.9214 | 1.9214 | 0.80021 | 1.0157 | 1.0157 | 1.0157 | 1.0157 | 1.0157
2020-04-12 21:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.40296 | 0.40296 | 0.40296 | 0.40296 | 0.40296 | 0.40296 | 1.8672 | 2.6933 | 3.2346 | 3.5195 | 4.0892 | 4.659 | 0.57157 | 1.5526 | 1.9474 | 1.9474 | 1.9474 | 1.9474 | 0.80021 | 1.0157 | 1.0157 | 1.0157 | 1.0157 | 1.0157
2020-04-12 22:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.35152 | 0.35152 | 0.35152 | 0.35152 | 0.35152 | 0.35152 | 1.7528 | 2.5284 | 3.0366 | 3.304 | 3.8389 | 4.3738 | 0.59444 | 1.6147 | 2.0253 | 2.0253 | 2.0253 | 2.0253 | 0.78115 | 0.9915 | 0.9915 | 0.9915 | 0.9915 | 0.9915
2020-04-12 23:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 1.7909 | 2.5834 | 3.1026 | 3.3758 | 3.9223 | 4.4688 | 0.54871 | 1.4905 | 1.8695 | 1.8695 | 1.8695 | 1.8695 | 0.78115 | 0.9915 | 0.9915 | 0.9915 | 0.9915 | 0.9915
2020-04-13 | Winter | 0.55854 | 0.85882 | 1.2996 | 1.2996 | 1.2996 | 1.2996 | 0.38295 | 0.38295 | 0.38295 | 0.38295 | 0.38295 | 0.38295 | 1.6576 | 2.391 | 2.8715 | 3.1244 | 3.6302 | 4.1361 | 0.51442 | 1.3974 | 1.7526 | 1.7526 | 1.7526 | 1.7526 | 0.80021 | 1.0157 | 1.0157 | 1.0157 | 1.0157 | 1.0157
2020-04-13 01:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.29143 | 0.29143 | 0.29143 | 0.29143 | 0.29143 | 0.29143 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.52966 | 1.4388 | 1.8046 | 1.8046 | 1.8046 | 1.8046 | 0.78115 | 0.9915 | 0.9915 | 0.9915 | 0.9915 | 0.9915
2020-04-13 02:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.51442 | 0.51442 | 0.51442 | 0.51442 | 0.51442 | 0.51442 | 1.5814 | 2.2811 | 2.7395 | 2.9808 | 3.4633 | 3.9459 | 0.52592 | 1.4286 | 1.7918 | 1.7918 | 1.7918 | 1.7918 | 0.80021 | 1.0157 | 1.0157 | 1.0157 | 1.0157 | 1.0157
2020-04-13 03:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 1.5433 | 2.2261 | 2.6735 | 2.909 | 3.3799 | 3.8508 | 0.50299 | 1.3663 | 1.7137 | 1.7137 | 1.7137 | 1.7137 | 0.80021 | 1.0157 | 1.0157 | 1.0157 | 1.0157 | 1.0157
2020-04-13 04:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.39724 | 0.39724 | 0.39724 | 0.39724 | 0.39724 | 0.39724 | 1.5433 | 2.2261 | 2.6735 | 2.909 | 3.3799 | 3.8508 | 0.49918 | 1.356 | 1.7007 | 1.7007 | 1.7007 | 1.7007 | 1.0474 | 1.3294 | 1.3294 | 1.3294 | 1.3294 | 1.3294
2020-04-13 05:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 1.6195 | 2.336 | 2.8055 | 3.0526 | 3.5468 | 4.041 | 0.5792 | 1.5733 | 1.9733 | 1.9733 | 1.9733 | 1.9733 | 1.2366 | 1.5696 | 1.5696 | 1.5696 | 1.5696 | 1.5696
2020-04-13 06:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.50298 | 0.50298 | 0.50298 | 0.50298 | 0.50298 | 0.50298 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.55252 | 1.5009 | 1.8825 | 1.8825 | 1.8825 | 1.8825 | 1.4093 | 1.7888 | 1.7888 | 1.7888 | 1.7888 | 1.7888
2020-04-13 07:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.4544 | 0.4544 | 0.4544 | 0.4544 | 0.4544 | 0.4544 | 1.7528 | 2.5284 | 3.0366 | 3.304 | 3.8389 | 4.3738 | 0.5449 | 1.4802 | 1.8565 | 1.8565 | 1.8565 | 1.8565 | 1.4861 | 1.8863 | 1.8863 | 1.8863 | 1.8863 | 1.8863
2020-04-13 08:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 1.8672 | 2.6933 | 3.2346 | 3.5195 | 4.0892 | 4.659 | 0.53728 | 1.4595 | 1.8305 | 1.8305 | 1.8305 | 1.8305 | 1.5623 | 1.983 | 1.983 | 1.983 | 1.983 | 1.983
2020-04-13 09:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 1.8672 | 2.6933 | 3.2346 | 3.5195 | 4.0892 | 4.659 | 0.58301 | 1.5837 | 1.9863 | 1.9863 | 1.9863 | 1.9863 | 1.6004 | 2.0314 | 2.0314 | 2.0314 | 2.0314 | 2.0314
2020-04-13 10:00 | Winter | 0.56641 | 0.87093 | 1.3179 | 1.3179 | 1.3179 | 1.3179 | 0.29832 | 0.29832 | 0.29832 | 0.29832 | 0.29832 | 0.29832 | 1.9815 | 2.8582 | 3.4326 | 3.735 | 4.3396 | 4.9443 | 0.56395 | 1.5319 | 1.9214 | 1.9214 | 1.9214 | 1.9214 | 1.5242 | 1.9346 | 1.9346 | 1.9346 | 1.9346 | 1.9346
2020-04-13 11:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.41439 | 0.41439 | 0.41439 | 0.41439 | 0.41439 | 0.41439 | 1.9785 | 2.8539 | 3.4274 | 3.7293 | 4.333 | 4.9367 | 0.56395 | 1.5319 | 1.9214 | 1.9214 | 1.9214 | 1.9214 | 1.467 | 1.8621 | 1.8621 | 1.8621 | 1.8621 | 1.8621
2020-04-13 12:00 | Winter | 0.63492 | 0.97626 | 1.4773 | 1.4773 | 1.4773 | 1.4773 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 1.9434 | 2.8032 | 3.3666 | 3.6631 | 4.2562 | 4.8492 | 0.5068 | 1.3767 | 1.7267 | 1.7267 | 1.7267 | 1.7267 | 1.4099 | 1.7895 | 1.7895 | 1.7895 | 1.7895 | 1.7895
2020-04-13 13:00 | Winter | 0.64779 | 0.99605 | 1.5072 | 1.5072 | 1.5072 | 1.5072 | 0.38009 | 0.38009 | 0.38009 | 0.38009 | 0.38009 | 0.38009 | 1.9815 | 2.8582 | 3.4326 | 3.735 | 4.3396 | 4.9443 | 0.51823 | 1.4077 | 1.7656 | 1.7656 | 1.7656 | 1.7656 | 1.4099 | 1.7895 | 1.7895 | 1.7895 | 1.7895 | 1.7895
2020-04-13 14:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.30293 | 0.30293 | 0.30293 | 0.30293 | 0.30293 | 0.30293 | 1.9053 | 2.7483 | 3.3006 | 3.5913 | 4.1727 | 4.7541 | 0.53728 | 1.4595 | 1.8305 | 1.8305 | 1.8305 | 1.8305 | 1.448 | 1.8379 | 1.8379 | 1.8379 | 1.8379 | 1.8379
2020-04-13 15:00 | Winter | 0.64779 | 0.99605 | 1.5072 | 1.5072 | 1.5072 | 1.5072 | 0.32294 | 0.32294 | 0.32294 | 0.32294 | 0.32294 | 0.32294 | 1.8919 | 2.729 | 3.2775 | 3.5661 | 4.1434 | 4.7207 | 0.49918 | 1.356 | 1.7007 | 1.7007 | 1.7007 | 1.7007 | 1.3908 | 1.7654 | 1.7654 | 1.7654 | 1.7654 | 1.7654
2020-04-13 16:00 | Winter | 0.60826 | 0.93527 | 1.4153 | 1.4153 | 1.4153 | 1.4153 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 1.9434 | 2.8032 | 3.3666 | 3.6631 | 4.2562 | 4.8492 | 0.51823 | 1.4077 | 1.7656 | 1.7656 | 1.7656 | 1.7656 | 1.3908 | 1.7654 | 1.7654 | 1.7654 | 1.7654 | 1.7654
2020-04-13 17:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.41153 | 0.41153 | 0.41153 | 0.41153 | 0.41153 | 0.41153 | 2.0577 | 2.9681 | 3.5647 | 3.8786 | 4.5065 | 5.1344 | 0.53728 | 1.4595 | 1.8305 | 1.8305 | 1.8305 | 1.8305 | 1.3153 | 1.6695 | 1.6695 | 1.6695 | 1.6695 | 1.6695
2020-04-13 18:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.34008 | 0.34008 | 0.34008 | 0.34008 | 0.34008 | 0.34008 | 2.0767 | 2.9956 | 3.5977 | 3.9145 | 4.5482 | 5.182 | 0.63635 | 1.7286 | 2.1681 | 2.1681 | 2.1681 | 2.1681 | 1.0358 | 1.3147 | 1.3147 | 1.3147 | 1.3147 | 1.3147
2020-04-13 19:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.43154 | 0.43154 | 0.43154 | 0.43154 | 0.43154 | 0.43154 | 2.0196 | 2.9132 | 3.4986 | 3.8068 | 4.4231 | 5.0393 | 0.60206 | 1.6354 | 2.0512 | 2.0512 | 2.0512 | 2.0512 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-04-13 20:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.36295 | 0.36295 | 0.36295 | 0.36295 | 0.36295 | 0.36295 | 1.9243 | 2.7758 | 3.3336 | 3.6272 | 4.2144 | 4.8016 | 0.58682 | 1.594 | 1.9993 | 1.9993 | 1.9993 | 1.9993 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-04-13 21:00 | Winter | 0.55214 | 0.84898 | 1.2847 | 1.2847 | 1.2847 | 1.2847 | 0.39438 | 0.39438 | 0.39438 | 0.39438 | 0.39438 | 0.39438 | 1.8672 | 2.6933 | 3.2346 | 3.5195 | 4.0892 | 4.659 | 0.55252 | 1.5009 | 1.8825 | 1.8825 | 1.8825 | 1.8825 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-04-13 22:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.41153 | 0.41153 | 0.41153 | 0.41153 | 0.41153 | 0.41153 | 1.7808 | 2.5688 | 3.085 | 3.3568 | 3.9002 | 4.4436 | 0.57539 | 1.563 | 1.9603 | 1.9603 | 1.9603 | 1.9603 | 0.80036 | 1.0159 | 1.0159 | 1.0159 | 1.0159 | 1.0159
2020-04-13 23:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.38867 | 0.38867 | 0.38867 | 0.38867 | 0.38867 | 0.38867 | 1.6526 | 2.3838 | 2.8628 | 3.115 | 3.6193 | 4.1236 | 0.52966 | 1.4388 | 1.8046 | 1.8046 | 1.8046 | 1.8046 | 0.80021 | 1.0157 | 1.0157 | 1.0157 | 1.0157 | 1.0157
2020-04-14 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 1.5814 | 2.2811 | 2.7395 | 2.9808 | 3.4633 | 3.9459 | 0.52966 | 1.4388 | 1.8046 | 1.8046 | 1.8046 | 1.8046 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-04-14 01:00 | Winter | 0.55209 | 0.8489 | 1.2846 | 1.2846 | 1.2846 | 1.2846 | 0.39724 | 0.39724 | 0.39724 | 0.39724 | 0.39724 | 0.39724 | 1.6004 | 2.3086 | 2.7725 | 3.0167 | 3.5051 | 3.9934 | 0.5068 | 1.3767 | 1.7267 | 1.7267 | 1.7267 | 1.7267 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-04-14 02:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.4544 | 0.4544 | 0.4544 | 0.4544 | 0.4544 | 0.4544 | 1.5531 | 2.2403 | 2.6906 | 2.9275 | 3.4015 | 3.8754 | 0.48774 | 1.3249 | 1.6618 | 1.6618 | 1.6618 | 1.6618 | 0.78389 | 0.99498 | 0.99498 | 0.99498 | 0.99498 | 0.99498
2020-04-14 03:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.43439 | 0.43439 | 0.43439 | 0.43439 | 0.43439 | 0.43439 | 1.5052 | 2.1711 | 2.6075 | 2.8371 | 3.2964 | 3.7557 | 0.51421 | 1.3968 | 1.7519 | 1.7519 | 1.7519 | 1.7519 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-04-14 04:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.43439 | 0.43439 | 0.43439 | 0.43439 | 0.43439 | 0.43439 | 1.5814 | 2.2811 | 2.7395 | 2.9808 | 3.4633 | 3.9459 | 0.51442 | 1.3974 | 1.7526 | 1.7526 | 1.7526 | 1.7526 | 1.0288 | 1.3059 | 1.3059 | 1.3059 | 1.3059 | 1.3059
2020-04-14 05:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.6373 | 0.6373 | 0.6373 | 0.6373 | 0.6373 | 0.6373 | 1.6004 | 2.3086 | 2.7725 | 3.0167 | 3.5051 | 3.9934 | 0.56776 | 1.5423 | 1.9344 | 1.9344 | 1.9344 | 1.9344 | 1.3249 | 1.6817 | 1.6817 | 1.6817 | 1.6817 | 1.6817
2020-04-14 06:00 | Winter | 0.66386 | 1.0208 | 1.5446 | 1.5446 | 1.5446 | 1.5446 | 0.67422 | 0.67422 | 0.67422 | 0.67422 | 0.67422 | 0.67422 | 1.7909 | 2.5834 | 3.1026 | 3.3758 | 3.9223 | 4.4688 | 0.62111 | 1.6872 | 2.1161 | 2.1161 | 2.1161 | 2.1161 | 1.6027 | 2.0343 | 2.0343 | 2.0343 | 2.0343 | 2.0343
2020-04-14 07:00 | Winter | 0.92258 | 1.4186 | 2.1466 | 2.1466 | 2.1466 | 2.1466 | 0.73733 | 0.73733 | 0.73733 | 0.73733 | 0.73733 | 0.73733 | 2.0196 | 2.9132 | 3.4986 | 3.8068 | 4.4231 | 5.0393 | 0.73162 | 1.9874 | 2.4926 | 2.4926 | 2.4926 | 2.4926 | 1.9815 | 2.515 | 2.515 | 2.515 | 2.515 | 2.515
2020-04-14 08:00 | Winter | 1.1622 | 1.787 | 2.7041 | 2.7041 | 2.7041 | 2.7041 | 0.84467 | 0.84467 | 0.84467 | 0.84467 | 0.84467 | 0.84467 | 2.1529 | 3.1056 | 3.7297 | 4.0582 | 4.7151 | 5.3721 | 0.75448 | 2.0495 | 2.5705 | 2.5705 | 2.5705 | 2.5705 | 2.0958 | 2.6601 | 2.6601 | 2.6601 | 2.6601 | 2.6601
2020-04-14 09:00 | Winter | 1.1432 | 1.7577 | 2.6598 | 2.6598 | 2.6598 | 2.6598 | 0.84879 | 0.84879 | 0.84879 | 0.84879 | 0.84879 | 0.84879 | 2.1148 | 3.0506 | 3.6637 | 3.9863 | 4.6317 | 5.277 | 0.73543 | 1.9977 | 2.5056 | 2.5056 | 2.5056 | 2.5056 | 2.1148 | 2.6843 | 2.6843 | 2.6843 | 2.6843 | 2.6843
2020-04-14 10:00 | Winter | 1.2384 | 1.9042 | 2.8814 | 2.8814 | 2.8814 | 2.8814 | 0.82878 | 0.82878 | 0.82878 | 0.82878 | 0.82878 | 0.82878 | 2.1148 | 3.0506 | 3.6637 | 3.9863 | 4.6317 | 5.277 | 0.75001 | 2.0373 | 2.5553 | 2.5553 | 2.5553 | 2.5553 | 2.0196 | 2.5634 | 2.5634 | 2.5634 | 2.5634 | 2.5634
2020-04-14 11:00 | Winter | 1.2194 | 1.8749 | 2.8371 | 2.8371 | 2.8371 | 2.8371 | 0.8345 | 0.8345 | 0.8345 | 0.8345 | 0.8345 | 0.8345 | 2.2393 | 3.2301 | 3.8793 | 4.221 | 4.9043 | 5.5876 | 0.76591 | 2.0805 | 2.6095 | 2.6095 | 2.6095 | 2.6095 | 2.0767 | 2.6359 | 2.6359 | 2.6359 | 2.6359 | 2.6359
2020-04-14 12:00 | Winter | 1.2384 | 1.9042 | 2.8814 | 2.8814 | 2.8814 | 2.8814 | 0.76019 | 0.76019 | 0.76019 | 0.76019 | 0.76019 | 0.76019 | 2.2673 | 3.2705 | 3.9277 | 4.2736 | 4.9655 | 5.6574 | 0.69351 | 1.8839 | 2.3628 | 2.3628 | 2.3628 | 2.3628 | 1.9815 | 2.515 | 2.515 | 2.515 | 2.515 | 2.515
2020-04-14 13:00 | Winter | 1.2003 | 1.8456 | 2.7928 | 2.7928 | 2.7928 | 2.7928 | 0.71161 | 0.71161 | 0.71161 | 0.71161 | 0.71161 | 0.71161 | 2.2101 | 3.188 | 3.8287 | 4.1659 | 4.8403 | 5.5147 | 0.6516 | 1.77 | 2.22 | 2.22 | 2.22 | 2.22 | 2.0386 | 2.5876 | 2.5876 | 2.5876 | 2.5876 | 2.5876
2020-04-14 14:00 | Winter | 1.2003 | 1.8456 | 2.7928 | 2.7928 | 2.7928 | 2.7928 | 0.84307 | 0.84307 | 0.84307 | 0.84307 | 0.84307 | 0.84307 | 2.1529 | 3.1056 | 3.7297 | 4.0582 | 4.7151 | 5.3721 | 0.64016 | 1.7389 | 2.1811 | 2.1811 | 2.1811 | 2.1811 | 1.9434 | 2.4667 | 2.4667 | 2.4667 | 2.4667 | 2.4667
2020-04-14 15:00 | Winter | 1.2003 | 1.8456 | 2.7928 | 2.7928 | 2.7928 | 2.7928 | 0.84021 | 0.84021 | 0.84021 | 0.84021 | 0.84021 | 0.84021 | 2.1529 | 3.1056 | 3.7297 | 4.0582 | 4.7151 | 5.3721 | 0.67065 | 1.8218 | 2.2849 | 2.2849 | 2.2849 | 2.2849 | 1.9434 | 2.4667 | 2.4667 | 2.4667 | 2.4667 | 2.4667
2020-04-14 16:00 | Winter | 1.2194 | 1.8749 | 2.8371 | 2.8371 | 2.8371 | 2.8371 | 0.76019 | 0.76019 | 0.76019 | 0.76019 | 0.76019 | 0.76019 | 2.0958 | 3.0231 | 3.6307 | 3.9504 | 4.59 | 5.2295 | 0.65541 | 1.7803 | 2.233 | 2.233 | 2.233 | 2.233 | 1.8672 | 2.3699 | 2.3699 | 2.3699 | 2.3699 | 2.3699
2020-04-14 17:00 | Winter | 1.086 | 1.6698 | 2.5268 | 2.5268 | 2.5268 | 2.5268 | 0.67948 | 0.67948 | 0.67948 | 0.67948 | 0.67948 | 0.67948 | 2.191 | 3.1605 | 3.7957 | 4.13 | 4.7986 | 5.4672 | 0.62873 | 1.7079 | 2.1421 | 2.1421 | 2.1421 | 2.1421 | 1.81 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974
2020-04-14 18:00 | Winter | 0.8294 | 1.2753 | 1.9298 | 1.9298 | 1.9298 | 1.9298 | 0.58586 | 0.58586 | 0.58586 | 0.58586 | 0.58586 | 0.58586 | 2.2101 | 3.188 | 3.8287 | 4.1659 | 4.8403 | 5.5147 | 0.60968 | 1.6561 | 2.0772 | 2.0772 | 2.0772 | 2.0772 | 1.4568 | 1.8491 | 1.8491 | 1.8491 | 1.8491 | 1.8491
2020-04-14 19:00 | Winter | 0.64779 | 0.99605 | 1.5072 | 1.5072 | 1.5072 | 1.5072 | 0.46869 | 0.46869 | 0.46869 | 0.46869 | 0.46869 | 0.46869 | 2.1556 | 3.1093 | 3.7342 | 4.0631 | 4.7209 | 5.3787 | 0.56014 | 1.5216 | 1.9084 | 1.9084 | 1.9084 | 1.9084 | 1.1101 | 1.4091 | 1.4091 | 1.4091 | 1.4091 | 1.4091
2020-04-14 20:00 | Winter | 0.58949 | 0.90641 | 1.3716 | 1.3716 | 1.3716 | 1.3716 | 0.36581 | 0.36581 | 0.36581 | 0.36581 | 0.36581 | 0.36581 | 1.9624 | 2.8307 | 3.3996 | 3.699 | 4.2979 | 4.8967 | 0.58301 | 1.5837 | 1.9863 | 1.9863 | 1.9863 | 1.9863 | 0.98953 | 1.256 | 1.256 | 1.256 | 1.256 | 1.256
2020-04-14 21:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.39153 | 0.39153 | 0.39153 | 0.39153 | 0.39153 | 0.39153 | 1.9271 | 2.7799 | 3.3385 | 3.6326 | 4.2206 | 4.8087 | 0.54871 | 1.4905 | 1.8695 | 1.8695 | 1.8695 | 1.8695 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-04-14 22:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 1.8862 | 2.7208 | 3.2676 | 3.5554 | 4.131 | 4.7066 | 0.55252 | 1.5009 | 1.8825 | 1.8825 | 1.8825 | 1.8825 | 0.81616 | 1.0359 | 1.0359 | 1.0359 | 1.0359 | 1.0359
2020-04-14 23:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.40296 | 0.40296 | 0.40296 | 0.40296 | 0.40296 | 0.40296 | 1.7147 | 2.4735 | 2.9705 | 3.2322 | 3.7554 | 4.2787 | 0.51442 | 1.3974 | 1.7526 | 1.7526 | 1.7526 | 1.7526 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-04-15 | Winter | 0.5869 | 0.90243 | 1.3656 | 1.3656 | 1.3656 | 1.3656 | 0.40582 | 0.40582 | 0.40582 | 0.40582 | 0.40582 | 0.40582 | 1.6508 | 2.3812 | 2.8597 | 3.1116 | 3.6153 | 4.1191 | 0.47631 | 1.2939 | 1.6228 | 1.6228 | 1.6228 | 1.6228 | 0.80021 | 1.0157 | 1.0157 | 1.0157 | 1.0157 | 1.0157
2020-04-15 01:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.40582 | 0.40582 | 0.40582 | 0.40582 | 0.40582 | 0.40582 | 1.5623 | 2.2536 | 2.7065 | 2.9449 | 3.4216 | 3.8984 | 0.46488 | 1.2628 | 1.5839 | 1.5839 | 1.5839 | 1.5839 | 0.78115 | 0.9915 | 0.9915 | 0.9915 | 0.9915 | 0.9915
2020-04-15 02:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 1.6576 | 2.391 | 2.8715 | 3.1244 | 3.6302 | 4.1361 | 0.48774 | 1.3249 | 1.6618 | 1.6618 | 1.6618 | 1.6618 | 0.79288 | 1.0064 | 1.0064 | 1.0064 | 1.0064 | 1.0064
2020-04-15 03:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.41439 | 0.41439 | 0.41439 | 0.41439 | 0.41439 | 0.41439 | 1.5433 | 2.2261 | 2.6735 | 2.909 | 3.3799 | 3.8508 | 0.46869 | 1.2732 | 1.5968 | 1.5968 | 1.5968 | 1.5968 | 0.80021 | 1.0157 | 1.0157 | 1.0157 | 1.0157 | 1.0157
2020-04-15 04:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.47726 | 0.47726 | 0.47726 | 0.47726 | 0.47726 | 0.47726 | 1.5433 | 2.2261 | 2.6735 | 2.909 | 3.3799 | 3.8508 | 0.47209 | 1.2824 | 1.6084 | 1.6084 | 1.6084 | 1.6084 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-04-15 05:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.53156 | 0.53156 | 0.53156 | 0.53156 | 0.53156 | 0.53156 | 1.6195 | 2.336 | 2.8055 | 3.0526 | 3.5468 | 4.041 | 0.54109 | 1.4698 | 1.8435 | 1.8435 | 1.8435 | 1.8435 | 1.1278 | 1.4315 | 1.4315 | 1.4315 | 1.4315 | 1.4315
2020-04-15 06:00 | Winter | 0.67749 | 1.0417 | 1.5763 | 1.5763 | 1.5763 | 1.5763 | 0.66588 | 0.66588 | 0.66588 | 0.66588 | 0.66588 | 0.66588 | 1.7147 | 2.4735 | 2.9705 | 3.2322 | 3.7554 | 4.2787 | 0.51823 | 1.4077 | 1.7656 | 1.7656 | 1.7656 | 1.7656 | 1.4896 | 1.8907 | 1.8907 | 1.8907 | 1.8907 | 1.8907
2020-04-15 07:00 | Winter | 0.85737 | 1.3183 | 1.9948 | 1.9948 | 1.9948 | 1.9948 | 0.86594 | 0.86594 | 0.86594 | 0.86594 | 0.86594 | 0.86594 | 1.9243 | 2.7758 | 3.3336 | 3.6272 | 4.2144 | 4.8016 | 0.6897 | 1.8735 | 2.3498 | 2.3498 | 2.3498 | 2.3498 | 1.829 | 2.3216 | 2.3216 | 2.3216 | 2.3216 | 2.3216
2020-04-15 08:00 | Winter | 1.1813 | 1.8163 | 2.7485 | 2.7485 | 2.7485 | 2.7485 | 0.96882 | 0.96882 | 0.96882 | 0.96882 | 0.96882 | 0.96882 | 2.0577 | 2.9681 | 3.5647 | 3.8786 | 4.5065 | 5.1344 | 0.74686 | 2.0288 | 2.5446 | 2.5446 | 2.5446 | 2.5446 | 2.0386 | 2.5876 | 2.5876 | 2.5876 | 2.5876 | 2.5876
2020-04-15 09:00 | Winter | 1.2384 | 1.9042 | 2.8814 | 2.8814 | 2.8814 | 2.8814 | 0.8345 | 0.8345 | 0.8345 | 0.8345 | 0.8345 | 0.8345 | 2.172 | 3.133 | 3.7627 | 4.0941 | 4.7569 | 5.4197 | 0.75448 | 2.0495 | 2.5705 | 2.5705 | 2.5705 | 2.5705 | 2.0386 | 2.5876 | 2.5876 | 2.5876 | 2.5876 | 2.5876
2020-04-15 10:00 | Winter | 1.4099 | 2.1679 | 3.2804 | 3.2804 | 3.2804 | 3.2804 | 0.74305 | 0.74305 | 0.74305 | 0.74305 | 0.74305 | 0.74305 | 2.3054 | 3.3254 | 3.9937 | 4.3455 | 5.049 | 5.7525 | 0.70494 | 1.9149 | 2.4018 | 2.4018 | 2.4018 | 2.4018 | 2.0005 | 2.5392 | 2.5392 | 2.5392 | 2.5392 | 2.5392
2020-04-15 11:00 | Winter | 1.3146 | 2.0214 | 3.0588 | 3.0588 | 3.0588 | 3.0588 | 0.83164 | 0.83164 | 0.83164 | 0.83164 | 0.83164 | 0.83164 | 2.3435 | 3.3804 | 4.0597 | 4.4173 | 5.1324 | 5.8475 | 0.68589 | 1.8632 | 2.3368 | 2.3368 | 2.3368 | 2.3368 | 2.0196 | 2.5634 | 2.5634 | 2.5634 | 2.5634 | 2.5634
2020-04-15 12:00 | Winter | 1.2956 | 1.9921 | 3.0144 | 3.0144 | 3.0144 | 3.0144 | 0.81449 | 0.81449 | 0.81449 | 0.81449 | 0.81449 | 0.81449 | 2.3054 | 3.3254 | 3.9937 | 4.3455 | 5.049 | 5.7525 | 0.74305 | 2.0184 | 2.5316 | 2.5316 | 2.5316 | 2.5316 | 2.0386 | 2.5876 | 2.5876 | 2.5876 | 2.5876 | 2.5876
2020-04-15 13:00 | Winter | 1.3908 | 2.1386 | 3.2361 | 3.2361 | 3.2361 | 3.2361 | 0.85736 | 0.85736 | 0.85736 | 0.85736 | 0.85736 | 0.85736 | 2.2863 | 3.2979 | 3.9607 | 4.3096 | 5.0072 | 5.7049 | 0.724 | 1.9667 | 2.4667 | 2.4667 | 2.4667 | 2.4667 | 2.0701 | 2.6276 | 2.6276 | 2.6276 | 2.6276 | 2.6276
2020-04-15 14:00 | Winter | 1.3146 | 2.0214 | 3.0588 | 3.0588 | 3.0588 | 3.0588 | 0.95739 | 0.95739 | 0.95739 | 0.95739 | 0.95739 | 0.95739 | 2.2673 | 3.2705 | 3.9277 | 4.2736 | 4.9655 | 5.6574 | 0.75067 | 2.0391 | 2.5575 | 2.5575 | 2.5575 | 2.5575 | 2.0767 | 2.6359 | 2.6359 | 2.6359 | 2.6359 | 2.6359
2020-04-15 15:00 | Winter | 1.3146 | 2.0214 | 3.0588 | 3.0588 | 3.0588 | 3.0588 | 0.91738 | 0.91738 | 0.91738 | 0.91738 | 0.91738 | 0.91738 | 2.2101 | 3.188 | 3.8287 | 4.1659 | 4.8403 | 5.5147 | 0.79258 | 2.153 | 2.7003 | 2.7003 | 2.7003 | 2.7003 | 2.0386 | 2.5876 | 2.5876 | 2.5876 | 2.5876 | 2.5876
2020-04-15 16:00 | Winter | 1.3146 | 2.0214 | 3.0588 | 3.0588 | 3.0588 | 3.0588 | 0.79163 | 0.79163 | 0.79163 | 0.79163 | 0.79163 | 0.79163 | 2.2482 | 3.243 | 3.8947 | 4.2377 | 4.9238 | 5.6098 | 0.74686 | 2.0288 | 2.5446 | 2.5446 | 2.5446 | 2.5446 | 2.0005 | 2.5392 | 2.5392 | 2.5392 | 2.5392 | 2.5392
2020-04-15 17:00 | Winter | 1.2384 | 1.9042 | 2.8814 | 2.8814 | 2.8814 | 2.8814 | 0.70875 | 0.70875 | 0.70875 | 0.70875 | 0.70875 | 0.70875 | 2.2101 | 3.188 | 3.8287 | 4.1659 | 4.8403 | 5.5147 | 0.6897 | 1.8735 | 2.3498 | 2.3498 | 2.3498 | 2.3498 | 1.8482 | 2.3459 | 2.3459 | 2.3459 | 2.3459 | 2.3459
2020-04-15 18:00 | Winter | 0.87056 | 1.3386 | 2.0256 | 2.0256 | 2.0256 | 2.0256 | 0.62646 | 0.62646 | 0.62646 | 0.62646 | 0.62646 | 0.62646 | 2.2101 | 3.188 | 3.8287 | 4.1659 | 4.8403 | 5.5147 | 0.57157 | 1.5526 | 1.9474 | 1.9474 | 1.9474 | 1.9474 | 1.4421 | 1.8304 | 1.8304 | 1.8304 | 1.8304 | 1.8304
2020-04-15 19:00 | Winter | 0.66684 | 1.0253 | 1.5515 | 1.5515 | 1.5515 | 1.5515 | 0.49155 | 0.49155 | 0.49155 | 0.49155 | 0.49155 | 0.49155 | 2.0197 | 2.9134 | 3.4989 | 3.8071 | 4.4234 | 5.0398 | 0.57539 | 1.563 | 1.9603 | 1.9603 | 1.9603 | 1.9603 | 1.0532 | 1.3368 | 1.3368 | 1.3368 | 1.3368 | 1.3368
2020-04-15 20:00 | Winter | 0.66684 | 1.0253 | 1.5515 | 1.5515 | 1.5515 | 1.5515 | 0.36581 | 0.36581 | 0.36581 | 0.36581 | 0.36581 | 0.36581 | 1.9243 | 2.7758 | 3.3336 | 3.6272 | 4.2144 | 4.8016 | 0.55633 | 1.5112 | 1.8954 | 1.8954 | 1.8954 | 1.8954 | 0.97168 | 1.2333 | 1.2333 | 1.2333 | 1.2333 | 1.2333
2020-04-15 21:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.3258 | 0.3258 | 0.3258 | 0.3258 | 0.3258 | 0.3258 | 1.8481 | 2.6658 | 3.2016 | 3.4836 | 4.0475 | 4.6115 | 0.50299 | 1.3663 | 1.7137 | 1.7137 | 1.7137 | 1.7137 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-04-15 22:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.3458 | 0.3458 | 0.3458 | 0.3458 | 0.3458 | 0.3458 | 1.7528 | 2.5284 | 3.0366 | 3.304 | 3.8389 | 4.3738 | 0.49155 | 1.3353 | 1.6747 | 1.6747 | 1.6747 | 1.6747 | 0.82009 | 1.0409 | 1.0409 | 1.0409 | 1.0409 | 1.0409
2020-04-15 23:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.31881 | 0.31881 | 0.31881 | 0.31881 | 0.31881 | 0.31881 | 1.7147 | 2.4735 | 2.9705 | 3.2322 | 3.7554 | 4.2787 | 0.46488 | 1.2628 | 1.5839 | 1.5839 | 1.5839 | 1.5839 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-04-16 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.35437 | 0.35437 | 0.35437 | 0.35437 | 0.35437 | 0.35437 | 1.5433 | 2.2261 | 2.6735 | 2.909 | 3.3799 | 3.8508 | 0.4344 | 1.18 | 1.48 | 1.48 | 1.48 | 1.48 | 0.7621 | 0.96732 | 0.96732 | 0.96732 | 0.96732 | 0.96732
2020-04-16 01:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.34866 | 0.34866 | 0.34866 | 0.34866 | 0.34866 | 0.34866 | 1.5085 | 2.176 | 2.6133 | 2.8434 | 3.3037 | 3.7641 | 0.43821 | 1.1903 | 1.493 | 1.493 | 1.493 | 1.493 | 0.80021 | 1.0157 | 1.0157 | 1.0157 | 1.0157 | 1.0157
2020-04-16 02:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.25973 | 0.25973 | 0.25973 | 0.25973 | 0.25973 | 0.25973 | 1.5052 | 2.1711 | 2.6075 | 2.8371 | 3.2964 | 3.7557 | 0.44202 | 1.2007 | 1.506 | 1.506 | 1.506 | 1.506 | 0.80021 | 1.0157 | 1.0157 | 1.0157 | 1.0157 | 1.0157
2020-04-16 03:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.36581 | 0.36581 | 0.36581 | 0.36581 | 0.36581 | 0.36581 | 1.5052 | 2.1711 | 2.6075 | 2.8371 | 3.2964 | 3.7557 | 0.44335 | 1.2043 | 1.5105 | 1.5105 | 1.5105 | 1.5105 | 0.80021 | 1.0157 | 1.0157 | 1.0157 | 1.0157 | 1.0157
2020-04-16 04:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.36866 | 0.36866 | 0.36866 | 0.36866 | 0.36866 | 0.36866 | 1.5623 | 2.2536 | 2.7065 | 2.9449 | 3.4216 | 3.8984 | 0.45726 | 1.2421 | 1.5579 | 1.5579 | 1.5579 | 1.5579 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-04-16 05:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.37438 | 0.37438 | 0.37438 | 0.37438 | 0.37438 | 0.37438 | 1.5814 | 2.2811 | 2.7395 | 2.9808 | 3.4633 | 3.9459 | 0.47233 | 1.283 | 1.6092 | 1.6092 | 1.6092 | 1.6092 | 1.1319 | 1.4367 | 1.4367 | 1.4367 | 1.4367 | 1.4367
2020-04-16 06:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.64302 | 0.64302 | 0.64302 | 0.64302 | 0.64302 | 0.64302 | 1.7909 | 2.5834 | 3.1026 | 3.3758 | 3.9223 | 4.4688 | 0.54871 | 1.4905 | 1.8695 | 1.8695 | 1.8695 | 1.8695 | 1.3523 | 1.7164 | 1.7164 | 1.7164 | 1.7164 | 1.7164
2020-04-16 07:00 | Winter | 0.77022 | 1.1843 | 1.7921 | 1.7921 | 1.7921 | 1.7921 | 0.68017 | 0.68017 | 0.68017 | 0.68017 | 0.68017 | 0.68017 | 1.9624 | 2.8307 | 3.3996 | 3.699 | 4.2979 | 4.8967 | 0.62111 | 1.6872 | 2.1161 | 2.1161 | 2.1161 | 2.1161 | 1.6576 | 2.1039 | 2.1039 | 2.1039 | 2.1039 | 2.1039
2020-04-16 08:00 | Winter | 1.2765 | 1.9628 | 2.9701 | 2.9701 | 2.9701 | 2.9701 | 0.77448 | 0.77448 | 0.77448 | 0.77448 | 0.77448 | 0.77448 | 2.0767 | 2.9956 | 3.5977 | 3.9145 | 4.5482 | 5.182 | 0.74305 | 2.0184 | 2.5316 | 2.5316 | 2.5316 | 2.5316 | 1.9243 | 2.4425 | 2.4425 | 2.4425 | 2.4425 | 2.4425
2020-04-16 09:00 | Winter | 1.2194 | 1.8749 | 2.8371 | 2.8371 | 2.8371 | 2.8371 | 0.91452 | 0.91452 | 0.91452 | 0.91452 | 0.91452 | 0.91452 | 2.2673 | 3.2705 | 3.9277 | 4.2736 | 4.9655 | 5.6574 | 0.70113 | 1.9046 | 2.3888 | 2.3888 | 2.3888 | 2.3888 | 1.9815 | 2.515 | 2.515 | 2.515 | 2.515 | 2.515
2020-04-16 10:00 | Winter | 1.2956 | 1.9921 | 3.0144 | 3.0144 | 3.0144 | 3.0144 | 0.88594 | 0.88594 | 0.88594 | 0.88594 | 0.88594 | 0.88594 | 2.3244 | 3.3529 | 4.0267 | 4.3814 | 5.0907 | 5.8 | 0.71256 | 1.9356 | 2.4277 | 2.4277 | 2.4277 | 2.4277 | 2.0005 | 2.5392 | 2.5392 | 2.5392 | 2.5392 | 2.5392
2020-04-16 11:00 | Winter | 1.2718 | 1.9555 | 2.959 | 2.959 | 2.959 | 2.959 | 0.93738 | 0.93738 | 0.93738 | 0.93738 | 0.93738 | 0.93738 | 2.3225 | 3.3502 | 4.0235 | 4.3778 | 5.0866 | 5.7953 | 0.69351 | 1.8839 | 2.3628 | 2.3628 | 2.3628 | 2.3628 | 2.0196 | 2.5634 | 2.5634 | 2.5634 | 2.5634 | 2.5634
2020-04-16 12:00 | Winter | 1.2003 | 1.8456 | 2.7928 | 2.7928 | 2.7928 | 2.7928 | 0.9431 | 0.9431 | 0.9431 | 0.9431 | 0.9431 | 0.9431 | 2.3625 | 3.4079 | 4.0927 | 4.4532 | 5.1741 | 5.8951 | 0.68589 | 1.8632 | 2.3368 | 2.3368 | 2.3368 | 2.3368 | 2.0356 | 2.5837 | 2.5837 | 2.5837 | 2.5837 | 2.5837
2020-04-16 13:00 | Winter | 1.2003 | 1.8456 | 2.7928 | 2.7928 | 2.7928 | 2.7928 | 1.0431 | 1.0431 | 1.0431 | 1.0431 | 1.0431 | 1.0431 | 2.2482 | 3.243 | 3.8947 | 4.2377 | 4.9238 | 5.6098 | 0.67827 | 1.8425 | 2.3109 | 2.3109 | 2.3109 | 2.3109 | 2.0386 | 2.5876 | 2.5876 | 2.5876 | 2.5876 | 2.5876
2020-04-16 14:00 | Winter | 1.2194 | 1.8749 | 2.8371 | 2.8371 | 2.8371 | 2.8371 | 0.9431 | 0.9431 | 0.9431 | 0.9431 | 0.9431 | 0.9431 | 2.2482 | 3.243 | 3.8947 | 4.2377 | 4.9238 | 5.6098 | 0.65922 | 1.7907 | 2.246 | 2.246 | 2.246 | 2.246 | 2.0196 | 2.5634 | 2.5634 | 2.5634 | 2.5634 | 2.5634
2020-04-16 15:00 | Winter | 1.2003 | 1.8456 | 2.7928 | 2.7928 | 2.7928 | 2.7928 | 0.86308 | 0.86308 | 0.86308 | 0.86308 | 0.86308 | 0.86308 | 2.3816 | 3.4353 | 4.1258 | 4.4891 | 5.2159 | 5.9426 | 0.65541 | 1.7803 | 2.233 | 2.233 | 2.233 | 2.233 | 2.0196 | 2.5634 | 2.5634 | 2.5634 | 2.5634 | 2.5634
2020-04-16 16:00 | Winter | 1.1622 | 1.787 | 2.7041 | 2.7041 | 2.7041 | 2.7041 | 0.91738 | 0.91738 | 0.91738 | 0.91738 | 0.91738 | 0.91738 | 2.2482 | 3.243 | 3.8947 | 4.2377 | 4.9238 | 5.6098 | 0.66684 | 1.8114 | 2.2719 | 2.2719 | 2.2719 | 2.2719 | 1.9243 | 2.4425 | 2.4425 | 2.4425 | 2.4425 | 2.4425
2020-04-16 17:00 | Winter | 1.086 | 1.6698 | 2.5268 | 2.5268 | 2.5268 | 2.5268 | 0.76591 | 0.76591 | 0.76591 | 0.76591 | 0.76591 | 0.76591 | 2.2673 | 3.2705 | 3.9277 | 4.2736 | 4.9655 | 5.6574 | 0.62111 | 1.6872 | 2.1161 | 2.1161 | 2.1161 | 2.1161 | 1.8672 | 2.3699 | 2.3699 | 2.3699 | 2.3699 | 2.3699
2020-04-16 18:00 | Winter | 0.83571 | 1.285 | 1.9445 | 1.9445 | 1.9445 | 1.9445 | 0.59158 | 0.59158 | 0.59158 | 0.59158 | 0.59158 | 0.59158 | 2.2863 | 3.2979 | 3.9607 | 4.3096 | 5.0072 | 5.7049 | 0.56014 | 1.5216 | 1.9084 | 1.9084 | 1.9084 | 1.9084 | 1.4156 | 1.7968 | 1.7968 | 1.7968 | 1.7968 | 1.7968
2020-04-16 19:00 | Winter | 0.66684 | 1.0253 | 1.5515 | 1.5515 | 1.5515 | 1.5515 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 2.1196 | 3.0575 | 3.672 | 3.9954 | 4.6422 | 5.289 | 0.5449 | 1.4802 | 1.8565 | 1.8565 | 1.8565 | 1.8565 | 1.069 | 1.3569 | 1.3569 | 1.3569 | 1.3569 | 1.3569
2020-04-16 20:00 | Winter | 0.64779 | 0.99605 | 1.5072 | 1.5072 | 1.5072 | 1.5072 | 0.37438 | 0.37438 | 0.37438 | 0.37438 | 0.37438 | 0.37438 | 1.9815 | 2.8582 | 3.4326 | 3.735 | 4.3396 | 4.9443 | 0.54109 | 1.4698 | 1.8435 | 1.8435 | 1.8435 | 1.8435 | 0.98011 | 1.244 | 1.244 | 1.244 | 1.244 | 1.244
2020-04-16 21:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.37152 | 0.37152 | 0.37152 | 0.37152 | 0.37152 | 0.37152 | 1.9176 | 2.7661 | 3.3221 | 3.6146 | 4.1998 | 4.785 | 0.53728 | 1.4595 | 1.8305 | 1.8305 | 1.8305 | 1.8305 | 0.93358 | 1.185 | 1.185 | 1.185 | 1.185 | 1.185
2020-04-16 22:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.34008 | 0.34008 | 0.34008 | 0.34008 | 0.34008 | 0.34008 | 1.829 | 2.6383 | 3.1686 | 3.4477 | 4.0058 | 4.5639 | 0.47631 | 1.2939 | 1.6228 | 1.6228 | 1.6228 | 1.6228 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-04-16 23:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.36581 | 0.36581 | 0.36581 | 0.36581 | 0.36581 | 0.36581 | 1.7528 | 2.5284 | 3.0366 | 3.304 | 3.8389 | 4.3738 | 0.46107 | 1.2525 | 1.5709 | 1.5709 | 1.5709 | 1.5709 | 0.83852 | 1.0643 | 1.0643 | 1.0643 | 1.0643 | 1.0643
2020-04-17 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.36295 | 0.36295 | 0.36295 | 0.36295 | 0.36295 | 0.36295 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.45726 | 1.2421 | 1.5579 | 1.5579 | 1.5579 | 1.5579 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-04-17 01:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.36009 | 0.36009 | 0.36009 | 0.36009 | 0.36009 | 0.36009 | 1.5435 | 2.2265 | 2.674 | 2.9095 | 3.3805 | 3.8515 | 0.44202 | 1.2007 | 1.506 | 1.506 | 1.506 | 1.506 | 0.80021 | 1.0157 | 1.0157 | 1.0157 | 1.0157 | 1.0157
2020-04-17 02:00 | Winter | 0.58656 | 0.9019 | 1.3647 | 1.3647 | 1.3647 | 1.3647 | 0.35437 | 0.35437 | 0.35437 | 0.35437 | 0.35437 | 0.35437 | 1.467 | 2.1162 | 2.5415 | 2.7653 | 3.213 | 3.6607 | 0.44583 | 1.211 | 1.5189 | 1.5189 | 1.5189 | 1.5189 | 0.80021 | 1.0157 | 1.0157 | 1.0157 | 1.0157 | 1.0157
2020-04-17 03:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.2715 | 0.2715 | 0.2715 | 0.2715 | 0.2715 | 0.2715 | 1.467 | 2.1162 | 2.5415 | 2.7653 | 3.213 | 3.6607 | 0.44583 | 1.211 | 1.5189 | 1.5189 | 1.5189 | 1.5189 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-04-17 04:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.2645 | 0.2645 | 0.2645 | 0.2645 | 0.2645 | 0.2645 | 1.5236 | 2.1977 | 2.6394 | 2.8718 | 3.3368 | 3.8017 | 0.44583 | 1.211 | 1.5189 | 1.5189 | 1.5189 | 1.5189 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-04-17 05:00 | Winter | 0.5905 | 0.90796 | 1.3739 | 1.3739 | 1.3739 | 1.3739 | 0.52013 | 0.52013 | 0.52013 | 0.52013 | 0.52013 | 0.52013 | 1.5571 | 2.2461 | 2.6975 | 2.9351 | 3.4103 | 3.8854 | 0.5068 | 1.3767 | 1.7267 | 1.7267 | 1.7267 | 1.7267 | 1.1385 | 1.445 | 1.445 | 1.445 | 1.445 | 1.445
2020-04-17 06:00 | Winter | 0.64093 | 0.9855 | 1.4913 | 1.4913 | 1.4913 | 1.4913 | 0.66017 | 0.66017 | 0.66017 | 0.66017 | 0.66017 | 0.66017 | 1.6576 | 2.391 | 2.8715 | 3.1244 | 3.6302 | 4.1361 | 0.50299 | 1.3663 | 1.7137 | 1.7137 | 1.7137 | 1.7137 | 1.4614 | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 1.8549
2020-04-17 07:00 | Winter | 0.78115 | 1.2011 | 1.8175 | 1.8175 | 1.8175 | 1.8175 | 0.76019 | 0.76019 | 0.76019 | 0.76019 | 0.76019 | 0.76019 | 1.9053 | 2.7483 | 3.3006 | 3.5913 | 4.1727 | 4.7541 | 0.69351 | 1.8839 | 2.3628 | 2.3628 | 2.3628 | 2.3628 | 1.6089 | 2.0422 | 2.0422 | 2.0422 | 2.0422 | 2.0422
2020-04-17 08:00 | Winter | 1.0288 | 1.582 | 2.3938 | 2.3938 | 2.3938 | 2.3938 | 0.80592 | 0.80592 | 0.80592 | 0.80592 | 0.80592 | 0.80592 | 2.0577 | 2.9681 | 3.5647 | 3.8786 | 4.5065 | 5.1344 | 0.72018 | 1.9563 | 2.4537 | 2.4537 | 2.4537 | 2.4537 | 1.9434 | 2.4667 | 2.4667 | 2.4667 | 2.4667 | 2.4667
2020-04-17 09:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 0.8545 | 0.8545 | 0.8545 | 0.8545 | 0.8545 | 0.8545 | 2.0386 | 2.9407 | 3.5316 | 3.8427 | 4.4648 | 5.0869 | 0.6897 | 1.8735 | 2.3498 | 2.3498 | 2.3498 | 2.3498 | 1.8686 | 2.3718 | 2.3718 | 2.3718 | 2.3718 | 2.3718
2020-04-17 10:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 0.77448 | 0.77448 | 0.77448 | 0.77448 | 0.77448 | 0.77448 | 2.1861 | 3.1534 | 3.7871 | 4.1206 | 4.7877 | 5.4548 | 0.66684 | 1.8114 | 2.2719 | 2.2719 | 2.2719 | 2.2719 | 1.9053 | 2.4183 | 2.4183 | 2.4183 | 2.4183 | 2.4183
2020-04-17 11:00 | Winter | 1.2384 | 1.9042 | 2.8814 | 2.8814 | 2.8814 | 2.8814 | 0.80306 | 0.80306 | 0.80306 | 0.80306 | 0.80306 | 0.80306 | 2.2101 | 3.188 | 3.8287 | 4.1659 | 4.8403 | 5.5147 | 0.67446 | 1.8321 | 2.2979 | 2.2979 | 2.2979 | 2.2979 | 2.0196 | 2.5634 | 2.5634 | 2.5634 | 2.5634 | 2.5634
2020-04-17 12:00 | Winter | 1.2003 | 1.8456 | 2.7928 | 2.7928 | 2.7928 | 2.7928 | 0.8345 | 0.8345 | 0.8345 | 0.8345 | 0.8345 | 0.8345 | 2.191 | 3.1605 | 3.7957 | 4.13 | 4.7986 | 5.4672 | 0.65631 | 1.7828 | 2.236 | 2.236 | 2.236 | 2.236 | 1.9243 | 2.4425 | 2.4425 | 2.4425 | 2.4425 | 2.4425
2020-04-17 13:00 | Winter | 1.2194 | 1.8749 | 2.8371 | 2.8371 | 2.8371 | 2.8371 | 0.79735 | 0.79735 | 0.79735 | 0.79735 | 0.79735 | 0.79735 | 2.172 | 3.133 | 3.7627 | 4.0941 | 4.7569 | 5.4197 | 0.66303 | 1.8011 | 2.2589 | 2.2589 | 2.2589 | 2.2589 | 1.9243 | 2.4425 | 2.4425 | 2.4425 | 2.4425 | 2.4425
2020-04-17 14:00 | Winter | 1.2194 | 1.8749 | 2.8371 | 2.8371 | 2.8371 | 2.8371 | 0.8545 | 0.8545 | 0.8545 | 0.8545 | 0.8545 | 0.8545 | 2.1339 | 3.0781 | 3.6967 | 4.0223 | 4.6734 | 5.3246 | 0.65541 | 1.7803 | 2.233 | 2.233 | 2.233 | 2.233 | 1.8672 | 2.3699 | 2.3699 | 2.3699 | 2.3699 | 2.3699
2020-04-17 15:00 | Winter | 1.1622 | 1.787 | 2.7041 | 2.7041 | 2.7041 | 2.7041 | 0.84593 | 0.84593 | 0.84593 | 0.84593 | 0.84593 | 0.84593 | 2.0958 | 3.0231 | 3.6307 | 3.9504 | 4.59 | 5.2295 | 0.62111 | 1.6872 | 2.1161 | 2.1161 | 2.1161 | 2.1161 | 1.8672 | 2.3699 | 2.3699 | 2.3699 | 2.3699 | 2.3699
2020-04-17 16:00 | Winter | 1.1432 | 1.7577 | 2.6598 | 2.6598 | 2.6598 | 2.6598 | 0.86022 | 0.86022 | 0.86022 | 0.86022 | 0.86022 | 0.86022 | 2.1339 | 3.0781 | 3.6967 | 4.0223 | 4.6734 | 5.3246 | 0.6173 | 1.6768 | 2.1032 | 2.1032 | 2.1032 | 2.1032 | 1.8481 | 2.3458 | 2.3458 | 2.3458 | 2.3458 | 2.3458
2020-04-17 17:00 | Winter | 1.0669 | 1.6405 | 2.4825 | 2.4825 | 2.4825 | 2.4825 | 0.77448 | 0.77448 | 0.77448 | 0.77448 | 0.77448 | 0.77448 | 2.172 | 3.133 | 3.7627 | 4.0941 | 4.7569 | 5.4197 | 0.62873 | 1.7079 | 2.1421 | 2.1421 | 2.1421 | 2.1421 | 1.7531 | 2.2252 | 2.2252 | 2.2252 | 2.2252 | 2.2252
2020-04-17 18:00 | Winter | 0.81823 | 1.2581 | 1.9038 | 1.9038 | 1.9038 | 1.9038 | 0.59729 | 0.59729 | 0.59729 | 0.59729 | 0.59729 | 0.59729 | 2.1339 | 3.0781 | 3.6967 | 4.0223 | 4.6734 | 5.3246 | 0.58301 | 1.5837 | 1.9863 | 1.9863 | 1.9863 | 1.9863 | 1.3669 | 1.735 | 1.735 | 1.735 | 1.735 | 1.735
2020-04-17 19:00 | Winter | 0.64779 | 0.99605 | 1.5072 | 1.5072 | 1.5072 | 1.5072 | 0.49155 | 0.49155 | 0.49155 | 0.49155 | 0.49155 | 0.49155 | 2.0489 | 2.9555 | 3.5495 | 3.8621 | 4.4874 | 5.1126 | 0.5792 | 1.5733 | 1.9733 | 1.9733 | 1.9733 | 1.9733 | 1.0296 | 1.3068 | 1.3068 | 1.3068 | 1.3068 | 1.3068
2020-04-17 20:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.39438 | 0.39438 | 0.39438 | 0.39438 | 0.39438 | 0.39438 | 1.9815 | 2.8582 | 3.4326 | 3.735 | 4.3396 | 4.9443 | 0.58301 | 1.5837 | 1.9863 | 1.9863 | 1.9863 | 1.9863 | 0.96911 | 1.2301 | 1.2301 | 1.2301 | 1.2301 | 1.2301
2020-04-17 21:00 | Winter | 0.57151 | 0.87877 | 1.3297 | 1.3297 | 1.3297 | 1.3297 | 0.37724 | 0.37724 | 0.37724 | 0.37724 | 0.37724 | 0.37724 | 1.9243 | 2.7758 | 3.3336 | 3.6272 | 4.2144 | 4.8016 | 0.57936 | 1.5738 | 1.9739 | 1.9739 | 1.9739 | 1.9739 | 0.91452 | 1.1608 | 1.1608 | 1.1608 | 1.1608 | 1.1608
2020-04-17 22:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.41439 | 0.41439 | 0.41439 | 0.41439 | 0.41439 | 0.41439 | 1.8672 | 2.6933 | 3.2346 | 3.5195 | 4.0892 | 4.659 | 0.54871 | 1.4905 | 1.8695 | 1.8695 | 1.8695 | 1.8695 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-04-17 23:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.2796 | 0.2796 | 0.2796 | 0.2796 | 0.2796 | 0.2796 | 1.7147 | 2.4735 | 2.9705 | 3.2322 | 3.7554 | 4.2787 | 0.49536 | 1.3456 | 1.6877 | 1.6877 | 1.6877 | 1.6877 | 0.80021 | 1.0157 | 1.0157 | 1.0157 | 1.0157 | 1.0157
2020-04-18 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.26006 | 0.26006 | 0.26006 | 0.26006 | 0.26006 | 0.26006 | 1.6195 | 2.336 | 2.8055 | 3.0526 | 3.5468 | 4.041 | 0.49536 | 1.3456 | 1.6877 | 1.6877 | 1.6877 | 1.6877 | 0.80021 | 1.0157 | 1.0157 | 1.0157 | 1.0157 | 1.0157
2020-04-18 01:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.27721 | 0.27721 | 0.27721 | 0.27721 | 0.27721 | 0.27721 | 1.5478 | 2.2327 | 2.6814 | 2.9176 | 3.3899 | 3.8623 | 0.46488 | 1.2628 | 1.5839 | 1.5839 | 1.5839 | 1.5839 | 0.80021 | 1.0157 | 1.0157 | 1.0157 | 1.0157 | 1.0157
2020-04-18 02:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 1.5623 | 2.2536 | 2.7065 | 2.9449 | 3.4216 | 3.8984 | 0.46488 | 1.2628 | 1.5839 | 1.5839 | 1.5839 | 1.5839 | 0.80021 | 1.0157 | 1.0157 | 1.0157 | 1.0157 | 1.0157
2020-04-18 03:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 1.5242 | 2.1986 | 2.6405 | 2.873 | 3.3382 | 3.8033 | 0.47631 | 1.2939 | 1.6228 | 1.6228 | 1.6228 | 1.6228 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-04-18 04:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.39724 | 0.39724 | 0.39724 | 0.39724 | 0.39724 | 0.39724 | 1.5242 | 2.1986 | 2.6405 | 2.873 | 3.3382 | 3.8033 | 0.46488 | 1.2628 | 1.5839 | 1.5839 | 1.5839 | 1.5839 | 0.78115 | 0.9915 | 0.9915 | 0.9915 | 0.9915 | 0.9915
2020-04-18 05:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.32294 | 0.32294 | 0.32294 | 0.32294 | 0.32294 | 0.32294 | 1.5242 | 2.1986 | 2.6405 | 2.873 | 3.3382 | 3.8033 | 0.4725 | 1.2835 | 1.6098 | 1.6098 | 1.6098 | 1.6098 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-04-18 06:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.49727 | 0.49727 | 0.49727 | 0.49727 | 0.49727 | 0.49727 | 1.6004 | 2.3086 | 2.7725 | 3.0167 | 3.5051 | 3.9934 | 0.47631 | 1.2939 | 1.6228 | 1.6228 | 1.6228 | 1.6228 | 1.0096 | 1.2814 | 1.2814 | 1.2814 | 1.2814 | 1.2814
2020-04-18 07:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.5087 | 0.5087 | 0.5087 | 0.5087 | 0.5087 | 0.5087 | 1.6195 | 2.336 | 2.8055 | 3.0526 | 3.5468 | 4.041 | 0.48393 | 1.3146 | 1.6488 | 1.6488 | 1.6488 | 1.6488 | 1.0669 | 1.3542 | 1.3542 | 1.3542 | 1.3542 | 1.3542
2020-04-18 08:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 1.6576 | 2.391 | 2.8715 | 3.1244 | 3.6302 | 4.1361 | 0.48393 | 1.3146 | 1.6488 | 1.6488 | 1.6488 | 1.6488 | 0.93358 | 1.185 | 1.185 | 1.185 | 1.185 | 1.185
2020-04-18 09:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.5287 | 0.5287 | 0.5287 | 0.5287 | 0.5287 | 0.5287 | 1.7333 | 2.5002 | 3.0026 | 3.2671 | 3.796 | 4.3249 | 0.59063 | 1.6044 | 2.0123 | 2.0123 | 2.0123 | 2.0123 | 0.99073 | 1.2575 | 1.2575 | 1.2575 | 1.2575 | 1.2575
2020-04-18 10:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.54871 | 0.54871 | 0.54871 | 0.54871 | 0.54871 | 0.54871 | 1.9624 | 2.8307 | 3.3996 | 3.699 | 4.2979 | 4.8967 | 0.55252 | 1.5009 | 1.8825 | 1.8825 | 1.8825 | 1.8825 | 1.0288 | 1.3059 | 1.3059 | 1.3059 | 1.3059 | 1.3059
2020-04-18 11:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 1.8672 | 2.6933 | 3.2346 | 3.5195 | 4.0892 | 4.659 | 0.52204 | 1.4181 | 1.7786 | 1.7786 | 1.7786 | 1.7786 | 1.0098 | 1.2817 | 1.2817 | 1.2817 | 1.2817 | 1.2817
2020-04-18 12:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 1.8481 | 2.6658 | 3.2016 | 3.4836 | 4.0475 | 4.6115 | 0.57539 | 1.563 | 1.9603 | 1.9603 | 1.9603 | 1.9603 | 0.93358 | 1.185 | 1.185 | 1.185 | 1.185 | 1.185
2020-04-18 13:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 1.9053 | 2.7483 | 3.3006 | 3.5913 | 4.1727 | 4.7541 | 0.52585 | 1.4284 | 1.7916 | 1.7916 | 1.7916 | 1.7916 | 0.93358 | 1.185 | 1.185 | 1.185 | 1.185 | 1.185
2020-04-18 14:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 1.829 | 2.6383 | 3.1686 | 3.4477 | 4.0058 | 4.5639 | 0.4725 | 1.2835 | 1.6098 | 1.6098 | 1.6098 | 1.6098 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-04-18 15:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 1.829 | 2.6383 | 3.1686 | 3.4477 | 4.0058 | 4.5639 | 0.44202 | 1.2007 | 1.506 | 1.506 | 1.506 | 1.506 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-04-18 16:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 1.8481 | 2.6658 | 3.2016 | 3.4836 | 4.0475 | 4.6115 | 0.5068 | 1.3767 | 1.7267 | 1.7267 | 1.7267 | 1.7267 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-04-18 17:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.43439 | 0.43439 | 0.43439 | 0.43439 | 0.43439 | 0.43439 | 1.9815 | 2.8582 | 3.4326 | 3.735 | 4.3396 | 4.9443 | 0.53347 | 1.4491 | 1.8175 | 1.8175 | 1.8175 | 1.8175 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-04-18 18:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 1.9815 | 2.8582 | 3.4326 | 3.735 | 4.3396 | 4.9443 | 0.56014 | 1.5216 | 1.9084 | 1.9084 | 1.9084 | 1.9084 | 0.85908 | 1.0904 | 1.0904 | 1.0904 | 1.0904 | 1.0904
2020-04-18 19:00 | Winter | 0.55604 | 0.85498 | 1.2937 | 1.2937 | 1.2937 | 1.2937 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 1.8865 | 2.7212 | 3.2681 | 3.5559 | 4.1316 | 4.7072 | 0.54109 | 1.4698 | 1.8435 | 1.8435 | 1.8435 | 1.8435 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-04-18 20:00 | Winter | 0.51729 | 0.7954 | 1.2036 | 1.2036 | 1.2036 | 1.2036 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 1.9053 | 2.7483 | 3.3006 | 3.5913 | 4.1727 | 4.7541 | 0.54109 | 1.4698 | 1.8435 | 1.8435 | 1.8435 | 1.8435 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-04-18 21:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.37438 | 0.37438 | 0.37438 | 0.37438 | 0.37438 | 0.37438 | 1.8481 | 2.6658 | 3.2016 | 3.4836 | 4.0475 | 4.6115 | 0.53352 | 1.4493 | 1.8177 | 1.8177 | 1.8177 | 1.8177 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-04-18 22:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.26864 | 0.26864 | 0.26864 | 0.26864 | 0.26864 | 0.26864 | 1.7338 | 2.5009 | 3.0036 | 3.2681 | 3.7972 | 4.3262 | 0.52966 | 1.4388 | 1.8046 | 1.8046 | 1.8046 | 1.8046 | 0.80021 | 1.0157 | 1.0157 | 1.0157 | 1.0157 | 1.0157
2020-04-18 23:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.28864 | 0.28864 | 0.28864 | 0.28864 | 0.28864 | 0.28864 | 1.6576 | 2.391 | 2.8715 | 3.1244 | 3.6302 | 4.1361 | 0.49536 | 1.3456 | 1.6877 | 1.6877 | 1.6877 | 1.6877 | 0.80021 | 1.0157 | 1.0157 | 1.0157 | 1.0157 | 1.0157
2020-04-19 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 1.5623 | 2.2536 | 2.7065 | 2.9449 | 3.4216 | 3.8984 | 0.46869 | 1.2732 | 1.5968 | 1.5968 | 1.5968 | 1.5968 | 0.7621 | 0.96732 | 0.96732 | 0.96732 | 0.96732 | 0.96732
2020-04-19 01:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.40296 | 0.40296 | 0.40296 | 0.40296 | 0.40296 | 0.40296 | 1.5052 | 2.1711 | 2.6075 | 2.8371 | 3.2964 | 3.7557 | 0.45345 | 1.2318 | 1.5449 | 1.5449 | 1.5449 | 1.5449 | 0.78115 | 0.9915 | 0.9915 | 0.9915 | 0.9915 | 0.9915
2020-04-19 02:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.26292 | 0.26292 | 0.26292 | 0.26292 | 0.26292 | 0.26292 | 1.4861 | 2.1437 | 2.5745 | 2.8012 | 3.2547 | 3.7082 | 0.46488 | 1.2628 | 1.5839 | 1.5839 | 1.5839 | 1.5839 | 0.7621 | 0.96732 | 0.96732 | 0.96732 | 0.96732 | 0.96732
2020-04-19 03:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.39153 | 0.39153 | 0.39153 | 0.39153 | 0.39153 | 0.39153 | 1.4861 | 2.1437 | 2.5745 | 2.8012 | 3.2547 | 3.7082 | 0.46488 | 1.2628 | 1.5839 | 1.5839 | 1.5839 | 1.5839 | 0.78115 | 0.9915 | 0.9915 | 0.9915 | 0.9915 | 0.9915
2020-04-19 04:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.33437 | 0.33437 | 0.33437 | 0.33437 | 0.33437 | 0.33437 | 1.5242 | 2.1986 | 2.6405 | 2.873 | 3.3382 | 3.8033 | 0.47631 | 1.2939 | 1.6228 | 1.6228 | 1.6228 | 1.6228 | 0.78115 | 0.9915 | 0.9915 | 0.9915 | 0.9915 | 0.9915
2020-04-19 05:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 1.5426 | 2.2252 | 2.6724 | 2.9078 | 3.3785 | 3.8493 | 0.51442 | 1.3974 | 1.7526 | 1.7526 | 1.7526 | 1.7526 | 0.80021 | 1.0157 | 1.0157 | 1.0157 | 1.0157 | 1.0157
2020-04-19 06:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 1.5814 | 2.2811 | 2.7395 | 2.9808 | 3.4633 | 3.9459 | 0.49155 | 1.3353 | 1.6747 | 1.6747 | 1.6747 | 1.6747 | 0.80021 | 1.0157 | 1.0157 | 1.0157 | 1.0157 | 1.0157
2020-04-19 07:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.52013 | 0.52013 | 0.52013 | 0.52013 | 0.52013 | 0.52013 | 1.6576 | 2.391 | 2.8715 | 3.1244 | 3.6302 | 4.1361 | 0.49918 | 1.356 | 1.7007 | 1.7007 | 1.7007 | 1.7007 | 0.78115 | 0.9915 | 0.9915 | 0.9915 | 0.9915 | 0.9915
2020-04-19 08:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.50013 | 0.50013 | 0.50013 | 0.50013 | 0.50013 | 0.50013 | 1.7528 | 2.5284 | 3.0366 | 3.304 | 3.8389 | 4.3738 | 0.56395 | 1.5319 | 1.9214 | 1.9214 | 1.9214 | 1.9214 | 0.80021 | 1.0157 | 1.0157 | 1.0157 | 1.0157 | 1.0157
2020-04-19 09:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.49155 | 0.49155 | 0.49155 | 0.49155 | 0.49155 | 0.49155 | 1.7719 | 2.5559 | 3.0696 | 3.3399 | 3.8806 | 4.4213 | 0.55252 | 1.5009 | 1.8825 | 1.8825 | 1.8825 | 1.8825 | 0.7799 | 0.98991 | 0.98991 | 0.98991 | 0.98991 | 0.98991
2020-04-19 10:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 1.8862 | 2.7208 | 3.2676 | 3.5554 | 4.131 | 4.7066 | 0.5068 | 1.3767 | 1.7267 | 1.7267 | 1.7267 | 1.7267 | 0.78115 | 0.9915 | 0.9915 | 0.9915 | 0.9915 | 0.9915
2020-04-19 11:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 1.8794 | 2.711 | 3.2558 | 3.5426 | 4.1161 | 4.6896 | 0.53728 | 1.4595 | 1.8305 | 1.8305 | 1.8305 | 1.8305 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-04-19 12:00 | Winter | 0.58227 | 0.89531 | 1.3548 | 1.3548 | 1.3548 | 1.3548 | 0.41499 | 0.41499 | 0.41499 | 0.41499 | 0.41499 | 0.41499 | 1.9243 | 2.7758 | 3.3336 | 3.6272 | 4.2144 | 4.8016 | 0.53728 | 1.4595 | 1.8305 | 1.8305 | 1.8305 | 1.8305 | 0.74305 | 0.94314 | 0.94314 | 0.94314 | 0.94314 | 0.94314
2020-04-19 13:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 1.9063 | 2.7498 | 3.3024 | 3.5933 | 4.175 | 4.7567 | 0.49918 | 1.356 | 1.7007 | 1.7007 | 1.7007 | 1.7007 | 0.78115 | 0.9915 | 0.9915 | 0.9915 | 0.9915 | 0.9915
2020-04-19 14:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 1.9243 | 2.7758 | 3.3336 | 3.6272 | 4.2144 | 4.8016 | 0.44964 | 1.2214 | 1.5319 | 1.5319 | 1.5319 | 1.5319 | 0.78115 | 0.9915 | 0.9915 | 0.9915 | 0.9915 | 0.9915
2020-04-19 15:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.49727 | 0.49727 | 0.49727 | 0.49727 | 0.49727 | 0.49727 | 1.8862 | 2.7208 | 3.2676 | 3.5554 | 4.131 | 4.7066 | 0.46488 | 1.2628 | 1.5839 | 1.5839 | 1.5839 | 1.5839 | 0.78115 | 0.9915 | 0.9915 | 0.9915 | 0.9915 | 0.9915
2020-04-19 16:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.46089 | 0.46089 | 0.46089 | 0.46089 | 0.46089 | 0.46089 | 1.8648 | 2.6899 | 3.2305 | 3.515 | 4.084 | 4.6531 | 0.46107 | 1.2525 | 1.5709 | 1.5709 | 1.5709 | 1.5709 | 0.78115 | 0.9915 | 0.9915 | 0.9915 | 0.9915 | 0.9915
2020-04-19 17:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 1.9815 | 2.8582 | 3.4326 | 3.735 | 4.3396 | 4.9443 | 0.56776 | 1.5423 | 1.9344 | 1.9344 | 1.9344 | 1.9344 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-04-19 18:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 1.9624 | 2.8307 | 3.3996 | 3.699 | 4.2979 | 4.8967 | 0.55633 | 1.5112 | 1.8954 | 1.8954 | 1.8954 | 1.8954 | 0.80021 | 1.0157 | 1.0157 | 1.0157 | 1.0157 | 1.0157
2020-04-19 19:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.50584 | 0.50584 | 0.50584 | 0.50584 | 0.50584 | 0.50584 | 1.9815 | 2.8582 | 3.4326 | 3.735 | 4.3396 | 4.9443 | 0.53728 | 1.4595 | 1.8305 | 1.8305 | 1.8305 | 1.8305 | 0.80021 | 1.0157 | 1.0157 | 1.0157 | 1.0157 | 1.0157
2020-04-19 20:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.43154 | 0.43154 | 0.43154 | 0.43154 | 0.43154 | 0.43154 | 1.9053 | 2.7483 | 3.3006 | 3.5913 | 4.1727 | 4.7541 | 0.51823 | 1.4077 | 1.7656 | 1.7656 | 1.7656 | 1.7656 | 0.80021 | 1.0157 | 1.0157 | 1.0157 | 1.0157 | 1.0157
2020-04-19 21:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.38295 | 0.38295 | 0.38295 | 0.38295 | 0.38295 | 0.38295 | 1.8862 | 2.7208 | 3.2676 | 3.5554 | 4.131 | 4.7066 | 0.57157 | 1.5526 | 1.9474 | 1.9474 | 1.9474 | 1.9474 | 0.80021 | 1.0157 | 1.0157 | 1.0157 | 1.0157 | 1.0157
2020-04-19 22:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.26873 | 0.26873 | 0.26873 | 0.26873 | 0.26873 | 0.26873 | 1.7147 | 2.4735 | 2.9705 | 3.2322 | 3.7554 | 4.2787 | 0.53347 | 1.4491 | 1.8175 | 1.8175 | 1.8175 | 1.8175 | 0.78115 | 0.9915 | 0.9915 | 0.9915 | 0.9915 | 0.9915
2020-04-19 23:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.41439 | 0.41439 | 0.41439 | 0.41439 | 0.41439 | 0.41439 | 1.6578 | 2.3914 | 2.872 | 3.1249 | 3.6308 | 4.1367 | 0.52966 | 1.4388 | 1.8046 | 1.8046 | 1.8046 | 1.8046 | 0.78115 | 0.9915 | 0.9915 | 0.9915 | 0.9915 | 0.9915
2020-04-20 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 1.5623 | 2.2536 | 2.7065 | 2.9449 | 3.4216 | 3.8984 | 0.47631 | 1.2939 | 1.6228 | 1.6228 | 1.6228 | 1.6228 | 0.80021 | 1.0157 | 1.0157 | 1.0157 | 1.0157 | 1.0157
2020-04-20 01:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.27717 | 0.27717 | 0.27717 | 0.27717 | 0.27717 | 0.27717 | 1.5052 | 2.1711 | 2.6075 | 2.8371 | 3.2964 | 3.7557 | 0.48012 | 1.3042 | 1.6358 | 1.6358 | 1.6358 | 1.6358 | 0.80021 | 1.0157 | 1.0157 | 1.0157 | 1.0157 | 1.0157
2020-04-20 02:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.48012 | 0.48012 | 0.48012 | 0.48012 | 0.48012 | 0.48012 | 1.5242 | 2.1986 | 2.6405 | 2.873 | 3.3382 | 3.8033 | 0.46488 | 1.2628 | 1.5839 | 1.5839 | 1.5839 | 1.5839 | 0.80021 | 1.0157 | 1.0157 | 1.0157 | 1.0157 | 1.0157
2020-04-20 03:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.36866 | 0.36866 | 0.36866 | 0.36866 | 0.36866 | 0.36866 | 1.4861 | 2.1437 | 2.5745 | 2.8012 | 3.2547 | 3.7082 | 0.46467 | 1.2622 | 1.5831 | 1.5831 | 1.5831 | 1.5831 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-04-20 04:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.27147 | 0.27147 | 0.27147 | 0.27147 | 0.27147 | 0.27147 | 1.5242 | 2.1985 | 2.6404 | 2.8729 | 3.338 | 3.8031 | 0.48012 | 1.3042 | 1.6358 | 1.6358 | 1.6358 | 1.6358 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-04-20 05:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 1.5814 | 2.2811 | 2.7395 | 2.9808 | 3.4633 | 3.9459 | 0.50299 | 1.3663 | 1.7137 | 1.7137 | 1.7137 | 1.7137 | 1.2952 | 1.644 | 1.644 | 1.644 | 1.644 | 1.644
2020-04-20 06:00 | Winter | 0.64756 | 0.99571 | 1.5067 | 1.5067 | 1.5067 | 1.5067 | 0.63445 | 0.63445 | 0.63445 | 0.63445 | 0.63445 | 0.63445 | 1.7849 | 2.5746 | 3.092 | 3.3644 | 3.909 | 4.4537 | 0.56014 | 1.5216 | 1.9084 | 1.9084 | 1.9084 | 1.9084 | 1.4778 | 1.8757 | 1.8757 | 1.8757 | 1.8757 | 1.8757
2020-04-20 07:00 | Winter | 0.91123 | 1.4011 | 2.1202 | 2.1202 | 2.1202 | 2.1202 | 0.7259 | 0.7259 | 0.7259 | 0.7259 | 0.7259 | 0.7259 | 1.9624 | 2.8307 | 3.3996 | 3.699 | 4.2979 | 4.8967 | 0.64779 | 1.7596 | 2.207 | 2.207 | 2.207 | 2.207 | 1.9434 | 2.4667 | 2.4667 | 2.4667 | 2.4667 | 2.4667
2020-04-20 08:00 | Winter | 1.0288 | 1.582 | 2.3938 | 2.3938 | 2.3938 | 2.3938 | 1.0517 | 1.0517 | 1.0517 | 1.0517 | 1.0517 | 1.0517 | 2.1339 | 3.0781 | 3.6967 | 4.0223 | 4.6734 | 5.3246 | 0.65541 | 1.7803 | 2.233 | 2.233 | 2.233 | 2.233 | 2.0958 | 2.6601 | 2.6601 | 2.6601 | 2.6601 | 2.6601
2020-04-20 09:00 | Winter | 1.0669 | 1.6405 | 2.4825 | 2.4825 | 2.4825 | 2.4825 | 0.94596 | 0.94596 | 0.94596 | 0.94596 | 0.94596 | 0.94596 | 2.0958 | 3.0231 | 3.6307 | 3.9504 | 4.59 | 5.2295 | 0.67827 | 1.8425 | 2.3109 | 2.3109 | 2.3109 | 2.3109 | 2.0386 | 2.5876 | 2.5876 | 2.5876 | 2.5876 | 2.5876
2020-04-20 10:00 | Winter | 1.0669 | 1.6405 | 2.4825 | 2.4825 | 2.4825 | 2.4825 | 1.0603 | 1.0603 | 1.0603 | 1.0603 | 1.0603 | 1.0603 | 2.1339 | 3.0781 | 3.6967 | 4.0223 | 4.6734 | 5.3246 | 0.76472 | 2.0773 | 2.6054 | 2.6054 | 2.6054 | 2.6054 | 2.0577 | 2.6118 | 2.6118 | 2.6118 | 2.6118 | 2.6118
2020-04-20 11:00 | Winter | 1.105 | 1.6991 | 2.5711 | 2.5711 | 2.5711 | 2.5711 | 0.75162 | 0.75162 | 0.75162 | 0.75162 | 0.75162 | 0.75162 | 2.2101 | 3.188 | 3.8287 | 4.1659 | 4.8403 | 5.5147 | 0.80783 | 2.1944 | 2.7523 | 2.7523 | 2.7523 | 2.7523 | 2.0005 | 2.5392 | 2.5392 | 2.5392 | 2.5392 | 2.5392
2020-04-20 12:00 | Winter | 1.2003 | 1.8456 | 2.7928 | 2.7928 | 2.7928 | 2.7928 | 0.75734 | 0.75734 | 0.75734 | 0.75734 | 0.75734 | 0.75734 | 2.172 | 3.133 | 3.7627 | 4.0941 | 4.7569 | 5.4197 | 0.64397 | 1.7493 | 2.194 | 2.194 | 2.194 | 2.194 | 2.0196 | 2.5634 | 2.5634 | 2.5634 | 2.5634 | 2.5634
2020-04-20 13:00 | Winter | 1.2194 | 1.8749 | 2.8371 | 2.8371 | 2.8371 | 2.8371 | 0.88022 | 0.88022 | 0.88022 | 0.88022 | 0.88022 | 0.88022 | 2.1148 | 3.0506 | 3.6637 | 3.9863 | 4.6317 | 5.277 | 0.66303 | 1.8011 | 2.2589 | 2.2589 | 2.2589 | 2.2589 | 2.0577 | 2.6118 | 2.6118 | 2.6118 | 2.6118 | 2.6118
2020-04-20 14:00 | Winter | 1.1622 | 1.787 | 2.7041 | 2.7041 | 2.7041 | 2.7041 | 0.86022 | 0.86022 | 0.86022 | 0.86022 | 0.86022 | 0.86022 | 2.0953 | 3.0225 | 3.6299 | 3.9496 | 4.589 | 5.2284 | 0.6516 | 1.77 | 2.22 | 2.22 | 2.22 | 2.22 | 2.0005 | 2.5392 | 2.5392 | 2.5392 | 2.5392 | 2.5392
2020-04-20 15:00 | Winter | 1.1432 | 1.7577 | 2.6598 | 2.6598 | 2.6598 | 2.6598 | 0.79735 | 0.79735 | 0.79735 | 0.79735 | 0.79735 | 0.79735 | 2.1148 | 3.0506 | 3.6637 | 3.9863 | 4.6317 | 5.277 | 0.70494 | 1.9149 | 2.4018 | 2.4018 | 2.4018 | 2.4018 | 1.8672 | 2.3699 | 2.3699 | 2.3699 | 2.3699 | 2.3699
2020-04-20 16:00 | Winter | 1.2003 | 1.8456 | 2.7928 | 2.7928 | 2.7928 | 2.7928 | 0.82021 | 0.82021 | 0.82021 | 0.82021 | 0.82021 | 0.82021 | 2.0958 | 3.0231 | 3.6307 | 3.9504 | 4.59 | 5.2295 | 0.65922 | 1.7907 | 2.246 | 2.246 | 2.246 | 2.246 | 1.8627 | 2.3643 | 2.3643 | 2.3643 | 2.3643 | 2.3643
2020-04-20 17:00 | Winter | 1.086 | 1.6698 | 2.5268 | 2.5268 | 2.5268 | 2.5268 | 0.68589 | 0.68589 | 0.68589 | 0.68589 | 0.68589 | 0.68589 | 2.2291 | 3.2155 | 3.8617 | 4.2018 | 4.8821 | 5.5623 | 0.62873 | 1.7079 | 2.1421 | 2.1421 | 2.1421 | 2.1421 | 1.9053 | 2.4183 | 2.4183 | 2.4183 | 2.4183 | 2.4183
2020-04-20 18:00 | Winter | 0.85737 | 1.3183 | 1.9948 | 1.9948 | 1.9948 | 1.9948 | 0.58043 | 0.58043 | 0.58043 | 0.58043 | 0.58043 | 0.58043 | 2.2291 | 3.2155 | 3.8617 | 4.2018 | 4.8821 | 5.5623 | 0.59063 | 1.6044 | 2.0123 | 2.0123 | 2.0123 | 2.0123 | 1.3772 | 1.748 | 1.748 | 1.748 | 1.748 | 1.748
2020-04-20 19:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.47523 | 0.47523 | 0.47523 | 0.47523 | 0.47523 | 0.47523 | 2.1339 | 3.0781 | 3.6967 | 4.0223 | 4.6734 | 5.3246 | 0.5792 | 1.5733 | 1.9733 | 1.9733 | 1.9733 | 1.9733 | 1.0669 | 1.3542 | 1.3542 | 1.3542 | 1.3542 | 1.3542
2020-04-20 20:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.27721 | 0.27721 | 0.27721 | 0.27721 | 0.27721 | 0.27721 | 1.8845 | 2.7184 | 3.2647 | 3.5522 | 4.1273 | 4.7024 | 0.59063 | 1.6044 | 2.0123 | 2.0123 | 2.0123 | 2.0123 | 0.97168 | 1.2333 | 1.2333 | 1.2333 | 1.2333 | 1.2333
2020-04-20 21:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.27146 | 0.27146 | 0.27146 | 0.27146 | 0.27146 | 0.27146 | 1.8672 | 2.6933 | 3.2346 | 3.5195 | 4.0892 | 4.659 | 0.55633 | 1.5112 | 1.8954 | 1.8954 | 1.8954 | 1.8954 | 0.89533 | 1.1364 | 1.1364 | 1.1364 | 1.1364 | 1.1364
2020-04-20 22:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 1.7723 | 2.5564 | 3.0702 | 3.3406 | 3.8814 | 4.4223 | 0.55633 | 1.5112 | 1.8954 | 1.8954 | 1.8954 | 1.8954 | 0.80023 | 1.0157 | 1.0157 | 1.0157 | 1.0157 | 1.0157
2020-04-20 23:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 1.6766 | 2.4185 | 2.9045 | 3.1603 | 3.672 | 4.1836 | 0.48774 | 1.3249 | 1.6618 | 1.6618 | 1.6618 | 1.6618 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-04-21 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.3692 | 0.3692 | 0.3692 | 0.3692 | 0.3692 | 0.3692 | 1.5814 | 2.2811 | 2.7395 | 2.9808 | 3.4633 | 3.9459 | 0.4725 | 1.2835 | 1.6098 | 1.6098 | 1.6098 | 1.6098 | 0.78115 | 0.9915 | 0.9915 | 0.9915 | 0.9915 | 0.9915
2020-04-21 01:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.38009 | 0.38009 | 0.38009 | 0.38009 | 0.38009 | 0.38009 | 1.5433 | 2.2261 | 2.6735 | 2.909 | 3.3799 | 3.8508 | 0.46107 | 1.2525 | 1.5709 | 1.5709 | 1.5709 | 1.5709 | 0.78115 | 0.9915 | 0.9915 | 0.9915 | 0.9915 | 0.9915
2020-04-21 02:00 | Winter | 0.55653 | 0.85572 | 1.2949 | 1.2949 | 1.2949 | 1.2949 | 0.40582 | 0.40582 | 0.40582 | 0.40582 | 0.40582 | 0.40582 | 1.5242 | 2.1986 | 2.6405 | 2.873 | 3.3382 | 3.8033 | 0.45345 | 1.2318 | 1.5449 | 1.5449 | 1.5449 | 1.5449 | 0.80021 | 1.0157 | 1.0157 | 1.0157 | 1.0157 | 1.0157
2020-04-21 03:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.4001 | 0.4001 | 0.4001 | 0.4001 | 0.4001 | 0.4001 | 1.5242 | 2.1986 | 2.6405 | 2.873 | 3.3382 | 3.8033 | 0.46107 | 1.2525 | 1.5709 | 1.5709 | 1.5709 | 1.5709 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-04-21 04:00 | Winter | 0.58823 | 0.90447 | 1.3686 | 1.3686 | 1.3686 | 1.3686 | 0.29143 | 0.29143 | 0.29143 | 0.29143 | 0.29143 | 0.29143 | 1.5623 | 2.2536 | 2.7065 | 2.9449 | 3.4216 | 3.8984 | 0.48774 | 1.3249 | 1.6618 | 1.6618 | 1.6618 | 1.6618 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-04-21 05:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 1.548 | 2.233 | 2.6817 | 2.9179 | 3.3903 | 3.8627 | 0.49536 | 1.3456 | 1.6877 | 1.6877 | 1.6877 | 1.6877 | 1.1761 | 1.4927 | 1.4927 | 1.4927 | 1.4927 | 1.4927
2020-04-21 06:00 | Winter | 0.64779 | 0.99605 | 1.5072 | 1.5072 | 1.5072 | 1.5072 | 0.64302 | 0.64302 | 0.64302 | 0.64302 | 0.64302 | 0.64302 | 1.7528 | 2.5284 | 3.0366 | 3.304 | 3.8389 | 4.3738 | 0.53728 | 1.4595 | 1.8305 | 1.8305 | 1.8305 | 1.8305 | 1.5797 | 2.005 | 2.005 | 2.005 | 2.005 | 2.005
2020-04-21 07:00 | Winter | 0.94968 | 1.4602 | 2.2096 | 2.2096 | 2.2096 | 2.2096 | 0.72304 | 0.72304 | 0.72304 | 0.72304 | 0.72304 | 0.72304 | 2.0503 | 2.9576 | 3.5519 | 3.8648 | 4.4904 | 5.1161 | 0.67827 | 1.8425 | 2.3109 | 2.3109 | 2.3109 | 2.3109 | 1.8862 | 2.3941 | 2.3941 | 2.3941 | 2.3941 | 2.3941
2020-04-21 08:00 | Winter | 1.086 | 1.6698 | 2.5268 | 2.5268 | 2.5268 | 2.5268 | 0.96882 | 0.96882 | 0.96882 | 0.96882 | 0.96882 | 0.96882 | 2.1339 | 3.0781 | 3.6967 | 4.0223 | 4.6734 | 5.3246 | 0.72018 | 1.9563 | 2.4537 | 2.4537 | 2.4537 | 2.4537 | 2.0624 | 2.6178 | 2.6178 | 2.6178 | 2.6178 | 2.6178
2020-04-21 09:00 | Winter | 1.105 | 1.6991 | 2.5711 | 2.5711 | 2.5711 | 2.5711 | 1.0546 | 1.0546 | 1.0546 | 1.0546 | 1.0546 | 1.0546 | 2.1339 | 3.0781 | 3.6967 | 4.0223 | 4.6734 | 5.3246 | 0.70494 | 1.9149 | 2.4018 | 2.4018 | 2.4018 | 2.4018 | 2.1339 | 2.7085 | 2.7085 | 2.7085 | 2.7085 | 2.7085
2020-04-21 10:00 | Winter | 1.1432 | 1.7577 | 2.6598 | 2.6598 | 2.6598 | 2.6598 | 0.77162 | 0.77162 | 0.77162 | 0.77162 | 0.77162 | 0.77162 | 2.2482 | 3.243 | 3.8947 | 4.2377 | 4.9238 | 5.6098 | 0.84212 | 2.2875 | 2.8691 | 2.8691 | 2.8691 | 2.8691 | 2.0196 | 2.5634 | 2.5634 | 2.5634 | 2.5634 | 2.5634
2020-04-21 11:00 | Winter | 1.1432 | 1.7577 | 2.6598 | 2.6598 | 2.6598 | 2.6598 | 0.77162 | 0.77162 | 0.77162 | 0.77162 | 0.77162 | 0.77162 | 2.2101 | 3.188 | 3.8287 | 4.1659 | 4.8403 | 5.5147 | 0.75448 | 2.0495 | 2.5705 | 2.5705 | 2.5705 | 2.5705 | 2.0767 | 2.6359 | 2.6359 | 2.6359 | 2.6359 | 2.6359
2020-04-21 12:00 | Winter | 1.3527 | 2.08 | 3.1474 | 3.1474 | 3.1474 | 3.1474 | 0.80592 | 0.80592 | 0.80592 | 0.80592 | 0.80592 | 0.80592 | 2.3435 | 3.3804 | 4.0597 | 4.4173 | 5.1324 | 5.8475 | 0.7621 | 2.0702 | 2.5965 | 2.5965 | 2.5965 | 2.5965 | 2.0694 | 2.6266 | 2.6266 | 2.6266 | 2.6266 | 2.6266
2020-04-21 13:00 | Winter | 1.2194 | 1.8749 | 2.8371 | 2.8371 | 2.8371 | 2.8371 | 0.81164 | 0.81164 | 0.81164 | 0.81164 | 0.81164 | 0.81164 | 2.2482 | 3.243 | 3.8947 | 4.2377 | 4.9238 | 5.6098 | 0.70875 | 1.9253 | 2.4147 | 2.4147 | 2.4147 | 2.4147 | 2.0958 | 2.6601 | 2.6601 | 2.6601 | 2.6601 | 2.6601
2020-04-21 14:00 | Winter | 1.2384 | 1.9042 | 2.8814 | 2.8814 | 2.8814 | 2.8814 | 0.82878 | 0.82878 | 0.82878 | 0.82878 | 0.82878 | 0.82878 | 2.191 | 3.1605 | 3.7957 | 4.13 | 4.7986 | 5.4672 | 0.724 | 1.9667 | 2.4667 | 2.4667 | 2.4667 | 2.4667 | 1.9815 | 2.515 | 2.515 | 2.515 | 2.515 | 2.515
2020-04-21 15:00 | Winter | 1.2194 | 1.8749 | 2.8371 | 2.8371 | 2.8371 | 2.8371 | 0.79449 | 0.79449 | 0.79449 | 0.79449 | 0.79449 | 0.79449 | 2.1529 | 3.1056 | 3.7297 | 4.0582 | 4.7151 | 5.3721 | 0.70113 | 1.9046 | 2.3888 | 2.3888 | 2.3888 | 2.3888 | 1.9624 | 2.4908 | 2.4908 | 2.4908 | 2.4908 | 2.4908
2020-04-21 16:00 | Winter | 1.1622 | 1.787 | 2.7041 | 2.7041 | 2.7041 | 2.7041 | 0.8002 | 0.8002 | 0.8002 | 0.8002 | 0.8002 | 0.8002 | 2.1339 | 3.0781 | 3.6967 | 4.0223 | 4.6734 | 5.3246 | 0.71256 | 1.9356 | 2.4277 | 2.4277 | 2.4277 | 2.4277 | 1.8672 | 2.3699 | 2.3699 | 2.3699 | 2.3699 | 2.3699
2020-04-21 17:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 0.64874 | 0.64874 | 0.64874 | 0.64874 | 0.64874 | 0.64874 | 2.2101 | 3.188 | 3.8287 | 4.1659 | 4.8403 | 5.5147 | 0.6897 | 1.8735 | 2.3498 | 2.3498 | 2.3498 | 2.3498 | 1.7528 | 2.2248 | 2.2248 | 2.2248 | 2.2248 | 2.2248
2020-04-21 18:00 | Winter | 0.78457 | 1.2064 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 0.62016 | 0.62016 | 0.62016 | 0.62016 | 0.62016 | 0.62016 | 2.2101 | 3.188 | 3.8287 | 4.1659 | 4.8403 | 5.5147 | 0.63254 | 1.7182 | 2.1551 | 2.1551 | 2.1551 | 2.1551 | 1.3508 | 1.7146 | 1.7146 | 1.7146 | 1.7146 | 1.7146
2020-04-21 19:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.41439 | 0.41439 | 0.41439 | 0.41439 | 0.41439 | 0.41439 | 2.0105 | 2.9001 | 3.4829 | 3.7897 | 4.4032 | 5.0167 | 0.62873 | 1.7079 | 2.1421 | 2.1421 | 2.1421 | 2.1421 | 1.022 | 1.2972 | 1.2972 | 1.2972 | 1.2972 | 1.2972
2020-04-21 20:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.40451 | 0.40451 | 0.40451 | 0.40451 | 0.40451 | 0.40451 | 1.8862 | 2.7208 | 3.2676 | 3.5554 | 4.131 | 4.7066 | 0.59444 | 1.6147 | 2.0253 | 2.0253 | 2.0253 | 2.0253 | 0.99073 | 1.2575 | 1.2575 | 1.2575 | 1.2575 | 1.2575
2020-04-21 21:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.51156 | 0.51156 | 0.51156 | 0.51156 | 0.51156 | 0.51156 | 1.829 | 2.6383 | 3.1686 | 3.4477 | 4.0058 | 4.5639 | 0.65922 | 1.7907 | 2.246 | 2.246 | 2.246 | 2.246 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-04-21 22:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.38009 | 0.38009 | 0.38009 | 0.38009 | 0.38009 | 0.38009 | 1.7338 | 2.5009 | 3.0036 | 3.2681 | 3.7972 | 4.3262 | 0.57157 | 1.5526 | 1.9474 | 1.9474 | 1.9474 | 1.9474 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-04-21 23:00 | Winter | 0.55262 | 0.84971 | 1.2858 | 1.2858 | 1.2858 | 1.2858 | 0.28007 | 0.28007 | 0.28007 | 0.28007 | 0.28007 | 0.28007 | 1.6649 | 2.4015 | 2.8842 | 3.1382 | 3.6463 | 4.1543 | 0.55633 | 1.5112 | 1.8954 | 1.8954 | 1.8954 | 1.8954 | 0.80021 | 1.0157 | 1.0157 | 1.0157 | 1.0157 | 1.0157
2020-04-22 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.2715 | 0.2715 | 0.2715 | 0.2715 | 0.2715 | 0.2715 | 1.5433 | 2.2261 | 2.6735 | 2.909 | 3.3799 | 3.8508 | 0.53347 | 1.4491 | 1.8175 | 1.8175 | 1.8175 | 1.8175 | 0.80021 | 1.0157 | 1.0157 | 1.0157 | 1.0157 | 1.0157
2020-04-22 01:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.39957 | 0.39957 | 0.39957 | 0.39957 | 0.39957 | 0.39957 | 1.5139 | 2.1838 | 2.6227 | 2.8537 | 3.3156 | 3.7776 | 0.5068 | 1.3767 | 1.7267 | 1.7267 | 1.7267 | 1.7267 | 0.78115 | 0.9915 | 0.9915 | 0.9915 | 0.9915 | 0.9915
2020-04-22 02:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.4001 | 0.4001 | 0.4001 | 0.4001 | 0.4001 | 0.4001 | 1.4668 | 2.1159 | 2.5411 | 2.7649 | 3.2125 | 3.6601 | 0.5068 | 1.3767 | 1.7267 | 1.7267 | 1.7267 | 1.7267 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-04-22 03:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.28568 | 0.28568 | 0.28568 | 0.28568 | 0.28568 | 0.28568 | 1.5052 | 2.1711 | 2.6075 | 2.8371 | 3.2964 | 3.7557 | 0.51061 | 1.387 | 1.7396 | 1.7396 | 1.7396 | 1.7396 | 0.78115 | 0.9915 | 0.9915 | 0.9915 | 0.9915 | 0.9915
2020-04-22 04:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.37414 | 0.37414 | 0.37414 | 0.37414 | 0.37414 | 0.37414 | 1.5066 | 2.1733 | 2.61 | 2.8399 | 3.2996 | 3.7594 | 0.54109 | 1.4698 | 1.8435 | 1.8435 | 1.8435 | 1.8435 | 0.81853 | 1.0389 | 1.0389 | 1.0389 | 1.0389 | 1.0389
2020-04-22 05:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.52585 | 0.52585 | 0.52585 | 0.52585 | 0.52585 | 0.52585 | 1.5623 | 2.2536 | 2.7065 | 2.9449 | 3.4216 | 3.8984 | 0.57539 | 1.563 | 1.9603 | 1.9603 | 1.9603 | 1.9603 | 1.1143 | 1.4144 | 1.4144 | 1.4144 | 1.4144 | 1.4144
2020-04-22 06:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.56586 | 0.56586 | 0.56586 | 0.56586 | 0.56586 | 0.56586 | 1.6195 | 2.336 | 2.8055 | 3.0526 | 3.5468 | 4.041 | 0.60587 | 1.6458 | 2.0642 | 2.0642 | 2.0642 | 2.0642 | 1.6531 | 2.0983 | 2.0983 | 2.0983 | 2.0983 | 2.0983
2020-04-22 07:00 | Winter | 0.9307 | 1.4311 | 2.1655 | 2.1655 | 2.1655 | 2.1655 | 0.77448 | 0.77448 | 0.77448 | 0.77448 | 0.77448 | 0.77448 | 1.9434 | 2.8032 | 3.3666 | 3.6631 | 4.2562 | 4.8492 | 0.724 | 1.9667 | 2.4667 | 2.4667 | 2.4667 | 2.4667 | 1.81 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974
2020-04-22 08:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.81735 | 0.81735 | 0.81735 | 0.81735 | 0.81735 | 0.81735 | 2.0386 | 2.9407 | 3.5316 | 3.8427 | 4.4648 | 5.0869 | 0.87642 | 2.3807 | 2.986 | 2.986 | 2.986 | 2.986 | 2.0196 | 2.5634 | 2.5634 | 2.5634 | 2.5634 | 2.5634
2020-04-22 09:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 0.81449 | 0.81449 | 0.81449 | 0.81449 | 0.81449 | 0.81449 | 2.0767 | 2.9956 | 3.5977 | 3.9145 | 4.5482 | 5.182 | 0.81926 | 2.2254 | 2.7912 | 2.7912 | 2.7912 | 2.7912 | 2.0005 | 2.5392 | 2.5392 | 2.5392 | 2.5392 | 2.5392
2020-04-22 10:00 | Winter | 1.0669 | 1.6405 | 2.4825 | 2.4825 | 2.4825 | 2.4825 | 0.86308 | 0.86308 | 0.86308 | 0.86308 | 0.86308 | 0.86308 | 2.172 | 3.133 | 3.7627 | 4.0941 | 4.7569 | 5.4197 | 0.7621 | 2.0702 | 2.5965 | 2.5965 | 2.5965 | 2.5965 | 1.9815 | 2.515 | 2.515 | 2.515 | 2.515 | 2.515
2020-04-22 11:00 | Winter | 1.1622 | 1.787 | 2.7041 | 2.7041 | 2.7041 | 2.7041 | 0.84021 | 0.84021 | 0.84021 | 0.84021 | 0.84021 | 0.84021 | 2.2291 | 3.2155 | 3.8617 | 4.2018 | 4.8821 | 5.5623 | 0.75829 | 2.0598 | 2.5835 | 2.5835 | 2.5835 | 2.5835 | 2.0165 | 2.5595 | 2.5595 | 2.5595 | 2.5595 | 2.5595
2020-04-22 12:00 | Winter | 1.1432 | 1.7577 | 2.6598 | 2.6598 | 2.6598 | 2.6598 | 0.84593 | 0.84593 | 0.84593 | 0.84593 | 0.84593 | 0.84593 | 2.2863 | 3.2979 | 3.9607 | 4.3096 | 5.0072 | 5.7049 | 0.75829 | 2.0598 | 2.5835 | 2.5835 | 2.5835 | 2.5835 | 2.0196 | 2.5634 | 2.5634 | 2.5634 | 2.5634 | 2.5634
2020-04-22 13:00 | Winter | 1.1241 | 1.7284 | 2.6155 | 2.6155 | 2.6155 | 2.6155 | 0.85165 | 0.85165 | 0.85165 | 0.85165 | 0.85165 | 0.85165 | 2.2482 | 3.243 | 3.8947 | 4.2377 | 4.9238 | 5.6098 | 0.7621 | 2.0702 | 2.5965 | 2.5965 | 2.5965 | 2.5965 | 1.9434 | 2.4667 | 2.4667 | 2.4667 | 2.4667 | 2.4667
2020-04-22 14:00 | Winter | 1.1432 | 1.7577 | 2.6598 | 2.6598 | 2.6598 | 2.6598 | 0.77734 | 0.77734 | 0.77734 | 0.77734 | 0.77734 | 0.77734 | 2.2482 | 3.243 | 3.8947 | 4.2377 | 4.9238 | 5.6098 | 0.79258 | 2.153 | 2.7003 | 2.7003 | 2.7003 | 2.7003 | 1.9243 | 2.4425 | 2.4425 | 2.4425 | 2.4425 | 2.4425
2020-04-22 15:00 | Winter | 1.1432 | 1.7577 | 2.6598 | 2.6598 | 2.6598 | 2.6598 | 0.82725 | 0.82725 | 0.82725 | 0.82725 | 0.82725 | 0.82725 | 2.172 | 3.133 | 3.7627 | 4.0941 | 4.7569 | 5.4197 | 0.72018 | 1.9563 | 2.4537 | 2.4537 | 2.4537 | 2.4537 | 1.9243 | 2.4425 | 2.4425 | 2.4425 | 2.4425 | 2.4425
2020-04-22 16:00 | Winter | 1.086 | 1.6698 | 2.5268 | 2.5268 | 2.5268 | 2.5268 | 0.93167 | 0.93167 | 0.93167 | 0.93167 | 0.93167 | 0.93167 | 2.1529 | 3.1056 | 3.7297 | 4.0582 | 4.7151 | 5.3721 | 0.724 | 1.9667 | 2.4667 | 2.4667 | 2.4667 | 2.4667 | 1.9243 | 2.4425 | 2.4425 | 2.4425 | 2.4425 | 2.4425
2020-04-22 17:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 0.8002 | 0.8002 | 0.8002 | 0.8002 | 0.8002 | 0.8002 | 2.2482 | 3.243 | 3.8947 | 4.2377 | 4.9238 | 5.6098 | 0.73162 | 1.9874 | 2.4926 | 2.4926 | 2.4926 | 2.4926 | 1.7826 | 2.2626 | 2.2626 | 2.2626 | 2.2626 | 2.2626
2020-04-22 18:00 | Winter | 0.85532 | 1.3152 | 1.9901 | 1.9901 | 1.9901 | 1.9901 | 0.6373 | 0.6373 | 0.6373 | 0.6373 | 0.6373 | 0.6373 | 2.1905 | 3.1598 | 3.7948 | 4.1291 | 4.7975 | 5.466 | 0.64779 | 1.7596 | 2.207 | 2.207 | 2.207 | 2.207 | 1.4127 | 1.7931 | 1.7931 | 1.7931 | 1.7931 | 1.7931
2020-04-22 19:00 | Winter | 0.68303 | 1.0502 | 1.5892 | 1.5892 | 1.5892 | 1.5892 | 0.55157 | 0.55157 | 0.55157 | 0.55157 | 0.55157 | 0.55157 | 2.033 | 2.9325 | 3.5219 | 3.8321 | 4.4524 | 5.0728 | 0.6897 | 1.8735 | 2.3498 | 2.3498 | 2.3498 | 2.3498 | 1.0481 | 1.3303 | 1.3303 | 1.3303 | 1.3303 | 1.3303
2020-04-22 20:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.2915 | 0.2915 | 0.2915 | 0.2915 | 0.2915 | 0.2915 | 1.9243 | 2.7758 | 3.3336 | 3.6272 | 4.2144 | 4.8016 | 0.62873 | 1.7079 | 2.1421 | 2.1421 | 2.1421 | 2.1421 | 0.95277 | 1.2093 | 1.2093 | 1.2093 | 1.2093 | 1.2093
2020-04-22 21:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.2915 | 0.2915 | 0.2915 | 0.2915 | 0.2915 | 0.2915 | 1.9243 | 2.7758 | 3.3336 | 3.6272 | 4.2144 | 4.8016 | 0.6173 | 1.6768 | 2.1032 | 2.1032 | 2.1032 | 2.1032 | 0.91452 | 1.1608 | 1.1608 | 1.1608 | 1.1608 | 1.1608
2020-04-22 22:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.26296 | 0.26296 | 0.26296 | 0.26296 | 0.26296 | 0.26296 | 1.7909 | 2.5834 | 3.1026 | 3.3758 | 3.9223 | 4.4688 | 0.5792 | 1.5733 | 1.9733 | 1.9733 | 1.9733 | 1.9733 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-04-22 23:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.48869 | 0.48869 | 0.48869 | 0.48869 | 0.48869 | 0.48869 | 1.6766 | 2.4185 | 2.9045 | 3.1603 | 3.672 | 4.1836 | 0.55252 | 1.5009 | 1.8825 | 1.8825 | 1.8825 | 1.8825 | 0.80021 | 1.0157 | 1.0157 | 1.0157 | 1.0157 | 1.0157
2020-04-23 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 1.6004 | 2.3086 | 2.7725 | 3.0167 | 3.5051 | 3.9934 | 0.50299 | 1.3663 | 1.7137 | 1.7137 | 1.7137 | 1.7137 | 0.80021 | 1.0157 | 1.0157 | 1.0157 | 1.0157 | 1.0157
2020-04-23 01:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.37724 | 0.37724 | 0.37724 | 0.37724 | 0.37724 | 0.37724 | 1.5814 | 2.2811 | 2.7395 | 2.9808 | 3.4633 | 3.9459 | 0.51442 | 1.3974 | 1.7526 | 1.7526 | 1.7526 | 1.7526 | 0.78115 | 0.9915 | 0.9915 | 0.9915 | 0.9915 | 0.9915
2020-04-23 02:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.28287 | 0.28287 | 0.28287 | 0.28287 | 0.28287 | 0.28287 | 1.5814 | 2.2811 | 2.7395 | 2.9808 | 3.4633 | 3.9459 | 0.49536 | 1.3456 | 1.6877 | 1.6877 | 1.6877 | 1.6877 | 0.80021 | 1.0157 | 1.0157 | 1.0157 | 1.0157 | 1.0157
2020-04-23 03:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.4001 | 0.4001 | 0.4001 | 0.4001 | 0.4001 | 0.4001 | 1.5814 | 2.2811 | 2.7395 | 2.9808 | 3.4633 | 3.9459 | 0.52204 | 1.4181 | 1.7786 | 1.7786 | 1.7786 | 1.7786 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-04-23 04:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.41153 | 0.41153 | 0.41153 | 0.41153 | 0.41153 | 0.41153 | 1.5052 | 2.1711 | 2.6075 | 2.8371 | 3.2964 | 3.7557 | 0.53347 | 1.4491 | 1.8175 | 1.8175 | 1.8175 | 1.8175 | 0.83715 | 1.0626 | 1.0626 | 1.0626 | 1.0626 | 1.0626
2020-04-23 05:00 | Winter | 0.60914 | 0.93663 | 1.4173 | 1.4173 | 1.4173 | 1.4173 | 0.48869 | 0.48869 | 0.48869 | 0.48869 | 0.48869 | 0.48869 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.56395 | 1.5319 | 1.9214 | 1.9214 | 1.9214 | 1.9214 | 1.2164 | 1.5439 | 1.5439 | 1.5439 | 1.5439 | 1.5439
2020-04-23 06:00 | Winter | 0.66414 | 1.0212 | 1.5453 | 1.5453 | 1.5453 | 1.5453 | 0.72876 | 0.72876 | 0.72876 | 0.72876 | 0.72876 | 0.72876 | 1.7827 | 2.5716 | 3.0884 | 3.3604 | 3.9044 | 4.4484 | 0.59825 | 1.6251 | 2.0382 | 2.0382 | 2.0382 | 2.0382 | 1.6661 | 2.1147 | 2.1147 | 2.1147 | 2.1147 | 2.1147
2020-04-23 07:00 | Winter | 0.89527 | 1.3766 | 2.083 | 2.083 | 2.083 | 2.083 | 0.93452 | 0.93452 | 0.93452 | 0.93452 | 0.93452 | 0.93452 | 2.0767 | 2.9956 | 3.5977 | 3.9145 | 4.5482 | 5.182 | 0.78115 | 2.1219 | 2.6614 | 2.6614 | 2.6614 | 2.6614 | 1.829 | 2.3216 | 2.3216 | 2.3216 | 2.3216 | 2.3216
2020-04-23 08:00 | Winter | 1.1622 | 1.787 | 2.7041 | 2.7041 | 2.7041 | 2.7041 | 1.0546 | 1.0546 | 1.0546 | 1.0546 | 1.0546 | 1.0546 | 2.1339 | 3.0781 | 3.6967 | 4.0223 | 4.6734 | 5.3246 | 0.81926 | 2.2254 | 2.7912 | 2.7912 | 2.7912 | 2.7912 | 1.9815 | 2.515 | 2.515 | 2.515 | 2.515 | 2.515
2020-04-23 09:00 | Winter | 1.086 | 1.6698 | 2.5268 | 2.5268 | 2.5268 | 2.5268 | 0.91166 | 0.91166 | 0.91166 | 0.91166 | 0.91166 | 0.91166 | 2.1529 | 3.1056 | 3.7297 | 4.0582 | 4.7151 | 5.3721 | 0.83069 | 2.2565 | 2.8302 | 2.8302 | 2.8302 | 2.8302 | 2.0767 | 2.6359 | 2.6359 | 2.6359 | 2.6359 | 2.6359
2020-04-23 10:00 | Winter | 1.086 | 1.6698 | 2.5268 | 2.5268 | 2.5268 | 2.5268 | 0.91452 | 0.91452 | 0.91452 | 0.91452 | 0.91452 | 0.91452 | 2.172 | 3.133 | 3.7627 | 4.0941 | 4.7569 | 5.4197 | 0.78115 | 2.1219 | 2.6614 | 2.6614 | 2.6614 | 2.6614 | 2.0005 | 2.5392 | 2.5392 | 2.5392 | 2.5392 | 2.5392
2020-04-23 11:00 | Winter | 1.1241 | 1.7284 | 2.6155 | 2.6155 | 2.6155 | 2.6155 | 0.77162 | 0.77162 | 0.77162 | 0.77162 | 0.77162 | 0.77162 | 2.1529 | 3.1056 | 3.7297 | 4.0582 | 4.7151 | 5.3721 | 0.74305 | 2.0184 | 2.5316 | 2.5316 | 2.5316 | 2.5316 | 2.0577 | 2.6118 | 2.6118 | 2.6118 | 2.6118 | 2.6118
2020-04-23 12:00 | Winter | 1.1432 | 1.7577 | 2.6598 | 2.6598 | 2.6598 | 2.6598 | 0.83164 | 0.83164 | 0.83164 | 0.83164 | 0.83164 | 0.83164 | 2.3054 | 3.3254 | 3.9937 | 4.3455 | 5.049 | 5.7525 | 0.69351 | 1.8839 | 2.3628 | 2.3628 | 2.3628 | 2.3628 | 1.9438 | 2.4672 | 2.4672 | 2.4672 | 2.4672 | 2.4672
2020-04-23 13:00 | Winter | 1.1241 | 1.7284 | 2.6155 | 2.6155 | 2.6155 | 2.6155 | 0.82592 | 0.82592 | 0.82592 | 0.82592 | 0.82592 | 0.82592 | 2.2101 | 3.188 | 3.8287 | 4.1659 | 4.8403 | 5.5147 | 0.66684 | 1.8114 | 2.2719 | 2.2719 | 2.2719 | 2.2719 | 1.9243 | 2.4425 | 2.4425 | 2.4425 | 2.4425 | 2.4425
2020-04-23 14:00 | Winter | 1.1622 | 1.787 | 2.7041 | 2.7041 | 2.7041 | 2.7041 | 0.84021 | 0.84021 | 0.84021 | 0.84021 | 0.84021 | 0.84021 | 2.1529 | 3.1056 | 3.7297 | 4.0582 | 4.7151 | 5.3721 | 0.68208 | 1.8528 | 2.3239 | 2.3239 | 2.3239 | 2.3239 | 1.9053 | 2.4183 | 2.4183 | 2.4183 | 2.4183 | 2.4183
2020-04-23 15:00 | Winter | 1.1432 | 1.7577 | 2.6598 | 2.6598 | 2.6598 | 2.6598 | 0.77734 | 0.77734 | 0.77734 | 0.77734 | 0.77734 | 0.77734 | 2.1148 | 3.0506 | 3.6637 | 3.9863 | 4.6317 | 5.277 | 0.69732 | 1.8942 | 2.3758 | 2.3758 | 2.3758 | 2.3758 | 1.8862 | 2.3941 | 2.3941 | 2.3941 | 2.3941 | 2.3941
2020-04-23 16:00 | Winter | 1.105 | 1.6991 | 2.5711 | 2.5711 | 2.5711 | 2.5711 | 0.77162 | 0.77162 | 0.77162 | 0.77162 | 0.77162 | 0.77162 | 2.1339 | 3.0781 | 3.6967 | 4.0223 | 4.6734 | 5.3246 | 0.66303 | 1.8011 | 2.2589 | 2.2589 | 2.2589 | 2.2589 | 1.829 | 2.3216 | 2.3216 | 2.3216 | 2.3216 | 2.3216
2020-04-23 17:00 | Winter | 1.0669 | 1.6405 | 2.4825 | 2.4825 | 2.4825 | 2.4825 | 0.62873 | 0.62873 | 0.62873 | 0.62873 | 0.62873 | 0.62873 | 2.1529 | 3.1056 | 3.7297 | 4.0582 | 4.7151 | 5.3721 | 0.66684 | 1.8114 | 2.2719 | 2.2719 | 2.2719 | 2.2719 | 1.7513 | 2.2228 | 2.2228 | 2.2228 | 2.2228 | 2.2228
2020-04-23 18:00 | Winter | 0.83601 | 1.2855 | 1.9452 | 1.9452 | 1.9452 | 1.9452 | 0.58015 | 0.58015 | 0.58015 | 0.58015 | 0.58015 | 0.58015 | 2.1339 | 3.0781 | 3.6967 | 4.0223 | 4.6734 | 5.3246 | 0.64779 | 1.7596 | 2.207 | 2.207 | 2.207 | 2.207 | 1.3481 | 1.7111 | 1.7111 | 1.7111 | 1.7111 | 1.7111
2020-04-23 19:00 | Winter | 0.68589 | 1.0546 | 1.5959 | 1.5959 | 1.5959 | 1.5959 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 2.0127 | 2.9033 | 3.4868 | 3.7939 | 4.4081 | 5.0223 | 0.65541 | 1.7803 | 2.233 | 2.233 | 2.233 | 2.233 | 1.0046 | 1.2751 | 1.2751 | 1.2751 | 1.2751 | 1.2751
2020-04-23 20:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.47726 | 0.47726 | 0.47726 | 0.47726 | 0.47726 | 0.47726 | 1.8672 | 2.6933 | 3.2346 | 3.5195 | 4.0892 | 4.659 | 0.62492 | 1.6975 | 2.1291 | 2.1291 | 2.1291 | 2.1291 | 0.97168 | 1.2333 | 1.2333 | 1.2333 | 1.2333 | 1.2333
2020-04-23 21:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.37438 | 0.37438 | 0.37438 | 0.37438 | 0.37438 | 0.37438 | 1.829 | 2.6383 | 3.1686 | 3.4477 | 4.0058 | 4.5639 | 0.58682 | 1.594 | 1.9993 | 1.9993 | 1.9993 | 1.9993 | 0.86987 | 1.1041 | 1.1041 | 1.1041 | 1.1041 | 1.1041
2020-04-23 22:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.38581 | 0.38581 | 0.38581 | 0.38581 | 0.38581 | 0.38581 | 1.7147 | 2.4735 | 2.9705 | 3.2322 | 3.7554 | 4.2787 | 0.59063 | 1.6044 | 2.0123 | 2.0123 | 2.0123 | 2.0123 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-04-23 23:00 | Winter | 0.56121 | 0.86293 | 1.3058 | 1.3058 | 1.3058 | 1.3058 | 0.24611 | 0.24611 | 0.24611 | 0.24611 | 0.24611 | 0.24611 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.53852 | 1.4629 | 1.8348 | 1.8348 | 1.8348 | 1.8348 | 0.78115 | 0.9915 | 0.9915 | 0.9915 | 0.9915 | 0.9915
2020-04-24 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.25939 | 0.25939 | 0.25939 | 0.25939 | 0.25939 | 0.25939 | 1.6004 | 2.3086 | 2.7725 | 3.0167 | 3.5051 | 3.9934 | 0.52585 | 1.4284 | 1.7916 | 1.7916 | 1.7916 | 1.7916 | 0.80021 | 1.0157 | 1.0157 | 1.0157 | 1.0157 | 1.0157
2020-04-24 01:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.37589 | 0.37589 | 0.37589 | 0.37589 | 0.37589 | 0.37589 | 1.5248 | 2.1995 | 2.6415 | 2.8741 | 3.3394 | 3.8047 | 0.5068 | 1.3767 | 1.7267 | 1.7267 | 1.7267 | 1.7267 | 0.78115 | 0.9915 | 0.9915 | 0.9915 | 0.9915 | 0.9915
2020-04-24 02:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.39724 | 0.39724 | 0.39724 | 0.39724 | 0.39724 | 0.39724 | 1.5433 | 2.2261 | 2.6735 | 2.909 | 3.3799 | 3.8508 | 0.51823 | 1.4077 | 1.7656 | 1.7656 | 1.7656 | 1.7656 | 0.7621 | 0.96732 | 0.96732 | 0.96732 | 0.96732 | 0.96732
2020-04-24 03:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.2715 | 0.2715 | 0.2715 | 0.2715 | 0.2715 | 0.2715 | 1.6004 | 2.3086 | 2.7725 | 3.0167 | 3.5051 | 3.9934 | 0.49155 | 1.3353 | 1.6747 | 1.6747 | 1.6747 | 1.6747 | 0.78115 | 0.9915 | 0.9915 | 0.9915 | 0.9915 | 0.9915
2020-04-24 04:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.26864 | 0.26864 | 0.26864 | 0.26864 | 0.26864 | 0.26864 | 1.6195 | 2.336 | 2.8055 | 3.0526 | 3.5468 | 4.041 | 0.51442 | 1.3974 | 1.7526 | 1.7526 | 1.7526 | 1.7526 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-04-24 05:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 1.6576 | 2.391 | 2.8715 | 3.1244 | 3.6302 | 4.1361 | 0.55188 | 1.4991 | 1.8803 | 1.8803 | 1.8803 | 1.8803 | 1.1923 | 1.5133 | 1.5133 | 1.5133 | 1.5133 | 1.5133
2020-04-24 06:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.56014 | 0.56014 | 0.56014 | 0.56014 | 0.56014 | 0.56014 | 1.709 | 2.4652 | 2.9606 | 3.2214 | 3.7429 | 4.2644 | 0.57157 | 1.5526 | 1.9474 | 1.9474 | 1.9474 | 1.9474 | 1.517 | 1.9255 | 1.9255 | 1.9255 | 1.9255 | 1.9255
2020-04-24 07:00 | Winter | 0.88515 | 1.361 | 2.0595 | 2.0595 | 2.0595 | 2.0595 | 0.7259 | 0.7259 | 0.7259 | 0.7259 | 0.7259 | 0.7259 | 1.9624 | 2.8307 | 3.3996 | 3.699 | 4.2979 | 4.8967 | 0.73162 | 1.9874 | 2.4926 | 2.4926 | 2.4926 | 2.4926 | 1.81 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974
2020-04-24 08:00 | Winter | 0.97127 | 1.4934 | 2.2599 | 2.2599 | 2.2599 | 2.2599 | 0.78591 | 0.78591 | 0.78591 | 0.78591 | 0.78591 | 0.78591 | 2.0767 | 2.9956 | 3.5977 | 3.9145 | 4.5482 | 5.182 | 0.83831 | 2.2772 | 2.8561 | 2.8561 | 2.8561 | 2.8561 | 1.9434 | 2.4667 | 2.4667 | 2.4667 | 2.4667 | 2.4667
2020-04-24 09:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 0.78306 | 0.78306 | 0.78306 | 0.78306 | 0.78306 | 0.78306 | 2.2291 | 3.2155 | 3.8617 | 4.2018 | 4.8821 | 5.5623 | 0.70494 | 1.9149 | 2.4018 | 2.4018 | 2.4018 | 2.4018 | 1.9434 | 2.4667 | 2.4667 | 2.4667 | 2.4667 | 2.4667
2020-04-24 10:00 | Winter | 1.0526 | 1.6185 | 2.4491 | 2.4491 | 2.4491 | 2.4491 | 0.78591 | 0.78591 | 0.78591 | 0.78591 | 0.78591 | 0.78591 | 2.3435 | 3.3804 | 4.0597 | 4.4173 | 5.1324 | 5.8475 | 0.78115 | 2.1219 | 2.6614 | 2.6614 | 2.6614 | 2.6614 | 2.0196 | 2.5634 | 2.5634 | 2.5634 | 2.5634 | 2.5634
2020-04-24 11:00 | Winter | 1.1432 | 1.7577 | 2.6598 | 2.6598 | 2.6598 | 2.6598 | 0.77448 | 0.77448 | 0.77448 | 0.77448 | 0.77448 | 0.77448 | 2.2863 | 3.2979 | 3.9607 | 4.3096 | 5.0072 | 5.7049 | 0.70494 | 1.9149 | 2.4018 | 2.4018 | 2.4018 | 2.4018 | 2.0386 | 2.5876 | 2.5876 | 2.5876 | 2.5876 | 2.5876
2020-04-24 12:00 | Winter | 1.1813 | 1.8163 | 2.7485 | 2.7485 | 2.7485 | 2.7485 | 0.8888 | 0.8888 | 0.8888 | 0.8888 | 0.8888 | 0.8888 | 2.3625 | 3.4079 | 4.0927 | 4.4532 | 5.1741 | 5.8951 | 0.70875 | 1.9253 | 2.4147 | 2.4147 | 2.4147 | 2.4147 | 2.0196 | 2.5634 | 2.5634 | 2.5634 | 2.5634 | 2.5634
2020-04-24 13:00 | Winter | 1.467 | 2.2558 | 3.4134 | 3.4134 | 3.4134 | 3.4134 | 0.95739 | 0.95739 | 0.95739 | 0.95739 | 0.95739 | 0.95739 | 2.4197 | 3.4903 | 4.1918 | 4.561 | 5.2993 | 6.0377 | 0.69732 | 1.8942 | 2.3758 | 2.3758 | 2.3758 | 2.3758 | 2.0386 | 2.5876 | 2.5876 | 2.5876 | 2.5876 | 2.5876
2020-04-24 14:00 | Winter | 1.3146 | 2.0214 | 3.0588 | 3.0588 | 3.0588 | 3.0588 | 0.91738 | 0.91738 | 0.91738 | 0.91738 | 0.91738 | 0.91738 | 2.2673 | 3.2705 | 3.9277 | 4.2736 | 4.9655 | 5.6574 | 0.73162 | 1.9874 | 2.4926 | 2.4926 | 2.4926 | 2.4926 | 1.9815 | 2.515 | 2.515 | 2.515 | 2.515 | 2.515
2020-04-24 15:00 | Winter | 1.2384 | 1.9042 | 2.8814 | 2.8814 | 2.8814 | 2.8814 | 0.97168 | 0.97168 | 0.97168 | 0.97168 | 0.97168 | 0.97168 | 2.2673 | 3.2705 | 3.9277 | 4.2736 | 4.9655 | 5.6574 | 0.70113 | 1.9046 | 2.3888 | 2.3888 | 2.3888 | 2.3888 | 1.9815 | 2.515 | 2.515 | 2.515 | 2.515 | 2.515
2020-04-24 16:00 | Winter | 1.2384 | 1.9042 | 2.8814 | 2.8814 | 2.8814 | 2.8814 | 0.95453 | 0.95453 | 0.95453 | 0.95453 | 0.95453 | 0.95453 | 2.2291 | 3.2155 | 3.8617 | 4.2018 | 4.8821 | 5.5623 | 0.71256 | 1.9356 | 2.4277 | 2.4277 | 2.4277 | 2.4277 | 1.9243 | 2.4425 | 2.4425 | 2.4425 | 2.4425 | 2.4425
2020-04-24 17:00 | Winter | 1.086 | 1.6698 | 2.5268 | 2.5268 | 2.5268 | 2.5268 | 0.75734 | 0.75734 | 0.75734 | 0.75734 | 0.75734 | 0.75734 | 2.1529 | 3.1056 | 3.7297 | 4.0582 | 4.7151 | 5.3721 | 0.69351 | 1.8839 | 2.3628 | 2.3628 | 2.3628 | 2.3628 | 1.7362 | 2.2037 | 2.2037 | 2.2037 | 2.2037 | 2.2037
2020-04-24 18:00 | Winter | 0.82621 | 1.2704 | 1.9224 | 1.9224 | 1.9224 | 1.9224 | 0.53728 | 0.53728 | 0.53728 | 0.53728 | 0.53728 | 0.53728 | 2.0767 | 2.9956 | 3.5977 | 3.9145 | 4.5482 | 5.182 | 0.62111 | 1.6872 | 2.1161 | 2.1161 | 2.1161 | 2.1161 | 1.3252 | 1.6821 | 1.6821 | 1.6821 | 1.6821 | 1.6821
2020-04-24 19:00 | Winter | 0.64779 | 0.99605 | 1.5072 | 1.5072 | 1.5072 | 1.5072 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 1.9815 | 2.8582 | 3.4326 | 3.735 | 4.3396 | 4.9443 | 0.58682 | 1.594 | 1.9993 | 1.9993 | 1.9993 | 1.9993 | 1.0192 | 1.2936 | 1.2936 | 1.2936 | 1.2936 | 1.2936
2020-04-24 20:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.38867 | 0.38867 | 0.38867 | 0.38867 | 0.38867 | 0.38867 | 1.8862 | 2.7208 | 3.2676 | 3.5554 | 4.131 | 4.7066 | 0.59444 | 1.6147 | 2.0253 | 2.0253 | 2.0253 | 2.0253 | 0.97168 | 1.2333 | 1.2333 | 1.2333 | 1.2333 | 1.2333
2020-04-24 21:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.39438 | 0.39438 | 0.39438 | 0.39438 | 0.39438 | 0.39438 | 1.8481 | 2.6658 | 3.2016 | 3.4836 | 4.0475 | 4.6115 | 0.58301 | 1.5837 | 1.9863 | 1.9863 | 1.9863 | 1.9863 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-04-24 22:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.37438 | 0.37438 | 0.37438 | 0.37438 | 0.37438 | 0.37438 | 1.7719 | 2.5559 | 3.0696 | 3.3399 | 3.8806 | 4.4213 | 0.58682 | 1.594 | 1.9993 | 1.9993 | 1.9993 | 1.9993 | 0.85076 | 1.0799 | 1.0799 | 1.0799 | 1.0799 | 1.0799
2020-04-24 23:00 | Winter | 0.55261 | 0.8497 | 1.2858 | 1.2858 | 1.2858 | 1.2858 | 0.27793 | 0.27793 | 0.27793 | 0.27793 | 0.27793 | 0.27793 | 1.6004 | 2.3086 | 2.7725 | 3.0167 | 3.5051 | 3.9934 | 0.55633 | 1.5112 | 1.8954 | 1.8954 | 1.8954 | 1.8954 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-04-25 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.24577 | 0.24577 | 0.24577 | 0.24577 | 0.24577 | 0.24577 | 1.6195 | 2.336 | 2.8055 | 3.0526 | 3.5468 | 4.041 | 0.5449 | 1.4802 | 1.8565 | 1.8565 | 1.8565 | 1.8565 | 0.80021 | 1.0157 | 1.0157 | 1.0157 | 1.0157 | 1.0157
2020-04-25 01:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.37152 | 0.37152 | 0.37152 | 0.37152 | 0.37152 | 0.37152 | 1.5433 | 2.2261 | 2.6735 | 2.909 | 3.3799 | 3.8508 | 0.53728 | 1.4595 | 1.8305 | 1.8305 | 1.8305 | 1.8305 | 0.80021 | 1.0157 | 1.0157 | 1.0157 | 1.0157 | 1.0157
2020-04-25 02:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.25569 | 0.25569 | 0.25569 | 0.25569 | 0.25569 | 0.25569 | 1.5814 | 2.2811 | 2.7395 | 2.9808 | 3.4633 | 3.9459 | 0.53728 | 1.4595 | 1.8305 | 1.8305 | 1.8305 | 1.8305 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-04-25 03:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.41153 | 0.41153 | 0.41153 | 0.41153 | 0.41153 | 0.41153 | 1.5054 | 2.1715 | 2.6079 | 2.8376 | 3.297 | 3.7564 | 0.5068 | 1.3767 | 1.7267 | 1.7267 | 1.7267 | 1.7267 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-04-25 04:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.26634 | 0.26634 | 0.26634 | 0.26634 | 0.26634 | 0.26634 | 1.5623 | 2.2536 | 2.7065 | 2.9449 | 3.4216 | 3.8984 | 0.53728 | 1.4595 | 1.8305 | 1.8305 | 1.8305 | 1.8305 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-04-25 05:00 | Winter | 0.55355 | 0.85115 | 1.288 | 1.288 | 1.288 | 1.288 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 1.5433 | 2.2261 | 2.6735 | 2.909 | 3.3799 | 3.8508 | 0.50299 | 1.3663 | 1.7137 | 1.7137 | 1.7137 | 1.7137 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-04-25 06:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.40582 | 0.40582 | 0.40582 | 0.40582 | 0.40582 | 0.40582 | 1.5433 | 2.2261 | 2.6735 | 2.909 | 3.3799 | 3.8508 | 0.52966 | 1.4388 | 1.8046 | 1.8046 | 1.8046 | 1.8046 | 0.93358 | 1.185 | 1.185 | 1.185 | 1.185 | 1.185
2020-04-25 07:00 | Winter | 0.55957 | 0.8604 | 1.302 | 1.302 | 1.302 | 1.302 | 0.40582 | 0.40582 | 0.40582 | 0.40582 | 0.40582 | 0.40582 | 1.6576 | 2.391 | 2.8715 | 3.1244 | 3.6302 | 4.1361 | 0.57157 | 1.5526 | 1.9474 | 1.9474 | 1.9474 | 1.9474 | 1.0479 | 1.3301 | 1.3301 | 1.3301 | 1.3301 | 1.3301
2020-04-25 08:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.47726 | 0.47726 | 0.47726 | 0.47726 | 0.47726 | 0.47726 | 1.7147 | 2.4735 | 2.9705 | 3.2322 | 3.7554 | 4.2787 | 0.56395 | 1.5319 | 1.9214 | 1.9214 | 1.9214 | 1.9214 | 1.086 | 1.3784 | 1.3784 | 1.3784 | 1.3784 | 1.3784
2020-04-25 09:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.4001 | 0.4001 | 0.4001 | 0.4001 | 0.4001 | 0.4001 | 1.7542 | 2.5303 | 3.0388 | 3.3065 | 3.8418 | 4.3771 | 0.54871 | 1.4905 | 1.8695 | 1.8695 | 1.8695 | 1.8695 | 1.086 | 1.3784 | 1.3784 | 1.3784 | 1.3784 | 1.3784
2020-04-25 10:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.32865 | 0.32865 | 0.32865 | 0.32865 | 0.32865 | 0.32865 | 1.8672 | 2.6933 | 3.2346 | 3.5195 | 4.0892 | 4.659 | 0.5792 | 1.5733 | 1.9733 | 1.9733 | 1.9733 | 1.9733 | 1.0288 | 1.3059 | 1.3059 | 1.3059 | 1.3059 | 1.3059
2020-04-25 11:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.30579 | 0.30579 | 0.30579 | 0.30579 | 0.30579 | 0.30579 | 1.8862 | 2.7208 | 3.2676 | 3.5554 | 4.131 | 4.7066 | 0.49155 | 1.3353 | 1.6747 | 1.6747 | 1.6747 | 1.6747 | 1.0098 | 1.2817 | 1.2817 | 1.2817 | 1.2817 | 1.2817
2020-04-25 12:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.38581 | 0.38581 | 0.38581 | 0.38581 | 0.38581 | 0.38581 | 1.9053 | 2.7483 | 3.3006 | 3.5913 | 4.1727 | 4.7541 | 0.5068 | 1.3767 | 1.7267 | 1.7267 | 1.7267 | 1.7267 | 1.086 | 1.3784 | 1.3784 | 1.3784 | 1.3784 | 1.3784
2020-04-25 13:00 | Winter | 0.53347 | 0.82027 | 1.2412 | 1.2412 | 1.2412 | 1.2412 | 0.26578 | 0.26578 | 0.26578 | 0.26578 | 0.26578 | 0.26578 | 1.8672 | 2.6933 | 3.2346 | 3.5195 | 4.0892 | 4.659 | 0.50299 | 1.3663 | 1.7137 | 1.7137 | 1.7137 | 1.7137 | 1.0288 | 1.3059 | 1.3059 | 1.3059 | 1.3059 | 1.3059
2020-04-25 14:00 | Winter | 0.58004 | 0.89188 | 1.3496 | 1.3496 | 1.3496 | 1.3496 | 0.36009 | 0.36009 | 0.36009 | 0.36009 | 0.36009 | 0.36009 | 1.8672 | 2.6933 | 3.2346 | 3.5195 | 4.0892 | 4.659 | 0.5068 | 1.3767 | 1.7267 | 1.7267 | 1.7267 | 1.7267 | 1.0098 | 1.2817 | 1.2817 | 1.2817 | 1.2817 | 1.2817
2020-04-25 15:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.38295 | 0.38295 | 0.38295 | 0.38295 | 0.38295 | 0.38295 | 1.8481 | 2.6658 | 3.2016 | 3.4836 | 4.0475 | 4.6115 | 0.48012 | 1.3042 | 1.6358 | 1.6358 | 1.6358 | 1.6358 | 0.97168 | 1.2333 | 1.2333 | 1.2333 | 1.2333 | 1.2333
2020-04-25 16:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 1.8395 | 2.6535 | 3.1868 | 3.4674 | 4.0288 | 4.5901 | 0.53728 | 1.4595 | 1.8305 | 1.8305 | 1.8305 | 1.8305 | 0.97168 | 1.2333 | 1.2333 | 1.2333 | 1.2333 | 1.2333
2020-04-25 17:00 | Winter | 0.55319 | 0.85059 | 1.2871 | 1.2871 | 1.2871 | 1.2871 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 2.0196 | 2.9132 | 3.4986 | 3.8068 | 4.4231 | 5.0393 | 0.61349 | 1.6665 | 2.0902 | 2.0902 | 2.0902 | 2.0902 | 0.91561 | 1.1622 | 1.1622 | 1.1622 | 1.1622 | 1.1622
2020-04-25 18:00 | Winter | 0.55296 | 0.85024 | 1.2866 | 1.2866 | 1.2866 | 1.2866 | 0.40582 | 0.40582 | 0.40582 | 0.40582 | 0.40582 | 0.40582 | 1.9053 | 2.7483 | 3.3006 | 3.5913 | 4.1727 | 4.7541 | 0.62873 | 1.7079 | 2.1421 | 2.1421 | 2.1421 | 2.1421 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-04-25 19:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.38581 | 0.38581 | 0.38581 | 0.38581 | 0.38581 | 0.38581 | 1.8481 | 2.6658 | 3.2016 | 3.4836 | 4.0475 | 4.6115 | 0.63635 | 1.7286 | 2.1681 | 2.1681 | 2.1681 | 2.1681 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-04-25 20:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.36581 | 0.36581 | 0.36581 | 0.36581 | 0.36581 | 0.36581 | 1.81 | 2.6109 | 3.1356 | 3.4117 | 3.9641 | 4.5164 | 0.61349 | 1.6665 | 2.0902 | 2.0902 | 2.0902 | 2.0902 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-04-25 21:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.36581 | 0.36581 | 0.36581 | 0.36581 | 0.36581 | 0.36581 | 1.7719 | 2.5559 | 3.0696 | 3.3399 | 3.8806 | 4.4213 | 0.56014 | 1.5216 | 1.9084 | 1.9084 | 1.9084 | 1.9084 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-04-25 22:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.33437 | 0.33437 | 0.33437 | 0.33437 | 0.33437 | 0.33437 | 1.7338 | 2.5009 | 3.0036 | 3.2681 | 3.7972 | 4.3262 | 0.56395 | 1.5319 | 1.9214 | 1.9214 | 1.9214 | 1.9214 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-04-25 23:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.39724 | 0.39724 | 0.39724 | 0.39724 | 0.39724 | 0.39724 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.56395 | 1.5319 | 1.9214 | 1.9214 | 1.9214 | 1.9214 | 0.80021 | 1.0157 | 1.0157 | 1.0157 | 1.0157 | 1.0157
2020-04-26 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.31722 | 0.31722 | 0.31722 | 0.31722 | 0.31722 | 0.31722 | 1.6004 | 2.3086 | 2.7725 | 3.0167 | 3.5051 | 3.9934 | 0.55633 | 1.5112 | 1.8954 | 1.8954 | 1.8954 | 1.8954 | 0.78115 | 0.9915 | 0.9915 | 0.9915 | 0.9915 | 0.9915
2020-04-26 01:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.31436 | 0.31436 | 0.31436 | 0.31436 | 0.31436 | 0.31436 | 1.5623 | 2.2536 | 2.7065 | 2.9449 | 3.4216 | 3.8984 | 0.53728 | 1.4595 | 1.8305 | 1.8305 | 1.8305 | 1.8305 | 0.78115 | 0.9915 | 0.9915 | 0.9915 | 0.9915 | 0.9915
2020-04-26 02:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.32865 | 0.32865 | 0.32865 | 0.32865 | 0.32865 | 0.32865 | 1.5242 | 2.1986 | 2.6405 | 2.873 | 3.3382 | 3.8033 | 0.51823 | 1.4077 | 1.7656 | 1.7656 | 1.7656 | 1.7656 | 0.80021 | 1.0157 | 1.0157 | 1.0157 | 1.0157 | 1.0157
2020-04-26 03:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.33151 | 0.33151 | 0.33151 | 0.33151 | 0.33151 | 0.33151 | 1.5052 | 2.1711 | 2.6075 | 2.8371 | 3.2964 | 3.7557 | 0.5068 | 1.3767 | 1.7267 | 1.7267 | 1.7267 | 1.7267 | 0.78115 | 0.9915 | 0.9915 | 0.9915 | 0.9915 | 0.9915
2020-04-26 04:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.30865 | 0.30865 | 0.30865 | 0.30865 | 0.30865 | 0.30865 | 1.5496 | 2.2352 | 2.6845 | 2.9209 | 3.3938 | 3.8666 | 0.52585 | 1.4284 | 1.7916 | 1.7916 | 1.7916 | 1.7916 | 0.80021 | 1.0157 | 1.0157 | 1.0157 | 1.0157 | 1.0157
2020-04-26 05:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 1.6195 | 2.336 | 2.8055 | 3.0526 | 3.5468 | 4.041 | 0.50299 | 1.3663 | 1.7137 | 1.7137 | 1.7137 | 1.7137 | 0.80021 | 1.0157 | 1.0157 | 1.0157 | 1.0157 | 1.0157
2020-04-26 06:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.37438 | 0.37438 | 0.37438 | 0.37438 | 0.37438 | 0.37438 | 1.6004 | 2.3086 | 2.7725 | 3.0167 | 3.5051 | 3.9934 | 0.52966 | 1.4388 | 1.8046 | 1.8046 | 1.8046 | 1.8046 | 0.80021 | 1.0157 | 1.0157 | 1.0157 | 1.0157 | 1.0157
2020-04-26 07:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 1.6004 | 2.3086 | 2.7725 | 3.0167 | 3.5051 | 3.9934 | 0.51823 | 1.4077 | 1.7656 | 1.7656 | 1.7656 | 1.7656 | 0.78115 | 0.9915 | 0.9915 | 0.9915 | 0.9915 | 0.9915
2020-04-26 08:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.43127 | 0.43127 | 0.43127 | 0.43127 | 0.43127 | 0.43127 | 1.6766 | 2.4185 | 2.9045 | 3.1603 | 3.672 | 4.1836 | 0.50299 | 1.3663 | 1.7137 | 1.7137 | 1.7137 | 1.7137 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-04-26 09:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 1.7338 | 2.5009 | 3.0036 | 3.2681 | 3.7972 | 4.3262 | 0.53347 | 1.4491 | 1.8175 | 1.8175 | 1.8175 | 1.8175 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-04-26 10:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 1.9053 | 2.7483 | 3.3006 | 3.5913 | 4.1727 | 4.7541 | 0.5068 | 1.3767 | 1.7267 | 1.7267 | 1.7267 | 1.7267 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-04-26 11:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 1.9053 | 2.7483 | 3.3006 | 3.5913 | 4.1727 | 4.7541 | 0.53728 | 1.4595 | 1.8305 | 1.8305 | 1.8305 | 1.8305 | 0.78115 | 0.9915 | 0.9915 | 0.9915 | 0.9915 | 0.9915
2020-04-26 12:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 1.9243 | 2.7758 | 3.3336 | 3.6272 | 4.2144 | 4.8016 | 0.52204 | 1.4181 | 1.7786 | 1.7786 | 1.7786 | 1.7786 | 0.80021 | 1.0157 | 1.0157 | 1.0157 | 1.0157 | 1.0157
2020-04-26 13:00 | Winter | 0.57178 | 0.87918 | 1.3304 | 1.3304 | 1.3304 | 1.3304 | 0.38295 | 0.38295 | 0.38295 | 0.38295 | 0.38295 | 0.38295 | 1.8672 | 2.6933 | 3.2346 | 3.5195 | 4.0892 | 4.659 | 0.55633 | 1.5112 | 1.8954 | 1.8954 | 1.8954 | 1.8954 | 0.80021 | 1.0157 | 1.0157 | 1.0157 | 1.0157 | 1.0157
2020-04-26 14:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 1.8622 | 2.6862 | 3.2261 | 3.5102 | 4.0785 | 4.6468 | 0.48393 | 1.3146 | 1.6488 | 1.6488 | 1.6488 | 1.6488 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-04-26 15:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.43439 | 0.43439 | 0.43439 | 0.43439 | 0.43439 | 0.43439 | 1.8672 | 2.6933 | 3.2346 | 3.5195 | 4.0892 | 4.659 | 0.48774 | 1.3249 | 1.6618 | 1.6618 | 1.6618 | 1.6618 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-04-26 16:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.41439 | 0.41439 | 0.41439 | 0.41439 | 0.41439 | 0.41439 | 1.8672 | 2.6933 | 3.2346 | 3.5195 | 4.0892 | 4.659 | 0.49536 | 1.3456 | 1.6877 | 1.6877 | 1.6877 | 1.6877 | 0.97168 | 1.2333 | 1.2333 | 1.2333 | 1.2333 | 1.2333
2020-04-26 17:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.50298 | 0.50298 | 0.50298 | 0.50298 | 0.50298 | 0.50298 | 1.9434 | 2.8032 | 3.3666 | 3.6631 | 4.2562 | 4.8492 | 0.58187 | 1.5806 | 1.9824 | 1.9824 | 1.9824 | 1.9824 | 0.83686 | 1.0622 | 1.0622 | 1.0622 | 1.0622 | 1.0622
2020-04-26 18:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.40582 | 0.40582 | 0.40582 | 0.40582 | 0.40582 | 0.40582 | 2.0005 | 2.8857 | 3.4656 | 3.7709 | 4.3813 | 4.9918 | 0.59063 | 1.6044 | 2.0123 | 2.0123 | 2.0123 | 2.0123 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-04-26 19:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.37947 | 0.37947 | 0.37947 | 0.37947 | 0.37947 | 0.37947 | 1.9434 | 2.8032 | 3.3666 | 3.6631 | 4.2562 | 4.8492 | 0.58301 | 1.5837 | 1.9863 | 1.9863 | 1.9863 | 1.9863 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-04-26 20:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 1.8481 | 2.6658 | 3.2016 | 3.4836 | 4.0475 | 4.6115 | 0.58301 | 1.5837 | 1.9863 | 1.9863 | 1.9863 | 1.9863 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-04-26 21:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.38867 | 0.38867 | 0.38867 | 0.38867 | 0.38867 | 0.38867 | 1.7411 | 2.5115 | 3.0163 | 3.2819 | 3.8132 | 4.3446 | 0.58301 | 1.5837 | 1.9863 | 1.9863 | 1.9863 | 1.9863 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-04-26 22:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.39438 | 0.39438 | 0.39438 | 0.39438 | 0.39438 | 0.39438 | 1.7147 | 2.4735 | 2.9705 | 3.2322 | 3.7554 | 4.2787 | 0.57539 | 1.563 | 1.9603 | 1.9603 | 1.9603 | 1.9603 | 0.78115 | 0.9915 | 0.9915 | 0.9915 | 0.9915 | 0.9915
2020-04-26 23:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.39153 | 0.39153 | 0.39153 | 0.39153 | 0.39153 | 0.39153 | 1.6576 | 2.391 | 2.8715 | 3.1244 | 3.6302 | 4.1361 | 0.51442 | 1.3974 | 1.7526 | 1.7526 | 1.7526 | 1.7526 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-04-27 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.35437 | 0.35437 | 0.35437 | 0.35437 | 0.35437 | 0.35437 | 1.6004 | 2.3086 | 2.7725 | 3.0167 | 3.5051 | 3.9934 | 0.53347 | 1.4491 | 1.8175 | 1.8175 | 1.8175 | 1.8175 | 0.80021 | 1.0157 | 1.0157 | 1.0157 | 1.0157 | 1.0157
2020-04-27 01:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.36009 | 0.36009 | 0.36009 | 0.36009 | 0.36009 | 0.36009 | 1.5433 | 2.2261 | 2.6735 | 2.909 | 3.3799 | 3.8508 | 0.51442 | 1.3974 | 1.7526 | 1.7526 | 1.7526 | 1.7526 | 0.80021 | 1.0157 | 1.0157 | 1.0157 | 1.0157 | 1.0157
2020-04-27 02:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 1.5242 | 2.1986 | 2.6405 | 2.873 | 3.3382 | 3.8033 | 0.51442 | 1.3974 | 1.7526 | 1.7526 | 1.7526 | 1.7526 | 0.78115 | 0.9915 | 0.9915 | 0.9915 | 0.9915 | 0.9915
2020-04-27 03:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.34008 | 0.34008 | 0.34008 | 0.34008 | 0.34008 | 0.34008 | 1.4861 | 2.1437 | 2.5745 | 2.8012 | 3.2547 | 3.7082 | 0.5068 | 1.3767 | 1.7267 | 1.7267 | 1.7267 | 1.7267 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-04-27 04:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.35152 | 0.35152 | 0.35152 | 0.35152 | 0.35152 | 0.35152 | 1.5466 | 2.2309 | 2.6792 | 2.9152 | 3.3871 | 3.8591 | 0.49654 | 1.3488 | 1.6917 | 1.6917 | 1.6917 | 1.6917 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-04-27 05:00 | Winter | 0.57221 | 0.87984 | 1.3314 | 1.3314 | 1.3314 | 1.3314 | 0.38009 | 0.38009 | 0.38009 | 0.38009 | 0.38009 | 0.38009 | 1.6004 | 2.3086 | 2.7725 | 3.0167 | 3.5051 | 3.9934 | 0.5068 | 1.3767 | 1.7267 | 1.7267 | 1.7267 | 1.7267 | 1.1033 | 1.4004 | 1.4004 | 1.4004 | 1.4004 | 1.4004
2020-04-27 06:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.38009 | 0.38009 | 0.38009 | 0.38009 | 0.38009 | 0.38009 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.52204 | 1.4181 | 1.7786 | 1.7786 | 1.7786 | 1.7786 | 1.5007 | 1.9048 | 1.9048 | 1.9048 | 1.9048 | 1.9048
2020-04-27 07:00 | Winter | 0.57151 | 0.87876 | 1.3297 | 1.3297 | 1.3297 | 1.3297 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 1.7338 | 2.5009 | 3.0036 | 3.2681 | 3.7972 | 4.3262 | 0.51823 | 1.4077 | 1.7656 | 1.7656 | 1.7656 | 1.7656 | 1.6004 | 2.0314 | 2.0314 | 2.0314 | 2.0314 | 2.0314
2020-04-27 08:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 1.7719 | 2.5559 | 3.0696 | 3.3399 | 3.8806 | 4.4213 | 0.53728 | 1.4595 | 1.8305 | 1.8305 | 1.8305 | 1.8305 | 1.6004 | 2.0314 | 2.0314 | 2.0314 | 2.0314 | 2.0314
2020-04-27 09:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.40296 | 0.40296 | 0.40296 | 0.40296 | 0.40296 | 0.40296 | 1.9053 | 2.7483 | 3.3006 | 3.5913 | 4.1727 | 4.7541 | 0.56395 | 1.5319 | 1.9214 | 1.9214 | 1.9214 | 1.9214 | 1.6004 | 2.0314 | 2.0314 | 2.0314 | 2.0314 | 2.0314
2020-04-27 10:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.50013 | 0.50013 | 0.50013 | 0.50013 | 0.50013 | 0.50013 | 1.9815 | 2.8582 | 3.4326 | 3.735 | 4.3396 | 4.9443 | 0.56395 | 1.5319 | 1.9214 | 1.9214 | 1.9214 | 1.9214 | 1.6195 | 2.0556 | 2.0556 | 2.0556 | 2.0556 | 2.0556
2020-04-27 11:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.27721 | 0.27721 | 0.27721 | 0.27721 | 0.27721 | 0.27721 | 1.9613 | 2.8291 | 3.3976 | 3.6969 | 4.2953 | 4.8938 | 0.54109 | 1.4698 | 1.8435 | 1.8435 | 1.8435 | 1.8435 | 1.6061 | 2.0386 | 2.0386 | 2.0386 | 2.0386 | 2.0386
2020-04-27 12:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.48012 | 0.48012 | 0.48012 | 0.48012 | 0.48012 | 0.48012 | 2.0005 | 2.8857 | 3.4656 | 3.7709 | 4.3813 | 4.9918 | 0.48012 | 1.3042 | 1.6358 | 1.6358 | 1.6358 | 1.6358 | 1.5242 | 1.9346 | 1.9346 | 1.9346 | 1.9346 | 1.9346
2020-04-27 13:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.26578 | 0.26578 | 0.26578 | 0.26578 | 0.26578 | 0.26578 | 1.9815 | 2.8582 | 3.4326 | 3.735 | 4.3396 | 4.9443 | 0.49155 | 1.3353 | 1.6747 | 1.6747 | 1.6747 | 1.6747 | 1.448 | 1.8379 | 1.8379 | 1.8379 | 1.8379 | 1.8379
2020-04-27 14:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.48869 | 0.48869 | 0.48869 | 0.48869 | 0.48869 | 0.48869 | 1.9243 | 2.7758 | 3.3336 | 3.6272 | 4.2144 | 4.8016 | 0.48393 | 1.3146 | 1.6488 | 1.6488 | 1.6488 | 1.6488 | 1.4289 | 1.8137 | 1.8137 | 1.8137 | 1.8137 | 1.8137
2020-04-27 15:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.48012 | 0.48012 | 0.48012 | 0.48012 | 0.48012 | 0.48012 | 2.0386 | 2.9407 | 3.5316 | 3.8427 | 4.4648 | 5.0869 | 0.51442 | 1.3974 | 1.7526 | 1.7526 | 1.7526 | 1.7526 | 1.4289 | 1.8137 | 1.8137 | 1.8137 | 1.8137 | 1.8137
2020-04-27 16:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.49441 | 0.49441 | 0.49441 | 0.49441 | 0.49441 | 0.49441 | 1.9589 | 2.8257 | 3.3935 | 3.6924 | 4.2902 | 4.888 | 0.53347 | 1.4491 | 1.8175 | 1.8175 | 1.8175 | 1.8175 | 1.4289 | 1.8137 | 1.8137 | 1.8137 | 1.8137 | 1.8137
2020-04-27 17:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.45061 | 0.45061 | 0.45061 | 0.45061 | 0.45061 | 0.45061 | 1.9243 | 2.7758 | 3.3336 | 3.6272 | 4.2144 | 4.8016 | 0.62492 | 1.6975 | 2.1291 | 2.1291 | 2.1291 | 2.1291 | 1.4099 | 1.7895 | 1.7895 | 1.7895 | 1.7895 | 1.7895
2020-04-27 18:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 2.0005 | 2.8857 | 3.4656 | 3.7709 | 4.3813 | 4.9918 | 0.60206 | 1.6354 | 2.0512 | 2.0512 | 2.0512 | 2.0512 | 1.0064 | 1.2774 | 1.2774 | 1.2774 | 1.2774 | 1.2774
2020-04-27 19:00 | Winter | 0.55521 | 0.8537 | 1.2918 | 1.2918 | 1.2918 | 1.2918 | 0.31245 | 0.31245 | 0.31245 | 0.31245 | 0.31245 | 0.31245 | 1.9301 | 2.7841 | 3.3436 | 3.6381 | 4.2271 | 4.816 | 0.60587 | 1.6458 | 2.0642 | 2.0642 | 2.0642 | 2.0642 | 0.89573 | 1.1369 | 1.1369 | 1.1369 | 1.1369 | 1.1369
2020-04-27 20:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.38295 | 0.38295 | 0.38295 | 0.38295 | 0.38295 | 0.38295 | 1.8862 | 2.7208 | 3.2676 | 3.5554 | 4.131 | 4.7066 | 0.62873 | 1.7079 | 2.1421 | 2.1421 | 2.1421 | 2.1421 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-04-27 21:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.25575 | 0.25575 | 0.25575 | 0.25575 | 0.25575 | 0.25575 | 1.829 | 2.6383 | 3.1686 | 3.4477 | 4.0058 | 4.5639 | 0.62111 | 1.6872 | 2.1161 | 2.1161 | 2.1161 | 2.1161 | 0.82836 | 1.0514 | 1.0514 | 1.0514 | 1.0514 | 1.0514
2020-04-27 22:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.37724 | 0.37724 | 0.37724 | 0.37724 | 0.37724 | 0.37724 | 1.6957 | 2.446 | 2.9375 | 3.1963 | 3.7137 | 4.2311 | 0.5792 | 1.5733 | 1.9733 | 1.9733 | 1.9733 | 1.9733 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-04-27 23:00 | Winter | 0.57621 | 0.886 | 1.3407 | 1.3407 | 1.3407 | 1.3407 | 0.39438 | 0.39438 | 0.39438 | 0.39438 | 0.39438 | 0.39438 | 1.6576 | 2.391 | 2.8715 | 3.1244 | 3.6302 | 4.1361 | 0.58301 | 1.5837 | 1.9863 | 1.9863 | 1.9863 | 1.9863 | 0.78843 | 1.0007 | 1.0007 | 1.0007 | 1.0007 | 1.0007
2020-04-28 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.32294 | 0.32294 | 0.32294 | 0.32294 | 0.32294 | 0.32294 | 1.5433 | 2.2261 | 2.6735 | 2.909 | 3.3799 | 3.8508 | 0.53701 | 1.4587 | 1.8296 | 1.8296 | 1.8296 | 1.8296 | 0.80021 | 1.0157 | 1.0157 | 1.0157 | 1.0157 | 1.0157
2020-04-28 01:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.24377 | 0.24377 | 0.24377 | 0.24377 | 0.24377 | 0.24377 | 1.5242 | 2.1986 | 2.6405 | 2.873 | 3.3382 | 3.8033 | 0.53728 | 1.4595 | 1.8305 | 1.8305 | 1.8305 | 1.8305 | 0.80021 | 1.0157 | 1.0157 | 1.0157 | 1.0157 | 1.0157
2020-04-28 02:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.38581 | 0.38581 | 0.38581 | 0.38581 | 0.38581 | 0.38581 | 1.4861 | 2.1437 | 2.5745 | 2.8012 | 3.2547 | 3.7082 | 0.49536 | 1.3456 | 1.6877 | 1.6877 | 1.6877 | 1.6877 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-04-28 03:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.38009 | 0.38009 | 0.38009 | 0.38009 | 0.38009 | 0.38009 | 1.5026 | 2.1675 | 2.6031 | 2.8323 | 3.2908 | 3.7494 | 0.52585 | 1.4284 | 1.7916 | 1.7916 | 1.7916 | 1.7916 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-04-28 04:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.4544 | 0.4544 | 0.4544 | 0.4544 | 0.4544 | 0.4544 | 1.5471 | 2.2317 | 2.6802 | 2.9162 | 3.3883 | 3.8604 | 0.49155 | 1.3353 | 1.6747 | 1.6747 | 1.6747 | 1.6747 | 0.87743 | 1.1137 | 1.1137 | 1.1137 | 1.1137 | 1.1137
2020-04-28 05:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.59444 | 0.59444 | 0.59444 | 0.59444 | 0.59444 | 0.59444 | 1.5882 | 2.291 | 2.7514 | 2.9938 | 3.4784 | 3.9631 | 0.53728 | 1.4595 | 1.8305 | 1.8305 | 1.8305 | 1.8305 | 1.2546 | 1.5925 | 1.5925 | 1.5925 | 1.5925 | 1.5925
2020-04-28 06:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.66303 | 0.66303 | 0.66303 | 0.66303 | 0.66303 | 0.66303 | 1.7111 | 2.4683 | 2.9643 | 3.2254 | 3.7475 | 4.2697 | 0.62111 | 1.6872 | 2.1161 | 2.1161 | 2.1161 | 2.1161 | 1.6576 | 2.1039 | 2.1039 | 2.1039 | 2.1039 | 2.1039
2020-04-28 07:00 | Winter | 0.87642 | 1.3476 | 2.0392 | 2.0392 | 2.0392 | 2.0392 | 0.76591 | 0.76591 | 0.76591 | 0.76591 | 0.76591 | 0.76591 | 2.044 | 2.9484 | 3.541 | 3.8528 | 4.4766 | 5.1003 | 0.70113 | 1.9046 | 2.3888 | 2.3888 | 2.3888 | 2.3888 | 1.9624 | 2.4908 | 2.4908 | 2.4908 | 2.4908 | 2.4908
2020-04-28 08:00 | Winter | 1.1498 | 1.7679 | 2.6752 | 2.6752 | 2.6752 | 2.6752 | 0.81735 | 0.81735 | 0.81735 | 0.81735 | 0.81735 | 0.81735 | 2.1339 | 3.0781 | 3.6967 | 4.0223 | 4.6734 | 5.3246 | 0.75829 | 2.0598 | 2.5835 | 2.5835 | 2.5835 | 2.5835 | 2.0958 | 2.6601 | 2.6601 | 2.6601 | 2.6601 | 2.6601
2020-04-28 09:00 | Winter | 1.3337 | 2.0507 | 3.1031 | 3.1031 | 3.1031 | 3.1031 | 0.82592 | 0.82592 | 0.82592 | 0.82592 | 0.82592 | 0.82592 | 2.2482 | 3.243 | 3.8947 | 4.2377 | 4.9238 | 5.6098 | 0.81164 | 2.2047 | 2.7653 | 2.7653 | 2.7653 | 2.7653 | 2.1529 | 2.7327 | 2.7327 | 2.7327 | 2.7327 | 2.7327
2020-04-28 10:00 | Winter | 1.2384 | 1.9042 | 2.8814 | 2.8814 | 2.8814 | 2.8814 | 0.8545 | 0.8545 | 0.8545 | 0.8545 | 0.8545 | 0.8545 | 2.2673 | 3.2705 | 3.9277 | 4.2736 | 4.9655 | 5.6574 | 0.7964 | 2.1633 | 2.7133 | 2.7133 | 2.7133 | 2.7133 | 2.172 | 2.7569 | 2.7569 | 2.7569 | 2.7569 | 2.7569
2020-04-28 11:00 | Winter | 1.2956 | 1.9921 | 3.0144 | 3.0144 | 3.0144 | 3.0144 | 0.82878 | 0.82878 | 0.82878 | 0.82878 | 0.82878 | 0.82878 | 2.3625 | 3.4079 | 4.0927 | 4.4532 | 5.1741 | 5.8951 | 0.75067 | 2.0391 | 2.5575 | 2.5575 | 2.5575 | 2.5575 | 2.1148 | 2.6843 | 2.6843 | 2.6843 | 2.6843 | 2.6843
2020-04-28 12:00 | Winter | 1.2575 | 1.9335 | 2.9258 | 2.9258 | 2.9258 | 2.9258 | 0.87737 | 0.87737 | 0.87737 | 0.87737 | 0.87737 | 0.87737 | 2.3244 | 3.3529 | 4.0267 | 4.3814 | 5.0907 | 5.8 | 0.7621 | 2.0702 | 2.5965 | 2.5965 | 2.5965 | 2.5965 | 2.0958 | 2.6601 | 2.6601 | 2.6601 | 2.6601 | 2.6601
2020-04-28 13:00 | Winter | 1.2575 | 1.9335 | 2.9258 | 2.9258 | 2.9258 | 2.9258 | 0.79735 | 0.79735 | 0.79735 | 0.79735 | 0.79735 | 0.79735 | 2.3625 | 3.4079 | 4.0927 | 4.4532 | 5.1741 | 5.8951 | 0.71256 | 1.9356 | 2.4277 | 2.4277 | 2.4277 | 2.4277 | 2.0386 | 2.5876 | 2.5876 | 2.5876 | 2.5876 | 2.5876
2020-04-28 14:00 | Winter | 1.2765 | 1.9628 | 2.9701 | 2.9701 | 2.9701 | 2.9701 | 0.88594 | 0.88594 | 0.88594 | 0.88594 | 0.88594 | 0.88594 | 2.4578 | 3.5453 | 4.2578 | 4.6328 | 5.3828 | 6.1328 | 0.70113 | 1.9046 | 2.3888 | 2.3888 | 2.3888 | 2.3888 | 2.0386 | 2.5876 | 2.5876 | 2.5876 | 2.5876 | 2.5876
2020-04-28 15:00 | Winter | 1.2575 | 1.9335 | 2.9258 | 2.9258 | 2.9258 | 2.9258 | 0.81735 | 0.81735 | 0.81735 | 0.81735 | 0.81735 | 0.81735 | 2.4387 | 3.5178 | 4.2248 | 4.5969 | 5.3411 | 6.0852 | 0.724 | 1.9667 | 2.4667 | 2.4667 | 2.4667 | 2.4667 | 2.0386 | 2.5876 | 2.5876 | 2.5876 | 2.5876 | 2.5876
2020-04-28 16:00 | Winter | 1.2575 | 1.9335 | 2.9258 | 2.9258 | 2.9258 | 2.9258 | 0.87165 | 0.87165 | 0.87165 | 0.87165 | 0.87165 | 0.87165 | 2.3244 | 3.3529 | 4.0267 | 4.3814 | 5.0907 | 5.8 | 0.73543 | 1.9977 | 2.5056 | 2.5056 | 2.5056 | 2.5056 | 1.9815 | 2.515 | 2.515 | 2.515 | 2.515 | 2.515
2020-04-28 17:00 | Winter | 1.1813 | 1.8163 | 2.7485 | 2.7485 | 2.7485 | 2.7485 | 0.82307 | 0.82307 | 0.82307 | 0.82307 | 0.82307 | 0.82307 | 2.2863 | 3.2979 | 3.9607 | 4.3096 | 5.0072 | 5.7049 | 0.72018 | 1.9563 | 2.4537 | 2.4537 | 2.4537 | 2.4537 | 1.8481 | 2.3458 | 2.3458 | 2.3458 | 2.3458 | 2.3458
2020-04-28 18:00 | Winter | 0.81973 | 1.2604 | 1.9073 | 1.9073 | 1.9073 | 1.9073 | 0.62873 | 0.62873 | 0.62873 | 0.62873 | 0.62873 | 0.62873 | 2.2863 | 3.2979 | 3.9607 | 4.3096 | 5.0072 | 5.7049 | 0.67827 | 1.8425 | 2.3109 | 2.3109 | 2.3109 | 2.3109 | 1.393 | 1.7682 | 1.7682 | 1.7682 | 1.7682 | 1.7682
2020-04-28 19:00 | Winter | 0.70361 | 1.0819 | 1.6371 | 1.6371 | 1.6371 | 1.6371 | 0.5594 | 0.5594 | 0.5594 | 0.5594 | 0.5594 | 0.5594 | 2.1148 | 3.0506 | 3.6637 | 3.9863 | 4.6317 | 5.277 | 0.66303 | 1.8011 | 2.2589 | 2.2589 | 2.2589 | 2.2589 | 1.086 | 1.3784 | 1.3784 | 1.3784 | 1.3784 | 1.3784
2020-04-28 20:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 1.9815 | 2.8582 | 3.4326 | 3.735 | 4.3396 | 4.9443 | 0.62873 | 1.7079 | 2.1421 | 2.1421 | 2.1421 | 2.1421 | 1.0288 | 1.3059 | 1.3059 | 1.3059 | 1.3059 | 1.3059
2020-04-28 21:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 1.8862 | 2.7208 | 3.2676 | 3.5554 | 4.131 | 4.7066 | 0.65541 | 1.7803 | 2.233 | 2.233 | 2.233 | 2.233 | 0.93358 | 1.185 | 1.185 | 1.185 | 1.185 | 1.185
2020-04-28 22:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 1.829 | 2.6383 | 3.1686 | 3.4477 | 4.0058 | 4.5639 | 0.60206 | 1.6354 | 2.0512 | 2.0512 | 2.0512 | 2.0512 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-04-28 23:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 1.7148 | 2.4736 | 2.9707 | 3.2323 | 3.7556 | 4.2789 | 0.55252 | 1.5009 | 1.8825 | 1.8825 | 1.8825 | 1.8825 | 0.83824 | 1.064 | 1.064 | 1.064 | 1.064 | 1.064
2020-04-29 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.3258 | 0.3258 | 0.3258 | 0.3258 | 0.3258 | 0.3258 | 1.6389 | 2.364 | 2.8392 | 3.0892 | 3.5893 | 4.0894 | 0.54871 | 1.4905 | 1.8695 | 1.8695 | 1.8695 | 1.8695 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-04-29 01:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.36295 | 0.36295 | 0.36295 | 0.36295 | 0.36295 | 0.36295 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.5449 | 1.4802 | 1.8565 | 1.8565 | 1.8565 | 1.8565 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-04-29 02:00 | Winter | 0.57231 | 0.87999 | 1.3316 | 1.3316 | 1.3316 | 1.3316 | 0.38009 | 0.38009 | 0.38009 | 0.38009 | 0.38009 | 0.38009 | 1.6195 | 2.336 | 2.8055 | 3.0526 | 3.5468 | 4.041 | 0.51442 | 1.3974 | 1.7526 | 1.7526 | 1.7526 | 1.7526 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-04-29 03:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.3458 | 0.3458 | 0.3458 | 0.3458 | 0.3458 | 0.3458 | 1.6004 | 2.3086 | 2.7725 | 3.0167 | 3.5051 | 3.9934 | 0.54109 | 1.4698 | 1.8435 | 1.8435 | 1.8435 | 1.8435 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-04-29 04:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.37438 | 0.37438 | 0.37438 | 0.37438 | 0.37438 | 0.37438 | 1.6004 | 2.3086 | 2.7725 | 3.0167 | 3.5051 | 3.9934 | 0.52204 | 1.4181 | 1.7786 | 1.7786 | 1.7786 | 1.7786 | 0.94022 | 1.1934 | 1.1934 | 1.1934 | 1.1934 | 1.1934
2020-04-29 05:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 1.6617 | 2.3969 | 2.8786 | 3.1322 | 3.6392 | 4.1463 | 0.56776 | 1.5423 | 1.9344 | 1.9344 | 1.9344 | 1.9344 | 1.1513 | 1.4613 | 1.4613 | 1.4613 | 1.4613 | 1.4613
2020-04-29 06:00 | Winter | 0.61268 | 0.94207 | 1.4255 | 1.4255 | 1.4255 | 1.4255 | 0.65445 | 0.65445 | 0.65445 | 0.65445 | 0.65445 | 0.65445 | 1.7711 | 2.5548 | 3.0682 | 3.3384 | 3.8789 | 4.4193 | 0.56395 | 1.5319 | 1.9214 | 1.9214 | 1.9214 | 1.9214 | 1.5688 | 1.9912 | 1.9912 | 1.9912 | 1.9912 | 1.9912
2020-04-29 07:00 | Winter | 0.83813 | 1.2887 | 1.9501 | 1.9501 | 1.9501 | 1.9501 | 0.72304 | 0.72304 | 0.72304 | 0.72304 | 0.72304 | 0.72304 | 2.0196 | 2.9132 | 3.4986 | 3.8068 | 4.4231 | 5.0393 | 0.78877 | 2.1426 | 2.6874 | 2.6874 | 2.6874 | 2.6874 | 1.8481 | 2.3458 | 2.3458 | 2.3458 | 2.3458 | 2.3458
2020-04-29 08:00 | Winter | 1.2003 | 1.8456 | 2.7928 | 2.7928 | 2.7928 | 2.7928 | 0.80592 | 0.80592 | 0.80592 | 0.80592 | 0.80592 | 0.80592 | 2.2095 | 3.1871 | 3.8277 | 4.1648 | 4.839 | 5.5132 | 0.80021 | 2.1737 | 2.7263 | 2.7263 | 2.7263 | 2.7263 | 2.0386 | 2.5876 | 2.5876 | 2.5876 | 2.5876 | 2.5876
2020-04-29 09:00 | Winter | 1.1622 | 1.787 | 2.7041 | 2.7041 | 2.7041 | 2.7041 | 0.8345 | 0.8345 | 0.8345 | 0.8345 | 0.8345 | 0.8345 | 2.2291 | 3.2155 | 3.8617 | 4.2018 | 4.8821 | 5.5623 | 0.80402 | 2.184 | 2.7393 | 2.7393 | 2.7393 | 2.7393 | 2.0005 | 2.5392 | 2.5392 | 2.5392 | 2.5392 | 2.5392
2020-04-29 10:00 | Winter | 1.1813 | 1.8163 | 2.7485 | 2.7485 | 2.7485 | 2.7485 | 0.8545 | 0.8545 | 0.8545 | 0.8545 | 0.8545 | 0.8545 | 2.212 | 3.1908 | 3.832 | 4.1695 | 4.8445 | 5.5195 | 0.88023 | 2.3911 | 2.9989 | 2.9989 | 2.9989 | 2.9989 | 2.0344 | 2.5822 | 2.5822 | 2.5822 | 2.5822 | 2.5822
2020-04-29 11:00 | Winter | 1.2194 | 1.8749 | 2.8371 | 2.8371 | 2.8371 | 2.8371 | 0.84593 | 0.84593 | 0.84593 | 0.84593 | 0.84593 | 0.84593 | 2.2863 | 3.2979 | 3.9607 | 4.3096 | 5.0072 | 5.7049 | 0.87642 | 2.3807 | 2.986 | 2.986 | 2.986 | 2.986 | 2.1148 | 2.6843 | 2.6843 | 2.6843 | 2.6843 | 2.6843
2020-04-29 12:00 | Winter | 1.2194 | 1.8749 | 2.8371 | 2.8371 | 2.8371 | 2.8371 | 0.88594 | 0.88594 | 0.88594 | 0.88594 | 0.88594 | 0.88594 | 2.4006 | 3.4628 | 4.1588 | 4.525 | 5.2576 | 5.9902 | 0.88785 | 2.4118 | 3.0249 | 3.0249 | 3.0249 | 3.0249 | 2.0386 | 2.5876 | 2.5876 | 2.5876 | 2.5876 | 2.5876
2020-04-29 13:00 | Winter | 1.1813 | 1.8163 | 2.7485 | 2.7485 | 2.7485 | 2.7485 | 0.87737 | 0.87737 | 0.87737 | 0.87737 | 0.87737 | 0.87737 | 2.3054 | 3.3254 | 3.9937 | 4.3455 | 5.049 | 5.7525 | 0.87642 | 2.3807 | 2.986 | 2.986 | 2.986 | 2.986 | 2.0958 | 2.6601 | 2.6601 | 2.6601 | 2.6601 | 2.6601
2020-04-29 14:00 | Winter | 1.1432 | 1.7577 | 2.6598 | 2.6598 | 2.6598 | 2.6598 | 0.88594 | 0.88594 | 0.88594 | 0.88594 | 0.88594 | 0.88594 | 2.2482 | 3.243 | 3.8947 | 4.2377 | 4.9238 | 5.6098 | 0.88785 | 2.4118 | 3.0249 | 3.0249 | 3.0249 | 3.0249 | 2.0448 | 2.5954 | 2.5954 | 2.5954 | 2.5954 | 2.5954
2020-04-29 15:00 | Winter | 1.1432 | 1.7577 | 2.6598 | 2.6598 | 2.6598 | 2.6598 | 0.8002 | 0.8002 | 0.8002 | 0.8002 | 0.8002 | 0.8002 | 2.2673 | 3.2705 | 3.9277 | 4.2736 | 4.9655 | 5.6574 | 0.86879 | 2.36 | 2.96 | 2.96 | 2.96 | 2.96 | 2.0386 | 2.5876 | 2.5876 | 2.5876 | 2.5876 | 2.5876
2020-04-29 16:00 | Winter | 1.086 | 1.6698 | 2.5268 | 2.5268 | 2.5268 | 2.5268 | 0.81735 | 0.81735 | 0.81735 | 0.81735 | 0.81735 | 0.81735 | 2.2673 | 3.2705 | 3.9277 | 4.2736 | 4.9655 | 5.6574 | 0.87642 | 2.3807 | 2.986 | 2.986 | 2.986 | 2.986 | 1.9624 | 2.4908 | 2.4908 | 2.4908 | 2.4908 | 2.4908
2020-04-29 17:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 0.82307 | 0.82307 | 0.82307 | 0.82307 | 0.82307 | 0.82307 | 2.3435 | 3.3804 | 4.0597 | 4.4173 | 5.1324 | 5.8475 | 0.81545 | 2.2151 | 2.7782 | 2.7782 | 2.7782 | 2.7782 | 1.9243 | 2.4425 | 2.4425 | 2.4425 | 2.4425 | 2.4425
2020-04-29 18:00 | Winter | 0.90766 | 1.3956 | 2.1119 | 2.1119 | 2.1119 | 2.1119 | 0.64302 | 0.64302 | 0.64302 | 0.64302 | 0.64302 | 0.64302 | 2.3054 | 3.3254 | 3.9937 | 4.3455 | 5.049 | 5.7525 | 0.7621 | 2.0702 | 2.5965 | 2.5965 | 2.5965 | 2.5965 | 1.3539 | 1.7185 | 1.7185 | 1.7185 | 1.7185 | 1.7185
2020-04-29 19:00 | Winter | 0.68589 | 1.0546 | 1.5959 | 1.5959 | 1.5959 | 1.5959 | 0.53442 | 0.53442 | 0.53442 | 0.53442 | 0.53442 | 0.53442 | 2.1339 | 3.0781 | 3.6967 | 4.0223 | 4.6734 | 5.3246 | 0.65922 | 1.7907 | 2.246 | 2.246 | 2.246 | 2.246 | 1.093 | 1.3873 | 1.3873 | 1.3873 | 1.3873 | 1.3873
2020-04-29 20:00 | Winter | 0.66684 | 1.0253 | 1.5515 | 1.5515 | 1.5515 | 1.5515 | 0.57443 | 0.57443 | 0.57443 | 0.57443 | 0.57443 | 0.57443 | 2.0577 | 2.9681 | 3.5647 | 3.8786 | 4.5065 | 5.1344 | 0.63635 | 1.7286 | 2.1681 | 2.1681 | 2.1681 | 2.1681 | 1.0288 | 1.3059 | 1.3059 | 1.3059 | 1.3059 | 1.3059
2020-04-29 21:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.48584 | 0.48584 | 0.48584 | 0.48584 | 0.48584 | 0.48584 | 1.9434 | 2.8032 | 3.3666 | 3.6631 | 4.2562 | 4.8492 | 0.61349 | 1.6665 | 2.0902 | 2.0902 | 2.0902 | 2.0902 | 0.93358 | 1.185 | 1.185 | 1.185 | 1.185 | 1.185
2020-04-29 22:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.51156 | 0.51156 | 0.51156 | 0.51156 | 0.51156 | 0.51156 | 1.8862 | 2.7208 | 3.2676 | 3.5554 | 4.131 | 4.7066 | 0.5792 | 1.5733 | 1.9733 | 1.9733 | 1.9733 | 1.9733 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-04-29 23:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.51156 | 0.51156 | 0.51156 | 0.51156 | 0.51156 | 0.51156 | 1.7719 | 2.5559 | 3.0696 | 3.3399 | 3.8806 | 4.4213 | 0.57539 | 1.563 | 1.9603 | 1.9603 | 1.9603 | 1.9603 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-04-30 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 1.6768 | 2.4187 | 2.9048 | 3.1606 | 3.6723 | 4.1839 | 0.52966 | 1.4388 | 1.8046 | 1.8046 | 1.8046 | 1.8046 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-04-30 01:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.56776 | 1.5423 | 1.9344 | 1.9344 | 1.9344 | 1.9344 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-04-30 02:00 | Winter | 0.59005 | 0.90727 | 1.3729 | 1.3729 | 1.3729 | 1.3729 | 0.36866 | 0.36866 | 0.36866 | 0.36866 | 0.36866 | 0.36866 | 1.6004 | 2.3086 | 2.7725 | 3.0167 | 3.5051 | 3.9934 | 0.54871 | 1.4905 | 1.8695 | 1.8695 | 1.8695 | 1.8695 | 0.91452 | 1.1608 | 1.1608 | 1.1608 | 1.1608 | 1.1608
2020-04-30 03:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.37438 | 0.37438 | 0.37438 | 0.37438 | 0.37438 | 0.37438 | 1.5814 | 2.2811 | 2.7395 | 2.9808 | 3.4633 | 3.9459 | 0.56776 | 1.5423 | 1.9344 | 1.9344 | 1.9344 | 1.9344 | 0.91452 | 1.1608 | 1.1608 | 1.1608 | 1.1608 | 1.1608
2020-04-30 04:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 1.6195 | 2.336 | 2.8055 | 3.0526 | 3.5468 | 4.041 | 0.53347 | 1.4491 | 1.8175 | 1.8175 | 1.8175 | 1.8175 | 0.93358 | 1.185 | 1.185 | 1.185 | 1.185 | 1.185
2020-04-30 05:00 | Winter | 0.58299 | 0.89641 | 1.3564 | 1.3564 | 1.3564 | 1.3564 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 1.6957 | 2.446 | 2.9375 | 3.1963 | 3.7137 | 4.2311 | 0.56395 | 1.5319 | 1.9214 | 1.9214 | 1.9214 | 1.9214 | 1.2876 | 1.6343 | 1.6343 | 1.6343 | 1.6343 | 1.6343
2020-04-30 06:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.58789 | 0.58789 | 0.58789 | 0.58789 | 0.58789 | 0.58789 | 1.7338 | 2.5009 | 3.0036 | 3.2681 | 3.7972 | 4.3262 | 0.60968 | 1.6561 | 2.0772 | 2.0772 | 2.0772 | 2.0772 | 1.6757 | 2.1269 | 2.1269 | 2.1269 | 2.1269 | 2.1269
2020-04-30 07:00 | Winter | 0.90222 | 1.3873 | 2.0992 | 2.0992 | 2.0992 | 2.0992 | 0.76019 | 0.76019 | 0.76019 | 0.76019 | 0.76019 | 0.76019 | 1.9815 | 2.8582 | 3.4326 | 3.735 | 4.3396 | 4.9443 | 0.69351 | 1.8839 | 2.3628 | 2.3628 | 2.3628 | 2.3628 | 1.9624 | 2.4908 | 2.4908 | 2.4908 | 2.4908 | 2.4908
2020-04-30 08:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 0.81735 | 0.81735 | 0.81735 | 0.81735 | 0.81735 | 0.81735 | 2.1339 | 3.0781 | 3.6967 | 4.0223 | 4.6734 | 5.3246 | 0.7621 | 2.0702 | 2.5965 | 2.5965 | 2.5965 | 2.5965 | 2.1339 | 2.7085 | 2.7085 | 2.7085 | 2.7085 | 2.7085
2020-04-30 09:00 | Winter | 1.0669 | 1.6405 | 2.4825 | 2.4825 | 2.4825 | 2.4825 | 0.89451 | 0.89451 | 0.89451 | 0.89451 | 0.89451 | 0.89451 | 2.1529 | 3.1056 | 3.7297 | 4.0582 | 4.7151 | 5.3721 | 0.73543 | 1.9977 | 2.5056 | 2.5056 | 2.5056 | 2.5056 | 2.1339 | 2.7085 | 2.7085 | 2.7085 | 2.7085 | 2.7085
2020-04-30 10:00 | Winter | 1.0669 | 1.6405 | 2.4825 | 2.4825 | 2.4825 | 2.4825 | 0.9631 | 0.9631 | 0.9631 | 0.9631 | 0.9631 | 0.9631 | 2.3054 | 3.3254 | 3.9937 | 4.3455 | 5.049 | 5.7525 | 0.724 | 1.9667 | 2.4667 | 2.4667 | 2.4667 | 2.4667 | 2.2291 | 2.8294 | 2.8294 | 2.8294 | 2.8294 | 2.8294
2020-04-30 11:00 | Winter | 1.086 | 1.6698 | 2.5268 | 2.5268 | 2.5268 | 2.5268 | 1.0517 | 1.0517 | 1.0517 | 1.0517 | 1.0517 | 1.0517 | 2.3024 | 3.3212 | 3.9886 | 4.3399 | 5.0425 | 5.7451 | 0.75067 | 2.0391 | 2.5575 | 2.5575 | 2.5575 | 2.5575 | 2.2101 | 2.8052 | 2.8052 | 2.8052 | 2.8052 | 2.8052
2020-04-30 12:00 | Winter | 1.086 | 1.6698 | 2.5268 | 2.5268 | 2.5268 | 2.5268 | 0.98597 | 0.98597 | 0.98597 | 0.98597 | 0.98597 | 0.98597 | 2.3625 | 3.4079 | 4.0927 | 4.4532 | 5.1741 | 5.8951 | 0.80402 | 2.184 | 2.7393 | 2.7393 | 2.7393 | 2.7393 | 2.2673 | 2.8778 | 2.8778 | 2.8778 | 2.8778 | 2.8778
2020-04-30 13:00 | Winter | 1.0606 | 1.6307 | 2.4676 | 2.4676 | 2.4676 | 2.4676 | 0.9631 | 0.9631 | 0.9631 | 0.9631 | 0.9631 | 0.9631 | 2.3625 | 3.4079 | 4.0927 | 4.4532 | 5.1741 | 5.8951 | 0.75067 | 2.0391 | 2.5575 | 2.5575 | 2.5575 | 2.5575 | 2.2482 | 2.8536 | 2.8536 | 2.8536 | 2.8536 | 2.8536
2020-04-30 14:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 0.94881 | 0.94881 | 0.94881 | 0.94881 | 0.94881 | 0.94881 | 2.2871 | 3.2991 | 3.9621 | 4.3111 | 5.009 | 5.7069 | 0.73924 | 2.0081 | 2.5186 | 2.5186 | 2.5186 | 2.5186 | 2.172 | 2.7569 | 2.7569 | 2.7569 | 2.7569 | 2.7569
2020-04-30 15:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 0.9431 | 0.9431 | 0.9431 | 0.9431 | 0.9431 | 0.9431 | 2.2673 | 3.2705 | 3.9277 | 4.2736 | 4.9655 | 5.6574 | 0.75448 | 2.0495 | 2.5705 | 2.5705 | 2.5705 | 2.5705 | 2.0767 | 2.6359 | 2.6359 | 2.6359 | 2.6359 | 2.6359
2020-04-30 16:00 | Winter | 1.0086 | 1.5508 | 2.3467 | 2.3467 | 2.3467 | 2.3467 | 0.95167 | 0.95167 | 0.95167 | 0.95167 | 0.95167 | 0.95167 | 2.2673 | 3.2705 | 3.9277 | 4.2736 | 4.9655 | 5.6574 | 0.79258 | 2.153 | 2.7003 | 2.7003 | 2.7003 | 2.7003 | 2.0577 | 2.6118 | 2.6118 | 2.6118 | 2.6118 | 2.6118
2020-04-30 17:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.95167 | 0.95167 | 0.95167 | 0.95167 | 0.95167 | 0.95167 | 2.3625 | 3.4079 | 4.0927 | 4.4532 | 5.1741 | 5.8951 | 0.80783 | 2.1944 | 2.7523 | 2.7523 | 2.7523 | 2.7523 | 2.0011 | 2.5399 | 2.5399 | 2.5399 | 2.5399 | 2.5399
2020-04-30 18:00 | Winter | 0.82765 | 1.2726 | 1.9257 | 1.9257 | 1.9257 | 1.9257 | 0.73447 | 0.73447 | 0.73447 | 0.73447 | 0.73447 | 0.73447 | 2.3054 | 3.3254 | 3.9937 | 4.3455 | 5.049 | 5.7525 | 0.74012 | 2.0105 | 2.5216 | 2.5216 | 2.5216 | 2.5216 | 1.4388 | 1.8263 | 1.8263 | 1.8263 | 1.8263 | 1.8263
2020-04-30 19:00 | Winter | 0.68589 | 1.0546 | 1.5959 | 1.5959 | 1.5959 | 1.5959 | 0.64016 | 0.64016 | 0.64016 | 0.64016 | 0.64016 | 0.64016 | 2.2673 | 3.2705 | 3.9277 | 4.2736 | 4.9655 | 5.6574 | 0.75448 | 2.0495 | 2.5705 | 2.5705 | 2.5705 | 2.5705 | 1.1432 | 1.451 | 1.451 | 1.451 | 1.451 | 1.451
2020-04-30 20:00 | Winter | 0.59089 | 0.90856 | 1.3748 | 1.3748 | 1.3748 | 1.3748 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 2.1198 | 3.0577 | 3.6722 | 3.9956 | 4.6425 | 5.2894 | 0.68208 | 1.8528 | 2.3239 | 2.3239 | 2.3239 | 2.3239 | 1.0669 | 1.3542 | 1.3542 | 1.3542 | 1.3542 | 1.3542
2020-04-30 21:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 2.0386 | 2.9407 | 3.5316 | 3.8427 | 4.4648 | 5.0869 | 0.70113 | 1.9046 | 2.3888 | 2.3888 | 2.3888 | 2.3888 | 1.0098 | 1.2817 | 1.2817 | 1.2817 | 1.2817 | 1.2817
2020-04-30 22:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 1.8773 | 2.708 | 3.2522 | 3.5386 | 4.1115 | 4.6844 | 0.66303 | 1.8011 | 2.2589 | 2.2589 | 2.2589 | 2.2589 | 0.91459 | 1.1609 | 1.1609 | 1.1609 | 1.1609 | 1.1609
2020-04-30 23:00 | Winter | 0.60943 | 0.93708 | 1.418 | 1.418 | 1.418 | 1.418 | 0.40582 | 0.40582 | 0.40582 | 0.40582 | 0.40582 | 0.40582 | 1.7504 | 2.5249 | 3.0324 | 3.2994 | 3.8336 | 4.3677 | 0.62873 | 1.7079 | 2.1421 | 2.1421 | 2.1421 | 2.1421 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-05-01 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.42296 | 0.42296 | 0.42296 | 0.42296 | 0.42296 | 0.42296 | 1.6766 | 2.4185 | 2.9045 | 3.1603 | 3.672 | 4.1836 | 0.62873 | 1.7079 | 2.1421 | 2.1421 | 2.1421 | 2.1421 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-05-01 01:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.37724 | 0.37724 | 0.37724 | 0.37724 | 0.37724 | 0.37724 | 1.6576 | 2.391 | 2.8715 | 3.1244 | 3.6302 | 4.1361 | 0.5792 | 1.5733 | 1.9733 | 1.9733 | 1.9733 | 1.9733 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-05-01 02:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 1.5623 | 2.2536 | 2.7065 | 2.9449 | 3.4216 | 3.8984 | 0.57539 | 1.563 | 1.9603 | 1.9603 | 1.9603 | 1.9603 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-05-01 03:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 1.5814 | 2.2811 | 2.7395 | 2.9808 | 3.4633 | 3.9459 | 0.63254 | 1.7182 | 2.1551 | 2.1551 | 2.1551 | 2.1551 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-05-01 04:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 1.5814 | 2.2811 | 2.7395 | 2.9808 | 3.4633 | 3.9459 | 0.5792 | 1.5733 | 1.9733 | 1.9733 | 1.9733 | 1.9733 | 1.1313 | 1.4359 | 1.4359 | 1.4359 | 1.4359 | 1.4359
2020-05-01 05:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.57729 | 0.57729 | 0.57729 | 0.57729 | 0.57729 | 0.57729 | 1.7517 | 2.5267 | 3.0345 | 3.3018 | 3.8363 | 4.3708 | 0.67446 | 1.8321 | 2.2979 | 2.2979 | 2.2979 | 2.2979 | 1.4861 | 1.8863 | 1.8863 | 1.8863 | 1.8863 | 1.8863
2020-05-01 06:00 | Winter | 0.64216 | 0.98739 | 1.4941 | 1.4941 | 1.4941 | 1.4941 | 0.63445 | 0.63445 | 0.63445 | 0.63445 | 0.63445 | 0.63445 | 1.9099 | 2.755 | 3.3086 | 3.6 | 4.1829 | 4.7657 | 0.6516 | 1.77 | 2.22 | 2.22 | 2.22 | 2.22 | 1.8479 | 2.3455 | 2.3455 | 2.3455 | 2.3455 | 2.3455
2020-05-01 07:00 | Winter | 1.0516 | 1.617 | 2.4469 | 2.4469 | 2.4469 | 2.4469 | 0.76019 | 0.76019 | 0.76019 | 0.76019 | 0.76019 | 0.76019 | 2.2955 | 3.3112 | 3.9767 | 4.3269 | 5.0274 | 5.7279 | 0.78115 | 2.1219 | 2.6614 | 2.6614 | 2.6614 | 2.6614 | 2.1339 | 2.7085 | 2.7085 | 2.7085 | 2.7085 | 2.7085
2020-05-01 08:00 | Winter | 1.2194 | 1.8749 | 2.8371 | 2.8371 | 2.8371 | 2.8371 | 0.87451 | 0.87451 | 0.87451 | 0.87451 | 0.87451 | 0.87451 | 2.4768 | 3.5728 | 4.2908 | 4.6687 | 5.4245 | 6.1803 | 0.80783 | 2.1944 | 2.7523 | 2.7523 | 2.7523 | 2.7523 | 2.3816 | 3.0229 | 3.0229 | 3.0229 | 3.0229 | 3.0229
2020-05-01 09:00 | Winter | 1.1241 | 1.7284 | 2.6155 | 2.6155 | 2.6155 | 2.6155 | 0.90309 | 0.90309 | 0.90309 | 0.90309 | 0.90309 | 0.90309 | 2.4006 | 3.4628 | 4.1588 | 4.525 | 5.2576 | 5.9902 | 0.86117 | 2.3393 | 2.934 | 2.934 | 2.934 | 2.934 | 2.3244 | 2.9503 | 2.9503 | 2.9503 | 2.9503 | 2.9503
2020-05-01 10:00 | Winter | 1.105 | 1.6991 | 2.5711 | 2.5711 | 2.5711 | 2.5711 | 0.96882 | 0.96882 | 0.96882 | 0.96882 | 0.96882 | 0.96882 | 2.534 | 3.6552 | 4.3898 | 4.7764 | 5.5497 | 6.3229 | 0.80783 | 2.1944 | 2.7523 | 2.7523 | 2.7523 | 2.7523 | 2.3054 | 2.9261 | 2.9261 | 2.9261 | 2.9261 | 2.9261
2020-05-01 11:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 0.99168 | 0.99168 | 0.99168 | 0.99168 | 0.99168 | 0.99168 | 2.5721 | 3.7102 | 4.4558 | 4.8483 | 5.6331 | 6.418 | 0.81164 | 2.2047 | 2.7653 | 2.7653 | 2.7653 | 2.7653 | 2.3244 | 2.9503 | 2.9503 | 2.9503 | 2.9503 | 2.9503
2020-05-01 12:00 | Winter | 1.0288 | 1.582 | 2.3938 | 2.3938 | 2.3938 | 2.3938 | 1.166 | 1.166 | 1.166 | 1.166 | 1.166 | 1.166 | 2.534 | 3.6552 | 4.3898 | 4.7764 | 5.5497 | 6.3229 | 0.75448 | 2.0495 | 2.5705 | 2.5705 | 2.5705 | 2.5705 | 2.2291 | 2.8294 | 2.8294 | 2.8294 | 2.8294 | 2.8294
2020-05-01 13:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 1.1517 | 1.1517 | 1.1517 | 1.1517 | 1.1517 | 1.1517 | 2.4006 | 3.4628 | 4.1588 | 4.525 | 5.2576 | 5.9902 | 0.75448 | 2.0495 | 2.5705 | 2.5705 | 2.5705 | 2.5705 | 2.2101 | 2.8052 | 2.8052 | 2.8052 | 2.8052 | 2.8052
2020-05-01 14:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 1.0117 | 1.0117 | 1.0117 | 1.0117 | 1.0117 | 1.0117 | 2.4006 | 3.4628 | 4.1588 | 4.525 | 5.2576 | 5.9902 | 0.78115 | 2.1219 | 2.6614 | 2.6614 | 2.6614 | 2.6614 | 2.3244 | 2.9503 | 2.9503 | 2.9503 | 2.9503 | 2.9503
2020-05-01 15:00 | Winter | 1.0669 | 1.6405 | 2.4825 | 2.4825 | 2.4825 | 2.4825 | 0.89737 | 0.89737 | 0.89737 | 0.89737 | 0.89737 | 0.89737 | 2.3816 | 3.4353 | 4.1258 | 4.4891 | 5.2159 | 5.9426 | 0.7964 | 2.1633 | 2.7133 | 2.7133 | 2.7133 | 2.7133 | 2.2482 | 2.8536 | 2.8536 | 2.8536 | 2.8536 | 2.8536
2020-05-01 16:00 | Winter | 1.0288 | 1.582 | 2.3938 | 2.3938 | 2.3938 | 2.3938 | 0.90309 | 0.90309 | 0.90309 | 0.90309 | 0.90309 | 0.90309 | 2.4197 | 3.4903 | 4.1918 | 4.561 | 5.2993 | 6.0377 | 0.75448 | 2.0495 | 2.5705 | 2.5705 | 2.5705 | 2.5705 | 2.2291 | 2.8294 | 2.8294 | 2.8294 | 2.8294 | 2.8294
2020-05-01 17:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.80592 | 0.80592 | 0.80592 | 0.80592 | 0.80592 | 0.80592 | 2.5911 | 3.7377 | 4.4888 | 4.8842 | 5.6749 | 6.4656 | 0.76591 | 2.0805 | 2.6095 | 2.6095 | 2.6095 | 2.6095 | 2.0532 | 2.6061 | 2.6061 | 2.6061 | 2.6061 | 2.6061
2020-05-01 18:00 | Winter | 0.89579 | 1.3774 | 2.0843 | 2.0843 | 2.0843 | 2.0843 | 0.73171 | 0.73171 | 0.73171 | 0.73171 | 0.73171 | 0.73171 | 2.5555 | 3.6863 | 4.4271 | 4.8171 | 5.5969 | 6.3767 | 0.75829 | 2.0598 | 2.5835 | 2.5835 | 2.5835 | 2.5835 | 1.4867 | 1.887 | 1.887 | 1.887 | 1.887 | 1.887
2020-05-01 19:00 | Winter | 0.68589 | 1.0546 | 1.5959 | 1.5959 | 1.5959 | 1.5959 | 0.57443 | 0.57443 | 0.57443 | 0.57443 | 0.57443 | 0.57443 | 2.3625 | 3.4079 | 4.0927 | 4.4532 | 5.1741 | 5.8951 | 0.72018 | 1.9563 | 2.4537 | 2.4537 | 2.4537 | 2.4537 | 1.1117 | 1.4111 | 1.4111 | 1.4111 | 1.4111 | 1.4111
2020-05-01 20:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 2.2295 | 3.216 | 3.8624 | 4.2025 | 4.8829 | 5.5632 | 0.67446 | 1.8321 | 2.2979 | 2.2979 | 2.2979 | 2.2979 | 1.086 | 1.3784 | 1.3784 | 1.3784 | 1.3784 | 1.3784
2020-05-01 21:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 2.1343 | 3.0787 | 3.6975 | 4.0231 | 4.6744 | 5.3257 | 0.62873 | 1.7079 | 2.1421 | 2.1421 | 2.1421 | 2.1421 | 1.0288 | 1.3059 | 1.3059 | 1.3059 | 1.3059 | 1.3059
2020-05-01 22:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 2.0005 | 2.8857 | 3.4656 | 3.7709 | 4.3813 | 4.9918 | 0.64397 | 1.7493 | 2.194 | 2.194 | 2.194 | 2.194 | 0.93579 | 1.1878 | 1.1878 | 1.1878 | 1.1878 | 1.1878
2020-05-01 23:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 1.81 | 2.6109 | 3.1356 | 3.4117 | 3.9641 | 4.5164 | 0.59444 | 1.6147 | 2.0253 | 2.0253 | 2.0253 | 2.0253 | 0.91452 | 1.1608 | 1.1608 | 1.1608 | 1.1608 | 1.1608
2020-05-02 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.5087 | 0.5087 | 0.5087 | 0.5087 | 0.5087 | 0.5087 | 1.7338 | 2.5009 | 3.0036 | 3.2681 | 3.7972 | 4.3262 | 0.56014 | 1.5216 | 1.9084 | 1.9084 | 1.9084 | 1.9084 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-05-02 01:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.40296 | 0.40296 | 0.40296 | 0.40296 | 0.40296 | 0.40296 | 1.6957 | 2.446 | 2.9375 | 3.1963 | 3.7137 | 4.2311 | 0.58301 | 1.5837 | 1.9863 | 1.9863 | 1.9863 | 1.9863 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-05-02 02:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.37152 | 0.37152 | 0.37152 | 0.37152 | 0.37152 | 0.37152 | 1.6576 | 2.391 | 2.8715 | 3.1244 | 3.6302 | 4.1361 | 0.54871 | 1.4905 | 1.8695 | 1.8695 | 1.8695 | 1.8695 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-05-02 03:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 1.6766 | 2.4185 | 2.9045 | 3.1603 | 3.672 | 4.1836 | 0.53728 | 1.4595 | 1.8305 | 1.8305 | 1.8305 | 1.8305 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-05-02 04:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.43154 | 0.43154 | 0.43154 | 0.43154 | 0.43154 | 0.43154 | 1.6766 | 2.4185 | 2.9045 | 3.1603 | 3.672 | 4.1836 | 0.55252 | 1.5009 | 1.8825 | 1.8825 | 1.8825 | 1.8825 | 0.88557 | 1.124 | 1.124 | 1.124 | 1.124 | 1.124
2020-05-02 05:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.38581 | 0.38581 | 0.38581 | 0.38581 | 0.38581 | 0.38581 | 1.6766 | 2.4185 | 2.9045 | 3.1603 | 3.672 | 4.1836 | 0.51823 | 1.4077 | 1.7656 | 1.7656 | 1.7656 | 1.7656 | 0.95263 | 1.2092 | 1.2092 | 1.2092 | 1.2092 | 1.2092
2020-05-02 06:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 1.7147 | 2.4735 | 2.9705 | 3.2322 | 3.7554 | 4.2787 | 0.54097 | 1.4695 | 1.8431 | 1.8431 | 1.8431 | 1.8431 | 1.086 | 1.3784 | 1.3784 | 1.3784 | 1.3784 | 1.3784
2020-05-02 07:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.57157 | 0.57157 | 0.57157 | 0.57157 | 0.57157 | 0.57157 | 1.8215 | 2.6275 | 3.1555 | 3.4335 | 3.9893 | 4.5452 | 0.54871 | 1.4905 | 1.8695 | 1.8695 | 1.8695 | 1.8695 | 1.1622 | 1.4752 | 1.4752 | 1.4752 | 1.4752 | 1.4752
2020-05-02 08:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.56896 | 0.56896 | 0.56896 | 0.56896 | 0.56896 | 0.56896 | 1.9434 | 2.8032 | 3.3666 | 3.6631 | 4.2562 | 4.8492 | 0.56395 | 1.5319 | 1.9214 | 1.9214 | 1.9214 | 1.9214 | 1.3337 | 1.6928 | 1.6928 | 1.6928 | 1.6928 | 1.6928
2020-05-02 09:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.60301 | 0.60301 | 0.60301 | 0.60301 | 0.60301 | 0.60301 | 1.9624 | 2.8307 | 3.3996 | 3.699 | 4.2979 | 4.8967 | 0.60206 | 1.6354 | 2.0512 | 2.0512 | 2.0512 | 2.0512 | 1.3337 | 1.6928 | 1.6928 | 1.6928 | 1.6928 | 1.6928
2020-05-02 10:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.55728 | 0.55728 | 0.55728 | 0.55728 | 0.55728 | 0.55728 | 2.0577 | 2.9681 | 3.5647 | 3.8786 | 4.5065 | 5.1344 | 0.5792 | 1.5733 | 1.9733 | 1.9733 | 1.9733 | 1.9733 | 1.1622 | 1.4752 | 1.4752 | 1.4752 | 1.4752 | 1.4752
2020-05-02 11:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.56014 | 0.56014 | 0.56014 | 0.56014 | 0.56014 | 0.56014 | 2.0386 | 2.9407 | 3.5316 | 3.8427 | 4.4648 | 5.0869 | 0.58682 | 1.594 | 1.9993 | 1.9993 | 1.9993 | 1.9993 | 1.1622 | 1.4752 | 1.4752 | 1.4752 | 1.4752 | 1.4752
2020-05-02 12:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.55157 | 0.55157 | 0.55157 | 0.55157 | 0.55157 | 0.55157 | 2.0577 | 2.9681 | 3.5647 | 3.8786 | 4.5065 | 5.1344 | 0.57539 | 1.563 | 1.9603 | 1.9603 | 1.9603 | 1.9603 | 1.1622 | 1.4752 | 1.4752 | 1.4752 | 1.4752 | 1.4752
2020-05-02 13:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.55728 | 0.55728 | 0.55728 | 0.55728 | 0.55728 | 0.55728 | 2.1148 | 3.0506 | 3.6637 | 3.9863 | 4.6317 | 5.277 | 0.62492 | 1.6975 | 2.1291 | 2.1291 | 2.1291 | 2.1291 | 1.106 | 1.4038 | 1.4038 | 1.4038 | 1.4038 | 1.4038
2020-05-02 14:00 | Winter | 0.60471 | 0.92982 | 1.407 | 1.407 | 1.407 | 1.407 | 0.54585 | 0.54585 | 0.54585 | 0.54585 | 0.54585 | 0.54585 | 2.1339 | 3.0781 | 3.6967 | 4.0223 | 4.6734 | 5.3246 | 0.59444 | 1.6147 | 2.0253 | 2.0253 | 2.0253 | 2.0253 | 1.1432 | 1.451 | 1.451 | 1.451 | 1.451 | 1.451
2020-05-02 15:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.70304 | 0.70304 | 0.70304 | 0.70304 | 0.70304 | 0.70304 | 2.1339 | 3.0781 | 3.6967 | 4.0223 | 4.6734 | 5.3246 | 0.58301 | 1.5837 | 1.9863 | 1.9863 | 1.9863 | 1.9863 | 1.2194 | 1.5477 | 1.5477 | 1.5477 | 1.5477 | 1.5477
2020-05-02 16:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.63445 | 0.63445 | 0.63445 | 0.63445 | 0.63445 | 0.63445 | 2.172 | 3.133 | 3.7627 | 4.0941 | 4.7569 | 5.4197 | 0.62873 | 1.7079 | 2.1421 | 2.1421 | 2.1421 | 2.1421 | 1.1432 | 1.451 | 1.451 | 1.451 | 1.451 | 1.451
2020-05-02 17:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.63159 | 0.63159 | 0.63159 | 0.63159 | 0.63159 | 0.63159 | 2.3625 | 3.4079 | 4.0927 | 4.4532 | 5.1741 | 5.8951 | 0.70875 | 1.9253 | 2.4147 | 2.4147 | 2.4147 | 2.4147 | 1.1123 | 1.4118 | 1.4118 | 1.4118 | 1.4118 | 1.4118
2020-05-02 18:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.59444 | 0.59444 | 0.59444 | 0.59444 | 0.59444 | 0.59444 | 2.4387 | 3.5178 | 4.2248 | 4.5969 | 5.3411 | 6.0852 | 0.63635 | 1.7286 | 2.1681 | 2.1681 | 2.1681 | 2.1681 | 0.99073 | 1.2575 | 1.2575 | 1.2575 | 1.2575 | 1.2575
2020-05-02 19:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.54585 | 0.54585 | 0.54585 | 0.54585 | 0.54585 | 0.54585 | 2.3435 | 3.3804 | 4.0597 | 4.4173 | 5.1324 | 5.8475 | 0.65922 | 1.7907 | 2.246 | 2.246 | 2.246 | 2.246 | 0.97168 | 1.2333 | 1.2333 | 1.2333 | 1.2333 | 1.2333
2020-05-02 20:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 2.191 | 3.1605 | 3.7957 | 4.13 | 4.7986 | 5.4672 | 0.67827 | 1.8425 | 2.3109 | 2.3109 | 2.3109 | 2.3109 | 0.95263 | 1.2092 | 1.2092 | 1.2092 | 1.2092 | 1.2092
2020-05-02 21:00 | Winter | 0.5821 | 0.89505 | 1.3544 | 1.3544 | 1.3544 | 1.3544 | 0.41439 | 0.41439 | 0.41439 | 0.41439 | 0.41439 | 0.41439 | 2.0958 | 3.0231 | 3.6307 | 3.9504 | 4.59 | 5.2295 | 0.6516 | 1.77 | 2.22 | 2.22 | 2.22 | 2.22 | 0.93358 | 1.185 | 1.185 | 1.185 | 1.185 | 1.185
2020-05-02 22:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.34866 | 0.34866 | 0.34866 | 0.34866 | 0.34866 | 0.34866 | 2.0958 | 3.0231 | 3.6307 | 3.9504 | 4.59 | 5.2295 | 0.6173 | 1.6768 | 2.1032 | 2.1032 | 2.1032 | 2.1032 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-05-02 23:00 | Winter | 0.59116 | 0.90898 | 1.3755 | 1.3755 | 1.3755 | 1.3755 | 0.38581 | 0.38581 | 0.38581 | 0.38581 | 0.38581 | 0.38581 | 1.9053 | 2.7483 | 3.3006 | 3.5913 | 4.1727 | 4.7541 | 0.59444 | 1.6147 | 2.0253 | 2.0253 | 2.0253 | 2.0253 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-05-03 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.48869 | 0.48869 | 0.48869 | 0.48869 | 0.48869 | 0.48869 | 1.7528 | 2.5284 | 3.0366 | 3.304 | 3.8389 | 4.3738 | 0.5449 | 1.4802 | 1.8565 | 1.8565 | 1.8565 | 1.8565 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-05-03 01:00 | Winter | 0.55282 | 0.85003 | 1.2863 | 1.2863 | 1.2863 | 1.2863 | 0.39153 | 0.39153 | 0.39153 | 0.39153 | 0.39153 | 0.39153 | 1.6783 | 2.421 | 2.9075 | 3.1636 | 3.6757 | 4.1879 | 0.55633 | 1.5112 | 1.8954 | 1.8954 | 1.8954 | 1.8954 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-05-03 02:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.39438 | 0.39438 | 0.39438 | 0.39438 | 0.39438 | 0.39438 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.53728 | 1.4595 | 1.8305 | 1.8305 | 1.8305 | 1.8305 | 0.81985 | 1.0406 | 1.0406 | 1.0406 | 1.0406 | 1.0406
2020-05-03 03:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.53347 | 1.4491 | 1.8175 | 1.8175 | 1.8175 | 1.8175 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-05-03 04:00 | Winter | 0.60928 | 0.93684 | 1.4176 | 1.4176 | 1.4176 | 1.4176 | 0.41439 | 0.41439 | 0.41439 | 0.41439 | 0.41439 | 0.41439 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.53347 | 1.4491 | 1.8175 | 1.8175 | 1.8175 | 1.8175 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-05-03 05:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.51823 | 1.4077 | 1.7656 | 1.7656 | 1.7656 | 1.7656 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-05-03 06:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.49155 | 0.49155 | 0.49155 | 0.49155 | 0.49155 | 0.49155 | 1.6957 | 2.446 | 2.9375 | 3.1963 | 3.7137 | 4.2311 | 0.56395 | 1.5319 | 1.9214 | 1.9214 | 1.9214 | 1.9214 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-05-03 07:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.51442 | 0.51442 | 0.51442 | 0.51442 | 0.51442 | 0.51442 | 1.7719 | 2.5559 | 3.0696 | 3.3399 | 3.8806 | 4.4213 | 0.53728 | 1.4595 | 1.8305 | 1.8305 | 1.8305 | 1.8305 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-05-03 08:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.51442 | 0.51442 | 0.51442 | 0.51442 | 0.51442 | 0.51442 | 1.9053 | 2.7483 | 3.3006 | 3.5913 | 4.1727 | 4.7541 | 0.56014 | 1.5216 | 1.9084 | 1.9084 | 1.9084 | 1.9084 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-05-03 09:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.48584 | 0.48584 | 0.48584 | 0.48584 | 0.48584 | 0.48584 | 1.9053 | 2.7483 | 3.3006 | 3.5913 | 4.1727 | 4.7541 | 0.56395 | 1.5319 | 1.9214 | 1.9214 | 1.9214 | 1.9214 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-05-03 10:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.48869 | 0.48869 | 0.48869 | 0.48869 | 0.48869 | 0.48869 | 1.9624 | 2.8307 | 3.3996 | 3.699 | 4.2979 | 4.8967 | 0.56776 | 1.5423 | 1.9344 | 1.9344 | 1.9344 | 1.9344 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-05-03 11:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.50584 | 0.50584 | 0.50584 | 0.50584 | 0.50584 | 0.50584 | 1.9434 | 2.8032 | 3.3666 | 3.6631 | 4.2562 | 4.8492 | 0.51061 | 1.387 | 1.7396 | 1.7396 | 1.7396 | 1.7396 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-05-03 12:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.39153 | 0.39153 | 0.39153 | 0.39153 | 0.39153 | 0.39153 | 2.0005 | 2.8857 | 3.4656 | 3.7709 | 4.3813 | 4.9918 | 0.58301 | 1.5837 | 1.9863 | 1.9863 | 1.9863 | 1.9863 | 0.80116 | 1.0169 | 1.0169 | 1.0169 | 1.0169 | 1.0169
2020-05-03 13:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.42582 | 0.42582 | 0.42582 | 0.42582 | 0.42582 | 0.42582 | 1.9243 | 2.7758 | 3.3336 | 3.6272 | 4.2144 | 4.8016 | 0.5449 | 1.4802 | 1.8565 | 1.8565 | 1.8565 | 1.8565 | 0.80021 | 1.0157 | 1.0157 | 1.0157 | 1.0157 | 1.0157
2020-05-03 14:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 1.9815 | 2.8582 | 3.4326 | 3.735 | 4.3396 | 4.9443 | 0.47631 | 1.2939 | 1.6228 | 1.6228 | 1.6228 | 1.6228 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-05-03 15:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 1.9053 | 2.7483 | 3.3006 | 3.5913 | 4.1727 | 4.7541 | 0.51442 | 1.3974 | 1.7526 | 1.7526 | 1.7526 | 1.7526 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-05-03 16:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.43016 | 0.43016 | 0.43016 | 0.43016 | 0.43016 | 0.43016 | 1.9624 | 2.8307 | 3.3996 | 3.699 | 4.2979 | 4.8967 | 0.55633 | 1.5112 | 1.8954 | 1.8954 | 1.8954 | 1.8954 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-05-03 17:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.43154 | 0.43154 | 0.43154 | 0.43154 | 0.43154 | 0.43154 | 2.1339 | 3.0781 | 3.6967 | 4.0223 | 4.6734 | 5.3246 | 0.6173 | 1.6768 | 2.1032 | 2.1032 | 2.1032 | 2.1032 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-05-03 18:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 2.172 | 3.133 | 3.7627 | 4.0941 | 4.7569 | 5.4197 | 0.63254 | 1.7182 | 2.1551 | 2.1551 | 2.1551 | 2.1551 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-05-03 19:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.52299 | 0.52299 | 0.52299 | 0.52299 | 0.52299 | 0.52299 | 2.172 | 3.133 | 3.7627 | 4.0941 | 4.7569 | 5.4197 | 0.61349 | 1.6665 | 2.0902 | 2.0902 | 2.0902 | 2.0902 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-05-03 20:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 2.1529 | 3.1056 | 3.7297 | 4.0582 | 4.7151 | 5.3721 | 0.61349 | 1.6665 | 2.0902 | 2.0902 | 2.0902 | 2.0902 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-05-03 21:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 2.0404 | 2.9432 | 3.5347 | 3.846 | 4.4686 | 5.0912 | 0.64016 | 1.7389 | 2.1811 | 2.1811 | 2.1811 | 2.1811 | 0.85813 | 1.0892 | 1.0892 | 1.0892 | 1.0892 | 1.0892
2020-05-03 22:00 | Winter | 0.58929 | 0.90611 | 1.3711 | 1.3711 | 1.3711 | 1.3711 | 0.34866 | 0.34866 | 0.34866 | 0.34866 | 0.34866 | 0.34866 | 1.9243 | 2.7758 | 3.3336 | 3.6272 | 4.2144 | 4.8016 | 0.61349 | 1.6665 | 2.0902 | 2.0902 | 2.0902 | 2.0902 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-05-03 23:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.39724 | 0.39724 | 0.39724 | 0.39724 | 0.39724 | 0.39724 | 1.8481 | 2.6658 | 3.2016 | 3.4836 | 4.0475 | 4.6115 | 0.56776 | 1.5423 | 1.9344 | 1.9344 | 1.9344 | 1.9344 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-05-04 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 1.6957 | 2.446 | 2.9375 | 3.1963 | 3.7137 | 4.2311 | 0.56395 | 1.5319 | 1.9214 | 1.9214 | 1.9214 | 1.9214 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-05-04 01:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.40296 | 0.40296 | 0.40296 | 0.40296 | 0.40296 | 0.40296 | 1.6576 | 2.391 | 2.8715 | 3.1244 | 3.6302 | 4.1361 | 0.54109 | 1.4698 | 1.8435 | 1.8435 | 1.8435 | 1.8435 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-05-04 02:00 | Winter | 0.58374 | 0.89757 | 1.3582 | 1.3582 | 1.3582 | 1.3582 | 0.41439 | 0.41439 | 0.41439 | 0.41439 | 0.41439 | 0.41439 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.53347 | 1.4491 | 1.8175 | 1.8175 | 1.8175 | 1.8175 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-05-04 03:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 1.6195 | 2.336 | 2.8055 | 3.0526 | 3.5468 | 4.041 | 0.56776 | 1.5423 | 1.9344 | 1.9344 | 1.9344 | 1.9344 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-05-04 04:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.43154 | 0.43154 | 0.43154 | 0.43154 | 0.43154 | 0.43154 | 1.7334 | 2.5004 | 3.0029 | 3.2674 | 3.7963 | 4.3253 | 0.51823 | 1.4077 | 1.7656 | 1.7656 | 1.7656 | 1.7656 | 1.1432 | 1.451 | 1.451 | 1.451 | 1.451 | 1.451
2020-05-04 05:00 | Winter | 0.76196 | 1.1716 | 1.7729 | 1.7729 | 1.7729 | 1.7729 | 0.60873 | 0.60873 | 0.60873 | 0.60873 | 0.60873 | 0.60873 | 1.8024 | 2.5999 | 3.1224 | 3.3974 | 3.9474 | 4.4974 | 0.63635 | 1.7286 | 2.1681 | 2.1681 | 2.1681 | 2.1681 | 1.4937 | 1.8959 | 1.8959 | 1.8959 | 1.8959 | 1.8959
2020-05-04 06:00 | Winter | 0.95275 | 1.465 | 2.2168 | 2.2168 | 2.2168 | 2.2168 | 0.71083 | 0.71083 | 0.71083 | 0.71083 | 0.71083 | 0.71083 | 1.9992 | 2.8838 | 3.4634 | 3.7685 | 4.3785 | 4.9886 | 0.64397 | 1.7493 | 2.194 | 2.194 | 2.194 | 2.194 | 1.8154 | 2.3042 | 2.3042 | 2.3042 | 2.3042 | 2.3042
2020-05-04 07:00 | Winter | 1.1241 | 1.7284 | 2.6155 | 2.6155 | 2.6155 | 2.6155 | 1.0803 | 1.0803 | 1.0803 | 1.0803 | 1.0803 | 1.0803 | 2.224 | 3.2081 | 3.8528 | 4.1921 | 4.8708 | 5.5494 | 0.724 | 1.9667 | 2.4667 | 2.4667 | 2.4667 | 2.4667 | 2.0958 | 2.6601 | 2.6601 | 2.6601 | 2.6601 | 2.6601
2020-05-04 08:00 | Winter | 1.1622 | 1.787 | 2.7041 | 2.7041 | 2.7041 | 2.7041 | 1.1289 | 1.1289 | 1.1289 | 1.1289 | 1.1289 | 1.1289 | 2.4006 | 3.4628 | 4.1588 | 4.525 | 5.2576 | 5.9902 | 0.7964 | 2.1633 | 2.7133 | 2.7133 | 2.7133 | 2.7133 | 2.2482 | 2.8536 | 2.8536 | 2.8536 | 2.8536 | 2.8536
2020-05-04 09:00 | Winter | 1.1813 | 1.8163 | 2.7485 | 2.7485 | 2.7485 | 2.7485 | 1.206 | 1.206 | 1.206 | 1.206 | 1.206 | 1.206 | 2.3435 | 3.3804 | 4.0597 | 4.4173 | 5.1324 | 5.8475 | 0.73162 | 1.9874 | 2.4926 | 2.4926 | 2.4926 | 2.4926 | 2.3816 | 3.0229 | 3.0229 | 3.0229 | 3.0229 | 3.0229
2020-05-04 10:00 | Winter | 1.1241 | 1.7284 | 2.6155 | 2.6155 | 2.6155 | 2.6155 | 1.2089 | 1.2089 | 1.2089 | 1.2089 | 1.2089 | 1.2089 | 2.4387 | 3.5178 | 4.2248 | 4.5969 | 5.3411 | 6.0852 | 0.74305 | 2.0184 | 2.5316 | 2.5316 | 2.5316 | 2.5316 | 2.2863 | 2.902 | 2.902 | 2.902 | 2.902 | 2.902
2020-05-04 11:00 | Winter | 1.105 | 1.6991 | 2.5711 | 2.5711 | 2.5711 | 2.5711 | 1.0431 | 1.0431 | 1.0431 | 1.0431 | 1.0431 | 1.0431 | 2.4359 | 3.5137 | 4.2198 | 4.5915 | 5.3348 | 6.0781 | 0.76591 | 2.0805 | 2.6095 | 2.6095 | 2.6095 | 2.6095 | 2.3244 | 2.9503 | 2.9503 | 2.9503 | 2.9503 | 2.9503
2020-05-04 12:00 | Winter | 1.1432 | 1.7577 | 2.6598 | 2.6598 | 2.6598 | 2.6598 | 1.0117 | 1.0117 | 1.0117 | 1.0117 | 1.0117 | 1.0117 | 2.3435 | 3.3804 | 4.0597 | 4.4173 | 5.1324 | 5.8475 | 0.75448 | 2.0495 | 2.5705 | 2.5705 | 2.5705 | 2.5705 | 2.2291 | 2.8294 | 2.8294 | 2.8294 | 2.8294 | 2.8294
2020-05-04 13:00 | Winter | 1.1432 | 1.7577 | 2.6598 | 2.6598 | 2.6598 | 2.6598 | 0.91738 | 0.91738 | 0.91738 | 0.91738 | 0.91738 | 0.91738 | 2.3625 | 3.4079 | 4.0927 | 4.4532 | 5.1741 | 5.8951 | 0.74686 | 2.0288 | 2.5446 | 2.5446 | 2.5446 | 2.5446 | 2.191 | 2.781 | 2.781 | 2.781 | 2.781 | 2.781
2020-05-04 14:00 | Winter | 1.086 | 1.6698 | 2.5267 | 2.5267 | 2.5267 | 2.5267 | 0.89737 | 0.89737 | 0.89737 | 0.89737 | 0.89737 | 0.89737 | 2.3054 | 3.3254 | 3.9937 | 4.3455 | 5.049 | 5.7525 | 0.724 | 1.9667 | 2.4667 | 2.4667 | 2.4667 | 2.4667 | 2.1144 | 2.6838 | 2.6838 | 2.6838 | 2.6838 | 2.6838
2020-05-04 15:00 | Winter | 1.086 | 1.6698 | 2.5268 | 2.5268 | 2.5268 | 2.5268 | 0.8002 | 0.8002 | 0.8002 | 0.8002 | 0.8002 | 0.8002 | 2.2668 | 3.2699 | 3.927 | 4.2729 | 4.9646 | 5.6563 | 0.69732 | 1.8942 | 2.3758 | 2.3758 | 2.3758 | 2.3758 | 2.0577 | 2.6118 | 2.6118 | 2.6118 | 2.6118 | 2.6118
2020-05-04 16:00 | Winter | 1.105 | 1.6991 | 2.5711 | 2.5711 | 2.5711 | 2.5711 | 0.7802 | 0.7802 | 0.7802 | 0.7802 | 0.7802 | 0.7802 | 2.2673 | 3.2705 | 3.9277 | 4.2736 | 4.9655 | 5.6574 | 0.70875 | 1.9253 | 2.4147 | 2.4147 | 2.4147 | 2.4147 | 2.0386 | 2.5876 | 2.5876 | 2.5876 | 2.5876 | 2.5876
2020-05-04 17:00 | Winter | 1.086 | 1.6698 | 2.5268 | 2.5268 | 2.5268 | 2.5268 | 0.7802 | 0.7802 | 0.7802 | 0.7802 | 0.7802 | 0.7802 | 2.4006 | 3.4628 | 4.1588 | 4.525 | 5.2576 | 5.9902 | 0.69351 | 1.8839 | 2.3628 | 2.3628 | 2.3628 | 2.3628 | 1.8862 | 2.3941 | 2.3941 | 2.3941 | 2.3941 | 2.3941
2020-05-04 18:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.60015 | 0.60015 | 0.60015 | 0.60015 | 0.60015 | 0.60015 | 2.3178 | 3.3434 | 4.0153 | 4.3689 | 5.0762 | 5.7835 | 0.67065 | 1.8218 | 2.2849 | 2.2849 | 2.2849 | 2.2849 | 1.3791 | 1.7505 | 1.7505 | 1.7505 | 1.7505 | 1.7505
2020-05-04 19:00 | Winter | 0.64779 | 0.99605 | 1.5072 | 1.5072 | 1.5072 | 1.5072 | 0.5287 | 0.5287 | 0.5287 | 0.5287 | 0.5287 | 0.5287 | 2.2291 | 3.2155 | 3.8617 | 4.2018 | 4.8821 | 5.5623 | 0.63635 | 1.7286 | 2.1681 | 2.1681 | 2.1681 | 2.1681 | 1.1046 | 1.402 | 1.402 | 1.402 | 1.402 | 1.402
2020-05-04 20:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.38581 | 0.38581 | 0.38581 | 0.38581 | 0.38581 | 0.38581 | 2.1339 | 3.0781 | 3.6967 | 4.0223 | 4.6734 | 5.3246 | 0.64397 | 1.7493 | 2.194 | 2.194 | 2.194 | 2.194 | 0.99073 | 1.2575 | 1.2575 | 1.2575 | 1.2575 | 1.2575
2020-05-04 21:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.33151 | 0.33151 | 0.33151 | 0.33151 | 0.33151 | 0.33151 | 2.0575 | 2.9679 | 3.5644 | 3.8783 | 4.5062 | 5.134 | 0.63635 | 1.7286 | 2.1681 | 2.1681 | 2.1681 | 2.1681 | 0.93358 | 1.185 | 1.185 | 1.185 | 1.185 | 1.185
2020-05-04 22:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.37438 | 0.37438 | 0.37438 | 0.37438 | 0.37438 | 0.37438 | 2.0577 | 2.9681 | 3.5647 | 3.8786 | 4.5065 | 5.1344 | 0.56395 | 1.5319 | 1.9214 | 1.9214 | 1.9214 | 1.9214 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-05-04 23:00 | Winter | 0.58782 | 0.90384 | 1.3677 | 1.3677 | 1.3677 | 1.3677 | 0.38009 | 0.38009 | 0.38009 | 0.38009 | 0.38009 | 0.38009 | 1.7528 | 2.5284 | 3.0366 | 3.304 | 3.8389 | 4.3738 | 0.5449 | 1.4802 | 1.8565 | 1.8565 | 1.8565 | 1.8565 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-05-05 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.40296 | 0.40296 | 0.40296 | 0.40296 | 0.40296 | 0.40296 | 1.7338 | 2.5009 | 3.0036 | 3.2681 | 3.7972 | 4.3262 | 0.57157 | 1.5526 | 1.9474 | 1.9474 | 1.9474 | 1.9474 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-05-05 01:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.4001 | 0.4001 | 0.4001 | 0.4001 | 0.4001 | 0.4001 | 1.6576 | 2.391 | 2.8715 | 3.1244 | 3.6302 | 4.1361 | 0.5068 | 1.3767 | 1.7267 | 1.7267 | 1.7267 | 1.7267 | 0.83971 | 1.0658 | 1.0658 | 1.0658 | 1.0658 | 1.0658
2020-05-05 02:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 1.5814 | 2.2811 | 2.7395 | 2.9808 | 3.4633 | 3.9459 | 0.55252 | 1.5009 | 1.8825 | 1.8825 | 1.8825 | 1.8825 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-05-05 03:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 1.5623 | 2.2536 | 2.7065 | 2.9449 | 3.4216 | 3.8984 | 0.5068 | 1.3767 | 1.7267 | 1.7267 | 1.7267 | 1.7267 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-05-05 04:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.40582 | 0.40582 | 0.40582 | 0.40582 | 0.40582 | 0.40582 | 1.6195 | 2.336 | 2.8055 | 3.0526 | 3.5468 | 4.041 | 0.55252 | 1.5009 | 1.8825 | 1.8825 | 1.8825 | 1.8825 | 1.1241 | 1.4268 | 1.4268 | 1.4268 | 1.4268 | 1.4268
2020-05-05 05:00 | Winter | 0.62853 | 0.96644 | 1.4624 | 1.4624 | 1.4624 | 1.4624 | 0.50298 | 0.50298 | 0.50298 | 0.50298 | 0.50298 | 0.50298 | 1.7909 | 2.5834 | 3.1026 | 3.3758 | 3.9223 | 4.4688 | 0.59444 | 1.6147 | 2.0253 | 2.0253 | 2.0253 | 2.0253 | 1.4703 | 1.8662 | 1.8662 | 1.8662 | 1.8662 | 1.8662
2020-05-05 06:00 | Winter | 0.80021 | 1.2304 | 1.8619 | 1.8619 | 1.8619 | 1.8619 | 0.70589 | 0.70589 | 0.70589 | 0.70589 | 0.70589 | 0.70589 | 2.0196 | 2.9132 | 3.4986 | 3.8068 | 4.4231 | 5.0393 | 0.62873 | 1.7079 | 2.1421 | 2.1421 | 2.1421 | 2.1421 | 1.6952 | 2.1516 | 2.1516 | 2.1516 | 2.1516 | 2.1516
2020-05-05 07:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 0.84021 | 0.84021 | 0.84021 | 0.84021 | 0.84021 | 0.84021 | 2.2291 | 3.2155 | 3.8617 | 4.2018 | 4.8821 | 5.5623 | 0.70875 | 1.9253 | 2.4147 | 2.4147 | 2.4147 | 2.4147 | 2.172 | 2.7569 | 2.7569 | 2.7569 | 2.7569 | 2.7569
2020-05-05 08:00 | Winter | 1.0669 | 1.6405 | 2.4825 | 2.4825 | 2.4825 | 2.4825 | 0.90023 | 0.90023 | 0.90023 | 0.90023 | 0.90023 | 0.90023 | 2.3054 | 3.3254 | 3.9937 | 4.3455 | 5.049 | 5.7525 | 0.76972 | 2.0909 | 2.6225 | 2.6225 | 2.6225 | 2.6225 | 2.4578 | 3.1196 | 3.1196 | 3.1196 | 3.1196 | 3.1196
2020-05-05 09:00 | Winter | 1.1241 | 1.7284 | 2.6155 | 2.6155 | 2.6155 | 2.6155 | 0.9631 | 0.9631 | 0.9631 | 0.9631 | 0.9631 | 0.9631 | 2.4197 | 3.4903 | 4.1918 | 4.561 | 5.2993 | 6.0377 | 0.78496 | 2.1323 | 2.6744 | 2.6744 | 2.6744 | 2.6744 | 2.3447 | 2.9761 | 2.9761 | 2.9761 | 2.9761 | 2.9761
2020-05-05 10:00 | Winter | 1.105 | 1.6991 | 2.5711 | 2.5711 | 2.5711 | 2.5711 | 0.90309 | 0.90309 | 0.90309 | 0.90309 | 0.90309 | 0.90309 | 2.4387 | 3.5178 | 4.2248 | 4.5969 | 5.3411 | 6.0852 | 0.75448 | 2.0495 | 2.5705 | 2.5705 | 2.5705 | 2.5705 | 2.3625 | 2.9987 | 2.9987 | 2.9987 | 2.9987 | 2.9987
2020-05-05 11:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 0.85165 | 0.85165 | 0.85165 | 0.85165 | 0.85165 | 0.85165 | 2.3556 | 3.398 | 4.0809 | 4.4403 | 5.1591 | 5.8779 | 0.65922 | 1.7907 | 2.246 | 2.246 | 2.246 | 2.246 | 2.2673 | 2.8778 | 2.8778 | 2.8778 | 2.8778 | 2.8778
2020-05-05 12:00 | Winter | 1.0669 | 1.6405 | 2.4825 | 2.4825 | 2.4825 | 2.4825 | 0.79735 | 0.79735 | 0.79735 | 0.79735 | 0.79735 | 0.79735 | 2.4387 | 3.5178 | 4.2248 | 4.5969 | 5.3411 | 6.0852 | 0.64779 | 1.7596 | 2.207 | 2.207 | 2.207 | 2.207 | 2.3054 | 2.9261 | 2.9261 | 2.9261 | 2.9261 | 2.9261
2020-05-05 13:00 | Winter | 1.086 | 1.6698 | 2.5268 | 2.5268 | 2.5268 | 2.5268 | 0.81735 | 0.81735 | 0.81735 | 0.81735 | 0.81735 | 0.81735 | 2.4387 | 3.5178 | 4.2248 | 4.5969 | 5.3411 | 6.0852 | 0.64779 | 1.7596 | 2.207 | 2.207 | 2.207 | 2.207 | 2.191 | 2.781 | 2.781 | 2.781 | 2.781 | 2.781
2020-05-05 14:00 | Winter | 1.086 | 1.6698 | 2.5268 | 2.5268 | 2.5268 | 2.5268 | 0.80878 | 0.80878 | 0.80878 | 0.80878 | 0.80878 | 0.80878 | 2.3872 | 3.4434 | 4.1355 | 4.4997 | 5.2281 | 5.9566 | 0.61349 | 1.6665 | 2.0902 | 2.0902 | 2.0902 | 2.0902 | 2.1148 | 2.6843 | 2.6843 | 2.6843 | 2.6843 | 2.6843
2020-05-05 15:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 0.80306 | 0.80306 | 0.80306 | 0.80306 | 0.80306 | 0.80306 | 2.3435 | 3.3804 | 4.0597 | 4.4173 | 5.1324 | 5.8475 | 0.62492 | 1.6975 | 2.1291 | 2.1291 | 2.1291 | 2.1291 | 2.0958 | 2.6601 | 2.6601 | 2.6601 | 2.6601 | 2.6601
2020-05-05 16:00 | Winter | 1.105 | 1.6991 | 2.5711 | 2.5711 | 2.5711 | 2.5711 | 0.78306 | 0.78306 | 0.78306 | 0.78306 | 0.78306 | 0.78306 | 2.2482 | 3.243 | 3.8947 | 4.2377 | 4.9238 | 5.6098 | 0.64397 | 1.7493 | 2.194 | 2.194 | 2.194 | 2.194 | 2.0958 | 2.6601 | 2.6601 | 2.6601 | 2.6601 | 2.6601
2020-05-05 17:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.73583 | 0.73583 | 0.73583 | 0.73583 | 0.73583 | 0.73583 | 2.4197 | 3.4903 | 4.1918 | 4.561 | 5.2993 | 6.0377 | 0.65541 | 1.7803 | 2.233 | 2.233 | 2.233 | 2.233 | 1.9815 | 2.515 | 2.515 | 2.515 | 2.515 | 2.515
2020-05-05 18:00 | Winter | 0.87878 | 1.3512 | 2.0447 | 2.0447 | 2.0447 | 2.0447 | 0.68017 | 0.68017 | 0.68017 | 0.68017 | 0.68017 | 0.68017 | 2.4197 | 3.4903 | 4.1918 | 4.561 | 5.2993 | 6.0377 | 0.67065 | 1.8218 | 2.2849 | 2.2849 | 2.2849 | 2.2849 | 1.4191 | 1.8012 | 1.8012 | 1.8012 | 1.8012 | 1.8012
2020-05-05 19:00 | Winter | 0.66684 | 1.0253 | 1.5515 | 1.5515 | 1.5515 | 1.5515 | 0.55728 | 0.55728 | 0.55728 | 0.55728 | 0.55728 | 0.55728 | 2.2873 | 3.2993 | 3.9624 | 4.3114 | 5.0093 | 5.7073 | 0.58682 | 1.594 | 1.9993 | 1.9993 | 1.9993 | 1.9993 | 1.1057 | 1.4035 | 1.4035 | 1.4035 | 1.4035 | 1.4035
2020-05-05 20:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.37724 | 0.37724 | 0.37724 | 0.37724 | 0.37724 | 0.37724 | 2.1266 | 3.0675 | 3.684 | 4.0084 | 4.6574 | 5.3063 | 0.55252 | 1.5009 | 1.8825 | 1.8825 | 1.8825 | 1.8825 | 1.0032 | 1.2733 | 1.2733 | 1.2733 | 1.2733 | 1.2733
2020-05-05 21:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.41153 | 0.41153 | 0.41153 | 0.41153 | 0.41153 | 0.41153 | 2.0386 | 2.9407 | 3.5316 | 3.8427 | 4.4648 | 5.0869 | 0.56395 | 1.5319 | 1.9214 | 1.9214 | 1.9214 | 1.9214 | 0.91482 | 1.1612 | 1.1612 | 1.1612 | 1.1612 | 1.1612
2020-05-05 22:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.40582 | 0.40582 | 0.40582 | 0.40582 | 0.40582 | 0.40582 | 2.0196 | 2.9132 | 3.4986 | 3.8068 | 4.4231 | 5.0393 | 0.5792 | 1.5733 | 1.9733 | 1.9733 | 1.9733 | 1.9733 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-05-05 23:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.41439 | 0.41439 | 0.41439 | 0.41439 | 0.41439 | 0.41439 | 1.8865 | 2.7212 | 3.2681 | 3.556 | 4.1316 | 4.7073 | 0.50885 | 1.3822 | 1.7336 | 1.7336 | 1.7336 | 1.7336 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-05-06 | Winter | 0.62468 | 0.96052 | 1.4535 | 1.4535 | 1.4535 | 1.4535 | 0.36866 | 0.36866 | 0.36866 | 0.36866 | 0.36866 | 0.36866 | 1.81 | 2.6109 | 3.1356 | 3.4117 | 3.9641 | 4.5164 | 0.51061 | 1.387 | 1.7396 | 1.7396 | 1.7396 | 1.7396 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-05-06 01:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.36866 | 0.36866 | 0.36866 | 0.36866 | 0.36866 | 0.36866 | 1.7719 | 2.5559 | 3.0696 | 3.3399 | 3.8806 | 4.4213 | 0.48393 | 1.3146 | 1.6488 | 1.6488 | 1.6488 | 1.6488 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-05-06 02:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.37152 | 0.37152 | 0.37152 | 0.37152 | 0.37152 | 0.37152 | 1.7147 | 2.4735 | 2.9705 | 3.2322 | 3.7554 | 4.2787 | 0.49155 | 1.3353 | 1.6747 | 1.6747 | 1.6747 | 1.6747 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-05-06 03:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.39724 | 0.39724 | 0.39724 | 0.39724 | 0.39724 | 0.39724 | 1.7147 | 2.4735 | 2.9705 | 3.2322 | 3.7554 | 4.2787 | 0.48012 | 1.3042 | 1.6358 | 1.6358 | 1.6358 | 1.6358 | 0.86161 | 1.0936 | 1.0936 | 1.0936 | 1.0936 | 1.0936
2020-05-06 04:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 1.7147 | 2.4735 | 2.9705 | 3.2322 | 3.7554 | 4.2787 | 0.48774 | 1.3249 | 1.6618 | 1.6618 | 1.6618 | 1.6618 | 1.0471 | 1.3291 | 1.3291 | 1.3291 | 1.3291 | 1.3291
2020-05-06 05:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.563 | 0.563 | 0.563 | 0.563 | 0.563 | 0.563 | 1.8862 | 2.7208 | 3.2676 | 3.5554 | 4.131 | 4.7066 | 0.55252 | 1.5009 | 1.8825 | 1.8825 | 1.8825 | 1.8825 | 1.3905 | 1.765 | 1.765 | 1.765 | 1.765 | 1.765
2020-05-06 06:00 | Winter | 0.84491 | 1.2991 | 1.9659 | 1.9659 | 1.9659 | 1.9659 | 0.68017 | 0.68017 | 0.68017 | 0.68017 | 0.68017 | 0.68017 | 2.1143 | 3.0498 | 3.6627 | 3.9853 | 4.6304 | 5.2756 | 0.59825 | 1.6251 | 2.0382 | 2.0382 | 2.0382 | 2.0382 | 1.7358 | 2.2032 | 2.2032 | 2.2032 | 2.2032 | 2.2032
2020-05-06 07:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.81449 | 0.81449 | 0.81449 | 0.81449 | 0.81449 | 0.81449 | 2.2863 | 3.2979 | 3.9607 | 4.3096 | 5.0072 | 5.7049 | 0.71637 | 1.946 | 2.4407 | 2.4407 | 2.4407 | 2.4407 | 2.1148 | 2.6843 | 2.6843 | 2.6843 | 2.6843 | 2.6843
2020-05-06 08:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 0.89737 | 0.89737 | 0.89737 | 0.89737 | 0.89737 | 0.89737 | 2.4578 | 3.5453 | 4.2578 | 4.6328 | 5.3828 | 6.1328 | 0.724 | 1.9667 | 2.4667 | 2.4667 | 2.4667 | 2.4667 | 2.3816 | 3.0229 | 3.0229 | 3.0229 | 3.0229 | 3.0229
2020-05-06 09:00 | Winter | 1.1241 | 1.7284 | 2.6155 | 2.6155 | 2.6155 | 2.6155 | 0.9088 | 0.9088 | 0.9088 | 0.9088 | 0.9088 | 0.9088 | 2.4006 | 3.4628 | 4.1588 | 4.525 | 5.2576 | 5.9902 | 0.73924 | 2.0081 | 2.5186 | 2.5186 | 2.5186 | 2.5186 | 2.4387 | 3.0954 | 3.0954 | 3.0954 | 3.0954 | 3.0954
2020-05-06 10:00 | Winter | 1.105 | 1.6991 | 2.5711 | 2.5711 | 2.5711 | 2.5711 | 0.89737 | 0.89737 | 0.89737 | 0.89737 | 0.89737 | 0.89737 | 2.4768 | 3.5728 | 4.2908 | 4.6687 | 5.4245 | 6.1803 | 0.72018 | 1.9563 | 2.4537 | 2.4537 | 2.4537 | 2.4537 | 2.3816 | 3.0229 | 3.0229 | 3.0229 | 3.0229 | 3.0229
2020-05-06 11:00 | Winter | 1.1241 | 1.7284 | 2.6155 | 2.6155 | 2.6155 | 2.6155 | 0.88308 | 0.88308 | 0.88308 | 0.88308 | 0.88308 | 0.88308 | 2.5149 | 3.6277 | 4.3568 | 4.7405 | 5.508 | 6.2754 | 0.6516 | 1.77 | 2.22 | 2.22 | 2.22 | 2.22 | 2.3054 | 2.9261 | 2.9261 | 2.9261 | 2.9261 | 2.9261
2020-05-06 12:00 | Winter | 1.1241 | 1.7284 | 2.6155 | 2.6155 | 2.6155 | 2.6155 | 0.77734 | 0.77734 | 0.77734 | 0.77734 | 0.77734 | 0.77734 | 2.5149 | 3.6277 | 4.3568 | 4.7405 | 5.508 | 6.2754 | 0.67065 | 1.8218 | 2.2849 | 2.2849 | 2.2849 | 2.2849 | 2.2673 | 2.8778 | 2.8778 | 2.8778 | 2.8778 | 2.8778
2020-05-06 13:00 | Winter | 1.105 | 1.6991 | 2.5711 | 2.5711 | 2.5711 | 2.5711 | 0.77448 | 0.77448 | 0.77448 | 0.77448 | 0.77448 | 0.77448 | 2.4959 | 3.6002 | 4.3238 | 4.7046 | 5.4662 | 6.2279 | 0.724 | 1.9667 | 2.4667 | 2.4667 | 2.4667 | 2.4667 | 2.1529 | 2.7327 | 2.7327 | 2.7327 | 2.7327 | 2.7327
2020-05-06 14:00 | Winter | 1.1241 | 1.7284 | 2.6155 | 2.6155 | 2.6155 | 2.6155 | 0.76877 | 0.76877 | 0.76877 | 0.76877 | 0.76877 | 0.76877 | 2.4768 | 3.5728 | 4.2908 | 4.6687 | 5.4245 | 6.1803 | 0.70494 | 1.9149 | 2.4018 | 2.4018 | 2.4018 | 2.4018 | 2.1148 | 2.6843 | 2.6843 | 2.6843 | 2.6843 | 2.6843
2020-05-06 15:00 | Winter | 1.1432 | 1.7577 | 2.6598 | 2.6598 | 2.6598 | 2.6598 | 0.8002 | 0.8002 | 0.8002 | 0.8002 | 0.8002 | 0.8002 | 2.3244 | 3.3529 | 4.0267 | 4.3814 | 5.0907 | 5.8 | 0.6516 | 1.77 | 2.22 | 2.22 | 2.22 | 2.22 | 2.0577 | 2.6118 | 2.6118 | 2.6118 | 2.6118 | 2.6118
2020-05-06 16:00 | Winter | 1.1241 | 1.7284 | 2.6155 | 2.6155 | 2.6155 | 2.6155 | 0.79163 | 0.79163 | 0.79163 | 0.79163 | 0.79163 | 0.79163 | 2.4006 | 3.4628 | 4.1588 | 4.525 | 5.2576 | 5.9902 | 0.6516 | 1.77 | 2.22 | 2.22 | 2.22 | 2.22 | 2.1148 | 2.6843 | 2.6843 | 2.6843 | 2.6843 | 2.6843
2020-05-06 17:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 0.70618 | 0.70618 | 0.70618 | 0.70618 | 0.70618 | 0.70618 | 2.4578 | 3.5453 | 4.2578 | 4.6328 | 5.3828 | 6.1328 | 0.67065 | 1.8218 | 2.2849 | 2.2849 | 2.2849 | 2.2849 | 2.0005 | 2.5392 | 2.5392 | 2.5392 | 2.5392 | 2.5392
2020-05-06 18:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.58872 | 0.58872 | 0.58872 | 0.58872 | 0.58872 | 0.58872 | 2.3532 | 3.3944 | 4.0765 | 4.4356 | 5.1536 | 5.8717 | 0.62873 | 1.7079 | 2.1421 | 2.1421 | 2.1421 | 2.1421 | 1.4839 | 1.8834 | 1.8834 | 1.8834 | 1.8834 | 1.8834
2020-05-06 19:00 | Winter | 0.68589 | 1.0546 | 1.5959 | 1.5959 | 1.5959 | 1.5959 | 0.54014 | 0.54014 | 0.54014 | 0.54014 | 0.54014 | 0.54014 | 2.2551 | 3.2529 | 3.9067 | 4.2507 | 4.9389 | 5.627 | 0.58682 | 1.594 | 1.9993 | 1.9993 | 1.9993 | 1.9993 | 1.1052 | 1.4028 | 1.4028 | 1.4028 | 1.4028 | 1.4028
2020-05-06 20:00 | Winter | 0.60992 | 0.93783 | 1.4191 | 1.4191 | 1.4191 | 1.4191 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 2.2863 | 3.2979 | 3.9607 | 4.3096 | 5.0072 | 5.7049 | 0.57157 | 1.5526 | 1.9474 | 1.9474 | 1.9474 | 1.9474 | 0.99073 | 1.2575 | 1.2575 | 1.2575 | 1.2575 | 1.2575
2020-05-06 21:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.33723 | 0.33723 | 0.33723 | 0.33723 | 0.33723 | 0.33723 | 2.0958 | 3.0231 | 3.6307 | 3.9504 | 4.59 | 5.2295 | 0.5183 | 1.4079 | 1.7658 | 1.7658 | 1.7658 | 1.7658 | 0.89634 | 1.1377 | 1.1377 | 1.1377 | 1.1377 | 1.1377
2020-05-06 22:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.38867 | 0.38867 | 0.38867 | 0.38867 | 0.38867 | 0.38867 | 2.0005 | 2.8857 | 3.4656 | 3.7709 | 4.3813 | 4.9918 | 0.5068 | 1.3767 | 1.7267 | 1.7267 | 1.7267 | 1.7267 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-05-06 23:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.39153 | 0.39153 | 0.39153 | 0.39153 | 0.39153 | 0.39153 | 1.9243 | 2.7758 | 3.3336 | 3.6272 | 4.2144 | 4.8016 | 0.49576 | 1.3467 | 1.689 | 1.689 | 1.689 | 1.689 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-05-07 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.3458 | 0.3458 | 0.3458 | 0.3458 | 0.3458 | 0.3458 | 1.81 | 2.6109 | 3.1356 | 3.4117 | 3.9641 | 4.5164 | 0.49918 | 1.356 | 1.7007 | 1.7007 | 1.7007 | 1.7007 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-05-07 01:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.36866 | 0.36866 | 0.36866 | 0.36866 | 0.36866 | 0.36866 | 1.7147 | 2.4735 | 2.9705 | 3.2322 | 3.7554 | 4.2787 | 0.44964 | 1.2214 | 1.5319 | 1.5319 | 1.5319 | 1.5319 | 0.80021 | 1.0157 | 1.0157 | 1.0157 | 1.0157 | 1.0157
2020-05-07 02:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.38295 | 0.38295 | 0.38295 | 0.38295 | 0.38295 | 0.38295 | 1.7147 | 2.4735 | 2.9705 | 3.2322 | 3.7554 | 4.2787 | 0.44964 | 1.2214 | 1.5319 | 1.5319 | 1.5319 | 1.5319 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-05-07 03:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.39724 | 0.39724 | 0.39724 | 0.39724 | 0.39724 | 0.39724 | 1.6957 | 2.446 | 2.9375 | 3.1963 | 3.7137 | 4.2311 | 0.48393 | 1.3146 | 1.6488 | 1.6488 | 1.6488 | 1.6488 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-05-07 04:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.39438 | 0.39438 | 0.39438 | 0.39438 | 0.39438 | 0.39438 | 1.7476 | 2.5208 | 3.0275 | 3.2941 | 3.8274 | 4.3607 | 0.49155 | 1.3353 | 1.6747 | 1.6747 | 1.6747 | 1.6747 | 0.89522 | 1.1363 | 1.1363 | 1.1363 | 1.1363 | 1.1363
2020-05-07 05:00 | Winter | 0.58942 | 0.9063 | 1.3714 | 1.3714 | 1.3714 | 1.3714 | 0.54299 | 0.54299 | 0.54299 | 0.54299 | 0.54299 | 0.54299 | 1.8653 | 2.6906 | 3.2314 | 3.516 | 4.0852 | 4.6544 | 0.53347 | 1.4491 | 1.8175 | 1.8175 | 1.8175 | 1.8175 | 1.2443 | 1.5794 | 1.5794 | 1.5794 | 1.5794 | 1.5794
2020-05-07 06:00 | Winter | 0.66993 | 1.0301 | 1.5587 | 1.5587 | 1.5587 | 1.5587 | 0.62301 | 0.62301 | 0.62301 | 0.62301 | 0.62301 | 0.62301 | 2.0577 | 2.9681 | 3.5647 | 3.8786 | 4.5065 | 5.1344 | 0.58682 | 1.594 | 1.9993 | 1.9993 | 1.9993 | 1.9993 | 1.6651 | 2.1134 | 2.1134 | 2.1134 | 2.1134 | 2.1134
2020-05-07 07:00 | Winter | 1.0288 | 1.582 | 2.3938 | 2.3938 | 2.3938 | 2.3938 | 0.80592 | 0.80592 | 0.80592 | 0.80592 | 0.80592 | 0.80592 | 2.3054 | 3.3254 | 3.9937 | 4.3455 | 5.049 | 5.7525 | 0.724 | 1.9667 | 2.4667 | 2.4667 | 2.4667 | 2.4667 | 2.1098 | 2.678 | 2.678 | 2.678 | 2.678 | 2.678
2020-05-07 08:00 | Winter | 1.1622 | 1.787 | 2.7041 | 2.7041 | 2.7041 | 2.7041 | 0.87451 | 0.87451 | 0.87451 | 0.87451 | 0.87451 | 0.87451 | 2.4197 | 3.4903 | 4.1918 | 4.561 | 5.2993 | 6.0377 | 0.73924 | 2.0081 | 2.5186 | 2.5186 | 2.5186 | 2.5186 | 2.3244 | 2.9503 | 2.9503 | 2.9503 | 2.9503 | 2.9503
2020-05-07 09:00 | Winter | 1.1813 | 1.8163 | 2.7485 | 2.7485 | 2.7485 | 2.7485 | 0.86022 | 0.86022 | 0.86022 | 0.86022 | 0.86022 | 0.86022 | 2.4387 | 3.5178 | 4.2248 | 4.5969 | 5.3411 | 6.0852 | 0.72018 | 1.9563 | 2.4537 | 2.4537 | 2.4537 | 2.4537 | 2.4197 | 3.0712 | 3.0712 | 3.0712 | 3.0712 | 3.0712
2020-05-07 10:00 | Winter | 1.105 | 1.6991 | 2.5711 | 2.5711 | 2.5711 | 2.5711 | 0.81164 | 0.81164 | 0.81164 | 0.81164 | 0.81164 | 0.81164 | 2.4768 | 3.5728 | 4.2908 | 4.6687 | 5.4245 | 6.1803 | 0.68208 | 1.8528 | 2.3239 | 2.3239 | 2.3239 | 2.3239 | 2.3014 | 2.9211 | 2.9211 | 2.9211 | 2.9211 | 2.9211
2020-05-07 11:00 | Winter | 1.086 | 1.6698 | 2.5268 | 2.5268 | 2.5268 | 2.5268 | 0.77734 | 0.77734 | 0.77734 | 0.77734 | 0.77734 | 0.77734 | 2.3816 | 3.4353 | 4.1258 | 4.4891 | 5.2159 | 5.9426 | 0.65922 | 1.7907 | 2.246 | 2.246 | 2.246 | 2.246 | 2.1903 | 2.7801 | 2.7801 | 2.7801 | 2.7801 | 2.7801
2020-05-07 12:00 | Winter | 1.105 | 1.6991 | 2.5711 | 2.5711 | 2.5711 | 2.5711 | 0.70589 | 0.70589 | 0.70589 | 0.70589 | 0.70589 | 0.70589 | 2.4197 | 3.4903 | 4.1918 | 4.561 | 5.2993 | 6.0377 | 0.60587 | 1.6458 | 2.0642 | 2.0642 | 2.0642 | 2.0642 | 2.1529 | 2.7327 | 2.7327 | 2.7327 | 2.7327 | 2.7327
2020-05-07 13:00 | Winter | 1.105 | 1.6991 | 2.5711 | 2.5711 | 2.5711 | 2.5711 | 0.78591 | 0.78591 | 0.78591 | 0.78591 | 0.78591 | 0.78591 | 2.3816 | 3.4353 | 4.1258 | 4.4891 | 5.2159 | 5.9426 | 0.5792 | 1.5733 | 1.9733 | 1.9733 | 1.9733 | 1.9733 | 2.0958 | 2.6601 | 2.6601 | 2.6601 | 2.6601 | 2.6601
2020-05-07 14:00 | Winter | 1.3908 | 2.1386 | 3.2361 | 3.2361 | 3.2361 | 3.2361 | 0.78877 | 0.78877 | 0.78877 | 0.78877 | 0.78877 | 0.78877 | 2.3816 | 3.4353 | 4.1258 | 4.4891 | 5.2159 | 5.9426 | 0.67446 | 1.8321 | 2.2979 | 2.2979 | 2.2979 | 2.2979 | 2.0767 | 2.6359 | 2.6359 | 2.6359 | 2.6359 | 2.6359
2020-05-07 15:00 | Winter | 1.1813 | 1.8163 | 2.7485 | 2.7485 | 2.7485 | 2.7485 | 0.76877 | 0.76877 | 0.76877 | 0.76877 | 0.76877 | 0.76877 | 2.3625 | 3.4079 | 4.0927 | 4.4532 | 5.1741 | 5.8951 | 0.64016 | 1.7389 | 2.1811 | 2.1811 | 2.1811 | 2.1811 | 2.0005 | 2.5392 | 2.5392 | 2.5392 | 2.5392 | 2.5392
2020-05-07 16:00 | Winter | 1.1432 | 1.7577 | 2.6598 | 2.6598 | 2.6598 | 2.6598 | 0.77734 | 0.77734 | 0.77734 | 0.77734 | 0.77734 | 0.77734 | 2.3187 | 3.3447 | 4.0169 | 4.3707 | 5.0782 | 5.7858 | 0.64397 | 1.7493 | 2.194 | 2.194 | 2.194 | 2.194 | 2.0196 | 2.5634 | 2.5634 | 2.5634 | 2.5634 | 2.5634
2020-05-07 17:00 | Winter | 1.1241 | 1.7284 | 2.6155 | 2.6155 | 2.6155 | 2.6155 | 0.65445 | 0.65445 | 0.65445 | 0.65445 | 0.65445 | 0.65445 | 2.4197 | 3.4903 | 4.1918 | 4.561 | 5.2993 | 6.0377 | 0.63254 | 1.7182 | 2.1551 | 2.1551 | 2.1551 | 2.1551 | 1.9624 | 2.4908 | 2.4908 | 2.4908 | 2.4908 | 2.4908
2020-05-07 18:00 | Winter | 0.83624 | 1.2858 | 1.9457 | 1.9457 | 1.9457 | 1.9457 | 0.53457 | 0.53457 | 0.53457 | 0.53457 | 0.53457 | 0.53457 | 2.3054 | 3.3254 | 3.9937 | 4.3455 | 5.049 | 5.7525 | 0.57157 | 1.5526 | 1.9474 | 1.9474 | 1.9474 | 1.9474 | 1.4458 | 1.8351 | 1.8351 | 1.8351 | 1.8351 | 1.8351
2020-05-07 19:00 | Winter | 0.64779 | 0.99605 | 1.5072 | 1.5072 | 1.5072 | 1.5072 | 0.49727 | 0.49727 | 0.49727 | 0.49727 | 0.49727 | 0.49727 | 2.2673 | 3.2705 | 3.9277 | 4.2736 | 4.9655 | 5.6574 | 0.59444 | 1.6147 | 2.0253 | 2.0253 | 2.0253 | 2.0253 | 1.0885 | 1.3816 | 1.3816 | 1.3816 | 1.3816 | 1.3816
2020-05-07 20:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 2.0958 | 3.0231 | 3.6307 | 3.9504 | 4.59 | 5.2295 | 0.57539 | 1.563 | 1.9603 | 1.9603 | 1.9603 | 1.9603 | 0.9737 | 1.2359 | 1.2359 | 1.2359 | 1.2359 | 1.2359
2020-05-07 21:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 1.9815 | 2.8582 | 3.4326 | 3.735 | 4.3396 | 4.9443 | 0.56776 | 1.5423 | 1.9344 | 1.9344 | 1.9344 | 1.9344 | 0.91452 | 1.1608 | 1.1608 | 1.1608 | 1.1608 | 1.1608
2020-05-07 22:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.37152 | 0.37152 | 0.37152 | 0.37152 | 0.37152 | 0.37152 | 1.9243 | 2.7758 | 3.3336 | 3.6272 | 4.2144 | 4.8016 | 0.49536 | 1.3456 | 1.6877 | 1.6877 | 1.6877 | 1.6877 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-05-07 23:00 | Winter | 0.60914 | 0.93662 | 1.4173 | 1.4173 | 1.4173 | 1.4173 | 0.36581 | 0.36581 | 0.36581 | 0.36581 | 0.36581 | 0.36581 | 1.7899 | 2.5818 | 3.1007 | 3.3738 | 3.92 | 4.4661 | 0.4725 | 1.2835 | 1.6098 | 1.6098 | 1.6098 | 1.6098 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-05-08 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.3458 | 0.3458 | 0.3458 | 0.3458 | 0.3458 | 0.3458 | 1.6957 | 2.446 | 2.9375 | 3.1963 | 3.7137 | 4.2311 | 0.44335 | 1.2043 | 1.5105 | 1.5105 | 1.5105 | 1.5105 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-05-08 01:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.33151 | 0.33151 | 0.33151 | 0.33151 | 0.33151 | 0.33151 | 1.7338 | 2.5009 | 3.0036 | 3.2681 | 3.7972 | 4.3262 | 0.44202 | 1.2007 | 1.506 | 1.506 | 1.506 | 1.506 | 0.7621 | 0.96732 | 0.96732 | 0.96732 | 0.96732 | 0.96732
2020-05-08 02:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.39438 | 0.39438 | 0.39438 | 0.39438 | 0.39438 | 0.39438 | 1.6806 | 2.4242 | 2.9114 | 3.1678 | 3.6806 | 4.1935 | 0.44964 | 1.2214 | 1.5319 | 1.5319 | 1.5319 | 1.5319 | 0.78115 | 0.9915 | 0.9915 | 0.9915 | 0.9915 | 0.9915
2020-05-08 03:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.37152 | 0.37152 | 0.37152 | 0.37152 | 0.37152 | 0.37152 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.44583 | 1.211 | 1.5189 | 1.5189 | 1.5189 | 1.5189 | 0.80021 | 1.0157 | 1.0157 | 1.0157 | 1.0157 | 1.0157
2020-05-08 04:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.40296 | 0.40296 | 0.40296 | 0.40296 | 0.40296 | 0.40296 | 1.6766 | 2.4185 | 2.9045 | 3.1603 | 3.672 | 4.1836 | 0.45345 | 1.2318 | 1.5449 | 1.5449 | 1.5449 | 1.5449 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-05-08 05:00 | Winter | 0.57181 | 0.87923 | 1.3304 | 1.3304 | 1.3304 | 1.3304 | 0.50584 | 0.50584 | 0.50584 | 0.50584 | 0.50584 | 0.50584 | 1.7719 | 2.5559 | 3.0696 | 3.3399 | 3.8806 | 4.4213 | 0.53728 | 1.4595 | 1.8305 | 1.8305 | 1.8305 | 1.8305 | 1.1782 | 1.4955 | 1.4955 | 1.4955 | 1.4955 | 1.4955
2020-05-08 06:00 | Winter | 0.61386 | 0.94389 | 1.4283 | 1.4283 | 1.4283 | 1.4283 | 0.60873 | 0.60873 | 0.60873 | 0.60873 | 0.60873 | 0.60873 | 1.81 | 2.6109 | 3.1356 | 3.4117 | 3.9641 | 4.5164 | 0.54109 | 1.4698 | 1.8435 | 1.8435 | 1.8435 | 1.8435 | 1.5241 | 1.9345 | 1.9345 | 1.9345 | 1.9345 | 1.9345
2020-05-08 07:00 | Winter | 0.93273 | 1.4342 | 2.1702 | 2.1702 | 2.1702 | 2.1702 | 0.72304 | 0.72304 | 0.72304 | 0.72304 | 0.72304 | 0.72304 | 2.1148 | 3.0506 | 3.6637 | 3.9863 | 4.6317 | 5.277 | 0.65541 | 1.7803 | 2.233 | 2.233 | 2.233 | 2.233 | 1.9815 | 2.515 | 2.515 | 2.515 | 2.515 | 2.515
2020-05-08 08:00 | Winter | 1.086 | 1.6698 | 2.5268 | 2.5268 | 2.5268 | 2.5268 | 0.75448 | 0.75448 | 0.75448 | 0.75448 | 0.75448 | 0.75448 | 2.2863 | 3.2979 | 3.9607 | 4.3096 | 5.0072 | 5.7049 | 0.6516 | 1.77 | 2.22 | 2.22 | 2.22 | 2.22 | 2.108 | 2.6756 | 2.6756 | 2.6756 | 2.6756 | 2.6756
2020-05-08 09:00 | Winter | 1.1622 | 1.787 | 2.7041 | 2.7041 | 2.7041 | 2.7041 | 0.71447 | 0.71447 | 0.71447 | 0.71447 | 0.71447 | 0.71447 | 2.2291 | 3.2155 | 3.8617 | 4.2018 | 4.8821 | 5.5623 | 0.73162 | 1.9874 | 2.4926 | 2.4926 | 2.4926 | 2.4926 | 2.1529 | 2.7327 | 2.7327 | 2.7327 | 2.7327 | 2.7327
2020-05-08 10:00 | Winter | 1.1432 | 1.7577 | 2.6598 | 2.6598 | 2.6598 | 2.6598 | 0.81735 | 0.81735 | 0.81735 | 0.81735 | 0.81735 | 0.81735 | 2.3263 | 3.3557 | 4.0301 | 4.385 | 5.0949 | 5.8048 | 0.65541 | 1.7803 | 2.233 | 2.233 | 2.233 | 2.233 | 2.0386 | 2.5876 | 2.5876 | 2.5876 | 2.5876 | 2.5876
2020-05-08 11:00 | Winter | 1.1813 | 1.8163 | 2.7485 | 2.7485 | 2.7485 | 2.7485 | 0.82307 | 0.82307 | 0.82307 | 0.82307 | 0.82307 | 0.82307 | 2.3625 | 3.4079 | 4.0927 | 4.4532 | 5.1741 | 5.8951 | 0.6897 | 1.8735 | 2.3498 | 2.3498 | 2.3498 | 2.3498 | 2.896 | 3.6758 | 3.6758 | 3.6758 | 3.6758 | 3.6758
2020-05-08 12:00 | Winter | 1.1813 | 1.8163 | 2.7485 | 2.7485 | 2.7485 | 2.7485 | 0.77734 | 0.77734 | 0.77734 | 0.77734 | 0.77734 | 0.77734 | 2.4387 | 3.5178 | 4.2248 | 4.5969 | 5.3411 | 6.0852 | 0.6516 | 1.77 | 2.22 | 2.22 | 2.22 | 2.22 | 2.915 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
2020-05-08 13:00 | Winter | 1.1622 | 1.787 | 2.7041 | 2.7041 | 2.7041 | 2.7041 | 0.83164 | 0.83164 | 0.83164 | 0.83164 | 0.83164 | 0.83164 | 3.277 | 4.727 | 5.677 | 6.177 | 7.177 | 8.177 | 0.65541 | 1.7803 | 2.233 | 2.233 | 2.233 | 2.233 | 1.9624 | 2.4908 | 2.4908 | 2.4908 | 2.4908 | 2.4908
2020-05-08 14:00 | Winter | 1.1432 | 1.7577 | 2.6598 | 2.6598 | 2.6598 | 2.6598 | 0.83164 | 0.83164 | 0.83164 | 0.83164 | 0.83164 | 0.83164 | 2.3244 | 3.3529 | 4.0267 | 4.3814 | 5.0907 | 5.8 | 0.65541 | 1.7803 | 2.233 | 2.233 | 2.233 | 2.233 | 1.9624 | 2.4908 | 2.4908 | 2.4908 | 2.4908 | 2.4908
2020-05-08 15:00 | Winter | 1.1432 | 1.7577 | 2.6598 | 2.6598 | 2.6598 | 2.6598 | 0.76305 | 0.76305 | 0.76305 | 0.76305 | 0.76305 | 0.76305 | 2.4197 | 3.4903 | 4.1918 | 4.561 | 5.2993 | 6.0377 | 0.67446 | 1.8321 | 2.2979 | 2.2979 | 2.2979 | 2.2979 | 1.9815 | 2.515 | 2.515 | 2.515 | 2.515 | 2.515
2020-05-08 16:00 | Winter | 1.105 | 1.6991 | 2.5711 | 2.5711 | 2.5711 | 2.5711 | 0.73161 | 0.73161 | 0.73161 | 0.73161 | 0.73161 | 0.73161 | 2.2101 | 3.188 | 3.8287 | 4.1659 | 4.8403 | 5.5147 | 0.6516 | 1.77 | 2.22 | 2.22 | 2.22 | 2.22 | 1.9434 | 2.4667 | 2.4667 | 2.4667 | 2.4667 | 2.4667
2020-05-08 17:00 | Winter | 1.0669 | 1.6405 | 2.4825 | 2.4825 | 2.4825 | 2.4825 | 0.66874 | 0.66874 | 0.66874 | 0.66874 | 0.66874 | 0.66874 | 2.2863 | 3.2979 | 3.9607 | 4.3096 | 5.0072 | 5.7049 | 0.62873 | 1.7079 | 2.1421 | 2.1421 | 2.1421 | 2.1421 | 1.8139 | 2.3023 | 2.3023 | 2.3023 | 2.3023 | 2.3023
2020-05-08 18:00 | Winter | 0.85739 | 1.3183 | 1.9949 | 1.9949 | 1.9949 | 1.9949 | 0.52585 | 0.52585 | 0.52585 | 0.52585 | 0.52585 | 0.52585 | 2.2673 | 3.2705 | 3.9277 | 4.2736 | 4.9655 | 5.6574 | 0.60968 | 1.6561 | 2.0772 | 2.0772 | 2.0772 | 2.0772 | 1.4192 | 1.8014 | 1.8014 | 1.8014 | 1.8014 | 1.8014
2020-05-08 19:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.42938 | 0.42938 | 0.42938 | 0.42938 | 0.42938 | 0.42938 | 2.0767 | 2.9956 | 3.5977 | 3.9145 | 4.5482 | 5.182 | 0.5792 | 1.5733 | 1.9733 | 1.9733 | 1.9733 | 1.9733 | 1.0337 | 1.312 | 1.312 | 1.312 | 1.312 | 1.312
2020-05-08 20:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 1.9815 | 2.8582 | 3.4326 | 3.735 | 4.3396 | 4.9443 | 0.52585 | 1.4284 | 1.7916 | 1.7916 | 1.7916 | 1.7916 | 0.97168 | 1.2333 | 1.2333 | 1.2333 | 1.2333 | 1.2333
2020-05-08 21:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.41439 | 0.41439 | 0.41439 | 0.41439 | 0.41439 | 0.41439 | 1.9364 | 2.7932 | 3.3546 | 3.65 | 4.2409 | 4.8318 | 0.53347 | 1.4491 | 1.8175 | 1.8175 | 1.8175 | 1.8175 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-05-08 22:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.42582 | 0.42582 | 0.42582 | 0.42582 | 0.42582 | 0.42582 | 1.8481 | 2.6658 | 3.2016 | 3.4836 | 4.0475 | 4.6115 | 0.53728 | 1.4595 | 1.8305 | 1.8305 | 1.8305 | 1.8305 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-05-08 23:00 | Winter | 0.55216 | 0.849 | 1.2847 | 1.2847 | 1.2847 | 1.2847 | 0.37724 | 0.37724 | 0.37724 | 0.37724 | 0.37724 | 0.37724 | 1.7719 | 2.5559 | 3.0696 | 3.3399 | 3.8806 | 4.4213 | 0.46907 | 1.2742 | 1.5981 | 1.5981 | 1.5981 | 1.5981 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-05-09 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.32538 | 0.32538 | 0.32538 | 0.32538 | 0.32538 | 0.32538 | 1.7338 | 2.5009 | 3.0036 | 3.2681 | 3.7972 | 4.3262 | 0.47631 | 1.2939 | 1.6228 | 1.6228 | 1.6228 | 1.6228 | 0.80021 | 1.0157 | 1.0157 | 1.0157 | 1.0157 | 1.0157
2020-05-09 01:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.38581 | 0.38581 | 0.38581 | 0.38581 | 0.38581 | 0.38581 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.48012 | 1.3042 | 1.6358 | 1.6358 | 1.6358 | 1.6358 | 0.77036 | 0.9778 | 0.9778 | 0.9778 | 0.9778 | 0.9778
2020-05-09 02:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.34253 | 0.34253 | 0.34253 | 0.34253 | 0.34253 | 0.34253 | 1.7147 | 2.4735 | 2.9705 | 3.2322 | 3.7554 | 4.2787 | 0.48012 | 1.3042 | 1.6358 | 1.6358 | 1.6358 | 1.6358 | 0.80021 | 1.0157 | 1.0157 | 1.0157 | 1.0157 | 1.0157
2020-05-09 03:00 | Winter | 0.55318 | 0.85057 | 1.2871 | 1.2871 | 1.2871 | 1.2871 | 0.34294 | 0.34294 | 0.34294 | 0.34294 | 0.34294 | 0.34294 | 1.657 | 2.3902 | 2.8705 | 3.1234 | 3.629 | 4.1347 | 0.47631 | 1.2939 | 1.6228 | 1.6228 | 1.6228 | 1.6228 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-05-09 04:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.35437 | 0.35437 | 0.35437 | 0.35437 | 0.35437 | 0.35437 | 1.6576 | 2.391 | 2.8715 | 3.1244 | 3.6302 | 4.1361 | 0.50299 | 1.3663 | 1.7137 | 1.7137 | 1.7137 | 1.7137 | 0.80021 | 1.0157 | 1.0157 | 1.0157 | 1.0157 | 1.0157
2020-05-09 05:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.38581 | 0.38581 | 0.38581 | 0.38581 | 0.38581 | 0.38581 | 1.7338 | 2.5009 | 3.0036 | 3.2681 | 3.7972 | 4.3262 | 0.4344 | 1.18 | 1.48 | 1.48 | 1.48 | 1.48 | 0.8106 | 1.0289 | 1.0289 | 1.0289 | 1.0289 | 1.0289
2020-05-09 06:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.49155 | 0.49155 | 0.49155 | 0.49155 | 0.49155 | 0.49155 | 1.7338 | 2.5009 | 3.0036 | 3.2681 | 3.7972 | 4.3262 | 0.4725 | 1.2835 | 1.6098 | 1.6098 | 1.6098 | 1.6098 | 0.93187 | 1.1828 | 1.1828 | 1.1828 | 1.1828 | 1.1828
2020-05-09 07:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 1.8672 | 2.6933 | 3.2346 | 3.5195 | 4.0892 | 4.659 | 0.53347 | 1.4491 | 1.8175 | 1.8175 | 1.8175 | 1.8175 | 1.0669 | 1.3542 | 1.3542 | 1.3542 | 1.3542 | 1.3542
2020-05-09 08:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 1.8672 | 2.6933 | 3.2346 | 3.5195 | 4.0892 | 4.659 | 0.49536 | 1.3456 | 1.6877 | 1.6877 | 1.6877 | 1.6877 | 1.1241 | 1.4268 | 1.4268 | 1.4268 | 1.4268 | 1.4268
2020-05-09 09:00 | Winter | 0.57213 | 0.87972 | 1.3312 | 1.3312 | 1.3312 | 1.3312 | 0.53728 | 0.53728 | 0.53728 | 0.53728 | 0.53728 | 0.53728 | 1.8707 | 2.6984 | 3.2407 | 3.5262 | 4.097 | 4.6679 | 0.49155 | 1.3353 | 1.6747 | 1.6747 | 1.6747 | 1.6747 | 1.1612 | 1.4739 | 1.4739 | 1.4739 | 1.4739 | 1.4739
2020-05-09 10:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 2.0386 | 2.9407 | 3.5316 | 3.8427 | 4.4648 | 5.0869 | 0.48012 | 1.3042 | 1.6358 | 1.6358 | 1.6358 | 1.6358 | 1.1622 | 1.4752 | 1.4752 | 1.4752 | 1.4752 | 1.4752
2020-05-09 11:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 1.9675 | 2.8381 | 3.4084 | 3.7086 | 4.309 | 4.9094 | 0.49155 | 1.3353 | 1.6747 | 1.6747 | 1.6747 | 1.6747 | 1.1622 | 1.4752 | 1.4752 | 1.4752 | 1.4752 | 1.4752
2020-05-09 12:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.563 | 0.563 | 0.563 | 0.563 | 0.563 | 0.563 | 2.0005 | 2.8857 | 3.4656 | 3.7709 | 4.3813 | 4.9918 | 0.52204 | 1.4181 | 1.7786 | 1.7786 | 1.7786 | 1.7786 | 1.1241 | 1.4268 | 1.4268 | 1.4268 | 1.4268 | 1.4268
2020-05-09 13:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.53442 | 0.53442 | 0.53442 | 0.53442 | 0.53442 | 0.53442 | 2.0577 | 2.9681 | 3.5647 | 3.8786 | 4.5065 | 5.1344 | 0.51061 | 1.387 | 1.7396 | 1.7396 | 1.7396 | 1.7396 | 1.0485 | 1.3308 | 1.3308 | 1.3308 | 1.3308 | 1.3308
2020-05-09 14:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 1.9567 | 2.8225 | 3.3897 | 3.6882 | 4.2853 | 4.8824 | 0.52585 | 1.4284 | 1.7916 | 1.7916 | 1.7916 | 1.7916 | 1.0098 | 1.2817 | 1.2817 | 1.2817 | 1.2817 | 1.2817
2020-05-09 15:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 1.925 | 2.7768 | 3.3348 | 3.6285 | 4.216 | 4.8034 | 0.51061 | 1.387 | 1.7396 | 1.7396 | 1.7396 | 1.7396 | 1.0288 | 1.3059 | 1.3059 | 1.3059 | 1.3059 | 1.3059
2020-05-09 16:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 2.0577 | 2.9681 | 3.5647 | 3.8786 | 4.5065 | 5.1344 | 0.53728 | 1.4595 | 1.8305 | 1.8305 | 1.8305 | 1.8305 | 1.0288 | 1.3059 | 1.3059 | 1.3059 | 1.3059 | 1.3059
2020-05-09 17:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 2.2482 | 3.243 | 3.8947 | 4.2377 | 4.9238 | 5.6098 | 0.56395 | 1.5319 | 1.9214 | 1.9214 | 1.9214 | 1.9214 | 1.105 | 1.4026 | 1.4026 | 1.4026 | 1.4026 | 1.4026
2020-05-09 18:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.42582 | 0.42582 | 0.42582 | 0.42582 | 0.42582 | 0.42582 | 2.1404 | 3.0874 | 3.7079 | 4.0345 | 4.6876 | 5.3408 | 0.53347 | 1.4491 | 1.8175 | 1.8175 | 1.8175 | 1.8175 | 1.0176 | 1.2916 | 1.2916 | 1.2916 | 1.2916 | 1.2916
2020-05-09 19:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.43439 | 0.43439 | 0.43439 | 0.43439 | 0.43439 | 0.43439 | 2.0958 | 3.0231 | 3.6307 | 3.9504 | 4.59 | 5.2295 | 0.56014 | 1.5216 | 1.9084 | 1.9084 | 1.9084 | 1.9084 | 0.93358 | 1.185 | 1.185 | 1.185 | 1.185 | 1.185
2020-05-09 20:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 2.0196 | 2.9132 | 3.4986 | 3.8068 | 4.4231 | 5.0393 | 0.56776 | 1.5423 | 1.9344 | 1.9344 | 1.9344 | 1.9344 | 0.91452 | 1.1608 | 1.1608 | 1.1608 | 1.1608 | 1.1608
2020-05-09 21:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 1.9815 | 2.8582 | 3.4326 | 3.735 | 4.3396 | 4.9443 | 0.5792 | 1.5733 | 1.9733 | 1.9733 | 1.9733 | 1.9733 | 0.91452 | 1.1608 | 1.1608 | 1.1608 | 1.1608 | 1.1608
2020-05-09 22:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.29206 | 0.29206 | 0.29206 | 0.29206 | 0.29206 | 0.29206 | 1.8862 | 2.7208 | 3.2676 | 3.5554 | 4.131 | 4.7066 | 0.53347 | 1.4491 | 1.8175 | 1.8175 | 1.8175 | 1.8175 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-05-09 23:00 | Winter | 0.55224 | 0.84914 | 1.2849 | 1.2849 | 1.2849 | 1.2849 | 0.43439 | 0.43439 | 0.43439 | 0.43439 | 0.43439 | 0.43439 | 1.7916 | 2.5843 | 3.1037 | 3.3771 | 3.9238 | 4.4705 | 0.55633 | 1.5112 | 1.8954 | 1.8954 | 1.8954 | 1.8954 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-05-10 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.36866 | 0.36866 | 0.36866 | 0.36866 | 0.36866 | 0.36866 | 1.7338 | 2.5009 | 3.0036 | 3.2681 | 3.7972 | 4.3262 | 0.5068 | 1.3767 | 1.7267 | 1.7267 | 1.7267 | 1.7267 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-05-10 01:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.29722 | 0.29722 | 0.29722 | 0.29722 | 0.29722 | 0.29722 | 1.6766 | 2.4185 | 2.9045 | 3.1603 | 3.672 | 4.1836 | 0.48633 | 1.3211 | 1.6569 | 1.6569 | 1.6569 | 1.6569 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-05-10 02:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.4001 | 0.4001 | 0.4001 | 0.4001 | 0.4001 | 0.4001 | 1.6195 | 2.336 | 2.8055 | 3.0526 | 3.5468 | 4.041 | 0.5068 | 1.3767 | 1.7267 | 1.7267 | 1.7267 | 1.7267 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-05-10 03:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.38581 | 0.38581 | 0.38581 | 0.38581 | 0.38581 | 0.38581 | 1.6195 | 2.336 | 2.8055 | 3.0526 | 3.5468 | 4.041 | 0.46488 | 1.2628 | 1.5839 | 1.5839 | 1.5839 | 1.5839 | 0.83791 | 1.0635 | 1.0635 | 1.0635 | 1.0635 | 1.0635
2020-05-10 04:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.4001 | 0.4001 | 0.4001 | 0.4001 | 0.4001 | 0.4001 | 1.7147 | 2.4735 | 2.9705 | 3.2322 | 3.7554 | 4.2787 | 0.46869 | 1.2732 | 1.5968 | 1.5968 | 1.5968 | 1.5968 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-05-10 05:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 1.6766 | 2.4185 | 2.9045 | 3.1603 | 3.672 | 4.1836 | 0.46869 | 1.2732 | 1.5968 | 1.5968 | 1.5968 | 1.5968 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-05-10 06:00 | Winter | 0.56709 | 0.87197 | 1.3195 | 1.3195 | 1.3195 | 1.3195 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 1.7147 | 2.4735 | 2.9705 | 3.2322 | 3.7554 | 4.2787 | 0.48774 | 1.3249 | 1.6618 | 1.6618 | 1.6618 | 1.6618 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-05-10 07:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.51442 | 0.51442 | 0.51442 | 0.51442 | 0.51442 | 0.51442 | 1.829 | 2.6383 | 3.1686 | 3.4477 | 4.0058 | 4.5639 | 0.55252 | 1.5009 | 1.8825 | 1.8825 | 1.8825 | 1.8825 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-05-10 08:00 | Winter | 0.56501 | 0.86877 | 1.3146 | 1.3146 | 1.3146 | 1.3146 | 0.53156 | 0.53156 | 0.53156 | 0.53156 | 0.53156 | 0.53156 | 1.9243 | 2.7758 | 3.3336 | 3.6272 | 4.2144 | 4.8016 | 0.54109 | 1.4698 | 1.8435 | 1.8435 | 1.8435 | 1.8435 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-05-10 09:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.51156 | 0.51156 | 0.51156 | 0.51156 | 0.51156 | 0.51156 | 1.9243 | 2.7758 | 3.3336 | 3.6272 | 4.2144 | 4.8016 | 0.52966 | 1.4388 | 1.8046 | 1.8046 | 1.8046 | 1.8046 | 0.78115 | 0.9915 | 0.9915 | 0.9915 | 0.9915 | 0.9915
2020-05-10 10:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.56014 | 0.56014 | 0.56014 | 0.56014 | 0.56014 | 0.56014 | 2.0005 | 2.8857 | 3.4656 | 3.7709 | 4.3813 | 4.9918 | 0.54871 | 1.4905 | 1.8695 | 1.8695 | 1.8695 | 1.8695 | 0.7621 | 0.96732 | 0.96732 | 0.96732 | 0.96732 | 0.96732
2020-05-10 11:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.54585 | 0.54585 | 0.54585 | 0.54585 | 0.54585 | 0.54585 | 1.9434 | 2.8032 | 3.3666 | 3.6631 | 4.2562 | 4.8492 | 0.53347 | 1.4491 | 1.8175 | 1.8175 | 1.8175 | 1.8175 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-05-10 12:00 | Winter | 0.53347 | 0.82027 | 1.2412 | 1.2412 | 1.2412 | 1.2412 | 0.53442 | 0.53442 | 0.53442 | 0.53442 | 0.53442 | 0.53442 | 2.0196 | 2.9132 | 3.4986 | 3.8068 | 4.4231 | 5.0393 | 0.51823 | 1.4077 | 1.7656 | 1.7656 | 1.7656 | 1.7656 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-05-10 13:00 | Winter | 0.53347 | 0.82027 | 1.2412 | 1.2412 | 1.2412 | 1.2412 | 0.51442 | 0.51442 | 0.51442 | 0.51442 | 0.51442 | 0.51442 | 2.0196 | 2.9132 | 3.4986 | 3.8068 | 4.4231 | 5.0393 | 0.49536 | 1.3456 | 1.6877 | 1.6877 | 1.6877 | 1.6877 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-05-10 14:00 | Winter | 0.53347 | 0.82027 | 1.2412 | 1.2412 | 1.2412 | 1.2412 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 2.0386 | 2.9407 | 3.5316 | 3.8427 | 4.4648 | 5.0869 | 0.46869 | 1.2732 | 1.5968 | 1.5968 | 1.5968 | 1.5968 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-05-10 15:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 2.0577 | 2.9681 | 3.5647 | 3.8786 | 4.5065 | 5.1344 | 0.46869 | 1.2732 | 1.5968 | 1.5968 | 1.5968 | 1.5968 | 0.84013 | 1.0664 | 1.0664 | 1.0664 | 1.0664 | 1.0664
2020-05-10 16:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.42582 | 0.42582 | 0.42582 | 0.42582 | 0.42582 | 0.42582 | 2.0767 | 2.9956 | 3.5977 | 3.9145 | 4.5482 | 5.182 | 0.55252 | 1.5009 | 1.8825 | 1.8825 | 1.8825 | 1.8825 | 0.87615 | 1.1121 | 1.1121 | 1.1121 | 1.1121 | 1.1121
2020-05-10 17:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.44163 | 0.44163 | 0.44163 | 0.44163 | 0.44163 | 0.44163 | 2.3435 | 3.3804 | 4.0597 | 4.4173 | 5.1324 | 5.8475 | 0.55633 | 1.5112 | 1.8954 | 1.8954 | 1.8954 | 1.8954 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-05-10 18:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.48869 | 0.48869 | 0.48869 | 0.48869 | 0.48869 | 0.48869 | 2.3095 | 3.3314 | 4.0009 | 4.3533 | 5.058 | 5.7628 | 0.60968 | 1.6561 | 2.0772 | 2.0772 | 2.0772 | 2.0772 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-05-10 19:00 | Winter | 0.55155 | 0.84807 | 1.2833 | 1.2833 | 1.2833 | 1.2833 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 2.2291 | 3.2155 | 3.8617 | 4.2018 | 4.8821 | 5.5623 | 0.63254 | 1.7182 | 2.1551 | 2.1551 | 2.1551 | 2.1551 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-05-10 20:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.55443 | 0.55443 | 0.55443 | 0.55443 | 0.55443 | 0.55443 | 2.1529 | 3.1056 | 3.7297 | 4.0582 | 4.7151 | 5.3721 | 0.5792 | 1.5733 | 1.9733 | 1.9733 | 1.9733 | 1.9733 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-05-10 21:00 | Winter | 0.53347 | 0.82027 | 1.2412 | 1.2412 | 1.2412 | 1.2412 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 2.0958 | 3.0231 | 3.6307 | 3.9504 | 4.59 | 5.2295 | 0.5792 | 1.5733 | 1.9733 | 1.9733 | 1.9733 | 1.9733 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-05-10 22:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 1.9338 | 2.7895 | 3.3501 | 3.6452 | 4.2353 | 4.8254 | 0.56776 | 1.5423 | 1.9344 | 1.9344 | 1.9344 | 1.9344 | 0.87322 | 1.1084 | 1.1084 | 1.1084 | 1.1084 | 1.1084
2020-05-10 23:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.37152 | 0.37152 | 0.37152 | 0.37152 | 0.37152 | 0.37152 | 1.8481 | 2.6658 | 3.2016 | 3.4836 | 4.0475 | 4.6115 | 0.5068 | 1.3767 | 1.7267 | 1.7267 | 1.7267 | 1.7267 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-05-11 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.41153 | 0.41153 | 0.41153 | 0.41153 | 0.41153 | 0.41153 | 1.7719 | 2.5559 | 3.0696 | 3.3399 | 3.8806 | 4.4213 | 0.51061 | 1.387 | 1.7396 | 1.7396 | 1.7396 | 1.7396 | 0.87609 | 1.112 | 1.112 | 1.112 | 1.112 | 1.112
2020-05-11 01:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.37724 | 0.37724 | 0.37724 | 0.37724 | 0.37724 | 0.37724 | 1.6766 | 2.4185 | 2.9045 | 3.1603 | 3.672 | 4.1836 | 0.5068 | 1.3767 | 1.7267 | 1.7267 | 1.7267 | 1.7267 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-05-11 02:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.49918 | 1.356 | 1.7007 | 1.7007 | 1.7007 | 1.7007 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-05-11 03:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.39724 | 0.39724 | 0.39724 | 0.39724 | 0.39724 | 0.39724 | 1.6202 | 2.3372 | 2.8069 | 3.0541 | 3.5485 | 4.0429 | 0.52204 | 1.4181 | 1.7786 | 1.7786 | 1.7786 | 1.7786 | 0.91452 | 1.1608 | 1.1608 | 1.1608 | 1.1608 | 1.1608
2020-05-11 04:00 | Winter | 0.64779 | 0.99605 | 1.5072 | 1.5072 | 1.5072 | 1.5072 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 1.81 | 2.6109 | 3.1356 | 3.4117 | 3.9641 | 4.5164 | 0.48393 | 1.3146 | 1.6488 | 1.6488 | 1.6488 | 1.6488 | 1.1622 | 1.4752 | 1.4752 | 1.4752 | 1.4752 | 1.4752
2020-05-11 05:00 | Winter | 0.724 | 1.1132 | 1.6845 | 1.6845 | 1.6845 | 1.6845 | 0.66303 | 0.66303 | 0.66303 | 0.66303 | 0.66303 | 0.66303 | 1.9153 | 2.7628 | 3.318 | 3.6102 | 4.1947 | 4.7791 | 0.56395 | 1.5319 | 1.9214 | 1.9214 | 1.9214 | 1.9214 | 1.5008 | 1.9049 | 1.9049 | 1.9049 | 1.9049 | 1.9049
2020-05-11 06:00 | Winter | 0.89958 | 1.3832 | 2.0931 | 2.0931 | 2.0931 | 2.0931 | 0.82592 | 0.82592 | 0.82592 | 0.82592 | 0.82592 | 0.82592 | 2.0975 | 3.0255 | 3.6336 | 3.9536 | 4.5936 | 5.2337 | 0.63635 | 1.7286 | 2.1681 | 2.1681 | 2.1681 | 2.1681 | 1.7017 | 2.16 | 2.16 | 2.16 | 2.16 | 2.16
2020-05-11 07:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 1.0517 | 1.0517 | 1.0517 | 1.0517 | 1.0517 | 1.0517 | 2.3244 | 3.3529 | 4.0267 | 4.3814 | 5.0907 | 5.8 | 0.6897 | 1.8735 | 2.3498 | 2.3498 | 2.3498 | 2.3498 | 2.0577 | 2.6118 | 2.6118 | 2.6118 | 2.6118 | 2.6118
2020-05-11 08:00 | Winter | 1.1432 | 1.7577 | 2.6598 | 2.6598 | 2.6598 | 2.6598 | 1.2489 | 1.2489 | 1.2489 | 1.2489 | 1.2489 | 1.2489 | 2.4387 | 3.5178 | 4.2248 | 4.5969 | 5.3411 | 6.0852 | 0.75829 | 2.0598 | 2.5835 | 2.5835 | 2.5835 | 2.5835 | 2.3244 | 2.9503 | 2.9503 | 2.9503 | 2.9503 | 2.9503
2020-05-11 09:00 | Winter | 1.1614 | 1.7858 | 2.7022 | 2.7022 | 2.7022 | 2.7022 | 1.3118 | 1.3118 | 1.3118 | 1.3118 | 1.3118 | 1.3118 | 2.4768 | 3.5728 | 4.2908 | 4.6687 | 5.4245 | 6.1803 | 0.73543 | 1.9977 | 2.5056 | 2.5056 | 2.5056 | 2.5056 | 2.3054 | 2.9261 | 2.9261 | 2.9261 | 2.9261 | 2.9261
2020-05-11 10:00 | Winter | 1.1622 | 1.787 | 2.7041 | 2.7041 | 2.7041 | 2.7041 | 1.1917 | 1.1917 | 1.1917 | 1.1917 | 1.1917 | 1.1917 | 2.4387 | 3.5178 | 4.2248 | 4.5969 | 5.3411 | 6.0852 | 0.74305 | 2.0184 | 2.5316 | 2.5316 | 2.5316 | 2.5316 | 2.3054 | 2.9261 | 2.9261 | 2.9261 | 2.9261 | 2.9261
2020-05-11 11:00 | Winter | 1.1241 | 1.7284 | 2.6155 | 2.6155 | 2.6155 | 2.6155 | 1.0717 | 1.0717 | 1.0717 | 1.0717 | 1.0717 | 1.0717 | 2.4006 | 3.4628 | 4.1588 | 4.525 | 5.2576 | 5.9902 | 0.70494 | 1.9149 | 2.4018 | 2.4018 | 2.4018 | 2.4018 | 2.3244 | 2.9503 | 2.9503 | 2.9503 | 2.9503 | 2.9503
2020-05-11 12:00 | Winter | 1.105 | 1.6991 | 2.5711 | 2.5711 | 2.5711 | 2.5711 | 1.0088 | 1.0088 | 1.0088 | 1.0088 | 1.0088 | 1.0088 | 2.4387 | 3.5178 | 4.2248 | 4.5969 | 5.3411 | 6.0852 | 0.71256 | 1.9356 | 2.4277 | 2.4277 | 2.4277 | 2.4277 | 2.191 | 2.781 | 2.781 | 2.781 | 2.781 | 2.781
2020-05-11 13:00 | Winter | 1.0669 | 1.6405 | 2.4825 | 2.4825 | 2.4825 | 2.4825 | 0.97168 | 0.97168 | 0.97168 | 0.97168 | 0.97168 | 0.97168 | 2.3244 | 3.3529 | 4.0267 | 4.3814 | 5.0907 | 5.8 | 0.72781 | 1.977 | 2.4796 | 2.4796 | 2.4796 | 2.4796 | 2.2101 | 2.8052 | 2.8052 | 2.8052 | 2.8052 | 2.8052
2020-05-11 14:00 | Winter | 1.086 | 1.6698 | 2.5268 | 2.5268 | 2.5268 | 2.5268 | 0.97168 | 0.97168 | 0.97168 | 0.97168 | 0.97168 | 0.97168 | 2.3054 | 3.3254 | 3.9937 | 4.3455 | 5.049 | 5.7525 | 0.69732 | 1.8942 | 2.3758 | 2.3758 | 2.3758 | 2.3758 | 2.191 | 2.781 | 2.781 | 2.781 | 2.781 | 2.781
2020-05-11 15:00 | Winter | 1.0669 | 1.6405 | 2.4825 | 2.4825 | 2.4825 | 2.4825 | 0.91452 | 0.91452 | 0.91452 | 0.91452 | 0.91452 | 0.91452 | 2.3435 | 3.3804 | 4.0597 | 4.4173 | 5.1324 | 5.8475 | 0.67827 | 1.8425 | 2.3109 | 2.3109 | 2.3109 | 2.3109 | 2.1529 | 2.7327 | 2.7327 | 2.7327 | 2.7327 | 2.7327
2020-05-11 16:00 | Winter | 1.0669 | 1.6405 | 2.4825 | 2.4825 | 2.4825 | 2.4825 | 0.94596 | 0.94596 | 0.94596 | 0.94596 | 0.94596 | 0.94596 | 2.3244 | 3.3529 | 4.0267 | 4.3814 | 5.0907 | 5.8 | 0.73162 | 1.9874 | 2.4926 | 2.4926 | 2.4926 | 2.4926 | 2.0196 | 2.5634 | 2.5634 | 2.5634 | 2.5634 | 2.5634
2020-05-11 17:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.81164 | 0.81164 | 0.81164 | 0.81164 | 0.81164 | 0.81164 | 2.4382 | 3.517 | 4.2238 | 4.5958 | 5.3398 | 6.0838 | 0.71256 | 1.9356 | 2.4277 | 2.4277 | 2.4277 | 2.4277 | 1.8862 | 2.3941 | 2.3941 | 2.3941 | 2.3941 | 2.3941
2020-05-11 18:00 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.67731 | 0.67731 | 0.67731 | 0.67731 | 0.67731 | 0.67731 | 2.4768 | 3.5728 | 4.2908 | 4.6687 | 5.4245 | 6.1803 | 0.67446 | 1.8321 | 2.2979 | 2.2979 | 2.2979 | 2.2979 | 1.4018 | 1.7792 | 1.7792 | 1.7792 | 1.7792 | 1.7792
2020-05-11 19:00 | Winter | 0.68589 | 1.0546 | 1.5959 | 1.5959 | 1.5959 | 1.5959 | 0.61458 | 0.61458 | 0.61458 | 0.61458 | 0.61458 | 0.61458 | 2.3244 | 3.3529 | 4.0267 | 4.3814 | 5.0907 | 5.8 | 0.66684 | 1.8114 | 2.2719 | 2.2719 | 2.2719 | 2.2719 | 1.1241 | 1.4268 | 1.4268 | 1.4268 | 1.4268 | 1.4268
2020-05-11 20:00 | Winter | 0.60981 | 0.93766 | 1.4189 | 1.4189 | 1.4189 | 1.4189 | 0.43154 | 0.43154 | 0.43154 | 0.43154 | 0.43154 | 0.43154 | 2.2673 | 3.2705 | 3.9277 | 4.2736 | 4.9655 | 5.6574 | 0.59063 | 1.6044 | 2.0123 | 2.0123 | 2.0123 | 2.0123 | 1.0669 | 1.3542 | 1.3542 | 1.3542 | 1.3542 | 1.3542
2020-05-11 21:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.35723 | 0.35723 | 0.35723 | 0.35723 | 0.35723 | 0.35723 | 2.1529 | 3.1056 | 3.7297 | 4.0582 | 4.7151 | 5.3721 | 0.63254 | 1.7182 | 2.1551 | 2.1551 | 2.1551 | 2.1551 | 0.95263 | 1.2092 | 1.2092 | 1.2092 | 1.2092 | 1.2092
2020-05-11 22:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 1.9815 | 2.8582 | 3.4326 | 3.735 | 4.3396 | 4.9443 | 0.55633 | 1.5112 | 1.8954 | 1.8954 | 1.8954 | 1.8954 | 0.87681 | 1.1129 | 1.1129 | 1.1129 | 1.1129 | 1.1129
2020-05-11 23:00 | Winter | 0.58974 | 0.9068 | 1.3722 | 1.3722 | 1.3722 | 1.3722 | 0.39438 | 0.39438 | 0.39438 | 0.39438 | 0.39438 | 0.39438 | 1.8862 | 2.7208 | 3.2676 | 3.5554 | 4.131 | 4.7066 | 0.52204 | 1.4181 | 1.7786 | 1.7786 | 1.7786 | 1.7786 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-05-12 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.35437 | 0.35437 | 0.35437 | 0.35437 | 0.35437 | 0.35437 | 1.856 | 2.6772 | 3.2152 | 3.4984 | 4.0647 | 4.6311 | 0.48653 | 1.3216 | 1.6576 | 1.6576 | 1.6576 | 1.6576 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-05-12 01:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.37438 | 0.37438 | 0.37438 | 0.37438 | 0.37438 | 0.37438 | 1.7147 | 2.4735 | 2.9705 | 3.2322 | 3.7554 | 4.2787 | 0.51442 | 1.3974 | 1.7526 | 1.7526 | 1.7526 | 1.7526 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-05-12 02:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.34866 | 0.34866 | 0.34866 | 0.34866 | 0.34866 | 0.34866 | 1.6957 | 2.446 | 2.9375 | 3.1963 | 3.7137 | 4.2311 | 0.5068 | 1.3767 | 1.7267 | 1.7267 | 1.7267 | 1.7267 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-05-12 03:00 | Winter | 0.57812 | 0.88892 | 1.3451 | 1.3451 | 1.3451 | 1.3451 | 0.34294 | 0.34294 | 0.34294 | 0.34294 | 0.34294 | 0.34294 | 1.6957 | 2.446 | 2.9375 | 3.1963 | 3.7137 | 4.2311 | 0.52585 | 1.4284 | 1.7916 | 1.7916 | 1.7916 | 1.7916 | 0.89529 | 1.1364 | 1.1364 | 1.1364 | 1.1364 | 1.1364
2020-05-12 04:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.42296 | 0.42296 | 0.42296 | 0.42296 | 0.42296 | 0.42296 | 1.7147 | 2.4735 | 2.9705 | 3.2322 | 3.7554 | 4.2787 | 0.51061 | 1.387 | 1.7396 | 1.7396 | 1.7396 | 1.7396 | 1.086 | 1.3784 | 1.3784 | 1.3784 | 1.3784 | 1.3784
2020-05-12 05:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.65731 | 0.65731 | 0.65731 | 0.65731 | 0.65731 | 0.65731 | 1.8939 | 2.7319 | 3.2809 | 3.5698 | 4.1478 | 4.7257 | 0.56395 | 1.5319 | 1.9214 | 1.9214 | 1.9214 | 1.9214 | 1.4565 | 1.8486 | 1.8486 | 1.8486 | 1.8486 | 1.8486
2020-05-12 06:00 | Winter | 0.89843 | 1.3814 | 2.0904 | 2.0904 | 2.0904 | 2.0904 | 0.70875 | 0.70875 | 0.70875 | 0.70875 | 0.70875 | 0.70875 | 2.1506 | 3.1022 | 3.7257 | 4.0538 | 4.7101 | 5.3664 | 0.62111 | 1.6872 | 2.1161 | 2.1161 | 2.1161 | 2.1161 | 1.8343 | 2.3283 | 2.3283 | 2.3283 | 2.3283 | 2.3283
2020-05-12 07:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 1.0917 | 1.0917 | 1.0917 | 1.0917 | 1.0917 | 1.0917 | 2.3929 | 3.4516 | 4.1453 | 4.5104 | 5.2406 | 5.9708 | 0.72018 | 1.9563 | 2.4537 | 2.4537 | 2.4537 | 2.4537 | 2.2482 | 2.8536 | 2.8536 | 2.8536 | 2.8536 | 2.8536
2020-05-12 08:00 | Winter | 1.1432 | 1.7577 | 2.6598 | 2.6598 | 2.6598 | 2.6598 | 1.1489 | 1.1489 | 1.1489 | 1.1489 | 1.1489 | 1.1489 | 2.5149 | 3.6277 | 4.3568 | 4.7405 | 5.508 | 6.2754 | 0.82688 | 2.2461 | 2.8172 | 2.8172 | 2.8172 | 2.8172 | 2.4578 | 3.1196 | 3.1196 | 3.1196 | 3.1196 | 3.1196
2020-05-12 09:00 | Winter | 1.1813 | 1.8163 | 2.7485 | 2.7485 | 2.7485 | 2.7485 | 1.1374 | 1.1374 | 1.1374 | 1.1374 | 1.1374 | 1.1374 | 2.5149 | 3.6277 | 4.3568 | 4.7405 | 5.508 | 6.2754 | 0.73162 | 1.9874 | 2.4926 | 2.4926 | 2.4926 | 2.4926 | 2.4387 | 3.0954 | 3.0954 | 3.0954 | 3.0954 | 3.0954
2020-05-12 10:00 | Winter | 1.1432 | 1.7577 | 2.6598 | 2.6598 | 2.6598 | 2.6598 | 1.1803 | 1.1803 | 1.1803 | 1.1803 | 1.1803 | 1.1803 | 2.553 | 3.6827 | 4.4228 | 4.8123 | 5.5914 | 6.3705 | 0.78496 | 2.1323 | 2.6744 | 2.6744 | 2.6744 | 2.6744 | 2.4006 | 3.0471 | 3.0471 | 3.0471 | 3.0471 | 3.0471
2020-05-12 11:00 | Winter | 1.105 | 1.6991 | 2.5711 | 2.5711 | 2.5711 | 2.5711 | 1.046 | 1.046 | 1.046 | 1.046 | 1.046 | 1.046 | 2.553 | 3.6827 | 4.4228 | 4.8123 | 5.5914 | 6.3705 | 0.75448 | 2.0495 | 2.5705 | 2.5705 | 2.5705 | 2.5705 | 2.4006 | 3.0471 | 3.0471 | 3.0471 | 3.0471 | 3.0471
2020-05-12 12:00 | Winter | 1.1622 | 1.787 | 2.7041 | 2.7041 | 2.7041 | 2.7041 | 0.98025 | 0.98025 | 0.98025 | 0.98025 | 0.98025 | 0.98025 | 2.4578 | 3.5453 | 4.2578 | 4.6328 | 5.3828 | 6.1328 | 0.73543 | 1.9977 | 2.5056 | 2.5056 | 2.5056 | 2.5056 | 2.3816 | 3.0229 | 3.0229 | 3.0229 | 3.0229 | 3.0229
2020-05-12 13:00 | Winter | 1.1241 | 1.7284 | 2.6155 | 2.6155 | 2.6155 | 2.6155 | 1.0231 | 1.0231 | 1.0231 | 1.0231 | 1.0231 | 1.0231 | 2.4387 | 3.5178 | 4.2248 | 4.5969 | 5.3411 | 6.0852 | 0.78496 | 2.1323 | 2.6744 | 2.6744 | 2.6744 | 2.6744 | 2.3435 | 2.9745 | 2.9745 | 2.9745 | 2.9745 | 2.9745
2020-05-12 14:00 | Winter | 1.105 | 1.6991 | 2.5711 | 2.5711 | 2.5711 | 2.5711 | 0.93738 | 0.93738 | 0.93738 | 0.93738 | 0.93738 | 0.93738 | 2.3728 | 3.4227 | 4.1106 | 4.4726 | 5.1967 | 5.9208 | 0.7621 | 2.0702 | 2.5965 | 2.5965 | 2.5965 | 2.5965 | 2.2673 | 2.8778 | 2.8778 | 2.8778 | 2.8778 | 2.8778
2020-05-12 15:00 | Winter | 1.1241 | 1.7284 | 2.6155 | 2.6155 | 2.6155 | 2.6155 | 0.92023 | 0.92023 | 0.92023 | 0.92023 | 0.92023 | 0.92023 | 2.3625 | 3.4079 | 4.0927 | 4.4532 | 5.1741 | 5.8951 | 0.75067 | 2.0391 | 2.5575 | 2.5575 | 2.5575 | 2.5575 | 2.1339 | 2.7085 | 2.7085 | 2.7085 | 2.7085 | 2.7085
2020-05-12 16:00 | Winter | 1.0555 | 1.6229 | 2.4558 | 2.4558 | 2.4558 | 2.4558 | 0.89737 | 0.89737 | 0.89737 | 0.89737 | 0.89737 | 0.89737 | 2.3054 | 3.3254 | 3.9937 | 4.3455 | 5.049 | 5.7525 | 0.70494 | 1.9149 | 2.4018 | 2.4018 | 2.4018 | 2.4018 | 2.0958 | 2.6601 | 2.6601 | 2.6601 | 2.6601 | 2.6601
2020-05-12 17:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.76877 | 0.76877 | 0.76877 | 0.76877 | 0.76877 | 0.76877 | 2.5911 | 3.7377 | 4.4888 | 4.8842 | 5.6749 | 6.4656 | 0.74305 | 2.0184 | 2.5316 | 2.5316 | 2.5316 | 2.5316 | 2.1148 | 2.6843 | 2.6843 | 2.6843 | 2.6843 | 2.6843
2020-05-12 18:00 | Winter | 0.83752 | 1.2878 | 1.9487 | 1.9487 | 1.9487 | 1.9487 | 0.68303 | 0.68303 | 0.68303 | 0.68303 | 0.68303 | 0.68303 | 2.534 | 3.6552 | 4.3898 | 4.7764 | 5.5497 | 6.3229 | 0.73543 | 1.9977 | 2.5056 | 2.5056 | 2.5056 | 2.5056 | 1.5691 | 1.9916 | 1.9916 | 1.9916 | 1.9916 | 1.9916
2020-05-12 19:00 | Winter | 0.64779 | 0.99605 | 1.5072 | 1.5072 | 1.5072 | 1.5072 | 0.51156 | 0.51156 | 0.51156 | 0.51156 | 0.51156 | 0.51156 | 2.3763 | 3.4277 | 4.1166 | 4.4792 | 5.2043 | 5.9295 | 0.68208 | 1.8528 | 2.3239 | 2.3239 | 2.3239 | 2.3239 | 1.105 | 1.4026 | 1.4026 | 1.4026 | 1.4026 | 1.4026
2020-05-12 20:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.37724 | 0.37724 | 0.37724 | 0.37724 | 0.37724 | 0.37724 | 2.2267 | 3.2119 | 3.8574 | 4.1972 | 4.8767 | 5.5561 | 0.64779 | 1.7596 | 2.207 | 2.207 | 2.207 | 2.207 | 1.0479 | 1.3301 | 1.3301 | 1.3301 | 1.3301 | 1.3301
2020-05-12 21:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.38867 | 0.38867 | 0.38867 | 0.38867 | 0.38867 | 0.38867 | 2.0965 | 3.0241 | 3.6319 | 3.9518 | 4.5915 | 5.2313 | 0.62492 | 1.6975 | 2.1291 | 2.1291 | 2.1291 | 2.1291 | 0.95263 | 1.2092 | 1.2092 | 1.2092 | 1.2092 | 1.2092
2020-05-12 22:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.35723 | 0.35723 | 0.35723 | 0.35723 | 0.35723 | 0.35723 | 1.9243 | 2.7758 | 3.3336 | 3.6272 | 4.2144 | 4.8016 | 0.69732 | 1.8942 | 2.3758 | 2.3758 | 2.3758 | 2.3758 | 0.87713 | 1.1133 | 1.1133 | 1.1133 | 1.1133 | 1.1133
2020-05-12 23:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.36581 | 0.36581 | 0.36581 | 0.36581 | 0.36581 | 0.36581 | 1.9053 | 2.7483 | 3.3006 | 3.5913 | 4.1727 | 4.7541 | 0.59444 | 1.6147 | 2.0253 | 2.0253 | 2.0253 | 2.0253 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-05-13 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.38295 | 0.38295 | 0.38295 | 0.38295 | 0.38295 | 0.38295 | 1.7531 | 2.5288 | 3.037 | 3.3045 | 3.8395 | 4.3744 | 0.55633 | 1.5112 | 1.8954 | 1.8954 | 1.8954 | 1.8954 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-05-13 01:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.37724 | 0.37724 | 0.37724 | 0.37724 | 0.37724 | 0.37724 | 1.6957 | 2.446 | 2.9375 | 3.1963 | 3.7137 | 4.2311 | 0.55252 | 1.5009 | 1.8825 | 1.8825 | 1.8825 | 1.8825 | 0.84293 | 1.0699 | 1.0699 | 1.0699 | 1.0699 | 1.0699
2020-05-13 02:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.38009 | 0.38009 | 0.38009 | 0.38009 | 0.38009 | 0.38009 | 1.7338 | 2.5009 | 3.0036 | 3.2681 | 3.7972 | 4.3262 | 0.53728 | 1.4595 | 1.8305 | 1.8305 | 1.8305 | 1.8305 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-05-13 03:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.36581 | 0.36581 | 0.36581 | 0.36581 | 0.36581 | 0.36581 | 1.6957 | 2.446 | 2.9375 | 3.1963 | 3.7137 | 4.2311 | 0.51442 | 1.3974 | 1.7526 | 1.7526 | 1.7526 | 1.7526 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-05-13 04:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 1.722 | 2.484 | 2.9832 | 3.2459 | 3.7714 | 4.2969 | 0.5792 | 1.5733 | 1.9733 | 1.9733 | 1.9733 | 1.9733 | 1.1113 | 1.4106 | 1.4106 | 1.4106 | 1.4106 | 1.4106
2020-05-13 05:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.57275 | 0.57275 | 0.57275 | 0.57275 | 0.57275 | 0.57275 | 1.9022 | 2.7438 | 3.2953 | 3.5855 | 4.166 | 4.7464 | 0.6516 | 1.77 | 2.22 | 2.22 | 2.22 | 2.22 | 1.3997 | 1.7766 | 1.7766 | 1.7766 | 1.7766 | 1.7766
2020-05-13 06:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.68303 | 0.68303 | 0.68303 | 0.68303 | 0.68303 | 0.68303 | 2.0951 | 3.0221 | 3.6294 | 3.9491 | 4.5884 | 5.2278 | 0.67827 | 1.8425 | 2.3109 | 2.3109 | 2.3109 | 2.3109 | 1.7822 | 2.2622 | 2.2622 | 2.2622 | 2.2622 | 2.2622
2020-05-13 07:00 | Winter | 1.0355 | 1.5922 | 2.4094 | 2.4094 | 2.4094 | 2.4094 | 0.81449 | 0.81449 | 0.81449 | 0.81449 | 0.81449 | 0.81449 | 2.3435 | 3.3804 | 4.0597 | 4.4173 | 5.1324 | 5.8475 | 0.76591 | 2.0805 | 2.6095 | 2.6095 | 2.6095 | 2.6095 | 2.2101 | 2.8052 | 2.8052 | 2.8052 | 2.8052 | 2.8052
2020-05-13 08:00 | Winter | 1.2003 | 1.8456 | 2.7928 | 2.7928 | 2.7928 | 2.7928 | 0.9088 | 0.9088 | 0.9088 | 0.9088 | 0.9088 | 0.9088 | 2.5911 | 3.7377 | 4.4888 | 4.8842 | 5.6749 | 6.4656 | 0.89547 | 2.4325 | 3.0509 | 3.0509 | 3.0509 | 3.0509 | 2.4578 | 3.1196 | 3.1196 | 3.1196 | 3.1196 | 3.1196
2020-05-13 09:00 | Winter | 1.1813 | 1.8163 | 2.7485 | 2.7485 | 2.7485 | 2.7485 | 0.96882 | 0.96882 | 0.96882 | 0.96882 | 0.96882 | 0.96882 | 2.5149 | 3.6277 | 4.3568 | 4.7405 | 5.508 | 6.2754 | 0.74044 | 2.0113 | 2.5227 | 2.5227 | 2.5227 | 2.5227 | 2.4387 | 3.0954 | 3.0954 | 3.0954 | 3.0954 | 3.0954
2020-05-13 10:00 | Winter | 1.1241 | 1.7284 | 2.6155 | 2.6155 | 2.6155 | 2.6155 | 0.95453 | 0.95453 | 0.95453 | 0.95453 | 0.95453 | 0.95453 | 2.5721 | 3.7102 | 4.4558 | 4.8483 | 5.6331 | 6.418 | 0.74305 | 2.0184 | 2.5316 | 2.5316 | 2.5316 | 2.5316 | 2.3816 | 3.0229 | 3.0229 | 3.0229 | 3.0229 | 3.0229
2020-05-13 11:00 | Winter | 1.086 | 1.6698 | 2.5268 | 2.5268 | 2.5268 | 2.5268 | 0.94596 | 0.94596 | 0.94596 | 0.94596 | 0.94596 | 0.94596 | 2.5252 | 3.6426 | 4.3746 | 4.7599 | 5.5305 | 6.3011 | 0.69592 | 1.8904 | 2.371 | 2.371 | 2.371 | 2.371 | 2.4006 | 3.0471 | 3.0471 | 3.0471 | 3.0471 | 3.0471
2020-05-13 12:00 | Winter | 1.086 | 1.6698 | 2.5268 | 2.5268 | 2.5268 | 2.5268 | 0.84307 | 0.84307 | 0.84307 | 0.84307 | 0.84307 | 0.84307 | 2.4006 | 3.4628 | 4.1588 | 4.525 | 5.2576 | 5.9902 | 0.73924 | 2.0081 | 2.5186 | 2.5186 | 2.5186 | 2.5186 | 2.2482 | 2.8536 | 2.8536 | 2.8536 | 2.8536 | 2.8536
2020-05-13 13:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 0.83736 | 0.83736 | 0.83736 | 0.83736 | 0.83736 | 0.83736 | 2.4197 | 3.4903 | 4.1918 | 4.561 | 5.2993 | 6.0377 | 0.71637 | 1.946 | 2.4407 | 2.4407 | 2.4407 | 2.4407 | 2.1845 | 2.7727 | 2.7727 | 2.7727 | 2.7727 | 2.7727
2020-05-13 14:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 0.87451 | 0.87451 | 0.87451 | 0.87451 | 0.87451 | 0.87451 | 2.3625 | 3.4079 | 4.0927 | 4.4532 | 5.1741 | 5.8951 | 0.67827 | 1.8425 | 2.3109 | 2.3109 | 2.3109 | 2.3109 | 2.1148 | 2.6843 | 2.6843 | 2.6843 | 2.6843 | 2.6843
2020-05-13 15:00 | Winter | 1.0669 | 1.6405 | 2.4825 | 2.4825 | 2.4825 | 2.4825 | 0.79449 | 0.79449 | 0.79449 | 0.79449 | 0.79449 | 0.79449 | 2.3435 | 3.3804 | 4.0597 | 4.4173 | 5.1324 | 5.8475 | 0.77734 | 2.1116 | 2.6484 | 2.6484 | 2.6484 | 2.6484 | 2.1148 | 2.6843 | 2.6843 | 2.6843 | 2.6843 | 2.6843
2020-05-13 16:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 0.81735 | 0.81735 | 0.81735 | 0.81735 | 0.81735 | 0.81735 | 2.3322 | 3.3641 | 4.0402 | 4.396 | 5.1077 | 5.8193 | 0.75067 | 2.0391 | 2.5575 | 2.5575 | 2.5575 | 2.5575 | 2.1148 | 2.6843 | 2.6843 | 2.6843 | 2.6843 | 2.6843
2020-05-13 17:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.75448 | 0.75448 | 0.75448 | 0.75448 | 0.75448 | 0.75448 | 2.4768 | 3.5728 | 4.2908 | 4.6687 | 5.4245 | 6.1803 | 0.724 | 1.9667 | 2.4667 | 2.4667 | 2.4667 | 2.4667 | 1.9554 | 2.482 | 2.482 | 2.482 | 2.482 | 2.482
2020-05-13 18:00 | Winter | 0.89547 | 1.3769 | 2.0835 | 2.0835 | 2.0835 | 2.0835 | 0.66588 | 0.66588 | 0.66588 | 0.66588 | 0.66588 | 0.66588 | 2.4387 | 3.5178 | 4.2248 | 4.5969 | 5.3411 | 6.0852 | 0.68208 | 1.8528 | 2.3239 | 2.3239 | 2.3239 | 2.3239 | 1.5003 | 1.9043 | 1.9043 | 1.9043 | 1.9043 | 1.9043
2020-05-13 19:00 | Winter | 0.66684 | 1.0253 | 1.5515 | 1.5515 | 1.5515 | 1.5515 | 0.62873 | 0.62873 | 0.62873 | 0.62873 | 0.62873 | 0.62873 | 2.2847 | 3.2956 | 3.9579 | 4.3065 | 5.0037 | 5.7009 | 0.67065 | 1.8218 | 2.2849 | 2.2849 | 2.2849 | 2.2849 | 1.0669 | 1.3542 | 1.3542 | 1.3542 | 1.3542 | 1.3542
2020-05-13 20:00 | Winter | 0.6292 | 0.96747 | 1.464 | 1.464 | 1.464 | 1.464 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 2.1529 | 3.1056 | 3.7297 | 4.0582 | 4.7151 | 5.3721 | 0.64397 | 1.7493 | 2.194 | 2.194 | 2.194 | 2.194 | 1.0669 | 1.3542 | 1.3542 | 1.3542 | 1.3542 | 1.3542
2020-05-13 21:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.34866 | 0.34866 | 0.34866 | 0.34866 | 0.34866 | 0.34866 | 2.172 | 3.133 | 3.7627 | 4.0941 | 4.7569 | 5.4197 | 0.60587 | 1.6458 | 2.0642 | 2.0642 | 2.0642 | 2.0642 | 0.93358 | 1.185 | 1.185 | 1.185 | 1.185 | 1.185
2020-05-13 22:00 | Winter | 0.60055 | 0.92341 | 1.3973 | 1.3973 | 1.3973 | 1.3973 | 0.32865 | 0.32865 | 0.32865 | 0.32865 | 0.32865 | 0.32865 | 2.0767 | 2.9956 | 3.5977 | 3.9145 | 4.5482 | 5.182 | 0.54871 | 1.4905 | 1.8695 | 1.8695 | 1.8695 | 1.8695 | 0.87675 | 1.1128 | 1.1128 | 1.1128 | 1.1128 | 1.1128
2020-05-13 23:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.34294 | 0.34294 | 0.34294 | 0.34294 | 0.34294 | 0.34294 | 1.829 | 2.6383 | 3.1686 | 3.4477 | 4.0058 | 4.5639 | 0.52585 | 1.4284 | 1.7916 | 1.7916 | 1.7916 | 1.7916 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-05-14 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.36295 | 0.36295 | 0.36295 | 0.36295 | 0.36295 | 0.36295 | 1.81 | 2.6109 | 3.1356 | 3.4117 | 3.9641 | 4.5164 | 0.54871 | 1.4905 | 1.8695 | 1.8695 | 1.8695 | 1.8695 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-05-14 01:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.33723 | 0.33723 | 0.33723 | 0.33723 | 0.33723 | 0.33723 | 1.6957 | 2.446 | 2.9375 | 3.1963 | 3.7137 | 4.2311 | 0.52997 | 1.4396 | 1.8056 | 1.8056 | 1.8056 | 1.8056 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-05-14 02:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.34008 | 0.34008 | 0.34008 | 0.34008 | 0.34008 | 0.34008 | 1.6766 | 2.4185 | 2.9045 | 3.1603 | 3.672 | 4.1836 | 0.5449 | 1.4802 | 1.8565 | 1.8565 | 1.8565 | 1.8565 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-05-14 03:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.3458 | 0.3458 | 0.3458 | 0.3458 | 0.3458 | 0.3458 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.56014 | 1.5216 | 1.9084 | 1.9084 | 1.9084 | 1.9084 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-05-14 04:00 | Winter | 0.57707 | 0.88732 | 1.3427 | 1.3427 | 1.3427 | 1.3427 | 0.4001 | 0.4001 | 0.4001 | 0.4001 | 0.4001 | 0.4001 | 1.81 | 2.6109 | 3.1356 | 3.4117 | 3.9641 | 4.5164 | 0.52966 | 1.4388 | 1.8046 | 1.8046 | 1.8046 | 1.8046 | 1.086 | 1.3784 | 1.3784 | 1.3784 | 1.3784 | 1.3784
2020-05-14 05:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.59158 | 0.59158 | 0.59158 | 0.59158 | 0.59158 | 0.59158 | 1.9053 | 2.7483 | 3.3006 | 3.5913 | 4.1727 | 4.7541 | 0.62111 | 1.6872 | 2.1161 | 2.1161 | 2.1161 | 2.1161 | 1.3615 | 1.7281 | 1.7281 | 1.7281 | 1.7281 | 1.7281
2020-05-14 06:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.67446 | 0.67446 | 0.67446 | 0.67446 | 0.67446 | 0.67446 | 2.0577 | 2.9681 | 3.5647 | 3.8786 | 4.5065 | 5.1344 | 0.69732 | 1.8942 | 2.3758 | 2.3758 | 2.3758 | 2.3758 | 1.7211 | 2.1845 | 2.1845 | 2.1845 | 2.1845 | 2.1845
2020-05-14 07:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.82878 | 0.82878 | 0.82878 | 0.82878 | 0.82878 | 0.82878 | 2.3435 | 3.3804 | 4.0597 | 4.4173 | 5.1324 | 5.8475 | 0.74686 | 2.0288 | 2.5446 | 2.5446 | 2.5446 | 2.5446 | 2.1339 | 2.7085 | 2.7085 | 2.7085 | 2.7085 | 2.7085
2020-05-14 08:00 | Winter | 1.1622 | 1.787 | 2.7041 | 2.7041 | 2.7041 | 2.7041 | 0.9088 | 0.9088 | 0.9088 | 0.9088 | 0.9088 | 0.9088 | 2.4197 | 3.4903 | 4.1918 | 4.561 | 5.2993 | 6.0377 | 0.77734 | 2.1116 | 2.6484 | 2.6484 | 2.6484 | 2.6484 | 2.3625 | 2.9987 | 2.9987 | 2.9987 | 2.9987 | 2.9987
2020-05-14 09:00 | Winter | 1.1241 | 1.7284 | 2.6155 | 2.6155 | 2.6155 | 2.6155 | 1.0003 | 1.0003 | 1.0003 | 1.0003 | 1.0003 | 1.0003 | 2.3244 | 3.3529 | 4.0267 | 4.3814 | 5.0907 | 5.8 | 0.75067 | 2.0391 | 2.5575 | 2.5575 | 2.5575 | 2.5575 | 2.3372 | 2.9666 | 2.9666 | 2.9666 | 2.9666 | 2.9666
2020-05-14 10:00 | Winter | 1.105 | 1.6991 | 2.5711 | 2.5711 | 2.5711 | 2.5711 | 1.0346 | 1.0346 | 1.0346 | 1.0346 | 1.0346 | 1.0346 | 2.4959 | 3.6002 | 4.3238 | 4.7046 | 5.4662 | 6.2279 | 0.73543 | 1.9977 | 2.5056 | 2.5056 | 2.5056 | 2.5056 | 2.3625 | 2.9987 | 2.9987 | 2.9987 | 2.9987 | 2.9987
2020-05-14 11:00 | Winter | 1.087 | 1.6714 | 2.5291 | 2.5291 | 2.5291 | 2.5291 | 0.98311 | 0.98311 | 0.98311 | 0.98311 | 0.98311 | 0.98311 | 2.4493 | 3.533 | 4.243 | 4.6167 | 5.3641 | 6.1115 | 0.77734 | 2.1116 | 2.6484 | 2.6484 | 2.6484 | 2.6484 | 2.2673 | 2.8778 | 2.8778 | 2.8778 | 2.8778 | 2.8778
2020-05-14 12:00 | Winter | 1.1241 | 1.7284 | 2.6155 | 2.6155 | 2.6155 | 2.6155 | 0.94881 | 0.94881 | 0.94881 | 0.94881 | 0.94881 | 0.94881 | 2.3054 | 3.3254 | 3.9937 | 4.3455 | 5.049 | 5.7525 | 0.7462 | 2.027 | 2.5423 | 2.5423 | 2.5423 | 2.5423 | 2.2101 | 2.8052 | 2.8052 | 2.8052 | 2.8052 | 2.8052
2020-05-14 13:00 | Winter | 1.105 | 1.6991 | 2.5711 | 2.5711 | 2.5711 | 2.5711 | 0.92595 | 0.92595 | 0.92595 | 0.92595 | 0.92595 | 0.92595 | 2.3435 | 3.3804 | 4.0597 | 4.4173 | 5.1324 | 5.8475 | 0.74686 | 2.0288 | 2.5446 | 2.5446 | 2.5446 | 2.5446 | 2.0958 | 2.6601 | 2.6601 | 2.6601 | 2.6601 | 2.6601
2020-05-14 14:00 | Winter | 1.2575 | 1.9335 | 2.9258 | 2.9258 | 2.9258 | 2.9258 | 0.96596 | 0.96596 | 0.96596 | 0.96596 | 0.96596 | 0.96596 | 2.4197 | 3.4903 | 4.1918 | 4.561 | 5.2993 | 6.0377 | 0.69732 | 1.8942 | 2.3758 | 2.3758 | 2.3758 | 2.3758 | 2.0958 | 2.6601 | 2.6601 | 2.6601 | 2.6601 | 2.6601
2020-05-14 15:00 | Winter | 1.2194 | 1.8749 | 2.8371 | 2.8371 | 2.8371 | 2.8371 | 0.92309 | 0.92309 | 0.92309 | 0.92309 | 0.92309 | 0.92309 | 2.4006 | 3.4628 | 4.1588 | 4.525 | 5.2576 | 5.9902 | 0.70113 | 1.9046 | 2.3888 | 2.3888 | 2.3888 | 2.3888 | 2.0386 | 2.5876 | 2.5876 | 2.5876 | 2.5876 | 2.5876
2020-05-14 16:00 | Winter | 1.1438 | 1.7588 | 2.6614 | 2.6614 | 2.6614 | 2.6614 | 0.77734 | 0.77734 | 0.77734 | 0.77734 | 0.77734 | 0.77734 | 2.2673 | 3.2705 | 3.9277 | 4.2736 | 4.9655 | 5.6574 | 0.73543 | 1.9977 | 2.5056 | 2.5056 | 2.5056 | 2.5056 | 2.0386 | 2.5876 | 2.5876 | 2.5876 | 2.5876 | 2.5876
2020-05-14 17:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.75448 | 0.75448 | 0.75448 | 0.75448 | 0.75448 | 0.75448 | 2.4578 | 3.5453 | 4.2578 | 4.6328 | 5.3828 | 6.1328 | 0.71637 | 1.946 | 2.4407 | 2.4407 | 2.4407 | 2.4407 | 1.9624 | 2.4908 | 2.4908 | 2.4908 | 2.4908 | 2.4908
2020-05-14 18:00 | Winter | 0.82283 | 1.2652 | 1.9145 | 1.9145 | 1.9145 | 1.9145 | 0.67731 | 0.67731 | 0.67731 | 0.67731 | 0.67731 | 0.67731 | 2.4387 | 3.5178 | 4.2248 | 4.5969 | 5.3411 | 6.0852 | 0.68245 | 1.8538 | 2.3251 | 2.3251 | 2.3251 | 2.3251 | 1.5433 | 1.9588 | 1.9588 | 1.9588 | 1.9588 | 1.9588
2020-05-14 19:00 | Winter | 0.68589 | 1.0546 | 1.5959 | 1.5959 | 1.5959 | 1.5959 | 0.55157 | 0.55157 | 0.55157 | 0.55157 | 0.55157 | 0.55157 | 2.3054 | 3.3254 | 3.9937 | 4.3455 | 5.049 | 5.7525 | 0.66303 | 1.8011 | 2.2589 | 2.2589 | 2.2589 | 2.2589 | 1.1241 | 1.4268 | 1.4268 | 1.4268 | 1.4268 | 1.4268
2020-05-14 20:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.48869 | 0.48869 | 0.48869 | 0.48869 | 0.48869 | 0.48869 | 2.172 | 3.133 | 3.7627 | 4.0941 | 4.7569 | 5.4197 | 0.61349 | 1.6665 | 2.0902 | 2.0902 | 2.0902 | 2.0902 | 1.054 | 1.3378 | 1.3378 | 1.3378 | 1.3378 | 1.3378
2020-05-14 21:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 2.1529 | 3.1056 | 3.7297 | 4.0582 | 4.7151 | 5.3721 | 0.60968 | 1.6561 | 2.0772 | 2.0772 | 2.0772 | 2.0772 | 0.97168 | 1.2333 | 1.2333 | 1.2333 | 1.2333 | 1.2333
2020-05-14 22:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 1.9243 | 2.7758 | 3.3336 | 3.6272 | 4.2144 | 4.8016 | 0.57157 | 1.5526 | 1.9474 | 1.9474 | 1.9474 | 1.9474 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-05-14 23:00 | Winter | 0.53347 | 0.82027 | 1.2412 | 1.2412 | 1.2412 | 1.2412 | 0.39153 | 0.39153 | 0.39153 | 0.39153 | 0.39153 | 0.39153 | 1.8811 | 2.7135 | 3.2588 | 3.5458 | 4.1198 | 4.6939 | 0.5068 | 1.3767 | 1.7267 | 1.7267 | 1.7267 | 1.7267 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-05-15 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.37152 | 0.37152 | 0.37152 | 0.37152 | 0.37152 | 0.37152 | 1.7338 | 2.5009 | 3.0036 | 3.2681 | 3.7972 | 4.3262 | 0.52585 | 1.4284 | 1.7916 | 1.7916 | 1.7916 | 1.7916 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-05-15 01:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 1.7147 | 2.4735 | 2.9705 | 3.2322 | 3.7554 | 4.2787 | 0.49259 | 1.3381 | 1.6783 | 1.6783 | 1.6783 | 1.6783 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-05-15 02:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 1.7338 | 2.5009 | 3.0036 | 3.2681 | 3.7972 | 4.3262 | 0.51061 | 1.387 | 1.7396 | 1.7396 | 1.7396 | 1.7396 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-05-15 03:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.43439 | 0.43439 | 0.43439 | 0.43439 | 0.43439 | 0.43439 | 1.7147 | 2.4735 | 2.9705 | 3.2322 | 3.7554 | 4.2787 | 0.53728 | 1.4595 | 1.8305 | 1.8305 | 1.8305 | 1.8305 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-05-15 04:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 1.7431 | 2.5144 | 3.0197 | 3.2856 | 3.8175 | 4.3495 | 0.49918 | 1.356 | 1.7007 | 1.7007 | 1.7007 | 1.7007 | 1.086 | 1.3784 | 1.3784 | 1.3784 | 1.3784 | 1.3784
2020-05-15 05:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.58872 | 0.58872 | 0.58872 | 0.58872 | 0.58872 | 0.58872 | 1.8481 | 2.6658 | 3.2016 | 3.4836 | 4.0475 | 4.6115 | 0.54871 | 1.4905 | 1.8695 | 1.8695 | 1.8695 | 1.8695 | 1.408 | 1.7872 | 1.7872 | 1.7872 | 1.7872 | 1.7872
2020-05-15 06:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.67731 | 0.67731 | 0.67731 | 0.67731 | 0.67731 | 0.67731 | 2.191 | 3.1605 | 3.7957 | 4.13 | 4.7986 | 5.4672 | 0.63254 | 1.7182 | 2.1551 | 2.1551 | 2.1551 | 2.1551 | 1.7735 | 2.251 | 2.251 | 2.251 | 2.251 | 2.251
2020-05-15 07:00 | Winter | 1.0035 | 1.543 | 2.3348 | 2.3348 | 2.3348 | 2.3348 | 0.83954 | 0.83954 | 0.83954 | 0.83954 | 0.83954 | 0.83954 | 2.3244 | 3.3529 | 4.0267 | 4.3814 | 5.0907 | 5.8 | 0.72781 | 1.977 | 2.4796 | 2.4796 | 2.4796 | 2.4796 | 2.1592 | 2.7406 | 2.7406 | 2.7406 | 2.7406 | 2.7406
2020-05-15 08:00 | Winter | 1.1241 | 1.7284 | 2.6155 | 2.6155 | 2.6155 | 2.6155 | 0.90595 | 0.90595 | 0.90595 | 0.90595 | 0.90595 | 0.90595 | 2.4768 | 3.5728 | 4.2908 | 4.6687 | 5.4245 | 6.1803 | 0.7964 | 2.1633 | 2.7133 | 2.7133 | 2.7133 | 2.7133 | 2.3054 | 2.9261 | 2.9261 | 2.9261 | 2.9261 | 2.9261
2020-05-15 09:00 | Winter | 1.1241 | 1.7284 | 2.6155 | 2.6155 | 2.6155 | 2.6155 | 0.90309 | 0.90309 | 0.90309 | 0.90309 | 0.90309 | 0.90309 | 2.553 | 3.6827 | 4.4228 | 4.8123 | 5.5914 | 6.3705 | 0.7621 | 2.0702 | 2.5965 | 2.5965 | 2.5965 | 2.5965 | 2.2673 | 2.8778 | 2.8778 | 2.8778 | 2.8778 | 2.8778
2020-05-15 10:00 | Winter | 1.0745 | 1.6522 | 2.5 | 2.5 | 2.5 | 2.5 | 0.88308 | 0.88308 | 0.88308 | 0.88308 | 0.88308 | 0.88308 | 2.4387 | 3.5178 | 4.2248 | 4.5969 | 5.3411 | 6.0852 | 0.81926 | 2.2254 | 2.7912 | 2.7912 | 2.7912 | 2.7912 | 2.2673 | 2.8778 | 2.8778 | 2.8778 | 2.8778 | 2.8778
2020-05-15 11:00 | Winter | 1.105 | 1.6991 | 2.5711 | 2.5711 | 2.5711 | 2.5711 | 0.92595 | 0.92595 | 0.92595 | 0.92595 | 0.92595 | 0.92595 | 2.4568 | 3.5438 | 4.256 | 4.6309 | 5.3805 | 6.1302 | 0.81926 | 2.2254 | 2.7912 | 2.7912 | 2.7912 | 2.7912 | 2.3244 | 2.9503 | 2.9503 | 2.9503 | 2.9503 | 2.9503
2020-05-15 12:00 | Winter | 1.086 | 1.6698 | 2.5268 | 2.5268 | 2.5268 | 2.5268 | 0.94881 | 0.94881 | 0.94881 | 0.94881 | 0.94881 | 0.94881 | 2.4768 | 3.5728 | 4.2908 | 4.6687 | 5.4245 | 6.1803 | 0.7621 | 2.0702 | 2.5965 | 2.5965 | 2.5965 | 2.5965 | 2.2291 | 2.8294 | 2.8294 | 2.8294 | 2.8294 | 2.8294
2020-05-15 13:00 | Winter | 1.1241 | 1.7284 | 2.6155 | 2.6155 | 2.6155 | 2.6155 | 0.86022 | 0.86022 | 0.86022 | 0.86022 | 0.86022 | 0.86022 | 2.3816 | 3.4353 | 4.1258 | 4.4891 | 5.2159 | 5.9426 | 0.76972 | 2.0909 | 2.6225 | 2.6225 | 2.6225 | 2.6225 | 2.191 | 2.781 | 2.781 | 2.781 | 2.781 | 2.781
2020-05-15 14:00 | Winter | 1.105 | 1.6991 | 2.5711 | 2.5711 | 2.5711 | 2.5711 | 0.87451 | 0.87451 | 0.87451 | 0.87451 | 0.87451 | 0.87451 | 2.4006 | 3.4628 | 4.1588 | 4.525 | 5.2576 | 5.9902 | 0.75067 | 2.0391 | 2.5575 | 2.5575 | 2.5575 | 2.5575 | 2.0577 | 2.6118 | 2.6118 | 2.6118 | 2.6118 | 2.6118
2020-05-15 15:00 | Winter | 1.086 | 1.6698 | 2.5268 | 2.5268 | 2.5268 | 2.5268 | 0.8345 | 0.8345 | 0.8345 | 0.8345 | 0.8345 | 0.8345 | 2.4006 | 3.4628 | 4.1588 | 4.525 | 5.2576 | 5.9902 | 0.76591 | 2.0805 | 2.6095 | 2.6095 | 2.6095 | 2.6095 | 2.0386 | 2.5876 | 2.5876 | 2.5876 | 2.5876 | 2.5876
2020-05-15 16:00 | Winter | 1.0669 | 1.6405 | 2.4825 | 2.4825 | 2.4825 | 2.4825 | 0.84021 | 0.84021 | 0.84021 | 0.84021 | 0.84021 | 0.84021 | 2.4197 | 3.4903 | 4.1918 | 4.561 | 5.2993 | 6.0377 | 0.75829 | 2.0598 | 2.5835 | 2.5835 | 2.5835 | 2.5835 | 2.0005 | 2.5392 | 2.5392 | 2.5392 | 2.5392 | 2.5392
2020-05-15 17:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.76877 | 0.76877 | 0.76877 | 0.76877 | 0.76877 | 0.76877 | 2.4387 | 3.5178 | 4.2248 | 4.5969 | 5.3411 | 6.0852 | 0.72018 | 1.9563 | 2.4537 | 2.4537 | 2.4537 | 2.4537 | 1.8862 | 2.3941 | 2.3941 | 2.3941 | 2.3941 | 2.3941
2020-05-15 18:00 | Winter | 0.89845 | 1.3815 | 2.0904 | 2.0904 | 2.0904 | 2.0904 | 0.65731 | 0.65731 | 0.65731 | 0.65731 | 0.65731 | 0.65731 | 2.4163 | 3.4855 | 4.186 | 4.5547 | 5.292 | 6.0294 | 0.70113 | 1.9046 | 2.3888 | 2.3888 | 2.3888 | 2.3888 | 1.5081 | 1.9142 | 1.9142 | 1.9142 | 1.9142 | 1.9142
2020-05-15 19:00 | Winter | 0.6316 | 0.97116 | 1.4696 | 1.4696 | 1.4696 | 1.4696 | 0.57157 | 0.57157 | 0.57157 | 0.57157 | 0.57157 | 0.57157 | 2.2426 | 3.2349 | 3.885 | 4.2271 | 4.9115 | 5.5958 | 0.69732 | 1.8942 | 2.3758 | 2.3758 | 2.3758 | 2.3758 | 1.0676 | 1.3551 | 1.3551 | 1.3551 | 1.3551 | 1.3551
2020-05-15 20:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.51156 | 0.51156 | 0.51156 | 0.51156 | 0.51156 | 0.51156 | 2.216 | 3.1964 | 3.8388 | 4.1769 | 4.8531 | 5.5294 | 0.67446 | 1.8321 | 2.2979 | 2.2979 | 2.2979 | 2.2979 | 1.0059 | 1.2768 | 1.2768 | 1.2768 | 1.2768 | 1.2768
2020-05-15 21:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.48584 | 0.48584 | 0.48584 | 0.48584 | 0.48584 | 0.48584 | 2.2291 | 3.2155 | 3.8617 | 4.2018 | 4.8821 | 5.5623 | 0.68589 | 1.8632 | 2.3368 | 2.3368 | 2.3368 | 2.3368 | 0.93358 | 1.185 | 1.185 | 1.185 | 1.185 | 1.185
2020-05-15 22:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 1.9624 | 2.8307 | 3.3996 | 3.699 | 4.2979 | 4.8967 | 0.68208 | 1.8528 | 2.3239 | 2.3239 | 2.3239 | 2.3239 | 0.85744 | 1.0883 | 1.0883 | 1.0883 | 1.0883 | 1.0883
2020-05-15 23:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.47726 | 0.47726 | 0.47726 | 0.47726 | 0.47726 | 0.47726 | 1.9434 | 2.8032 | 3.3666 | 3.6631 | 4.2562 | 4.8492 | 0.62111 | 1.6872 | 2.1161 | 2.1161 | 2.1161 | 2.1161 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-05-16 | Winter | 0.55232 | 0.84926 | 1.2851 | 1.2851 | 1.2851 | 1.2851 | 0.39153 | 0.39153 | 0.39153 | 0.39153 | 0.39153 | 0.39153 | 2.0958 | 3.0231 | 3.6307 | 3.9504 | 4.59 | 5.2295 | 0.57157 | 1.5526 | 1.9474 | 1.9474 | 1.9474 | 1.9474 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-05-16 01:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.39438 | 0.39438 | 0.39438 | 0.39438 | 0.39438 | 0.39438 | 1.6766 | 2.4185 | 2.9045 | 3.1603 | 3.672 | 4.1836 | 0.5449 | 1.4802 | 1.8565 | 1.8565 | 1.8565 | 1.8565 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-05-16 02:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.39153 | 0.39153 | 0.39153 | 0.39153 | 0.39153 | 0.39153 | 1.6957 | 2.446 | 2.9375 | 3.1963 | 3.7137 | 4.2311 | 0.56395 | 1.5319 | 1.9214 | 1.9214 | 1.9214 | 1.9214 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-05-16 03:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 1.6576 | 2.391 | 2.8715 | 3.1244 | 3.6302 | 4.1361 | 0.51442 | 1.3974 | 1.7526 | 1.7526 | 1.7526 | 1.7526 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-05-16 04:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.41034 | 0.41034 | 0.41034 | 0.41034 | 0.41034 | 0.41034 | 1.6478 | 2.3769 | 2.8545 | 3.1059 | 3.6088 | 4.1116 | 0.51823 | 1.4077 | 1.7656 | 1.7656 | 1.7656 | 1.7656 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-05-16 05:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.5287 | 0.5287 | 0.5287 | 0.5287 | 0.5287 | 0.5287 | 1.7047 | 2.459 | 2.9532 | 3.2133 | 3.7335 | 4.2536 | 0.51442 | 1.3974 | 1.7526 | 1.7526 | 1.7526 | 1.7526 | 0.87601 | 1.1119 | 1.1119 | 1.1119 | 1.1119 | 1.1119
2020-05-16 06:00 | Winter | 0.56342 | 0.86632 | 1.3109 | 1.3109 | 1.3109 | 1.3109 | 0.53442 | 0.53442 | 0.53442 | 0.53442 | 0.53442 | 0.53442 | 1.7719 | 2.5559 | 3.0696 | 3.3399 | 3.8806 | 4.4213 | 0.53347 | 1.4491 | 1.8175 | 1.8175 | 1.8175 | 1.8175 | 0.93358 | 1.185 | 1.185 | 1.185 | 1.185 | 1.185
2020-05-16 07:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.583 | 0.583 | 0.583 | 0.583 | 0.583 | 0.583 | 1.8481 | 2.6658 | 3.2016 | 3.4836 | 4.0475 | 4.6115 | 0.54871 | 1.4905 | 1.8695 | 1.8695 | 1.8695 | 1.8695 | 0.97168 | 1.2333 | 1.2333 | 1.2333 | 1.2333 | 1.2333
2020-05-16 08:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.60301 | 0.60301 | 0.60301 | 0.60301 | 0.60301 | 0.60301 | 1.9243 | 2.7758 | 3.3336 | 3.6272 | 4.2144 | 4.8016 | 0.60968 | 1.6561 | 2.0772 | 2.0772 | 2.0772 | 2.0772 | 1.0288 | 1.3059 | 1.3059 | 1.3059 | 1.3059 | 1.3059
2020-05-16 09:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.58586 | 0.58586 | 0.58586 | 0.58586 | 0.58586 | 0.58586 | 1.9714 | 2.8437 | 3.4152 | 3.716 | 4.3176 | 4.9192 | 0.56776 | 1.5423 | 1.9344 | 1.9344 | 1.9344 | 1.9344 | 1.0098 | 1.2817 | 1.2817 | 1.2817 | 1.2817 | 1.2817
2020-05-16 10:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.563 | 0.563 | 0.563 | 0.563 | 0.563 | 0.563 | 2.0386 | 2.9407 | 3.5316 | 3.8427 | 4.4648 | 5.0869 | 0.58301 | 1.5837 | 1.9863 | 1.9863 | 1.9863 | 1.9863 | 1.0098 | 1.2817 | 1.2817 | 1.2817 | 1.2817 | 1.2817
2020-05-16 11:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.55443 | 0.55443 | 0.55443 | 0.55443 | 0.55443 | 0.55443 | 2.0767 | 2.9956 | 3.5977 | 3.9145 | 4.5482 | 5.182 | 0.52585 | 1.4284 | 1.7916 | 1.7916 | 1.7916 | 1.7916 | 1.0479 | 1.3301 | 1.3301 | 1.3301 | 1.3301 | 1.3301
2020-05-16 12:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 2.1529 | 3.1056 | 3.7297 | 4.0582 | 4.7151 | 5.3721 | 0.59444 | 1.6147 | 2.0253 | 2.0253 | 2.0253 | 2.0253 | 1.0479 | 1.3301 | 1.3301 | 1.3301 | 1.3301 | 1.3301
2020-05-16 13:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 2.0386 | 2.9407 | 3.5316 | 3.8427 | 4.4648 | 5.0869 | 0.52585 | 1.4284 | 1.7916 | 1.7916 | 1.7916 | 1.7916 | 1.01 | 1.2819 | 1.2819 | 1.2819 | 1.2819 | 1.2819
2020-05-16 14:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 2.0005 | 2.8857 | 3.4656 | 3.7709 | 4.3813 | 4.9918 | 0.54871 | 1.4905 | 1.8695 | 1.8695 | 1.8695 | 1.8695 | 1.086 | 1.3784 | 1.3784 | 1.3784 | 1.3784 | 1.3784
2020-05-16 15:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.46869 | 0.46869 | 0.46869 | 0.46869 | 0.46869 | 0.46869 | 2.0767 | 2.9956 | 3.5977 | 3.9145 | 4.5482 | 5.182 | 0.52204 | 1.4181 | 1.7786 | 1.7786 | 1.7786 | 1.7786 | 1.0288 | 1.3059 | 1.3059 | 1.3059 | 1.3059 | 1.3059
2020-05-16 16:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 2.0386 | 2.9407 | 3.5316 | 3.8427 | 4.4648 | 5.0869 | 0.60587 | 1.6458 | 2.0642 | 2.0642 | 2.0642 | 2.0642 | 0.93358 | 1.185 | 1.185 | 1.185 | 1.185 | 1.185
2020-05-16 17:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.55157 | 0.55157 | 0.55157 | 0.55157 | 0.55157 | 0.55157 | 2.3435 | 3.3804 | 4.0597 | 4.4173 | 5.1324 | 5.8475 | 0.64397 | 1.7493 | 2.194 | 2.194 | 2.194 | 2.194 | 0.93358 | 1.185 | 1.185 | 1.185 | 1.185 | 1.185
2020-05-16 18:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.51727 | 0.51727 | 0.51727 | 0.51727 | 0.51727 | 0.51727 | 2.2482 | 3.243 | 3.8947 | 4.2377 | 4.9238 | 5.6098 | 0.6516 | 1.77 | 2.22 | 2.22 | 2.22 | 2.22 | 0.91452 | 1.1608 | 1.1608 | 1.1608 | 1.1608 | 1.1608
2020-05-16 19:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.55443 | 0.55443 | 0.55443 | 0.55443 | 0.55443 | 0.55443 | 2.1339 | 3.0781 | 3.6967 | 4.0223 | 4.6734 | 5.3246 | 0.66303 | 1.8011 | 2.2589 | 2.2589 | 2.2589 | 2.2589 | 0.91452 | 1.1608 | 1.1608 | 1.1608 | 1.1608 | 1.1608
2020-05-16 20:00 | Winter | 0.54296 | 0.83487 | 1.2633 | 1.2633 | 1.2633 | 1.2633 | 0.49727 | 0.49727 | 0.49727 | 0.49727 | 0.49727 | 0.49727 | 2.191 | 3.1605 | 3.7957 | 4.13 | 4.7986 | 5.4672 | 0.69732 | 1.8942 | 2.3758 | 2.3758 | 2.3758 | 2.3758 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-05-16 21:00 | Winter | 0.53347 | 0.82027 | 1.2412 | 1.2412 | 1.2412 | 1.2412 | 0.4544 | 0.4544 | 0.4544 | 0.4544 | 0.4544 | 0.4544 | 2.0386 | 2.9407 | 3.5316 | 3.8427 | 4.4648 | 5.0869 | 0.67065 | 1.8218 | 2.2849 | 2.2849 | 2.2849 | 2.2849 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-05-16 22:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.37724 | 0.37724 | 0.37724 | 0.37724 | 0.37724 | 0.37724 | 1.9815 | 2.8582 | 3.4326 | 3.735 | 4.3396 | 4.9443 | 0.62492 | 1.6975 | 2.1291 | 2.1291 | 2.1291 | 2.1291 | 0.82476 | 1.0469 | 1.0469 | 1.0469 | 1.0469 | 1.0469
2020-05-16 23:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.42296 | 0.42296 | 0.42296 | 0.42296 | 0.42296 | 0.42296 | 1.9053 | 2.7483 | 3.3006 | 3.5913 | 4.1727 | 4.7541 | 0.56776 | 1.5423 | 1.9344 | 1.9344 | 1.9344 | 1.9344 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-05-17 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.4001 | 0.4001 | 0.4001 | 0.4001 | 0.4001 | 0.4001 | 1.7719 | 2.5559 | 3.0696 | 3.3399 | 3.8806 | 4.4213 | 0.60206 | 1.6354 | 2.0512 | 2.0512 | 2.0512 | 2.0512 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-05-17 01:00 | Winter | 0.53378 | 0.82075 | 1.242 | 1.242 | 1.242 | 1.242 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 1.6873 | 2.4338 | 2.923 | 3.1804 | 3.6953 | 4.2101 | 0.54109 | 1.4698 | 1.8435 | 1.8435 | 1.8435 | 1.8435 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-05-17 02:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.38009 | 0.38009 | 0.38009 | 0.38009 | 0.38009 | 0.38009 | 1.7528 | 2.5284 | 3.0366 | 3.304 | 3.8389 | 4.3738 | 0.57157 | 1.5526 | 1.9474 | 1.9474 | 1.9474 | 1.9474 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-05-17 03:00 | Winter | 0.53347 | 0.82027 | 1.2412 | 1.2412 | 1.2412 | 1.2412 | 0.38518 | 0.38518 | 0.38518 | 0.38518 | 0.38518 | 0.38518 | 1.7338 | 2.5009 | 3.0036 | 3.2681 | 3.7972 | 4.3262 | 0.48012 | 1.3042 | 1.6358 | 1.6358 | 1.6358 | 1.6358 | 0.80021 | 1.0157 | 1.0157 | 1.0157 | 1.0157 | 1.0157
2020-05-17 04:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 1.6957 | 2.446 | 2.9375 | 3.1963 | 3.7137 | 4.2311 | 0.51442 | 1.3974 | 1.7526 | 1.7526 | 1.7526 | 1.7526 | 0.80021 | 1.0157 | 1.0157 | 1.0157 | 1.0157 | 1.0157
2020-05-17 05:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.50013 | 0.50013 | 0.50013 | 0.50013 | 0.50013 | 0.50013 | 1.7385 | 2.5077 | 3.0117 | 3.277 | 3.8075 | 4.338 | 0.51061 | 1.387 | 1.7396 | 1.7396 | 1.7396 | 1.7396 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-05-17 06:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.46869 | 0.46869 | 0.46869 | 0.46869 | 0.46869 | 0.46869 | 1.829 | 2.6383 | 3.1686 | 3.4477 | 4.0058 | 4.5639 | 0.54109 | 1.4698 | 1.8435 | 1.8435 | 1.8435 | 1.8435 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-05-17 07:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.56586 | 0.56586 | 0.56586 | 0.56586 | 0.56586 | 0.56586 | 1.8481 | 2.6658 | 3.2016 | 3.4836 | 4.0475 | 4.6115 | 0.54109 | 1.4698 | 1.8435 | 1.8435 | 1.8435 | 1.8435 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-05-17 08:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.58872 | 0.58872 | 0.58872 | 0.58872 | 0.58872 | 0.58872 | 1.9815 | 2.8582 | 3.4326 | 3.735 | 4.3396 | 4.9443 | 0.53728 | 1.4595 | 1.8305 | 1.8305 | 1.8305 | 1.8305 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-05-17 09:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.56872 | 0.56872 | 0.56872 | 0.56872 | 0.56872 | 0.56872 | 1.9434 | 2.8032 | 3.3666 | 3.6631 | 4.2562 | 4.8492 | 0.63635 | 1.7286 | 2.1681 | 2.1681 | 2.1681 | 2.1681 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-05-17 10:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.51727 | 0.51727 | 0.51727 | 0.51727 | 0.51727 | 0.51727 | 1.9624 | 2.8307 | 3.3996 | 3.699 | 4.2979 | 4.8967 | 0.62492 | 1.6975 | 2.1291 | 2.1291 | 2.1291 | 2.1291 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-05-17 11:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.43439 | 0.43439 | 0.43439 | 0.43439 | 0.43439 | 0.43439 | 1.9815 | 2.8582 | 3.4326 | 3.735 | 4.3396 | 4.9443 | 0.54871 | 1.4905 | 1.8695 | 1.8695 | 1.8695 | 1.8695 | 0.81939 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04
2020-05-17 12:00 | Winter | 0.56697 | 0.87178 | 1.3192 | 1.3192 | 1.3192 | 1.3192 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 2.0386 | 2.9407 | 3.5316 | 3.8427 | 4.4648 | 5.0869 | 0.5449 | 1.4802 | 1.8565 | 1.8565 | 1.8565 | 1.8565 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-05-17 13:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.42296 | 0.42296 | 0.42296 | 0.42296 | 0.42296 | 0.42296 | 1.9815 | 2.8582 | 3.4326 | 3.735 | 4.3396 | 4.9443 | 0.52585 | 1.4284 | 1.7916 | 1.7916 | 1.7916 | 1.7916 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-05-17 14:00 | Winter | 0.56439 | 0.86782 | 1.3132 | 1.3132 | 1.3132 | 1.3132 | 0.43439 | 0.43439 | 0.43439 | 0.43439 | 0.43439 | 0.43439 | 1.9815 | 2.8582 | 3.4326 | 3.735 | 4.3396 | 4.9443 | 0.48774 | 1.3249 | 1.6618 | 1.6618 | 1.6618 | 1.6618 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-05-17 15:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 2.0196 | 2.9132 | 3.4986 | 3.8068 | 4.4231 | 5.0393 | 0.55252 | 1.5009 | 1.8825 | 1.8825 | 1.8825 | 1.8825 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-05-17 16:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 2.0386 | 2.9407 | 3.5316 | 3.8427 | 4.4648 | 5.0869 | 0.57157 | 1.5526 | 1.9474 | 1.9474 | 1.9474 | 1.9474 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-05-17 17:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.53728 | 0.53728 | 0.53728 | 0.53728 | 0.53728 | 0.53728 | 2.2863 | 3.2979 | 3.9607 | 4.3096 | 5.0072 | 5.7049 | 0.65541 | 1.7803 | 2.233 | 2.233 | 2.233 | 2.233 | 0.86983 | 1.1041 | 1.1041 | 1.1041 | 1.1041 | 1.1041
2020-05-17 18:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.50298 | 0.50298 | 0.50298 | 0.50298 | 0.50298 | 0.50298 | 2.3244 | 3.3529 | 4.0267 | 4.3814 | 5.0907 | 5.8 | 0.64397 | 1.7493 | 2.194 | 2.194 | 2.194 | 2.194 | 0.93358 | 1.185 | 1.185 | 1.185 | 1.185 | 1.185
2020-05-17 19:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.49727 | 0.49727 | 0.49727 | 0.49727 | 0.49727 | 0.49727 | 2.2863 | 3.2979 | 3.9607 | 4.3096 | 5.0072 | 5.7049 | 0.63635 | 1.7286 | 2.1681 | 2.1681 | 2.1681 | 2.1681 | 0.89404 | 1.1348 | 1.1348 | 1.1348 | 1.1348 | 1.1348
2020-05-17 20:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.41153 | 0.41153 | 0.41153 | 0.41153 | 0.41153 | 0.41153 | 2.1529 | 3.1056 | 3.7297 | 4.0582 | 4.7151 | 5.3721 | 0.59444 | 1.6147 | 2.0253 | 2.0253 | 2.0253 | 2.0253 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-05-17 21:00 | Winter | 0.53364 | 0.82054 | 1.2416 | 1.2416 | 1.2416 | 1.2416 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 2.0196 | 2.9132 | 3.4986 | 3.8068 | 4.4231 | 5.0393 | 0.59063 | 1.6044 | 2.0123 | 2.0123 | 2.0123 | 2.0123 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-05-17 22:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 1.9243 | 2.7758 | 3.3336 | 3.6272 | 4.2144 | 4.8016 | 0.58301 | 1.5837 | 1.9863 | 1.9863 | 1.9863 | 1.9863 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-05-17 23:00 | Winter | 0.59145 | 0.90943 | 1.3761 | 1.3761 | 1.3761 | 1.3761 | 0.34294 | 0.34294 | 0.34294 | 0.34294 | 0.34294 | 0.34294 | 1.8485 | 2.6664 | 3.2022 | 3.4843 | 4.0483 | 4.6124 | 0.5068 | 1.3767 | 1.7267 | 1.7267 | 1.7267 | 1.7267 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-05-18 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.38867 | 0.38867 | 0.38867 | 0.38867 | 0.38867 | 0.38867 | 1.6576 | 2.391 | 2.8715 | 3.1244 | 3.6302 | 4.1361 | 0.5449 | 1.4802 | 1.8565 | 1.8565 | 1.8565 | 1.8565 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-05-18 01:00 | Winter | 0.57151 | 0.87876 | 1.3297 | 1.3297 | 1.3297 | 1.3297 | 0.40296 | 0.40296 | 0.40296 | 0.40296 | 0.40296 | 0.40296 | 1.6766 | 2.4185 | 2.9045 | 3.1603 | 3.672 | 4.1836 | 0.48012 | 1.3042 | 1.6358 | 1.6358 | 1.6358 | 1.6358 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-05-18 02:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 1.6576 | 2.391 | 2.8715 | 3.1244 | 3.6302 | 4.1361 | 0.52966 | 1.4388 | 1.8046 | 1.8046 | 1.8046 | 1.8046 | 1.0479 | 1.3301 | 1.3301 | 1.3301 | 1.3301 | 1.3301
2020-05-18 03:00 | Winter | 0.59016 | 0.90743 | 1.3731 | 1.3731 | 1.3731 | 1.3731 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 1.6926 | 2.4416 | 2.9323 | 3.1905 | 3.7071 | 4.2236 | 0.53728 | 1.4595 | 1.8305 | 1.8305 | 1.8305 | 1.8305 | 1.0288 | 1.3059 | 1.3059 | 1.3059 | 1.3059 | 1.3059
2020-05-18 04:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.48584 | 0.48584 | 0.48584 | 0.48584 | 0.48584 | 0.48584 | 1.7338 | 2.5009 | 3.0036 | 3.2681 | 3.7972 | 4.3262 | 0.52966 | 1.4388 | 1.8046 | 1.8046 | 1.8046 | 1.8046 | 1.105 | 1.4026 | 1.4026 | 1.4026 | 1.4026 | 1.4026
2020-05-18 05:00 | Winter | 0.724 | 1.1132 | 1.6845 | 1.6845 | 1.6845 | 1.6845 | 0.58872 | 0.58872 | 0.58872 | 0.58872 | 0.58872 | 0.58872 | 1.8651 | 2.6903 | 3.231 | 3.5155 | 4.0847 | 4.6538 | 0.56014 | 1.5216 | 1.9084 | 1.9084 | 1.9084 | 1.9084 | 1.5149 | 1.9228 | 1.9228 | 1.9228 | 1.9228 | 1.9228
2020-05-18 06:00 | Winter | 0.84063 | 1.2926 | 1.9559 | 1.9559 | 1.9559 | 1.9559 | 0.72304 | 0.72304 | 0.72304 | 0.72304 | 0.72304 | 0.72304 | 2.076 | 2.9946 | 3.5965 | 3.9132 | 4.5467 | 5.1802 | 0.6173 | 1.6768 | 2.1032 | 2.1032 | 2.1032 | 2.1032 | 1.85 | 2.3481 | 2.3481 | 2.3481 | 2.3481 | 2.3481
2020-05-18 07:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 0.80878 | 0.80878 | 0.80878 | 0.80878 | 0.80878 | 0.80878 | 2.3435 | 3.3804 | 4.0597 | 4.4173 | 5.1324 | 5.8475 | 0.78115 | 2.1219 | 2.6614 | 2.6614 | 2.6614 | 2.6614 | 2.2482 | 2.8536 | 2.8536 | 2.8536 | 2.8536 | 2.8536
2020-05-18 08:00 | Winter | 1.1622 | 1.787 | 2.7041 | 2.7041 | 2.7041 | 2.7041 | 0.91166 | 0.91166 | 0.91166 | 0.91166 | 0.91166 | 0.91166 | 2.5911 | 3.7377 | 4.4888 | 4.8842 | 5.6749 | 6.4656 | 0.80402 | 2.184 | 2.7393 | 2.7393 | 2.7393 | 2.7393 | 2.4578 | 3.1196 | 3.1196 | 3.1196 | 3.1196 | 3.1196
2020-05-18 09:00 | Winter | 1.1622 | 1.787 | 2.7041 | 2.7041 | 2.7041 | 2.7041 | 0.92595 | 0.92595 | 0.92595 | 0.92595 | 0.92595 | 0.92595 | 2.4768 | 3.5728 | 4.2908 | 4.6687 | 5.4245 | 6.1803 | 0.85355 | 2.3186 | 2.9081 | 2.9081 | 2.9081 | 2.9081 | 2.4578 | 3.1196 | 3.1196 | 3.1196 | 3.1196 | 3.1196
2020-05-18 10:00 | Winter | 1.1488 | 1.7663 | 2.6728 | 2.6728 | 2.6728 | 2.6728 | 1.0746 | 1.0746 | 1.0746 | 1.0746 | 1.0746 | 1.0746 | 2.4768 | 3.5728 | 4.2908 | 4.6687 | 5.4245 | 6.1803 | 0.75448 | 2.0495 | 2.5705 | 2.5705 | 2.5705 | 2.5705 | 2.4578 | 3.1196 | 3.1196 | 3.1196 | 3.1196 | 3.1196
2020-05-18 11:00 | Winter | 1.1241 | 1.7284 | 2.6155 | 2.6155 | 2.6155 | 2.6155 | 0.91738 | 0.91738 | 0.91738 | 0.91738 | 0.91738 | 0.91738 | 2.4197 | 3.4903 | 4.1918 | 4.561 | 5.2993 | 6.0377 | 0.74686 | 2.0288 | 2.5446 | 2.5446 | 2.5446 | 2.5446 | 2.3816 | 3.0229 | 3.0229 | 3.0229 | 3.0229 | 3.0229
2020-05-18 12:00 | Winter | 1.2956 | 1.9921 | 3.0144 | 3.0144 | 3.0144 | 3.0144 | 0.96882 | 0.96882 | 0.96882 | 0.96882 | 0.96882 | 0.96882 | 2.3816 | 3.4353 | 4.1258 | 4.4891 | 5.2159 | 5.9426 | 0.73162 | 1.9874 | 2.4926 | 2.4926 | 2.4926 | 2.4926 | 2.325 | 2.9511 | 2.9511 | 2.9511 | 2.9511 | 2.9511
2020-05-18 13:00 | Winter | 1.2384 | 1.9042 | 2.8814 | 2.8814 | 2.8814 | 2.8814 | 0.8545 | 0.8545 | 0.8545 | 0.8545 | 0.8545 | 0.8545 | 2.3816 | 3.4353 | 4.1258 | 4.4891 | 5.2159 | 5.9426 | 0.68208 | 1.8528 | 2.3239 | 2.3239 | 2.3239 | 2.3239 | 2.3054 | 2.9261 | 2.9261 | 2.9261 | 2.9261 | 2.9261
2020-05-18 14:00 | Winter | 1.1432 | 1.7577 | 2.6598 | 2.6598 | 2.6598 | 2.6598 | 0.81164 | 0.81164 | 0.81164 | 0.81164 | 0.81164 | 0.81164 | 2.3625 | 3.4079 | 4.0927 | 4.4532 | 5.1741 | 5.8951 | 0.69732 | 1.8942 | 2.3758 | 2.3758 | 2.3758 | 2.3758 | 2.191 | 2.781 | 2.781 | 2.781 | 2.781 | 2.781
2020-05-18 15:00 | Winter | 1.1622 | 1.787 | 2.7041 | 2.7041 | 2.7041 | 2.7041 | 0.80306 | 0.80306 | 0.80306 | 0.80306 | 0.80306 | 0.80306 | 2.2101 | 3.188 | 3.8287 | 4.1659 | 4.8403 | 5.5147 | 0.69732 | 1.8942 | 2.3758 | 2.3758 | 2.3758 | 2.3758 | 2.0767 | 2.6359 | 2.6359 | 2.6359 | 2.6359 | 2.6359
2020-05-18 16:00 | Winter | 1.1241 | 1.7284 | 2.6155 | 2.6155 | 2.6155 | 2.6155 | 0.78327 | 0.78327 | 0.78327 | 0.78327 | 0.78327 | 0.78327 | 2.3244 | 3.3529 | 4.0267 | 4.3814 | 5.0907 | 5.8 | 0.67065 | 1.8218 | 2.2849 | 2.2849 | 2.2849 | 2.2849 | 2.0767 | 2.6359 | 2.6359 | 2.6359 | 2.6359 | 2.6359
2020-05-18 17:00 | Winter | 1.105 | 1.6991 | 2.5711 | 2.5711 | 2.5711 | 2.5711 | 0.65731 | 0.65731 | 0.65731 | 0.65731 | 0.65731 | 0.65731 | 2.4006 | 3.4628 | 4.1588 | 4.525 | 5.2576 | 5.9902 | 0.7964 | 2.1633 | 2.7133 | 2.7133 | 2.7133 | 2.7133 | 2.0199 | 2.5638 | 2.5638 | 2.5638 | 2.5638 | 2.5638
2020-05-18 18:00 | Winter | 0.8961 | 1.3779 | 2.085 | 2.085 | 2.085 | 2.085 | 0.58872 | 0.58872 | 0.58872 | 0.58872 | 0.58872 | 0.58872 | 2.3054 | 3.3254 | 3.9937 | 4.3455 | 5.049 | 5.7525 | 0.75829 | 2.0598 | 2.5835 | 2.5835 | 2.5835 | 2.5835 | 1.4891 | 1.8901 | 1.8901 | 1.8901 | 1.8901 | 1.8901
2020-05-18 19:00 | Winter | 0.65152 | 1.0018 | 1.5159 | 1.5159 | 1.5159 | 1.5159 | 0.47726 | 0.47726 | 0.47726 | 0.47726 | 0.47726 | 0.47726 | 2.3054 | 3.3254 | 3.9937 | 4.3455 | 5.049 | 5.7525 | 0.67323 | 1.8288 | 2.2937 | 2.2937 | 2.2937 | 2.2937 | 1.0497 | 1.3323 | 1.3323 | 1.3323 | 1.3323 | 1.3323
2020-05-18 20:00 | Winter | 0.5792 | 0.89059 | 1.3476 | 1.3476 | 1.3476 | 1.3476 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 2.0958 | 3.0231 | 3.6307 | 3.9504 | 4.59 | 5.2295 | 0.64397 | 1.7493 | 2.194 | 2.194 | 2.194 | 2.194 | 1.0098 | 1.2817 | 1.2817 | 1.2817 | 1.2817 | 1.2817
2020-05-18 21:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.42582 | 0.42582 | 0.42582 | 0.42582 | 0.42582 | 0.42582 | 2.0386 | 2.9407 | 3.5316 | 3.8427 | 4.4648 | 5.0869 | 0.62873 | 1.7079 | 2.1421 | 2.1421 | 2.1421 | 2.1421 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-05-18 22:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 1.8862 | 2.7208 | 3.2676 | 3.5554 | 4.131 | 4.7066 | 0.5792 | 1.5733 | 1.9733 | 1.9733 | 1.9733 | 1.9733 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-05-18 23:00 | Winter | 0.5719 | 0.87937 | 1.3307 | 1.3307 | 1.3307 | 1.3307 | 0.35723 | 0.35723 | 0.35723 | 0.35723 | 0.35723 | 0.35723 | 1.7909 | 2.5834 | 3.1026 | 3.3758 | 3.9223 | 4.4688 | 0.55252 | 1.5009 | 1.8825 | 1.8825 | 1.8825 | 1.8825 | 0.80021 | 1.0157 | 1.0157 | 1.0157 | 1.0157 | 1.0157
2020-05-19 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.35723 | 0.35723 | 0.35723 | 0.35723 | 0.35723 | 0.35723 | 1.6766 | 2.4185 | 2.9045 | 3.1603 | 3.672 | 4.1836 | 0.52585 | 1.4284 | 1.7916 | 1.7916 | 1.7916 | 1.7916 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-05-19 01:00 | Winter | 0.57199 | 0.8795 | 1.3309 | 1.3309 | 1.3309 | 1.3309 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 1.6195 | 2.336 | 2.8055 | 3.0526 | 3.5468 | 4.041 | 0.52204 | 1.4181 | 1.7786 | 1.7786 | 1.7786 | 1.7786 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-05-19 02:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.38867 | 0.38867 | 0.38867 | 0.38867 | 0.38867 | 0.38867 | 1.6004 | 2.3086 | 2.7725 | 3.0167 | 3.5051 | 3.9934 | 0.50299 | 1.3663 | 1.7137 | 1.7137 | 1.7137 | 1.7137 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-05-19 03:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.43154 | 0.43154 | 0.43154 | 0.43154 | 0.43154 | 0.43154 | 1.6195 | 2.336 | 2.8055 | 3.0526 | 3.5468 | 4.041 | 0.5068 | 1.3767 | 1.7267 | 1.7267 | 1.7267 | 1.7267 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-05-19 04:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 1.682 | 2.4262 | 2.9138 | 3.1705 | 3.6837 | 4.197 | 0.48012 | 1.3042 | 1.6358 | 1.6358 | 1.6358 | 1.6358 | 1.0744 | 1.3638 | 1.3638 | 1.3638 | 1.3638 | 1.3638
2020-05-19 05:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.61444 | 0.61444 | 0.61444 | 0.61444 | 0.61444 | 0.61444 | 1.7528 | 2.5284 | 3.0366 | 3.304 | 3.8389 | 4.3738 | 0.64779 | 1.7596 | 2.207 | 2.207 | 2.207 | 2.207 | 1.414 | 1.7948 | 1.7948 | 1.7948 | 1.7948 | 1.7948
2020-05-19 06:00 | Winter | 0.66684 | 1.0253 | 1.5515 | 1.5515 | 1.5515 | 1.5515 | 0.69446 | 0.69446 | 0.69446 | 0.69446 | 0.69446 | 0.69446 | 2.0196 | 2.9132 | 3.4986 | 3.8068 | 4.4231 | 5.0393 | 0.65541 | 1.7803 | 2.233 | 2.233 | 2.233 | 2.233 | 1.7724 | 2.2496 | 2.2496 | 2.2496 | 2.2496 | 2.2496
2020-05-19 07:00 | Winter | 1.0308 | 1.5849 | 2.3983 | 2.3983 | 2.3983 | 2.3983 | 0.80306 | 0.80306 | 0.80306 | 0.80306 | 0.80306 | 0.80306 | 2.3625 | 3.4079 | 4.0927 | 4.4532 | 5.1741 | 5.8951 | 0.73162 | 1.9874 | 2.4926 | 2.4926 | 2.4926 | 2.4926 | 2.1529 | 2.7327 | 2.7327 | 2.7327 | 2.7327 | 2.7327
2020-05-19 08:00 | Winter | 1.2194 | 1.8749 | 2.8371 | 2.8371 | 2.8371 | 2.8371 | 0.88022 | 0.88022 | 0.88022 | 0.88022 | 0.88022 | 0.88022 | 2.3816 | 3.4353 | 4.1258 | 4.4891 | 5.2159 | 5.9426 | 0.78496 | 2.1323 | 2.6744 | 2.6744 | 2.6744 | 2.6744 | 2.4387 | 3.0954 | 3.0954 | 3.0954 | 3.0954 | 3.0954
2020-05-19 09:00 | Winter | 1.1432 | 1.7577 | 2.6598 | 2.6598 | 2.6598 | 2.6598 | 0.94881 | 0.94881 | 0.94881 | 0.94881 | 0.94881 | 0.94881 | 2.3816 | 3.4353 | 4.1258 | 4.4891 | 5.2159 | 5.9426 | 0.78115 | 2.1219 | 2.6614 | 2.6614 | 2.6614 | 2.6614 | 2.3816 | 3.0229 | 3.0229 | 3.0229 | 3.0229 | 3.0229
2020-05-19 10:00 | Winter | 1.105 | 1.6991 | 2.5711 | 2.5711 | 2.5711 | 2.5711 | 0.91452 | 0.91452 | 0.91452 | 0.91452 | 0.91452 | 0.91452 | 2.4197 | 3.4903 | 4.1918 | 4.561 | 5.2993 | 6.0377 | 0.76972 | 2.0909 | 2.6225 | 2.6225 | 2.6225 | 2.6225 | 2.3435 | 2.9745 | 2.9745 | 2.9745 | 2.9745 | 2.9745
2020-05-19 11:00 | Winter | 1.2765 | 1.9628 | 2.9701 | 2.9701 | 2.9701 | 2.9701 | 0.80592 | 0.80592 | 0.80592 | 0.80592 | 0.80592 | 0.80592 | 2.4578 | 3.5453 | 4.2578 | 4.6328 | 5.3828 | 6.1328 | 0.69351 | 1.8839 | 2.3628 | 2.3628 | 2.3628 | 2.3628 | 2.2673 | 2.8778 | 2.8778 | 2.8778 | 2.8778 | 2.8778
2020-05-19 12:00 | Winter | 1.2003 | 1.8456 | 2.7928 | 2.7928 | 2.7928 | 2.7928 | 0.84593 | 0.84593 | 0.84593 | 0.84593 | 0.84593 | 0.84593 | 2.4578 | 3.5453 | 4.2578 | 4.6328 | 5.3828 | 6.1328 | 0.67065 | 1.8218 | 2.2849 | 2.2849 | 2.2849 | 2.2849 | 2.2863 | 2.902 | 2.902 | 2.902 | 2.902 | 2.902
2020-05-19 13:00 | Winter | 1.2194 | 1.8749 | 2.8371 | 2.8371 | 2.8371 | 2.8371 | 0.87451 | 0.87451 | 0.87451 | 0.87451 | 0.87451 | 0.87451 | 2.4006 | 3.4628 | 4.1588 | 4.525 | 5.2576 | 5.9902 | 0.7964 | 2.1633 | 2.7133 | 2.7133 | 2.7133 | 2.7133 | 2.2291 | 2.8294 | 2.8294 | 2.8294 | 2.8294 | 2.8294
2020-05-19 14:00 | Winter | 1.1622 | 1.787 | 2.7041 | 2.7041 | 2.7041 | 2.7041 | 0.82021 | 0.82021 | 0.82021 | 0.82021 | 0.82021 | 0.82021 | 2.2676 | 3.2709 | 3.9283 | 4.2742 | 4.9662 | 5.6582 | 0.80021 | 2.1737 | 2.7263 | 2.7263 | 2.7263 | 2.7263 | 2.1148 | 2.6843 | 2.6843 | 2.6843 | 2.6843 | 2.6843
2020-05-19 15:00 | Winter | 1.1622 | 1.787 | 2.7041 | 2.7041 | 2.7041 | 2.7041 | 0.79163 | 0.79163 | 0.79163 | 0.79163 | 0.79163 | 0.79163 | 2.2673 | 3.2705 | 3.9277 | 4.2736 | 4.9655 | 5.6574 | 0.78115 | 2.1219 | 2.6614 | 2.6614 | 2.6614 | 2.6614 | 2.0958 | 2.6601 | 2.6601 | 2.6601 | 2.6601 | 2.6601
2020-05-19 16:00 | Winter | 1.105 | 1.6991 | 2.5711 | 2.5711 | 2.5711 | 2.5711 | 0.83736 | 0.83736 | 0.83736 | 0.83736 | 0.83736 | 0.83736 | 2.1858 | 3.1529 | 3.7866 | 4.1201 | 4.7871 | 5.4541 | 0.68589 | 1.8632 | 2.3368 | 2.3368 | 2.3368 | 2.3368 | 2.0386 | 2.5876 | 2.5876 | 2.5876 | 2.5876 | 2.5876
2020-05-19 17:00 | Winter | 1.0669 | 1.6405 | 2.4825 | 2.4825 | 2.4825 | 2.4825 | 0.73733 | 0.73733 | 0.73733 | 0.73733 | 0.73733 | 0.73733 | 2.4387 | 3.5178 | 4.2248 | 4.5969 | 5.3411 | 6.0852 | 0.70875 | 1.9253 | 2.4147 | 2.4147 | 2.4147 | 2.4147 | 2.0016 | 2.5406 | 2.5406 | 2.5406 | 2.5406 | 2.5406
2020-05-19 18:00 | Winter | 0.84861 | 1.3048 | 1.9745 | 1.9745 | 1.9745 | 1.9745 | 0.6173 | 0.6173 | 0.6173 | 0.6173 | 0.6173 | 0.6173 | 2.3435 | 3.3804 | 4.0597 | 4.4173 | 5.1324 | 5.8475 | 0.67827 | 1.8425 | 2.3109 | 2.3109 | 2.3109 | 2.3109 | 1.5226 | 1.9326 | 1.9326 | 1.9326 | 1.9326 | 1.9326
2020-05-19 19:00 | Winter | 0.64438 | 0.99081 | 1.4993 | 1.4993 | 1.4993 | 1.4993 | 0.55157 | 0.55157 | 0.55157 | 0.55157 | 0.55157 | 0.55157 | 2.1529 | 3.1056 | 3.7297 | 4.0582 | 4.7151 | 5.3721 | 0.69351 | 1.8839 | 2.3628 | 2.3628 | 2.3628 | 2.3628 | 1.0672 | 1.3546 | 1.3546 | 1.3546 | 1.3546 | 1.3546
2020-05-19 20:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 2.0577 | 2.9681 | 3.5647 | 3.8786 | 4.5065 | 5.1344 | 0.64016 | 1.7389 | 2.1811 | 2.1811 | 2.1811 | 2.1811 | 0.97877 | 1.2423 | 1.2423 | 1.2423 | 1.2423 | 1.2423
2020-05-19 21:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.3575 | 0.3575 | 0.3575 | 0.3575 | 0.3575 | 0.3575 | 1.9815 | 2.8582 | 3.4326 | 3.735 | 4.3396 | 4.9443 | 0.63635 | 1.7286 | 2.1681 | 2.1681 | 2.1681 | 2.1681 | 0.87974 | 1.1166 | 1.1166 | 1.1166 | 1.1166 | 1.1166
2020-05-19 22:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.34866 | 0.34866 | 0.34866 | 0.34866 | 0.34866 | 0.34866 | 1.8481 | 2.6658 | 3.2016 | 3.4836 | 4.0475 | 4.6115 | 0.63254 | 1.7182 | 2.1551 | 2.1551 | 2.1551 | 2.1551 | 0.80021 | 1.0157 | 1.0157 | 1.0157 | 1.0157 | 1.0157
2020-05-19 23:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.34866 | 0.34866 | 0.34866 | 0.34866 | 0.34866 | 0.34866 | 1.6576 | 2.391 | 2.8715 | 3.1244 | 3.6302 | 4.1361 | 0.56014 | 1.5216 | 1.9084 | 1.9084 | 1.9084 | 1.9084 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-05-20 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.39724 | 0.39724 | 0.39724 | 0.39724 | 0.39724 | 0.39724 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.52966 | 1.4388 | 1.8046 | 1.8046 | 1.8046 | 1.8046 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-05-20 01:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.4001 | 0.4001 | 0.4001 | 0.4001 | 0.4001 | 0.4001 | 1.5623 | 2.2536 | 2.7065 | 2.9449 | 3.4216 | 3.8984 | 0.49155 | 1.3353 | 1.6747 | 1.6747 | 1.6747 | 1.6747 | 0.80021 | 1.0157 | 1.0157 | 1.0157 | 1.0157 | 1.0157
2020-05-20 02:00 | Winter | 0.56213 | 0.86434 | 1.3079 | 1.3079 | 1.3079 | 1.3079 | 0.38295 | 0.38295 | 0.38295 | 0.38295 | 0.38295 | 0.38295 | 1.5623 | 2.2536 | 2.7065 | 2.9449 | 3.4216 | 3.8984 | 0.5068 | 1.3767 | 1.7267 | 1.7267 | 1.7267 | 1.7267 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-05-20 03:00 | Winter | 0.57389 | 0.88242 | 1.3353 | 1.3353 | 1.3353 | 1.3353 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 1.5594 | 2.2493 | 2.7014 | 2.9393 | 3.4152 | 3.891 | 0.48774 | 1.3249 | 1.6618 | 1.6618 | 1.6618 | 1.6618 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-05-20 04:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 1.5859 | 2.2876 | 2.7473 | 2.9893 | 3.4733 | 3.9572 | 0.52966 | 1.4388 | 1.8046 | 1.8046 | 1.8046 | 1.8046 | 1.0098 | 1.2817 | 1.2817 | 1.2817 | 1.2817 | 1.2817
2020-05-20 05:00 | Winter | 0.59097 | 0.90868 | 1.375 | 1.375 | 1.375 | 1.375 | 0.50298 | 0.50298 | 0.50298 | 0.50298 | 0.50298 | 0.50298 | 1.7528 | 2.5284 | 3.0366 | 3.304 | 3.8389 | 4.3738 | 0.54871 | 1.4905 | 1.8695 | 1.8695 | 1.8695 | 1.8695 | 1.3124 | 1.6658 | 1.6658 | 1.6658 | 1.6658 | 1.6658
2020-05-20 06:00 | Winter | 0.61835 | 0.95078 | 1.4387 | 1.4387 | 1.4387 | 1.4387 | 0.82307 | 0.82307 | 0.82307 | 0.82307 | 0.82307 | 0.82307 | 1.9624 | 2.8307 | 3.3996 | 3.699 | 4.2979 | 4.8967 | 0.60968 | 1.6561 | 2.0772 | 2.0772 | 2.0772 | 2.0772 | 1.6457 | 2.0888 | 2.0888 | 2.0888 | 2.0888 | 2.0888
2020-05-20 07:00 | Winter | 1.0184 | 1.5659 | 2.3696 | 2.3696 | 2.3696 | 2.3696 | 0.84593 | 0.84593 | 0.84593 | 0.84593 | 0.84593 | 0.84593 | 2.1529 | 3.1056 | 3.7297 | 4.0582 | 4.7151 | 5.3721 | 0.73924 | 2.0081 | 2.5186 | 2.5186 | 2.5186 | 2.5186 | 2.0577 | 2.6118 | 2.6118 | 2.6118 | 2.6118 | 2.6118
2020-05-20 08:00 | Winter | 1.1432 | 1.7577 | 2.6598 | 2.6598 | 2.6598 | 2.6598 | 0.90309 | 0.90309 | 0.90309 | 0.90309 | 0.90309 | 0.90309 | 2.3054 | 3.3254 | 3.9937 | 4.3455 | 5.049 | 5.7525 | 0.7621 | 2.0702 | 2.5965 | 2.5965 | 2.5965 | 2.5965 | 2.2572 | 2.8651 | 2.8651 | 2.8651 | 2.8651 | 2.8651
2020-05-20 09:00 | Winter | 1.1241 | 1.7284 | 2.6155 | 2.6155 | 2.6155 | 2.6155 | 1.0088 | 1.0088 | 1.0088 | 1.0088 | 1.0088 | 1.0088 | 2.3435 | 3.3804 | 4.0597 | 4.4173 | 5.1324 | 5.8475 | 0.74686 | 2.0288 | 2.5446 | 2.5446 | 2.5446 | 2.5446 | 2.3244 | 2.9503 | 2.9503 | 2.9503 | 2.9503 | 2.9503
2020-05-20 10:00 | Winter | 1.1241 | 1.7284 | 2.6155 | 2.6155 | 2.6155 | 2.6155 | 0.98025 | 0.98025 | 0.98025 | 0.98025 | 0.98025 | 0.98025 | 2.3816 | 3.4353 | 4.1258 | 4.4891 | 5.2159 | 5.9426 | 0.70494 | 1.9149 | 2.4018 | 2.4018 | 2.4018 | 2.4018 | 2.2658 | 2.8759 | 2.8759 | 2.8759 | 2.8759 | 2.8759
2020-05-20 11:00 | Winter | 1.1432 | 1.7577 | 2.6598 | 2.6598 | 2.6598 | 2.6598 | 0.9088 | 0.9088 | 0.9088 | 0.9088 | 0.9088 | 0.9088 | 2.4006 | 3.4628 | 4.1588 | 4.525 | 5.2576 | 5.9902 | 0.82688 | 2.2461 | 2.8172 | 2.8172 | 2.8172 | 2.8172 | 2.2291 | 2.8294 | 2.8294 | 2.8294 | 2.8294 | 2.8294
2020-05-20 12:00 | Winter | 1.105 | 1.6991 | 2.5711 | 2.5711 | 2.5711 | 2.5711 | 0.95167 | 0.95167 | 0.95167 | 0.95167 | 0.95167 | 0.95167 | 2.4197 | 3.4903 | 4.1918 | 4.561 | 5.2993 | 6.0377 | 0.81164 | 2.2047 | 2.7653 | 2.7653 | 2.7653 | 2.7653 | 2.2291 | 2.8294 | 2.8294 | 2.8294 | 2.8294 | 2.8294
2020-05-20 13:00 | Winter | 1.2575 | 1.9335 | 2.9258 | 2.9258 | 2.9258 | 2.9258 | 0.94024 | 0.94024 | 0.94024 | 0.94024 | 0.94024 | 0.94024 | 2.3816 | 3.4353 | 4.1258 | 4.4891 | 5.2159 | 5.9426 | 0.7964 | 2.1633 | 2.7133 | 2.7133 | 2.7133 | 2.7133 | 2.2291 | 2.8294 | 2.8294 | 2.8294 | 2.8294 | 2.8294
2020-05-20 14:00 | Winter | 1.1813 | 1.8163 | 2.7485 | 2.7485 | 2.7485 | 2.7485 | 0.92023 | 0.92023 | 0.92023 | 0.92023 | 0.92023 | 0.92023 | 2.3244 | 3.3529 | 4.0267 | 4.3814 | 5.0907 | 5.8 | 0.74305 | 2.0184 | 2.5316 | 2.5316 | 2.5316 | 2.5316 | 2.2101 | 2.8052 | 2.8052 | 2.8052 | 2.8052 | 2.8052
2020-05-20 15:00 | Winter | 1.1432 | 1.7577 | 2.6598 | 2.6598 | 2.6598 | 2.6598 | 0.82878 | 0.82878 | 0.82878 | 0.82878 | 0.82878 | 0.82878 | 2.3244 | 3.3529 | 4.0267 | 4.3814 | 5.0907 | 5.8 | 0.76972 | 2.0909 | 2.6225 | 2.6225 | 2.6225 | 2.6225 | 2.1245 | 2.6966 | 2.6966 | 2.6966 | 2.6966 | 2.6966
2020-05-20 16:00 | Winter | 1.0288 | 1.582 | 2.3938 | 2.3938 | 2.3938 | 2.3938 | 0.80878 | 0.80878 | 0.80878 | 0.80878 | 0.80878 | 0.80878 | 2.3054 | 3.3254 | 3.9937 | 4.3455 | 5.049 | 5.7525 | 0.70113 | 1.9046 | 2.3888 | 2.3888 | 2.3888 | 2.3888 | 2.172 | 2.7569 | 2.7569 | 2.7569 | 2.7569 | 2.7569
2020-05-20 17:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.75162 | 0.75162 | 0.75162 | 0.75162 | 0.75162 | 0.75162 | 2.4091 | 3.4751 | 4.1734 | 4.541 | 5.2762 | 6.0113 | 0.69351 | 1.8839 | 2.3628 | 2.3628 | 2.3628 | 2.3628 | 1.9624 | 2.4908 | 2.4908 | 2.4908 | 2.4908 | 2.4908
2020-05-20 18:00 | Winter | 0.8623 | 1.3259 | 2.0063 | 2.0063 | 2.0063 | 2.0063 | 0.69446 | 0.69446 | 0.69446 | 0.69446 | 0.69446 | 0.69446 | 2.4387 | 3.5178 | 4.2248 | 4.5969 | 5.3411 | 6.0852 | 0.69351 | 1.8839 | 2.3628 | 2.3628 | 2.3628 | 2.3628 | 1.5481 | 1.965 | 1.965 | 1.965 | 1.965 | 1.965
2020-05-20 19:00 | Winter | 0.6612 | 1.0167 | 1.5384 | 1.5384 | 1.5384 | 1.5384 | 0.49155 | 0.49155 | 0.49155 | 0.49155 | 0.49155 | 0.49155 | 2.2763 | 3.2835 | 3.9434 | 4.2908 | 4.9854 | 5.68 | 0.65541 | 1.7803 | 2.233 | 2.233 | 2.233 | 2.233 | 1.115 | 1.4153 | 1.4153 | 1.4153 | 1.4153 | 1.4153
2020-05-20 20:00 | Winter | 0.58977 | 0.90685 | 1.3722 | 1.3722 | 1.3722 | 1.3722 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 2.0196 | 2.9132 | 3.4986 | 3.8068 | 4.4231 | 5.0393 | 0.66303 | 1.8011 | 2.2589 | 2.2589 | 2.2589 | 2.2589 | 1.0088 | 1.2804 | 1.2804 | 1.2804 | 1.2804 | 1.2804
2020-05-20 21:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 2.0196 | 2.9132 | 3.4986 | 3.8068 | 4.4231 | 5.0393 | 0.60587 | 1.6458 | 2.0642 | 2.0642 | 2.0642 | 2.0642 | 0.93358 | 1.185 | 1.185 | 1.185 | 1.185 | 1.185
2020-05-20 22:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.34866 | 0.34866 | 0.34866 | 0.34866 | 0.34866 | 0.34866 | 1.8481 | 2.6658 | 3.2016 | 3.4836 | 4.0475 | 4.6115 | 0.58682 | 1.594 | 1.9993 | 1.9993 | 1.9993 | 1.9993 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-05-20 23:00 | Winter | 0.58528 | 0.89994 | 1.3618 | 1.3618 | 1.3618 | 1.3618 | 0.37438 | 0.37438 | 0.37438 | 0.37438 | 0.37438 | 0.37438 | 1.7719 | 2.5559 | 3.0696 | 3.3399 | 3.8806 | 4.4213 | 0.56776 | 1.5423 | 1.9344 | 1.9344 | 1.9344 | 1.9344 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-05-21 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.39438 | 0.39438 | 0.39438 | 0.39438 | 0.39438 | 0.39438 | 1.6004 | 2.3086 | 2.7725 | 3.0167 | 3.5051 | 3.9934 | 0.54109 | 1.4698 | 1.8435 | 1.8435 | 1.8435 | 1.8435 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-05-21 01:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.37724 | 0.37724 | 0.37724 | 0.37724 | 0.37724 | 0.37724 | 1.5623 | 2.2536 | 2.7065 | 2.9449 | 3.4216 | 3.8984 | 0.51442 | 1.3974 | 1.7526 | 1.7526 | 1.7526 | 1.7526 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-05-21 02:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.40296 | 0.40296 | 0.40296 | 0.40296 | 0.40296 | 0.40296 | 1.5623 | 2.2536 | 2.7065 | 2.9449 | 3.4216 | 3.8984 | 0.5068 | 1.3767 | 1.7267 | 1.7267 | 1.7267 | 1.7267 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-05-21 03:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.4001 | 0.4001 | 0.4001 | 0.4001 | 0.4001 | 0.4001 | 1.5623 | 2.2536 | 2.7065 | 2.9449 | 3.4216 | 3.8984 | 0.5068 | 1.3767 | 1.7267 | 1.7267 | 1.7267 | 1.7267 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-05-21 04:00 | Winter | 0.59544 | 0.91555 | 1.3854 | 1.3854 | 1.3854 | 1.3854 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 1.6524 | 2.3835 | 2.8625 | 3.1147 | 3.6189 | 4.1231 | 0.49536 | 1.3456 | 1.6877 | 1.6877 | 1.6877 | 1.6877 | 1.03 | 1.3074 | 1.3074 | 1.3074 | 1.3074 | 1.3074
2020-05-21 05:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.47726 | 0.47726 | 0.47726 | 0.47726 | 0.47726 | 0.47726 | 1.718 | 2.4782 | 2.9762 | 3.2383 | 3.7626 | 4.2868 | 0.60206 | 1.6354 | 2.0512 | 2.0512 | 2.0512 | 2.0512 | 1.3593 | 1.7253 | 1.7253 | 1.7253 | 1.7253 | 1.7253
2020-05-21 06:00 | Winter | 0.62959 | 0.96807 | 1.4649 | 1.4649 | 1.4649 | 1.4649 | 0.67731 | 0.67731 | 0.67731 | 0.67731 | 0.67731 | 0.67731 | 1.9728 | 2.8457 | 3.4176 | 3.7186 | 4.3206 | 4.9226 | 0.63635 | 1.7286 | 2.1681 | 2.1681 | 2.1681 | 2.1681 | 1.7524 | 2.2243 | 2.2243 | 2.2243 | 2.2243 | 2.2243
2020-05-21 07:00 | Winter | 1.0142 | 1.5595 | 2.3598 | 2.3598 | 2.3598 | 2.3598 | 0.8002 | 0.8002 | 0.8002 | 0.8002 | 0.8002 | 0.8002 | 2.2863 | 3.2979 | 3.9607 | 4.3096 | 5.0072 | 5.7049 | 0.69351 | 1.8839 | 2.3628 | 2.3628 | 2.3628 | 2.3628 | 2.1529 | 2.7327 | 2.7327 | 2.7327 | 2.7327 | 2.7327
2020-05-21 08:00 | Winter | 1.1432 | 1.7577 | 2.6598 | 2.6598 | 2.6598 | 2.6598 | 0.89166 | 0.89166 | 0.89166 | 0.89166 | 0.89166 | 0.89166 | 2.3054 | 3.3254 | 3.9937 | 4.3455 | 5.049 | 5.7525 | 0.7964 | 2.1633 | 2.7133 | 2.7133 | 2.7133 | 2.7133 | 2.3244 | 2.9503 | 2.9503 | 2.9503 | 2.9503 | 2.9503
2020-05-21 09:00 | Winter | 1.1813 | 1.8163 | 2.7485 | 2.7485 | 2.7485 | 2.7485 | 0.87165 | 0.87165 | 0.87165 | 0.87165 | 0.87165 | 0.87165 | 2.3054 | 3.3254 | 3.9937 | 4.3455 | 5.049 | 5.7525 | 0.724 | 1.9667 | 2.4667 | 2.4667 | 2.4667 | 2.4667 | 2.3435 | 2.9745 | 2.9745 | 2.9745 | 2.9745 | 2.9745
2020-05-21 10:00 | Winter | 1.0669 | 1.6405 | 2.4825 | 2.4825 | 2.4825 | 2.4825 | 0.90023 | 0.90023 | 0.90023 | 0.90023 | 0.90023 | 0.90023 | 2.3244 | 3.3529 | 4.0267 | 4.3814 | 5.0907 | 5.8 | 0.75829 | 2.0598 | 2.5835 | 2.5835 | 2.5835 | 2.5835 | 2.2863 | 2.902 | 2.902 | 2.902 | 2.902 | 2.902
2020-05-21 11:00 | Winter | 1.105 | 1.6991 | 2.5711 | 2.5711 | 2.5711 | 2.5711 | 0.82307 | 0.82307 | 0.82307 | 0.82307 | 0.82307 | 0.82307 | 2.3054 | 3.3254 | 3.9937 | 4.3455 | 5.049 | 5.7525 | 0.74305 | 2.0184 | 2.5316 | 2.5316 | 2.5316 | 2.5316 | 2.191 | 2.781 | 2.781 | 2.781 | 2.781 | 2.781
2020-05-21 12:00 | Winter | 1.086 | 1.6698 | 2.5268 | 2.5268 | 2.5268 | 2.5268 | 0.79163 | 0.79163 | 0.79163 | 0.79163 | 0.79163 | 0.79163 | 2.2892 | 3.3021 | 3.9657 | 4.315 | 5.0135 | 5.7121 | 0.75829 | 2.0598 | 2.5835 | 2.5835 | 2.5835 | 2.5835 | 2.1721 | 2.757 | 2.757 | 2.757 | 2.757 | 2.757
2020-05-21 13:00 | Winter | 1.1622 | 1.787 | 2.7041 | 2.7041 | 2.7041 | 2.7041 | 0.83164 | 0.83164 | 0.83164 | 0.83164 | 0.83164 | 0.83164 | 2.3244 | 3.3529 | 4.0267 | 4.3814 | 5.0907 | 5.8 | 0.75067 | 2.0391 | 2.5575 | 2.5575 | 2.5575 | 2.5575 | 2.1529 | 2.7327 | 2.7327 | 2.7327 | 2.7327 | 2.7327
2020-05-21 14:00 | Winter | 1.11 | 1.7067 | 2.5826 | 2.5826 | 2.5826 | 2.5826 | 0.87451 | 0.87451 | 0.87451 | 0.87451 | 0.87451 | 0.87451 | 2.2482 | 3.243 | 3.8947 | 4.2377 | 4.9238 | 5.6098 | 0.72018 | 1.9563 | 2.4537 | 2.4537 | 2.4537 | 2.4537 | 2.1148 | 2.6843 | 2.6843 | 2.6843 | 2.6843 | 2.6843
2020-05-21 15:00 | Winter | 1.1241 | 1.7284 | 2.6155 | 2.6155 | 2.6155 | 2.6155 | 0.88308 | 0.88308 | 0.88308 | 0.88308 | 0.88308 | 0.88308 | 2.2482 | 3.243 | 3.8947 | 4.2377 | 4.9238 | 5.6098 | 0.74686 | 2.0288 | 2.5446 | 2.5446 | 2.5446 | 2.5446 | 2.0386 | 2.5876 | 2.5876 | 2.5876 | 2.5876 | 2.5876
2020-05-21 16:00 | Winter | 1.105 | 1.6991 | 2.5711 | 2.5711 | 2.5711 | 2.5711 | 0.85736 | 0.85736 | 0.85736 | 0.85736 | 0.85736 | 0.85736 | 2.1933 | 3.1637 | 3.7996 | 4.1342 | 4.8035 | 5.4728 | 0.76972 | 2.0909 | 2.6225 | 2.6225 | 2.6225 | 2.6225 | 2.0577 | 2.6118 | 2.6118 | 2.6118 | 2.6118 | 2.6118
2020-05-21 17:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.82592 | 0.82592 | 0.82592 | 0.82592 | 0.82592 | 0.82592 | 2.4197 | 3.4903 | 4.1918 | 4.561 | 5.2993 | 6.0377 | 0.76591 | 2.0805 | 2.6095 | 2.6095 | 2.6095 | 2.6095 | 2.0162 | 2.5591 | 2.5591 | 2.5591 | 2.5591 | 2.5591
2020-05-21 18:00 | Winter | 0.81714 | 1.2564 | 1.9012 | 1.9012 | 1.9012 | 1.9012 | 0.71447 | 0.71447 | 0.71447 | 0.71447 | 0.71447 | 0.71447 | 2.3054 | 3.3254 | 3.9937 | 4.3455 | 5.049 | 5.7525 | 0.72018 | 1.9563 | 2.4537 | 2.4537 | 2.4537 | 2.4537 | 1.5633 | 1.9842 | 1.9842 | 1.9842 | 1.9842 | 1.9842
2020-05-21 19:00 | Winter | 0.64812 | 0.99657 | 1.508 | 1.508 | 1.508 | 1.508 | 0.57086 | 0.57086 | 0.57086 | 0.57086 | 0.57086 | 0.57086 | 2.192 | 3.1619 | 3.7974 | 4.1318 | 4.8007 | 5.4696 | 0.6897 | 1.8735 | 2.3498 | 2.3498 | 2.3498 | 2.3498 | 1.1437 | 1.4516 | 1.4516 | 1.4516 | 1.4516 | 1.4516
2020-05-21 20:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 2.0577 | 2.9681 | 3.5647 | 3.8786 | 4.5065 | 5.1344 | 0.6173 | 1.6768 | 2.1032 | 2.1032 | 2.1032 | 2.1032 | 1.0479 | 1.3301 | 1.3301 | 1.3301 | 1.3301 | 1.3301
2020-05-21 21:00 | Winter | 0.55287 | 0.85011 | 1.2864 | 1.2864 | 1.2864 | 1.2864 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 1.9815 | 2.8582 | 3.4326 | 3.735 | 4.3396 | 4.9443 | 0.66303 | 1.8011 | 2.2589 | 2.2589 | 2.2589 | 2.2589 | 0.96951 | 1.2306 | 1.2306 | 1.2306 | 1.2306 | 1.2306
2020-05-21 22:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 1.829 | 2.6383 | 3.1686 | 3.4477 | 4.0058 | 4.5639 | 0.59444 | 1.6147 | 2.0253 | 2.0253 | 2.0253 | 2.0253 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-05-21 23:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.41153 | 0.41153 | 0.41153 | 0.41153 | 0.41153 | 0.41153 | 1.6576 | 2.391 | 2.8715 | 3.1244 | 3.6302 | 4.1361 | 0.59063 | 1.6044 | 2.0123 | 2.0123 | 2.0123 | 2.0123 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-05-22 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.36295 | 0.36295 | 0.36295 | 0.36295 | 0.36295 | 0.36295 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.54871 | 1.4905 | 1.8695 | 1.8695 | 1.8695 | 1.8695 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-05-22 01:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.36295 | 0.36295 | 0.36295 | 0.36295 | 0.36295 | 0.36295 | 1.5433 | 2.2261 | 2.6735 | 2.909 | 3.3799 | 3.8508 | 0.53728 | 1.4595 | 1.8305 | 1.8305 | 1.8305 | 1.8305 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-05-22 02:00 | Winter | 0.53347 | 0.82027 | 1.2412 | 1.2412 | 1.2412 | 1.2412 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 1.5242 | 2.1986 | 2.6405 | 2.873 | 3.3382 | 3.8033 | 0.56014 | 1.5216 | 1.9084 | 1.9084 | 1.9084 | 1.9084 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-05-22 03:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.39153 | 0.39153 | 0.39153 | 0.39153 | 0.39153 | 0.39153 | 1.5564 | 2.2451 | 2.6963 | 2.9338 | 3.4087 | 3.8836 | 0.52585 | 1.4284 | 1.7916 | 1.7916 | 1.7916 | 1.7916 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-05-22 04:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 1.5623 | 2.2536 | 2.7065 | 2.9449 | 3.4216 | 3.8984 | 0.54871 | 1.4905 | 1.8695 | 1.8695 | 1.8695 | 1.8695 | 1.0282 | 1.305 | 1.305 | 1.305 | 1.305 | 1.305
2020-05-22 05:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.57729 | 0.57729 | 0.57729 | 0.57729 | 0.57729 | 0.57729 | 1.6766 | 2.4185 | 2.9045 | 3.1603 | 3.672 | 4.1836 | 0.60587 | 1.6458 | 2.0642 | 2.0642 | 2.0642 | 2.0642 | 1.4287 | 1.8135 | 1.8135 | 1.8135 | 1.8135 | 1.8135
2020-05-22 06:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.71733 | 0.71733 | 0.71733 | 0.71733 | 0.71733 | 0.71733 | 1.8481 | 2.6658 | 3.2016 | 3.4836 | 4.0475 | 4.6115 | 0.68208 | 1.8528 | 2.3239 | 2.3239 | 2.3239 | 2.3239 | 1.7798 | 2.259 | 2.259 | 2.259 | 2.259 | 2.259
2020-05-22 07:00 | Winter | 1.0313 | 1.5857 | 2.3994 | 2.3994 | 2.3994 | 2.3994 | 0.78591 | 0.78591 | 0.78591 | 0.78591 | 0.78591 | 0.78591 | 2.2261 | 3.2111 | 3.8564 | 4.1961 | 4.8754 | 5.5547 | 0.80021 | 2.1737 | 2.7263 | 2.7263 | 2.7263 | 2.7263 | 2.0958 | 2.6601 | 2.6601 | 2.6601 | 2.6601 | 2.6601
2020-05-22 08:00 | Winter | 1.1622 | 1.787 | 2.7041 | 2.7041 | 2.7041 | 2.7041 | 0.93452 | 0.93452 | 0.93452 | 0.93452 | 0.93452 | 0.93452 | 2.3816 | 3.4353 | 4.1258 | 4.4891 | 5.2159 | 5.9426 | 0.80783 | 2.1944 | 2.7523 | 2.7523 | 2.7523 | 2.7523 | 2.3054 | 2.9261 | 2.9261 | 2.9261 | 2.9261 | 2.9261
2020-05-22 09:00 | Winter | 1.1622 | 1.787 | 2.7041 | 2.7041 | 2.7041 | 2.7041 | 0.9431 | 0.9431 | 0.9431 | 0.9431 | 0.9431 | 0.9431 | 2.4578 | 3.5453 | 4.2578 | 4.6328 | 5.3828 | 6.1328 | 0.78496 | 2.1323 | 2.6744 | 2.6744 | 2.6744 | 2.6744 | 2.3625 | 2.9987 | 2.9987 | 2.9987 | 2.9987 | 2.9987
2020-05-22 10:00 | Winter | 1.086 | 1.6698 | 2.5268 | 2.5268 | 2.5268 | 2.5268 | 0.99168 | 0.99168 | 0.99168 | 0.99168 | 0.99168 | 0.99168 | 2.3625 | 3.4079 | 4.0927 | 4.4532 | 5.1741 | 5.8951 | 0.74686 | 2.0288 | 2.5446 | 2.5446 | 2.5446 | 2.5446 | 2.3435 | 2.9745 | 2.9745 | 2.9745 | 2.9745 | 2.9745
2020-05-22 11:00 | Winter | 1.086 | 1.6698 | 2.5268 | 2.5268 | 2.5268 | 2.5268 | 0.92098 | 0.92098 | 0.92098 | 0.92098 | 0.92098 | 0.92098 | 2.3229 | 3.3507 | 4.0241 | 4.3785 | 5.0873 | 5.7961 | 0.72781 | 1.977 | 2.4796 | 2.4796 | 2.4796 | 2.4796 | 2.3435 | 2.9745 | 2.9745 | 2.9745 | 2.9745 | 2.9745
2020-05-22 12:00 | Winter | 1.086 | 1.6698 | 2.5268 | 2.5268 | 2.5268 | 2.5268 | 0.89737 | 0.89737 | 0.89737 | 0.89737 | 0.89737 | 0.89737 | 2.3429 | 3.3796 | 4.0588 | 4.4163 | 5.1313 | 5.8462 | 0.76972 | 2.0909 | 2.6225 | 2.6225 | 2.6225 | 2.6225 | 2.3625 | 2.9987 | 2.9987 | 2.9987 | 2.9987 | 2.9987
2020-05-22 13:00 | Winter | 1.086 | 1.6698 | 2.5268 | 2.5268 | 2.5268 | 2.5268 | 0.97453 | 0.97453 | 0.97453 | 0.97453 | 0.97453 | 0.97453 | 2.3435 | 3.3804 | 4.0597 | 4.4173 | 5.1324 | 5.8475 | 0.76591 | 2.0805 | 2.6095 | 2.6095 | 2.6095 | 2.6095 | 2.2482 | 2.8536 | 2.8536 | 2.8536 | 2.8536 | 2.8536
2020-05-22 14:00 | Winter | 1.0669 | 1.6405 | 2.4825 | 2.4825 | 2.4825 | 2.4825 | 0.95453 | 0.95453 | 0.95453 | 0.95453 | 0.95453 | 0.95453 | 2.3054 | 3.3254 | 3.9937 | 4.3455 | 5.049 | 5.7525 | 0.77734 | 2.1116 | 2.6484 | 2.6484 | 2.6484 | 2.6484 | 2.2482 | 2.8536 | 2.8536 | 2.8536 | 2.8536 | 2.8536
2020-05-22 15:00 | Winter | 1.0288 | 1.582 | 2.3938 | 2.3938 | 2.3938 | 2.3938 | 0.77448 | 0.77448 | 0.77448 | 0.77448 | 0.77448 | 0.77448 | 2.3244 | 3.3529 | 4.0267 | 4.3814 | 5.0907 | 5.8 | 0.75067 | 2.0391 | 2.5575 | 2.5575 | 2.5575 | 2.5575 | 2.1529 | 2.7327 | 2.7327 | 2.7327 | 2.7327 | 2.7327
2020-05-22 16:00 | Winter | 1.0669 | 1.6405 | 2.4825 | 2.4825 | 2.4825 | 2.4825 | 0.81164 | 0.81164 | 0.81164 | 0.81164 | 0.81164 | 0.81164 | 2.3435 | 3.3804 | 4.0597 | 4.4173 | 5.1324 | 5.8475 | 0.81164 | 2.2047 | 2.7653 | 2.7653 | 2.7653 | 2.7653 | 2.2101 | 2.8052 | 2.8052 | 2.8052 | 2.8052 | 2.8052
2020-05-22 17:00 | Winter | 0.95292 | 1.4652 | 2.2172 | 2.2172 | 2.2172 | 2.2172 | 0.78877 | 0.78877 | 0.78877 | 0.78877 | 0.78877 | 0.78877 | 2.4387 | 3.5178 | 4.2248 | 4.5969 | 5.3411 | 6.0852 | 0.78115 | 2.1219 | 2.6614 | 2.6614 | 2.6614 | 2.6614 | 2.0577 | 2.6118 | 2.6118 | 2.6118 | 2.6118 | 2.6118
2020-05-22 18:00 | Winter | 0.83959 | 1.291 | 1.9535 | 1.9535 | 1.9535 | 1.9535 | 0.70304 | 0.70304 | 0.70304 | 0.70304 | 0.70304 | 0.70304 | 2.3263 | 3.3557 | 4.03 | 4.385 | 5.0949 | 5.8048 | 0.73924 | 2.0081 | 2.5186 | 2.5186 | 2.5186 | 2.5186 | 1.6967 | 2.1535 | 2.1535 | 2.1535 | 2.1535 | 2.1535
2020-05-22 19:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.60587 | 0.60587 | 0.60587 | 0.60587 | 0.60587 | 0.60587 | 2.2101 | 3.188 | 3.8287 | 4.1659 | 4.8403 | 5.5147 | 0.724 | 1.9667 | 2.4667 | 2.4667 | 2.4667 | 2.4667 | 1.1427 | 1.4504 | 1.4504 | 1.4504 | 1.4504 | 1.4504
2020-05-22 20:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.53442 | 0.53442 | 0.53442 | 0.53442 | 0.53442 | 0.53442 | 2.0005 | 2.8857 | 3.4656 | 3.7709 | 4.3813 | 4.9918 | 0.73162 | 1.9874 | 2.4926 | 2.4926 | 2.4926 | 2.4926 | 1.0871 | 1.3798 | 1.3798 | 1.3798 | 1.3798 | 1.3798
2020-05-22 21:00 | Winter | 0.55258 | 0.84965 | 1.2857 | 1.2857 | 1.2857 | 1.2857 | 0.50298 | 0.50298 | 0.50298 | 0.50298 | 0.50298 | 0.50298 | 1.9545 | 2.8193 | 3.3859 | 3.6842 | 4.2806 | 4.877 | 0.67065 | 1.8218 | 2.2849 | 2.2849 | 2.2849 | 2.2849 | 0.95159 | 1.2078 | 1.2078 | 1.2078 | 1.2078 | 1.2078
2020-05-22 22:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 1.8672 | 2.6933 | 3.2346 | 3.5195 | 4.0892 | 4.659 | 0.70113 | 1.9046 | 2.3888 | 2.3888 | 2.3888 | 2.3888 | 0.87652 | 1.1125 | 1.1125 | 1.1125 | 1.1125 | 1.1125
2020-05-22 23:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.4001 | 0.4001 | 0.4001 | 0.4001 | 0.4001 | 0.4001 | 1.7528 | 2.5284 | 3.0366 | 3.304 | 3.8389 | 4.3738 | 0.59444 | 1.6147 | 2.0253 | 2.0253 | 2.0253 | 2.0253 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-05-23 | Winter | 0.55247 | 0.84948 | 1.2854 | 1.2854 | 1.2854 | 1.2854 | 0.41153 | 0.41153 | 0.41153 | 0.41153 | 0.41153 | 0.41153 | 1.6004 | 2.3086 | 2.7725 | 3.0167 | 3.5051 | 3.9934 | 0.59444 | 1.6147 | 2.0253 | 2.0253 | 2.0253 | 2.0253 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-05-23 01:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 1.5623 | 2.2536 | 2.7065 | 2.9449 | 3.4216 | 3.8984 | 0.55252 | 1.5009 | 1.8825 | 1.8825 | 1.8825 | 1.8825 | 0.80021 | 1.0157 | 1.0157 | 1.0157 | 1.0157 | 1.0157
2020-05-23 02:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 1.5376 | 2.218 | 2.6637 | 2.8984 | 3.3676 | 3.8368 | 0.55252 | 1.5009 | 1.8825 | 1.8825 | 1.8825 | 1.8825 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-05-23 03:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.39153 | 0.39153 | 0.39153 | 0.39153 | 0.39153 | 0.39153 | 1.5433 | 2.2261 | 2.6735 | 2.909 | 3.3799 | 3.8508 | 0.54871 | 1.4905 | 1.8695 | 1.8695 | 1.8695 | 1.8695 | 0.83708 | 1.0625 | 1.0625 | 1.0625 | 1.0625 | 1.0625
2020-05-23 04:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.38867 | 0.38867 | 0.38867 | 0.38867 | 0.38867 | 0.38867 | 1.5623 | 2.2536 | 2.7065 | 2.9449 | 3.4216 | 3.8984 | 0.53347 | 1.4491 | 1.8175 | 1.8175 | 1.8175 | 1.8175 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-05-23 05:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 1.5623 | 2.2536 | 2.7065 | 2.9449 | 3.4216 | 3.8984 | 0.56014 | 1.5216 | 1.9084 | 1.9084 | 1.9084 | 1.9084 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-05-23 06:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 1.6576 | 2.391 | 2.8715 | 3.1244 | 3.6302 | 4.1361 | 0.59063 | 1.6044 | 2.0123 | 2.0123 | 2.0123 | 2.0123 | 0.88164 | 1.119 | 1.119 | 1.119 | 1.119 | 1.119
2020-05-23 07:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.52585 | 0.52585 | 0.52585 | 0.52585 | 0.52585 | 0.52585 | 1.7528 | 2.5284 | 3.0366 | 3.304 | 3.8389 | 4.3738 | 0.5792 | 1.5733 | 1.9733 | 1.9733 | 1.9733 | 1.9733 | 1.1241 | 1.4268 | 1.4268 | 1.4268 | 1.4268 | 1.4268
2020-05-23 08:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.59158 | 0.59158 | 0.59158 | 0.59158 | 0.59158 | 0.59158 | 1.8672 | 2.6933 | 3.2346 | 3.5195 | 4.0892 | 4.659 | 0.58301 | 1.5837 | 1.9863 | 1.9863 | 1.9863 | 1.9863 | 1.1241 | 1.4268 | 1.4268 | 1.4268 | 1.4268 | 1.4268
2020-05-23 09:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.60873 | 0.60873 | 0.60873 | 0.60873 | 0.60873 | 0.60873 | 1.8919 | 2.7291 | 3.2775 | 3.5662 | 4.1435 | 4.7209 | 0.59444 | 1.6147 | 2.0253 | 2.0253 | 2.0253 | 2.0253 | 1.0068 | 1.278 | 1.278 | 1.278 | 1.278 | 1.278
2020-05-23 10:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.57729 | 0.57729 | 0.57729 | 0.57729 | 0.57729 | 0.57729 | 1.9815 | 2.8582 | 3.4326 | 3.735 | 4.3396 | 4.9443 | 0.63254 | 1.7182 | 2.1551 | 2.1551 | 2.1551 | 2.1551 | 1.0669 | 1.3542 | 1.3542 | 1.3542 | 1.3542 | 1.3542
2020-05-23 11:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.56014 | 0.56014 | 0.56014 | 0.56014 | 0.56014 | 0.56014 | 2.0386 | 2.9407 | 3.5316 | 3.8427 | 4.4648 | 5.0869 | 0.55252 | 1.5009 | 1.8825 | 1.8825 | 1.8825 | 1.8825 | 1.1241 | 1.4268 | 1.4268 | 1.4268 | 1.4268 | 1.4268
2020-05-23 12:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.51731 | 0.51731 | 0.51731 | 0.51731 | 0.51731 | 0.51731 | 1.9624 | 2.8307 | 3.3996 | 3.699 | 4.2979 | 4.8967 | 0.61349 | 1.6665 | 2.0902 | 2.0902 | 2.0902 | 2.0902 | 1.0669 | 1.3542 | 1.3542 | 1.3542 | 1.3542 | 1.3542
2020-05-23 13:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.56014 | 0.56014 | 0.56014 | 0.56014 | 0.56014 | 0.56014 | 1.9624 | 2.8307 | 3.3996 | 3.699 | 4.2979 | 4.8967 | 0.54101 | 1.4696 | 1.8432 | 1.8432 | 1.8432 | 1.8432 | 1.0669 | 1.3542 | 1.3542 | 1.3542 | 1.3542 | 1.3542
2020-05-23 14:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.57157 | 0.57157 | 0.57157 | 0.57157 | 0.57157 | 0.57157 | 1.9624 | 2.8307 | 3.3996 | 3.699 | 4.2979 | 4.8967 | 0.56395 | 1.5319 | 1.9214 | 1.9214 | 1.9214 | 1.9214 | 1.0288 | 1.3059 | 1.3059 | 1.3059 | 1.3059 | 1.3059
2020-05-23 15:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.59158 | 0.59158 | 0.59158 | 0.59158 | 0.59158 | 0.59158 | 2.0386 | 2.9407 | 3.5316 | 3.8427 | 4.4648 | 5.0869 | 0.56014 | 1.5216 | 1.9084 | 1.9084 | 1.9084 | 1.9084 | 1.0098 | 1.2817 | 1.2817 | 1.2817 | 1.2817 | 1.2817
2020-05-23 16:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.56014 | 0.56014 | 0.56014 | 0.56014 | 0.56014 | 0.56014 | 2.1148 | 3.0506 | 3.6637 | 3.9863 | 4.6317 | 5.277 | 0.5792 | 1.5733 | 1.9733 | 1.9733 | 1.9733 | 1.9733 | 0.97168 | 1.2333 | 1.2333 | 1.2333 | 1.2333 | 1.2333
2020-05-23 17:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.57157 | 0.57157 | 0.57157 | 0.57157 | 0.57157 | 0.57157 | 2.191 | 3.1605 | 3.7957 | 4.13 | 4.7986 | 5.4672 | 0.6516 | 1.77 | 2.22 | 2.22 | 2.22 | 2.22 | 0.99073 | 1.2575 | 1.2575 | 1.2575 | 1.2575 | 1.2575
2020-05-23 18:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.56586 | 0.56586 | 0.56586 | 0.56586 | 0.56586 | 0.56586 | 2.172 | 3.133 | 3.7627 | 4.0941 | 4.7569 | 5.4197 | 0.62492 | 1.6975 | 2.1291 | 2.1291 | 2.1291 | 2.1291 | 0.93358 | 1.185 | 1.185 | 1.185 | 1.185 | 1.185
2020-05-23 19:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.49155 | 0.49155 | 0.49155 | 0.49155 | 0.49155 | 0.49155 | 2.0767 | 2.9956 | 3.5977 | 3.9145 | 4.5482 | 5.182 | 0.62873 | 1.7079 | 2.1421 | 2.1421 | 2.1421 | 2.1421 | 0.93358 | 1.185 | 1.185 | 1.185 | 1.185 | 1.185
2020-05-23 20:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 2.0386 | 2.9407 | 3.5316 | 3.8427 | 4.4648 | 5.0869 | 0.65541 | 1.7803 | 2.233 | 2.233 | 2.233 | 2.233 | 0.93358 | 1.185 | 1.185 | 1.185 | 1.185 | 1.185
2020-05-23 21:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 2.0577 | 2.9681 | 3.5647 | 3.8786 | 4.5065 | 5.1344 | 0.62492 | 1.6975 | 2.1291 | 2.1291 | 2.1291 | 2.1291 | 0.91242 | 1.1581 | 1.1581 | 1.1581 | 1.1581 | 1.1581
2020-05-23 22:00 | Winter | 0.5715 | 0.87874 | 1.3297 | 1.3297 | 1.3297 | 1.3297 | 0.41439 | 0.41439 | 0.41439 | 0.41439 | 0.41439 | 0.41439 | 1.8862 | 2.7208 | 3.2676 | 3.5554 | 4.131 | 4.7066 | 0.57157 | 1.5526 | 1.9474 | 1.9474 | 1.9474 | 1.9474 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-05-23 23:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.35437 | 0.35437 | 0.35437 | 0.35437 | 0.35437 | 0.35437 | 1.81 | 2.6109 | 3.1356 | 3.4117 | 3.9641 | 4.5164 | 0.56395 | 1.5319 | 1.9214 | 1.9214 | 1.9214 | 1.9214 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-05-24 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.36009 | 0.36009 | 0.36009 | 0.36009 | 0.36009 | 0.36009 | 1.6766 | 2.4185 | 2.9045 | 3.1603 | 3.672 | 4.1836 | 0.49536 | 1.3456 | 1.6877 | 1.6877 | 1.6877 | 1.6877 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-05-24 01:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.37724 | 0.37724 | 0.37724 | 0.37724 | 0.37724 | 0.37724 | 1.6766 | 2.4185 | 2.9045 | 3.1603 | 3.672 | 4.1836 | 0.49155 | 1.3353 | 1.6747 | 1.6747 | 1.6747 | 1.6747 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-05-24 02:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.38295 | 0.38295 | 0.38295 | 0.38295 | 0.38295 | 0.38295 | 1.5623 | 2.2536 | 2.7065 | 2.9449 | 3.4216 | 3.8984 | 0.49918 | 1.356 | 1.7007 | 1.7007 | 1.7007 | 1.7007 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-05-24 03:00 | Winter | 0.55255 | 0.84961 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.39438 | 0.39438 | 0.39438 | 0.39438 | 0.39438 | 0.39438 | 1.5242 | 2.1986 | 2.6405 | 2.873 | 3.3382 | 3.8033 | 0.52966 | 1.4388 | 1.8046 | 1.8046 | 1.8046 | 1.8046 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-05-24 04:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.39153 | 0.39153 | 0.39153 | 0.39153 | 0.39153 | 0.39153 | 1.5623 | 2.2536 | 2.7065 | 2.9449 | 3.4216 | 3.8984 | 0.49197 | 1.3364 | 1.6761 | 1.6761 | 1.6761 | 1.6761 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-05-24 05:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.50298 | 0.50298 | 0.50298 | 0.50298 | 0.50298 | 0.50298 | 1.6004 | 2.3086 | 2.7725 | 3.0167 | 3.5051 | 3.9934 | 0.50299 | 1.3663 | 1.7137 | 1.7137 | 1.7137 | 1.7137 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-05-24 06:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.5068 | 1.3767 | 1.7267 | 1.7267 | 1.7267 | 1.7267 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-05-24 07:00 | Winter | 0.58782 | 0.90384 | 1.3677 | 1.3677 | 1.3677 | 1.3677 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 1.7719 | 2.5559 | 3.0696 | 3.3399 | 3.8806 | 4.4213 | 0.52585 | 1.4284 | 1.7916 | 1.7916 | 1.7916 | 1.7916 | 1.0098 | 1.2817 | 1.2817 | 1.2817 | 1.2817 | 1.2817
2020-05-24 08:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.53442 | 0.53442 | 0.53442 | 0.53442 | 0.53442 | 0.53442 | 1.8277 | 2.6364 | 3.1662 | 3.4451 | 4.0028 | 4.5605 | 0.59063 | 1.6044 | 2.0123 | 2.0123 | 2.0123 | 2.0123 | 1.0669 | 1.3542 | 1.3542 | 1.3542 | 1.3542 | 1.3542
2020-05-24 09:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.55157 | 0.55157 | 0.55157 | 0.55157 | 0.55157 | 0.55157 | 1.8481 | 2.6658 | 3.2016 | 3.4836 | 4.0475 | 4.6115 | 0.59444 | 1.6147 | 2.0253 | 2.0253 | 2.0253 | 2.0253 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-05-24 10:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.54585 | 0.54585 | 0.54585 | 0.54585 | 0.54585 | 0.54585 | 1.8862 | 2.7208 | 3.2676 | 3.5554 | 4.131 | 4.7066 | 0.55633 | 1.5112 | 1.8954 | 1.8954 | 1.8954 | 1.8954 | 0.91452 | 1.1608 | 1.1608 | 1.1608 | 1.1608 | 1.1608
2020-05-24 11:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.51727 | 0.51727 | 0.51727 | 0.51727 | 0.51727 | 0.51727 | 1.8672 | 2.6933 | 3.2346 | 3.5195 | 4.0892 | 4.659 | 0.52966 | 1.4388 | 1.8046 | 1.8046 | 1.8046 | 1.8046 | 0.97168 | 1.2333 | 1.2333 | 1.2333 | 1.2333 | 1.2333
2020-05-24 12:00 | Winter | 0.56843 | 0.87402 | 1.3226 | 1.3226 | 1.3226 | 1.3226 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 1.9434 | 2.8032 | 3.3666 | 3.6631 | 4.2562 | 4.8492 | 0.51823 | 1.4077 | 1.7656 | 1.7656 | 1.7656 | 1.7656 | 0.95263 | 1.2092 | 1.2092 | 1.2092 | 1.2092 | 1.2092
2020-05-24 13:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 1.9243 | 2.7758 | 3.3336 | 3.6272 | 4.2144 | 4.8016 | 0.5068 | 1.3767 | 1.7267 | 1.7267 | 1.7267 | 1.7267 | 0.99073 | 1.2575 | 1.2575 | 1.2575 | 1.2575 | 1.2575
2020-05-24 14:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.52585 | 0.52585 | 0.52585 | 0.52585 | 0.52585 | 0.52585 | 1.9243 | 2.7758 | 3.3336 | 3.6272 | 4.2144 | 4.8016 | 0.53347 | 1.4491 | 1.8175 | 1.8175 | 1.8175 | 1.8175 | 0.98443 | 1.2495 | 1.2495 | 1.2495 | 1.2495 | 1.2495
2020-05-24 15:00 | Winter | 0.58994 | 0.9071 | 1.3726 | 1.3726 | 1.3726 | 1.3726 | 0.46869 | 0.46869 | 0.46869 | 0.46869 | 0.46869 | 0.46869 | 1.9624 | 2.8307 | 3.3996 | 3.699 | 4.2979 | 4.8967 | 0.55252 | 1.5009 | 1.8825 | 1.8825 | 1.8825 | 1.8825 | 0.97168 | 1.2333 | 1.2333 | 1.2333 | 1.2333 | 1.2333
2020-05-24 16:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 2.0196 | 2.9132 | 3.4986 | 3.8068 | 4.4231 | 5.0393 | 0.60968 | 1.6561 | 2.0772 | 2.0772 | 2.0772 | 2.0772 | 0.91452 | 1.1608 | 1.1608 | 1.1608 | 1.1608 | 1.1608
2020-05-24 17:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.46869 | 0.46869 | 0.46869 | 0.46869 | 0.46869 | 0.46869 | 2.2101 | 3.188 | 3.8287 | 4.1659 | 4.8403 | 5.5147 | 0.66684 | 1.8114 | 2.2719 | 2.2719 | 2.2719 | 2.2719 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-05-24 18:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.49727 | 0.49727 | 0.49727 | 0.49727 | 0.49727 | 0.49727 | 2.191 | 3.1605 | 3.7957 | 4.13 | 4.7986 | 5.4672 | 0.65922 | 1.7907 | 2.246 | 2.246 | 2.246 | 2.246 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-05-24 19:00 | Winter | 0.55958 | 0.86041 | 1.302 | 1.302 | 1.302 | 1.302 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 2.191 | 3.1605 | 3.7957 | 4.13 | 4.7986 | 5.4672 | 0.62873 | 1.7079 | 2.1421 | 2.1421 | 2.1421 | 2.1421 | 0.8364 | 1.0616 | 1.0616 | 1.0616 | 1.0616 | 1.0616
2020-05-24 20:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 2.1339 | 3.0781 | 3.6967 | 4.0223 | 4.6734 | 5.3246 | 0.63254 | 1.7182 | 2.1551 | 2.1551 | 2.1551 | 2.1551 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-05-24 21:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 2.0005 | 2.8857 | 3.4656 | 3.7709 | 4.3813 | 4.9918 | 0.62492 | 1.6975 | 2.1291 | 2.1291 | 2.1291 | 2.1291 | 0.85802 | 1.0891 | 1.0891 | 1.0891 | 1.0891 | 1.0891
2020-05-24 22:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.4001 | 0.4001 | 0.4001 | 0.4001 | 0.4001 | 0.4001 | 1.9088 | 2.7535 | 3.3068 | 3.5981 | 4.1806 | 4.7631 | 0.54871 | 1.4905 | 1.8695 | 1.8695 | 1.8695 | 1.8695 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-05-24 23:00 | Winter | 0.55843 | 0.85865 | 1.2993 | 1.2993 | 1.2993 | 1.2993 | 0.36866 | 0.36866 | 0.36866 | 0.36866 | 0.36866 | 0.36866 | 1.7909 | 2.5834 | 3.1026 | 3.3758 | 3.9223 | 4.4688 | 0.5449 | 1.4802 | 1.8565 | 1.8565 | 1.8565 | 1.8565 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-05-25 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.37145 | 0.37145 | 0.37145 | 0.37145 | 0.37145 | 0.37145 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.5068 | 1.3767 | 1.7267 | 1.7267 | 1.7267 | 1.7267 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-05-25 01:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.39438 | 0.39438 | 0.39438 | 0.39438 | 0.39438 | 0.39438 | 1.5814 | 2.2811 | 2.7395 | 2.9808 | 3.4633 | 3.9459 | 0.51061 | 1.387 | 1.7396 | 1.7396 | 1.7396 | 1.7396 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-05-25 02:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 1.5814 | 2.2811 | 2.7395 | 2.9808 | 3.4633 | 3.9459 | 0.52966 | 1.4388 | 1.8046 | 1.8046 | 1.8046 | 1.8046 | 1.0288 | 1.3059 | 1.3059 | 1.3059 | 1.3059 | 1.3059
2020-05-25 03:00 | Winter | 0.57153 | 0.87879 | 1.3298 | 1.3298 | 1.3298 | 1.3298 | 0.37152 | 0.37152 | 0.37152 | 0.37152 | 0.37152 | 0.37152 | 1.5433 | 2.2261 | 2.6735 | 2.909 | 3.3799 | 3.8508 | 0.5068 | 1.3767 | 1.7267 | 1.7267 | 1.7267 | 1.7267 | 1.0479 | 1.3301 | 1.3301 | 1.3301 | 1.3301 | 1.3301
2020-05-25 04:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 1.6957 | 2.446 | 2.9375 | 3.1963 | 3.7137 | 4.2311 | 0.55633 | 1.5112 | 1.8954 | 1.8954 | 1.8954 | 1.8954 | 1.1039 | 1.4012 | 1.4012 | 1.4012 | 1.4012 | 1.4012
2020-05-25 05:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.64302 | 0.64302 | 0.64302 | 0.64302 | 0.64302 | 0.64302 | 1.7374 | 2.5062 | 3.0099 | 3.275 | 3.8051 | 4.3353 | 0.60206 | 1.6354 | 2.0512 | 2.0512 | 2.0512 | 2.0512 | 1.5623 | 1.983 | 1.983 | 1.983 | 1.983 | 1.983
2020-05-25 06:00 | Winter | 0.73929 | 1.1367 | 1.7201 | 1.7201 | 1.7201 | 1.7201 | 0.71586 | 0.71586 | 0.71586 | 0.71586 | 0.71586 | 0.71586 | 2.0005 | 2.8857 | 3.4656 | 3.7709 | 4.3813 | 4.9918 | 0.67065 | 1.8218 | 2.2849 | 2.2849 | 2.2849 | 2.2849 | 1.8672 | 2.3701 | 2.3701 | 2.3701 | 2.3701 | 2.3701
2020-05-25 07:00 | Winter | 1.1241 | 1.7284 | 2.6155 | 2.6155 | 2.6155 | 2.6155 | 0.79735 | 0.79735 | 0.79735 | 0.79735 | 0.79735 | 0.79735 | 2.2482 | 3.243 | 3.8947 | 4.2377 | 4.9238 | 5.6098 | 0.77734 | 2.1116 | 2.6484 | 2.6484 | 2.6484 | 2.6484 | 2.3625 | 2.9987 | 2.9987 | 2.9987 | 2.9987 | 2.9987
2020-05-25 08:00 | Winter | 1.2003 | 1.8456 | 2.7928 | 2.7928 | 2.7928 | 2.7928 | 0.92595 | 0.92595 | 0.92595 | 0.92595 | 0.92595 | 0.92595 | 2.4197 | 3.4903 | 4.1918 | 4.561 | 5.2993 | 6.0377 | 0.77353 | 2.1012 | 2.6354 | 2.6354 | 2.6354 | 2.6354 | 2.5167 | 3.1944 | 3.1944 | 3.1944 | 3.1944 | 3.1944
2020-05-25 09:00 | Winter | 1.2003 | 1.8456 | 2.7928 | 2.7928 | 2.7928 | 2.7928 | 0.95167 | 0.95167 | 0.95167 | 0.95167 | 0.95167 | 0.95167 | 2.4387 | 3.5178 | 4.2248 | 4.5969 | 5.3411 | 6.0852 | 0.79258 | 2.153 | 2.7003 | 2.7003 | 2.7003 | 2.7003 | 2.534 | 3.2163 | 3.2163 | 3.2163 | 3.2163 | 3.2163
2020-05-25 10:00 | Winter | 1.2003 | 1.8456 | 2.7928 | 2.7928 | 2.7928 | 2.7928 | 0.93738 | 0.93738 | 0.93738 | 0.93738 | 0.93738 | 0.93738 | 2.4006 | 3.4628 | 4.1588 | 4.525 | 5.2576 | 5.9902 | 0.74305 | 2.0184 | 2.5316 | 2.5316 | 2.5316 | 2.5316 | 2.553 | 3.2405 | 3.2405 | 3.2405 | 3.2405 | 3.2405
2020-05-25 11:00 | Winter | 1.1432 | 1.7577 | 2.6598 | 2.6598 | 2.6598 | 2.6598 | 0.93167 | 0.93167 | 0.93167 | 0.93167 | 0.93167 | 0.93167 | 2.3435 | 3.3804 | 4.0597 | 4.4173 | 5.1324 | 5.8475 | 0.78877 | 2.1426 | 2.6874 | 2.6874 | 2.6874 | 2.6874 | 2.4768 | 3.1438 | 3.1438 | 3.1438 | 3.1438 | 3.1438
2020-05-25 12:00 | Winter | 1.1241 | 1.7284 | 2.6155 | 2.6155 | 2.6155 | 2.6155 | 0.90309 | 0.90309 | 0.90309 | 0.90309 | 0.90309 | 0.90309 | 2.3625 | 3.4079 | 4.0927 | 4.4532 | 5.1741 | 5.8951 | 0.75829 | 2.0598 | 2.5835 | 2.5835 | 2.5835 | 2.5835 | 2.4006 | 3.0471 | 3.0471 | 3.0471 | 3.0471 | 3.0471
2020-05-25 13:00 | Winter | 1.1241 | 1.7284 | 2.6155 | 2.6155 | 2.6155 | 2.6155 | 0.90023 | 0.90023 | 0.90023 | 0.90023 | 0.90023 | 0.90023 | 2.4578 | 3.5453 | 4.2578 | 4.6328 | 5.3828 | 6.1328 | 0.72018 | 1.9563 | 2.4537 | 2.4537 | 2.4537 | 2.4537 | 2.4197 | 3.0712 | 3.0712 | 3.0712 | 3.0712 | 3.0712
2020-05-25 14:00 | Winter | 1.1241 | 1.7284 | 2.6155 | 2.6155 | 2.6155 | 2.6155 | 0.97453 | 0.97453 | 0.97453 | 0.97453 | 0.97453 | 0.97453 | 2.3816 | 3.4353 | 4.1258 | 4.4891 | 5.2159 | 5.9426 | 0.75067 | 2.0391 | 2.5575 | 2.5575 | 2.5575 | 2.5575 | 2.3816 | 3.0229 | 3.0229 | 3.0229 | 3.0229 | 3.0229
2020-05-25 15:00 | Winter | 1.0784 | 1.6582 | 2.5092 | 2.5092 | 2.5092 | 2.5092 | 0.85736 | 0.85736 | 0.85736 | 0.85736 | 0.85736 | 0.85736 | 2.3054 | 3.3254 | 3.9937 | 4.3455 | 5.049 | 5.7525 | 0.724 | 1.9667 | 2.4667 | 2.4667 | 2.4667 | 2.4667 | 2.2673 | 2.8778 | 2.8778 | 2.8778 | 2.8778 | 2.8778
2020-05-25 16:00 | Winter | 1.0669 | 1.6405 | 2.4825 | 2.4825 | 2.4825 | 2.4825 | 0.86879 | 0.86879 | 0.86879 | 0.86879 | 0.86879 | 0.86879 | 2.361 | 3.4056 | 4.09 | 4.4503 | 5.1707 | 5.8912 | 0.70113 | 1.9046 | 2.3888 | 2.3888 | 2.3888 | 2.3888 | 2.2482 | 2.8536 | 2.8536 | 2.8536 | 2.8536 | 2.8536
2020-05-25 17:00 | Winter | 1.0288 | 1.582 | 2.3938 | 2.3938 | 2.3938 | 2.3938 | 0.76305 | 0.76305 | 0.76305 | 0.76305 | 0.76305 | 0.76305 | 2.6293 | 3.7926 | 4.5548 | 4.956 | 5.7583 | 6.5606 | 0.75067 | 2.0391 | 2.5575 | 2.5575 | 2.5575 | 2.5575 | 2.2101 | 2.8052 | 2.8052 | 2.8052 | 2.8052 | 2.8052
2020-05-25 18:00 | Winter | 0.93358 | 1.4355 | 2.1722 | 2.1722 | 2.1722 | 2.1722 | 0.6716 | 0.6716 | 0.6716 | 0.6716 | 0.6716 | 0.6716 | 2.6102 | 3.7651 | 4.5218 | 4.9201 | 5.7166 | 6.5131 | 0.72018 | 1.9563 | 2.4537 | 2.4537 | 2.4537 | 2.4537 | 1.6022 | 2.0337 | 2.0337 | 2.0337 | 2.0337 | 2.0337
2020-05-25 19:00 | Winter | 0.66034 | 1.0154 | 1.5364 | 1.5364 | 1.5364 | 1.5364 | 0.49155 | 0.49155 | 0.49155 | 0.49155 | 0.49155 | 0.49155 | 2.4387 | 3.5178 | 4.2248 | 4.5969 | 5.3411 | 6.0852 | 0.66303 | 1.8011 | 2.2589 | 2.2589 | 2.2589 | 2.2589 | 1.1622 | 1.4752 | 1.4752 | 1.4752 | 1.4752 | 1.4752
2020-05-25 20:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 2.2101 | 3.188 | 3.8287 | 4.1659 | 4.8403 | 5.5147 | 0.64016 | 1.7389 | 2.1811 | 2.1811 | 2.1811 | 2.1811 | 1.0098 | 1.2817 | 1.2817 | 1.2817 | 1.2817 | 1.2817
2020-05-25 21:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 2.1218 | 3.0606 | 3.6757 | 3.9995 | 4.647 | 5.2944 | 0.59444 | 1.6147 | 2.0253 | 2.0253 | 2.0253 | 2.0253 | 0.95263 | 1.2092 | 1.2092 | 1.2092 | 1.2092 | 1.2092
2020-05-25 22:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.39802 | 0.39802 | 0.39802 | 0.39802 | 0.39802 | 0.39802 | 1.9624 | 2.8307 | 3.3996 | 3.699 | 4.2979 | 4.8967 | 0.58682 | 1.594 | 1.9993 | 1.9993 | 1.9993 | 1.9993 | 0.90169 | 1.1445 | 1.1445 | 1.1445 | 1.1445 | 1.1445
2020-05-25 23:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.42582 | 0.42582 | 0.42582 | 0.42582 | 0.42582 | 0.42582 | 1.8481 | 2.6658 | 3.2016 | 3.4836 | 4.0475 | 4.6115 | 0.54109 | 1.4698 | 1.8435 | 1.8435 | 1.8435 | 1.8435 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-05-26 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.41439 | 0.41439 | 0.41439 | 0.41439 | 0.41439 | 0.41439 | 1.7338 | 2.5009 | 3.0036 | 3.2681 | 3.7972 | 4.3262 | 0.54109 | 1.4698 | 1.8435 | 1.8435 | 1.8435 | 1.8435 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-05-26 01:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.38257 | 0.38257 | 0.38257 | 0.38257 | 0.38257 | 0.38257 | 1.6721 | 2.412 | 2.8968 | 3.1519 | 3.6622 | 4.1724 | 0.54871 | 1.4905 | 1.8695 | 1.8695 | 1.8695 | 1.8695 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-05-26 02:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 1.6195 | 2.336 | 2.8055 | 3.0526 | 3.5468 | 4.041 | 0.5068 | 1.3767 | 1.7267 | 1.7267 | 1.7267 | 1.7267 | 1.0475 | 1.3296 | 1.3296 | 1.3296 | 1.3296 | 1.3296
2020-05-26 03:00 | Winter | 0.55871 | 0.85908 | 1.3 | 1.3 | 1.3 | 1.3 | 0.40582 | 0.40582 | 0.40582 | 0.40582 | 0.40582 | 0.40582 | 1.6195 | 2.336 | 2.8055 | 3.0526 | 3.5468 | 4.041 | 0.52204 | 1.4181 | 1.7786 | 1.7786 | 1.7786 | 1.7786 | 1.0479 | 1.3301 | 1.3301 | 1.3301 | 1.3301 | 1.3301
2020-05-26 04:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.50299 | 1.3663 | 1.7137 | 1.7137 | 1.7137 | 1.7137 | 1.0842 | 1.3762 | 1.3762 | 1.3762 | 1.3762 | 1.3762
2020-05-26 05:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.58586 | 0.58586 | 0.58586 | 0.58586 | 0.58586 | 0.58586 | 1.798 | 2.5936 | 3.1149 | 3.3892 | 3.9379 | 4.4866 | 0.54109 | 1.4698 | 1.8435 | 1.8435 | 1.8435 | 1.8435 | 1.4516 | 1.8425 | 1.8425 | 1.8425 | 1.8425 | 1.8425
2020-05-26 06:00 | Winter | 0.66684 | 1.0253 | 1.5515 | 1.5515 | 1.5515 | 1.5515 | 0.69732 | 0.69732 | 0.69732 | 0.69732 | 0.69732 | 0.69732 | 1.9624 | 2.8307 | 3.3996 | 3.699 | 4.2979 | 4.8967 | 0.6516 | 1.77 | 2.22 | 2.22 | 2.22 | 2.22 | 1.8449 | 2.3417 | 2.3417 | 2.3417 | 2.3417 | 2.3417
2020-05-26 07:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.80002 | 0.80002 | 0.80002 | 0.80002 | 0.80002 | 0.80002 | 2.3884 | 3.4452 | 4.1376 | 4.502 | 5.2308 | 5.9596 | 0.70875 | 1.9253 | 2.4147 | 2.4147 | 2.4147 | 2.4147 | 2.1981 | 2.79 | 2.79 | 2.79 | 2.79 | 2.79
2020-05-26 08:00 | Winter | 1.2003 | 1.8456 | 2.7928 | 2.7928 | 2.7928 | 2.7928 | 0.86017 | 0.86017 | 0.86017 | 0.86017 | 0.86017 | 0.86017 | 2.4197 | 3.4903 | 4.1918 | 4.561 | 5.2993 | 6.0377 | 0.80021 | 2.1737 | 2.7263 | 2.7263 | 2.7263 | 2.7263 | 2.3816 | 3.0229 | 3.0229 | 3.0229 | 3.0229 | 3.0229
2020-05-26 09:00 | Winter | 1.2003 | 1.8456 | 2.7928 | 2.7928 | 2.7928 | 2.7928 | 0.96025 | 0.96025 | 0.96025 | 0.96025 | 0.96025 | 0.96025 | 2.3816 | 3.4353 | 4.1258 | 4.4891 | 5.2159 | 5.9426 | 0.78496 | 2.1323 | 2.6744 | 2.6744 | 2.6744 | 2.6744 | 2.4387 | 3.0954 | 3.0954 | 3.0954 | 3.0954 | 3.0954
2020-05-26 10:00 | Winter | 1.1622 | 1.787 | 2.7041 | 2.7041 | 2.7041 | 2.7041 | 0.93167 | 0.93167 | 0.93167 | 0.93167 | 0.93167 | 0.93167 | 2.4959 | 3.6002 | 4.3238 | 4.7046 | 5.4662 | 6.2279 | 0.68208 | 1.8528 | 2.3239 | 2.3239 | 2.3239 | 2.3239 | 2.4197 | 3.0712 | 3.0712 | 3.0712 | 3.0712 | 3.0712
2020-05-26 11:00 | Winter | 1.105 | 1.6991 | 2.5711 | 2.5711 | 2.5711 | 2.5711 | 0.93452 | 0.93452 | 0.93452 | 0.93452 | 0.93452 | 0.93452 | 2.4639 | 3.554 | 4.2683 | 4.6442 | 5.3961 | 6.1479 | 0.67827 | 1.8425 | 2.3109 | 2.3109 | 2.3109 | 2.3109 | 2.3625 | 2.9987 | 2.9987 | 2.9987 | 2.9987 | 2.9987
2020-05-26 12:00 | Winter | 1.1622 | 1.787 | 2.7041 | 2.7041 | 2.7041 | 2.7041 | 0.89166 | 0.89166 | 0.89166 | 0.89166 | 0.89166 | 0.89166 | 2.4387 | 3.5178 | 4.2248 | 4.5969 | 5.3411 | 6.0852 | 0.69351 | 1.8839 | 2.3628 | 2.3628 | 2.3628 | 2.3628 | 2.3435 | 2.9745 | 2.9745 | 2.9745 | 2.9745 | 2.9745
2020-05-26 13:00 | Winter | 1.1432 | 1.7577 | 2.6598 | 2.6598 | 2.6598 | 2.6598 | 0.82307 | 0.82307 | 0.82307 | 0.82307 | 0.82307 | 0.82307 | 2.4197 | 3.4903 | 4.1918 | 4.561 | 5.2993 | 6.0377 | 0.72018 | 1.9563 | 2.4537 | 2.4537 | 2.4537 | 2.4537 | 2.3816 | 3.0229 | 3.0229 | 3.0229 | 3.0229 | 3.0229
2020-05-26 14:00 | Winter | 1.105 | 1.6991 | 2.5711 | 2.5711 | 2.5711 | 2.5711 | 0.8002 | 0.8002 | 0.8002 | 0.8002 | 0.8002 | 0.8002 | 2.3625 | 3.4079 | 4.0927 | 4.4532 | 5.1741 | 5.8951 | 0.724 | 1.9667 | 2.4667 | 2.4667 | 2.4667 | 2.4667 | 2.2863 | 2.902 | 2.902 | 2.902 | 2.902 | 2.902
2020-05-26 15:00 | Winter | 1.105 | 1.6991 | 2.5711 | 2.5711 | 2.5711 | 2.5711 | 0.79163 | 0.79163 | 0.79163 | 0.79163 | 0.79163 | 0.79163 | 2.3244 | 3.3529 | 4.0267 | 4.3814 | 5.0907 | 5.8 | 0.70494 | 1.9149 | 2.4018 | 2.4018 | 2.4018 | 2.4018 | 2.1339 | 2.7085 | 2.7085 | 2.7085 | 2.7085 | 2.7085
2020-05-26 16:00 | Winter | 1.086 | 1.6698 | 2.5268 | 2.5268 | 2.5268 | 2.5268 | 0.78306 | 0.78306 | 0.78306 | 0.78306 | 0.78306 | 0.78306 | 2.2765 | 3.2837 | 3.9437 | 4.291 | 4.9857 | 5.6804 | 0.70113 | 1.9046 | 2.3888 | 2.3888 | 2.3888 | 2.3888 | 2.1148 | 2.6843 | 2.6843 | 2.6843 | 2.6843 | 2.6843
2020-05-26 17:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.78591 | 0.78591 | 0.78591 | 0.78591 | 0.78591 | 0.78591 | 2.534 | 3.6552 | 4.3898 | 4.7764 | 5.5497 | 6.3229 | 0.70875 | 1.9253 | 2.4147 | 2.4147 | 2.4147 | 2.4147 | 2.0577 | 2.6118 | 2.6118 | 2.6118 | 2.6118 | 2.6118
2020-05-26 18:00 | Winter | 0.88309 | 1.3579 | 2.0547 | 2.0547 | 2.0547 | 2.0547 | 0.6373 | 0.6373 | 0.6373 | 0.6373 | 0.6373 | 0.6373 | 2.4959 | 3.6002 | 4.3238 | 4.7046 | 5.4662 | 6.2279 | 0.70113 | 1.9046 | 2.3888 | 2.3888 | 2.3888 | 2.3888 | 1.5475 | 1.9642 | 1.9642 | 1.9642 | 1.9642 | 1.9642
2020-05-26 19:00 | Winter | 0.68589 | 1.0546 | 1.5959 | 1.5959 | 1.5959 | 1.5959 | 0.56872 | 0.56872 | 0.56872 | 0.56872 | 0.56872 | 0.56872 | 2.3488 | 3.3881 | 4.069 | 4.4274 | 5.1441 | 5.8609 | 0.65541 | 1.7803 | 2.233 | 2.233 | 2.233 | 2.233 | 1.0801 | 1.3709 | 1.3709 | 1.3709 | 1.3709 | 1.3709
2020-05-26 20:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 2.153 | 3.1056 | 3.7298 | 4.0583 | 4.7152 | 5.3722 | 0.62873 | 1.7079 | 2.1421 | 2.1421 | 2.1421 | 2.1421 | 1.0289 | 1.306 | 1.306 | 1.306 | 1.306 | 1.306
2020-05-26 21:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 2.0767 | 2.9956 | 3.5977 | 3.9145 | 4.5482 | 5.182 | 0.5792 | 1.5733 | 1.9733 | 1.9733 | 1.9733 | 1.9733 | 0.91459 | 1.1609 | 1.1609 | 1.1609 | 1.1609 | 1.1609
2020-05-26 22:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.36866 | 0.36866 | 0.36866 | 0.36866 | 0.36866 | 0.36866 | 1.8862 | 2.7208 | 3.2676 | 3.5554 | 4.131 | 4.7066 | 0.58301 | 1.5837 | 1.9863 | 1.9863 | 1.9863 | 1.9863 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-05-26 23:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.40296 | 0.40296 | 0.40296 | 0.40296 | 0.40296 | 0.40296 | 1.829 | 2.6383 | 3.1686 | 3.4477 | 4.0058 | 4.5639 | 0.51996 | 1.4124 | 1.7715 | 1.7715 | 1.7715 | 1.7715 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-05-27 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 1.6766 | 2.4185 | 2.9045 | 3.1603 | 3.672 | 4.1836 | 0.52204 | 1.4181 | 1.7786 | 1.7786 | 1.7786 | 1.7786 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-05-27 01:00 | Winter | 0.54795 | 0.84254 | 1.2749 | 1.2749 | 1.2749 | 1.2749 | 0.36864 | 0.36864 | 0.36864 | 0.36864 | 0.36864 | 0.36864 | 1.6576 | 2.391 | 2.8715 | 3.1244 | 3.6302 | 4.1361 | 0.49918 | 1.356 | 1.7007 | 1.7007 | 1.7007 | 1.7007 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-05-27 02:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 1.6195 | 2.336 | 2.8055 | 3.0526 | 3.5468 | 4.041 | 0.48012 | 1.3042 | 1.6358 | 1.6358 | 1.6358 | 1.6358 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-05-27 03:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.39255 | 0.39255 | 0.39255 | 0.39255 | 0.39255 | 0.39255 | 1.6766 | 2.4185 | 2.9045 | 3.1603 | 3.672 | 4.1836 | 0.46869 | 1.2732 | 1.5968 | 1.5968 | 1.5968 | 1.5968 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-05-27 04:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 1.6195 | 2.336 | 2.8055 | 3.0526 | 3.5468 | 4.041 | 0.47652 | 1.2944 | 1.6235 | 1.6235 | 1.6235 | 1.6235 | 1.0666 | 1.3539 | 1.3539 | 1.3539 | 1.3539 | 1.3539
2020-05-27 05:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.54585 | 0.54585 | 0.54585 | 0.54585 | 0.54585 | 0.54585 | 1.7147 | 2.4735 | 2.9705 | 3.2322 | 3.7554 | 4.2787 | 0.56395 | 1.5319 | 1.9214 | 1.9214 | 1.9214 | 1.9214 | 1.3994 | 1.7763 | 1.7763 | 1.7763 | 1.7763 | 1.7763
2020-05-27 06:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.72018 | 0.72018 | 0.72018 | 0.72018 | 0.72018 | 0.72018 | 2.0196 | 2.9132 | 3.4986 | 3.8068 | 4.4231 | 5.0393 | 0.64016 | 1.7389 | 2.1811 | 2.1811 | 2.1811 | 2.1811 | 1.7475 | 2.2181 | 2.2181 | 2.2181 | 2.2181 | 2.2181
2020-05-27 07:00 | Winter | 1.028 | 1.5807 | 2.3919 | 2.3919 | 2.3919 | 2.3919 | 0.79304 | 0.79304 | 0.79304 | 0.79304 | 0.79304 | 0.79304 | 2.3054 | 3.3254 | 3.9937 | 4.3455 | 5.049 | 5.7525 | 0.74305 | 2.0184 | 2.5316 | 2.5316 | 2.5316 | 2.5316 | 2.1316 | 2.7056 | 2.7056 | 2.7056 | 2.7056 | 2.7056
2020-05-27 08:00 | Winter | 1.2003 | 1.8456 | 2.7928 | 2.7928 | 2.7928 | 2.7928 | 0.85165 | 0.85165 | 0.85165 | 0.85165 | 0.85165 | 0.85165 | 2.3625 | 3.4079 | 4.0927 | 4.4532 | 5.1741 | 5.8951 | 0.7621 | 2.0702 | 2.5965 | 2.5965 | 2.5965 | 2.5965 | 2.3435 | 2.9745 | 2.9745 | 2.9745 | 2.9745 | 2.9745
2020-05-27 09:00 | Winter | 1.1813 | 1.8163 | 2.7485 | 2.7485 | 2.7485 | 2.7485 | 0.88594 | 0.88594 | 0.88594 | 0.88594 | 0.88594 | 0.88594 | 2.3281 | 3.3582 | 4.033 | 4.3883 | 5.0987 | 5.8091 | 0.74686 | 2.0288 | 2.5446 | 2.5446 | 2.5446 | 2.5446 | 2.3816 | 3.0229 | 3.0229 | 3.0229 | 3.0229 | 3.0229
2020-05-27 10:00 | Winter | 1.105 | 1.6991 | 2.5711 | 2.5711 | 2.5711 | 2.5711 | 0.90023 | 0.90023 | 0.90023 | 0.90023 | 0.90023 | 0.90023 | 2.3625 | 3.4079 | 4.0927 | 4.4532 | 5.1741 | 5.8951 | 0.71637 | 1.946 | 2.4407 | 2.4407 | 2.4407 | 2.4407 | 2.3627 | 2.9989 | 2.9989 | 2.9989 | 2.9989 | 2.9989
2020-05-27 11:00 | Winter | 1.086 | 1.6698 | 2.5268 | 2.5268 | 2.5268 | 2.5268 | 0.78877 | 0.78877 | 0.78877 | 0.78877 | 0.78877 | 0.78877 | 2.3959 | 3.456 | 4.1505 | 4.5161 | 5.2472 | 5.9783 | 0.65541 | 1.7803 | 2.233 | 2.233 | 2.233 | 2.233 | 2.4006 | 3.0471 | 3.0471 | 3.0471 | 3.0471 | 3.0471
2020-05-27 12:00 | Winter | 1.086 | 1.6698 | 2.5268 | 2.5268 | 2.5268 | 2.5268 | 0.8002 | 0.8002 | 0.8002 | 0.8002 | 0.8002 | 0.8002 | 2.4197 | 3.4903 | 4.1918 | 4.561 | 5.2993 | 6.0377 | 0.65541 | 1.7803 | 2.233 | 2.233 | 2.233 | 2.233 | 2.2647 | 2.8745 | 2.8745 | 2.8745 | 2.8745 | 2.8745
2020-05-27 13:00 | Winter | 1.086 | 1.6698 | 2.5268 | 2.5268 | 2.5268 | 2.5268 | 0.7802 | 0.7802 | 0.7802 | 0.7802 | 0.7802 | 0.7802 | 2.3435 | 3.3804 | 4.0597 | 4.4173 | 5.1324 | 5.8475 | 0.70875 | 1.9253 | 2.4147 | 2.4147 | 2.4147 | 2.4147 | 2.2482 | 2.8536 | 2.8536 | 2.8536 | 2.8536 | 2.8536
2020-05-27 14:00 | Winter | 1.0288 | 1.582 | 2.3938 | 2.3938 | 2.3938 | 2.3938 | 0.80878 | 0.80878 | 0.80878 | 0.80878 | 0.80878 | 0.80878 | 2.2673 | 3.2705 | 3.9277 | 4.2736 | 4.9655 | 5.6574 | 0.71637 | 1.946 | 2.4407 | 2.4407 | 2.4407 | 2.4407 | 2.2673 | 2.8778 | 2.8778 | 2.8778 | 2.8778 | 2.8778
2020-05-27 15:00 | Winter | 1.0288 | 1.582 | 2.3938 | 2.3938 | 2.3938 | 2.3938 | 0.73161 | 0.73161 | 0.73161 | 0.73161 | 0.73161 | 0.73161 | 2.2863 | 3.2979 | 3.9607 | 4.3096 | 5.0072 | 5.7049 | 0.67065 | 1.8218 | 2.2849 | 2.2849 | 2.2849 | 2.2849 | 2.1339 | 2.7085 | 2.7085 | 2.7085 | 2.7085 | 2.7085
2020-05-27 16:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.73733 | 0.73733 | 0.73733 | 0.73733 | 0.73733 | 0.73733 | 2.3551 | 3.3971 | 4.0798 | 4.4392 | 5.1578 | 5.8765 | 0.67446 | 1.8321 | 2.2979 | 2.2979 | 2.2979 | 2.2979 | 2.172 | 2.7569 | 2.7569 | 2.7569 | 2.7569 | 2.7569
2020-05-27 17:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.66874 | 0.66874 | 0.66874 | 0.66874 | 0.66874 | 0.66874 | 2.534 | 3.6552 | 4.3898 | 4.7764 | 5.5497 | 6.3229 | 0.70494 | 1.9149 | 2.4018 | 2.4018 | 2.4018 | 2.4018 | 2.0579 | 2.612 | 2.612 | 2.612 | 2.612 | 2.612
2020-05-27 18:00 | Winter | 0.85922 | 1.3212 | 1.9992 | 1.9992 | 1.9992 | 1.9992 | 0.61607 | 0.61607 | 0.61607 | 0.61607 | 0.61607 | 0.61607 | 2.4578 | 3.5453 | 4.2578 | 4.6328 | 5.3828 | 6.1328 | 0.70875 | 1.9253 | 2.4147 | 2.4147 | 2.4147 | 2.4147 | 1.6303 | 2.0693 | 2.0693 | 2.0693 | 2.0693 | 2.0693
2020-05-27 19:00 | Winter | 0.67245 | 1.034 | 1.5646 | 1.5646 | 1.5646 | 1.5646 | 0.43154 | 0.43154 | 0.43154 | 0.43154 | 0.43154 | 0.43154 | 2.3443 | 3.3815 | 4.0611 | 4.4188 | 5.1342 | 5.8495 | 0.66303 | 1.8011 | 2.2589 | 2.2589 | 2.2589 | 2.2589 | 1.2194 | 1.5477 | 1.5477 | 1.5477 | 1.5477 | 1.5477
2020-05-27 20:00 | Winter | 0.62947 | 0.96789 | 1.4646 | 1.4646 | 1.4646 | 1.4646 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 2.1529 | 3.1056 | 3.7297 | 4.0582 | 4.7151 | 5.3721 | 0.63635 | 1.7286 | 2.1681 | 2.1681 | 2.1681 | 2.1681 | 1.0669 | 1.3542 | 1.3542 | 1.3542 | 1.3542 | 1.3542
2020-05-27 21:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 2.0386 | 2.9407 | 3.5316 | 3.8427 | 4.4648 | 5.0869 | 0.65541 | 1.7803 | 2.233 | 2.233 | 2.233 | 2.233 | 1.0098 | 1.2817 | 1.2817 | 1.2817 | 1.2817 | 1.2817
2020-05-27 22:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.37438 | 0.37438 | 0.37438 | 0.37438 | 0.37438 | 0.37438 | 1.9624 | 2.8307 | 3.3996 | 3.699 | 4.2979 | 4.8967 | 0.54871 | 1.4905 | 1.8695 | 1.8695 | 1.8695 | 1.8695 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-05-27 23:00 | Winter | 0.58934 | 0.90618 | 1.3712 | 1.3712 | 1.3712 | 1.3712 | 0.39438 | 0.39438 | 0.39438 | 0.39438 | 0.39438 | 0.39438 | 1.7701 | 2.5533 | 3.0665 | 3.3365 | 3.8767 | 4.4168 | 0.52204 | 1.4181 | 1.7786 | 1.7786 | 1.7786 | 1.7786 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-05-28 | Winter | 0.58835 | 0.90465 | 1.3689 | 1.3689 | 1.3689 | 1.3689 | 0.40582 | 0.40582 | 0.40582 | 0.40582 | 0.40582 | 0.40582 | 1.7147 | 2.4735 | 2.9705 | 3.2322 | 3.7554 | 4.2787 | 0.51442 | 1.3974 | 1.7526 | 1.7526 | 1.7526 | 1.7526 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-05-28 01:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.38295 | 0.38295 | 0.38295 | 0.38295 | 0.38295 | 0.38295 | 1.6576 | 2.391 | 2.8715 | 3.1244 | 3.6302 | 4.1361 | 0.48012 | 1.3042 | 1.6358 | 1.6358 | 1.6358 | 1.6358 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-05-28 02:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.38295 | 0.38295 | 0.38295 | 0.38295 | 0.38295 | 0.38295 | 1.5623 | 2.2536 | 2.7065 | 2.9449 | 3.4216 | 3.8984 | 0.46869 | 1.2732 | 1.5968 | 1.5968 | 1.5968 | 1.5968 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-05-28 03:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.39153 | 0.39153 | 0.39153 | 0.39153 | 0.39153 | 0.39153 | 1.5623 | 2.2536 | 2.7065 | 2.9449 | 3.4216 | 3.8984 | 0.46488 | 1.2628 | 1.5839 | 1.5839 | 1.5839 | 1.5839 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-05-28 04:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.4544 | 0.4544 | 0.4544 | 0.4544 | 0.4544 | 0.4544 | 1.6576 | 2.391 | 2.8715 | 3.1244 | 3.6302 | 4.1361 | 0.50299 | 1.3663 | 1.7137 | 1.7137 | 1.7137 | 1.7137 | 1.0669 | 1.3542 | 1.3542 | 1.3542 | 1.3542 | 1.3542
2020-05-28 05:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.57443 | 0.57443 | 0.57443 | 0.57443 | 0.57443 | 0.57443 | 1.7719 | 2.5559 | 3.0696 | 3.3399 | 3.8806 | 4.4213 | 0.60587 | 1.6458 | 2.0642 | 2.0642 | 2.0642 | 2.0642 | 1.4693 | 1.8649 | 1.8649 | 1.8649 | 1.8649 | 1.8649
2020-05-28 06:00 | Winter | 0.6438 | 0.98992 | 1.4979 | 1.4979 | 1.4979 | 1.4979 | 0.70018 | 0.70018 | 0.70018 | 0.70018 | 0.70018 | 0.70018 | 1.9243 | 2.7758 | 3.3336 | 3.6272 | 4.2144 | 4.8016 | 0.65922 | 1.7907 | 2.246 | 2.246 | 2.246 | 2.246 | 1.741 | 2.2098 | 2.2098 | 2.2098 | 2.2098 | 2.2098
2020-05-28 07:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 0.8002 | 0.8002 | 0.8002 | 0.8002 | 0.8002 | 0.8002 | 2.3625 | 3.4079 | 4.0927 | 4.4532 | 5.1741 | 5.8951 | 0.73924 | 2.0081 | 2.5186 | 2.5186 | 2.5186 | 2.5186 | 2.141 | 2.7175 | 2.7175 | 2.7175 | 2.7175 | 2.7175
2020-05-28 08:00 | Winter | 1.1813 | 1.8163 | 2.7485 | 2.7485 | 2.7485 | 2.7485 | 0.89166 | 0.89166 | 0.89166 | 0.89166 | 0.89166 | 0.89166 | 2.4959 | 3.6002 | 4.3238 | 4.7046 | 5.4662 | 6.2279 | 0.75067 | 2.0391 | 2.5575 | 2.5575 | 2.5575 | 2.5575 | 2.4123 | 3.0619 | 3.0619 | 3.0619 | 3.0619 | 3.0619
2020-05-28 09:00 | Winter | 1.1622 | 1.787 | 2.7041 | 2.7041 | 2.7041 | 2.7041 | 0.92881 | 0.92881 | 0.92881 | 0.92881 | 0.92881 | 0.92881 | 2.4768 | 3.5728 | 4.2908 | 4.6687 | 5.4245 | 6.1803 | 0.77353 | 2.1012 | 2.6354 | 2.6354 | 2.6354 | 2.6354 | 2.5149 | 3.1922 | 3.1922 | 3.1922 | 3.1922 | 3.1922
2020-05-28 10:00 | Winter | 1.1432 | 1.7577 | 2.6598 | 2.6598 | 2.6598 | 2.6598 | 0.89737 | 0.89737 | 0.89737 | 0.89737 | 0.89737 | 0.89737 | 2.553 | 3.6827 | 4.4228 | 4.8123 | 5.5914 | 6.3705 | 0.7621 | 2.0702 | 2.5965 | 2.5965 | 2.5965 | 2.5965 | 2.4197 | 3.0712 | 3.0712 | 3.0712 | 3.0712 | 3.0712
2020-05-28 11:00 | Winter | 1.0669 | 1.6405 | 2.4825 | 2.4825 | 2.4825 | 2.4825 | 0.8545 | 0.8545 | 0.8545 | 0.8545 | 0.8545 | 0.8545 | 2.4572 | 3.5445 | 4.2568 | 4.6318 | 5.3816 | 6.1314 | 0.75448 | 2.0495 | 2.5705 | 2.5705 | 2.5705 | 2.5705 | 2.2673 | 2.8778 | 2.8778 | 2.8778 | 2.8778 | 2.8778
2020-05-28 12:00 | Winter | 1.105 | 1.6991 | 2.5711 | 2.5711 | 2.5711 | 2.5711 | 0.85165 | 0.85165 | 0.85165 | 0.85165 | 0.85165 | 0.85165 | 2.4768 | 3.5728 | 4.2908 | 4.6687 | 5.4245 | 6.1803 | 0.66684 | 1.8114 | 2.2719 | 2.2719 | 2.2719 | 2.2719 | 2.3244 | 2.9503 | 2.9503 | 2.9503 | 2.9503 | 2.9503
2020-05-28 13:00 | Winter | 1.105 | 1.6991 | 2.5711 | 2.5711 | 2.5711 | 2.5711 | 0.86879 | 0.86879 | 0.86879 | 0.86879 | 0.86879 | 0.86879 | 2.4197 | 3.4903 | 4.1918 | 4.561 | 5.2993 | 6.0377 | 0.69351 | 1.8839 | 2.3628 | 2.3628 | 2.3628 | 2.3628 | 2.2482 | 2.8536 | 2.8536 | 2.8536 | 2.8536 | 2.8536
2020-05-28 14:00 | Winter | 1.2003 | 1.8456 | 2.7928 | 2.7928 | 2.7928 | 2.7928 | 0.93167 | 0.93167 | 0.93167 | 0.93167 | 0.93167 | 0.93167 | 2.4006 | 3.4628 | 4.1588 | 4.525 | 5.2576 | 5.9902 | 0.7964 | 2.1633 | 2.7133 | 2.7133 | 2.7133 | 2.7133 | 2.172 | 2.7569 | 2.7569 | 2.7569 | 2.7569 | 2.7569
2020-05-28 15:00 | Winter | 1.1622 | 1.787 | 2.7041 | 2.7041 | 2.7041 | 2.7041 | 0.84593 | 0.84593 | 0.84593 | 0.84593 | 0.84593 | 0.84593 | 2.3244 | 3.3529 | 4.0267 | 4.3814 | 5.0907 | 5.8 | 0.76591 | 2.0805 | 2.6095 | 2.6095 | 2.6095 | 2.6095 | 2.1339 | 2.7085 | 2.7085 | 2.7085 | 2.7085 | 2.7085
2020-05-28 16:00 | Winter | 1.1813 | 1.8163 | 2.7485 | 2.7485 | 2.7485 | 2.7485 | 0.78591 | 0.78591 | 0.78591 | 0.78591 | 0.78591 | 0.78591 | 2.2863 | 3.2979 | 3.9607 | 4.3096 | 5.0072 | 5.7049 | 0.71637 | 1.946 | 2.4407 | 2.4407 | 2.4407 | 2.4407 | 2.0798 | 2.6399 | 2.6399 | 2.6399 | 2.6399 | 2.6399
2020-05-28 17:00 | Winter | 1.0288 | 1.582 | 2.3938 | 2.3938 | 2.3938 | 2.3938 | 0.69732 | 0.69732 | 0.69732 | 0.69732 | 0.69732 | 0.69732 | 2.4768 | 3.5728 | 4.2908 | 4.6687 | 5.4245 | 6.1803 | 0.724 | 1.9667 | 2.4667 | 2.4667 | 2.4667 | 2.4667 | 1.9092 | 2.4233 | 2.4233 | 2.4233 | 2.4233 | 2.4233
2020-05-28 18:00 | Winter | 0.87642 | 1.3476 | 2.0392 | 2.0392 | 2.0392 | 2.0392 | 0.65445 | 0.65445 | 0.65445 | 0.65445 | 0.65445 | 0.65445 | 2.3625 | 3.4079 | 4.0927 | 4.4532 | 5.1741 | 5.8951 | 0.65541 | 1.7803 | 2.233 | 2.233 | 2.233 | 2.233 | 1.4925 | 1.8944 | 1.8944 | 1.8944 | 1.8944 | 1.8944
2020-05-28 19:00 | Winter | 0.63478 | 0.97604 | 1.4769 | 1.4769 | 1.4769 | 1.4769 | 0.52585 | 0.52585 | 0.52585 | 0.52585 | 0.52585 | 0.52585 | 2.2676 | 3.2709 | 3.9283 | 4.2742 | 4.9662 | 5.6582 | 0.64779 | 1.7596 | 2.207 | 2.207 | 2.207 | 2.207 | 1.1813 | 1.4993 | 1.4993 | 1.4993 | 1.4993 | 1.4993
2020-05-28 20:00 | Winter | 0.58011 | 0.89198 | 1.3497 | 1.3497 | 1.3497 | 1.3497 | 0.4544 | 0.4544 | 0.4544 | 0.4544 | 0.4544 | 0.4544 | 2.2291 | 3.2155 | 3.8617 | 4.2018 | 4.8821 | 5.5623 | 0.60206 | 1.6354 | 2.0512 | 2.0512 | 2.0512 | 2.0512 | 1.0479 | 1.3301 | 1.3301 | 1.3301 | 1.3301 | 1.3301
2020-05-28 21:00 | Winter | 0.5702 | 0.87675 | 1.3267 | 1.3267 | 1.3267 | 1.3267 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 2.1732 | 3.1348 | 3.7648 | 4.0964 | 4.7596 | 5.4227 | 0.60587 | 1.6458 | 2.0642 | 2.0642 | 2.0642 | 2.0642 | 0.91565 | 1.1622 | 1.1622 | 1.1622 | 1.1622 | 1.1622
2020-05-28 22:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 1.9205 | 2.7702 | 3.3269 | 3.62 | 4.206 | 4.792 | 0.58348 | 1.585 | 1.9879 | 1.9879 | 1.9879 | 1.9879 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-05-28 23:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 1.8481 | 2.6658 | 3.2016 | 3.4836 | 4.0475 | 4.6115 | 0.55252 | 1.5009 | 1.8825 | 1.8825 | 1.8825 | 1.8825 | 0.8209 | 1.0419 | 1.0419 | 1.0419 | 1.0419 | 1.0419
2020-05-29 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.42582 | 0.42582 | 0.42582 | 0.42582 | 0.42582 | 0.42582 | 1.6957 | 2.446 | 2.9375 | 3.1963 | 3.7137 | 4.2311 | 0.56776 | 1.5423 | 1.9344 | 1.9344 | 1.9344 | 1.9344 | 0.91452 | 1.1608 | 1.1608 | 1.1608 | 1.1608 | 1.1608
2020-05-29 01:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.42296 | 0.42296 | 0.42296 | 0.42296 | 0.42296 | 0.42296 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.51061 | 1.387 | 1.7396 | 1.7396 | 1.7396 | 1.7396 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-05-29 02:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.46869 | 0.46869 | 0.46869 | 0.46869 | 0.46869 | 0.46869 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.5068 | 1.3767 | 1.7267 | 1.7267 | 1.7267 | 1.7267 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-05-29 03:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 1.6195 | 2.336 | 2.8055 | 3.0526 | 3.5468 | 4.041 | 0.5449 | 1.4802 | 1.8565 | 1.8565 | 1.8565 | 1.8565 | 0.90107 | 1.1437 | 1.1437 | 1.1437 | 1.1437 | 1.1437
2020-05-29 04:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.4544 | 0.4544 | 0.4544 | 0.4544 | 0.4544 | 0.4544 | 1.6957 | 2.446 | 2.9375 | 3.1963 | 3.7137 | 4.2311 | 0.49185 | 1.3361 | 1.6757 | 1.6757 | 1.6757 | 1.6757 | 1.0669 | 1.3542 | 1.3542 | 1.3542 | 1.3542 | 1.3542
2020-05-29 05:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.62301 | 0.62301 | 0.62301 | 0.62301 | 0.62301 | 0.62301 | 1.7909 | 2.5834 | 3.1026 | 3.3758 | 3.9223 | 4.4688 | 0.55252 | 1.5009 | 1.8825 | 1.8825 | 1.8825 | 1.8825 | 1.4792 | 1.8776 | 1.8776 | 1.8776 | 1.8776 | 1.8776
2020-05-29 06:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.70589 | 0.70589 | 0.70589 | 0.70589 | 0.70589 | 0.70589 | 1.9815 | 2.8582 | 3.4326 | 3.735 | 4.3396 | 4.9443 | 0.61349 | 1.6665 | 2.0902 | 2.0902 | 2.0902 | 2.0902 | 1.7756 | 2.2537 | 2.2537 | 2.2537 | 2.2537 | 2.2537
2020-05-29 07:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.79163 | 0.79163 | 0.79163 | 0.79163 | 0.79163 | 0.79163 | 2.3033 | 3.3225 | 3.9902 | 4.3417 | 5.0445 | 5.7474 | 0.74686 | 2.0288 | 2.5446 | 2.5446 | 2.5446 | 2.5446 | 2.1148 | 2.6843 | 2.6843 | 2.6843 | 2.6843 | 2.6843
2020-05-29 08:00 | Winter | 1.1813 | 1.8163 | 2.7485 | 2.7485 | 2.7485 | 2.7485 | 1.6861 | 1.6861 | 1.6861 | 1.6861 | 1.6861 | 1.6861 | 2.4577 | 3.5452 | 4.2577 | 4.6327 | 5.3826 | 6.1326 | 0.78115 | 2.1219 | 2.6614 | 2.6614 | 2.6614 | 2.6614 | 2.3435 | 2.9745 | 2.9745 | 2.9745 | 2.9745 | 2.9745
2020-05-29 09:00 | Winter | 1.105 | 1.6991 | 2.5711 | 2.5711 | 2.5711 | 2.5711 | 1.3203 | 1.3203 | 1.3203 | 1.3203 | 1.3203 | 1.3203 | 2.4768 | 3.5728 | 4.2908 | 4.6687 | 5.4245 | 6.1803 | 0.80021 | 2.1737 | 2.7263 | 2.7263 | 2.7263 | 2.7263 | 2.4006 | 3.0471 | 3.0471 | 3.0471 | 3.0471 | 3.0471
2020-05-29 10:00 | Winter | 1.105 | 1.6991 | 2.5711 | 2.5711 | 2.5711 | 2.5711 | 1.186 | 1.186 | 1.186 | 1.186 | 1.186 | 1.186 | 2.5149 | 3.6277 | 4.3568 | 4.7405 | 5.508 | 6.2754 | 0.77353 | 2.1012 | 2.6354 | 2.6354 | 2.6354 | 2.6354 | 2.4006 | 3.0471 | 3.0471 | 3.0471 | 3.0471 | 3.0471
2020-05-29 11:00 | Winter | 1.105 | 1.6991 | 2.5711 | 2.5711 | 2.5711 | 2.5711 | 1.1917 | 1.1917 | 1.1917 | 1.1917 | 1.1917 | 1.1917 | 2.4913 | 3.5936 | 4.3158 | 4.6959 | 5.4561 | 6.2163 | 0.81545 | 2.2151 | 2.7782 | 2.7782 | 2.7782 | 2.7782 | 2.3625 | 2.9987 | 2.9987 | 2.9987 | 2.9987 | 2.9987
2020-05-29 12:00 | Winter | 1.105 | 1.6991 | 2.5711 | 2.5711 | 2.5711 | 2.5711 | 1.1289 | 1.1289 | 1.1289 | 1.1289 | 1.1289 | 1.1289 | 2.4768 | 3.5728 | 4.2908 | 4.6687 | 5.4245 | 6.1803 | 0.72781 | 1.977 | 2.4796 | 2.4796 | 2.4796 | 2.4796 | 2.2709 | 2.8825 | 2.8825 | 2.8825 | 2.8825 | 2.8825
2020-05-29 13:00 | Winter | 1.086 | 1.6698 | 2.5268 | 2.5268 | 2.5268 | 2.5268 | 1.4004 | 1.4004 | 1.4004 | 1.4004 | 1.4004 | 1.4004 | 2.4578 | 3.5453 | 4.2578 | 4.6328 | 5.3828 | 6.1328 | 0.71637 | 1.946 | 2.4407 | 2.4407 | 2.4407 | 2.4407 | 2.172 | 2.7569 | 2.7569 | 2.7569 | 2.7569 | 2.7569
2020-05-29 14:00 | Winter | 1.0511 | 1.6162 | 2.4456 | 2.4456 | 2.4456 | 2.4456 | 0.93738 | 0.93738 | 0.93738 | 0.93738 | 0.93738 | 0.93738 | 2.4578 | 3.5453 | 4.2578 | 4.6328 | 5.3828 | 6.1328 | 0.70875 | 1.9253 | 2.4147 | 2.4147 | 2.4147 | 2.4147 | 2.1339 | 2.7085 | 2.7085 | 2.7085 | 2.7085 | 2.7085
2020-05-29 15:00 | Winter | 1.105 | 1.6991 | 2.5711 | 2.5711 | 2.5711 | 2.5711 | 0.87737 | 0.87737 | 0.87737 | 0.87737 | 0.87737 | 0.87737 | 2.4197 | 3.4903 | 4.1918 | 4.561 | 5.2993 | 6.0377 | 0.76972 | 2.0909 | 2.6225 | 2.6225 | 2.6225 | 2.6225 | 2.1148 | 2.6843 | 2.6843 | 2.6843 | 2.6843 | 2.6843
2020-05-29 16:00 | Winter | 1.2384 | 1.9042 | 2.8814 | 2.8814 | 2.8814 | 2.8814 | 0.8345 | 0.8345 | 0.8345 | 0.8345 | 0.8345 | 0.8345 | 2.3625 | 3.4079 | 4.0927 | 4.4532 | 5.1741 | 5.8951 | 0.72781 | 1.977 | 2.4796 | 2.4796 | 2.4796 | 2.4796 | 2.0577 | 2.6118 | 2.6118 | 2.6118 | 2.6118 | 2.6118
2020-05-29 17:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.75162 | 0.75162 | 0.75162 | 0.75162 | 0.75162 | 0.75162 | 2.3816 | 3.4353 | 4.1258 | 4.4891 | 5.2159 | 5.9426 | 0.69351 | 1.8839 | 2.3628 | 2.3628 | 2.3628 | 2.3628 | 2.0452 | 2.596 | 2.596 | 2.596 | 2.596 | 2.596
2020-05-29 18:00 | Winter | 0.73678 | 1.1329 | 1.7143 | 1.7143 | 1.7143 | 1.7143 | 0.69446 | 0.69446 | 0.69446 | 0.69446 | 0.69446 | 0.69446 | 2.3816 | 3.4353 | 4.1258 | 4.4891 | 5.2159 | 5.9426 | 0.64397 | 1.7493 | 2.194 | 2.194 | 2.194 | 2.194 | 1.5521 | 1.9701 | 1.9701 | 1.9701 | 1.9701 | 1.9701
2020-05-29 19:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.64874 | 0.64874 | 0.64874 | 0.64874 | 0.64874 | 0.64874 | 2.1611 | 3.1173 | 3.7438 | 4.0735 | 4.733 | 5.3924 | 0.59475 | 1.6156 | 2.0263 | 2.0263 | 2.0263 | 2.0263 | 1.1718 | 1.4874 | 1.4874 | 1.4874 | 1.4874 | 1.4874
2020-05-29 20:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.5087 | 0.5087 | 0.5087 | 0.5087 | 0.5087 | 0.5087 | 2.0394 | 2.9418 | 3.533 | 3.8442 | 4.4665 | 5.0888 | 0.62111 | 1.6872 | 2.1161 | 2.1161 | 2.1161 | 2.1161 | 1.0479 | 1.3301 | 1.3301 | 1.3301 | 1.3301 | 1.3301
2020-05-29 21:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.50013 | 0.50013 | 0.50013 | 0.50013 | 0.50013 | 0.50013 | 2.0386 | 2.9407 | 3.5316 | 3.8427 | 4.4648 | 5.0869 | 0.62111 | 1.6872 | 2.1161 | 2.1161 | 2.1161 | 2.1161 | 0.95263 | 1.2092 | 1.2092 | 1.2092 | 1.2092 | 1.2092
2020-05-29 22:00 | Winter | 0.57341 | 0.88168 | 1.3342 | 1.3342 | 1.3342 | 1.3342 | 0.49155 | 0.49155 | 0.49155 | 0.49155 | 0.49155 | 0.49155 | 1.9144 | 2.7615 | 3.3165 | 3.6086 | 4.1928 | 4.777 | 0.6516 | 1.77 | 2.22 | 2.22 | 2.22 | 2.22 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-05-29 23:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.42428 | 0.42428 | 0.42428 | 0.42428 | 0.42428 | 0.42428 | 1.7719 | 2.5559 | 3.0696 | 3.3399 | 3.8806 | 4.4213 | 0.57157 | 1.5526 | 1.9474 | 1.9474 | 1.9474 | 1.9474 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-05-30 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.39724 | 0.39724 | 0.39724 | 0.39724 | 0.39724 | 0.39724 | 1.7147 | 2.4735 | 2.9705 | 3.2322 | 3.7554 | 4.2787 | 0.58301 | 1.5837 | 1.9863 | 1.9863 | 1.9863 | 1.9863 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-05-30 01:00 | Winter | 0.55354 | 0.85113 | 1.2879 | 1.2879 | 1.2879 | 1.2879 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 1.5623 | 2.2536 | 2.7065 | 2.9449 | 3.4216 | 3.8984 | 0.51823 | 1.4077 | 1.7656 | 1.7656 | 1.7656 | 1.7656 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-05-30 02:00 | Winter | 0.54346 | 0.83564 | 1.2645 | 1.2645 | 1.2645 | 1.2645 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 1.6004 | 2.3086 | 2.7725 | 3.0167 | 3.5051 | 3.9934 | 0.51706 | 1.4046 | 1.7616 | 1.7616 | 1.7616 | 1.7616 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-05-30 03:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.4544 | 0.4544 | 0.4544 | 0.4544 | 0.4544 | 0.4544 | 1.5814 | 2.2811 | 2.7395 | 2.9808 | 3.4633 | 3.9459 | 0.51823 | 1.4077 | 1.7656 | 1.7656 | 1.7656 | 1.7656 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-05-30 04:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 1.622 | 2.3397 | 2.8099 | 3.0574 | 3.5524 | 4.0473 | 0.51061 | 1.387 | 1.7396 | 1.7396 | 1.7396 | 1.7396 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-05-30 05:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.5087 | 0.5087 | 0.5087 | 0.5087 | 0.5087 | 0.5087 | 1.6576 | 2.391 | 2.8715 | 3.1244 | 3.6302 | 4.1361 | 0.5068 | 1.3767 | 1.7267 | 1.7267 | 1.7267 | 1.7267 | 0.90378 | 1.1472 | 1.1472 | 1.1472 | 1.1472 | 1.1472
2020-05-30 06:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.55728 | 0.55728 | 0.55728 | 0.55728 | 0.55728 | 0.55728 | 1.7638 | 2.5443 | 3.0556 | 3.3247 | 3.863 | 4.4012 | 0.5449 | 1.4802 | 1.8565 | 1.8565 | 1.8565 | 1.8565 | 0.95263 | 1.2092 | 1.2092 | 1.2092 | 1.2092 | 1.2092
2020-05-30 07:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.60873 | 0.60873 | 0.60873 | 0.60873 | 0.60873 | 0.60873 | 1.829 | 2.6383 | 3.1686 | 3.4477 | 4.0058 | 4.5639 | 0.54871 | 1.4905 | 1.8695 | 1.8695 | 1.8695 | 1.8695 | 1.2003 | 1.5235 | 1.5235 | 1.5235 | 1.5235 | 1.5235
2020-05-30 08:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.62301 | 0.62301 | 0.62301 | 0.62301 | 0.62301 | 0.62301 | 1.9624 | 2.8307 | 3.3996 | 3.699 | 4.2979 | 4.8967 | 0.58301 | 1.5837 | 1.9863 | 1.9863 | 1.9863 | 1.9863 | 1.2575 | 1.5961 | 1.5961 | 1.5961 | 1.5961 | 1.5961
2020-05-30 09:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.60587 | 0.60587 | 0.60587 | 0.60587 | 0.60587 | 0.60587 | 2.0005 | 2.8857 | 3.4656 | 3.7709 | 4.3813 | 4.9918 | 0.56014 | 1.5216 | 1.9084 | 1.9084 | 1.9084 | 1.9084 | 1.1432 | 1.451 | 1.451 | 1.451 | 1.451 | 1.451
2020-05-30 10:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.59158 | 0.59158 | 0.59158 | 0.59158 | 0.59158 | 0.59158 | 2.0958 | 3.0231 | 3.6307 | 3.9504 | 4.59 | 5.2295 | 0.60206 | 1.6354 | 2.0512 | 2.0512 | 2.0512 | 2.0512 | 1.1622 | 1.4752 | 1.4752 | 1.4752 | 1.4752 | 1.4752
2020-05-30 11:00 | Winter | 0.7621 | 1.1718 | 1.7732 | 1.7732 | 1.7732 | 1.7732 | 0.55728 | 0.55728 | 0.55728 | 0.55728 | 0.55728 | 0.55728 | 2.0029 | 2.8892 | 3.4698 | 3.7754 | 4.3866 | 4.9978 | 0.56395 | 1.5319 | 1.9214 | 1.9214 | 1.9214 | 1.9214 | 1.1241 | 1.4268 | 1.4268 | 1.4268 | 1.4268 | 1.4268
2020-05-30 12:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.51156 | 0.51156 | 0.51156 | 0.51156 | 0.51156 | 0.51156 | 1.9815 | 2.8582 | 3.4326 | 3.735 | 4.3396 | 4.9443 | 0.51442 | 1.3974 | 1.7526 | 1.7526 | 1.7526 | 1.7526 | 1.086 | 1.3784 | 1.3784 | 1.3784 | 1.3784 | 1.3784
2020-05-30 13:00 | Winter | 0.66684 | 1.0253 | 1.5515 | 1.5515 | 1.5515 | 1.5515 | 0.51727 | 0.51727 | 0.51727 | 0.51727 | 0.51727 | 0.51727 | 1.9624 | 2.8307 | 3.3996 | 3.699 | 4.2979 | 4.8967 | 0.48774 | 1.3249 | 1.6618 | 1.6618 | 1.6618 | 1.6618 | 1.1241 | 1.4268 | 1.4268 | 1.4268 | 1.4268 | 1.4268
2020-05-30 14:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.47441 | 0.47441 | 0.47441 | 0.47441 | 0.47441 | 0.47441 | 1.9815 | 2.8582 | 3.4326 | 3.735 | 4.3396 | 4.9443 | 0.51823 | 1.4077 | 1.7656 | 1.7656 | 1.7656 | 1.7656 | 1.0288 | 1.3059 | 1.3059 | 1.3059 | 1.3059 | 1.3059
2020-05-30 15:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 2.0005 | 2.8857 | 3.4656 | 3.7709 | 4.3813 | 4.9918 | 0.51061 | 1.387 | 1.7396 | 1.7396 | 1.7396 | 1.7396 | 1.0669 | 1.3542 | 1.3542 | 1.3542 | 1.3542 | 1.3542
2020-05-30 16:00 | Winter | 0.64779 | 0.99605 | 1.5072 | 1.5072 | 1.5072 | 1.5072 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 2.0767 | 2.9956 | 3.5977 | 3.9145 | 4.5482 | 5.182 | 0.51061 | 1.387 | 1.7396 | 1.7396 | 1.7396 | 1.7396 | 1.0098 | 1.2817 | 1.2817 | 1.2817 | 1.2817 | 1.2817
2020-05-30 17:00 | Winter | 0.60419 | 0.92902 | 1.4058 | 1.4058 | 1.4058 | 1.4058 | 0.48869 | 0.48869 | 0.48869 | 0.48869 | 0.48869 | 0.48869 | 2.2101 | 3.188 | 3.8287 | 4.1659 | 4.8403 | 5.5147 | 0.5792 | 1.5733 | 1.9733 | 1.9733 | 1.9733 | 1.9733 | 1.105 | 1.4026 | 1.4026 | 1.4026 | 1.4026 | 1.4026
2020-05-30 18:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.52585 | 0.52585 | 0.52585 | 0.52585 | 0.52585 | 0.52585 | 2.1148 | 3.0506 | 3.6637 | 3.9863 | 4.6317 | 5.277 | 0.61349 | 1.6665 | 2.0902 | 2.0902 | 2.0902 | 2.0902 | 1.0098 | 1.2817 | 1.2817 | 1.2817 | 1.2817 | 1.2817
2020-05-30 19:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.52585 | 0.52585 | 0.52585 | 0.52585 | 0.52585 | 0.52585 | 2.078 | 2.9974 | 3.5998 | 3.9168 | 4.5509 | 5.185 | 0.62492 | 1.6975 | 2.1291 | 2.1291 | 2.1291 | 2.1291 | 0.97168 | 1.2333 | 1.2333 | 1.2333 | 1.2333 | 1.2333
2020-05-30 20:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 2.0386 | 2.9407 | 3.5316 | 3.8427 | 4.4648 | 5.0869 | 0.6173 | 1.6768 | 2.1032 | 2.1032 | 2.1032 | 2.1032 | 0.99073 | 1.2575 | 1.2575 | 1.2575 | 1.2575 | 1.2575
2020-05-30 21:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.48584 | 0.48584 | 0.48584 | 0.48584 | 0.48584 | 0.48584 | 2.0958 | 3.0231 | 3.6307 | 3.9504 | 4.59 | 5.2295 | 0.62492 | 1.6975 | 2.1291 | 2.1291 | 2.1291 | 2.1291 | 0.91452 | 1.1608 | 1.1608 | 1.1608 | 1.1608 | 1.1608
2020-05-30 22:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 1.9624 | 2.8307 | 3.3996 | 3.699 | 4.2979 | 4.8967 | 0.53728 | 1.4595 | 1.8305 | 1.8305 | 1.8305 | 1.8305 | 0.85744 | 1.0883 | 1.0883 | 1.0883 | 1.0883 | 1.0883
2020-05-30 23:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 1.8481 | 2.6658 | 3.2016 | 3.4836 | 4.0475 | 4.6115 | 0.53728 | 1.4595 | 1.8305 | 1.8305 | 1.8305 | 1.8305 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-05-31 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.41153 | 0.41153 | 0.41153 | 0.41153 | 0.41153 | 0.41153 | 1.7147 | 2.4735 | 2.9705 | 3.2322 | 3.7554 | 4.2787 | 0.53728 | 1.4595 | 1.8305 | 1.8305 | 1.8305 | 1.8305 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-05-31 01:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 1.6195 | 2.336 | 2.8055 | 3.0526 | 3.5468 | 4.041 | 0.50889 | 1.3824 | 1.7338 | 1.7338 | 1.7338 | 1.7338 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-05-31 02:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.36581 | 0.36581 | 0.36581 | 0.36581 | 0.36581 | 0.36581 | 1.5664 | 2.2595 | 2.7136 | 2.9526 | 3.4306 | 3.9086 | 0.52966 | 1.4388 | 1.8046 | 1.8046 | 1.8046 | 1.8046 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-05-31 03:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.40582 | 0.40582 | 0.40582 | 0.40582 | 0.40582 | 0.40582 | 1.5623 | 2.2536 | 2.7065 | 2.9449 | 3.4216 | 3.8984 | 0.4725 | 1.2835 | 1.6098 | 1.6098 | 1.6098 | 1.6098 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-05-31 04:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.36866 | 0.36866 | 0.36866 | 0.36866 | 0.36866 | 0.36866 | 1.5814 | 2.2811 | 2.7395 | 2.9808 | 3.4633 | 3.9459 | 0.48774 | 1.3249 | 1.6618 | 1.6618 | 1.6618 | 1.6618 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-05-31 05:00 | Winter | 0.53331 | 0.82003 | 1.2409 | 1.2409 | 1.2409 | 1.2409 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.46869 | 1.2732 | 1.5968 | 1.5968 | 1.5968 | 1.5968 | 0.80021 | 1.0157 | 1.0157 | 1.0157 | 1.0157 | 1.0157
2020-05-31 06:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 1.6576 | 2.391 | 2.8715 | 3.1244 | 3.6302 | 4.1361 | 0.46869 | 1.2732 | 1.5968 | 1.5968 | 1.5968 | 1.5968 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-05-31 07:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.50298 | 0.50298 | 0.50298 | 0.50298 | 0.50298 | 0.50298 | 1.7528 | 2.5284 | 3.0366 | 3.304 | 3.8389 | 4.3738 | 0.52204 | 1.4181 | 1.7786 | 1.7786 | 1.7786 | 1.7786 | 0.85062 | 1.0797 | 1.0797 | 1.0797 | 1.0797 | 1.0797
2020-05-31 08:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.51727 | 0.51727 | 0.51727 | 0.51727 | 0.51727 | 0.51727 | 1.8862 | 2.7208 | 3.2676 | 3.5554 | 4.131 | 4.7066 | 0.53347 | 1.4491 | 1.8175 | 1.8175 | 1.8175 | 1.8175 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-05-31 09:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.53442 | 0.53442 | 0.53442 | 0.53442 | 0.53442 | 0.53442 | 1.8862 | 2.7208 | 3.2676 | 3.5554 | 4.131 | 4.7066 | 0.52585 | 1.4284 | 1.7916 | 1.7916 | 1.7916 | 1.7916 | 0.91452 | 1.1608 | 1.1608 | 1.1608 | 1.1608 | 1.1608
2020-05-31 10:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 1.9053 | 2.7483 | 3.3006 | 3.5913 | 4.1727 | 4.7541 | 0.51823 | 1.4077 | 1.7656 | 1.7656 | 1.7656 | 1.7656 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-05-31 11:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 1.8903 | 2.7268 | 3.2748 | 3.5632 | 4.14 | 4.7169 | 0.56395 | 1.5319 | 1.9214 | 1.9214 | 1.9214 | 1.9214 | 0.83156 | 1.0555 | 1.0555 | 1.0555 | 1.0555 | 1.0555
2020-05-31 12:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.43439 | 0.43439 | 0.43439 | 0.43439 | 0.43439 | 0.43439 | 1.9434 | 2.8032 | 3.3666 | 3.6631 | 4.2562 | 4.8492 | 0.51061 | 1.387 | 1.7396 | 1.7396 | 1.7396 | 1.7396 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-05-31 13:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 1.8862 | 2.7208 | 3.2676 | 3.5554 | 4.131 | 4.7066 | 0.48012 | 1.3042 | 1.6358 | 1.6358 | 1.6358 | 1.6358 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-05-31 14:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 1.9243 | 2.7758 | 3.3336 | 3.6272 | 4.2144 | 4.8016 | 0.51823 | 1.4077 | 1.7656 | 1.7656 | 1.7656 | 1.7656 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-05-31 15:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 1.8954 | 2.7341 | 3.2836 | 3.5728 | 4.1512 | 4.7296 | 0.49155 | 1.3353 | 1.6747 | 1.6747 | 1.6747 | 1.6747 | 0.83684 | 1.0622 | 1.0622 | 1.0622 | 1.0622 | 1.0622
2020-05-31 16:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 2.0255 | 2.9217 | 3.5088 | 3.8179 | 4.436 | 5.054 | 0.5068 | 1.3767 | 1.7267 | 1.7267 | 1.7267 | 1.7267 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-05-31 17:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.49441 | 0.49441 | 0.49441 | 0.49441 | 0.49441 | 0.49441 | 2.1339 | 3.0781 | 3.6967 | 4.0223 | 4.6734 | 5.3246 | 0.56776 | 1.5423 | 1.9344 | 1.9344 | 1.9344 | 1.9344 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-05-31 18:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.47441 | 0.47441 | 0.47441 | 0.47441 | 0.47441 | 0.47441 | 2.1339 | 3.0781 | 3.6967 | 4.0223 | 4.6734 | 5.3246 | 0.58682 | 1.594 | 1.9993 | 1.9993 | 1.9993 | 1.9993 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-05-31 19:00 | Winter | 0.53347 | 0.82027 | 1.2412 | 1.2412 | 1.2412 | 1.2412 | 0.52299 | 0.52299 | 0.52299 | 0.52299 | 0.52299 | 0.52299 | 1.9952 | 2.8781 | 3.4565 | 3.7609 | 4.3698 | 4.9786 | 0.54109 | 1.4698 | 1.8435 | 1.8435 | 1.8435 | 1.8435 | 0.93358 | 1.185 | 1.185 | 1.185 | 1.185 | 1.185
2020-05-31 20:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.47726 | 0.47726 | 0.47726 | 0.47726 | 0.47726 | 0.47726 | 2.0005 | 2.8857 | 3.4656 | 3.7709 | 4.3813 | 4.9918 | 0.56776 | 1.5423 | 1.9344 | 1.9344 | 1.9344 | 1.9344 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-05-31 21:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 1.9624 | 2.8307 | 3.3996 | 3.699 | 4.2979 | 4.8967 | 0.58301 | 1.5837 | 1.9863 | 1.9863 | 1.9863 | 1.9863 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-05-31 22:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.38581 | 0.38581 | 0.38581 | 0.38581 | 0.38581 | 0.38581 | 1.9056 | 2.7487 | 3.3012 | 3.5919 | 4.1734 | 4.7549 | 0.58682 | 1.594 | 1.9993 | 1.9993 | 1.9993 | 1.9993 | 0.81939 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04
2020-05-31 23:00 | Winter | 0.55228 | 0.84919 | 1.285 | 1.285 | 1.285 | 1.285 | 0.38581 | 0.38581 | 0.38581 | 0.38581 | 0.38581 | 0.38581 | 1.7149 | 2.4736 | 2.9708 | 3.2324 | 3.7557 | 4.279 | 0.46488 | 1.2628 | 1.5839 | 1.5839 | 1.5839 | 1.5839 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-06-01 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.35723 | 0.35723 | 0.35723 | 0.35723 | 0.35723 | 0.35723 | 1.7147 | 2.4735 | 2.9705 | 3.2322 | 3.7554 | 4.2787 | 0.49536 | 1.3456 | 1.6877 | 1.6877 | 1.6877 | 1.6877 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-06-01 01:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.38581 | 0.38581 | 0.38581 | 0.38581 | 0.38581 | 0.38581 | 1.5433 | 2.2261 | 2.6735 | 2.909 | 3.3799 | 3.8508 | 0.46869 | 1.2732 | 1.5968 | 1.5968 | 1.5968 | 1.5968 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-06-01 02:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.41439 | 0.41439 | 0.41439 | 0.41439 | 0.41439 | 0.41439 | 1.5814 | 2.2811 | 2.7395 | 2.9808 | 3.4633 | 3.9459 | 0.45345 | 1.2318 | 1.5449 | 1.5449 | 1.5449 | 1.5449 | 0.99073 | 1.2575 | 1.2575 | 1.2575 | 1.2575 | 1.2575
2020-06-01 03:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.36866 | 0.36866 | 0.36866 | 0.36866 | 0.36866 | 0.36866 | 1.5623 | 2.2536 | 2.7065 | 2.9449 | 3.4216 | 3.8984 | 0.46488 | 1.2628 | 1.5839 | 1.5839 | 1.5839 | 1.5839 | 0.99073 | 1.2575 | 1.2575 | 1.2575 | 1.2575 | 1.2575
2020-06-01 04:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.36009 | 0.36009 | 0.36009 | 0.36009 | 0.36009 | 0.36009 | 1.5401 | 2.2216 | 2.668 | 2.903 | 3.373 | 3.843 | 0.46107 | 1.2525 | 1.5709 | 1.5709 | 1.5709 | 1.5709 | 1.0288 | 1.3059 | 1.3059 | 1.3059 | 1.3059 | 1.3059
2020-06-01 05:00 | Winter | 0.57152 | 0.87878 | 1.3298 | 1.3298 | 1.3298 | 1.3298 | 0.37724 | 0.37724 | 0.37724 | 0.37724 | 0.37724 | 0.37724 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.5068 | 1.3767 | 1.7267 | 1.7267 | 1.7267 | 1.7267 | 1.3568 | 1.7222 | 1.7222 | 1.7222 | 1.7222 | 1.7222
2020-06-01 06:00 | Winter | 0.57638 | 0.88626 | 1.3411 | 1.3411 | 1.3411 | 1.3411 | 0.39438 | 0.39438 | 0.39438 | 0.39438 | 0.39438 | 0.39438 | 1.6764 | 2.4181 | 2.9041 | 3.1598 | 3.6714 | 4.1829 | 0.54109 | 1.4698 | 1.8435 | 1.8435 | 1.8435 | 1.8435 | 1.5242 | 1.9346 | 1.9346 | 1.9346 | 1.9346 | 1.9346
2020-06-01 07:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 1.9291 | 2.7826 | 3.3418 | 3.6362 | 4.2248 | 4.8135 | 0.5068 | 1.3767 | 1.7267 | 1.7267 | 1.7267 | 1.7267 | 1.7495 | 2.2206 | 2.2206 | 2.2206 | 2.2206 | 2.2206
2020-06-01 08:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.43154 | 0.43154 | 0.43154 | 0.43154 | 0.43154 | 0.43154 | 2.0577 | 2.9681 | 3.5647 | 3.8786 | 4.5065 | 5.1344 | 0.53347 | 1.4491 | 1.8175 | 1.8175 | 1.8175 | 1.8175 | 1.7719 | 2.249 | 2.249 | 2.249 | 2.249 | 2.249
2020-06-01 09:00 | Winter | 0.64779 | 0.99605 | 1.5072 | 1.5072 | 1.5072 | 1.5072 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 2.0577 | 2.9681 | 3.5647 | 3.8786 | 4.5065 | 5.1344 | 0.53347 | 1.4491 | 1.8175 | 1.8175 | 1.8175 | 1.8175 | 1.81 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974
2020-06-01 10:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.40296 | 0.40296 | 0.40296 | 0.40296 | 0.40296 | 0.40296 | 2.0767 | 2.9956 | 3.5977 | 3.9145 | 4.5482 | 5.182 | 0.59063 | 1.6044 | 2.0123 | 2.0123 | 2.0123 | 2.0123 | 1.7719 | 2.249 | 2.249 | 2.249 | 2.249 | 2.249
2020-06-01 11:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.34803 | 0.34803 | 0.34803 | 0.34803 | 0.34803 | 0.34803 | 2.0047 | 2.8917 | 3.4728 | 3.7787 | 4.3904 | 5.0022 | 0.51442 | 1.3974 | 1.7526 | 1.7526 | 1.7526 | 1.7526 | 1.7719 | 2.249 | 2.249 | 2.249 | 2.249 | 2.249
2020-06-01 12:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.43154 | 0.43154 | 0.43154 | 0.43154 | 0.43154 | 0.43154 | 2.1529 | 3.1056 | 3.7297 | 4.0582 | 4.7151 | 5.3721 | 0.50299 | 1.3663 | 1.7137 | 1.7137 | 1.7137 | 1.7137 | 1.7338 | 2.2007 | 2.2007 | 2.2007 | 2.2007 | 2.2007
2020-06-01 13:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.39724 | 0.39724 | 0.39724 | 0.39724 | 0.39724 | 0.39724 | 2.0958 | 3.0231 | 3.6307 | 3.9504 | 4.59 | 5.2295 | 0.51823 | 1.4077 | 1.7656 | 1.7656 | 1.7656 | 1.7656 | 1.7147 | 2.1765 | 2.1765 | 2.1765 | 2.1765 | 2.1765
2020-06-01 14:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.41176 | 0.41176 | 0.41176 | 0.41176 | 0.41176 | 0.41176 | 2.172 | 3.133 | 3.7627 | 4.0941 | 4.7569 | 5.4197 | 0.50299 | 1.3663 | 1.7137 | 1.7137 | 1.7137 | 1.7137 | 1.7909 | 2.2732 | 2.2732 | 2.2732 | 2.2732 | 2.2732
2020-06-01 15:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 2.2482 | 3.243 | 3.8947 | 4.2377 | 4.9238 | 5.6098 | 0.54871 | 1.4905 | 1.8695 | 1.8695 | 1.8695 | 1.8695 | 1.7528 | 2.2248 | 2.2248 | 2.2248 | 2.2248 | 2.2248
2020-06-01 16:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 2.2482 | 3.243 | 3.8947 | 4.2377 | 4.9238 | 5.6098 | 0.56395 | 1.5319 | 1.9214 | 1.9214 | 1.9214 | 1.9214 | 1.7366 | 2.2043 | 2.2043 | 2.2043 | 2.2043 | 2.2043
2020-06-01 17:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 2.4197 | 3.4903 | 4.1918 | 4.561 | 5.2993 | 6.0377 | 0.62492 | 1.6975 | 2.1291 | 2.1291 | 2.1291 | 2.1291 | 1.6766 | 2.1281 | 2.1281 | 2.1281 | 2.1281 | 2.1281
2020-06-01 18:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 2.3625 | 3.4079 | 4.0927 | 4.4532 | 5.1741 | 5.8951 | 0.68208 | 1.8528 | 2.3239 | 2.3239 | 2.3239 | 2.3239 | 1.1947 | 1.5164 | 1.5164 | 1.5164 | 1.5164 | 1.5164
2020-06-01 19:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 2.2958 | 3.3117 | 3.9773 | 4.3275 | 5.0281 | 5.7287 | 0.63254 | 1.7182 | 2.1551 | 2.1551 | 2.1551 | 2.1551 | 0.97168 | 1.2333 | 1.2333 | 1.2333 | 1.2333 | 1.2333
2020-06-01 20:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.42409 | 0.42409 | 0.42409 | 0.42409 | 0.42409 | 0.42409 | 2.172 | 3.133 | 3.7627 | 4.0941 | 4.7569 | 5.4197 | 0.64016 | 1.7389 | 2.1811 | 2.1811 | 2.1811 | 2.1811 | 0.97168 | 1.2333 | 1.2333 | 1.2333 | 1.2333 | 1.2333
2020-06-01 21:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 2.0577 | 2.9681 | 3.5647 | 3.8786 | 4.5065 | 5.1344 | 0.59825 | 1.6251 | 2.0382 | 2.0382 | 2.0382 | 2.0382 | 0.97168 | 1.2333 | 1.2333 | 1.2333 | 1.2333 | 1.2333
2020-06-01 22:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 1.9624 | 2.8307 | 3.3996 | 3.699 | 4.2979 | 4.8967 | 0.5792 | 1.5733 | 1.9733 | 1.9733 | 1.9733 | 1.9733 | 0.91952 | 1.1671 | 1.1671 | 1.1671 | 1.1671 | 1.1671
2020-06-01 23:00 | Winter | 0.54262 | 0.83435 | 1.2625 | 1.2625 | 1.2625 | 1.2625 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 1.829 | 2.6383 | 3.1686 | 3.4477 | 4.0058 | 4.5639 | 0.54109 | 1.4698 | 1.8435 | 1.8435 | 1.8435 | 1.8435 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-06-02 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 1.6576 | 2.391 | 2.8715 | 3.1244 | 3.6302 | 4.1361 | 0.51061 | 1.387 | 1.7396 | 1.7396 | 1.7396 | 1.7396 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-06-02 01:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 1.5814 | 2.2811 | 2.7395 | 2.9808 | 3.4633 | 3.9459 | 0.50299 | 1.3663 | 1.7137 | 1.7137 | 1.7137 | 1.7137 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-06-02 02:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.4544 | 0.4544 | 0.4544 | 0.4544 | 0.4544 | 0.4544 | 1.5814 | 2.2811 | 2.7395 | 2.9808 | 3.4633 | 3.9459 | 0.5068 | 1.3767 | 1.7267 | 1.7267 | 1.7267 | 1.7267 | 1.0669 | 1.3542 | 1.3542 | 1.3542 | 1.3542 | 1.3542
2020-06-02 03:00 | Winter | 0.55611 | 0.85508 | 1.2939 | 1.2939 | 1.2939 | 1.2939 | 0.45368 | 0.45368 | 0.45368 | 0.45368 | 0.45368 | 0.45368 | 1.5708 | 2.2658 | 2.7212 | 2.9609 | 3.4402 | 3.9195 | 0.49918 | 1.356 | 1.7007 | 1.7007 | 1.7007 | 1.7007 | 1.105 | 1.4026 | 1.4026 | 1.4026 | 1.4026 | 1.4026
2020-06-02 04:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.49155 | 0.49155 | 0.49155 | 0.49155 | 0.49155 | 0.49155 | 1.6653 | 2.4022 | 2.885 | 3.1391 | 3.6473 | 4.1555 | 0.51061 | 1.387 | 1.7396 | 1.7396 | 1.7396 | 1.7396 | 1.1007 | 1.3971 | 1.3971 | 1.3971 | 1.3971 | 1.3971
2020-06-02 05:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.61442 | 0.61442 | 0.61442 | 0.61442 | 0.61442 | 0.61442 | 1.8862 | 2.7208 | 3.2676 | 3.5554 | 4.131 | 4.7066 | 0.64779 | 1.7596 | 2.207 | 2.207 | 2.207 | 2.207 | 1.4869 | 1.8872 | 1.8872 | 1.8872 | 1.8872 | 1.8872
2020-06-02 06:00 | Winter | 0.89547 | 1.3769 | 2.0835 | 2.0835 | 2.0835 | 2.0835 | 0.7459 | 0.7459 | 0.7459 | 0.7459 | 0.7459 | 0.7459 | 2.0577 | 2.9681 | 3.5647 | 3.8786 | 4.5065 | 5.1344 | 0.6516 | 1.77 | 2.22 | 2.22 | 2.22 | 2.22 | 1.7909 | 2.2732 | 2.2732 | 2.2732 | 2.2732 | 2.2732
2020-06-02 07:00 | Winter | 1.1813 | 1.8163 | 2.7485 | 2.7485 | 2.7485 | 2.7485 | 0.86022 | 0.86022 | 0.86022 | 0.86022 | 0.86022 | 0.86022 | 2.6071 | 3.7606 | 4.5164 | 4.9142 | 5.7098 | 6.5053 | 0.72018 | 1.9563 | 2.4537 | 2.4537 | 2.4537 | 2.4537 | 2.2665 | 2.8768 | 2.8768 | 2.8768 | 2.8768 | 2.8768
2020-06-02 08:00 | Winter | 1.2956 | 1.9921 | 3.0144 | 3.0144 | 3.0144 | 3.0144 | 1.0117 | 1.0117 | 1.0117 | 1.0117 | 1.0117 | 1.0117 | 2.6674 | 3.8476 | 4.6208 | 5.0278 | 5.8418 | 6.6557 | 0.76972 | 2.0909 | 2.6225 | 2.6225 | 2.6225 | 2.6225 | 2.6102 | 3.3131 | 3.3131 | 3.3131 | 3.3131 | 3.3131
2020-06-02 09:00 | Winter | 1.2956 | 1.9921 | 3.0144 | 3.0144 | 3.0144 | 3.0144 | 1.0603 | 1.0603 | 1.0603 | 1.0603 | 1.0603 | 1.0603 | 2.5544 | 3.6846 | 4.4251 | 4.8149 | 5.5943 | 6.3738 | 0.73162 | 1.9874 | 2.4926 | 2.4926 | 2.4926 | 2.4926 | 2.6674 | 3.3856 | 3.3856 | 3.3856 | 3.3856 | 3.3856
2020-06-02 10:00 | Winter | 1.2575 | 1.9335 | 2.9258 | 2.9258 | 2.9258 | 2.9258 | 1.1146 | 1.1146 | 1.1146 | 1.1146 | 1.1146 | 1.1146 | 2.534 | 3.6552 | 4.3898 | 4.7764 | 5.5497 | 6.3229 | 0.75067 | 2.0391 | 2.5575 | 2.5575 | 2.5575 | 2.5575 | 2.553 | 3.2405 | 3.2405 | 3.2405 | 3.2405 | 3.2405
2020-06-02 11:00 | Winter | 1.2194 | 1.8749 | 2.8371 | 2.8371 | 2.8371 | 2.8371 | 1.0374 | 1.0374 | 1.0374 | 1.0374 | 1.0374 | 1.0374 | 2.4959 | 3.6002 | 4.3238 | 4.7046 | 5.4662 | 6.2279 | 0.7964 | 2.1633 | 2.7133 | 2.7133 | 2.7133 | 2.7133 | 2.5911 | 3.2889 | 3.2889 | 3.2889 | 3.2889 | 3.2889
2020-06-02 12:00 | Winter | 1.1813 | 1.8163 | 2.7485 | 2.7485 | 2.7485 | 2.7485 | 1.0603 | 1.0603 | 1.0603 | 1.0603 | 1.0603 | 1.0603 | 2.553 | 3.6827 | 4.4228 | 4.8123 | 5.5914 | 6.3705 | 0.80402 | 2.184 | 2.7393 | 2.7393 | 2.7393 | 2.7393 | 2.6102 | 3.3131 | 3.3131 | 3.3131 | 3.3131 | 3.3131
2020-06-02 13:00 | Winter | 1.2003 | 1.8456 | 2.7928 | 2.7928 | 2.7928 | 2.7928 | 0.99454 | 0.99454 | 0.99454 | 0.99454 | 0.99454 | 0.99454 | 2.4959 | 3.6002 | 4.3238 | 4.7046 | 5.4662 | 6.2279 | 0.79258 | 2.153 | 2.7003 | 2.7003 | 2.7003 | 2.7003 | 2.5149 | 3.1922 | 3.1922 | 3.1922 | 3.1922 | 3.1922
2020-06-02 14:00 | Winter | 1.1599 | 1.7835 | 2.6987 | 2.6987 | 2.6987 | 2.6987 | 0.98597 | 0.98597 | 0.98597 | 0.98597 | 0.98597 | 0.98597 | 2.4006 | 3.4628 | 4.1588 | 4.525 | 5.2576 | 5.9902 | 0.78115 | 2.1219 | 2.6614 | 2.6614 | 2.6614 | 2.6614 | 2.3625 | 2.9987 | 2.9987 | 2.9987 | 2.9987 | 2.9987
2020-06-02 15:00 | Winter | 1.1813 | 1.8163 | 2.7485 | 2.7485 | 2.7485 | 2.7485 | 0.93738 | 0.93738 | 0.93738 | 0.93738 | 0.93738 | 0.93738 | 2.4006 | 3.4628 | 4.1588 | 4.525 | 5.2576 | 5.9902 | 0.80783 | 2.1944 | 2.7523 | 2.7523 | 2.7523 | 2.7523 | 2.2873 | 2.9033 | 2.9033 | 2.9033 | 2.9033 | 2.9033
2020-06-02 16:00 | Winter | 1.1241 | 1.7284 | 2.6155 | 2.6155 | 2.6155 | 2.6155 | 0.9088 | 0.9088 | 0.9088 | 0.9088 | 0.9088 | 0.9088 | 2.3625 | 3.4079 | 4.0927 | 4.4532 | 5.1741 | 5.8951 | 0.83831 | 2.2772 | 2.8561 | 2.8561 | 2.8561 | 2.8561 | 2.3435 | 2.9745 | 2.9745 | 2.9745 | 2.9745 | 2.9745
2020-06-02 17:00 | Winter | 1.0669 | 1.6405 | 2.4825 | 2.4825 | 2.4825 | 2.4825 | 0.89737 | 0.89737 | 0.89737 | 0.89737 | 0.89737 | 0.89737 | 2.5721 | 3.7102 | 4.4558 | 4.8483 | 5.6331 | 6.418 | 0.86498 | 2.3496 | 2.947 | 2.947 | 2.947 | 2.947 | 2.254 | 2.861 | 2.861 | 2.861 | 2.861 | 2.861
2020-06-02 18:00 | Winter | 0.97183 | 1.4943 | 2.2612 | 2.2612 | 2.2612 | 2.2612 | 0.75734 | 0.75734 | 0.75734 | 0.75734 | 0.75734 | 0.75734 | 2.534 | 3.6552 | 4.3898 | 4.7764 | 5.5497 | 6.3229 | 0.84286 | 2.2895 | 2.8716 | 2.8716 | 2.8716 | 2.8716 | 1.7368 | 2.2044 | 2.2044 | 2.2044 | 2.2044 | 2.2044
2020-06-02 19:00 | Winter | 0.64779 | 0.99605 | 1.5072 | 1.5072 | 1.5072 | 1.5072 | 0.56586 | 0.56586 | 0.56586 | 0.56586 | 0.56586 | 0.56586 | 2.3816 | 3.4353 | 4.1258 | 4.4891 | 5.2159 | 5.9426 | 0.74686 | 2.0288 | 2.5446 | 2.5446 | 2.5446 | 2.5446 | 1.1813 | 1.4993 | 1.4993 | 1.4993 | 1.4993 | 1.4993
2020-06-02 20:00 | Winter | 0.62911 | 0.96732 | 1.4637 | 1.4637 | 1.4637 | 1.4637 | 0.43439 | 0.43439 | 0.43439 | 0.43439 | 0.43439 | 0.43439 | 2.3244 | 3.3529 | 4.0267 | 4.3814 | 5.0907 | 5.8 | 0.67827 | 1.8425 | 2.3109 | 2.3109 | 2.3109 | 2.3109 | 1.0669 | 1.3542 | 1.3542 | 1.3542 | 1.3542 | 1.3542
2020-06-02 21:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.48584 | 0.48584 | 0.48584 | 0.48584 | 0.48584 | 0.48584 | 2.1148 | 3.0506 | 3.6637 | 3.9863 | 4.6317 | 5.277 | 0.71256 | 1.9356 | 2.4277 | 2.4277 | 2.4277 | 2.4277 | 0.99073 | 1.2575 | 1.2575 | 1.2575 | 1.2575 | 1.2575
2020-06-02 22:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.38581 | 0.38581 | 0.38581 | 0.38581 | 0.38581 | 0.38581 | 2.0005 | 2.8857 | 3.4656 | 3.7709 | 4.3813 | 4.9918 | 0.65922 | 1.7907 | 2.246 | 2.246 | 2.246 | 2.246 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-06-02 23:00 | Winter | 0.59025 | 0.90758 | 1.3733 | 1.3733 | 1.3733 | 1.3733 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 1.9624 | 2.8307 | 3.3996 | 3.699 | 4.2979 | 4.8967 | 0.61458 | 1.6694 | 2.0939 | 2.0939 | 2.0939 | 2.0939 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-06-03 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 1.7338 | 2.5009 | 3.0036 | 3.2681 | 3.7972 | 4.3262 | 0.59444 | 1.6147 | 2.0253 | 2.0253 | 2.0253 | 2.0253 | 0.85723 | 1.0881 | 1.0881 | 1.0881 | 1.0881 | 1.0881
2020-06-03 01:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.40296 | 0.40296 | 0.40296 | 0.40296 | 0.40296 | 0.40296 | 1.6602 | 2.3947 | 2.876 | 3.1293 | 3.6359 | 4.1425 | 0.56014 | 1.5216 | 1.9084 | 1.9084 | 1.9084 | 1.9084 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-06-03 02:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 1.5695 | 2.264 | 2.719 | 2.9585 | 3.4375 | 3.9164 | 0.55633 | 1.5112 | 1.8954 | 1.8954 | 1.8954 | 1.8954 | 1.0433 | 1.3242 | 1.3242 | 1.3242 | 1.3242 | 1.3242
2020-06-03 03:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.41439 | 0.41439 | 0.41439 | 0.41439 | 0.41439 | 0.41439 | 1.6195 | 2.336 | 2.8055 | 3.0526 | 3.5468 | 4.041 | 0.5792 | 1.5733 | 1.9733 | 1.9733 | 1.9733 | 1.9733 | 1.086 | 1.3784 | 1.3784 | 1.3784 | 1.3784 | 1.3784
2020-06-03 04:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.49155 | 0.49155 | 0.49155 | 0.49155 | 0.49155 | 0.49155 | 1.6195 | 2.336 | 2.8055 | 3.0526 | 3.5468 | 4.041 | 0.5449 | 1.4802 | 1.8565 | 1.8565 | 1.8565 | 1.8565 | 1.086 | 1.3784 | 1.3784 | 1.3784 | 1.3784 | 1.3784
2020-06-03 05:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.68017 | 0.68017 | 0.68017 | 0.68017 | 0.68017 | 0.68017 | 1.7822 | 2.5708 | 3.0875 | 3.3594 | 3.9033 | 4.4471 | 0.6173 | 1.6768 | 2.1032 | 2.1032 | 2.1032 | 2.1032 | 1.5052 | 1.9105 | 1.9105 | 1.9105 | 1.9105 | 1.9105
2020-06-03 06:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.77734 | 0.77734 | 0.77734 | 0.77734 | 0.77734 | 0.77734 | 2.0386 | 2.9407 | 3.5316 | 3.8427 | 4.4648 | 5.0869 | 0.73924 | 2.0081 | 2.5186 | 2.5186 | 2.5186 | 2.5186 | 1.7338 | 2.2007 | 2.2007 | 2.2007 | 2.2007 | 2.2007
2020-06-03 07:00 | Winter | 1.0785 | 1.6583 | 2.5093 | 2.5093 | 2.5093 | 2.5093 | 0.85724 | 0.85724 | 0.85724 | 0.85724 | 0.85724 | 0.85724 | 2.3054 | 3.3254 | 3.9937 | 4.3455 | 5.049 | 5.7525 | 0.76972 | 2.0909 | 2.6225 | 2.6225 | 2.6225 | 2.6225 | 2.2021 | 2.795 | 2.795 | 2.795 | 2.795 | 2.795
2020-06-03 08:00 | Winter | 1.2575 | 1.9335 | 2.9258 | 2.9258 | 2.9258 | 2.9258 | 1.0145 | 1.0145 | 1.0145 | 1.0145 | 1.0145 | 1.0145 | 2.4768 | 3.5728 | 4.2908 | 4.6687 | 5.4245 | 6.1803 | 0.87642 | 2.3807 | 2.986 | 2.986 | 2.986 | 2.986 | 2.4959 | 3.168 | 3.168 | 3.168 | 3.168 | 3.168
2020-06-03 09:00 | Winter | 1.2194 | 1.8749 | 2.8371 | 2.8371 | 2.8371 | 2.8371 | 0.99454 | 0.99454 | 0.99454 | 0.99454 | 0.99454 | 0.99454 | 2.5613 | 3.6947 | 4.4372 | 4.828 | 5.6096 | 6.3912 | 0.81926 | 2.2254 | 2.7912 | 2.7912 | 2.7912 | 2.7912 | 2.4768 | 3.1438 | 3.1438 | 3.1438 | 3.1438 | 3.1438
2020-06-03 10:00 | Winter | 1.1813 | 1.8163 | 2.7485 | 2.7485 | 2.7485 | 2.7485 | 0.97739 | 0.97739 | 0.97739 | 0.97739 | 0.97739 | 0.97739 | 2.5721 | 3.7102 | 4.4558 | 4.8483 | 5.6331 | 6.418 | 0.82688 | 2.2461 | 2.8172 | 2.8172 | 2.8172 | 2.8172 | 2.4959 | 3.168 | 3.168 | 3.168 | 3.168 | 3.168
2020-06-03 11:00 | Winter | 1.1241 | 1.7284 | 2.6155 | 2.6155 | 2.6155 | 2.6155 | 0.97739 | 0.97739 | 0.97739 | 0.97739 | 0.97739 | 0.97739 | 2.5149 | 3.6277 | 4.3568 | 4.7405 | 5.508 | 6.2754 | 0.82307 | 2.2358 | 2.8042 | 2.8042 | 2.8042 | 2.8042 | 2.553 | 3.2405 | 3.2405 | 3.2405 | 3.2405 | 3.2405
2020-06-03 12:00 | Winter | 1.1622 | 1.787 | 2.7041 | 2.7041 | 2.7041 | 2.7041 | 1.0003 | 1.0003 | 1.0003 | 1.0003 | 1.0003 | 1.0003 | 2.5149 | 3.6277 | 4.3568 | 4.7405 | 5.508 | 6.2754 | 0.78496 | 2.1323 | 2.6744 | 2.6744 | 2.6744 | 2.6744 | 2.4006 | 3.0471 | 3.0471 | 3.0471 | 3.0471 | 3.0471
2020-06-03 13:00 | Winter | 1.1241 | 1.7284 | 2.6155 | 2.6155 | 2.6155 | 2.6155 | 0.9974 | 0.9974 | 0.9974 | 0.9974 | 0.9974 | 0.9974 | 2.4768 | 3.5728 | 4.2908 | 4.6687 | 5.4245 | 6.1803 | 0.79258 | 2.153 | 2.7003 | 2.7003 | 2.7003 | 2.7003 | 2.3244 | 2.9503 | 2.9503 | 2.9503 | 2.9503 | 2.9503
2020-06-03 14:00 | Winter | 1.1432 | 1.7577 | 2.6598 | 2.6598 | 2.6598 | 2.6598 | 0.98025 | 0.98025 | 0.98025 | 0.98025 | 0.98025 | 0.98025 | 2.4959 | 3.6002 | 4.3238 | 4.7046 | 5.4662 | 6.2279 | 0.80021 | 2.1737 | 2.7263 | 2.7263 | 2.7263 | 2.7263 | 2.3435 | 2.9745 | 2.9745 | 2.9745 | 2.9745 | 2.9745
2020-06-03 15:00 | Winter | 1.1241 | 1.7284 | 2.6155 | 2.6155 | 2.6155 | 2.6155 | 1.0203 | 1.0203 | 1.0203 | 1.0203 | 1.0203 | 1.0203 | 2.4578 | 3.5453 | 4.2578 | 4.6328 | 5.3828 | 6.1328 | 0.83831 | 2.2772 | 2.8561 | 2.8561 | 2.8561 | 2.8561 | 2.1529 | 2.7327 | 2.7327 | 2.7327 | 2.7327 | 2.7327
2020-06-03 16:00 | Winter | 1.086 | 1.6698 | 2.5268 | 2.5268 | 2.5268 | 2.5268 | 1.0488 | 1.0488 | 1.0488 | 1.0488 | 1.0488 | 1.0488 | 2.4006 | 3.4628 | 4.1588 | 4.525 | 5.2576 | 5.9902 | 0.83831 | 2.2772 | 2.8561 | 2.8561 | 2.8561 | 2.8561 | 2.2482 | 2.8536 | 2.8536 | 2.8536 | 2.8536 | 2.8536
2020-06-03 17:00 | Winter | 1.0288 | 1.582 | 2.3938 | 2.3938 | 2.3938 | 2.3938 | 0.9088 | 0.9088 | 0.9088 | 0.9088 | 0.9088 | 0.9088 | 2.5149 | 3.6277 | 4.3568 | 4.7405 | 5.508 | 6.2754 | 0.82688 | 2.2461 | 2.8172 | 2.8172 | 2.8172 | 2.8172 | 2.191 | 2.781 | 2.781 | 2.781 | 2.781 | 2.781
2020-06-03 18:00 | Winter | 0.91452 | 1.4062 | 2.1278 | 2.1278 | 2.1278 | 2.1278 | 0.81164 | 0.81164 | 0.81164 | 0.81164 | 0.81164 | 0.81164 | 2.4959 | 3.6002 | 4.3238 | 4.7046 | 5.4662 | 6.2279 | 0.84593 | 2.2979 | 2.8821 | 2.8821 | 2.8821 | 2.8821 | 1.6293 | 2.068 | 2.068 | 2.068 | 2.068 | 2.068
2020-06-03 19:00 | Winter | 0.64779 | 0.99605 | 1.5072 | 1.5072 | 1.5072 | 1.5072 | 0.57544 | 0.57544 | 0.57544 | 0.57544 | 0.57544 | 0.57544 | 2.3636 | 3.4094 | 4.0946 | 4.4552 | 5.1765 | 5.8978 | 0.78877 | 2.1426 | 2.6874 | 2.6874 | 2.6874 | 2.6874 | 1.2003 | 1.5235 | 1.5235 | 1.5235 | 1.5235 | 1.5235
2020-06-03 20:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.49155 | 0.49155 | 0.49155 | 0.49155 | 0.49155 | 0.49155 | 2.2471 | 3.2413 | 3.8928 | 4.2356 | 4.9213 | 5.607 | 0.74686 | 2.0288 | 2.5446 | 2.5446 | 2.5446 | 2.5446 | 1.105 | 1.4026 | 1.4026 | 1.4026 | 1.4026 | 1.4026
2020-06-03 21:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 2.1339 | 3.0781 | 3.6967 | 4.0223 | 4.6734 | 5.3246 | 0.67446 | 1.8321 | 2.2979 | 2.2979 | 2.2979 | 2.2979 | 1.0288 | 1.3059 | 1.3059 | 1.3059 | 1.3059 | 1.3059
2020-06-03 22:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 1.9815 | 2.8582 | 3.4326 | 3.735 | 4.3396 | 4.9443 | 0.73162 | 1.9874 | 2.4926 | 2.4926 | 2.4926 | 2.4926 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-06-03 23:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 1.81 | 2.6109 | 3.1356 | 3.4117 | 3.9641 | 4.5164 | 0.64779 | 1.7596 | 2.207 | 2.207 | 2.207 | 2.207 | 0.91452 | 1.1608 | 1.1608 | 1.1608 | 1.1608 | 1.1608
2020-06-04 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 1.7147 | 2.4735 | 2.9705 | 3.2322 | 3.7554 | 4.2787 | 0.60206 | 1.6354 | 2.0512 | 2.0512 | 2.0512 | 2.0512 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-06-04 01:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 1.6195 | 2.336 | 2.8055 | 3.0526 | 3.5468 | 4.041 | 0.5449 | 1.4802 | 1.8565 | 1.8565 | 1.8565 | 1.8565 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-06-04 02:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.46869 | 0.46869 | 0.46869 | 0.46869 | 0.46869 | 0.46869 | 1.6195 | 2.336 | 2.8055 | 3.0526 | 3.5468 | 4.041 | 0.51823 | 1.4077 | 1.7656 | 1.7656 | 1.7656 | 1.7656 | 1.0859 | 1.3783 | 1.3783 | 1.3783 | 1.3783 | 1.3783
2020-06-04 03:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.52966 | 1.4388 | 1.8046 | 1.8046 | 1.8046 | 1.8046 | 1.086 | 1.3784 | 1.3784 | 1.3784 | 1.3784 | 1.3784
2020-06-04 04:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.51442 | 0.51442 | 0.51442 | 0.51442 | 0.51442 | 0.51442 | 1.6542 | 2.3862 | 2.8657 | 3.1181 | 3.6229 | 4.1277 | 0.56014 | 1.5216 | 1.9084 | 1.9084 | 1.9084 | 1.9084 | 1.105 | 1.4026 | 1.4026 | 1.4026 | 1.4026 | 1.4026
2020-06-04 05:00 | Winter | 0.5982 | 0.9198 | 1.3918 | 1.3918 | 1.3918 | 1.3918 | 0.64016 | 0.64016 | 0.64016 | 0.64016 | 0.64016 | 0.64016 | 1.8524 | 2.672 | 3.209 | 3.4916 | 4.0569 | 4.6221 | 0.63254 | 1.7182 | 2.1551 | 2.1551 | 2.1551 | 2.1551 | 1.5119 | 1.919 | 1.919 | 1.919 | 1.919 | 1.919
2020-06-04 06:00 | Winter | 0.66684 | 1.0253 | 1.5515 | 1.5515 | 1.5515 | 1.5515 | 0.78302 | 0.78302 | 0.78302 | 0.78302 | 0.78302 | 0.78302 | 2.0767 | 2.9956 | 3.5977 | 3.9145 | 4.5482 | 5.182 | 0.73162 | 1.9874 | 2.4926 | 2.4926 | 2.4926 | 2.4926 | 1.9218 | 2.4393 | 2.4393 | 2.4393 | 2.4393 | 2.4393
2020-06-04 07:00 | Winter | 1.0669 | 1.6405 | 2.4825 | 2.4825 | 2.4825 | 2.4825 | 0.91738 | 0.91738 | 0.91738 | 0.91738 | 0.91738 | 0.91738 | 2.4959 | 3.6002 | 4.3238 | 4.7046 | 5.4662 | 6.2279 | 0.82307 | 2.2358 | 2.8042 | 2.8042 | 2.8042 | 2.8042 | 2.2673 | 2.8778 | 2.8778 | 2.8778 | 2.8778 | 2.8778
2020-06-04 08:00 | Winter | 1.2384 | 1.9042 | 2.8814 | 2.8814 | 2.8814 | 2.8814 | 0.99454 | 0.99454 | 0.99454 | 0.99454 | 0.99454 | 0.99454 | 2.5721 | 3.7102 | 4.4558 | 4.8483 | 5.6331 | 6.418 | 0.82307 | 2.2358 | 2.8042 | 2.8042 | 2.8042 | 2.8042 | 2.5525 | 3.2398 | 3.2398 | 3.2398 | 3.2398 | 3.2398
2020-06-04 09:00 | Winter | 1.2384 | 1.9042 | 2.8814 | 2.8814 | 2.8814 | 2.8814 | 1.0603 | 1.0603 | 1.0603 | 1.0603 | 1.0603 | 1.0603 | 2.6293 | 3.7926 | 4.5548 | 4.956 | 5.7583 | 6.5606 | 0.77353 | 2.1012 | 2.6354 | 2.6354 | 2.6354 | 2.6354 | 2.6293 | 3.3373 | 3.3373 | 3.3373 | 3.3373 | 3.3373
2020-06-04 10:00 | Winter | 1.2003 | 1.8456 | 2.7928 | 2.7928 | 2.7928 | 2.7928 | 0.9974 | 0.9974 | 0.9974 | 0.9974 | 0.9974 | 0.9974 | 2.5149 | 3.6277 | 4.3568 | 4.7405 | 5.508 | 6.2754 | 0.83069 | 2.2565 | 2.8302 | 2.8302 | 2.8302 | 2.8302 | 2.5721 | 3.2647 | 3.2647 | 3.2647 | 3.2647 | 3.2647
2020-06-04 11:00 | Winter | 1.1622 | 1.787 | 2.7041 | 2.7041 | 2.7041 | 2.7041 | 0.98882 | 0.98882 | 0.98882 | 0.98882 | 0.98882 | 0.98882 | 2.553 | 3.6827 | 4.4228 | 4.8123 | 5.5914 | 6.3705 | 0.7621 | 2.0702 | 2.5965 | 2.5965 | 2.5965 | 2.5965 | 2.5721 | 3.2647 | 3.2647 | 3.2647 | 3.2647 | 3.2647
2020-06-04 12:00 | Winter | 1.2003 | 1.8456 | 2.7928 | 2.7928 | 2.7928 | 2.7928 | 0.98882 | 0.98882 | 0.98882 | 0.98882 | 0.98882 | 0.98882 | 2.5149 | 3.6277 | 4.3568 | 4.7405 | 5.508 | 6.2754 | 0.84974 | 2.3082 | 2.8951 | 2.8951 | 2.8951 | 2.8951 | 2.5721 | 3.2647 | 3.2647 | 3.2647 | 3.2647 | 3.2647
2020-06-04 13:00 | Winter | 1.1432 | 1.7577 | 2.6598 | 2.6598 | 2.6598 | 2.6598 | 1.046 | 1.046 | 1.046 | 1.046 | 1.046 | 1.046 | 2.553 | 3.6827 | 4.4228 | 4.8123 | 5.5914 | 6.3705 | 0.77353 | 2.1012 | 2.6354 | 2.6354 | 2.6354 | 2.6354 | 2.4197 | 3.0712 | 3.0712 | 3.0712 | 3.0712 | 3.0712
2020-06-04 14:00 | Winter | 1.1622 | 1.787 | 2.7041 | 2.7041 | 2.7041 | 2.7041 | 0.94596 | 0.94596 | 0.94596 | 0.94596 | 0.94596 | 0.94596 | 2.4197 | 3.4903 | 4.1918 | 4.561 | 5.2993 | 6.0377 | 0.80021 | 2.1737 | 2.7263 | 2.7263 | 2.7263 | 2.7263 | 2.3816 | 3.0229 | 3.0229 | 3.0229 | 3.0229 | 3.0229
2020-06-04 15:00 | Winter | 1.1241 | 1.7284 | 2.6155 | 2.6155 | 2.6155 | 2.6155 | 1.0203 | 1.0203 | 1.0203 | 1.0203 | 1.0203 | 1.0203 | 2.4006 | 3.4628 | 4.1588 | 4.525 | 5.2576 | 5.9902 | 0.79258 | 2.153 | 2.7003 | 2.7003 | 2.7003 | 2.7003 | 2.2374 | 2.8399 | 2.8399 | 2.8399 | 2.8399 | 2.8399
2020-06-04 16:00 | Winter | 1.1241 | 1.7284 | 2.6155 | 2.6155 | 2.6155 | 2.6155 | 1.0031 | 1.0031 | 1.0031 | 1.0031 | 1.0031 | 1.0031 | 2.3816 | 3.4353 | 4.1258 | 4.4891 | 5.2159 | 5.9426 | 0.9069 | 2.4635 | 3.0898 | 3.0898 | 3.0898 | 3.0898 | 2.191 | 2.781 | 2.781 | 2.781 | 2.781 | 2.781
2020-06-04 17:00 | Winter | 1.0656 | 1.6384 | 2.4793 | 2.4793 | 2.4793 | 2.4793 | 0.87451 | 0.87451 | 0.87451 | 0.87451 | 0.87451 | 0.87451 | 2.4768 | 3.5728 | 4.2908 | 4.6687 | 5.4245 | 6.1803 | 0.85355 | 2.3186 | 2.9081 | 2.9081 | 2.9081 | 2.9081 | 2.2482 | 2.8536 | 2.8536 | 2.8536 | 2.8536 | 2.8536
2020-06-04 18:00 | Winter | 0.89618 | 1.378 | 2.0852 | 2.0852 | 2.0852 | 2.0852 | 0.77162 | 0.77162 | 0.77162 | 0.77162 | 0.77162 | 0.77162 | 2.4578 | 3.5453 | 4.2578 | 4.6328 | 5.3828 | 6.1328 | 0.79258 | 2.153 | 2.7003 | 2.7003 | 2.7003 | 2.7003 | 1.6587 | 2.1053 | 2.1053 | 2.1053 | 2.1053 | 2.1053
2020-06-04 19:00 | Winter | 0.64779 | 0.99605 | 1.5072 | 1.5072 | 1.5072 | 1.5072 | 0.6173 | 0.6173 | 0.6173 | 0.6173 | 0.6173 | 0.6173 | 2.3625 | 3.4079 | 4.0927 | 4.4532 | 5.1741 | 5.8951 | 0.73924 | 2.0081 | 2.5186 | 2.5186 | 2.5186 | 2.5186 | 1.1622 | 1.4752 | 1.4752 | 1.4752 | 1.4752 | 1.4752
2020-06-04 20:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.50584 | 0.50584 | 0.50584 | 0.50584 | 0.50584 | 0.50584 | 2.2673 | 3.2705 | 3.9277 | 4.2736 | 4.9655 | 5.6574 | 0.73543 | 1.9977 | 2.5056 | 2.5056 | 2.5056 | 2.5056 | 1.0629 | 1.3491 | 1.3491 | 1.3491 | 1.3491 | 1.3491
2020-06-04 21:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.50298 | 0.50298 | 0.50298 | 0.50298 | 0.50298 | 0.50298 | 2.172 | 3.133 | 3.7627 | 4.0941 | 4.7569 | 5.4197 | 0.67827 | 1.8425 | 2.3109 | 2.3109 | 2.3109 | 2.3109 | 0.99073 | 1.2575 | 1.2575 | 1.2575 | 1.2575 | 1.2575
2020-06-04 22:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.49727 | 0.49727 | 0.49727 | 0.49727 | 0.49727 | 0.49727 | 1.9624 | 2.8307 | 3.3996 | 3.699 | 4.2979 | 4.8967 | 0.67065 | 1.8218 | 2.2849 | 2.2849 | 2.2849 | 2.2849 | 0.89466 | 1.1356 | 1.1356 | 1.1356 | 1.1356 | 1.1356
2020-06-04 23:00 | Winter | 0.55013 | 0.84589 | 1.28 | 1.28 | 1.28 | 1.28 | 0.45768 | 0.45768 | 0.45768 | 0.45768 | 0.45768 | 0.45768 | 1.8101 | 2.6111 | 3.1358 | 3.412 | 3.9644 | 4.5167 | 0.60587 | 1.6458 | 2.0642 | 2.0642 | 2.0642 | 2.0642 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-06-05 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 1.7338 | 2.5009 | 3.0036 | 3.2681 | 3.7972 | 4.3262 | 0.57157 | 1.5526 | 1.9474 | 1.9474 | 1.9474 | 1.9474 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-06-05 01:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 1.6206 | 2.3377 | 2.8075 | 3.0547 | 3.5492 | 4.0438 | 0.57157 | 1.5526 | 1.9474 | 1.9474 | 1.9474 | 1.9474 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-06-05 02:00 | Winter | 0.55247 | 0.84949 | 1.2854 | 1.2854 | 1.2854 | 1.2854 | 0.49441 | 0.49441 | 0.49441 | 0.49441 | 0.49441 | 0.49441 | 1.5814 | 2.2811 | 2.7395 | 2.9808 | 3.4633 | 3.9459 | 0.56014 | 1.5216 | 1.9084 | 1.9084 | 1.9084 | 1.9084 | 1.086 | 1.3784 | 1.3784 | 1.3784 | 1.3784 | 1.3784
2020-06-05 03:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 1.6004 | 2.3086 | 2.7725 | 3.0167 | 3.5051 | 3.9934 | 0.59063 | 1.6044 | 2.0123 | 2.0123 | 2.0123 | 2.0123 | 1.0669 | 1.3542 | 1.3542 | 1.3542 | 1.3542 | 1.3542
2020-06-05 04:00 | Winter | 0.56981 | 0.87615 | 1.3258 | 1.3258 | 1.3258 | 1.3258 | 0.51727 | 0.51727 | 0.51727 | 0.51727 | 0.51727 | 0.51727 | 1.6576 | 2.391 | 2.8715 | 3.1244 | 3.6302 | 4.1361 | 0.56776 | 1.5423 | 1.9344 | 1.9344 | 1.9344 | 1.9344 | 1.1248 | 1.4277 | 1.4277 | 1.4277 | 1.4277 | 1.4277
2020-06-05 05:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.73447 | 0.73447 | 0.73447 | 0.73447 | 0.73447 | 0.73447 | 1.7909 | 2.5834 | 3.1026 | 3.3758 | 3.9223 | 4.4688 | 0.60587 | 1.6458 | 2.0642 | 2.0642 | 2.0642 | 2.0642 | 1.4754 | 1.8727 | 1.8727 | 1.8727 | 1.8727 | 1.8727
2020-06-05 06:00 | Winter | 0.64779 | 0.99605 | 1.5072 | 1.5072 | 1.5072 | 1.5072 | 0.81449 | 0.81449 | 0.81449 | 0.81449 | 0.81449 | 0.81449 | 2.0386 | 2.9407 | 3.5316 | 3.8427 | 4.4648 | 5.0869 | 0.6897 | 1.8735 | 2.3498 | 2.3498 | 2.3498 | 2.3498 | 1.8357 | 2.33 | 2.33 | 2.33 | 2.33 | 2.33
2020-06-05 07:00 | Winter | 1.1133 | 1.7118 | 2.5903 | 2.5903 | 2.5903 | 2.5903 | 0.90302 | 0.90302 | 0.90302 | 0.90302 | 0.90302 | 0.90302 | 2.3816 | 3.4353 | 4.1258 | 4.4891 | 5.2159 | 5.9426 | 0.75067 | 2.0391 | 2.5575 | 2.5575 | 2.5575 | 2.5575 | 2.3054 | 2.9261 | 2.9261 | 2.9261 | 2.9261 | 2.9261
2020-06-05 08:00 | Winter | 1.2765 | 1.9628 | 2.9701 | 2.9701 | 2.9701 | 2.9701 | 0.97739 | 0.97739 | 0.97739 | 0.97739 | 0.97739 | 0.97739 | 2.5911 | 3.7377 | 4.4888 | 4.8842 | 5.6749 | 6.4656 | 0.86117 | 2.3393 | 2.934 | 2.934 | 2.934 | 2.934 | 2.5451 | 3.2305 | 3.2305 | 3.2305 | 3.2305 | 3.2305
2020-06-05 09:00 | Winter | 1.2956 | 1.9921 | 3.0144 | 3.0144 | 3.0144 | 3.0144 | 1.0203 | 1.0203 | 1.0203 | 1.0203 | 1.0203 | 1.0203 | 2.5149 | 3.6277 | 4.3568 | 4.7405 | 5.508 | 6.2754 | 0.82688 | 2.2461 | 2.8172 | 2.8172 | 2.8172 | 2.8172 | 2.5911 | 3.2889 | 3.2889 | 3.2889 | 3.2889 | 3.2889
2020-06-05 10:00 | Winter | 1.1432 | 1.7577 | 2.6598 | 2.6598 | 2.6598 | 2.6598 | 1.0231 | 1.0231 | 1.0231 | 1.0231 | 1.0231 | 1.0231 | 2.5149 | 3.6277 | 4.3568 | 4.7405 | 5.508 | 6.2754 | 0.77734 | 2.1116 | 2.6484 | 2.6484 | 2.6484 | 2.6484 | 2.553 | 3.2405 | 3.2405 | 3.2405 | 3.2405 | 3.2405
2020-06-05 11:00 | Winter | 1.1432 | 1.7577 | 2.6598 | 2.6598 | 2.6598 | 2.6598 | 1.0488 | 1.0488 | 1.0488 | 1.0488 | 1.0488 | 1.0488 | 2.4959 | 3.6002 | 4.3238 | 4.7046 | 5.4662 | 6.2279 | 0.78612 | 2.1354 | 2.6783 | 2.6783 | 2.6783 | 2.6783 | 2.5902 | 3.2876 | 3.2876 | 3.2876 | 3.2876 | 3.2876
2020-06-05 12:00 | Winter | 1.105 | 1.6991 | 2.5711 | 2.5711 | 2.5711 | 2.5711 | 0.90023 | 0.90023 | 0.90023 | 0.90023 | 0.90023 | 0.90023 | 2.3816 | 3.4353 | 4.1258 | 4.4891 | 5.2159 | 5.9426 | 0.81164 | 2.2047 | 2.7653 | 2.7653 | 2.7653 | 2.7653 | 2.5911 | 3.2889 | 3.2889 | 3.2889 | 3.2889 | 3.2889
2020-06-05 13:00 | Winter | 1.13 | 1.7375 | 2.6291 | 2.6291 | 2.6291 | 2.6291 | 0.90023 | 0.90023 | 0.90023 | 0.90023 | 0.90023 | 0.90023 | 2.4959 | 3.6002 | 4.3238 | 4.7046 | 5.4662 | 6.2279 | 0.83831 | 2.2772 | 2.8561 | 2.8561 | 2.8561 | 2.8561 | 2.4578 | 3.1196 | 3.1196 | 3.1196 | 3.1196 | 3.1196
2020-06-05 14:00 | Winter | 1.1432 | 1.7577 | 2.6598 | 2.6598 | 2.6598 | 2.6598 | 0.93452 | 0.93452 | 0.93452 | 0.93452 | 0.93452 | 0.93452 | 2.4959 | 3.6002 | 4.3238 | 4.7046 | 5.4662 | 6.2279 | 0.80402 | 2.184 | 2.7393 | 2.7393 | 2.7393 | 2.7393 | 2.3625 | 2.9987 | 2.9987 | 2.9987 | 2.9987 | 2.9987
2020-06-05 15:00 | Winter | 1.086 | 1.6698 | 2.5268 | 2.5268 | 2.5268 | 2.5268 | 0.9431 | 0.9431 | 0.9431 | 0.9431 | 0.9431 | 0.9431 | 2.3625 | 3.4079 | 4.0927 | 4.4532 | 5.1741 | 5.8951 | 0.82307 | 2.2358 | 2.8042 | 2.8042 | 2.8042 | 2.8042 | 2.2673 | 2.8778 | 2.8778 | 2.8778 | 2.8778 | 2.8778
2020-06-05 16:00 | Winter | 1.0669 | 1.6405 | 2.4825 | 2.4825 | 2.4825 | 2.4825 | 0.88022 | 0.88022 | 0.88022 | 0.88022 | 0.88022 | 0.88022 | 2.4197 | 3.4903 | 4.1918 | 4.561 | 5.2993 | 6.0377 | 0.86117 | 2.3393 | 2.934 | 2.934 | 2.934 | 2.934 | 2.2482 | 2.8536 | 2.8536 | 2.8536 | 2.8536 | 2.8536
2020-06-05 17:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 0.84307 | 0.84307 | 0.84307 | 0.84307 | 0.84307 | 0.84307 | 2.4768 | 3.5728 | 4.2908 | 4.6687 | 5.4245 | 6.1803 | 0.82307 | 2.2358 | 2.8042 | 2.8042 | 2.8042 | 2.8042 | 2.1339 | 2.7085 | 2.7085 | 2.7085 | 2.7085 | 2.7085
2020-06-05 18:00 | Winter | 0.95302 | 1.4654 | 2.2174 | 2.2174 | 2.2174 | 2.2174 | 0.74019 | 0.74019 | 0.74019 | 0.74019 | 0.74019 | 0.74019 | 2.4011 | 3.4635 | 4.1595 | 4.5259 | 5.2586 | 5.9913 | 0.80402 | 2.184 | 2.7393 | 2.7393 | 2.7393 | 2.7393 | 1.6226 | 2.0595 | 2.0595 | 2.0595 | 2.0595 | 2.0595
2020-06-05 19:00 | Winter | 0.66684 | 1.0253 | 1.5515 | 1.5515 | 1.5515 | 1.5515 | 0.6373 | 0.6373 | 0.6373 | 0.6373 | 0.6373 | 0.6373 | 2.3244 | 3.3529 | 4.0267 | 4.3814 | 5.0907 | 5.8 | 0.78877 | 2.1426 | 2.6874 | 2.6874 | 2.6874 | 2.6874 | 1.2003 | 1.5235 | 1.5235 | 1.5235 | 1.5235 | 1.5235
2020-06-05 20:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.61444 | 0.61444 | 0.61444 | 0.61444 | 0.61444 | 0.61444 | 2.2482 | 3.243 | 3.8947 | 4.2377 | 4.9238 | 5.6098 | 0.79258 | 2.153 | 2.7003 | 2.7003 | 2.7003 | 2.7003 | 1.1432 | 1.451 | 1.451 | 1.451 | 1.451 | 1.451
2020-06-05 21:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.53442 | 0.53442 | 0.53442 | 0.53442 | 0.53442 | 0.53442 | 2.0958 | 3.0231 | 3.6307 | 3.9504 | 4.59 | 5.2295 | 0.76591 | 2.0805 | 2.6095 | 2.6095 | 2.6095 | 2.6095 | 1.0363 | 1.3154 | 1.3154 | 1.3154 | 1.3154 | 1.3154
2020-06-05 22:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.56014 | 0.56014 | 0.56014 | 0.56014 | 0.56014 | 0.56014 | 1.9815 | 2.8582 | 3.4326 | 3.735 | 4.3396 | 4.9443 | 0.72018 | 1.9563 | 2.4537 | 2.4537 | 2.4537 | 2.4537 | 0.91452 | 1.1608 | 1.1608 | 1.1608 | 1.1608 | 1.1608
2020-06-05 23:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.47726 | 0.47726 | 0.47726 | 0.47726 | 0.47726 | 0.47726 | 1.9053 | 2.7483 | 3.3006 | 3.5913 | 4.1727 | 4.7541 | 0.67827 | 1.8425 | 2.3109 | 2.3109 | 2.3109 | 2.3109 | 0.93358 | 1.185 | 1.185 | 1.185 | 1.185 | 1.185
2020-06-06 | Winter | 0.58696 | 0.90251 | 1.3657 | 1.3657 | 1.3657 | 1.3657 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 1.81 | 2.6109 | 3.1356 | 3.4117 | 3.9641 | 4.5164 | 0.60587 | 1.6458 | 2.0642 | 2.0642 | 2.0642 | 2.0642 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-06-06 01:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 1.6957 | 2.446 | 2.9375 | 3.1963 | 3.7137 | 4.2311 | 0.5792 | 1.5733 | 1.9733 | 1.9733 | 1.9733 | 1.9733 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-06-06 02:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 1.6173 | 2.333 | 2.8018 | 3.0486 | 3.5421 | 4.0357 | 0.5792 | 1.5733 | 1.9733 | 1.9733 | 1.9733 | 1.9733 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-06-06 03:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.46869 | 0.46869 | 0.46869 | 0.46869 | 0.46869 | 0.46869 | 1.6195 | 2.336 | 2.8055 | 3.0526 | 3.5468 | 4.041 | 0.54871 | 1.4905 | 1.8695 | 1.8695 | 1.8695 | 1.8695 | 0.91452 | 1.1608 | 1.1608 | 1.1608 | 1.1608 | 1.1608
2020-06-06 04:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 1.6766 | 2.4185 | 2.9045 | 3.1603 | 3.672 | 4.1836 | 0.54871 | 1.4905 | 1.8695 | 1.8695 | 1.8695 | 1.8695 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-06-06 05:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.49727 | 0.49727 | 0.49727 | 0.49727 | 0.49727 | 0.49727 | 1.7147 | 2.4735 | 2.9705 | 3.2322 | 3.7554 | 4.2787 | 0.56776 | 1.5423 | 1.9344 | 1.9344 | 1.9344 | 1.9344 | 0.91452 | 1.1608 | 1.1608 | 1.1608 | 1.1608 | 1.1608
2020-06-06 06:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.5287 | 0.5287 | 0.5287 | 0.5287 | 0.5287 | 0.5287 | 1.7909 | 2.5834 | 3.1026 | 3.3758 | 3.9223 | 4.4688 | 0.56776 | 1.5423 | 1.9344 | 1.9344 | 1.9344 | 1.9344 | 1.0288 | 1.3059 | 1.3059 | 1.3059 | 1.3059 | 1.3059
2020-06-06 07:00 | Winter | 0.5652 | 0.86906 | 1.3151 | 1.3151 | 1.3151 | 1.3151 | 0.66017 | 0.66017 | 0.66017 | 0.66017 | 0.66017 | 0.66017 | 1.8876 | 2.7228 | 3.27 | 3.558 | 4.134 | 4.7099 | 0.6516 | 1.77 | 2.22 | 2.22 | 2.22 | 2.22 | 1.0669 | 1.3542 | 1.3542 | 1.3542 | 1.3542 | 1.3542
2020-06-06 08:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.69416 | 0.69416 | 0.69416 | 0.69416 | 0.69416 | 0.69416 | 2.1339 | 3.0781 | 3.6967 | 4.0223 | 4.6734 | 5.3246 | 0.68208 | 1.8528 | 2.3239 | 2.3239 | 2.3239 | 2.3239 | 1.086 | 1.3784 | 1.3784 | 1.3784 | 1.3784 | 1.3784
2020-06-06 09:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.69446 | 0.69446 | 0.69446 | 0.69446 | 0.69446 | 0.69446 | 2.1339 | 3.0781 | 3.6967 | 4.0223 | 4.6734 | 5.3246 | 0.71256 | 1.9356 | 2.4277 | 2.4277 | 2.4277 | 2.4277 | 1.1599 | 1.4723 | 1.4723 | 1.4723 | 1.4723 | 1.4723
2020-06-06 10:00 | Winter | 0.57137 | 0.87854 | 1.3294 | 1.3294 | 1.3294 | 1.3294 | 0.64588 | 0.64588 | 0.64588 | 0.64588 | 0.64588 | 0.64588 | 2.191 | 3.1605 | 3.7957 | 4.13 | 4.7986 | 5.4672 | 0.63254 | 1.7182 | 2.1551 | 2.1551 | 2.1551 | 2.1551 | 1.1813 | 1.4993 | 1.4993 | 1.4993 | 1.4993 | 1.4993
2020-06-06 11:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.64874 | 0.64874 | 0.64874 | 0.64874 | 0.64874 | 0.64874 | 2.1893 | 3.158 | 3.7926 | 4.1267 | 4.7947 | 5.4628 | 0.63635 | 1.7286 | 2.1681 | 2.1681 | 2.1681 | 2.1681 | 1.1549 | 1.4659 | 1.4659 | 1.4659 | 1.4659 | 1.4659
2020-06-06 12:00 | Winter | 0.55248 | 0.8495 | 1.2855 | 1.2855 | 1.2855 | 1.2855 | 0.58872 | 0.58872 | 0.58872 | 0.58872 | 0.58872 | 0.58872 | 2.0577 | 2.9681 | 3.5647 | 3.8786 | 4.5065 | 5.1344 | 0.68589 | 1.8632 | 2.3368 | 2.3368 | 2.3368 | 2.3368 | 1.1813 | 1.4993 | 1.4993 | 1.4993 | 1.4993 | 1.4993
2020-06-06 13:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.58872 | 0.58872 | 0.58872 | 0.58872 | 0.58872 | 0.58872 | 2.0767 | 2.9956 | 3.5977 | 3.9145 | 4.5482 | 5.182 | 0.65922 | 1.7907 | 2.246 | 2.246 | 2.246 | 2.246 | 1.1241 | 1.4268 | 1.4268 | 1.4268 | 1.4268 | 1.4268
2020-06-06 14:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.58872 | 0.58872 | 0.58872 | 0.58872 | 0.58872 | 0.58872 | 2.0386 | 2.9407 | 3.5316 | 3.8427 | 4.4648 | 5.0869 | 0.63635 | 1.7286 | 2.1681 | 2.1681 | 2.1681 | 2.1681 | 1.086 | 1.3784 | 1.3784 | 1.3784 | 1.3784 | 1.3784
2020-06-06 15:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.60301 | 0.60301 | 0.60301 | 0.60301 | 0.60301 | 0.60301 | 2.0196 | 2.9132 | 3.4986 | 3.8068 | 4.4231 | 5.0393 | 0.69351 | 1.8839 | 2.3628 | 2.3628 | 2.3628 | 2.3628 | 0.99073 | 1.2575 | 1.2575 | 1.2575 | 1.2575 | 1.2575
2020-06-06 16:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.55728 | 0.55728 | 0.55728 | 0.55728 | 0.55728 | 0.55728 | 2.1141 | 3.0495 | 3.6623 | 3.9849 | 4.63 | 5.2751 | 0.72018 | 1.9563 | 2.4537 | 2.4537 | 2.4537 | 2.4537 | 1.0855 | 1.3778 | 1.3778 | 1.3778 | 1.3778 | 1.3778
2020-06-06 17:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.55443 | 0.55443 | 0.55443 | 0.55443 | 0.55443 | 0.55443 | 2.2482 | 3.243 | 3.8947 | 4.2377 | 4.9238 | 5.6098 | 0.7621 | 2.0702 | 2.5965 | 2.5965 | 2.5965 | 2.5965 | 1.105 | 1.4026 | 1.4026 | 1.4026 | 1.4026 | 1.4026
2020-06-06 18:00 | Winter | 0.55273 | 0.84988 | 1.286 | 1.286 | 1.286 | 1.286 | 0.58872 | 0.58872 | 0.58872 | 0.58872 | 0.58872 | 0.58872 | 2.2482 | 3.243 | 3.8947 | 4.2377 | 4.9238 | 5.6098 | 0.85355 | 2.3186 | 2.9081 | 2.9081 | 2.9081 | 2.9081 | 1.0486 | 1.331 | 1.331 | 1.331 | 1.331 | 1.331
2020-06-06 19:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.65731 | 0.65731 | 0.65731 | 0.65731 | 0.65731 | 0.65731 | 2.1529 | 3.1056 | 3.7297 | 4.0582 | 4.7151 | 5.3721 | 0.81926 | 2.2254 | 2.7912 | 2.7912 | 2.7912 | 2.7912 | 1.0103 | 1.2823 | 1.2823 | 1.2823 | 1.2823 | 1.2823
2020-06-06 20:00 | Winter | 0.55248 | 0.84951 | 1.2855 | 1.2855 | 1.2855 | 1.2855 | 0.56586 | 0.56586 | 0.56586 | 0.56586 | 0.56586 | 0.56586 | 2.1339 | 3.0781 | 3.6967 | 4.0223 | 4.6734 | 5.3246 | 0.81545 | 2.2151 | 2.7782 | 2.7782 | 2.7782 | 2.7782 | 0.99073 | 1.2575 | 1.2575 | 1.2575 | 1.2575 | 1.2575
2020-06-06 21:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.57157 | 0.57157 | 0.57157 | 0.57157 | 0.57157 | 0.57157 | 2.0386 | 2.9407 | 3.5316 | 3.8427 | 4.4648 | 5.0869 | 0.7621 | 2.0702 | 2.5965 | 2.5965 | 2.5965 | 2.5965 | 0.91452 | 1.1608 | 1.1608 | 1.1608 | 1.1608 | 1.1608
2020-06-06 22:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.53156 | 0.53156 | 0.53156 | 0.53156 | 0.53156 | 0.53156 | 2.0386 | 2.9407 | 3.5316 | 3.8427 | 4.4648 | 5.0869 | 0.74686 | 2.0288 | 2.5446 | 2.5446 | 2.5446 | 2.5446 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-06-06 23:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.51442 | 0.51442 | 0.51442 | 0.51442 | 0.51442 | 0.51442 | 1.829 | 2.6383 | 3.1686 | 3.4477 | 4.0058 | 4.5639 | 0.65541 | 1.7803 | 2.233 | 2.233 | 2.233 | 2.233 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-06-07 | Winter | 0.55438 | 0.85242 | 1.2899 | 1.2899 | 1.2899 | 1.2899 | 0.50013 | 0.50013 | 0.50013 | 0.50013 | 0.50013 | 0.50013 | 1.7338 | 2.5009 | 3.0036 | 3.2681 | 3.7972 | 4.3262 | 0.6516 | 1.77 | 2.22 | 2.22 | 2.22 | 2.22 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-06-07 01:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.48584 | 0.48584 | 0.48584 | 0.48584 | 0.48584 | 0.48584 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.60587 | 1.6458 | 2.0642 | 2.0642 | 2.0642 | 2.0642 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-06-07 02:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.49441 | 0.49441 | 0.49441 | 0.49441 | 0.49441 | 0.49441 | 1.6004 | 2.3086 | 2.7725 | 3.0167 | 3.5051 | 3.9934 | 0.56395 | 1.5319 | 1.9214 | 1.9214 | 1.9214 | 1.9214 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-06-07 03:00 | Winter | 0.5588 | 0.85922 | 1.3002 | 1.3002 | 1.3002 | 1.3002 | 0.47441 | 0.47441 | 0.47441 | 0.47441 | 0.47441 | 0.47441 | 1.5623 | 2.2536 | 2.7065 | 2.9449 | 3.4216 | 3.8984 | 0.56379 | 1.5315 | 1.9208 | 1.9208 | 1.9208 | 1.9208 | 0.85389 | 1.0838 | 1.0838 | 1.0838 | 1.0838 | 1.0838
2020-06-07 04:00 | Winter | 0.57156 | 0.87884 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.47441 | 0.47441 | 0.47441 | 0.47441 | 0.47441 | 0.47441 | 1.6766 | 2.4185 | 2.9045 | 3.1603 | 3.672 | 4.1836 | 0.56776 | 1.5423 | 1.9344 | 1.9344 | 1.9344 | 1.9344 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-06-07 05:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.52013 | 0.52013 | 0.52013 | 0.52013 | 0.52013 | 0.52013 | 1.658 | 2.3916 | 2.8722 | 3.1252 | 3.6312 | 4.1371 | 0.52585 | 1.4284 | 1.7916 | 1.7916 | 1.7916 | 1.7916 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-06-07 06:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.52585 | 0.52585 | 0.52585 | 0.52585 | 0.52585 | 0.52585 | 1.7719 | 2.5559 | 3.0696 | 3.3399 | 3.8806 | 4.4213 | 0.60587 | 1.6458 | 2.0642 | 2.0642 | 2.0642 | 2.0642 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-06-07 07:00 | Winter | 0.56963 | 0.87587 | 1.3254 | 1.3254 | 1.3254 | 1.3254 | 0.61444 | 0.61444 | 0.61444 | 0.61444 | 0.61444 | 0.61444 | 1.829 | 2.6383 | 3.1686 | 3.4477 | 4.0058 | 4.5639 | 0.64397 | 1.7493 | 2.194 | 2.194 | 2.194 | 2.194 | 0.91452 | 1.1608 | 1.1608 | 1.1608 | 1.1608 | 1.1608
2020-06-07 08:00 | Winter | 0.53432 | 0.82158 | 1.2432 | 1.2432 | 1.2432 | 1.2432 | 0.68303 | 0.68303 | 0.68303 | 0.68303 | 0.68303 | 0.68303 | 2.1148 | 3.0506 | 3.6637 | 3.9863 | 4.6317 | 5.277 | 0.6897 | 1.8735 | 2.3498 | 2.3498 | 2.3498 | 2.3498 | 0.91452 | 1.1608 | 1.1608 | 1.1608 | 1.1608 | 1.1608
2020-06-07 09:00 | Winter | 0.55243 | 0.84943 | 1.2854 | 1.2854 | 1.2854 | 1.2854 | 0.64016 | 0.64016 | 0.64016 | 0.64016 | 0.64016 | 0.64016 | 2.0386 | 2.9407 | 3.5316 | 3.8427 | 4.4648 | 5.0869 | 0.75067 | 2.0391 | 2.5575 | 2.5575 | 2.5575 | 2.5575 | 0.93358 | 1.185 | 1.185 | 1.185 | 1.185 | 1.185
2020-06-07 10:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.62301 | 0.62301 | 0.62301 | 0.62301 | 0.62301 | 0.62301 | 2.172 | 3.133 | 3.7627 | 4.0941 | 4.7569 | 5.4197 | 0.72018 | 1.9563 | 2.4537 | 2.4537 | 2.4537 | 2.4537 | 0.95263 | 1.2092 | 1.2092 | 1.2092 | 1.2092 | 1.2092
2020-06-07 11:00 | Winter | 0.53347 | 0.82027 | 1.2412 | 1.2412 | 1.2412 | 1.2412 | 0.59444 | 0.59444 | 0.59444 | 0.59444 | 0.59444 | 0.59444 | 2.1148 | 3.0506 | 3.6637 | 3.9863 | 4.6317 | 5.277 | 0.68589 | 1.8632 | 2.3368 | 2.3368 | 2.3368 | 2.3368 | 0.99073 | 1.2575 | 1.2575 | 1.2575 | 1.2575 | 1.2575
2020-06-07 12:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.6173 | 0.6173 | 0.6173 | 0.6173 | 0.6173 | 0.6173 | 2.0958 | 3.0231 | 3.6307 | 3.9504 | 4.59 | 5.2295 | 0.6516 | 1.77 | 2.22 | 2.22 | 2.22 | 2.22 | 1.0479 | 1.3301 | 1.3301 | 1.3301 | 1.3301 | 1.3301
2020-06-07 13:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.60015 | 0.60015 | 0.60015 | 0.60015 | 0.60015 | 0.60015 | 2.1148 | 3.0506 | 3.6637 | 3.9863 | 4.6317 | 5.277 | 0.64204 | 1.744 | 2.1874 | 2.1874 | 2.1874 | 2.1874 | 1.0098 | 1.2817 | 1.2817 | 1.2817 | 1.2817 | 1.2817
2020-06-07 14:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.62016 | 0.62016 | 0.62016 | 0.62016 | 0.62016 | 0.62016 | 2.0958 | 3.0231 | 3.6307 | 3.9504 | 4.59 | 5.2295 | 0.60968 | 1.6561 | 2.0772 | 2.0772 | 2.0772 | 2.0772 | 0.93358 | 1.185 | 1.185 | 1.185 | 1.185 | 1.185
2020-06-07 15:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.51442 | 0.51442 | 0.51442 | 0.51442 | 0.51442 | 0.51442 | 2.0005 | 2.8857 | 3.4656 | 3.7709 | 4.3813 | 4.9918 | 0.62492 | 1.6975 | 2.1291 | 2.1291 | 2.1291 | 2.1291 | 0.95263 | 1.2092 | 1.2092 | 1.2092 | 1.2092 | 1.2092
2020-06-07 16:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.55728 | 0.55728 | 0.55728 | 0.55728 | 0.55728 | 0.55728 | 2.2482 | 3.243 | 3.8947 | 4.2377 | 4.9238 | 5.6098 | 0.67446 | 1.8321 | 2.2979 | 2.2979 | 2.2979 | 2.2979 | 0.93444 | 1.1861 | 1.1861 | 1.1861 | 1.1861 | 1.1861
2020-06-07 17:00 | Winter | 0.56097 | 0.86256 | 1.3052 | 1.3052 | 1.3052 | 1.3052 | 0.63159 | 0.63159 | 0.63159 | 0.63159 | 0.63159 | 0.63159 | 2.4387 | 3.5178 | 4.2248 | 4.5969 | 5.3411 | 6.0852 | 0.77619 | 2.1084 | 2.6445 | 2.6445 | 2.6445 | 2.6445 | 0.95263 | 1.2092 | 1.2092 | 1.2092 | 1.2092 | 1.2092
2020-06-07 18:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.66017 | 0.66017 | 0.66017 | 0.66017 | 0.66017 | 0.66017 | 2.3521 | 3.3928 | 4.0747 | 4.4336 | 5.1513 | 5.8691 | 0.78115 | 2.1219 | 2.6614 | 2.6614 | 2.6614 | 2.6614 | 0.93358 | 1.185 | 1.185 | 1.185 | 1.185 | 1.185
2020-06-07 19:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.60301 | 0.60301 | 0.60301 | 0.60301 | 0.60301 | 0.60301 | 2.2482 | 3.243 | 3.8947 | 4.2377 | 4.9238 | 5.6098 | 0.72781 | 1.977 | 2.4796 | 2.4796 | 2.4796 | 2.4796 | 0.95263 | 1.2092 | 1.2092 | 1.2092 | 1.2092 | 1.2092
2020-06-07 20:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.54299 | 0.54299 | 0.54299 | 0.54299 | 0.54299 | 0.54299 | 2.2079 | 3.1848 | 3.8248 | 4.1617 | 4.8354 | 5.5092 | 0.7621 | 2.0702 | 2.5965 | 2.5965 | 2.5965 | 2.5965 | 0.93358 | 1.185 | 1.185 | 1.185 | 1.185 | 1.185
2020-06-07 21:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.54299 | 0.54299 | 0.54299 | 0.54299 | 0.54299 | 0.54299 | 2.1529 | 3.1056 | 3.7297 | 4.0582 | 4.7151 | 5.3721 | 0.76591 | 2.0805 | 2.6095 | 2.6095 | 2.6095 | 2.6095 | 0.88237 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12
2020-06-07 22:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.46869 | 0.46869 | 0.46869 | 0.46869 | 0.46869 | 0.46869 | 2.0577 | 2.9681 | 3.5647 | 3.8786 | 4.5065 | 5.1344 | 0.73543 | 1.9977 | 2.5056 | 2.5056 | 2.5056 | 2.5056 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-06-07 23:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 1.8423 | 2.6574 | 3.1915 | 3.4725 | 4.0347 | 4.5969 | 0.66303 | 1.8011 | 2.2589 | 2.2589 | 2.2589 | 2.2589 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-06-08 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 1.7147 | 2.4735 | 2.9705 | 3.2322 | 3.7554 | 4.2787 | 0.5792 | 1.5733 | 1.9733 | 1.9733 | 1.9733 | 1.9733 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-06-08 01:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.56395 | 1.5319 | 1.9214 | 1.9214 | 1.9214 | 1.9214 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-06-08 02:00 | Winter | 0.53373 | 0.82068 | 1.2418 | 1.2418 | 1.2418 | 1.2418 | 0.48869 | 0.48869 | 0.48869 | 0.48869 | 0.48869 | 0.48869 | 1.611 | 2.3239 | 2.7909 | 3.0367 | 3.5283 | 4.0199 | 0.56776 | 1.5423 | 1.9344 | 1.9344 | 1.9344 | 1.9344 | 1.0667 | 1.354 | 1.354 | 1.354 | 1.354 | 1.354
2020-06-08 03:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.58682 | 1.594 | 1.9993 | 1.9993 | 1.9993 | 1.9993 | 1.105 | 1.4026 | 1.4026 | 1.4026 | 1.4026 | 1.4026
2020-06-08 04:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.46565 | 0.46565 | 0.46565 | 0.46565 | 0.46565 | 0.46565 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.51815 | 1.4075 | 1.7654 | 1.7654 | 1.7654 | 1.7654 | 1.1432 | 1.451 | 1.451 | 1.451 | 1.451 | 1.451
2020-06-08 05:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.54585 | 0.54585 | 0.54585 | 0.54585 | 0.54585 | 0.54585 | 1.6663 | 2.4036 | 2.8867 | 3.1409 | 3.6494 | 4.1579 | 0.59063 | 1.6044 | 2.0123 | 2.0123 | 2.0123 | 2.0123 | 1.4522 | 1.8432 | 1.8432 | 1.8432 | 1.8432 | 1.8432
2020-06-08 06:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.54871 | 0.54871 | 0.54871 | 0.54871 | 0.54871 | 0.54871 | 1.7712 | 2.5549 | 3.0684 | 3.3386 | 3.8791 | 4.4196 | 0.6516 | 1.77 | 2.22 | 2.22 | 2.22 | 2.22 | 1.5623 | 1.983 | 1.983 | 1.983 | 1.983 | 1.983
2020-06-08 07:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.563 | 0.563 | 0.563 | 0.563 | 0.563 | 0.563 | 2.0005 | 2.8857 | 3.4656 | 3.7709 | 4.3813 | 4.9918 | 0.6516 | 1.77 | 2.22 | 2.22 | 2.22 | 2.22 | 1.81 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974
2020-06-08 08:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.64874 | 0.64874 | 0.64874 | 0.64874 | 0.64874 | 0.64874 | 2.0958 | 3.0231 | 3.6307 | 3.9504 | 4.59 | 5.2295 | 0.73162 | 1.9874 | 2.4926 | 2.4926 | 2.4926 | 2.4926 | 1.8481 | 2.3458 | 2.3458 | 2.3458 | 2.3458 | 2.3458
2020-06-08 09:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.57443 | 0.57443 | 0.57443 | 0.57443 | 0.57443 | 0.57443 | 2.1057 | 3.0373 | 3.6478 | 3.969 | 4.6116 | 5.2541 | 0.72018 | 1.9563 | 2.4537 | 2.4537 | 2.4537 | 2.4537 | 1.8481 | 2.3458 | 2.3458 | 2.3458 | 2.3458 | 2.3458
2020-06-08 10:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.53728 | 0.53728 | 0.53728 | 0.53728 | 0.53728 | 0.53728 | 2.2291 | 3.2155 | 3.8617 | 4.2018 | 4.8821 | 5.5623 | 0.67065 | 1.8218 | 2.2849 | 2.2849 | 2.2849 | 2.2849 | 1.7719 | 2.249 | 2.249 | 2.249 | 2.249 | 2.249
2020-06-08 11:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.52585 | 0.52585 | 0.52585 | 0.52585 | 0.52585 | 0.52585 | 2.1148 | 3.0506 | 3.6637 | 3.9863 | 4.6317 | 5.277 | 0.63779 | 1.7325 | 2.173 | 2.173 | 2.173 | 2.173 | 1.7909 | 2.2732 | 2.2732 | 2.2732 | 2.2732 | 2.2732
2020-06-08 12:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 2.1339 | 3.0781 | 3.6967 | 4.0223 | 4.6734 | 5.3246 | 0.73924 | 2.0081 | 2.5186 | 2.5186 | 2.5186 | 2.5186 | 1.7909 | 2.2732 | 2.2732 | 2.2732 | 2.2732 | 2.2732
2020-06-08 13:00 | Winter | 0.60939 | 0.93701 | 1.4179 | 1.4179 | 1.4179 | 1.4179 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 2.1529 | 3.1056 | 3.7297 | 4.0582 | 4.7151 | 5.3721 | 0.58301 | 1.5837 | 1.9863 | 1.9863 | 1.9863 | 1.9863 | 1.7719 | 2.249 | 2.249 | 2.249 | 2.249 | 2.249
2020-06-08 14:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 2.0577 | 2.9681 | 3.5647 | 3.8786 | 4.5065 | 5.1344 | 0.67065 | 1.8218 | 2.2849 | 2.2849 | 2.2849 | 2.2849 | 1.6766 | 2.1281 | 2.1281 | 2.1281 | 2.1281 | 2.1281
2020-06-08 15:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.50584 | 0.50584 | 0.50584 | 0.50584 | 0.50584 | 0.50584 | 2.0196 | 2.9132 | 3.4986 | 3.8068 | 4.4231 | 5.0393 | 0.65922 | 1.7907 | 2.246 | 2.246 | 2.246 | 2.246 | 1.6004 | 2.0314 | 2.0314 | 2.0314 | 2.0314 | 2.0314
2020-06-08 16:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.50013 | 0.50013 | 0.50013 | 0.50013 | 0.50013 | 0.50013 | 2.2101 | 3.188 | 3.8287 | 4.1659 | 4.8403 | 5.5147 | 0.67827 | 1.8425 | 2.3109 | 2.3109 | 2.3109 | 2.3109 | 1.7147 | 2.1765 | 2.1765 | 2.1765 | 2.1765 | 2.1765
2020-06-08 17:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.5287 | 0.5287 | 0.5287 | 0.5287 | 0.5287 | 0.5287 | 2.3054 | 3.3254 | 3.9937 | 4.3455 | 5.049 | 5.7525 | 0.69351 | 1.8839 | 2.3628 | 2.3628 | 2.3628 | 2.3628 | 1.6195 | 2.0556 | 2.0556 | 2.0556 | 2.0556 | 2.0556
2020-06-08 18:00 | Winter | 0.57258 | 0.88041 | 1.3322 | 1.3322 | 1.3322 | 1.3322 | 0.46869 | 0.46869 | 0.46869 | 0.46869 | 0.46869 | 0.46869 | 2.3054 | 3.3254 | 3.9937 | 4.3455 | 5.049 | 5.7525 | 0.73162 | 1.9874 | 2.4926 | 2.4926 | 2.4926 | 2.4926 | 1.1972 | 1.5196 | 1.5196 | 1.5196 | 1.5196 | 1.5196
2020-06-08 19:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 2.172 | 3.133 | 3.7627 | 4.0941 | 4.7569 | 5.4197 | 0.73924 | 2.0081 | 2.5186 | 2.5186 | 2.5186 | 2.5186 | 0.97168 | 1.2333 | 1.2333 | 1.2333 | 1.2333 | 1.2333
2020-06-08 20:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 2.191 | 3.1605 | 3.7957 | 4.13 | 4.7986 | 5.4672 | 0.69732 | 1.8942 | 2.3758 | 2.3758 | 2.3758 | 2.3758 | 0.91452 | 1.1608 | 1.1608 | 1.1608 | 1.1608 | 1.1608
2020-06-08 21:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 2.0767 | 2.9956 | 3.5977 | 3.9145 | 4.5482 | 5.182 | 0.70875 | 1.9253 | 2.4147 | 2.4147 | 2.4147 | 2.4147 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-06-08 22:00 | Winter | 0.55243 | 0.84943 | 1.2854 | 1.2854 | 1.2854 | 1.2854 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 1.9624 | 2.8307 | 3.3996 | 3.699 | 4.2979 | 4.8967 | 0.62979 | 1.7108 | 2.1457 | 2.1457 | 2.1457 | 2.1457 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-06-08 23:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 1.8161 | 2.6197 | 3.1462 | 3.4233 | 3.9774 | 4.5316 | 0.5792 | 1.5733 | 1.9733 | 1.9733 | 1.9733 | 1.9733 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-06-09 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.41675 | 0.41675 | 0.41675 | 0.41675 | 0.41675 | 0.41675 | 1.7338 | 2.5009 | 3.0036 | 3.2681 | 3.7972 | 4.3262 | 0.56395 | 1.5319 | 1.9214 | 1.9214 | 1.9214 | 1.9214 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-06-09 01:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 1.6982 | 2.4496 | 2.942 | 3.2011 | 3.7193 | 4.2375 | 0.56014 | 1.5216 | 1.9084 | 1.9084 | 1.9084 | 1.9084 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-06-09 02:00 | Winter | 0.53347 | 0.82027 | 1.2412 | 1.2412 | 1.2412 | 1.2412 | 0.46869 | 0.46869 | 0.46869 | 0.46869 | 0.46869 | 0.46869 | 1.6004 | 2.3086 | 2.7725 | 3.0167 | 3.5051 | 3.9934 | 0.51442 | 1.3974 | 1.7526 | 1.7526 | 1.7526 | 1.7526 | 1.086 | 1.3784 | 1.3784 | 1.3784 | 1.3784 | 1.3784
2020-06-09 03:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.46869 | 0.46869 | 0.46869 | 0.46869 | 0.46869 | 0.46869 | 1.5433 | 2.2261 | 2.6735 | 2.909 | 3.3799 | 3.8508 | 0.52966 | 1.4388 | 1.8046 | 1.8046 | 1.8046 | 1.8046 | 1.086 | 1.3784 | 1.3784 | 1.3784 | 1.3784 | 1.3784
2020-06-09 04:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.5051 | 0.5051 | 0.5051 | 0.5051 | 0.5051 | 0.5051 | 1.661 | 2.396 | 2.8775 | 3.1309 | 3.6378 | 4.1447 | 0.53347 | 1.4491 | 1.8175 | 1.8175 | 1.8175 | 1.8175 | 1.1044 | 1.4018 | 1.4018 | 1.4018 | 1.4018 | 1.4018
2020-06-09 05:00 | Winter | 0.78115 | 1.2011 | 1.8175 | 1.8175 | 1.8175 | 1.8175 | 0.70018 | 0.70018 | 0.70018 | 0.70018 | 0.70018 | 0.70018 | 1.8657 | 2.6912 | 3.232 | 3.5167 | 4.086 | 4.6553 | 0.67827 | 1.8425 | 2.3109 | 2.3109 | 2.3109 | 2.3109 | 1.4739 | 1.8708 | 1.8708 | 1.8708 | 1.8708 | 1.8708
2020-06-09 06:00 | Winter | 0.93358 | 1.4355 | 2.1722 | 2.1722 | 2.1722 | 2.1722 | 0.77162 | 0.77162 | 0.77162 | 0.77162 | 0.77162 | 0.77162 | 2.1671 | 3.1259 | 3.7542 | 4.0848 | 4.7461 | 5.4074 | 0.73543 | 1.9977 | 2.5056 | 2.5056 | 2.5056 | 2.5056 | 1.9164 | 2.4324 | 2.4324 | 2.4324 | 2.4324 | 2.4324
2020-06-09 07:00 | Winter | 1.105 | 1.6991 | 2.5711 | 2.5711 | 2.5711 | 2.5711 | 0.90595 | 0.90595 | 0.90595 | 0.90595 | 0.90595 | 0.90595 | 2.4387 | 3.5178 | 4.2248 | 4.5969 | 5.3411 | 6.0852 | 0.82688 | 2.2461 | 2.8172 | 2.8172 | 2.8172 | 2.8172 | 2.3466 | 2.9785 | 2.9785 | 2.9785 | 2.9785 | 2.9785
2020-06-09 08:00 | Winter | 1.3337 | 2.0507 | 3.1031 | 3.1031 | 3.1031 | 3.1031 | 1.1117 | 1.1117 | 1.1117 | 1.1117 | 1.1117 | 1.1117 | 2.6674 | 3.8476 | 4.6208 | 5.0278 | 5.8418 | 6.6557 | 0.9069 | 2.4635 | 3.0898 | 3.0898 | 3.0898 | 3.0898 | 2.6483 | 3.3614 | 3.3614 | 3.3614 | 3.3614 | 3.3614
2020-06-09 09:00 | Winter | 1.3337 | 2.0507 | 3.1031 | 3.1031 | 3.1031 | 3.1031 | 1.1374 | 1.1374 | 1.1374 | 1.1374 | 1.1374 | 1.1374 | 2.7055 | 3.9026 | 4.6869 | 5.0996 | 5.9252 | 6.7508 | 0.88023 | 2.3911 | 2.9989 | 2.9989 | 2.9989 | 2.9989 | 2.7436 | 3.4824 | 3.4824 | 3.4824 | 3.4824 | 3.4824
2020-06-09 10:00 | Winter | 1.2777 | 1.9645 | 2.9727 | 2.9727 | 2.9727 | 2.9727 | 1.0888 | 1.0888 | 1.0888 | 1.0888 | 1.0888 | 1.0888 | 2.7626 | 3.985 | 4.7859 | 5.2074 | 6.0504 | 6.8934 | 0.88404 | 2.4014 | 3.0119 | 3.0119 | 3.0119 | 3.0119 | 2.7626 | 3.5065 | 3.5065 | 3.5065 | 3.5065 | 3.5065
2020-06-09 11:00 | Winter | 1.2575 | 1.9335 | 2.9258 | 2.9258 | 2.9258 | 2.9258 | 1.1431 | 1.1431 | 1.1431 | 1.1431 | 1.1431 | 1.1431 | 2.7245 | 3.93 | 4.7199 | 5.1356 | 5.967 | 6.7984 | 0.83069 | 2.2565 | 2.8302 | 2.8302 | 2.8302 | 2.8302 | 2.7055 | 3.434 | 3.434 | 3.434 | 3.434 | 3.434
2020-06-09 12:00 | Winter | 1.2765 | 1.9628 | 2.9701 | 2.9701 | 2.9701 | 2.9701 | 1.106 | 1.106 | 1.106 | 1.106 | 1.106 | 1.106 | 2.6674 | 3.8476 | 4.6208 | 5.0278 | 5.8418 | 6.6557 | 0.84974 | 2.3082 | 2.8951 | 2.8951 | 2.8951 | 2.8951 | 2.7055 | 3.434 | 3.434 | 3.434 | 3.434 | 3.434
2020-06-09 13:00 | Winter | 1.2375 | 1.9028 | 2.8793 | 2.8793 | 2.8793 | 2.8793 | 1.0431 | 1.0431 | 1.0431 | 1.0431 | 1.0431 | 1.0431 | 2.6483 | 3.8201 | 4.5878 | 4.9919 | 5.8 | 6.6082 | 0.81926 | 2.2254 | 2.7912 | 2.7912 | 2.7912 | 2.7912 | 2.5911 | 3.2889 | 3.2889 | 3.2889 | 3.2889 | 3.2889
2020-06-09 14:00 | Winter | 1.2384 | 1.9042 | 2.8814 | 2.8814 | 2.8814 | 2.8814 | 1.026 | 1.026 | 1.026 | 1.026 | 1.026 | 1.026 | 2.5149 | 3.6277 | 4.3568 | 4.7405 | 5.508 | 6.2754 | 0.80783 | 2.1944 | 2.7523 | 2.7523 | 2.7523 | 2.7523 | 2.4768 | 3.1438 | 3.1438 | 3.1438 | 3.1438 | 3.1438
2020-06-09 15:00 | Winter | 1.2003 | 1.8456 | 2.7928 | 2.7928 | 2.7928 | 2.7928 | 1.0346 | 1.0346 | 1.0346 | 1.0346 | 1.0346 | 1.0346 | 2.3435 | 3.3804 | 4.0597 | 4.4173 | 5.1324 | 5.8475 | 0.81164 | 2.2047 | 2.7653 | 2.7653 | 2.7653 | 2.7653 | 2.4006 | 3.0471 | 3.0471 | 3.0471 | 3.0471 | 3.0471
2020-06-09 16:00 | Winter | 1.1432 | 1.7577 | 2.6598 | 2.6598 | 2.6598 | 2.6598 | 0.99454 | 0.99454 | 0.99454 | 0.99454 | 0.99454 | 0.99454 | 2.3435 | 3.3804 | 4.0597 | 4.4173 | 5.1324 | 5.8475 | 0.83069 | 2.2565 | 2.8302 | 2.8302 | 2.8302 | 2.8302 | 2.3435 | 2.9745 | 2.9745 | 2.9745 | 2.9745 | 2.9745
2020-06-09 17:00 | Winter | 1.086 | 1.6698 | 2.5268 | 2.5268 | 2.5268 | 2.5268 | 0.90023 | 0.90023 | 0.90023 | 0.90023 | 0.90023 | 0.90023 | 2.5911 | 3.7377 | 4.4888 | 4.8842 | 5.6749 | 6.4656 | 0.80783 | 2.1944 | 2.7523 | 2.7523 | 2.7523 | 2.7523 | 2.2863 | 2.902 | 2.902 | 2.902 | 2.902 | 2.902
2020-06-09 18:00 | Winter | 0.84035 | 1.2921 | 1.9553 | 1.9553 | 1.9553 | 1.9553 | 0.78591 | 0.78591 | 0.78591 | 0.78591 | 0.78591 | 0.78591 | 2.5081 | 3.6179 | 4.345 | 4.7277 | 5.493 | 6.2584 | 0.78115 | 2.1219 | 2.6614 | 2.6614 | 2.6614 | 2.6614 | 1.7155 | 2.1774 | 2.1774 | 2.1774 | 2.1774 | 2.1774
2020-06-09 19:00 | Winter | 0.65903 | 1.0133 | 1.5334 | 1.5334 | 1.5334 | 1.5334 | 0.56872 | 0.56872 | 0.56872 | 0.56872 | 0.56872 | 0.56872 | 2.4197 | 3.4903 | 4.1918 | 4.561 | 5.2993 | 6.0377 | 0.73924 | 2.0081 | 2.5186 | 2.5186 | 2.5186 | 2.5186 | 1.1622 | 1.4752 | 1.4752 | 1.4752 | 1.4752 | 1.4752
2020-06-09 20:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.50719 | 0.50719 | 0.50719 | 0.50719 | 0.50719 | 0.50719 | 2.3435 | 3.3804 | 4.0597 | 4.4173 | 5.1324 | 5.8475 | 0.73543 | 1.9977 | 2.5056 | 2.5056 | 2.5056 | 2.5056 | 1.0669 | 1.3542 | 1.3542 | 1.3542 | 1.3542 | 1.3542
2020-06-09 21:00 | Winter | 0.58679 | 0.90226 | 1.3653 | 1.3653 | 1.3653 | 1.3653 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 2.2489 | 3.244 | 3.8959 | 4.2391 | 4.9253 | 5.6116 | 0.75067 | 2.0391 | 2.5575 | 2.5575 | 2.5575 | 2.5575 | 0.97168 | 1.2333 | 1.2333 | 1.2333 | 1.2333 | 1.2333
2020-06-09 22:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.40582 | 0.40582 | 0.40582 | 0.40582 | 0.40582 | 0.40582 | 2.0207 | 2.9149 | 3.5007 | 3.809 | 4.4256 | 5.0423 | 0.67827 | 1.8425 | 2.3109 | 2.3109 | 2.3109 | 2.3109 | 0.85765 | 1.0886 | 1.0886 | 1.0886 | 1.0886 | 1.0886
2020-06-09 23:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 1.8481 | 2.6658 | 3.2016 | 3.4836 | 4.0475 | 4.6115 | 0.70113 | 1.9046 | 2.3888 | 2.3888 | 2.3888 | 2.3888 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-06-10 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 1.7528 | 2.5284 | 3.0366 | 3.304 | 3.8389 | 4.3738 | 0.60587 | 1.6458 | 2.0642 | 2.0642 | 2.0642 | 2.0642 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-06-10 01:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 1.6743 | 2.4152 | 2.9005 | 3.156 | 3.6669 | 4.1779 | 0.59825 | 1.6251 | 2.0382 | 2.0382 | 2.0382 | 2.0382 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-06-10 02:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 1.6539 | 2.3857 | 2.8652 | 3.1175 | 3.6222 | 4.1269 | 0.5792 | 1.5733 | 1.9733 | 1.9733 | 1.9733 | 1.9733 | 1.0288 | 1.3059 | 1.3059 | 1.3059 | 1.3059 | 1.3059
2020-06-10 03:00 | Winter | 0.57141 | 0.87862 | 1.3295 | 1.3295 | 1.3295 | 1.3295 | 0.40582 | 0.40582 | 0.40582 | 0.40582 | 0.40582 | 0.40582 | 1.6576 | 2.391 | 2.8715 | 3.1244 | 3.6302 | 4.1361 | 0.51061 | 1.387 | 1.7396 | 1.7396 | 1.7396 | 1.7396 | 1.0288 | 1.3059 | 1.3059 | 1.3059 | 1.3059 | 1.3059
2020-06-10 04:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 1.6581 | 2.3918 | 2.8724 | 3.1254 | 3.6314 | 4.1374 | 0.54466 | 1.4795 | 1.8557 | 1.8557 | 1.8557 | 1.8557 | 1.0932 | 1.3876 | 1.3876 | 1.3876 | 1.3876 | 1.3876
2020-06-10 05:00 | Winter | 0.7553 | 1.1614 | 1.7574 | 1.7574 | 1.7574 | 1.7574 | 0.63445 | 0.63445 | 0.63445 | 0.63445 | 0.63445 | 0.63445 | 1.7338 | 2.5009 | 3.0036 | 3.2681 | 3.7972 | 4.3262 | 0.71256 | 1.9356 | 2.4277 | 2.4277 | 2.4277 | 2.4277 | 1.4898 | 1.8909 | 1.8909 | 1.8909 | 1.8909 | 1.8909
2020-06-10 06:00 | Winter | 0.88345 | 1.3584 | 2.0555 | 2.0555 | 2.0555 | 2.0555 | 0.78877 | 0.78877 | 0.78877 | 0.78877 | 0.78877 | 0.78877 | 2.1174 | 3.0543 | 3.6681 | 3.9912 | 4.6373 | 5.2835 | 0.76778 | 2.0856 | 2.6159 | 2.6159 | 2.6159 | 2.6159 | 1.8285 | 2.3209 | 2.3209 | 2.3209 | 2.3209 | 2.3209
2020-06-10 07:00 | Winter | 1.105 | 1.6991 | 2.5711 | 2.5711 | 2.5711 | 2.5711 | 0.92491 | 0.92491 | 0.92491 | 0.92491 | 0.92491 | 0.92491 | 2.4578 | 3.5453 | 4.2578 | 4.6328 | 5.3828 | 6.1328 | 0.86117 | 2.3393 | 2.934 | 2.934 | 2.934 | 2.934 | 2.3049 | 2.9256 | 2.9256 | 2.9256 | 2.9256 | 2.9256
2020-06-10 08:00 | Winter | 1.3146 | 2.0214 | 3.0588 | 3.0588 | 3.0588 | 3.0588 | 1.0917 | 1.0917 | 1.0917 | 1.0917 | 1.0917 | 1.0917 | 2.6038 | 3.756 | 4.5108 | 4.9081 | 5.7027 | 6.4972 | 0.90309 | 2.4532 | 3.0768 | 3.0768 | 3.0768 | 3.0768 | 2.5721 | 3.2647 | 3.2647 | 3.2647 | 3.2647 | 3.2647
2020-06-10 09:00 | Winter | 1.2956 | 1.9921 | 3.0144 | 3.0144 | 3.0144 | 3.0144 | 1.1374 | 1.1374 | 1.1374 | 1.1374 | 1.1374 | 1.1374 | 2.6102 | 3.7651 | 4.5218 | 4.9201 | 5.7166 | 6.5131 | 0.87261 | 2.3704 | 2.973 | 2.973 | 2.973 | 2.973 | 2.6293 | 3.3373 | 3.3373 | 3.3373 | 3.3373 | 3.3373
2020-06-10 10:00 | Winter | 1.2384 | 1.9042 | 2.8814 | 2.8814 | 2.8814 | 2.8814 | 1.046 | 1.046 | 1.046 | 1.046 | 1.046 | 1.046 | 2.6674 | 3.8476 | 4.6208 | 5.0278 | 5.8418 | 6.6557 | 0.84212 | 2.2875 | 2.8691 | 2.8691 | 2.8691 | 2.8691 | 2.6293 | 3.3373 | 3.3373 | 3.3373 | 3.3373 | 3.3373
2020-06-10 11:00 | Winter | 1.2003 | 1.8456 | 2.7928 | 2.7928 | 2.7928 | 2.7928 | 1.0034 | 1.0034 | 1.0034 | 1.0034 | 1.0034 | 1.0034 | 2.5911 | 3.7377 | 4.4888 | 4.8842 | 5.6749 | 6.4656 | 0.81164 | 2.2047 | 2.7653 | 2.7653 | 2.7653 | 2.7653 | 2.553 | 3.2405 | 3.2405 | 3.2405 | 3.2405 | 3.2405
2020-06-10 12:00 | Winter | 1.2003 | 1.8456 | 2.7928 | 2.7928 | 2.7928 | 2.7928 | 1.0746 | 1.0746 | 1.0746 | 1.0746 | 1.0746 | 1.0746 | 2.553 | 3.6827 | 4.4228 | 4.8123 | 5.5914 | 6.3705 | 0.81545 | 2.2151 | 2.7782 | 2.7782 | 2.7782 | 2.7782 | 2.4983 | 3.171 | 3.171 | 3.171 | 3.171 | 3.171
2020-06-10 13:00 | Winter | 1.2003 | 1.8456 | 2.7928 | 2.7928 | 2.7928 | 2.7928 | 0.9431 | 0.9431 | 0.9431 | 0.9431 | 0.9431 | 0.9431 | 2.5911 | 3.7377 | 4.4888 | 4.8842 | 5.6749 | 6.4656 | 0.75067 | 2.0391 | 2.5575 | 2.5575 | 2.5575 | 2.5575 | 2.5149 | 3.1922 | 3.1922 | 3.1922 | 3.1922 | 3.1922
2020-06-10 14:00 | Winter | 1.1813 | 1.8163 | 2.7485 | 2.7485 | 2.7485 | 2.7485 | 1.0145 | 1.0145 | 1.0145 | 1.0145 | 1.0145 | 1.0145 | 2.4768 | 3.5728 | 4.2908 | 4.6687 | 5.4245 | 6.1803 | 0.76972 | 2.0909 | 2.6225 | 2.6225 | 2.6225 | 2.6225 | 2.4197 | 3.0712 | 3.0712 | 3.0712 | 3.0712 | 3.0712
2020-06-10 15:00 | Winter | 1.1241 | 1.7284 | 2.6155 | 2.6155 | 2.6155 | 2.6155 | 0.90023 | 0.90023 | 0.90023 | 0.90023 | 0.90023 | 0.90023 | 2.4768 | 3.5728 | 4.2908 | 4.6687 | 5.4245 | 6.1803 | 0.7621 | 2.0702 | 2.5965 | 2.5965 | 2.5965 | 2.5965 | 2.2673 | 2.8778 | 2.8778 | 2.8778 | 2.8778 | 2.8778
2020-06-10 16:00 | Winter | 1.086 | 1.6698 | 2.5268 | 2.5268 | 2.5268 | 2.5268 | 0.95453 | 0.95453 | 0.95453 | 0.95453 | 0.95453 | 0.95453 | 2.4197 | 3.4903 | 4.1918 | 4.561 | 5.2993 | 6.0377 | 0.77734 | 2.1116 | 2.6484 | 2.6484 | 2.6484 | 2.6484 | 2.2291 | 2.8294 | 2.8294 | 2.8294 | 2.8294 | 2.8294
2020-06-10 17:00 | Winter | 1.086 | 1.6698 | 2.5268 | 2.5268 | 2.5268 | 2.5268 | 0.86022 | 0.86022 | 0.86022 | 0.86022 | 0.86022 | 0.86022 | 2.5145 | 3.627 | 4.356 | 4.7396 | 5.5069 | 6.2742 | 0.84593 | 2.2979 | 2.8821 | 2.8821 | 2.8821 | 2.8821 | 2.172 | 2.7569 | 2.7569 | 2.7569 | 2.7569 | 2.7569
2020-06-10 18:00 | Winter | 0.93437 | 1.4367 | 2.174 | 2.174 | 2.174 | 2.174 | 0.80592 | 0.80592 | 0.80592 | 0.80592 | 0.80592 | 0.80592 | 2.534 | 3.6552 | 4.3898 | 4.7764 | 5.5497 | 6.3229 | 0.80402 | 2.184 | 2.7393 | 2.7393 | 2.7393 | 2.7393 | 1.7088 | 2.1689 | 2.1689 | 2.1689 | 2.1689 | 2.1689
2020-06-10 19:00 | Winter | 0.68589 | 1.0546 | 1.5959 | 1.5959 | 1.5959 | 1.5959 | 0.66303 | 0.66303 | 0.66303 | 0.66303 | 0.66303 | 0.66303 | 2.3054 | 3.3254 | 3.9937 | 4.3455 | 5.049 | 5.7525 | 0.71637 | 1.946 | 2.4407 | 2.4407 | 2.4407 | 2.4407 | 1.1454 | 1.4538 | 1.4538 | 1.4538 | 1.4538 | 1.4538
2020-06-10 20:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.49441 | 0.49441 | 0.49441 | 0.49441 | 0.49441 | 0.49441 | 2.2482 | 3.243 | 3.8947 | 4.2377 | 4.9238 | 5.6098 | 0.71637 | 1.946 | 2.4407 | 2.4407 | 2.4407 | 2.4407 | 1.0669 | 1.3542 | 1.3542 | 1.3542 | 1.3542 | 1.3542
2020-06-10 21:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 2.0958 | 3.0231 | 3.6307 | 3.9504 | 4.59 | 5.2295 | 0.68589 | 1.8632 | 2.3368 | 2.3368 | 2.3368 | 2.3368 | 0.99073 | 1.2575 | 1.2575 | 1.2575 | 1.2575 | 1.2575
2020-06-10 22:00 | Winter | 0.57104 | 0.87804 | 1.3286 | 1.3286 | 1.3286 | 1.3286 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 1.9631 | 2.8317 | 3.4008 | 3.7003 | 4.2993 | 4.8984 | 0.6516 | 1.77 | 2.22 | 2.22 | 2.22 | 2.22 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-06-10 23:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.43154 | 0.43154 | 0.43154 | 0.43154 | 0.43154 | 0.43154 | 1.7807 | 2.5687 | 3.0849 | 3.3566 | 3.9 | 4.4434 | 0.65922 | 1.7907 | 2.246 | 2.246 | 2.246 | 2.246 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-06-11 | Winter | 0.53347 | 0.82027 | 1.2412 | 1.2412 | 1.2412 | 1.2412 | 0.41153 | 0.41153 | 0.41153 | 0.41153 | 0.41153 | 0.41153 | 1.7414 | 2.5119 | 3.0168 | 3.2825 | 3.8139 | 4.3452 | 0.5449 | 1.4802 | 1.8565 | 1.8565 | 1.8565 | 1.8565 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-06-11 01:00 | Winter | 0.55233 | 0.84928 | 1.2851 | 1.2851 | 1.2851 | 1.2851 | 0.39724 | 0.39724 | 0.39724 | 0.39724 | 0.39724 | 0.39724 | 1.6395 | 2.3649 | 2.8402 | 3.0903 | 3.5906 | 4.0909 | 0.55252 | 1.5009 | 1.8825 | 1.8825 | 1.8825 | 1.8825 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-06-11 02:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.4001 | 0.4001 | 0.4001 | 0.4001 | 0.4001 | 0.4001 | 1.6004 | 2.3086 | 2.7725 | 3.0167 | 3.5051 | 3.9934 | 0.5449 | 1.4802 | 1.8565 | 1.8565 | 1.8565 | 1.8565 | 0.88659 | 1.1253 | 1.1253 | 1.1253 | 1.1253 | 1.1253
2020-06-11 03:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.41153 | 0.41153 | 0.41153 | 0.41153 | 0.41153 | 0.41153 | 1.5814 | 2.2811 | 2.7395 | 2.9808 | 3.4633 | 3.9459 | 0.51061 | 1.387 | 1.7396 | 1.7396 | 1.7396 | 1.7396 | 1.0479 | 1.3301 | 1.3301 | 1.3301 | 1.3301 | 1.3301
2020-06-11 04:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.48584 | 0.48584 | 0.48584 | 0.48584 | 0.48584 | 0.48584 | 1.5841 | 2.285 | 2.7442 | 2.9859 | 3.4693 | 3.9527 | 0.5792 | 1.5733 | 1.9733 | 1.9733 | 1.9733 | 1.9733 | 1.0288 | 1.3059 | 1.3059 | 1.3059 | 1.3059 | 1.3059
2020-06-11 05:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.53685 | 0.53685 | 0.53685 | 0.53685 | 0.53685 | 0.53685 | 1.6486 | 2.3781 | 2.856 | 3.1075 | 3.6106 | 4.1137 | 0.6897 | 1.8735 | 2.3498 | 2.3498 | 2.3498 | 2.3498 | 1.4471 | 1.8367 | 1.8367 | 1.8367 | 1.8367 | 1.8367
2020-06-11 06:00 | Winter | 0.66617 | 1.0243 | 1.55 | 1.55 | 1.55 | 1.55 | 0.75734 | 0.75734 | 0.75734 | 0.75734 | 0.75734 | 0.75734 | 2.0707 | 2.987 | 3.5873 | 3.9032 | 4.5351 | 5.167 | 0.76591 | 2.0805 | 2.6095 | 2.6095 | 2.6095 | 2.6095 | 1.7147 | 2.1765 | 2.1765 | 2.1765 | 2.1765 | 2.1765
2020-06-11 07:00 | Winter | 1.0662 | 1.6394 | 2.4808 | 2.4808 | 2.4808 | 2.4808 | 0.79163 | 0.79163 | 0.79163 | 0.79163 | 0.79163 | 0.79163 | 2.4387 | 3.5178 | 4.2248 | 4.5969 | 5.3411 | 6.0852 | 0.91833 | 2.4946 | 3.1288 | 3.1288 | 3.1288 | 3.1288 | 2.2963 | 2.9147 | 2.9147 | 2.9147 | 2.9147 | 2.9147
2020-06-11 08:00 | Winter | 1.2956 | 1.9921 | 3.0144 | 3.0144 | 3.0144 | 3.0144 | 0.97453 | 0.97453 | 0.97453 | 0.97453 | 0.97453 | 0.97453 | 2.553 | 3.6827 | 4.4228 | 4.8123 | 5.5914 | 6.3705 | 0.9108 | 2.4741 | 3.1031 | 3.1031 | 3.1031 | 3.1031 | 2.5332 | 3.2153 | 3.2153 | 3.2153 | 3.2153 | 3.2153
2020-06-11 09:00 | Winter | 1.2765 | 1.9628 | 2.9701 | 2.9701 | 2.9701 | 2.9701 | 1.0631 | 1.0631 | 1.0631 | 1.0631 | 1.0631 | 1.0631 | 2.5721 | 3.7102 | 4.4558 | 4.8483 | 5.6331 | 6.418 | 0.8345 | 2.2668 | 2.8432 | 2.8432 | 2.8432 | 2.8432 | 2.5721 | 3.2647 | 3.2647 | 3.2647 | 3.2647 | 3.2647
2020-06-11 10:00 | Winter | 1.2233 | 1.8809 | 2.8462 | 2.8462 | 2.8462 | 2.8462 | 1.0203 | 1.0203 | 1.0203 | 1.0203 | 1.0203 | 1.0203 | 2.6293 | 3.7926 | 4.5548 | 4.956 | 5.7583 | 6.5606 | 0.83831 | 2.2772 | 2.8561 | 2.8561 | 2.8561 | 2.8561 | 2.534 | 3.2163 | 3.2163 | 3.2163 | 3.2163 | 3.2163
2020-06-11 11:00 | Winter | 1.2003 | 1.8456 | 2.7928 | 2.7928 | 2.7928 | 2.7928 | 0.9974 | 0.9974 | 0.9974 | 0.9974 | 0.9974 | 0.9974 | 2.6483 | 3.8201 | 4.5878 | 4.9919 | 5.8 | 6.6082 | 0.80021 | 2.1737 | 2.7263 | 2.7263 | 2.7263 | 2.7263 | 2.5721 | 3.2647 | 3.2647 | 3.2647 | 3.2647 | 3.2647
2020-06-11 12:00 | Winter | 1.1622 | 1.787 | 2.7041 | 2.7041 | 2.7041 | 2.7041 | 0.98025 | 0.98025 | 0.98025 | 0.98025 | 0.98025 | 0.98025 | 2.4578 | 3.5453 | 4.2578 | 4.6328 | 5.3828 | 6.1328 | 0.79258 | 2.153 | 2.7003 | 2.7003 | 2.7003 | 2.7003 | 2.5149 | 3.1922 | 3.1922 | 3.1922 | 3.1922 | 3.1922
2020-06-11 13:00 | Winter | 1.1622 | 1.787 | 2.7041 | 2.7041 | 2.7041 | 2.7041 | 1.0141 | 1.0141 | 1.0141 | 1.0141 | 1.0141 | 1.0141 | 2.4768 | 3.5728 | 4.2908 | 4.6687 | 5.4245 | 6.1803 | 0.76591 | 2.0805 | 2.6095 | 2.6095 | 2.6095 | 2.6095 | 2.4197 | 3.0712 | 3.0712 | 3.0712 | 3.0712 | 3.0712
2020-06-11 14:00 | Winter | 1.1622 | 1.787 | 2.7041 | 2.7041 | 2.7041 | 2.7041 | 1.0174 | 1.0174 | 1.0174 | 1.0174 | 1.0174 | 1.0174 | 2.4432 | 3.5242 | 4.2324 | 4.6052 | 5.3507 | 6.0963 | 0.80783 | 2.1944 | 2.7523 | 2.7523 | 2.7523 | 2.7523 | 2.2673 | 2.8778 | 2.8778 | 2.8778 | 2.8778 | 2.8778
2020-06-11 15:00 | Winter | 1.105 | 1.6991 | 2.5711 | 2.5711 | 2.5711 | 2.5711 | 0.9974 | 0.9974 | 0.9974 | 0.9974 | 0.9974 | 0.9974 | 2.4387 | 3.5178 | 4.2248 | 4.5969 | 5.3411 | 6.0852 | 0.78496 | 2.1323 | 2.6744 | 2.6744 | 2.6744 | 2.6744 | 2.3244 | 2.9503 | 2.9503 | 2.9503 | 2.9503 | 2.9503
2020-06-11 16:00 | Winter | 1.105 | 1.6991 | 2.5711 | 2.5711 | 2.5711 | 2.5711 | 1.0603 | 1.0603 | 1.0603 | 1.0603 | 1.0603 | 1.0603 | 2.4197 | 3.4903 | 4.1918 | 4.561 | 5.2993 | 6.0377 | 0.78877 | 2.1426 | 2.6874 | 2.6874 | 2.6874 | 2.6874 | 2.2863 | 2.902 | 2.902 | 2.902 | 2.902 | 2.902
2020-06-11 17:00 | Winter | 1.0547 | 1.6218 | 2.4541 | 2.4541 | 2.4541 | 2.4541 | 0.94596 | 0.94596 | 0.94596 | 0.94596 | 0.94596 | 0.94596 | 2.5721 | 3.7102 | 4.4558 | 4.8483 | 5.6331 | 6.418 | 0.81164 | 2.2047 | 2.7653 | 2.7653 | 2.7653 | 2.7653 | 2.1981 | 2.79 | 2.79 | 2.79 | 2.79 | 2.79
2020-06-11 18:00 | Winter | 0.79371 | 1.2204 | 1.8467 | 1.8467 | 1.8467 | 1.8467 | 0.75734 | 0.75734 | 0.75734 | 0.75734 | 0.75734 | 0.75734 | 2.4006 | 3.4628 | 4.1588 | 4.525 | 5.2576 | 5.9902 | 0.76591 | 2.0805 | 2.6095 | 2.6095 | 2.6095 | 2.6095 | 1.7528 | 2.2248 | 2.2248 | 2.2248 | 2.2248 | 2.2248
2020-06-11 19:00 | Winter | 0.66684 | 1.0253 | 1.5515 | 1.5515 | 1.5515 | 1.5515 | 0.67446 | 0.67446 | 0.67446 | 0.67446 | 0.67446 | 0.67446 | 2.3817 | 3.4356 | 4.126 | 4.4894 | 5.2162 | 5.943 | 0.7621 | 2.0702 | 2.5965 | 2.5965 | 2.5965 | 2.5965 | 1.1688 | 1.4835 | 1.4835 | 1.4835 | 1.4835 | 1.4835
2020-06-11 20:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.52585 | 0.52585 | 0.52585 | 0.52585 | 0.52585 | 0.52585 | 2.2863 | 3.2979 | 3.9607 | 4.3096 | 5.0072 | 5.7049 | 0.73162 | 1.9874 | 2.4926 | 2.4926 | 2.4926 | 2.4926 | 1.0672 | 1.3545 | 1.3545 | 1.3545 | 1.3545 | 1.3545
2020-06-11 21:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.47441 | 0.47441 | 0.47441 | 0.47441 | 0.47441 | 0.47441 | 2.1529 | 3.1056 | 3.7297 | 4.0582 | 4.7151 | 5.3721 | 0.724 | 1.9667 | 2.4667 | 2.4667 | 2.4667 | 2.4667 | 0.95263 | 1.2092 | 1.2092 | 1.2092 | 1.2092 | 1.2092
2020-06-11 22:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 1.9434 | 2.8032 | 3.3666 | 3.6631 | 4.2562 | 4.8492 | 0.69732 | 1.8942 | 2.3758 | 2.3758 | 2.3758 | 2.3758 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-06-11 23:00 | Winter | 0.559 | 0.85953 | 1.3006 | 1.3006 | 1.3006 | 1.3006 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 1.81 | 2.6109 | 3.1356 | 3.4117 | 3.9641 | 4.5164 | 0.6173 | 1.6768 | 2.1032 | 2.1032 | 2.1032 | 2.1032 | 0.87367 | 1.1089 | 1.1089 | 1.1089 | 1.1089 | 1.1089
2020-06-12 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.41153 | 0.41153 | 0.41153 | 0.41153 | 0.41153 | 0.41153 | 1.7719 | 2.5559 | 3.0696 | 3.3399 | 3.8806 | 4.4213 | 0.5792 | 1.5733 | 1.9733 | 1.9733 | 1.9733 | 1.9733 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-06-12 01:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 1.6957 | 2.446 | 2.9375 | 3.1963 | 3.7137 | 4.2311 | 0.58682 | 1.594 | 1.9993 | 1.9993 | 1.9993 | 1.9993 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-06-12 02:00 | Winter | 0.55115 | 0.84746 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 0.43438 | 0.43438 | 0.43438 | 0.43438 | 0.43438 | 0.43438 | 1.6766 | 2.4185 | 2.9045 | 3.1603 | 3.672 | 4.1836 | 0.57539 | 1.563 | 1.9603 | 1.9603 | 1.9603 | 1.9603 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-06-12 03:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.43439 | 0.43439 | 0.43439 | 0.43439 | 0.43439 | 0.43439 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.55246 | 1.5007 | 1.8822 | 1.8822 | 1.8822 | 1.8822 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-06-12 04:00 | Winter | 0.55782 | 0.85771 | 1.2979 | 1.2979 | 1.2979 | 1.2979 | 0.47441 | 0.47441 | 0.47441 | 0.47441 | 0.47441 | 0.47441 | 1.6576 | 2.391 | 2.8715 | 3.1244 | 3.6302 | 4.1361 | 0.56395 | 1.5319 | 1.9214 | 1.9214 | 1.9214 | 1.9214 | 1.0669 | 1.3542 | 1.3542 | 1.3542 | 1.3542 | 1.3542
2020-06-12 05:00 | Winter | 0.59039 | 0.90779 | 1.3737 | 1.3737 | 1.3737 | 1.3737 | 0.64588 | 0.64588 | 0.64588 | 0.64588 | 0.64588 | 0.64588 | 1.7528 | 2.5284 | 3.0366 | 3.304 | 3.8389 | 4.3738 | 0.67446 | 1.8321 | 2.2979 | 2.2979 | 2.2979 | 2.2979 | 1.3961 | 1.7721 | 1.7721 | 1.7721 | 1.7721 | 1.7721
2020-06-12 06:00 | Winter | 0.68048 | 1.0463 | 1.5833 | 1.5833 | 1.5833 | 1.5833 | 0.77162 | 0.77162 | 0.77162 | 0.77162 | 0.77162 | 0.77162 | 2.0196 | 2.9132 | 3.4986 | 3.8068 | 4.4231 | 5.0393 | 0.80402 | 2.184 | 2.7393 | 2.7393 | 2.7393 | 2.7393 | 1.7899 | 2.2719 | 2.2719 | 2.2719 | 2.2719 | 2.2719
2020-06-12 07:00 | Winter | 1.0873 | 1.6719 | 2.5299 | 2.5299 | 2.5299 | 2.5299 | 0.93167 | 0.93167 | 0.93167 | 0.93167 | 0.93167 | 0.93167 | 2.3536 | 3.395 | 4.0773 | 4.4364 | 5.1546 | 5.8728 | 0.81545 | 2.2151 | 2.7782 | 2.7782 | 2.7782 | 2.7782 | 2.3244 | 2.9503 | 2.9503 | 2.9503 | 2.9503 | 2.9503
2020-06-12 08:00 | Winter | 1.2384 | 1.9042 | 2.8814 | 2.8814 | 2.8814 | 2.8814 | 0.97453 | 0.97453 | 0.97453 | 0.97453 | 0.97453 | 0.97453 | 2.4578 | 3.5453 | 4.2578 | 4.6328 | 5.3828 | 6.1328 | 0.86498 | 2.3496 | 2.947 | 2.947 | 2.947 | 2.947 | 2.534 | 3.2163 | 3.2163 | 3.2163 | 3.2163 | 3.2163
2020-06-12 09:00 | Winter | 1.2575 | 1.9335 | 2.9258 | 2.9258 | 2.9258 | 2.9258 | 0.97739 | 0.97739 | 0.97739 | 0.97739 | 0.97739 | 0.97739 | 2.4959 | 3.6002 | 4.3238 | 4.7046 | 5.4662 | 6.2279 | 0.88785 | 2.4118 | 3.0249 | 3.0249 | 3.0249 | 3.0249 | 2.4959 | 3.168 | 3.168 | 3.168 | 3.168 | 3.168
2020-06-12 10:00 | Winter | 1.2194 | 1.8749 | 2.8371 | 2.8371 | 2.8371 | 2.8371 | 0.98311 | 0.98311 | 0.98311 | 0.98311 | 0.98311 | 0.98311 | 2.4578 | 3.5453 | 4.2578 | 4.6328 | 5.3828 | 6.1328 | 0.89547 | 2.4325 | 3.0509 | 3.0509 | 3.0509 | 3.0509 | 2.4768 | 3.1438 | 3.1438 | 3.1438 | 3.1438 | 3.1438
2020-06-12 11:00 | Winter | 1.1813 | 1.8163 | 2.7485 | 2.7485 | 2.7485 | 2.7485 | 0.93452 | 0.93452 | 0.93452 | 0.93452 | 0.93452 | 0.93452 | 2.4197 | 3.4903 | 4.1918 | 4.561 | 5.2993 | 6.0377 | 0.83831 | 2.2772 | 2.8561 | 2.8561 | 2.8561 | 2.8561 | 2.4768 | 3.1438 | 3.1438 | 3.1438 | 3.1438 | 3.1438
2020-06-12 12:00 | Winter | 1.2194 | 1.8749 | 2.8371 | 2.8371 | 2.8371 | 2.8371 | 0.99168 | 0.99168 | 0.99168 | 0.99168 | 0.99168 | 0.99168 | 2.3435 | 3.3804 | 4.0597 | 4.4173 | 5.1324 | 5.8475 | 0.81926 | 2.2254 | 2.7912 | 2.7912 | 2.7912 | 2.7912 | 2.4197 | 3.0712 | 3.0712 | 3.0712 | 3.0712 | 3.0712
2020-06-12 13:00 | Winter | 1.2003 | 1.8456 | 2.7928 | 2.7928 | 2.7928 | 2.7928 | 1.0288 | 1.0288 | 1.0288 | 1.0288 | 1.0288 | 1.0288 | 2.3435 | 3.3804 | 4.0597 | 4.4173 | 5.1324 | 5.8475 | 0.76972 | 2.0909 | 2.6225 | 2.6225 | 2.6225 | 2.6225 | 2.3244 | 2.9503 | 2.9503 | 2.9503 | 2.9503 | 2.9503
2020-06-12 14:00 | Winter | 1.2194 | 1.8749 | 2.8371 | 2.8371 | 2.8371 | 2.8371 | 0.92023 | 0.92023 | 0.92023 | 0.92023 | 0.92023 | 0.92023 | 2.4006 | 3.4628 | 4.1588 | 4.525 | 5.2576 | 5.9902 | 0.72781 | 1.977 | 2.4796 | 2.4796 | 2.4796 | 2.4796 | 2.4197 | 3.0712 | 3.0712 | 3.0712 | 3.0712 | 3.0712
2020-06-12 15:00 | Winter | 1.1241 | 1.7284 | 2.6155 | 2.6155 | 2.6155 | 2.6155 | 0.82021 | 0.82021 | 0.82021 | 0.82021 | 0.82021 | 0.82021 | 2.3435 | 3.3804 | 4.0597 | 4.4173 | 5.1324 | 5.8475 | 0.78115 | 2.1219 | 2.6614 | 2.6614 | 2.6614 | 2.6614 | 2.2101 | 2.8052 | 2.8052 | 2.8052 | 2.8052 | 2.8052
2020-06-12 16:00 | Winter | 1.1622 | 1.787 | 2.7041 | 2.7041 | 2.7041 | 2.7041 | 0.79449 | 0.79449 | 0.79449 | 0.79449 | 0.79449 | 0.79449 | 2.3435 | 3.3804 | 4.0597 | 4.4173 | 5.1324 | 5.8475 | 0.80402 | 2.184 | 2.7393 | 2.7393 | 2.7393 | 2.7393 | 2.172 | 2.7569 | 2.7569 | 2.7569 | 2.7569 | 2.7569
2020-06-12 17:00 | Winter | 1.0556 | 1.6232 | 2.4562 | 2.4562 | 2.4562 | 2.4562 | 0.81164 | 0.81164 | 0.81164 | 0.81164 | 0.81164 | 0.81164 | 2.4768 | 3.5728 | 4.2908 | 4.6687 | 5.4245 | 6.1803 | 0.82688 | 2.2461 | 2.8172 | 2.8172 | 2.8172 | 2.8172 | 2.0005 | 2.5392 | 2.5392 | 2.5392 | 2.5392 | 2.5392
2020-06-12 18:00 | Winter | 0.93402 | 1.4362 | 2.1732 | 2.1732 | 2.1732 | 2.1732 | 0.68303 | 0.68303 | 0.68303 | 0.68303 | 0.68303 | 0.68303 | 2.3625 | 3.4079 | 4.0927 | 4.4532 | 5.1741 | 5.8951 | 0.75829 | 2.0598 | 2.5835 | 2.5835 | 2.5835 | 2.5835 | 1.6576 | 2.1039 | 2.1039 | 2.1039 | 2.1039 | 2.1039
2020-06-12 19:00 | Winter | 0.70783 | 1.0884 | 1.6469 | 1.6469 | 1.6469 | 1.6469 | 0.5861 | 0.5861 | 0.5861 | 0.5861 | 0.5861 | 0.5861 | 2.2482 | 3.243 | 3.8947 | 4.2377 | 4.9238 | 5.6098 | 0.76591 | 2.0805 | 2.6095 | 2.6095 | 2.6095 | 2.6095 | 1.1241 | 1.4268 | 1.4268 | 1.4268 | 1.4268 | 1.4268
2020-06-12 20:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.50584 | 0.50584 | 0.50584 | 0.50584 | 0.50584 | 0.50584 | 2.1339 | 3.0781 | 3.6967 | 4.0223 | 4.6734 | 5.3246 | 0.68208 | 1.8528 | 2.3239 | 2.3239 | 2.3239 | 2.3239 | 1.1241 | 1.4268 | 1.4268 | 1.4268 | 1.4268 | 1.4268
2020-06-12 21:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.49727 | 0.49727 | 0.49727 | 0.49727 | 0.49727 | 0.49727 | 2.0274 | 2.9245 | 3.5123 | 3.8216 | 4.4403 | 5.059 | 0.70113 | 1.9046 | 2.3888 | 2.3888 | 2.3888 | 2.3888 | 1.0098 | 1.2817 | 1.2817 | 1.2817 | 1.2817 | 1.2817
2020-06-12 22:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 1.9624 | 2.8307 | 3.3996 | 3.699 | 4.2979 | 4.8967 | 0.64016 | 1.7389 | 2.1811 | 2.1811 | 2.1811 | 2.1811 | 0.9561 | 1.2136 | 1.2136 | 1.2136 | 1.2136 | 1.2136
2020-06-12 23:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 1.8672 | 2.6933 | 3.2346 | 3.5195 | 4.0892 | 4.659 | 0.59444 | 1.6147 | 2.0253 | 2.0253 | 2.0253 | 2.0253 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-06-13 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.38295 | 0.38295 | 0.38295 | 0.38295 | 0.38295 | 0.38295 | 1.7147 | 2.4735 | 2.9705 | 3.2322 | 3.7554 | 4.2787 | 0.5449 | 1.4802 | 1.8565 | 1.8565 | 1.8565 | 1.8565 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-06-13 01:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.40296 | 0.40296 | 0.40296 | 0.40296 | 0.40296 | 0.40296 | 1.6576 | 2.391 | 2.8715 | 3.1244 | 3.6302 | 4.1361 | 0.55208 | 1.4997 | 1.881 | 1.881 | 1.881 | 1.881 | 0.81971 | 1.0404 | 1.0404 | 1.0404 | 1.0404 | 1.0404
2020-06-13 02:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.39153 | 0.39153 | 0.39153 | 0.39153 | 0.39153 | 0.39153 | 1.6195 | 2.336 | 2.8055 | 3.0526 | 3.5468 | 4.041 | 0.55252 | 1.5009 | 1.8825 | 1.8825 | 1.8825 | 1.8825 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-06-13 03:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 1.6195 | 2.336 | 2.8055 | 3.0526 | 3.5468 | 4.041 | 0.5449 | 1.4802 | 1.8565 | 1.8565 | 1.8565 | 1.8565 | 0.8141 | 1.0333 | 1.0333 | 1.0333 | 1.0333 | 1.0333
2020-06-13 04:00 | Winter | 0.64779 | 0.99605 | 1.5072 | 1.5072 | 1.5072 | 1.5072 | 0.42582 | 0.42582 | 0.42582 | 0.42582 | 0.42582 | 0.42582 | 1.6181 | 2.3341 | 2.8032 | 3.0501 | 3.5438 | 4.0376 | 0.54871 | 1.4905 | 1.8695 | 1.8695 | 1.8695 | 1.8695 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-06-13 05:00 | Winter | 0.60954 | 0.93723 | 1.4182 | 1.4182 | 1.4182 | 1.4182 | 0.51442 | 0.51442 | 0.51442 | 0.51442 | 0.51442 | 0.51442 | 1.6957 | 2.446 | 2.9375 | 3.1963 | 3.7137 | 4.2311 | 0.56014 | 1.5216 | 1.9084 | 1.9084 | 1.9084 | 1.9084 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-06-13 06:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.51727 | 0.51727 | 0.51727 | 0.51727 | 0.51727 | 0.51727 | 1.7338 | 2.5009 | 3.0036 | 3.2681 | 3.7972 | 4.3262 | 0.59825 | 1.6251 | 2.0382 | 2.0382 | 2.0382 | 2.0382 | 0.97037 | 1.2317 | 1.2317 | 1.2317 | 1.2317 | 1.2317
2020-06-13 07:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.56872 | 0.56872 | 0.56872 | 0.56872 | 0.56872 | 0.56872 | 1.7909 | 2.5833 | 3.1025 | 3.3757 | 3.9222 | 4.4687 | 0.63254 | 1.7182 | 2.1551 | 2.1551 | 2.1551 | 2.1551 | 1.0097 | 1.2816 | 1.2816 | 1.2816 | 1.2816 | 1.2816
2020-06-13 08:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.59158 | 0.59158 | 0.59158 | 0.59158 | 0.59158 | 0.59158 | 2.0767 | 2.9956 | 3.5977 | 3.9145 | 4.5482 | 5.182 | 0.66684 | 1.8114 | 2.2719 | 2.2719 | 2.2719 | 2.2719 | 1.105 | 1.4026 | 1.4026 | 1.4026 | 1.4026 | 1.4026
2020-06-13 09:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.59729 | 0.59729 | 0.59729 | 0.59729 | 0.59729 | 0.59729 | 2.0577 | 2.9681 | 3.5647 | 3.8786 | 4.5065 | 5.1344 | 0.65541 | 1.7803 | 2.233 | 2.233 | 2.233 | 2.233 | 1.0669 | 1.3542 | 1.3542 | 1.3542 | 1.3542 | 1.3542
2020-06-13 10:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.6173 | 0.6173 | 0.6173 | 0.6173 | 0.6173 | 0.6173 | 2.1339 | 3.0781 | 3.6967 | 4.0223 | 4.6734 | 5.3246 | 0.6516 | 1.77 | 2.22 | 2.22 | 2.22 | 2.22 | 1.0669 | 1.3542 | 1.3542 | 1.3542 | 1.3542 | 1.3542
2020-06-13 11:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.54585 | 0.54585 | 0.54585 | 0.54585 | 0.54585 | 0.54585 | 2.1148 | 3.0506 | 3.6637 | 3.9863 | 4.6317 | 5.277 | 0.65541 | 1.7803 | 2.233 | 2.233 | 2.233 | 2.233 | 1.105 | 1.4026 | 1.4026 | 1.4026 | 1.4026 | 1.4026
2020-06-13 12:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.50298 | 0.50298 | 0.50298 | 0.50298 | 0.50298 | 0.50298 | 2.0386 | 2.9407 | 3.5316 | 3.8427 | 4.4648 | 5.0869 | 0.62873 | 1.7079 | 2.1421 | 2.1421 | 2.1421 | 2.1421 | 1.105 | 1.4026 | 1.4026 | 1.4026 | 1.4026 | 1.4026
2020-06-13 13:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.53442 | 0.53442 | 0.53442 | 0.53442 | 0.53442 | 0.53442 | 2.0577 | 2.9681 | 3.5647 | 3.8786 | 4.5065 | 5.1344 | 0.58682 | 1.594 | 1.9993 | 1.9993 | 1.9993 | 1.9993 | 1.0288 | 1.3059 | 1.3059 | 1.3059 | 1.3059 | 1.3059
2020-06-13 14:00 | Winter | 0.57218 | 0.87979 | 1.3313 | 1.3313 | 1.3313 | 1.3313 | 0.51156 | 0.51156 | 0.51156 | 0.51156 | 0.51156 | 0.51156 | 2.0386 | 2.9407 | 3.5316 | 3.8427 | 4.4648 | 5.0869 | 0.62873 | 1.7079 | 2.1421 | 2.1421 | 2.1421 | 2.1421 | 1.0288 | 1.3059 | 1.3059 | 1.3059 | 1.3059 | 1.3059
2020-06-13 15:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.51156 | 0.51156 | 0.51156 | 0.51156 | 0.51156 | 0.51156 | 2.0767 | 2.9956 | 3.5977 | 3.9145 | 4.5482 | 5.182 | 0.61349 | 1.6665 | 2.0902 | 2.0902 | 2.0902 | 2.0902 | 1.0288 | 1.3059 | 1.3059 | 1.3059 | 1.3059 | 1.3059
2020-06-13 16:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.50584 | 0.50584 | 0.50584 | 0.50584 | 0.50584 | 0.50584 | 2.1339 | 3.0781 | 3.6967 | 4.0223 | 4.6734 | 5.3246 | 0.62873 | 1.7079 | 2.1421 | 2.1421 | 2.1421 | 2.1421 | 0.95263 | 1.2092 | 1.2092 | 1.2092 | 1.2092 | 1.2092
2020-06-13 17:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.51727 | 0.51727 | 0.51727 | 0.51727 | 0.51727 | 0.51727 | 2.1529 | 3.1056 | 3.7297 | 4.0582 | 4.7151 | 5.3721 | 0.72018 | 1.9563 | 2.4537 | 2.4537 | 2.4537 | 2.4537 | 0.99073 | 1.2575 | 1.2575 | 1.2575 | 1.2575 | 1.2575
2020-06-13 18:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.52013 | 0.52013 | 0.52013 | 0.52013 | 0.52013 | 0.52013 | 2.2101 | 3.188 | 3.8287 | 4.1659 | 4.8403 | 5.5147 | 0.73543 | 1.9977 | 2.5056 | 2.5056 | 2.5056 | 2.5056 | 0.99073 | 1.2575 | 1.2575 | 1.2575 | 1.2575 | 1.2575
2020-06-13 19:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.5087 | 0.5087 | 0.5087 | 0.5087 | 0.5087 | 0.5087 | 2.0767 | 2.9956 | 3.5977 | 3.9145 | 4.5482 | 5.182 | 0.72018 | 1.9563 | 2.4537 | 2.4537 | 2.4537 | 2.4537 | 0.97168 | 1.2333 | 1.2333 | 1.2333 | 1.2333 | 1.2333
2020-06-13 20:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 2.0386 | 2.9407 | 3.5316 | 3.8427 | 4.4648 | 5.0869 | 0.69732 | 1.8942 | 2.3758 | 2.3758 | 2.3758 | 2.3758 | 0.93358 | 1.185 | 1.185 | 1.185 | 1.185 | 1.185
2020-06-13 21:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 2.0577 | 2.9681 | 3.5647 | 3.8786 | 4.5065 | 5.1344 | 0.70494 | 1.9149 | 2.4018 | 2.4018 | 2.4018 | 2.4018 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-06-13 22:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 1.9434 | 2.8032 | 3.3666 | 3.6631 | 4.2562 | 4.8492 | 0.67827 | 1.8425 | 2.3109 | 2.3109 | 2.3109 | 2.3109 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-06-13 23:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.39153 | 0.39153 | 0.39153 | 0.39153 | 0.39153 | 0.39153 | 1.81 | 2.6109 | 3.1356 | 3.4117 | 3.9641 | 4.5164 | 0.63635 | 1.7286 | 2.1681 | 2.1681 | 2.1681 | 2.1681 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-06-14 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.35437 | 0.35437 | 0.35437 | 0.35437 | 0.35437 | 0.35437 | 1.7338 | 2.5009 | 3.0036 | 3.2681 | 3.7972 | 4.3262 | 0.55633 | 1.5112 | 1.8954 | 1.8954 | 1.8954 | 1.8954 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-06-14 01:00 | Winter | 0.57179 | 0.87919 | 1.3304 | 1.3304 | 1.3304 | 1.3304 | 0.36295 | 0.36295 | 0.36295 | 0.36295 | 0.36295 | 0.36295 | 1.6957 | 2.446 | 2.9375 | 3.1963 | 3.7137 | 4.2311 | 0.57157 | 1.5526 | 1.9474 | 1.9474 | 1.9474 | 1.9474 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-06-14 02:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.37152 | 0.37152 | 0.37152 | 0.37152 | 0.37152 | 0.37152 | 1.5622 | 2.2535 | 2.7064 | 2.9447 | 3.4215 | 3.8982 | 0.55252 | 1.5009 | 1.8825 | 1.8825 | 1.8825 | 1.8825 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-06-14 03:00 | Winter | 0.59012 | 0.90737 | 1.373 | 1.373 | 1.373 | 1.373 | 0.36295 | 0.36295 | 0.36295 | 0.36295 | 0.36295 | 0.36295 | 1.5814 | 2.2811 | 2.7395 | 2.9808 | 3.4633 | 3.9459 | 0.51442 | 1.3974 | 1.7526 | 1.7526 | 1.7526 | 1.7526 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-06-14 04:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.36866 | 0.36866 | 0.36866 | 0.36866 | 0.36866 | 0.36866 | 1.5814 | 2.2811 | 2.7395 | 2.9808 | 3.4633 | 3.9459 | 0.53728 | 1.4595 | 1.8305 | 1.8305 | 1.8305 | 1.8305 | 0.80021 | 1.0157 | 1.0157 | 1.0157 | 1.0157 | 1.0157
2020-06-14 05:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.46869 | 0.46869 | 0.46869 | 0.46869 | 0.46869 | 0.46869 | 1.5918 | 2.2961 | 2.7575 | 3.0004 | 3.4861 | 3.9718 | 0.52585 | 1.4284 | 1.7916 | 1.7916 | 1.7916 | 1.7916 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-06-14 06:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 1.7261 | 2.4899 | 2.9903 | 3.2537 | 3.7804 | 4.3071 | 0.59825 | 1.6251 | 2.0382 | 2.0382 | 2.0382 | 2.0382 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-06-14 07:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.49155 | 0.49155 | 0.49155 | 0.49155 | 0.49155 | 0.49155 | 1.7749 | 2.5602 | 3.0748 | 3.3456 | 3.8872 | 4.4288 | 0.56356 | 1.5309 | 1.9201 | 1.9201 | 1.9201 | 1.9201 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-06-14 08:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.51727 | 0.51727 | 0.51727 | 0.51727 | 0.51727 | 0.51727 | 1.9434 | 2.8032 | 3.3666 | 3.6631 | 4.2562 | 4.8492 | 0.64016 | 1.7389 | 2.1811 | 2.1811 | 2.1811 | 2.1811 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-06-14 09:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.57443 | 0.57443 | 0.57443 | 0.57443 | 0.57443 | 0.57443 | 1.9917 | 2.873 | 3.4504 | 3.7542 | 4.362 | 4.9698 | 0.66303 | 1.8011 | 2.2589 | 2.2589 | 2.2589 | 2.2589 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-06-14 10:00 | Winter | 0.57842 | 0.88938 | 1.3458 | 1.3458 | 1.3458 | 1.3458 | 0.56014 | 0.56014 | 0.56014 | 0.56014 | 0.56014 | 0.56014 | 2.0386 | 2.9407 | 3.5316 | 3.8427 | 4.4648 | 5.0869 | 0.67827 | 1.8425 | 2.3109 | 2.3109 | 2.3109 | 2.3109 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-06-14 11:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.52299 | 0.52299 | 0.52299 | 0.52299 | 0.52299 | 0.52299 | 2.0386 | 2.9407 | 3.5316 | 3.8427 | 4.4648 | 5.0869 | 0.59444 | 1.6147 | 2.0253 | 2.0253 | 2.0253 | 2.0253 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-06-14 12:00 | Winter | 0.58665 | 0.90204 | 1.365 | 1.365 | 1.365 | 1.365 | 0.55728 | 0.55728 | 0.55728 | 0.55728 | 0.55728 | 0.55728 | 2.0577 | 2.9681 | 3.5647 | 3.8786 | 4.5065 | 5.1344 | 0.58682 | 1.594 | 1.9993 | 1.9993 | 1.9993 | 1.9993 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-06-14 13:00 | Winter | 0.59049 | 0.90795 | 1.3739 | 1.3739 | 1.3739 | 1.3739 | 0.53728 | 0.53728 | 0.53728 | 0.53728 | 0.53728 | 0.53728 | 2.0386 | 2.9407 | 3.5316 | 3.8427 | 4.4648 | 5.0869 | 0.59444 | 1.6147 | 2.0253 | 2.0253 | 2.0253 | 2.0253 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-06-14 14:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.52623 | 0.52623 | 0.52623 | 0.52623 | 0.52623 | 0.52623 | 2.0577 | 2.9681 | 3.5647 | 3.8786 | 4.5065 | 5.1344 | 0.59063 | 1.6044 | 2.0123 | 2.0123 | 2.0123 | 2.0123 | 0.83861 | 1.0644 | 1.0644 | 1.0644 | 1.0644 | 1.0644
2020-06-14 15:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.5287 | 0.5287 | 0.5287 | 0.5287 | 0.5287 | 0.5287 | 2.0767 | 2.9956 | 3.5977 | 3.9145 | 4.5482 | 5.182 | 0.58682 | 1.594 | 1.9993 | 1.9993 | 1.9993 | 1.9993 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-06-14 16:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.57729 | 0.57729 | 0.57729 | 0.57729 | 0.57729 | 0.57729 | 2.2281 | 3.214 | 3.8599 | 4.1999 | 4.8798 | 5.5597 | 0.62492 | 1.6975 | 2.1291 | 2.1291 | 2.1291 | 2.1291 | 0.95263 | 1.2092 | 1.2092 | 1.2092 | 1.2092 | 1.2092
2020-06-14 17:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.6373 | 0.6373 | 0.6373 | 0.6373 | 0.6373 | 0.6373 | 2.4006 | 3.4628 | 4.1588 | 4.525 | 5.2576 | 5.9902 | 0.67827 | 1.8425 | 2.3109 | 2.3109 | 2.3109 | 2.3109 | 0.93358 | 1.185 | 1.185 | 1.185 | 1.185 | 1.185
2020-06-14 18:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.6373 | 0.6373 | 0.6373 | 0.6373 | 0.6373 | 0.6373 | 2.3614 | 3.4063 | 4.0909 | 4.4512 | 5.1718 | 5.8924 | 0.73543 | 1.9977 | 2.5056 | 2.5056 | 2.5056 | 2.5056 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-06-14 19:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.66017 | 0.66017 | 0.66017 | 0.66017 | 0.66017 | 0.66017 | 2.2673 | 3.2705 | 3.9277 | 4.2736 | 4.9655 | 5.6574 | 0.74686 | 2.0288 | 2.5446 | 2.5446 | 2.5446 | 2.5446 | 0.91428 | 1.1605 | 1.1605 | 1.1605 | 1.1605 | 1.1605
2020-06-14 20:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.58586 | 0.58586 | 0.58586 | 0.58586 | 0.58586 | 0.58586 | 2.2291 | 3.2155 | 3.8617 | 4.2018 | 4.8821 | 5.5623 | 0.69351 | 1.8839 | 2.3628 | 2.3628 | 2.3628 | 2.3628 | 0.91452 | 1.1608 | 1.1608 | 1.1608 | 1.1608 | 1.1608
2020-06-14 21:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 2.191 | 3.1605 | 3.7957 | 4.13 | 4.7986 | 5.4672 | 0.65541 | 1.7803 | 2.233 | 2.233 | 2.233 | 2.233 | 0.93358 | 1.185 | 1.185 | 1.185 | 1.185 | 1.185
2020-06-14 22:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 2.0577 | 2.9681 | 3.5647 | 3.8786 | 4.5065 | 5.1344 | 0.71637 | 1.946 | 2.4407 | 2.4407 | 2.4407 | 2.4407 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-06-14 23:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.43154 | 0.43154 | 0.43154 | 0.43154 | 0.43154 | 0.43154 | 1.8672 | 2.6933 | 3.2346 | 3.5195 | 4.0892 | 4.659 | 0.60206 | 1.6354 | 2.0512 | 2.0512 | 2.0512 | 2.0512 | 0.80034 | 1.0159 | 1.0159 | 1.0159 | 1.0159 | 1.0159
2020-06-15 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 1.7909 | 2.5834 | 3.1026 | 3.3758 | 3.9223 | 4.4688 | 0.55252 | 1.5009 | 1.8825 | 1.8825 | 1.8825 | 1.8825 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-06-15 01:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.38581 | 0.38581 | 0.38581 | 0.38581 | 0.38581 | 0.38581 | 1.7147 | 2.4735 | 2.9705 | 3.2322 | 3.7554 | 4.2787 | 0.62111 | 1.6872 | 2.1161 | 2.1161 | 2.1161 | 2.1161 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-06-15 02:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.50298 | 0.50298 | 0.50298 | 0.50298 | 0.50298 | 0.50298 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.52585 | 1.4284 | 1.7916 | 1.7916 | 1.7916 | 1.7916 | 1.0479 | 1.3301 | 1.3301 | 1.3301 | 1.3301 | 1.3301
2020-06-15 03:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.41439 | 0.41439 | 0.41439 | 0.41439 | 0.41439 | 0.41439 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.52204 | 1.4181 | 1.7786 | 1.7786 | 1.7786 | 1.7786 | 1.0288 | 1.3059 | 1.3059 | 1.3059 | 1.3059 | 1.3059
2020-06-15 04:00 | Winter | 0.66684 | 1.0253 | 1.5515 | 1.5515 | 1.5515 | 1.5515 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.53347 | 1.4491 | 1.8175 | 1.8175 | 1.8175 | 1.8175 | 1.0912 | 1.3851 | 1.3851 | 1.3851 | 1.3851 | 1.3851
2020-06-15 05:00 | Winter | 0.78115 | 1.2011 | 1.8175 | 1.8175 | 1.8175 | 1.8175 | 0.60873 | 0.60873 | 0.60873 | 0.60873 | 0.60873 | 0.60873 | 1.7714 | 2.5552 | 3.0688 | 3.339 | 3.8796 | 4.4201 | 0.63254 | 1.7182 | 2.1551 | 2.1551 | 2.1551 | 2.1551 | 1.4149 | 1.7959 | 1.7959 | 1.7959 | 1.7959 | 1.7959
2020-06-15 06:00 | Winter | 0.90722 | 1.395 | 2.1108 | 2.1108 | 2.1108 | 2.1108 | 0.72018 | 0.72018 | 0.72018 | 0.72018 | 0.72018 | 0.72018 | 2.0196 | 2.9132 | 3.4986 | 3.8068 | 4.4231 | 5.0393 | 0.75829 | 2.0598 | 2.5835 | 2.5835 | 2.5835 | 2.5835 | 1.7528 | 2.2248 | 2.2248 | 2.2248 | 2.2248 | 2.2248
2020-06-15 07:00 | Winter | 1.1298 | 1.7373 | 2.6288 | 2.6288 | 2.6288 | 2.6288 | 0.90019 | 0.90019 | 0.90019 | 0.90019 | 0.90019 | 0.90019 | 2.2093 | 3.1869 | 3.8274 | 4.1644 | 4.8386 | 5.5128 | 0.87261 | 2.3704 | 2.973 | 2.973 | 2.973 | 2.973 | 2.2482 | 2.8536 | 2.8536 | 2.8536 | 2.8536 | 2.8536
2020-06-15 08:00 | Winter | 1.2384 | 1.9042 | 2.8814 | 2.8814 | 2.8814 | 2.8814 | 1.0003 | 1.0003 | 1.0003 | 1.0003 | 1.0003 | 1.0003 | 2.4197 | 3.4903 | 4.1918 | 4.561 | 5.2993 | 6.0377 | 0.87261 | 2.3704 | 2.973 | 2.973 | 2.973 | 2.973 | 2.5278 | 3.2085 | 3.2085 | 3.2085 | 3.2085 | 3.2085
2020-06-15 09:00 | Winter | 1.2575 | 1.9335 | 2.9258 | 2.9258 | 2.9258 | 2.9258 | 1.0117 | 1.0117 | 1.0117 | 1.0117 | 1.0117 | 1.0117 | 2.4959 | 3.6002 | 4.3238 | 4.7046 | 5.4662 | 6.2279 | 0.90309 | 2.4532 | 3.0768 | 3.0768 | 3.0768 | 3.0768 | 2.6864 | 3.4098 | 3.4098 | 3.4098 | 3.4098 | 3.4098
2020-06-15 10:00 | Winter | 1.2194 | 1.8749 | 2.8371 | 2.8371 | 2.8371 | 2.8371 | 0.98061 | 0.98061 | 0.98061 | 0.98061 | 0.98061 | 0.98061 | 2.5149 | 3.6277 | 4.3568 | 4.7405 | 5.508 | 6.2754 | 0.82307 | 2.2358 | 2.8042 | 2.8042 | 2.8042 | 2.8042 | 2.6483 | 3.3614 | 3.3614 | 3.3614 | 3.3614 | 3.3614
2020-06-15 11:00 | Winter | 1.1813 | 1.8163 | 2.7485 | 2.7485 | 2.7485 | 2.7485 | 1.0174 | 1.0174 | 1.0174 | 1.0174 | 1.0174 | 1.0174 | 2.4387 | 3.5178 | 4.2248 | 4.5969 | 5.3411 | 6.0852 | 0.80402 | 2.184 | 2.7393 | 2.7393 | 2.7393 | 2.7393 | 2.5721 | 3.2647 | 3.2647 | 3.2647 | 3.2647 | 3.2647
2020-06-15 12:00 | Winter | 1.1813 | 1.8163 | 2.7485 | 2.7485 | 2.7485 | 2.7485 | 0.95739 | 0.95739 | 0.95739 | 0.95739 | 0.95739 | 0.95739 | 2.4959 | 3.6002 | 4.3238 | 4.7046 | 5.4662 | 6.2279 | 0.78496 | 2.1323 | 2.6744 | 2.6744 | 2.6744 | 2.6744 | 2.4959 | 3.168 | 3.168 | 3.168 | 3.168 | 3.168
2020-06-15 13:00 | Winter | 1.1813 | 1.8163 | 2.7485 | 2.7485 | 2.7485 | 2.7485 | 0.93738 | 0.93738 | 0.93738 | 0.93738 | 0.93738 | 0.93738 | 2.4197 | 3.4903 | 4.1918 | 4.561 | 5.2993 | 6.0377 | 0.76591 | 2.0805 | 2.6095 | 2.6095 | 2.6095 | 2.6095 | 2.4197 | 3.0712 | 3.0712 | 3.0712 | 3.0712 | 3.0712
2020-06-15 14:00 | Winter | 1.2003 | 1.8456 | 2.7928 | 2.7928 | 2.7928 | 2.7928 | 0.91738 | 0.91738 | 0.91738 | 0.91738 | 0.91738 | 0.91738 | 2.4006 | 3.4628 | 4.1588 | 4.525 | 5.2576 | 5.9902 | 0.80021 | 2.1737 | 2.7263 | 2.7263 | 2.7263 | 2.7263 | 2.3244 | 2.9503 | 2.9503 | 2.9503 | 2.9503 | 2.9503
2020-06-15 15:00 | Winter | 1.1432 | 1.7577 | 2.6598 | 2.6598 | 2.6598 | 2.6598 | 0.91738 | 0.91738 | 0.91738 | 0.91738 | 0.91738 | 0.91738 | 2.3435 | 3.3804 | 4.0597 | 4.4173 | 5.1324 | 5.8475 | 0.78115 | 2.1219 | 2.6614 | 2.6614 | 2.6614 | 2.6614 | 2.2482 | 2.8536 | 2.8536 | 2.8536 | 2.8536 | 2.8536
2020-06-15 16:00 | Winter | 1.1268 | 1.7326 | 2.6218 | 2.6218 | 2.6218 | 2.6218 | 0.90309 | 0.90309 | 0.90309 | 0.90309 | 0.90309 | 0.90309 | 2.3244 | 3.3529 | 4.0267 | 4.3814 | 5.0907 | 5.8 | 0.76591 | 2.0805 | 2.6095 | 2.6095 | 2.6095 | 2.6095 | 2.2482 | 2.8536 | 2.8536 | 2.8536 | 2.8536 | 2.8536
2020-06-15 17:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 0.85165 | 0.85165 | 0.85165 | 0.85165 | 0.85165 | 0.85165 | 2.4959 | 3.6002 | 4.3238 | 4.7046 | 5.4662 | 6.2279 | 0.76972 | 2.0909 | 2.6225 | 2.6225 | 2.6225 | 2.6225 | 2.172 | 2.7569 | 2.7569 | 2.7569 | 2.7569 | 2.7569
2020-06-15 18:00 | Winter | 0.80737 | 1.2414 | 1.8785 | 1.8785 | 1.8785 | 1.8785 | 0.78306 | 0.78306 | 0.78306 | 0.78306 | 0.78306 | 0.78306 | 2.4578 | 3.5453 | 4.2578 | 4.6328 | 5.3828 | 6.1328 | 0.77353 | 2.1012 | 2.6354 | 2.6354 | 2.6354 | 2.6354 | 1.6585 | 2.1051 | 2.1051 | 2.1051 | 2.1051 | 2.1051
2020-06-15 19:00 | Winter | 0.70494 | 1.0839 | 1.6402 | 1.6402 | 1.6402 | 1.6402 | 0.56872 | 0.56872 | 0.56872 | 0.56872 | 0.56872 | 0.56872 | 2.3244 | 3.3529 | 4.0267 | 4.3814 | 5.0907 | 5.8 | 0.76591 | 2.0805 | 2.6095 | 2.6095 | 2.6095 | 2.6095 | 1.1432 | 1.451 | 1.451 | 1.451 | 1.451 | 1.451
2020-06-15 20:00 | Winter | 0.66684 | 1.0253 | 1.5515 | 1.5515 | 1.5515 | 1.5515 | 0.43154 | 0.43154 | 0.43154 | 0.43154 | 0.43154 | 0.43154 | 2.3054 | 3.3254 | 3.9937 | 4.3455 | 5.049 | 5.7525 | 0.70494 | 1.9149 | 2.4018 | 2.4018 | 2.4018 | 2.4018 | 1.105 | 1.4026 | 1.4026 | 1.4026 | 1.4026 | 1.4026
2020-06-15 21:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.38295 | 0.38295 | 0.38295 | 0.38295 | 0.38295 | 0.38295 | 2.172 | 3.133 | 3.7627 | 4.0941 | 4.7569 | 5.4197 | 0.64397 | 1.7493 | 2.194 | 2.194 | 2.194 | 2.194 | 0.97168 | 1.2333 | 1.2333 | 1.2333 | 1.2333 | 1.2333
2020-06-15 22:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.37724 | 0.37724 | 0.37724 | 0.37724 | 0.37724 | 0.37724 | 2.0005 | 2.8857 | 3.4656 | 3.7709 | 4.3813 | 4.9918 | 0.6516 | 1.77 | 2.22 | 2.22 | 2.22 | 2.22 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-06-15 23:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.36581 | 0.36581 | 0.36581 | 0.36581 | 0.36581 | 0.36581 | 1.7909 | 2.5834 | 3.1026 | 3.3758 | 3.9223 | 4.4688 | 0.62111 | 1.6872 | 2.1161 | 2.1161 | 2.1161 | 2.1161 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-06-16 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.35723 | 0.35723 | 0.35723 | 0.35723 | 0.35723 | 0.35723 | 1.6766 | 2.4185 | 2.9045 | 3.1603 | 3.672 | 4.1836 | 0.54871 | 1.4905 | 1.8695 | 1.8695 | 1.8695 | 1.8695 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-06-16 01:00 | Winter | 0.55004 | 0.84575 | 1.2798 | 1.2798 | 1.2798 | 1.2798 | 0.36581 | 0.36581 | 0.36581 | 0.36581 | 0.36581 | 0.36581 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.52204 | 1.4181 | 1.7786 | 1.7786 | 1.7786 | 1.7786 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-06-16 02:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.37438 | 0.37438 | 0.37438 | 0.37438 | 0.37438 | 0.37438 | 1.6004 | 2.3086 | 2.7725 | 3.0167 | 3.5051 | 3.9934 | 0.54871 | 1.4905 | 1.8695 | 1.8695 | 1.8695 | 1.8695 | 1.0288 | 1.3059 | 1.3059 | 1.3059 | 1.3059 | 1.3059
2020-06-16 03:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.36295 | 0.36295 | 0.36295 | 0.36295 | 0.36295 | 0.36295 | 1.5814 | 2.2811 | 2.7395 | 2.9808 | 3.4633 | 3.9459 | 0.51442 | 1.3974 | 1.7526 | 1.7526 | 1.7526 | 1.7526 | 1.0099 | 1.2819 | 1.2819 | 1.2819 | 1.2819 | 1.2819
2020-06-16 04:00 | Winter | 0.60963 | 0.93738 | 1.4184 | 1.4184 | 1.4184 | 1.4184 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 1.5997 | 2.3075 | 2.7712 | 3.0153 | 3.5034 | 3.9916 | 0.60968 | 1.6561 | 2.0772 | 2.0772 | 2.0772 | 2.0772 | 1.0288 | 1.3059 | 1.3059 | 1.3059 | 1.3059 | 1.3059
2020-06-16 05:00 | Winter | 0.64779 | 0.99605 | 1.5072 | 1.5072 | 1.5072 | 1.5072 | 0.54299 | 0.54299 | 0.54299 | 0.54299 | 0.54299 | 0.54299 | 1.6762 | 2.4178 | 2.9038 | 3.1595 | 3.671 | 4.1825 | 0.60206 | 1.6354 | 2.0512 | 2.0512 | 2.0512 | 2.0512 | 1.3735 | 1.7433 | 1.7433 | 1.7433 | 1.7433 | 1.7433
2020-06-16 06:00 | Winter | 0.74271 | 1.142 | 1.7281 | 1.7281 | 1.7281 | 1.7281 | 0.68017 | 0.68017 | 0.68017 | 0.68017 | 0.68017 | 0.68017 | 2.0174 | 2.91 | 3.4948 | 3.8026 | 4.4182 | 5.0338 | 0.7621 | 2.0702 | 2.5965 | 2.5965 | 2.5965 | 2.5965 | 1.8244 | 2.3156 | 2.3156 | 2.3156 | 2.3156 | 2.3156
2020-06-16 07:00 | Winter | 1.086 | 1.6698 | 2.5268 | 2.5268 | 2.5268 | 2.5268 | 0.82592 | 0.82592 | 0.82592 | 0.82592 | 0.82592 | 0.82592 | 2.3435 | 3.3804 | 4.0597 | 4.4173 | 5.1324 | 5.8475 | 0.85355 | 2.3186 | 2.9081 | 2.9081 | 2.9081 | 2.9081 | 2.1716 | 2.7563 | 2.7563 | 2.7563 | 2.7563 | 2.7563
2020-06-16 08:00 | Winter | 1.2003 | 1.8456 | 2.7928 | 2.7928 | 2.7928 | 2.7928 | 0.96596 | 0.96596 | 0.96596 | 0.96596 | 0.96596 | 0.96596 | 2.4768 | 3.5728 | 4.2908 | 4.6687 | 5.4245 | 6.1803 | 0.94501 | 2.567 | 3.2196 | 3.2196 | 3.2196 | 3.2196 | 2.4387 | 3.0954 | 3.0954 | 3.0954 | 3.0954 | 3.0954
2020-06-16 09:00 | Winter | 1.2003 | 1.8456 | 2.7928 | 2.7928 | 2.7928 | 2.7928 | 1.0031 | 1.0031 | 1.0031 | 1.0031 | 1.0031 | 1.0031 | 2.4197 | 3.4903 | 4.1918 | 4.561 | 5.2993 | 6.0377 | 0.92976 | 2.5256 | 3.1677 | 3.1677 | 3.1677 | 3.1677 | 2.4768 | 3.1438 | 3.1438 | 3.1438 | 3.1438 | 3.1438
2020-06-16 10:00 | Winter | 1.1813 | 1.8163 | 2.7485 | 2.7485 | 2.7485 | 2.7485 | 1.0031 | 1.0031 | 1.0031 | 1.0031 | 1.0031 | 1.0031 | 2.4959 | 3.6002 | 4.3238 | 4.7046 | 5.4662 | 6.2279 | 0.93357 | 2.536 | 3.1807 | 3.1807 | 3.1807 | 3.1807 | 2.4768 | 3.1438 | 3.1438 | 3.1438 | 3.1438 | 3.1438
2020-06-16 11:00 | Winter | 1.1813 | 1.8163 | 2.7485 | 2.7485 | 2.7485 | 2.7485 | 0.98311 | 0.98311 | 0.98311 | 0.98311 | 0.98311 | 0.98311 | 2.4387 | 3.5178 | 4.2248 | 4.5969 | 5.3411 | 6.0852 | 0.7964 | 2.1633 | 2.7133 | 2.7133 | 2.7133 | 2.7133 | 2.3625 | 2.9987 | 2.9987 | 2.9987 | 2.9987 | 2.9987
2020-06-16 12:00 | Winter | 1.2003 | 1.8456 | 2.7928 | 2.7928 | 2.7928 | 2.7928 | 0.96025 | 0.96025 | 0.96025 | 0.96025 | 0.96025 | 0.96025 | 2.4959 | 3.6002 | 4.3238 | 4.7046 | 5.4662 | 6.2279 | 0.84593 | 2.2979 | 2.8821 | 2.8821 | 2.8821 | 2.8821 | 2.4197 | 3.0712 | 3.0712 | 3.0712 | 3.0712 | 3.0712
2020-06-16 13:00 | Winter | 1.1622 | 1.787 | 2.7041 | 2.7041 | 2.7041 | 2.7041 | 1.166 | 1.166 | 1.166 | 1.166 | 1.166 | 1.166 | 2.4768 | 3.5728 | 4.2908 | 4.6687 | 5.4245 | 6.1803 | 0.81545 | 2.2151 | 2.7782 | 2.7782 | 2.7782 | 2.7782 | 2.3435 | 2.9745 | 2.9745 | 2.9745 | 2.9745 | 2.9745
2020-06-16 14:00 | Winter | 1.1813 | 1.8163 | 2.7485 | 2.7485 | 2.7485 | 2.7485 | 0.92023 | 0.92023 | 0.92023 | 0.92023 | 0.92023 | 0.92023 | 2.4762 | 3.5718 | 4.2896 | 4.6675 | 5.4231 | 6.1787 | 0.83831 | 2.2772 | 2.8561 | 2.8561 | 2.8561 | 2.8561 | 2.3054 | 2.9261 | 2.9261 | 2.9261 | 2.9261 | 2.9261
2020-06-16 15:00 | Winter | 1.105 | 1.6991 | 2.5711 | 2.5711 | 2.5711 | 2.5711 | 0.96882 | 0.96882 | 0.96882 | 0.96882 | 0.96882 | 0.96882 | 2.3054 | 3.3254 | 3.9937 | 4.3455 | 5.049 | 5.7525 | 0.78496 | 2.1323 | 2.6744 | 2.6744 | 2.6744 | 2.6744 | 2.1148 | 2.6843 | 2.6843 | 2.6843 | 2.6843 | 2.6843
2020-06-16 16:00 | Winter | 1.105 | 1.6991 | 2.5711 | 2.5711 | 2.5711 | 2.5711 | 0.96882 | 0.96882 | 0.96882 | 0.96882 | 0.96882 | 0.96882 | 2.3816 | 3.4353 | 4.1258 | 4.4891 | 5.2159 | 5.9426 | 0.79258 | 2.153 | 2.7003 | 2.7003 | 2.7003 | 2.7003 | 2.0767 | 2.6359 | 2.6359 | 2.6359 | 2.6359 | 2.6359
2020-06-16 17:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 0.89166 | 0.89166 | 0.89166 | 0.89166 | 0.89166 | 0.89166 | 2.4387 | 3.5178 | 4.2248 | 4.5969 | 5.3411 | 6.0852 | 0.81164 | 2.2047 | 2.7653 | 2.7653 | 2.7653 | 2.7653 | 2.1339 | 2.7085 | 2.7085 | 2.7085 | 2.7085 | 2.7085
2020-06-16 18:00 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.81449 | 0.81449 | 0.81449 | 0.81449 | 0.81449 | 0.81449 | 2.4197 | 3.4903 | 4.1918 | 4.561 | 5.2993 | 6.0377 | 0.76972 | 2.0909 | 2.6225 | 2.6225 | 2.6225 | 2.6225 | 1.5884 | 2.0161 | 2.0161 | 2.0161 | 2.0161 | 2.0161
2020-06-16 19:00 | Winter | 0.63246 | 0.97247 | 1.4715 | 1.4715 | 1.4715 | 1.4715 | 0.54255 | 0.54255 | 0.54255 | 0.54255 | 0.54255 | 0.54255 | 2.2673 | 3.2705 | 3.9277 | 4.2736 | 4.9655 | 5.6574 | 0.73543 | 1.9977 | 2.5056 | 2.5056 | 2.5056 | 2.5056 | 1.105 | 1.4026 | 1.4026 | 1.4026 | 1.4026 | 1.4026
2020-06-16 20:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.5087 | 0.5087 | 0.5087 | 0.5087 | 0.5087 | 0.5087 | 2.191 | 3.1605 | 3.7957 | 4.13 | 4.7986 | 5.4672 | 0.73924 | 2.0081 | 2.5186 | 2.5186 | 2.5186 | 2.5186 | 1.0288 | 1.3059 | 1.3059 | 1.3059 | 1.3059 | 1.3059
2020-06-16 21:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.38938 | 0.38938 | 0.38938 | 0.38938 | 0.38938 | 0.38938 | 2.0767 | 2.9956 | 3.5977 | 3.9145 | 4.5482 | 5.182 | 0.69732 | 1.8942 | 2.3758 | 2.3758 | 2.3758 | 2.3758 | 0.99073 | 1.2575 | 1.2575 | 1.2575 | 1.2575 | 1.2575
2020-06-16 22:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.4544 | 0.4544 | 0.4544 | 0.4544 | 0.4544 | 0.4544 | 1.9154 | 2.7628 | 3.3181 | 3.6103 | 4.1948 | 4.7793 | 0.64016 | 1.7389 | 2.1811 | 2.1811 | 2.1811 | 2.1811 | 0.91452 | 1.1608 | 1.1608 | 1.1608 | 1.1608 | 1.1608
2020-06-16 23:00 | Winter | 0.55838 | 0.85858 | 1.2992 | 1.2992 | 1.2992 | 1.2992 | 0.40296 | 0.40296 | 0.40296 | 0.40296 | 0.40296 | 0.40296 | 1.7338 | 2.5009 | 3.0036 | 3.2681 | 3.7972 | 4.3262 | 0.62111 | 1.6872 | 2.1161 | 2.1161 | 2.1161 | 2.1161 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-06-17 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.39724 | 0.39724 | 0.39724 | 0.39724 | 0.39724 | 0.39724 | 1.6586 | 2.3924 | 2.8732 | 3.1263 | 3.6324 | 4.1385 | 0.55633 | 1.5112 | 1.8954 | 1.8954 | 1.8954 | 1.8954 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-06-17 01:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.42187 | 0.42187 | 0.42187 | 0.42187 | 0.42187 | 0.42187 | 1.5816 | 2.2814 | 2.7399 | 2.9812 | 3.4638 | 3.9465 | 0.52966 | 1.4388 | 1.8046 | 1.8046 | 1.8046 | 1.8046 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-06-17 02:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.48584 | 0.48584 | 0.48584 | 0.48584 | 0.48584 | 0.48584 | 1.5245 | 2.1991 | 2.641 | 2.8736 | 3.3388 | 3.804 | 0.53347 | 1.4491 | 1.8175 | 1.8175 | 1.8175 | 1.8175 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-06-17 03:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 1.5623 | 2.2536 | 2.7065 | 2.9449 | 3.4216 | 3.8984 | 0.56395 | 1.5319 | 1.9214 | 1.9214 | 1.9214 | 1.9214 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-06-17 04:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.48012 | 0.48012 | 0.48012 | 0.48012 | 0.48012 | 0.48012 | 1.5814 | 2.2811 | 2.7395 | 2.9808 | 3.4633 | 3.9459 | 0.59444 | 1.6147 | 2.0253 | 2.0253 | 2.0253 | 2.0253 | 1.086 | 1.3784 | 1.3784 | 1.3784 | 1.3784 | 1.3784
2020-06-17 05:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.65159 | 0.65159 | 0.65159 | 0.65159 | 0.65159 | 0.65159 | 1.6828 | 2.4274 | 2.9152 | 3.172 | 3.6855 | 4.199 | 0.69058 | 1.8759 | 2.3528 | 2.3528 | 2.3528 | 2.3528 | 1.4971 | 1.9002 | 1.9002 | 1.9002 | 1.9002 | 1.9002
2020-06-17 06:00 | Winter | 0.72155 | 1.1095 | 1.6788 | 1.6788 | 1.6788 | 1.6788 | 0.7802 | 0.7802 | 0.7802 | 0.7802 | 0.7802 | 0.7802 | 1.9434 | 2.8032 | 3.3666 | 3.6631 | 4.2562 | 4.8492 | 0.80402 | 2.184 | 2.7393 | 2.7393 | 2.7393 | 2.7393 | 1.8231 | 2.3141 | 2.3141 | 2.3141 | 2.3141 | 2.3141
2020-06-17 07:00 | Winter | 1.0608 | 1.6311 | 2.4682 | 2.4682 | 2.4682 | 2.4682 | 0.90595 | 0.90595 | 0.90595 | 0.90595 | 0.90595 | 0.90595 | 2.3244 | 3.3529 | 4.0267 | 4.3814 | 5.0907 | 5.8 | 0.86498 | 2.3496 | 2.947 | 2.947 | 2.947 | 2.947 | 2.3054 | 2.9261 | 2.9261 | 2.9261 | 2.9261 | 2.9261
2020-06-17 08:00 | Winter | 1.2194 | 1.8749 | 2.8371 | 2.8371 | 2.8371 | 2.8371 | 0.99454 | 0.99454 | 0.99454 | 0.99454 | 0.99454 | 0.99454 | 2.4183 | 3.4884 | 4.1894 | 4.5584 | 5.2964 | 6.0344 | 0.93357 | 2.536 | 3.1807 | 3.1807 | 3.1807 | 3.1807 | 2.534 | 3.2163 | 3.2163 | 3.2163 | 3.2163 | 3.2163
2020-06-17 09:00 | Winter | 1.2575 | 1.9335 | 2.9258 | 2.9258 | 2.9258 | 2.9258 | 1.0031 | 1.0031 | 1.0031 | 1.0031 | 1.0031 | 1.0031 | 2.5149 | 3.6277 | 4.3568 | 4.7405 | 5.508 | 6.2754 | 0.9075 | 2.4651 | 3.0919 | 3.0919 | 3.0919 | 3.0919 | 2.5149 | 3.1922 | 3.1922 | 3.1922 | 3.1922 | 3.1922
2020-06-17 10:00 | Winter | 1.1813 | 1.8163 | 2.7485 | 2.7485 | 2.7485 | 2.7485 | 1.0003 | 1.0003 | 1.0003 | 1.0003 | 1.0003 | 1.0003 | 2.6102 | 3.7651 | 4.5218 | 4.9201 | 5.7166 | 6.5131 | 0.88785 | 2.4118 | 3.0249 | 3.0249 | 3.0249 | 3.0249 | 2.4768 | 3.1438 | 3.1438 | 3.1438 | 3.1438 | 3.1438
2020-06-17 11:00 | Winter | 1.1241 | 1.7284 | 2.6155 | 2.6155 | 2.6155 | 2.6155 | 0.97453 | 0.97453 | 0.97453 | 0.97453 | 0.97453 | 0.97453 | 2.4959 | 3.6002 | 4.3238 | 4.7046 | 5.4662 | 6.2279 | 0.8345 | 2.2668 | 2.8432 | 2.8432 | 2.8432 | 2.8432 | 2.4387 | 3.0954 | 3.0954 | 3.0954 | 3.0954 | 3.0954
2020-06-17 12:00 | Winter | 1.1622 | 1.787 | 2.7041 | 2.7041 | 2.7041 | 2.7041 | 0.94881 | 0.94881 | 0.94881 | 0.94881 | 0.94881 | 0.94881 | 2.4959 | 3.6002 | 4.3238 | 4.7046 | 5.4662 | 6.2279 | 0.83069 | 2.2565 | 2.8302 | 2.8302 | 2.8302 | 2.8302 | 2.4006 | 3.0471 | 3.0471 | 3.0471 | 3.0471 | 3.0471
2020-06-17 13:00 | Winter | 1.1622 | 1.787 | 2.7041 | 2.7041 | 2.7041 | 2.7041 | 1.0546 | 1.0546 | 1.0546 | 1.0546 | 1.0546 | 1.0546 | 2.5149 | 3.6277 | 4.3568 | 4.7405 | 5.508 | 6.2754 | 0.83831 | 2.2772 | 2.8561 | 2.8561 | 2.8561 | 2.8561 | 2.3054 | 2.9261 | 2.9261 | 2.9261 | 2.9261 | 2.9261
2020-06-17 14:00 | Winter | 1.1241 | 1.7284 | 2.6155 | 2.6155 | 2.6155 | 2.6155 | 0.98597 | 0.98597 | 0.98597 | 0.98597 | 0.98597 | 0.98597 | 2.4014 | 3.464 | 4.1601 | 4.5265 | 5.2593 | 5.9921 | 0.83831 | 2.2772 | 2.8561 | 2.8561 | 2.8561 | 2.8561 | 2.2863 | 2.902 | 2.902 | 2.902 | 2.902 | 2.902
2020-06-17 15:00 | Winter | 1.086 | 1.6698 | 2.5268 | 2.5268 | 2.5268 | 2.5268 | 0.86022 | 0.86022 | 0.86022 | 0.86022 | 0.86022 | 0.86022 | 2.3816 | 3.4353 | 4.1258 | 4.4891 | 5.2159 | 5.9426 | 0.83069 | 2.2565 | 2.8302 | 2.8302 | 2.8302 | 2.8302 | 2.2101 | 2.8052 | 2.8052 | 2.8052 | 2.8052 | 2.8052
2020-06-17 16:00 | Winter | 1.0669 | 1.6405 | 2.4825 | 2.4825 | 2.4825 | 2.4825 | 0.86879 | 0.86879 | 0.86879 | 0.86879 | 0.86879 | 0.86879 | 2.3625 | 3.4079 | 4.0927 | 4.4532 | 5.1741 | 5.8951 | 0.82688 | 2.2461 | 2.8172 | 2.8172 | 2.8172 | 2.8172 | 2.191 | 2.781 | 2.781 | 2.781 | 2.781 | 2.781
2020-06-17 17:00 | Winter | 1.0162 | 1.5625 | 2.3644 | 2.3644 | 2.3644 | 2.3644 | 0.90595 | 0.90595 | 0.90595 | 0.90595 | 0.90595 | 0.90595 | 2.4959 | 3.6002 | 4.3238 | 4.7046 | 5.4662 | 6.2279 | 0.7964 | 2.1633 | 2.7133 | 2.7133 | 2.7133 | 2.7133 | 2.0958 | 2.6601 | 2.6601 | 2.6601 | 2.6601 | 2.6601
2020-06-17 18:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.81449 | 0.81449 | 0.81449 | 0.81449 | 0.81449 | 0.81449 | 2.5149 | 3.6277 | 4.3568 | 4.7405 | 5.508 | 6.2754 | 0.80402 | 2.184 | 2.7393 | 2.7393 | 2.7393 | 2.7393 | 1.5972 | 2.0273 | 2.0273 | 2.0273 | 2.0273 | 2.0273
2020-06-17 19:00 | Winter | 0.66684 | 1.0253 | 1.5515 | 1.5515 | 1.5515 | 1.5515 | 0.62587 | 0.62587 | 0.62587 | 0.62587 | 0.62587 | 0.62587 | 2.2863 | 3.2979 | 3.9607 | 4.3096 | 5.0072 | 5.7049 | 0.75448 | 2.0495 | 2.5705 | 2.5705 | 2.5705 | 2.5705 | 1.1815 | 1.4997 | 1.4997 | 1.4997 | 1.4997 | 1.4997
2020-06-17 20:00 | Winter | 0.66684 | 1.0253 | 1.5515 | 1.5515 | 1.5515 | 1.5515 | 0.55728 | 0.55728 | 0.55728 | 0.55728 | 0.55728 | 0.55728 | 2.1915 | 3.1612 | 3.7965 | 4.1309 | 4.7996 | 5.4684 | 0.73924 | 2.0081 | 2.5186 | 2.5186 | 2.5186 | 2.5186 | 1.086 | 1.3784 | 1.3784 | 1.3784 | 1.3784 | 1.3784
2020-06-17 21:00 | Winter | 0.57233 | 0.88003 | 1.3317 | 1.3317 | 1.3317 | 1.3317 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 2.1148 | 3.0506 | 3.6637 | 3.9863 | 4.6317 | 5.277 | 0.70494 | 1.9149 | 2.4018 | 2.4018 | 2.4018 | 2.4018 | 0.95942 | 1.2178 | 1.2178 | 1.2178 | 1.2178 | 1.2178
2020-06-17 22:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 1.9815 | 2.8582 | 3.4326 | 3.735 | 4.3396 | 4.9443 | 0.69351 | 1.8839 | 2.3628 | 2.3628 | 2.3628 | 2.3628 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-06-17 23:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.41439 | 0.41439 | 0.41439 | 0.41439 | 0.41439 | 0.41439 | 1.81 | 2.6109 | 3.1356 | 3.4117 | 3.9641 | 4.5164 | 0.62492 | 1.6975 | 2.1291 | 2.1291 | 2.1291 | 2.1291 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-06-18 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 1.715 | 2.4738 | 2.971 | 3.2327 | 3.756 | 4.2793 | 0.58682 | 1.594 | 1.9993 | 1.9993 | 1.9993 | 1.9993 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-06-18 01:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.37152 | 0.37152 | 0.37152 | 0.37152 | 0.37152 | 0.37152 | 1.6195 | 2.336 | 2.8055 | 3.0526 | 3.5468 | 4.041 | 0.54871 | 1.4905 | 1.8695 | 1.8695 | 1.8695 | 1.8695 | 0.83278 | 1.057 | 1.057 | 1.057 | 1.057 | 1.057
2020-06-18 02:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 1.6195 | 2.336 | 2.8055 | 3.0526 | 3.5468 | 4.041 | 0.52585 | 1.4284 | 1.7916 | 1.7916 | 1.7916 | 1.7916 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-06-18 03:00 | Winter | 0.59353 | 0.91262 | 1.381 | 1.381 | 1.381 | 1.381 | 0.3925 | 0.3925 | 0.3925 | 0.3925 | 0.3925 | 0.3925 | 1.5814 | 2.2811 | 2.7395 | 2.9808 | 3.4633 | 3.9459 | 0.55633 | 1.5112 | 1.8954 | 1.8954 | 1.8954 | 1.8954 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-06-18 04:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 1.6328 | 2.3553 | 2.8286 | 3.0778 | 3.576 | 4.0743 | 0.60206 | 1.6354 | 2.0512 | 2.0512 | 2.0512 | 2.0512 | 1.0479 | 1.3301 | 1.3301 | 1.3301 | 1.3301 | 1.3301
2020-06-18 05:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.563 | 0.563 | 0.563 | 0.563 | 0.563 | 0.563 | 1.712 | 2.4695 | 2.9658 | 3.227 | 3.7495 | 4.2719 | 0.63521 | 1.7255 | 2.1642 | 2.1642 | 2.1642 | 2.1642 | 1.409 | 1.7884 | 1.7884 | 1.7884 | 1.7884 | 1.7884
2020-06-18 06:00 | Winter | 0.66306 | 1.0195 | 1.5427 | 1.5427 | 1.5427 | 1.5427 | 0.6916 | 0.6916 | 0.6916 | 0.6916 | 0.6916 | 0.6916 | 2.0583 | 2.969 | 3.5657 | 3.8798 | 4.5078 | 5.1359 | 0.724 | 1.9667 | 2.4667 | 2.4667 | 2.4667 | 2.4667 | 1.6752 | 2.1263 | 2.1263 | 2.1263 | 2.1263 | 2.1263
2020-06-18 07:00 | Winter | 1.122 | 1.7253 | 2.6107 | 2.6107 | 2.6107 | 2.6107 | 0.79163 | 0.79163 | 0.79163 | 0.79163 | 0.79163 | 0.79163 | 2.4006 | 3.4628 | 4.1588 | 4.525 | 5.2576 | 5.9902 | 0.89166 | 2.4221 | 3.0379 | 3.0379 | 3.0379 | 3.0379 | 2.1529 | 2.7327 | 2.7327 | 2.7327 | 2.7327 | 2.7327
2020-06-18 08:00 | Winter | 1.2384 | 1.9042 | 2.8814 | 2.8814 | 2.8814 | 2.8814 | 0.92309 | 0.92309 | 0.92309 | 0.92309 | 0.92309 | 0.92309 | 2.4578 | 3.5453 | 4.2578 | 4.6328 | 5.3828 | 6.1328 | 0.95644 | 2.5981 | 3.2586 | 3.2586 | 3.2586 | 3.2586 | 2.3625 | 2.9987 | 2.9987 | 2.9987 | 2.9987 | 2.9987
2020-06-18 09:00 | Winter | 1.2194 | 1.8749 | 2.8371 | 2.8371 | 2.8371 | 2.8371 | 0.95739 | 0.95739 | 0.95739 | 0.95739 | 0.95739 | 0.95739 | 2.4959 | 3.6002 | 4.3238 | 4.7046 | 5.4662 | 6.2279 | 0.92214 | 2.5049 | 3.1418 | 3.1418 | 3.1418 | 3.1418 | 2.4768 | 3.1438 | 3.1438 | 3.1438 | 3.1438 | 3.1438
2020-06-18 10:00 | Winter | 1.2003 | 1.8456 | 2.7928 | 2.7928 | 2.7928 | 2.7928 | 0.97739 | 0.97739 | 0.97739 | 0.97739 | 0.97739 | 0.97739 | 2.553 | 3.6827 | 4.4228 | 4.8123 | 5.5914 | 6.3705 | 0.84974 | 2.3082 | 2.8951 | 2.8951 | 2.8951 | 2.8951 | 2.4197 | 3.0712 | 3.0712 | 3.0712 | 3.0712 | 3.0712
2020-06-18 11:00 | Winter | 1.2003 | 1.8456 | 2.7928 | 2.7928 | 2.7928 | 2.7928 | 0.93738 | 0.93738 | 0.93738 | 0.93738 | 0.93738 | 0.93738 | 2.4387 | 3.5178 | 4.2248 | 4.5969 | 5.3411 | 6.0852 | 0.86117 | 2.3393 | 2.934 | 2.934 | 2.934 | 2.934 | 2.4387 | 3.0954 | 3.0954 | 3.0954 | 3.0954 | 3.0954
2020-06-18 12:00 | Winter | 1.1813 | 1.8163 | 2.7485 | 2.7485 | 2.7485 | 2.7485 | 0.94024 | 0.94024 | 0.94024 | 0.94024 | 0.94024 | 0.94024 | 2.4387 | 3.5178 | 4.2248 | 4.5969 | 5.3411 | 6.0852 | 0.77734 | 2.1116 | 2.6484 | 2.6484 | 2.6484 | 2.6484 | 2.2893 | 2.9057 | 2.9057 | 2.9057 | 2.9057 | 2.9057
2020-06-18 13:00 | Winter | 1.1813 | 1.8163 | 2.7485 | 2.7485 | 2.7485 | 2.7485 | 0.87737 | 0.87737 | 0.87737 | 0.87737 | 0.87737 | 0.87737 | 2.4578 | 3.5453 | 4.2578 | 4.6328 | 5.3828 | 6.1328 | 0.79258 | 2.153 | 2.7003 | 2.7003 | 2.7003 | 2.7003 | 2.2673 | 2.8778 | 2.8778 | 2.8778 | 2.8778 | 2.8778
2020-06-18 14:00 | Winter | 1.1625 | 1.7875 | 2.7048 | 2.7048 | 2.7048 | 2.7048 | 0.89737 | 0.89737 | 0.89737 | 0.89737 | 0.89737 | 0.89737 | 2.4768 | 3.5728 | 4.2908 | 4.6687 | 5.4245 | 6.1803 | 0.95263 | 2.5877 | 3.2456 | 3.2456 | 3.2456 | 3.2456 | 2.2291 | 2.8294 | 2.8294 | 2.8294 | 2.8294 | 2.8294
2020-06-18 15:00 | Winter | 1.1432 | 1.7577 | 2.6598 | 2.6598 | 2.6598 | 2.6598 | 0.89166 | 0.89166 | 0.89166 | 0.89166 | 0.89166 | 0.89166 | 2.3054 | 3.3254 | 3.9937 | 4.3455 | 5.049 | 5.7525 | 0.9069 | 2.4635 | 3.0898 | 3.0898 | 3.0898 | 3.0898 | 2.191 | 2.781 | 2.781 | 2.781 | 2.781 | 2.781
2020-06-18 16:00 | Winter | 1.1241 | 1.7284 | 2.6155 | 2.6155 | 2.6155 | 2.6155 | 0.93452 | 0.93452 | 0.93452 | 0.93452 | 0.93452 | 0.93452 | 2.3004 | 3.3182 | 3.9851 | 4.3361 | 5.0381 | 5.74 | 0.80783 | 2.1944 | 2.7523 | 2.7523 | 2.7523 | 2.7523 | 2.0767 | 2.6359 | 2.6359 | 2.6359 | 2.6359 | 2.6359
2020-06-18 17:00 | Winter | 1.0102 | 1.5533 | 2.3504 | 2.3504 | 2.3504 | 2.3504 | 0.90023 | 0.90023 | 0.90023 | 0.90023 | 0.90023 | 0.90023 | 2.4768 | 3.5728 | 4.2908 | 4.6687 | 5.4245 | 6.1803 | 0.8345 | 2.2668 | 2.8432 | 2.8432 | 2.8432 | 2.8432 | 2.0386 | 2.5876 | 2.5876 | 2.5876 | 2.5876 | 2.5876
2020-06-18 18:00 | Winter | 0.91534 | 1.4074 | 2.1297 | 2.1297 | 2.1297 | 2.1297 | 0.76591 | 0.76591 | 0.76591 | 0.76591 | 0.76591 | 0.76591 | 2.4006 | 3.4628 | 4.1588 | 4.525 | 5.2576 | 5.9902 | 0.78877 | 2.1426 | 2.6874 | 2.6874 | 2.6874 | 2.6874 | 1.6779 | 2.1297 | 2.1297 | 2.1297 | 2.1297 | 2.1297
2020-06-18 19:00 | Winter | 0.64784 | 0.99613 | 1.5073 | 1.5073 | 1.5073 | 1.5073 | 0.64842 | 0.64842 | 0.64842 | 0.64842 | 0.64842 | 0.64842 | 2.2482 | 3.243 | 3.8947 | 4.2377 | 4.9238 | 5.6098 | 0.74305 | 2.0184 | 2.5316 | 2.5316 | 2.5316 | 2.5316 | 1.2332 | 1.5652 | 1.5652 | 1.5652 | 1.5652 | 1.5652
2020-06-18 20:00 | Winter | 0.60509 | 0.9304 | 1.4079 | 1.4079 | 1.4079 | 1.4079 | 0.50298 | 0.50298 | 0.50298 | 0.50298 | 0.50298 | 0.50298 | 2.2673 | 3.2705 | 3.9277 | 4.2736 | 4.9655 | 5.6574 | 0.7621 | 2.0702 | 2.5965 | 2.5965 | 2.5965 | 2.5965 | 1.0669 | 1.3542 | 1.3542 | 1.3542 | 1.3542 | 1.3542
2020-06-18 21:00 | Winter | 0.57161 | 0.87892 | 1.33 | 1.33 | 1.33 | 1.33 | 0.48012 | 0.48012 | 0.48012 | 0.48012 | 0.48012 | 0.48012 | 2.0958 | 3.0231 | 3.6307 | 3.9504 | 4.59 | 5.2295 | 0.71637 | 1.946 | 2.4407 | 2.4407 | 2.4407 | 2.4407 | 0.99073 | 1.2575 | 1.2575 | 1.2575 | 1.2575 | 1.2575
2020-06-18 22:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.49441 | 0.49441 | 0.49441 | 0.49441 | 0.49441 | 0.49441 | 1.9624 | 2.8307 | 3.3996 | 3.699 | 4.2979 | 4.8967 | 0.65541 | 1.7803 | 2.233 | 2.233 | 2.233 | 2.233 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-06-18 23:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.43154 | 0.43154 | 0.43154 | 0.43154 | 0.43154 | 0.43154 | 1.8396 | 2.6535 | 3.1868 | 3.4675 | 4.0289 | 4.5902 | 0.6516 | 1.77 | 2.22 | 2.22 | 2.22 | 2.22 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-06-19 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.4001 | 0.4001 | 0.4001 | 0.4001 | 0.4001 | 0.4001 | 1.7338 | 2.5009 | 3.0036 | 3.2681 | 3.7972 | 4.3262 | 0.59063 | 1.6044 | 2.0123 | 2.0123 | 2.0123 | 2.0123 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-06-19 01:00 | Winter | 0.54903 | 0.8442 | 1.2774 | 1.2774 | 1.2774 | 1.2774 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 1.6957 | 2.446 | 2.9375 | 3.1963 | 3.7137 | 4.2311 | 0.5449 | 1.4802 | 1.8565 | 1.8565 | 1.8565 | 1.8565 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-06-19 02:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 1.6766 | 2.4185 | 2.9045 | 3.1603 | 3.672 | 4.1836 | 0.53728 | 1.4595 | 1.8305 | 1.8305 | 1.8305 | 1.8305 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-06-19 03:00 | Winter | 0.57155 | 0.87882 | 1.3298 | 1.3298 | 1.3298 | 1.3298 | 0.40296 | 0.40296 | 0.40296 | 0.40296 | 0.40296 | 0.40296 | 1.6576 | 2.391 | 2.8715 | 3.1244 | 3.6302 | 4.1361 | 0.51823 | 1.4077 | 1.7656 | 1.7656 | 1.7656 | 1.7656 | 0.91452 | 1.1608 | 1.1608 | 1.1608 | 1.1608 | 1.1608
2020-06-19 04:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 1.6957 | 2.446 | 2.9375 | 3.1963 | 3.7137 | 4.2311 | 0.54109 | 1.4698 | 1.8435 | 1.8435 | 1.8435 | 1.8435 | 1.1432 | 1.451 | 1.451 | 1.451 | 1.451 | 1.451
2020-06-19 05:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.6373 | 0.6373 | 0.6373 | 0.6373 | 0.6373 | 0.6373 | 1.829 | 2.6383 | 3.1686 | 3.4477 | 4.0058 | 4.5639 | 0.6516 | 1.77 | 2.22 | 2.22 | 2.22 | 2.22 | 1.5057 | 1.9111 | 1.9111 | 1.9111 | 1.9111 | 1.9111
2020-06-19 06:00 | Winter | 0.65635 | 1.0092 | 1.5271 | 1.5271 | 1.5271 | 1.5271 | 0.7459 | 0.7459 | 0.7459 | 0.7459 | 0.7459 | 0.7459 | 2.0547 | 2.9639 | 3.5595 | 3.873 | 4.5 | 5.127 | 0.72781 | 1.977 | 2.4796 | 2.4796 | 2.4796 | 2.4796 | 1.7797 | 2.259 | 2.259 | 2.259 | 2.259 | 2.259
2020-06-19 07:00 | Winter | 1.086 | 1.6698 | 2.5268 | 2.5268 | 2.5268 | 2.5268 | 0.84067 | 0.84067 | 0.84067 | 0.84067 | 0.84067 | 0.84067 | 2.3758 | 3.427 | 4.1157 | 4.4782 | 5.2032 | 5.9281 | 0.81164 | 2.2047 | 2.7653 | 2.7653 | 2.7653 | 2.7653 | 2.2863 | 2.902 | 2.902 | 2.902 | 2.902 | 2.902
2020-06-19 08:00 | Winter | 1.2575 | 1.9335 | 2.9258 | 2.9258 | 2.9258 | 2.9258 | 0.97168 | 0.97168 | 0.97168 | 0.97168 | 0.97168 | 0.97168 | 2.553 | 3.6827 | 4.4228 | 4.8123 | 5.5914 | 6.3705 | 0.92595 | 2.5153 | 3.1547 | 3.1547 | 3.1547 | 3.1547 | 2.4387 | 3.0954 | 3.0954 | 3.0954 | 3.0954 | 3.0954
2020-06-19 09:00 | Winter | 1.2575 | 1.9335 | 2.9258 | 2.9258 | 2.9258 | 2.9258 | 0.95739 | 0.95739 | 0.95739 | 0.95739 | 0.95739 | 0.95739 | 2.5149 | 3.6277 | 4.3568 | 4.7405 | 5.508 | 6.2754 | 0.86879 | 2.36 | 2.96 | 2.96 | 2.96 | 2.96 | 2.4578 | 3.1196 | 3.1196 | 3.1196 | 3.1196 | 3.1196
2020-06-19 10:00 | Winter | 1.2003 | 1.8456 | 2.7928 | 2.7928 | 2.7928 | 2.7928 | 0.95739 | 0.95739 | 0.95739 | 0.95739 | 0.95739 | 0.95739 | 2.5721 | 3.7102 | 4.4558 | 4.8483 | 5.6331 | 6.418 | 0.87642 | 2.3807 | 2.986 | 2.986 | 2.986 | 2.986 | 2.4578 | 3.1196 | 3.1196 | 3.1196 | 3.1196 | 3.1196
2020-06-19 11:00 | Winter | 1.1813 | 1.8163 | 2.7485 | 2.7485 | 2.7485 | 2.7485 | 0.90309 | 0.90309 | 0.90309 | 0.90309 | 0.90309 | 0.90309 | 2.4773 | 3.5735 | 4.2916 | 4.6696 | 5.4256 | 6.1815 | 0.85355 | 2.3186 | 2.9081 | 2.9081 | 2.9081 | 2.9081 | 2.4959 | 3.168 | 3.168 | 3.168 | 3.168 | 3.168
2020-06-19 12:00 | Winter | 1.2003 | 1.8456 | 2.7928 | 2.7928 | 2.7928 | 2.7928 | 0.94881 | 0.94881 | 0.94881 | 0.94881 | 0.94881 | 0.94881 | 2.4578 | 3.5453 | 4.2578 | 4.6328 | 5.3828 | 6.1328 | 0.83069 | 2.2565 | 2.8302 | 2.8302 | 2.8302 | 2.8302 | 2.4006 | 3.0471 | 3.0471 | 3.0471 | 3.0471 | 3.0471
2020-06-19 13:00 | Winter | 1.1622 | 1.787 | 2.7041 | 2.7041 | 2.7041 | 2.7041 | 0.86022 | 0.86022 | 0.86022 | 0.86022 | 0.86022 | 0.86022 | 2.4578 | 3.5453 | 4.2578 | 4.6328 | 5.3828 | 6.1328 | 0.84593 | 2.2979 | 2.8821 | 2.8821 | 2.8821 | 2.8821 | 2.2673 | 2.8778 | 2.8778 | 2.8778 | 2.8778 | 2.8778
2020-06-19 14:00 | Winter | 1.2194 | 1.8749 | 2.8371 | 2.8371 | 2.8371 | 2.8371 | 0.91166 | 0.91166 | 0.91166 | 0.91166 | 0.91166 | 0.91166 | 2.4387 | 3.5178 | 4.2248 | 4.5969 | 5.3411 | 6.0852 | 0.8804 | 2.3915 | 2.9995 | 2.9995 | 2.9995 | 2.9995 | 2.1582 | 2.7393 | 2.7393 | 2.7393 | 2.7393 | 2.7393
2020-06-19 15:00 | Winter | 1.1432 | 1.7577 | 2.6598 | 2.6598 | 2.6598 | 2.6598 | 0.92309 | 0.92309 | 0.92309 | 0.92309 | 0.92309 | 0.92309 | 2.3435 | 3.3804 | 4.0597 | 4.4173 | 5.1324 | 5.8475 | 0.9069 | 2.4635 | 3.0898 | 3.0898 | 3.0898 | 3.0898 | 2.0781 | 2.6377 | 2.6377 | 2.6377 | 2.6377 | 2.6377
2020-06-19 16:00 | Winter | 1.086 | 1.6698 | 2.5268 | 2.5268 | 2.5268 | 2.5268 | 0.95739 | 0.95739 | 0.95739 | 0.95739 | 0.95739 | 0.95739 | 2.4197 | 3.4903 | 4.1918 | 4.561 | 5.2993 | 6.0377 | 0.89166 | 2.4221 | 3.0379 | 3.0379 | 3.0379 | 3.0379 | 2.0958 | 2.6601 | 2.6601 | 2.6601 | 2.6601 | 2.6601
2020-06-19 17:00 | Winter | 1.0669 | 1.6405 | 2.4825 | 2.4825 | 2.4825 | 2.4825 | 0.90595 | 0.90595 | 0.90595 | 0.90595 | 0.90595 | 0.90595 | 2.5721 | 3.7102 | 4.4558 | 4.8483 | 5.6331 | 6.418 | 0.82307 | 2.2358 | 2.8042 | 2.8042 | 2.8042 | 2.8042 | 2.0168 | 2.5599 | 2.5599 | 2.5599 | 2.5599 | 2.5599
2020-06-19 18:00 | Winter | 0.88143 | 1.3553 | 2.0508 | 2.0508 | 2.0508 | 2.0508 | 0.71161 | 0.71161 | 0.71161 | 0.71161 | 0.71161 | 0.71161 | 2.5149 | 3.6277 | 4.3568 | 4.7405 | 5.508 | 6.2754 | 0.86498 | 2.3496 | 2.947 | 2.947 | 2.947 | 2.947 | 1.5829 | 2.0091 | 2.0091 | 2.0091 | 2.0091 | 2.0091
2020-06-19 19:00 | Winter | 0.66684 | 1.0253 | 1.5515 | 1.5515 | 1.5515 | 1.5515 | 0.62016 | 0.62016 | 0.62016 | 0.62016 | 0.62016 | 0.62016 | 2.2104 | 3.1884 | 3.8292 | 4.1664 | 4.8409 | 5.5155 | 0.81164 | 2.2047 | 2.7653 | 2.7653 | 2.7653 | 2.7653 | 1.1624 | 1.4754 | 1.4754 | 1.4754 | 1.4754 | 1.4754
2020-06-19 20:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.50584 | 0.50584 | 0.50584 | 0.50584 | 0.50584 | 0.50584 | 2.0767 | 2.9956 | 3.5977 | 3.9145 | 4.5482 | 5.182 | 0.82307 | 2.2358 | 2.8042 | 2.8042 | 2.8042 | 2.8042 | 1.0098 | 1.2817 | 1.2817 | 1.2817 | 1.2817 | 1.2817
2020-06-19 21:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.49441 | 0.49441 | 0.49441 | 0.49441 | 0.49441 | 0.49441 | 2.0386 | 2.9407 | 3.5316 | 3.8427 | 4.4648 | 5.0869 | 0.79735 | 2.1659 | 2.7166 | 2.7166 | 2.7166 | 2.7166 | 0.9528 | 1.2094 | 1.2094 | 1.2094 | 1.2094 | 1.2094
2020-06-19 22:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.48584 | 0.48584 | 0.48584 | 0.48584 | 0.48584 | 0.48584 | 1.912 | 2.7581 | 3.3124 | 3.6041 | 4.1876 | 4.771 | 0.79258 | 2.153 | 2.7003 | 2.7003 | 2.7003 | 2.7003 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-06-19 23:00 | Winter | 0.60862 | 0.93582 | 1.4161 | 1.4161 | 1.4161 | 1.4161 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 1.8672 | 2.6933 | 3.2346 | 3.5195 | 4.0892 | 4.659 | 0.64397 | 1.7493 | 2.194 | 2.194 | 2.194 | 2.194 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-06-20 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.43154 | 0.43154 | 0.43154 | 0.43154 | 0.43154 | 0.43154 | 1.7228 | 2.4851 | 2.9846 | 3.2474 | 3.7732 | 4.2989 | 0.59825 | 1.6251 | 2.0382 | 2.0382 | 2.0382 | 2.0382 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-06-20 01:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.38581 | 0.38581 | 0.38581 | 0.38581 | 0.38581 | 0.38581 | 1.6766 | 2.4185 | 2.9045 | 3.1603 | 3.672 | 4.1836 | 0.59063 | 1.6044 | 2.0123 | 2.0123 | 2.0123 | 2.0123 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-06-20 02:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.36009 | 0.36009 | 0.36009 | 0.36009 | 0.36009 | 0.36009 | 1.6195 | 2.336 | 2.8055 | 3.0526 | 3.5468 | 4.041 | 0.60587 | 1.6458 | 2.0642 | 2.0642 | 2.0642 | 2.0642 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-06-20 03:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.35723 | 0.35723 | 0.35723 | 0.35723 | 0.35723 | 0.35723 | 1.6195 | 2.336 | 2.8055 | 3.0526 | 3.5468 | 4.041 | 0.56776 | 1.5423 | 1.9344 | 1.9344 | 1.9344 | 1.9344 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-06-20 04:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.35438 | 0.35438 | 0.35438 | 0.35438 | 0.35438 | 0.35438 | 1.6188 | 2.3351 | 2.8043 | 3.0513 | 3.5453 | 4.0393 | 0.56092 | 1.5237 | 1.9111 | 1.9111 | 1.9111 | 1.9111 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-06-20 05:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 1.6576 | 2.391 | 2.8715 | 3.1244 | 3.6302 | 4.1361 | 0.60968 | 1.6561 | 2.0772 | 2.0772 | 2.0772 | 2.0772 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-06-20 06:00 | Winter | 0.56667 | 0.87132 | 1.3185 | 1.3185 | 1.3185 | 1.3185 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 1.8672 | 2.6933 | 3.2346 | 3.5195 | 4.0892 | 4.659 | 0.66684 | 1.8114 | 2.2719 | 2.2719 | 2.2719 | 2.2719 | 0.93 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 1.1804
2020-06-20 07:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 1.9243 | 2.7758 | 3.3336 | 3.6272 | 4.2144 | 4.8016 | 0.67446 | 1.8321 | 2.2979 | 2.2979 | 2.2979 | 2.2979 | 0.95263 | 1.2092 | 1.2092 | 1.2092 | 1.2092 | 1.2092
2020-06-20 08:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.59158 | 0.59158 | 0.59158 | 0.59158 | 0.59158 | 0.59158 | 2.1148 | 3.0506 | 3.6637 | 3.9863 | 4.6317 | 5.277 | 0.70875 | 1.9253 | 2.4147 | 2.4147 | 2.4147 | 2.4147 | 1.0288 | 1.3059 | 1.3059 | 1.3059 | 1.3059 | 1.3059
2020-06-20 09:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.6173 | 0.6173 | 0.6173 | 0.6173 | 0.6173 | 0.6173 | 2.0767 | 2.9956 | 3.5977 | 3.9145 | 4.5482 | 5.182 | 0.70875 | 1.9253 | 2.4147 | 2.4147 | 2.4147 | 2.4147 | 1.086 | 1.3784 | 1.3784 | 1.3784 | 1.3784 | 1.3784
2020-06-20 10:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.62587 | 0.62587 | 0.62587 | 0.62587 | 0.62587 | 0.62587 | 2.0767 | 2.9956 | 3.5977 | 3.9145 | 4.5482 | 5.182 | 0.64779 | 1.7596 | 2.207 | 2.207 | 2.207 | 2.207 | 1.105 | 1.4026 | 1.4026 | 1.4026 | 1.4026 | 1.4026
2020-06-20 11:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.54585 | 0.54585 | 0.54585 | 0.54585 | 0.54585 | 0.54585 | 2.0196 | 2.9132 | 3.4986 | 3.8068 | 4.4231 | 5.0393 | 0.67827 | 1.8425 | 2.3109 | 2.3109 | 2.3109 | 2.3109 | 1.1432 | 1.451 | 1.451 | 1.451 | 1.451 | 1.451
2020-06-20 12:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.54871 | 0.54871 | 0.54871 | 0.54871 | 0.54871 | 0.54871 | 2.0958 | 3.0231 | 3.6307 | 3.9504 | 4.59 | 5.2295 | 0.67827 | 1.8425 | 2.3109 | 2.3109 | 2.3109 | 2.3109 | 1.086 | 1.3784 | 1.3784 | 1.3784 | 1.3784 | 1.3784
2020-06-20 13:00 | Winter | 0.58163 | 0.89433 | 1.3533 | 1.3533 | 1.3533 | 1.3533 | 0.52299 | 0.52299 | 0.52299 | 0.52299 | 0.52299 | 0.52299 | 2.0767 | 2.9956 | 3.5977 | 3.9145 | 4.5482 | 5.182 | 0.63635 | 1.7286 | 2.1681 | 2.1681 | 2.1681 | 2.1681 | 1.1241 | 1.4268 | 1.4268 | 1.4268 | 1.4268 | 1.4268
2020-06-20 14:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.53442 | 0.53442 | 0.53442 | 0.53442 | 0.53442 | 0.53442 | 2.0577 | 2.9681 | 3.5647 | 3.8786 | 4.5065 | 5.1344 | 0.66303 | 1.8011 | 2.2589 | 2.2589 | 2.2589 | 2.2589 | 1.086 | 1.3784 | 1.3784 | 1.3784 | 1.3784 | 1.3784
2020-06-20 15:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.53442 | 0.53442 | 0.53442 | 0.53442 | 0.53442 | 0.53442 | 2.0577 | 2.9681 | 3.5647 | 3.8786 | 4.5065 | 5.1344 | 0.70113 | 1.9046 | 2.3888 | 2.3888 | 2.3888 | 2.3888 | 1.0669 | 1.3542 | 1.3542 | 1.3542 | 1.3542 | 1.3542
2020-06-20 16:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.5087 | 0.5087 | 0.5087 | 0.5087 | 0.5087 | 0.5087 | 2.191 | 3.1605 | 3.7957 | 4.13 | 4.7986 | 5.4672 | 0.70113 | 1.9046 | 2.3888 | 2.3888 | 2.3888 | 2.3888 | 1.0669 | 1.3542 | 1.3542 | 1.3542 | 1.3542 | 1.3542
2020-06-20 17:00 | Winter | 0.59079 | 0.90841 | 1.3746 | 1.3746 | 1.3746 | 1.3746 | 0.54585 | 0.54585 | 0.54585 | 0.54585 | 0.54585 | 0.54585 | 2.3435 | 3.3804 | 4.0597 | 4.4173 | 5.1324 | 5.8475 | 0.82688 | 2.2461 | 2.8172 | 2.8172 | 2.8172 | 2.8172 | 1.0669 | 1.3542 | 1.3542 | 1.3542 | 1.3542 | 1.3542
2020-06-20 18:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.52585 | 0.52585 | 0.52585 | 0.52585 | 0.52585 | 0.52585 | 2.2101 | 3.188 | 3.8287 | 4.1659 | 4.8403 | 5.5147 | 0.83069 | 2.2565 | 2.8302 | 2.8302 | 2.8302 | 2.8302 | 1.0291 | 1.3062 | 1.3062 | 1.3062 | 1.3062 | 1.3062
2020-06-20 19:00 | Winter | 0.54614 | 0.83975 | 1.2707 | 1.2707 | 1.2707 | 1.2707 | 0.5087 | 0.5087 | 0.5087 | 0.5087 | 0.5087 | 0.5087 | 2.1529 | 3.1056 | 3.7297 | 4.0582 | 4.7151 | 5.3721 | 0.81545 | 2.2151 | 2.7782 | 2.7782 | 2.7782 | 2.7782 | 1.0288 | 1.3059 | 1.3059 | 1.3059 | 1.3059 | 1.3059
2020-06-20 20:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.47726 | 0.47726 | 0.47726 | 0.47726 | 0.47726 | 0.47726 | 2.0767 | 2.9956 | 3.5977 | 3.9145 | 4.5482 | 5.182 | 0.77734 | 2.1116 | 2.6484 | 2.6484 | 2.6484 | 2.6484 | 1.0098 | 1.2817 | 1.2817 | 1.2817 | 1.2817 | 1.2817
2020-06-20 21:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.39153 | 0.39153 | 0.39153 | 0.39153 | 0.39153 | 0.39153 | 2.0577 | 2.9681 | 3.5647 | 3.8786 | 4.5065 | 5.1344 | 0.80021 | 2.1737 | 2.7263 | 2.7263 | 2.7263 | 2.7263 | 0.95263 | 1.2092 | 1.2092 | 1.2092 | 1.2092 | 1.2092
2020-06-20 22:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.37717 | 0.37717 | 0.37717 | 0.37717 | 0.37717 | 0.37717 | 2.0005 | 2.8857 | 3.4656 | 3.7709 | 4.3813 | 4.9918 | 0.7621 | 2.0702 | 2.5965 | 2.5965 | 2.5965 | 2.5965 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-06-20 23:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.39717 | 0.39717 | 0.39717 | 0.39717 | 0.39717 | 0.39717 | 1.8672 | 2.6933 | 3.2346 | 3.5195 | 4.0892 | 4.659 | 0.67827 | 1.8425 | 2.3109 | 2.3109 | 2.3109 | 2.3109 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-06-21 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.39724 | 0.39724 | 0.39724 | 0.39724 | 0.39724 | 0.39724 | 1.7338 | 2.5009 | 3.0036 | 3.2681 | 3.7972 | 4.3262 | 0.60968 | 1.6561 | 2.0772 | 2.0772 | 2.0772 | 2.0772 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-06-21 01:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 1.6576 | 2.391 | 2.8715 | 3.1244 | 3.6302 | 4.1361 | 0.55633 | 1.5112 | 1.8954 | 1.8954 | 1.8954 | 1.8954 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-06-21 02:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.39153 | 0.39153 | 0.39153 | 0.39153 | 0.39153 | 0.39153 | 1.5814 | 2.2811 | 2.7395 | 2.9808 | 3.4633 | 3.9459 | 0.55252 | 1.5009 | 1.8825 | 1.8825 | 1.8825 | 1.8825 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-06-21 03:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.38583 | 0.38583 | 0.38583 | 0.38583 | 0.38583 | 0.38583 | 1.5814 | 2.2811 | 2.7395 | 2.9808 | 3.4633 | 3.9459 | 0.54871 | 1.4905 | 1.8695 | 1.8695 | 1.8695 | 1.8695 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-06-21 04:00 | Winter | 0.5901 | 0.90735 | 1.373 | 1.373 | 1.373 | 1.373 | 0.40296 | 0.40296 | 0.40296 | 0.40296 | 0.40296 | 0.40296 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.5792 | 1.5733 | 1.9733 | 1.9733 | 1.9733 | 1.9733 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-06-21 05:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.5087 | 0.5087 | 0.5087 | 0.5087 | 0.5087 | 0.5087 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.60551 | 1.6448 | 2.063 | 2.063 | 2.063 | 2.063 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-06-21 06:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.4544 | 0.4544 | 0.4544 | 0.4544 | 0.4544 | 0.4544 | 1.7719 | 2.5559 | 3.0696 | 3.3399 | 3.8806 | 4.4213 | 0.68208 | 1.8528 | 2.3239 | 2.3239 | 2.3239 | 2.3239 | 0.91452 | 1.1608 | 1.1608 | 1.1608 | 1.1608 | 1.1608
2020-06-21 07:00 | Winter | 0.59061 | 0.90813 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.51727 | 0.51727 | 0.51727 | 0.51727 | 0.51727 | 0.51727 | 1.8481 | 2.6658 | 3.2016 | 3.4836 | 4.0475 | 4.6115 | 0.74305 | 2.0184 | 2.5316 | 2.5316 | 2.5316 | 2.5316 | 0.93358 | 1.185 | 1.185 | 1.185 | 1.185 | 1.185
2020-06-21 08:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.56872 | 0.56872 | 0.56872 | 0.56872 | 0.56872 | 0.56872 | 2.0767 | 2.9956 | 3.5977 | 3.9145 | 4.5482 | 5.182 | 0.68589 | 1.8632 | 2.3368 | 2.3368 | 2.3368 | 2.3368 | 0.91452 | 1.1608 | 1.1608 | 1.1608 | 1.1608 | 1.1608
2020-06-21 09:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.58872 | 0.58872 | 0.58872 | 0.58872 | 0.58872 | 0.58872 | 2.1148 | 3.0506 | 3.6637 | 3.9863 | 4.6317 | 5.277 | 0.73162 | 1.9874 | 2.4926 | 2.4926 | 2.4926 | 2.4926 | 0.99073 | 1.2575 | 1.2575 | 1.2575 | 1.2575 | 1.2575
2020-06-21 10:00 | Winter | 0.55231 | 0.84923 | 1.2851 | 1.2851 | 1.2851 | 1.2851 | 0.55443 | 0.55443 | 0.55443 | 0.55443 | 0.55443 | 0.55443 | 2.0767 | 2.9956 | 3.5977 | 3.9145 | 4.5482 | 5.182 | 0.72018 | 1.9563 | 2.4537 | 2.4537 | 2.4537 | 2.4537 | 0.97168 | 1.2333 | 1.2333 | 1.2333 | 1.2333 | 1.2333
2020-06-21 11:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.54014 | 0.54014 | 0.54014 | 0.54014 | 0.54014 | 0.54014 | 2.0666 | 2.9811 | 3.5802 | 3.8955 | 4.5261 | 5.1568 | 0.68208 | 1.8528 | 2.3239 | 2.3239 | 2.3239 | 2.3239 | 0.95263 | 1.2092 | 1.2092 | 1.2092 | 1.2092 | 1.2092
2020-06-21 12:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 2.0767 | 2.9956 | 3.5977 | 3.9145 | 4.5482 | 5.182 | 0.68589 | 1.8632 | 2.3368 | 2.3368 | 2.3368 | 2.3368 | 0.95263 | 1.2092 | 1.2092 | 1.2092 | 1.2092 | 1.2092
2020-06-21 13:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.49155 | 0.49155 | 0.49155 | 0.49155 | 0.49155 | 0.49155 | 2.1529 | 3.1056 | 3.7297 | 4.0582 | 4.7151 | 5.3721 | 0.64016 | 1.7389 | 2.1811 | 2.1811 | 2.1811 | 2.1811 | 1.0288 | 1.3059 | 1.3059 | 1.3059 | 1.3059 | 1.3059
2020-06-21 14:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.55728 | 0.55728 | 0.55728 | 0.55728 | 0.55728 | 0.55728 | 2.1529 | 3.1056 | 3.7297 | 4.0582 | 4.7151 | 5.3721 | 0.6516 | 1.77 | 2.22 | 2.22 | 2.22 | 2.22 | 0.93358 | 1.185 | 1.185 | 1.185 | 1.185 | 1.185
2020-06-21 15:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.55728 | 0.55728 | 0.55728 | 0.55728 | 0.55728 | 0.55728 | 2.1148 | 3.0506 | 3.6637 | 3.9863 | 4.6317 | 5.277 | 0.66684 | 1.8114 | 2.2719 | 2.2719 | 2.2719 | 2.2719 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-06-21 16:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.60587 | 0.60587 | 0.60587 | 0.60587 | 0.60587 | 0.60587 | 2.2863 | 3.2979 | 3.9607 | 4.3096 | 5.0072 | 5.7049 | 0.724 | 1.9667 | 2.4667 | 2.4667 | 2.4667 | 2.4667 | 0.99073 | 1.2575 | 1.2575 | 1.2575 | 1.2575 | 1.2575
2020-06-21 17:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.62301 | 0.62301 | 0.62301 | 0.62301 | 0.62301 | 0.62301 | 2.3435 | 3.3804 | 4.0597 | 4.4173 | 5.1324 | 5.8475 | 0.76591 | 2.0805 | 2.6095 | 2.6095 | 2.6095 | 2.6095 | 0.93358 | 1.185 | 1.185 | 1.185 | 1.185 | 1.185
2020-06-21 18:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.60301 | 0.60301 | 0.60301 | 0.60301 | 0.60301 | 0.60301 | 2.281 | 3.2903 | 3.9515 | 4.2996 | 4.9956 | 5.6917 | 0.76591 | 2.0805 | 2.6095 | 2.6095 | 2.6095 | 2.6095 | 0.93358 | 1.185 | 1.185 | 1.185 | 1.185 | 1.185
2020-06-21 19:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.57157 | 0.57157 | 0.57157 | 0.57157 | 0.57157 | 0.57157 | 2.2291 | 3.2155 | 3.8617 | 4.2018 | 4.8821 | 5.5623 | 0.75829 | 2.0598 | 2.5835 | 2.5835 | 2.5835 | 2.5835 | 0.95263 | 1.2092 | 1.2092 | 1.2092 | 1.2092 | 1.2092
2020-06-21 20:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.56014 | 0.56014 | 0.56014 | 0.56014 | 0.56014 | 0.56014 | 2.191 | 3.1605 | 3.7957 | 4.13 | 4.7986 | 5.4672 | 0.74686 | 2.0288 | 2.5446 | 2.5446 | 2.5446 | 2.5446 | 0.91452 | 1.1608 | 1.1608 | 1.1608 | 1.1608 | 1.1608
2020-06-21 21:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.4544 | 0.4544 | 0.4544 | 0.4544 | 0.4544 | 0.4544 | 2.1529 | 3.1056 | 3.7297 | 4.0582 | 4.7151 | 5.3721 | 0.7621 | 2.0702 | 2.5965 | 2.5965 | 2.5965 | 2.5965 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-06-21 22:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.42296 | 0.42296 | 0.42296 | 0.42296 | 0.42296 | 0.42296 | 2.0196 | 2.9132 | 3.4986 | 3.8068 | 4.4231 | 5.0393 | 0.6897 | 1.8735 | 2.3498 | 2.3498 | 2.3498 | 2.3498 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-06-21 23:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.42296 | 0.42296 | 0.42296 | 0.42296 | 0.42296 | 0.42296 | 1.7909 | 2.5834 | 3.1026 | 3.3758 | 3.9223 | 4.4688 | 0.57157 | 1.5526 | 1.9474 | 1.9474 | 1.9474 | 1.9474 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-06-22 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.42582 | 0.42582 | 0.42582 | 0.42582 | 0.42582 | 0.42582 | 1.6583 | 2.392 | 2.8727 | 3.1257 | 3.6317 | 4.1378 | 0.57539 | 1.563 | 1.9603 | 1.9603 | 1.9603 | 1.9603 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-06-22 01:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.40582 | 0.40582 | 0.40582 | 0.40582 | 0.40582 | 0.40582 | 1.5814 | 2.2811 | 2.7395 | 2.9808 | 3.4633 | 3.9459 | 0.5449 | 1.4802 | 1.8565 | 1.8565 | 1.8565 | 1.8565 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-06-22 02:00 | Winter | 0.60725 | 0.93371 | 1.4129 | 1.4129 | 1.4129 | 1.4129 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 1.5814 | 2.2811 | 2.7395 | 2.9808 | 3.4633 | 3.9459 | 0.55633 | 1.5112 | 1.8954 | 1.8954 | 1.8954 | 1.8954 | 1.105 | 1.4026 | 1.4026 | 1.4026 | 1.4026 | 1.4026
2020-06-22 03:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.49441 | 0.49441 | 0.49441 | 0.49441 | 0.49441 | 0.49441 | 1.5433 | 2.2261 | 2.6735 | 2.909 | 3.3799 | 3.8508 | 0.53728 | 1.4595 | 1.8305 | 1.8305 | 1.8305 | 1.8305 | 1.0701 | 1.3582 | 1.3582 | 1.3582 | 1.3582 | 1.3582
2020-06-22 04:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.52585 | 1.4284 | 1.7916 | 1.7916 | 1.7916 | 1.7916 | 1.1498 | 1.4594 | 1.4594 | 1.4594 | 1.4594 | 1.4594
2020-06-22 05:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.63445 | 0.63445 | 0.63445 | 0.63445 | 0.63445 | 0.63445 | 1.7139 | 2.4723 | 2.9691 | 3.2306 | 3.7537 | 4.2767 | 0.73162 | 1.9874 | 2.4926 | 2.4926 | 2.4926 | 2.4926 | 1.5242 | 1.9346 | 1.9346 | 1.9346 | 1.9346 | 1.9346
2020-06-22 06:00 | Winter | 0.7575 | 1.1647 | 1.7625 | 1.7625 | 1.7625 | 1.7625 | 0.76877 | 0.76877 | 0.76877 | 0.76877 | 0.76877 | 0.76877 | 2.0516 | 2.9594 | 3.5541 | 3.8672 | 4.4932 | 5.1193 | 0.77734 | 2.1116 | 2.6484 | 2.6484 | 2.6484 | 2.6484 | 1.7909 | 2.2732 | 2.2732 | 2.2732 | 2.2732 | 2.2732
2020-06-22 07:00 | Winter | 1.1813 | 1.8163 | 2.7485 | 2.7485 | 2.7485 | 2.7485 | 0.85165 | 0.85165 | 0.85165 | 0.85165 | 0.85165 | 0.85165 | 2.4002 | 3.4622 | 4.158 | 4.5242 | 5.2566 | 5.989 | 0.83831 | 2.2772 | 2.8561 | 2.8561 | 2.8561 | 2.8561 | 2.3054 | 2.9262 | 2.9262 | 2.9262 | 2.9262 | 2.9262
2020-06-22 08:00 | Winter | 1.3337 | 2.0507 | 3.1031 | 3.1031 | 3.1031 | 3.1031 | 0.95739 | 0.95739 | 0.95739 | 0.95739 | 0.95739 | 0.95739 | 2.534 | 3.6552 | 4.3898 | 4.7764 | 5.5497 | 6.3229 | 0.89928 | 2.4428 | 3.0639 | 3.0639 | 3.0639 | 3.0639 | 2.534 | 3.2163 | 3.2163 | 3.2163 | 3.2163 | 3.2163
2020-06-22 09:00 | Winter | 1.3337 | 2.0507 | 3.1031 | 3.1031 | 3.1031 | 3.1031 | 0.96882 | 0.96882 | 0.96882 | 0.96882 | 0.96882 | 0.96882 | 2.6102 | 3.7651 | 4.5218 | 4.9201 | 5.7166 | 6.5131 | 0.89547 | 2.4325 | 3.0509 | 3.0509 | 3.0509 | 3.0509 | 2.6674 | 3.3856 | 3.3856 | 3.3856 | 3.3856 | 3.3856
2020-06-22 10:00 | Winter | 1.2956 | 1.9921 | 3.0144 | 3.0144 | 3.0144 | 3.0144 | 0.98025 | 0.98025 | 0.98025 | 0.98025 | 0.98025 | 0.98025 | 2.6102 | 3.7651 | 4.5218 | 4.9201 | 5.7166 | 6.5131 | 0.83831 | 2.2772 | 2.8561 | 2.8561 | 2.8561 | 2.8561 | 2.6674 | 3.3856 | 3.3856 | 3.3856 | 3.3856 | 3.3856
2020-06-22 11:00 | Winter | 1.2384 | 1.9042 | 2.8814 | 2.8814 | 2.8814 | 2.8814 | 1.0088 | 1.0088 | 1.0088 | 1.0088 | 1.0088 | 1.0088 | 2.534 | 3.6552 | 4.3898 | 4.7764 | 5.5497 | 6.3229 | 0.81545 | 2.2151 | 2.7782 | 2.7782 | 2.7782 | 2.7782 | 2.6483 | 3.3614 | 3.3614 | 3.3614 | 3.3614 | 3.3614
2020-06-22 12:00 | Winter | 1.2575 | 1.9335 | 2.9258 | 2.9258 | 2.9258 | 2.9258 | 0.95739 | 0.95739 | 0.95739 | 0.95739 | 0.95739 | 0.95739 | 2.6293 | 3.7926 | 4.5548 | 4.956 | 5.7583 | 6.5606 | 0.92214 | 2.5049 | 3.1418 | 3.1418 | 3.1418 | 3.1418 | 2.6295 | 3.3375 | 3.3375 | 3.3375 | 3.3375 | 3.3375
2020-06-22 13:00 | Winter | 1.2384 | 1.9042 | 2.8814 | 2.8814 | 2.8814 | 2.8814 | 0.94881 | 0.94881 | 0.94881 | 0.94881 | 0.94881 | 0.94881 | 2.5911 | 3.7377 | 4.4888 | 4.8842 | 5.6749 | 6.4656 | 0.84974 | 2.3082 | 2.8951 | 2.8951 | 2.8951 | 2.8951 | 2.5721 | 3.2647 | 3.2647 | 3.2647 | 3.2647 | 3.2647
2020-06-22 14:00 | Winter | 1.1813 | 1.8163 | 2.7485 | 2.7485 | 2.7485 | 2.7485 | 0.96596 | 0.96596 | 0.96596 | 0.96596 | 0.96596 | 0.96596 | 2.5891 | 3.7347 | 4.4853 | 4.8804 | 5.6704 | 6.4605 | 0.84593 | 2.2979 | 2.8821 | 2.8821 | 2.8821 | 2.8821 | 2.5149 | 3.1922 | 3.1922 | 3.1922 | 3.1922 | 3.1922
2020-06-22 15:00 | Winter | 1.1813 | 1.8163 | 2.7485 | 2.7485 | 2.7485 | 2.7485 | 0.97739 | 0.97739 | 0.97739 | 0.97739 | 0.97739 | 0.97739 | 2.4578 | 3.5453 | 4.2578 | 4.6328 | 5.3828 | 6.1328 | 0.88023 | 2.3911 | 2.9989 | 2.9989 | 2.9989 | 2.9989 | 2.4578 | 3.1196 | 3.1196 | 3.1196 | 3.1196 | 3.1196
2020-06-22 16:00 | Winter | 1.1622 | 1.787 | 2.7041 | 2.7041 | 2.7041 | 2.7041 | 0.93452 | 0.93452 | 0.93452 | 0.93452 | 0.93452 | 0.93452 | 2.553 | 3.6827 | 4.4228 | 4.8123 | 5.5914 | 6.3705 | 0.86498 | 2.3496 | 2.947 | 2.947 | 2.947 | 2.947 | 2.4387 | 3.0954 | 3.0954 | 3.0954 | 3.0954 | 3.0954
2020-06-22 17:00 | Winter | 1.105 | 1.6991 | 2.5711 | 2.5711 | 2.5711 | 2.5711 | 0.90023 | 0.90023 | 0.90023 | 0.90023 | 0.90023 | 0.90023 | 2.7817 | 4.0125 | 4.8189 | 5.2433 | 6.0921 | 6.941 | 0.86879 | 2.36 | 2.96 | 2.96 | 2.96 | 2.96 | 2.2291 | 2.8294 | 2.8294 | 2.8294 | 2.8294 | 2.8294
2020-06-22 18:00 | Winter | 0.97855 | 1.5046 | 2.2768 | 2.2768 | 2.2768 | 2.2768 | 0.73161 | 0.73161 | 0.73161 | 0.73161 | 0.73161 | 0.73161 | 2.6882 | 3.8777 | 4.657 | 5.0671 | 5.8875 | 6.7078 | 0.84212 | 2.2875 | 2.8691 | 2.8691 | 2.8691 | 2.8691 | 1.6229 | 2.06 | 2.06 | 2.06 | 2.06 | 2.06
2020-06-22 19:00 | Winter | 0.68589 | 1.0546 | 1.5959 | 1.5959 | 1.5959 | 1.5959 | 0.60427 | 0.60427 | 0.60427 | 0.60427 | 0.60427 | 0.60427 | 2.5345 | 3.6559 | 4.3906 | 4.7773 | 5.5507 | 6.3241 | 0.74686 | 2.0288 | 2.5446 | 2.5446 | 2.5446 | 2.5446 | 1.2194 | 1.5477 | 1.5477 | 1.5477 | 1.5477 | 1.5477
2020-06-22 20:00 | Winter | 0.66684 | 1.0253 | 1.5515 | 1.5515 | 1.5515 | 1.5515 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 2.4197 | 3.4903 | 4.1918 | 4.561 | 5.2993 | 6.0377 | 0.76972 | 2.0909 | 2.6225 | 2.6225 | 2.6225 | 2.6225 | 1.1241 | 1.4268 | 1.4268 | 1.4268 | 1.4268 | 1.4268
2020-06-22 21:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.39724 | 0.39724 | 0.39724 | 0.39724 | 0.39724 | 0.39724 | 2.3054 | 3.3254 | 3.9937 | 4.3455 | 5.049 | 5.7525 | 0.72018 | 1.9563 | 2.4537 | 2.4537 | 2.4537 | 2.4537 | 1.0232 | 1.2987 | 1.2987 | 1.2987 | 1.2987 | 1.2987
2020-06-22 22:00 | Winter | 0.57121 | 0.87831 | 1.3291 | 1.3291 | 1.3291 | 1.3291 | 0.37724 | 0.37724 | 0.37724 | 0.37724 | 0.37724 | 0.37724 | 2.1339 | 3.0781 | 3.6967 | 4.0223 | 4.6734 | 5.3246 | 0.6516 | 1.77 | 2.22 | 2.22 | 2.22 | 2.22 | 0.93358 | 1.185 | 1.185 | 1.185 | 1.185 | 1.185
2020-06-22 23:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.42582 | 0.42582 | 0.42582 | 0.42582 | 0.42582 | 0.42582 | 1.8481 | 2.6658 | 3.2016 | 3.4836 | 4.0475 | 4.6115 | 0.59063 | 1.6044 | 2.0123 | 2.0123 | 2.0123 | 2.0123 | 0.91452 | 1.1608 | 1.1608 | 1.1608 | 1.1608 | 1.1608
2020-06-23 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.37724 | 0.37724 | 0.37724 | 0.37724 | 0.37724 | 0.37724 | 1.7147 | 2.4735 | 2.9705 | 3.2322 | 3.7554 | 4.2787 | 0.56014 | 1.5216 | 1.9084 | 1.9084 | 1.9084 | 1.9084 | 0.93358 | 1.185 | 1.185 | 1.185 | 1.185 | 1.185
2020-06-23 01:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.40296 | 0.40296 | 0.40296 | 0.40296 | 0.40296 | 0.40296 | 1.6576 | 2.391 | 2.8715 | 3.1244 | 3.6302 | 4.1361 | 0.52966 | 1.4388 | 1.8046 | 1.8046 | 1.8046 | 1.8046 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-06-23 02:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.54871 | 1.4905 | 1.8695 | 1.8695 | 1.8695 | 1.8695 | 1.1241 | 1.4268 | 1.4268 | 1.4268 | 1.4268 | 1.4268
2020-06-23 03:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.37152 | 0.37152 | 0.37152 | 0.37152 | 0.37152 | 0.37152 | 1.6004 | 2.3086 | 2.7725 | 3.0167 | 3.5051 | 3.9934 | 0.5449 | 1.4802 | 1.8565 | 1.8565 | 1.8565 | 1.8565 | 1.086 | 1.3784 | 1.3784 | 1.3784 | 1.3784 | 1.3784
2020-06-23 04:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 1.6576 | 2.391 | 2.8715 | 3.1244 | 3.6302 | 4.1361 | 0.54109 | 1.4698 | 1.8435 | 1.8435 | 1.8435 | 1.8435 | 1.0669 | 1.3542 | 1.3542 | 1.3542 | 1.3542 | 1.3542
2020-06-23 05:00 | Winter | 0.6387 | 0.98208 | 1.4861 | 1.4861 | 1.4861 | 1.4861 | 0.58872 | 0.58872 | 0.58872 | 0.58872 | 0.58872 | 0.58872 | 1.81 | 2.6109 | 3.1356 | 3.4117 | 3.9641 | 4.5164 | 0.75067 | 2.0391 | 2.5575 | 2.5575 | 2.5575 | 2.5575 | 1.4728 | 1.8694 | 1.8694 | 1.8694 | 1.8694 | 1.8694
2020-06-23 06:00 | Winter | 0.74617 | 1.1473 | 1.7361 | 1.7361 | 1.7361 | 1.7361 | 0.72584 | 0.72584 | 0.72584 | 0.72584 | 0.72584 | 0.72584 | 2.0659 | 2.9801 | 3.579 | 3.8942 | 4.5246 | 5.1551 | 0.78115 | 2.1219 | 2.6614 | 2.6614 | 2.6614 | 2.6614 | 1.8831 | 2.3902 | 2.3902 | 2.3902 | 2.3902 | 2.3902
2020-06-23 07:00 | Winter | 1.1344 | 1.7442 | 2.6393 | 2.6393 | 2.6393 | 2.6393 | 0.9477 | 0.9477 | 0.9477 | 0.9477 | 0.9477 | 0.9477 | 2.534 | 3.6552 | 4.3898 | 4.7764 | 5.5497 | 6.3229 | 0.83831 | 2.2772 | 2.8561 | 2.8561 | 2.8561 | 2.8561 | 2.3389 | 2.9688 | 2.9688 | 2.9688 | 2.9688 | 2.9688
2020-06-23 08:00 | Winter | 1.2765 | 1.9628 | 2.9701 | 2.9701 | 2.9701 | 2.9701 | 0.97979 | 0.97979 | 0.97979 | 0.97979 | 0.97979 | 0.97979 | 2.5911 | 3.7377 | 4.4888 | 4.8842 | 5.6749 | 6.4656 | 0.88404 | 2.4014 | 3.0119 | 3.0119 | 3.0119 | 3.0119 | 2.6102 | 3.3131 | 3.3131 | 3.3131 | 3.3131 | 3.3131
2020-06-23 09:00 | Winter | 1.2956 | 1.9921 | 3.0144 | 3.0144 | 3.0144 | 3.0144 | 0.98597 | 0.98597 | 0.98597 | 0.98597 | 0.98597 | 0.98597 | 2.6293 | 3.7926 | 4.5548 | 4.956 | 5.7583 | 6.5606 | 0.86879 | 2.36 | 2.96 | 2.96 | 2.96 | 2.96 | 2.7245 | 3.4582 | 3.4582 | 3.4582 | 3.4582 | 3.4582
2020-06-23 10:00 | Winter | 1.2765 | 1.9628 | 2.9701 | 2.9701 | 2.9701 | 2.9701 | 0.9631 | 0.9631 | 0.9631 | 0.9631 | 0.9631 | 0.9631 | 2.7626 | 3.985 | 4.7859 | 5.2074 | 6.0504 | 6.8934 | 0.85355 | 2.3186 | 2.9081 | 2.9081 | 2.9081 | 2.9081 | 2.6483 | 3.3614 | 3.3614 | 3.3614 | 3.3614 | 3.3614
2020-06-23 11:00 | Winter | 1.2384 | 1.9042 | 2.8814 | 2.8814 | 2.8814 | 2.8814 | 1.0088 | 1.0088 | 1.0088 | 1.0088 | 1.0088 | 1.0088 | 2.6682 | 3.8488 | 4.6223 | 5.0294 | 5.8437 | 6.6579 | 0.82307 | 2.2358 | 2.8042 | 2.8042 | 2.8042 | 2.8042 | 2.6293 | 3.3373 | 3.3373 | 3.3373 | 3.3373 | 3.3373
2020-06-23 12:00 | Winter | 1.2575 | 1.9335 | 2.9258 | 2.9258 | 2.9258 | 2.9258 | 0.99454 | 0.99454 | 0.99454 | 0.99454 | 0.99454 | 0.99454 | 2.6483 | 3.8201 | 4.5878 | 4.9919 | 5.8 | 6.6082 | 0.76591 | 2.0805 | 2.6095 | 2.6095 | 2.6095 | 2.6095 | 2.553 | 3.2405 | 3.2405 | 3.2405 | 3.2405 | 3.2405
2020-06-23 13:00 | Winter | 1.2575 | 1.9335 | 2.9258 | 2.9258 | 2.9258 | 2.9258 | 0.96882 | 0.96882 | 0.96882 | 0.96882 | 0.96882 | 0.96882 | 2.6293 | 3.7926 | 4.5548 | 4.956 | 5.7583 | 6.5606 | 0.86498 | 2.3496 | 2.947 | 2.947 | 2.947 | 2.947 | 2.5496 | 3.2361 | 3.2361 | 3.2361 | 3.2361 | 3.2361
2020-06-23 14:00 | Winter | 1.2194 | 1.8749 | 2.8371 | 2.8371 | 2.8371 | 2.8371 | 0.98025 | 0.98025 | 0.98025 | 0.98025 | 0.98025 | 0.98025 | 2.553 | 3.6827 | 4.4228 | 4.8123 | 5.5914 | 6.3705 | 0.80783 | 2.1944 | 2.7523 | 2.7523 | 2.7523 | 2.7523 | 2.4387 | 3.0954 | 3.0954 | 3.0954 | 3.0954 | 3.0954
2020-06-23 15:00 | Winter | 1.2003 | 1.8456 | 2.7928 | 2.7928 | 2.7928 | 2.7928 | 0.97168 | 0.97168 | 0.97168 | 0.97168 | 0.97168 | 0.97168 | 2.534 | 3.6552 | 4.3898 | 4.7764 | 5.5497 | 6.3229 | 0.86879 | 2.36 | 2.96 | 2.96 | 2.96 | 2.96 | 2.4006 | 3.0471 | 3.0471 | 3.0471 | 3.0471 | 3.0471
2020-06-23 16:00 | Winter | 1.1432 | 1.7577 | 2.6598 | 2.6598 | 2.6598 | 2.6598 | 1.0145 | 1.0145 | 1.0145 | 1.0145 | 1.0145 | 1.0145 | 2.534 | 3.6552 | 4.3898 | 4.7764 | 5.5497 | 6.3229 | 0.83069 | 2.2565 | 2.8302 | 2.8302 | 2.8302 | 2.8302 | 2.3816 | 3.0229 | 3.0229 | 3.0229 | 3.0229 | 3.0229
2020-06-23 17:00 | Winter | 1.105 | 1.6991 | 2.5711 | 2.5711 | 2.5711 | 2.5711 | 0.93167 | 0.93167 | 0.93167 | 0.93167 | 0.93167 | 0.93167 | 2.7626 | 3.985 | 4.7859 | 5.2074 | 6.0504 | 6.8934 | 0.86498 | 2.3496 | 2.947 | 2.947 | 2.947 | 2.947 | 2.3054 | 2.9261 | 2.9261 | 2.9261 | 2.9261 | 2.9261
2020-06-23 18:00 | Winter | 0.99093 | 1.5237 | 2.3056 | 2.3056 | 2.3056 | 2.3056 | 0.8002 | 0.8002 | 0.8002 | 0.8002 | 0.8002 | 0.8002 | 2.7436 | 3.9575 | 4.7529 | 5.1715 | 6.0087 | 6.8459 | 0.86117 | 2.3393 | 2.934 | 2.934 | 2.934 | 2.934 | 1.6748 | 2.1258 | 2.1258 | 2.1258 | 2.1258 | 2.1258
2020-06-23 19:00 | Winter | 0.68589 | 1.0546 | 1.5959 | 1.5959 | 1.5959 | 1.5959 | 0.7259 | 0.7259 | 0.7259 | 0.7259 | 0.7259 | 0.7259 | 2.4779 | 3.5743 | 4.2927 | 4.6708 | 5.4269 | 6.1831 | 0.78496 | 2.1323 | 2.6744 | 2.6744 | 2.6744 | 2.6744 | 1.2384 | 1.5719 | 1.5719 | 1.5719 | 1.5719 | 1.5719
2020-06-23 20:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.47726 | 0.47726 | 0.47726 | 0.47726 | 0.47726 | 0.47726 | 2.3816 | 3.4353 | 4.1258 | 4.4891 | 5.2159 | 5.9426 | 0.73543 | 1.9977 | 2.5056 | 2.5056 | 2.5056 | 2.5056 | 1.1241 | 1.4268 | 1.4268 | 1.4268 | 1.4268 | 1.4268
2020-06-23 21:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 2.2336 | 3.2219 | 3.8694 | 4.2102 | 4.8918 | 5.5734 | 0.73543 | 1.9977 | 2.5056 | 2.5056 | 2.5056 | 2.5056 | 1.0448 | 1.3261 | 1.3261 | 1.3261 | 1.3261 | 1.3261
2020-06-23 22:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.43154 | 0.43154 | 0.43154 | 0.43154 | 0.43154 | 0.43154 | 2.0005 | 2.8857 | 3.4656 | 3.7709 | 4.3813 | 4.9918 | 0.73543 | 1.9977 | 2.5056 | 2.5056 | 2.5056 | 2.5056 | 0.91449 | 1.1607 | 1.1607 | 1.1607 | 1.1607 | 1.1607
2020-06-23 23:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 1.8672 | 2.6933 | 3.2346 | 3.5195 | 4.0892 | 4.659 | 0.59825 | 1.6251 | 2.0382 | 2.0382 | 2.0382 | 2.0382 | 0.91452 | 1.1608 | 1.1608 | 1.1608 | 1.1608 | 1.1608
2020-06-24 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.42582 | 0.42582 | 0.42582 | 0.42582 | 0.42582 | 0.42582 | 1.829 | 2.6383 | 3.1686 | 3.4477 | 4.0058 | 4.5639 | 0.57157 | 1.5526 | 1.9474 | 1.9474 | 1.9474 | 1.9474 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-06-24 01:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 1.7147 | 2.4735 | 2.9705 | 3.2322 | 3.7554 | 4.2787 | 0.56014 | 1.5216 | 1.9084 | 1.9084 | 1.9084 | 1.9084 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-06-24 02:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 1.6195 | 2.336 | 2.8055 | 3.0526 | 3.5468 | 4.041 | 0.5449 | 1.4802 | 1.8565 | 1.8565 | 1.8565 | 1.8565 | 1.086 | 1.3784 | 1.3784 | 1.3784 | 1.3784 | 1.3784
2020-06-24 03:00 | Winter | 0.57308 | 0.88118 | 1.3334 | 1.3334 | 1.3334 | 1.3334 | 0.43439 | 0.43439 | 0.43439 | 0.43439 | 0.43439 | 0.43439 | 1.7909 | 2.5834 | 3.1026 | 3.3758 | 3.9223 | 4.4688 | 0.52204 | 1.4181 | 1.7786 | 1.7786 | 1.7786 | 1.7786 | 1.0789 | 1.3695 | 1.3695 | 1.3695 | 1.3695 | 1.3695
2020-06-24 04:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.47441 | 0.47441 | 0.47441 | 0.47441 | 0.47441 | 0.47441 | 1.7276 | 2.4921 | 2.9929 | 3.2565 | 3.7837 | 4.3109 | 0.57223 | 1.5544 | 1.9496 | 1.9496 | 1.9496 | 1.9496 | 1.086 | 1.3784 | 1.3784 | 1.3784 | 1.3784 | 1.3784
2020-06-24 05:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.66017 | 0.66017 | 0.66017 | 0.66017 | 0.66017 | 0.66017 | 1.81 | 2.6109 | 3.1356 | 3.4117 | 3.9641 | 4.5164 | 0.64397 | 1.7493 | 2.194 | 2.194 | 2.194 | 2.194 | 1.5135 | 1.9211 | 1.9211 | 1.9211 | 1.9211 | 1.9211
2020-06-24 06:00 | Winter | 0.67733 | 1.0415 | 1.5759 | 1.5759 | 1.5759 | 1.5759 | 0.75162 | 0.75162 | 0.75162 | 0.75162 | 0.75162 | 0.75162 | 2.1464 | 3.0962 | 3.7184 | 4.0459 | 4.7009 | 5.3559 | 0.78496 | 2.1323 | 2.6744 | 2.6744 | 2.6744 | 2.6744 | 1.7794 | 2.2586 | 2.2586 | 2.2586 | 2.2586 | 2.2586
2020-06-24 07:00 | Winter | 1.0878 | 1.6727 | 2.5311 | 2.5311 | 2.5311 | 2.5311 | 0.85974 | 0.85974 | 0.85974 | 0.85974 | 0.85974 | 0.85974 | 2.498 | 3.6032 | 4.3274 | 4.7085 | 5.4708 | 6.2331 | 0.85355 | 2.3186 | 2.9081 | 2.9081 | 2.9081 | 2.9081 | 2.3054 | 2.9261 | 2.9261 | 2.9261 | 2.9261 | 2.9261
2020-06-24 08:00 | Winter | 1.2956 | 1.9921 | 3.0144 | 3.0144 | 3.0144 | 3.0144 | 0.99168 | 0.99168 | 0.99168 | 0.99168 | 0.99168 | 0.99168 | 2.6483 | 3.8201 | 4.5878 | 4.9919 | 5.8 | 6.6082 | 0.89166 | 2.4221 | 3.0379 | 3.0379 | 3.0379 | 3.0379 | 2.553 | 3.2405 | 3.2405 | 3.2405 | 3.2405 | 3.2405
2020-06-24 09:00 | Winter | 1.2956 | 1.9921 | 3.0144 | 3.0144 | 3.0144 | 3.0144 | 0.99454 | 0.99454 | 0.99454 | 0.99454 | 0.99454 | 0.99454 | 2.6483 | 3.8201 | 4.5878 | 4.9919 | 5.8 | 6.6082 | 0.89547 | 2.4325 | 3.0509 | 3.0509 | 3.0509 | 3.0509 | 2.6102 | 3.3131 | 3.3131 | 3.3131 | 3.3131 | 3.3131
2020-06-24 10:00 | Winter | 1.2194 | 1.8749 | 2.8371 | 2.8371 | 2.8371 | 2.8371 | 0.98597 | 0.98597 | 0.98597 | 0.98597 | 0.98597 | 0.98597 | 2.6483 | 3.8201 | 4.5878 | 4.9919 | 5.8 | 6.6082 | 0.88404 | 2.4014 | 3.0119 | 3.0119 | 3.0119 | 3.0119 | 2.6293 | 3.3373 | 3.3373 | 3.3373 | 3.3373 | 3.3373
2020-06-24 11:00 | Winter | 1.1744 | 1.8059 | 2.7326 | 2.7326 | 2.7326 | 2.7326 | 0.98311 | 0.98311 | 0.98311 | 0.98311 | 0.98311 | 0.98311 | 2.531 | 3.6509 | 4.3847 | 4.7708 | 5.5432 | 6.3156 | 0.81926 | 2.2254 | 2.7912 | 2.7912 | 2.7912 | 2.7912 | 2.553 | 3.2405 | 3.2405 | 3.2405 | 3.2405 | 3.2405
2020-06-24 12:00 | Winter | 1.2384 | 1.9042 | 2.8814 | 2.8814 | 2.8814 | 2.8814 | 1.0231 | 1.0231 | 1.0231 | 1.0231 | 1.0231 | 1.0231 | 2.4959 | 3.6002 | 4.3238 | 4.7046 | 5.4662 | 6.2279 | 0.7621 | 2.0702 | 2.5965 | 2.5965 | 2.5965 | 2.5965 | 2.4768 | 3.1438 | 3.1438 | 3.1438 | 3.1438 | 3.1438
2020-06-24 13:00 | Winter | 1.1813 | 1.8163 | 2.7485 | 2.7485 | 2.7485 | 2.7485 | 1.0374 | 1.0374 | 1.0374 | 1.0374 | 1.0374 | 1.0374 | 2.534 | 3.6552 | 4.3898 | 4.7764 | 5.5497 | 6.3229 | 0.80021 | 2.1737 | 2.7263 | 2.7263 | 2.7263 | 2.7263 | 2.4197 | 3.0712 | 3.0712 | 3.0712 | 3.0712 | 3.0712
2020-06-24 14:00 | Winter | 1.1813 | 1.8163 | 2.7485 | 2.7485 | 2.7485 | 2.7485 | 0.97739 | 0.97739 | 0.97739 | 0.97739 | 0.97739 | 0.97739 | 2.4387 | 3.5178 | 4.2248 | 4.5969 | 5.3411 | 6.0852 | 0.78877 | 2.1426 | 2.6874 | 2.6874 | 2.6874 | 2.6874 | 2.3244 | 2.9503 | 2.9503 | 2.9503 | 2.9503 | 2.9503
2020-06-24 15:00 | Winter | 1.1813 | 1.8163 | 2.7485 | 2.7485 | 2.7485 | 2.7485 | 1.006 | 1.006 | 1.006 | 1.006 | 1.006 | 1.006 | 2.4197 | 3.4903 | 4.1918 | 4.561 | 5.2993 | 6.0377 | 0.78115 | 2.1219 | 2.6614 | 2.6614 | 2.6614 | 2.6614 | 2.3007 | 2.9202 | 2.9202 | 2.9202 | 2.9202 | 2.9202
2020-06-24 16:00 | Winter | 1.1241 | 1.7284 | 2.6155 | 2.6155 | 2.6155 | 2.6155 | 0.95739 | 0.95739 | 0.95739 | 0.95739 | 0.95739 | 0.95739 | 2.4578 | 3.5453 | 4.2578 | 4.6328 | 5.3828 | 6.1328 | 0.80402 | 2.184 | 2.7393 | 2.7393 | 2.7393 | 2.7393 | 2.2291 | 2.8294 | 2.8294 | 2.8294 | 2.8294 | 2.8294
2020-06-24 17:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 0.93452 | 0.93452 | 0.93452 | 0.93452 | 0.93452 | 0.93452 | 2.6293 | 3.7926 | 4.5548 | 4.956 | 5.7583 | 6.5606 | 0.78877 | 2.1426 | 2.6874 | 2.6874 | 2.6874 | 2.6874 | 2.1529 | 2.7327 | 2.7327 | 2.7327 | 2.7327 | 2.7327
2020-06-24 18:00 | Winter | 0.89679 | 1.3789 | 2.0866 | 2.0866 | 2.0866 | 2.0866 | 0.82592 | 0.82592 | 0.82592 | 0.82592 | 0.82592 | 0.82592 | 2.5747 | 3.714 | 4.4604 | 4.8532 | 5.6389 | 6.4246 | 0.8345 | 2.2668 | 2.8432 | 2.8432 | 2.8432 | 2.8432 | 1.6102 | 2.0439 | 2.0439 | 2.0439 | 2.0439 | 2.0439
2020-06-24 19:00 | Winter | 0.67263 | 1.0342 | 1.565 | 1.565 | 1.565 | 1.565 | 0.63159 | 0.63159 | 0.63159 | 0.63159 | 0.63159 | 0.63159 | 2.4006 | 3.4628 | 4.1588 | 4.525 | 5.2576 | 5.9902 | 0.724 | 1.9667 | 2.4667 | 2.4667 | 2.4667 | 2.4667 | 1.1696 | 1.4845 | 1.4845 | 1.4845 | 1.4845 | 1.4845
2020-06-24 20:00 | Winter | 0.64825 | 0.99675 | 1.5083 | 1.5083 | 1.5083 | 1.5083 | 0.49727 | 0.49727 | 0.49727 | 0.49727 | 0.49727 | 0.49727 | 2.3054 | 3.3254 | 3.9937 | 4.3455 | 5.049 | 5.7525 | 0.69351 | 1.8839 | 2.3628 | 2.3628 | 2.3628 | 2.3628 | 1.0591 | 1.3443 | 1.3443 | 1.3443 | 1.3443 | 1.3443
2020-06-24 21:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.46869 | 0.46869 | 0.46869 | 0.46869 | 0.46869 | 0.46869 | 2.172 | 3.133 | 3.7627 | 4.0941 | 4.7569 | 5.4197 | 0.69732 | 1.8942 | 2.3758 | 2.3758 | 2.3758 | 2.3758 | 0.99073 | 1.2575 | 1.2575 | 1.2575 | 1.2575 | 1.2575
2020-06-24 22:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.39438 | 0.39438 | 0.39438 | 0.39438 | 0.39438 | 0.39438 | 2.0094 | 2.8985 | 3.4811 | 3.7877 | 4.4008 | 5.014 | 0.64779 | 1.7596 | 2.207 | 2.207 | 2.207 | 2.207 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-06-24 23:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.39152 | 0.39152 | 0.39152 | 0.39152 | 0.39152 | 0.39152 | 1.8672 | 2.6933 | 3.2346 | 3.5195 | 4.0892 | 4.659 | 0.61349 | 1.6665 | 2.0902 | 2.0902 | 2.0902 | 2.0902 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-06-25 | Winter | 0.58917 | 0.90592 | 1.3708 | 1.3708 | 1.3708 | 1.3708 | 0.35152 | 0.35152 | 0.35152 | 0.35152 | 0.35152 | 0.35152 | 1.7551 | 2.5317 | 3.0405 | 3.3083 | 3.8438 | 4.3794 | 0.5792 | 1.5733 | 1.9733 | 1.9733 | 1.9733 | 1.9733 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-06-25 01:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.3458 | 0.3458 | 0.3458 | 0.3458 | 0.3458 | 0.3458 | 1.6766 | 2.4185 | 2.9045 | 3.1603 | 3.672 | 4.1836 | 0.54109 | 1.4698 | 1.8435 | 1.8435 | 1.8435 | 1.8435 | 0.89423 | 1.135 | 1.135 | 1.135 | 1.135 | 1.135
2020-06-25 02:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.36009 | 0.36009 | 0.36009 | 0.36009 | 0.36009 | 0.36009 | 1.6957 | 2.446 | 2.9375 | 3.1963 | 3.7137 | 4.2311 | 0.52204 | 1.4181 | 1.7786 | 1.7786 | 1.7786 | 1.7786 | 1.0288 | 1.3059 | 1.3059 | 1.3059 | 1.3059 | 1.3059
2020-06-25 03:00 | Winter | 0.59175 | 0.90989 | 1.3768 | 1.3768 | 1.3768 | 1.3768 | 0.35437 | 0.35437 | 0.35437 | 0.35437 | 0.35437 | 0.35437 | 1.6576 | 2.391 | 2.8715 | 3.1244 | 3.6302 | 4.1361 | 0.5068 | 1.3767 | 1.7267 | 1.7267 | 1.7267 | 1.7267 | 1.0669 | 1.3542 | 1.3542 | 1.3542 | 1.3542 | 1.3542
2020-06-25 04:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 1.6679 | 2.406 | 2.8895 | 3.144 | 3.653 | 4.1619 | 0.56395 | 1.5319 | 1.9214 | 1.9214 | 1.9214 | 1.9214 | 1.0596 | 1.3449 | 1.3449 | 1.3449 | 1.3449 | 1.3449
2020-06-25 05:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.66017 | 0.66017 | 0.66017 | 0.66017 | 0.66017 | 0.66017 | 1.8352 | 2.6472 | 3.1792 | 3.4592 | 4.0193 | 4.5793 | 0.71637 | 1.946 | 2.4407 | 2.4407 | 2.4407 | 2.4407 | 1.4524 | 1.8435 | 1.8435 | 1.8435 | 1.8435 | 1.8435
2020-06-25 06:00 | Winter | 0.70494 | 1.0839 | 1.6402 | 1.6402 | 1.6402 | 1.6402 | 0.72876 | 0.72876 | 0.72876 | 0.72876 | 0.72876 | 0.72876 | 2.0577 | 2.9681 | 3.5647 | 3.8786 | 4.5065 | 5.1344 | 0.76591 | 2.0805 | 2.6095 | 2.6095 | 2.6095 | 2.6095 | 1.8765 | 2.3818 | 2.3818 | 2.3818 | 2.3818 | 2.3818
2020-06-25 07:00 | Winter | 1.0669 | 1.6405 | 2.4825 | 2.4825 | 2.4825 | 2.4825 | 0.86241 | 0.86241 | 0.86241 | 0.86241 | 0.86241 | 0.86241 | 2.4197 | 3.4903 | 4.1918 | 4.561 | 5.2993 | 6.0377 | 0.85355 | 2.3186 | 2.9081 | 2.9081 | 2.9081 | 2.9081 | 2.2101 | 2.8052 | 2.8052 | 2.8052 | 2.8052 | 2.8052
2020-06-25 08:00 | Winter | 1.3146 | 2.0214 | 3.0588 | 3.0588 | 3.0588 | 3.0588 | 0.97168 | 0.97168 | 0.97168 | 0.97168 | 0.97168 | 0.97168 | 2.6864 | 3.8751 | 4.6539 | 5.0637 | 5.8835 | 6.7033 | 0.94119 | 2.5567 | 3.2067 | 3.2067 | 3.2067 | 3.2067 | 2.553 | 3.2405 | 3.2405 | 3.2405 | 3.2405 | 3.2405
2020-06-25 09:00 | Winter | 1.2765 | 1.9628 | 2.9701 | 2.9701 | 2.9701 | 2.9701 | 0.98597 | 0.98597 | 0.98597 | 0.98597 | 0.98597 | 0.98597 | 2.6102 | 3.7651 | 4.5218 | 4.9201 | 5.7166 | 6.5131 | 0.93357 | 2.536 | 3.1807 | 3.1807 | 3.1807 | 3.1807 | 2.5721 | 3.2647 | 3.2647 | 3.2647 | 3.2647 | 3.2647
2020-06-25 10:00 | Winter | 1.2012 | 1.8469 | 2.7948 | 2.7948 | 2.7948 | 2.7948 | 0.92595 | 0.92595 | 0.92595 | 0.92595 | 0.92595 | 0.92595 | 2.7055 | 3.9026 | 4.6869 | 5.0996 | 5.9252 | 6.7508 | 0.83069 | 2.2565 | 2.8302 | 2.8302 | 2.8302 | 2.8302 | 2.534 | 3.2163 | 3.2163 | 3.2163 | 3.2163 | 3.2163
2020-06-25 11:00 | Winter | 1.2194 | 1.8749 | 2.8371 | 2.8371 | 2.8371 | 2.8371 | 0.9631 | 0.9631 | 0.9631 | 0.9631 | 0.9631 | 0.9631 | 2.5625 | 3.6963 | 4.4392 | 4.8302 | 5.6121 | 6.3941 | 0.81545 | 2.2151 | 2.7782 | 2.7782 | 2.7782 | 2.7782 | 2.4768 | 3.1438 | 3.1438 | 3.1438 | 3.1438 | 3.1438
2020-06-25 12:00 | Winter | 1.2575 | 1.9335 | 2.9258 | 2.9258 | 2.9258 | 2.9258 | 0.97739 | 0.97739 | 0.97739 | 0.97739 | 0.97739 | 0.97739 | 2.4959 | 3.6002 | 4.3238 | 4.7046 | 5.4662 | 6.2279 | 0.80021 | 2.1737 | 2.7263 | 2.7263 | 2.7263 | 2.7263 | 2.534 | 3.2163 | 3.2163 | 3.2163 | 3.2163 | 3.2163
2020-06-25 13:00 | Winter | 1.2575 | 1.9335 | 2.9258 | 2.9258 | 2.9258 | 2.9258 | 0.90595 | 0.90595 | 0.90595 | 0.90595 | 0.90595 | 0.90595 | 2.553 | 3.6827 | 4.4228 | 4.8123 | 5.5914 | 6.3705 | 0.78496 | 2.1323 | 2.6744 | 2.6744 | 2.6744 | 2.6744 | 2.3816 | 3.0229 | 3.0229 | 3.0229 | 3.0229 | 3.0229
2020-06-25 14:00 | Winter | 1.2173 | 1.8717 | 2.8322 | 2.8322 | 2.8322 | 2.8322 | 0.94596 | 0.94596 | 0.94596 | 0.94596 | 0.94596 | 0.94596 | 2.534 | 3.6552 | 4.3898 | 4.7764 | 5.5497 | 6.3229 | 0.77353 | 2.1012 | 2.6354 | 2.6354 | 2.6354 | 2.6354 | 2.3054 | 2.9261 | 2.9261 | 2.9261 | 2.9261 | 2.9261
2020-06-25 15:00 | Winter | 1.2003 | 1.8456 | 2.7928 | 2.7928 | 2.7928 | 2.7928 | 0.92881 | 0.92881 | 0.92881 | 0.92881 | 0.92881 | 0.92881 | 2.5721 | 3.7102 | 4.4558 | 4.8483 | 5.6331 | 6.418 | 0.82307 | 2.2358 | 2.8042 | 2.8042 | 2.8042 | 2.8042 | 2.2101 | 2.8052 | 2.8052 | 2.8052 | 2.8052 | 2.8052
2020-06-25 16:00 | Winter | 1.1432 | 1.7577 | 2.6598 | 2.6598 | 2.6598 | 2.6598 | 0.92023 | 0.92023 | 0.92023 | 0.92023 | 0.92023 | 0.92023 | 2.6293 | 3.7926 | 4.5548 | 4.956 | 5.7583 | 6.5606 | 0.79258 | 2.153 | 2.7003 | 2.7003 | 2.7003 | 2.7003 | 2.2482 | 2.8536 | 2.8536 | 2.8536 | 2.8536 | 2.8536
2020-06-25 17:00 | Winter | 1.1241 | 1.7284 | 2.6155 | 2.6155 | 2.6155 | 2.6155 | 0.92595 | 0.92595 | 0.92595 | 0.92595 | 0.92595 | 0.92595 | 2.7436 | 3.9575 | 4.7529 | 5.1715 | 6.0087 | 6.8459 | 0.80402 | 2.184 | 2.7393 | 2.7393 | 2.7393 | 2.7393 | 2.1148 | 2.6843 | 2.6843 | 2.6843 | 2.6843 | 2.6843
2020-06-25 18:00 | Winter | 0.99499 | 1.5299 | 2.3151 | 2.3151 | 2.3151 | 2.3151 | 0.77338 | 0.77338 | 0.77338 | 0.77338 | 0.77338 | 0.77338 | 2.6483 | 3.8201 | 4.5878 | 4.9919 | 5.8 | 6.6082 | 0.76972 | 2.0909 | 2.6225 | 2.6225 | 2.6225 | 2.6225 | 1.6648 | 2.1132 | 2.1132 | 2.1132 | 2.1132 | 2.1132
2020-06-25 19:00 | Winter | 0.70494 | 1.0839 | 1.6402 | 1.6402 | 1.6402 | 1.6402 | 0.66874 | 0.66874 | 0.66874 | 0.66874 | 0.66874 | 0.66874 | 2.5092 | 3.6195 | 4.3469 | 4.7298 | 5.4955 | 6.2612 | 0.74686 | 2.0288 | 2.5446 | 2.5446 | 2.5446 | 2.5446 | 1.1813 | 1.4993 | 1.4993 | 1.4993 | 1.4993 | 1.4993
2020-06-25 20:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.53442 | 0.53442 | 0.53442 | 0.53442 | 0.53442 | 0.53442 | 2.3539 | 3.3955 | 4.0779 | 4.4371 | 5.1554 | 5.8737 | 0.77734 | 2.1116 | 2.6484 | 2.6484 | 2.6484 | 2.6484 | 1.086 | 1.3784 | 1.3784 | 1.3784 | 1.3784 | 1.3784
2020-06-25 21:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.53156 | 0.53156 | 0.53156 | 0.53156 | 0.53156 | 0.53156 | 2.2482 | 3.243 | 3.8947 | 4.2377 | 4.9238 | 5.6098 | 0.67065 | 1.8218 | 2.2849 | 2.2849 | 2.2849 | 2.2849 | 1.0098 | 1.2817 | 1.2817 | 1.2817 | 1.2817 | 1.2817
2020-06-25 22:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.5287 | 0.5287 | 0.5287 | 0.5287 | 0.5287 | 0.5287 | 2.1148 | 3.0506 | 3.6637 | 3.9863 | 4.6317 | 5.277 | 0.71637 | 1.946 | 2.4407 | 2.4407 | 2.4407 | 2.4407 | 0.97586 | 1.2386 | 1.2386 | 1.2386 | 1.2386 | 1.2386
2020-06-25 23:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 2.0005 | 2.8857 | 3.4656 | 3.7709 | 4.3813 | 4.9918 | 0.6377 | 1.7323 | 2.1727 | 2.1727 | 2.1727 | 2.1727 | 0.95263 | 1.2092 | 1.2092 | 1.2092 | 1.2092 | 1.2092
2020-06-26 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 1.81 | 2.6109 | 3.1356 | 3.4117 | 3.9641 | 4.5164 | 0.56014 | 1.5216 | 1.9084 | 1.9084 | 1.9084 | 1.9084 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-06-26 01:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 1.6766 | 2.4185 | 2.9045 | 3.1603 | 3.672 | 4.1836 | 0.56776 | 1.5423 | 1.9344 | 1.9344 | 1.9344 | 1.9344 | 0.87984 | 1.1168 | 1.1168 | 1.1168 | 1.1168 | 1.1168
2020-06-26 02:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 1.6576 | 2.391 | 2.8715 | 3.1244 | 3.6302 | 4.1361 | 0.55633 | 1.5112 | 1.8954 | 1.8954 | 1.8954 | 1.8954 | 1.0479 | 1.3301 | 1.3301 | 1.3301 | 1.3301 | 1.3301
2020-06-26 03:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.51823 | 1.4077 | 1.7656 | 1.7656 | 1.7656 | 1.7656 | 1.0795 | 1.3702 | 1.3702 | 1.3702 | 1.3702 | 1.3702
2020-06-26 04:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 1.7147 | 2.4735 | 2.9705 | 3.2322 | 3.7554 | 4.2787 | 0.54871 | 1.4905 | 1.8695 | 1.8695 | 1.8695 | 1.8695 | 1.1497 | 1.4593 | 1.4593 | 1.4593 | 1.4593 | 1.4593
2020-06-26 05:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.68846 | 0.68846 | 0.68846 | 0.68846 | 0.68846 | 0.68846 | 1.81 | 2.6109 | 3.1356 | 3.4117 | 3.9641 | 4.5164 | 0.67065 | 1.8218 | 2.2849 | 2.2849 | 2.2849 | 2.2849 | 1.5266 | 1.9377 | 1.9377 | 1.9377 | 1.9377 | 1.9377
2020-06-26 06:00 | Winter | 0.68625 | 1.0552 | 1.5967 | 1.5967 | 1.5967 | 1.5967 | 0.79163 | 0.79163 | 0.79163 | 0.79163 | 0.79163 | 0.79163 | 2.0958 | 3.0231 | 3.6307 | 3.9504 | 4.59 | 5.2295 | 0.78496 | 2.1323 | 2.6744 | 2.6744 | 2.6744 | 2.6744 | 1.876 | 2.3812 | 2.3812 | 2.3812 | 2.3812 | 2.3812
2020-06-26 07:00 | Winter | 1.0858 | 1.6695 | 2.5263 | 2.5263 | 2.5263 | 2.5263 | 0.88022 | 0.88022 | 0.88022 | 0.88022 | 0.88022 | 0.88022 | 2.4197 | 3.4903 | 4.1918 | 4.561 | 5.2993 | 6.0377 | 0.87261 | 2.3704 | 2.973 | 2.973 | 2.973 | 2.973 | 2.3054 | 2.9261 | 2.9261 | 2.9261 | 2.9261 | 2.9261
2020-06-26 08:00 | Winter | 1.2794 | 1.9673 | 2.9769 | 2.9769 | 2.9769 | 2.9769 | 1.0231 | 1.0231 | 1.0231 | 1.0231 | 1.0231 | 1.0231 | 2.6102 | 3.7651 | 4.5218 | 4.9201 | 5.7166 | 6.5131 | 0.9069 | 2.4635 | 3.0898 | 3.0898 | 3.0898 | 3.0898 | 2.534 | 3.2163 | 3.2163 | 3.2163 | 3.2163 | 3.2163
2020-06-26 09:00 | Winter | 1.2956 | 1.9921 | 3.0144 | 3.0144 | 3.0144 | 3.0144 | 1.0231 | 1.0231 | 1.0231 | 1.0231 | 1.0231 | 1.0231 | 2.7245 | 3.93 | 4.7199 | 5.1356 | 5.967 | 6.7984 | 0.88023 | 2.3911 | 2.9989 | 2.9989 | 2.9989 | 2.9989 | 2.6102 | 3.3131 | 3.3131 | 3.3131 | 3.3131 | 3.3131
2020-06-26 10:00 | Winter | 1.2765 | 1.9628 | 2.9701 | 2.9701 | 2.9701 | 2.9701 | 0.99454 | 0.99454 | 0.99454 | 0.99454 | 0.99454 | 0.99454 | 2.7436 | 3.9575 | 4.7529 | 5.1715 | 6.0087 | 6.8459 | 0.85736 | 2.3289 | 2.9211 | 2.9211 | 2.9211 | 2.9211 | 2.5911 | 3.2889 | 3.2889 | 3.2889 | 3.2889 | 3.2889
2020-06-26 11:00 | Winter | 1.2384 | 1.9042 | 2.8814 | 2.8814 | 2.8814 | 2.8814 | 1.0088 | 1.0088 | 1.0088 | 1.0088 | 1.0088 | 1.0088 | 2.6437 | 3.8135 | 4.5799 | 4.9833 | 5.79 | 6.5968 | 0.91071 | 2.4739 | 3.1028 | 3.1028 | 3.1028 | 3.1028 | 2.5911 | 3.2889 | 3.2889 | 3.2889 | 3.2889 | 3.2889
2020-06-26 12:00 | Winter | 1.1813 | 1.8163 | 2.7485 | 2.7485 | 2.7485 | 2.7485 | 0.93452 | 0.93452 | 0.93452 | 0.93452 | 0.93452 | 0.93452 | 2.534 | 3.6552 | 4.3898 | 4.7764 | 5.5497 | 6.3229 | 0.82307 | 2.2358 | 2.8042 | 2.8042 | 2.8042 | 2.8042 | 2.534 | 3.2163 | 3.2163 | 3.2163 | 3.2163 | 3.2163
2020-06-26 13:00 | Winter | 1.2194 | 1.8749 | 2.8371 | 2.8371 | 2.8371 | 2.8371 | 0.96596 | 0.96596 | 0.96596 | 0.96596 | 0.96596 | 0.96596 | 2.4578 | 3.5453 | 4.2578 | 4.6328 | 5.3828 | 6.1328 | 0.80783 | 2.1944 | 2.7523 | 2.7523 | 2.7523 | 2.7523 | 2.4578 | 3.1196 | 3.1196 | 3.1196 | 3.1196 | 3.1196
2020-06-26 14:00 | Winter | 1.1813 | 1.8163 | 2.7485 | 2.7485 | 2.7485 | 2.7485 | 1.0003 | 1.0003 | 1.0003 | 1.0003 | 1.0003 | 1.0003 | 2.4768 | 3.5728 | 4.2908 | 4.6687 | 5.4245 | 6.1803 | 0.83069 | 2.2565 | 2.8302 | 2.8302 | 2.8302 | 2.8302 | 2.3244 | 2.9503 | 2.9503 | 2.9503 | 2.9503 | 2.9503
2020-06-26 15:00 | Winter | 1.1813 | 1.8163 | 2.7485 | 2.7485 | 2.7485 | 2.7485 | 0.98597 | 0.98597 | 0.98597 | 0.98597 | 0.98597 | 0.98597 | 2.4387 | 3.5178 | 4.2248 | 4.5969 | 5.3411 | 6.0852 | 0.87261 | 2.3704 | 2.973 | 2.973 | 2.973 | 2.973 | 2.2101 | 2.8052 | 2.8052 | 2.8052 | 2.8052 | 2.8052
2020-06-26 16:00 | Winter | 1.105 | 1.6991 | 2.5711 | 2.5711 | 2.5711 | 2.5711 | 0.95739 | 0.95739 | 0.95739 | 0.95739 | 0.95739 | 0.95739 | 2.4197 | 3.4903 | 4.1918 | 4.561 | 5.2993 | 6.0377 | 0.81926 | 2.2254 | 2.7912 | 2.7912 | 2.7912 | 2.7912 | 2.2673 | 2.8778 | 2.8778 | 2.8778 | 2.8778 | 2.8778
2020-06-26 17:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 0.92595 | 0.92595 | 0.92595 | 0.92595 | 0.92595 | 0.92595 | 2.5911 | 3.7377 | 4.4888 | 4.8842 | 5.6749 | 6.4656 | 0.89547 | 2.4325 | 3.0509 | 3.0509 | 3.0509 | 3.0509 | 2.095 | 2.6592 | 2.6592 | 2.6592 | 2.6592 | 2.6592
2020-06-26 18:00 | Winter | 0.93414 | 1.4364 | 2.1735 | 2.1735 | 2.1735 | 2.1735 | 0.87451 | 0.87451 | 0.87451 | 0.87451 | 0.87451 | 0.87451 | 2.5161 | 3.6294 | 4.3588 | 4.7428 | 5.5106 | 6.2784 | 0.87642 | 2.3807 | 2.986 | 2.986 | 2.986 | 2.986 | 1.6585 | 2.1051 | 2.1051 | 2.1051 | 2.1051 | 2.1051
2020-06-26 19:00 | Winter | 0.63098 | 0.9702 | 1.4681 | 1.4681 | 1.4681 | 1.4681 | 0.76398 | 0.76398 | 0.76398 | 0.76398 | 0.76398 | 0.76398 | 2.3357 | 3.3691 | 4.0462 | 4.4026 | 5.1153 | 5.8281 | 0.74305 | 2.0184 | 2.5316 | 2.5316 | 2.5316 | 2.5316 | 1.1437 | 1.4516 | 1.4516 | 1.4516 | 1.4516 | 1.4516
2020-06-26 20:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.60873 | 0.60873 | 0.60873 | 0.60873 | 0.60873 | 0.60873 | 2.1999 | 3.1733 | 3.811 | 4.1467 | 4.818 | 5.4893 | 0.71256 | 1.9356 | 2.4277 | 2.4277 | 2.4277 | 2.4277 | 1.105 | 1.4026 | 1.4026 | 1.4026 | 1.4026 | 1.4026
2020-06-26 21:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.55728 | 0.55728 | 0.55728 | 0.55728 | 0.55728 | 0.55728 | 2.2101 | 3.188 | 3.8287 | 4.1659 | 4.8403 | 5.5147 | 0.67827 | 1.8425 | 2.3109 | 2.3109 | 2.3109 | 2.3109 | 1.0479 | 1.3301 | 1.3301 | 1.3301 | 1.3301 | 1.3301
2020-06-26 22:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.50584 | 0.50584 | 0.50584 | 0.50584 | 0.50584 | 0.50584 | 2.1339 | 3.0781 | 3.6967 | 4.0223 | 4.6734 | 5.3246 | 0.73162 | 1.9874 | 2.4926 | 2.4926 | 2.4926 | 2.4926 | 0.97178 | 1.2335 | 1.2335 | 1.2335 | 1.2335 | 1.2335
2020-06-26 23:00 | Winter | 0.57102 | 0.878 | 1.3286 | 1.3286 | 1.3286 | 1.3286 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 1.9815 | 2.8582 | 3.4326 | 3.735 | 4.3396 | 4.9443 | 0.62111 | 1.6872 | 2.1161 | 2.1161 | 2.1161 | 2.1161 | 0.93358 | 1.185 | 1.185 | 1.185 | 1.185 | 1.185
2020-06-27 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 1.829 | 2.6383 | 3.1686 | 3.4477 | 4.0058 | 4.5639 | 0.56395 | 1.5319 | 1.9214 | 1.9214 | 1.9214 | 1.9214 | 0.91452 | 1.1608 | 1.1608 | 1.1608 | 1.1608 | 1.1608
2020-06-27 01:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.41439 | 0.41439 | 0.41439 | 0.41439 | 0.41439 | 0.41439 | 1.7719 | 2.5559 | 3.0696 | 3.3399 | 3.8806 | 4.4213 | 0.55252 | 1.5009 | 1.8825 | 1.8825 | 1.8825 | 1.8825 | 0.91452 | 1.1608 | 1.1608 | 1.1608 | 1.1608 | 1.1608
2020-06-27 02:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 1.7147 | 2.4735 | 2.9705 | 3.2322 | 3.7554 | 4.2787 | 0.55633 | 1.5112 | 1.8954 | 1.8954 | 1.8954 | 1.8954 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-06-27 03:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 1.6576 | 2.391 | 2.8715 | 3.1244 | 3.6302 | 4.1361 | 0.51823 | 1.4077 | 1.7656 | 1.7656 | 1.7656 | 1.7656 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-06-27 04:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 1.6766 | 2.4185 | 2.9045 | 3.1603 | 3.672 | 4.1836 | 0.51442 | 1.3974 | 1.7526 | 1.7526 | 1.7526 | 1.7526 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-06-27 05:00 | Winter | 0.55262 | 0.84971 | 1.2858 | 1.2858 | 1.2858 | 1.2858 | 0.51727 | 0.51727 | 0.51727 | 0.51727 | 0.51727 | 0.51727 | 1.7528 | 2.5284 | 3.0366 | 3.304 | 3.8389 | 4.3738 | 0.53728 | 1.4595 | 1.8305 | 1.8305 | 1.8305 | 1.8305 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-06-27 06:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.50013 | 0.50013 | 0.50013 | 0.50013 | 0.50013 | 0.50013 | 1.829 | 2.6383 | 3.1686 | 3.4477 | 4.0058 | 4.5639 | 0.59825 | 1.6251 | 2.0382 | 2.0382 | 2.0382 | 2.0382 | 1.0574 | 1.3422 | 1.3422 | 1.3422 | 1.3422 | 1.3422
2020-06-27 07:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.59158 | 0.59158 | 0.59158 | 0.59158 | 0.59158 | 0.59158 | 1.9807 | 2.8571 | 3.4313 | 3.7335 | 4.3379 | 4.9423 | 0.61349 | 1.6665 | 2.0902 | 2.0902 | 2.0902 | 2.0902 | 1.086 | 1.3784 | 1.3784 | 1.3784 | 1.3784 | 1.3784
2020-06-27 08:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.65731 | 0.65731 | 0.65731 | 0.65731 | 0.65731 | 0.65731 | 2.172 | 3.133 | 3.7627 | 4.0941 | 4.7569 | 5.4197 | 0.68208 | 1.8528 | 2.3239 | 2.3239 | 2.3239 | 2.3239 | 1.0669 | 1.3542 | 1.3542 | 1.3542 | 1.3542 | 1.3542
2020-06-27 09:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.67446 | 0.67446 | 0.67446 | 0.67446 | 0.67446 | 0.67446 | 2.172 | 3.133 | 3.7627 | 4.0941 | 4.7569 | 5.4197 | 0.67446 | 1.8321 | 2.2979 | 2.2979 | 2.2979 | 2.2979 | 1.105 | 1.4026 | 1.4026 | 1.4026 | 1.4026 | 1.4026
2020-06-27 10:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.66303 | 0.66303 | 0.66303 | 0.66303 | 0.66303 | 0.66303 | 2.3054 | 3.3254 | 3.9937 | 4.3455 | 5.049 | 5.7525 | 0.6897 | 1.8735 | 2.3498 | 2.3498 | 2.3498 | 2.3498 | 1.1813 | 1.4993 | 1.4993 | 1.4993 | 1.4993 | 1.4993
2020-06-27 11:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.63159 | 0.63159 | 0.63159 | 0.63159 | 0.63159 | 0.63159 | 2.2779 | 3.2858 | 3.9461 | 4.2936 | 4.9887 | 5.6838 | 0.64779 | 1.7596 | 2.207 | 2.207 | 2.207 | 2.207 | 1.1622 | 1.4752 | 1.4752 | 1.4752 | 1.4752 | 1.4752
2020-06-27 12:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.68017 | 0.68017 | 0.68017 | 0.68017 | 0.68017 | 0.68017 | 2.1148 | 3.0506 | 3.6637 | 3.9863 | 4.6317 | 5.277 | 0.65453 | 1.778 | 2.23 | 2.23 | 2.23 | 2.23 | 1.1241 | 1.4268 | 1.4268 | 1.4268 | 1.4268 | 1.4268
2020-06-27 13:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.62873 | 0.62873 | 0.62873 | 0.62873 | 0.62873 | 0.62873 | 2.0958 | 3.0231 | 3.6307 | 3.9504 | 4.59 | 5.2295 | 0.66684 | 1.8114 | 2.2719 | 2.2719 | 2.2719 | 2.2719 | 1.1432 | 1.451 | 1.451 | 1.451 | 1.451 | 1.451
2020-06-27 14:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.65731 | 0.65731 | 0.65731 | 0.65731 | 0.65731 | 0.65731 | 2.1514 | 3.1033 | 3.727 | 4.0552 | 4.7117 | 5.3682 | 0.67827 | 1.8425 | 2.3109 | 2.3109 | 2.3109 | 2.3109 | 1.086 | 1.3784 | 1.3784 | 1.3784 | 1.3784 | 1.3784
2020-06-27 15:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.61158 | 0.61158 | 0.61158 | 0.61158 | 0.61158 | 0.61158 | 2.191 | 3.1605 | 3.7957 | 4.13 | 4.7986 | 5.4672 | 0.69732 | 1.8942 | 2.3758 | 2.3758 | 2.3758 | 2.3758 | 0.99073 | 1.2575 | 1.2575 | 1.2575 | 1.2575 | 1.2575
2020-06-27 16:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.61158 | 0.61158 | 0.61158 | 0.61158 | 0.61158 | 0.61158 | 2.2482 | 3.243 | 3.8947 | 4.2377 | 4.9238 | 5.6098 | 0.7621 | 2.0702 | 2.5965 | 2.5965 | 2.5965 | 2.5965 | 1.0098 | 1.2817 | 1.2817 | 1.2817 | 1.2817 | 1.2817
2020-06-27 17:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.60586 | 0.60586 | 0.60586 | 0.60586 | 0.60586 | 0.60586 | 2.3625 | 3.4079 | 4.0927 | 4.4532 | 5.1741 | 5.8951 | 0.8345 | 2.2668 | 2.8432 | 2.8432 | 2.8432 | 2.8432 | 1.086 | 1.3784 | 1.3784 | 1.3784 | 1.3784 | 1.3784
2020-06-27 18:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.70018 | 0.70018 | 0.70018 | 0.70018 | 0.70018 | 0.70018 | 2.3054 | 3.3254 | 3.9937 | 4.3455 | 5.049 | 5.7525 | 0.85736 | 2.3289 | 2.9211 | 2.9211 | 2.9211 | 2.9211 | 1.0301 | 1.3075 | 1.3075 | 1.3075 | 1.3075 | 1.3075
2020-06-27 19:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.58872 | 0.58872 | 0.58872 | 0.58872 | 0.58872 | 0.58872 | 2.2482 | 3.243 | 3.8947 | 4.2377 | 4.9238 | 5.6098 | 0.80402 | 2.184 | 2.7393 | 2.7393 | 2.7393 | 2.7393 | 0.97168 | 1.2333 | 1.2333 | 1.2333 | 1.2333 | 1.2333
2020-06-27 20:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.56586 | 0.56586 | 0.56586 | 0.56586 | 0.56586 | 0.56586 | 2.191 | 3.1605 | 3.7957 | 4.13 | 4.7986 | 5.4672 | 0.76972 | 2.0909 | 2.6225 | 2.6225 | 2.6225 | 2.6225 | 0.97168 | 1.2333 | 1.2333 | 1.2333 | 1.2333 | 1.2333
2020-06-27 21:00 | Winter | 0.57185 | 0.87929 | 1.3305 | 1.3305 | 1.3305 | 1.3305 | 0.49155 | 0.49155 | 0.49155 | 0.49155 | 0.49155 | 0.49155 | 2.0958 | 3.0231 | 3.6307 | 3.9504 | 4.59 | 5.2295 | 0.77734 | 2.1116 | 2.6484 | 2.6484 | 2.6484 | 2.6484 | 0.96133 | 1.2202 | 1.2202 | 1.2202 | 1.2202 | 1.2202
2020-06-27 22:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.46869 | 0.46869 | 0.46869 | 0.46869 | 0.46869 | 0.46869 | 2.0386 | 2.9407 | 3.5316 | 3.8427 | 4.4648 | 5.0869 | 0.68208 | 1.8528 | 2.3239 | 2.3239 | 2.3239 | 2.3239 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-06-27 23:00 | Winter | 0.5534 | 0.85091 | 1.2876 | 1.2876 | 1.2876 | 1.2876 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 1.8582 | 2.6805 | 3.2192 | 3.5027 | 4.0697 | 4.6368 | 0.61876 | 1.6808 | 2.1081 | 2.1081 | 2.1081 | 2.1081 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-06-28 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 1.7528 | 2.5284 | 3.0366 | 3.304 | 3.8389 | 4.3738 | 0.5792 | 1.5733 | 1.9733 | 1.9733 | 1.9733 | 1.9733 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-06-28 01:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.54109 | 1.4698 | 1.8435 | 1.8435 | 1.8435 | 1.8435 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-06-28 02:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 1.6576 | 2.391 | 2.8715 | 3.1244 | 3.6302 | 4.1361 | 0.53728 | 1.4595 | 1.8305 | 1.8305 | 1.8305 | 1.8305 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-06-28 03:00 | Winter | 0.57239 | 0.88011 | 1.3318 | 1.3318 | 1.3318 | 1.3318 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 1.6766 | 2.4185 | 2.9045 | 3.1603 | 3.672 | 4.1836 | 0.52585 | 1.4284 | 1.7916 | 1.7916 | 1.7916 | 1.7916 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-06-28 04:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 1.6004 | 2.3086 | 2.7725 | 3.0167 | 3.5051 | 3.9934 | 0.53728 | 1.4595 | 1.8305 | 1.8305 | 1.8305 | 1.8305 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-06-28 05:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.51442 | 0.51442 | 0.51442 | 0.51442 | 0.51442 | 0.51442 | 1.7147 | 2.4735 | 2.9705 | 3.2322 | 3.7554 | 4.2787 | 0.57539 | 1.563 | 1.9603 | 1.9603 | 1.9603 | 1.9603 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-06-28 06:00 | Winter | 0.5722 | 0.87983 | 1.3314 | 1.3314 | 1.3314 | 1.3314 | 0.53728 | 0.53728 | 0.53728 | 0.53728 | 0.53728 | 0.53728 | 1.8756 | 2.7055 | 3.2492 | 3.5354 | 4.1077 | 4.68 | 0.5792 | 1.5733 | 1.9733 | 1.9733 | 1.9733 | 1.9733 | 0.95263 | 1.2092 | 1.2092 | 1.2092 | 1.2092 | 1.2092
2020-06-28 07:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.64016 | 0.64016 | 0.64016 | 0.64016 | 0.64016 | 0.64016 | 1.9053 | 2.7483 | 3.3006 | 3.5913 | 4.1727 | 4.7541 | 0.6173 | 1.6768 | 2.1032 | 2.1032 | 2.1032 | 2.1032 | 0.93358 | 1.185 | 1.185 | 1.185 | 1.185 | 1.185
2020-06-28 08:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.64016 | 0.64016 | 0.64016 | 0.64016 | 0.64016 | 0.64016 | 2.1339 | 3.0781 | 3.6967 | 4.0223 | 4.6734 | 5.3246 | 0.65922 | 1.7907 | 2.246 | 2.246 | 2.246 | 2.246 | 0.93279 | 1.184 | 1.184 | 1.184 | 1.184 | 1.184
2020-06-28 09:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.65731 | 0.65731 | 0.65731 | 0.65731 | 0.65731 | 0.65731 | 2.2482 | 3.243 | 3.8947 | 4.2377 | 4.9238 | 5.6098 | 0.70494 | 1.9149 | 2.4018 | 2.4018 | 2.4018 | 2.4018 | 0.97168 | 1.2333 | 1.2333 | 1.2333 | 1.2333 | 1.2333
2020-06-28 10:00 | Winter | 0.6096 | 0.93733 | 1.4184 | 1.4184 | 1.4184 | 1.4184 | 0.57729 | 0.57729 | 0.57729 | 0.57729 | 0.57729 | 0.57729 | 2.2863 | 3.2979 | 3.9607 | 4.3096 | 5.0072 | 5.7049 | 0.67446 | 1.8321 | 2.2979 | 2.2979 | 2.2979 | 2.2979 | 0.95263 | 1.2092 | 1.2092 | 1.2092 | 1.2092 | 1.2092
2020-06-28 11:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.59729 | 0.59729 | 0.59729 | 0.59729 | 0.59729 | 0.59729 | 2.172 | 3.133 | 3.7627 | 4.0941 | 4.7569 | 5.4197 | 0.6173 | 1.6768 | 2.1032 | 2.1032 | 2.1032 | 2.1032 | 0.97168 | 1.2333 | 1.2333 | 1.2333 | 1.2333 | 1.2333
2020-06-28 12:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.5319 | 0.5319 | 0.5319 | 0.5319 | 0.5319 | 0.5319 | 2.172 | 3.133 | 3.7627 | 4.0941 | 4.7569 | 5.4197 | 0.64016 | 1.7389 | 2.1811 | 2.1811 | 2.1811 | 2.1811 | 1.0288 | 1.3059 | 1.3059 | 1.3059 | 1.3059 | 1.3059
2020-06-28 13:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.55157 | 0.55157 | 0.55157 | 0.55157 | 0.55157 | 0.55157 | 2.1339 | 3.0781 | 3.6967 | 4.0223 | 4.6734 | 5.3246 | 0.58682 | 1.594 | 1.9993 | 1.9993 | 1.9993 | 1.9993 | 0.93358 | 1.185 | 1.185 | 1.185 | 1.185 | 1.185
2020-06-28 14:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.56014 | 0.56014 | 0.56014 | 0.56014 | 0.56014 | 0.56014 | 2.1148 | 3.0506 | 3.6637 | 3.9863 | 4.6317 | 5.277 | 0.58301 | 1.5837 | 1.9863 | 1.9863 | 1.9863 | 1.9863 | 0.93358 | 1.185 | 1.185 | 1.185 | 1.185 | 1.185
2020-06-28 15:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.58015 | 0.58015 | 0.58015 | 0.58015 | 0.58015 | 0.58015 | 2.1138 | 3.0491 | 3.6619 | 3.9844 | 4.6294 | 5.2744 | 0.64016 | 1.7389 | 2.1811 | 2.1811 | 2.1811 | 2.1811 | 0.91452 | 1.1608 | 1.1608 | 1.1608 | 1.1608 | 1.1608
2020-06-28 16:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.53442 | 0.53442 | 0.53442 | 0.53442 | 0.53442 | 0.53442 | 2.1529 | 3.1056 | 3.7297 | 4.0582 | 4.7151 | 5.3721 | 0.70113 | 1.9046 | 2.3888 | 2.3888 | 2.3888 | 2.3888 | 0.95263 | 1.2092 | 1.2092 | 1.2092 | 1.2092 | 1.2092
2020-06-28 17:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.57157 | 0.57157 | 0.57157 | 0.57157 | 0.57157 | 0.57157 | 2.3435 | 3.3804 | 4.0597 | 4.4173 | 5.1324 | 5.8475 | 0.74305 | 2.0184 | 2.5316 | 2.5316 | 2.5316 | 2.5316 | 0.93358 | 1.185 | 1.185 | 1.185 | 1.185 | 1.185
2020-06-28 18:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.59158 | 0.59158 | 0.59158 | 0.59158 | 0.59158 | 0.59158 | 2.3625 | 3.4079 | 4.0927 | 4.4532 | 5.1741 | 5.8951 | 0.75448 | 2.0495 | 2.5705 | 2.5705 | 2.5705 | 2.5705 | 0.91163 | 1.1571 | 1.1571 | 1.1571 | 1.1571 | 1.1571
2020-06-28 19:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.58586 | 0.58586 | 0.58586 | 0.58586 | 0.58586 | 0.58586 | 2.2863 | 3.2979 | 3.9607 | 4.3096 | 5.0072 | 5.7049 | 0.75067 | 2.0391 | 2.5575 | 2.5575 | 2.5575 | 2.5575 | 0.97168 | 1.2333 | 1.2333 | 1.2333 | 1.2333 | 1.2333
2020-06-28 20:00 | Winter | 0.59802 | 0.91953 | 1.3914 | 1.3914 | 1.3914 | 1.3914 | 0.54299 | 0.54299 | 0.54299 | 0.54299 | 0.54299 | 0.54299 | 2.217 | 3.1979 | 3.8406 | 4.1788 | 4.8553 | 5.5319 | 0.69351 | 1.8839 | 2.3628 | 2.3628 | 2.3628 | 2.3628 | 0.97168 | 1.2333 | 1.2333 | 1.2333 | 1.2333 | 1.2333
2020-06-28 21:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.49727 | 0.49727 | 0.49727 | 0.49727 | 0.49727 | 0.49727 | 2.0652 | 2.979 | 3.5776 | 3.8927 | 4.5229 | 5.1531 | 0.73543 | 1.9977 | 2.5056 | 2.5056 | 2.5056 | 2.5056 | 0.95263 | 1.2092 | 1.2092 | 1.2092 | 1.2092 | 1.2092
2020-06-28 22:00 | Winter | 0.57151 | 0.87876 | 1.3297 | 1.3297 | 1.3297 | 1.3297 | 0.47441 | 0.47441 | 0.47441 | 0.47441 | 0.47441 | 0.47441 | 1.9434 | 2.8032 | 3.3666 | 3.6631 | 4.2562 | 4.8492 | 0.68589 | 1.8632 | 2.3368 | 2.3368 | 2.3368 | 2.3368 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-06-28 23:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.47441 | 0.47441 | 0.47441 | 0.47441 | 0.47441 | 0.47441 | 1.7721 | 2.5563 | 3.07 | 3.3404 | 3.8812 | 4.422 | 0.57157 | 1.5526 | 1.9474 | 1.9474 | 1.9474 | 1.9474 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-06-29 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 1.696 | 2.4464 | 2.9381 | 3.1968 | 3.7144 | 4.2319 | 0.53728 | 1.4595 | 1.8305 | 1.8305 | 1.8305 | 1.8305 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-06-29 01:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 1.6576 | 2.391 | 2.8715 | 3.1244 | 3.6302 | 4.1361 | 0.54871 | 1.4905 | 1.8695 | 1.8695 | 1.8695 | 1.8695 | 0.91452 | 1.1608 | 1.1608 | 1.1608 | 1.1608 | 1.1608
2020-06-29 02:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.55443 | 0.55443 | 0.55443 | 0.55443 | 0.55443 | 0.55443 | 1.6195 | 2.336 | 2.8055 | 3.0526 | 3.5468 | 4.041 | 0.52204 | 1.4181 | 1.7786 | 1.7786 | 1.7786 | 1.7786 | 1.1241 | 1.4268 | 1.4268 | 1.4268 | 1.4268 | 1.4268
2020-06-29 03:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.48869 | 0.48869 | 0.48869 | 0.48869 | 0.48869 | 0.48869 | 1.5623 | 2.2536 | 2.7065 | 2.9449 | 3.4216 | 3.8984 | 0.54109 | 1.4698 | 1.8435 | 1.8435 | 1.8435 | 1.8435 | 1.1432 | 1.451 | 1.451 | 1.451 | 1.451 | 1.451
2020-06-29 04:00 | Winter | 0.66684 | 1.0253 | 1.5515 | 1.5515 | 1.5515 | 1.5515 | 0.51442 | 0.51442 | 0.51442 | 0.51442 | 0.51442 | 0.51442 | 1.702 | 2.455 | 2.9484 | 3.2081 | 3.7274 | 4.2468 | 0.54077 | 1.4689 | 1.8424 | 1.8424 | 1.8424 | 1.8424 | 1.1878 | 1.5077 | 1.5077 | 1.5077 | 1.5077 | 1.5077
2020-06-29 05:00 | Winter | 0.78115 | 1.2011 | 1.8175 | 1.8175 | 1.8175 | 1.8175 | 0.74876 | 0.74876 | 0.74876 | 0.74876 | 0.74876 | 0.74876 | 1.9243 | 2.7758 | 3.3336 | 3.6272 | 4.2144 | 4.8016 | 0.69351 | 1.8839 | 2.3628 | 2.3628 | 2.3628 | 2.3628 | 1.5483 | 1.9652 | 1.9652 | 1.9652 | 1.9652 | 1.9652
2020-06-29 06:00 | Winter | 0.94609 | 1.4547 | 2.2013 | 2.2013 | 2.2013 | 2.2013 | 0.84303 | 0.84303 | 0.84303 | 0.84303 | 0.84303 | 0.84303 | 2.1272 | 3.0684 | 3.685 | 4.0096 | 4.6587 | 5.3078 | 0.72781 | 1.977 | 2.4796 | 2.4796 | 2.4796 | 2.4796 | 1.971 | 2.5018 | 2.5018 | 2.5018 | 2.5018 | 2.5018
2020-06-29 07:00 | Winter | 1.1432 | 1.7577 | 2.6598 | 2.6598 | 2.6598 | 2.6598 | 0.98025 | 0.98025 | 0.98025 | 0.98025 | 0.98025 | 0.98025 | 2.4836 | 3.5825 | 4.3025 | 4.6815 | 5.4394 | 6.1972 | 0.85355 | 2.3186 | 2.9081 | 2.9081 | 2.9081 | 2.9081 | 2.3816 | 3.0229 | 3.0229 | 3.0229 | 3.0229 | 3.0229
2020-06-29 08:00 | Winter | 1.2956 | 1.9921 | 3.0144 | 3.0144 | 3.0144 | 3.0144 | 1.066 | 1.066 | 1.066 | 1.066 | 1.066 | 1.066 | 2.6674 | 3.8476 | 4.6208 | 5.0278 | 5.8418 | 6.6557 | 0.85355 | 2.3186 | 2.9081 | 2.9081 | 2.9081 | 2.9081 | 2.6674 | 3.3856 | 3.3856 | 3.3856 | 3.3856 | 3.3856
2020-06-29 09:00 | Winter | 1.3718 | 2.1093 | 3.1918 | 3.1918 | 3.1918 | 3.1918 | 1.0688 | 1.0688 | 1.0688 | 1.0688 | 1.0688 | 1.0688 | 2.6483 | 3.8201 | 4.5878 | 4.9919 | 5.8 | 6.6082 | 0.89166 | 2.4221 | 3.0379 | 3.0379 | 3.0379 | 3.0379 | 2.6864 | 3.4098 | 3.4098 | 3.4098 | 3.4098 | 3.4098
2020-06-29 10:00 | Winter | 1.2765 | 1.9628 | 2.9701 | 2.9701 | 2.9701 | 2.9701 | 1.0917 | 1.0917 | 1.0917 | 1.0917 | 1.0917 | 1.0917 | 2.6293 | 3.7926 | 4.5548 | 4.956 | 5.7583 | 6.5606 | 0.82688 | 2.2461 | 2.8172 | 2.8172 | 2.8172 | 2.8172 | 2.8198 | 3.5791 | 3.5791 | 3.5791 | 3.5791 | 3.5791
2020-06-29 11:00 | Winter | 1.2575 | 1.9335 | 2.9258 | 2.9258 | 2.9258 | 2.9258 | 1.1117 | 1.1117 | 1.1117 | 1.1117 | 1.1117 | 1.1117 | 2.6674 | 3.8476 | 4.6208 | 5.0278 | 5.8418 | 6.6557 | 0.86879 | 2.36 | 2.96 | 2.96 | 2.96 | 2.96 | 2.7817 | 3.5307 | 3.5307 | 3.5307 | 3.5307 | 3.5307
2020-06-29 12:00 | Winter | 1.2384 | 1.9042 | 2.8814 | 2.8814 | 2.8814 | 2.8814 | 1.1174 | 1.1174 | 1.1174 | 1.1174 | 1.1174 | 1.1174 | 2.7245 | 3.93 | 4.7199 | 5.1356 | 5.967 | 6.7984 | 0.84593 | 2.2979 | 2.8821 | 2.8821 | 2.8821 | 2.8821 | 2.6864 | 3.4098 | 3.4098 | 3.4098 | 3.4098 | 3.4098
2020-06-29 13:00 | Winter | 1.2384 | 1.9042 | 2.8814 | 2.8814 | 2.8814 | 2.8814 | 1.0317 | 1.0317 | 1.0317 | 1.0317 | 1.0317 | 1.0317 | 2.6293 | 3.7926 | 4.5548 | 4.956 | 5.7583 | 6.5606 | 0.84593 | 2.2979 | 2.8821 | 2.8821 | 2.8821 | 2.8821 | 2.6674 | 3.3856 | 3.3856 | 3.3856 | 3.3856 | 3.3856
2020-06-29 14:00 | Winter | 1.2384 | 1.9042 | 2.8814 | 2.8814 | 2.8814 | 2.8814 | 1.0946 | 1.0946 | 1.0946 | 1.0946 | 1.0946 | 1.0946 | 2.6293 | 3.7926 | 4.5548 | 4.956 | 5.7583 | 6.5606 | 0.81164 | 2.2047 | 2.7653 | 2.7653 | 2.7653 | 2.7653 | 2.5721 | 3.2647 | 3.2647 | 3.2647 | 3.2647 | 3.2647
2020-06-29 15:00 | Winter | 1.1813 | 1.8163 | 2.7485 | 2.7485 | 2.7485 | 2.7485 | 1.046 | 1.046 | 1.046 | 1.046 | 1.046 | 1.046 | 2.5721 | 3.7102 | 4.4558 | 4.8483 | 5.6331 | 6.418 | 0.85736 | 2.3289 | 2.9211 | 2.9211 | 2.9211 | 2.9211 | 2.4768 | 3.1438 | 3.1438 | 3.1438 | 3.1438 | 3.1438
2020-06-29 16:00 | Winter | 1.1622 | 1.787 | 2.7041 | 2.7041 | 2.7041 | 2.7041 | 1.0346 | 1.0346 | 1.0346 | 1.0346 | 1.0346 | 1.0346 | 2.5721 | 3.7102 | 4.4558 | 4.8483 | 5.6331 | 6.418 | 0.83831 | 2.2772 | 2.8561 | 2.8561 | 2.8561 | 2.8561 | 2.4006 | 3.0471 | 3.0471 | 3.0471 | 3.0471 | 3.0471
2020-06-29 17:00 | Winter | 1.1241 | 1.7284 | 2.6155 | 2.6155 | 2.6155 | 2.6155 | 0.98025 | 0.98025 | 0.98025 | 0.98025 | 0.98025 | 0.98025 | 2.7626 | 3.985 | 4.7859 | 5.2074 | 6.0504 | 6.8934 | 0.88023 | 2.3911 | 2.9989 | 2.9989 | 2.9989 | 2.9989 | 2.3625 | 2.9987 | 2.9987 | 2.9987 | 2.9987 | 2.9987
2020-06-29 18:00 | Winter | 0.90513 | 1.3917 | 2.106 | 2.106 | 2.106 | 2.106 | 0.78222 | 0.78222 | 0.78222 | 0.78222 | 0.78222 | 0.78222 | 2.6174 | 3.7755 | 4.5342 | 4.9336 | 5.7323 | 6.531 | 0.80021 | 2.1737 | 2.7263 | 2.7263 | 2.7263 | 2.7263 | 1.6194 | 2.0554 | 2.0554 | 2.0554 | 2.0554 | 2.0554
2020-06-29 19:00 | Winter | 0.68983 | 1.0607 | 1.605 | 1.605 | 1.605 | 1.605 | 0.61444 | 0.61444 | 0.61444 | 0.61444 | 0.61444 | 0.61444 | 2.4431 | 3.5242 | 4.2324 | 4.6052 | 5.3507 | 6.0963 | 0.72018 | 1.9563 | 2.4537 | 2.4537 | 2.4537 | 2.4537 | 1.1815 | 1.4996 | 1.4996 | 1.4996 | 1.4996 | 1.4996
2020-06-29 20:00 | Winter | 0.6289 | 0.96701 | 1.4633 | 1.4633 | 1.4633 | 1.4633 | 0.51442 | 0.51442 | 0.51442 | 0.51442 | 0.51442 | 0.51442 | 2.3054 | 3.3254 | 3.9937 | 4.3455 | 5.049 | 5.7525 | 0.73543 | 1.9977 | 2.5056 | 2.5056 | 2.5056 | 2.5056 | 1.1241 | 1.4268 | 1.4268 | 1.4268 | 1.4268 | 1.4268
2020-06-29 21:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.42582 | 0.42582 | 0.42582 | 0.42582 | 0.42582 | 0.42582 | 2.2291 | 3.2155 | 3.8617 | 4.2018 | 4.8821 | 5.5623 | 0.68589 | 1.8632 | 2.3368 | 2.3368 | 2.3368 | 2.3368 | 0.97168 | 1.2333 | 1.2333 | 1.2333 | 1.2333 | 1.2333
2020-06-29 22:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 2.191 | 3.1605 | 3.7957 | 4.13 | 4.7986 | 5.4672 | 0.67827 | 1.8425 | 2.3109 | 2.3109 | 2.3109 | 2.3109 | 0.93358 | 1.185 | 1.185 | 1.185 | 1.185 | 1.185
2020-06-29 23:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 1.8452 | 2.6616 | 3.1966 | 3.4781 | 4.0412 | 4.6042 | 0.58744 | 1.5957 | 2.0014 | 2.0014 | 2.0014 | 2.0014 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-06-30 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 1.7408 | 2.511 | 3.0157 | 3.2813 | 3.8125 | 4.3437 | 0.53728 | 1.4595 | 1.8305 | 1.8305 | 1.8305 | 1.8305 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-06-30 01:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 1.6766 | 2.4185 | 2.9045 | 3.1603 | 3.672 | 4.1836 | 0.54109 | 1.4698 | 1.8435 | 1.8435 | 1.8435 | 1.8435 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-06-30 02:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.47441 | 0.47441 | 0.47441 | 0.47441 | 0.47441 | 0.47441 | 1.6766 | 2.4185 | 2.9045 | 3.1603 | 3.672 | 4.1836 | 0.53728 | 1.4595 | 1.8305 | 1.8305 | 1.8305 | 1.8305 | 1.1241 | 1.4268 | 1.4268 | 1.4268 | 1.4268 | 1.4268
2020-06-30 03:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 1.6004 | 2.3086 | 2.7725 | 3.0167 | 3.5051 | 3.9934 | 0.49536 | 1.3456 | 1.6877 | 1.6877 | 1.6877 | 1.6877 | 1.1241 | 1.4268 | 1.4268 | 1.4268 | 1.4268 | 1.4268
2020-06-30 04:00 | Winter | 0.60944 | 0.93709 | 1.418 | 1.418 | 1.418 | 1.418 | 0.53728 | 0.53728 | 0.53728 | 0.53728 | 0.53728 | 0.53728 | 1.6195 | 2.336 | 2.8055 | 3.0526 | 3.5468 | 4.041 | 0.5068 | 1.3767 | 1.7267 | 1.7267 | 1.7267 | 1.7267 | 1.1432 | 1.451 | 1.451 | 1.451 | 1.451 | 1.451
2020-06-30 05:00 | Winter | 0.81198 | 1.2485 | 1.8892 | 1.8892 | 1.8892 | 1.8892 | 0.68875 | 0.68875 | 0.68875 | 0.68875 | 0.68875 | 0.68875 | 1.7521 | 2.5274 | 3.0353 | 3.3026 | 3.8373 | 4.3719 | 0.64016 | 1.7389 | 2.1811 | 2.1811 | 2.1811 | 2.1811 | 1.4853 | 1.8852 | 1.8852 | 1.8852 | 1.8852 | 1.8852
2020-06-30 06:00 | Winter | 0.85737 | 1.3183 | 1.9948 | 1.9948 | 1.9948 | 1.9948 | 0.84307 | 0.84307 | 0.84307 | 0.84307 | 0.84307 | 0.84307 | 2.136 | 3.0812 | 3.7004 | 4.0263 | 4.6782 | 5.33 | 0.75067 | 2.0391 | 2.5575 | 2.5575 | 2.5575 | 2.5575 | 1.9172 | 2.4334 | 2.4334 | 2.4334 | 2.4334 | 2.4334
2020-06-30 07:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 0.96279 | 0.96279 | 0.96279 | 0.96279 | 0.96279 | 0.96279 | 2.5911 | 3.7377 | 4.4888 | 4.8842 | 5.6749 | 6.4656 | 0.89166 | 2.4221 | 3.0379 | 3.0379 | 3.0379 | 3.0379 | 2.3244 | 2.9503 | 2.9503 | 2.9503 | 2.9503 | 2.9503
2020-06-30 08:00 | Winter | 1.3337 | 2.0507 | 3.1031 | 3.1031 | 3.1031 | 3.1031 | 1.1031 | 1.1031 | 1.1031 | 1.1031 | 1.1031 | 1.1031 | 2.7436 | 3.9575 | 4.7529 | 5.1715 | 6.0087 | 6.8459 | 0.89166 | 2.4221 | 3.0379 | 3.0379 | 3.0379 | 3.0379 | 2.5911 | 3.2889 | 3.2889 | 3.2889 | 3.2889 | 3.2889
2020-06-30 09:00 | Winter | 1.3527 | 2.08 | 3.1474 | 3.1474 | 3.1474 | 3.1474 | 1.1517 | 1.1517 | 1.1517 | 1.1517 | 1.1517 | 1.1517 | 2.6674 | 3.8476 | 4.6208 | 5.0278 | 5.8418 | 6.6557 | 0.87642 | 2.3807 | 2.986 | 2.986 | 2.986 | 2.986 | 2.6674 | 3.3856 | 3.3856 | 3.3856 | 3.3856 | 3.3856
2020-06-30 10:00 | Winter | 1.3337 | 2.0507 | 3.1031 | 3.1031 | 3.1031 | 3.1031 | 1.1089 | 1.1089 | 1.1089 | 1.1089 | 1.1089 | 1.1089 | 2.6864 | 3.8751 | 4.6539 | 5.0637 | 5.8835 | 6.7033 | 0.92595 | 2.5153 | 3.1547 | 3.1547 | 3.1547 | 3.1547 | 2.6674 | 3.3856 | 3.3856 | 3.3856 | 3.3856 | 3.3856
2020-06-30 11:00 | Winter | 1.2956 | 1.9921 | 3.0144 | 3.0144 | 3.0144 | 3.0144 | 1.0203 | 1.0203 | 1.0203 | 1.0203 | 1.0203 | 1.0203 | 2.6297 | 3.7933 | 4.5557 | 4.9569 | 5.7594 | 6.5619 | 0.85355 | 2.3186 | 2.9081 | 2.9081 | 2.9081 | 2.9081 | 2.6864 | 3.4098 | 3.4098 | 3.4098 | 3.4098 | 3.4098
2020-06-30 12:00 | Winter | 1.2956 | 1.9921 | 3.0144 | 3.0144 | 3.0144 | 3.0144 | 1.0088 | 1.0088 | 1.0088 | 1.0088 | 1.0088 | 1.0088 | 2.6483 | 3.8201 | 4.5878 | 4.9919 | 5.8 | 6.6082 | 0.80021 | 2.1737 | 2.7263 | 2.7263 | 2.7263 | 2.7263 | 2.534 | 3.2163 | 3.2163 | 3.2163 | 3.2163 | 3.2163
2020-06-30 13:00 | Winter | 1.2956 | 1.9921 | 3.0144 | 3.0144 | 3.0144 | 3.0144 | 0.9974 | 0.9974 | 0.9974 | 0.9974 | 0.9974 | 0.9974 | 2.6293 | 3.7926 | 4.5548 | 4.956 | 5.7583 | 6.5606 | 0.83069 | 2.2565 | 2.8302 | 2.8302 | 2.8302 | 2.8302 | 2.5149 | 3.1922 | 3.1922 | 3.1922 | 3.1922 | 3.1922
2020-06-30 14:00 | Winter | 1.2765 | 1.9628 | 2.9701 | 2.9701 | 2.9701 | 2.9701 | 1.0003 | 1.0003 | 1.0003 | 1.0003 | 1.0003 | 1.0003 | 2.6483 | 3.8201 | 4.5878 | 4.9919 | 5.8 | 6.6082 | 0.82688 | 2.2461 | 2.8172 | 2.8172 | 2.8172 | 2.8172 | 2.5149 | 3.1922 | 3.1922 | 3.1922 | 3.1922 | 3.1922
2020-06-30 15:00 | Winter | 1.2003 | 1.8456 | 2.7928 | 2.7928 | 2.7928 | 2.7928 | 0.98025 | 0.98025 | 0.98025 | 0.98025 | 0.98025 | 0.98025 | 2.5149 | 3.6277 | 4.3568 | 4.7405 | 5.508 | 6.2754 | 0.93357 | 2.536 | 3.1807 | 3.1807 | 3.1807 | 3.1807 | 2.4197 | 3.0712 | 3.0712 | 3.0712 | 3.0712 | 3.0712
2020-06-30 16:00 | Winter | 1.1432 | 1.7577 | 2.6598 | 2.6598 | 2.6598 | 2.6598 | 0.9431 | 0.9431 | 0.9431 | 0.9431 | 0.9431 | 0.9431 | 2.534 | 3.6552 | 4.3898 | 4.7764 | 5.5497 | 6.3229 | 0.87261 | 2.3704 | 2.973 | 2.973 | 2.973 | 2.973 | 2.2673 | 2.8778 | 2.8778 | 2.8778 | 2.8778 | 2.8778
2020-06-30 17:00 | Winter | 1.1241 | 1.7284 | 2.6155 | 2.6155 | 2.6155 | 2.6155 | 0.9431 | 0.9431 | 0.9431 | 0.9431 | 0.9431 | 0.9431 | 2.7055 | 3.9026 | 4.6869 | 5.0996 | 5.9252 | 6.7508 | 0.9069 | 2.4635 | 3.0898 | 3.0898 | 3.0898 | 3.0898 | 2.1339 | 2.7085 | 2.7085 | 2.7085 | 2.7085 | 2.7085
2020-06-30 18:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 0.7802 | 0.7802 | 0.7802 | 0.7802 | 0.7802 | 0.7802 | 2.6365 | 3.8031 | 4.5674 | 4.9697 | 5.7742 | 6.5788 | 0.88785 | 2.4118 | 3.0249 | 3.0249 | 3.0249 | 3.0249 | 1.6076 | 2.0405 | 2.0405 | 2.0405 | 2.0405 | 2.0405
2020-06-30 19:00 | Winter | 0.724 | 1.1132 | 1.6845 | 1.6845 | 1.6845 | 1.6845 | 0.53368 | 0.53368 | 0.53368 | 0.53368 | 0.53368 | 0.53368 | 2.4591 | 3.5471 | 4.26 | 4.6352 | 5.3856 | 6.1359 | 0.77353 | 2.1012 | 2.6354 | 2.6354 | 2.6354 | 2.6354 | 1.1627 | 1.4758 | 1.4758 | 1.4758 | 1.4758 | 1.4758
2020-06-30 20:00 | Winter | 0.64779 | 0.99605 | 1.5072 | 1.5072 | 1.5072 | 1.5072 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 2.4578 | 3.5453 | 4.2578 | 4.6328 | 5.3828 | 6.1328 | 0.79258 | 2.153 | 2.7003 | 2.7003 | 2.7003 | 2.7003 | 1.1003 | 1.3966 | 1.3966 | 1.3966 | 1.3966 | 1.3966
2020-06-30 21:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.41153 | 0.41153 | 0.41153 | 0.41153 | 0.41153 | 0.41153 | 2.2482 | 3.243 | 3.8947 | 4.2377 | 4.9238 | 5.6098 | 0.76972 | 2.0909 | 2.6225 | 2.6225 | 2.6225 | 2.6225 | 1.0098 | 1.2817 | 1.2817 | 1.2817 | 1.2817 | 1.2817
2020-06-30 22:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.38867 | 0.38867 | 0.38867 | 0.38867 | 0.38867 | 0.38867 | 2.0958 | 3.0231 | 3.6307 | 3.9504 | 4.59 | 5.2295 | 0.7621 | 2.0702 | 2.5965 | 2.5965 | 2.5965 | 2.5965 | 0.93492 | 1.1867 | 1.1867 | 1.1867 | 1.1867 | 1.1867
2020-06-30 23:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 1.81 | 2.6109 | 3.1356 | 3.4117 | 3.9641 | 4.5164 | 0.64779 | 1.7596 | 2.207 | 2.207 | 2.207 | 2.207 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-07-01 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 1.7528 | 2.5284 | 3.0366 | 3.304 | 3.8389 | 4.3738 | 0.5792 | 1.5733 | 1.9733 | 1.9733 | 1.9733 | 1.9733 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-07-01 01:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.37724 | 0.37724 | 0.37724 | 0.37724 | 0.37724 | 0.37724 | 1.6583 | 2.392 | 2.8727 | 3.1257 | 3.6317 | 4.1378 | 0.56776 | 1.5423 | 1.9344 | 1.9344 | 1.9344 | 1.9344 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-07-01 02:00 | Winter | 0.59032 | 0.90768 | 1.3735 | 1.3735 | 1.3735 | 1.3735 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 1.6957 | 2.446 | 2.9375 | 3.1963 | 3.7137 | 4.2311 | 0.61349 | 1.6665 | 2.0902 | 2.0902 | 2.0902 | 2.0902 | 1.0475 | 1.3296 | 1.3296 | 1.3296 | 1.3296 | 1.3296
2020-07-01 03:00 | Winter | 0.60702 | 0.93336 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 0.43439 | 0.43439 | 0.43439 | 0.43439 | 0.43439 | 0.43439 | 1.6766 | 2.4185 | 2.9045 | 3.1603 | 3.672 | 4.1836 | 0.56014 | 1.5216 | 1.9084 | 1.9084 | 1.9084 | 1.9084 | 1.105 | 1.4026 | 1.4026 | 1.4026 | 1.4026 | 1.4026
2020-07-01 04:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.48584 | 0.48584 | 0.48584 | 0.48584 | 0.48584 | 0.48584 | 1.6326 | 2.355 | 2.8283 | 3.0773 | 3.5755 | 4.0737 | 0.5792 | 1.5733 | 1.9733 | 1.9733 | 1.9733 | 1.9733 | 1.1432 | 1.451 | 1.451 | 1.451 | 1.451 | 1.451
2020-07-01 05:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.58015 | 0.58015 | 0.58015 | 0.58015 | 0.58015 | 0.58015 | 1.8021 | 2.5994 | 3.1219 | 3.3968 | 3.9467 | 4.4966 | 0.724 | 1.9667 | 2.4667 | 2.4667 | 2.4667 | 2.4667 | 1.5242 | 1.9346 | 1.9346 | 1.9346 | 1.9346 | 1.9346
2020-07-01 06:00 | Winter | 0.81926 | 1.2597 | 1.9062 | 1.9062 | 1.9062 | 1.9062 | 0.70304 | 0.70304 | 0.70304 | 0.70304 | 0.70304 | 0.70304 | 2.0958 | 3.0231 | 3.6307 | 3.9504 | 4.59 | 5.2295 | 0.81926 | 2.2254 | 2.7912 | 2.7912 | 2.7912 | 2.7912 | 1.7908 | 2.2731 | 2.2731 | 2.2731 | 2.2731 | 2.2731
2020-07-01 07:00 | Winter | 1.1048 | 1.6988 | 2.5706 | 2.5706 | 2.5706 | 2.5706 | 0.87449 | 0.87449 | 0.87449 | 0.87449 | 0.87449 | 0.87449 | 2.4006 | 3.4628 | 4.1588 | 4.525 | 5.2576 | 5.9902 | 0.94882 | 2.5774 | 3.2326 | 3.2326 | 3.2326 | 3.2326 | 2.3054 | 2.9261 | 2.9261 | 2.9261 | 2.9261 | 2.9261
2020-07-01 08:00 | Winter | 1.2765 | 1.9628 | 2.9701 | 2.9701 | 2.9701 | 2.9701 | 0.96596 | 0.96596 | 0.96596 | 0.96596 | 0.96596 | 0.96596 | 2.5721 | 3.7102 | 4.4558 | 4.8483 | 5.6331 | 6.418 | 0.97549 | 2.6498 | 3.3235 | 3.3235 | 3.3235 | 3.3235 | 2.5911 | 3.2889 | 3.2889 | 3.2889 | 3.2889 | 3.2889
2020-07-01 09:00 | Winter | 1.2765 | 1.9628 | 2.9701 | 2.9701 | 2.9701 | 2.9701 | 1.0317 | 1.0317 | 1.0317 | 1.0317 | 1.0317 | 1.0317 | 2.6102 | 3.7651 | 4.5218 | 4.9201 | 5.7166 | 6.5131 | 1.086 | 2.95 | 3.7 | 3.7 | 3.7 | 3.7 | 2.6293 | 3.3373 | 3.3373 | 3.3373 | 3.3373 | 3.3373
2020-07-01 10:00 | Winter | 1.3337 | 2.0507 | 3.1031 | 3.1031 | 3.1031 | 3.1031 | 0.9631 | 0.9631 | 0.9631 | 0.9631 | 0.9631 | 0.9631 | 2.6102 | 3.7651 | 4.5218 | 4.9201 | 5.7166 | 6.5131 | 0.92214 | 2.5049 | 3.1418 | 3.1418 | 3.1418 | 3.1418 | 2.6102 | 3.3131 | 3.3131 | 3.3131 | 3.3131 | 3.3131
2020-07-01 11:00 | Winter | 1.2765 | 1.9628 | 2.9701 | 2.9701 | 2.9701 | 2.9701 | 0.98311 | 0.98311 | 0.98311 | 0.98311 | 0.98311 | 0.98311 | 2.6293 | 3.7926 | 4.5548 | 4.956 | 5.7583 | 6.5606 | 0.89547 | 2.4325 | 3.0509 | 3.0509 | 3.0509 | 3.0509 | 2.5721 | 3.2647 | 3.2647 | 3.2647 | 3.2647 | 3.2647
2020-07-01 12:00 | Winter | 1.2575 | 1.9335 | 2.9258 | 2.9258 | 2.9258 | 2.9258 | 0.9631 | 0.9631 | 0.9631 | 0.9631 | 0.9631 | 0.9631 | 2.6864 | 3.8751 | 4.6539 | 5.0637 | 5.8835 | 6.7033 | 0.81545 | 2.2151 | 2.7782 | 2.7782 | 2.7782 | 2.7782 | 2.5149 | 3.1922 | 3.1922 | 3.1922 | 3.1922 | 3.1922
2020-07-01 13:00 | Winter | 1.2575 | 1.9335 | 2.9258 | 2.9258 | 2.9258 | 2.9258 | 0.92595 | 0.92595 | 0.92595 | 0.92595 | 0.92595 | 0.92595 | 2.6674 | 3.8476 | 4.6208 | 5.0278 | 5.8418 | 6.6557 | 0.82688 | 2.2461 | 2.8172 | 2.8172 | 2.8172 | 2.8172 | 2.4486 | 3.108 | 3.108 | 3.108 | 3.108 | 3.108
2020-07-01 14:00 | Winter | 1.2575 | 1.9335 | 2.9258 | 2.9258 | 2.9258 | 2.9258 | 0.98025 | 0.98025 | 0.98025 | 0.98025 | 0.98025 | 0.98025 | 2.6293 | 3.7926 | 4.5548 | 4.956 | 5.7583 | 6.5606 | 0.80783 | 2.1944 | 2.7523 | 2.7523 | 2.7523 | 2.7523 | 2.2868 | 2.9026 | 2.9026 | 2.9026 | 2.9026 | 2.9026
2020-07-01 15:00 | Winter | 1.2003 | 1.8456 | 2.7928 | 2.7928 | 2.7928 | 2.7928 | 0.96025 | 0.96025 | 0.96025 | 0.96025 | 0.96025 | 0.96025 | 2.534 | 3.6552 | 4.3898 | 4.7764 | 5.5497 | 6.3229 | 0.81926 | 2.2254 | 2.7912 | 2.7912 | 2.7912 | 2.7912 | 2.2101 | 2.8052 | 2.8052 | 2.8052 | 2.8052 | 2.8052
2020-07-01 16:00 | Winter | 1.2003 | 1.8456 | 2.7928 | 2.7928 | 2.7928 | 2.7928 | 0.96596 | 0.96596 | 0.96596 | 0.96596 | 0.96596 | 0.96596 | 2.5143 | 3.6268 | 4.3557 | 4.7393 | 5.5066 | 6.2738 | 0.83831 | 2.2772 | 2.8561 | 2.8561 | 2.8561 | 2.8561 | 2.191 | 2.781 | 2.781 | 2.781 | 2.781 | 2.781
2020-07-01 17:00 | Winter | 1.105 | 1.6991 | 2.5711 | 2.5711 | 2.5711 | 2.5711 | 0.95739 | 0.95739 | 0.95739 | 0.95739 | 0.95739 | 0.95739 | 2.6102 | 3.7651 | 4.5218 | 4.9201 | 5.7166 | 6.5131 | 0.86879 | 2.36 | 2.96 | 2.96 | 2.96 | 2.96 | 2.0958 | 2.6601 | 2.6601 | 2.6601 | 2.6601 | 2.6601
2020-07-01 18:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.83164 | 0.83164 | 0.83164 | 0.83164 | 0.83164 | 0.83164 | 2.553 | 3.6827 | 4.4228 | 4.8123 | 5.5914 | 6.3705 | 0.85736 | 2.3289 | 2.9211 | 2.9211 | 2.9211 | 2.9211 | 1.6384 | 2.0795 | 2.0795 | 2.0795 | 2.0795 | 2.0795
2020-07-01 19:00 | Winter | 0.66707 | 1.0257 | 1.5521 | 1.5521 | 1.5521 | 1.5521 | 0.64302 | 0.64302 | 0.64302 | 0.64302 | 0.64302 | 0.64302 | 2.5381 | 3.6612 | 4.397 | 4.7842 | 5.5587 | 6.3333 | 0.81164 | 2.2047 | 2.7653 | 2.7653 | 2.7653 | 2.7653 | 1.2003 | 1.5235 | 1.5235 | 1.5235 | 1.5235 | 1.5235
2020-07-01 20:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.54014 | 0.54014 | 0.54014 | 0.54014 | 0.54014 | 0.54014 | 2.3625 | 3.4079 | 4.0927 | 4.4532 | 5.1741 | 5.8951 | 0.76591 | 2.0805 | 2.6095 | 2.6095 | 2.6095 | 2.6095 | 1.1241 | 1.4268 | 1.4268 | 1.4268 | 1.4268 | 1.4268
2020-07-01 21:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.47441 | 0.47441 | 0.47441 | 0.47441 | 0.47441 | 0.47441 | 2.2482 | 3.243 | 3.8947 | 4.2377 | 4.9238 | 5.6098 | 0.70875 | 1.9253 | 2.4147 | 2.4147 | 2.4147 | 2.4147 | 0.99073 | 1.2575 | 1.2575 | 1.2575 | 1.2575 | 1.2575
2020-07-01 22:00 | Winter | 0.57176 | 0.87915 | 1.3303 | 1.3303 | 1.3303 | 1.3303 | 0.49155 | 0.49155 | 0.49155 | 0.49155 | 0.49155 | 0.49155 | 2.0005 | 2.8857 | 3.4656 | 3.7709 | 4.3813 | 4.9918 | 0.69351 | 1.8839 | 2.3628 | 2.3628 | 2.3628 | 2.3628 | 0.87646 | 1.1125 | 1.1125 | 1.1125 | 1.1125 | 1.1125
2020-07-01 23:00 | Winter | 0.60898 | 0.93637 | 1.4169 | 1.4169 | 1.4169 | 1.4169 | 0.38867 | 0.38867 | 0.38867 | 0.38867 | 0.38867 | 0.38867 | 1.8645 | 2.6894 | 3.23 | 3.5144 | 4.0834 | 4.6523 | 0.62492 | 1.6975 | 2.1291 | 2.1291 | 2.1291 | 2.1291 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-07-02 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.42582 | 0.42582 | 0.42582 | 0.42582 | 0.42582 | 0.42582 | 1.7909 | 2.5834 | 3.1026 | 3.3758 | 3.9223 | 4.4688 | 0.55633 | 1.5112 | 1.8954 | 1.8954 | 1.8954 | 1.8954 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-07-02 01:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.36295 | 0.36295 | 0.36295 | 0.36295 | 0.36295 | 0.36295 | 1.7909 | 2.5834 | 3.1026 | 3.3758 | 3.9223 | 4.4688 | 0.55252 | 1.5009 | 1.8825 | 1.8825 | 1.8825 | 1.8825 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-07-02 02:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.40582 | 0.40582 | 0.40582 | 0.40582 | 0.40582 | 0.40582 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.54871 | 1.4905 | 1.8695 | 1.8695 | 1.8695 | 1.8695 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-07-02 03:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.41153 | 0.41153 | 0.41153 | 0.41153 | 0.41153 | 0.41153 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.53347 | 1.4491 | 1.8175 | 1.8175 | 1.8175 | 1.8175 | 1.0288 | 1.3059 | 1.3059 | 1.3059 | 1.3059 | 1.3059
2020-07-02 04:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.53728 | 1.4595 | 1.8305 | 1.8305 | 1.8305 | 1.8305 | 1.1241 | 1.4268 | 1.4268 | 1.4268 | 1.4268 | 1.4268
2020-07-02 05:00 | Winter | 0.60963 | 0.93738 | 1.4184 | 1.4184 | 1.4184 | 1.4184 | 0.58015 | 0.58015 | 0.58015 | 0.58015 | 0.58015 | 0.58015 | 1.7574 | 2.535 | 3.0444 | 3.3125 | 3.8488 | 4.3851 | 0.67446 | 1.8321 | 2.2979 | 2.2979 | 2.2979 | 2.2979 | 1.3906 | 1.765 | 1.765 | 1.765 | 1.765 | 1.765
2020-07-02 06:00 | Winter | 0.68589 | 1.0546 | 1.5959 | 1.5959 | 1.5959 | 1.5959 | 0.66017 | 0.66017 | 0.66017 | 0.66017 | 0.66017 | 0.66017 | 2.0719 | 2.9887 | 3.5893 | 3.9055 | 4.5377 | 5.17 | 0.84593 | 2.2979 | 2.8821 | 2.8821 | 2.8821 | 2.8821 | 1.8097 | 2.297 | 2.297 | 2.297 | 2.297 | 2.297
2020-07-02 07:00 | Winter | 1.086 | 1.6698 | 2.5268 | 2.5268 | 2.5268 | 2.5268 | 0.79382 | 0.79382 | 0.79382 | 0.79382 | 0.79382 | 0.79382 | 2.3625 | 3.4079 | 4.0927 | 4.4532 | 5.1741 | 5.8951 | 0.89547 | 2.4325 | 3.0509 | 3.0509 | 3.0509 | 3.0509 | 2.2707 | 2.8822 | 2.8822 | 2.8822 | 2.8822 | 2.8822
2020-07-02 08:00 | Winter | 1.2384 | 1.9042 | 2.8814 | 2.8814 | 2.8814 | 2.8814 | 0.91452 | 0.91452 | 0.91452 | 0.91452 | 0.91452 | 0.91452 | 2.534 | 3.6552 | 4.3898 | 4.7764 | 5.5497 | 6.3229 | 0.88785 | 2.4118 | 3.0249 | 3.0249 | 3.0249 | 3.0249 | 2.4387 | 3.0954 | 3.0954 | 3.0954 | 3.0954 | 3.0954
2020-07-02 09:00 | Winter | 1.2956 | 1.9921 | 3.0144 | 3.0144 | 3.0144 | 3.0144 | 0.94881 | 0.94881 | 0.94881 | 0.94881 | 0.94881 | 0.94881 | 2.6102 | 3.7651 | 4.5218 | 4.9201 | 5.7166 | 6.5131 | 0.85736 | 2.3289 | 2.9211 | 2.9211 | 2.9211 | 2.9211 | 2.534 | 3.2163 | 3.2163 | 3.2163 | 3.2163 | 3.2163
2020-07-02 10:00 | Winter | 1.2575 | 1.9335 | 2.9258 | 2.9258 | 2.9258 | 2.9258 | 0.88594 | 0.88594 | 0.88594 | 0.88594 | 0.88594 | 0.88594 | 2.6102 | 3.7651 | 4.5218 | 4.9201 | 5.7166 | 6.5131 | 0.89166 | 2.4221 | 3.0379 | 3.0379 | 3.0379 | 3.0379 | 2.4959 | 3.168 | 3.168 | 3.168 | 3.168 | 3.168
2020-07-02 11:00 | Winter | 1.2194 | 1.8749 | 2.8371 | 2.8371 | 2.8371 | 2.8371 | 0.91166 | 0.91166 | 0.91166 | 0.91166 | 0.91166 | 0.91166 | 2.6293 | 3.7926 | 4.5548 | 4.956 | 5.7583 | 6.5606 | 0.78877 | 2.1426 | 2.6874 | 2.6874 | 2.6874 | 2.6874 | 2.4578 | 3.1196 | 3.1196 | 3.1196 | 3.1196 | 3.1196
2020-07-02 12:00 | Winter | 1.2384 | 1.9042 | 2.8814 | 2.8814 | 2.8814 | 2.8814 | 0.87737 | 0.87737 | 0.87737 | 0.87737 | 0.87737 | 0.87737 | 2.6483 | 3.8201 | 4.5878 | 4.9919 | 5.8 | 6.6082 | 0.84593 | 2.2979 | 2.8821 | 2.8821 | 2.8821 | 2.8821 | 2.4578 | 3.1196 | 3.1196 | 3.1196 | 3.1196 | 3.1196
2020-07-02 13:00 | Winter | 1.2765 | 1.9628 | 2.9701 | 2.9701 | 2.9701 | 2.9701 | 0.87451 | 0.87451 | 0.87451 | 0.87451 | 0.87451 | 0.87451 | 2.6674 | 3.8476 | 4.6208 | 5.0278 | 5.8418 | 6.6557 | 0.86117 | 2.3393 | 2.934 | 2.934 | 2.934 | 2.934 | 2.3435 | 2.9745 | 2.9745 | 2.9745 | 2.9745 | 2.9745
2020-07-02 14:00 | Winter | 1.2194 | 1.8749 | 2.8371 | 2.8371 | 2.8371 | 2.8371 | 0.87451 | 0.87451 | 0.87451 | 0.87451 | 0.87451 | 0.87451 | 2.6102 | 3.7651 | 4.5218 | 4.9201 | 5.7166 | 6.5131 | 0.86498 | 2.3496 | 2.947 | 2.947 | 2.947 | 2.947 | 2.3054 | 2.9261 | 2.9261 | 2.9261 | 2.9261 | 2.9261
2020-07-02 15:00 | Winter | 1.2003 | 1.8456 | 2.7928 | 2.7928 | 2.7928 | 2.7928 | 0.91452 | 0.91452 | 0.91452 | 0.91452 | 0.91452 | 0.91452 | 2.553 | 3.6827 | 4.4228 | 4.8123 | 5.5914 | 6.3705 | 0.86498 | 2.3496 | 2.947 | 2.947 | 2.947 | 2.947 | 2.172 | 2.7569 | 2.7569 | 2.7569 | 2.7569 | 2.7569
2020-07-02 16:00 | Winter | 1.1622 | 1.787 | 2.7041 | 2.7041 | 2.7041 | 2.7041 | 0.88594 | 0.88594 | 0.88594 | 0.88594 | 0.88594 | 0.88594 | 2.5151 | 3.628 | 4.3571 | 4.7409 | 5.5084 | 6.2759 | 0.84974 | 2.3082 | 2.8951 | 2.8951 | 2.8951 | 2.8951 | 2.172 | 2.7569 | 2.7569 | 2.7569 | 2.7569 | 2.7569
2020-07-02 17:00 | Winter | 1.0669 | 1.6405 | 2.4825 | 2.4825 | 2.4825 | 2.4825 | 0.92595 | 0.92595 | 0.92595 | 0.92595 | 0.92595 | 0.92595 | 2.5721 | 3.7102 | 4.4558 | 4.8483 | 5.6331 | 6.418 | 0.84974 | 2.3082 | 2.8951 | 2.8951 | 2.8951 | 2.8951 | 2.0387 | 2.5877 | 2.5877 | 2.5877 | 2.5877 | 2.5877
2020-07-02 18:00 | Winter | 0.96364 | 1.4817 | 2.2421 | 2.2421 | 2.2421 | 2.2421 | 0.76019 | 0.76019 | 0.76019 | 0.76019 | 0.76019 | 0.76019 | 2.5721 | 3.7102 | 4.4558 | 4.8483 | 5.6331 | 6.418 | 0.82307 | 2.2358 | 2.8042 | 2.8042 | 2.8042 | 2.8042 | 1.5775 | 2.0023 | 2.0023 | 2.0023 | 2.0023 | 2.0023
2020-07-02 19:00 | Winter | 0.724 | 1.1132 | 1.6845 | 1.6845 | 1.6845 | 1.6845 | 0.68017 | 0.68017 | 0.68017 | 0.68017 | 0.68017 | 0.68017 | 2.4013 | 3.4638 | 4.1599 | 4.5263 | 5.2591 | 5.9918 | 0.75448 | 2.0495 | 2.5705 | 2.5705 | 2.5705 | 2.5705 | 1.1558 | 1.467 | 1.467 | 1.467 | 1.467 | 1.467
2020-07-02 20:00 | Winter | 0.66684 | 1.0253 | 1.5515 | 1.5515 | 1.5515 | 1.5515 | 0.58015 | 0.58015 | 0.58015 | 0.58015 | 0.58015 | 0.58015 | 2.3244 | 3.3529 | 4.0267 | 4.3814 | 5.0907 | 5.8 | 0.74686 | 2.0288 | 2.5446 | 2.5446 | 2.5446 | 2.5446 | 1.0606 | 1.3462 | 1.3462 | 1.3462 | 1.3462 | 1.3462
2020-07-02 21:00 | Winter | 0.57476 | 0.88376 | 1.3373 | 1.3373 | 1.3373 | 1.3373 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 2.2482 | 3.243 | 3.8947 | 4.2377 | 4.9238 | 5.6098 | 0.7964 | 2.1633 | 2.7133 | 2.7133 | 2.7133 | 2.7133 | 0.95263 | 1.2092 | 1.2092 | 1.2092 | 1.2092 | 1.2092
2020-07-02 22:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 2.0239 | 2.9194 | 3.5061 | 3.8149 | 4.4325 | 5.0501 | 0.724 | 1.9667 | 2.4667 | 2.4667 | 2.4667 | 2.4667 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-07-02 23:00 | Winter | 0.57029 | 0.87689 | 1.3269 | 1.3269 | 1.3269 | 1.3269 | 0.4544 | 0.4544 | 0.4544 | 0.4544 | 0.4544 | 0.4544 | 1.8672 | 2.6934 | 3.2347 | 3.5196 | 4.0894 | 4.6591 | 0.63635 | 1.7286 | 2.1681 | 2.1681 | 2.1681 | 2.1681 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-07-03 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.38581 | 0.38581 | 0.38581 | 0.38581 | 0.38581 | 0.38581 | 1.6957 | 2.446 | 2.9375 | 3.1963 | 3.7137 | 4.2311 | 0.62111 | 1.6872 | 2.1161 | 2.1161 | 2.1161 | 2.1161 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-07-03 01:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.38009 | 0.38009 | 0.38009 | 0.38009 | 0.38009 | 0.38009 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.59063 | 1.6044 | 2.0123 | 2.0123 | 2.0123 | 2.0123 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-07-03 02:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.4544 | 0.4544 | 0.4544 | 0.4544 | 0.4544 | 0.4544 | 1.6004 | 2.3086 | 2.7725 | 3.0167 | 3.5051 | 3.9934 | 0.5449 | 1.4802 | 1.8565 | 1.8565 | 1.8565 | 1.8565 | 0.97168 | 1.2333 | 1.2333 | 1.2333 | 1.2333 | 1.2333
2020-07-03 03:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 1.6004 | 2.3086 | 2.7725 | 3.0167 | 3.5051 | 3.9934 | 0.59444 | 1.6147 | 2.0253 | 2.0253 | 2.0253 | 2.0253 | 0.99073 | 1.2575 | 1.2575 | 1.2575 | 1.2575 | 1.2575
2020-07-03 04:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 1.6665 | 2.4038 | 2.887 | 3.1412 | 3.6497 | 4.1583 | 0.6173 | 1.6768 | 2.1032 | 2.1032 | 2.1032 | 2.1032 | 1.086 | 1.3784 | 1.3784 | 1.3784 | 1.3784 | 1.3784
2020-07-03 05:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.60587 | 0.60587 | 0.60587 | 0.60587 | 0.60587 | 0.60587 | 1.7528 | 2.5283 | 3.0364 | 3.3038 | 3.8387 | 4.3736 | 0.71256 | 1.9356 | 2.4277 | 2.4277 | 2.4277 | 2.4277 | 1.4706 | 1.8665 | 1.8665 | 1.8665 | 1.8665 | 1.8665
2020-07-03 06:00 | Winter | 0.68554 | 1.0541 | 1.595 | 1.595 | 1.595 | 1.595 | 0.73447 | 0.73447 | 0.73447 | 0.73447 | 0.73447 | 0.73447 | 2.0767 | 2.9956 | 3.5977 | 3.9145 | 4.5482 | 5.182 | 0.7621 | 2.0702 | 2.5965 | 2.5965 | 2.5965 | 2.5965 | 1.7715 | 2.2485 | 2.2485 | 2.2485 | 2.2485 | 2.2485
2020-07-03 07:00 | Winter | 1.1518 | 1.771 | 2.6799 | 2.6799 | 2.6799 | 2.6799 | 0.88022 | 0.88022 | 0.88022 | 0.88022 | 0.88022 | 0.88022 | 2.4127 | 3.4802 | 4.1796 | 4.5477 | 5.284 | 6.0202 | 0.92595 | 2.5153 | 3.1547 | 3.1547 | 3.1547 | 3.1547 | 2.191 | 2.781 | 2.781 | 2.781 | 2.781 | 2.781
2020-07-03 08:00 | Winter | 1.2956 | 1.9921 | 3.0144 | 3.0144 | 3.0144 | 3.0144 | 0.98597 | 0.98597 | 0.98597 | 0.98597 | 0.98597 | 0.98597 | 2.534 | 3.6552 | 4.3898 | 4.7764 | 5.5497 | 6.3229 | 0.93738 | 2.5463 | 3.1937 | 3.1937 | 3.1937 | 3.1937 | 2.5028 | 3.1767 | 3.1767 | 3.1767 | 3.1767 | 3.1767
2020-07-03 09:00 | Winter | 1.2575 | 1.9335 | 2.9258 | 2.9258 | 2.9258 | 2.9258 | 0.96596 | 0.96596 | 0.96596 | 0.96596 | 0.96596 | 0.96596 | 2.553 | 3.6827 | 4.4228 | 4.8123 | 5.5914 | 6.3705 | 0.95644 | 2.5981 | 3.2586 | 3.2586 | 3.2586 | 3.2586 | 2.553 | 3.2405 | 3.2405 | 3.2405 | 3.2405 | 3.2405
2020-07-03 10:00 | Winter | 1.2196 | 1.8753 | 2.8378 | 2.8378 | 2.8378 | 2.8378 | 0.94881 | 0.94881 | 0.94881 | 0.94881 | 0.94881 | 0.94881 | 2.6293 | 3.7926 | 4.5548 | 4.956 | 5.7583 | 6.5606 | 0.88404 | 2.4014 | 3.0119 | 3.0119 | 3.0119 | 3.0119 | 2.4768 | 3.1438 | 3.1438 | 3.1438 | 3.1438 | 3.1438
2020-07-03 11:00 | Winter | 1.2194 | 1.8749 | 2.8371 | 2.8371 | 2.8371 | 2.8371 | 0.91738 | 0.91738 | 0.91738 | 0.91738 | 0.91738 | 0.91738 | 2.6102 | 3.7651 | 4.5218 | 4.9201 | 5.7166 | 6.5131 | 0.90309 | 2.4532 | 3.0768 | 3.0768 | 3.0768 | 3.0768 | 2.5149 | 3.1922 | 3.1922 | 3.1922 | 3.1922 | 3.1922
2020-07-03 12:00 | Winter | 1.1622 | 1.787 | 2.7041 | 2.7041 | 2.7041 | 2.7041 | 0.94881 | 0.94881 | 0.94881 | 0.94881 | 0.94881 | 0.94881 | 2.553 | 3.6827 | 4.4228 | 4.8123 | 5.5914 | 6.3705 | 0.87642 | 2.3807 | 2.986 | 2.986 | 2.986 | 2.986 | 2.4413 | 3.0987 | 3.0987 | 3.0987 | 3.0987 | 3.0987
2020-07-03 13:00 | Winter | 1.2194 | 1.8749 | 2.8371 | 2.8371 | 2.8371 | 2.8371 | 0.95167 | 0.95167 | 0.95167 | 0.95167 | 0.95167 | 0.95167 | 2.534 | 3.6552 | 4.3898 | 4.7764 | 5.5497 | 6.3229 | 0.84974 | 2.3082 | 2.8951 | 2.8951 | 2.8951 | 2.8951 | 2.4768 | 3.1438 | 3.1438 | 3.1438 | 3.1438 | 3.1438
2020-07-03 14:00 | Winter | 1.2194 | 1.8749 | 2.8371 | 2.8371 | 2.8371 | 2.8371 | 1.0203 | 1.0203 | 1.0203 | 1.0203 | 1.0203 | 1.0203 | 2.5048 | 3.6131 | 4.3392 | 4.7214 | 5.4857 | 6.2501 | 0.83831 | 2.2772 | 2.8561 | 2.8561 | 2.8561 | 2.8561 | 2.3054 | 2.9261 | 2.9261 | 2.9261 | 2.9261 | 2.9261
2020-07-03 15:00 | Winter | 1.1622 | 1.787 | 2.7041 | 2.7041 | 2.7041 | 2.7041 | 0.95167 | 0.95167 | 0.95167 | 0.95167 | 0.95167 | 0.95167 | 2.5149 | 3.6277 | 4.3568 | 4.7405 | 5.508 | 6.2754 | 0.89166 | 2.4221 | 3.0379 | 3.0379 | 3.0379 | 3.0379 | 2.2482 | 2.8536 | 2.8536 | 2.8536 | 2.8536 | 2.8536
2020-07-03 16:00 | Winter | 1.1241 | 1.7284 | 2.6155 | 2.6155 | 2.6155 | 2.6155 | 1.0088 | 1.0088 | 1.0088 | 1.0088 | 1.0088 | 1.0088 | 2.5721 | 3.7102 | 4.4558 | 4.8483 | 5.6331 | 6.418 | 0.89547 | 2.4325 | 3.0509 | 3.0509 | 3.0509 | 3.0509 | 2.2482 | 2.8536 | 2.8536 | 2.8536 | 2.8536 | 2.8536
2020-07-03 17:00 | Winter | 1.0288 | 1.582 | 2.3938 | 2.3938 | 2.3938 | 2.3938 | 0.95453 | 0.95453 | 0.95453 | 0.95453 | 0.95453 | 0.95453 | 2.7245 | 3.93 | 4.7199 | 5.1356 | 5.967 | 6.7984 | 0.91833 | 2.4946 | 3.1288 | 3.1288 | 3.1288 | 3.1288 | 2.1148 | 2.6843 | 2.6843 | 2.6843 | 2.6843 | 2.6843
2020-07-03 18:00 | Winter | 0.92136 | 1.4167 | 2.1437 | 2.1437 | 2.1437 | 2.1437 | 0.8545 | 0.8545 | 0.8545 | 0.8545 | 0.8545 | 0.8545 | 2.6674 | 3.8476 | 4.6208 | 5.0278 | 5.8418 | 6.6557 | 0.91833 | 2.4946 | 3.1288 | 3.1288 | 3.1288 | 3.1288 | 1.6773 | 2.129 | 2.129 | 2.129 | 2.129 | 2.129
2020-07-03 19:00 | Winter | 0.64779 | 0.99605 | 1.5072 | 1.5072 | 1.5072 | 1.5072 | 0.81449 | 0.81449 | 0.81449 | 0.81449 | 0.81449 | 0.81449 | 2.4442 | 3.5257 | 4.2342 | 4.6072 | 5.353 | 6.0989 | 0.84593 | 2.2979 | 2.8821 | 2.8821 | 2.8821 | 2.8821 | 1.1813 | 1.4993 | 1.4993 | 1.4993 | 1.4993 | 1.4993
2020-07-03 20:00 | Winter | 0.64779 | 0.99605 | 1.5072 | 1.5072 | 1.5072 | 1.5072 | 0.583 | 0.583 | 0.583 | 0.583 | 0.583 | 0.583 | 2.3435 | 3.3804 | 4.0597 | 4.4173 | 5.1324 | 5.8475 | 0.78496 | 2.1323 | 2.6744 | 2.6744 | 2.6744 | 2.6744 | 1.105 | 1.4026 | 1.4026 | 1.4026 | 1.4026 | 1.4026
2020-07-03 21:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.55443 | 0.55443 | 0.55443 | 0.55443 | 0.55443 | 0.55443 | 2.2291 | 3.2155 | 3.8617 | 4.2018 | 4.8821 | 5.5623 | 0.80402 | 2.184 | 2.7393 | 2.7393 | 2.7393 | 2.7393 | 0.99126 | 1.2582 | 1.2582 | 1.2582 | 1.2582 | 1.2582
2020-07-03 22:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.53156 | 0.53156 | 0.53156 | 0.53156 | 0.53156 | 0.53156 | 2.0767 | 2.9956 | 3.5977 | 3.9145 | 4.5482 | 5.182 | 0.78496 | 2.1323 | 2.6744 | 2.6744 | 2.6744 | 2.6744 | 0.99073 | 1.2575 | 1.2575 | 1.2575 | 1.2575 | 1.2575
2020-07-03 23:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.47441 | 0.47441 | 0.47441 | 0.47441 | 0.47441 | 0.47441 | 2.0005 | 2.8857 | 3.4656 | 3.7709 | 4.3813 | 4.9918 | 0.68208 | 1.8528 | 2.3239 | 2.3239 | 2.3239 | 2.3239 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-07-04 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 1.7719 | 2.5559 | 3.0696 | 3.3399 | 3.8806 | 4.4213 | 0.63635 | 1.7286 | 2.1681 | 2.1681 | 2.1681 | 2.1681 | 0.89234 | 1.1326 | 1.1326 | 1.1326 | 1.1326 | 1.1326
2020-07-04 01:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.60587 | 1.6458 | 2.0642 | 2.0642 | 2.0642 | 2.0642 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-07-04 02:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 1.5737 | 2.27 | 2.7263 | 2.9664 | 3.4466 | 3.9268 | 0.5792 | 1.5733 | 1.9733 | 1.9733 | 1.9733 | 1.9733 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-07-04 03:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 1.6576 | 2.391 | 2.8715 | 3.1244 | 3.6302 | 4.1361 | 0.57539 | 1.563 | 1.9603 | 1.9603 | 1.9603 | 1.9603 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-07-04 04:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.49727 | 0.49727 | 0.49727 | 0.49727 | 0.49727 | 0.49727 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.55252 | 1.5009 | 1.8825 | 1.8825 | 1.8825 | 1.8825 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-07-04 05:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.50013 | 0.50013 | 0.50013 | 0.50013 | 0.50013 | 0.50013 | 1.7147 | 2.4735 | 2.9705 | 3.2322 | 3.7554 | 4.2787 | 0.58301 | 1.5837 | 1.9863 | 1.9863 | 1.9863 | 1.9863 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-07-04 06:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.53442 | 0.53442 | 0.53442 | 0.53442 | 0.53442 | 0.53442 | 1.9064 | 2.7499 | 3.3025 | 3.5934 | 4.1751 | 4.7568 | 0.6516 | 1.77 | 2.22 | 2.22 | 2.22 | 2.22 | 0.97858 | 1.2421 | 1.2421 | 1.2421 | 1.2421 | 1.2421
2020-07-04 07:00 | Winter | 0.724 | 1.1132 | 1.6845 | 1.6845 | 1.6845 | 1.6845 | 0.62873 | 0.62873 | 0.62873 | 0.62873 | 0.62873 | 0.62873 | 1.9624 | 2.8307 | 3.3996 | 3.699 | 4.2979 | 4.8967 | 0.65541 | 1.7803 | 2.233 | 2.233 | 2.233 | 2.233 | 0.99073 | 1.2575 | 1.2575 | 1.2575 | 1.2575 | 1.2575
2020-07-04 08:00 | Winter | 0.70494 | 1.0839 | 1.6402 | 1.6402 | 1.6402 | 1.6402 | 0.64588 | 0.64588 | 0.64588 | 0.64588 | 0.64588 | 0.64588 | 2.1148 | 3.0506 | 3.6637 | 3.9863 | 4.6317 | 5.277 | 0.7621 | 2.0702 | 2.5965 | 2.5965 | 2.5965 | 2.5965 | 1.0479 | 1.3301 | 1.3301 | 1.3301 | 1.3301 | 1.3301
2020-07-04 09:00 | Winter | 0.70494 | 1.0839 | 1.6402 | 1.6402 | 1.6402 | 1.6402 | 0.66588 | 0.66588 | 0.66588 | 0.66588 | 0.66588 | 0.66588 | 2.191 | 3.1605 | 3.7957 | 4.13 | 4.7986 | 5.4672 | 0.74305 | 2.0184 | 2.5316 | 2.5316 | 2.5316 | 2.5316 | 1.086 | 1.3784 | 1.3784 | 1.3784 | 1.3784 | 1.3784
2020-07-04 10:00 | Winter | 0.64779 | 0.99605 | 1.5072 | 1.5072 | 1.5072 | 1.5072 | 0.64016 | 0.64016 | 0.64016 | 0.64016 | 0.64016 | 0.64016 | 2.2291 | 3.2155 | 3.8617 | 4.2018 | 4.8821 | 5.5623 | 0.74305 | 2.0184 | 2.5316 | 2.5316 | 2.5316 | 2.5316 | 1.1432 | 1.451 | 1.451 | 1.451 | 1.451 | 1.451
2020-07-04 11:00 | Winter | 0.64779 | 0.99605 | 1.5072 | 1.5072 | 1.5072 | 1.5072 | 0.62873 | 0.62873 | 0.62873 | 0.62873 | 0.62873 | 0.62873 | 2.2482 | 3.243 | 3.8947 | 4.2377 | 4.9238 | 5.6098 | 0.70494 | 1.9149 | 2.4018 | 2.4018 | 2.4018 | 2.4018 | 1.1241 | 1.4268 | 1.4268 | 1.4268 | 1.4268 | 1.4268
2020-07-04 12:00 | Winter | 0.66684 | 1.0253 | 1.5515 | 1.5515 | 1.5515 | 1.5515 | 0.62016 | 0.62016 | 0.62016 | 0.62016 | 0.62016 | 0.62016 | 2.1529 | 3.1056 | 3.7297 | 4.0582 | 4.7151 | 5.3721 | 0.72018 | 1.9563 | 2.4537 | 2.4537 | 2.4537 | 2.4537 | 1.086 | 1.3784 | 1.3784 | 1.3784 | 1.3784 | 1.3784
2020-07-04 13:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.58872 | 0.58872 | 0.58872 | 0.58872 | 0.58872 | 0.58872 | 2.172 | 3.133 | 3.7627 | 4.0941 | 4.7569 | 5.4197 | 0.69732 | 1.8942 | 2.3758 | 2.3758 | 2.3758 | 2.3758 | 1.0669 | 1.3542 | 1.3542 | 1.3542 | 1.3542 | 1.3542
2020-07-04 14:00 | Winter | 0.64779 | 0.99605 | 1.5072 | 1.5072 | 1.5072 | 1.5072 | 0.58586 | 0.58586 | 0.58586 | 0.58586 | 0.58586 | 0.58586 | 2.1339 | 3.0781 | 3.6967 | 4.0223 | 4.6734 | 5.3246 | 0.70875 | 1.9253 | 2.4147 | 2.4147 | 2.4147 | 2.4147 | 0.99073 | 1.2575 | 1.2575 | 1.2575 | 1.2575 | 1.2575
2020-07-04 15:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.62873 | 0.62873 | 0.62873 | 0.62873 | 0.62873 | 0.62873 | 2.1724 | 3.1336 | 3.7634 | 4.0949 | 4.7578 | 5.4207 | 0.74305 | 2.0184 | 2.5316 | 2.5316 | 2.5316 | 2.5316 | 1.0098 | 1.2817 | 1.2817 | 1.2817 | 1.2817 | 1.2817
2020-07-04 16:00 | Winter | 0.64779 | 0.99605 | 1.5072 | 1.5072 | 1.5072 | 1.5072 | 0.62873 | 0.62873 | 0.62873 | 0.62873 | 0.62873 | 0.62873 | 2.3816 | 3.4353 | 4.1258 | 4.4891 | 5.2159 | 5.9426 | 0.7621 | 2.0702 | 2.5965 | 2.5965 | 2.5965 | 2.5965 | 0.99073 | 1.2575 | 1.2575 | 1.2575 | 1.2575 | 1.2575
2020-07-04 17:00 | Winter | 0.62921 | 0.96749 | 1.464 | 1.464 | 1.464 | 1.464 | 0.65159 | 0.65159 | 0.65159 | 0.65159 | 0.65159 | 0.65159 | 2.4197 | 3.4903 | 4.1918 | 4.561 | 5.2993 | 6.0377 | 0.84593 | 2.2979 | 2.8821 | 2.8821 | 2.8821 | 2.8821 | 0.99073 | 1.2575 | 1.2575 | 1.2575 | 1.2575 | 1.2575
2020-07-04 18:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.68875 | 0.68875 | 0.68875 | 0.68875 | 0.68875 | 0.68875 | 2.5149 | 3.6277 | 4.3568 | 4.7405 | 5.508 | 6.2754 | 0.89547 | 2.4325 | 3.0509 | 3.0509 | 3.0509 | 3.0509 | 0.97168 | 1.2333 | 1.2333 | 1.2333 | 1.2333 | 1.2333
2020-07-04 19:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.62016 | 0.62016 | 0.62016 | 0.62016 | 0.62016 | 0.62016 | 2.4006 | 3.4628 | 4.1588 | 4.525 | 5.2576 | 5.9902 | 0.84974 | 2.3082 | 2.8951 | 2.8951 | 2.8951 | 2.8951 | 0.95263 | 1.2092 | 1.2092 | 1.2092 | 1.2092 | 1.2092
2020-07-04 20:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.60587 | 0.60587 | 0.60587 | 0.60587 | 0.60587 | 0.60587 | 2.2942 | 3.3093 | 3.9744 | 4.3244 | 5.0245 | 5.7246 | 0.78877 | 2.1426 | 2.6874 | 2.6874 | 2.6874 | 2.6874 | 0.93358 | 1.185 | 1.185 | 1.185 | 1.185 | 1.185
2020-07-04 21:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.51727 | 0.51727 | 0.51727 | 0.51727 | 0.51727 | 0.51727 | 2.2863 | 3.2979 | 3.9607 | 4.3096 | 5.0072 | 5.7049 | 0.80021 | 2.1737 | 2.7263 | 2.7263 | 2.7263 | 2.7263 | 0.93358 | 1.185 | 1.185 | 1.185 | 1.185 | 1.185
2020-07-04 22:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.47726 | 0.47726 | 0.47726 | 0.47726 | 0.47726 | 0.47726 | 2.1796 | 3.144 | 3.7759 | 4.1085 | 4.7736 | 5.4387 | 0.75067 | 2.0391 | 2.5575 | 2.5575 | 2.5575 | 2.5575 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-07-04 23:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.48012 | 0.48012 | 0.48012 | 0.48012 | 0.48012 | 0.48012 | 1.9968 | 2.8804 | 3.4593 | 3.7639 | 4.3733 | 4.9826 | 0.69351 | 1.8839 | 2.3628 | 2.3628 | 2.3628 | 2.3628 | 0.85746 | 1.0884 | 1.0884 | 1.0884 | 1.0884 | 1.0884
2020-07-05 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 1.81 | 2.6109 | 3.1356 | 3.4117 | 3.9641 | 4.5164 | 0.69351 | 1.8839 | 2.3628 | 2.3628 | 2.3628 | 2.3628 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-07-05 01:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.42296 | 0.42296 | 0.42296 | 0.42296 | 0.42296 | 0.42296 | 1.6576 | 2.391 | 2.8715 | 3.1244 | 3.6302 | 4.1361 | 0.6173 | 1.6768 | 2.1032 | 2.1032 | 2.1032 | 2.1032 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-07-05 02:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.5087 | 0.5087 | 0.5087 | 0.5087 | 0.5087 | 0.5087 | 1.6004 | 2.3086 | 2.7725 | 3.0167 | 3.5051 | 3.9934 | 0.57539 | 1.563 | 1.9603 | 1.9603 | 1.9603 | 1.9603 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-07-05 03:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.46549 | 0.46549 | 0.46549 | 0.46549 | 0.46549 | 0.46549 | 1.5623 | 2.2536 | 2.7065 | 2.9449 | 3.4216 | 3.8984 | 0.59825 | 1.6251 | 2.0382 | 2.0382 | 2.0382 | 2.0382 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-07-05 04:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.50013 | 0.50013 | 0.50013 | 0.50013 | 0.50013 | 0.50013 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.59921 | 1.6277 | 2.0415 | 2.0415 | 2.0415 | 2.0415 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-07-05 05:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.52013 | 0.52013 | 0.52013 | 0.52013 | 0.52013 | 0.52013 | 1.6351 | 2.3586 | 2.8326 | 3.0821 | 3.581 | 4.08 | 0.60206 | 1.6354 | 2.0512 | 2.0512 | 2.0512 | 2.0512 | 0.93358 | 1.185 | 1.185 | 1.185 | 1.185 | 1.185
2020-07-05 06:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.5087 | 0.5087 | 0.5087 | 0.5087 | 0.5087 | 0.5087 | 1.7909 | 2.5834 | 3.1026 | 3.3758 | 3.9223 | 4.4688 | 0.60206 | 1.6354 | 2.0512 | 2.0512 | 2.0512 | 2.0512 | 0.91452 | 1.1608 | 1.1608 | 1.1608 | 1.1608 | 1.1608
2020-07-05 07:00 | Winter | 0.66684 | 1.0253 | 1.5515 | 1.5515 | 1.5515 | 1.5515 | 0.62016 | 0.62016 | 0.62016 | 0.62016 | 0.62016 | 0.62016 | 1.8716 | 2.6997 | 3.2423 | 3.5278 | 4.099 | 4.6701 | 0.65922 | 1.7907 | 2.246 | 2.246 | 2.246 | 2.246 | 0.91452 | 1.1608 | 1.1608 | 1.1608 | 1.1608 | 1.1608
2020-07-05 08:00 | Winter | 0.68589 | 1.0546 | 1.5959 | 1.5959 | 1.5959 | 1.5959 | 0.64016 | 0.64016 | 0.64016 | 0.64016 | 0.64016 | 0.64016 | 2.0958 | 3.0231 | 3.6307 | 3.9504 | 4.59 | 5.2295 | 0.67065 | 1.8218 | 2.2849 | 2.2849 | 2.2849 | 2.2849 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-07-05 09:00 | Winter | 0.64779 | 0.99605 | 1.5072 | 1.5072 | 1.5072 | 1.5072 | 0.58586 | 0.58586 | 0.58586 | 0.58586 | 0.58586 | 0.58586 | 2.1529 | 3.1056 | 3.7297 | 4.0582 | 4.7151 | 5.3721 | 0.74305 | 2.0184 | 2.5316 | 2.5316 | 2.5316 | 2.5316 | 0.95263 | 1.2092 | 1.2092 | 1.2092 | 1.2092 | 1.2092
2020-07-05 10:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.58015 | 0.58015 | 0.58015 | 0.58015 | 0.58015 | 0.58015 | 2.1529 | 3.1056 | 3.7297 | 4.0582 | 4.7151 | 5.3721 | 0.71256 | 1.9356 | 2.4277 | 2.4277 | 2.4277 | 2.4277 | 1.105 | 1.4026 | 1.4026 | 1.4026 | 1.4026 | 1.4026
2020-07-05 11:00 | Winter | 0.62544 | 0.96169 | 1.4552 | 1.4552 | 1.4552 | 1.4552 | 0.54299 | 0.54299 | 0.54299 | 0.54299 | 0.54299 | 0.54299 | 2.0958 | 3.0231 | 3.6307 | 3.9504 | 4.59 | 5.2295 | 0.6897 | 1.8735 | 2.3498 | 2.3498 | 2.3498 | 2.3498 | 1.0098 | 1.2817 | 1.2817 | 1.2817 | 1.2817 | 1.2817
2020-07-05 12:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.53728 | 0.53728 | 0.53728 | 0.53728 | 0.53728 | 0.53728 | 2.1148 | 3.0506 | 3.6637 | 3.9863 | 4.6317 | 5.277 | 0.63635 | 1.7286 | 2.1681 | 2.1681 | 2.1681 | 2.1681 | 0.99073 | 1.2575 | 1.2575 | 1.2575 | 1.2575 | 1.2575
2020-07-05 13:00 | Winter | 0.66684 | 1.0253 | 1.5515 | 1.5515 | 1.5515 | 1.5515 | 0.53156 | 0.53156 | 0.53156 | 0.53156 | 0.53156 | 0.53156 | 2.1148 | 3.0506 | 3.6637 | 3.9863 | 4.6317 | 5.277 | 0.60968 | 1.6561 | 2.0772 | 2.0772 | 2.0772 | 2.0772 | 0.95263 | 1.2092 | 1.2092 | 1.2092 | 1.2092 | 1.2092
2020-07-05 14:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.54585 | 0.54585 | 0.54585 | 0.54585 | 0.54585 | 0.54585 | 2.0586 | 2.9695 | 3.5662 | 3.8803 | 4.5085 | 5.1367 | 0.6173 | 1.6768 | 2.1032 | 2.1032 | 2.1032 | 2.1032 | 0.93358 | 1.185 | 1.185 | 1.185 | 1.185 | 1.185
2020-07-05 15:00 | Winter | 0.64779 | 0.99605 | 1.5072 | 1.5072 | 1.5072 | 1.5072 | 0.56586 | 0.56586 | 0.56586 | 0.56586 | 0.56586 | 0.56586 | 2.1339 | 3.0781 | 3.6967 | 4.0223 | 4.6734 | 5.3246 | 0.67065 | 1.8218 | 2.2849 | 2.2849 | 2.2849 | 2.2849 | 0.86099 | 1.0928 | 1.0928 | 1.0928 | 1.0928 | 1.0928
2020-07-05 16:00 | Winter | 0.64779 | 0.99605 | 1.5072 | 1.5072 | 1.5072 | 1.5072 | 0.59679 | 0.59679 | 0.59679 | 0.59679 | 0.59679 | 0.59679 | 2.2673 | 3.2705 | 3.9277 | 4.2736 | 4.9655 | 5.6574 | 0.67827 | 1.8425 | 2.3109 | 2.3109 | 2.3109 | 2.3109 | 0.93358 | 1.185 | 1.185 | 1.185 | 1.185 | 1.185
2020-07-05 17:00 | Winter | 0.60726 | 0.93373 | 1.4129 | 1.4129 | 1.4129 | 1.4129 | 0.64016 | 0.64016 | 0.64016 | 0.64016 | 0.64016 | 0.64016 | 2.3816 | 3.4353 | 4.1258 | 4.4891 | 5.2159 | 5.9426 | 0.76972 | 2.0909 | 2.6225 | 2.6225 | 2.6225 | 2.6225 | 0.93358 | 1.185 | 1.185 | 1.185 | 1.185 | 1.185
2020-07-05 18:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.59158 | 0.59158 | 0.59158 | 0.59158 | 0.59158 | 0.59158 | 2.4197 | 3.4903 | 4.1918 | 4.561 | 5.2993 | 6.0377 | 0.77353 | 2.1012 | 2.6354 | 2.6354 | 2.6354 | 2.6354 | 0.97168 | 1.2333 | 1.2333 | 1.2333 | 1.2333 | 1.2333
2020-07-05 19:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.60873 | 0.60873 | 0.60873 | 0.60873 | 0.60873 | 0.60873 | 2.4006 | 3.4628 | 4.1588 | 4.525 | 5.2576 | 5.9902 | 0.86498 | 2.3496 | 2.947 | 2.947 | 2.947 | 2.947 | 0.93358 | 1.185 | 1.185 | 1.185 | 1.185 | 1.185
2020-07-05 20:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.60873 | 0.60873 | 0.60873 | 0.60873 | 0.60873 | 0.60873 | 2.3054 | 3.3254 | 3.9937 | 4.3455 | 5.049 | 5.7525 | 0.75448 | 2.0495 | 2.5705 | 2.5705 | 2.5705 | 2.5705 | 0.95263 | 1.2092 | 1.2092 | 1.2092 | 1.2092 | 1.2092
2020-07-05 21:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 2.2301 | 3.2169 | 3.8634 | 4.2036 | 4.8841 | 5.5647 | 0.76972 | 2.0909 | 2.6225 | 2.6225 | 2.6225 | 2.6225 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-07-05 22:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.42296 | 0.42296 | 0.42296 | 0.42296 | 0.42296 | 0.42296 | 2.0196 | 2.9132 | 3.4986 | 3.8068 | 4.4231 | 5.0393 | 0.76591 | 2.0805 | 2.6095 | 2.6095 | 2.6095 | 2.6095 | 0.88853 | 1.1278 | 1.1278 | 1.1278 | 1.1278 | 1.1278
2020-07-05 23:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.43995 | 0.43995 | 0.43995 | 0.43995 | 0.43995 | 0.43995 | 1.9053 | 2.7483 | 3.3006 | 3.5913 | 4.1727 | 4.7541 | 0.65922 | 1.7907 | 2.246 | 2.246 | 2.246 | 2.246 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-07-06 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 1.658 | 2.3916 | 2.8723 | 3.1252 | 3.6312 | 4.1371 | 0.59063 | 1.6044 | 2.0123 | 2.0123 | 2.0123 | 2.0123 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-07-06 01:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 1.6576 | 2.391 | 2.8715 | 3.1244 | 3.6302 | 4.1361 | 0.59063 | 1.6044 | 2.0123 | 2.0123 | 2.0123 | 2.0123 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-07-06 02:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.49727 | 0.49727 | 0.49727 | 0.49727 | 0.49727 | 0.49727 | 1.5623 | 2.2536 | 2.7065 | 2.9449 | 3.4216 | 3.8984 | 0.5792 | 1.5733 | 1.9733 | 1.9733 | 1.9733 | 1.9733 | 1.1241 | 1.4268 | 1.4268 | 1.4268 | 1.4268 | 1.4268
2020-07-06 03:00 | Winter | 0.54847 | 0.84333 | 1.2761 | 1.2761 | 1.2761 | 1.2761 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 1.5244 | 2.1989 | 2.6408 | 2.8734 | 3.3386 | 3.8038 | 0.52585 | 1.4284 | 1.7916 | 1.7916 | 1.7916 | 1.7916 | 1.1432 | 1.451 | 1.451 | 1.451 | 1.451 | 1.451
2020-07-06 04:00 | Winter | 0.64779 | 0.99605 | 1.5072 | 1.5072 | 1.5072 | 1.5072 | 0.54871 | 0.54871 | 0.54871 | 0.54871 | 0.54871 | 0.54871 | 1.6858 | 2.4317 | 2.9204 | 3.1776 | 3.692 | 4.2065 | 0.56395 | 1.5319 | 1.9214 | 1.9214 | 1.9214 | 1.9214 | 1.1241 | 1.4268 | 1.4268 | 1.4268 | 1.4268 | 1.4268
2020-07-06 05:00 | Winter | 0.78115 | 1.2011 | 1.8175 | 1.8175 | 1.8175 | 1.8175 | 0.65445 | 0.65445 | 0.65445 | 0.65445 | 0.65445 | 0.65445 | 1.8888 | 2.7245 | 3.2721 | 3.5602 | 4.1366 | 4.713 | 0.74686 | 2.0288 | 2.5446 | 2.5446 | 2.5446 | 2.5446 | 1.5389 | 1.9532 | 1.9532 | 1.9532 | 1.9532 | 1.9532
2020-07-06 06:00 | Winter | 0.91364 | 1.4048 | 2.1258 | 2.1258 | 2.1258 | 2.1258 | 0.77734 | 0.77734 | 0.77734 | 0.77734 | 0.77734 | 0.77734 | 2.0879 | 3.0118 | 3.617 | 3.9356 | 4.5728 | 5.2099 | 0.80021 | 2.1737 | 2.7263 | 2.7263 | 2.7263 | 2.7263 | 1.9568 | 2.4837 | 2.4837 | 2.4837 | 2.4837 | 2.4837
2020-07-06 07:00 | Winter | 1.1813 | 1.8163 | 2.7485 | 2.7485 | 2.7485 | 2.7485 | 0.88807 | 0.88807 | 0.88807 | 0.88807 | 0.88807 | 0.88807 | 2.3625 | 3.4079 | 4.0927 | 4.4532 | 5.1741 | 5.8951 | 0.89928 | 2.4428 | 3.0639 | 3.0639 | 3.0639 | 3.0639 | 2.4768 | 3.1438 | 3.1438 | 3.1438 | 3.1438 | 3.1438
2020-07-06 08:00 | Winter | 1.3718 | 2.1093 | 3.1918 | 3.1918 | 3.1918 | 3.1918 | 0.9974 | 0.9974 | 0.9974 | 0.9974 | 0.9974 | 0.9974 | 2.6674 | 3.8476 | 4.6208 | 5.0278 | 5.8418 | 6.6557 | 0.94119 | 2.5567 | 3.2067 | 3.2067 | 3.2067 | 3.2067 | 2.6483 | 3.3614 | 3.3614 | 3.3614 | 3.3614 | 3.3614
2020-07-06 09:00 | Winter | 1.3527 | 2.08 | 3.1474 | 3.1474 | 3.1474 | 3.1474 | 1.1317 | 1.1317 | 1.1317 | 1.1317 | 1.1317 | 1.1317 | 2.8388 | 4.0949 | 4.9179 | 5.351 | 6.2173 | 7.0836 | 0.92214 | 2.5049 | 3.1418 | 3.1418 | 3.1418 | 3.1418 | 2.7436 | 3.4824 | 3.4824 | 3.4824 | 3.4824 | 3.4824
2020-07-06 10:00 | Winter | 1.3146 | 2.0214 | 3.0588 | 3.0588 | 3.0588 | 3.0588 | 1.0774 | 1.0774 | 1.0774 | 1.0774 | 1.0774 | 1.0774 | 2.7817 | 4.0125 | 4.8189 | 5.2433 | 6.0921 | 6.941 | 0.89547 | 2.4325 | 3.0509 | 3.0509 | 3.0509 | 3.0509 | 2.7817 | 3.5307 | 3.5307 | 3.5307 | 3.5307 | 3.5307
2020-07-06 11:00 | Winter | 1.2956 | 1.9921 | 3.0144 | 3.0144 | 3.0144 | 3.0144 | 1.0917 | 1.0917 | 1.0917 | 1.0917 | 1.0917 | 1.0917 | 2.7817 | 4.0125 | 4.8189 | 5.2433 | 6.0921 | 6.941 | 0.92976 | 2.5256 | 3.1677 | 3.1677 | 3.1677 | 3.1677 | 2.7626 | 3.5065 | 3.5065 | 3.5065 | 3.5065 | 3.5065
2020-07-06 12:00 | Winter | 1.2765 | 1.9628 | 2.9701 | 2.9701 | 2.9701 | 2.9701 | 0.9974 | 0.9974 | 0.9974 | 0.9974 | 0.9974 | 0.9974 | 2.7436 | 3.9575 | 4.7529 | 5.1715 | 6.0087 | 6.8459 | 0.89547 | 2.4325 | 3.0509 | 3.0509 | 3.0509 | 3.0509 | 2.6486 | 3.3618 | 3.3618 | 3.3618 | 3.3618 | 3.3618
2020-07-06 13:00 | Winter | 1.2384 | 1.9042 | 2.8814 | 2.8814 | 2.8814 | 2.8814 | 1.0174 | 1.0174 | 1.0174 | 1.0174 | 1.0174 | 1.0174 | 2.6293 | 3.7926 | 4.5548 | 4.956 | 5.7583 | 6.5606 | 0.92976 | 2.5256 | 3.1677 | 3.1677 | 3.1677 | 3.1677 | 2.6102 | 3.3131 | 3.3131 | 3.3131 | 3.3131 | 3.3131
2020-07-06 14:00 | Winter | 1.2233 | 1.8809 | 2.8462 | 2.8462 | 2.8462 | 2.8462 | 0.99168 | 0.99168 | 0.99168 | 0.99168 | 0.99168 | 0.99168 | 2.5721 | 3.7102 | 4.4558 | 4.8483 | 5.6331 | 6.418 | 0.88349 | 2.3999 | 3.0101 | 3.0101 | 3.0101 | 3.0101 | 2.4959 | 3.168 | 3.168 | 3.168 | 3.168 | 3.168
2020-07-06 15:00 | Winter | 1.2575 | 1.9335 | 2.9258 | 2.9258 | 2.9258 | 2.9258 | 1.0546 | 1.0546 | 1.0546 | 1.0546 | 1.0546 | 1.0546 | 2.6102 | 3.7651 | 4.5218 | 4.9201 | 5.7166 | 6.5131 | 0.92214 | 2.5049 | 3.1418 | 3.1418 | 3.1418 | 3.1418 | 2.4959 | 3.168 | 3.168 | 3.168 | 3.168 | 3.168
2020-07-06 16:00 | Winter | 1.2194 | 1.8749 | 2.8371 | 2.8371 | 2.8371 | 2.8371 | 1.066 | 1.066 | 1.066 | 1.066 | 1.066 | 1.066 | 2.6483 | 3.8201 | 4.5878 | 4.9919 | 5.8 | 6.6082 | 0.91833 | 2.4946 | 3.1288 | 3.1288 | 3.1288 | 3.1288 | 2.4387 | 3.0954 | 3.0954 | 3.0954 | 3.0954 | 3.0954
2020-07-06 17:00 | Winter | 1.1241 | 1.7284 | 2.6155 | 2.6155 | 2.6155 | 2.6155 | 0.91452 | 0.91452 | 0.91452 | 0.91452 | 0.91452 | 0.91452 | 2.7055 | 3.9026 | 4.6869 | 5.0996 | 5.9252 | 6.7508 | 0.95263 | 2.5877 | 3.2456 | 3.2456 | 3.2456 | 3.2456 | 2.3126 | 2.9354 | 2.9354 | 2.9354 | 2.9354 | 2.9354
2020-07-06 18:00 | Winter | 0.92324 | 1.4196 | 2.1481 | 2.1481 | 2.1481 | 2.1481 | 0.82592 | 0.82592 | 0.82592 | 0.82592 | 0.82592 | 0.82592 | 2.6864 | 3.8751 | 4.6539 | 5.0637 | 5.8835 | 6.7033 | 0.89547 | 2.4325 | 3.0509 | 3.0509 | 3.0509 | 3.0509 | 1.642 | 2.0841 | 2.0841 | 2.0841 | 2.0841 | 2.0841
2020-07-06 19:00 | Winter | 0.724 | 1.1132 | 1.6845 | 1.6845 | 1.6845 | 1.6845 | 0.66588 | 0.66588 | 0.66588 | 0.66588 | 0.66588 | 0.66588 | 2.5442 | 3.67 | 4.4075 | 4.7957 | 5.5721 | 6.3485 | 0.80021 | 2.1737 | 2.7263 | 2.7263 | 2.7263 | 2.7263 | 1.2859 | 1.6321 | 1.6321 | 1.6321 | 1.6321 | 1.6321
2020-07-06 20:00 | Winter | 0.66684 | 1.0253 | 1.5515 | 1.5515 | 1.5515 | 1.5515 | 0.43439 | 0.43439 | 0.43439 | 0.43439 | 0.43439 | 0.43439 | 2.3625 | 3.4079 | 4.0927 | 4.4532 | 5.1741 | 5.8951 | 0.85736 | 2.3289 | 2.9211 | 2.9211 | 2.9211 | 2.9211 | 1.1241 | 1.4268 | 1.4268 | 1.4268 | 1.4268 | 1.4268
2020-07-06 21:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 2.3244 | 3.3529 | 4.0267 | 4.3814 | 5.0907 | 5.8 | 0.76591 | 2.0805 | 2.6095 | 2.6095 | 2.6095 | 2.6095 | 1.0288 | 1.3059 | 1.3059 | 1.3059 | 1.3059 | 1.3059
2020-07-06 22:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 2.1529 | 3.1056 | 3.7297 | 4.0582 | 4.7151 | 5.3721 | 0.80402 | 2.184 | 2.7393 | 2.7393 | 2.7393 | 2.7393 | 0.88668 | 1.1254 | 1.1254 | 1.1254 | 1.1254 | 1.1254
2020-07-06 23:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 1.8862 | 2.7208 | 3.2676 | 3.5554 | 4.131 | 4.7066 | 0.64808 | 1.7605 | 2.208 | 2.208 | 2.208 | 2.208 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-07-07 | Winter | 0.62154 | 0.95569 | 1.4461 | 1.4461 | 1.4461 | 1.4461 | 0.39438 | 0.39438 | 0.39438 | 0.39438 | 0.39438 | 0.39438 | 1.7147 | 2.4735 | 2.9705 | 3.2322 | 3.7554 | 4.2787 | 0.60968 | 1.6561 | 2.0772 | 2.0772 | 2.0772 | 2.0772 | 0.91452 | 1.1608 | 1.1608 | 1.1608 | 1.1608 | 1.1608
2020-07-07 01:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 1.5815 | 2.2813 | 2.7397 | 2.981 | 3.4636 | 3.9462 | 0.59063 | 1.6044 | 2.0123 | 2.0123 | 2.0123 | 2.0123 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-07-07 02:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 1.6004 | 2.3086 | 2.7725 | 3.0167 | 3.5051 | 3.9934 | 0.57157 | 1.5526 | 1.9474 | 1.9474 | 1.9474 | 1.9474 | 1.1432 | 1.451 | 1.451 | 1.451 | 1.451 | 1.451
2020-07-07 03:00 | Winter | 0.60329 | 0.92762 | 1.4037 | 1.4037 | 1.4037 | 1.4037 | 0.43439 | 0.43439 | 0.43439 | 0.43439 | 0.43439 | 0.43439 | 1.5433 | 2.2261 | 2.6735 | 2.909 | 3.3799 | 3.8508 | 0.58301 | 1.5837 | 1.9863 | 1.9863 | 1.9863 | 1.9863 | 1.1432 | 1.451 | 1.451 | 1.451 | 1.451 | 1.451
2020-07-07 04:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 1.5636 | 2.2555 | 2.7088 | 2.9473 | 3.4245 | 3.9016 | 0.55252 | 1.5009 | 1.8825 | 1.8825 | 1.8825 | 1.8825 | 1.2219 | 1.551 | 1.551 | 1.551 | 1.551 | 1.551
2020-07-07 05:00 | Winter | 0.79912 | 1.2287 | 1.8593 | 1.8593 | 1.8593 | 1.8593 | 0.64302 | 0.64302 | 0.64302 | 0.64302 | 0.64302 | 0.64302 | 1.84 | 2.6542 | 3.1876 | 3.4683 | 4.0298 | 4.5913 | 0.70113 | 1.9046 | 2.3888 | 2.3888 | 2.3888 | 2.3888 | 1.5323 | 1.9449 | 1.9449 | 1.9449 | 1.9449 | 1.9449
2020-07-07 06:00 | Winter | 0.93358 | 1.4355 | 2.1722 | 2.1722 | 2.1722 | 2.1722 | 0.73161 | 0.73161 | 0.73161 | 0.73161 | 0.73161 | 0.73161 | 2.1817 | 3.147 | 3.7795 | 4.1124 | 4.7781 | 5.4439 | 0.80783 | 2.1944 | 2.7523 | 2.7523 | 2.7523 | 2.7523 | 1.9255 | 2.444 | 2.444 | 2.444 | 2.444 | 2.444
2020-07-07 07:00 | Winter | 1.0859 | 1.6697 | 2.5265 | 2.5265 | 2.5265 | 2.5265 | 0.9088 | 0.9088 | 0.9088 | 0.9088 | 0.9088 | 0.9088 | 2.4768 | 3.5728 | 4.2908 | 4.6687 | 5.4245 | 6.1803 | 0.89928 | 2.4428 | 3.0639 | 3.0639 | 3.0639 | 3.0639 | 2.4006 | 3.0471 | 3.0471 | 3.0471 | 3.0471 | 3.0471
2020-07-07 08:00 | Winter | 1.3146 | 2.0214 | 3.0588 | 3.0588 | 3.0588 | 3.0588 | 1.1403 | 1.1403 | 1.1403 | 1.1403 | 1.1403 | 1.1403 | 2.6483 | 3.8201 | 4.5878 | 4.9919 | 5.8 | 6.6082 | 0.9793 | 2.6602 | 3.3365 | 3.3365 | 3.3365 | 3.3365 | 2.6483 | 3.3614 | 3.3614 | 3.3614 | 3.3614 | 3.3614
2020-07-07 09:00 | Winter | 1.3527 | 2.08 | 3.1474 | 3.1474 | 3.1474 | 3.1474 | 1.1517 | 1.1517 | 1.1517 | 1.1517 | 1.1517 | 1.1517 | 2.7055 | 3.9026 | 4.6869 | 5.0996 | 5.9252 | 6.7508 | 0.92976 | 2.5256 | 3.1677 | 3.1677 | 3.1677 | 3.1677 | 2.6864 | 3.4098 | 3.4098 | 3.4098 | 3.4098 | 3.4098
2020-07-07 10:00 | Winter | 1.3146 | 2.0214 | 3.0588 | 3.0588 | 3.0588 | 3.0588 | 1.1431 | 1.1431 | 1.1431 | 1.1431 | 1.1431 | 1.1431 | 2.6864 | 3.8751 | 4.6539 | 5.0637 | 5.8835 | 6.7033 | 0.87261 | 2.3704 | 2.973 | 2.973 | 2.973 | 2.973 | 2.6293 | 3.3373 | 3.3373 | 3.3373 | 3.3373 | 3.3373
2020-07-07 11:00 | Winter | 1.3146 | 2.0214 | 3.0588 | 3.0588 | 3.0588 | 3.0588 | 1.1174 | 1.1174 | 1.1174 | 1.1174 | 1.1174 | 1.1174 | 2.7436 | 3.9575 | 4.7529 | 5.1715 | 6.0087 | 6.8459 | 0.86498 | 2.3496 | 2.947 | 2.947 | 2.947 | 2.947 | 2.6483 | 3.3614 | 3.3614 | 3.3614 | 3.3614 | 3.3614
2020-07-07 12:00 | Winter | 1.2765 | 1.9628 | 2.9701 | 2.9701 | 2.9701 | 2.9701 | 1.126 | 1.126 | 1.126 | 1.126 | 1.126 | 1.126 | 2.6864 | 3.8751 | 4.6539 | 5.0637 | 5.8835 | 6.7033 | 0.8345 | 2.2668 | 2.8432 | 2.8432 | 2.8432 | 2.8432 | 2.56 | 3.2494 | 3.2494 | 3.2494 | 3.2494 | 3.2494
2020-07-07 13:00 | Winter | 1.2765 | 1.9628 | 2.9701 | 2.9701 | 2.9701 | 2.9701 | 0.99454 | 0.99454 | 0.99454 | 0.99454 | 0.99454 | 0.99454 | 2.6674 | 3.8476 | 4.6208 | 5.0278 | 5.8418 | 6.6557 | 0.7964 | 2.1633 | 2.7133 | 2.7133 | 2.7133 | 2.7133 | 2.4959 | 3.168 | 3.168 | 3.168 | 3.168 | 3.168
2020-07-07 14:00 | Winter | 1.2956 | 1.9921 | 3.0144 | 3.0144 | 3.0144 | 3.0144 | 0.89737 | 0.89737 | 0.89737 | 0.89737 | 0.89737 | 0.89737 | 2.6075 | 3.7613 | 4.5172 | 4.915 | 5.7107 | 6.5064 | 0.7964 | 2.1633 | 2.7133 | 2.7133 | 2.7133 | 2.7133 | 2.3816 | 3.0229 | 3.0229 | 3.0229 | 3.0229 | 3.0229
2020-07-07 15:00 | Winter | 1.2765 | 1.9628 | 2.9701 | 2.9701 | 2.9701 | 2.9701 | 0.94596 | 0.94596 | 0.94596 | 0.94596 | 0.94596 | 0.94596 | 2.534 | 3.6552 | 4.3898 | 4.7764 | 5.5497 | 6.3229 | 0.86117 | 2.3393 | 2.934 | 2.934 | 2.934 | 2.934 | 2.3625 | 2.9987 | 2.9987 | 2.9987 | 2.9987 | 2.9987
2020-07-07 16:00 | Winter | 1.2003 | 1.8456 | 2.7928 | 2.7928 | 2.7928 | 2.7928 | 0.95453 | 0.95453 | 0.95453 | 0.95453 | 0.95453 | 0.95453 | 2.4959 | 3.6002 | 4.3238 | 4.7046 | 5.4662 | 6.2279 | 0.87642 | 2.3807 | 2.986 | 2.986 | 2.986 | 2.986 | 2.3054 | 2.9261 | 2.9261 | 2.9261 | 2.9261 | 2.9261
2020-07-07 17:00 | Winter | 1.1432 | 1.7577 | 2.6598 | 2.6598 | 2.6598 | 2.6598 | 0.91452 | 0.91452 | 0.91452 | 0.91452 | 0.91452 | 0.91452 | 2.6102 | 3.7651 | 4.5218 | 4.9201 | 5.7166 | 6.5131 | 0.86879 | 2.36 | 2.96 | 2.96 | 2.96 | 2.96 | 2.191 | 2.781 | 2.781 | 2.781 | 2.781 | 2.781
2020-07-07 18:00 | Winter | 0.89934 | 1.3828 | 2.0925 | 2.0925 | 2.0925 | 2.0925 | 0.82307 | 0.82307 | 0.82307 | 0.82307 | 0.82307 | 0.82307 | 2.5554 | 3.6861 | 4.427 | 4.8169 | 5.5966 | 6.3764 | 0.84212 | 2.2875 | 2.8691 | 2.8691 | 2.8691 | 2.8691 | 1.697 | 2.154 | 2.154 | 2.154 | 2.154 | 2.154
2020-07-07 19:00 | Winter | 0.68589 | 1.0546 | 1.5959 | 1.5959 | 1.5959 | 1.5959 | 0.64307 | 0.64307 | 0.64307 | 0.64307 | 0.64307 | 0.64307 | 2.4441 | 3.5256 | 4.2341 | 4.607 | 5.3529 | 6.0987 | 0.81926 | 2.2254 | 2.7912 | 2.7912 | 2.7912 | 2.7912 | 1.2003 | 1.5235 | 1.5235 | 1.5235 | 1.5235 | 1.5235
2020-07-07 20:00 | Winter | 0.66684 | 1.0253 | 1.5515 | 1.5515 | 1.5515 | 1.5515 | 0.4557 | 0.4557 | 0.4557 | 0.4557 | 0.4557 | 0.4557 | 2.3244 | 3.3529 | 4.0267 | 4.3814 | 5.0907 | 5.8 | 0.75067 | 2.0391 | 2.5575 | 2.5575 | 2.5575 | 2.5575 | 1.086 | 1.3784 | 1.3784 | 1.3784 | 1.3784 | 1.3784
2020-07-07 21:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 2.2101 | 3.188 | 3.8287 | 4.1659 | 4.8403 | 5.5147 | 0.73543 | 1.9977 | 2.5056 | 2.5056 | 2.5056 | 2.5056 | 0.98539 | 1.2507 | 1.2507 | 1.2507 | 1.2507 | 1.2507
2020-07-07 22:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 2.0962 | 3.0238 | 3.6314 | 3.9513 | 4.5909 | 5.2306 | 0.71256 | 1.9356 | 2.4277 | 2.4277 | 2.4277 | 2.4277 | 0.93358 | 1.185 | 1.185 | 1.185 | 1.185 | 1.185
2020-07-07 23:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 1.8839 | 2.7175 | 3.2636 | 3.5511 | 4.1259 | 4.7008 | 0.59444 | 1.6147 | 2.0253 | 2.0253 | 2.0253 | 2.0253 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-07-08 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.41439 | 0.41439 | 0.41439 | 0.41439 | 0.41439 | 0.41439 | 1.7338 | 2.5009 | 3.0036 | 3.2681 | 3.7972 | 4.3262 | 0.56776 | 1.5423 | 1.9344 | 1.9344 | 1.9344 | 1.9344 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-07-08 01:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 1.6907 | 2.4388 | 2.9289 | 3.1868 | 3.7028 | 4.2187 | 0.5449 | 1.4802 | 1.8565 | 1.8565 | 1.8565 | 1.8565 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-07-08 02:00 | Winter | 0.57245 | 0.88021 | 1.3319 | 1.3319 | 1.3319 | 1.3319 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 1.6004 | 2.3086 | 2.7725 | 3.0167 | 3.5051 | 3.9934 | 0.51061 | 1.387 | 1.7396 | 1.7396 | 1.7396 | 1.7396 | 1.0479 | 1.3301 | 1.3301 | 1.3301 | 1.3301 | 1.3301
2020-07-08 03:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 1.6004 | 2.3086 | 2.7725 | 3.0167 | 3.5051 | 3.9934 | 0.52204 | 1.4181 | 1.7786 | 1.7786 | 1.7786 | 1.7786 | 1.1241 | 1.4268 | 1.4268 | 1.4268 | 1.4268 | 1.4268
2020-07-08 04:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.45447 | 0.45447 | 0.45447 | 0.45447 | 0.45447 | 0.45447 | 1.6957 | 2.446 | 2.9375 | 3.1963 | 3.7137 | 4.2311 | 0.53347 | 1.4491 | 1.8175 | 1.8175 | 1.8175 | 1.8175 | 1.105 | 1.4026 | 1.4026 | 1.4026 | 1.4026 | 1.4026
2020-07-08 05:00 | Winter | 0.80021 | 1.2304 | 1.8619 | 1.8619 | 1.8619 | 1.8619 | 0.64016 | 0.64016 | 0.64016 | 0.64016 | 0.64016 | 0.64016 | 1.81 | 2.6109 | 3.1356 | 3.4117 | 3.9641 | 4.5164 | 0.70113 | 1.9046 | 2.3888 | 2.3888 | 2.3888 | 2.3888 | 1.4662 | 1.861 | 1.861 | 1.861 | 1.861 | 1.861
2020-07-08 06:00 | Winter | 0.85631 | 1.3167 | 1.9924 | 1.9924 | 1.9924 | 1.9924 | 0.74298 | 0.74298 | 0.74298 | 0.74298 | 0.74298 | 0.74298 | 2.0767 | 2.9956 | 3.5977 | 3.9145 | 4.5482 | 5.182 | 0.75448 | 2.0495 | 2.5705 | 2.5705 | 2.5705 | 2.5705 | 1.8097 | 2.297 | 2.297 | 2.297 | 2.297 | 2.297
2020-07-08 07:00 | Winter | 1.122 | 1.7252 | 2.6105 | 2.6105 | 2.6105 | 2.6105 | 0.93329 | 0.93329 | 0.93329 | 0.93329 | 0.93329 | 0.93329 | 2.5729 | 3.7114 | 4.4573 | 4.8499 | 5.635 | 6.4201 | 0.83069 | 2.2565 | 2.8302 | 2.8302 | 2.8302 | 2.8302 | 2.4387 | 3.0954 | 3.0954 | 3.0954 | 3.0954 | 3.0954
2020-07-08 08:00 | Winter | 1.3908 | 2.1386 | 3.2361 | 3.2361 | 3.2361 | 3.2361 | 1.0288 | 1.0288 | 1.0288 | 1.0288 | 1.0288 | 1.0288 | 2.7055 | 3.9026 | 4.6869 | 5.0996 | 5.9252 | 6.7508 | 0.88785 | 2.4118 | 3.0249 | 3.0249 | 3.0249 | 3.0249 | 2.6277 | 3.3353 | 3.3353 | 3.3353 | 3.3353 | 3.3353
2020-07-08 09:00 | Winter | 1.3146 | 2.0214 | 3.0588 | 3.0588 | 3.0588 | 3.0588 | 1.066 | 1.066 | 1.066 | 1.066 | 1.066 | 1.066 | 2.8388 | 4.0949 | 4.9179 | 5.351 | 6.2173 | 7.0836 | 0.90309 | 2.4532 | 3.0768 | 3.0768 | 3.0768 | 3.0768 | 2.7245 | 3.4582 | 3.4582 | 3.4582 | 3.4582 | 3.4582
2020-07-08 10:00 | Winter | 1.3337 | 2.0507 | 3.1031 | 3.1031 | 3.1031 | 3.1031 | 1.0517 | 1.0517 | 1.0517 | 1.0517 | 1.0517 | 1.0517 | 2.8769 | 4.1499 | 4.9839 | 5.4229 | 6.3008 | 7.1787 | 0.80402 | 2.184 | 2.7393 | 2.7393 | 2.7393 | 2.7393 | 2.7055 | 3.434 | 3.434 | 3.434 | 3.434 | 3.434
2020-07-08 11:00 | Winter | 1.2765 | 1.9628 | 2.9701 | 2.9701 | 2.9701 | 2.9701 | 1.0231 | 1.0231 | 1.0231 | 1.0231 | 1.0231 | 1.0231 | 2.8579 | 4.1224 | 4.9509 | 5.387 | 6.259 | 7.1311 | 0.85355 | 2.3186 | 2.9081 | 2.9081 | 2.9081 | 2.9081 | 2.7055 | 3.434 | 3.434 | 3.434 | 3.434 | 3.434
2020-07-08 12:00 | Winter | 1.2956 | 1.9921 | 3.0144 | 3.0144 | 3.0144 | 3.0144 | 0.9974 | 0.9974 | 0.9974 | 0.9974 | 0.9974 | 0.9974 | 2.8198 | 4.0675 | 4.8849 | 5.3151 | 6.1756 | 7.0361 | 0.86498 | 2.3496 | 2.947 | 2.947 | 2.947 | 2.947 | 2.5937 | 3.2922 | 3.2922 | 3.2922 | 3.2922 | 3.2922
2020-07-08 13:00 | Winter | 1.2384 | 1.9042 | 2.8814 | 2.8814 | 2.8814 | 2.8814 | 0.98597 | 0.98597 | 0.98597 | 0.98597 | 0.98597 | 0.98597 | 2.7436 | 3.9575 | 4.7529 | 5.1715 | 6.0087 | 6.8459 | 0.82688 | 2.2461 | 2.8172 | 2.8172 | 2.8172 | 2.8172 | 2.534 | 3.2163 | 3.2163 | 3.2163 | 3.2163 | 3.2163
2020-07-08 14:00 | Winter | 1.2575 | 1.9335 | 2.9258 | 2.9258 | 2.9258 | 2.9258 | 0.94881 | 0.94881 | 0.94881 | 0.94881 | 0.94881 | 0.94881 | 2.6674 | 3.8476 | 4.6208 | 5.0278 | 5.8418 | 6.6557 | 0.84593 | 2.2979 | 2.8821 | 2.8821 | 2.8821 | 2.8821 | 2.5032 | 3.1773 | 3.1773 | 3.1773 | 3.1773 | 3.1773
2020-07-08 15:00 | Winter | 1.2384 | 1.9042 | 2.8814 | 2.8814 | 2.8814 | 2.8814 | 0.96882 | 0.96882 | 0.96882 | 0.96882 | 0.96882 | 0.96882 | 2.7055 | 3.9026 | 4.6869 | 5.0996 | 5.9252 | 6.7508 | 0.82688 | 2.2461 | 2.8172 | 2.8172 | 2.8172 | 2.8172 | 2.3054 | 2.9261 | 2.9261 | 2.9261 | 2.9261 | 2.9261
2020-07-08 16:00 | Winter | 1.2003 | 1.8456 | 2.7928 | 2.7928 | 2.7928 | 2.7928 | 1.0145 | 1.0145 | 1.0145 | 1.0145 | 1.0145 | 1.0145 | 2.6102 | 3.7651 | 4.5218 | 4.9201 | 5.7166 | 6.5131 | 0.86879 | 2.36 | 2.96 | 2.96 | 2.96 | 2.96 | 2.2291 | 2.8294 | 2.8294 | 2.8294 | 2.8294 | 2.8294
2020-07-08 17:00 | Winter | 1.1813 | 1.8163 | 2.7485 | 2.7485 | 2.7485 | 2.7485 | 0.96596 | 0.96596 | 0.96596 | 0.96596 | 0.96596 | 0.96596 | 2.7436 | 3.9575 | 4.7529 | 5.1715 | 6.0087 | 6.8459 | 0.84974 | 2.3082 | 2.8951 | 2.8951 | 2.8951 | 2.8951 | 2.1339 | 2.7085 | 2.7085 | 2.7085 | 2.7085 | 2.7085
2020-07-08 18:00 | Winter | 0.9943 | 1.5289 | 2.3135 | 2.3135 | 2.3135 | 2.3135 | 0.91738 | 0.91738 | 0.91738 | 0.91738 | 0.91738 | 0.91738 | 2.6293 | 3.7926 | 4.5548 | 4.956 | 5.7583 | 6.5606 | 0.91833 | 2.4946 | 3.1288 | 3.1288 | 3.1288 | 3.1288 | 1.7058 | 2.1652 | 2.1652 | 2.1652 | 2.1652 | 2.1652
2020-07-08 19:00 | Winter | 0.69483 | 1.0684 | 1.6167 | 1.6167 | 1.6167 | 1.6167 | 0.54649 | 0.54649 | 0.54649 | 0.54649 | 0.54649 | 0.54649 | 2.5479 | 3.6752 | 4.4138 | 4.8026 | 5.5801 | 6.3575 | 0.82688 | 2.2461 | 2.8172 | 2.8172 | 2.8172 | 2.8172 | 1.2005 | 1.5238 | 1.5238 | 1.5238 | 1.5238 | 1.5238
2020-07-08 20:00 | Winter | 0.64779 | 0.99605 | 1.5072 | 1.5072 | 1.5072 | 1.5072 | 0.53442 | 0.53442 | 0.53442 | 0.53442 | 0.53442 | 0.53442 | 2.4197 | 3.4903 | 4.1918 | 4.561 | 5.2993 | 6.0377 | 0.73543 | 1.9977 | 2.5056 | 2.5056 | 2.5056 | 2.5056 | 1.086 | 1.3784 | 1.3784 | 1.3784 | 1.3784 | 1.3784
2020-07-08 21:00 | Winter | 0.61053 | 0.93876 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 0.50298 | 0.50298 | 0.50298 | 0.50298 | 0.50298 | 0.50298 | 2.3816 | 3.4353 | 4.1258 | 4.4891 | 5.2159 | 5.9426 | 0.73162 | 1.9874 | 2.4926 | 2.4926 | 2.4926 | 2.4926 | 0.97168 | 1.2333 | 1.2333 | 1.2333 | 1.2333 | 1.2333
2020-07-08 22:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.4544 | 0.4544 | 0.4544 | 0.4544 | 0.4544 | 0.4544 | 2.1625 | 3.1193 | 3.7462 | 4.0761 | 4.736 | 5.3959 | 0.70494 | 1.9149 | 2.4018 | 2.4018 | 2.4018 | 2.4018 | 0.88649 | 1.1252 | 1.1252 | 1.1252 | 1.1252 | 1.1252
2020-07-08 23:00 | Winter | 0.62827 | 0.96603 | 1.4618 | 1.4618 | 1.4618 | 1.4618 | 0.39592 | 0.39592 | 0.39592 | 0.39592 | 0.39592 | 0.39592 | 1.9013 | 2.7426 | 3.2937 | 3.5838 | 4.164 | 4.7442 | 0.63635 | 1.7286 | 2.1681 | 2.1681 | 2.1681 | 2.1681 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-07-09 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.42296 | 0.42296 | 0.42296 | 0.42296 | 0.42296 | 0.42296 | 1.7379 | 2.5068 | 3.0106 | 3.2758 | 3.8061 | 4.3364 | 0.59825 | 1.6251 | 2.0382 | 2.0382 | 2.0382 | 2.0382 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-07-09 01:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.41423 | 0.41423 | 0.41423 | 0.41423 | 0.41423 | 0.41423 | 1.6957 | 2.446 | 2.9375 | 3.1963 | 3.7137 | 4.2311 | 0.54109 | 1.4698 | 1.8435 | 1.8435 | 1.8435 | 1.8435 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-07-09 02:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.42296 | 0.42296 | 0.42296 | 0.42296 | 0.42296 | 0.42296 | 1.6195 | 2.336 | 2.8055 | 3.0526 | 3.5468 | 4.041 | 0.5449 | 1.4802 | 1.8565 | 1.8565 | 1.8565 | 1.8565 | 0.99073 | 1.2575 | 1.2575 | 1.2575 | 1.2575 | 1.2575
2020-07-09 03:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.40582 | 0.40582 | 0.40582 | 0.40582 | 0.40582 | 0.40582 | 1.6195 | 2.336 | 2.8055 | 3.0526 | 3.5468 | 4.041 | 0.52966 | 1.4388 | 1.8046 | 1.8046 | 1.8046 | 1.8046 | 1.0288 | 1.3059 | 1.3059 | 1.3059 | 1.3059 | 1.3059
2020-07-09 04:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.5287 | 0.5287 | 0.5287 | 0.5287 | 0.5287 | 0.5287 | 1.723 | 2.4853 | 2.9848 | 3.2477 | 3.7734 | 4.2992 | 0.51061 | 1.387 | 1.7396 | 1.7396 | 1.7396 | 1.7396 | 1.1048 | 1.4023 | 1.4023 | 1.4023 | 1.4023 | 1.4023
2020-07-09 05:00 | Winter | 0.78115 | 1.2011 | 1.8175 | 1.8175 | 1.8175 | 1.8175 | 0.59729 | 0.59729 | 0.59729 | 0.59729 | 0.59729 | 0.59729 | 1.8474 | 2.6648 | 3.2004 | 3.4822 | 4.046 | 4.6097 | 0.77353 | 2.1012 | 2.6354 | 2.6354 | 2.6354 | 2.6354 | 1.4091 | 1.7886 | 1.7886 | 1.7886 | 1.7886 | 1.7886
2020-07-09 06:00 | Winter | 0.87596 | 1.3469 | 2.0381 | 2.0381 | 2.0381 | 2.0381 | 0.79735 | 0.79735 | 0.79735 | 0.79735 | 0.79735 | 0.79735 | 2.1339 | 3.0781 | 3.6967 | 4.0223 | 4.6734 | 5.3246 | 0.78496 | 2.1323 | 2.6744 | 2.6744 | 2.6744 | 2.6744 | 1.8313 | 2.3244 | 2.3244 | 2.3244 | 2.3244 | 2.3244
2020-07-09 07:00 | Winter | 1.1432 | 1.7577 | 2.6598 | 2.6598 | 2.6598 | 2.6598 | 0.99716 | 0.99716 | 0.99716 | 0.99716 | 0.99716 | 0.99716 | 2.4959 | 3.6002 | 4.3238 | 4.7046 | 5.4662 | 6.2279 | 0.89166 | 2.4221 | 3.0379 | 3.0379 | 3.0379 | 3.0379 | 2.3625 | 2.9987 | 2.9987 | 2.9987 | 2.9987 | 2.9987
2020-07-09 08:00 | Winter | 1.4099 | 2.1679 | 3.2804 | 3.2804 | 3.2804 | 3.2804 | 1.0231 | 1.0231 | 1.0231 | 1.0231 | 1.0231 | 1.0231 | 2.7369 | 3.9479 | 4.7413 | 5.1589 | 5.994 | 6.8292 | 0.96406 | 2.6188 | 3.2846 | 3.2846 | 3.2846 | 3.2846 | 2.6864 | 3.4098 | 3.4098 | 3.4098 | 3.4098 | 3.4098
2020-07-09 09:00 | Winter | 1.3718 | 2.1093 | 3.1918 | 3.1918 | 3.1918 | 3.1918 | 1.0574 | 1.0574 | 1.0574 | 1.0574 | 1.0574 | 1.0574 | 2.8769 | 4.1499 | 4.9839 | 5.4229 | 6.3008 | 7.1787 | 0.9069 | 2.4635 | 3.0898 | 3.0898 | 3.0898 | 3.0898 | 2.7245 | 3.4582 | 3.4582 | 3.4582 | 3.4582 | 3.4582
2020-07-09 10:00 | Winter | 1.2765 | 1.9628 | 2.9701 | 2.9701 | 2.9701 | 2.9701 | 1.026 | 1.026 | 1.026 | 1.026 | 1.026 | 1.026 | 2.8579 | 4.1224 | 4.9509 | 5.387 | 6.259 | 7.1311 | 0.86498 | 2.3496 | 2.947 | 2.947 | 2.947 | 2.947 | 2.6293 | 3.3373 | 3.3373 | 3.3373 | 3.3373 | 3.3373
2020-07-09 11:00 | Winter | 1.2361 | 1.9006 | 2.876 | 2.876 | 2.876 | 2.876 | 0.97453 | 0.97453 | 0.97453 | 0.97453 | 0.97453 | 0.97453 | 2.8388 | 4.0949 | 4.9179 | 5.351 | 6.2173 | 7.0836 | 0.86498 | 2.3496 | 2.947 | 2.947 | 2.947 | 2.947 | 2.6674 | 3.3856 | 3.3856 | 3.3856 | 3.3856 | 3.3856
2020-07-09 12:00 | Winter | 1.2575 | 1.9335 | 2.9258 | 2.9258 | 2.9258 | 2.9258 | 0.98597 | 0.98597 | 0.98597 | 0.98597 | 0.98597 | 0.98597 | 2.7626 | 3.985 | 4.7859 | 5.2074 | 6.0504 | 6.8934 | 0.84974 | 2.3082 | 2.8951 | 2.8951 | 2.8951 | 2.8951 | 2.6483 | 3.3614 | 3.3614 | 3.3614 | 3.3614 | 3.3614
2020-07-09 13:00 | Winter | 1.2575 | 1.9335 | 2.9258 | 2.9258 | 2.9258 | 2.9258 | 0.98311 | 0.98311 | 0.98311 | 0.98311 | 0.98311 | 0.98311 | 2.6864 | 3.8751 | 4.6539 | 5.0637 | 5.8835 | 6.7033 | 0.83946 | 2.2803 | 2.86 | 2.86 | 2.86 | 2.86 | 2.534 | 3.2163 | 3.2163 | 3.2163 | 3.2163 | 3.2163
2020-07-09 14:00 | Winter | 1.2956 | 1.9921 | 3.0144 | 3.0144 | 3.0144 | 3.0144 | 0.96882 | 0.96882 | 0.96882 | 0.96882 | 0.96882 | 0.96882 | 2.6293 | 3.7926 | 4.5548 | 4.956 | 5.7583 | 6.5606 | 0.79258 | 2.153 | 2.7003 | 2.7003 | 2.7003 | 2.7003 | 2.4006 | 3.0471 | 3.0471 | 3.0471 | 3.0471 | 3.0471
2020-07-09 15:00 | Winter | 1.2194 | 1.8749 | 2.8371 | 2.8371 | 2.8371 | 2.8371 | 0.92595 | 0.92595 | 0.92595 | 0.92595 | 0.92595 | 0.92595 | 2.6102 | 3.7651 | 4.5218 | 4.9201 | 5.7166 | 6.5131 | 0.86498 | 2.3496 | 2.947 | 2.947 | 2.947 | 2.947 | 2.2863 | 2.902 | 2.902 | 2.902 | 2.902 | 2.902
2020-07-09 16:00 | Winter | 1.1813 | 1.8163 | 2.7485 | 2.7485 | 2.7485 | 2.7485 | 1.0317 | 1.0317 | 1.0317 | 1.0317 | 1.0317 | 1.0317 | 2.5721 | 3.7102 | 4.4558 | 4.8483 | 5.6331 | 6.418 | 0.86117 | 2.3393 | 2.934 | 2.934 | 2.934 | 2.934 | 2.172 | 2.7569 | 2.7569 | 2.7569 | 2.7569 | 2.7569
2020-07-09 17:00 | Winter | 1.1622 | 1.787 | 2.7041 | 2.7041 | 2.7041 | 2.7041 | 0.94881 | 0.94881 | 0.94881 | 0.94881 | 0.94881 | 0.94881 | 2.7245 | 3.93 | 4.7199 | 5.1356 | 5.967 | 6.7984 | 0.83831 | 2.2772 | 2.8561 | 2.8561 | 2.8561 | 2.8561 | 2.1339 | 2.7085 | 2.7085 | 2.7085 | 2.7085 | 2.7085
2020-07-09 18:00 | Winter | 0.95329 | 1.4658 | 2.218 | 2.218 | 2.218 | 2.218 | 0.81449 | 0.81449 | 0.81449 | 0.81449 | 0.81449 | 0.81449 | 2.6293 | 3.7926 | 4.5548 | 4.956 | 5.7583 | 6.5606 | 0.82307 | 2.2358 | 2.8042 | 2.8042 | 2.8042 | 2.8042 | 1.6388 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08
2020-07-09 19:00 | Winter | 0.70501 | 1.084 | 1.6404 | 1.6404 | 1.6404 | 1.6404 | 0.70018 | 0.70018 | 0.70018 | 0.70018 | 0.70018 | 0.70018 | 2.4387 | 3.5178 | 4.2248 | 4.5969 | 5.3411 | 6.0852 | 0.80783 | 2.1944 | 2.7523 | 2.7523 | 2.7523 | 2.7523 | 1.1718 | 1.4874 | 1.4874 | 1.4874 | 1.4874 | 1.4874
2020-07-09 20:00 | Winter | 0.64779 | 0.99605 | 1.5072 | 1.5072 | 1.5072 | 1.5072 | 0.61158 | 0.61158 | 0.61158 | 0.61158 | 0.61158 | 0.61158 | 2.3435 | 3.3804 | 4.0597 | 4.4173 | 5.1324 | 5.8475 | 0.78496 | 2.1323 | 2.6744 | 2.6744 | 2.6744 | 2.6744 | 1.0861 | 1.3786 | 1.3786 | 1.3786 | 1.3786 | 1.3786
2020-07-09 21:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.64016 | 0.64016 | 0.64016 | 0.64016 | 0.64016 | 0.64016 | 2.2291 | 3.2155 | 3.8617 | 4.2018 | 4.8821 | 5.5623 | 0.70875 | 1.9253 | 2.4147 | 2.4147 | 2.4147 | 2.4147 | 1.0288 | 1.3059 | 1.3059 | 1.3059 | 1.3059 | 1.3059
2020-07-09 22:00 | Winter | 0.64779 | 0.99605 | 1.5072 | 1.5072 | 1.5072 | 1.5072 | 0.50584 | 0.50584 | 0.50584 | 0.50584 | 0.50584 | 0.50584 | 2.0772 | 2.9963 | 3.5984 | 3.9154 | 4.5492 | 5.1831 | 0.71256 | 1.9356 | 2.4277 | 2.4277 | 2.4277 | 2.4277 | 1.0012 | 1.2708 | 1.2708 | 1.2708 | 1.2708 | 1.2708
2020-07-09 23:00 | Winter | 0.63 | 0.9687 | 1.4658 | 1.4658 | 1.4658 | 1.4658 | 0.41153 | 0.41153 | 0.41153 | 0.41153 | 0.41153 | 0.41153 | 1.8672 | 2.6933 | 3.2346 | 3.5195 | 4.0892 | 4.659 | 0.63635 | 1.7286 | 2.1681 | 2.1681 | 2.1681 | 2.1681 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-07-10 | Winter | 0.59049 | 0.90794 | 1.3739 | 1.3739 | 1.3739 | 1.3739 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 1.7338 | 2.5009 | 3.0036 | 3.2681 | 3.7972 | 4.3262 | 0.56776 | 1.5423 | 1.9344 | 1.9344 | 1.9344 | 1.9344 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-07-10 01:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.41439 | 0.41439 | 0.41439 | 0.41439 | 0.41439 | 0.41439 | 1.6197 | 2.3364 | 2.806 | 3.0531 | 3.5474 | 4.0416 | 0.55633 | 1.5112 | 1.8954 | 1.8954 | 1.8954 | 1.8954 | 0.85817 | 1.0893 | 1.0893 | 1.0893 | 1.0893 | 1.0893
2020-07-10 02:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 1.6195 | 2.336 | 2.8055 | 3.0526 | 3.5468 | 4.041 | 0.52204 | 1.4181 | 1.7786 | 1.7786 | 1.7786 | 1.7786 | 1.0477 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 1.3299
2020-07-10 03:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.4001 | 0.4001 | 0.4001 | 0.4001 | 0.4001 | 0.4001 | 1.6004 | 2.3086 | 2.7725 | 3.0167 | 3.5051 | 3.9934 | 0.52204 | 1.4181 | 1.7786 | 1.7786 | 1.7786 | 1.7786 | 1.0479 | 1.3301 | 1.3301 | 1.3301 | 1.3301 | 1.3301
2020-07-10 04:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 1.6207 | 2.3378 | 2.8076 | 3.0549 | 3.5495 | 4.044 | 0.53347 | 1.4491 | 1.8175 | 1.8175 | 1.8175 | 1.8175 | 1.105 | 1.4026 | 1.4026 | 1.4026 | 1.4026 | 1.4026
2020-07-10 05:00 | Winter | 0.81926 | 1.2597 | 1.9062 | 1.9062 | 1.9062 | 1.9062 | 0.62587 | 0.62587 | 0.62587 | 0.62587 | 0.62587 | 0.62587 | 1.7909 | 2.5834 | 3.1026 | 3.3758 | 3.9223 | 4.4688 | 0.65541 | 1.7803 | 2.233 | 2.233 | 2.233 | 2.233 | 1.507 | 1.9127 | 1.9127 | 1.9127 | 1.9127 | 1.9127
2020-07-10 06:00 | Winter | 0.87642 | 1.3476 | 2.0392 | 2.0392 | 2.0392 | 2.0392 | 0.80306 | 0.80306 | 0.80306 | 0.80306 | 0.80306 | 0.80306 | 2.0808 | 3.0015 | 3.6047 | 3.9221 | 4.5571 | 5.192 | 0.73543 | 1.9977 | 2.5056 | 2.5056 | 2.5056 | 2.5056 | 1.9448 | 2.4685 | 2.4685 | 2.4685 | 2.4685 | 2.4685
2020-07-10 07:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 0.88305 | 0.88305 | 0.88305 | 0.88305 | 0.88305 | 0.88305 | 2.4378 | 3.5164 | 4.2231 | 4.5951 | 5.339 | 6.0829 | 0.87642 | 2.3807 | 2.986 | 2.986 | 2.986 | 2.986 | 2.2863 | 2.902 | 2.902 | 2.902 | 2.902 | 2.902
2020-07-10 08:00 | Winter | 1.2765 | 1.9628 | 2.9701 | 2.9701 | 2.9701 | 2.9701 | 0.98311 | 0.98311 | 0.98311 | 0.98311 | 0.98311 | 0.98311 | 2.5911 | 3.7377 | 4.4888 | 4.8842 | 5.6749 | 6.4656 | 0.95263 | 2.5877 | 3.2456 | 3.2456 | 3.2456 | 3.2456 | 2.553 | 3.2405 | 3.2405 | 3.2405 | 3.2405 | 3.2405
2020-07-10 09:00 | Winter | 1.2765 | 1.9628 | 2.9701 | 2.9701 | 2.9701 | 2.9701 | 0.98597 | 0.98597 | 0.98597 | 0.98597 | 0.98597 | 0.98597 | 2.6674 | 3.8476 | 4.6208 | 5.0278 | 5.8418 | 6.6557 | 0.94882 | 2.5774 | 3.2326 | 3.2326 | 3.2326 | 3.2326 | 2.6102 | 3.3131 | 3.3131 | 3.3131 | 3.3131 | 3.3131
2020-07-10 10:00 | Winter | 1.2384 | 1.9042 | 2.8814 | 2.8814 | 2.8814 | 2.8814 | 0.93452 | 0.93452 | 0.93452 | 0.93452 | 0.93452 | 0.93452 | 2.5721 | 3.7102 | 4.4558 | 4.8483 | 5.6331 | 6.418 | 0.83831 | 2.2772 | 2.8561 | 2.8561 | 2.8561 | 2.8561 | 2.5721 | 3.2647 | 3.2647 | 3.2647 | 3.2647 | 3.2647
2020-07-10 11:00 | Winter | 1.2384 | 1.9042 | 2.8814 | 2.8814 | 2.8814 | 2.8814 | 0.92595 | 0.92595 | 0.92595 | 0.92595 | 0.92595 | 0.92595 | 2.553 | 3.6827 | 4.4228 | 4.8123 | 5.5914 | 6.3705 | 0.82688 | 2.2461 | 2.8172 | 2.8172 | 2.8172 | 2.8172 | 2.5099 | 3.1857 | 3.1857 | 3.1857 | 3.1857 | 3.1857
2020-07-10 12:00 | Winter | 1.2003 | 1.8456 | 2.7928 | 2.7928 | 2.7928 | 2.7928 | 0.93167 | 0.93167 | 0.93167 | 0.93167 | 0.93167 | 0.93167 | 2.553 | 3.6827 | 4.4228 | 4.8123 | 5.5914 | 6.3705 | 0.83831 | 2.2772 | 2.8561 | 2.8561 | 2.8561 | 2.8561 | 2.4578 | 3.1196 | 3.1196 | 3.1196 | 3.1196 | 3.1196
2020-07-10 13:00 | Winter | 1.2384 | 1.9042 | 2.8814 | 2.8814 | 2.8814 | 2.8814 | 0.91452 | 0.91452 | 0.91452 | 0.91452 | 0.91452 | 0.91452 | 2.6483 | 3.8201 | 4.5878 | 4.9919 | 5.8 | 6.6082 | 0.82688 | 2.2461 | 2.8172 | 2.8172 | 2.8172 | 2.8172 | 2.3625 | 2.9987 | 2.9987 | 2.9987 | 2.9987 | 2.9987
2020-07-10 14:00 | Winter | 1.2003 | 1.8456 | 2.7928 | 2.7928 | 2.7928 | 2.7928 | 0.96596 | 0.96596 | 0.96596 | 0.96596 | 0.96596 | 0.96596 | 2.6365 | 3.8031 | 4.5674 | 4.9697 | 5.7743 | 6.5788 | 0.81926 | 2.2254 | 2.7912 | 2.7912 | 2.7912 | 2.7912 | 2.3244 | 2.9503 | 2.9503 | 2.9503 | 2.9503 | 2.9503
2020-07-10 15:00 | Winter | 1.1622 | 1.787 | 2.7041 | 2.7041 | 2.7041 | 2.7041 | 0.91738 | 0.91738 | 0.91738 | 0.91738 | 0.91738 | 0.91738 | 2.5721 | 3.7102 | 4.4558 | 4.8483 | 5.6331 | 6.418 | 0.80783 | 2.1944 | 2.7523 | 2.7523 | 2.7523 | 2.7523 | 2.191 | 2.781 | 2.781 | 2.781 | 2.781 | 2.781
2020-07-10 16:00 | Winter | 1.1241 | 1.7284 | 2.6155 | 2.6155 | 2.6155 | 2.6155 | 0.95739 | 0.95739 | 0.95739 | 0.95739 | 0.95739 | 0.95739 | 2.5721 | 3.7102 | 4.4558 | 4.8483 | 5.6331 | 6.418 | 0.81926 | 2.2254 | 2.7912 | 2.7912 | 2.7912 | 2.7912 | 2.1339 | 2.7085 | 2.7085 | 2.7085 | 2.7085 | 2.7085
2020-07-10 17:00 | Winter | 1.105 | 1.6991 | 2.5711 | 2.5711 | 2.5711 | 2.5711 | 0.91738 | 0.91738 | 0.91738 | 0.91738 | 0.91738 | 0.91738 | 2.5721 | 3.7102 | 4.4558 | 4.8483 | 5.6331 | 6.418 | 0.84974 | 2.3082 | 2.8951 | 2.8951 | 2.8951 | 2.8951 | 2.0005 | 2.5392 | 2.5392 | 2.5392 | 2.5392 | 2.5392
2020-07-10 18:00 | Winter | 0.89131 | 1.3705 | 2.0738 | 2.0738 | 2.0738 | 2.0738 | 0.77448 | 0.77448 | 0.77448 | 0.77448 | 0.77448 | 0.77448 | 2.4387 | 3.5178 | 4.2248 | 4.5969 | 5.3411 | 6.0852 | 0.81926 | 2.2254 | 2.7912 | 2.7912 | 2.7912 | 2.7912 | 1.6202 | 2.0564 | 2.0564 | 2.0564 | 2.0564 | 2.0564
2020-07-10 19:00 | Winter | 0.66684 | 1.0253 | 1.5515 | 1.5515 | 1.5515 | 1.5515 | 0.72906 | 0.72906 | 0.72906 | 0.72906 | 0.72906 | 0.72906 | 2.2595 | 3.2593 | 3.9143 | 4.259 | 4.9485 | 5.638 | 0.75448 | 2.0495 | 2.5705 | 2.5705 | 2.5705 | 2.5705 | 1.1843 | 1.5031 | 1.5031 | 1.5031 | 1.5031 | 1.5031
2020-07-10 20:00 | Winter | 0.66684 | 1.0253 | 1.5515 | 1.5515 | 1.5515 | 1.5515 | 0.5287 | 0.5287 | 0.5287 | 0.5287 | 0.5287 | 0.5287 | 2.2482 | 3.243 | 3.8947 | 4.2377 | 4.9238 | 5.6098 | 0.80021 | 2.1737 | 2.7263 | 2.7263 | 2.7263 | 2.7263 | 1.0479 | 1.3301 | 1.3301 | 1.3301 | 1.3301 | 1.3301
2020-07-10 21:00 | Winter | 0.60848 | 0.93561 | 1.4158 | 1.4158 | 1.4158 | 1.4158 | 0.51442 | 0.51442 | 0.51442 | 0.51442 | 0.51442 | 0.51442 | 2.0677 | 2.9826 | 3.582 | 3.8974 | 4.5284 | 5.1594 | 0.7964 | 2.1633 | 2.7133 | 2.7133 | 2.7133 | 2.7133 | 0.97168 | 1.2333 | 1.2333 | 1.2333 | 1.2333 | 1.2333
2020-07-10 22:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.49441 | 0.49441 | 0.49441 | 0.49441 | 0.49441 | 0.49441 | 1.9551 | 2.8202 | 3.387 | 3.6853 | 4.2819 | 4.8785 | 0.75067 | 2.0391 | 2.5575 | 2.5575 | 2.5575 | 2.5575 | 0.8967 | 1.1382 | 1.1382 | 1.1382 | 1.1382 | 1.1382
2020-07-10 23:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 1.9815 | 2.8582 | 3.4326 | 3.735 | 4.3396 | 4.9443 | 0.64779 | 1.7596 | 2.207 | 2.207 | 2.207 | 2.207 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-07-11 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.38867 | 0.38867 | 0.38867 | 0.38867 | 0.38867 | 0.38867 | 1.7909 | 2.5834 | 3.1026 | 3.3758 | 3.9223 | 4.4688 | 0.56776 | 1.5423 | 1.9344 | 1.9344 | 1.9344 | 1.9344 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-07-11 01:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 1.6766 | 2.4185 | 2.9045 | 3.1603 | 3.672 | 4.1836 | 0.52204 | 1.4181 | 1.7786 | 1.7786 | 1.7786 | 1.7786 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-07-11 02:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.43439 | 0.43439 | 0.43439 | 0.43439 | 0.43439 | 0.43439 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.52204 | 1.4181 | 1.7786 | 1.7786 | 1.7786 | 1.7786 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-07-11 03:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.41439 | 0.41439 | 0.41439 | 0.41439 | 0.41439 | 0.41439 | 1.6957 | 2.446 | 2.9375 | 3.1963 | 3.7137 | 4.2311 | 0.51823 | 1.4077 | 1.7656 | 1.7656 | 1.7656 | 1.7656 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-07-11 04:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.42582 | 0.42582 | 0.42582 | 0.42582 | 0.42582 | 0.42582 | 1.6413 | 2.3675 | 2.8433 | 3.0937 | 3.5946 | 4.0954 | 0.49918 | 1.356 | 1.7007 | 1.7007 | 1.7007 | 1.7007 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-07-11 05:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 1.6766 | 2.4185 | 2.9045 | 3.1603 | 3.672 | 4.1836 | 0.54871 | 1.4905 | 1.8695 | 1.8695 | 1.8695 | 1.8695 | 0.86842 | 1.1023 | 1.1023 | 1.1023 | 1.1023 | 1.1023
2020-07-11 06:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.47581 | 0.47581 | 0.47581 | 0.47581 | 0.47581 | 0.47581 | 1.81 | 2.6109 | 3.1356 | 3.4117 | 3.9641 | 4.5164 | 0.6173 | 1.6768 | 2.1032 | 2.1032 | 2.1032 | 2.1032 | 0.95263 | 1.2092 | 1.2092 | 1.2092 | 1.2092 | 1.2092
2020-07-11 07:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.59158 | 0.59158 | 0.59158 | 0.59158 | 0.59158 | 0.59158 | 1.984 | 2.8618 | 3.437 | 3.7397 | 4.3451 | 4.9505 | 0.61349 | 1.6665 | 2.0902 | 2.0902 | 2.0902 | 2.0902 | 1.0288 | 1.3059 | 1.3059 | 1.3059 | 1.3059 | 1.3059
2020-07-11 08:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.65445 | 0.65445 | 0.65445 | 0.65445 | 0.65445 | 0.65445 | 2.1529 | 3.1056 | 3.7297 | 4.0582 | 4.7151 | 5.3721 | 0.65922 | 1.7907 | 2.246 | 2.246 | 2.246 | 2.246 | 1.0288 | 1.3059 | 1.3059 | 1.3059 | 1.3059 | 1.3059
2020-07-11 09:00 | Winter | 0.60981 | 0.93765 | 1.4188 | 1.4188 | 1.4188 | 1.4188 | 0.77734 | 0.77734 | 0.77734 | 0.77734 | 0.77734 | 0.77734 | 2.172 | 3.133 | 3.7627 | 4.0941 | 4.7569 | 5.4197 | 0.69351 | 1.8839 | 2.3628 | 2.3628 | 2.3628 | 2.3628 | 1.1241 | 1.4268 | 1.4268 | 1.4268 | 1.4268 | 1.4268
2020-07-11 10:00 | Winter | 0.64779 | 0.99605 | 1.5072 | 1.5072 | 1.5072 | 1.5072 | 0.72876 | 0.72876 | 0.72876 | 0.72876 | 0.72876 | 0.72876 | 2.191 | 3.1605 | 3.7957 | 4.13 | 4.7986 | 5.4672 | 0.70875 | 1.9253 | 2.4147 | 2.4147 | 2.4147 | 2.4147 | 1.2003 | 1.5235 | 1.5235 | 1.5235 | 1.5235 | 1.5235
2020-07-11 11:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.64874 | 0.64874 | 0.64874 | 0.64874 | 0.64874 | 0.64874 | 2.2673 | 3.2705 | 3.9277 | 4.2736 | 4.9655 | 5.6574 | 0.72781 | 1.977 | 2.4796 | 2.4796 | 2.4796 | 2.4796 | 1.1813 | 1.4993 | 1.4993 | 1.4993 | 1.4993 | 1.4993
2020-07-11 12:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.66303 | 0.66303 | 0.66303 | 0.66303 | 0.66303 | 0.66303 | 2.4387 | 3.5178 | 4.2248 | 4.5969 | 5.3411 | 6.0852 | 0.71256 | 1.9356 | 2.4277 | 2.4277 | 2.4277 | 2.4277 | 1.1241 | 1.4268 | 1.4268 | 1.4268 | 1.4268 | 1.4268
2020-07-11 13:00 | Winter | 0.64779 | 0.99605 | 1.5072 | 1.5072 | 1.5072 | 1.5072 | 0.63445 | 0.63445 | 0.63445 | 0.63445 | 0.63445 | 0.63445 | 2.3625 | 3.4079 | 4.0927 | 4.4532 | 5.1741 | 5.8951 | 0.70113 | 1.9046 | 2.3888 | 2.3888 | 2.3888 | 2.3888 | 1.105 | 1.4026 | 1.4026 | 1.4026 | 1.4026 | 1.4026
2020-07-11 14:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.65445 | 0.65445 | 0.65445 | 0.65445 | 0.65445 | 0.65445 | 2.3625 | 3.4079 | 4.0927 | 4.4532 | 5.1741 | 5.8951 | 0.73162 | 1.9874 | 2.4926 | 2.4926 | 2.4926 | 2.4926 | 1.0669 | 1.3542 | 1.3542 | 1.3542 | 1.3542 | 1.3542
2020-07-11 15:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.65445 | 0.65445 | 0.65445 | 0.65445 | 0.65445 | 0.65445 | 2.4141 | 3.4823 | 4.1821 | 4.5505 | 5.2872 | 6.0238 | 0.69549 | 1.8892 | 2.3696 | 2.3696 | 2.3696 | 2.3696 | 1.0479 | 1.3301 | 1.3301 | 1.3301 | 1.3301 | 1.3301
2020-07-11 16:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.62301 | 0.62301 | 0.62301 | 0.62301 | 0.62301 | 0.62301 | 2.4197 | 3.4903 | 4.1918 | 4.561 | 5.2993 | 6.0377 | 0.73543 | 1.9977 | 2.5056 | 2.5056 | 2.5056 | 2.5056 | 1.0288 | 1.3059 | 1.3059 | 1.3059 | 1.3059 | 1.3059
2020-07-11 17:00 | Winter | 0.60881 | 0.93612 | 1.4165 | 1.4165 | 1.4165 | 1.4165 | 0.58872 | 0.58872 | 0.58872 | 0.58872 | 0.58872 | 0.58872 | 2.4006 | 3.4628 | 4.1588 | 4.525 | 5.2576 | 5.9902 | 0.83069 | 2.2565 | 2.8302 | 2.8302 | 2.8302 | 2.8302 | 1.0288 | 1.3059 | 1.3059 | 1.3059 | 1.3059 | 1.3059
2020-07-11 18:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.583 | 0.583 | 0.583 | 0.583 | 0.583 | 0.583 | 2.3816 | 3.4353 | 4.1258 | 4.4891 | 5.2159 | 5.9426 | 0.87261 | 2.3704 | 2.973 | 2.973 | 2.973 | 2.973 | 0.97168 | 1.2333 | 1.2333 | 1.2333 | 1.2333 | 1.2333
2020-07-11 19:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.54585 | 0.54585 | 0.54585 | 0.54585 | 0.54585 | 0.54585 | 2.3244 | 3.3529 | 4.0267 | 4.3814 | 5.0907 | 5.8 | 0.84974 | 2.3082 | 2.8951 | 2.8951 | 2.8951 | 2.8951 | 0.99073 | 1.2575 | 1.2575 | 1.2575 | 1.2575 | 1.2575
2020-07-11 20:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.54585 | 0.54585 | 0.54585 | 0.54585 | 0.54585 | 0.54585 | 2.2482 | 3.243 | 3.8947 | 4.2377 | 4.9238 | 5.6098 | 0.81164 | 2.2047 | 2.7653 | 2.7653 | 2.7653 | 2.7653 | 0.97168 | 1.2333 | 1.2333 | 1.2333 | 1.2333 | 1.2333
2020-07-11 21:00 | Winter | 0.56296 | 0.86561 | 1.3098 | 1.3098 | 1.3098 | 1.3098 | 0.49441 | 0.49441 | 0.49441 | 0.49441 | 0.49441 | 0.49441 | 2.1725 | 3.1337 | 3.7635 | 4.095 | 4.758 | 5.4209 | 0.83069 | 2.2565 | 2.8302 | 2.8302 | 2.8302 | 2.8302 | 0.95263 | 1.2092 | 1.2092 | 1.2092 | 1.2092 | 1.2092
2020-07-11 22:00 | Winter | 0.60935 | 0.93695 | 1.4178 | 1.4178 | 1.4178 | 1.4178 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 2.0386 | 2.9407 | 3.5316 | 3.8427 | 4.4648 | 5.0869 | 0.75829 | 2.0598 | 2.5835 | 2.5835 | 2.5835 | 2.5835 | 0.9323 | 1.1833 | 1.1833 | 1.1833 | 1.1833 | 1.1833
2020-07-11 23:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 1.9815 | 2.8582 | 3.4326 | 3.735 | 4.3396 | 4.9443 | 0.65541 | 1.7803 | 2.233 | 2.233 | 2.233 | 2.233 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-07-12 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.43246 | 0.43246 | 0.43246 | 0.43246 | 0.43246 | 0.43246 | 1.7909 | 2.5834 | 3.1026 | 3.3758 | 3.9223 | 4.4688 | 0.56014 | 1.5216 | 1.9084 | 1.9084 | 1.9084 | 1.9084 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-07-12 01:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.43439 | 0.43439 | 0.43439 | 0.43439 | 0.43439 | 0.43439 | 1.7528 | 2.5284 | 3.0366 | 3.304 | 3.8389 | 4.3738 | 0.54871 | 1.4905 | 1.8695 | 1.8695 | 1.8695 | 1.8695 | 0.91452 | 1.1608 | 1.1608 | 1.1608 | 1.1608 | 1.1608
2020-07-12 02:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.39438 | 0.39438 | 0.39438 | 0.39438 | 0.39438 | 0.39438 | 1.6195 | 2.336 | 2.8055 | 3.0526 | 3.5468 | 4.041 | 0.53347 | 1.4491 | 1.8175 | 1.8175 | 1.8175 | 1.8175 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-07-12 03:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.46869 | 0.46869 | 0.46869 | 0.46869 | 0.46869 | 0.46869 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.51061 | 1.387 | 1.7396 | 1.7396 | 1.7396 | 1.7396 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-07-12 04:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 1.6004 | 2.3086 | 2.7725 | 3.0167 | 3.5051 | 3.9934 | 0.56395 | 1.5319 | 1.9214 | 1.9214 | 1.9214 | 1.9214 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-07-12 05:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.50298 | 0.50298 | 0.50298 | 0.50298 | 0.50298 | 0.50298 | 1.6751 | 2.4162 | 2.9018 | 3.1574 | 3.6685 | 4.1797 | 0.56014 | 1.5216 | 1.9084 | 1.9084 | 1.9084 | 1.9084 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-07-12 06:00 | Winter | 0.6033 | 0.92765 | 1.4037 | 1.4037 | 1.4037 | 1.4037 | 0.46869 | 0.46869 | 0.46869 | 0.46869 | 0.46869 | 0.46869 | 1.829 | 2.6383 | 3.1686 | 3.4477 | 4.0058 | 4.5639 | 0.5792 | 1.5733 | 1.9733 | 1.9733 | 1.9733 | 1.9733 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-07-12 07:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.57443 | 0.57443 | 0.57443 | 0.57443 | 0.57443 | 0.57443 | 1.8687 | 2.6956 | 3.2373 | 3.5224 | 4.0927 | 4.6629 | 0.63635 | 1.7286 | 2.1681 | 2.1681 | 2.1681 | 2.1681 | 0.91452 | 1.1608 | 1.1608 | 1.1608 | 1.1608 | 1.1608
2020-07-12 08:00 | Winter | 0.59129 | 0.90918 | 1.3758 | 1.3758 | 1.3758 | 1.3758 | 0.59158 | 0.59158 | 0.59158 | 0.59158 | 0.59158 | 0.59158 | 2.1148 | 3.0506 | 3.6637 | 3.9863 | 4.6317 | 5.277 | 0.69351 | 1.8839 | 2.3628 | 2.3628 | 2.3628 | 2.3628 | 0.89634 | 1.1377 | 1.1377 | 1.1377 | 1.1377 | 1.1377
2020-07-12 09:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.58586 | 0.58586 | 0.58586 | 0.58586 | 0.58586 | 0.58586 | 2.1652 | 3.1232 | 3.7508 | 4.0812 | 4.7419 | 5.4026 | 0.72018 | 1.9563 | 2.4537 | 2.4537 | 2.4537 | 2.4537 | 0.97168 | 1.2333 | 1.2333 | 1.2333 | 1.2333 | 1.2333
2020-07-12 10:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.52585 | 0.52585 | 0.52585 | 0.52585 | 0.52585 | 0.52585 | 2.2291 | 3.2155 | 3.8617 | 4.2018 | 4.8821 | 5.5623 | 0.74686 | 2.0288 | 2.5446 | 2.5446 | 2.5446 | 2.5446 | 0.97168 | 1.2333 | 1.2333 | 1.2333 | 1.2333 | 1.2333
2020-07-12 11:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.53442 | 0.53442 | 0.53442 | 0.53442 | 0.53442 | 0.53442 | 2.3244 | 3.3529 | 4.0267 | 4.3814 | 5.0907 | 5.8 | 0.72554 | 1.9709 | 2.4719 | 2.4719 | 2.4719 | 2.4719 | 1.086 | 1.3784 | 1.3784 | 1.3784 | 1.3784 | 1.3784
2020-07-12 12:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.5287 | 0.5287 | 0.5287 | 0.5287 | 0.5287 | 0.5287 | 2.2863 | 3.2979 | 3.9607 | 4.3096 | 5.0072 | 5.7049 | 0.65922 | 1.7907 | 2.246 | 2.246 | 2.246 | 2.246 | 1.0479 | 1.3301 | 1.3301 | 1.3301 | 1.3301 | 1.3301
2020-07-12 13:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.51156 | 0.51156 | 0.51156 | 0.51156 | 0.51156 | 0.51156 | 2.3054 | 3.3254 | 3.9937 | 4.3455 | 5.049 | 5.7525 | 0.62873 | 1.7079 | 2.1421 | 2.1421 | 2.1421 | 2.1421 | 1.0292 | 1.3064 | 1.3064 | 1.3064 | 1.3064 | 1.3064
2020-07-12 14:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.50584 | 0.50584 | 0.50584 | 0.50584 | 0.50584 | 0.50584 | 2.2291 | 3.2155 | 3.8617 | 4.2018 | 4.8821 | 5.5623 | 0.65922 | 1.7907 | 2.246 | 2.246 | 2.246 | 2.246 | 0.95263 | 1.2092 | 1.2092 | 1.2092 | 1.2092 | 1.2092
2020-07-12 15:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.52299 | 0.52299 | 0.52299 | 0.52299 | 0.52299 | 0.52299 | 2.2291 | 3.2155 | 3.8617 | 4.2018 | 4.8821 | 5.5623 | 0.60318 | 1.6385 | 2.0551 | 2.0551 | 2.0551 | 2.0551 | 0.95263 | 1.2092 | 1.2092 | 1.2092 | 1.2092 | 1.2092
2020-07-12 16:00 | Winter | 0.62792 | 0.96551 | 1.461 | 1.461 | 1.461 | 1.461 | 0.56586 | 0.56586 | 0.56586 | 0.56586 | 0.56586 | 0.56586 | 2.191 | 3.1605 | 3.7957 | 4.13 | 4.7986 | 5.4672 | 0.67446 | 1.8321 | 2.2979 | 2.2979 | 2.2979 | 2.2979 | 0.97168 | 1.2333 | 1.2333 | 1.2333 | 1.2333 | 1.2333
2020-07-12 17:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.58586 | 0.58586 | 0.58586 | 0.58586 | 0.58586 | 0.58586 | 2.3625 | 3.4079 | 4.0927 | 4.4532 | 5.1741 | 5.8951 | 0.80783 | 2.1944 | 2.7523 | 2.7523 | 2.7523 | 2.7523 | 0.93358 | 1.185 | 1.185 | 1.185 | 1.185 | 1.185
2020-07-12 18:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.56872 | 0.56872 | 0.56872 | 0.56872 | 0.56872 | 0.56872 | 2.4006 | 3.4628 | 4.1588 | 4.525 | 5.2576 | 5.9902 | 0.77353 | 2.1012 | 2.6354 | 2.6354 | 2.6354 | 2.6354 | 0.93358 | 1.185 | 1.185 | 1.185 | 1.185 | 1.185
2020-07-12 19:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 2.2863 | 3.2979 | 3.9607 | 4.3096 | 5.0072 | 5.7049 | 0.73543 | 1.9977 | 2.5056 | 2.5056 | 2.5056 | 2.5056 | 0.91452 | 1.1608 | 1.1608 | 1.1608 | 1.1608 | 1.1608
2020-07-12 20:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.49155 | 0.49155 | 0.49155 | 0.49155 | 0.49155 | 0.49155 | 2.1936 | 3.1642 | 3.8001 | 4.1348 | 4.8041 | 5.4735 | 0.73924 | 2.0081 | 2.5186 | 2.5186 | 2.5186 | 2.5186 | 0.91452 | 1.1608 | 1.1608 | 1.1608 | 1.1608 | 1.1608
2020-07-12 21:00 | Winter | 0.56793 | 0.87326 | 1.3214 | 1.3214 | 1.3214 | 1.3214 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 2.0577 | 2.9681 | 3.5647 | 3.8786 | 4.5065 | 5.1344 | 0.76591 | 2.0805 | 2.6095 | 2.6095 | 2.6095 | 2.6095 | 0.95263 | 1.2092 | 1.2092 | 1.2092 | 1.2092 | 1.2092
2020-07-12 22:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 1.9302 | 2.7842 | 3.3438 | 3.6383 | 4.2272 | 4.8162 | 0.66303 | 1.8011 | 2.2589 | 2.2589 | 2.2589 | 2.2589 | 0.93358 | 1.185 | 1.185 | 1.185 | 1.185 | 1.185
2020-07-12 23:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.41147 | 0.41147 | 0.41147 | 0.41147 | 0.41147 | 0.41147 | 1.7528 | 2.5284 | 3.0366 | 3.304 | 3.8389 | 4.3738 | 0.58682 | 1.594 | 1.9993 | 1.9993 | 1.9993 | 1.9993 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-07-13 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.53728 | 1.4595 | 1.8305 | 1.8305 | 1.8305 | 1.8305 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-07-13 01:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.40582 | 0.40582 | 0.40582 | 0.40582 | 0.40582 | 0.40582 | 1.6195 | 2.336 | 2.8055 | 3.0526 | 3.5468 | 4.041 | 0.53728 | 1.4595 | 1.8305 | 1.8305 | 1.8305 | 1.8305 | 0.93358 | 1.185 | 1.185 | 1.185 | 1.185 | 1.185
2020-07-13 02:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 1.5811 | 2.2807 | 2.739 | 2.9803 | 3.4627 | 3.9452 | 0.51442 | 1.3974 | 1.7526 | 1.7526 | 1.7526 | 1.7526 | 1.105 | 1.4026 | 1.4026 | 1.4026 | 1.4026 | 1.4026
2020-07-13 03:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.43439 | 0.43439 | 0.43439 | 0.43439 | 0.43439 | 0.43439 | 1.5814 | 2.2811 | 2.7395 | 2.9808 | 3.4633 | 3.9459 | 0.51823 | 1.4077 | 1.7656 | 1.7656 | 1.7656 | 1.7656 | 1.105 | 1.4026 | 1.4026 | 1.4026 | 1.4026 | 1.4026
2020-07-13 04:00 | Winter | 0.70494 | 1.0839 | 1.6402 | 1.6402 | 1.6402 | 1.6402 | 0.50584 | 0.50584 | 0.50584 | 0.50584 | 0.50584 | 0.50584 | 1.6957 | 2.446 | 2.9375 | 3.1963 | 3.7137 | 4.2311 | 0.52204 | 1.4181 | 1.7786 | 1.7786 | 1.7786 | 1.7786 | 1.0906 | 1.3843 | 1.3843 | 1.3843 | 1.3843 | 1.3843
2020-07-13 05:00 | Winter | 0.85737 | 1.3183 | 1.9948 | 1.9948 | 1.9948 | 1.9948 | 0.66303 | 0.66303 | 0.66303 | 0.66303 | 0.66303 | 0.66303 | 1.9153 | 2.7628 | 3.3181 | 3.6103 | 4.1948 | 4.7792 | 0.75448 | 2.0495 | 2.5705 | 2.5705 | 2.5705 | 2.5705 | 1.5457 | 1.9619 | 1.9619 | 1.9619 | 1.9619 | 1.9619
2020-07-13 06:00 | Winter | 0.98356 | 1.5123 | 2.2885 | 2.2885 | 2.2885 | 2.2885 | 0.7802 | 0.7802 | 0.7802 | 0.7802 | 0.7802 | 0.7802 | 2.1591 | 3.1144 | 3.7404 | 4.0698 | 4.7287 | 5.3875 | 0.77734 | 2.1116 | 2.6484 | 2.6484 | 2.6484 | 2.6484 | 1.996 | 2.5335 | 2.5335 | 2.5335 | 2.5335 | 2.5335
2020-07-13 07:00 | Winter | 1.2003 | 1.8456 | 2.7928 | 2.7928 | 2.7928 | 2.7928 | 0.90875 | 0.90875 | 0.90875 | 0.90875 | 0.90875 | 0.90875 | 2.3816 | 3.4353 | 4.1258 | 4.4891 | 5.2159 | 5.9426 | 0.88595 | 2.4066 | 3.0185 | 3.0185 | 3.0185 | 3.0185 | 2.4163 | 3.0669 | 3.0669 | 3.0669 | 3.0669 | 3.0669
2020-07-13 08:00 | Winter | 1.3908 | 2.1386 | 3.2361 | 3.2361 | 3.2361 | 3.2361 | 1.0431 | 1.0431 | 1.0431 | 1.0431 | 1.0431 | 1.0431 | 2.679 | 3.8644 | 4.6411 | 5.0498 | 5.8673 | 6.6848 | 0.96406 | 2.6188 | 3.2846 | 3.2846 | 3.2846 | 3.2846 | 2.6476 | 3.3606 | 3.3606 | 3.3606 | 3.3606 | 3.3606
2020-07-13 09:00 | Winter | 1.4289 | 2.1972 | 3.3247 | 3.3247 | 3.3247 | 3.3247 | 1.0688 | 1.0688 | 1.0688 | 1.0688 | 1.0688 | 1.0688 | 2.6864 | 3.8751 | 4.6539 | 5.0637 | 5.8835 | 6.7033 | 0.94119 | 2.5567 | 3.2067 | 3.2067 | 3.2067 | 3.2067 | 2.6864 | 3.4098 | 3.4098 | 3.4098 | 3.4098 | 3.4098
2020-07-13 10:00 | Winter | 1.3337 | 2.0507 | 3.1031 | 3.1031 | 3.1031 | 3.1031 | 1.0145 | 1.0145 | 1.0145 | 1.0145 | 1.0145 | 1.0145 | 2.6864 | 3.8751 | 4.6539 | 5.0637 | 5.8835 | 6.7033 | 0.88023 | 2.3911 | 2.9989 | 2.9989 | 2.9989 | 2.9989 | 2.6864 | 3.4098 | 3.4098 | 3.4098 | 3.4098 | 3.4098
2020-07-13 11:00 | Winter | 1.3039 | 2.0049 | 3.0338 | 3.0338 | 3.0338 | 3.0338 | 1.0517 | 1.0517 | 1.0517 | 1.0517 | 1.0517 | 1.0517 | 2.6864 | 3.8751 | 4.6539 | 5.0637 | 5.8835 | 6.7033 | 0.87642 | 2.3807 | 2.986 | 2.986 | 2.986 | 2.986 | 2.7626 | 3.5065 | 3.5065 | 3.5065 | 3.5065 | 3.5065
2020-07-13 12:00 | Winter | 1.3146 | 2.0214 | 3.0588 | 3.0588 | 3.0588 | 3.0588 | 1.0288 | 1.0288 | 1.0288 | 1.0288 | 1.0288 | 1.0288 | 2.7436 | 3.9575 | 4.7529 | 5.1715 | 6.0087 | 6.8459 | 0.86879 | 2.36 | 2.96 | 2.96 | 2.96 | 2.96 | 2.682 | 3.4043 | 3.4043 | 3.4043 | 3.4043 | 3.4043
2020-07-13 13:00 | Winter | 1.2956 | 1.9921 | 3.0144 | 3.0144 | 3.0144 | 3.0144 | 1.0088 | 1.0088 | 1.0088 | 1.0088 | 1.0088 | 1.0088 | 2.6375 | 3.8044 | 4.569 | 4.9714 | 5.7763 | 6.5811 | 0.84212 | 2.2875 | 2.8691 | 2.8691 | 2.8691 | 2.8691 | 2.6864 | 3.4098 | 3.4098 | 3.4098 | 3.4098 | 3.4098
2020-07-13 14:00 | Winter | 1.2575 | 1.9335 | 2.9258 | 2.9258 | 2.9258 | 2.9258 | 1.0003 | 1.0003 | 1.0003 | 1.0003 | 1.0003 | 1.0003 | 2.6102 | 3.7651 | 4.5218 | 4.9201 | 5.7166 | 6.5131 | 0.84212 | 2.2875 | 2.8691 | 2.8691 | 2.8691 | 2.8691 | 2.4478 | 3.107 | 3.107 | 3.107 | 3.107 | 3.107
2020-07-13 15:00 | Winter | 1.2194 | 1.8749 | 2.8371 | 2.8371 | 2.8371 | 2.8371 | 0.94881 | 0.94881 | 0.94881 | 0.94881 | 0.94881 | 0.94881 | 2.4959 | 3.6002 | 4.3238 | 4.7046 | 5.4662 | 6.2279 | 0.91071 | 2.4739 | 3.1028 | 3.1028 | 3.1028 | 3.1028 | 2.3435 | 2.9745 | 2.9745 | 2.9745 | 2.9745 | 2.9745
2020-07-13 16:00 | Winter | 1.1432 | 1.7577 | 2.6598 | 2.6598 | 2.6598 | 2.6598 | 0.97453 | 0.97453 | 0.97453 | 0.97453 | 0.97453 | 0.97453 | 2.4959 | 3.6002 | 4.3238 | 4.7046 | 5.4662 | 6.2279 | 0.86498 | 2.3496 | 2.947 | 2.947 | 2.947 | 2.947 | 2.3244 | 2.9503 | 2.9503 | 2.9503 | 2.9503 | 2.9503
2020-07-13 17:00 | Winter | 1.1241 | 1.7284 | 2.6155 | 2.6155 | 2.6155 | 2.6155 | 1.0003 | 1.0003 | 1.0003 | 1.0003 | 1.0003 | 1.0003 | 2.5908 | 3.7372 | 4.4882 | 4.8835 | 5.6741 | 6.4647 | 0.91833 | 2.4946 | 3.1288 | 3.1288 | 3.1288 | 3.1288 | 2.2181 | 2.8154 | 2.8154 | 2.8154 | 2.8154 | 2.8154
2020-07-13 18:00 | Winter | 1.0101 | 1.5531 | 2.3501 | 2.3501 | 2.3501 | 2.3501 | 0.872 | 0.872 | 0.872 | 0.872 | 0.872 | 0.872 | 2.5911 | 3.7377 | 4.4888 | 4.8842 | 5.6749 | 6.4656 | 0.84974 | 2.3082 | 2.8951 | 2.8951 | 2.8951 | 2.8951 | 1.7147 | 2.1765 | 2.1765 | 2.1765 | 2.1765 | 2.1765
2020-07-13 19:00 | Winter | 0.68589 | 1.0546 | 1.5959 | 1.5959 | 1.5959 | 1.5959 | 0.63066 | 0.63066 | 0.63066 | 0.63066 | 0.63066 | 0.63066 | 2.4273 | 3.5014 | 4.2051 | 4.5754 | 5.3161 | 6.0568 | 0.78877 | 2.1426 | 2.6874 | 2.6874 | 2.6874 | 2.6874 | 1.1813 | 1.4993 | 1.4993 | 1.4993 | 1.4993 | 1.4993
2020-07-13 20:00 | Winter | 0.68394 | 1.0516 | 1.5913 | 1.5913 | 1.5913 | 1.5913 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 2.3244 | 3.3529 | 4.0267 | 4.3814 | 5.0907 | 5.8 | 0.76972 | 2.0909 | 2.6225 | 2.6225 | 2.6225 | 2.6225 | 1.0863 | 1.3788 | 1.3788 | 1.3788 | 1.3788 | 1.3788
2020-07-13 21:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.43439 | 0.43439 | 0.43439 | 0.43439 | 0.43439 | 0.43439 | 2.2119 | 3.1906 | 3.8318 | 4.1693 | 4.8443 | 5.5193 | 0.73924 | 2.0081 | 2.5186 | 2.5186 | 2.5186 | 2.5186 | 1.0098 | 1.2817 | 1.2817 | 1.2817 | 1.2817 | 1.2817
2020-07-13 22:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.42296 | 0.42296 | 0.42296 | 0.42296 | 0.42296 | 0.42296 | 2.1339 | 3.0781 | 3.6967 | 4.0223 | 4.6734 | 5.3246 | 0.68589 | 1.8632 | 2.3368 | 2.3368 | 2.3368 | 2.3368 | 0.91452 | 1.1608 | 1.1608 | 1.1608 | 1.1608 | 1.1608
2020-07-13 23:00 | Winter | 0.59155 | 0.90958 | 1.3764 | 1.3764 | 1.3764 | 1.3764 | 0.40296 | 0.40296 | 0.40296 | 0.40296 | 0.40296 | 0.40296 | 1.7908 | 2.5832 | 3.1024 | 3.3756 | 3.9221 | 4.4686 | 0.60206 | 1.6354 | 2.0512 | 2.0512 | 2.0512 | 2.0512 | 0.87218 | 1.107 | 1.107 | 1.107 | 1.107 | 1.107
2020-07-14 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.41153 | 0.41153 | 0.41153 | 0.41153 | 0.41153 | 0.41153 | 1.6576 | 2.391 | 2.8715 | 3.1244 | 3.6302 | 4.1361 | 0.56395 | 1.5319 | 1.9214 | 1.9214 | 1.9214 | 1.9214 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-07-14 01:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.41719 | 0.41719 | 0.41719 | 0.41719 | 0.41719 | 0.41719 | 1.5814 | 2.2811 | 2.7395 | 2.9808 | 3.4633 | 3.9459 | 0.58301 | 1.5837 | 1.9863 | 1.9863 | 1.9863 | 1.9863 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-07-14 02:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 1.5623 | 2.2536 | 2.7065 | 2.9449 | 3.4216 | 3.8984 | 0.54871 | 1.4905 | 1.8695 | 1.8695 | 1.8695 | 1.8695 | 1.1241 | 1.4268 | 1.4268 | 1.4268 | 1.4268 | 1.4268
2020-07-14 03:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.37724 | 0.37724 | 0.37724 | 0.37724 | 0.37724 | 0.37724 | 1.5433 | 2.2261 | 2.6735 | 2.909 | 3.3799 | 3.8508 | 0.5449 | 1.4802 | 1.8565 | 1.8565 | 1.8565 | 1.8565 | 1.0879 | 1.3808 | 1.3808 | 1.3808 | 1.3808 | 1.3808
2020-07-14 04:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 1.6269 | 2.3468 | 2.8184 | 3.0667 | 3.5631 | 4.0596 | 0.5792 | 1.5733 | 1.9733 | 1.9733 | 1.9733 | 1.9733 | 1.1165 | 1.4171 | 1.4171 | 1.4171 | 1.4171 | 1.4171
2020-07-14 05:00 | Winter | 0.71773 | 1.1036 | 1.67 | 1.67 | 1.67 | 1.67 | 0.60301 | 0.60301 | 0.60301 | 0.60301 | 0.60301 | 0.60301 | 1.7691 | 2.5519 | 3.0648 | 3.3347 | 3.8746 | 4.4145 | 0.7228 | 1.9634 | 2.4626 | 2.4626 | 2.4626 | 2.4626 | 1.5052 | 1.9105 | 1.9105 | 1.9105 | 1.9105 | 1.9105
2020-07-14 06:00 | Winter | 0.83831 | 1.289 | 1.9505 | 1.9505 | 1.9505 | 1.9505 | 0.72018 | 0.72018 | 0.72018 | 0.72018 | 0.72018 | 0.72018 | 2.1142 | 3.0497 | 3.6626 | 3.9852 | 4.6304 | 5.2756 | 0.86117 | 2.3393 | 2.934 | 2.934 | 2.934 | 2.934 | 1.896 | 2.4065 | 2.4065 | 2.4065 | 2.4065 | 2.4065
2020-07-14 07:00 | Winter | 1.1432 | 1.7577 | 2.6598 | 2.6598 | 2.6598 | 2.6598 | 0.82307 | 0.82307 | 0.82307 | 0.82307 | 0.82307 | 0.82307 | 2.5364 | 3.6586 | 4.3939 | 4.7809 | 5.5549 | 6.3289 | 0.88404 | 2.4014 | 3.0119 | 3.0119 | 3.0119 | 3.0119 | 2.346 | 2.9777 | 2.9777 | 2.9777 | 2.9777 | 2.9777
2020-07-14 08:00 | Winter | 1.3908 | 2.1386 | 3.2361 | 3.2361 | 3.2361 | 3.2361 | 1.0307 | 1.0307 | 1.0307 | 1.0307 | 1.0307 | 1.0307 | 2.6293 | 3.7926 | 4.5548 | 4.956 | 5.7583 | 6.5606 | 0.92595 | 2.5153 | 3.1547 | 3.1547 | 3.1547 | 3.1547 | 2.6102 | 3.3131 | 3.3131 | 3.3131 | 3.3131 | 3.3131
2020-07-14 09:00 | Winter | 1.3718 | 2.1093 | 3.1918 | 3.1918 | 3.1918 | 3.1918 | 1.086 | 1.086 | 1.086 | 1.086 | 1.086 | 1.086 | 2.6293 | 3.7926 | 4.5548 | 4.956 | 5.7583 | 6.5606 | 0.98692 | 2.6809 | 3.3625 | 3.3625 | 3.3625 | 3.3625 | 2.5911 | 3.2889 | 3.2889 | 3.2889 | 3.2889 | 3.2889
2020-07-14 10:00 | Winter | 1.3337 | 2.0507 | 3.1031 | 3.1031 | 3.1031 | 3.1031 | 0.99454 | 0.99454 | 0.99454 | 0.99454 | 0.99454 | 0.99454 | 2.643 | 3.8125 | 4.5787 | 4.982 | 5.7885 | 6.595 | 0.96406 | 2.6188 | 3.2846 | 3.2846 | 3.2846 | 3.2846 | 2.6674 | 3.3856 | 3.3856 | 3.3856 | 3.3856 | 3.3856
2020-07-14 11:00 | Winter | 1.2765 | 1.9628 | 2.9701 | 2.9701 | 2.9701 | 2.9701 | 0.98311 | 0.98311 | 0.98311 | 0.98311 | 0.98311 | 0.98311 | 2.7245 | 3.93 | 4.7199 | 5.1356 | 5.967 | 6.7984 | 0.87642 | 2.3807 | 2.986 | 2.986 | 2.986 | 2.986 | 2.6674 | 3.3856 | 3.3856 | 3.3856 | 3.3856 | 3.3856
2020-07-14 12:00 | Winter | 1.3146 | 2.0214 | 3.0588 | 3.0588 | 3.0588 | 3.0588 | 0.9631 | 0.9631 | 0.9631 | 0.9631 | 0.9631 | 0.9631 | 2.6102 | 3.7651 | 4.5218 | 4.9201 | 5.7166 | 6.5131 | 0.92976 | 2.5256 | 3.1677 | 3.1677 | 3.1677 | 3.1677 | 2.6102 | 3.3131 | 3.3131 | 3.3131 | 3.3131 | 3.3131
2020-07-14 13:00 | Winter | 1.2956 | 1.9921 | 3.0144 | 3.0144 | 3.0144 | 3.0144 | 0.93452 | 0.93452 | 0.93452 | 0.93452 | 0.93452 | 0.93452 | 2.553 | 3.6827 | 4.4228 | 4.8123 | 5.5914 | 6.3705 | 0.91833 | 2.4946 | 3.1288 | 3.1288 | 3.1288 | 3.1288 | 2.534 | 3.2163 | 3.2163 | 3.2163 | 3.2163 | 3.2163
2020-07-14 14:00 | Winter | 1.2485 | 1.9197 | 2.9048 | 2.9048 | 2.9048 | 2.9048 | 0.98882 | 0.98882 | 0.98882 | 0.98882 | 0.98882 | 0.98882 | 2.4959 | 3.6002 | 4.3238 | 4.7046 | 5.4662 | 6.2279 | 0.88785 | 2.4118 | 3.0249 | 3.0249 | 3.0249 | 3.0249 | 2.4387 | 3.0954 | 3.0954 | 3.0954 | 3.0954 | 3.0954
2020-07-14 15:00 | Winter | 1.2384 | 1.9042 | 2.8814 | 2.8814 | 2.8814 | 2.8814 | 1.0346 | 1.0346 | 1.0346 | 1.0346 | 1.0346 | 1.0346 | 2.5149 | 3.6277 | 4.3568 | 4.7405 | 5.508 | 6.2754 | 0.86498 | 2.3496 | 2.947 | 2.947 | 2.947 | 2.947 | 2.3244 | 2.9503 | 2.9503 | 2.9503 | 2.9503 | 2.9503
2020-07-14 16:00 | Winter | 1.2194 | 1.8749 | 2.8371 | 2.8371 | 2.8371 | 2.8371 | 0.85736 | 0.85736 | 0.85736 | 0.85736 | 0.85736 | 0.85736 | 2.6293 | 3.7926 | 4.5548 | 4.956 | 5.7583 | 6.5606 | 0.87261 | 2.3704 | 2.973 | 2.973 | 2.973 | 2.973 | 2.2291 | 2.8294 | 2.8294 | 2.8294 | 2.8294 | 2.8294
2020-07-14 17:00 | Winter | 1.1432 | 1.7577 | 2.6598 | 2.6598 | 2.6598 | 2.6598 | 0.9431 | 0.9431 | 0.9431 | 0.9431 | 0.9431 | 0.9431 | 2.7245 | 3.93 | 4.7199 | 5.1356 | 5.967 | 6.7984 | 0.92214 | 2.5049 | 3.1418 | 3.1418 | 3.1418 | 3.1418 | 2.1217 | 2.6931 | 2.6931 | 2.6931 | 2.6931 | 2.6931
2020-07-14 18:00 | Winter | 0.86701 | 1.3331 | 2.0173 | 2.0173 | 2.0173 | 2.0173 | 0.88022 | 0.88022 | 0.88022 | 0.88022 | 0.88022 | 0.88022 | 2.6885 | 3.8781 | 4.6575 | 5.0677 | 5.8881 | 6.7085 | 0.89547 | 2.4325 | 3.0509 | 3.0509 | 3.0509 | 3.0509 | 1.6372 | 2.0781 | 2.0781 | 2.0781 | 2.0781 | 2.0781
2020-07-14 19:00 | Winter | 0.70556 | 1.0849 | 1.6416 | 1.6416 | 1.6416 | 1.6416 | 0.64773 | 0.64773 | 0.64773 | 0.64773 | 0.64773 | 0.64773 | 2.5726 | 3.7109 | 4.4567 | 4.8492 | 5.6343 | 6.4193 | 0.82688 | 2.2461 | 2.8172 | 2.8172 | 2.8172 | 2.8172 | 1.2194 | 1.5477 | 1.5477 | 1.5477 | 1.5477 | 1.5477
2020-07-14 20:00 | Winter | 0.64779 | 0.99605 | 1.5072 | 1.5072 | 1.5072 | 1.5072 | 0.49441 | 0.49441 | 0.49441 | 0.49441 | 0.49441 | 0.49441 | 2.3816 | 3.4353 | 4.1258 | 4.4891 | 5.2159 | 5.9426 | 0.79258 | 2.153 | 2.7003 | 2.7003 | 2.7003 | 2.7003 | 1.086 | 1.3784 | 1.3784 | 1.3784 | 1.3784 | 1.3784
2020-07-14 21:00 | Winter | 0.59057 | 0.90807 | 1.3741 | 1.3741 | 1.3741 | 1.3741 | 0.4544 | 0.4544 | 0.4544 | 0.4544 | 0.4544 | 0.4544 | 2.2482 | 3.243 | 3.8947 | 4.2377 | 4.9238 | 5.6098 | 0.75829 | 2.0598 | 2.5835 | 2.5835 | 2.5835 | 2.5835 | 0.95696 | 1.2146 | 1.2146 | 1.2146 | 1.2146 | 1.2146
2020-07-14 22:00 | Winter | 0.59801 | 0.91951 | 1.3914 | 1.3914 | 1.3914 | 1.3914 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 2.0577 | 2.9681 | 3.5647 | 3.8786 | 4.5065 | 5.1344 | 0.73162 | 1.9874 | 2.4926 | 2.4926 | 2.4926 | 2.4926 | 0.8768 | 1.1129 | 1.1129 | 1.1129 | 1.1129 | 1.1129
2020-07-14 23:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.42296 | 0.42296 | 0.42296 | 0.42296 | 0.42296 | 0.42296 | 1.8964 | 2.7355 | 3.2853 | 3.5746 | 4.1533 | 4.732 | 0.63635 | 1.7286 | 2.1681 | 2.1681 | 2.1681 | 2.1681 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-07-15 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.41986 | 0.41986 | 0.41986 | 0.41986 | 0.41986 | 0.41986 | 1.7683 | 2.5508 | 3.0634 | 3.3332 | 3.8728 | 4.4124 | 0.63254 | 1.7182 | 2.1551 | 2.1551 | 2.1551 | 2.1551 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-07-15 01:00 | Winter | 0.55257 | 0.84963 | 1.2857 | 1.2857 | 1.2857 | 1.2857 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 1.6957 | 2.446 | 2.9375 | 3.1963 | 3.7137 | 4.2311 | 0.60968 | 1.6561 | 2.0772 | 2.0772 | 2.0772 | 2.0772 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-07-15 02:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.60968 | 1.6561 | 2.0772 | 2.0772 | 2.0772 | 2.0772 | 0.99073 | 1.2575 | 1.2575 | 1.2575 | 1.2575 | 1.2575
2020-07-15 03:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.41744 | 0.41744 | 0.41744 | 0.41744 | 0.41744 | 0.41744 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.59444 | 1.6147 | 2.0253 | 2.0253 | 2.0253 | 2.0253 | 1.0669 | 1.3542 | 1.3542 | 1.3542 | 1.3542 | 1.3542
2020-07-15 04:00 | Winter | 0.64426 | 0.99062 | 1.499 | 1.499 | 1.499 | 1.499 | 0.47441 | 0.47441 | 0.47441 | 0.47441 | 0.47441 | 0.47441 | 1.6909 | 2.4391 | 2.9292 | 3.1872 | 3.7032 | 4.2192 | 0.657 | 1.7847 | 2.2384 | 2.2384 | 2.2384 | 2.2384 | 1.105 | 1.4026 | 1.4026 | 1.4026 | 1.4026 | 1.4026
2020-07-15 05:00 | Winter | 0.68589 | 1.0546 | 1.5959 | 1.5959 | 1.5959 | 1.5959 | 0.61158 | 0.61158 | 0.61158 | 0.61158 | 0.61158 | 0.61158 | 1.9434 | 2.8032 | 3.3666 | 3.6631 | 4.2562 | 4.8492 | 0.74305 | 2.0184 | 2.5316 | 2.5316 | 2.5316 | 2.5316 | 1.5052 | 1.9105 | 1.9105 | 1.9105 | 1.9105 | 1.9105
2020-07-15 06:00 | Winter | 0.79046 | 1.2154 | 1.8392 | 1.8392 | 1.8392 | 1.8392 | 0.76591 | 0.76591 | 0.76591 | 0.76591 | 0.76591 | 0.76591 | 2.189 | 3.1576 | 3.7922 | 4.1262 | 4.7942 | 5.4621 | 0.8345 | 2.2668 | 2.8432 | 2.8432 | 2.8432 | 2.8432 | 1.899 | 2.4103 | 2.4103 | 2.4103 | 2.4103 | 2.4103
2020-07-15 07:00 | Winter | 1.1432 | 1.7577 | 2.6598 | 2.6598 | 2.6598 | 2.6598 | 0.85736 | 0.85736 | 0.85736 | 0.85736 | 0.85736 | 0.85736 | 2.4768 | 3.5728 | 4.2908 | 4.6687 | 5.4245 | 6.1803 | 0.96406 | 2.6188 | 3.2846 | 3.2846 | 3.2846 | 3.2846 | 2.3054 | 2.9261 | 2.9261 | 2.9261 | 2.9261 | 2.9261
2020-07-15 08:00 | Winter | 1.3527 | 2.08 | 3.1474 | 3.1474 | 3.1474 | 3.1474 | 0.98882 | 0.98882 | 0.98882 | 0.98882 | 0.98882 | 0.98882 | 2.5911 | 3.7377 | 4.4888 | 4.8842 | 5.6749 | 6.4656 | 0.99454 | 2.7016 | 3.3884 | 3.3884 | 3.3884 | 3.3884 | 2.4768 | 3.1438 | 3.1438 | 3.1438 | 3.1438 | 3.1438
2020-07-15 09:00 | Winter | 1.3718 | 2.1093 | 3.1918 | 3.1918 | 3.1918 | 3.1918 | 1.0288 | 1.0288 | 1.0288 | 1.0288 | 1.0288 | 1.0288 | 2.6293 | 3.7926 | 4.5548 | 4.956 | 5.7583 | 6.5606 | 0.99454 | 2.7016 | 3.3884 | 3.3884 | 3.3884 | 3.3884 | 2.6102 | 3.3131 | 3.3131 | 3.3131 | 3.3131 | 3.3131
2020-07-15 10:00 | Winter | 1.2765 | 1.9628 | 2.9701 | 2.9701 | 2.9701 | 2.9701 | 1.0774 | 1.0774 | 1.0774 | 1.0774 | 1.0774 | 1.0774 | 2.6674 | 3.8476 | 4.6208 | 5.0278 | 5.8418 | 6.6557 | 0.96406 | 2.6188 | 3.2846 | 3.2846 | 3.2846 | 3.2846 | 2.6674 | 3.3856 | 3.3856 | 3.3856 | 3.3856 | 3.3856
2020-07-15 11:00 | Winter | 1.2956 | 1.9921 | 3.0144 | 3.0144 | 3.0144 | 3.0144 | 1.0374 | 1.0374 | 1.0374 | 1.0374 | 1.0374 | 1.0374 | 2.5721 | 3.7102 | 4.4558 | 4.8483 | 5.6331 | 6.418 | 0.89547 | 2.4325 | 3.0509 | 3.0509 | 3.0509 | 3.0509 | 2.5721 | 3.2647 | 3.2647 | 3.2647 | 3.2647 | 3.2647
2020-07-15 12:00 | Winter | 1.2194 | 1.8749 | 2.8371 | 2.8371 | 2.8371 | 2.8371 | 1.0145 | 1.0145 | 1.0145 | 1.0145 | 1.0145 | 1.0145 | 2.6102 | 3.7651 | 4.5218 | 4.9201 | 5.7166 | 6.5131 | 0.95263 | 2.5877 | 3.2456 | 3.2456 | 3.2456 | 3.2456 | 2.5224 | 3.2017 | 3.2017 | 3.2017 | 3.2017 | 3.2017
2020-07-15 13:00 | Winter | 1.2765 | 1.9628 | 2.9701 | 2.9701 | 2.9701 | 2.9701 | 1.0488 | 1.0488 | 1.0488 | 1.0488 | 1.0488 | 1.0488 | 2.6483 | 3.8201 | 4.5878 | 4.9919 | 5.8 | 6.6082 | 0.88023 | 2.3911 | 2.9989 | 2.9989 | 2.9989 | 2.9989 | 2.4578 | 3.1196 | 3.1196 | 3.1196 | 3.1196 | 3.1196
2020-07-15 14:00 | Winter | 1.2194 | 1.8749 | 2.8371 | 2.8371 | 2.8371 | 2.8371 | 1.0117 | 1.0117 | 1.0117 | 1.0117 | 1.0117 | 1.0117 | 2.6483 | 3.8201 | 4.5878 | 4.9919 | 5.8 | 6.6082 | 0.86498 | 2.3496 | 2.947 | 2.947 | 2.947 | 2.947 | 2.2863 | 2.902 | 2.902 | 2.902 | 2.902 | 2.902
2020-07-15 15:00 | Winter | 1.2194 | 1.8749 | 2.8371 | 2.8371 | 2.8371 | 2.8371 | 1.0374 | 1.0374 | 1.0374 | 1.0374 | 1.0374 | 1.0374 | 2.5149 | 3.6277 | 4.3568 | 4.7405 | 5.508 | 6.2754 | 0.89928 | 2.4428 | 3.0639 | 3.0639 | 3.0639 | 3.0639 | 2.2101 | 2.8052 | 2.8052 | 2.8052 | 2.8052 | 2.8052
2020-07-15 16:00 | Winter | 1.1432 | 1.7577 | 2.6598 | 2.6598 | 2.6598 | 2.6598 | 0.94024 | 0.94024 | 0.94024 | 0.94024 | 0.94024 | 0.94024 | 2.5721 | 3.7102 | 4.4558 | 4.8483 | 5.6331 | 6.418 | 0.93738 | 2.5463 | 3.1937 | 3.1937 | 3.1937 | 3.1937 | 2.2291 | 2.8294 | 2.8294 | 2.8294 | 2.8294 | 2.8294
2020-07-15 17:00 | Winter | 1.105 | 1.6991 | 2.5711 | 2.5711 | 2.5711 | 2.5711 | 0.91738 | 0.91738 | 0.91738 | 0.91738 | 0.91738 | 0.91738 | 2.6674 | 3.8476 | 4.6208 | 5.0278 | 5.8418 | 6.6557 | 0.96025 | 2.6084 | 3.2716 | 3.2716 | 3.2716 | 3.2716 | 2.172 | 2.7569 | 2.7569 | 2.7569 | 2.7569 | 2.7569
2020-07-15 18:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.80306 | 0.80306 | 0.80306 | 0.80306 | 0.80306 | 0.80306 | 2.6483 | 3.8201 | 4.5878 | 4.9919 | 5.8 | 6.6082 | 0.9069 | 2.4635 | 3.0898 | 3.0898 | 3.0898 | 3.0898 | 1.5617 | 1.9823 | 1.9823 | 1.9823 | 1.9823 | 1.9823
2020-07-15 19:00 | Winter | 0.7052 | 1.0843 | 1.6408 | 1.6408 | 1.6408 | 1.6408 | 0.58015 | 0.58015 | 0.58015 | 0.58015 | 0.58015 | 0.58015 | 2.5046 | 3.6128 | 4.3388 | 4.721 | 5.4852 | 6.2495 | 0.78877 | 2.1426 | 2.6874 | 2.6874 | 2.6874 | 2.6874 | 1.2199 | 1.5484 | 1.5484 | 1.5484 | 1.5484 | 1.5484
2020-07-15 20:00 | Winter | 0.64779 | 0.99605 | 1.5072 | 1.5072 | 1.5072 | 1.5072 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 2.3625 | 3.4079 | 4.0927 | 4.4532 | 5.1741 | 5.8951 | 0.78496 | 2.1323 | 2.6744 | 2.6744 | 2.6744 | 2.6744 | 1.105 | 1.4026 | 1.4026 | 1.4026 | 1.4026 | 1.4026
2020-07-15 21:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 2.2291 | 3.2155 | 3.8617 | 4.2018 | 4.8821 | 5.5623 | 0.79258 | 2.153 | 2.7003 | 2.7003 | 2.7003 | 2.7003 | 0.97168 | 1.2333 | 1.2333 | 1.2333 | 1.2333 | 1.2333
2020-07-15 22:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 2.0579 | 2.9685 | 3.5651 | 3.8791 | 4.507 | 5.135 | 0.72018 | 1.9563 | 2.4537 | 2.4537 | 2.4537 | 2.4537 | 0.90306 | 1.1462 | 1.1462 | 1.1462 | 1.1462 | 1.1462
2020-07-15 23:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.38009 | 0.38009 | 0.38009 | 0.38009 | 0.38009 | 0.38009 | 1.81 | 2.6109 | 3.1356 | 3.4117 | 3.9641 | 4.5164 | 0.63635 | 1.7286 | 2.1681 | 2.1681 | 2.1681 | 2.1681 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-07-16 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.38867 | 0.38867 | 0.38867 | 0.38867 | 0.38867 | 0.38867 | 1.7147 | 2.4735 | 2.9705 | 3.2322 | 3.7554 | 4.2787 | 0.62111 | 1.6872 | 2.1161 | 2.1161 | 2.1161 | 2.1161 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-07-16 01:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.37724 | 0.37724 | 0.37724 | 0.37724 | 0.37724 | 0.37724 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.59444 | 1.6147 | 2.0253 | 2.0253 | 2.0253 | 2.0253 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-07-16 02:00 | Winter | 0.59012 | 0.90737 | 1.373 | 1.373 | 1.373 | 1.373 | 0.41439 | 0.41439 | 0.41439 | 0.41439 | 0.41439 | 0.41439 | 1.6198 | 2.3365 | 2.806 | 3.0532 | 3.5475 | 4.0417 | 0.58301 | 1.5837 | 1.9863 | 1.9863 | 1.9863 | 1.9863 | 0.99073 | 1.2575 | 1.2575 | 1.2575 | 1.2575 | 1.2575
2020-07-16 03:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 1.6766 | 2.4185 | 2.9045 | 3.1603 | 3.672 | 4.1836 | 0.53728 | 1.4595 | 1.8305 | 1.8305 | 1.8305 | 1.8305 | 0.99073 | 1.2575 | 1.2575 | 1.2575 | 1.2575 | 1.2575
2020-07-16 04:00 | Winter | 0.62703 | 0.96414 | 1.4589 | 1.4589 | 1.4589 | 1.4589 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 1.7201 | 2.4812 | 2.9799 | 3.2423 | 3.7672 | 4.2921 | 0.56395 | 1.5319 | 1.9214 | 1.9214 | 1.9214 | 1.9214 | 1.0477 | 1.3298 | 1.3298 | 1.3298 | 1.3298 | 1.3298
2020-07-16 05:00 | Winter | 0.66684 | 1.0253 | 1.5515 | 1.5515 | 1.5515 | 1.5515 | 0.57729 | 0.57729 | 0.57729 | 0.57729 | 0.57729 | 0.57729 | 1.8862 | 2.7208 | 3.2676 | 3.5554 | 4.131 | 4.7066 | 0.73162 | 1.9874 | 2.4926 | 2.4926 | 2.4926 | 2.4926 | 1.4368 | 1.8237 | 1.8237 | 1.8237 | 1.8237 | 1.8237
2020-07-16 06:00 | Winter | 0.80001 | 1.2301 | 1.8614 | 1.8614 | 1.8614 | 1.8614 | 0.73161 | 0.73161 | 0.73161 | 0.73161 | 0.73161 | 0.73161 | 2.1919 | 3.1618 | 3.7972 | 4.1316 | 4.8005 | 5.4694 | 0.7621 | 2.0702 | 2.5965 | 2.5965 | 2.5965 | 2.5965 | 1.8072 | 2.2938 | 2.2938 | 2.2938 | 2.2938 | 2.2938
2020-07-16 07:00 | Winter | 1.199 | 1.8436 | 2.7898 | 2.7898 | 2.7898 | 2.7898 | 0.92023 | 0.92023 | 0.92023 | 0.92023 | 0.92023 | 0.92023 | 2.4578 | 3.5453 | 4.2578 | 4.6328 | 5.3828 | 6.1328 | 0.88023 | 2.3911 | 2.9989 | 2.9989 | 2.9989 | 2.9989 | 2.3291 | 2.9562 | 2.9562 | 2.9562 | 2.9562 | 2.9562
2020-07-16 08:00 | Winter | 1.3527 | 2.08 | 3.1474 | 3.1474 | 3.1474 | 3.1474 | 0.9631 | 0.9631 | 0.9631 | 0.9631 | 0.9631 | 0.9631 | 2.7436 | 3.9575 | 4.7529 | 5.1715 | 6.0087 | 6.8459 | 0.92976 | 2.5256 | 3.1677 | 3.1677 | 3.1677 | 3.1677 | 2.5721 | 3.2647 | 3.2647 | 3.2647 | 3.2647 | 3.2647
2020-07-16 09:00 | Winter | 1.3337 | 2.0507 | 3.1031 | 3.1031 | 3.1031 | 3.1031 | 0.99168 | 0.99168 | 0.99168 | 0.99168 | 0.99168 | 0.99168 | 2.6674 | 3.8476 | 4.6208 | 5.0278 | 5.8418 | 6.6557 | 0.98311 | 2.6705 | 3.3495 | 3.3495 | 3.3495 | 3.3495 | 2.534 | 3.2163 | 3.2163 | 3.2163 | 3.2163 | 3.2163
2020-07-16 10:00 | Winter | 1.2765 | 1.9628 | 2.9701 | 2.9701 | 2.9701 | 2.9701 | 0.96882 | 0.96882 | 0.96882 | 0.96882 | 0.96882 | 0.96882 | 2.7436 | 3.9575 | 4.7529 | 5.1715 | 6.0087 | 6.8459 | 0.93738 | 2.5463 | 3.1937 | 3.1937 | 3.1937 | 3.1937 | 2.4959 | 3.168 | 3.168 | 3.168 | 3.168 | 3.168
2020-07-16 11:00 | Winter | 1.2679 | 1.9496 | 2.9501 | 2.9501 | 2.9501 | 2.9501 | 0.89451 | 0.89451 | 0.89451 | 0.89451 | 0.89451 | 0.89451 | 2.7436 | 3.9575 | 4.7529 | 5.1715 | 6.0087 | 6.8459 | 0.89547 | 2.4325 | 3.0509 | 3.0509 | 3.0509 | 3.0509 | 2.5149 | 3.1922 | 3.1922 | 3.1922 | 3.1922 | 3.1922
2020-07-16 12:00 | Winter | 1.2956 | 1.9921 | 3.0144 | 3.0144 | 3.0144 | 3.0144 | 1.0317 | 1.0317 | 1.0317 | 1.0317 | 1.0317 | 1.0317 | 2.6478 | 3.8194 | 4.587 | 4.991 | 5.7989 | 6.6069 | 0.86498 | 2.3496 | 2.947 | 2.947 | 2.947 | 2.947 | 2.5149 | 3.1922 | 3.1922 | 3.1922 | 3.1922 | 3.1922
2020-07-16 13:00 | Winter | 1.2575 | 1.9335 | 2.9258 | 2.9258 | 2.9258 | 2.9258 | 0.96882 | 0.96882 | 0.96882 | 0.96882 | 0.96882 | 0.96882 | 2.6483 | 3.8201 | 4.5878 | 4.9919 | 5.8 | 6.6082 | 0.88023 | 2.3911 | 2.9989 | 2.9989 | 2.9989 | 2.9989 | 2.4348 | 3.0905 | 3.0905 | 3.0905 | 3.0905 | 3.0905
2020-07-16 14:00 | Winter | 1.2194 | 1.8749 | 2.8371 | 2.8371 | 2.8371 | 2.8371 | 0.9631 | 0.9631 | 0.9631 | 0.9631 | 0.9631 | 0.9631 | 2.5721 | 3.7102 | 4.4558 | 4.8483 | 5.6331 | 6.418 | 0.88785 | 2.4118 | 3.0249 | 3.0249 | 3.0249 | 3.0249 | 2.3816 | 3.0229 | 3.0229 | 3.0229 | 3.0229 | 3.0229
2020-07-16 15:00 | Winter | 1.1813 | 1.8163 | 2.7485 | 2.7485 | 2.7485 | 2.7485 | 0.98597 | 0.98597 | 0.98597 | 0.98597 | 0.98597 | 0.98597 | 2.553 | 3.6827 | 4.4228 | 4.8123 | 5.5914 | 6.3705 | 0.83831 | 2.2772 | 2.8561 | 2.8561 | 2.8561 | 2.8561 | 2.2673 | 2.8778 | 2.8778 | 2.8778 | 2.8778 | 2.8778
2020-07-16 16:00 | Winter | 1.1432 | 1.7577 | 2.6598 | 2.6598 | 2.6598 | 2.6598 | 0.90309 | 0.90309 | 0.90309 | 0.90309 | 0.90309 | 0.90309 | 2.5721 | 3.7102 | 4.4558 | 4.8483 | 5.6331 | 6.418 | 0.84974 | 2.3082 | 2.8951 | 2.8951 | 2.8951 | 2.8951 | 2.2482 | 2.8536 | 2.8536 | 2.8536 | 2.8536 | 2.8536
2020-07-16 17:00 | Winter | 1.1241 | 1.7284 | 2.6155 | 2.6155 | 2.6155 | 2.6155 | 0.87165 | 0.87165 | 0.87165 | 0.87165 | 0.87165 | 0.87165 | 2.6483 | 3.8201 | 4.5878 | 4.9919 | 5.8 | 6.6082 | 0.86498 | 2.3496 | 2.947 | 2.947 | 2.947 | 2.947 | 2.1529 | 2.7327 | 2.7327 | 2.7327 | 2.7327 | 2.7327
2020-07-16 18:00 | Winter | 1.0288 | 1.582 | 2.3938 | 2.3938 | 2.3938 | 2.3938 | 0.73733 | 0.73733 | 0.73733 | 0.73733 | 0.73733 | 0.73733 | 2.6293 | 3.7926 | 4.5548 | 4.956 | 5.7583 | 6.5606 | 0.91452 | 2.4842 | 3.1158 | 3.1158 | 3.1158 | 3.1158 | 1.662 | 2.1095 | 2.1095 | 2.1095 | 2.1095 | 2.1095
2020-07-16 19:00 | Winter | 0.68623 | 1.0552 | 1.5967 | 1.5967 | 1.5967 | 1.5967 | 0.56872 | 0.56872 | 0.56872 | 0.56872 | 0.56872 | 0.56872 | 2.4435 | 3.5247 | 4.2331 | 4.6059 | 5.3516 | 6.0972 | 0.81926 | 2.2254 | 2.7912 | 2.7912 | 2.7912 | 2.7912 | 1.1439 | 1.4519 | 1.4519 | 1.4519 | 1.4519 | 1.4519
2020-07-16 20:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.49441 | 0.49441 | 0.49441 | 0.49441 | 0.49441 | 0.49441 | 2.3244 | 3.3529 | 4.0267 | 4.3814 | 5.0907 | 5.8 | 0.74686 | 2.0288 | 2.5446 | 2.5446 | 2.5446 | 2.5446 | 1.0377 | 1.3171 | 1.3171 | 1.3171 | 1.3171 | 1.3171
2020-07-16 21:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.50584 | 0.50584 | 0.50584 | 0.50584 | 0.50584 | 0.50584 | 2.2673 | 3.2705 | 3.9277 | 4.2736 | 4.9655 | 5.6574 | 0.83831 | 2.2772 | 2.8561 | 2.8561 | 2.8561 | 2.8561 | 0.95263 | 1.2092 | 1.2092 | 1.2092 | 1.2092 | 1.2092
2020-07-16 22:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 2.0961 | 3.0236 | 3.6313 | 3.9511 | 4.5908 | 5.2304 | 0.724 | 1.9667 | 2.4667 | 2.4667 | 2.4667 | 2.4667 | 0.87654 | 1.1126 | 1.1126 | 1.1126 | 1.1126 | 1.1126
2020-07-16 23:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 1.8672 | 2.6933 | 3.2346 | 3.5195 | 4.0892 | 4.659 | 0.65548 | 1.7805 | 2.2332 | 2.2332 | 2.2332 | 2.2332 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-07-17 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 1.7719 | 2.5559 | 3.0696 | 3.3399 | 3.8806 | 4.4213 | 0.63635 | 1.7286 | 2.1681 | 2.1681 | 2.1681 | 2.1681 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-07-17 01:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.43439 | 0.43439 | 0.43439 | 0.43439 | 0.43439 | 0.43439 | 1.6576 | 2.391 | 2.8715 | 3.1244 | 3.6302 | 4.1361 | 0.60968 | 1.6561 | 2.0772 | 2.0772 | 2.0772 | 2.0772 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-07-17 02:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 1.6766 | 2.4185 | 2.9045 | 3.1603 | 3.672 | 4.1836 | 0.55867 | 1.5176 | 1.9034 | 1.9034 | 1.9034 | 1.9034 | 0.99073 | 1.2575 | 1.2575 | 1.2575 | 1.2575 | 1.2575
2020-07-17 03:00 | Winter | 0.59014 | 0.9074 | 1.3731 | 1.3731 | 1.3731 | 1.3731 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 1.6766 | 2.4185 | 2.9045 | 3.1603 | 3.672 | 4.1836 | 0.60587 | 1.6458 | 2.0642 | 2.0642 | 2.0642 | 2.0642 | 1.0097 | 1.2816 | 1.2816 | 1.2816 | 1.2816 | 1.2816
2020-07-17 04:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.47441 | 0.47441 | 0.47441 | 0.47441 | 0.47441 | 0.47441 | 1.6841 | 2.4292 | 2.9174 | 3.1744 | 3.6883 | 4.2022 | 0.57539 | 1.563 | 1.9603 | 1.9603 | 1.9603 | 1.9603 | 1.0669 | 1.3542 | 1.3542 | 1.3542 | 1.3542 | 1.3542
2020-07-17 05:00 | Winter | 0.83831 | 1.289 | 1.9505 | 1.9505 | 1.9505 | 1.9505 | 0.59729 | 0.59729 | 0.59729 | 0.59729 | 0.59729 | 0.59729 | 1.9047 | 2.7475 | 3.2996 | 3.5902 | 4.1715 | 4.7527 | 0.75448 | 2.0495 | 2.5705 | 2.5705 | 2.5705 | 2.5705 | 1.4161 | 1.7974 | 1.7974 | 1.7974 | 1.7974 | 1.7974
2020-07-17 06:00 | Winter | 0.95545 | 1.4691 | 2.2231 | 2.2231 | 2.2231 | 2.2231 | 0.70304 | 0.70304 | 0.70304 | 0.70304 | 0.70304 | 0.70304 | 2.0767 | 2.9956 | 3.5977 | 3.9145 | 4.5482 | 5.182 | 0.80783 | 2.1944 | 2.7523 | 2.7523 | 2.7523 | 2.7523 | 1.8037 | 2.2895 | 2.2895 | 2.2895 | 2.2895 | 2.2895
2020-07-17 07:00 | Winter | 1.0881 | 1.6731 | 2.5317 | 2.5317 | 2.5317 | 2.5317 | 0.86594 | 0.86594 | 0.86594 | 0.86594 | 0.86594 | 0.86594 | 2.4387 | 3.5178 | 4.2248 | 4.5969 | 5.3411 | 6.0852 | 0.92976 | 2.5256 | 3.1677 | 3.1677 | 3.1677 | 3.1677 | 2.3001 | 2.9194 | 2.9194 | 2.9194 | 2.9194 | 2.9194
2020-07-17 08:00 | Winter | 1.2575 | 1.9335 | 2.9258 | 2.9258 | 2.9258 | 2.9258 | 0.96025 | 0.96025 | 0.96025 | 0.96025 | 0.96025 | 0.96025 | 2.6483 | 3.8201 | 4.5878 | 4.9919 | 5.8 | 6.6082 | 0.99454 | 2.7016 | 3.3884 | 3.3884 | 3.3884 | 3.3884 | 2.5149 | 3.1922 | 3.1922 | 3.1922 | 3.1922 | 3.1922
2020-07-17 09:00 | Winter | 1.2575 | 1.9335 | 2.9258 | 2.9258 | 2.9258 | 2.9258 | 1.026 | 1.026 | 1.026 | 1.026 | 1.026 | 1.026 | 2.6674 | 3.8476 | 4.6208 | 5.0278 | 5.8418 | 6.6557 | 1.025 | 2.7844 | 3.4923 | 3.4923 | 3.4923 | 3.4923 | 2.5721 | 3.2647 | 3.2647 | 3.2647 | 3.2647 | 3.2647
2020-07-17 10:00 | Winter | 1.2384 | 1.9042 | 2.8814 | 2.8814 | 2.8814 | 2.8814 | 0.92023 | 0.92023 | 0.92023 | 0.92023 | 0.92023 | 0.92023 | 2.6293 | 3.7926 | 4.5548 | 4.956 | 5.7583 | 6.5606 | 0.88023 | 2.3911 | 2.9989 | 2.9989 | 2.9989 | 2.9989 | 2.4959 | 3.168 | 3.168 | 3.168 | 3.168 | 3.168
2020-07-17 11:00 | Winter | 1.2003 | 1.8456 | 2.7928 | 2.7928 | 2.7928 | 2.7928 | 0.97168 | 0.97168 | 0.97168 | 0.97168 | 0.97168 | 0.97168 | 2.5911 | 3.7377 | 4.4888 | 4.8842 | 5.6749 | 6.4656 | 0.85355 | 2.3186 | 2.9081 | 2.9081 | 2.9081 | 2.9081 | 2.553 | 3.2405 | 3.2405 | 3.2405 | 3.2405 | 3.2405
2020-07-17 12:00 | Winter | 1.1813 | 1.8163 | 2.7485 | 2.7485 | 2.7485 | 2.7485 | 0.98025 | 0.98025 | 0.98025 | 0.98025 | 0.98025 | 0.98025 | 2.553 | 3.6827 | 4.4228 | 4.8123 | 5.5914 | 6.3705 | 0.85355 | 2.3186 | 2.9081 | 2.9081 | 2.9081 | 2.9081 | 2.4387 | 3.0954 | 3.0954 | 3.0954 | 3.0954 | 3.0954
2020-07-17 13:00 | Winter | 1.1622 | 1.787 | 2.7041 | 2.7041 | 2.7041 | 2.7041 | 0.95739 | 0.95739 | 0.95739 | 0.95739 | 0.95739 | 0.95739 | 2.6102 | 3.7651 | 4.5218 | 4.9201 | 5.7166 | 6.5131 | 0.88023 | 2.3911 | 2.9989 | 2.9989 | 2.9989 | 2.9989 | 2.4387 | 3.0954 | 3.0954 | 3.0954 | 3.0954 | 3.0954
2020-07-17 14:00 | Winter | 1.2384 | 1.9042 | 2.8814 | 2.8814 | 2.8814 | 2.8814 | 0.86308 | 0.86308 | 0.86308 | 0.86308 | 0.86308 | 0.86308 | 2.553 | 3.6827 | 4.4228 | 4.8123 | 5.5914 | 6.3705 | 0.89166 | 2.4221 | 3.0379 | 3.0379 | 3.0379 | 3.0379 | 2.2482 | 2.8536 | 2.8536 | 2.8536 | 2.8536 | 2.8536
2020-07-17 15:00 | Winter | 1.2194 | 1.8749 | 2.8371 | 2.8371 | 2.8371 | 2.8371 | 0.8545 | 0.8545 | 0.8545 | 0.8545 | 0.8545 | 0.8545 | 2.5149 | 3.6277 | 4.3568 | 4.7405 | 5.508 | 6.2754 | 0.94501 | 2.567 | 3.2196 | 3.2196 | 3.2196 | 3.2196 | 2.1514 | 2.7307 | 2.7307 | 2.7307 | 2.7307 | 2.7307
2020-07-17 16:00 | Winter | 1.2384 | 1.9042 | 2.8814 | 2.8814 | 2.8814 | 2.8814 | 0.87165 | 0.87165 | 0.87165 | 0.87165 | 0.87165 | 0.87165 | 2.4768 | 3.5728 | 4.2908 | 4.6687 | 5.4245 | 6.1803 | 0.99454 | 2.7016 | 3.3884 | 3.3884 | 3.3884 | 3.3884 | 2.0958 | 2.6601 | 2.6601 | 2.6601 | 2.6601 | 2.6601
2020-07-17 17:00 | Winter | 1.086 | 1.6698 | 2.5268 | 2.5268 | 2.5268 | 2.5268 | 0.90595 | 0.90595 | 0.90595 | 0.90595 | 0.90595 | 0.90595 | 2.6293 | 3.7926 | 4.5548 | 4.956 | 5.7583 | 6.5606 | 0.9069 | 2.4635 | 3.0898 | 3.0898 | 3.0898 | 3.0898 | 1.9184 | 2.435 | 2.435 | 2.435 | 2.435 | 2.435
2020-07-17 18:00 | Winter | 0.97258 | 1.4955 | 2.2629 | 2.2629 | 2.2629 | 2.2629 | 0.77162 | 0.77162 | 0.77162 | 0.77162 | 0.77162 | 0.77162 | 2.5149 | 3.6277 | 4.3568 | 4.7405 | 5.508 | 6.2754 | 0.94501 | 2.567 | 3.2196 | 3.2196 | 3.2196 | 3.2196 | 1.677 | 2.1286 | 2.1286 | 2.1286 | 2.1286 | 2.1286
2020-07-17 19:00 | Winter | 0.64779 | 0.99605 | 1.5072 | 1.5072 | 1.5072 | 1.5072 | 0.59365 | 0.59365 | 0.59365 | 0.59365 | 0.59365 | 0.59365 | 2.3764 | 3.4279 | 4.1169 | 4.4794 | 5.2046 | 5.9298 | 0.88023 | 2.3911 | 2.9989 | 2.9989 | 2.9989 | 2.9989 | 1.1277 | 1.4313 | 1.4313 | 1.4313 | 1.4313 | 1.4313
2020-07-17 20:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.59444 | 0.59444 | 0.59444 | 0.59444 | 0.59444 | 0.59444 | 2.3625 | 3.4079 | 4.0927 | 4.4532 | 5.1741 | 5.8951 | 0.84212 | 2.2875 | 2.8691 | 2.8691 | 2.8691 | 2.8691 | 1.082 | 1.3733 | 1.3733 | 1.3733 | 1.3733 | 1.3733
2020-07-17 21:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.60015 | 0.60015 | 0.60015 | 0.60015 | 0.60015 | 0.60015 | 2.2101 | 3.188 | 3.8287 | 4.1659 | 4.8403 | 5.5147 | 0.84593 | 2.2979 | 2.8821 | 2.8821 | 2.8821 | 2.8821 | 0.97168 | 1.2333 | 1.2333 | 1.2333 | 1.2333 | 1.2333
2020-07-17 22:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.5087 | 0.5087 | 0.5087 | 0.5087 | 0.5087 | 0.5087 | 2.0435 | 2.9477 | 3.5401 | 3.8519 | 4.4754 | 5.099 | 0.7621 | 2.0702 | 2.5965 | 2.5965 | 2.5965 | 2.5965 | 0.91714 | 1.1641 | 1.1641 | 1.1641 | 1.1641 | 1.1641
2020-07-17 23:00 | Winter | 0.58902 | 0.90569 | 1.3705 | 1.3705 | 1.3705 | 1.3705 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 1.9624 | 2.8307 | 3.3996 | 3.699 | 4.2979 | 4.8967 | 0.64101 | 1.7412 | 2.1839 | 2.1839 | 2.1839 | 2.1839 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-07-18 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 1.81 | 2.6109 | 3.1356 | 3.4117 | 3.9641 | 4.5164 | 0.5792 | 1.5733 | 1.9733 | 1.9733 | 1.9733 | 1.9733 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-07-18 01:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.38581 | 0.38581 | 0.38581 | 0.38581 | 0.38581 | 0.38581 | 1.6766 | 2.4185 | 2.9045 | 3.1603 | 3.672 | 4.1836 | 0.58301 | 1.5837 | 1.9863 | 1.9863 | 1.9863 | 1.9863 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-07-18 02:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 1.7338 | 2.5009 | 3.0036 | 3.2681 | 3.7972 | 4.3262 | 0.53728 | 1.4595 | 1.8305 | 1.8305 | 1.8305 | 1.8305 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-07-18 03:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.40296 | 0.40296 | 0.40296 | 0.40296 | 0.40296 | 0.40296 | 1.6576 | 2.391 | 2.8715 | 3.1244 | 3.6302 | 4.1361 | 0.51823 | 1.4077 | 1.7656 | 1.7656 | 1.7656 | 1.7656 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-07-18 04:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 1.7338 | 2.5009 | 3.0036 | 3.2681 | 3.7972 | 4.3262 | 0.5792 | 1.5733 | 1.9733 | 1.9733 | 1.9733 | 1.9733 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-07-18 05:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.49155 | 0.49155 | 0.49155 | 0.49155 | 0.49155 | 0.49155 | 1.7147 | 2.4735 | 2.9705 | 3.2322 | 3.7554 | 4.2787 | 0.5792 | 1.5733 | 1.9733 | 1.9733 | 1.9733 | 1.9733 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-07-18 06:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.5287 | 0.5287 | 0.5287 | 0.5287 | 0.5287 | 0.5287 | 1.81 | 2.6109 | 3.1356 | 3.4117 | 3.9641 | 4.5164 | 0.65922 | 1.7907 | 2.246 | 2.246 | 2.246 | 2.246 | 1.0479 | 1.3301 | 1.3301 | 1.3301 | 1.3301 | 1.3301
2020-07-18 07:00 | Winter | 0.64779 | 0.99605 | 1.5072 | 1.5072 | 1.5072 | 1.5072 | 0.60849 | 0.60849 | 0.60849 | 0.60849 | 0.60849 | 0.60849 | 1.9243 | 2.7758 | 3.3336 | 3.6272 | 4.2144 | 4.8016 | 0.70494 | 1.9149 | 2.4018 | 2.4018 | 2.4018 | 2.4018 | 1.0094 | 1.2812 | 1.2812 | 1.2812 | 1.2812 | 1.2812
2020-07-18 08:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.6173 | 0.6173 | 0.6173 | 0.6173 | 0.6173 | 0.6173 | 2.1237 | 3.0633 | 3.679 | 4.003 | 4.6511 | 5.2991 | 0.69732 | 1.8942 | 2.3758 | 2.3758 | 2.3758 | 2.3758 | 1.0098 | 1.2817 | 1.2817 | 1.2817 | 1.2817 | 1.2817
2020-07-18 09:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.60015 | 0.60015 | 0.60015 | 0.60015 | 0.60015 | 0.60015 | 2.172 | 3.133 | 3.7627 | 4.0941 | 4.7569 | 5.4197 | 0.76591 | 2.0805 | 2.6095 | 2.6095 | 2.6095 | 2.6095 | 1.0288 | 1.3059 | 1.3059 | 1.3059 | 1.3059 | 1.3059
2020-07-18 10:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.62587 | 0.62587 | 0.62587 | 0.62587 | 0.62587 | 0.62587 | 2.1529 | 3.1056 | 3.7297 | 4.0582 | 4.7151 | 5.3721 | 0.77353 | 2.1012 | 2.6354 | 2.6354 | 2.6354 | 2.6354 | 1.105 | 1.4026 | 1.4026 | 1.4026 | 1.4026 | 1.4026
2020-07-18 11:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.58586 | 0.58586 | 0.58586 | 0.58586 | 0.58586 | 0.58586 | 2.191 | 3.1605 | 3.7957 | 4.13 | 4.7986 | 5.4672 | 0.71637 | 1.946 | 2.4407 | 2.4407 | 2.4407 | 2.4407 | 1.1622 | 1.4752 | 1.4752 | 1.4752 | 1.4752 | 1.4752
2020-07-18 12:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.59444 | 0.59444 | 0.59444 | 0.59444 | 0.59444 | 0.59444 | 2.191 | 3.1605 | 3.7957 | 4.13 | 4.7986 | 5.4672 | 0.71256 | 1.9356 | 2.4277 | 2.4277 | 2.4277 | 2.4277 | 1.1241 | 1.4268 | 1.4268 | 1.4268 | 1.4268 | 1.4268
2020-07-18 13:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.54014 | 0.54014 | 0.54014 | 0.54014 | 0.54014 | 0.54014 | 2.1529 | 3.1056 | 3.7297 | 4.0582 | 4.7151 | 5.3721 | 0.70113 | 1.9046 | 2.3888 | 2.3888 | 2.3888 | 2.3888 | 1.086 | 1.3784 | 1.3784 | 1.3784 | 1.3784 | 1.3784
2020-07-18 14:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.53442 | 0.53442 | 0.53442 | 0.53442 | 0.53442 | 0.53442 | 2.1339 | 3.0781 | 3.6967 | 4.0223 | 4.6734 | 5.3246 | 0.67446 | 1.8321 | 2.2979 | 2.2979 | 2.2979 | 2.2979 | 1.086 | 1.3784 | 1.3784 | 1.3784 | 1.3784 | 1.3784
2020-07-18 15:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.56586 | 0.56586 | 0.56586 | 0.56586 | 0.56586 | 0.56586 | 2.1529 | 3.1056 | 3.7297 | 4.0582 | 4.7151 | 5.3721 | 0.67446 | 1.8321 | 2.2979 | 2.2979 | 2.2979 | 2.2979 | 1.0479 | 1.3301 | 1.3301 | 1.3301 | 1.3301 | 1.3301
2020-07-18 16:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.53728 | 0.53728 | 0.53728 | 0.53728 | 0.53728 | 0.53728 | 2.2101 | 3.188 | 3.8287 | 4.1659 | 4.8403 | 5.5147 | 0.70494 | 1.9149 | 2.4018 | 2.4018 | 2.4018 | 2.4018 | 0.99073 | 1.2575 | 1.2575 | 1.2575 | 1.2575 | 1.2575
2020-07-18 17:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.54014 | 0.54014 | 0.54014 | 0.54014 | 0.54014 | 0.54014 | 2.3244 | 3.3529 | 4.0267 | 4.3814 | 5.0907 | 5.8 | 0.81164 | 2.2047 | 2.7653 | 2.7653 | 2.7653 | 2.7653 | 1.1241 | 1.4268 | 1.4268 | 1.4268 | 1.4268 | 1.4268
2020-07-18 18:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.58586 | 0.58586 | 0.58586 | 0.58586 | 0.58586 | 0.58586 | 2.3244 | 3.3529 | 4.0267 | 4.3814 | 5.0907 | 5.8 | 0.85736 | 2.3289 | 2.9211 | 2.9211 | 2.9211 | 2.9211 | 1.105 | 1.4026 | 1.4026 | 1.4026 | 1.4026 | 1.4026
2020-07-18 19:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.52299 | 0.52299 | 0.52299 | 0.52299 | 0.52299 | 0.52299 | 2.2673 | 3.2705 | 3.9277 | 4.2736 | 4.9655 | 5.6574 | 0.80021 | 2.1737 | 2.7263 | 2.7263 | 2.7263 | 2.7263 | 1.0097 | 1.2816 | 1.2816 | 1.2816 | 1.2816 | 1.2816
2020-07-18 20:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.55443 | 0.55443 | 0.55443 | 0.55443 | 0.55443 | 0.55443 | 2.2291 | 3.2155 | 3.8617 | 4.2018 | 4.8821 | 5.5623 | 0.82688 | 2.2461 | 2.8172 | 2.8172 | 2.8172 | 2.8172 | 1.0479 | 1.3301 | 1.3301 | 1.3301 | 1.3301 | 1.3301
2020-07-18 21:00 | Winter | 0.55243 | 0.84943 | 1.2854 | 1.2854 | 1.2854 | 1.2854 | 0.51727 | 0.51727 | 0.51727 | 0.51727 | 0.51727 | 0.51727 | 2.1529 | 3.1056 | 3.7297 | 4.0582 | 4.7151 | 5.3721 | 0.77353 | 2.1012 | 2.6354 | 2.6354 | 2.6354 | 2.6354 | 1.0288 | 1.3059 | 1.3059 | 1.3059 | 1.3059 | 1.3059
2020-07-18 22:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 2.0196 | 2.9132 | 3.4986 | 3.8068 | 4.4231 | 5.0393 | 0.75829 | 2.0598 | 2.5835 | 2.5835 | 2.5835 | 2.5835 | 0.95263 | 1.2092 | 1.2092 | 1.2092 | 1.2092 | 1.2092
2020-07-18 23:00 | Winter | 0.5729 | 0.8809 | 1.333 | 1.333 | 1.333 | 1.333 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 1.8481 | 2.6658 | 3.2016 | 3.4836 | 4.0475 | 4.6115 | 0.68208 | 1.8528 | 2.3239 | 2.3239 | 2.3239 | 2.3239 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-07-19 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.41971 | 0.41971 | 0.41971 | 0.41971 | 0.41971 | 0.41971 | 1.7338 | 2.5009 | 3.0036 | 3.2681 | 3.7972 | 4.3262 | 0.58682 | 1.594 | 1.9993 | 1.9993 | 1.9993 | 1.9993 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-07-19 01:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 1.6576 | 2.391 | 2.8715 | 3.1244 | 3.6302 | 4.1361 | 0.54871 | 1.4905 | 1.8695 | 1.8695 | 1.8695 | 1.8695 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-07-19 02:00 | Winter | 0.58539 | 0.9001 | 1.362 | 1.362 | 1.362 | 1.362 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 1.6195 | 2.336 | 2.8055 | 3.0526 | 3.5468 | 4.041 | 0.54109 | 1.4698 | 1.8435 | 1.8435 | 1.8435 | 1.8435 | 0.91452 | 1.1608 | 1.1608 | 1.1608 | 1.1608 | 1.1608
2020-07-19 03:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.42296 | 0.42296 | 0.42296 | 0.42296 | 0.42296 | 0.42296 | 1.6004 | 2.3086 | 2.7725 | 3.0167 | 3.5051 | 3.9934 | 0.57539 | 1.563 | 1.9603 | 1.9603 | 1.9603 | 1.9603 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-07-19 04:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.4544 | 0.4544 | 0.4544 | 0.4544 | 0.4544 | 0.4544 | 1.6576 | 2.391 | 2.8715 | 3.1244 | 3.6302 | 4.1361 | 0.5792 | 1.5733 | 1.9733 | 1.9733 | 1.9733 | 1.9733 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-07-19 05:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.49727 | 0.49727 | 0.49727 | 0.49727 | 0.49727 | 0.49727 | 1.7147 | 2.4735 | 2.9705 | 3.2322 | 3.7554 | 4.2787 | 0.60206 | 1.6354 | 2.0512 | 2.0512 | 2.0512 | 2.0512 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-07-19 06:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 1.8672 | 2.6933 | 3.2346 | 3.5195 | 4.0892 | 4.659 | 0.6897 | 1.8735 | 2.3498 | 2.3498 | 2.3498 | 2.3498 | 0.95263 | 1.2092 | 1.2092 | 1.2092 | 1.2092 | 1.2092
2020-07-19 07:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.563 | 0.563 | 0.563 | 0.563 | 0.563 | 0.563 | 1.9815 | 2.8582 | 3.4326 | 3.735 | 4.3396 | 4.9443 | 0.72018 | 1.9563 | 2.4537 | 2.4537 | 2.4537 | 2.4537 | 0.97168 | 1.2333 | 1.2333 | 1.2333 | 1.2333 | 1.2333
2020-07-19 08:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.61444 | 0.61444 | 0.61444 | 0.61444 | 0.61444 | 0.61444 | 2.1529 | 3.1056 | 3.7297 | 4.0582 | 4.7151 | 5.3721 | 0.74686 | 2.0288 | 2.5446 | 2.5446 | 2.5446 | 2.5446 | 0.95263 | 1.2092 | 1.2092 | 1.2092 | 1.2092 | 1.2092
2020-07-19 09:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.57443 | 0.57443 | 0.57443 | 0.57443 | 0.57443 | 0.57443 | 2.1529 | 3.1056 | 3.7297 | 4.0582 | 4.7151 | 5.3721 | 0.76972 | 2.0909 | 2.6225 | 2.6225 | 2.6225 | 2.6225 | 0.95263 | 1.2092 | 1.2092 | 1.2092 | 1.2092 | 1.2092
2020-07-19 10:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.53728 | 0.53728 | 0.53728 | 0.53728 | 0.53728 | 0.53728 | 2.191 | 3.1605 | 3.7957 | 4.13 | 4.7986 | 5.4672 | 0.78877 | 2.1426 | 2.6874 | 2.6874 | 2.6874 | 2.6874 | 0.97168 | 1.2333 | 1.2333 | 1.2333 | 1.2333 | 1.2333
2020-07-19 11:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.54014 | 0.54014 | 0.54014 | 0.54014 | 0.54014 | 0.54014 | 2.1339 | 3.0781 | 3.6967 | 4.0223 | 4.6734 | 5.3246 | 0.64016 | 1.7389 | 2.1811 | 2.1811 | 2.1811 | 2.1811 | 0.93358 | 1.185 | 1.185 | 1.185 | 1.185 | 1.185
2020-07-19 12:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.52585 | 0.52585 | 0.52585 | 0.52585 | 0.52585 | 0.52585 | 2.0958 | 3.0231 | 3.6307 | 3.9504 | 4.59 | 5.2295 | 0.6173 | 1.6768 | 2.1032 | 2.1032 | 2.1032 | 2.1032 | 0.95263 | 1.2092 | 1.2092 | 1.2092 | 1.2092 | 1.2092
2020-07-19 13:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.57729 | 0.57729 | 0.57729 | 0.57729 | 0.57729 | 0.57729 | 2.1529 | 3.1056 | 3.7297 | 4.0582 | 4.7151 | 5.3721 | 0.61349 | 1.6665 | 2.0902 | 2.0902 | 2.0902 | 2.0902 | 0.9388 | 1.1916 | 1.1916 | 1.1916 | 1.1916 | 1.1916
2020-07-19 14:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.51156 | 0.51156 | 0.51156 | 0.51156 | 0.51156 | 0.51156 | 2.2291 | 3.2155 | 3.8617 | 4.2018 | 4.8821 | 5.5623 | 0.58301 | 1.5837 | 1.9863 | 1.9863 | 1.9863 | 1.9863 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-07-19 15:00 | Winter | 0.58434 | 0.89849 | 1.3596 | 1.3596 | 1.3596 | 1.3596 | 0.52585 | 0.52585 | 0.52585 | 0.52585 | 0.52585 | 0.52585 | 2.1148 | 3.0506 | 3.6637 | 3.9863 | 4.6317 | 5.277 | 0.62111 | 1.6872 | 2.1161 | 2.1161 | 2.1161 | 2.1161 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-07-19 16:00 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.53156 | 0.53156 | 0.53156 | 0.53156 | 0.53156 | 0.53156 | 2.1339 | 3.0781 | 3.6967 | 4.0223 | 4.6734 | 5.3246 | 0.62492 | 1.6975 | 2.1291 | 2.1291 | 2.1291 | 2.1291 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-07-19 17:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.52013 | 0.52013 | 0.52013 | 0.52013 | 0.52013 | 0.52013 | 2.2673 | 3.2705 | 3.9277 | 4.2736 | 4.9655 | 5.6574 | 0.70494 | 1.9149 | 2.4018 | 2.4018 | 2.4018 | 2.4018 | 0.91378 | 1.1598 | 1.1598 | 1.1598 | 1.1598 | 1.1598
2020-07-19 18:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.57729 | 0.57729 | 0.57729 | 0.57729 | 0.57729 | 0.57729 | 2.3054 | 3.3254 | 3.9937 | 4.3455 | 5.049 | 5.7525 | 0.76972 | 2.0909 | 2.6225 | 2.6225 | 2.6225 | 2.6225 | 0.93358 | 1.185 | 1.185 | 1.185 | 1.185 | 1.185
2020-07-19 19:00 | Winter | 0.55252 | 0.84957 | 1.2856 | 1.2856 | 1.2856 | 1.2856 | 0.55443 | 0.55443 | 0.55443 | 0.55443 | 0.55443 | 0.55443 | 2.1933 | 3.1638 | 3.7996 | 4.1342 | 4.8035 | 5.4728 | 0.73162 | 1.9874 | 2.4926 | 2.4926 | 2.4926 | 2.4926 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-07-19 20:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.48584 | 0.48584 | 0.48584 | 0.48584 | 0.48584 | 0.48584 | 2.191 | 3.1605 | 3.7957 | 4.13 | 4.7986 | 5.4672 | 0.74686 | 2.0288 | 2.5446 | 2.5446 | 2.5446 | 2.5446 | 0.91452 | 1.1608 | 1.1608 | 1.1608 | 1.1608 | 1.1608
2020-07-19 21:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 2.0721 | 2.9889 | 3.5896 | 3.9058 | 4.5381 | 5.1704 | 0.69351 | 1.8839 | 2.3628 | 2.3628 | 2.3628 | 2.3628 | 0.95263 | 1.2092 | 1.2092 | 1.2092 | 1.2092 | 1.2092
2020-07-19 22:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.39153 | 0.39153 | 0.39153 | 0.39153 | 0.39153 | 0.39153 | 2.0196 | 2.9132 | 3.4986 | 3.8068 | 4.4231 | 5.0393 | 0.65541 | 1.7803 | 2.233 | 2.233 | 2.233 | 2.233 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-07-19 23:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.39724 | 0.39724 | 0.39724 | 0.39724 | 0.39724 | 0.39724 | 1.81 | 2.6109 | 3.1356 | 3.4117 | 3.9641 | 4.5164 | 0.62873 | 1.7079 | 2.1421 | 2.1421 | 2.1421 | 2.1421 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-07-20 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.43154 | 0.43154 | 0.43154 | 0.43154 | 0.43154 | 0.43154 | 1.6957 | 2.446 | 2.9375 | 3.1963 | 3.7137 | 4.2311 | 0.56395 | 1.5319 | 1.9214 | 1.9214 | 1.9214 | 1.9214 | 0.91614 | 1.1628 | 1.1628 | 1.1628 | 1.1628 | 1.1628
2020-07-20 01:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.42296 | 0.42296 | 0.42296 | 0.42296 | 0.42296 | 0.42296 | 1.6576 | 2.391 | 2.8715 | 3.1244 | 3.6302 | 4.1361 | 0.5449 | 1.4802 | 1.8565 | 1.8565 | 1.8565 | 1.8565 | 0.93358 | 1.185 | 1.185 | 1.185 | 1.185 | 1.185
2020-07-20 02:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.5792 | 1.5733 | 1.9733 | 1.9733 | 1.9733 | 1.9733 | 1.086 | 1.3784 | 1.3784 | 1.3784 | 1.3784 | 1.3784
2020-07-20 03:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.41439 | 0.41439 | 0.41439 | 0.41439 | 0.41439 | 0.41439 | 1.6194 | 2.3359 | 2.8054 | 3.0524 | 3.5466 | 4.0408 | 0.56014 | 1.5216 | 1.9084 | 1.9084 | 1.9084 | 1.9084 | 1.086 | 1.3784 | 1.3784 | 1.3784 | 1.3784 | 1.3784
2020-07-20 04:00 | Winter | 0.64779 | 0.99605 | 1.5072 | 1.5072 | 1.5072 | 1.5072 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 1.7338 | 2.5009 | 3.0036 | 3.2681 | 3.7972 | 4.3262 | 0.57539 | 1.563 | 1.9603 | 1.9603 | 1.9603 | 1.9603 | 1.0669 | 1.3542 | 1.3542 | 1.3542 | 1.3542 | 1.3542
2020-07-20 05:00 | Winter | 0.81926 | 1.2597 | 1.9062 | 1.9062 | 1.9062 | 1.9062 | 0.63983 | 0.63983 | 0.63983 | 0.63983 | 0.63983 | 0.63983 | 1.9053 | 2.7483 | 3.3006 | 3.5913 | 4.1727 | 4.7541 | 0.72781 | 1.977 | 2.4796 | 2.4796 | 2.4796 | 2.4796 | 1.5023 | 1.9068 | 1.9068 | 1.9068 | 1.9068 | 1.9068
2020-07-20 06:00 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.76305 | 0.76305 | 0.76305 | 0.76305 | 0.76305 | 0.76305 | 2.1467 | 3.0965 | 3.7189 | 4.0464 | 4.7015 | 5.3565 | 0.77734 | 2.1116 | 2.6484 | 2.6484 | 2.6484 | 2.6484 | 1.9712 | 2.502 | 2.502 | 2.502 | 2.502 | 2.502
2020-07-20 07:00 | Winter | 1.2373 | 1.9024 | 2.8787 | 2.8787 | 2.8787 | 2.8787 | 0.93386 | 0.93386 | 0.93386 | 0.93386 | 0.93386 | 0.93386 | 2.3237 | 3.3518 | 4.0254 | 4.38 | 5.089 | 5.7981 | 0.84593 | 2.2979 | 2.8821 | 2.8821 | 2.8821 | 2.8821 | 2.3435 | 2.9745 | 2.9745 | 2.9745 | 2.9745 | 2.9745
2020-07-20 08:00 | Winter | 1.3527 | 2.08 | 3.1474 | 3.1474 | 3.1474 | 3.1474 | 1.0003 | 1.0003 | 1.0003 | 1.0003 | 1.0003 | 1.0003 | 2.6293 | 3.7926 | 4.5548 | 4.956 | 5.7583 | 6.5606 | 0.89166 | 2.4221 | 3.0379 | 3.0379 | 3.0379 | 3.0379 | 2.6293 | 3.3373 | 3.3373 | 3.3373 | 3.3373 | 3.3373
2020-07-20 09:00 | Winter | 1.3908 | 2.1386 | 3.2361 | 3.2361 | 3.2361 | 3.2361 | 1.0145 | 1.0145 | 1.0145 | 1.0145 | 1.0145 | 1.0145 | 2.7436 | 3.9575 | 4.7529 | 5.1715 | 6.0087 | 6.8459 | 0.91452 | 2.4842 | 3.1158 | 3.1158 | 3.1158 | 3.1158 | 2.7055 | 3.434 | 3.434 | 3.434 | 3.434 | 3.434
2020-07-20 10:00 | Winter | 1.2956 | 1.9921 | 3.0144 | 3.0144 | 3.0144 | 3.0144 | 1.026 | 1.026 | 1.026 | 1.026 | 1.026 | 1.026 | 2.6864 | 3.8751 | 4.6539 | 5.0637 | 5.8835 | 6.7033 | 0.92976 | 2.5256 | 3.1677 | 3.1677 | 3.1677 | 3.1677 | 2.7055 | 3.434 | 3.434 | 3.434 | 3.434 | 3.434
2020-07-20 11:00 | Winter | 1.2956 | 1.9921 | 3.0144 | 3.0144 | 3.0144 | 3.0144 | 1.0403 | 1.0403 | 1.0403 | 1.0403 | 1.0403 | 1.0403 | 2.6483 | 3.8201 | 4.5878 | 4.9919 | 5.8 | 6.6082 | 0.92595 | 2.5153 | 3.1547 | 3.1547 | 3.1547 | 3.1547 | 2.7436 | 3.4824 | 3.4824 | 3.4824 | 3.4824 | 3.4824
2020-07-20 12:00 | Winter | 1.2956 | 1.9921 | 3.0144 | 3.0144 | 3.0144 | 3.0144 | 0.95739 | 0.95739 | 0.95739 | 0.95739 | 0.95739 | 0.95739 | 2.6864 | 3.8751 | 4.6539 | 5.0637 | 5.8835 | 6.7033 | 0.85736 | 2.3289 | 2.9211 | 2.9211 | 2.9211 | 2.9211 | 2.553 | 3.2405 | 3.2405 | 3.2405 | 3.2405 | 3.2405
2020-07-20 13:00 | Winter | 1.2765 | 1.9628 | 2.9701 | 2.9701 | 2.9701 | 2.9701 | 1.006 | 1.006 | 1.006 | 1.006 | 1.006 | 1.006 | 2.6293 | 3.7926 | 4.5548 | 4.956 | 5.7583 | 6.5606 | 0.86879 | 2.36 | 2.96 | 2.96 | 2.96 | 2.96 | 2.5721 | 3.2647 | 3.2647 | 3.2647 | 3.2647 | 3.2647
2020-07-20 14:00 | Winter | 1.2575 | 1.9335 | 2.9258 | 2.9258 | 2.9258 | 2.9258 | 0.97168 | 0.97168 | 0.97168 | 0.97168 | 0.97168 | 0.97168 | 2.5911 | 3.7377 | 4.4888 | 4.8842 | 5.6749 | 6.4656 | 0.86117 | 2.3393 | 2.934 | 2.934 | 2.934 | 2.934 | 2.4053 | 3.053 | 3.053 | 3.053 | 3.053 | 3.053
2020-07-20 15:00 | Winter | 1.2575 | 1.9335 | 2.9258 | 2.9258 | 2.9258 | 2.9258 | 1.0231 | 1.0231 | 1.0231 | 1.0231 | 1.0231 | 1.0231 | 2.4768 | 3.5728 | 4.2908 | 4.6687 | 5.4245 | 6.1803 | 0.93357 | 2.536 | 3.1807 | 3.1807 | 3.1807 | 3.1807 | 2.3816 | 3.0229 | 3.0229 | 3.0229 | 3.0229 | 3.0229
2020-07-20 16:00 | Winter | 1.2384 | 1.9042 | 2.8814 | 2.8814 | 2.8814 | 2.8814 | 0.9974 | 0.9974 | 0.9974 | 0.9974 | 0.9974 | 0.9974 | 2.4586 | 3.5464 | 4.2592 | 4.6343 | 5.3846 | 6.1348 | 0.88404 | 2.4014 | 3.0119 | 3.0119 | 3.0119 | 3.0119 | 2.2673 | 2.8778 | 2.8778 | 2.8778 | 2.8778 | 2.8778
2020-07-20 17:00 | Winter | 1.1241 | 1.7284 | 2.6155 | 2.6155 | 2.6155 | 2.6155 | 0.94881 | 0.94881 | 0.94881 | 0.94881 | 0.94881 | 0.94881 | 2.6102 | 3.7651 | 4.5218 | 4.9201 | 5.7166 | 6.5131 | 0.87261 | 2.3704 | 2.973 | 2.973 | 2.973 | 2.973 | 2.191 | 2.781 | 2.781 | 2.781 | 2.781 | 2.781
2020-07-20 18:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.88315 | 0.88315 | 0.88315 | 0.88315 | 0.88315 | 0.88315 | 2.6864 | 3.8751 | 4.6539 | 5.0637 | 5.8835 | 6.7033 | 0.84212 | 2.2875 | 2.8691 | 2.8691 | 2.8691 | 2.8691 | 1.6685 | 2.1178 | 2.1178 | 2.1178 | 2.1178 | 2.1178
2020-07-20 19:00 | Winter | 0.70494 | 1.0839 | 1.6402 | 1.6402 | 1.6402 | 1.6402 | 0.64351 | 0.64351 | 0.64351 | 0.64351 | 0.64351 | 0.64351 | 2.5721 | 3.7102 | 4.4558 | 4.8483 | 5.6331 | 6.418 | 0.76591 | 2.0805 | 2.6095 | 2.6095 | 2.6095 | 2.6095 | 1.1609 | 1.4735 | 1.4735 | 1.4735 | 1.4735 | 1.4735
2020-07-20 20:00 | Winter | 0.64779 | 0.99605 | 1.5072 | 1.5072 | 1.5072 | 1.5072 | 0.47726 | 0.47726 | 0.47726 | 0.47726 | 0.47726 | 0.47726 | 2.4293 | 3.5042 | 4.2085 | 4.5791 | 5.3204 | 6.0618 | 0.7454 | 2.0248 | 2.5396 | 2.5396 | 2.5396 | 2.5396 | 1.0479 | 1.3301 | 1.3301 | 1.3301 | 1.3301 | 1.3301
2020-07-20 21:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 2.2513 | 3.2475 | 3.9001 | 4.2436 | 4.9306 | 5.6176 | 0.69732 | 1.8942 | 2.3758 | 2.3758 | 2.3758 | 2.3758 | 1.0098 | 1.2817 | 1.2817 | 1.2817 | 1.2817 | 1.2817
2020-07-20 22:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 2.0919 | 3.0175 | 3.6239 | 3.9431 | 4.5814 | 5.2198 | 0.68208 | 1.8528 | 2.3239 | 2.3239 | 2.3239 | 2.3239 | 0.89558 | 1.1367 | 1.1367 | 1.1367 | 1.1367 | 1.1367
2020-07-20 23:00 | Winter | 0.62791 | 0.96548 | 1.461 | 1.461 | 1.461 | 1.461 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 1.8481 | 2.6658 | 3.2016 | 3.4836 | 4.0475 | 4.6115 | 0.61349 | 1.6665 | 2.0902 | 2.0902 | 2.0902 | 2.0902 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-07-21 | Winter | 0.62873 | 0.96675 | 1.4629 | 1.4629 | 1.4629 | 1.4629 | 0.43154 | 0.43154 | 0.43154 | 0.43154 | 0.43154 | 0.43154 | 1.7338 | 2.5009 | 3.0036 | 3.2681 | 3.7972 | 4.3262 | 0.58301 | 1.5837 | 1.9863 | 1.9863 | 1.9863 | 1.9863 | 0.85737 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 1.0882
2020-07-21 01:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 1.6766 | 2.4185 | 2.9045 | 3.1603 | 3.672 | 4.1836 | 0.58301 | 1.5837 | 1.9863 | 1.9863 | 1.9863 | 1.9863 | 0.87642 | 1.1124 | 1.1124 | 1.1124 | 1.1124 | 1.1124
2020-07-21 02:00 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 1.5967 | 2.3032 | 2.7661 | 3.0097 | 3.497 | 3.9842 | 0.56395 | 1.5319 | 1.9214 | 1.9214 | 1.9214 | 1.9214 | 1.1048 | 1.4023 | 1.4023 | 1.4023 | 1.4023 | 1.4023
2020-07-21 03:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 1.5623 | 2.2536 | 2.7065 | 2.9449 | 3.4216 | 3.8984 | 0.60587 | 1.6458 | 2.0642 | 2.0642 | 2.0642 | 2.0642 | 1.105 | 1.4026 | 1.4026 | 1.4026 | 1.4026 | 1.4026
2020-07-21 04:00 | Winter | 0.66709 | 1.0257 | 1.5521 | 1.5521 | 1.5521 | 1.5521 | 0.49441 | 0.49441 | 0.49441 | 0.49441 | 0.49441 | 0.49441 | 1.6259 | 2.3454 | 2.8167 | 3.0648 | 3.561 | 4.0571 | 0.60587 | 1.6458 | 2.0642 | 2.0642 | 2.0642 | 2.0642 | 1.105 | 1.4026 | 1.4026 | 1.4026 | 1.4026 | 1.4026
2020-07-21 05:00 | Winter | 0.82502 | 1.2686 | 1.9196 | 1.9196 | 1.9196 | 1.9196 | 0.66303 | 0.66303 | 0.66303 | 0.66303 | 0.66303 | 0.66303 | 1.8481 | 2.6658 | 3.2016 | 3.4836 | 4.0475 | 4.6115 | 0.724 | 1.9667 | 2.4667 | 2.4667 | 2.4667 | 2.4667 | 1.4663 | 1.8612 | 1.8612 | 1.8612 | 1.8612 | 1.8612
2020-07-21 06:00 | Winter | 1.029 | 1.5823 | 2.3943 | 2.3943 | 2.3943 | 2.3943 | 0.78591 | 0.78591 | 0.78591 | 0.78591 | 0.78591 | 0.78591 | 2.172 | 3.133 | 3.7627 | 4.0941 | 4.7569 | 5.4197 | 0.77734 | 2.1116 | 2.6484 | 2.6484 | 2.6484 | 2.6484 | 1.8493 | 2.3473 | 2.3473 | 2.3473 | 2.3473 | 2.3473
2020-07-21 07:00 | Winter | 1.1622 | 1.787 | 2.7041 | 2.7041 | 2.7041 | 2.7041 | 0.92595 | 0.92595 | 0.92595 | 0.92595 | 0.92595 | 0.92595 | 2.4767 | 3.5726 | 4.2906 | 4.6685 | 5.4243 | 6.18 | 0.84212 | 2.2875 | 2.8691 | 2.8691 | 2.8691 | 2.8691 | 2.4123 | 3.0618 | 3.0618 | 3.0618 | 3.0618 | 3.0618
2020-07-21 08:00 | Winter | 1.3527 | 2.08 | 3.1474 | 3.1474 | 3.1474 | 3.1474 | 1.0346 | 1.0346 | 1.0346 | 1.0346 | 1.0346 | 1.0346 | 2.7055 | 3.9026 | 4.6869 | 5.0996 | 5.9252 | 6.7508 | 0.91452 | 2.4842 | 3.1158 | 3.1158 | 3.1158 | 3.1158 | 2.6674 | 3.3856 | 3.3856 | 3.3856 | 3.3856 | 3.3856
2020-07-21 09:00 | Winter | 1.3527 | 2.08 | 3.1474 | 3.1474 | 3.1474 | 3.1474 | 1.0803 | 1.0803 | 1.0803 | 1.0803 | 1.0803 | 1.0803 | 2.7245 | 3.93 | 4.7199 | 5.1356 | 5.967 | 6.7984 | 0.9069 | 2.4635 | 3.0898 | 3.0898 | 3.0898 | 3.0898 | 2.6674 | 3.3856 | 3.3856 | 3.3856 | 3.3856 | 3.3856
2020-07-21 10:00 | Winter | 1.3337 | 2.0507 | 3.1031 | 3.1031 | 3.1031 | 3.1031 | 1.0346 | 1.0346 | 1.0346 | 1.0346 | 1.0346 | 1.0346 | 2.6674 | 3.8476 | 4.6208 | 5.0278 | 5.8418 | 6.6557 | 0.89547 | 2.4325 | 3.0509 | 3.0509 | 3.0509 | 3.0509 | 2.6674 | 3.3856 | 3.3856 | 3.3856 | 3.3856 | 3.3856
2020-07-21 11:00 | Winter | 1.2765 | 1.9628 | 2.9701 | 2.9701 | 2.9701 | 2.9701 | 1.026 | 1.026 | 1.026 | 1.026 | 1.026 | 1.026 | 2.6293 | 3.7926 | 4.5548 | 4.956 | 5.7583 | 6.5606 | 0.81164 | 2.2047 | 2.7653 | 2.7653 | 2.7653 | 2.7653 | 2.6864 | 3.4098 | 3.4098 | 3.4098 | 3.4098 | 3.4098
2020-07-21 12:00 | Winter | 1.3146 | 2.0214 | 3.0588 | 3.0588 | 3.0588 | 3.0588 | 0.99168 | 0.99168 | 0.99168 | 0.99168 | 0.99168 | 0.99168 | 2.6293 | 3.7926 | 4.5548 | 4.956 | 5.7583 | 6.5606 | 0.85736 | 2.3289 | 2.9211 | 2.9211 | 2.9211 | 2.9211 | 2.553 | 3.2405 | 3.2405 | 3.2405 | 3.2405 | 3.2405
2020-07-21 13:00 | Winter | 1.3146 | 2.0214 | 3.0588 | 3.0588 | 3.0588 | 3.0588 | 1.0431 | 1.0431 | 1.0431 | 1.0431 | 1.0431 | 1.0431 | 2.6483 | 3.8201 | 4.5878 | 4.9919 | 5.8 | 6.6082 | 0.77734 | 2.1116 | 2.6484 | 2.6484 | 2.6484 | 2.6484 | 2.4768 | 3.1438 | 3.1438 | 3.1438 | 3.1438 | 3.1438
2020-07-21 14:00 | Winter | 1.2765 | 1.9628 | 2.9701 | 2.9701 | 2.9701 | 2.9701 | 0.94596 | 0.94596 | 0.94596 | 0.94596 | 0.94596 | 0.94596 | 2.5911 | 3.7377 | 4.4888 | 4.8842 | 5.6749 | 6.4656 | 0.81926 | 2.2254 | 2.7912 | 2.7912 | 2.7912 | 2.7912 | 2.4055 | 3.0532 | 3.0532 | 3.0532 | 3.0532 | 3.0532
2020-07-21 15:00 | Winter | 1.2765 | 1.9628 | 2.9701 | 2.9701 | 2.9701 | 2.9701 | 1.0031 | 1.0031 | 1.0031 | 1.0031 | 1.0031 | 1.0031 | 2.4959 | 3.6002 | 4.3238 | 4.7046 | 5.4662 | 6.2279 | 0.81545 | 2.2151 | 2.7782 | 2.7782 | 2.7782 | 2.7782 | 2.328 | 2.9549 | 2.9549 | 2.9549 | 2.9549 | 2.9549
2020-07-21 16:00 | Winter | 1.2575 | 1.9335 | 2.9258 | 2.9258 | 2.9258 | 2.9258 | 0.97739 | 0.97739 | 0.97739 | 0.97739 | 0.97739 | 0.97739 | 2.4387 | 3.5178 | 4.2248 | 4.5969 | 5.3411 | 6.0852 | 0.78877 | 2.1426 | 2.6874 | 2.6874 | 2.6874 | 2.6874 | 2.2863 | 2.902 | 2.902 | 2.902 | 2.902 | 2.902
2020-07-21 17:00 | Winter | 1.1622 | 1.787 | 2.7041 | 2.7041 | 2.7041 | 2.7041 | 0.90309 | 0.90309 | 0.90309 | 0.90309 | 0.90309 | 0.90309 | 2.553 | 3.6827 | 4.4228 | 4.8123 | 5.5914 | 6.3705 | 0.82688 | 2.2461 | 2.8172 | 2.8172 | 2.8172 | 2.8172 | 2.175 | 2.7607 | 2.7607 | 2.7607 | 2.7607 | 2.7607
2020-07-21 18:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.76877 | 0.76877 | 0.76877 | 0.76877 | 0.76877 | 0.76877 | 2.5721 | 3.7102 | 4.4558 | 4.8483 | 5.6331 | 6.418 | 0.82307 | 2.2358 | 2.8042 | 2.8042 | 2.8042 | 2.8042 | 1.7313 | 2.1975 | 2.1975 | 2.1975 | 2.1975 | 2.1975
2020-07-21 19:00 | Winter | 0.72451 | 1.114 | 1.6857 | 1.6857 | 1.6857 | 1.6857 | 0.563 | 0.563 | 0.563 | 0.563 | 0.563 | 0.563 | 2.3816 | 3.4353 | 4.1258 | 4.4891 | 5.2159 | 5.9426 | 0.73162 | 1.9874 | 2.4926 | 2.4926 | 2.4926 | 2.4926 | 1.2384 | 1.5719 | 1.5719 | 1.5719 | 1.5719 | 1.5719
2020-07-21 20:00 | Winter | 0.64779 | 0.99605 | 1.5072 | 1.5072 | 1.5072 | 1.5072 | 0.49727 | 0.49727 | 0.49727 | 0.49727 | 0.49727 | 0.49727 | 2.3054 | 3.3254 | 3.9937 | 4.3455 | 5.049 | 5.7525 | 0.71256 | 1.9356 | 2.4277 | 2.4277 | 2.4277 | 2.4277 | 1.086 | 1.3784 | 1.3784 | 1.3784 | 1.3784 | 1.3784
2020-07-21 21:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.49727 | 0.49727 | 0.49727 | 0.49727 | 0.49727 | 0.49727 | 2.2335 | 3.2217 | 3.8692 | 4.21 | 4.8916 | 5.5731 | 0.66684 | 1.8114 | 2.2719 | 2.2719 | 2.2719 | 2.2719 | 0.97168 | 1.2333 | 1.2333 | 1.2333 | 1.2333 | 1.2333
2020-07-21 22:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.46869 | 0.46869 | 0.46869 | 0.46869 | 0.46869 | 0.46869 | 1.9815 | 2.8582 | 3.4326 | 3.735 | 4.3396 | 4.9443 | 0.68589 | 1.8632 | 2.3368 | 2.3368 | 2.3368 | 2.3368 | 0.8765 | 1.1125 | 1.1125 | 1.1125 | 1.1125 | 1.1125
2020-07-21 23:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 1.777 | 2.5632 | 3.0784 | 3.3495 | 3.8917 | 4.434 | 0.55633 | 1.5112 | 1.8954 | 1.8954 | 1.8954 | 1.8954 | 0.93358 | 1.185 | 1.185 | 1.185 | 1.185 | 1.185
2020-07-22 | Winter | 0.57158 | 0.87887 | 1.3299 | 1.3299 | 1.3299 | 1.3299 | 0.4457 | 0.4457 | 0.4457 | 0.4457 | 0.4457 | 0.4457 | 1.6967 | 2.4475 | 2.9393 | 3.1982 | 3.716 | 4.2337 | 0.51823 | 1.4077 | 1.7656 | 1.7656 | 1.7656 | 1.7656 | 0.91452 | 1.1608 | 1.1608 | 1.1608 | 1.1608 | 1.1608
2020-07-22 01:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 1.6195 | 2.336 | 2.8055 | 3.0526 | 3.5468 | 4.041 | 0.53728 | 1.4595 | 1.8305 | 1.8305 | 1.8305 | 1.8305 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
2020-07-22 02:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 1.6004 | 2.3086 | 2.7725 | 3.0167 | 3.5051 | 3.9934 | 0.52204 | 1.4181 | 1.7786 | 1.7786 | 1.7786 | 1.7786 | 1.0479 | 1.3301 | 1.3301 | 1.3301 | 1.3301 | 1.3301
2020-07-22 03:00 | Winter | 0.59063 | 0.90816 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 1.5814 | 2.2811 | 2.7395 | 2.9808 | 3.4633 | 3.9459 | 0.52204 | 1.4181 | 1.7786 | 1.7786 | 1.7786 | 1.7786 | 1.086 | 1.3784 | 1.3784 | 1.3784 | 1.3784 | 1.3784
2020-07-22 04:00 | Winter | 0.60968 | 0.93746 | 1.4186 | 1.4186 | 1.4186 | 1.4186 | 0.55443 | 0.55443 | 0.55443 | 0.55443 | 0.55443 | 0.55443 | 1.6222 | 2.3399 | 2.8102 | 3.0577 | 3.5527 | 4.0477 | 0.54109 | 1.4698 | 1.8435 | 1.8435 | 1.8435 | 1.8435 | 1.157 | 1.4686 | 1.4686 | 1.4686 | 1.4686 | 1.4686
2020-07-22 05:00 | Winter | 0.81926 | 1.2597 | 1.9062 | 1.9062 | 1.9062 | 1.9062 | 0.60587 | 0.60587 | 0.60587 | 0.60587 | 0.60587 | 0.60587 | 1.8481 | 2.6658 | 3.2016 | 3.4836 | 4.0475 | 4.6115 | 0.66684 | 1.8114 | 2.2719 | 2.2719 | 2.2719 | 2.2719 | 1.448 | 1.8379 | 1.8379 | 1.8379 | 1.8379 | 1.8379
2020-07-22 06:00 | Winter | 0.91353 | 1.4047 | 2.1255 | 2.1255 | 2.1255 | 2.1255 | 0.77734 | 0.77734 | 0.77734 | 0.77734 | 0.77734 | 0.77734 | 2.191 | 3.1605 | 3.7957 | 4.13 | 4.7986 | 5.4672 | 0.73924 | 2.0081 | 2.5186 | 2.5186 | 2.5186 | 2.5186 | 1.8475 | 2.345 | 2.345 | 2.345 | 2.345 | 2.345
2020-07-22 07:00 | Winter | 1.1492 | 1.767 | 2.6738 | 2.6738 | 2.6738 | 2.6738 | 0.94596 | 0.94596 | 0.94596 | 0.94596 | 0.94596 | 0.94596 | 2.4485 | 3.5318 | 4.2416 | 4.6152 | 5.3624 | 6.1095 | 0.83831 | 2.2772 | 2.8561 | 2.8561 | 2.8561 | 2.8561 | 2.3625 | 2.9987 | 2.9987 | 2.9987 | 2.9987 | 2.9987
2020-07-22 08:00 | Winter | 1.3337 | 2.0507 | 3.1031 | 3.1031 | 3.1031 | 3.1031 | 1.0317 | 1.0317 | 1.0317 | 1.0317 | 1.0317 | 1.0317 | 2.6293 | 3.7926 | 4.5548 | 4.956 | 5.7583 | 6.5606 | 0.86117 | 2.3393 | 2.934 | 2.934 | 2.934 | 2.934 | 2.6674 | 3.3856 | 3.3856 | 3.3856 | 3.3856 | 3.3856
2020-07-22 09:00 | Winter | 1.3146 | 2.0214 | 3.0588 | 3.0588 | 3.0588 | 3.0588 | 1.086 | 1.086 | 1.086 | 1.086 | 1.086 | 1.086 | 2.7817 | 4.0125 | 4.8189 | 5.2433 | 6.0921 | 6.941 | 0.88023 | 2.3911 | 2.9989 | 2.9989 | 2.9989 | 2.9989 | 2.7436 | 3.4824 | 3.4824 | 3.4824 | 3.4824 | 3.4824
2020-07-22 10:00 | Winter | 1.2765 | 1.9628 | 2.9701 | 2.9701 | 2.9701 | 2.9701 | 1.0717 | 1.0717 | 1.0717 | 1.0717 | 1.0717 | 1.0717 | 2.6594 | 3.8362 | 4.6071 | 5.0129 | 5.8244 | 6.6359 | 0.83069 | 2.2565 | 2.8302 | 2.8302 | 2.8302 | 2.8302 | 2.6293 | 3.3373 | 3.3373 | 3.3373 | 3.3373 | 3.3373
2020-07-22 11:00 | Winter | 1.2765 | 1.9628 | 2.9701 | 2.9701 | 2.9701 | 2.9701 | 1.0174 | 1.0174 | 1.0174 | 1.0174 | 1.0174 | 1.0174 | 2.7055 | 3.9026 | 4.6869 | 5.0996 | 5.9252 | 6.7508 | 0.75067 | 2.0391 | 2.5575 | 2.5575 | 2.5575 | 2.5575 | 2.6483 | 3.3614 | 3.3614 | 3.3614 | 3.3614 | 3.3614
2020-07-22 12:00 | Winter | 1.2956 | 1.9921 | 3.0144 | 3.0144 | 3.0144 | 3.0144 | 0.97739 | 0.97739 | 0.97739 | 0.97739 | 0.97739 | 0.97739 | 2.5721 | 3.7102 | 4.4558 | 4.8483 | 5.6331 | 6.418 | 0.81545 | 2.2151 | 2.7782 | 2.7782 | 2.7782 | 2.7782 | 2.6102 | 3.3131 | 3.3131 | 3.3131 | 3.3131 | 3.3131
2020-07-22 13:00 | Winter | 1.2384 | 1.9042 | 2.8814 | 2.8814 | 2.8814 | 2.8814 | 1.0203 | 1.0203 | 1.0203 | 1.0203 | 1.0203 | 1.0203 | 2.6293 | 3.7926 | 4.5548 | 4.956 | 5.7583 | 6.5606 | 0.78115 | 2.1219 | 2.6614 | 2.6614 | 2.6614 | 2.6614 | 2.4768 | 3.1438 | 3.1438 | 3.1438 | 3.1438 | 3.1438
2020-07-22 14:00 | Winter | 1.2384 | 1.9042 | 2.8814 | 2.8814 | 2.8814 | 2.8814 | 1.0003 | 1.0003 | 1.0003 | 1.0003 | 1.0003 | 1.0003 | 2.553 | 3.6827 | 4.4228 | 4.8123 | 5.5914 | 6.3705 | 0.7621 | 2.0702 | 2.5965 | 2.5965 | 2.5965 | 2.5965 | 2.3816 | 3.0229 | 3.0229 | 3.0229 | 3.0229 | 3.0229
2020-07-22 15:00 | Winter | 2.4387 | 3.7498 | 5.6742 | 5.6742 | 5.6742 | 5.6742 | 0.91166 | 0.91166 | 0.91166 | 0.91166 | 0.91166 | 0.91166 | 2.5721 | 3.7102 | 4.4558 | 4.8483 | 5.6331 | 6.418 | 0.78496 | 2.1323 | 2.6744 | 2.6744 | 2.6744 | 2.6744 | 2.191 | 2.781 | 2.781 | 2.781 | 2.781 | 2.781
2020-07-22 16:00 | Winter | 2.0767 | 3.1932 | 4.832 | 4.832 | 4.832 | 4.832 | 0.91166 | 0.91166 | 0.91166 | 0.91166 | 0.91166 | 0.91166 | 2.5149 | 3.6277 | 4.3568 | 4.7405 | 5.508 | 6.2754 | 0.75448 | 2.0495 | 2.5705 | 2.5705 | 2.5705 | 2.5705 | 1.3146 | 1.6686 | 1.6686 | 1.6686 | 1.6686 | 1.6686
2020-07-22 17:00 | Winter | 2.0079 | 3.0874 | 4.6719 | 4.6719 | 4.6719 | 4.6719 | 0.89737 | 0.89737 | 0.89737 | 0.89737 | 0.89737 | 0.89737 | 2.4768 | 3.5728 | 4.2908 | 4.6687 | 5.4245 | 6.1803 | 0.78496 | 2.1323 | 2.6744 | 2.6744 | 2.6744 | 2.6744 | 1.2575 | 1.5961 | 1.5961 | 1.5961 | 1.5961 | 1.5961
2020-07-22 18:00 | Winter | 1.7719 | 2.7245 | 4.1227 | 4.1227 | 4.1227 | 4.1227 | 0.8888 | 0.8888 | 0.8888 | 0.8888 | 0.8888 | 0.8888 | 2.534 | 3.6552 | 4.3898 | 4.7764 | 5.5497 | 6.3229 | 0.71637 | 1.946 | 2.4407 | 2.4407 | 2.4407 | 2.4407 | 0.95278 | 1.2093 | 1.2093 | 1.2093 | 1.2093 | 1.2093
2020-07-22 19:00 | Winter | 1.1813 | 1.8163 | 2.7485 | 2.7485 | 2.7485 | 2.7485 | 0.69732 | 0.69732 | 0.69732 | 0.69732 | 0.69732 | 0.69732 | 2.458 | 3.5456 | 4.2581 | 4.6332 | 5.3832 | 6.1333 | 0.72781 | 1.977 | 2.4796 | 2.4796 | 2.4796 | 2.4796 | 0.78115 | 0.9915 | 0.9915 | 0.9915 | 0.9915 | 0.9915
2020-07-22 20:00 | Winter | 1.1813 | 1.8163 | 2.7485 | 2.7485 | 2.7485 | 2.7485 | 0.5087 | 0.5087 | 0.5087 | 0.5087 | 0.5087 | 0.5087 | 2.3435 | 3.3804 | 4.0597 | 4.4173 | 5.1324 | 5.8475 | 0.73162 | 1.9874 | 2.4926 | 2.4926 | 2.4926 | 2.4926 | 0.62873 | 0.79804 | 0.79804 | 0.79804 | 0.79804 | 0.79804
2020-07-22 21:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 2.172 | 3.133 | 3.7627 | 4.0941 | 4.7569 | 5.4197 | 0.68208 | 1.8528 | 2.3239 | 2.3239 | 2.3239 | 2.3239 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-07-22 22:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 2.0386 | 2.9407 | 3.5316 | 3.8427 | 4.4648 | 5.0869 | 0.63254 | 1.7182 | 2.1551 | 2.1551 | 2.1551 | 2.1551 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-07-22 23:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.39153 | 0.39153 | 0.39153 | 0.39153 | 0.39153 | 0.39153 | 1.8853 | 2.7195 | 3.266 | 3.5536 | 4.1289 | 4.7042 | 0.58682 | 1.594 | 1.9993 | 1.9993 | 1.9993 | 1.9993 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-07-23 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.39153 | 0.39153 | 0.39153 | 0.39153 | 0.39153 | 0.39153 | 1.7528 | 2.5284 | 3.0366 | 3.304 | 3.8389 | 4.3738 | 0.5449 | 1.4802 | 1.8565 | 1.8565 | 1.8565 | 1.8565 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-07-23 01:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 1.6195 | 2.336 | 2.8055 | 3.0526 | 3.5468 | 4.041 | 0.54871 | 1.4905 | 1.8695 | 1.8695 | 1.8695 | 1.8695 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-07-23 02:00 | Winter | 1.1241 | 1.7284 | 2.6155 | 2.6155 | 2.6155 | 2.6155 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.51442 | 1.3974 | 1.7526 | 1.7526 | 1.7526 | 1.7526 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-07-23 03:00 | Winter | 1.1622 | 1.787 | 2.7041 | 2.7041 | 2.7041 | 2.7041 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.54109 | 1.4698 | 1.8435 | 1.8435 | 1.8435 | 1.8435 | 0.49537 | 0.62876 | 0.62876 | 0.62876 | 0.62876 | 0.62876
2020-07-23 04:00 | Winter | 1.2373 | 1.9025 | 2.8788 | 2.8788 | 2.8788 | 2.8788 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 1.6766 | 2.4185 | 2.9045 | 3.1603 | 3.672 | 4.1836 | 0.52585 | 1.4284 | 1.7916 | 1.7916 | 1.7916 | 1.7916 | 0.55252 | 0.70131 | 0.70131 | 0.70131 | 0.70131 | 0.70131
2020-07-23 05:00 | Winter | 1.5126 | 2.3259 | 3.5195 | 3.5195 | 3.5195 | 3.5195 | 0.62873 | 0.62873 | 0.62873 | 0.62873 | 0.62873 | 0.62873 | 1.934 | 2.7897 | 3.3504 | 3.6455 | 4.2356 | 4.8258 | 0.68208 | 1.8528 | 2.3239 | 2.3239 | 2.3239 | 2.3239 | 0.74305 | 0.94314 | 0.94314 | 0.94314 | 0.94314 | 0.94314
2020-07-23 06:00 | Winter | 1.6938 | 2.6044 | 3.941 | 3.941 | 3.941 | 3.941 | 0.74305 | 0.74305 | 0.74305 | 0.74305 | 0.74305 | 0.74305 | 2.0767 | 2.9956 | 3.5977 | 3.9145 | 4.5482 | 5.182 | 0.75448 | 2.0495 | 2.5705 | 2.5705 | 2.5705 | 2.5705 | 0.99073 | 1.2575 | 1.2575 | 1.2575 | 1.2575 | 1.2575
2020-07-23 07:00 | Winter | 2.0767 | 3.1932 | 4.832 | 4.832 | 4.832 | 4.832 | 0.90309 | 0.90309 | 0.90309 | 0.90309 | 0.90309 | 0.90309 | 2.5376 | 3.6604 | 4.3961 | 4.7832 | 5.5576 | 6.3319 | 0.8345 | 2.2668 | 2.8432 | 2.8432 | 2.8432 | 2.8432 | 1.4289 | 1.8137 | 1.8137 | 1.8137 | 1.8137 | 1.8137
2020-07-23 08:00 | Winter | 2.3816 | 3.6619 | 5.5412 | 5.5412 | 5.5412 | 5.5412 | 1.1117 | 1.1117 | 1.1117 | 1.1117 | 1.1117 | 1.1117 | 2.7245 | 3.93 | 4.7199 | 5.1356 | 5.967 | 6.7984 | 0.84212 | 2.2875 | 2.8691 | 2.8691 | 2.8691 | 2.8691 | 1.6766 | 2.1281 | 2.1281 | 2.1281 | 2.1281 | 2.1281
2020-07-23 09:00 | Winter | 2.3816 | 3.6619 | 5.5412 | 5.5412 | 5.5412 | 5.5412 | 1.1022 | 1.1022 | 1.1022 | 1.1022 | 1.1022 | 1.1022 | 2.8198 | 4.0675 | 4.8849 | 5.3151 | 6.1756 | 7.0361 | 0.84974 | 2.3082 | 2.8951 | 2.8951 | 2.8951 | 2.8951 | 1.6957 | 2.1523 | 2.1523 | 2.1523 | 2.1523 | 2.1523
2020-07-23 10:00 | Winter | 2.3069 | 3.5472 | 5.3675 | 5.3675 | 5.3675 | 5.3675 | 1.1117 | 1.1117 | 1.1117 | 1.1117 | 1.1117 | 1.1117 | 2.8198 | 4.0675 | 4.8849 | 5.3151 | 6.1756 | 7.0361 | 0.84593 | 2.2979 | 2.8821 | 2.8821 | 2.8821 | 2.8821 | 1.7338 | 2.2007 | 2.2007 | 2.2007 | 2.2007 | 2.2007
2020-07-23 11:00 | Winter | 2.3054 | 3.5448 | 5.3639 | 5.3639 | 5.3639 | 5.3639 | 1.1089 | 1.1089 | 1.1089 | 1.1089 | 1.1089 | 1.1089 | 2.8769 | 4.1499 | 4.9839 | 5.4229 | 6.3008 | 7.1787 | 0.7964 | 2.1633 | 2.7133 | 2.7133 | 2.7133 | 2.7133 | 1.7338 | 2.2007 | 2.2007 | 2.2007 | 2.2007 | 2.2007
2020-07-23 12:00 | Winter | 2.191 | 3.369 | 5.0979 | 5.0979 | 5.0979 | 5.0979 | 1.0374 | 1.0374 | 1.0374 | 1.0374 | 1.0374 | 1.0374 | 2.7626 | 3.985 | 4.7859 | 5.2074 | 6.0504 | 6.8934 | 0.85736 | 2.3289 | 2.9211 | 2.9211 | 2.9211 | 2.9211 | 1.6195 | 2.0556 | 2.0556 | 2.0556 | 2.0556 | 2.0556
2020-07-23 13:00 | Winter | 2.191 | 3.369 | 5.0979 | 5.0979 | 5.0979 | 5.0979 | 1.0346 | 1.0346 | 1.0346 | 1.0346 | 1.0346 | 1.0346 | 2.7817 | 4.0125 | 4.8189 | 5.2433 | 6.0921 | 6.941 | 0.80021 | 2.1737 | 2.7263 | 2.7263 | 2.7263 | 2.7263 | 1.6195 | 2.0556 | 2.0556 | 2.0556 | 2.0556 | 2.0556
2020-07-23 14:00 | Winter | 2.2482 | 3.4569 | 5.2309 | 5.2309 | 5.2309 | 5.2309 | 1.0003 | 1.0003 | 1.0003 | 1.0003 | 1.0003 | 1.0003 | 2.7506 | 3.9676 | 4.765 | 5.1847 | 6.0241 | 6.8634 | 0.80783 | 2.1944 | 2.7523 | 2.7523 | 2.7523 | 2.7523 | 1.5052 | 1.9105 | 1.9105 | 1.9105 | 1.9105 | 1.9105
2020-07-23 15:00 | Winter | 2.1339 | 3.2811 | 4.9649 | 4.9649 | 4.9649 | 4.9649 | 0.90309 | 0.90309 | 0.90309 | 0.90309 | 0.90309 | 0.90309 | 2.6102 | 3.7651 | 4.5218 | 4.9201 | 5.7166 | 6.5131 | 0.82307 | 2.2358 | 2.8042 | 2.8042 | 2.8042 | 2.8042 | 1.4099 | 1.7895 | 1.7895 | 1.7895 | 1.7895 | 1.7895
2020-07-23 16:00 | Winter | 2.1339 | 3.2811 | 4.9649 | 4.9649 | 4.9649 | 4.9649 | 0.96596 | 0.96596 | 0.96596 | 0.96596 | 0.96596 | 0.96596 | 2.553 | 3.6827 | 4.4228 | 4.8123 | 5.5914 | 6.3705 | 0.82307 | 2.2358 | 2.8042 | 2.8042 | 2.8042 | 2.8042 | 1.3527 | 1.717 | 1.717 | 1.717 | 1.717 | 1.717
2020-07-23 17:00 | Winter | 2.0577 | 3.1639 | 4.7876 | 4.7876 | 4.7876 | 4.7876 | 0.96025 | 0.96025 | 0.96025 | 0.96025 | 0.96025 | 0.96025 | 2.6102 | 3.7651 | 4.5218 | 4.9201 | 5.7166 | 6.5131 | 0.82307 | 2.2358 | 2.8042 | 2.8042 | 2.8042 | 2.8042 | 1.2384 | 1.5719 | 1.5719 | 1.5719 | 1.5719 | 1.5719
2020-07-23 18:00 | Winter | 1.81 | 2.7831 | 4.2113 | 4.2113 | 4.2113 | 4.2113 | 0.89528 | 0.89528 | 0.89528 | 0.89528 | 0.89528 | 0.89528 | 2.6293 | 3.7926 | 4.5548 | 4.956 | 5.7583 | 6.5606 | 0.78115 | 2.1219 | 2.6614 | 2.6614 | 2.6614 | 2.6614 | 1.0669 | 1.3542 | 1.3542 | 1.3542 | 1.3542 | 1.3542
2020-07-23 19:00 | Winter | 1.1813 | 1.8163 | 2.7485 | 2.7485 | 2.7485 | 2.7485 | 0.68446 | 0.68446 | 0.68446 | 0.68446 | 0.68446 | 0.68446 | 2.5345 | 3.656 | 4.3908 | 4.7775 | 5.5509 | 6.3243 | 0.73162 | 1.9874 | 2.4926 | 2.4926 | 2.4926 | 2.4926 | 0.74305 | 0.94314 | 0.94314 | 0.94314 | 0.94314 | 0.94314
2020-07-23 20:00 | Winter | 1.086 | 1.6698 | 2.5268 | 2.5268 | 2.5268 | 2.5268 | 0.57157 | 0.57157 | 0.57157 | 0.57157 | 0.57157 | 0.57157 | 2.4197 | 3.4903 | 4.1918 | 4.561 | 5.2993 | 6.0377 | 0.68589 | 1.8632 | 2.3368 | 2.3368 | 2.3368 | 2.3368 | 0.70494 | 0.89477 | 0.89477 | 0.89477 | 0.89477 | 0.89477
2020-07-23 21:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.57157 | 0.57157 | 0.57157 | 0.57157 | 0.57157 | 0.57157 | 2.3374 | 3.3717 | 4.0493 | 4.4059 | 5.1192 | 5.8324 | 0.71256 | 1.9356 | 2.4277 | 2.4277 | 2.4277 | 2.4277 | 0.59063 | 0.74967 | 0.74967 | 0.74967 | 0.74967 | 0.74967
2020-07-23 22:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.5087 | 0.5087 | 0.5087 | 0.5087 | 0.5087 | 0.5087 | 2.1529 | 3.1056 | 3.7297 | 4.0582 | 4.7151 | 5.3721 | 0.62111 | 1.6872 | 2.1161 | 2.1161 | 2.1161 | 2.1161 | 0.57529 | 0.73021 | 0.73021 | 0.73021 | 0.73021 | 0.73021
2020-07-23 23:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.42582 | 0.42582 | 0.42582 | 0.42582 | 0.42582 | 0.42582 | 1.9624 | 2.8307 | 3.3996 | 3.699 | 4.2979 | 4.8967 | 0.56395 | 1.5319 | 1.9214 | 1.9214 | 1.9214 | 1.9214 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-07-24 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 1.81 | 2.6109 | 3.1356 | 3.4117 | 3.9641 | 4.5164 | 0.54871 | 1.4905 | 1.8695 | 1.8695 | 1.8695 | 1.8695 | 0.55252 | 0.70131 | 0.70131 | 0.70131 | 0.70131 | 0.70131
2020-07-24 01:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.4544 | 0.4544 | 0.4544 | 0.4544 | 0.4544 | 0.4544 | 1.7339 | 2.5011 | 3.0038 | 3.2683 | 3.7974 | 4.3265 | 0.55633 | 1.5112 | 1.8954 | 1.8954 | 1.8954 | 1.8954 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-07-24 02:00 | Winter | 1.1622 | 1.787 | 2.7041 | 2.7041 | 2.7041 | 2.7041 | 0.47726 | 0.47726 | 0.47726 | 0.47726 | 0.47726 | 0.47726 | 1.7519 | 2.5271 | 3.035 | 3.3023 | 3.8369 | 4.3715 | 0.5449 | 1.4802 | 1.8565 | 1.8565 | 1.8565 | 1.8565 | 0.55252 | 0.70131 | 0.70131 | 0.70131 | 0.70131 | 0.70131
2020-07-24 03:00 | Winter | 1.1438 | 1.7587 | 2.6613 | 2.6613 | 2.6613 | 2.6613 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 1.7528 | 2.5284 | 3.0366 | 3.304 | 3.8389 | 4.3738 | 0.52204 | 1.4181 | 1.7786 | 1.7786 | 1.7786 | 1.7786 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-07-24 04:00 | Winter | 1.2003 | 1.8456 | 2.7928 | 2.7928 | 2.7928 | 2.7928 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 1.7528 | 2.5284 | 3.0366 | 3.304 | 3.8389 | 4.3738 | 0.51955 | 1.4113 | 1.7701 | 1.7701 | 1.7701 | 1.7701 | 0.59095 | 0.75009 | 0.75009 | 0.75009 | 0.75009 | 0.75009
2020-07-24 05:00 | Winter | 1.5242 | 2.3436 | 3.5464 | 3.5464 | 3.5464 | 3.5464 | 0.60873 | 0.60873 | 0.60873 | 0.60873 | 0.60873 | 0.60873 | 1.9772 | 2.8521 | 3.4253 | 3.7269 | 4.3303 | 4.9337 | 0.724 | 1.9667 | 2.4667 | 2.4667 | 2.4667 | 2.4667 | 0.79903 | 1.0142 | 1.0142 | 1.0142 | 1.0142 | 1.0142
2020-07-24 06:00 | Winter | 1.6195 | 2.4901 | 3.768 | 3.768 | 3.768 | 3.768 | 0.72854 | 0.72854 | 0.72854 | 0.72854 | 0.72854 | 0.72854 | 2.3398 | 3.3751 | 4.0534 | 4.4104 | 5.1244 | 5.8384 | 0.76591 | 2.0805 | 2.6095 | 2.6095 | 2.6095 | 2.6095 | 1.1001 | 1.3963 | 1.3963 | 1.3963 | 1.3963 | 1.3963
2020-07-24 07:00 | Winter | 2.0577 | 3.1639 | 4.7876 | 4.7876 | 4.7876 | 4.7876 | 0.92836 | 0.92836 | 0.92836 | 0.92836 | 0.92836 | 0.92836 | 2.534 | 3.6552 | 4.3898 | 4.7764 | 5.5497 | 6.3229 | 0.84974 | 2.3082 | 2.8951 | 2.8951 | 2.8951 | 2.8951 | 1.3718 | 1.7412 | 1.7412 | 1.7412 | 1.7412 | 1.7412
2020-07-24 08:00 | Winter | 2.3816 | 3.6619 | 5.5412 | 5.5412 | 5.5412 | 5.5412 | 1.0231 | 1.0231 | 1.0231 | 1.0231 | 1.0231 | 1.0231 | 2.7626 | 3.985 | 4.7859 | 5.2074 | 6.0504 | 6.8934 | 0.91071 | 2.4739 | 3.1028 | 3.1028 | 3.1028 | 3.1028 | 1.5814 | 2.0072 | 2.0072 | 2.0072 | 2.0072 | 2.0072
2020-07-24 09:00 | Winter | 2.4006 | 3.6912 | 5.5856 | 5.5856 | 5.5856 | 5.5856 | 1.0346 | 1.0346 | 1.0346 | 1.0346 | 1.0346 | 1.0346 | 2.8769 | 4.1499 | 4.9839 | 5.4229 | 6.3008 | 7.1787 | 0.85107 | 2.3118 | 2.8996 | 2.8996 | 2.8996 | 2.8996 | 1.6385 | 2.0797 | 2.0797 | 2.0797 | 2.0797 | 2.0797
2020-07-24 10:00 | Winter | 2.2863 | 3.5155 | 5.3196 | 5.3196 | 5.3196 | 5.3196 | 1.126 | 1.126 | 1.126 | 1.126 | 1.126 | 1.126 | 2.7682 | 3.993 | 4.7955 | 5.2179 | 6.0626 | 6.9073 | 0.87261 | 2.3704 | 2.973 | 2.973 | 2.973 | 2.973 | 1.6195 | 2.0556 | 2.0556 | 2.0556 | 2.0556 | 2.0556
2020-07-24 11:00 | Winter | 2.2482 | 3.4569 | 5.2309 | 5.2309 | 5.2309 | 5.2309 | 1.0774 | 1.0774 | 1.0774 | 1.0774 | 1.0774 | 1.0774 | 2.7817 | 4.0125 | 4.8189 | 5.2433 | 6.0921 | 6.941 | 0.82688 | 2.2461 | 2.8172 | 2.8172 | 2.8172 | 2.8172 | 1.6195 | 2.0556 | 2.0556 | 2.0556 | 2.0556 | 2.0556
2020-07-24 12:00 | Winter | 2.2101 | 3.3983 | 5.1423 | 5.1423 | 5.1423 | 5.1423 | 1.0803 | 1.0803 | 1.0803 | 1.0803 | 1.0803 | 1.0803 | 2.7055 | 3.9026 | 4.6869 | 5.0996 | 5.9252 | 6.7508 | 0.86879 | 2.36 | 2.96 | 2.96 | 2.96 | 2.96 | 1.6195 | 2.0556 | 2.0556 | 2.0556 | 2.0556 | 2.0556
2020-07-24 13:00 | Winter | 2.191 | 3.369 | 5.0979 | 5.0979 | 5.0979 | 5.0979 | 1.0403 | 1.0403 | 1.0403 | 1.0403 | 1.0403 | 1.0403 | 2.6864 | 3.8751 | 4.6539 | 5.0637 | 5.8835 | 6.7033 | 0.77353 | 2.1012 | 2.6354 | 2.6354 | 2.6354 | 2.6354 | 1.5814 | 2.0072 | 2.0072 | 2.0072 | 2.0072 | 2.0072
2020-07-24 14:00 | Winter | 2.172 | 3.3397 | 5.0536 | 5.0536 | 5.0536 | 5.0536 | 0.98597 | 0.98597 | 0.98597 | 0.98597 | 0.98597 | 0.98597 | 2.6102 | 3.7651 | 4.5218 | 4.9201 | 5.7166 | 6.5131 | 0.79258 | 2.153 | 2.7003 | 2.7003 | 2.7003 | 2.7003 | 1.448 | 1.8379 | 1.8379 | 1.8379 | 1.8379 | 1.8379
2020-07-24 15:00 | Winter | 2.1529 | 3.3104 | 5.0093 | 5.0093 | 5.0093 | 5.0093 | 0.99709 | 0.99709 | 0.99709 | 0.99709 | 0.99709 | 0.99709 | 2.5721 | 3.7102 | 4.4558 | 4.8483 | 5.6331 | 6.418 | 0.7621 | 2.0702 | 2.5965 | 2.5965 | 2.5965 | 2.5965 | 1.3718 | 1.7412 | 1.7412 | 1.7412 | 1.7412 | 1.7412
2020-07-24 16:00 | Winter | 2.0386 | 3.1346 | 4.7433 | 4.7433 | 4.7433 | 4.7433 | 1.0003 | 1.0003 | 1.0003 | 1.0003 | 1.0003 | 1.0003 | 2.553 | 3.6827 | 4.4228 | 4.8123 | 5.5914 | 6.3705 | 0.82688 | 2.2461 | 2.8172 | 2.8172 | 2.8172 | 2.8172 | 1.3337 | 1.6928 | 1.6928 | 1.6928 | 1.6928 | 1.6928
2020-07-24 17:00 | Winter | 2.0005 | 3.076 | 4.6546 | 4.6546 | 4.6546 | 4.6546 | 0.99168 | 0.99168 | 0.99168 | 0.99168 | 0.99168 | 0.99168 | 2.5911 | 3.7377 | 4.4888 | 4.8842 | 5.6749 | 6.4656 | 0.85355 | 2.3186 | 2.9081 | 2.9081 | 2.9081 | 2.9081 | 1.2575 | 1.5961 | 1.5961 | 1.5961 | 1.5961 | 1.5961
2020-07-24 18:00 | Winter | 1.5408 | 2.3691 | 3.585 | 3.585 | 3.585 | 3.585 | 0.85282 | 0.85282 | 0.85282 | 0.85282 | 0.85282 | 0.85282 | 2.5607 | 3.6937 | 4.436 | 4.8267 | 5.6081 | 6.3895 | 0.85736 | 2.3289 | 2.9211 | 2.9211 | 2.9211 | 2.9211 | 0.95154 | 1.2078 | 1.2078 | 1.2078 | 1.2078 | 1.2078
2020-07-24 19:00 | Winter | 1.1632 | 1.7886 | 2.7065 | 2.7065 | 2.7065 | 2.7065 | 0.72435 | 0.72435 | 0.72435 | 0.72435 | 0.72435 | 0.72435 | 2.4578 | 3.5453 | 4.2578 | 4.6328 | 5.3828 | 6.1328 | 0.82688 | 2.2461 | 2.8172 | 2.8172 | 2.8172 | 2.8172 | 0.69923 | 0.88752 | 0.88752 | 0.88752 | 0.88752 | 0.88752
2020-07-24 20:00 | Winter | 1.1241 | 1.7284 | 2.6155 | 2.6155 | 2.6155 | 2.6155 | 0.66017 | 0.66017 | 0.66017 | 0.66017 | 0.66017 | 0.66017 | 2.3625 | 3.4079 | 4.0927 | 4.4532 | 5.1741 | 5.8951 | 0.75067 | 2.0391 | 2.5575 | 2.5575 | 2.5575 | 2.5575 | 0.66684 | 0.84641 | 0.84641 | 0.84641 | 0.84641 | 0.84641
2020-07-24 21:00 | Winter | 1.0669 | 1.6405 | 2.4825 | 2.4825 | 2.4825 | 2.4825 | 0.65159 | 0.65159 | 0.65159 | 0.65159 | 0.65159 | 0.65159 | 2.3054 | 3.3254 | 3.9937 | 4.3455 | 5.049 | 5.7525 | 0.75448 | 2.0495 | 2.5705 | 2.5705 | 2.5705 | 2.5705 | 0.60968 | 0.77386 | 0.77386 | 0.77386 | 0.77386 | 0.77386
2020-07-24 22:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.64016 | 0.64016 | 0.64016 | 0.64016 | 0.64016 | 0.64016 | 2.191 | 3.1605 | 3.7957 | 4.13 | 4.7986 | 5.4672 | 0.7964 | 2.1633 | 2.7133 | 2.7133 | 2.7133 | 2.7133 | 0.59063 | 0.74967 | 0.74967 | 0.74967 | 0.74967 | 0.74967
2020-07-24 23:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.51442 | 0.51442 | 0.51442 | 0.51442 | 0.51442 | 0.51442 | 1.9053 | 2.7483 | 3.3006 | 3.5913 | 4.1727 | 4.7541 | 0.6173 | 1.6768 | 2.1032 | 2.1032 | 2.1032 | 2.1032 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-07-25 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 1.829 | 2.6383 | 3.1686 | 3.4477 | 4.0058 | 4.5639 | 0.57539 | 1.563 | 1.9603 | 1.9603 | 1.9603 | 1.9603 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-07-25 01:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 1.6576 | 2.391 | 2.8715 | 3.1244 | 3.6302 | 4.1361 | 0.55633 | 1.5112 | 1.8954 | 1.8954 | 1.8954 | 1.8954 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-07-25 02:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.48869 | 0.48869 | 0.48869 | 0.48869 | 0.48869 | 0.48869 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.5449 | 1.4802 | 1.8565 | 1.8565 | 1.8565 | 1.8565 | 0.49568 | 0.62916 | 0.62916 | 0.62916 | 0.62916 | 0.62916
2020-07-25 03:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.47441 | 0.47441 | 0.47441 | 0.47441 | 0.47441 | 0.47441 | 1.6699 | 2.4088 | 2.8929 | 3.1476 | 3.6572 | 4.1668 | 0.53728 | 1.4595 | 1.8305 | 1.8305 | 1.8305 | 1.8305 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-07-25 04:00 | Winter | 1.0042 | 1.5441 | 2.3365 | 2.3365 | 2.3365 | 2.3365 | 0.50298 | 0.50298 | 0.50298 | 0.50298 | 0.50298 | 0.50298 | 1.7147 | 2.4735 | 2.9705 | 3.2322 | 3.7554 | 4.2787 | 0.52966 | 1.4388 | 1.8046 | 1.8046 | 1.8046 | 1.8046 | 0.47627 | 0.60452 | 0.60452 | 0.60452 | 0.60452 | 0.60452
2020-07-25 05:00 | Winter | 1.0288 | 1.582 | 2.3938 | 2.3938 | 2.3938 | 2.3938 | 0.56586 | 0.56586 | 0.56586 | 0.56586 | 0.56586 | 0.56586 | 1.81 | 2.6109 | 3.1356 | 3.4117 | 3.9641 | 4.5164 | 0.62111 | 1.6872 | 2.1161 | 2.1161 | 2.1161 | 2.1161 | 0.47619 | 0.60442 | 0.60442 | 0.60442 | 0.60442 | 0.60442
2020-07-25 06:00 | Winter | 1.105 | 1.6991 | 2.5711 | 2.5711 | 2.5711 | 2.5711 | 0.54585 | 0.54585 | 0.54585 | 0.54585 | 0.54585 | 0.54585 | 2.0386 | 2.9407 | 3.5316 | 3.8427 | 4.4648 | 5.0869 | 0.59825 | 1.6251 | 2.0382 | 2.0382 | 2.0382 | 2.0382 | 0.53613 | 0.68049 | 0.68049 | 0.68049 | 0.68049 | 0.68049
2020-07-25 07:00 | Winter | 1.1432 | 1.7577 | 2.6598 | 2.6598 | 2.6598 | 2.6598 | 0.65445 | 0.65445 | 0.65445 | 0.65445 | 0.65445 | 0.65445 | 1.9815 | 2.8582 | 3.4326 | 3.735 | 4.3396 | 4.9443 | 0.67065 | 1.8218 | 2.2849 | 2.2849 | 2.2849 | 2.2849 | 0.59063 | 0.74967 | 0.74967 | 0.74967 | 0.74967 | 0.74967
2020-07-25 08:00 | Winter | 1.1432 | 1.7577 | 2.6598 | 2.6598 | 2.6598 | 2.6598 | 0.66874 | 0.66874 | 0.66874 | 0.66874 | 0.66874 | 0.66874 | 2.2673 | 3.2705 | 3.9277 | 4.2736 | 4.9655 | 5.6574 | 0.70113 | 1.9046 | 2.3888 | 2.3888 | 2.3888 | 2.3888 | 0.74279 | 0.94281 | 0.94281 | 0.94281 | 0.94281 | 0.94281
2020-07-25 09:00 | Winter | 1.105 | 1.6991 | 2.5711 | 2.5711 | 2.5711 | 2.5711 | 0.6916 | 0.6916 | 0.6916 | 0.6916 | 0.6916 | 0.6916 | 2.3816 | 3.4353 | 4.1258 | 4.4891 | 5.2159 | 5.9426 | 0.72781 | 1.977 | 2.4796 | 2.4796 | 2.4796 | 2.4796 | 0.80021 | 1.0157 | 1.0157 | 1.0157 | 1.0157 | 1.0157
2020-07-25 10:00 | Winter | 1.0885 | 1.6736 | 2.5325 | 2.5325 | 2.5325 | 2.5325 | 0.6373 | 0.6373 | 0.6373 | 0.6373 | 0.6373 | 0.6373 | 2.3435 | 3.3804 | 4.0597 | 4.4173 | 5.1324 | 5.8475 | 0.69351 | 1.8839 | 2.3628 | 2.3628 | 2.3628 | 2.3628 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
2020-07-25 11:00 | Winter | 1.105 | 1.6991 | 2.5711 | 2.5711 | 2.5711 | 2.5711 | 0.62587 | 0.62587 | 0.62587 | 0.62587 | 0.62587 | 0.62587 | 2.3435 | 3.3804 | 4.0597 | 4.4173 | 5.1324 | 5.8475 | 0.68208 | 1.8528 | 2.3239 | 2.3239 | 2.3239 | 2.3239 | 0.78115 | 0.9915 | 0.9915 | 0.9915 | 0.9915 | 0.9915
2020-07-25 12:00 | Winter | 1.0669 | 1.6405 | 2.4825 | 2.4825 | 2.4825 | 2.4825 | 0.61158 | 0.61158 | 0.61158 | 0.61158 | 0.61158 | 0.61158 | 2.2649 | 3.267 | 3.9236 | 4.2691 | 4.9603 | 5.6514 | 0.71256 | 1.9356 | 2.4277 | 2.4277 | 2.4277 | 2.4277 | 0.78115 | 0.9915 | 0.9915 | 0.9915 | 0.9915 | 0.9915
2020-07-25 13:00 | Winter | 1.1622 | 1.787 | 2.7041 | 2.7041 | 2.7041 | 2.7041 | 0.58872 | 0.58872 | 0.58872 | 0.58872 | 0.58872 | 0.58872 | 2.2291 | 3.2155 | 3.8617 | 4.2018 | 4.8821 | 5.5623 | 0.70494 | 1.9149 | 2.4018 | 2.4018 | 2.4018 | 2.4018 | 0.74305 | 0.94314 | 0.94314 | 0.94314 | 0.94314 | 0.94314
2020-07-25 14:00 | Winter | 1.086 | 1.6698 | 2.5268 | 2.5268 | 2.5268 | 2.5268 | 0.61444 | 0.61444 | 0.61444 | 0.61444 | 0.61444 | 0.61444 | 2.2291 | 3.2155 | 3.8617 | 4.2018 | 4.8821 | 5.5623 | 0.71256 | 1.9356 | 2.4277 | 2.4277 | 2.4277 | 2.4277 | 0.724 | 0.91895 | 0.91895 | 0.91895 | 0.91895 | 0.91895
2020-07-25 15:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 0.60301 | 0.60301 | 0.60301 | 0.60301 | 0.60301 | 0.60301 | 2.2863 | 3.2979 | 3.9607 | 4.3096 | 5.0072 | 5.7049 | 0.67827 | 1.8425 | 2.3109 | 2.3109 | 2.3109 | 2.3109 | 0.68589 | 0.87059 | 0.87059 | 0.87059 | 0.87059 | 0.87059
2020-07-25 16:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 0.54871 | 0.54871 | 0.54871 | 0.54871 | 0.54871 | 0.54871 | 2.2863 | 3.2979 | 3.9607 | 4.3096 | 5.0072 | 5.7049 | 0.7621 | 2.0702 | 2.5965 | 2.5965 | 2.5965 | 2.5965 | 0.62873 | 0.79804 | 0.79804 | 0.79804 | 0.79804 | 0.79804
2020-07-25 17:00 | Winter | 1.0854 | 1.6689 | 2.5254 | 2.5254 | 2.5254 | 2.5254 | 0.52585 | 0.52585 | 0.52585 | 0.52585 | 0.52585 | 0.52585 | 2.38 | 3.4331 | 4.123 | 4.4861 | 5.2124 | 5.9386 | 0.84212 | 2.2875 | 2.8691 | 2.8691 | 2.8691 | 2.8691 | 0.64779 | 0.82222 | 0.82222 | 0.82222 | 0.82222 | 0.82222
2020-07-25 18:00 | Winter | 1.1432 | 1.7577 | 2.6598 | 2.6598 | 2.6598 | 2.6598 | 0.6716 | 0.6716 | 0.6716 | 0.6716 | 0.6716 | 0.6716 | 2.3816 | 3.4353 | 4.1258 | 4.4891 | 5.2159 | 5.9426 | 0.86498 | 2.3496 | 2.947 | 2.947 | 2.947 | 2.947 | 0.66684 | 0.84641 | 0.84641 | 0.84641 | 0.84641 | 0.84641
2020-07-25 19:00 | Winter | 1.1241 | 1.7284 | 2.6155 | 2.6155 | 2.6155 | 2.6155 | 0.55443 | 0.55443 | 0.55443 | 0.55443 | 0.55443 | 0.55443 | 2.4197 | 3.4903 | 4.1918 | 4.561 | 5.2993 | 6.0377 | 0.81164 | 2.2047 | 2.7653 | 2.7653 | 2.7653 | 2.7653 | 0.70494 | 0.89477 | 0.89477 | 0.89477 | 0.89477 | 0.89477
2020-07-25 20:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.49727 | 0.49727 | 0.49727 | 0.49727 | 0.49727 | 0.49727 | 2.2482 | 3.243 | 3.8947 | 4.2377 | 4.9238 | 5.6098 | 0.76972 | 2.0909 | 2.6225 | 2.6225 | 2.6225 | 2.6225 | 0.64779 | 0.82222 | 0.82222 | 0.82222 | 0.82222 | 0.82222
2020-07-25 21:00 | Winter | 1.0288 | 1.582 | 2.3938 | 2.3938 | 2.3938 | 2.3938 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 2.1339 | 3.0781 | 3.6967 | 4.0223 | 4.6734 | 5.3246 | 0.76591 | 2.0805 | 2.6095 | 2.6095 | 2.6095 | 2.6095 | 0.60968 | 0.77386 | 0.77386 | 0.77386 | 0.77386 | 0.77386
2020-07-25 22:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 1.9967 | 2.8801 | 3.459 | 3.7636 | 4.3729 | 4.9822 | 0.67446 | 1.8321 | 2.2979 | 2.2979 | 2.2979 | 2.2979 | 0.57158 | 0.72549 | 0.72549 | 0.72549 | 0.72549 | 0.72549
2020-07-25 23:00 | Winter | 0.97105 | 1.4931 | 2.2594 | 2.2594 | 2.2594 | 2.2594 | 0.41439 | 0.41439 | 0.41439 | 0.41439 | 0.41439 | 0.41439 | 1.9054 | 2.7485 | 3.3009 | 3.5916 | 4.1731 | 4.7545 | 0.65541 | 1.7803 | 2.233 | 2.233 | 2.233 | 2.233 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-07-26 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.42572 | 0.42572 | 0.42572 | 0.42572 | 0.42572 | 0.42572 | 1.7909 | 2.5834 | 3.1026 | 3.3758 | 3.9223 | 4.4688 | 0.58301 | 1.5837 | 1.9863 | 1.9863 | 1.9863 | 1.9863 | 0.55252 | 0.70131 | 0.70131 | 0.70131 | 0.70131 | 0.70131
2020-07-26 01:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.43154 | 0.43154 | 0.43154 | 0.43154 | 0.43154 | 0.43154 | 1.6201 | 2.3369 | 2.8065 | 3.0537 | 3.5481 | 4.0425 | 0.5449 | 1.4802 | 1.8565 | 1.8565 | 1.8565 | 1.8565 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-07-26 02:00 | Winter | 0.9624 | 1.4798 | 2.2392 | 2.2392 | 2.2392 | 2.2392 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 1.5814 | 2.2811 | 2.7395 | 2.9808 | 3.4633 | 3.9459 | 0.53728 | 1.4595 | 1.8305 | 1.8305 | 1.8305 | 1.8305 | 0.49537 | 0.62876 | 0.62876 | 0.62876 | 0.62876 | 0.62876
2020-07-26 03:00 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 1.5433 | 2.2261 | 2.6735 | 2.909 | 3.3799 | 3.8508 | 0.52966 | 1.4388 | 1.8046 | 1.8046 | 1.8046 | 1.8046 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-07-26 04:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.40582 | 0.40582 | 0.40582 | 0.40582 | 0.40582 | 0.40582 | 1.5623 | 2.2536 | 2.7065 | 2.9449 | 3.4216 | 3.8984 | 0.52966 | 1.4388 | 1.8046 | 1.8046 | 1.8046 | 1.8046 | 0.49161 | 0.62399 | 0.62399 | 0.62399 | 0.62399 | 0.62399
2020-07-26 05:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 1.7147 | 2.4735 | 2.9705 | 3.2322 | 3.7554 | 4.2787 | 0.53728 | 1.4595 | 1.8305 | 1.8305 | 1.8305 | 1.8305 | 0.49537 | 0.62876 | 0.62876 | 0.62876 | 0.62876 | 0.62876
2020-07-26 06:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 1.8672 | 2.6933 | 3.2346 | 3.5195 | 4.0892 | 4.659 | 0.57539 | 1.563 | 1.9603 | 1.9603 | 1.9603 | 1.9603 | 0.51435 | 0.65286 | 0.65286 | 0.65286 | 0.65286 | 0.65286
2020-07-26 07:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.52585 | 0.52585 | 0.52585 | 0.52585 | 0.52585 | 0.52585 | 1.8468 | 2.664 | 3.1994 | 3.4812 | 4.0448 | 4.6083 | 0.57539 | 1.563 | 1.9603 | 1.9603 | 1.9603 | 1.9603 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-07-26 08:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.54871 | 0.54871 | 0.54871 | 0.54871 | 0.54871 | 0.54871 | 2.1339 | 3.0781 | 3.6967 | 4.0223 | 4.6734 | 5.3246 | 0.68589 | 1.8632 | 2.3368 | 2.3368 | 2.3368 | 2.3368 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-07-26 09:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.58586 | 0.58586 | 0.58586 | 0.58586 | 0.58586 | 0.58586 | 2.3054 | 3.3254 | 3.9937 | 4.3455 | 5.049 | 5.7525 | 0.67065 | 1.8218 | 2.2849 | 2.2849 | 2.2849 | 2.2849 | 0.57158 | 0.72549 | 0.72549 | 0.72549 | 0.72549 | 0.72549
2020-07-26 10:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.57729 | 0.57729 | 0.57729 | 0.57729 | 0.57729 | 0.57729 | 2.3054 | 3.3254 | 3.9937 | 4.3455 | 5.049 | 5.7525 | 0.66684 | 1.8114 | 2.2719 | 2.2719 | 2.2719 | 2.2719 | 0.60968 | 0.77386 | 0.77386 | 0.77386 | 0.77386 | 0.77386
2020-07-26 11:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 0.55443 | 0.55443 | 0.55443 | 0.55443 | 0.55443 | 0.55443 | 2.3625 | 3.4079 | 4.0927 | 4.4532 | 5.1741 | 5.8951 | 0.66303 | 1.8011 | 2.2589 | 2.2589 | 2.2589 | 2.2589 | 0.60968 | 0.77386 | 0.77386 | 0.77386 | 0.77386 | 0.77386
2020-07-26 12:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.56586 | 0.56586 | 0.56586 | 0.56586 | 0.56586 | 0.56586 | 2.3625 | 3.4079 | 4.0927 | 4.4532 | 5.1741 | 5.8951 | 0.66684 | 1.8114 | 2.2719 | 2.2719 | 2.2719 | 2.2719 | 0.59044 | 0.74943 | 0.74943 | 0.74943 | 0.74943 | 0.74943
2020-07-26 13:00 | Winter | 1.0003 | 1.5381 | 2.3275 | 2.3275 | 2.3275 | 2.3275 | 0.5287 | 0.5287 | 0.5287 | 0.5287 | 0.5287 | 0.5287 | 2.3435 | 3.3804 | 4.0597 | 4.4173 | 5.1324 | 5.8475 | 0.58682 | 1.594 | 1.9993 | 1.9993 | 1.9993 | 1.9993 | 0.59063 | 0.74967 | 0.74967 | 0.74967 | 0.74967 | 0.74967
2020-07-26 14:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.53728 | 0.53728 | 0.53728 | 0.53728 | 0.53728 | 0.53728 | 2.3625 | 3.4079 | 4.0927 | 4.4532 | 5.1741 | 5.8951 | 0.62111 | 1.6872 | 2.1161 | 2.1161 | 2.1161 | 2.1161 | 0.57158 | 0.72549 | 0.72549 | 0.72549 | 0.72549 | 0.72549
2020-07-26 15:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.52585 | 0.52585 | 0.52585 | 0.52585 | 0.52585 | 0.52585 | 2.2482 | 3.243 | 3.8947 | 4.2377 | 4.9238 | 5.6098 | 0.62492 | 1.6975 | 2.1291 | 2.1291 | 2.1291 | 2.1291 | 0.55252 | 0.70131 | 0.70131 | 0.70131 | 0.70131 | 0.70131
2020-07-26 16:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.51156 | 0.51156 | 0.51156 | 0.51156 | 0.51156 | 0.51156 | 2.2863 | 3.2979 | 3.9607 | 4.3096 | 5.0072 | 5.7049 | 0.62873 | 1.7079 | 2.1421 | 2.1421 | 2.1421 | 2.1421 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-07-26 17:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 0.56586 | 0.56586 | 0.56586 | 0.56586 | 0.56586 | 0.56586 | 2.4578 | 3.5453 | 4.2578 | 4.6328 | 5.3828 | 6.1328 | 0.70494 | 1.9149 | 2.4018 | 2.4018 | 2.4018 | 2.4018 | 0.59063 | 0.74967 | 0.74967 | 0.74967 | 0.74967 | 0.74967
2020-07-26 18:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 0.563 | 0.563 | 0.563 | 0.563 | 0.563 | 0.563 | 2.4145 | 3.4829 | 4.1828 | 4.5512 | 5.288 | 6.0248 | 0.71256 | 1.9356 | 2.4277 | 2.4277 | 2.4277 | 2.4277 | 0.55252 | 0.70131 | 0.70131 | 0.70131 | 0.70131 | 0.70131
2020-07-26 19:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.563 | 0.563 | 0.563 | 0.563 | 0.563 | 0.563 | 2.3054 | 3.3254 | 3.9937 | 4.3455 | 5.049 | 5.7525 | 0.69351 | 1.8839 | 2.3628 | 2.3628 | 2.3628 | 2.3628 | 0.55252 | 0.70131 | 0.70131 | 0.70131 | 0.70131 | 0.70131
2020-07-26 20:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.48869 | 0.48869 | 0.48869 | 0.48869 | 0.48869 | 0.48869 | 2.2482 | 3.243 | 3.8947 | 4.2377 | 4.9238 | 5.6098 | 0.67827 | 1.8425 | 2.3109 | 2.3109 | 2.3109 | 2.3109 | 0.53567 | 0.67991 | 0.67991 | 0.67991 | 0.67991 | 0.67991
2020-07-26 21:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 2.1217 | 3.0605 | 3.6755 | 3.9992 | 4.6467 | 5.2941 | 0.68208 | 1.8528 | 2.3239 | 2.3239 | 2.3239 | 2.3239 | 0.55252 | 0.70131 | 0.70131 | 0.70131 | 0.70131 | 0.70131
2020-07-26 22:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.42582 | 0.42582 | 0.42582 | 0.42582 | 0.42582 | 0.42582 | 2.0196 | 2.9132 | 3.4986 | 3.8068 | 4.4231 | 5.0393 | 0.62873 | 1.7079 | 2.1421 | 2.1421 | 2.1421 | 2.1421 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-07-26 23:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.41153 | 0.41153 | 0.41153 | 0.41153 | 0.41153 | 0.41153 | 1.8481 | 2.6658 | 3.2016 | 3.4836 | 4.0475 | 4.6115 | 0.58682 | 1.594 | 1.9993 | 1.9993 | 1.9993 | 1.9993 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-07-27 | Winter | 0.99054 | 1.5231 | 2.3047 | 2.3047 | 2.3047 | 2.3047 | 0.39437 | 0.39437 | 0.39437 | 0.39437 | 0.39437 | 0.39437 | 1.7149 | 2.4737 | 2.9709 | 3.2325 | 3.7558 | 4.2791 | 0.52204 | 1.4181 | 1.7786 | 1.7786 | 1.7786 | 1.7786 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-07-27 01:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.42582 | 0.42582 | 0.42582 | 0.42582 | 0.42582 | 0.42582 | 1.6195 | 2.336 | 2.8055 | 3.0526 | 3.5468 | 4.041 | 0.52204 | 1.4181 | 1.7786 | 1.7786 | 1.7786 | 1.7786 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-07-27 02:00 | Winter | 1.2194 | 1.8749 | 2.8371 | 2.8371 | 2.8371 | 2.8371 | 0.46869 | 0.46869 | 0.46869 | 0.46869 | 0.46869 | 0.46869 | 1.6195 | 2.336 | 2.8055 | 3.0526 | 3.5468 | 4.041 | 0.49918 | 1.356 | 1.7007 | 1.7007 | 1.7007 | 1.7007 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-07-27 03:00 | Winter | 1.1617 | 1.7862 | 2.7029 | 2.7029 | 2.7029 | 2.7029 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 1.6195 | 2.336 | 2.8055 | 3.0526 | 3.5468 | 4.041 | 0.49155 | 1.3353 | 1.6747 | 1.6747 | 1.6747 | 1.6747 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-07-27 04:00 | Winter | 1.1813 | 1.8163 | 2.7485 | 2.7485 | 2.7485 | 2.7485 | 0.49155 | 0.49155 | 0.49155 | 0.49155 | 0.49155 | 0.49155 | 1.7528 | 2.5284 | 3.0366 | 3.304 | 3.8389 | 4.3738 | 0.53347 | 1.4491 | 1.8175 | 1.8175 | 1.8175 | 1.8175 | 0.51019 | 0.64758 | 0.64758 | 0.64758 | 0.64758 | 0.64758
2020-07-27 05:00 | Winter | 1.3575 | 2.0873 | 3.1585 | 3.1585 | 3.1585 | 3.1585 | 0.58015 | 0.58015 | 0.58015 | 0.58015 | 0.58015 | 0.58015 | 1.9232 | 2.7742 | 3.3318 | 3.6252 | 4.2121 | 4.799 | 0.64779 | 1.7596 | 2.207 | 2.207 | 2.207 | 2.207 | 0.74281 | 0.94283 | 0.94283 | 0.94283 | 0.94283 | 0.94283
2020-07-27 06:00 | Winter | 1.6665 | 2.5624 | 3.8774 | 3.8774 | 3.8774 | 3.8774 | 0.71447 | 0.71447 | 0.71447 | 0.71447 | 0.71447 | 0.71447 | 2.1424 | 3.0904 | 3.7115 | 4.0384 | 4.6922 | 5.3459 | 0.75067 | 2.0391 | 2.5575 | 2.5575 | 2.5575 | 2.5575 | 1.0159 | 1.2895 | 1.2895 | 1.2895 | 1.2895 | 1.2895
2020-07-27 07:00 | Winter | 2.1933 | 3.3725 | 5.1032 | 5.1032 | 5.1032 | 5.1032 | 0.83164 | 0.83164 | 0.83164 | 0.83164 | 0.83164 | 0.83164 | 2.3936 | 3.4528 | 4.1467 | 4.5119 | 5.2423 | 5.9727 | 0.80021 | 2.1737 | 2.7263 | 2.7263 | 2.7263 | 2.7263 | 1.3527 | 1.717 | 1.717 | 1.717 | 1.717 | 1.717
2020-07-27 08:00 | Winter | 2.3816 | 3.6619 | 5.5412 | 5.5412 | 5.5412 | 5.5412 | 0.98597 | 0.98597 | 0.98597 | 0.98597 | 0.98597 | 0.98597 | 2.553 | 3.6827 | 4.4228 | 4.8123 | 5.5914 | 6.3705 | 0.89166 | 2.4221 | 3.0379 | 3.0379 | 3.0379 | 3.0379 | 1.5052 | 1.9105 | 1.9105 | 1.9105 | 1.9105 | 1.9105
2020-07-27 09:00 | Winter | 2.4197 | 3.7205 | 5.6299 | 5.6299 | 5.6299 | 5.6299 | 0.98597 | 0.98597 | 0.98597 | 0.98597 | 0.98597 | 0.98597 | 2.7055 | 3.9026 | 4.6869 | 5.0996 | 5.9252 | 6.7508 | 0.8345 | 2.2668 | 2.8432 | 2.8432 | 2.8432 | 2.8432 | 1.5814 | 2.0072 | 2.0072 | 2.0072 | 2.0072 | 2.0072
2020-07-27 10:00 | Winter | 2.3054 | 3.5448 | 5.3639 | 5.3639 | 5.3639 | 5.3639 | 1.0374 | 1.0374 | 1.0374 | 1.0374 | 1.0374 | 1.0374 | 2.8007 | 4.04 | 4.8519 | 5.2792 | 6.1339 | 6.9885 | 0.86117 | 2.3393 | 2.934 | 2.934 | 2.934 | 2.934 | 1.6385 | 2.0797 | 2.0797 | 2.0797 | 2.0797 | 2.0797
2020-07-27 11:00 | Winter | 2.4006 | 3.6912 | 5.5856 | 5.5856 | 5.5856 | 5.5856 | 0.96882 | 0.96882 | 0.96882 | 0.96882 | 0.96882 | 0.96882 | 2.7626 | 3.985 | 4.7859 | 5.2074 | 6.0504 | 6.8934 | 0.84974 | 2.3082 | 2.8951 | 2.8951 | 2.8951 | 2.8951 | 1.6385 | 2.0797 | 2.0797 | 2.0797 | 2.0797 | 2.0797
2020-07-27 12:00 | Winter | 2.4197 | 3.7205 | 5.6299 | 5.6299 | 5.6299 | 5.6299 | 1.0803 | 1.0803 | 1.0803 | 1.0803 | 1.0803 | 1.0803 | 2.8866 | 4.1638 | 5.0006 | 5.441 | 6.3218 | 7.2027 | 0.84212 | 2.2875 | 2.8691 | 2.8691 | 2.8691 | 2.8691 | 1.6576 | 2.1039 | 2.1039 | 2.1039 | 2.1039 | 2.1039
2020-07-27 13:00 | Winter | 2.3054 | 3.5448 | 5.3639 | 5.3639 | 5.3639 | 5.3639 | 1.1346 | 1.1346 | 1.1346 | 1.1346 | 1.1346 | 1.1346 | 2.896 | 4.1774 | 5.0169 | 5.4588 | 6.3425 | 7.2262 | 0.78877 | 2.1426 | 2.6874 | 2.6874 | 2.6874 | 2.6874 | 1.6385 | 2.0797 | 2.0797 | 2.0797 | 2.0797 | 2.0797
2020-07-27 14:00 | Winter | 2.3435 | 3.6034 | 5.4526 | 5.4526 | 5.4526 | 5.4526 | 1.166 | 1.166 | 1.166 | 1.166 | 1.166 | 1.166 | 2.7436 | 3.9575 | 4.7529 | 5.1715 | 6.0087 | 6.8459 | 0.86498 | 2.3496 | 2.947 | 2.947 | 2.947 | 2.947 | 1.5242 | 1.9346 | 1.9346 | 1.9346 | 1.9346 | 1.9346
2020-07-27 15:00 | Winter | 2.2863 | 3.5155 | 5.3196 | 5.3196 | 5.3196 | 5.3196 | 1.1203 | 1.1203 | 1.1203 | 1.1203 | 1.1203 | 1.1203 | 2.6674 | 3.8476 | 4.6208 | 5.0278 | 5.8418 | 6.6557 | 0.84212 | 2.2875 | 2.8691 | 2.8691 | 2.8691 | 2.8691 | 1.448 | 1.8379 | 1.8379 | 1.8379 | 1.8379 | 1.8379
2020-07-27 16:00 | Winter | 2.191 | 3.369 | 5.0979 | 5.0979 | 5.0979 | 5.0979 | 1.0831 | 1.0831 | 1.0831 | 1.0831 | 1.0831 | 1.0831 | 2.7817 | 4.0125 | 4.8189 | 5.2433 | 6.0921 | 6.941 | 0.83831 | 2.2772 | 2.8561 | 2.8561 | 2.8561 | 2.8561 | 1.3908 | 1.7654 | 1.7654 | 1.7654 | 1.7654 | 1.7654
2020-07-27 17:00 | Winter | 2.0767 | 3.1932 | 4.832 | 4.832 | 4.832 | 4.832 | 1.126 | 1.126 | 1.126 | 1.126 | 1.126 | 1.126 | 2.7817 | 4.0125 | 4.8189 | 5.2433 | 6.0921 | 6.941 | 0.85355 | 2.3186 | 2.9081 | 2.9081 | 2.9081 | 2.9081 | 1.2956 | 1.6444 | 1.6444 | 1.6444 | 1.6444 | 1.6444
2020-07-27 18:00 | Winter | 1.5743 | 2.4207 | 3.663 | 3.663 | 3.663 | 3.663 | 0.92595 | 0.92595 | 0.92595 | 0.92595 | 0.92595 | 0.92595 | 2.7245 | 3.93 | 4.7199 | 5.1356 | 5.967 | 6.7984 | 0.78115 | 2.1219 | 2.6614 | 2.6614 | 2.6614 | 2.6614 | 0.9411 | 1.1945 | 1.1945 | 1.1945 | 1.1945 | 1.1945
2020-07-27 19:00 | Winter | 1.1813 | 1.8163 | 2.7485 | 2.7485 | 2.7485 | 2.7485 | 0.57157 | 0.57157 | 0.57157 | 0.57157 | 0.57157 | 0.57157 | 2.5914 | 3.738 | 4.4892 | 4.8846 | 5.6754 | 6.4662 | 0.75829 | 2.0598 | 2.5835 | 2.5835 | 2.5835 | 2.5835 | 0.6609 | 0.83886 | 0.83886 | 0.83886 | 0.83886 | 0.83886
2020-07-27 20:00 | Winter | 1.1241 | 1.7284 | 2.6155 | 2.6155 | 2.6155 | 2.6155 | 0.54585 | 0.54585 | 0.54585 | 0.54585 | 0.54585 | 0.54585 | 2.4387 | 3.5178 | 4.2248 | 4.5969 | 5.3411 | 6.0852 | 0.70494 | 1.9149 | 2.4018 | 2.4018 | 2.4018 | 2.4018 | 0.66684 | 0.84641 | 0.84641 | 0.84641 | 0.84641 | 0.84641
2020-07-27 21:00 | Winter | 1.0099 | 1.5528 | 2.3497 | 2.3497 | 2.3497 | 2.3497 | 0.48012 | 0.48012 | 0.48012 | 0.48012 | 0.48012 | 0.48012 | 2.3054 | 3.3254 | 3.9937 | 4.3455 | 5.049 | 5.7525 | 0.6516 | 1.77 | 2.22 | 2.22 | 2.22 | 2.22 | 0.55252 | 0.70131 | 0.70131 | 0.70131 | 0.70131 | 0.70131
2020-07-27 22:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.52585 | 0.52585 | 0.52585 | 0.52585 | 0.52585 | 0.52585 | 2.1148 | 3.0506 | 3.6637 | 3.9863 | 4.6317 | 5.277 | 0.65541 | 1.7803 | 2.233 | 2.233 | 2.233 | 2.233 | 0.49555 | 0.62899 | 0.62899 | 0.62899 | 0.62899 | 0.62899
2020-07-27 23:00 | Winter | 1.0093 | 1.5519 | 2.3483 | 2.3483 | 2.3483 | 2.3483 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 1.8681 | 2.6947 | 3.2362 | 3.5212 | 4.0913 | 4.6613 | 0.58301 | 1.5837 | 1.9863 | 1.9863 | 1.9863 | 1.9863 | 0.49537 | 0.62876 | 0.62876 | 0.62876 | 0.62876 | 0.62876
2020-07-28 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.43439 | 0.43439 | 0.43439 | 0.43439 | 0.43439 | 0.43439 | 1.7528 | 2.5284 | 3.0366 | 3.304 | 3.8389 | 4.3738 | 0.53347 | 1.4491 | 1.8175 | 1.8175 | 1.8175 | 1.8175 | 0.46997 | 0.59652 | 0.59652 | 0.59652 | 0.59652 | 0.59652
2020-07-28 01:00 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.52585 | 1.4284 | 1.7916 | 1.7916 | 1.7916 | 1.7916 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-07-28 02:00 | Winter | 1.1622 | 1.787 | 2.7041 | 2.7041 | 2.7041 | 2.7041 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 1.6957 | 2.446 | 2.9375 | 3.1963 | 3.7137 | 4.2311 | 0.55633 | 1.5112 | 1.8954 | 1.8954 | 1.8954 | 1.8954 | 0.53309 | 0.67664 | 0.67664 | 0.67664 | 0.67664 | 0.67664
2020-07-28 03:00 | Winter | 1.1432 | 1.7577 | 2.6598 | 2.6598 | 2.6598 | 2.6598 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 1.644 | 2.3714 | 2.8479 | 3.0988 | 3.6004 | 4.1021 | 0.50657 | 1.3761 | 1.7259 | 1.7259 | 1.7259 | 1.7259 | 0.55252 | 0.70131 | 0.70131 | 0.70131 | 0.70131 | 0.70131
2020-07-28 04:00 | Winter | 1.1622 | 1.787 | 2.7041 | 2.7041 | 2.7041 | 2.7041 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 1.7147 | 2.4735 | 2.9705 | 3.2322 | 3.7554 | 4.2787 | 0.5792 | 1.5733 | 1.9733 | 1.9733 | 1.9733 | 1.9733 | 0.53775 | 0.68256 | 0.68256 | 0.68256 | 0.68256 | 0.68256
2020-07-28 05:00 | Winter | 1.3569 | 2.0864 | 3.1571 | 3.1571 | 3.1571 | 3.1571 | 0.56014 | 0.56014 | 0.56014 | 0.56014 | 0.56014 | 0.56014 | 1.9244 | 2.776 | 3.3339 | 3.6275 | 4.2147 | 4.802 | 0.69351 | 1.8839 | 2.3628 | 2.3628 | 2.3628 | 2.3628 | 0.77764 | 0.98705 | 0.98705 | 0.98705 | 0.98705 | 0.98705
2020-07-28 06:00 | Winter | 1.6874 | 2.5946 | 3.9262 | 3.9262 | 3.9262 | 3.9262 | 0.69992 | 0.69992 | 0.69992 | 0.69992 | 0.69992 | 0.69992 | 2.2579 | 3.257 | 3.9116 | 4.2561 | 4.9451 | 5.6341 | 0.73924 | 2.0081 | 2.5186 | 2.5186 | 2.5186 | 2.5186 | 0.97168 | 1.2333 | 1.2333 | 1.2333 | 1.2333 | 1.2333
2020-07-28 07:00 | Winter | 2.0955 | 3.2221 | 4.8756 | 4.8756 | 4.8756 | 4.8756 | 0.87451 | 0.87451 | 0.87451 | 0.87451 | 0.87451 | 0.87451 | 2.4578 | 3.5453 | 4.2578 | 4.6328 | 5.3828 | 6.1328 | 0.81164 | 2.2047 | 2.7653 | 2.7653 | 2.7653 | 2.7653 | 1.3337 | 1.6928 | 1.6928 | 1.6928 | 1.6928 | 1.6928
2020-07-28 08:00 | Winter | 2.2482 | 3.4569 | 5.2309 | 5.2309 | 5.2309 | 5.2309 | 0.91452 | 0.91452 | 0.91452 | 0.91452 | 0.91452 | 0.91452 | 2.6102 | 3.7651 | 4.5218 | 4.9201 | 5.7166 | 6.5131 | 0.93738 | 2.5463 | 3.1937 | 3.1937 | 3.1937 | 3.1937 | 1.467 | 1.8621 | 1.8621 | 1.8621 | 1.8621 | 1.8621
2020-07-28 09:00 | Winter | 2.2863 | 3.5155 | 5.3196 | 5.3196 | 5.3196 | 5.3196 | 0.96025 | 0.96025 | 0.96025 | 0.96025 | 0.96025 | 0.96025 | 2.7245 | 3.93 | 4.7199 | 5.1356 | 5.967 | 6.7984 | 0.88404 | 2.4014 | 3.0119 | 3.0119 | 3.0119 | 3.0119 | 1.4861 | 1.8863 | 1.8863 | 1.8863 | 1.8863 | 1.8863
2020-07-28 10:00 | Winter | 2.2291 | 3.4276 | 5.1866 | 5.1866 | 5.1866 | 5.1866 | 1.1174 | 1.1174 | 1.1174 | 1.1174 | 1.1174 | 1.1174 | 2.7245 | 3.93 | 4.7199 | 5.1356 | 5.967 | 6.7984 | 0.92214 | 2.5049 | 3.1418 | 3.1418 | 3.1418 | 3.1418 | 1.5052 | 1.9105 | 1.9105 | 1.9105 | 1.9105 | 1.9105
2020-07-28 11:00 | Winter | 2.1529 | 3.3104 | 5.0093 | 5.0093 | 5.0093 | 5.0093 | 1.0374 | 1.0374 | 1.0374 | 1.0374 | 1.0374 | 1.0374 | 2.6864 | 3.8751 | 4.6539 | 5.0637 | 5.8835 | 6.7033 | 0.83069 | 2.2565 | 2.8302 | 2.8302 | 2.8302 | 2.8302 | 1.5623 | 1.983 | 1.983 | 1.983 | 1.983 | 1.983
2020-07-28 12:00 | Winter | 2.2101 | 3.3983 | 5.1423 | 5.1423 | 5.1423 | 5.1423 | 1.0088 | 1.0088 | 1.0088 | 1.0088 | 1.0088 | 1.0088 | 2.7245 | 3.93 | 4.7199 | 5.1356 | 5.967 | 6.7984 | 0.8345 | 2.2668 | 2.8432 | 2.8432 | 2.8432 | 2.8432 | 1.4149 | 1.796 | 1.796 | 1.796 | 1.796 | 1.796
2020-07-28 13:00 | Winter | 2.172 | 3.3397 | 5.0536 | 5.0536 | 5.0536 | 5.0536 | 1.0174 | 1.0174 | 1.0174 | 1.0174 | 1.0174 | 1.0174 | 2.7245 | 3.93 | 4.7199 | 5.1356 | 5.967 | 6.7984 | 0.80402 | 2.184 | 2.7393 | 2.7393 | 2.7393 | 2.7393 | 1.448 | 1.8379 | 1.8379 | 1.8379 | 1.8379 | 1.8379
2020-07-28 14:00 | Winter | 2.1339 | 3.2811 | 4.9649 | 4.9649 | 4.9649 | 4.9649 | 1.066 | 1.066 | 1.066 | 1.066 | 1.066 | 1.066 | 2.6483 | 3.8201 | 4.5878 | 4.9919 | 5.8 | 6.6082 | 0.80402 | 2.184 | 2.7393 | 2.7393 | 2.7393 | 2.7393 | 1.4024 | 1.7801 | 1.7801 | 1.7801 | 1.7801 | 1.7801
2020-07-28 15:00 | Winter | 2.1188 | 3.2579 | 4.9299 | 4.9299 | 4.9299 | 4.9299 | 0.98311 | 0.98311 | 0.98311 | 0.98311 | 0.98311 | 0.98311 | 2.5149 | 3.6277 | 4.3568 | 4.7405 | 5.508 | 6.2754 | 0.9069 | 2.4635 | 3.0898 | 3.0898 | 3.0898 | 3.0898 | 1.3146 | 1.6686 | 1.6686 | 1.6686 | 1.6686 | 1.6686
2020-07-28 16:00 | Winter | 2.0577 | 3.1639 | 4.7876 | 4.7876 | 4.7876 | 4.7876 | 0.94024 | 0.94024 | 0.94024 | 0.94024 | 0.94024 | 0.94024 | 2.5149 | 3.6277 | 4.3568 | 4.7405 | 5.508 | 6.2754 | 0.86117 | 2.3393 | 2.934 | 2.934 | 2.934 | 2.934 | 1.2003 | 1.5235 | 1.5235 | 1.5235 | 1.5235 | 1.5235
2020-07-28 17:00 | Winter | 1.9776 | 3.0409 | 4.6014 | 4.6014 | 4.6014 | 4.6014 | 0.84307 | 0.84307 | 0.84307 | 0.84307 | 0.84307 | 0.84307 | 2.5908 | 3.7371 | 4.4882 | 4.8835 | 5.6741 | 6.4647 | 0.85355 | 2.3186 | 2.9081 | 2.9081 | 2.9081 | 2.9081 | 1.1558 | 1.4671 | 1.4671 | 1.4671 | 1.4671 | 1.4671
2020-07-28 18:00 | Winter | 1.6108 | 2.4768 | 3.7479 | 3.7479 | 3.7479 | 3.7479 | 0.67731 | 0.67731 | 0.67731 | 0.67731 | 0.67731 | 0.67731 | 2.6293 | 3.7926 | 4.5548 | 4.956 | 5.7583 | 6.5606 | 0.80783 | 2.1944 | 2.7523 | 2.7523 | 2.7523 | 2.7523 | 0.93414 | 1.1857 | 1.1857 | 1.1857 | 1.1857 | 1.1857
2020-07-28 19:00 | Winter | 1.2197 | 1.8754 | 2.8379 | 2.8379 | 2.8379 | 2.8379 | 0.53987 | 0.53987 | 0.53987 | 0.53987 | 0.53987 | 0.53987 | 2.553 | 3.6827 | 4.4228 | 4.8123 | 5.5914 | 6.3705 | 0.80021 | 2.1737 | 2.7263 | 2.7263 | 2.7263 | 2.7263 | 0.76151 | 0.96657 | 0.96657 | 0.96657 | 0.96657 | 0.96657
2020-07-28 20:00 | Winter | 1.105 | 1.6991 | 2.5711 | 2.5711 | 2.5711 | 2.5711 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 2.3244 | 3.3529 | 4.0267 | 4.3814 | 5.0907 | 5.8 | 0.7621 | 2.0702 | 2.5965 | 2.5965 | 2.5965 | 2.5965 | 0.62873 | 0.79804 | 0.79804 | 0.79804 | 0.79804 | 0.79804
2020-07-28 21:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 2.2101 | 3.188 | 3.8287 | 4.1659 | 4.8403 | 5.5147 | 0.72781 | 1.977 | 2.4796 | 2.4796 | 2.4796 | 2.4796 | 0.51456 | 0.65312 | 0.65312 | 0.65312 | 0.65312 | 0.65312
2020-07-28 22:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.40582 | 0.40582 | 0.40582 | 0.40582 | 0.40582 | 0.40582 | 1.9858 | 2.8645 | 3.4402 | 3.7432 | 4.3491 | 4.9551 | 0.70875 | 1.9253 | 2.4147 | 2.4147 | 2.4147 | 2.4147 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-07-28 23:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.37438 | 0.37438 | 0.37438 | 0.37438 | 0.37438 | 0.37438 | 1.8101 | 2.611 | 3.1358 | 3.4119 | 3.9643 | 4.5166 | 0.62926 | 1.7093 | 2.1439 | 2.1439 | 2.1439 | 2.1439 | 0.49537 | 0.62876 | 0.62876 | 0.62876 | 0.62876 | 0.62876
2020-07-29 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.37724 | 0.37724 | 0.37724 | 0.37724 | 0.37724 | 0.37724 | 1.6766 | 2.4185 | 2.9045 | 3.1603 | 3.672 | 4.1836 | 0.55788 | 1.5154 | 1.9007 | 1.9007 | 1.9007 | 1.9007 | 0.49537 | 0.62876 | 0.62876 | 0.62876 | 0.62876 | 0.62876
2020-07-29 01:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.42582 | 0.42582 | 0.42582 | 0.42582 | 0.42582 | 0.42582 | 1.6572 | 2.3905 | 2.8709 | 3.1238 | 3.6295 | 4.1352 | 0.57539 | 1.563 | 1.9603 | 1.9603 | 1.9603 | 1.9603 | 0.49261 | 0.62526 | 0.62526 | 0.62526 | 0.62526 | 0.62526
2020-07-29 02:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.41439 | 0.41439 | 0.41439 | 0.41439 | 0.41439 | 0.41439 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.62492 | 1.6975 | 2.1291 | 2.1291 | 2.1291 | 2.1291 | 0.43821 | 0.55621 | 0.55621 | 0.55621 | 0.55621 | 0.55621
2020-07-29 03:00 | Winter | 1.0083 | 1.5504 | 2.346 | 2.346 | 2.346 | 2.346 | 0.39724 | 0.39724 | 0.39724 | 0.39724 | 0.39724 | 0.39724 | 1.6004 | 2.3086 | 2.7725 | 3.0167 | 3.5051 | 3.9934 | 0.60587 | 1.6458 | 2.0642 | 2.0642 | 2.0642 | 2.0642 | 0.48719 | 0.61837 | 0.61837 | 0.61837 | 0.61837 | 0.61837
2020-07-29 04:00 | Winter | 1.1813 | 1.8163 | 2.7485 | 2.7485 | 2.7485 | 2.7485 | 0.44873 | 0.44873 | 0.44873 | 0.44873 | 0.44873 | 0.44873 | 1.6791 | 2.422 | 2.9088 | 3.1649 | 3.6773 | 4.1897 | 0.56395 | 1.5319 | 1.9214 | 1.9214 | 1.9214 | 1.9214 | 0.5133 | 0.65152 | 0.65152 | 0.65152 | 0.65152 | 0.65152
2020-07-29 05:00 | Winter | 1.3141 | 2.0206 | 3.0575 | 3.0575 | 3.0575 | 3.0575 | 0.563 | 0.563 | 0.563 | 0.563 | 0.563 | 0.563 | 1.8901 | 2.7264 | 3.2743 | 3.5627 | 4.1394 | 4.7162 | 0.724 | 1.9667 | 2.4667 | 2.4667 | 2.4667 | 2.4667 | 0.7237 | 0.91857 | 0.91857 | 0.91857 | 0.91857 | 0.91857
2020-07-29 06:00 | Winter | 1.6194 | 2.4901 | 3.768 | 3.768 | 3.768 | 3.768 | 0.66011 | 0.66011 | 0.66011 | 0.66011 | 0.66011 | 0.66011 | 2.1339 | 3.0781 | 3.6967 | 4.0223 | 4.6734 | 5.3246 | 0.76591 | 2.0805 | 2.6095 | 2.6095 | 2.6095 | 2.6095 | 0.98114 | 1.2453 | 1.2453 | 1.2453 | 1.2453 | 1.2453
2020-07-29 07:00 | Winter | 2.0767 | 3.1932 | 4.832 | 4.832 | 4.832 | 4.832 | 1.0088 | 1.0088 | 1.0088 | 1.0088 | 1.0088 | 1.0088 | 2.4387 | 3.5178 | 4.2248 | 4.5969 | 5.3411 | 6.0852 | 0.93357 | 2.536 | 3.1807 | 3.1807 | 3.1807 | 3.1807 | 1.2956 | 1.6444 | 1.6444 | 1.6444 | 1.6444 | 1.6444
2020-07-29 08:00 | Winter | 2.2673 | 3.4862 | 5.2753 | 5.2753 | 5.2753 | 5.2753 | 1.2117 | 1.2117 | 1.2117 | 1.2117 | 1.2117 | 1.2117 | 2.6102 | 3.7651 | 4.5218 | 4.9201 | 5.7166 | 6.5131 | 1.025 | 2.7844 | 3.4923 | 3.4923 | 3.4923 | 3.4923 | 1.4861 | 1.8863 | 1.8863 | 1.8863 | 1.8863 | 1.8863
2020-07-29 09:00 | Winter | 2.3054 | 3.5448 | 5.3639 | 5.3639 | 5.3639 | 5.3639 | 1.1917 | 1.1917 | 1.1917 | 1.1917 | 1.1917 | 1.1917 | 2.6017 | 3.7528 | 4.507 | 4.904 | 5.6979 | 6.4918 | 0.92595 | 2.5153 | 3.1547 | 3.1547 | 3.1547 | 3.1547 | 1.5242 | 1.9346 | 1.9346 | 1.9346 | 1.9346 | 1.9346
2020-07-29 10:00 | Winter | 2.2245 | 3.4205 | 5.1758 | 5.1758 | 5.1758 | 5.1758 | 1.1546 | 1.1546 | 1.1546 | 1.1546 | 1.1546 | 1.1546 | 2.6864 | 3.8751 | 4.6539 | 5.0637 | 5.8835 | 6.7033 | 0.92976 | 2.5256 | 3.1677 | 3.1677 | 3.1677 | 3.1677 | 1.5814 | 2.0072 | 2.0072 | 2.0072 | 2.0072 | 2.0072
2020-07-29 11:00 | Winter | 2.1148 | 3.2518 | 4.9206 | 4.9206 | 4.9206 | 4.9206 | 1.0003 | 1.0003 | 1.0003 | 1.0003 | 1.0003 | 1.0003 | 2.6483 | 3.8201 | 4.5878 | 4.9919 | 5.8 | 6.6082 | 0.87276 | 2.3708 | 2.9735 | 2.9735 | 2.9735 | 2.9735 | 1.5289 | 1.9407 | 1.9407 | 1.9407 | 1.9407 | 1.9407
2020-07-29 12:00 | Winter | 2.172 | 3.3397 | 5.0536 | 5.0536 | 5.0536 | 5.0536 | 1.0431 | 1.0431 | 1.0431 | 1.0431 | 1.0431 | 1.0431 | 2.6102 | 3.7651 | 4.5218 | 4.9201 | 5.7166 | 6.5131 | 0.86879 | 2.36 | 2.96 | 2.96 | 2.96 | 2.96 | 1.5814 | 2.0072 | 2.0072 | 2.0072 | 2.0072 | 2.0072
2020-07-29 13:00 | Winter | 2.1339 | 3.2811 | 4.9649 | 4.9649 | 4.9649 | 4.9649 | 1.0117 | 1.0117 | 1.0117 | 1.0117 | 1.0117 | 1.0117 | 2.6102 | 3.7651 | 4.5218 | 4.9201 | 5.7166 | 6.5131 | 0.84974 | 2.3082 | 2.8951 | 2.8951 | 2.8951 | 2.8951 | 1.448 | 1.8379 | 1.8379 | 1.8379 | 1.8379 | 1.8379
2020-07-29 14:00 | Winter | 2.1529 | 3.3104 | 5.0093 | 5.0093 | 5.0093 | 5.0093 | 0.9431 | 0.9431 | 0.9431 | 0.9431 | 0.9431 | 0.9431 | 2.5911 | 3.7377 | 4.4888 | 4.8842 | 5.6749 | 6.4656 | 0.81545 | 2.2151 | 2.7782 | 2.7782 | 2.7782 | 2.7782 | 1.4099 | 1.7895 | 1.7895 | 1.7895 | 1.7895 | 1.7895
2020-07-29 15:00 | Winter | 2.1148 | 3.2518 | 4.9206 | 4.9206 | 4.9206 | 4.9206 | 0.9631 | 0.9631 | 0.9631 | 0.9631 | 0.9631 | 0.9631 | 2.4959 | 3.6002 | 4.3238 | 4.7046 | 5.4662 | 6.2279 | 0.82307 | 2.2358 | 2.8042 | 2.8042 | 2.8042 | 2.8042 | 1.2765 | 1.6203 | 1.6203 | 1.6203 | 1.6203 | 1.6203
2020-07-29 16:00 | Winter | 2.0767 | 3.1932 | 4.832 | 4.832 | 4.832 | 4.832 | 0.97739 | 0.97739 | 0.97739 | 0.97739 | 0.97739 | 0.97739 | 2.4578 | 3.5453 | 4.2578 | 4.6328 | 5.3828 | 6.1328 | 0.88404 | 2.4014 | 3.0119 | 3.0119 | 3.0119 | 3.0119 | 1.1813 | 1.4993 | 1.4993 | 1.4993 | 1.4993 | 1.4993
2020-07-29 17:00 | Winter | 1.9793 | 3.0434 | 4.6053 | 4.6053 | 4.6053 | 4.6053 | 0.90023 | 0.90023 | 0.90023 | 0.90023 | 0.90023 | 0.90023 | 2.5149 | 3.6277 | 4.3568 | 4.7405 | 5.508 | 6.2754 | 0.91452 | 2.4842 | 3.1158 | 3.1158 | 3.1158 | 3.1158 | 1.1813 | 1.4993 | 1.4993 | 1.4993 | 1.4993 | 1.4993
2020-07-29 18:00 | Winter | 1.7528 | 2.6952 | 4.0784 | 4.0784 | 4.0784 | 4.0784 | 0.78306 | 0.78306 | 0.78306 | 0.78306 | 0.78306 | 0.78306 | 2.4578 | 3.5453 | 4.2578 | 4.6328 | 5.3828 | 6.1328 | 0.81926 | 2.2254 | 2.7912 | 2.7912 | 2.7912 | 2.7912 | 0.95435 | 1.2113 | 1.2113 | 1.2113 | 1.2113 | 1.2113
2020-07-29 19:00 | Winter | 1.2194 | 1.8749 | 2.8371 | 2.8371 | 2.8371 | 2.8371 | 0.58586 | 0.58586 | 0.58586 | 0.58586 | 0.58586 | 0.58586 | 2.3439 | 3.381 | 4.0604 | 4.4181 | 5.1333 | 5.8485 | 0.80783 | 2.1944 | 2.7523 | 2.7523 | 2.7523 | 2.7523 | 0.70311 | 0.89244 | 0.89244 | 0.89244 | 0.89244 | 0.89244
2020-07-29 20:00 | Winter | 1.1432 | 1.7577 | 2.6598 | 2.6598 | 2.6598 | 2.6598 | 0.48012 | 0.48012 | 0.48012 | 0.48012 | 0.48012 | 0.48012 | 2.2291 | 3.2155 | 3.8617 | 4.2018 | 4.8821 | 5.5623 | 0.75067 | 2.0391 | 2.5575 | 2.5575 | 2.5575 | 2.5575 | 0.64779 | 0.82222 | 0.82222 | 0.82222 | 0.82222 | 0.82222
2020-07-29 21:00 | Winter | 1.0455 | 1.6076 | 2.4326 | 2.4326 | 2.4326 | 2.4326 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 2.1364 | 3.0817 | 3.701 | 4.027 | 4.6789 | 5.3308 | 0.71637 | 1.946 | 2.4407 | 2.4407 | 2.4407 | 2.4407 | 0.55293 | 0.70182 | 0.70182 | 0.70182 | 0.70182 | 0.70182
2020-07-29 22:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 2.0958 | 3.0231 | 3.6307 | 3.9504 | 4.59 | 5.2295 | 0.67446 | 1.8321 | 2.2979 | 2.2979 | 2.2979 | 2.2979 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-07-29 23:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 1.8751 | 2.7048 | 3.2483 | 3.5344 | 4.1066 | 4.6788 | 0.60968 | 1.6561 | 2.0772 | 2.0772 | 2.0772 | 2.0772 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-07-30 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 1.7147 | 2.4735 | 2.9705 | 3.2322 | 3.7554 | 4.2787 | 0.57539 | 1.563 | 1.9603 | 1.9603 | 1.9603 | 1.9603 | 0.43998 | 0.55846 | 0.55846 | 0.55846 | 0.55846 | 0.55846
2020-07-30 01:00 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 1.6766 | 2.4185 | 2.9045 | 3.1603 | 3.672 | 4.1836 | 0.60206 | 1.6354 | 2.0512 | 2.0512 | 2.0512 | 2.0512 | 0.45726 | 0.58039 | 0.58039 | 0.58039 | 0.58039 | 0.58039
2020-07-30 02:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 1.6576 | 2.391 | 2.8715 | 3.1244 | 3.6302 | 4.1361 | 0.59825 | 1.6251 | 2.0382 | 2.0382 | 2.0382 | 2.0382 | 0.45726 | 0.58039 | 0.58039 | 0.58039 | 0.58039 | 0.58039
2020-07-30 03:00 | Winter | 1.0285 | 1.5814 | 2.393 | 2.393 | 2.393 | 2.393 | 0.41439 | 0.41439 | 0.41439 | 0.41439 | 0.41439 | 0.41439 | 1.5813 | 2.2811 | 2.7395 | 2.9808 | 3.4633 | 3.9459 | 0.6173 | 1.6768 | 2.1032 | 2.1032 | 2.1032 | 2.1032 | 0.43817 | 0.55616 | 0.55616 | 0.55616 | 0.55616 | 0.55616
2020-07-30 04:00 | Winter | 1.2085 | 1.8582 | 2.8119 | 2.8119 | 2.8119 | 2.8119 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.56014 | 1.5216 | 1.9084 | 1.9084 | 1.9084 | 1.9084 | 0.51822 | 0.65776 | 0.65776 | 0.65776 | 0.65776 | 0.65776
2020-07-30 05:00 | Winter | 1.3139 | 2.0203 | 3.0572 | 3.0572 | 3.0572 | 3.0572 | 0.50027 | 0.50027 | 0.50027 | 0.50027 | 0.50027 | 0.50027 | 1.81 | 2.6109 | 3.1356 | 3.4117 | 3.9641 | 4.5164 | 0.75829 | 2.0598 | 2.5835 | 2.5835 | 2.5835 | 2.5835 | 0.74668 | 0.94774 | 0.94774 | 0.94774 | 0.94774 | 0.94774
2020-07-30 06:00 | Winter | 1.5333 | 2.3576 | 3.5675 | 3.5675 | 3.5675 | 3.5675 | 0.70589 | 0.70589 | 0.70589 | 0.70589 | 0.70589 | 0.70589 | 2.0895 | 3.014 | 3.6197 | 3.9385 | 4.5762 | 5.2138 | 0.82307 | 2.2358 | 2.8042 | 2.8042 | 2.8042 | 2.8042 | 0.95401 | 1.2109 | 1.2109 | 1.2109 | 1.2109 | 1.2109
2020-07-30 07:00 | Winter | 2.0381 | 3.1337 | 4.742 | 4.742 | 4.742 | 4.742 | 0.8888 | 0.8888 | 0.8888 | 0.8888 | 0.8888 | 0.8888 | 2.3435 | 3.3804 | 4.0597 | 4.4173 | 5.1324 | 5.8475 | 0.90309 | 2.4532 | 3.0768 | 3.0768 | 3.0768 | 3.0768 | 1.3516 | 1.7155 | 1.7155 | 1.7155 | 1.7155 | 1.7155
2020-07-30 08:00 | Winter | 2.3816 | 3.6619 | 5.5412 | 5.5412 | 5.5412 | 5.5412 | 0.98025 | 0.98025 | 0.98025 | 0.98025 | 0.98025 | 0.98025 | 2.5621 | 3.6958 | 4.4386 | 4.8295 | 5.6113 | 6.3932 | 1.0022 | 2.7223 | 3.4144 | 3.4144 | 3.4144 | 3.4144 | 1.467 | 1.8621 | 1.8621 | 1.8621 | 1.8621 | 1.8621
2020-07-30 09:00 | Winter | 2.3625 | 3.6326 | 5.4969 | 5.4969 | 5.4969 | 5.4969 | 1.0031 | 1.0031 | 1.0031 | 1.0031 | 1.0031 | 1.0031 | 2.7817 | 4.0125 | 4.8189 | 5.2433 | 6.0921 | 6.941 | 0.9069 | 2.4635 | 3.0898 | 3.0898 | 3.0898 | 3.0898 | 1.5242 | 1.9346 | 1.9346 | 1.9346 | 1.9346 | 1.9346
2020-07-30 10:00 | Winter | 2.2673 | 3.4862 | 5.2753 | 5.2753 | 5.2753 | 5.2753 | 1.0346 | 1.0346 | 1.0346 | 1.0346 | 1.0346 | 1.0346 | 2.7626 | 3.985 | 4.7859 | 5.2074 | 6.0504 | 6.8934 | 0.86498 | 2.3496 | 2.947 | 2.947 | 2.947 | 2.947 | 1.5242 | 1.9346 | 1.9346 | 1.9346 | 1.9346 | 1.9346
2020-07-30 11:00 | Winter | 2.1471 | 3.3014 | 4.9957 | 4.9957 | 4.9957 | 4.9957 | 1.046 | 1.046 | 1.046 | 1.046 | 1.046 | 1.046 | 2.7055 | 3.9026 | 4.6869 | 5.0996 | 5.9252 | 6.7508 | 0.89008 | 2.4178 | 3.0325 | 3.0325 | 3.0325 | 3.0325 | 1.5052 | 1.9105 | 1.9105 | 1.9105 | 1.9105 | 1.9105
2020-07-30 12:00 | Winter | 2.1529 | 3.3104 | 5.0093 | 5.0093 | 5.0093 | 5.0093 | 1.0546 | 1.0546 | 1.0546 | 1.0546 | 1.0546 | 1.0546 | 2.6483 | 3.8201 | 4.5878 | 4.9919 | 5.8 | 6.6082 | 0.89166 | 2.4221 | 3.0379 | 3.0379 | 3.0379 | 3.0379 | 1.467 | 1.8621 | 1.8621 | 1.8621 | 1.8621 | 1.8621
2020-07-30 13:00 | Winter | 2.191 | 3.369 | 5.0979 | 5.0979 | 5.0979 | 5.0979 | 1.0003 | 1.0003 | 1.0003 | 1.0003 | 1.0003 | 1.0003 | 2.6293 | 3.7926 | 4.5548 | 4.956 | 5.7583 | 6.5606 | 0.83831 | 2.2772 | 2.8561 | 2.8561 | 2.8561 | 2.8561 | 1.4289 | 1.8137 | 1.8137 | 1.8137 | 1.8137 | 1.8137
2020-07-30 14:00 | Winter | 2.191 | 3.369 | 5.0979 | 5.0979 | 5.0979 | 5.0979 | 0.93738 | 0.93738 | 0.93738 | 0.93738 | 0.93738 | 0.93738 | 2.6102 | 3.7651 | 4.5218 | 4.9201 | 5.7166 | 6.5131 | 0.87642 | 2.3807 | 2.986 | 2.986 | 2.986 | 2.986 | 1.4289 | 1.8137 | 1.8137 | 1.8137 | 1.8137 | 1.8137
2020-07-30 15:00 | Winter | 2.1148 | 3.2518 | 4.9206 | 4.9206 | 4.9206 | 4.9206 | 0.96025 | 0.96025 | 0.96025 | 0.96025 | 0.96025 | 0.96025 | 2.4976 | 3.6027 | 4.3267 | 4.7078 | 5.47 | 6.2321 | 0.89928 | 2.4428 | 3.0639 | 3.0639 | 3.0639 | 3.0639 | 1.3527 | 1.717 | 1.717 | 1.717 | 1.717 | 1.717
2020-07-30 16:00 | Winter | 2.0958 | 3.2225 | 4.8763 | 4.8763 | 4.8763 | 4.8763 | 0.95739 | 0.95739 | 0.95739 | 0.95739 | 0.95739 | 0.95739 | 2.4959 | 3.6002 | 4.3238 | 4.7046 | 5.4662 | 6.2279 | 0.88785 | 2.4118 | 3.0249 | 3.0249 | 3.0249 | 3.0249 | 1.2384 | 1.5719 | 1.5719 | 1.5719 | 1.5719 | 1.5719
2020-07-30 17:00 | Winter | 1.9815 | 3.0467 | 4.6103 | 4.6103 | 4.6103 | 4.6103 | 1.0145 | 1.0145 | 1.0145 | 1.0145 | 1.0145 | 1.0145 | 2.4768 | 3.5728 | 4.2908 | 4.6687 | 5.4245 | 6.1803 | 0.85736 | 2.3289 | 2.9211 | 2.9211 | 2.9211 | 2.9211 | 1.1813 | 1.4993 | 1.4993 | 1.4993 | 1.4993 | 1.4993
2020-07-30 18:00 | Winter | 1.6262 | 2.5005 | 3.7837 | 3.7837 | 3.7837 | 3.7837 | 0.87451 | 0.87451 | 0.87451 | 0.87451 | 0.87451 | 0.87451 | 2.553 | 3.6827 | 4.4228 | 4.8123 | 5.5914 | 6.3705 | 0.84974 | 2.3082 | 2.8951 | 2.8951 | 2.8951 | 2.8951 | 0.97212 | 1.2339 | 1.2339 | 1.2339 | 1.2339 | 1.2339
2020-07-30 19:00 | Winter | 1.1622 | 1.787 | 2.7041 | 2.7041 | 2.7041 | 2.7041 | 0.65731 | 0.65731 | 0.65731 | 0.65731 | 0.65731 | 0.65731 | 2.3435 | 3.3804 | 4.0597 | 4.4173 | 5.1324 | 5.8475 | 0.78115 | 2.1219 | 2.6614 | 2.6614 | 2.6614 | 2.6614 | 0.66237 | 0.84074 | 0.84074 | 0.84074 | 0.84074 | 0.84074
2020-07-30 20:00 | Winter | 1.086 | 1.6698 | 2.5268 | 2.5268 | 2.5268 | 2.5268 | 0.56586 | 0.56586 | 0.56586 | 0.56586 | 0.56586 | 0.56586 | 2.3625 | 3.4079 | 4.0927 | 4.4532 | 5.1741 | 5.8951 | 0.7621 | 2.0702 | 2.5965 | 2.5965 | 2.5965 | 2.5965 | 0.59063 | 0.74967 | 0.74967 | 0.74967 | 0.74967 | 0.74967
2020-07-30 21:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 0.51442 | 0.51442 | 0.51442 | 0.51442 | 0.51442 | 0.51442 | 2.191 | 3.1605 | 3.7957 | 4.13 | 4.7986 | 5.4672 | 0.724 | 1.9667 | 2.4667 | 2.4667 | 2.4667 | 2.4667 | 0.59063 | 0.74967 | 0.74967 | 0.74967 | 0.74967 | 0.74967
2020-07-30 22:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 2.0386 | 2.9407 | 3.5316 | 3.8427 | 4.4648 | 5.0869 | 0.76972 | 2.0909 | 2.6225 | 2.6225 | 2.6225 | 2.6225 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-07-30 23:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.43154 | 0.43154 | 0.43154 | 0.43154 | 0.43154 | 0.43154 | 1.9243 | 2.7758 | 3.3336 | 3.6272 | 4.2144 | 4.8016 | 0.72018 | 1.9563 | 2.4537 | 2.4537 | 2.4537 | 2.4537 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-07-31 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 1.7909 | 2.5834 | 3.1026 | 3.3758 | 3.9223 | 4.4688 | 0.59444 | 1.6147 | 2.0253 | 2.0253 | 2.0253 | 2.0253 | 0.49537 | 0.62876 | 0.62876 | 0.62876 | 0.62876 | 0.62876
2020-07-31 01:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.4544 | 0.4544 | 0.4544 | 0.4544 | 0.4544 | 0.4544 | 1.7147 | 2.4735 | 2.9705 | 3.2322 | 3.7554 | 4.2787 | 0.56395 | 1.5319 | 1.9214 | 1.9214 | 1.9214 | 1.9214 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-07-31 02:00 | Winter | 1.0042 | 1.5441 | 2.3366 | 2.3366 | 2.3366 | 2.3366 | 0.54585 | 0.54585 | 0.54585 | 0.54585 | 0.54585 | 0.54585 | 1.5814 | 2.2811 | 2.7395 | 2.9808 | 3.4633 | 3.9459 | 0.56776 | 1.5423 | 1.9344 | 1.9344 | 1.9344 | 1.9344 | 0.49537 | 0.62876 | 0.62876 | 0.62876 | 0.62876 | 0.62876
2020-07-31 03:00 | Winter | 1.0937 | 1.6817 | 2.5447 | 2.5447 | 2.5447 | 2.5447 | 0.55443 | 0.55443 | 0.55443 | 0.55443 | 0.55443 | 0.55443 | 1.6004 | 2.3086 | 2.7725 | 3.0167 | 3.5051 | 3.9934 | 0.54871 | 1.4905 | 1.8695 | 1.8695 | 1.8695 | 1.8695 | 0.49612 | 0.62971 | 0.62971 | 0.62971 | 0.62971 | 0.62971
2020-07-31 04:00 | Winter | 1.2194 | 1.8749 | 2.8371 | 2.8371 | 2.8371 | 2.8371 | 0.51442 | 0.51442 | 0.51442 | 0.51442 | 0.51442 | 0.51442 | 1.6766 | 2.4185 | 2.9045 | 3.1603 | 3.672 | 4.1836 | 0.58682 | 1.594 | 1.9993 | 1.9993 | 1.9993 | 1.9993 | 0.56474 | 0.71682 | 0.71682 | 0.71682 | 0.71682 | 0.71682
2020-07-31 05:00 | Winter | 1.4668 | 2.2554 | 3.4129 | 3.4129 | 3.4129 | 3.4129 | 0.65683 | 0.65683 | 0.65683 | 0.65683 | 0.65683 | 0.65683 | 1.9218 | 2.7722 | 3.3293 | 3.6225 | 4.209 | 4.7954 | 0.69351 | 1.8839 | 2.3628 | 2.3628 | 2.3628 | 2.3628 | 0.76181 | 0.96695 | 0.96695 | 0.96695 | 0.96695 | 0.96695
2020-07-31 06:00 | Winter | 1.6597 | 2.5521 | 3.8618 | 3.8618 | 3.8618 | 3.8618 | 0.95739 | 0.95739 | 0.95739 | 0.95739 | 0.95739 | 0.95739 | 2.1574 | 3.112 | 3.7374 | 4.0666 | 4.7249 | 5.3833 | 0.82688 | 2.2461 | 2.8172 | 2.8172 | 2.8172 | 2.8172 | 1.0062 | 1.2771 | 1.2771 | 1.2771 | 1.2771 | 1.2771
2020-07-31 07:00 | Winter | 2.0386 | 3.1346 | 4.7433 | 4.7433 | 4.7433 | 4.7433 | 1.2222 | 1.2222 | 1.2222 | 1.2222 | 1.2222 | 1.2222 | 2.4006 | 3.4628 | 4.1588 | 4.525 | 5.2576 | 5.9902 | 0.93738 | 2.5463 | 3.1937 | 3.1937 | 3.1937 | 3.1937 | 1.3527 | 1.717 | 1.717 | 1.717 | 1.717 | 1.717
2020-07-31 08:00 | Winter | 2.2101 | 3.3983 | 5.1423 | 5.1423 | 5.1423 | 5.1423 | 1.2232 | 1.2232 | 1.2232 | 1.2232 | 1.2232 | 1.2232 | 2.6102 | 3.7651 | 4.5218 | 4.9201 | 5.7166 | 6.5131 | 0.96406 | 2.6188 | 3.2846 | 3.2846 | 3.2846 | 3.2846 | 1.5433 | 1.9588 | 1.9588 | 1.9588 | 1.9588 | 1.9588
2020-07-31 09:00 | Winter | 2.2291 | 3.4276 | 5.1866 | 5.1866 | 5.1866 | 5.1866 | 1.186 | 1.186 | 1.186 | 1.186 | 1.186 | 1.186 | 2.6102 | 3.7651 | 4.5218 | 4.9201 | 5.7166 | 6.5131 | 0.95644 | 2.5981 | 3.2586 | 3.2586 | 3.2586 | 3.2586 | 1.6004 | 2.0314 | 2.0314 | 2.0314 | 2.0314 | 2.0314
2020-07-31 10:00 | Winter | 2.2101 | 3.3983 | 5.1423 | 5.1423 | 5.1423 | 5.1423 | 1.2203 | 1.2203 | 1.2203 | 1.2203 | 1.2203 | 1.2203 | 2.7055 | 3.9026 | 4.6869 | 5.0996 | 5.9252 | 6.7508 | 0.84974 | 2.3082 | 2.8951 | 2.8951 | 2.8951 | 2.8951 | 1.5433 | 1.9588 | 1.9588 | 1.9588 | 1.9588 | 1.9588
2020-07-31 11:00 | Winter | 2.1148 | 3.2518 | 4.9206 | 4.9206 | 4.9206 | 4.9206 | 1.1917 | 1.1917 | 1.1917 | 1.1917 | 1.1917 | 1.1917 | 2.7436 | 3.9575 | 4.7529 | 5.1715 | 6.0087 | 6.8459 | 0.85736 | 2.3289 | 2.9211 | 2.9211 | 2.9211 | 2.9211 | 1.5242 | 1.9346 | 1.9346 | 1.9346 | 1.9346 | 1.9346
2020-07-31 12:00 | Winter | 2.172 | 3.3397 | 5.0536 | 5.0536 | 5.0536 | 5.0536 | 1.1317 | 1.1317 | 1.1317 | 1.1317 | 1.1317 | 1.1317 | 2.6293 | 3.7926 | 4.5548 | 4.956 | 5.7583 | 6.5606 | 0.9069 | 2.4635 | 3.0898 | 3.0898 | 3.0898 | 3.0898 | 1.5814 | 2.0072 | 2.0072 | 2.0072 | 2.0072 | 2.0072
2020-07-31 13:00 | Winter | 2.172 | 3.3397 | 5.0536 | 5.0536 | 5.0536 | 5.0536 | 1.1374 | 1.1374 | 1.1374 | 1.1374 | 1.1374 | 1.1374 | 2.6864 | 3.8751 | 4.6539 | 5.0637 | 5.8835 | 6.7033 | 0.88023 | 2.3911 | 2.9989 | 2.9989 | 2.9989 | 2.9989 | 1.467 | 1.8621 | 1.8621 | 1.8621 | 1.8621 | 1.8621
2020-07-31 14:00 | Winter | 2.1529 | 3.3104 | 5.0093 | 5.0093 | 5.0093 | 5.0093 | 1.0917 | 1.0917 | 1.0917 | 1.0917 | 1.0917 | 1.0917 | 2.6674 | 3.8476 | 4.6208 | 5.0278 | 5.8418 | 6.6557 | 0.89928 | 2.4428 | 3.0639 | 3.0639 | 3.0639 | 3.0639 | 1.3729 | 1.7426 | 1.7426 | 1.7426 | 1.7426 | 1.7426
2020-07-31 15:00 | Winter | 2.1148 | 3.2518 | 4.9206 | 4.9206 | 4.9206 | 4.9206 | 1.1517 | 1.1517 | 1.1517 | 1.1517 | 1.1517 | 1.1517 | 2.663 | 3.8413 | 4.6132 | 5.0195 | 5.8322 | 6.6448 | 0.92214 | 2.5049 | 3.1418 | 3.1418 | 3.1418 | 3.1418 | 1.28 | 1.6246 | 1.6246 | 1.6246 | 1.6246 | 1.6246
2020-07-31 16:00 | Winter | 2.0958 | 3.2225 | 4.8763 | 4.8763 | 4.8763 | 4.8763 | 1.0403 | 1.0403 | 1.0403 | 1.0403 | 1.0403 | 1.0403 | 2.553 | 3.6827 | 4.4228 | 4.8123 | 5.5914 | 6.3705 | 0.88023 | 2.3911 | 2.9989 | 2.9989 | 2.9989 | 2.9989 | 1.2575 | 1.5961 | 1.5961 | 1.5961 | 1.5961 | 1.5961
2020-07-31 17:00 | Winter | 1.9053 | 2.9297 | 4.4331 | 4.4331 | 4.4331 | 4.4331 | 1.0317 | 1.0317 | 1.0317 | 1.0317 | 1.0317 | 1.0317 | 2.6102 | 3.7651 | 4.5218 | 4.9201 | 5.7166 | 6.5131 | 0.89928 | 2.4428 | 3.0639 | 3.0639 | 3.0639 | 3.0639 | 1.1622 | 1.4752 | 1.4752 | 1.4752 | 1.4752 | 1.4752
2020-07-31 18:00 | Winter | 1.6579 | 2.5492 | 3.8574 | 3.8574 | 3.8574 | 3.8574 | 0.88308 | 0.88308 | 0.88308 | 0.88308 | 0.88308 | 0.88308 | 2.534 | 3.6552 | 4.3898 | 4.7764 | 5.5497 | 6.3229 | 0.8666 | 2.354 | 2.9525 | 2.9525 | 2.9525 | 2.9525 | 0.88433 | 1.1225 | 1.1225 | 1.1225 | 1.1225 | 1.1225
2020-07-31 19:00 | Winter | 1.2003 | 1.8456 | 2.7928 | 2.7928 | 2.7928 | 2.7928 | 0.78591 | 0.78591 | 0.78591 | 0.78591 | 0.78591 | 0.78591 | 2.3816 | 3.4353 | 4.1258 | 4.4891 | 5.2159 | 5.9426 | 0.78115 | 2.1219 | 2.6614 | 2.6614 | 2.6614 | 2.6614 | 0.66684 | 0.84641 | 0.84641 | 0.84641 | 0.84641 | 0.84641
2020-07-31 20:00 | Winter | 1.105 | 1.6991 | 2.5711 | 2.5711 | 2.5711 | 2.5711 | 0.73733 | 0.73733 | 0.73733 | 0.73733 | 0.73733 | 0.73733 | 2.2674 | 3.2706 | 3.9279 | 4.2739 | 4.9658 | 5.6577 | 0.73924 | 2.0081 | 2.5186 | 2.5186 | 2.5186 | 2.5186 | 0.62873 | 0.79804 | 0.79804 | 0.79804 | 0.79804 | 0.79804
2020-07-31 21:00 | Winter | 1.0485 | 1.6121 | 2.4394 | 2.4394 | 2.4394 | 2.4394 | 0.68303 | 0.68303 | 0.68303 | 0.68303 | 0.68303 | 0.68303 | 2.191 | 3.1605 | 3.7957 | 4.13 | 4.7986 | 5.4672 | 0.78496 | 2.1323 | 2.6744 | 2.6744 | 2.6744 | 2.6744 | 0.59063 | 0.74967 | 0.74967 | 0.74967 | 0.74967 | 0.74967
2020-07-31 22:00 | Winter | 0.99752 | 1.5338 | 2.3209 | 2.3209 | 2.3209 | 2.3209 | 0.60587 | 0.60587 | 0.60587 | 0.60587 | 0.60587 | 0.60587 | 2.0958 | 3.0231 | 3.6307 | 3.9504 | 4.59 | 5.2295 | 0.75067 | 2.0391 | 2.5575 | 2.5575 | 2.5575 | 2.5575 | 0.49828 | 0.63245 | 0.63245 | 0.63245 | 0.63245 | 0.63245
2020-07-31 23:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.47441 | 0.47441 | 0.47441 | 0.47441 | 0.47441 | 0.47441 | 2.0012 | 2.8867 | 3.4669 | 3.7722 | 4.3829 | 4.9936 | 0.6516 | 1.77 | 2.22 | 2.22 | 2.22 | 2.22 | 0.49537 | 0.62876 | 0.62876 | 0.62876 | 0.62876 | 0.62876
2020-08-01 | Winter | 0.93961 | 1.4448 | 2.1862 | 2.1862 | 2.1862 | 2.1862 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 1.7528 | 2.5284 | 3.0366 | 3.304 | 3.8389 | 4.3738 | 0.60206 | 1.6354 | 2.0512 | 2.0512 | 2.0512 | 2.0512 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-08-01 01:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 1.6957 | 2.446 | 2.9375 | 3.1963 | 3.7137 | 4.2311 | 0.62111 | 1.6872 | 2.1161 | 2.1161 | 2.1161 | 2.1161 | 0.49537 | 0.62876 | 0.62876 | 0.62876 | 0.62876 | 0.62876
2020-08-01 02:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 1.6573 | 2.3906 | 2.8711 | 3.1239 | 3.6297 | 4.1354 | 0.55633 | 1.5112 | 1.8954 | 1.8954 | 1.8954 | 1.8954 | 0.47628 | 0.60453 | 0.60453 | 0.60453 | 0.60453 | 0.60453
2020-08-01 03:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.43154 | 0.43154 | 0.43154 | 0.43154 | 0.43154 | 0.43154 | 1.6576 | 2.391 | 2.8715 | 3.1244 | 3.6302 | 4.1361 | 0.63635 | 1.7286 | 2.1681 | 2.1681 | 2.1681 | 2.1681 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-08-01 04:00 | Winter | 1.0288 | 1.582 | 2.3938 | 2.3938 | 2.3938 | 2.3938 | 0.43154 | 0.43154 | 0.43154 | 0.43154 | 0.43154 | 0.43154 | 1.6953 | 2.4454 | 2.9369 | 3.1956 | 3.7129 | 4.2302 | 0.54871 | 1.4905 | 1.8695 | 1.8695 | 1.8695 | 1.8695 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-08-01 05:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.48012 | 0.48012 | 0.48012 | 0.48012 | 0.48012 | 0.48012 | 1.7528 | 2.5284 | 3.0366 | 3.304 | 3.8389 | 4.3738 | 0.66303 | 1.8011 | 2.2589 | 2.2589 | 2.2589 | 2.2589 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-08-01 06:00 | Winter | 1.086 | 1.6698 | 2.5268 | 2.5268 | 2.5268 | 2.5268 | 0.46869 | 0.46869 | 0.46869 | 0.46869 | 0.46869 | 0.46869 | 1.9434 | 2.8032 | 3.3666 | 3.6631 | 4.2562 | 4.8492 | 0.72018 | 1.9563 | 2.4537 | 2.4537 | 2.4537 | 2.4537 | 0.55143 | 0.69992 | 0.69992 | 0.69992 | 0.69992 | 0.69992
2020-08-01 07:00 | Winter | 1.1241 | 1.7284 | 2.6155 | 2.6155 | 2.6155 | 2.6155 | 0.60873 | 0.60873 | 0.60873 | 0.60873 | 0.60873 | 0.60873 | 2.0005 | 2.8857 | 3.4656 | 3.7709 | 4.3813 | 4.9918 | 0.6897 | 1.8735 | 2.3498 | 2.3498 | 2.3498 | 2.3498 | 0.57158 | 0.72549 | 0.72549 | 0.72549 | 0.72549 | 0.72549
2020-08-01 08:00 | Winter | 1.1432 | 1.7577 | 2.6598 | 2.6598 | 2.6598 | 2.6598 | 0.66303 | 0.66303 | 0.66303 | 0.66303 | 0.66303 | 0.66303 | 2.172 | 3.133 | 3.7627 | 4.0941 | 4.7569 | 5.4197 | 0.70113 | 1.9046 | 2.3888 | 2.3888 | 2.3888 | 2.3888 | 0.57152 | 0.72542 | 0.72542 | 0.72542 | 0.72542 | 0.72542
2020-08-01 09:00 | Winter | 1.1241 | 1.7284 | 2.6155 | 2.6155 | 2.6155 | 2.6155 | 0.6716 | 0.6716 | 0.6716 | 0.6716 | 0.6716 | 0.6716 | 2.3244 | 3.3529 | 4.0267 | 4.3814 | 5.0907 | 5.8 | 0.76972 | 2.0909 | 2.6225 | 2.6225 | 2.6225 | 2.6225 | 0.62873 | 0.79804 | 0.79804 | 0.79804 | 0.79804 | 0.79804
2020-08-01 10:00 | Winter | 1.105 | 1.6991 | 2.5711 | 2.5711 | 2.5711 | 2.5711 | 0.69732 | 0.69732 | 0.69732 | 0.69732 | 0.69732 | 0.69732 | 2.3816 | 3.4353 | 4.1258 | 4.4891 | 5.2159 | 5.9426 | 0.73543 | 1.9977 | 2.5056 | 2.5056 | 2.5056 | 2.5056 | 0.64779 | 0.82222 | 0.82222 | 0.82222 | 0.82222 | 0.82222
2020-08-01 11:00 | Winter | 1.0659 | 1.6389 | 2.48 | 2.48 | 2.48 | 2.48 | 0.66874 | 0.66874 | 0.66874 | 0.66874 | 0.66874 | 0.66874 | 2.3244 | 3.3529 | 4.0267 | 4.3814 | 5.0907 | 5.8 | 0.724 | 1.9667 | 2.4667 | 2.4667 | 2.4667 | 2.4667 | 0.64779 | 0.82222 | 0.82222 | 0.82222 | 0.82222 | 0.82222
2020-08-01 12:00 | Winter | 1.0669 | 1.6405 | 2.4825 | 2.4825 | 2.4825 | 2.4825 | 0.68303 | 0.68303 | 0.68303 | 0.68303 | 0.68303 | 0.68303 | 2.2291 | 3.2155 | 3.8617 | 4.2018 | 4.8821 | 5.5623 | 0.72781 | 1.977 | 2.4796 | 2.4796 | 2.4796 | 2.4796 | 0.65474 | 0.83105 | 0.83105 | 0.83105 | 0.83105 | 0.83105
2020-08-01 13:00 | Winter | 1.0288 | 1.582 | 2.3938 | 2.3938 | 2.3938 | 2.3938 | 0.63159 | 0.63159 | 0.63159 | 0.63159 | 0.63159 | 0.63159 | 2.2107 | 3.1889 | 3.8297 | 4.167 | 4.8416 | 5.5162 | 0.75067 | 2.0391 | 2.5575 | 2.5575 | 2.5575 | 2.5575 | 0.68589 | 0.87059 | 0.87059 | 0.87059 | 0.87059 | 0.87059
2020-08-01 14:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.68017 | 0.68017 | 0.68017 | 0.68017 | 0.68017 | 0.68017 | 2.2291 | 3.2155 | 3.8617 | 4.2018 | 4.8821 | 5.5623 | 0.76972 | 2.0909 | 2.6225 | 2.6225 | 2.6225 | 2.6225 | 0.62873 | 0.79804 | 0.79804 | 0.79804 | 0.79804 | 0.79804
2020-08-01 15:00 | Winter | 1.0859 | 1.6697 | 2.5266 | 2.5266 | 2.5266 | 2.5266 | 0.66303 | 0.66303 | 0.66303 | 0.66303 | 0.66303 | 0.66303 | 2.229 | 3.2153 | 3.8614 | 4.2015 | 4.8817 | 5.5619 | 0.72018 | 1.9563 | 2.4537 | 2.4537 | 2.4537 | 2.4537 | 0.57158 | 0.72549 | 0.72549 | 0.72549 | 0.72549 | 0.72549
2020-08-01 16:00 | Winter | 1.1241 | 1.7284 | 2.6155 | 2.6155 | 2.6155 | 2.6155 | 0.61158 | 0.61158 | 0.61158 | 0.61158 | 0.61158 | 0.61158 | 2.2291 | 3.2155 | 3.8617 | 4.2018 | 4.8821 | 5.5623 | 0.73543 | 1.9977 | 2.5056 | 2.5056 | 2.5056 | 2.5056 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-08-01 17:00 | Winter | 1.086 | 1.6698 | 2.5268 | 2.5268 | 2.5268 | 2.5268 | 0.66303 | 0.66303 | 0.66303 | 0.66303 | 0.66303 | 0.66303 | 2.3631 | 3.4086 | 4.0937 | 4.4542 | 5.1753 | 5.8964 | 0.85736 | 2.3289 | 2.9211 | 2.9211 | 2.9211 | 2.9211 | 0.57158 | 0.72549 | 0.72549 | 0.72549 | 0.72549 | 0.72549
2020-08-01 18:00 | Winter | 1.0288 | 1.582 | 2.3938 | 2.3938 | 2.3938 | 2.3938 | 0.69446 | 0.69446 | 0.69446 | 0.69446 | 0.69446 | 0.69446 | 2.4387 | 3.5178 | 4.2248 | 4.5969 | 5.3411 | 6.0852 | 0.86498 | 2.3496 | 2.947 | 2.947 | 2.947 | 2.947 | 0.59063 | 0.74967 | 0.74967 | 0.74967 | 0.74967 | 0.74967
2020-08-01 19:00 | Winter | 1.0669 | 1.6405 | 2.4825 | 2.4825 | 2.4825 | 2.4825 | 0.61444 | 0.61444 | 0.61444 | 0.61444 | 0.61444 | 0.61444 | 2.3054 | 3.3254 | 3.9937 | 4.3455 | 5.049 | 5.7525 | 0.86117 | 2.3393 | 2.934 | 2.934 | 2.934 | 2.934 | 0.58459 | 0.74201 | 0.74201 | 0.74201 | 0.74201 | 0.74201
2020-08-01 20:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 0.63159 | 0.63159 | 0.63159 | 0.63159 | 0.63159 | 0.63159 | 2.2863 | 3.2979 | 3.9607 | 4.3096 | 5.0072 | 5.7049 | 0.7964 | 2.1633 | 2.7133 | 2.7133 | 2.7133 | 2.7133 | 0.59063 | 0.74967 | 0.74967 | 0.74967 | 0.74967 | 0.74967
2020-08-01 21:00 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.56586 | 0.56586 | 0.56586 | 0.56586 | 0.56586 | 0.56586 | 2.2291 | 3.2155 | 3.8617 | 4.2018 | 4.8821 | 5.5623 | 0.79258 | 2.153 | 2.7003 | 2.7003 | 2.7003 | 2.7003 | 0.55252 | 0.70131 | 0.70131 | 0.70131 | 0.70131 | 0.70131
2020-08-01 22:00 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 2.1529 | 3.1056 | 3.7297 | 4.0582 | 4.7151 | 5.3721 | 0.80783 | 2.1944 | 2.7523 | 2.7523 | 2.7523 | 2.7523 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-08-01 23:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.46811 | 0.46811 | 0.46811 | 0.46811 | 0.46811 | 0.46811 | 1.9197 | 2.769 | 3.3255 | 3.6184 | 4.2042 | 4.79 | 0.75448 | 2.0495 | 2.5705 | 2.5705 | 2.5705 | 2.5705 | 0.51388 | 0.65225 | 0.65225 | 0.65225 | 0.65225 | 0.65225
2020-08-02 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.46869 | 0.46869 | 0.46869 | 0.46869 | 0.46869 | 0.46869 | 1.7338 | 2.5009 | 3.0036 | 3.2681 | 3.7972 | 4.3262 | 0.64779 | 1.7596 | 2.207 | 2.207 | 2.207 | 2.207 | 0.49537 | 0.62876 | 0.62876 | 0.62876 | 0.62876 | 0.62876
2020-08-02 01:00 | Winter | 0.96781 | 1.4881 | 2.2518 | 2.2518 | 2.2518 | 2.2518 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 1.6576 | 2.391 | 2.8715 | 3.1244 | 3.6302 | 4.1361 | 0.62111 | 1.6872 | 2.1161 | 2.1161 | 2.1161 | 2.1161 | 0.50069 | 0.63551 | 0.63551 | 0.63551 | 0.63551 | 0.63551
2020-08-02 02:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 1.6004 | 2.3086 | 2.7725 | 3.0167 | 3.5051 | 3.9934 | 0.58301 | 1.5837 | 1.9863 | 1.9863 | 1.9863 | 1.9863 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-08-02 03:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.46869 | 0.46869 | 0.46869 | 0.46869 | 0.46869 | 0.46869 | 1.5626 | 2.254 | 2.707 | 2.9454 | 3.4222 | 3.899 | 0.57157 | 1.5526 | 1.9474 | 1.9474 | 1.9474 | 1.9474 | 0.45726 | 0.58039 | 0.58039 | 0.58039 | 0.58039 | 0.58039
2020-08-02 04:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 1.6474 | 2.3764 | 2.854 | 3.1053 | 3.608 | 4.1107 | 0.60587 | 1.6458 | 2.0642 | 2.0642 | 2.0642 | 2.0642 | 0.45726 | 0.58039 | 0.58039 | 0.58039 | 0.58039 | 0.58039
2020-08-02 05:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 1.7891 | 2.5808 | 3.0994 | 3.3724 | 3.9184 | 4.4643 | 0.58682 | 1.594 | 1.9993 | 1.9993 | 1.9993 | 1.9993 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-08-02 06:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.48012 | 0.48012 | 0.48012 | 0.48012 | 0.48012 | 0.48012 | 1.9053 | 2.7483 | 3.3006 | 3.5913 | 4.1727 | 4.7541 | 0.64397 | 1.7493 | 2.194 | 2.194 | 2.194 | 2.194 | 0.49537 | 0.62876 | 0.62876 | 0.62876 | 0.62876 | 0.62876
2020-08-02 07:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.60873 | 0.60873 | 0.60873 | 0.60873 | 0.60873 | 0.60873 | 1.9624 | 2.8307 | 3.3996 | 3.699 | 4.2979 | 4.8967 | 0.64397 | 1.7493 | 2.194 | 2.194 | 2.194 | 2.194 | 0.54027 | 0.68575 | 0.68575 | 0.68575 | 0.68575 | 0.68575
2020-08-02 08:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.60015 | 0.60015 | 0.60015 | 0.60015 | 0.60015 | 0.60015 | 2.2328 | 3.2208 | 3.8681 | 4.2088 | 4.8901 | 5.5715 | 0.77734 | 2.1116 | 2.6484 | 2.6484 | 2.6484 | 2.6484 | 0.55252 | 0.70131 | 0.70131 | 0.70131 | 0.70131 | 0.70131
2020-08-02 09:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.60873 | 0.60873 | 0.60873 | 0.60873 | 0.60873 | 0.60873 | 2.4387 | 3.5178 | 4.2248 | 4.5969 | 5.3411 | 6.0852 | 0.72781 | 1.977 | 2.4796 | 2.4796 | 2.4796 | 2.4796 | 0.62873 | 0.79804 | 0.79804 | 0.79804 | 0.79804 | 0.79804
2020-08-02 10:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.57443 | 0.57443 | 0.57443 | 0.57443 | 0.57443 | 0.57443 | 2.3244 | 3.3529 | 4.0267 | 4.3814 | 5.0907 | 5.8 | 0.724 | 1.9667 | 2.4667 | 2.4667 | 2.4667 | 2.4667 | 0.66684 | 0.84641 | 0.84641 | 0.84641 | 0.84641 | 0.84641
2020-08-02 11:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.55443 | 0.55443 | 0.55443 | 0.55443 | 0.55443 | 0.55443 | 2.3435 | 3.3804 | 4.0597 | 4.4173 | 5.1324 | 5.8475 | 0.74305 | 2.0184 | 2.5316 | 2.5316 | 2.5316 | 2.5316 | 0.64604 | 0.82001 | 0.82001 | 0.82001 | 0.82001 | 0.82001
2020-08-02 12:00 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.52585 | 0.52585 | 0.52585 | 0.52585 | 0.52585 | 0.52585 | 2.2863 | 3.2979 | 3.9607 | 4.3096 | 5.0072 | 5.7049 | 0.69351 | 1.8839 | 2.3628 | 2.3628 | 2.3628 | 2.3628 | 0.60968 | 0.77386 | 0.77386 | 0.77386 | 0.77386 | 0.77386
2020-08-02 13:00 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.52013 | 0.52013 | 0.52013 | 0.52013 | 0.52013 | 0.52013 | 2.2863 | 3.2979 | 3.9607 | 4.3096 | 5.0072 | 5.7049 | 0.69351 | 1.8839 | 2.3628 | 2.3628 | 2.3628 | 2.3628 | 0.62873 | 0.79804 | 0.79804 | 0.79804 | 0.79804 | 0.79804
2020-08-02 14:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.51727 | 0.51727 | 0.51727 | 0.51727 | 0.51727 | 0.51727 | 2.2482 | 3.243 | 3.8947 | 4.2377 | 4.9238 | 5.6098 | 0.67827 | 1.8425 | 2.3109 | 2.3109 | 2.3109 | 2.3109 | 0.59063 | 0.74967 | 0.74967 | 0.74967 | 0.74967 | 0.74967
2020-08-02 15:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.54585 | 0.54585 | 0.54585 | 0.54585 | 0.54585 | 0.54585 | 2.2482 | 3.243 | 3.8947 | 4.2377 | 4.9238 | 5.6098 | 0.70113 | 1.9046 | 2.3888 | 2.3888 | 2.3888 | 2.3888 | 0.59063 | 0.74967 | 0.74967 | 0.74967 | 0.74967 | 0.74967
2020-08-02 16:00 | Winter | 1.2194 | 1.8749 | 2.8371 | 2.8371 | 2.8371 | 2.8371 | 0.55728 | 0.55728 | 0.55728 | 0.55728 | 0.55728 | 0.55728 | 2.2101 | 3.188 | 3.8287 | 4.1659 | 4.8403 | 5.5147 | 0.75067 | 2.0391 | 2.5575 | 2.5575 | 2.5575 | 2.5575 | 0.55252 | 0.70131 | 0.70131 | 0.70131 | 0.70131 | 0.70131
2020-08-02 17:00 | Winter | 1.1622 | 1.787 | 2.7041 | 2.7041 | 2.7041 | 2.7041 | 0.59444 | 0.59444 | 0.59444 | 0.59444 | 0.59444 | 0.59444 | 2.4006 | 3.4628 | 4.1588 | 4.525 | 5.2576 | 5.9902 | 0.78115 | 2.1219 | 2.6614 | 2.6614 | 2.6614 | 2.6614 | 0.55252 | 0.70131 | 0.70131 | 0.70131 | 0.70131 | 0.70131
2020-08-02 18:00 | Winter | 1.0101 | 1.5531 | 2.3502 | 2.3502 | 2.3502 | 2.3502 | 0.54299 | 0.54299 | 0.54299 | 0.54299 | 0.54299 | 0.54299 | 2.4387 | 3.5178 | 4.2248 | 4.5969 | 5.3411 | 6.0852 | 0.80783 | 2.1944 | 2.7523 | 2.7523 | 2.7523 | 2.7523 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-08-02 19:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.5287 | 0.5287 | 0.5287 | 0.5287 | 0.5287 | 0.5287 | 2.389 | 3.446 | 4.1386 | 4.5031 | 5.232 | 5.961 | 0.78877 | 2.1426 | 2.6874 | 2.6874 | 2.6874 | 2.6874 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-08-02 20:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.56586 | 0.56586 | 0.56586 | 0.56586 | 0.56586 | 0.56586 | 2.3244 | 3.3529 | 4.0267 | 4.3814 | 5.0907 | 5.8 | 0.79258 | 2.153 | 2.7003 | 2.7003 | 2.7003 | 2.7003 | 0.55252 | 0.70131 | 0.70131 | 0.70131 | 0.70131 | 0.70131
2020-08-02 21:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.48012 | 0.48012 | 0.48012 | 0.48012 | 0.48012 | 0.48012 | 2.1926 | 3.1628 | 3.7984 | 4.133 | 4.8021 | 5.4711 | 0.70494 | 1.9149 | 2.4018 | 2.4018 | 2.4018 | 2.4018 | 0.55252 | 0.70131 | 0.70131 | 0.70131 | 0.70131 | 0.70131
2020-08-02 22:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 2.0386 | 2.9407 | 3.5316 | 3.8427 | 4.4648 | 5.0869 | 0.70494 | 1.9149 | 2.4018 | 2.4018 | 2.4018 | 2.4018 | 0.55252 | 0.70131 | 0.70131 | 0.70131 | 0.70131 | 0.70131
2020-08-02 23:00 | Winter | 0.97245 | 1.4953 | 2.2626 | 2.2626 | 2.2626 | 2.2626 | 0.39438 | 0.39438 | 0.39438 | 0.39438 | 0.39438 | 0.39438 | 1.849 | 2.6672 | 3.2032 | 3.4853 | 4.0496 | 4.6138 | 0.64397 | 1.7493 | 2.194 | 2.194 | 2.194 | 2.194 | 0.55252 | 0.70131 | 0.70131 | 0.70131 | 0.70131 | 0.70131
2020-08-03 | Winter | 1.0288 | 1.582 | 2.3938 | 2.3938 | 2.3938 | 2.3938 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 1.7338 | 2.5009 | 3.0036 | 3.2681 | 3.7972 | 4.3262 | 0.61349 | 1.6665 | 2.0902 | 2.0902 | 2.0902 | 2.0902 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-08-03 01:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 1.6576 | 2.391 | 2.8715 | 3.1244 | 3.6302 | 4.1361 | 0.6173 | 1.6768 | 2.1032 | 2.1032 | 2.1032 | 2.1032 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-08-03 02:00 | Winter | 1.1813 | 1.8163 | 2.7485 | 2.7485 | 2.7485 | 2.7485 | 0.47726 | 0.47726 | 0.47726 | 0.47726 | 0.47726 | 0.47726 | 1.6576 | 2.391 | 2.8715 | 3.1244 | 3.6302 | 4.1361 | 0.54871 | 1.4905 | 1.8695 | 1.8695 | 1.8695 | 1.8695 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-08-03 03:00 | Winter | 1.2384 | 1.9042 | 2.8814 | 2.8814 | 2.8814 | 2.8814 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 1.6549 | 2.3871 | 2.8668 | 3.1193 | 3.6243 | 4.1293 | 0.5449 | 1.4802 | 1.8565 | 1.8565 | 1.8565 | 1.8565 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-08-03 04:00 | Winter | 1.2575 | 1.9335 | 2.9258 | 2.9258 | 2.9258 | 2.9258 | 0.5087 | 0.5087 | 0.5087 | 0.5087 | 0.5087 | 0.5087 | 1.829 | 2.6383 | 3.1686 | 3.4477 | 4.0058 | 4.5639 | 0.56395 | 1.5319 | 1.9214 | 1.9214 | 1.9214 | 1.9214 | 0.51436 | 0.65287 | 0.65287 | 0.65287 | 0.65287 | 0.65287
2020-08-03 05:00 | Winter | 1.5814 | 2.4315 | 3.6794 | 3.6794 | 3.6794 | 3.6794 | 0.81735 | 0.81735 | 0.81735 | 0.81735 | 0.81735 | 0.81735 | 1.9434 | 2.8032 | 3.3666 | 3.6631 | 4.2562 | 4.8492 | 0.68208 | 1.8528 | 2.3239 | 2.3239 | 2.3239 | 2.3239 | 0.84777 | 1.0761 | 1.0761 | 1.0761 | 1.0761 | 1.0761
2020-08-03 06:00 | Winter | 1.958 | 3.0107 | 4.5557 | 4.5557 | 4.5557 | 4.5557 | 0.90023 | 0.90023 | 0.90023 | 0.90023 | 0.90023 | 0.90023 | 2.1529 | 3.1056 | 3.7297 | 4.0582 | 4.7151 | 5.3721 | 0.78877 | 2.1426 | 2.6874 | 2.6874 | 2.6874 | 2.6874 | 1.0463 | 1.3281 | 1.3281 | 1.3281 | 1.3281 | 1.3281
2020-08-03 07:00 | Winter | 2.1909 | 3.3688 | 5.0977 | 5.0977 | 5.0977 | 5.0977 | 1.2632 | 1.2632 | 1.2632 | 1.2632 | 1.2632 | 1.2632 | 2.5456 | 3.6719 | 4.4098 | 4.7982 | 5.575 | 6.3518 | 0.86498 | 2.3496 | 2.947 | 2.947 | 2.947 | 2.947 | 1.4099 | 1.7895 | 1.7895 | 1.7895 | 1.7895 | 1.7895
2020-08-03 08:00 | Winter | 2.5149 | 3.867 | 5.8515 | 5.8515 | 5.8515 | 5.8515 | 1.306 | 1.306 | 1.306 | 1.306 | 1.306 | 1.306 | 2.7572 | 3.9772 | 4.7765 | 5.1972 | 6.0386 | 6.88 | 0.91833 | 2.4946 | 3.1288 | 3.1288 | 3.1288 | 3.1288 | 1.6766 | 2.1281 | 2.1281 | 2.1281 | 2.1281 | 2.1281
2020-08-03 09:00 | Winter | 2.5149 | 3.867 | 5.8515 | 5.8515 | 5.8515 | 5.8515 | 1.2603 | 1.2603 | 1.2603 | 1.2603 | 1.2603 | 1.2603 | 2.9531 | 4.2598 | 5.1159 | 5.5665 | 6.4677 | 7.3688 | 0.91077 | 2.474 | 3.103 | 3.103 | 3.103 | 3.103 | 1.7147 | 2.1765 | 2.1765 | 2.1765 | 2.1765 | 2.1765
2020-08-03 10:00 | Winter | 2.4387 | 3.7498 | 5.6742 | 5.6742 | 5.6742 | 5.6742 | 1.3518 | 1.3518 | 1.3518 | 1.3518 | 1.3518 | 1.3518 | 2.9531 | 4.2598 | 5.1159 | 5.5665 | 6.4677 | 7.3688 | 0.87261 | 2.3704 | 2.973 | 2.973 | 2.973 | 2.973 | 1.81 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974
2020-08-03 11:00 | Winter | 2.4006 | 3.6912 | 5.5856 | 5.5856 | 5.5856 | 5.5856 | 1.2546 | 1.2546 | 1.2546 | 1.2546 | 1.2546 | 1.2546 | 2.8579 | 4.1224 | 4.9509 | 5.387 | 6.259 | 7.1311 | 0.86117 | 2.3393 | 2.934 | 2.934 | 2.934 | 2.934 | 1.81 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974
2020-08-03 12:00 | Winter | 2.2863 | 3.5155 | 5.3196 | 5.3196 | 5.3196 | 5.3196 | 1.1574 | 1.1574 | 1.1574 | 1.1574 | 1.1574 | 1.1574 | 2.8769 | 4.1499 | 4.9839 | 5.4229 | 6.3008 | 7.1787 | 0.88785 | 2.4118 | 3.0249 | 3.0249 | 3.0249 | 3.0249 | 1.7338 | 2.2007 | 2.2007 | 2.2007 | 2.2007 | 2.2007
2020-08-03 13:00 | Winter | 2.2291 | 3.4276 | 5.1866 | 5.1866 | 5.1866 | 5.1866 | 1.1317 | 1.1317 | 1.1317 | 1.1317 | 1.1317 | 1.1317 | 2.7626 | 3.985 | 4.7859 | 5.2074 | 6.0504 | 6.8934 | 0.86498 | 2.3496 | 2.947 | 2.947 | 2.947 | 2.947 | 1.6766 | 2.1281 | 2.1281 | 2.1281 | 2.1281 | 2.1281
2020-08-03 14:00 | Winter | 2.2482 | 3.4569 | 5.2309 | 5.2309 | 5.2309 | 5.2309 | 1.0117 | 1.0117 | 1.0117 | 1.0117 | 1.0117 | 1.0117 | 2.7245 | 3.93 | 4.7199 | 5.1356 | 5.967 | 6.7984 | 0.8345 | 2.2668 | 2.8432 | 2.8432 | 2.8432 | 2.8432 | 1.5242 | 1.9346 | 1.9346 | 1.9346 | 1.9346 | 1.9346
2020-08-03 15:00 | Winter | 2.172 | 3.3397 | 5.0536 | 5.0536 | 5.0536 | 5.0536 | 1.0803 | 1.0803 | 1.0803 | 1.0803 | 1.0803 | 1.0803 | 2.6483 | 3.8201 | 4.5878 | 4.9919 | 5.8 | 6.6082 | 0.84974 | 2.3082 | 2.8951 | 2.8951 | 2.8951 | 2.8951 | 1.4289 | 1.8137 | 1.8137 | 1.8137 | 1.8137 | 1.8137
2020-08-03 16:00 | Winter | 2.1529 | 3.3104 | 5.0093 | 5.0093 | 5.0093 | 5.0093 | 1.0488 | 1.0488 | 1.0488 | 1.0488 | 1.0488 | 1.0488 | 2.6102 | 3.7651 | 4.5218 | 4.9201 | 5.7166 | 6.5131 | 0.84212 | 2.2875 | 2.8691 | 2.8691 | 2.8691 | 2.8691 | 1.3337 | 1.6928 | 1.6928 | 1.6928 | 1.6928 | 1.6928
2020-08-03 17:00 | Winter | 2.0577 | 3.1639 | 4.7876 | 4.7876 | 4.7876 | 4.7876 | 1.0117 | 1.0117 | 1.0117 | 1.0117 | 1.0117 | 1.0117 | 2.6674 | 3.8476 | 4.6208 | 5.0278 | 5.8418 | 6.6557 | 0.85736 | 2.3289 | 2.9211 | 2.9211 | 2.9211 | 2.9211 | 1.2864 | 1.6328 | 1.6328 | 1.6328 | 1.6328 | 1.6328
2020-08-03 18:00 | Winter | 1.6106 | 2.4764 | 3.7473 | 3.7473 | 3.7473 | 3.7473 | 0.98025 | 0.98025 | 0.98025 | 0.98025 | 0.98025 | 0.98025 | 2.6864 | 3.8751 | 4.6539 | 5.0637 | 5.8835 | 6.7033 | 0.8345 | 2.2668 | 2.8432 | 2.8432 | 2.8432 | 2.8432 | 0.9636 | 1.2231 | 1.2231 | 1.2231 | 1.2231 | 1.2231
2020-08-03 19:00 | Winter | 1.1813 | 1.8163 | 2.7485 | 2.7485 | 2.7485 | 2.7485 | 0.6716 | 0.6716 | 0.6716 | 0.6716 | 0.6716 | 0.6716 | 2.523 | 3.6393 | 4.3707 | 4.7557 | 5.5256 | 6.2955 | 0.80021 | 2.1737 | 2.7263 | 2.7263 | 2.7263 | 2.7263 | 0.72146 | 0.91574 | 0.91574 | 0.91574 | 0.91574 | 0.91574
2020-08-03 20:00 | Winter | 1.1241 | 1.7284 | 2.6155 | 2.6155 | 2.6155 | 2.6155 | 0.54299 | 0.54299 | 0.54299 | 0.54299 | 0.54299 | 0.54299 | 2.3435 | 3.3804 | 4.0597 | 4.4173 | 5.1324 | 5.8475 | 0.75829 | 2.0598 | 2.5835 | 2.5835 | 2.5835 | 2.5835 | 0.64779 | 0.82222 | 0.82222 | 0.82222 | 0.82222 | 0.82222
2020-08-03 21:00 | Winter | 1.0291 | 1.5824 | 2.3945 | 2.3945 | 2.3945 | 2.3945 | 0.51442 | 0.51442 | 0.51442 | 0.51442 | 0.51442 | 0.51442 | 2.2673 | 3.2705 | 3.9277 | 4.2736 | 4.9655 | 5.6574 | 0.70494 | 1.9149 | 2.4018 | 2.4018 | 2.4018 | 2.4018 | 0.55278 | 0.70164 | 0.70164 | 0.70164 | 0.70164 | 0.70164
2020-08-03 22:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 2.0577 | 2.9681 | 3.5647 | 3.8786 | 4.5065 | 5.1344 | 0.63254 | 1.7182 | 2.1551 | 2.1551 | 2.1551 | 2.1551 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-08-03 23:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 1.8854 | 2.7196 | 3.2662 | 3.5539 | 4.1292 | 4.7045 | 0.66274 | 1.8003 | 2.258 | 2.258 | 2.258 | 2.258 | 0.49537 | 0.62876 | 0.62876 | 0.62876 | 0.62876 | 0.62876
2020-08-04 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.4001 | 0.4001 | 0.4001 | 0.4001 | 0.4001 | 0.4001 | 1.7147 | 2.4735 | 2.9705 | 3.2322 | 3.7554 | 4.2787 | 0.66303 | 1.8011 | 2.2589 | 2.2589 | 2.2589 | 2.2589 | 0.45726 | 0.58039 | 0.58039 | 0.58039 | 0.58039 | 0.58039
2020-08-04 01:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.4544 | 0.4544 | 0.4544 | 0.4544 | 0.4544 | 0.4544 | 1.6195 | 2.336 | 2.8055 | 3.0526 | 3.5468 | 4.041 | 0.63635 | 1.7286 | 2.1681 | 2.1681 | 2.1681 | 2.1681 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-08-04 02:00 | Winter | 1.2194 | 1.8749 | 2.8371 | 2.8371 | 2.8371 | 2.8371 | 0.48584 | 0.48584 | 0.48584 | 0.48584 | 0.48584 | 0.48584 | 1.6195 | 2.336 | 2.8055 | 3.0526 | 3.5468 | 4.041 | 0.56395 | 1.5319 | 1.9214 | 1.9214 | 1.9214 | 1.9214 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-08-04 03:00 | Winter | 1.1928 | 1.8341 | 2.7754 | 2.7754 | 2.7754 | 2.7754 | 0.40296 | 0.40296 | 0.40296 | 0.40296 | 0.40296 | 0.40296 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.58682 | 1.594 | 1.9993 | 1.9993 | 1.9993 | 1.9993 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-08-04 04:00 | Winter | 1.2565 | 1.932 | 2.9235 | 2.9235 | 2.9235 | 2.9235 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.57263 | 1.5555 | 1.951 | 1.951 | 1.951 | 1.951 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-08-04 05:00 | Winter | 1.5433 | 2.3729 | 3.5907 | 3.5907 | 3.5907 | 3.5907 | 0.75734 | 0.75734 | 0.75734 | 0.75734 | 0.75734 | 0.75734 | 1.9053 | 2.7483 | 3.3006 | 3.5913 | 4.1727 | 4.7541 | 0.6897 | 1.8735 | 2.3498 | 2.3498 | 2.3498 | 2.3498 | 0.78683 | 0.99871 | 0.99871 | 0.99871 | 0.99871 | 0.99871
2020-08-04 06:00 | Winter | 1.7719 | 2.7245 | 4.1227 | 4.1227 | 4.1227 | 4.1227 | 0.93452 | 0.93452 | 0.93452 | 0.93452 | 0.93452 | 0.93452 | 2.236 | 3.2254 | 3.8736 | 4.2148 | 4.8971 | 5.5794 | 0.78496 | 2.1323 | 2.6744 | 2.6744 | 2.6744 | 2.6744 | 0.97168 | 1.2333 | 1.2333 | 1.2333 | 1.2333 | 1.2333
2020-08-04 07:00 | Winter | 2.0386 | 3.1346 | 4.7433 | 4.7433 | 4.7433 | 4.7433 | 1.0803 | 1.0803 | 1.0803 | 1.0803 | 1.0803 | 1.0803 | 2.4959 | 3.6002 | 4.3238 | 4.7046 | 5.4662 | 6.2279 | 0.89928 | 2.4428 | 3.0639 | 3.0639 | 3.0639 | 3.0639 | 1.4315 | 1.817 | 1.817 | 1.817 | 1.817 | 1.817
2020-08-04 08:00 | Winter | 2.3816 | 3.6619 | 5.5412 | 5.5412 | 5.5412 | 5.5412 | 1.246 | 1.246 | 1.246 | 1.246 | 1.246 | 1.246 | 2.6674 | 3.8476 | 4.6208 | 5.0278 | 5.8418 | 6.6557 | 0.94501 | 2.567 | 3.2196 | 3.2196 | 3.2196 | 3.2196 | 1.6576 | 2.1039 | 2.1039 | 2.1039 | 2.1039 | 2.1039
2020-08-04 09:00 | Winter | 2.3244 | 3.5741 | 5.4082 | 5.4082 | 5.4082 | 5.4082 | 1.3118 | 1.3118 | 1.3118 | 1.3118 | 1.3118 | 1.3118 | 2.6674 | 3.8476 | 4.6208 | 5.0278 | 5.8418 | 6.6557 | 0.92214 | 2.5049 | 3.1418 | 3.1418 | 3.1418 | 3.1418 | 1.6063 | 2.0388 | 2.0388 | 2.0388 | 2.0388 | 2.0388
2020-08-04 10:00 | Winter | 2.2673 | 3.4862 | 5.2753 | 5.2753 | 5.2753 | 5.2753 | 1.2317 | 1.2317 | 1.2317 | 1.2317 | 1.2317 | 1.2317 | 2.6674 | 3.8476 | 4.6208 | 5.0278 | 5.8418 | 6.6557 | 0.83069 | 2.2565 | 2.8302 | 2.8302 | 2.8302 | 2.8302 | 1.6385 | 2.0797 | 2.0797 | 2.0797 | 2.0797 | 2.0797
2020-08-04 11:00 | Winter | 2.2673 | 3.4862 | 5.2753 | 5.2753 | 5.2753 | 5.2753 | 1.106 | 1.106 | 1.106 | 1.106 | 1.106 | 1.106 | 2.6674 | 3.8476 | 4.6208 | 5.0278 | 5.8418 | 6.6557 | 0.80402 | 2.184 | 2.7393 | 2.7393 | 2.7393 | 2.7393 | 1.6004 | 2.0314 | 2.0314 | 2.0314 | 2.0314 | 2.0314
2020-08-04 12:00 | Winter | 2.2673 | 3.4862 | 5.2753 | 5.2753 | 5.2753 | 5.2753 | 1.1089 | 1.1089 | 1.1089 | 1.1089 | 1.1089 | 1.1089 | 2.7245 | 3.93 | 4.7199 | 5.1356 | 5.967 | 6.7984 | 0.87642 | 2.3807 | 2.986 | 2.986 | 2.986 | 2.986 | 1.5623 | 1.983 | 1.983 | 1.983 | 1.983 | 1.983
2020-08-04 13:00 | Winter | 2.3244 | 3.5741 | 5.4082 | 5.4082 | 5.4082 | 5.4082 | 1.0374 | 1.0374 | 1.0374 | 1.0374 | 1.0374 | 1.0374 | 2.7245 | 3.93 | 4.7199 | 5.1356 | 5.967 | 6.7984 | 0.85355 | 2.3186 | 2.9081 | 2.9081 | 2.9081 | 2.9081 | 1.5814 | 2.0072 | 2.0072 | 2.0072 | 2.0072 | 2.0072
2020-08-04 14:00 | Winter | 2.2291 | 3.4276 | 5.1866 | 5.1866 | 5.1866 | 5.1866 | 0.94602 | 0.94602 | 0.94602 | 0.94602 | 0.94602 | 0.94602 | 2.6674 | 3.8476 | 4.6208 | 5.0278 | 5.8418 | 6.6557 | 0.87642 | 2.3807 | 2.986 | 2.986 | 2.986 | 2.986 | 1.4861 | 1.8863 | 1.8863 | 1.8863 | 1.8863 | 1.8863
2020-08-04 15:00 | Winter | 2.172 | 3.3397 | 5.0536 | 5.0536 | 5.0536 | 5.0536 | 1.0003 | 1.0003 | 1.0003 | 1.0003 | 1.0003 | 1.0003 | 2.5911 | 3.7377 | 4.4888 | 4.8842 | 5.6749 | 6.4656 | 0.83831 | 2.2772 | 2.8561 | 2.8561 | 2.8561 | 2.8561 | 1.4289 | 1.8137 | 1.8137 | 1.8137 | 1.8137 | 1.8137
2020-08-04 16:00 | Winter | 2.1529 | 3.3104 | 5.0093 | 5.0093 | 5.0093 | 5.0093 | 1.0288 | 1.0288 | 1.0288 | 1.0288 | 1.0288 | 1.0288 | 2.5911 | 3.7377 | 4.4888 | 4.8842 | 5.6749 | 6.4656 | 0.85355 | 2.3186 | 2.9081 | 2.9081 | 2.9081 | 2.9081 | 1.3718 | 1.7412 | 1.7412 | 1.7412 | 1.7412 | 1.7412
2020-08-04 17:00 | Winter | 2.1148 | 3.2518 | 4.9206 | 4.9206 | 4.9206 | 4.9206 | 0.9974 | 0.9974 | 0.9974 | 0.9974 | 0.9974 | 0.9974 | 2.7245 | 3.93 | 4.7199 | 5.1356 | 5.967 | 6.7984 | 0.87126 | 2.3667 | 2.9684 | 2.9684 | 2.9684 | 2.9684 | 1.3146 | 1.6686 | 1.6686 | 1.6686 | 1.6686 | 1.6686
2020-08-04 18:00 | Winter | 1.7468 | 2.686 | 4.0644 | 4.0644 | 4.0644 | 4.0644 | 0.90663 | 0.90663 | 0.90663 | 0.90663 | 0.90663 | 0.90663 | 2.8007 | 4.04 | 4.8519 | 5.2792 | 6.1339 | 6.9885 | 0.88404 | 2.4014 | 3.0119 | 3.0119 | 3.0119 | 3.0119 | 0.98804 | 1.2541 | 1.2541 | 1.2541 | 1.2541 | 1.2541
2020-08-04 19:00 | Winter | 1.2149 | 1.8681 | 2.8268 | 2.8268 | 2.8268 | 2.8268 | 0.6716 | 0.6716 | 0.6716 | 0.6716 | 0.6716 | 0.6716 | 2.5913 | 3.7378 | 4.489 | 4.8844 | 5.6751 | 6.4658 | 0.83831 | 2.2772 | 2.8561 | 2.8561 | 2.8561 | 2.8561 | 0.72418 | 0.91918 | 0.91918 | 0.91918 | 0.91918 | 0.91918
2020-08-04 20:00 | Winter | 1.105 | 1.6991 | 2.5711 | 2.5711 | 2.5711 | 2.5711 | 0.52585 | 0.52585 | 0.52585 | 0.52585 | 0.52585 | 0.52585 | 2.5149 | 3.6277 | 4.3568 | 4.7405 | 5.508 | 6.2754 | 0.76591 | 2.0805 | 2.6095 | 2.6095 | 2.6095 | 2.6095 | 0.61899 | 0.78568 | 0.78568 | 0.78568 | 0.78568 | 0.78568
2020-08-04 21:00 | Winter | 1.0669 | 1.6405 | 2.4825 | 2.4825 | 2.4825 | 2.4825 | 0.5287 | 0.5287 | 0.5287 | 0.5287 | 0.5287 | 0.5287 | 2.4578 | 3.5453 | 4.2578 | 4.6328 | 5.3828 | 6.1328 | 0.71637 | 1.946 | 2.4407 | 2.4407 | 2.4407 | 2.4407 | 0.55716 | 0.70719 | 0.70719 | 0.70719 | 0.70719 | 0.70719
2020-08-04 22:00 | Winter | 1.0486 | 1.6123 | 2.4397 | 2.4397 | 2.4397 | 2.4397 | 0.51156 | 0.51156 | 0.51156 | 0.51156 | 0.51156 | 0.51156 | 2.0975 | 3.0256 | 3.6337 | 3.9537 | 4.5938 | 5.2339 | 0.76591 | 2.0805 | 2.6095 | 2.6095 | 2.6095 | 2.6095 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-08-04 23:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.46401 | 0.46401 | 0.46401 | 0.46401 | 0.46401 | 0.46401 | 1.9053 | 2.7483 | 3.3006 | 3.5913 | 4.1727 | 4.7541 | 0.65922 | 1.7907 | 2.246 | 2.246 | 2.246 | 2.246 | 0.49537 | 0.62876 | 0.62876 | 0.62876 | 0.62876 | 0.62876
2020-08-05 | Winter | 1.0288 | 1.582 | 2.3938 | 2.3938 | 2.3938 | 2.3938 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 1.7909 | 2.5834 | 3.1026 | 3.3758 | 3.9223 | 4.4688 | 0.61349 | 1.6665 | 2.0902 | 2.0902 | 2.0902 | 2.0902 | 0.49537 | 0.62876 | 0.62876 | 0.62876 | 0.62876 | 0.62876
2020-08-05 01:00 | Winter | 1.0288 | 1.582 | 2.3938 | 2.3938 | 2.3938 | 2.3938 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 1.6957 | 2.446 | 2.9375 | 3.1963 | 3.7137 | 4.2311 | 0.59444 | 1.6147 | 2.0253 | 2.0253 | 2.0253 | 2.0253 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-08-05 02:00 | Winter | 1.2384 | 1.9042 | 2.8814 | 2.8814 | 2.8814 | 2.8814 | 0.48584 | 0.48584 | 0.48584 | 0.48584 | 0.48584 | 0.48584 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.54871 | 1.4905 | 1.8695 | 1.8695 | 1.8695 | 1.8695 | 0.48701 | 0.61815 | 0.61815 | 0.61815 | 0.61815 | 0.61815
2020-08-05 03:00 | Winter | 1.2384 | 1.9042 | 2.8814 | 2.8814 | 2.8814 | 2.8814 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.54871 | 1.4905 | 1.8695 | 1.8695 | 1.8695 | 1.8695 | 0.53339 | 0.67702 | 0.67702 | 0.67702 | 0.67702 | 0.67702
2020-08-05 04:00 | Winter | 1.2383 | 1.9041 | 2.8813 | 2.8813 | 2.8813 | 2.8813 | 0.56586 | 0.56586 | 0.56586 | 0.56586 | 0.56586 | 0.56586 | 1.7472 | 2.5202 | 3.0267 | 3.2933 | 3.8265 | 4.3596 | 0.5792 | 1.5733 | 1.9733 | 1.9733 | 1.9733 | 1.9733 | 0.55252 | 0.70131 | 0.70131 | 0.70131 | 0.70131 | 0.70131
2020-08-05 05:00 | Winter | 1.5547 | 2.3905 | 3.6173 | 3.6173 | 3.6173 | 3.6173 | 0.6373 | 0.6373 | 0.6373 | 0.6373 | 0.6373 | 0.6373 | 1.9988 | 2.8832 | 3.4626 | 3.7676 | 4.3775 | 4.9875 | 0.73359 | 1.9927 | 2.4994 | 2.4994 | 2.4994 | 2.4994 | 0.78178 | 0.99229 | 0.99229 | 0.99229 | 0.99229 | 0.99229
2020-08-05 06:00 | Winter | 1.9113 | 2.9388 | 4.447 | 4.447 | 4.447 | 4.447 | 0.76014 | 0.76014 | 0.76014 | 0.76014 | 0.76014 | 0.76014 | 2.2061 | 3.1823 | 3.8218 | 4.1584 | 4.8316 | 5.5048 | 0.78496 | 2.1323 | 2.6744 | 2.6744 | 2.6744 | 2.6744 | 0.99073 | 1.2575 | 1.2575 | 1.2575 | 1.2575 | 1.2575
2020-08-05 07:00 | Winter | 2.172 | 3.3397 | 5.0536 | 5.0536 | 5.0536 | 5.0536 | 1.2089 | 1.2089 | 1.2089 | 1.2089 | 1.2089 | 1.2089 | 2.5187 | 3.6331 | 4.3633 | 4.7476 | 5.5161 | 6.2847 | 0.89166 | 2.4221 | 3.0379 | 3.0379 | 3.0379 | 3.0379 | 1.3908 | 1.7654 | 1.7654 | 1.7654 | 1.7654 | 1.7654
2020-08-05 08:00 | Winter | 2.4768 | 3.8084 | 5.7629 | 5.7629 | 5.7629 | 5.7629 | 1.3089 | 1.3089 | 1.3089 | 1.3089 | 1.3089 | 1.3089 | 2.7841 | 4.016 | 4.8231 | 5.2479 | 6.0974 | 6.947 | 0.9069 | 2.4635 | 3.0898 | 3.0898 | 3.0898 | 3.0898 | 1.6195 | 2.0556 | 2.0556 | 2.0556 | 2.0556 | 2.0556
2020-08-05 09:00 | Winter | 2.4427 | 3.756 | 5.6835 | 5.6835 | 5.6835 | 5.6835 | 1.2632 | 1.2632 | 1.2632 | 1.2632 | 1.2632 | 1.2632 | 2.8388 | 4.0949 | 4.9179 | 5.351 | 6.2173 | 7.0836 | 0.92976 | 2.5256 | 3.1677 | 3.1677 | 3.1677 | 3.1677 | 1.7147 | 2.1765 | 2.1765 | 2.1765 | 2.1765 | 2.1765
2020-08-05 10:00 | Winter | 2.3435 | 3.6034 | 5.4526 | 5.4526 | 5.4526 | 5.4526 | 1.2146 | 1.2146 | 1.2146 | 1.2146 | 1.2146 | 1.2146 | 2.8007 | 4.04 | 4.8519 | 5.2792 | 6.1339 | 6.9885 | 0.84593 | 2.2979 | 2.8821 | 2.8821 | 2.8821 | 2.8821 | 1.7147 | 2.1765 | 2.1765 | 2.1765 | 2.1765 | 2.1765
2020-08-05 11:00 | Winter | 2.3435 | 3.6034 | 5.4526 | 5.4526 | 5.4526 | 5.4526 | 1.166 | 1.166 | 1.166 | 1.166 | 1.166 | 1.166 | 2.7604 | 3.9818 | 4.782 | 5.2032 | 6.0455 | 6.8879 | 0.85355 | 2.3186 | 2.9081 | 2.9081 | 2.9081 | 2.9081 | 1.6957 | 2.1523 | 2.1523 | 2.1523 | 2.1523 | 2.1523
2020-08-05 12:00 | Winter | 2.3435 | 3.6034 | 5.4526 | 5.4526 | 5.4526 | 5.4526 | 1.1203 | 1.1203 | 1.1203 | 1.1203 | 1.1203 | 1.1203 | 2.7817 | 4.0125 | 4.8189 | 5.2433 | 6.0921 | 6.941 | 0.86117 | 2.3393 | 2.934 | 2.934 | 2.934 | 2.934 | 1.6024 | 2.0339 | 2.0339 | 2.0339 | 2.0339 | 2.0339
2020-08-05 13:00 | Winter | 2.2863 | 3.5155 | 5.3196 | 5.3196 | 5.3196 | 5.3196 | 1.0803 | 1.0803 | 1.0803 | 1.0803 | 1.0803 | 1.0803 | 2.7817 | 4.0125 | 4.8189 | 5.2433 | 6.0921 | 6.941 | 0.92595 | 2.5153 | 3.1547 | 3.1547 | 3.1547 | 3.1547 | 1.6195 | 2.0556 | 2.0556 | 2.0556 | 2.0556 | 2.0556
2020-08-05 14:00 | Winter | 2.2101 | 3.3983 | 5.1423 | 5.1423 | 5.1423 | 5.1423 | 1.0774 | 1.0774 | 1.0774 | 1.0774 | 1.0774 | 1.0774 | 2.6864 | 3.8751 | 4.6539 | 5.0637 | 5.8835 | 6.7033 | 0.80021 | 2.1737 | 2.7263 | 2.7263 | 2.7263 | 2.7263 | 1.5242 | 1.9346 | 1.9346 | 1.9346 | 1.9346 | 1.9346
2020-08-05 15:00 | Winter | 2.191 | 3.369 | 5.0979 | 5.0979 | 5.0979 | 5.0979 | 1.0003 | 1.0003 | 1.0003 | 1.0003 | 1.0003 | 1.0003 | 2.7055 | 3.9026 | 4.6869 | 5.0996 | 5.9252 | 6.7508 | 0.86498 | 2.3496 | 2.947 | 2.947 | 2.947 | 2.947 | 1.4289 | 1.8137 | 1.8137 | 1.8137 | 1.8137 | 1.8137
2020-08-05 16:00 | Winter | 2.2101 | 3.3983 | 5.1423 | 5.1423 | 5.1423 | 5.1423 | 1.0603 | 1.0603 | 1.0603 | 1.0603 | 1.0603 | 1.0603 | 2.7055 | 3.9026 | 4.6869 | 5.0996 | 5.9252 | 6.7508 | 0.89166 | 2.4221 | 3.0379 | 3.0379 | 3.0379 | 3.0379 | 1.3718 | 1.7412 | 1.7412 | 1.7412 | 1.7412 | 1.7412
2020-08-05 17:00 | Winter | 2.1148 | 3.2518 | 4.9206 | 4.9206 | 4.9206 | 4.9206 | 1.0174 | 1.0174 | 1.0174 | 1.0174 | 1.0174 | 1.0174 | 2.896 | 4.1774 | 5.0169 | 5.4588 | 6.3425 | 7.2262 | 0.83831 | 2.2772 | 2.8561 | 2.8561 | 2.8561 | 2.8561 | 1.3527 | 1.717 | 1.717 | 1.717 | 1.717 | 1.717
2020-08-05 18:00 | Winter | 1.7317 | 2.6627 | 4.0292 | 4.0292 | 4.0292 | 4.0292 | 0.94596 | 0.94596 | 0.94596 | 0.94596 | 0.94596 | 0.94596 | 2.8198 | 4.0675 | 4.8849 | 5.3151 | 6.1756 | 7.0361 | 0.88404 | 2.4014 | 3.0119 | 3.0119 | 3.0119 | 3.0119 | 0.9945 | 1.2623 | 1.2623 | 1.2623 | 1.2623 | 1.2623
2020-08-05 19:00 | Winter | 1.2194 | 1.8749 | 2.8371 | 2.8371 | 2.8371 | 2.8371 | 0.75817 | 0.75817 | 0.75817 | 0.75817 | 0.75817 | 0.75817 | 2.7245 | 3.93 | 4.7199 | 5.1356 | 5.967 | 6.7984 | 0.79258 | 2.153 | 2.7003 | 2.7003 | 2.7003 | 2.7003 | 0.724 | 0.91895 | 0.91895 | 0.91895 | 0.91895 | 0.91895
2020-08-05 20:00 | Winter | 1.1432 | 1.7577 | 2.6598 | 2.6598 | 2.6598 | 2.6598 | 0.60587 | 0.60587 | 0.60587 | 0.60587 | 0.60587 | 0.60587 | 2.6102 | 3.7651 | 4.5218 | 4.9201 | 5.7166 | 6.5131 | 0.75829 | 2.0598 | 2.5835 | 2.5835 | 2.5835 | 2.5835 | 0.64867 | 0.82334 | 0.82334 | 0.82334 | 0.82334 | 0.82334
2020-08-05 21:00 | Winter | 1.067 | 1.6407 | 2.4827 | 2.4827 | 2.4827 | 2.4827 | 0.54585 | 0.54585 | 0.54585 | 0.54585 | 0.54585 | 0.54585 | 2.4197 | 3.4903 | 4.1918 | 4.561 | 5.2993 | 6.0377 | 0.74686 | 2.0288 | 2.5446 | 2.5446 | 2.5446 | 2.5446 | 0.57158 | 0.72549 | 0.72549 | 0.72549 | 0.72549 | 0.72549
2020-08-05 22:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 0.52013 | 0.52013 | 0.52013 | 0.52013 | 0.52013 | 0.52013 | 2.2486 | 3.2435 | 3.8954 | 4.2384 | 4.9246 | 5.6108 | 0.67827 | 1.8425 | 2.3109 | 2.3109 | 2.3109 | 2.3109 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-08-05 23:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.49727 | 0.49727 | 0.49727 | 0.49727 | 0.49727 | 0.49727 | 2.0196 | 2.9132 | 3.4986 | 3.8068 | 4.4231 | 5.0393 | 0.63003 | 1.7114 | 2.1465 | 2.1465 | 2.1465 | 2.1465 | 0.49537 | 0.62876 | 0.62876 | 0.62876 | 0.62876 | 0.62876
2020-08-06 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 1.8293 | 2.6387 | 3.1689 | 3.448 | 4.0063 | 4.5645 | 0.65541 | 1.7803 | 2.233 | 2.233 | 2.233 | 2.233 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-08-06 01:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.48869 | 0.48869 | 0.48869 | 0.48869 | 0.48869 | 0.48869 | 1.7528 | 2.5284 | 3.0366 | 3.304 | 3.8389 | 4.3738 | 0.56014 | 1.5216 | 1.9084 | 1.9084 | 1.9084 | 1.9084 | 0.49537 | 0.62876 | 0.62876 | 0.62876 | 0.62876 | 0.62876
2020-08-06 02:00 | Winter | 1.1641 | 1.7899 | 2.7084 | 2.7084 | 2.7084 | 2.7084 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 1.6576 | 2.391 | 2.8715 | 3.1244 | 3.6302 | 4.1361 | 0.52966 | 1.4388 | 1.8046 | 1.8046 | 1.8046 | 1.8046 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-08-06 03:00 | Winter | 1.2003 | 1.8456 | 2.7928 | 2.7928 | 2.7928 | 2.7928 | 0.46869 | 0.46869 | 0.46869 | 0.46869 | 0.46869 | 0.46869 | 1.7417 | 2.5124 | 3.0173 | 3.2831 | 3.8146 | 4.3461 | 0.56395 | 1.5319 | 1.9214 | 1.9214 | 1.9214 | 1.9214 | 0.49537 | 0.62876 | 0.62876 | 0.62876 | 0.62876 | 0.62876
2020-08-06 04:00 | Winter | 1.2003 | 1.8456 | 2.7928 | 2.7928 | 2.7928 | 2.7928 | 0.52013 | 0.52013 | 0.52013 | 0.52013 | 0.52013 | 0.52013 | 1.7528 | 2.5284 | 3.0366 | 3.304 | 3.8389 | 4.3738 | 0.5792 | 1.5733 | 1.9733 | 1.9733 | 1.9733 | 1.9733 | 0.55252 | 0.70131 | 0.70131 | 0.70131 | 0.70131 | 0.70131
2020-08-06 05:00 | Winter | 1.5429 | 2.3724 | 3.5899 | 3.5899 | 3.5899 | 3.5899 | 0.70361 | 0.70361 | 0.70361 | 0.70361 | 0.70361 | 0.70361 | 1.9621 | 2.8303 | 3.3991 | 3.6985 | 4.2972 | 4.896 | 0.68589 | 1.8632 | 2.3368 | 2.3368 | 2.3368 | 2.3368 | 0.70454 | 0.89425 | 0.89425 | 0.89425 | 0.89425 | 0.89425
2020-08-06 06:00 | Winter | 1.8767 | 2.8857 | 4.3666 | 4.3666 | 4.3666 | 4.3666 | 0.77695 | 0.77695 | 0.77695 | 0.77695 | 0.77695 | 0.77695 | 2.2672 | 3.2703 | 3.9276 | 4.2735 | 4.9653 | 5.6571 | 0.78877 | 2.1426 | 2.6874 | 2.6874 | 2.6874 | 2.6874 | 0.99073 | 1.2575 | 1.2575 | 1.2575 | 1.2575 | 1.2575
2020-08-06 07:00 | Winter | 2.2863 | 3.5155 | 5.3196 | 5.3196 | 5.3196 | 5.3196 | 1.2232 | 1.2232 | 1.2232 | 1.2232 | 1.2232 | 1.2232 | 2.5721 | 3.7102 | 4.4558 | 4.8483 | 5.6331 | 6.418 | 0.86879 | 2.36 | 2.96 | 2.96 | 2.96 | 2.96 | 1.448 | 1.8379 | 1.8379 | 1.8379 | 1.8379 | 1.8379
2020-08-06 08:00 | Winter | 2.3816 | 3.6619 | 5.5412 | 5.5412 | 5.5412 | 5.5412 | 1.3603 | 1.3603 | 1.3603 | 1.3603 | 1.3603 | 1.3603 | 2.8007 | 4.04 | 4.8519 | 5.2792 | 6.1339 | 6.9885 | 0.89928 | 2.4428 | 3.0639 | 3.0639 | 3.0639 | 3.0639 | 1.6576 | 2.1039 | 2.1039 | 2.1039 | 2.1039 | 2.1039
2020-08-06 09:00 | Winter | 2.3816 | 3.6619 | 5.5412 | 5.5412 | 5.5412 | 5.5412 | 1.3603 | 1.3603 | 1.3603 | 1.3603 | 1.3603 | 1.3603 | 2.8388 | 4.0949 | 4.9179 | 5.351 | 6.2173 | 7.0836 | 0.89928 | 2.4428 | 3.0639 | 3.0639 | 3.0639 | 3.0639 | 1.6766 | 2.1281 | 2.1281 | 2.1281 | 2.1281 | 2.1281
2020-08-06 10:00 | Winter | 2.3054 | 3.5448 | 5.3639 | 5.3639 | 5.3639 | 5.3639 | 1.2889 | 1.2889 | 1.2889 | 1.2889 | 1.2889 | 1.2889 | 2.8198 | 4.0675 | 4.8849 | 5.3151 | 6.1756 | 7.0361 | 0.81926 | 2.2254 | 2.7912 | 2.7912 | 2.7912 | 2.7912 | 1.6766 | 2.1281 | 2.1281 | 2.1281 | 2.1281 | 2.1281
2020-08-06 11:00 | Winter | 2.2673 | 3.4862 | 5.2753 | 5.2753 | 5.2753 | 5.2753 | 1.2832 | 1.2832 | 1.2832 | 1.2832 | 1.2832 | 1.2832 | 2.8198 | 4.0675 | 4.8849 | 5.3151 | 6.1756 | 7.0361 | 0.81926 | 2.2254 | 2.7912 | 2.7912 | 2.7912 | 2.7912 | 1.6729 | 2.1234 | 2.1234 | 2.1234 | 2.1234 | 2.1234
2020-08-06 12:00 | Winter | 2.2673 | 3.4862 | 5.2753 | 5.2753 | 5.2753 | 5.2753 | 1.1746 | 1.1746 | 1.1746 | 1.1746 | 1.1746 | 1.1746 | 2.7626 | 3.985 | 4.7859 | 5.2074 | 6.0504 | 6.8934 | 0.82307 | 2.2358 | 2.8042 | 2.8042 | 2.8042 | 2.8042 | 1.6195 | 2.0556 | 2.0556 | 2.0556 | 2.0556 | 2.0556
2020-08-06 13:00 | Winter | 2.2863 | 3.5155 | 5.3196 | 5.3196 | 5.3196 | 5.3196 | 0.97453 | 0.97453 | 0.97453 | 0.97453 | 0.97453 | 0.97453 | 2.7245 | 3.93 | 4.7199 | 5.1356 | 5.967 | 6.7984 | 0.86879 | 2.36 | 2.96 | 2.96 | 2.96 | 2.96 | 1.5242 | 1.9346 | 1.9346 | 1.9346 | 1.9346 | 1.9346
2020-08-06 14:00 | Winter | 2.2101 | 3.3983 | 5.1423 | 5.1423 | 5.1423 | 5.1423 | 0.95167 | 0.95167 | 0.95167 | 0.95167 | 0.95167 | 0.95167 | 2.7055 | 3.9026 | 4.6869 | 5.0996 | 5.9252 | 6.7508 | 0.86879 | 2.36 | 2.96 | 2.96 | 2.96 | 2.96 | 1.5052 | 1.9105 | 1.9105 | 1.9105 | 1.9105 | 1.9105
2020-08-06 15:00 | Winter | 2.191 | 3.369 | 5.0979 | 5.0979 | 5.0979 | 5.0979 | 0.97168 | 0.97168 | 0.97168 | 0.97168 | 0.97168 | 0.97168 | 2.5911 | 3.7377 | 4.4888 | 4.8842 | 5.6749 | 6.4656 | 0.89547 | 2.4325 | 3.0509 | 3.0509 | 3.0509 | 3.0509 | 1.467 | 1.8621 | 1.8621 | 1.8621 | 1.8621 | 1.8621
2020-08-06 16:00 | Winter | 2.1339 | 3.2811 | 4.9649 | 4.9649 | 4.9649 | 4.9649 | 0.98597 | 0.98597 | 0.98597 | 0.98597 | 0.98597 | 0.98597 | 2.5721 | 3.7102 | 4.4558 | 4.8483 | 5.6331 | 6.418 | 0.86117 | 2.3393 | 2.934 | 2.934 | 2.934 | 2.934 | 1.3718 | 1.7412 | 1.7412 | 1.7412 | 1.7412 | 1.7412
2020-08-06 17:00 | Winter | 2.0196 | 3.1053 | 4.699 | 4.699 | 4.699 | 4.699 | 0.99168 | 0.99168 | 0.99168 | 0.99168 | 0.99168 | 0.99168 | 2.6483 | 3.8201 | 4.5878 | 4.9919 | 5.8 | 6.6082 | 0.86794 | 2.3577 | 2.9571 | 2.9571 | 2.9571 | 2.9571 | 1.3718 | 1.7412 | 1.7412 | 1.7412 | 1.7412 | 1.7412
2020-08-06 18:00 | Winter | 1.7547 | 2.698 | 4.0826 | 4.0826 | 4.0826 | 4.0826 | 0.93244 | 0.93244 | 0.93244 | 0.93244 | 0.93244 | 0.93244 | 2.6674 | 3.8476 | 4.6208 | 5.0278 | 5.8418 | 6.6557 | 0.93357 | 2.536 | 3.1807 | 3.1807 | 3.1807 | 3.1807 | 0.99178 | 1.2588 | 1.2588 | 1.2588 | 1.2588 | 1.2588
2020-08-06 19:00 | Winter | 1.2003 | 1.8456 | 2.7928 | 2.7928 | 2.7928 | 2.7928 | 0.6916 | 0.6916 | 0.6916 | 0.6916 | 0.6916 | 0.6916 | 2.6483 | 3.8201 | 4.5878 | 4.9919 | 5.8 | 6.6082 | 0.86879 | 2.36 | 2.96 | 2.96 | 2.96 | 2.96 | 0.70498 | 0.89482 | 0.89482 | 0.89482 | 0.89482 | 0.89482
2020-08-06 20:00 | Winter | 1.1936 | 1.8352 | 2.7771 | 2.7771 | 2.7771 | 2.7771 | 0.59729 | 0.59729 | 0.59729 | 0.59729 | 0.59729 | 0.59729 | 2.4578 | 3.5453 | 4.2578 | 4.6328 | 5.3828 | 6.1328 | 0.83069 | 2.2565 | 2.8302 | 2.8302 | 2.8302 | 2.8302 | 0.64827 | 0.82284 | 0.82284 | 0.82284 | 0.82284 | 0.82284
2020-08-06 21:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 0.58872 | 0.58872 | 0.58872 | 0.58872 | 0.58872 | 0.58872 | 2.351 | 3.3913 | 4.0729 | 4.4316 | 5.149 | 5.8664 | 0.73924 | 2.0081 | 2.5186 | 2.5186 | 2.5186 | 2.5186 | 0.55252 | 0.70131 | 0.70131 | 0.70131 | 0.70131 | 0.70131
2020-08-06 22:00 | Winter | 1.0288 | 1.582 | 2.3938 | 2.3938 | 2.3938 | 2.3938 | 0.57729 | 0.57729 | 0.57729 | 0.57729 | 0.57729 | 0.57729 | 2.096 | 3.0234 | 3.631 | 3.9508 | 4.5904 | 5.23 | 0.6897 | 1.8735 | 2.3498 | 2.3498 | 2.3498 | 2.3498 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-08-06 23:00 | Winter | 1.0288 | 1.582 | 2.3938 | 2.3938 | 2.3938 | 2.3938 | 0.48584 | 0.48584 | 0.48584 | 0.48584 | 0.48584 | 0.48584 | 1.9056 | 2.7488 | 3.3012 | 3.592 | 4.1735 | 4.755 | 0.64779 | 1.7596 | 2.207 | 2.207 | 2.207 | 2.207 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-08-07 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.51442 | 0.51442 | 0.51442 | 0.51442 | 0.51442 | 0.51442 | 1.7249 | 2.4881 | 2.9882 | 3.2514 | 3.7777 | 4.3041 | 0.59063 | 1.6044 | 2.0123 | 2.0123 | 2.0123 | 2.0123 | 0.46992 | 0.59646 | 0.59646 | 0.59646 | 0.59646 | 0.59646
2020-08-07 01:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 1.6576 | 2.391 | 2.8715 | 3.1244 | 3.6302 | 4.1361 | 0.59063 | 1.6044 | 2.0123 | 2.0123 | 2.0123 | 2.0123 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-08-07 02:00 | Winter | 1.2003 | 1.8456 | 2.7928 | 2.7928 | 2.7928 | 2.7928 | 0.48012 | 0.48012 | 0.48012 | 0.48012 | 0.48012 | 0.48012 | 1.6195 | 2.336 | 2.8055 | 3.0526 | 3.5468 | 4.041 | 0.57539 | 1.563 | 1.9603 | 1.9603 | 1.9603 | 1.9603 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-08-07 03:00 | Winter | 1.2003 | 1.8456 | 2.7928 | 2.7928 | 2.7928 | 2.7928 | 0.41439 | 0.41439 | 0.41439 | 0.41439 | 0.41439 | 0.41439 | 1.6576 | 2.391 | 2.8715 | 3.1244 | 3.6302 | 4.1361 | 0.58301 | 1.5837 | 1.9863 | 1.9863 | 1.9863 | 1.9863 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-08-07 04:00 | Winter | 1.2003 | 1.8456 | 2.7928 | 2.7928 | 2.7928 | 2.7928 | 0.51727 | 0.51727 | 0.51727 | 0.51727 | 0.51727 | 0.51727 | 1.6957 | 2.446 | 2.9375 | 3.1963 | 3.7137 | 4.2311 | 0.60968 | 1.6561 | 2.0772 | 2.0772 | 2.0772 | 2.0772 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-08-07 05:00 | Winter | 1.5433 | 2.3729 | 3.5907 | 3.5907 | 3.5907 | 3.5907 | 0.63159 | 0.63159 | 0.63159 | 0.63159 | 0.63159 | 0.63159 | 1.9239 | 2.7752 | 3.333 | 3.6265 | 4.2136 | 4.8007 | 0.72018 | 1.9563 | 2.4537 | 2.4537 | 2.4537 | 2.4537 | 0.7771 | 0.98635 | 0.98635 | 0.98635 | 0.98635 | 0.98635
2020-08-07 06:00 | Winter | 1.8315 | 2.8161 | 4.2613 | 4.2613 | 4.2613 | 4.2613 | 0.77162 | 0.77162 | 0.77162 | 0.77162 | 0.77162 | 0.77162 | 2.1699 | 3.1301 | 3.7591 | 4.0902 | 4.7524 | 5.4145 | 0.75067 | 2.0391 | 2.5575 | 2.5575 | 2.5575 | 2.5575 | 1.0219 | 1.297 | 1.297 | 1.297 | 1.297 | 1.297
2020-08-07 07:00 | Winter | 2.0983 | 3.2264 | 4.8822 | 4.8822 | 4.8822 | 4.8822 | 0.95931 | 0.95931 | 0.95931 | 0.95931 | 0.95931 | 0.95931 | 2.534 | 3.6552 | 4.3898 | 4.7764 | 5.5497 | 6.3229 | 0.87261 | 2.3704 | 2.973 | 2.973 | 2.973 | 2.973 | 1.3527 | 1.717 | 1.717 | 1.717 | 1.717 | 1.717
2020-08-07 08:00 | Winter | 2.4006 | 3.6912 | 5.5856 | 5.5856 | 5.5856 | 5.5856 | 1.046 | 1.046 | 1.046 | 1.046 | 1.046 | 1.046 | 2.7111 | 3.9107 | 4.6966 | 5.1103 | 5.9376 | 6.7649 | 0.92976 | 2.5256 | 3.1677 | 3.1677 | 3.1677 | 3.1677 | 1.5242 | 1.9346 | 1.9346 | 1.9346 | 1.9346 | 1.9346
2020-08-07 09:00 | Winter | 2.4006 | 3.6912 | 5.5856 | 5.5856 | 5.5856 | 5.5856 | 1.0917 | 1.0917 | 1.0917 | 1.0917 | 1.0917 | 1.0917 | 2.915 | 4.2049 | 5.0499 | 5.4947 | 6.3842 | 7.2738 | 0.87642 | 2.3807 | 2.986 | 2.986 | 2.986 | 2.986 | 1.6766 | 2.1281 | 2.1281 | 2.1281 | 2.1281 | 2.1281
2020-08-07 10:00 | Winter | 2.4006 | 3.6912 | 5.5856 | 5.5856 | 5.5856 | 5.5856 | 1.0974 | 1.0974 | 1.0974 | 1.0974 | 1.0974 | 1.0974 | 2.9341 | 4.2323 | 5.0829 | 5.5306 | 6.426 | 7.3213 | 0.89166 | 2.4221 | 3.0379 | 3.0379 | 3.0379 | 3.0379 | 1.6576 | 2.1039 | 2.1039 | 2.1039 | 2.1039 | 2.1039
2020-08-07 11:00 | Winter | 2.3244 | 3.5741 | 5.4082 | 5.4082 | 5.4082 | 5.4082 | 1.0631 | 1.0631 | 1.0631 | 1.0631 | 1.0631 | 1.0631 | 2.9531 | 4.2598 | 5.1159 | 5.5665 | 6.4677 | 7.3688 | 0.92214 | 2.5049 | 3.1418 | 3.1418 | 3.1418 | 3.1418 | 1.6576 | 2.1039 | 2.1039 | 2.1039 | 2.1039 | 2.1039
2020-08-07 12:00 | Winter | 2.3435 | 3.6034 | 5.4526 | 5.4526 | 5.4526 | 5.4526 | 1.2117 | 1.2117 | 1.2117 | 1.2117 | 1.2117 | 1.2117 | 2.9531 | 4.2598 | 5.1159 | 5.5665 | 6.4677 | 7.3688 | 0.86879 | 2.36 | 2.96 | 2.96 | 2.96 | 2.96 | 1.6195 | 2.0556 | 2.0556 | 2.0556 | 2.0556 | 2.0556
2020-08-07 13:00 | Winter | 2.3244 | 3.5741 | 5.4082 | 5.4082 | 5.4082 | 5.4082 | 1.1603 | 1.1603 | 1.1603 | 1.1603 | 1.1603 | 1.1603 | 2.9341 | 4.2323 | 5.0829 | 5.5306 | 6.426 | 7.3213 | 0.91071 | 2.4739 | 3.1028 | 3.1028 | 3.1028 | 3.1028 | 1.6385 | 2.0797 | 2.0797 | 2.0797 | 2.0797 | 2.0797
2020-08-07 14:00 | Winter | 2.3244 | 3.5741 | 5.4082 | 5.4082 | 5.4082 | 5.4082 | 1.1431 | 1.1431 | 1.1431 | 1.1431 | 1.1431 | 1.1431 | 2.9341 | 4.2323 | 5.0829 | 5.5306 | 6.426 | 7.3213 | 0.9069 | 2.4635 | 3.0898 | 3.0898 | 3.0898 | 3.0898 | 1.5435 | 1.9591 | 1.9591 | 1.9591 | 1.9591 | 1.9591
2020-08-07 15:00 | Winter | 2.2482 | 3.4569 | 5.2309 | 5.2309 | 5.2309 | 5.2309 | 1.1517 | 1.1517 | 1.1517 | 1.1517 | 1.1517 | 1.1517 | 2.8769 | 4.1499 | 4.9839 | 5.4229 | 6.3008 | 7.1787 | 0.92595 | 2.5153 | 3.1547 | 3.1547 | 3.1547 | 3.1547 | 1.467 | 1.8621 | 1.8621 | 1.8621 | 1.8621 | 1.8621
2020-08-07 16:00 | Winter | 2.172 | 3.3397 | 5.0536 | 5.0536 | 5.0536 | 5.0536 | 1.266 | 1.266 | 1.266 | 1.266 | 1.266 | 1.266 | 2.896 | 4.1774 | 5.0169 | 5.4588 | 6.3425 | 7.2262 | 0.91452 | 2.4842 | 3.1158 | 3.1158 | 3.1158 | 3.1158 | 1.3908 | 1.7654 | 1.7654 | 1.7654 | 1.7654 | 1.7654
2020-08-07 17:00 | Winter | 2.1148 | 3.2518 | 4.9206 | 4.9206 | 4.9206 | 4.9206 | 1.106 | 1.106 | 1.106 | 1.106 | 1.106 | 1.106 | 2.896 | 4.1774 | 5.0169 | 5.4588 | 6.3425 | 7.2262 | 0.89166 | 2.4221 | 3.0379 | 3.0379 | 3.0379 | 3.0379 | 1.2956 | 1.6444 | 1.6444 | 1.6444 | 1.6444 | 1.6444
2020-08-07 18:00 | Winter | 1.81 | 2.7831 | 4.2113 | 4.2113 | 4.2113 | 4.2113 | 0.92595 | 0.92595 | 0.92595 | 0.92595 | 0.92595 | 0.92595 | 2.7626 | 3.985 | 4.7859 | 5.2074 | 6.0504 | 6.8934 | 0.90309 | 2.4532 | 3.0768 | 3.0768 | 3.0768 | 3.0768 | 0.94449 | 1.1988 | 1.1988 | 1.1988 | 1.1988 | 1.1988
2020-08-07 19:00 | Winter | 1.1813 | 1.8163 | 2.7485 | 2.7485 | 2.7485 | 2.7485 | 0.70875 | 0.70875 | 0.70875 | 0.70875 | 0.70875 | 0.70875 | 2.5769 | 3.7171 | 4.4641 | 4.8573 | 5.6437 | 6.43 | 0.83069 | 2.2565 | 2.8302 | 2.8302 | 2.8302 | 2.8302 | 0.68589 | 0.87059 | 0.87059 | 0.87059 | 0.87059 | 0.87059
2020-08-07 20:00 | Winter | 1.086 | 1.6698 | 2.5268 | 2.5268 | 2.5268 | 2.5268 | 0.60301 | 0.60301 | 0.60301 | 0.60301 | 0.60301 | 0.60301 | 2.4387 | 3.5178 | 4.2248 | 4.5969 | 5.3411 | 6.0852 | 0.77353 | 2.1012 | 2.6354 | 2.6354 | 2.6354 | 2.6354 | 0.62873 | 0.79804 | 0.79804 | 0.79804 | 0.79804 | 0.79804
2020-08-07 21:00 | Winter | 1.0669 | 1.6405 | 2.4825 | 2.4825 | 2.4825 | 2.4825 | 0.57443 | 0.57443 | 0.57443 | 0.57443 | 0.57443 | 0.57443 | 2.3625 | 3.4079 | 4.0927 | 4.4532 | 5.1741 | 5.8951 | 0.78115 | 2.1219 | 2.6614 | 2.6614 | 2.6614 | 2.6614 | 0.55252 | 0.70131 | 0.70131 | 0.70131 | 0.70131 | 0.70131
2020-08-07 22:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.55157 | 0.55157 | 0.55157 | 0.55157 | 0.55157 | 0.55157 | 2.1529 | 3.1056 | 3.7297 | 4.0582 | 4.7151 | 5.3721 | 0.73543 | 1.9977 | 2.5056 | 2.5056 | 2.5056 | 2.5056 | 0.49537 | 0.62876 | 0.62876 | 0.62876 | 0.62876 | 0.62876
2020-08-07 23:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 0.44069 | 0.44069 | 0.44069 | 0.44069 | 0.44069 | 0.44069 | 1.9955 | 2.8785 | 3.457 | 3.7615 | 4.3704 | 4.9794 | 0.68589 | 1.8632 | 2.3368 | 2.3368 | 2.3368 | 2.3368 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-08-08 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.36604 | 0.36604 | 0.36604 | 0.36604 | 0.36604 | 0.36604 | 1.7719 | 2.5559 | 3.0696 | 3.3399 | 3.8806 | 4.4213 | 0.68227 | 1.8533 | 2.3245 | 2.3245 | 2.3245 | 2.3245 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-08-08 01:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.35443 | 0.35443 | 0.35443 | 0.35443 | 0.35443 | 0.35443 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.59825 | 1.6251 | 2.0382 | 2.0382 | 2.0382 | 2.0382 | 0.49537 | 0.62876 | 0.62876 | 0.62876 | 0.62876 | 0.62876
2020-08-08 02:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.3657 | 0.3657 | 0.3657 | 0.3657 | 0.3657 | 0.3657 | 1.618 | 2.334 | 2.803 | 3.0499 | 3.5437 | 4.0374 | 0.63635 | 1.7286 | 2.1681 | 2.1681 | 2.1681 | 2.1681 | 0.49537 | 0.62876 | 0.62876 | 0.62876 | 0.62876 | 0.62876
2020-08-08 03:00 | Winter | 1.0275 | 1.5799 | 2.3907 | 2.3907 | 2.3907 | 2.3907 | 0.36581 | 0.36581 | 0.36581 | 0.36581 | 0.36581 | 0.36581 | 1.5978 | 2.3048 | 2.768 | 3.0118 | 3.4994 | 3.987 | 0.5792 | 1.5733 | 1.9733 | 1.9733 | 1.9733 | 1.9733 | 0.49537 | 0.62876 | 0.62876 | 0.62876 | 0.62876 | 0.62876
2020-08-08 04:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 0.38543 | 0.38543 | 0.38543 | 0.38543 | 0.38543 | 0.38543 | 1.6195 | 2.336 | 2.8055 | 3.0526 | 3.5468 | 4.041 | 0.59063 | 1.6044 | 2.0123 | 2.0123 | 2.0123 | 2.0123 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-08-08 05:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.583 | 0.583 | 0.583 | 0.583 | 0.583 | 0.583 | 1.7338 | 2.5009 | 3.0036 | 3.2681 | 3.7972 | 4.3262 | 0.60968 | 1.6561 | 2.0772 | 2.0772 | 2.0772 | 2.0772 | 0.49008 | 0.62205 | 0.62205 | 0.62205 | 0.62205 | 0.62205
2020-08-08 06:00 | Winter | 1.086 | 1.6698 | 2.5268 | 2.5268 | 2.5268 | 2.5268 | 0.49155 | 0.49155 | 0.49155 | 0.49155 | 0.49155 | 0.49155 | 1.8672 | 2.6933 | 3.2346 | 3.5195 | 4.0892 | 4.659 | 0.68589 | 1.8632 | 2.3368 | 2.3368 | 2.3368 | 2.3368 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-08-08 07:00 | Winter | 1.105 | 1.6991 | 2.5711 | 2.5711 | 2.5711 | 2.5711 | 0.59729 | 0.59729 | 0.59729 | 0.59729 | 0.59729 | 0.59729 | 1.8481 | 2.6658 | 3.2016 | 3.4836 | 4.0475 | 4.6115 | 0.69351 | 1.8839 | 2.3628 | 2.3628 | 2.3628 | 2.3628 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-08-08 08:00 | Winter | 1.105 | 1.6991 | 2.5711 | 2.5711 | 2.5711 | 2.5711 | 0.66588 | 0.66588 | 0.66588 | 0.66588 | 0.66588 | 0.66588 | 2.0767 | 2.9956 | 3.5977 | 3.9145 | 4.5482 | 5.182 | 0.77353 | 2.1012 | 2.6354 | 2.6354 | 2.6354 | 2.6354 | 0.55252 | 0.70131 | 0.70131 | 0.70131 | 0.70131 | 0.70131
2020-08-08 09:00 | Winter | 1.105 | 1.6991 | 2.5711 | 2.5711 | 2.5711 | 2.5711 | 0.66874 | 0.66874 | 0.66874 | 0.66874 | 0.66874 | 0.66874 | 2.3435 | 3.3804 | 4.0597 | 4.4173 | 5.1324 | 5.8475 | 0.76972 | 2.0909 | 2.6225 | 2.6225 | 2.6225 | 2.6225 | 0.60968 | 0.77386 | 0.77386 | 0.77386 | 0.77386 | 0.77386
2020-08-08 10:00 | Winter | 1.1622 | 1.787 | 2.7041 | 2.7041 | 2.7041 | 2.7041 | 0.73733 | 0.73733 | 0.73733 | 0.73733 | 0.73733 | 0.73733 | 2.2673 | 3.2705 | 3.9277 | 4.2736 | 4.9655 | 5.6574 | 0.75067 | 2.0391 | 2.5575 | 2.5575 | 2.5575 | 2.5575 | 0.60968 | 0.77386 | 0.77386 | 0.77386 | 0.77386 | 0.77386
2020-08-08 11:00 | Winter | 1.105 | 1.6991 | 2.5711 | 2.5711 | 2.5711 | 2.5711 | 0.72876 | 0.72876 | 0.72876 | 0.72876 | 0.72876 | 0.72876 | 2.3625 | 3.4079 | 4.0927 | 4.4532 | 5.1741 | 5.8951 | 0.72018 | 1.9563 | 2.4537 | 2.4537 | 2.4537 | 2.4537 | 0.60968 | 0.77386 | 0.77386 | 0.77386 | 0.77386 | 0.77386
2020-08-08 12:00 | Winter | 1.105 | 1.6991 | 2.5711 | 2.5711 | 2.5711 | 2.5711 | 0.72304 | 0.72304 | 0.72304 | 0.72304 | 0.72304 | 0.72304 | 2.3435 | 3.3804 | 4.0597 | 4.4173 | 5.1324 | 5.8475 | 0.75067 | 2.0391 | 2.5575 | 2.5575 | 2.5575 | 2.5575 | 0.66684 | 0.84641 | 0.84641 | 0.84641 | 0.84641 | 0.84641
2020-08-08 13:00 | Winter | 1.105 | 1.6991 | 2.5711 | 2.5711 | 2.5711 | 2.5711 | 0.73161 | 0.73161 | 0.73161 | 0.73161 | 0.73161 | 0.73161 | 2.4768 | 3.5728 | 4.2908 | 4.6687 | 5.4245 | 6.1803 | 0.73924 | 2.0081 | 2.5186 | 2.5186 | 2.5186 | 2.5186 | 0.64779 | 0.82222 | 0.82222 | 0.82222 | 0.82222 | 0.82222
2020-08-08 14:00 | Winter | 1.0669 | 1.6405 | 2.4825 | 2.4825 | 2.4825 | 2.4825 | 0.70304 | 0.70304 | 0.70304 | 0.70304 | 0.70304 | 0.70304 | 2.4578 | 3.5453 | 4.2578 | 4.6328 | 5.3828 | 6.1328 | 0.73543 | 1.9977 | 2.5056 | 2.5056 | 2.5056 | 2.5056 | 0.59063 | 0.74967 | 0.74967 | 0.74967 | 0.74967 | 0.74967
2020-08-08 15:00 | Winter | 1.1432 | 1.7577 | 2.6598 | 2.6598 | 2.6598 | 2.6598 | 0.66303 | 0.66303 | 0.66303 | 0.66303 | 0.66303 | 0.66303 | 2.4197 | 3.4903 | 4.1918 | 4.561 | 5.2993 | 6.0377 | 0.69351 | 1.8839 | 2.3628 | 2.3628 | 2.3628 | 2.3628 | 0.59063 | 0.74967 | 0.74967 | 0.74967 | 0.74967 | 0.74967
2020-08-08 16:00 | Winter | 1.1432 | 1.7577 | 2.6598 | 2.6598 | 2.6598 | 2.6598 | 0.70018 | 0.70018 | 0.70018 | 0.70018 | 0.70018 | 0.70018 | 2.4578 | 3.5453 | 4.2578 | 4.6328 | 5.3828 | 6.1328 | 0.74305 | 2.0184 | 2.5316 | 2.5316 | 2.5316 | 2.5316 | 0.57158 | 0.72549 | 0.72549 | 0.72549 | 0.72549 | 0.72549
2020-08-08 17:00 | Winter | 1.1622 | 1.787 | 2.7041 | 2.7041 | 2.7041 | 2.7041 | 0.69446 | 0.69446 | 0.69446 | 0.69446 | 0.69446 | 0.69446 | 2.5721 | 3.7102 | 4.4558 | 4.8483 | 5.6331 | 6.418 | 0.82688 | 2.2461 | 2.8172 | 2.8172 | 2.8172 | 2.8172 | 0.55252 | 0.70131 | 0.70131 | 0.70131 | 0.70131 | 0.70131
2020-08-08 18:00 | Winter | 1.0669 | 1.6405 | 2.4825 | 2.4825 | 2.4825 | 2.4825 | 0.66667 | 0.66667 | 0.66667 | 0.66667 | 0.66667 | 0.66667 | 2.5149 | 3.6277 | 4.3568 | 4.7405 | 5.508 | 6.2754 | 0.85355 | 2.3186 | 2.9081 | 2.9081 | 2.9081 | 2.9081 | 0.55252 | 0.70131 | 0.70131 | 0.70131 | 0.70131 | 0.70131
2020-08-08 19:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 0.63445 | 0.63445 | 0.63445 | 0.63445 | 0.63445 | 0.63445 | 2.4006 | 3.4628 | 4.1588 | 4.525 | 5.2576 | 5.9902 | 0.81926 | 2.2254 | 2.7912 | 2.7912 | 2.7912 | 2.7912 | 0.57158 | 0.72549 | 0.72549 | 0.72549 | 0.72549 | 0.72549
2020-08-08 20:00 | Winter | 1.0669 | 1.6405 | 2.4825 | 2.4825 | 2.4825 | 2.4825 | 0.59158 | 0.59158 | 0.59158 | 0.59158 | 0.59158 | 0.59158 | 2.3816 | 3.4353 | 4.1258 | 4.4891 | 5.2159 | 5.9426 | 0.75448 | 2.0495 | 2.5705 | 2.5705 | 2.5705 | 2.5705 | 0.57158 | 0.72549 | 0.72549 | 0.72549 | 0.72549 | 0.72549
2020-08-08 21:00 | Winter | 1.0288 | 1.582 | 2.3938 | 2.3938 | 2.3938 | 2.3938 | 0.50298 | 0.50298 | 0.50298 | 0.50298 | 0.50298 | 0.50298 | 2.3404 | 3.3759 | 4.0544 | 4.4115 | 5.1257 | 5.8398 | 0.77734 | 2.1116 | 2.6484 | 2.6484 | 2.6484 | 2.6484 | 0.55252 | 0.70131 | 0.70131 | 0.70131 | 0.70131 | 0.70131
2020-08-08 22:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.44884 | 0.44884 | 0.44884 | 0.44884 | 0.44884 | 0.44884 | 2.2101 | 3.188 | 3.8287 | 4.1659 | 4.8403 | 5.5147 | 0.73543 | 1.9977 | 2.5056 | 2.5056 | 2.5056 | 2.5056 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-08-08 23:00 | Winter | 1.0288 | 1.582 | 2.3938 | 2.3938 | 2.3938 | 2.3938 | 0.38579 | 0.38579 | 0.38579 | 0.38579 | 0.38579 | 0.38579 | 2.0386 | 2.9407 | 3.5316 | 3.8427 | 4.4648 | 5.0869 | 0.67446 | 1.8321 | 2.2979 | 2.2979 | 2.2979 | 2.2979 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-08-09 | Winter | 0.97188 | 1.4944 | 2.2613 | 2.2613 | 2.2613 | 2.2613 | 0.38581 | 0.38581 | 0.38581 | 0.38581 | 0.38581 | 0.38581 | 1.81 | 2.6109 | 3.1356 | 3.4117 | 3.9641 | 4.5164 | 0.56392 | 1.5318 | 1.9213 | 1.9213 | 1.9213 | 1.9213 | 0.47739 | 0.60594 | 0.60594 | 0.60594 | 0.60594 | 0.60594
2020-08-09 01:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.37438 | 0.37438 | 0.37438 | 0.37438 | 0.37438 | 0.37438 | 1.6766 | 2.4185 | 2.9045 | 3.1603 | 3.672 | 4.1836 | 0.56395 | 1.5319 | 1.9214 | 1.9214 | 1.9214 | 1.9214 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-08-09 02:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.37415 | 0.37415 | 0.37415 | 0.37415 | 0.37415 | 0.37415 | 1.6195 | 2.336 | 2.8055 | 3.0526 | 3.5468 | 4.041 | 0.56014 | 1.5216 | 1.9084 | 1.9084 | 1.9084 | 1.9084 | 0.49537 | 0.62876 | 0.62876 | 0.62876 | 0.62876 | 0.62876
2020-08-09 03:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.37438 | 0.37438 | 0.37438 | 0.37438 | 0.37438 | 0.37438 | 1.6195 | 2.336 | 2.8055 | 3.0526 | 3.5468 | 4.041 | 0.56395 | 1.5319 | 1.9214 | 1.9214 | 1.9214 | 1.9214 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-08-09 04:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.40582 | 0.40582 | 0.40582 | 0.40582 | 0.40582 | 0.40582 | 1.6198 | 2.3365 | 2.8061 | 3.0532 | 3.5475 | 4.0418 | 0.57539 | 1.563 | 1.9603 | 1.9603 | 1.9603 | 1.9603 | 0.45723 | 0.58035 | 0.58035 | 0.58035 | 0.58035 | 0.58035
2020-08-09 05:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 0.52299 | 0.52299 | 0.52299 | 0.52299 | 0.52299 | 0.52299 | 1.7331 | 2.4999 | 3.0023 | 3.2668 | 3.7956 | 4.3245 | 0.6173 | 1.6768 | 2.1032 | 2.1032 | 2.1032 | 2.1032 | 0.49522 | 0.62857 | 0.62857 | 0.62857 | 0.62857 | 0.62857
2020-08-09 06:00 | Winter | 1.0288 | 1.582 | 2.3938 | 2.3938 | 2.3938 | 2.3938 | 0.48584 | 0.48584 | 0.48584 | 0.48584 | 0.48584 | 0.48584 | 1.905 | 2.748 | 3.3002 | 3.5909 | 4.1722 | 4.7536 | 0.66303 | 1.8011 | 2.2589 | 2.2589 | 2.2589 | 2.2589 | 0.49537 | 0.62876 | 0.62876 | 0.62876 | 0.62876 | 0.62876
2020-08-09 07:00 | Winter | 0.98876 | 1.5203 | 2.3006 | 2.3006 | 2.3006 | 2.3006 | 0.48012 | 0.48012 | 0.48012 | 0.48012 | 0.48012 | 0.48012 | 1.9434 | 2.8032 | 3.3666 | 3.6631 | 4.2562 | 4.8492 | 0.66303 | 1.8011 | 2.2589 | 2.2589 | 2.2589 | 2.2589 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-08-09 08:00 | Winter | 1.0288 | 1.582 | 2.3938 | 2.3938 | 2.3938 | 2.3938 | 0.58015 | 0.58015 | 0.58015 | 0.58015 | 0.58015 | 0.58015 | 2.2863 | 3.2979 | 3.9607 | 4.3096 | 5.0072 | 5.7049 | 0.70494 | 1.9149 | 2.4018 | 2.4018 | 2.4018 | 2.4018 | 0.55252 | 0.70131 | 0.70131 | 0.70131 | 0.70131 | 0.70131
2020-08-09 09:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.61444 | 0.61444 | 0.61444 | 0.61444 | 0.61444 | 0.61444 | 2.4006 | 3.4628 | 4.1588 | 4.525 | 5.2576 | 5.9902 | 0.70875 | 1.9253 | 2.4147 | 2.4147 | 2.4147 | 2.4147 | 0.60968 | 0.77386 | 0.77386 | 0.77386 | 0.77386 | 0.77386
2020-08-09 10:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.60873 | 0.60873 | 0.60873 | 0.60873 | 0.60873 | 0.60873 | 2.3816 | 3.4353 | 4.1258 | 4.4891 | 5.2159 | 5.9426 | 0.69732 | 1.8942 | 2.3758 | 2.3758 | 2.3758 | 2.3758 | 0.59063 | 0.74967 | 0.74967 | 0.74967 | 0.74967 | 0.74967
2020-08-09 11:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.57157 | 0.57157 | 0.57157 | 0.57157 | 0.57157 | 0.57157 | 2.4387 | 3.5178 | 4.2248 | 4.5969 | 5.3411 | 6.0852 | 0.69351 | 1.8839 | 2.3628 | 2.3628 | 2.3628 | 2.3628 | 0.59063 | 0.74967 | 0.74967 | 0.74967 | 0.74967 | 0.74967
2020-08-09 12:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 0.48012 | 0.48012 | 0.48012 | 0.48012 | 0.48012 | 0.48012 | 2.4387 | 3.5178 | 4.2248 | 4.5969 | 5.3411 | 6.0852 | 0.69351 | 1.8839 | 2.3628 | 2.3628 | 2.3628 | 2.3628 | 0.59063 | 0.74967 | 0.74967 | 0.74967 | 0.74967 | 0.74967
2020-08-09 13:00 | Winter | 1.0288 | 1.582 | 2.3938 | 2.3938 | 2.3938 | 2.3938 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 2.3435 | 3.3804 | 4.0597 | 4.4173 | 5.1324 | 5.8475 | 0.6516 | 1.77 | 2.22 | 2.22 | 2.22 | 2.22 | 0.57158 | 0.72549 | 0.72549 | 0.72549 | 0.72549 | 0.72549
2020-08-09 14:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.5087 | 0.5087 | 0.5087 | 0.5087 | 0.5087 | 0.5087 | 2.3054 | 3.3254 | 3.9937 | 4.3455 | 5.049 | 5.7525 | 0.66303 | 1.8011 | 2.2589 | 2.2589 | 2.2589 | 2.2589 | 0.57158 | 0.72549 | 0.72549 | 0.72549 | 0.72549 | 0.72549
2020-08-09 15:00 | Winter | 1.086 | 1.6698 | 2.5268 | 2.5268 | 2.5268 | 2.5268 | 0.49155 | 0.49155 | 0.49155 | 0.49155 | 0.49155 | 0.49155 | 2.2863 | 3.2979 | 3.9607 | 4.3096 | 5.0072 | 5.7049 | 0.65541 | 1.7803 | 2.233 | 2.233 | 2.233 | 2.233 | 0.57158 | 0.72549 | 0.72549 | 0.72549 | 0.72549 | 0.72549
2020-08-09 16:00 | Winter | 1.0669 | 1.6405 | 2.4825 | 2.4825 | 2.4825 | 2.4825 | 0.51442 | 0.51442 | 0.51442 | 0.51442 | 0.51442 | 0.51442 | 2.3816 | 3.4353 | 4.1258 | 4.4891 | 5.2159 | 5.9426 | 0.70875 | 1.9253 | 2.4147 | 2.4147 | 2.4147 | 2.4147 | 0.57158 | 0.72549 | 0.72549 | 0.72549 | 0.72549 | 0.72549
2020-08-09 17:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 0.583 | 0.583 | 0.583 | 0.583 | 0.583 | 0.583 | 2.3933 | 3.4523 | 4.1461 | 4.5113 | 5.2416 | 5.9719 | 0.75829 | 2.0598 | 2.5835 | 2.5835 | 2.5835 | 2.5835 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-08-09 18:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 0.58872 | 0.58872 | 0.58872 | 0.58872 | 0.58872 | 0.58872 | 2.4768 | 3.5728 | 4.2908 | 4.6687 | 5.4245 | 6.1803 | 0.77734 | 2.1116 | 2.6484 | 2.6484 | 2.6484 | 2.6484 | 0.55252 | 0.70131 | 0.70131 | 0.70131 | 0.70131 | 0.70131
2020-08-09 19:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.53442 | 0.53442 | 0.53442 | 0.53442 | 0.53442 | 0.53442 | 2.4387 | 3.5178 | 4.2248 | 4.5969 | 5.3411 | 6.0852 | 0.75067 | 2.0391 | 2.5575 | 2.5575 | 2.5575 | 2.5575 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-08-09 20:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 0.56014 | 0.56014 | 0.56014 | 0.56014 | 0.56014 | 0.56014 | 2.3054 | 3.3254 | 3.9937 | 4.3455 | 5.049 | 5.7525 | 0.724 | 1.9667 | 2.4667 | 2.4667 | 2.4667 | 2.4667 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-08-09 21:00 | Winter | 1.0272 | 1.5794 | 2.39 | 2.39 | 2.39 | 2.39 | 0.52013 | 0.52013 | 0.52013 | 0.52013 | 0.52013 | 0.52013 | 2.2863 | 3.2979 | 3.9607 | 4.3096 | 5.0072 | 5.7049 | 0.74686 | 2.0288 | 2.5446 | 2.5446 | 2.5446 | 2.5446 | 0.55252 | 0.70131 | 0.70131 | 0.70131 | 0.70131 | 0.70131
2020-08-09 22:00 | Winter | 1.0288 | 1.582 | 2.3938 | 2.3938 | 2.3938 | 2.3938 | 0.36009 | 0.36009 | 0.36009 | 0.36009 | 0.36009 | 0.36009 | 2.0108 | 2.9006 | 3.4835 | 3.7903 | 4.4039 | 5.0176 | 0.66684 | 1.8114 | 2.2719 | 2.2719 | 2.2719 | 2.2719 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-08-09 23:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.35723 | 0.35723 | 0.35723 | 0.35723 | 0.35723 | 0.35723 | 1.8463 | 2.6632 | 3.1985 | 3.4802 | 4.0436 | 4.607 | 0.65922 | 1.7907 | 2.246 | 2.246 | 2.246 | 2.246 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-08-10 | Winter | 0.99873 | 1.5357 | 2.3238 | 2.3238 | 2.3238 | 2.3238 | 0.35437 | 0.35437 | 0.35437 | 0.35437 | 0.35437 | 0.35437 | 1.6957 | 2.446 | 2.9375 | 3.1963 | 3.7137 | 4.2311 | 0.56395 | 1.5319 | 1.9214 | 1.9214 | 1.9214 | 1.9214 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-08-10 01:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.3458 | 0.3458 | 0.3458 | 0.3458 | 0.3458 | 0.3458 | 1.6195 | 2.336 | 2.8055 | 3.0526 | 3.5468 | 4.041 | 0.56395 | 1.5319 | 1.9214 | 1.9214 | 1.9214 | 1.9214 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-08-10 02:00 | Winter | 1.2003 | 1.8456 | 2.7928 | 2.7928 | 2.7928 | 2.7928 | 0.36581 | 0.36581 | 0.36581 | 0.36581 | 0.36581 | 0.36581 | 1.6004 | 2.3086 | 2.7725 | 3.0167 | 3.5051 | 3.9934 | 0.56014 | 1.5216 | 1.9084 | 1.9084 | 1.9084 | 1.9084 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-08-10 03:00 | Winter | 1.2575 | 1.9335 | 2.9258 | 2.9258 | 2.9258 | 2.9258 | 0.35437 | 0.35437 | 0.35437 | 0.35437 | 0.35437 | 0.35437 | 1.6004 | 2.3086 | 2.7725 | 3.0167 | 3.5051 | 3.9934 | 0.56776 | 1.5423 | 1.9344 | 1.9344 | 1.9344 | 1.9344 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-08-10 04:00 | Winter | 1.2003 | 1.8456 | 2.7928 | 2.7928 | 2.7928 | 2.7928 | 0.50298 | 0.50298 | 0.50298 | 0.50298 | 0.50298 | 0.50298 | 1.7528 | 2.5284 | 3.0366 | 3.304 | 3.8389 | 4.3738 | 0.6173 | 1.6768 | 2.1032 | 2.1032 | 2.1032 | 2.1032 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-08-10 05:00 | Winter | 1.3911 | 2.139 | 3.2367 | 3.2367 | 3.2367 | 3.2367 | 0.64016 | 0.64016 | 0.64016 | 0.64016 | 0.64016 | 0.64016 | 1.9434 | 2.8032 | 3.3666 | 3.6631 | 4.2562 | 4.8492 | 0.80783 | 2.1944 | 2.7523 | 2.7523 | 2.7523 | 2.7523 | 0.8735 | 1.1087 | 1.1087 | 1.1087 | 1.1087 | 1.1087
2020-08-10 06:00 | Winter | 1.6942 | 2.605 | 3.9419 | 3.9419 | 3.9419 | 3.9419 | 0.77734 | 0.77734 | 0.77734 | 0.77734 | 0.77734 | 0.77734 | 2.2482 | 3.243 | 3.8947 | 4.2377 | 4.9238 | 5.6098 | 0.80783 | 2.1944 | 2.7523 | 2.7523 | 2.7523 | 2.7523 | 1.0666 | 1.3538 | 1.3538 | 1.3538 | 1.3538 | 1.3538
2020-08-10 07:00 | Winter | 2.2291 | 3.4276 | 5.1866 | 5.1866 | 5.1866 | 5.1866 | 0.91733 | 0.91733 | 0.91733 | 0.91733 | 0.91733 | 0.91733 | 2.4197 | 3.4903 | 4.1918 | 4.561 | 5.2993 | 6.0377 | 0.89454 | 2.4299 | 3.0477 | 3.0477 | 3.0477 | 3.0477 | 1.4289 | 1.8137 | 1.8137 | 1.8137 | 1.8137 | 1.8137
2020-08-10 08:00 | Winter | 2.4578 | 3.7791 | 5.7186 | 5.7186 | 5.7186 | 5.7186 | 1.0574 | 1.0574 | 1.0574 | 1.0574 | 1.0574 | 1.0574 | 2.5911 | 3.7377 | 4.4888 | 4.8842 | 5.6749 | 6.4656 | 0.92595 | 2.5153 | 3.1547 | 3.1547 | 3.1547 | 3.1547 | 1.6766 | 2.1281 | 2.1281 | 2.1281 | 2.1281 | 2.1281
2020-08-10 09:00 | Winter | 2.4387 | 3.7498 | 5.6742 | 5.6742 | 5.6742 | 5.6742 | 1.0803 | 1.0803 | 1.0803 | 1.0803 | 1.0803 | 1.0803 | 2.6674 | 3.8476 | 4.6208 | 5.0278 | 5.8418 | 6.6557 | 0.97549 | 2.6498 | 3.3235 | 3.3235 | 3.3235 | 3.3235 | 1.6766 | 2.1281 | 2.1281 | 2.1281 | 2.1281 | 2.1281
2020-08-10 10:00 | Winter | 2.4012 | 3.692 | 5.5868 | 5.5868 | 5.5868 | 5.5868 | 1.0203 | 1.0203 | 1.0203 | 1.0203 | 1.0203 | 1.0203 | 2.7245 | 3.93 | 4.7199 | 5.1356 | 5.967 | 6.7984 | 0.92511 | 2.513 | 3.1519 | 3.1519 | 3.1519 | 3.1519 | 1.6957 | 2.1523 | 2.1523 | 2.1523 | 2.1523 | 2.1523
2020-08-10 11:00 | Winter | 2.3816 | 3.6619 | 5.5412 | 5.5412 | 5.5412 | 5.5412 | 1.006 | 1.006 | 1.006 | 1.006 | 1.006 | 1.006 | 2.7436 | 3.9575 | 4.7529 | 5.1715 | 6.0087 | 6.8459 | 0.92976 | 2.5256 | 3.1677 | 3.1677 | 3.1677 | 3.1677 | 1.7338 | 2.2007 | 2.2007 | 2.2007 | 2.2007 | 2.2007
2020-08-10 12:00 | Winter | 2.3435 | 3.6034 | 5.4526 | 5.4526 | 5.4526 | 5.4526 | 0.96025 | 0.96025 | 0.96025 | 0.96025 | 0.96025 | 0.96025 | 2.7245 | 3.93 | 4.7199 | 5.1356 | 5.967 | 6.7984 | 0.84212 | 2.2875 | 2.8691 | 2.8691 | 2.8691 | 2.8691 | 1.6576 | 2.1039 | 2.1039 | 2.1039 | 2.1039 | 2.1039
2020-08-10 13:00 | Winter | 2.2863 | 3.5155 | 5.3196 | 5.3196 | 5.3196 | 5.3196 | 0.91738 | 0.91738 | 0.91738 | 0.91738 | 0.91738 | 0.91738 | 2.7055 | 3.9026 | 4.6869 | 5.0996 | 5.9252 | 6.7508 | 0.86498 | 2.3496 | 2.947 | 2.947 | 2.947 | 2.947 | 1.6004 | 2.0314 | 2.0314 | 2.0314 | 2.0314 | 2.0314
2020-08-10 14:00 | Winter | 2.2863 | 3.5155 | 5.3196 | 5.3196 | 5.3196 | 5.3196 | 0.97453 | 0.97453 | 0.97453 | 0.97453 | 0.97453 | 0.97453 | 2.7055 | 3.9026 | 4.6869 | 5.0996 | 5.9252 | 6.7508 | 0.8345 | 2.2668 | 2.8432 | 2.8432 | 2.8432 | 2.8432 | 1.5242 | 1.9346 | 1.9346 | 1.9346 | 1.9346 | 1.9346
2020-08-10 15:00 | Winter | 2.191 | 3.369 | 5.0979 | 5.0979 | 5.0979 | 5.0979 | 1.0288 | 1.0288 | 1.0288 | 1.0288 | 1.0288 | 1.0288 | 2.5911 | 3.7377 | 4.4888 | 4.8842 | 5.6749 | 6.4656 | 0.82688 | 2.2461 | 2.8172 | 2.8172 | 2.8172 | 2.8172 | 1.4289 | 1.8137 | 1.8137 | 1.8137 | 1.8137 | 1.8137
2020-08-10 16:00 | Winter | 2.2482 | 3.4569 | 5.2309 | 5.2309 | 5.2309 | 5.2309 | 1.0003 | 1.0003 | 1.0003 | 1.0003 | 1.0003 | 1.0003 | 2.553 | 3.6827 | 4.4228 | 4.8123 | 5.5914 | 6.3705 | 0.8345 | 2.2668 | 2.8432 | 2.8432 | 2.8432 | 2.8432 | 1.4289 | 1.8137 | 1.8137 | 1.8137 | 1.8137 | 1.8137
2020-08-10 17:00 | Winter | 2.1342 | 3.2816 | 4.9657 | 4.9657 | 4.9657 | 4.9657 | 0.89451 | 0.89451 | 0.89451 | 0.89451 | 0.89451 | 0.89451 | 2.6102 | 3.7651 | 4.5218 | 4.9201 | 5.7166 | 6.5131 | 0.84974 | 2.3082 | 2.8951 | 2.8951 | 2.8951 | 2.8951 | 1.1989 | 1.5218 | 1.5218 | 1.5218 | 1.5218 | 1.5218
2020-08-10 18:00 | Winter | 1.8107 | 2.7841 | 4.2129 | 4.2129 | 4.2129 | 4.2129 | 0.81735 | 0.81735 | 0.81735 | 0.81735 | 0.81735 | 0.81735 | 2.5911 | 3.7377 | 4.4888 | 4.8842 | 5.6749 | 6.4656 | 0.86498 | 2.3496 | 2.947 | 2.947 | 2.947 | 2.947 | 0.99129 | 1.2582 | 1.2582 | 1.2582 | 1.2582 | 1.2582
2020-08-10 19:00 | Winter | 1.1692 | 1.7978 | 2.7204 | 2.7204 | 2.7204 | 2.7204 | 0.55728 | 0.55728 | 0.55728 | 0.55728 | 0.55728 | 0.55728 | 2.4974 | 3.6024 | 4.3264 | 4.7074 | 5.4695 | 6.2316 | 0.82688 | 2.2461 | 2.8172 | 2.8172 | 2.8172 | 2.8172 | 0.6611 | 0.83912 | 0.83912 | 0.83912 | 0.83912 | 0.83912
2020-08-10 20:00 | Winter | 1.105 | 1.6991 | 2.5711 | 2.5711 | 2.5711 | 2.5711 | 0.51156 | 0.51156 | 0.51156 | 0.51156 | 0.51156 | 0.51156 | 2.4197 | 3.4903 | 4.1918 | 4.561 | 5.2993 | 6.0377 | 0.80021 | 2.1737 | 2.7263 | 2.7263 | 2.7263 | 2.7263 | 0.62815 | 0.7973 | 0.7973 | 0.7973 | 0.7973 | 0.7973
2020-08-10 21:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 2.2101 | 3.188 | 3.8287 | 4.1659 | 4.8403 | 5.5147 | 0.78877 | 2.1426 | 2.6874 | 2.6874 | 2.6874 | 2.6874 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-08-10 22:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 2.1148 | 3.0506 | 3.6637 | 3.9863 | 4.6317 | 5.277 | 0.70494 | 1.9149 | 2.4018 | 2.4018 | 2.4018 | 2.4018 | 0.55252 | 0.70131 | 0.70131 | 0.70131 | 0.70131 | 0.70131
2020-08-10 23:00 | Winter | 0.98989 | 1.5221 | 2.3032 | 2.3032 | 2.3032 | 2.3032 | 0.48584 | 0.48584 | 0.48584 | 0.48584 | 0.48584 | 0.48584 | 1.8835 | 2.7169 | 3.263 | 3.5504 | 4.1251 | 4.6999 | 0.61349 | 1.6665 | 2.0902 | 2.0902 | 2.0902 | 2.0902 | 0.57158 | 0.72549 | 0.72549 | 0.72549 | 0.72549 | 0.72549
2020-08-11 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.49155 | 0.49155 | 0.49155 | 0.49155 | 0.49155 | 0.49155 | 1.7719 | 2.5559 | 3.0696 | 3.3399 | 3.8806 | 4.4213 | 0.60206 | 1.6354 | 2.0512 | 2.0512 | 2.0512 | 2.0512 | 0.55252 | 0.70131 | 0.70131 | 0.70131 | 0.70131 | 0.70131
2020-08-11 01:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.41153 | 0.41153 | 0.41153 | 0.41153 | 0.41153 | 0.41153 | 1.6774 | 2.4196 | 2.9059 | 3.1618 | 3.6737 | 4.1856 | 0.59444 | 1.6147 | 2.0253 | 2.0253 | 2.0253 | 2.0253 | 0.47566 | 0.60374 | 0.60374 | 0.60374 | 0.60374 | 0.60374
2020-08-11 02:00 | Winter | 1.2194 | 1.8749 | 2.8371 | 2.8371 | 2.8371 | 2.8371 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.59444 | 1.6147 | 2.0253 | 2.0253 | 2.0253 | 2.0253 | 0.53492 | 0.67896 | 0.67896 | 0.67896 | 0.67896 | 0.67896
2020-08-11 03:00 | Winter | 1.2194 | 1.8749 | 2.8371 | 2.8371 | 2.8371 | 2.8371 | 0.47441 | 0.47441 | 0.47441 | 0.47441 | 0.47441 | 0.47441 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.53347 | 1.4491 | 1.8175 | 1.8175 | 1.8175 | 1.8175 | 0.55252 | 0.70131 | 0.70131 | 0.70131 | 0.70131 | 0.70131
2020-08-11 04:00 | Winter | 1.2712 | 1.9546 | 2.9576 | 2.9576 | 2.9576 | 2.9576 | 0.49727 | 0.49727 | 0.49727 | 0.49727 | 0.49727 | 0.49727 | 1.7557 | 2.5325 | 3.0415 | 3.3094 | 3.8452 | 4.3809 | 0.58301 | 1.5837 | 1.9863 | 1.9863 | 1.9863 | 1.9863 | 0.55252 | 0.70131 | 0.70131 | 0.70131 | 0.70131 | 0.70131
2020-08-11 05:00 | Winter | 1.4871 | 2.2866 | 3.46 | 3.46 | 3.46 | 3.46 | 0.68747 | 0.68747 | 0.68747 | 0.68747 | 0.68747 | 0.68747 | 1.9615 | 2.8294 | 3.3981 | 3.6974 | 4.2959 | 4.8945 | 0.75829 | 2.0598 | 2.5835 | 2.5835 | 2.5835 | 2.5835 | 0.81448 | 1.0338 | 1.0338 | 1.0338 | 1.0338 | 1.0338
2020-08-11 06:00 | Winter | 1.9245 | 2.9591 | 4.4777 | 4.4777 | 4.4777 | 4.4777 | 0.77448 | 0.77448 | 0.77448 | 0.77448 | 0.77448 | 0.77448 | 2.3435 | 3.3804 | 4.0597 | 4.4173 | 5.1324 | 5.8475 | 0.79258 | 2.153 | 2.7003 | 2.7003 | 2.7003 | 2.7003 | 1.0669 | 1.3542 | 1.3542 | 1.3542 | 1.3542 | 1.3542
2020-08-11 07:00 | Winter | 2.191 | 3.369 | 5.0979 | 5.0979 | 5.0979 | 5.0979 | 0.92034 | 0.92034 | 0.92034 | 0.92034 | 0.92034 | 0.92034 | 2.6864 | 3.8751 | 4.6539 | 5.0637 | 5.8835 | 6.7033 | 0.88404 | 2.4014 | 3.0119 | 3.0119 | 3.0119 | 3.0119 | 1.4299 | 1.8149 | 1.8149 | 1.8149 | 1.8149 | 1.8149
2020-08-11 08:00 | Winter | 2.4387 | 3.7498 | 5.6742 | 5.6742 | 5.6742 | 5.6742 | 1.1089 | 1.1089 | 1.1089 | 1.1089 | 1.1089 | 1.1089 | 2.7245 | 3.93 | 4.7199 | 5.1356 | 5.967 | 6.7984 | 0.92214 | 2.5049 | 3.1418 | 3.1418 | 3.1418 | 3.1418 | 1.6004 | 2.0314 | 2.0314 | 2.0314 | 2.0314 | 2.0314
2020-08-11 09:00 | Winter | 2.4578 | 3.7791 | 5.7186 | 5.7186 | 5.7186 | 5.7186 | 1.0717 | 1.0717 | 1.0717 | 1.0717 | 1.0717 | 1.0717 | 2.8388 | 4.0949 | 4.9179 | 5.351 | 6.2173 | 7.0836 | 0.89547 | 2.4325 | 3.0509 | 3.0509 | 3.0509 | 3.0509 | 1.6752 | 2.1263 | 2.1263 | 2.1263 | 2.1263 | 2.1263
2020-08-11 10:00 | Winter | 2.4006 | 3.6912 | 5.5856 | 5.5856 | 5.5856 | 5.5856 | 1.0803 | 1.0803 | 1.0803 | 1.0803 | 1.0803 | 1.0803 | 2.8579 | 4.1224 | 4.9509 | 5.387 | 6.259 | 7.1311 | 0.89928 | 2.4428 | 3.0639 | 3.0639 | 3.0639 | 3.0639 | 1.7338 | 2.2007 | 2.2007 | 2.2007 | 2.2007 | 2.2007
2020-08-11 11:00 | Winter | 2.3054 | 3.5448 | 5.3639 | 5.3639 | 5.3639 | 5.3639 | 1.0288 | 1.0288 | 1.0288 | 1.0288 | 1.0288 | 1.0288 | 2.8449 | 4.1037 | 4.9284 | 5.3625 | 6.2306 | 7.0988 | 0.84593 | 2.2979 | 2.8821 | 2.8821 | 2.8821 | 2.8821 | 1.7338 | 2.2007 | 2.2007 | 2.2007 | 2.2007 | 2.2007
2020-08-11 12:00 | Winter | 2.2863 | 3.5155 | 5.3196 | 5.3196 | 5.3196 | 5.3196 | 1.0403 | 1.0403 | 1.0403 | 1.0403 | 1.0403 | 1.0403 | 2.8579 | 4.1224 | 4.9509 | 5.387 | 6.259 | 7.1311 | 0.89547 | 2.4325 | 3.0509 | 3.0509 | 3.0509 | 3.0509 | 1.6195 | 2.0556 | 2.0556 | 2.0556 | 2.0556 | 2.0556
2020-08-11 13:00 | Winter | 2.2101 | 3.3983 | 5.1423 | 5.1423 | 5.1423 | 5.1423 | 0.98025 | 0.98025 | 0.98025 | 0.98025 | 0.98025 | 0.98025 | 2.7436 | 3.9575 | 4.7529 | 5.1715 | 6.0087 | 6.8459 | 0.84593 | 2.2979 | 2.8821 | 2.8821 | 2.8821 | 2.8821 | 1.6004 | 2.0314 | 2.0314 | 2.0314 | 2.0314 | 2.0314
2020-08-11 14:00 | Winter | 2.191 | 3.369 | 5.0979 | 5.0979 | 5.0979 | 5.0979 | 0.99454 | 0.99454 | 0.99454 | 0.99454 | 0.99454 | 0.99454 | 2.7055 | 3.9026 | 4.6869 | 5.0996 | 5.9252 | 6.7508 | 0.80402 | 2.184 | 2.7393 | 2.7393 | 2.7393 | 2.7393 | 1.5253 | 1.9361 | 1.9361 | 1.9361 | 1.9361 | 1.9361
2020-08-11 15:00 | Winter | 2.2101 | 3.3983 | 5.1423 | 5.1423 | 5.1423 | 5.1423 | 0.98311 | 0.98311 | 0.98311 | 0.98311 | 0.98311 | 0.98311 | 2.5911 | 3.7377 | 4.4888 | 4.8842 | 5.6749 | 6.4656 | 0.89547 | 2.4325 | 3.0509 | 3.0509 | 3.0509 | 3.0509 | 1.3718 | 1.7412 | 1.7412 | 1.7412 | 1.7412 | 1.7412
2020-08-11 16:00 | Winter | 2.191 | 3.369 | 5.0979 | 5.0979 | 5.0979 | 5.0979 | 1.0717 | 1.0717 | 1.0717 | 1.0717 | 1.0717 | 1.0717 | 2.534 | 3.6552 | 4.3898 | 4.7764 | 5.5497 | 6.3229 | 0.84212 | 2.2875 | 2.8691 | 2.8691 | 2.8691 | 2.8691 | 1.3146 | 1.6686 | 1.6686 | 1.6686 | 1.6686 | 1.6686
2020-08-11 17:00 | Winter | 2.0577 | 3.1639 | 4.7876 | 4.7876 | 4.7876 | 4.7876 | 1.0117 | 1.0117 | 1.0117 | 1.0117 | 1.0117 | 1.0117 | 2.7245 | 3.93 | 4.7199 | 5.1356 | 5.967 | 6.7984 | 0.86498 | 2.3496 | 2.947 | 2.947 | 2.947 | 2.947 | 1.2575 | 1.5961 | 1.5961 | 1.5961 | 1.5961 | 1.5961
2020-08-11 18:00 | Winter | 1.6654 | 2.5608 | 3.875 | 3.875 | 3.875 | 3.875 | 0.77734 | 0.77734 | 0.77734 | 0.77734 | 0.77734 | 0.77734 | 2.6864 | 3.8751 | 4.6539 | 5.0637 | 5.8835 | 6.7033 | 0.82688 | 2.2461 | 2.8172 | 2.8172 | 2.8172 | 2.8172 | 0.93472 | 1.1864 | 1.1864 | 1.1864 | 1.1864 | 1.1864
2020-08-11 19:00 | Winter | 1.2003 | 1.8456 | 2.7928 | 2.7928 | 2.7928 | 2.7928 | 0.6373 | 0.6373 | 0.6373 | 0.6373 | 0.6373 | 0.6373 | 2.6102 | 3.7651 | 4.5218 | 4.9201 | 5.7166 | 6.5131 | 0.88404 | 2.4014 | 3.0119 | 3.0119 | 3.0119 | 3.0119 | 0.74305 | 0.94314 | 0.94314 | 0.94314 | 0.94314 | 0.94314
2020-08-11 20:00 | Winter | 1.1603 | 1.784 | 2.6996 | 2.6996 | 2.6996 | 2.6996 | 0.52585 | 0.52585 | 0.52585 | 0.52585 | 0.52585 | 0.52585 | 2.3621 | 3.4073 | 4.0921 | 4.4525 | 5.1733 | 5.8941 | 0.73162 | 1.9874 | 2.4926 | 2.4926 | 2.4926 | 2.4926 | 0.66684 | 0.84641 | 0.84641 | 0.84641 | 0.84641 | 0.84641
2020-08-11 21:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 2.2962 | 3.3123 | 3.9779 | 4.3283 | 5.029 | 5.7297 | 0.78496 | 2.1323 | 2.6744 | 2.6744 | 2.6744 | 2.6744 | 0.57158 | 0.72549 | 0.72549 | 0.72549 | 0.72549 | 0.72549
2020-08-11 22:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.48584 | 0.48584 | 0.48584 | 0.48584 | 0.48584 | 0.48584 | 2.0958 | 3.0231 | 3.6307 | 3.9504 | 4.59 | 5.2295 | 0.724 | 1.9667 | 2.4667 | 2.4667 | 2.4667 | 2.4667 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-08-11 23:00 | Winter | 0.97186 | 1.4944 | 2.2612 | 2.2612 | 2.2612 | 2.2612 | 0.48869 | 0.48869 | 0.48869 | 0.48869 | 0.48869 | 0.48869 | 1.9007 | 2.7418 | 3.2928 | 3.5828 | 4.1628 | 4.7428 | 0.60206 | 1.6354 | 2.0512 | 2.0512 | 2.0512 | 2.0512 | 0.49537 | 0.62876 | 0.62876 | 0.62876 | 0.62876 | 0.62876
2020-08-12 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.47441 | 0.47441 | 0.47441 | 0.47441 | 0.47441 | 0.47441 | 1.7909 | 2.5834 | 3.1026 | 3.3758 | 3.9223 | 4.4688 | 0.56014 | 1.5216 | 1.9084 | 1.9084 | 1.9084 | 1.9084 | 0.49537 | 0.62876 | 0.62876 | 0.62876 | 0.62876 | 0.62876
2020-08-12 01:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.46869 | 0.46869 | 0.46869 | 0.46869 | 0.46869 | 0.46869 | 1.6576 | 2.391 | 2.8715 | 3.1244 | 3.6302 | 4.1361 | 0.56776 | 1.5423 | 1.9344 | 1.9344 | 1.9344 | 1.9344 | 0.47694 | 0.60537 | 0.60537 | 0.60537 | 0.60537 | 0.60537
2020-08-12 02:00 | Winter | 1.1796 | 1.8138 | 2.7446 | 2.7446 | 2.7446 | 2.7446 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 1.6195 | 2.336 | 2.8055 | 3.0526 | 3.5468 | 4.041 | 0.53728 | 1.4595 | 1.8305 | 1.8305 | 1.8305 | 1.8305 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-08-12 03:00 | Winter | 1.1813 | 1.8163 | 2.7485 | 2.7485 | 2.7485 | 2.7485 | 0.48012 | 0.48012 | 0.48012 | 0.48012 | 0.48012 | 0.48012 | 1.6558 | 2.3885 | 2.8685 | 3.1212 | 3.6265 | 4.1318 | 0.53347 | 1.4491 | 1.8175 | 1.8175 | 1.8175 | 1.8175 | 0.5333 | 0.67691 | 0.67691 | 0.67691 | 0.67691 | 0.67691
2020-08-12 04:00 | Winter | 1.2002 | 1.8454 | 2.7925 | 2.7925 | 2.7925 | 2.7925 | 0.53728 | 0.53728 | 0.53728 | 0.53728 | 0.53728 | 0.53728 | 1.7369 | 2.5054 | 3.0089 | 3.274 | 3.804 | 4.334 | 0.58682 | 1.594 | 1.9993 | 1.9993 | 1.9993 | 1.9993 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-08-12 05:00 | Winter | 1.3328 | 2.0494 | 3.1011 | 3.1011 | 3.1011 | 3.1011 | 0.64016 | 0.64016 | 0.64016 | 0.64016 | 0.64016 | 0.64016 | 1.9683 | 2.8392 | 3.4098 | 3.7101 | 4.3108 | 4.9114 | 0.74686 | 2.0288 | 2.5446 | 2.5446 | 2.5446 | 2.5446 | 0.80021 | 1.0157 | 1.0157 | 1.0157 | 1.0157 | 1.0157
2020-08-12 06:00 | Winter | 1.6669 | 2.5631 | 3.8785 | 3.8785 | 3.8785 | 3.8785 | 0.76019 | 0.76019 | 0.76019 | 0.76019 | 0.76019 | 0.76019 | 2.2398 | 3.2308 | 3.8801 | 4.2218 | 4.9053 | 5.5888 | 0.73543 | 1.9977 | 2.5056 | 2.5056 | 2.5056 | 2.5056 | 1.009 | 1.2807 | 1.2807 | 1.2807 | 1.2807 | 1.2807
2020-08-12 07:00 | Winter | 2.1631 | 3.326 | 5.0328 | 5.0328 | 5.0328 | 5.0328 | 0.92251 | 0.92251 | 0.92251 | 0.92251 | 0.92251 | 0.92251 | 2.9159 | 4.2062 | 5.0515 | 5.4964 | 6.3862 | 7.276 | 0.88145 | 2.3944 | 3.0031 | 3.0031 | 3.0031 | 3.0031 | 1.4099 | 1.7895 | 1.7895 | 1.7895 | 1.7895 | 1.7895
2020-08-12 08:00 | Winter | 3.6604 | 5.6283 | 8.5168 | 8.5168 | 8.5168 | 8.5168 | 1.0431 | 1.0431 | 1.0431 | 1.0431 | 1.0431 | 1.0431 | 3.277 | 4.727 | 5.677 | 6.177 | 7.177 | 8.177 | 0.96025 | 2.6084 | 3.2716 | 3.2716 | 3.2716 | 3.2716 | 1.6766 | 2.1281 | 2.1281 | 2.1281 | 2.1281 | 2.1281
2020-08-12 09:00 | Winter | 3.6962 | 5.6833 | 8.6 | 8.6 | 8.6 | 8.6 | 1.0403 | 1.0403 | 1.0403 | 1.0403 | 1.0403 | 1.0403 | 0.58582 | 0.84502 | 1.0148 | 1.1042 | 1.283 | 1.4618 | 0.88023 | 2.3911 | 2.9989 | 2.9989 | 2.9989 | 2.9989 | 1.6766 | 2.1281 | 2.1281 | 2.1281 | 2.1281 | 2.1281
2020-08-12 10:00 | Winter | 3.6009 | 5.5369 | 8.3784 | 8.3784 | 8.3784 | 8.3784 | 0.98882 | 0.98882 | 0.98882 | 0.98882 | 0.98882 | 0.98882 | 0.9358 | 1.3499 | 1.6212 | 1.7639 | 2.0495 | 2.3351 | 0.88023 | 2.3911 | 2.9989 | 2.9989 | 2.9989 | 2.9989 | 1.6576 | 2.1039 | 2.1039 | 2.1039 | 2.1039 | 2.1039
2020-08-12 11:00 | Winter | 3.6009 | 5.5369 | 8.3784 | 8.3784 | 8.3784 | 8.3784 | 0.95453 | 0.95453 | 0.95453 | 0.95453 | 0.95453 | 0.95453 | 1.2858 | 1.8547 | 2.2275 | 2.4236 | 2.816 | 3.2084 | 0.87261 | 2.3704 | 2.973 | 2.973 | 2.973 | 2.973 | 1.6385 | 2.0797 | 2.0797 | 2.0797 | 2.0797 | 2.0797
2020-08-12 12:00 | Winter | 3.62 | 5.5662 | 8.4227 | 8.4227 | 8.4227 | 8.4227 | 0.97453 | 0.97453 | 0.97453 | 0.97453 | 0.97453 | 0.97453 | 1.6358 | 2.3596 | 2.8338 | 3.0833 | 3.5825 | 4.0817 | 0.90309 | 2.4532 | 3.0768 | 3.0768 | 3.0768 | 3.0768 | 1.6004 | 2.0314 | 2.0314 | 2.0314 | 2.0314 | 2.0314
2020-08-12 13:00 | Winter | 2.2482 | 3.4569 | 5.2309 | 5.2309 | 5.2309 | 5.2309 | 0.97453 | 0.97453 | 0.97453 | 0.97453 | 0.97453 | 0.97453 | 3.277 | 4.727 | 5.677 | 6.177 | 7.177 | 8.177 | 0.89547 | 2.4325 | 3.0509 | 3.0509 | 3.0509 | 3.0509 | 1.5057 | 1.9111 | 1.9111 | 1.9111 | 1.9111 | 1.9111
2020-08-12 14:00 | Winter | 2.2291 | 3.4276 | 5.1866 | 5.1866 | 5.1866 | 5.1866 | 0.94596 | 0.94596 | 0.94596 | 0.94596 | 0.94596 | 0.94596 | 2.8441 | 4.1026 | 4.9271 | 5.3611 | 6.229 | 7.0969 | 0.84974 | 2.3082 | 2.8951 | 2.8951 | 2.8951 | 2.8951 | 1.448 | 1.8379 | 1.8379 | 1.8379 | 1.8379 | 1.8379
2020-08-12 15:00 | Winter | 2.1529 | 3.3104 | 5.0093 | 5.0093 | 5.0093 | 5.0093 | 0.93738 | 0.93738 | 0.93738 | 0.93738 | 0.93738 | 0.93738 | 2.7055 | 3.9026 | 4.6869 | 5.0996 | 5.9252 | 6.7508 | 0.86879 | 2.36 | 2.96 | 2.96 | 2.96 | 2.96 | 1.448 | 1.8379 | 1.8379 | 1.8379 | 1.8379 | 1.8379
2020-08-12 16:00 | Winter | 2.0767 | 3.1932 | 4.832 | 4.832 | 4.832 | 4.832 | 0.92309 | 0.92309 | 0.92309 | 0.92309 | 0.92309 | 0.92309 | 2.6817 | 3.8683 | 4.6457 | 5.0549 | 5.8732 | 6.6915 | 0.84974 | 2.3082 | 2.8951 | 2.8951 | 2.8951 | 2.8951 | 1.3527 | 1.717 | 1.717 | 1.717 | 1.717 | 1.717
2020-08-12 17:00 | Winter | 2.0377 | 3.1333 | 4.7412 | 4.7412 | 4.7412 | 4.7412 | 0.87737 | 0.87737 | 0.87737 | 0.87737 | 0.87737 | 0.87737 | 2.8007 | 4.04 | 4.8519 | 5.2792 | 6.1339 | 6.9885 | 0.97168 | 2.6395 | 3.3105 | 3.3105 | 3.3105 | 3.3105 | 1.3337 | 1.6928 | 1.6928 | 1.6928 | 1.6928 | 1.6928
2020-08-12 18:00 | Winter | 1.6891 | 2.5971 | 3.93 | 3.93 | 3.93 | 3.93 | 0.71447 | 0.71447 | 0.71447 | 0.71447 | 0.71447 | 0.71447 | 2.7626 | 3.985 | 4.7859 | 5.2074 | 6.0504 | 6.8934 | 0.90343 | 2.4541 | 3.078 | 3.078 | 3.078 | 3.078 | 0.88406 | 1.1221 | 1.1221 | 1.1221 | 1.1221 | 1.1221
2020-08-12 19:00 | Winter | 1.1625 | 1.7874 | 2.7047 | 2.7047 | 2.7047 | 2.7047 | 0.54585 | 0.54585 | 0.54585 | 0.54585 | 0.54585 | 0.54585 | 2.7055 | 3.9026 | 4.6869 | 5.0996 | 5.9252 | 6.7508 | 0.79258 | 2.153 | 2.7003 | 2.7003 | 2.7003 | 2.7003 | 0.70494 | 0.89477 | 0.89477 | 0.89477 | 0.89477 | 0.89477
2020-08-12 20:00 | Winter | 1.105 | 1.6991 | 2.5711 | 2.5711 | 2.5711 | 2.5711 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 2.553 | 3.6827 | 4.4228 | 4.8123 | 5.5914 | 6.3705 | 0.72781 | 1.977 | 2.4796 | 2.4796 | 2.4796 | 2.4796 | 0.60968 | 0.77386 | 0.77386 | 0.77386 | 0.77386 | 0.77386
2020-08-12 21:00 | Winter | 1.0288 | 1.582 | 2.3938 | 2.3938 | 2.3938 | 2.3938 | 0.48012 | 0.48012 | 0.48012 | 0.48012 | 0.48012 | 0.48012 | 2.3244 | 3.3529 | 4.0267 | 4.3814 | 5.0907 | 5.8 | 0.70875 | 1.9253 | 2.4147 | 2.4147 | 2.4147 | 2.4147 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-08-12 22:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 2.205 | 3.1806 | 3.8198 | 4.1562 | 4.8291 | 5.5019 | 0.67446 | 1.8321 | 2.2979 | 2.2979 | 2.2979 | 2.2979 | 0.49592 | 0.62946 | 0.62946 | 0.62946 | 0.62946 | 0.62946
2020-08-12 23:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 1.9606 | 2.8282 | 3.3965 | 3.6957 | 4.294 | 4.8923 | 0.6516 | 1.77 | 2.22 | 2.22 | 2.22 | 2.22 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-08-13 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 1.7909 | 2.5834 | 3.1026 | 3.3758 | 3.9223 | 4.4688 | 0.56014 | 1.5216 | 1.9084 | 1.9084 | 1.9084 | 1.9084 | 0.49537 | 0.62876 | 0.62876 | 0.62876 | 0.62876 | 0.62876
2020-08-13 01:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 1.7338 | 2.5009 | 3.0036 | 3.2681 | 3.7972 | 4.3262 | 0.59063 | 1.6044 | 2.0123 | 2.0123 | 2.0123 | 2.0123 | 0.4952 | 0.62854 | 0.62854 | 0.62854 | 0.62854 | 0.62854
2020-08-13 02:00 | Winter | 1.105 | 1.6991 | 2.5711 | 2.5711 | 2.5711 | 2.5711 | 0.43439 | 0.43439 | 0.43439 | 0.43439 | 0.43439 | 0.43439 | 1.7147 | 2.4735 | 2.9705 | 3.2322 | 3.7554 | 4.2787 | 0.56046 | 1.5224 | 1.9095 | 1.9095 | 1.9095 | 1.9095 | 0.45726 | 0.58039 | 0.58039 | 0.58039 | 0.58039 | 0.58039
2020-08-13 03:00 | Winter | 1.1427 | 1.757 | 2.6587 | 2.6587 | 2.6587 | 2.6587 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 1.6766 | 2.4185 | 2.9045 | 3.1603 | 3.672 | 4.1836 | 0.53347 | 1.4491 | 1.8175 | 1.8175 | 1.8175 | 1.8175 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-08-13 04:00 | Winter | 1.2003 | 1.8456 | 2.7928 | 2.7928 | 2.7928 | 2.7928 | 0.49727 | 0.49727 | 0.49727 | 0.49727 | 0.49727 | 0.49727 | 1.7719 | 2.5559 | 3.0696 | 3.3399 | 3.8806 | 4.4213 | 0.56395 | 1.5319 | 1.9214 | 1.9214 | 1.9214 | 1.9214 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-08-13 05:00 | Winter | 1.3313 | 2.047 | 3.0975 | 3.0975 | 3.0975 | 3.0975 | 0.65832 | 0.65832 | 0.65832 | 0.65832 | 0.65832 | 0.65832 | 1.8972 | 2.7366 | 3.2866 | 3.5761 | 4.155 | 4.7339 | 0.69351 | 1.8839 | 2.3628 | 2.3628 | 2.3628 | 2.3628 | 0.74579 | 0.94662 | 0.94662 | 0.94662 | 0.94662 | 0.94662
2020-08-13 06:00 | Winter | 1.5551 | 2.3912 | 3.6184 | 3.6184 | 3.6184 | 3.6184 | 0.72304 | 0.72304 | 0.72304 | 0.72304 | 0.72304 | 0.72304 | 2.2341 | 3.2226 | 3.8702 | 4.2111 | 4.8928 | 5.5746 | 0.74305 | 2.0184 | 2.5316 | 2.5316 | 2.5316 | 2.5316 | 0.96784 | 1.2285 | 1.2285 | 1.2285 | 1.2285 | 1.2285
2020-08-13 07:00 | Winter | 1.991 | 3.0614 | 4.6326 | 4.6326 | 4.6326 | 4.6326 | 0.93285 | 0.93285 | 0.93285 | 0.93285 | 0.93285 | 0.93285 | 2.4768 | 3.5728 | 4.2908 | 4.6687 | 5.4245 | 6.1803 | 0.88023 | 2.3911 | 2.9989 | 2.9989 | 2.9989 | 2.9989 | 1.2956 | 1.6444 | 1.6444 | 1.6444 | 1.6444 | 1.6444
2020-08-13 08:00 | Winter | 2.2482 | 3.4569 | 5.2309 | 5.2309 | 5.2309 | 5.2309 | 0.9631 | 0.9631 | 0.9631 | 0.9631 | 0.9631 | 0.9631 | 2.5911 | 3.7377 | 4.4888 | 4.8842 | 5.6749 | 6.4656 | 0.97168 | 2.6395 | 3.3105 | 3.3105 | 3.3105 | 3.3105 | 1.6195 | 2.0556 | 2.0556 | 2.0556 | 2.0556 | 2.0556
2020-08-13 09:00 | Winter | 2.2482 | 3.4569 | 5.2309 | 5.2309 | 5.2309 | 5.2309 | 0.95739 | 0.95739 | 0.95739 | 0.95739 | 0.95739 | 0.95739 | 2.6293 | 3.7926 | 4.5548 | 4.956 | 5.7583 | 6.5606 | 0.9069 | 2.4635 | 3.0898 | 3.0898 | 3.0898 | 3.0898 | 1.5856 | 2.0125 | 2.0125 | 2.0125 | 2.0125 | 2.0125
2020-08-13 10:00 | Winter | 2.191 | 3.369 | 5.0979 | 5.0979 | 5.0979 | 5.0979 | 0.90023 | 0.90023 | 0.90023 | 0.90023 | 0.90023 | 0.90023 | 2.6483 | 3.8201 | 4.5878 | 4.9919 | 5.8 | 6.6082 | 0.9069 | 2.4635 | 3.0898 | 3.0898 | 3.0898 | 3.0898 | 1.6004 | 2.0314 | 2.0314 | 2.0314 | 2.0314 | 2.0314
2020-08-13 11:00 | Winter | 2.172 | 3.3397 | 5.0536 | 5.0536 | 5.0536 | 5.0536 | 0.90309 | 0.90309 | 0.90309 | 0.90309 | 0.90309 | 0.90309 | 2.5911 | 3.7377 | 4.4888 | 4.8842 | 5.6749 | 6.4656 | 0.81926 | 2.2254 | 2.7912 | 2.7912 | 2.7912 | 2.7912 | 1.5433 | 1.9588 | 1.9588 | 1.9588 | 1.9588 | 1.9588
2020-08-13 12:00 | Winter | 2.1148 | 3.2518 | 4.9206 | 4.9206 | 4.9206 | 4.9206 | 0.90595 | 0.90595 | 0.90595 | 0.90595 | 0.90595 | 0.90595 | 2.576 | 3.7158 | 4.4625 | 4.8556 | 5.6417 | 6.4277 | 0.80402 | 2.184 | 2.7393 | 2.7393 | 2.7393 | 2.7393 | 1.5052 | 1.9105 | 1.9105 | 1.9105 | 1.9105 | 1.9105
2020-08-13 13:00 | Winter | 2.1529 | 3.3104 | 5.0093 | 5.0093 | 5.0093 | 5.0093 | 0.8867 | 0.8867 | 0.8867 | 0.8867 | 0.8867 | 0.8867 | 2.6102 | 3.7651 | 4.5218 | 4.9201 | 5.7166 | 6.5131 | 0.79258 | 2.153 | 2.7003 | 2.7003 | 2.7003 | 2.7003 | 1.4289 | 1.8137 | 1.8137 | 1.8137 | 1.8137 | 1.8137
2020-08-13 14:00 | Winter | 2.1339 | 3.2811 | 4.9649 | 4.9649 | 4.9649 | 4.9649 | 0.87737 | 0.87737 | 0.87737 | 0.87737 | 0.87737 | 0.87737 | 2.5721 | 3.7102 | 4.4558 | 4.8483 | 5.6331 | 6.418 | 0.81545 | 2.2151 | 2.7782 | 2.7782 | 2.7782 | 2.7782 | 1.3527 | 1.717 | 1.717 | 1.717 | 1.717 | 1.717
2020-08-13 15:00 | Winter | 2.191 | 3.369 | 5.0979 | 5.0979 | 5.0979 | 5.0979 | 0.89451 | 0.89451 | 0.89451 | 0.89451 | 0.89451 | 0.89451 | 2.4959 | 3.6002 | 4.3238 | 4.7046 | 5.4662 | 6.2279 | 0.82717 | 2.2469 | 2.8182 | 2.8182 | 2.8182 | 2.8182 | 1.2956 | 1.6444 | 1.6444 | 1.6444 | 1.6444 | 1.6444
2020-08-13 16:00 | Winter | 2.1339 | 3.2811 | 4.9649 | 4.9649 | 4.9649 | 4.9649 | 0.89166 | 0.89166 | 0.89166 | 0.89166 | 0.89166 | 0.89166 | 2.4578 | 3.5453 | 4.2578 | 4.6328 | 5.3828 | 6.1328 | 0.92214 | 2.5049 | 3.1418 | 3.1418 | 3.1418 | 3.1418 | 1.2765 | 1.6203 | 1.6203 | 1.6203 | 1.6203 | 1.6203
2020-08-13 17:00 | Winter | 2.0196 | 3.1053 | 4.699 | 4.699 | 4.699 | 4.699 | 0.76305 | 0.76305 | 0.76305 | 0.76305 | 0.76305 | 0.76305 | 2.4959 | 3.6002 | 4.3238 | 4.7046 | 5.4662 | 6.2279 | 0.84974 | 2.3082 | 2.8951 | 2.8951 | 2.8951 | 2.8951 | 1.1622 | 1.4752 | 1.4752 | 1.4752 | 1.4752 | 1.4752
2020-08-13 18:00 | Winter | 1.5975 | 2.4563 | 3.7169 | 3.7169 | 3.7169 | 3.7169 | 0.70018 | 0.70018 | 0.70018 | 0.70018 | 0.70018 | 0.70018 | 2.4774 | 3.5736 | 4.2918 | 4.6698 | 5.4259 | 6.1819 | 0.84212 | 2.2875 | 2.8691 | 2.8691 | 2.8691 | 2.8691 | 0.87744 | 1.1137 | 1.1137 | 1.1137 | 1.1137 | 1.1137
2020-08-13 19:00 | Winter | 1.1836 | 1.8199 | 2.7538 | 2.7538 | 2.7538 | 2.7538 | 0.65445 | 0.65445 | 0.65445 | 0.65445 | 0.65445 | 0.65445 | 2.3625 | 3.4079 | 4.0927 | 4.4532 | 5.1741 | 5.8951 | 0.80021 | 2.1737 | 2.7263 | 2.7263 | 2.7263 | 2.7263 | 0.62873 | 0.79804 | 0.79804 | 0.79804 | 0.79804 | 0.79804
2020-08-13 20:00 | Winter | 1.1241 | 1.7284 | 2.6155 | 2.6155 | 2.6155 | 2.6155 | 0.50584 | 0.50584 | 0.50584 | 0.50584 | 0.50584 | 0.50584 | 2.2101 | 3.188 | 3.8287 | 4.1659 | 4.8403 | 5.5147 | 0.70494 | 1.9149 | 2.4018 | 2.4018 | 2.4018 | 2.4018 | 0.59063 | 0.74967 | 0.74967 | 0.74967 | 0.74967 | 0.74967
2020-08-13 21:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 0.50584 | 0.50584 | 0.50584 | 0.50584 | 0.50584 | 0.50584 | 2.1148 | 3.0506 | 3.6637 | 3.9863 | 4.6317 | 5.277 | 0.75448 | 2.0495 | 2.5705 | 2.5705 | 2.5705 | 2.5705 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-08-13 22:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.47441 | 0.47441 | 0.47441 | 0.47441 | 0.47441 | 0.47441 | 2.0196 | 2.9132 | 3.4986 | 3.8068 | 4.4231 | 5.0393 | 0.63254 | 1.7182 | 2.1551 | 2.1551 | 2.1551 | 2.1551 | 0.49537 | 0.62876 | 0.62876 | 0.62876 | 0.62876 | 0.62876
2020-08-13 23:00 | Winter | 1.007 | 1.5484 | 2.3431 | 2.3431 | 2.3431 | 2.3431 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 1.829 | 2.6383 | 3.1686 | 3.4477 | 4.0058 | 4.5639 | 0.60968 | 1.6561 | 2.0772 | 2.0772 | 2.0772 | 2.0772 | 0.45726 | 0.58039 | 0.58039 | 0.58039 | 0.58039 | 0.58039
2020-08-14 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.42582 | 0.42582 | 0.42582 | 0.42582 | 0.42582 | 0.42582 | 1.6766 | 2.4185 | 2.9045 | 3.1603 | 3.672 | 4.1836 | 0.56395 | 1.5319 | 1.9214 | 1.9214 | 1.9214 | 1.9214 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-08-14 01:00 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 1.552 | 2.2388 | 2.6887 | 2.9255 | 3.3991 | 3.8727 | 0.56395 | 1.5319 | 1.9214 | 1.9214 | 1.9214 | 1.9214 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-08-14 02:00 | Winter | 0.93358 | 1.4355 | 2.1722 | 2.1722 | 2.1722 | 2.1722 | 0.4544 | 0.4544 | 0.4544 | 0.4544 | 0.4544 | 0.4544 | 1.5623 | 2.2536 | 2.7065 | 2.9449 | 3.4216 | 3.8984 | 0.5449 | 1.4802 | 1.8565 | 1.8565 | 1.8565 | 1.8565 | 0.45726 | 0.58039 | 0.58039 | 0.58039 | 0.58039 | 0.58039
2020-08-14 03:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 0.43439 | 0.43439 | 0.43439 | 0.43439 | 0.43439 | 0.43439 | 1.5814 | 2.2811 | 2.7395 | 2.9808 | 3.4633 | 3.9459 | 0.63254 | 1.7182 | 2.1551 | 2.1551 | 2.1551 | 2.1551 | 0.45726 | 0.58039 | 0.58039 | 0.58039 | 0.58039 | 0.58039
2020-08-14 04:00 | Winter | 1.1432 | 1.7577 | 2.6598 | 2.6598 | 2.6598 | 2.6598 | 0.49441 | 0.49441 | 0.49441 | 0.49441 | 0.49441 | 0.49441 | 1.6805 | 2.424 | 2.9112 | 3.1676 | 3.6804 | 4.1932 | 0.59063 | 1.6044 | 2.0123 | 2.0123 | 2.0123 | 2.0123 | 0.55252 | 0.70131 | 0.70131 | 0.70131 | 0.70131 | 0.70131
2020-08-14 05:00 | Winter | 1.3171 | 2.0251 | 3.0644 | 3.0644 | 3.0644 | 3.0644 | 0.59444 | 0.59444 | 0.59444 | 0.59444 | 0.59444 | 0.59444 | 1.8254 | 2.6331 | 3.1623 | 3.4408 | 3.9978 | 4.5549 | 0.76591 | 2.0805 | 2.6095 | 2.6095 | 2.6095 | 2.6095 | 0.7421 | 0.94193 | 0.94193 | 0.94193 | 0.94193 | 0.94193
2020-08-14 06:00 | Winter | 1.5335 | 2.358 | 3.568 | 3.568 | 3.568 | 3.568 | 0.71733 | 0.71733 | 0.71733 | 0.71733 | 0.71733 | 0.71733 | 2.0955 | 3.0227 | 3.6302 | 3.9499 | 4.5894 | 5.2288 | 0.79258 | 2.153 | 2.7003 | 2.7003 | 2.7003 | 2.7003 | 0.93358 | 1.185 | 1.185 | 1.185 | 1.185 | 1.185
2020-08-14 07:00 | Winter | 2.0074 | 3.0867 | 4.6707 | 4.6707 | 4.6707 | 4.6707 | 0.87737 | 0.87737 | 0.87737 | 0.87737 | 0.87737 | 0.87737 | 2.4006 | 3.4628 | 4.1588 | 4.525 | 5.2576 | 5.9902 | 0.88404 | 2.4014 | 3.0119 | 3.0119 | 3.0119 | 3.0119 | 1.3337 | 1.6928 | 1.6928 | 1.6928 | 1.6928 | 1.6928
2020-08-14 08:00 | Winter | 2.4006 | 3.6912 | 5.5856 | 5.5856 | 5.5856 | 5.5856 | 0.98025 | 0.98025 | 0.98025 | 0.98025 | 0.98025 | 0.98025 | 2.4387 | 3.5178 | 4.2248 | 4.5969 | 5.3411 | 6.0852 | 0.92976 | 2.5256 | 3.1677 | 3.1677 | 3.1677 | 3.1677 | 1.467 | 1.8621 | 1.8621 | 1.8621 | 1.8621 | 1.8621
2020-08-14 09:00 | Winter | 2.4197 | 3.7205 | 5.6299 | 5.6299 | 5.6299 | 5.6299 | 0.97168 | 0.97168 | 0.97168 | 0.97168 | 0.97168 | 0.97168 | 2.5911 | 3.7377 | 4.4888 | 4.8842 | 5.6749 | 6.4656 | 0.91452 | 2.4842 | 3.1158 | 3.1158 | 3.1158 | 3.1158 | 1.5052 | 1.9105 | 1.9105 | 1.9105 | 1.9105 | 1.9105
2020-08-14 10:00 | Winter | 2.2863 | 3.5155 | 5.3196 | 5.3196 | 5.3196 | 5.3196 | 1.0003 | 1.0003 | 1.0003 | 1.0003 | 1.0003 | 1.0003 | 2.7055 | 3.9026 | 4.6869 | 5.0996 | 5.9252 | 6.7508 | 0.91833 | 2.4946 | 3.1288 | 3.1288 | 3.1288 | 3.1288 | 1.5814 | 2.0072 | 2.0072 | 2.0072 | 2.0072 | 2.0072
2020-08-14 11:00 | Winter | 2.2673 | 3.4862 | 5.2753 | 5.2753 | 5.2753 | 5.2753 | 0.9974 | 0.9974 | 0.9974 | 0.9974 | 0.9974 | 0.9974 | 2.7055 | 3.9026 | 4.6869 | 5.0996 | 5.9252 | 6.7508 | 0.89547 | 2.4325 | 3.0509 | 3.0509 | 3.0509 | 3.0509 | 1.5433 | 1.9588 | 1.9588 | 1.9588 | 1.9588 | 1.9588
2020-08-14 12:00 | Winter | 2.1339 | 3.2811 | 4.9649 | 4.9649 | 4.9649 | 4.9649 | 0.98311 | 0.98311 | 0.98311 | 0.98311 | 0.98311 | 0.98311 | 2.6864 | 3.8751 | 4.6539 | 5.0637 | 5.8835 | 6.7033 | 0.82307 | 2.2358 | 2.8042 | 2.8042 | 2.8042 | 2.8042 | 1.5433 | 1.9588 | 1.9588 | 1.9588 | 1.9588 | 1.9588
2020-08-14 13:00 | Winter | 2.1148 | 3.2518 | 4.9206 | 4.9206 | 4.9206 | 4.9206 | 0.93452 | 0.93452 | 0.93452 | 0.93452 | 0.93452 | 0.93452 | 2.5911 | 3.7377 | 4.4888 | 4.8842 | 5.6749 | 6.4656 | 0.82307 | 2.2358 | 2.8042 | 2.8042 | 2.8042 | 2.8042 | 1.467 | 1.8621 | 1.8621 | 1.8621 | 1.8621 | 1.8621
2020-08-14 14:00 | Winter | 2.0577 | 3.1639 | 4.7876 | 4.7876 | 4.7876 | 4.7876 | 0.95167 | 0.95167 | 0.95167 | 0.95167 | 0.95167 | 0.95167 | 2.5721 | 3.7102 | 4.4558 | 4.8483 | 5.6331 | 6.418 | 0.81545 | 2.2151 | 2.7782 | 2.7782 | 2.7782 | 2.7782 | 1.3527 | 1.717 | 1.717 | 1.717 | 1.717 | 1.717
2020-08-14 15:00 | Winter | 2.0577 | 3.1639 | 4.7876 | 4.7876 | 4.7876 | 4.7876 | 0.86879 | 0.86879 | 0.86879 | 0.86879 | 0.86879 | 0.86879 | 2.4197 | 3.4903 | 4.1918 | 4.561 | 5.2993 | 6.0377 | 0.80402 | 2.184 | 2.7393 | 2.7393 | 2.7393 | 2.7393 | 1.3146 | 1.6686 | 1.6686 | 1.6686 | 1.6686 | 1.6686
2020-08-14 16:00 | Winter | 2.0386 | 3.1346 | 4.7433 | 4.7433 | 4.7433 | 4.7433 | 0.83736 | 0.83736 | 0.83736 | 0.83736 | 0.83736 | 0.83736 | 2.5149 | 3.6277 | 4.3568 | 4.7405 | 5.508 | 6.2754 | 0.81926 | 2.2254 | 2.7912 | 2.7912 | 2.7912 | 2.7912 | 1.2194 | 1.5477 | 1.5477 | 1.5477 | 1.5477 | 1.5477
2020-08-14 17:00 | Winter | 1.9243 | 2.9588 | 4.4773 | 4.4773 | 4.4773 | 4.4773 | 0.87451 | 0.87451 | 0.87451 | 0.87451 | 0.87451 | 0.87451 | 2.553 | 3.6827 | 4.4228 | 4.8123 | 5.5914 | 6.3705 | 0.82307 | 2.2358 | 2.8042 | 2.8042 | 2.8042 | 2.8042 | 1.1813 | 1.4993 | 1.4993 | 1.4993 | 1.4993 | 1.4993
2020-08-14 18:00 | Winter | 1.5946 | 2.4519 | 3.7102 | 3.7102 | 3.7102 | 3.7102 | 0.78591 | 0.78591 | 0.78591 | 0.78591 | 0.78591 | 0.78591 | 2.4953 | 3.5993 | 4.3227 | 4.7034 | 5.4649 | 6.2263 | 0.80021 | 2.1737 | 2.7263 | 2.7263 | 2.7263 | 2.7263 | 0.91685 | 1.1637 | 1.1637 | 1.1637 | 1.1637 | 1.1637
2020-08-14 19:00 | Winter | 1.1241 | 1.7284 | 2.6155 | 2.6155 | 2.6155 | 2.6155 | 0.56586 | 0.56586 | 0.56586 | 0.56586 | 0.56586 | 0.56586 | 2.3254 | 3.3543 | 4.0284 | 4.3832 | 5.0928 | 5.8024 | 0.81164 | 2.2047 | 2.7653 | 2.7653 | 2.7653 | 2.7653 | 0.61367 | 0.77891 | 0.77891 | 0.77891 | 0.77891 | 0.77891
2020-08-14 20:00 | Winter | 1.0669 | 1.6405 | 2.4825 | 2.4825 | 2.4825 | 2.4825 | 0.59729 | 0.59729 | 0.59729 | 0.59729 | 0.59729 | 0.59729 | 2.3186 | 3.3445 | 4.0167 | 4.3705 | 5.078 | 5.7855 | 0.7621 | 2.0702 | 2.5965 | 2.5965 | 2.5965 | 2.5965 | 0.66684 | 0.84641 | 0.84641 | 0.84641 | 0.84641 | 0.84641
2020-08-14 21:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.52585 | 0.52585 | 0.52585 | 0.52585 | 0.52585 | 0.52585 | 2.191 | 3.1605 | 3.7957 | 4.13 | 4.7986 | 5.4672 | 0.73543 | 1.9977 | 2.5056 | 2.5056 | 2.5056 | 2.5056 | 0.55388 | 0.70302 | 0.70302 | 0.70302 | 0.70302 | 0.70302
2020-08-14 22:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.49727 | 0.49727 | 0.49727 | 0.49727 | 0.49727 | 0.49727 | 2.0767 | 2.9956 | 3.5977 | 3.9145 | 4.5482 | 5.182 | 0.71256 | 1.9356 | 2.4277 | 2.4277 | 2.4277 | 2.4277 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-08-14 23:00 | Winter | 0.91452 | 1.4062 | 2.1278 | 2.1278 | 2.1278 | 2.1278 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 1.9434 | 2.8032 | 3.3666 | 3.6631 | 4.2562 | 4.8492 | 0.62111 | 1.6872 | 2.1161 | 2.1161 | 2.1161 | 2.1161 | 0.47653 | 0.60485 | 0.60485 | 0.60485 | 0.60485 | 0.60485
2020-08-15 | Winter | 0.93358 | 1.4355 | 2.1722 | 2.1722 | 2.1722 | 2.1722 | 0.39153 | 0.39153 | 0.39153 | 0.39153 | 0.39153 | 0.39153 | 1.6976 | 2.4487 | 2.9408 | 3.1998 | 3.7178 | 4.2358 | 0.59825 | 1.6251 | 2.0382 | 2.0382 | 2.0382 | 2.0382 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-08-15 01:00 | Winter | 0.93358 | 1.4355 | 2.1722 | 2.1722 | 2.1722 | 2.1722 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.54549 | 1.4818 | 1.8585 | 1.8585 | 1.8585 | 1.8585 | 0.45974 | 0.58353 | 0.58353 | 0.58353 | 0.58353 | 0.58353
2020-08-15 02:00 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 1.6004 | 2.3086 | 2.7725 | 3.0167 | 3.5051 | 3.9934 | 0.58682 | 1.594 | 1.9993 | 1.9993 | 1.9993 | 1.9993 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-08-15 03:00 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.40758 | 0.40758 | 0.40758 | 0.40758 | 0.40758 | 0.40758 | 1.5814 | 2.2811 | 2.7395 | 2.9808 | 3.4633 | 3.9459 | 0.5792 | 1.5733 | 1.9733 | 1.9733 | 1.9733 | 1.9733 | 0.45726 | 0.58039 | 0.58039 | 0.58039 | 0.58039 | 0.58039
2020-08-15 04:00 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 1.6957 | 2.446 | 2.9375 | 3.1963 | 3.7137 | 4.2311 | 0.59825 | 1.6251 | 2.0382 | 2.0382 | 2.0382 | 2.0382 | 0.45726 | 0.58039 | 0.58039 | 0.58039 | 0.58039 | 0.58039
2020-08-15 05:00 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.47726 | 0.47726 | 0.47726 | 0.47726 | 0.47726 | 0.47726 | 1.7764 | 2.5625 | 3.0774 | 3.3485 | 3.8906 | 4.4327 | 0.58301 | 1.5837 | 1.9863 | 1.9863 | 1.9863 | 1.9863 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-08-15 06:00 | Winter | 1.0111 | 1.5547 | 2.3525 | 2.3525 | 2.3525 | 2.3525 | 0.48584 | 0.48584 | 0.48584 | 0.48584 | 0.48584 | 0.48584 | 1.9624 | 2.8307 | 3.3996 | 3.699 | 4.2979 | 4.8967 | 0.60587 | 1.6458 | 2.0642 | 2.0642 | 2.0642 | 2.0642 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-08-15 07:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 0.64874 | 0.64874 | 0.64874 | 0.64874 | 0.64874 | 0.64874 | 2.0005 | 2.8857 | 3.4656 | 3.7709 | 4.3813 | 4.9918 | 0.64016 | 1.7389 | 2.1811 | 2.1811 | 2.1811 | 2.1811 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-08-15 08:00 | Winter | 1.086 | 1.6698 | 2.5268 | 2.5268 | 2.5268 | 2.5268 | 0.71161 | 0.71161 | 0.71161 | 0.71161 | 0.71161 | 0.71161 | 2.0577 | 2.9681 | 3.5647 | 3.8786 | 4.5065 | 5.1344 | 0.67065 | 1.8218 | 2.2849 | 2.2849 | 2.2849 | 2.2849 | 0.55252 | 0.70131 | 0.70131 | 0.70131 | 0.70131 | 0.70131
2020-08-15 09:00 | Winter | 1.086 | 1.6698 | 2.5268 | 2.5268 | 2.5268 | 2.5268 | 0.70304 | 0.70304 | 0.70304 | 0.70304 | 0.70304 | 0.70304 | 2.1339 | 3.0781 | 3.6967 | 4.0223 | 4.6734 | 5.3246 | 0.73924 | 2.0081 | 2.5186 | 2.5186 | 2.5186 | 2.5186 | 0.55252 | 0.70131 | 0.70131 | 0.70131 | 0.70131 | 0.70131
2020-08-15 10:00 | Winter | 1.0478 | 1.6111 | 2.4379 | 2.4379 | 2.4379 | 2.4379 | 0.68875 | 0.68875 | 0.68875 | 0.68875 | 0.68875 | 0.68875 | 2.2101 | 3.188 | 3.8287 | 4.1659 | 4.8403 | 5.5147 | 0.70875 | 1.9253 | 2.4147 | 2.4147 | 2.4147 | 2.4147 | 0.62873 | 0.79804 | 0.79804 | 0.79804 | 0.79804 | 0.79804
2020-08-15 11:00 | Winter | 1.105 | 1.6991 | 2.5711 | 2.5711 | 2.5711 | 2.5711 | 0.73447 | 0.73447 | 0.73447 | 0.73447 | 0.73447 | 0.73447 | 2.2482 | 3.243 | 3.8947 | 4.2377 | 4.9238 | 5.6098 | 0.64779 | 1.7596 | 2.207 | 2.207 | 2.207 | 2.207 | 0.62873 | 0.79804 | 0.79804 | 0.79804 | 0.79804 | 0.79804
2020-08-15 12:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.76305 | 0.76305 | 0.76305 | 0.76305 | 0.76305 | 0.76305 | 2.2482 | 3.243 | 3.8947 | 4.2377 | 4.9238 | 5.6098 | 0.72781 | 1.977 | 2.4796 | 2.4796 | 2.4796 | 2.4796 | 0.62873 | 0.79804 | 0.79804 | 0.79804 | 0.79804 | 0.79804
2020-08-15 13:00 | Winter | 0.93358 | 1.4355 | 2.1722 | 2.1722 | 2.1722 | 2.1722 | 0.69446 | 0.69446 | 0.69446 | 0.69446 | 0.69446 | 0.69446 | 2.3244 | 3.3529 | 4.0267 | 4.3814 | 5.0907 | 5.8 | 0.63635 | 1.7286 | 2.1681 | 2.1681 | 2.1681 | 2.1681 | 0.59063 | 0.74967 | 0.74967 | 0.74967 | 0.74967 | 0.74967
2020-08-15 14:00 | Winter | 0.81926 | 1.2597 | 1.9062 | 1.9062 | 1.9062 | 1.9062 | 0.73733 | 0.73733 | 0.73733 | 0.73733 | 0.73733 | 0.73733 | 2.3054 | 3.3254 | 3.9937 | 4.3455 | 5.049 | 5.7525 | 0.67827 | 1.8425 | 2.3109 | 2.3109 | 2.3109 | 2.3109 | 0.59063 | 0.74967 | 0.74967 | 0.74967 | 0.74967 | 0.74967
2020-08-15 15:00 | Winter | 0.80021 | 1.2304 | 1.8619 | 1.8619 | 1.8619 | 1.8619 | 0.69446 | 0.69446 | 0.69446 | 0.69446 | 0.69446 | 0.69446 | 2.3829 | 3.4373 | 4.128 | 4.4916 | 5.2188 | 5.9459 | 0.70113 | 1.9046 | 2.3888 | 2.3888 | 2.3888 | 2.3888 | 0.59063 | 0.74967 | 0.74967 | 0.74967 | 0.74967 | 0.74967
2020-08-15 16:00 | Winter | 0.83831 | 1.289 | 1.9505 | 1.9505 | 1.9505 | 1.9505 | 0.62301 | 0.62301 | 0.62301 | 0.62301 | 0.62301 | 0.62301 | 2.4387 | 3.5178 | 4.2248 | 4.5969 | 5.3411 | 6.0852 | 0.72781 | 1.977 | 2.4796 | 2.4796 | 2.4796 | 2.4796 | 0.5155 | 0.65431 | 0.65431 | 0.65431 | 0.65431 | 0.65431
2020-08-15 17:00 | Winter | 0.81926 | 1.2597 | 1.9062 | 1.9062 | 1.9062 | 1.9062 | 0.60873 | 0.60873 | 0.60873 | 0.60873 | 0.60873 | 0.60873 | 2.3625 | 3.4079 | 4.0927 | 4.4532 | 5.1741 | 5.8951 | 0.82688 | 2.2461 | 2.8172 | 2.8172 | 2.8172 | 2.8172 | 0.55252 | 0.70131 | 0.70131 | 0.70131 | 0.70131 | 0.70131
2020-08-15 18:00 | Winter | 0.78115 | 1.2011 | 1.8175 | 1.8175 | 1.8175 | 1.8175 | 0.59158 | 0.59158 | 0.59158 | 0.59158 | 0.59158 | 0.59158 | 2.4197 | 3.4903 | 4.1918 | 4.561 | 5.2993 | 6.0377 | 0.84974 | 2.3082 | 2.8951 | 2.8951 | 2.8951 | 2.8951 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-08-15 19:00 | Winter | 0.76228 | 1.1721 | 1.7736 | 1.7736 | 1.7736 | 1.7736 | 0.6373 | 0.6373 | 0.6373 | 0.6373 | 0.6373 | 0.6373 | 2.4387 | 3.5178 | 4.2248 | 4.5969 | 5.3411 | 6.0852 | 0.84593 | 2.2979 | 2.8821 | 2.8821 | 2.8821 | 2.8821 | 0.55252 | 0.70131 | 0.70131 | 0.70131 | 0.70131 | 0.70131
2020-08-15 20:00 | Winter | 0.7621 | 1.1718 | 1.7732 | 1.7732 | 1.7732 | 1.7732 | 0.56586 | 0.56586 | 0.56586 | 0.56586 | 0.56586 | 0.56586 | 2.2482 | 3.243 | 3.8947 | 4.2377 | 4.9238 | 5.6098 | 0.73924 | 2.0081 | 2.5186 | 2.5186 | 2.5186 | 2.5186 | 0.55252 | 0.70131 | 0.70131 | 0.70131 | 0.70131 | 0.70131
2020-08-15 21:00 | Winter | 0.78115 | 1.2011 | 1.8175 | 1.8175 | 1.8175 | 1.8175 | 0.53156 | 0.53156 | 0.53156 | 0.53156 | 0.53156 | 0.53156 | 2.2101 | 3.188 | 3.8287 | 4.1659 | 4.8403 | 5.5147 | 0.74686 | 2.0288 | 2.5446 | 2.5446 | 2.5446 | 2.5446 | 0.55252 | 0.70131 | 0.70131 | 0.70131 | 0.70131 | 0.70131
2020-08-15 22:00 | Winter | 0.7621 | 1.1718 | 1.7732 | 1.7732 | 1.7732 | 1.7732 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 2.1339 | 3.0781 | 3.6967 | 4.0223 | 4.6734 | 5.3246 | 0.73924 | 2.0081 | 2.5186 | 2.5186 | 2.5186 | 2.5186 | 0.47112 | 0.59799 | 0.59799 | 0.59799 | 0.59799 | 0.59799
2020-08-15 23:00 | Winter | 0.78115 | 1.2011 | 1.8175 | 1.8175 | 1.8175 | 1.8175 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 1.9243 | 2.7758 | 3.3336 | 3.6272 | 4.2144 | 4.8016 | 0.64016 | 1.7389 | 2.1811 | 2.1811 | 2.1811 | 2.1811 | 0.49537 | 0.62876 | 0.62876 | 0.62876 | 0.62876 | 0.62876
2020-08-16 | Winter | 1.1432 | 1.7577 | 2.6598 | 2.6598 | 2.6598 | 2.6598 | 0.46869 | 0.46869 | 0.46869 | 0.46869 | 0.46869 | 0.46869 | 1.7338 | 2.5009 | 3.0036 | 3.2681 | 3.7972 | 4.3262 | 0.60587 | 1.6458 | 2.0642 | 2.0642 | 2.0642 | 2.0642 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-08-16 01:00 | Winter | 1.1241 | 1.7284 | 2.6155 | 2.6155 | 2.6155 | 2.6155 | 0.45837 | 0.45837 | 0.45837 | 0.45837 | 0.45837 | 0.45837 | 1.6576 | 2.391 | 2.8715 | 3.1244 | 3.6302 | 4.1361 | 0.60587 | 1.6458 | 2.0642 | 2.0642 | 2.0642 | 2.0642 | 0.49537 | 0.62876 | 0.62876 | 0.62876 | 0.62876 | 0.62876
2020-08-16 02:00 | Winter | 1.0398 | 1.5988 | 2.4192 | 2.4192 | 2.4192 | 2.4192 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 1.6004 | 2.3086 | 2.7725 | 3.0167 | 3.5051 | 3.9934 | 0.60206 | 1.6354 | 2.0512 | 2.0512 | 2.0512 | 2.0512 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-08-16 03:00 | Winter | 1.0095 | 1.5522 | 2.3488 | 2.3488 | 2.3488 | 2.3488 | 0.42296 | 0.42296 | 0.42296 | 0.42296 | 0.42296 | 0.42296 | 1.5623 | 2.2536 | 2.7065 | 2.9449 | 3.4216 | 3.8984 | 0.59444 | 1.6147 | 2.0253 | 2.0253 | 2.0253 | 2.0253 | 0.49537 | 0.62876 | 0.62876 | 0.62876 | 0.62876 | 0.62876
2020-08-16 04:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 0.40582 | 0.40582 | 0.40582 | 0.40582 | 0.40582 | 0.40582 | 1.5623 | 2.2536 | 2.7065 | 2.9449 | 3.4216 | 3.8984 | 0.62111 | 1.6872 | 2.1161 | 2.1161 | 2.1161 | 2.1161 | 0.45726 | 0.58039 | 0.58039 | 0.58039 | 0.58039 | 0.58039
2020-08-16 05:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 1.669 | 2.4075 | 2.8913 | 3.146 | 3.6553 | 4.1646 | 0.60587 | 1.6458 | 2.0642 | 2.0642 | 2.0642 | 2.0642 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-08-16 06:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 0.48869 | 0.48869 | 0.48869 | 0.48869 | 0.48869 | 0.48869 | 1.81 | 2.6109 | 3.1356 | 3.4117 | 3.9641 | 4.5164 | 0.63635 | 1.7286 | 2.1681 | 2.1681 | 2.1681 | 2.1681 | 0.49537 | 0.62876 | 0.62876 | 0.62876 | 0.62876 | 0.62876
2020-08-16 07:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 0.60301 | 0.60301 | 0.60301 | 0.60301 | 0.60301 | 0.60301 | 1.8481 | 2.6658 | 3.2016 | 3.4836 | 4.0475 | 4.6115 | 0.6897 | 1.8735 | 2.3498 | 2.3498 | 2.3498 | 2.3498 | 0.49537 | 0.62876 | 0.62876 | 0.62876 | 0.62876 | 0.62876
2020-08-16 08:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.59729 | 0.59729 | 0.59729 | 0.59729 | 0.59729 | 0.59729 | 1.9624 | 2.8307 | 3.3996 | 3.699 | 4.2979 | 4.8967 | 0.73543 | 1.9977 | 2.5056 | 2.5056 | 2.5056 | 2.5056 | 0.57139 | 0.72525 | 0.72525 | 0.72525 | 0.72525 | 0.72525
2020-08-16 09:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.61444 | 0.61444 | 0.61444 | 0.61444 | 0.61444 | 0.61444 | 2.0767 | 2.9956 | 3.5977 | 3.9145 | 4.5482 | 5.182 | 0.70494 | 1.9149 | 2.4018 | 2.4018 | 2.4018 | 2.4018 | 0.57158 | 0.72549 | 0.72549 | 0.72549 | 0.72549 | 0.72549
2020-08-16 10:00 | Winter | 1.0669 | 1.6405 | 2.4825 | 2.4825 | 2.4825 | 2.4825 | 0.60301 | 0.60301 | 0.60301 | 0.60301 | 0.60301 | 0.60301 | 2.0577 | 2.9681 | 3.5647 | 3.8786 | 4.5065 | 5.1344 | 0.6897 | 1.8735 | 2.3498 | 2.3498 | 2.3498 | 2.3498 | 0.59063 | 0.74967 | 0.74967 | 0.74967 | 0.74967 | 0.74967
2020-08-16 11:00 | Winter | 1.0374 | 1.5952 | 2.4138 | 2.4138 | 2.4138 | 2.4138 | 0.54033 | 0.54033 | 0.54033 | 0.54033 | 0.54033 | 0.54033 | 2.0237 | 2.9191 | 3.5058 | 3.8145 | 4.4321 | 5.0496 | 0.63549 | 1.7262 | 2.1651 | 2.1651 | 2.1651 | 2.1651 | 0.53876 | 0.68384 | 0.68384 | 0.68384 | 0.68384 | 0.68384
2020-08-16 12:00 | Winter | 1.0816 | 1.6631 | 2.5166 | 2.5166 | 2.5166 | 2.5166 | 0.54902 | 0.54902 | 0.54902 | 0.54902 | 0.54902 | 0.54902 | 2.0435 | 2.9477 | 3.5401 | 3.8519 | 4.4755 | 5.0991 | 0.63839 | 1.7341 | 2.175 | 2.175 | 2.175 | 2.175 | 0.57753 | 0.73305 | 0.73305 | 0.73305 | 0.73305 | 0.73305
2020-08-16 13:00 | Winter | 1.1258 | 1.731 | 2.6194 | 2.6194 | 2.6194 | 2.6194 | 0.5577 | 0.5577 | 0.5577 | 0.5577 | 0.5577 | 0.5577 | 2.0633 | 2.9763 | 3.5744 | 3.8892 | 4.5189 | 5.1485 | 0.64129 | 1.742 | 2.1849 | 2.1849 | 2.1849 | 2.1849 | 0.6163 | 0.78225 | 0.78225 | 0.78225 | 0.78225 | 0.78225
2020-08-16 14:00 | Winter | 1.17 | 1.7989 | 2.7222 | 2.7222 | 2.7222 | 2.7222 | 0.56638 | 0.56638 | 0.56638 | 0.56638 | 0.56638 | 0.56638 | 2.0831 | 3.0049 | 3.6087 | 3.9266 | 4.5623 | 5.1979 | 0.64419 | 1.7499 | 2.1948 | 2.1948 | 2.1948 | 2.1948 | 0.65507 | 0.83146 | 0.83146 | 0.83146 | 0.83146 | 0.83146
2020-08-16 15:00 | Winter | 1.2141 | 1.8669 | 2.8249 | 2.8249 | 2.8249 | 2.8249 | 0.57507 | 0.57507 | 0.57507 | 0.57507 | 0.57507 | 0.57507 | 2.1029 | 3.0334 | 3.6431 | 3.9639 | 4.6057 | 5.2474 | 0.64709 | 1.7577 | 2.2046 | 2.2046 | 2.2046 | 2.2046 | 0.69383 | 0.88067 | 0.88067 | 0.88067 | 0.88067 | 0.88067
2020-08-16 16:00 | Winter | 1.2583 | 1.9348 | 2.9277 | 2.9277 | 2.9277 | 2.9277 | 0.58375 | 0.58375 | 0.58375 | 0.58375 | 0.58375 | 0.58375 | 2.1228 | 3.062 | 3.6774 | 4.0013 | 4.649 | 5.2968 | 0.64999 | 1.7656 | 2.2145 | 2.2145 | 2.2145 | 2.2145 | 0.7326 | 0.92988 | 0.92988 | 0.92988 | 0.92988 | 0.92988
2020-08-16 17:00 | Winter | 1.3025 | 2.0027 | 3.0305 | 3.0305 | 3.0305 | 3.0305 | 0.59243 | 0.59243 | 0.59243 | 0.59243 | 0.59243 | 0.59243 | 2.1426 | 3.0906 | 3.7117 | 4.0386 | 4.6924 | 5.3463 | 0.65288 | 1.7735 | 2.2244 | 2.2244 | 2.2244 | 2.2244 | 0.77137 | 0.97909 | 0.97909 | 0.97909 | 0.97909 | 0.97909
2020-08-16 18:00 | Winter | 1.3467 | 2.0707 | 3.1333 | 3.1333 | 3.1333 | 3.1333 | 0.60112 | 0.60112 | 0.60112 | 0.60112 | 0.60112 | 0.60112 | 2.1624 | 3.1192 | 3.746 | 4.076 | 4.7358 | 5.3957 | 0.65578 | 1.7814 | 2.2343 | 2.2343 | 2.2343 | 2.2343 | 0.81014 | 1.0283 | 1.0283 | 1.0283 | 1.0283 | 1.0283
2020-08-16 19:00 | Winter | 1.3908 | 2.1386 | 3.2361 | 3.2361 | 3.2361 | 3.2361 | 0.6098 | 0.6098 | 0.6098 | 0.6098 | 0.6098 | 0.6098 | 2.1822 | 3.1478 | 3.7804 | 4.1133 | 4.7792 | 5.4451 | 0.65868 | 1.7893 | 2.2441 | 2.2441 | 2.2441 | 2.2441 | 0.84891 | 1.0775 | 1.0775 | 1.0775 | 1.0775 | 1.0775
2020-08-16 20:00 | Winter | 1.435 | 2.2065 | 3.3389 | 3.3389 | 3.3389 | 3.3389 | 0.61848 | 0.61848 | 0.61848 | 0.61848 | 0.61848 | 0.61848 | 2.202 | 3.1763 | 3.8147 | 4.1507 | 4.8226 | 5.4946 | 0.66158 | 1.7971 | 2.254 | 2.254 | 2.254 | 2.254 | 0.88768 | 1.1267 | 1.1267 | 1.1267 | 1.1267 | 1.1267
2020-08-16 21:00 | Winter | 1.4792 | 2.2744 | 3.4417 | 3.4417 | 3.4417 | 3.4417 | 0.62717 | 0.62717 | 0.62717 | 0.62717 | 0.62717 | 0.62717 | 2.2218 | 3.2049 | 3.849 | 4.188 | 4.866 | 5.544 | 0.66448 | 1.805 | 2.2639 | 2.2639 | 2.2639 | 2.2639 | 0.92644 | 1.1759 | 1.1759 | 1.1759 | 1.1759 | 1.1759
2020-08-16 22:00 | Winter | 1.5234 | 2.3424 | 3.5445 | 3.5445 | 3.5445 | 3.5445 | 0.63585 | 0.63585 | 0.63585 | 0.63585 | 0.63585 | 0.63585 | 2.2416 | 3.2335 | 3.8833 | 4.2254 | 4.9094 | 5.5935 | 0.66738 | 1.8129 | 2.2738 | 2.2738 | 2.2738 | 2.2738 | 0.96521 | 1.2251 | 1.2251 | 1.2251 | 1.2251 | 1.2251
2020-08-16 23:00 | Winter | 1.5676 | 2.4103 | 3.6472 | 3.6472 | 3.6472 | 3.6472 | 0.64454 | 0.64454 | 0.64454 | 0.64454 | 0.64454 | 0.64454 | 2.2615 | 3.2621 | 3.9177 | 4.2627 | 4.9528 | 5.6429 | 0.67028 | 1.8208 | 2.2837 | 2.2837 | 2.2837 | 2.2837 | 1.004 | 1.2743 | 1.2743 | 1.2743 | 1.2743 | 1.2743
2020-08-17 | Winter | 1.6117 | 2.4782 | 3.75 | 3.75 | 3.75 | 3.75 | 0.65322 | 0.65322 | 0.65322 | 0.65322 | 0.65322 | 0.65322 | 2.2813 | 3.2907 | 3.952 | 4.3001 | 4.9962 | 5.6923 | 0.67318 | 1.8286 | 2.2935 | 2.2935 | 2.2935 | 2.2935 | 1.0427 | 1.3235 | 1.3235 | 1.3235 | 1.3235 | 1.3235
2020-08-17 01:00 | Winter | 1.6559 | 2.5461 | 3.8528 | 3.8528 | 3.8528 | 3.8528 | 0.6619 | 0.6619 | 0.6619 | 0.6619 | 0.6619 | 0.6619 | 2.3011 | 3.3192 | 3.9863 | 4.3374 | 5.0396 | 5.7418 | 0.67608 | 1.8365 | 2.3034 | 2.3034 | 2.3034 | 2.3034 | 1.0815 | 1.3727 | 1.3727 | 1.3727 | 1.3727 | 1.3727
2020-08-17 02:00 | Winter | 1.7001 | 2.6141 | 3.9556 | 3.9556 | 3.9556 | 3.9556 | 0.67059 | 0.67059 | 0.67059 | 0.67059 | 0.67059 | 0.67059 | 2.3209 | 3.3478 | 4.0206 | 4.3748 | 5.083 | 5.7912 | 0.67898 | 1.8444 | 2.3133 | 2.3133 | 2.3133 | 2.3133 | 1.1203 | 1.422 | 1.422 | 1.422 | 1.422 | 1.422
2020-08-17 03:00 | Winter | 1.7443 | 2.682 | 4.0584 | 4.0584 | 4.0584 | 4.0584 | 0.67927 | 0.67927 | 0.67927 | 0.67927 | 0.67927 | 0.67927 | 2.3407 | 3.3764 | 4.055 | 4.4121 | 5.1264 | 5.8406 | 0.68188 | 1.8523 | 2.3232 | 2.3232 | 2.3232 | 2.3232 | 1.1591 | 1.4712 | 1.4712 | 1.4712 | 1.4712 | 1.4712
2020-08-17 04:00 | Winter | 1.7884 | 2.7499 | 4.1612 | 4.1612 | 4.1612 | 4.1612 | 0.68795 | 0.68795 | 0.68795 | 0.68795 | 0.68795 | 0.68795 | 2.3605 | 3.405 | 4.0893 | 4.4494 | 5.1698 | 5.8901 | 0.68478 | 1.8601 | 2.3331 | 2.3331 | 2.3331 | 2.3331 | 1.1978 | 1.5204 | 1.5204 | 1.5204 | 1.5204 | 1.5204
2020-08-17 05:00 | Winter | 1.8326 | 2.8179 | 4.264 | 4.264 | 4.264 | 4.264 | 0.69664 | 0.69664 | 0.69664 | 0.69664 | 0.69664 | 0.69664 | 2.3803 | 3.4336 | 4.1236 | 4.4868 | 5.2132 | 5.9395 | 0.68768 | 1.868 | 2.3429 | 2.3429 | 2.3429 | 2.3429 | 1.2366 | 1.5696 | 1.5696 | 1.5696 | 1.5696 | 1.5696
2020-08-17 06:00 | Winter | 1.8768 | 2.8858 | 4.3668 | 4.3668 | 4.3668 | 4.3668 | 0.70532 | 0.70532 | 0.70532 | 0.70532 | 0.70532 | 0.70532 | 2.4001 | 3.4621 | 4.1579 | 4.5241 | 5.2566 | 5.989 | 0.69058 | 1.8759 | 2.3528 | 2.3528 | 2.3528 | 2.3528 | 1.2754 | 1.6188 | 1.6188 | 1.6188 | 1.6188 | 1.6188
2020-08-17 07:00 | Winter | 1.921 | 2.9537 | 4.4696 | 4.4696 | 4.4696 | 4.4696 | 0.714 | 0.714 | 0.714 | 0.714 | 0.714 | 0.714 | 2.42 | 3.4907 | 4.1923 | 4.5615 | 5.3 | 6.0384 | 0.69348 | 1.8838 | 2.3627 | 2.3627 | 2.3627 | 2.3627 | 1.3141 | 1.668 | 1.668 | 1.668 | 1.668 | 1.668
2020-08-17 08:00 | Winter | 1.9651 | 3.0216 | 4.5723 | 4.5723 | 4.5723 | 4.5723 | 0.72269 | 0.72269 | 0.72269 | 0.72269 | 0.72269 | 0.72269 | 2.4398 | 3.5193 | 4.2266 | 4.5988 | 5.3433 | 6.0878 | 0.69638 | 1.8917 | 2.3726 | 2.3726 | 2.3726 | 2.3726 | 1.3529 | 1.7172 | 1.7172 | 1.7172 | 1.7172 | 1.7172
2020-08-17 09:00 | Winter | 2.0093 | 3.0896 | 4.6751 | 4.6751 | 4.6751 | 4.6751 | 0.73137 | 0.73137 | 0.73137 | 0.73137 | 0.73137 | 0.73137 | 2.4596 | 3.5479 | 4.2609 | 4.6362 | 5.3867 | 6.1373 | 0.69928 | 1.8995 | 2.3825 | 2.3825 | 2.3825 | 2.3825 | 1.3917 | 1.7664 | 1.7664 | 1.7664 | 1.7664 | 1.7664
2020-08-17 10:00 | Winter | 2.0535 | 3.1575 | 4.7779 | 4.7779 | 4.7779 | 4.7779 | 0.74005 | 0.74005 | 0.74005 | 0.74005 | 0.74005 | 0.74005 | 2.4794 | 3.5765 | 4.2952 | 4.6735 | 5.4301 | 6.1867 | 0.70218 | 1.9074 | 2.3923 | 2.3923 | 2.3923 | 2.3923 | 1.4304 | 1.8156 | 1.8156 | 1.8156 | 1.8156 | 1.8156
2020-08-17 11:00 | Winter | 2.1136 | 3.2499 | 4.9177 | 4.9177 | 4.9177 | 4.9177 | 0.74874 | 0.74874 | 0.74874 | 0.74874 | 0.74874 | 0.74874 | 2.4959 | 3.6002 | 4.3238 | 4.7046 | 5.4662 | 6.2279 | 0.75848 | 2.0603 | 2.5841 | 2.5841 | 2.5841 | 2.5841 | 1.5623 | 1.983 | 1.983 | 1.983 | 1.983 | 1.983
2020-08-17 12:00 | Winter | 2.2863 | 3.5155 | 5.3196 | 5.3196 | 5.3196 | 5.3196 | 0.92023 | 0.92023 | 0.92023 | 0.92023 | 0.92023 | 0.92023 | 2.5911 | 3.7377 | 4.4888 | 4.8842 | 5.6749 | 6.4656 | 0.81164 | 2.2047 | 2.7653 | 2.7653 | 2.7653 | 2.7653 | 1.5435 | 1.9591 | 1.9591 | 1.9591 | 1.9591 | 1.9591
2020-08-17 13:00 | Winter | 2.1529 | 3.3104 | 5.0093 | 5.0093 | 5.0093 | 5.0093 | 0.95739 | 0.95739 | 0.95739 | 0.95739 | 0.95739 | 0.95739 | 2.534 | 3.6552 | 4.3898 | 4.7764 | 5.5497 | 6.3229 | 0.82307 | 2.2358 | 2.8042 | 2.8042 | 2.8042 | 2.8042 | 1.5242 | 1.9346 | 1.9346 | 1.9346 | 1.9346 | 1.9346
2020-08-17 14:00 | Winter | 2.2673 | 3.4862 | 5.2753 | 5.2753 | 5.2753 | 5.2753 | 0.99454 | 0.99454 | 0.99454 | 0.99454 | 0.99454 | 0.99454 | 2.5721 | 3.7102 | 4.4558 | 4.8483 | 5.6331 | 6.418 | 0.7964 | 2.1633 | 2.7133 | 2.7133 | 2.7133 | 2.7133 | 1.4289 | 1.8137 | 1.8137 | 1.8137 | 1.8137 | 1.8137
2020-08-17 15:00 | Winter | 2.2101 | 3.3983 | 5.1423 | 5.1423 | 5.1423 | 5.1423 | 0.92595 | 0.92595 | 0.92595 | 0.92595 | 0.92595 | 0.92595 | 2.534 | 3.6552 | 4.3898 | 4.7764 | 5.5497 | 6.3229 | 0.81545 | 2.2151 | 2.7782 | 2.7782 | 2.7782 | 2.7782 | 1.3527 | 1.717 | 1.717 | 1.717 | 1.717 | 1.717
2020-08-17 16:00 | Winter | 2.1339 | 3.2811 | 4.9649 | 4.9649 | 4.9649 | 4.9649 | 0.90309 | 0.90309 | 0.90309 | 0.90309 | 0.90309 | 0.90309 | 2.4959 | 3.6002 | 4.3238 | 4.7046 | 5.4662 | 6.2279 | 0.78496 | 2.1323 | 2.6744 | 2.6744 | 2.6744 | 2.6744 | 1.2956 | 1.6444 | 1.6444 | 1.6444 | 1.6444 | 1.6444
2020-08-17 17:00 | Winter | 2.0577 | 3.1639 | 4.7876 | 4.7876 | 4.7876 | 4.7876 | 0.84021 | 0.84021 | 0.84021 | 0.84021 | 0.84021 | 0.84021 | 2.553 | 3.6827 | 4.4228 | 4.8123 | 5.5914 | 6.3705 | 0.80021 | 2.1737 | 2.7263 | 2.7263 | 2.7263 | 2.7263 | 1.2384 | 1.5719 | 1.5719 | 1.5719 | 1.5719 | 1.5719
2020-08-17 18:00 | Winter | 1.8481 | 2.8417 | 4.3 | 4.3 | 4.3 | 4.3 | 0.73447 | 0.73447 | 0.73447 | 0.73447 | 0.73447 | 0.73447 | 2.5911 | 3.7377 | 4.4888 | 4.8842 | 5.6749 | 6.4656 | 0.78115 | 2.1219 | 2.6614 | 2.6614 | 2.6614 | 2.6614 | 0.90712 | 1.1514 | 1.1514 | 1.1514 | 1.1514 | 1.1514
2020-08-17 19:00 | Winter | 1.2194 | 1.8749 | 2.8371 | 2.8371 | 2.8371 | 2.8371 | 0.65445 | 0.65445 | 0.65445 | 0.65445 | 0.65445 | 0.65445 | 2.4122 | 3.4796 | 4.1789 | 4.5469 | 5.283 | 6.0191 | 0.75067 | 2.0391 | 2.5575 | 2.5575 | 2.5575 | 2.5575 | 0.66684 | 0.84641 | 0.84641 | 0.84641 | 0.84641 | 0.84641
2020-08-17 20:00 | Winter | 1.1432 | 1.7577 | 2.6598 | 2.6598 | 2.6598 | 2.6598 | 0.51442 | 0.51442 | 0.51442 | 0.51442 | 0.51442 | 0.51442 | 2.3244 | 3.3529 | 4.0267 | 4.3814 | 5.0907 | 5.8 | 0.71256 | 1.9356 | 2.4277 | 2.4277 | 2.4277 | 2.4277 | 0.60968 | 0.77386 | 0.77386 | 0.77386 | 0.77386 | 0.77386
2020-08-17 21:00 | Winter | 1.0669 | 1.6405 | 2.4825 | 2.4825 | 2.4825 | 2.4825 | 0.50298 | 0.50298 | 0.50298 | 0.50298 | 0.50298 | 0.50298 | 2.1529 | 3.1056 | 3.7297 | 4.0582 | 4.7151 | 5.3721 | 0.69732 | 1.8942 | 2.3758 | 2.3758 | 2.3758 | 2.3758 | 0.57158 | 0.72549 | 0.72549 | 0.72549 | 0.72549 | 0.72549
2020-08-17 22:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.49727 | 0.49727 | 0.49727 | 0.49727 | 0.49727 | 0.49727 | 2.0005 | 2.8857 | 3.4656 | 3.7709 | 4.3813 | 4.9918 | 0.62873 | 1.7079 | 2.1421 | 2.1421 | 2.1421 | 2.1421 | 0.49537 | 0.62876 | 0.62876 | 0.62876 | 0.62876 | 0.62876
2020-08-17 23:00 | Winter | 1.0165 | 1.563 | 2.3652 | 2.3652 | 2.3652 | 2.3652 | 0.48584 | 0.48584 | 0.48584 | 0.48584 | 0.48584 | 0.48584 | 1.8862 | 2.7208 | 3.2676 | 3.5554 | 4.131 | 4.7066 | 0.65541 | 1.7803 | 2.233 | 2.233 | 2.233 | 2.233 | 0.45209 | 0.57382 | 0.57382 | 0.57382 | 0.57382 | 0.57382
2020-08-18 | Winter | 1.0288 | 1.582 | 2.3938 | 2.3938 | 2.3938 | 2.3938 | 0.49155 | 0.49155 | 0.49155 | 0.49155 | 0.49155 | 0.49155 | 1.6579 | 2.3914 | 2.872 | 3.125 | 3.6309 | 4.1368 | 0.60968 | 1.6561 | 2.0772 | 2.0772 | 2.0772 | 2.0772 | 0.45726 | 0.58039 | 0.58039 | 0.58039 | 0.58039 | 0.58039
2020-08-18 01:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.60587 | 1.6458 | 2.0642 | 2.0642 | 2.0642 | 2.0642 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-08-18 02:00 | Winter | 1.1813 | 1.8163 | 2.7485 | 2.7485 | 2.7485 | 2.7485 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 1.6004 | 2.3086 | 2.7725 | 3.0167 | 3.5051 | 3.9934 | 0.57539 | 1.563 | 1.9603 | 1.9603 | 1.9603 | 1.9603 | 0.49537 | 0.62876 | 0.62876 | 0.62876 | 0.62876 | 0.62876
2020-08-18 03:00 | Winter | 1.2003 | 1.8456 | 2.7928 | 2.7928 | 2.7928 | 2.7928 | 0.45425 | 0.45425 | 0.45425 | 0.45425 | 0.45425 | 0.45425 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.59444 | 1.6147 | 2.0253 | 2.0253 | 2.0253 | 2.0253 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-08-18 04:00 | Winter | 1.2537 | 1.9276 | 2.9169 | 2.9169 | 2.9169 | 2.9169 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 1.6666 | 2.404 | 2.8872 | 3.1415 | 3.65 | 4.1586 | 0.60206 | 1.6354 | 2.0512 | 2.0512 | 2.0512 | 2.0512 | 0.53269 | 0.67613 | 0.67613 | 0.67613 | 0.67613 | 0.67613
2020-08-18 05:00 | Winter | 1.3527 | 2.08 | 3.1474 | 3.1474 | 3.1474 | 3.1474 | 0.65731 | 0.65731 | 0.65731 | 0.65731 | 0.65731 | 0.65731 | 1.836 | 2.6484 | 3.1806 | 3.4607 | 4.021 | 4.5812 | 0.67827 | 1.8425 | 2.3109 | 2.3109 | 2.3109 | 2.3109 | 0.8124 | 1.0312 | 1.0312 | 1.0312 | 1.0312 | 1.0312
2020-08-18 06:00 | Winter | 1.6616 | 2.5549 | 3.866 | 3.866 | 3.866 | 3.866 | 0.71733 | 0.71733 | 0.71733 | 0.71733 | 0.71733 | 0.71733 | 2.0196 | 2.9132 | 3.4986 | 3.8068 | 4.4231 | 5.0393 | 0.78877 | 2.1426 | 2.6874 | 2.6874 | 2.6874 | 2.6874 | 0.93358 | 1.185 | 1.185 | 1.185 | 1.185 | 1.185
2020-08-18 07:00 | Winter | 2.0958 | 3.2225 | 4.8763 | 4.8763 | 4.8763 | 4.8763 | 0.84446 | 0.84446 | 0.84446 | 0.84446 | 0.84446 | 0.84446 | 2.4387 | 3.5178 | 4.2248 | 4.5969 | 5.3411 | 6.0852 | 0.88785 | 2.4118 | 3.0249 | 3.0249 | 3.0249 | 3.0249 | 1.3146 | 1.6686 | 1.6686 | 1.6686 | 1.6686 | 1.6686
2020-08-18 08:00 | Winter | 2.3054 | 3.5448 | 5.3639 | 5.3639 | 5.3639 | 5.3639 | 0.89451 | 0.89451 | 0.89451 | 0.89451 | 0.89451 | 0.89451 | 2.5911 | 3.7377 | 4.4888 | 4.8842 | 5.6749 | 6.4656 | 0.9069 | 2.4635 | 3.0898 | 3.0898 | 3.0898 | 3.0898 | 1.448 | 1.8379 | 1.8379 | 1.8379 | 1.8379 | 1.8379
2020-08-18 09:00 | Winter | 2.3054 | 3.5448 | 5.3639 | 5.3639 | 5.3639 | 5.3639 | 0.98025 | 0.98025 | 0.98025 | 0.98025 | 0.98025 | 0.98025 | 2.6483 | 3.8201 | 4.5878 | 4.9919 | 5.8 | 6.6082 | 0.85355 | 2.3186 | 2.9081 | 2.9081 | 2.9081 | 2.9081 | 1.5242 | 1.9346 | 1.9346 | 1.9346 | 1.9346 | 1.9346
2020-08-18 10:00 | Winter | 2.2291 | 3.4276 | 5.1866 | 5.1866 | 5.1866 | 5.1866 | 0.94881 | 0.94881 | 0.94881 | 0.94881 | 0.94881 | 0.94881 | 2.5915 | 3.7382 | 4.4895 | 4.8849 | 5.6757 | 6.4665 | 0.84593 | 2.2979 | 2.8821 | 2.8821 | 2.8821 | 2.8821 | 1.5242 | 1.9346 | 1.9346 | 1.9346 | 1.9346 | 1.9346
2020-08-18 11:00 | Winter | 2.2101 | 3.3983 | 5.1423 | 5.1423 | 5.1423 | 5.1423 | 0.95739 | 0.95739 | 0.95739 | 0.95739 | 0.95739 | 0.95739 | 2.6483 | 3.8201 | 4.5878 | 4.9919 | 5.8 | 6.6082 | 0.78115 | 2.1219 | 2.6614 | 2.6614 | 2.6614 | 2.6614 | 1.5433 | 1.9588 | 1.9588 | 1.9588 | 1.9588 | 1.9588
2020-08-18 12:00 | Winter | 2.2482 | 3.4569 | 5.2309 | 5.2309 | 5.2309 | 5.2309 | 0.9088 | 0.9088 | 0.9088 | 0.9088 | 0.9088 | 0.9088 | 2.6483 | 3.8201 | 4.5878 | 4.9919 | 5.8 | 6.6082 | 0.76591 | 2.0805 | 2.6095 | 2.6095 | 2.6095 | 2.6095 | 1.5052 | 1.9105 | 1.9105 | 1.9105 | 1.9105 | 1.9105
2020-08-18 13:00 | Winter | 2.2291 | 3.4276 | 5.1866 | 5.1866 | 5.1866 | 5.1866 | 0.94881 | 0.94881 | 0.94881 | 0.94881 | 0.94881 | 0.94881 | 2.6483 | 3.8201 | 4.5878 | 4.9919 | 5.8 | 6.6082 | 0.83069 | 2.2565 | 2.8302 | 2.8302 | 2.8302 | 2.8302 | 1.4289 | 1.8137 | 1.8137 | 1.8137 | 1.8137 | 1.8137
2020-08-18 14:00 | Winter | 2.2101 | 3.3983 | 5.1423 | 5.1423 | 5.1423 | 5.1423 | 0.90595 | 0.90595 | 0.90595 | 0.90595 | 0.90595 | 0.90595 | 2.6102 | 3.7651 | 4.5218 | 4.9201 | 5.7166 | 6.5131 | 0.79258 | 2.153 | 2.7003 | 2.7003 | 2.7003 | 2.7003 | 1.3908 | 1.7654 | 1.7654 | 1.7654 | 1.7654 | 1.7654
2020-08-18 15:00 | Winter | 2.172 | 3.3397 | 5.0536 | 5.0536 | 5.0536 | 5.0536 | 0.87451 | 0.87451 | 0.87451 | 0.87451 | 0.87451 | 0.87451 | 2.6102 | 3.7651 | 4.5218 | 4.9201 | 5.7166 | 6.5131 | 0.76972 | 2.0909 | 2.6225 | 2.6225 | 2.6225 | 2.6225 | 1.3527 | 1.717 | 1.717 | 1.717 | 1.717 | 1.717
2020-08-18 16:00 | Winter | 2.1148 | 3.2518 | 4.9206 | 4.9206 | 4.9206 | 4.9206 | 0.87451 | 0.87451 | 0.87451 | 0.87451 | 0.87451 | 0.87451 | 2.534 | 3.6552 | 4.3898 | 4.7764 | 5.5497 | 6.3229 | 0.76591 | 2.0805 | 2.6095 | 2.6095 | 2.6095 | 2.6095 | 1.2241 | 1.5537 | 1.5537 | 1.5537 | 1.5537 | 1.5537
2020-08-18 17:00 | Winter | 2.0196 | 3.1053 | 4.699 | 4.699 | 4.699 | 4.699 | 0.82021 | 0.82021 | 0.82021 | 0.82021 | 0.82021 | 0.82021 | 2.553 | 3.6827 | 4.4228 | 4.8123 | 5.5914 | 6.3705 | 0.74305 | 2.0184 | 2.5316 | 2.5316 | 2.5316 | 2.5316 | 1.2194 | 1.5477 | 1.5477 | 1.5477 | 1.5477 | 1.5477
2020-08-18 18:00 | Winter | 1.6824 | 2.5869 | 3.9145 | 3.9145 | 3.9145 | 3.9145 | 0.70589 | 0.70589 | 0.70589 | 0.70589 | 0.70589 | 0.70589 | 2.4959 | 3.6002 | 4.3238 | 4.7046 | 5.4662 | 6.2279 | 0.74686 | 2.0288 | 2.5446 | 2.5446 | 2.5446 | 2.5446 | 0.93022 | 1.1807 | 1.1807 | 1.1807 | 1.1807 | 1.1807
2020-08-18 19:00 | Winter | 1.1857 | 1.8232 | 2.7588 | 2.7588 | 2.7588 | 2.7588 | 0.58015 | 0.58015 | 0.58015 | 0.58015 | 0.58015 | 0.58015 | 2.4237 | 3.4961 | 4.1987 | 4.5685 | 5.3081 | 6.0477 | 0.70494 | 1.9149 | 2.4018 | 2.4018 | 2.4018 | 2.4018 | 0.68589 | 0.87059 | 0.87059 | 0.87059 | 0.87059 | 0.87059
2020-08-18 20:00 | Winter | 1.105 | 1.6991 | 2.5711 | 2.5711 | 2.5711 | 2.5711 | 0.50298 | 0.50298 | 0.50298 | 0.50298 | 0.50298 | 0.50298 | 2.3505 | 3.3905 | 4.0719 | 4.4305 | 5.1478 | 5.865 | 0.72781 | 1.977 | 2.4796 | 2.4796 | 2.4796 | 2.4796 | 0.61046 | 0.77485 | 0.77485 | 0.77485 | 0.77485 | 0.77485
2020-08-18 21:00 | Winter | 1.0288 | 1.582 | 2.3938 | 2.3938 | 2.3938 | 2.3938 | 0.39604 | 0.39604 | 0.39604 | 0.39604 | 0.39604 | 0.39604 | 2.2291 | 3.2155 | 3.8617 | 4.2018 | 4.8821 | 5.5623 | 0.70113 | 1.9046 | 2.3888 | 2.3888 | 2.3888 | 2.3888 | 0.57158 | 0.72549 | 0.72549 | 0.72549 | 0.72549 | 0.72549
2020-08-18 22:00 | Winter | 1.0288 | 1.582 | 2.3938 | 2.3938 | 2.3938 | 2.3938 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 1.9994 | 2.884 | 3.4636 | 3.7687 | 4.3788 | 4.9889 | 0.68589 | 1.8632 | 2.3368 | 2.3368 | 2.3368 | 2.3368 | 0.49537 | 0.62876 | 0.62876 | 0.62876 | 0.62876 | 0.62876
2020-08-18 23:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 1.7909 | 2.5834 | 3.1026 | 3.3758 | 3.9223 | 4.4688 | 0.57157 | 1.5526 | 1.9474 | 1.9474 | 1.9474 | 1.9474 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-08-19 | Winter | 1.043 | 1.6037 | 2.4267 | 2.4267 | 2.4267 | 2.4267 | 0.43439 | 0.43439 | 0.43439 | 0.43439 | 0.43439 | 0.43439 | 1.6957 | 2.446 | 2.9375 | 3.1963 | 3.7137 | 4.2311 | 0.51442 | 1.3974 | 1.7526 | 1.7526 | 1.7526 | 1.7526 | 0.43848 | 0.55656 | 0.55656 | 0.55656 | 0.55656 | 0.55656
2020-08-19 01:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 1.6008 | 2.3091 | 2.7731 | 3.0174 | 3.5058 | 3.9943 | 0.5068 | 1.3767 | 1.7267 | 1.7267 | 1.7267 | 1.7267 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-08-19 02:00 | Winter | 1.105 | 1.6991 | 2.5711 | 2.5711 | 2.5711 | 2.5711 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 1.5242 | 2.1986 | 2.6405 | 2.873 | 3.3382 | 3.8033 | 0.52966 | 1.4388 | 1.8046 | 1.8046 | 1.8046 | 1.8046 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-08-19 03:00 | Winter | 1.1813 | 1.8163 | 2.7485 | 2.7485 | 2.7485 | 2.7485 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 1.5615 | 2.2524 | 2.7051 | 2.9433 | 3.4198 | 3.8963 | 0.53347 | 1.4491 | 1.8175 | 1.8175 | 1.8175 | 1.8175 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-08-19 04:00 | Winter | 1.2194 | 1.8749 | 2.8371 | 2.8371 | 2.8371 | 2.8371 | 0.50584 | 0.50584 | 0.50584 | 0.50584 | 0.50584 | 0.50584 | 1.6105 | 2.3232 | 2.79 | 3.0358 | 3.5272 | 4.0187 | 0.57157 | 1.5526 | 1.9474 | 1.9474 | 1.9474 | 1.9474 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-08-19 05:00 | Winter | 1.4857 | 2.2844 | 3.4568 | 3.4568 | 3.4568 | 3.4568 | 0.59721 | 0.59721 | 0.59721 | 0.59721 | 0.59721 | 0.59721 | 1.8216 | 2.6276 | 3.1557 | 3.4336 | 3.9895 | 4.5454 | 0.64779 | 1.7596 | 2.207 | 2.207 | 2.207 | 2.207 | 0.77273 | 0.98081 | 0.98081 | 0.98081 | 0.98081 | 0.98081
2020-08-19 06:00 | Winter | 1.758 | 2.7031 | 4.0904 | 4.0904 | 4.0904 | 4.0904 | 0.69446 | 0.69446 | 0.69446 | 0.69446 | 0.69446 | 0.69446 | 2.0574 | 2.9677 | 3.5642 | 3.8781 | 4.5059 | 5.1337 | 0.70494 | 1.9149 | 2.4018 | 2.4018 | 2.4018 | 2.4018 | 0.97168 | 1.2333 | 1.2333 | 1.2333 | 1.2333 | 1.2333
2020-08-19 07:00 | Winter | 1.9792 | 3.0432 | 4.605 | 4.605 | 4.605 | 4.605 | 0.8565 | 0.8565 | 0.8565 | 0.8565 | 0.8565 | 0.8565 | 2.3244 | 3.3529 | 4.0267 | 4.3814 | 5.0907 | 5.8 | 0.83831 | 2.2772 | 2.8561 | 2.8561 | 2.8561 | 2.8561 | 1.2765 | 1.6203 | 1.6203 | 1.6203 | 1.6203 | 1.6203
2020-08-19 08:00 | Winter | 2.2673 | 3.4862 | 5.2753 | 5.2753 | 5.2753 | 5.2753 | 0.94671 | 0.94671 | 0.94671 | 0.94671 | 0.94671 | 0.94671 | 2.553 | 3.6827 | 4.4228 | 4.8123 | 5.5914 | 6.3705 | 0.88023 | 2.3911 | 2.9989 | 2.9989 | 2.9989 | 2.9989 | 1.5052 | 1.9105 | 1.9105 | 1.9105 | 1.9105 | 1.9105
2020-08-19 09:00 | Winter | 2.3054 | 3.5448 | 5.3639 | 5.3639 | 5.3639 | 5.3639 | 0.9974 | 0.9974 | 0.9974 | 0.9974 | 0.9974 | 0.9974 | 2.7817 | 4.0125 | 4.8189 | 5.2433 | 6.0921 | 6.941 | 0.87261 | 2.3704 | 2.973 | 2.973 | 2.973 | 2.973 | 1.5433 | 1.9588 | 1.9588 | 1.9588 | 1.9588 | 1.9588
2020-08-19 10:00 | Winter | 2.2482 | 3.4569 | 5.2309 | 5.2309 | 5.2309 | 5.2309 | 1.0203 | 1.0203 | 1.0203 | 1.0203 | 1.0203 | 1.0203 | 2.7436 | 3.9575 | 4.7529 | 5.1715 | 6.0087 | 6.8459 | 0.83069 | 2.2565 | 2.8302 | 2.8302 | 2.8302 | 2.8302 | 1.5623 | 1.983 | 1.983 | 1.983 | 1.983 | 1.983
2020-08-19 11:00 | Winter | 2.2101 | 3.3983 | 5.1423 | 5.1423 | 5.1423 | 5.1423 | 0.98311 | 0.98311 | 0.98311 | 0.98311 | 0.98311 | 0.98311 | 2.7055 | 3.9026 | 4.6869 | 5.0996 | 5.9252 | 6.7508 | 0.82307 | 2.2358 | 2.8042 | 2.8042 | 2.8042 | 2.8042 | 1.5433 | 1.9588 | 1.9588 | 1.9588 | 1.9588 | 1.9588
2020-08-19 12:00 | Winter | 2.2863 | 3.5155 | 5.3196 | 5.3196 | 5.3196 | 5.3196 | 1.0145 | 1.0145 | 1.0145 | 1.0145 | 1.0145 | 1.0145 | 2.7436 | 3.9575 | 4.7529 | 5.1715 | 6.0087 | 6.8459 | 0.76972 | 2.0909 | 2.6225 | 2.6225 | 2.6225 | 2.6225 | 1.5242 | 1.9346 | 1.9346 | 1.9346 | 1.9346 | 1.9346
2020-08-19 13:00 | Winter | 2.2474 | 3.4557 | 5.2291 | 5.2291 | 5.2291 | 5.2291 | 0.99454 | 0.99454 | 0.99454 | 0.99454 | 0.99454 | 0.99454 | 2.8007 | 4.04 | 4.8519 | 5.2792 | 6.1339 | 6.9885 | 0.80783 | 2.1944 | 2.7523 | 2.7523 | 2.7523 | 2.7523 | 1.5433 | 1.9588 | 1.9588 | 1.9588 | 1.9588 | 1.9588
2020-08-19 14:00 | Winter | 2.3054 | 3.5448 | 5.3639 | 5.3639 | 5.3639 | 5.3639 | 1.0288 | 1.0288 | 1.0288 | 1.0288 | 1.0288 | 1.0288 | 2.8007 | 4.04 | 4.8519 | 5.2792 | 6.1339 | 6.9885 | 0.83069 | 2.2565 | 2.8302 | 2.8302 | 2.8302 | 2.8302 | 1.424 | 1.8075 | 1.8075 | 1.8075 | 1.8075 | 1.8075
2020-08-19 15:00 | Winter | 2.2101 | 3.3983 | 5.1423 | 5.1423 | 5.1423 | 5.1423 | 0.96596 | 0.96596 | 0.96596 | 0.96596 | 0.96596 | 0.96596 | 2.8007 | 4.04 | 4.8519 | 5.2792 | 6.1339 | 6.9885 | 0.80402 | 2.184 | 2.7393 | 2.7393 | 2.7393 | 2.7393 | 1.3527 | 1.717 | 1.717 | 1.717 | 1.717 | 1.717
2020-08-19 16:00 | Winter | 2.191 | 3.369 | 5.0979 | 5.0979 | 5.0979 | 5.0979 | 0.95739 | 0.95739 | 0.95739 | 0.95739 | 0.95739 | 0.95739 | 2.8007 | 4.04 | 4.8519 | 5.2792 | 6.1339 | 6.9885 | 0.85355 | 2.3186 | 2.9081 | 2.9081 | 2.9081 | 2.9081 | 1.3908 | 1.7654 | 1.7654 | 1.7654 | 1.7654 | 1.7654
2020-08-19 17:00 | Winter | 2.0958 | 3.2225 | 4.8763 | 4.8763 | 4.8763 | 4.8763 | 0.91738 | 0.91738 | 0.91738 | 0.91738 | 0.91738 | 0.91738 | 2.8769 | 4.1499 | 4.9839 | 5.4229 | 6.3008 | 7.1787 | 0.83069 | 2.2565 | 2.8302 | 2.8302 | 2.8302 | 2.8302 | 1.3527 | 1.717 | 1.717 | 1.717 | 1.717 | 1.717
2020-08-19 18:00 | Winter | 1.7867 | 2.7472 | 4.1571 | 4.1571 | 4.1571 | 4.1571 | 0.8094 | 0.8094 | 0.8094 | 0.8094 | 0.8094 | 0.8094 | 2.8388 | 4.0949 | 4.9179 | 5.351 | 6.2173 | 7.0836 | 0.8345 | 2.2668 | 2.8432 | 2.8432 | 2.8432 | 2.8432 | 0.99517 | 1.2631 | 1.2631 | 1.2631 | 1.2631 | 1.2631
2020-08-19 19:00 | Winter | 1.2275 | 1.8874 | 2.856 | 2.856 | 2.856 | 2.856 | 0.64939 | 0.64939 | 0.64939 | 0.64939 | 0.64939 | 0.64939 | 2.7604 | 3.9819 | 4.7821 | 5.2033 | 6.0456 | 6.888 | 0.76972 | 2.0909 | 2.6225 | 2.6225 | 2.6225 | 2.6225 | 0.71446 | 0.90684 | 0.90684 | 0.90684 | 0.90684 | 0.90684
2020-08-19 20:00 | Winter | 1.105 | 1.6991 | 2.5711 | 2.5711 | 2.5711 | 2.5711 | 0.54871 | 0.54871 | 0.54871 | 0.54871 | 0.54871 | 0.54871 | 2.5721 | 3.7102 | 4.4558 | 4.8483 | 5.6331 | 6.418 | 0.70875 | 1.9253 | 2.4147 | 2.4147 | 2.4147 | 2.4147 | 0.64789 | 0.82235 | 0.82235 | 0.82235 | 0.82235 | 0.82235
2020-08-19 21:00 | Winter | 1.0669 | 1.6405 | 2.4825 | 2.4825 | 2.4825 | 2.4825 | 0.48312 | 0.48312 | 0.48312 | 0.48312 | 0.48312 | 0.48312 | 2.3448 | 3.3823 | 4.0621 | 4.4198 | 5.1354 | 5.8509 | 0.72781 | 1.977 | 2.4796 | 2.4796 | 2.4796 | 2.4796 | 0.55458 | 0.70392 | 0.70392 | 0.70392 | 0.70392 | 0.70392
2020-08-19 22:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.46869 | 0.46869 | 0.46869 | 0.46869 | 0.46869 | 0.46869 | 2.0767 | 2.9956 | 3.5977 | 3.9145 | 4.5482 | 5.182 | 0.63635 | 1.7286 | 2.1681 | 2.1681 | 2.1681 | 2.1681 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-08-19 23:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.48869 | 0.48869 | 0.48869 | 0.48869 | 0.48869 | 0.48869 | 1.8598 | 2.6826 | 3.2218 | 3.5055 | 4.073 | 4.6405 | 0.60587 | 1.6458 | 2.0642 | 2.0642 | 2.0642 | 2.0642 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-08-20 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.50584 | 0.50584 | 0.50584 | 0.50584 | 0.50584 | 0.50584 | 1.7074 | 2.4629 | 2.9578 | 3.2183 | 3.7393 | 4.2604 | 0.55633 | 1.5112 | 1.8954 | 1.8954 | 1.8954 | 1.8954 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-08-20 01:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 1.6957 | 2.446 | 2.9375 | 3.1963 | 3.7137 | 4.2311 | 0.54109 | 1.4698 | 1.8435 | 1.8435 | 1.8435 | 1.8435 | 0.49525 | 0.62861 | 0.62861 | 0.62861 | 0.62861 | 0.62861
2020-08-20 02:00 | Winter | 1.1432 | 1.7577 | 2.6598 | 2.6598 | 2.6598 | 2.6598 | 0.48869 | 0.48869 | 0.48869 | 0.48869 | 0.48869 | 0.48869 | 1.6529 | 2.3842 | 2.8634 | 3.1156 | 3.6199 | 4.1243 | 0.53728 | 1.4595 | 1.8305 | 1.8305 | 1.8305 | 1.8305 | 0.49537 | 0.62876 | 0.62876 | 0.62876 | 0.62876 | 0.62876
2020-08-20 03:00 | Winter | 1.1432 | 1.7577 | 2.6598 | 2.6598 | 2.6598 | 2.6598 | 0.50013 | 0.50013 | 0.50013 | 0.50013 | 0.50013 | 0.50013 | 1.6576 | 2.391 | 2.8715 | 3.1244 | 3.6302 | 4.1361 | 0.53347 | 1.4491 | 1.8175 | 1.8175 | 1.8175 | 1.8175 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-08-20 04:00 | Winter | 1.1813 | 1.8163 | 2.7485 | 2.7485 | 2.7485 | 2.7485 | 0.5087 | 0.5087 | 0.5087 | 0.5087 | 0.5087 | 0.5087 | 1.6576 | 2.391 | 2.8715 | 3.1244 | 3.6302 | 4.1361 | 0.51061 | 1.387 | 1.7396 | 1.7396 | 1.7396 | 1.7396 | 0.55252 | 0.70131 | 0.70131 | 0.70131 | 0.70131 | 0.70131
2020-08-20 05:00 | Winter | 1.5045 | 2.3134 | 3.5006 | 3.5006 | 3.5006 | 3.5006 | 0.63159 | 0.63159 | 0.63159 | 0.63159 | 0.63159 | 0.63159 | 1.8088 | 2.6092 | 3.1336 | 3.4096 | 3.9615 | 4.5135 | 0.65922 | 1.7907 | 2.246 | 2.246 | 2.246 | 2.246 | 0.78045 | 0.9906 | 0.9906 | 0.9906 | 0.9906 | 0.9906
2020-08-20 06:00 | Winter | 1.77 | 2.7216 | 4.1183 | 4.1183 | 4.1183 | 4.1183 | 0.7459 | 0.7459 | 0.7459 | 0.7459 | 0.7459 | 0.7459 | 2.172 | 3.133 | 3.7627 | 4.0941 | 4.7569 | 5.4197 | 0.70494 | 1.9149 | 2.4018 | 2.4018 | 2.4018 | 2.4018 | 0.97168 | 1.2333 | 1.2333 | 1.2333 | 1.2333 | 1.2333
2020-08-20 07:00 | Winter | 2.0386 | 3.1346 | 4.7433 | 4.7433 | 4.7433 | 4.7433 | 0.88877 | 0.88877 | 0.88877 | 0.88877 | 0.88877 | 0.88877 | 2.5681 | 3.7044 | 4.4488 | 4.8407 | 5.6243 | 6.408 | 0.84212 | 2.2875 | 2.8691 | 2.8691 | 2.8691 | 2.8691 | 1.3337 | 1.6928 | 1.6928 | 1.6928 | 1.6928 | 1.6928
2020-08-20 08:00 | Winter | 2.2673 | 3.4862 | 5.2753 | 5.2753 | 5.2753 | 5.2753 | 0.9974 | 0.9974 | 0.9974 | 0.9974 | 0.9974 | 0.9974 | 2.7245 | 3.93 | 4.7199 | 5.1356 | 5.967 | 6.7984 | 0.88023 | 2.3911 | 2.9989 | 2.9989 | 2.9989 | 2.9989 | 1.5623 | 1.983 | 1.983 | 1.983 | 1.983 | 1.983
2020-08-20 09:00 | Winter | 2.2863 | 3.5155 | 5.3196 | 5.3196 | 5.3196 | 5.3196 | 1.0145 | 1.0145 | 1.0145 | 1.0145 | 1.0145 | 1.0145 | 2.7436 | 3.9575 | 4.7529 | 5.1715 | 6.0087 | 6.8459 | 0.81545 | 2.2151 | 2.7782 | 2.7782 | 2.7782 | 2.7782 | 1.5433 | 1.9588 | 1.9588 | 1.9588 | 1.9588 | 1.9588
2020-08-20 10:00 | Winter | 2.2673 | 3.4862 | 5.2753 | 5.2753 | 5.2753 | 5.2753 | 1.0174 | 1.0174 | 1.0174 | 1.0174 | 1.0174 | 1.0174 | 2.7245 | 3.93 | 4.7199 | 5.1356 | 5.967 | 6.7984 | 0.84974 | 2.3082 | 2.8951 | 2.8951 | 2.8951 | 2.8951 | 1.5814 | 2.0072 | 2.0072 | 2.0072 | 2.0072 | 2.0072
2020-08-20 11:00 | Winter | 2.2291 | 3.4276 | 5.1866 | 5.1866 | 5.1866 | 5.1866 | 1.0003 | 1.0003 | 1.0003 | 1.0003 | 1.0003 | 1.0003 | 2.7055 | 3.9026 | 4.6869 | 5.0996 | 5.9252 | 6.7508 | 0.80783 | 2.1944 | 2.7523 | 2.7523 | 2.7523 | 2.7523 | 1.5052 | 1.9105 | 1.9105 | 1.9105 | 1.9105 | 1.9105
2020-08-20 12:00 | Winter | 2.2101 | 3.3983 | 5.1423 | 5.1423 | 5.1423 | 5.1423 | 1.046 | 1.046 | 1.046 | 1.046 | 1.046 | 1.046 | 2.7626 | 3.985 | 4.7859 | 5.2074 | 6.0504 | 6.8934 | 0.75067 | 2.0391 | 2.5575 | 2.5575 | 2.5575 | 2.5575 | 1.5281 | 1.9395 | 1.9395 | 1.9395 | 1.9395 | 1.9395
2020-08-20 13:00 | Winter | 2.2673 | 3.4862 | 5.2753 | 5.2753 | 5.2753 | 5.2753 | 0.93738 | 0.93738 | 0.93738 | 0.93738 | 0.93738 | 0.93738 | 2.6864 | 3.8751 | 4.6539 | 5.0637 | 5.8835 | 6.7033 | 0.74686 | 2.0288 | 2.5446 | 2.5446 | 2.5446 | 2.5446 | 1.5814 | 2.0072 | 2.0072 | 2.0072 | 2.0072 | 2.0072
2020-08-20 14:00 | Winter | 2.2101 | 3.3983 | 5.1423 | 5.1423 | 5.1423 | 5.1423 | 0.93167 | 0.93167 | 0.93167 | 0.93167 | 0.93167 | 0.93167 | 2.6864 | 3.8751 | 4.6539 | 5.0637 | 5.8835 | 6.7033 | 0.75829 | 2.0598 | 2.5835 | 2.5835 | 2.5835 | 2.5835 | 1.4484 | 1.8384 | 1.8384 | 1.8384 | 1.8384 | 1.8384
2020-08-20 15:00 | Winter | 2.1148 | 3.2518 | 4.9206 | 4.9206 | 4.9206 | 4.9206 | 0.89563 | 0.89563 | 0.89563 | 0.89563 | 0.89563 | 0.89563 | 2.534 | 3.6552 | 4.3898 | 4.7764 | 5.5497 | 6.3229 | 0.79258 | 2.153 | 2.7003 | 2.7003 | 2.7003 | 2.7003 | 1.3718 | 1.7412 | 1.7412 | 1.7412 | 1.7412 | 1.7412
2020-08-20 16:00 | Winter | 2.1339 | 3.2811 | 4.9649 | 4.9649 | 4.9649 | 4.9649 | 0.92023 | 0.92023 | 0.92023 | 0.92023 | 0.92023 | 0.92023 | 2.553 | 3.6827 | 4.4228 | 4.8123 | 5.5914 | 6.3705 | 0.79258 | 2.153 | 2.7003 | 2.7003 | 2.7003 | 2.7003 | 1.3527 | 1.717 | 1.717 | 1.717 | 1.717 | 1.717
2020-08-20 17:00 | Winter | 2.0577 | 3.1639 | 4.7876 | 4.7876 | 4.7876 | 4.7876 | 0.9088 | 0.9088 | 0.9088 | 0.9088 | 0.9088 | 0.9088 | 2.6293 | 3.7926 | 4.5548 | 4.956 | 5.7583 | 6.5606 | 0.85736 | 2.3289 | 2.9211 | 2.9211 | 2.9211 | 2.9211 | 1.2765 | 1.6203 | 1.6203 | 1.6203 | 1.6203 | 1.6203
2020-08-20 18:00 | Winter | 1.6549 | 2.5446 | 3.8504 | 3.8504 | 3.8504 | 3.8504 | 0.77162 | 0.77162 | 0.77162 | 0.77162 | 0.77162 | 0.77162 | 2.7245 | 3.93 | 4.7199 | 5.1356 | 5.967 | 6.7984 | 0.86117 | 2.3393 | 2.934 | 2.934 | 2.934 | 2.934 | 0.99372 | 1.2613 | 1.2613 | 1.2613 | 1.2613 | 1.2613
2020-08-20 19:00 | Winter | 1.1813 | 1.8163 | 2.7485 | 2.7485 | 2.7485 | 2.7485 | 0.65745 | 0.65745 | 0.65745 | 0.65745 | 0.65745 | 0.65745 | 2.5921 | 3.739 | 4.4904 | 4.8859 | 5.6769 | 6.4678 | 0.7964 | 2.1633 | 2.7133 | 2.7133 | 2.7133 | 2.7133 | 0.78115 | 0.9915 | 0.9915 | 0.9915 | 0.9915 | 0.9915
2020-08-20 20:00 | Winter | 1.1813 | 1.8163 | 2.7485 | 2.7485 | 2.7485 | 2.7485 | 0.59158 | 0.59158 | 0.59158 | 0.59158 | 0.59158 | 0.59158 | 2.4006 | 3.4628 | 4.1588 | 4.525 | 5.2576 | 5.9902 | 0.75829 | 2.0598 | 2.5835 | 2.5835 | 2.5835 | 2.5835 | 0.68589 | 0.87059 | 0.87059 | 0.87059 | 0.87059 | 0.87059
2020-08-20 21:00 | Winter | 1.0288 | 1.582 | 2.3938 | 2.3938 | 2.3938 | 2.3938 | 0.55728 | 0.55728 | 0.55728 | 0.55728 | 0.55728 | 0.55728 | 2.2863 | 3.2979 | 3.9607 | 4.3096 | 5.0072 | 5.7049 | 0.724 | 1.9667 | 2.4667 | 2.4667 | 2.4667 | 2.4667 | 0.60968 | 0.77386 | 0.77386 | 0.77386 | 0.77386 | 0.77386
2020-08-20 22:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.52299 | 0.52299 | 0.52299 | 0.52299 | 0.52299 | 0.52299 | 2.0958 | 3.0231 | 3.6307 | 3.9504 | 4.59 | 5.2295 | 0.67446 | 1.8321 | 2.2979 | 2.2979 | 2.2979 | 2.2979 | 0.57158 | 0.72549 | 0.72549 | 0.72549 | 0.72549 | 0.72549
2020-08-20 23:00 | Winter | 1.0086 | 1.5508 | 2.3466 | 2.3466 | 2.3466 | 2.3466 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 1.9434 | 2.8032 | 3.3666 | 3.6631 | 4.2562 | 4.8492 | 0.60968 | 1.6561 | 2.0772 | 2.0772 | 2.0772 | 2.0772 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-08-21 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 1.7338 | 2.5009 | 3.0036 | 3.2681 | 3.7972 | 4.3262 | 0.56395 | 1.5319 | 1.9214 | 1.9214 | 1.9214 | 1.9214 | 0.49537 | 0.62876 | 0.62876 | 0.62876 | 0.62876 | 0.62876
2020-08-21 01:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.43439 | 0.43439 | 0.43439 | 0.43439 | 0.43439 | 0.43439 | 1.6957 | 2.446 | 2.9375 | 3.1963 | 3.7137 | 4.2311 | 0.56014 | 1.5216 | 1.9084 | 1.9084 | 1.9084 | 1.9084 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-08-21 02:00 | Winter | 1.1241 | 1.7284 | 2.6155 | 2.6155 | 2.6155 | 2.6155 | 0.45295 | 0.45295 | 0.45295 | 0.45295 | 0.45295 | 0.45295 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.53728 | 1.4595 | 1.8305 | 1.8305 | 1.8305 | 1.8305 | 0.43456 | 0.55158 | 0.55158 | 0.55158 | 0.55158 | 0.55158
2020-08-21 03:00 | Winter | 1.1432 | 1.7577 | 2.6598 | 2.6598 | 2.6598 | 2.6598 | 0.4544 | 0.4544 | 0.4544 | 0.4544 | 0.4544 | 0.4544 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.58682 | 1.594 | 1.9993 | 1.9993 | 1.9993 | 1.9993 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-08-21 04:00 | Winter | 1.1813 | 1.8163 | 2.7485 | 2.7485 | 2.7485 | 2.7485 | 0.49727 | 0.49727 | 0.49727 | 0.49727 | 0.49727 | 0.49727 | 1.6711 | 2.4105 | 2.895 | 3.1499 | 3.6599 | 4.1698 | 0.58682 | 1.594 | 1.9993 | 1.9993 | 1.9993 | 1.9993 | 0.54362 | 0.69001 | 0.69001 | 0.69001 | 0.69001 | 0.69001
2020-08-21 05:00 | Winter | 1.3674 | 2.1026 | 3.1816 | 3.1816 | 3.1816 | 3.1816 | 0.62301 | 0.62301 | 0.62301 | 0.62301 | 0.62301 | 0.62301 | 1.9145 | 2.7616 | 3.3166 | 3.6087 | 4.1929 | 4.7771 | 0.70113 | 1.9046 | 2.3888 | 2.3888 | 2.3888 | 2.3888 | 0.74305 | 0.94314 | 0.94314 | 0.94314 | 0.94314 | 0.94314
2020-08-21 06:00 | Winter | 1.7591 | 2.7049 | 4.093 | 4.093 | 4.093 | 4.093 | 0.74019 | 0.74019 | 0.74019 | 0.74019 | 0.74019 | 0.74019 | 2.0908 | 3.016 | 3.6221 | 3.9411 | 4.5791 | 5.2172 | 0.72781 | 1.977 | 2.4796 | 2.4796 | 2.4796 | 2.4796 | 1.006 | 1.2769 | 1.2769 | 1.2769 | 1.2769 | 1.2769
2020-08-21 07:00 | Winter | 2.0386 | 3.1346 | 4.7433 | 4.7433 | 4.7433 | 4.7433 | 0.84307 | 0.84307 | 0.84307 | 0.84307 | 0.84307 | 0.84307 | 2.4578 | 3.5453 | 4.2578 | 4.6328 | 5.3828 | 6.1328 | 0.81545 | 2.2151 | 2.7782 | 2.7782 | 2.7782 | 2.7782 | 1.3337 | 1.6928 | 1.6928 | 1.6928 | 1.6928 | 1.6928
2020-08-21 08:00 | Winter | 2.3054 | 3.5448 | 5.3639 | 5.3639 | 5.3639 | 5.3639 | 0.99454 | 0.99454 | 0.99454 | 0.99454 | 0.99454 | 0.99454 | 2.6293 | 3.7926 | 4.5548 | 4.956 | 5.7583 | 6.5606 | 0.89166 | 2.4221 | 3.0379 | 3.0379 | 3.0379 | 3.0379 | 1.467 | 1.8621 | 1.8621 | 1.8621 | 1.8621 | 1.8621
2020-08-21 09:00 | Winter | 2.3435 | 3.6034 | 5.4526 | 5.4526 | 5.4526 | 5.4526 | 1.0688 | 1.0688 | 1.0688 | 1.0688 | 1.0688 | 1.0688 | 2.7817 | 4.0125 | 4.8189 | 5.2433 | 6.0921 | 6.941 | 0.86498 | 2.3496 | 2.947 | 2.947 | 2.947 | 2.947 | 1.5814 | 2.0072 | 2.0072 | 2.0072 | 2.0072 | 2.0072
2020-08-21 10:00 | Winter | 2.3244 | 3.5741 | 5.4082 | 5.4082 | 5.4082 | 5.4082 | 1.0088 | 1.0088 | 1.0088 | 1.0088 | 1.0088 | 1.0088 | 2.8388 | 4.0949 | 4.9179 | 5.351 | 6.2173 | 7.0836 | 0.8345 | 2.2668 | 2.8432 | 2.8432 | 2.8432 | 2.8432 | 1.5814 | 2.0072 | 2.0072 | 2.0072 | 2.0072 | 2.0072
2020-08-21 11:00 | Winter | 2.2291 | 3.4276 | 5.1866 | 5.1866 | 5.1866 | 5.1866 | 1.0403 | 1.0403 | 1.0403 | 1.0403 | 1.0403 | 1.0403 | 2.8388 | 4.0949 | 4.9179 | 5.351 | 6.2173 | 7.0836 | 0.85736 | 2.3289 | 2.9211 | 2.9211 | 2.9211 | 2.9211 | 1.6004 | 2.0314 | 2.0314 | 2.0314 | 2.0314 | 2.0314
2020-08-21 12:00 | Winter | 2.2101 | 3.3983 | 5.1423 | 5.1423 | 5.1423 | 5.1423 | 1.0031 | 1.0031 | 1.0031 | 1.0031 | 1.0031 | 1.0031 | 2.7436 | 3.9575 | 4.7529 | 5.1715 | 6.0087 | 6.8459 | 0.80021 | 2.1737 | 2.7263 | 2.7263 | 2.7263 | 2.7263 | 1.5814 | 2.0072 | 2.0072 | 2.0072 | 2.0072 | 2.0072
2020-08-21 13:00 | Winter | 2.191 | 3.369 | 5.0979 | 5.0979 | 5.0979 | 5.0979 | 0.96025 | 0.96025 | 0.96025 | 0.96025 | 0.96025 | 0.96025 | 2.6483 | 3.8201 | 4.5878 | 4.9919 | 5.8 | 6.6082 | 0.78877 | 2.1426 | 2.6874 | 2.6874 | 2.6874 | 2.6874 | 1.5814 | 2.0072 | 2.0072 | 2.0072 | 2.0072 | 2.0072
2020-08-21 14:00 | Winter | 2.2291 | 3.4276 | 5.1866 | 5.1866 | 5.1866 | 5.1866 | 0.98311 | 0.98311 | 0.98311 | 0.98311 | 0.98311 | 0.98311 | 2.7436 | 3.9575 | 4.7529 | 5.1715 | 6.0087 | 6.8459 | 0.82307 | 2.2358 | 2.8042 | 2.8042 | 2.8042 | 2.8042 | 1.467 | 1.8621 | 1.8621 | 1.8621 | 1.8621 | 1.8621
2020-08-21 15:00 | Winter | 2.191 | 3.369 | 5.0979 | 5.0979 | 5.0979 | 5.0979 | 0.98025 | 0.98025 | 0.98025 | 0.98025 | 0.98025 | 0.98025 | 2.7817 | 4.0125 | 4.8189 | 5.2433 | 6.0921 | 6.941 | 0.81545 | 2.2151 | 2.7782 | 2.7782 | 2.7782 | 2.7782 | 1.4099 | 1.7895 | 1.7895 | 1.7895 | 1.7895 | 1.7895
2020-08-21 16:00 | Winter | 2.1148 | 3.2518 | 4.9206 | 4.9206 | 4.9206 | 4.9206 | 0.96882 | 0.96882 | 0.96882 | 0.96882 | 0.96882 | 0.96882 | 2.8769 | 4.1499 | 4.9839 | 5.4229 | 6.3008 | 7.1787 | 0.84974 | 2.3082 | 2.8951 | 2.8951 | 2.8951 | 2.8951 | 1.3718 | 1.7412 | 1.7412 | 1.7412 | 1.7412 | 1.7412
2020-08-21 17:00 | Winter | 2.0015 | 3.0775 | 4.6569 | 4.6569 | 4.6569 | 4.6569 | 0.96596 | 0.96596 | 0.96596 | 0.96596 | 0.96596 | 0.96596 | 2.8769 | 4.1499 | 4.9839 | 5.4229 | 6.3008 | 7.1787 | 0.82307 | 2.2358 | 2.8042 | 2.8042 | 2.8042 | 2.8042 | 1.3146 | 1.6686 | 1.6686 | 1.6686 | 1.6686 | 1.6686
2020-08-21 18:00 | Winter | 1.7914 | 2.7546 | 4.1682 | 4.1682 | 4.1682 | 4.1682 | 0.78591 | 0.78591 | 0.78591 | 0.78591 | 0.78591 | 0.78591 | 2.8391 | 4.0953 | 4.9184 | 5.3515 | 6.2179 | 7.0843 | 0.7964 | 2.1633 | 2.7133 | 2.7133 | 2.7133 | 2.7133 | 0.88419 | 1.1223 | 1.1223 | 1.1223 | 1.1223 | 1.1223
2020-08-21 19:00 | Winter | 1.1526 | 1.7723 | 2.6818 | 2.6818 | 2.6818 | 2.6818 | 0.73161 | 0.73161 | 0.73161 | 0.73161 | 0.73161 | 0.73161 | 2.6293 | 3.7926 | 4.5548 | 4.956 | 5.7583 | 6.5606 | 0.73543 | 1.9977 | 2.5056 | 2.5056 | 2.5056 | 2.5056 | 0.68614 | 0.8709 | 0.8709 | 0.8709 | 0.8709 | 0.8709
2020-08-21 20:00 | Winter | 1.1053 | 1.6996 | 2.5718 | 2.5718 | 2.5718 | 2.5718 | 0.68303 | 0.68303 | 0.68303 | 0.68303 | 0.68303 | 0.68303 | 2.4768 | 3.5728 | 4.2908 | 4.6687 | 5.4245 | 6.1803 | 0.7964 | 2.1633 | 2.7133 | 2.7133 | 2.7133 | 2.7133 | 0.64779 | 0.82222 | 0.82222 | 0.82222 | 0.82222 | 0.82222
2020-08-21 21:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.65731 | 0.65731 | 0.65731 | 0.65731 | 0.65731 | 0.65731 | 2.3435 | 3.3804 | 4.0597 | 4.4173 | 5.1324 | 5.8475 | 0.70494 | 1.9149 | 2.4018 | 2.4018 | 2.4018 | 2.4018 | 0.57158 | 0.72549 | 0.72549 | 0.72549 | 0.72549 | 0.72549
2020-08-21 22:00 | Winter | 0.97294 | 1.496 | 2.2637 | 2.2637 | 2.2637 | 2.2637 | 0.60015 | 0.60015 | 0.60015 | 0.60015 | 0.60015 | 0.60015 | 2.172 | 3.133 | 3.7627 | 4.0941 | 4.7569 | 5.4197 | 0.73162 | 1.9874 | 2.4926 | 2.4926 | 2.4926 | 2.4926 | 0.55252 | 0.70131 | 0.70131 | 0.70131 | 0.70131 | 0.70131
2020-08-21 23:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.55728 | 0.55728 | 0.55728 | 0.55728 | 0.55728 | 0.55728 | 2.0367 | 2.9379 | 3.5284 | 3.8391 | 4.4606 | 5.0821 | 0.60587 | 1.6458 | 2.0642 | 2.0642 | 2.0642 | 2.0642 | 0.49537 | 0.62876 | 0.62876 | 0.62876 | 0.62876 | 0.62876
2020-08-22 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.52299 | 0.52299 | 0.52299 | 0.52299 | 0.52299 | 0.52299 | 1.81 | 2.6109 | 3.1356 | 3.4117 | 3.9641 | 4.5164 | 0.54871 | 1.4905 | 1.8695 | 1.8695 | 1.8695 | 1.8695 | 0.47758 | 0.60619 | 0.60619 | 0.60619 | 0.60619 | 0.60619
2020-08-22 01:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.47726 | 0.47726 | 0.47726 | 0.47726 | 0.47726 | 0.47726 | 1.7103 | 2.4671 | 2.9629 | 3.2239 | 3.7458 | 4.2677 | 0.51442 | 1.3974 | 1.7526 | 1.7526 | 1.7526 | 1.7526 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-08-22 02:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.50584 | 0.50584 | 0.50584 | 0.50584 | 0.50584 | 0.50584 | 1.6957 | 2.446 | 2.9375 | 3.1963 | 3.7137 | 4.2311 | 0.55252 | 1.5009 | 1.8825 | 1.8825 | 1.8825 | 1.8825 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-08-22 03:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.53156 | 0.53156 | 0.53156 | 0.53156 | 0.53156 | 0.53156 | 1.6576 | 2.391 | 2.8715 | 3.1244 | 3.6302 | 4.1361 | 0.52966 | 1.4388 | 1.8046 | 1.8046 | 1.8046 | 1.8046 | 0.43826 | 0.55627 | 0.55627 | 0.55627 | 0.55627 | 0.55627
2020-08-22 04:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.51156 | 0.51156 | 0.51156 | 0.51156 | 0.51156 | 0.51156 | 1.7301 | 2.4956 | 2.9971 | 3.2611 | 3.789 | 4.3169 | 0.54871 | 1.4905 | 1.8695 | 1.8695 | 1.8695 | 1.8695 | 0.44179 | 0.56075 | 0.56075 | 0.56075 | 0.56075 | 0.56075
2020-08-22 05:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.58872 | 0.58872 | 0.58872 | 0.58872 | 0.58872 | 0.58872 | 1.8672 | 2.6933 | 3.2346 | 3.5195 | 4.0892 | 4.659 | 0.56395 | 1.5319 | 1.9214 | 1.9214 | 1.9214 | 1.9214 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-08-22 06:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 0.66017 | 0.66017 | 0.66017 | 0.66017 | 0.66017 | 0.66017 | 2.0386 | 2.9407 | 3.5316 | 3.8427 | 4.4648 | 5.0869 | 0.56395 | 1.5319 | 1.9214 | 1.9214 | 1.9214 | 1.9214 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-08-22 07:00 | Winter | 1.086 | 1.6698 | 2.5268 | 2.5268 | 2.5268 | 2.5268 | 0.72018 | 0.72018 | 0.72018 | 0.72018 | 0.72018 | 0.72018 | 2.1339 | 3.0781 | 3.6967 | 4.0223 | 4.6734 | 5.3246 | 0.64016 | 1.7389 | 2.1811 | 2.1811 | 2.1811 | 2.1811 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-08-22 08:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 0.66017 | 0.66017 | 0.66017 | 0.66017 | 0.66017 | 0.66017 | 2.3054 | 3.3254 | 3.9937 | 4.3455 | 5.049 | 5.7525 | 0.6897 | 1.8735 | 2.3498 | 2.3498 | 2.3498 | 2.3498 | 0.57158 | 0.72549 | 0.72549 | 0.72549 | 0.72549 | 0.72549
2020-08-22 09:00 | Winter | 1.0288 | 1.582 | 2.3938 | 2.3938 | 2.3938 | 2.3938 | 0.72018 | 0.72018 | 0.72018 | 0.72018 | 0.72018 | 0.72018 | 2.4006 | 3.4628 | 4.1588 | 4.525 | 5.2576 | 5.9902 | 0.72018 | 1.9563 | 2.4537 | 2.4537 | 2.4537 | 2.4537 | 0.60968 | 0.77386 | 0.77386 | 0.77386 | 0.77386 | 0.77386
2020-08-22 10:00 | Winter | 1.0669 | 1.6405 | 2.4825 | 2.4825 | 2.4825 | 2.4825 | 0.69732 | 0.69732 | 0.69732 | 0.69732 | 0.69732 | 0.69732 | 2.3625 | 3.4079 | 4.0927 | 4.4532 | 5.1741 | 5.8951 | 0.6897 | 1.8735 | 2.3498 | 2.3498 | 2.3498 | 2.3498 | 0.64779 | 0.82222 | 0.82222 | 0.82222 | 0.82222 | 0.82222
2020-08-22 11:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 0.68303 | 0.68303 | 0.68303 | 0.68303 | 0.68303 | 0.68303 | 2.3816 | 3.4353 | 4.1258 | 4.4891 | 5.2159 | 5.9426 | 0.64779 | 1.7596 | 2.207 | 2.207 | 2.207 | 2.207 | 0.64779 | 0.82222 | 0.82222 | 0.82222 | 0.82222 | 0.82222
2020-08-22 12:00 | Winter | 1.105 | 1.6991 | 2.5711 | 2.5711 | 2.5711 | 2.5711 | 0.77162 | 0.77162 | 0.77162 | 0.77162 | 0.77162 | 0.77162 | 2.4959 | 3.6002 | 4.3238 | 4.7046 | 5.4662 | 6.2279 | 0.63635 | 1.7286 | 2.1681 | 2.1681 | 2.1681 | 2.1681 | 0.724 | 0.91895 | 0.91895 | 0.91895 | 0.91895 | 0.91895
2020-08-22 13:00 | Winter | 1.0768 | 1.6558 | 2.5055 | 2.5055 | 2.5055 | 2.5055 | 0.69732 | 0.69732 | 0.69732 | 0.69732 | 0.69732 | 0.69732 | 2.4906 | 3.5927 | 4.3147 | 4.6947 | 5.4547 | 6.2147 | 0.65922 | 1.7907 | 2.246 | 2.246 | 2.246 | 2.246 | 0.66684 | 0.84641 | 0.84641 | 0.84641 | 0.84641 | 0.84641
2020-08-22 14:00 | Winter | 1.086 | 1.6698 | 2.5268 | 2.5268 | 2.5268 | 2.5268 | 0.7459 | 0.7459 | 0.7459 | 0.7459 | 0.7459 | 0.7459 | 2.4959 | 3.6002 | 4.3238 | 4.7046 | 5.4662 | 6.2279 | 0.62492 | 1.6975 | 2.1291 | 2.1291 | 2.1291 | 2.1291 | 0.66684 | 0.84641 | 0.84641 | 0.84641 | 0.84641 | 0.84641
2020-08-22 15:00 | Winter | 1.105 | 1.6991 | 2.5711 | 2.5711 | 2.5711 | 2.5711 | 0.79163 | 0.79163 | 0.79163 | 0.79163 | 0.79163 | 0.79163 | 2.4387 | 3.5178 | 4.2248 | 4.5969 | 5.3411 | 6.0852 | 0.69732 | 1.8942 | 2.3758 | 2.3758 | 2.3758 | 2.3758 | 0.57158 | 0.72549 | 0.72549 | 0.72549 | 0.72549 | 0.72549
2020-08-22 16:00 | Winter | 1.0878 | 1.6726 | 2.531 | 2.531 | 2.531 | 2.531 | 0.73447 | 0.73447 | 0.73447 | 0.73447 | 0.73447 | 0.73447 | 2.4768 | 3.5728 | 4.2908 | 4.6687 | 5.4245 | 6.1803 | 0.71637 | 1.946 | 2.4407 | 2.4407 | 2.4407 | 2.4407 | 0.66684 | 0.84641 | 0.84641 | 0.84641 | 0.84641 | 0.84641
2020-08-22 17:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 0.78306 | 0.78306 | 0.78306 | 0.78306 | 0.78306 | 0.78306 | 2.5721 | 3.7102 | 4.4558 | 4.8483 | 5.6331 | 6.418 | 0.77734 | 2.1116 | 2.6484 | 2.6484 | 2.6484 | 2.6484 | 0.60968 | 0.77386 | 0.77386 | 0.77386 | 0.77386 | 0.77386
2020-08-22 18:00 | Winter | 1.0292 | 1.5826 | 2.3948 | 2.3948 | 2.3948 | 2.3948 | 0.75734 | 0.75734 | 0.75734 | 0.75734 | 0.75734 | 0.75734 | 2.5911 | 3.7377 | 4.4888 | 4.8842 | 5.6749 | 6.4656 | 0.78496 | 2.1323 | 2.6744 | 2.6744 | 2.6744 | 2.6744 | 0.60968 | 0.77386 | 0.77386 | 0.77386 | 0.77386 | 0.77386
2020-08-22 19:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.70589 | 0.70589 | 0.70589 | 0.70589 | 0.70589 | 0.70589 | 2.553 | 3.6827 | 4.4228 | 4.8123 | 5.5914 | 6.3705 | 0.7964 | 2.1633 | 2.7133 | 2.7133 | 2.7133 | 2.7133 | 0.59094 | 0.75007 | 0.75007 | 0.75007 | 0.75007 | 0.75007
2020-08-22 20:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.70018 | 0.70018 | 0.70018 | 0.70018 | 0.70018 | 0.70018 | 2.4387 | 3.5178 | 4.2248 | 4.5969 | 5.3411 | 6.0852 | 0.78877 | 2.1426 | 2.6874 | 2.6874 | 2.6874 | 2.6874 | 0.60968 | 0.77386 | 0.77386 | 0.77386 | 0.77386 | 0.77386
2020-08-22 21:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.66588 | 0.66588 | 0.66588 | 0.66588 | 0.66588 | 0.66588 | 2.3435 | 3.3804 | 4.0597 | 4.4173 | 5.1324 | 5.8475 | 0.71256 | 1.9356 | 2.4277 | 2.4277 | 2.4277 | 2.4277 | 0.60968 | 0.77386 | 0.77386 | 0.77386 | 0.77386 | 0.77386
2020-08-22 22:00 | Winter | 0.98683 | 1.5174 | 2.2961 | 2.2961 | 2.2961 | 2.2961 | 0.59729 | 0.59729 | 0.59729 | 0.59729 | 0.59729 | 0.59729 | 2.2868 | 3.2986 | 3.9615 | 4.3105 | 5.0083 | 5.7061 | 0.72018 | 1.9563 | 2.4537 | 2.4537 | 2.4537 | 2.4537 | 0.55252 | 0.70131 | 0.70131 | 0.70131 | 0.70131 | 0.70131
2020-08-22 23:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.5287 | 0.5287 | 0.5287 | 0.5287 | 0.5287 | 0.5287 | 2.0148 | 2.9063 | 3.4904 | 3.7978 | 4.4127 | 5.0275 | 0.63635 | 1.7286 | 2.1681 | 2.1681 | 2.1681 | 2.1681 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-08-23 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.48869 | 0.48869 | 0.48869 | 0.48869 | 0.48869 | 0.48869 | 1.8292 | 2.6386 | 3.1689 | 3.448 | 4.0062 | 4.5644 | 0.60206 | 1.6354 | 2.0512 | 2.0512 | 2.0512 | 2.0512 | 0.51434 | 0.65284 | 0.65284 | 0.65284 | 0.65284 | 0.65284
2020-08-23 01:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.50013 | 0.50013 | 0.50013 | 0.50013 | 0.50013 | 0.50013 | 1.7147 | 2.4735 | 2.9705 | 3.2322 | 3.7554 | 4.2787 | 0.55633 | 1.5112 | 1.8954 | 1.8954 | 1.8954 | 1.8954 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-08-23 02:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.55157 | 0.55157 | 0.55157 | 0.55157 | 0.55157 | 0.55157 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.53728 | 1.4595 | 1.8305 | 1.8305 | 1.8305 | 1.8305 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-08-23 03:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.53156 | 0.53156 | 0.53156 | 0.53156 | 0.53156 | 0.53156 | 1.6195 | 2.336 | 2.8055 | 3.0526 | 3.5468 | 4.041 | 0.54109 | 1.4698 | 1.8435 | 1.8435 | 1.8435 | 1.8435 | 0.50867 | 0.64565 | 0.64565 | 0.64565 | 0.64565 | 0.64565
2020-08-23 04:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.52013 | 0.52013 | 0.52013 | 0.52013 | 0.52013 | 0.52013 | 1.6576 | 2.391 | 2.8715 | 3.1244 | 3.6302 | 4.1361 | 0.55252 | 1.5009 | 1.8825 | 1.8825 | 1.8825 | 1.8825 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-08-23 05:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.54299 | 0.54299 | 0.54299 | 0.54299 | 0.54299 | 0.54299 | 1.7521 | 2.5273 | 3.0352 | 3.3026 | 3.8372 | 4.3719 | 0.55633 | 1.5112 | 1.8954 | 1.8954 | 1.8954 | 1.8954 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-08-23 06:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.55728 | 0.55728 | 0.55728 | 0.55728 | 0.55728 | 0.55728 | 1.9624 | 2.8307 | 3.3996 | 3.699 | 4.2979 | 4.8967 | 0.57539 | 1.563 | 1.9603 | 1.9603 | 1.9603 | 1.9603 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-08-23 07:00 | Winter | 0.95319 | 1.4656 | 2.2178 | 2.2178 | 2.2178 | 2.2178 | 0.67731 | 0.67731 | 0.67731 | 0.67731 | 0.67731 | 0.67731 | 1.9815 | 2.8582 | 3.4326 | 3.735 | 4.3396 | 4.9443 | 0.60587 | 1.6458 | 2.0642 | 2.0642 | 2.0642 | 2.0642 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-08-23 08:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.66017 | 0.66017 | 0.66017 | 0.66017 | 0.66017 | 0.66017 | 2.191 | 3.1605 | 3.7957 | 4.13 | 4.7986 | 5.4672 | 0.67827 | 1.8425 | 2.3109 | 2.3109 | 2.3109 | 2.3109 | 0.57158 | 0.72549 | 0.72549 | 0.72549 | 0.72549 | 0.72549
2020-08-23 09:00 | Winter | 0.89547 | 1.3769 | 2.0835 | 2.0835 | 2.0835 | 2.0835 | 0.66303 | 0.66303 | 0.66303 | 0.66303 | 0.66303 | 0.66303 | 2.3244 | 3.3529 | 4.0267 | 4.3814 | 5.0907 | 5.8 | 0.74305 | 2.0184 | 2.5316 | 2.5316 | 2.5316 | 2.5316 | 0.57158 | 0.72549 | 0.72549 | 0.72549 | 0.72549 | 0.72549
2020-08-23 10:00 | Winter | 0.89547 | 1.3769 | 2.0835 | 2.0835 | 2.0835 | 2.0835 | 0.62016 | 0.62016 | 0.62016 | 0.62016 | 0.62016 | 0.62016 | 2.3244 | 3.3529 | 4.0267 | 4.3814 | 5.0907 | 5.8 | 0.66303 | 1.8011 | 2.2589 | 2.2589 | 2.2589 | 2.2589 | 0.57158 | 0.72549 | 0.72549 | 0.72549 | 0.72549 | 0.72549
2020-08-23 11:00 | Winter | 0.93358 | 1.4355 | 2.1722 | 2.1722 | 2.1722 | 2.1722 | 0.60873 | 0.60873 | 0.60873 | 0.60873 | 0.60873 | 0.60873 | 2.2101 | 3.188 | 3.8287 | 4.1659 | 4.8403 | 5.5147 | 0.70875 | 1.9253 | 2.4147 | 2.4147 | 2.4147 | 2.4147 | 0.57158 | 0.72549 | 0.72549 | 0.72549 | 0.72549 | 0.72549
2020-08-23 12:00 | Winter | 0.91452 | 1.4062 | 2.1278 | 2.1278 | 2.1278 | 2.1278 | 0.59729 | 0.59729 | 0.59729 | 0.59729 | 0.59729 | 0.59729 | 2.2291 | 3.2155 | 3.8617 | 4.2018 | 4.8821 | 5.5623 | 0.64397 | 1.7493 | 2.194 | 2.194 | 2.194 | 2.194 | 0.55252 | 0.70131 | 0.70131 | 0.70131 | 0.70131 | 0.70131
2020-08-23 13:00 | Winter | 0.94905 | 1.4593 | 2.2082 | 2.2082 | 2.2082 | 2.2082 | 0.53442 | 0.53442 | 0.53442 | 0.53442 | 0.53442 | 0.53442 | 2.3054 | 3.3254 | 3.9937 | 4.3455 | 5.049 | 5.7525 | 0.5792 | 1.5733 | 1.9733 | 1.9733 | 1.9733 | 1.9733 | 0.58274 | 0.73966 | 0.73966 | 0.73966 | 0.73966 | 0.73966
2020-08-23 14:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.53442 | 0.53442 | 0.53442 | 0.53442 | 0.53442 | 0.53442 | 2.3054 | 3.3254 | 3.9937 | 4.3455 | 5.049 | 5.7525 | 0.61349 | 1.6665 | 2.0902 | 2.0902 | 2.0902 | 2.0902 | 0.59063 | 0.74967 | 0.74967 | 0.74967 | 0.74967 | 0.74967
2020-08-23 15:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.65445 | 0.65445 | 0.65445 | 0.65445 | 0.65445 | 0.65445 | 2.4387 | 3.5178 | 4.2248 | 4.5969 | 5.3411 | 6.0852 | 0.6516 | 1.77 | 2.22 | 2.22 | 2.22 | 2.22 | 0.55252 | 0.70131 | 0.70131 | 0.70131 | 0.70131 | 0.70131
2020-08-23 16:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.66303 | 0.66303 | 0.66303 | 0.66303 | 0.66303 | 0.66303 | 2.4006 | 3.4628 | 4.1588 | 4.525 | 5.2576 | 5.9902 | 0.66303 | 1.8011 | 2.2589 | 2.2589 | 2.2589 | 2.2589 | 0.55252 | 0.70131 | 0.70131 | 0.70131 | 0.70131 | 0.70131
2020-08-23 17:00 | Winter | 1.0288 | 1.582 | 2.3938 | 2.3938 | 2.3938 | 2.3938 | 0.71447 | 0.71447 | 0.71447 | 0.71447 | 0.71447 | 0.71447 | 2.534 | 3.6552 | 4.3898 | 4.7764 | 5.5497 | 6.3229 | 0.70494 | 1.9149 | 2.4018 | 2.4018 | 2.4018 | 2.4018 | 0.60968 | 0.77386 | 0.77386 | 0.77386 | 0.77386 | 0.77386
2020-08-23 18:00 | Winter | 1.01 | 1.553 | 2.35 | 2.35 | 2.35 | 2.35 | 0.69446 | 0.69446 | 0.69446 | 0.69446 | 0.69446 | 0.69446 | 2.534 | 3.6552 | 4.3898 | 4.7764 | 5.5497 | 6.3229 | 0.75448 | 2.0495 | 2.5705 | 2.5705 | 2.5705 | 2.5705 | 0.57158 | 0.72549 | 0.72549 | 0.72549 | 0.72549 | 0.72549
2020-08-23 19:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.66588 | 0.66588 | 0.66588 | 0.66588 | 0.66588 | 0.66588 | 2.4768 | 3.5728 | 4.2908 | 4.6687 | 5.4245 | 6.1803 | 0.75829 | 2.0598 | 2.5835 | 2.5835 | 2.5835 | 2.5835 | 0.59063 | 0.74967 | 0.74967 | 0.74967 | 0.74967 | 0.74967
2020-08-23 20:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.56872 | 0.56872 | 0.56872 | 0.56872 | 0.56872 | 0.56872 | 2.3625 | 3.4079 | 4.0927 | 4.4532 | 5.1741 | 5.8951 | 0.71637 | 1.946 | 2.4407 | 2.4407 | 2.4407 | 2.4407 | 0.57158 | 0.72549 | 0.72549 | 0.72549 | 0.72549 | 0.72549
2020-08-23 21:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.54299 | 0.54299 | 0.54299 | 0.54299 | 0.54299 | 0.54299 | 2.2673 | 3.2705 | 3.9277 | 4.2736 | 4.9655 | 5.6574 | 0.70875 | 1.9253 | 2.4147 | 2.4147 | 2.4147 | 2.4147 | 0.60968 | 0.77386 | 0.77386 | 0.77386 | 0.77386 | 0.77386
2020-08-23 22:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.51156 | 0.51156 | 0.51156 | 0.51156 | 0.51156 | 0.51156 | 2.0196 | 2.9132 | 3.4986 | 3.8068 | 4.4231 | 5.0393 | 0.67065 | 1.8218 | 2.2849 | 2.2849 | 2.2849 | 2.2849 | 0.57158 | 0.72549 | 0.72549 | 0.72549 | 0.72549 | 0.72549
2020-08-23 23:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.52013 | 0.52013 | 0.52013 | 0.52013 | 0.52013 | 0.52013 | 1.9053 | 2.7483 | 3.3006 | 3.5913 | 4.1727 | 4.7541 | 0.57539 | 1.563 | 1.9603 | 1.9603 | 1.9603 | 1.9603 | 0.55268 | 0.7015 | 0.7015 | 0.7015 | 0.7015 | 0.7015
2020-08-24 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.52013 | 0.52013 | 0.52013 | 0.52013 | 0.52013 | 0.52013 | 1.7147 | 2.4735 | 2.9705 | 3.2322 | 3.7554 | 4.2787 | 0.56776 | 1.5423 | 1.9344 | 1.9344 | 1.9344 | 1.9344 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-08-24 01:00 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.51156 | 0.51156 | 0.51156 | 0.51156 | 0.51156 | 0.51156 | 1.582 | 2.282 | 2.7406 | 2.9819 | 3.4647 | 3.9474 | 0.5449 | 1.4802 | 1.8565 | 1.8565 | 1.8565 | 1.8565 | 0.49537 | 0.62876 | 0.62876 | 0.62876 | 0.62876 | 0.62876
2020-08-24 02:00 | Winter | 1.1488 | 1.7664 | 2.673 | 2.673 | 2.673 | 2.673 | 0.55728 | 0.55728 | 0.55728 | 0.55728 | 0.55728 | 0.55728 | 1.6004 | 2.3086 | 2.7725 | 3.0167 | 3.5051 | 3.9934 | 0.53728 | 1.4595 | 1.8305 | 1.8305 | 1.8305 | 1.8305 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-08-24 03:00 | Winter | 1.2003 | 1.8456 | 2.7928 | 2.7928 | 2.7928 | 2.7928 | 0.52013 | 0.52013 | 0.52013 | 0.52013 | 0.52013 | 0.52013 | 1.6004 | 2.3086 | 2.7725 | 3.0167 | 3.5051 | 3.9934 | 0.54871 | 1.4905 | 1.8695 | 1.8695 | 1.8695 | 1.8695 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-08-24 04:00 | Winter | 1.2575 | 1.9335 | 2.9258 | 2.9258 | 2.9258 | 2.9258 | 0.54585 | 0.54585 | 0.54585 | 0.54585 | 0.54585 | 0.54585 | 1.7338 | 2.5009 | 3.0036 | 3.2681 | 3.7972 | 4.3262 | 0.55252 | 1.5009 | 1.8825 | 1.8825 | 1.8825 | 1.8825 | 0.56488 | 0.71699 | 0.71699 | 0.71699 | 0.71699 | 0.71699
2020-08-24 05:00 | Winter | 1.5591 | 2.3973 | 3.6276 | 3.6276 | 3.6276 | 3.6276 | 0.7372 | 0.7372 | 0.7372 | 0.7372 | 0.7372 | 0.7372 | 2.0101 | 2.8995 | 3.4822 | 3.7889 | 4.4023 | 5.0157 | 0.65922 | 1.7907 | 2.246 | 2.246 | 2.246 | 2.246 | 0.81687 | 1.0368 | 1.0368 | 1.0368 | 1.0368 | 1.0368
2020-08-24 06:00 | Winter | 1.8875 | 2.9022 | 4.3916 | 4.3916 | 4.3916 | 4.3916 | 0.83164 | 0.83164 | 0.83164 | 0.83164 | 0.83164 | 0.83164 | 2.1907 | 3.16 | 3.795 | 4.1293 | 4.7978 | 5.4663 | 0.72781 | 1.977 | 2.4796 | 2.4796 | 2.4796 | 2.4796 | 1.0476 | 1.3298 | 1.3298 | 1.3298 | 1.3298 | 1.3298
2020-08-24 07:00 | Winter | 2.2482 | 3.4569 | 5.2309 | 5.2309 | 5.2309 | 5.2309 | 0.9631 | 0.9631 | 0.9631 | 0.9631 | 0.9631 | 0.9631 | 2.5069 | 3.6162 | 4.3429 | 4.7254 | 5.4904 | 6.2554 | 0.80021 | 2.1737 | 2.7263 | 2.7263 | 2.7263 | 2.7263 | 1.4742 | 1.8712 | 1.8712 | 1.8712 | 1.8712 | 1.8712
2020-08-24 08:00 | Winter | 2.4768 | 3.8084 | 5.7629 | 5.7629 | 5.7629 | 5.7629 | 1.0517 | 1.0517 | 1.0517 | 1.0517 | 1.0517 | 1.0517 | 2.7626 | 3.985 | 4.7859 | 5.2074 | 6.0504 | 6.8934 | 0.83069 | 2.2565 | 2.8302 | 2.8302 | 2.8302 | 2.8302 | 1.6004 | 2.0314 | 2.0314 | 2.0314 | 2.0314 | 2.0314
2020-08-24 09:00 | Winter | 2.4578 | 3.7791 | 5.7186 | 5.7186 | 5.7186 | 5.7186 | 1.0917 | 1.0917 | 1.0917 | 1.0917 | 1.0917 | 1.0917 | 2.7817 | 4.0125 | 4.8189 | 5.2433 | 6.0921 | 6.941 | 0.81926 | 2.2254 | 2.7912 | 2.7912 | 2.7912 | 2.7912 | 1.6766 | 2.1281 | 2.1281 | 2.1281 | 2.1281 | 2.1281
2020-08-24 10:00 | Winter | 2.3816 | 3.6619 | 5.5412 | 5.5412 | 5.5412 | 5.5412 | 1.0688 | 1.0688 | 1.0688 | 1.0688 | 1.0688 | 1.0688 | 2.7055 | 3.9026 | 4.6869 | 5.0996 | 5.9252 | 6.7508 | 0.77734 | 2.1116 | 2.6484 | 2.6484 | 2.6484 | 2.6484 | 1.7147 | 2.1765 | 2.1765 | 2.1765 | 2.1765 | 2.1765
2020-08-24 11:00 | Winter | 2.3244 | 3.5741 | 5.4082 | 5.4082 | 5.4082 | 5.4082 | 1.0288 | 1.0288 | 1.0288 | 1.0288 | 1.0288 | 1.0288 | 2.7626 | 3.985 | 4.7859 | 5.2074 | 6.0504 | 6.8934 | 0.76972 | 2.0909 | 2.6225 | 2.6225 | 2.6225 | 2.6225 | 1.6766 | 2.1281 | 2.1281 | 2.1281 | 2.1281 | 2.1281
2020-08-24 12:00 | Winter | 2.3625 | 3.6326 | 5.4969 | 5.4969 | 5.4969 | 5.4969 | 0.98597 | 0.98597 | 0.98597 | 0.98597 | 0.98597 | 0.98597 | 2.7055 | 3.9026 | 4.6869 | 5.0996 | 5.9252 | 6.7508 | 0.82307 | 2.2358 | 2.8042 | 2.8042 | 2.8042 | 2.8042 | 1.6004 | 2.0314 | 2.0314 | 2.0314 | 2.0314 | 2.0314
2020-08-24 13:00 | Winter | 2.3244 | 3.5741 | 5.4082 | 5.4082 | 5.4082 | 5.4082 | 0.96025 | 0.96025 | 0.96025 | 0.96025 | 0.96025 | 0.96025 | 2.6864 | 3.8751 | 4.6539 | 5.0637 | 5.8835 | 6.7033 | 0.80021 | 2.1737 | 2.7263 | 2.7263 | 2.7263 | 2.7263 | 1.6004 | 2.0314 | 2.0314 | 2.0314 | 2.0314 | 2.0314
2020-08-24 14:00 | Winter | 2.2482 | 3.4569 | 5.2309 | 5.2309 | 5.2309 | 5.2309 | 0.97453 | 0.97453 | 0.97453 | 0.97453 | 0.97453 | 0.97453 | 2.6674 | 3.8476 | 4.6208 | 5.0278 | 5.8418 | 6.6557 | 0.76972 | 2.0909 | 2.6225 | 2.6225 | 2.6225 | 2.6225 | 1.4867 | 1.887 | 1.887 | 1.887 | 1.887 | 1.887
2020-08-24 15:00 | Winter | 2.2101 | 3.3983 | 5.1423 | 5.1423 | 5.1423 | 5.1423 | 0.94881 | 0.94881 | 0.94881 | 0.94881 | 0.94881 | 0.94881 | 2.6102 | 3.7651 | 4.5218 | 4.9201 | 5.7166 | 6.5131 | 0.76972 | 2.0909 | 2.6225 | 2.6225 | 2.6225 | 2.6225 | 1.4289 | 1.8137 | 1.8137 | 1.8137 | 1.8137 | 1.8137
2020-08-24 16:00 | Winter | 2.2101 | 3.3983 | 5.1423 | 5.1423 | 5.1423 | 5.1423 | 0.92881 | 0.92881 | 0.92881 | 0.92881 | 0.92881 | 0.92881 | 2.6483 | 3.8201 | 4.5878 | 4.9919 | 5.8 | 6.6082 | 0.75829 | 2.0598 | 2.5835 | 2.5835 | 2.5835 | 2.5835 | 1.3527 | 1.717 | 1.717 | 1.717 | 1.717 | 1.717
2020-08-24 17:00 | Winter | 2.1529 | 3.3104 | 5.0093 | 5.0093 | 5.0093 | 5.0093 | 0.89166 | 0.89166 | 0.89166 | 0.89166 | 0.89166 | 0.89166 | 2.6674 | 3.8476 | 4.6208 | 5.0278 | 5.8418 | 6.6557 | 0.74203 | 2.0157 | 2.5281 | 2.5281 | 2.5281 | 2.5281 | 1.2765 | 1.6203 | 1.6203 | 1.6203 | 1.6203 | 1.6203
2020-08-24 18:00 | Winter | 1.8112 | 2.7849 | 4.2141 | 4.2141 | 4.2141 | 4.2141 | 0.81735 | 0.81735 | 0.81735 | 0.81735 | 0.81735 | 0.81735 | 2.7436 | 3.9575 | 4.7529 | 5.1715 | 6.0087 | 6.8459 | 0.7621 | 2.0702 | 2.5965 | 2.5965 | 2.5965 | 2.5965 | 0.91543 | 1.1619 | 1.1619 | 1.1619 | 1.1619 | 1.1619
2020-08-24 19:00 | Winter | 1.2384 | 1.9042 | 2.8814 | 2.8814 | 2.8814 | 2.8814 | 0.66303 | 0.66303 | 0.66303 | 0.66303 | 0.66303 | 0.66303 | 2.6293 | 3.7926 | 4.5548 | 4.956 | 5.7583 | 6.5606 | 0.67446 | 1.8321 | 2.2979 | 2.2979 | 2.2979 | 2.2979 | 0.66684 | 0.84641 | 0.84641 | 0.84641 | 0.84641 | 0.84641
2020-08-24 20:00 | Winter | 1.0863 | 1.6704 | 2.5276 | 2.5276 | 2.5276 | 2.5276 | 0.55543 | 0.55543 | 0.55543 | 0.55543 | 0.55543 | 0.55543 | 2.5376 | 3.6604 | 4.396 | 4.7832 | 5.5575 | 6.3319 | 0.66303 | 1.8011 | 2.2589 | 2.2589 | 2.2589 | 2.2589 | 0.60998 | 0.77423 | 0.77423 | 0.77423 | 0.77423 | 0.77423
2020-08-24 21:00 | Winter | 1.0669 | 1.6405 | 2.4825 | 2.4825 | 2.4825 | 2.4825 | 0.55728 | 0.55728 | 0.55728 | 0.55728 | 0.55728 | 0.55728 | 2.3247 | 3.3533 | 4.0273 | 4.382 | 5.0914 | 5.8008 | 0.68589 | 1.8632 | 2.3368 | 2.3368 | 2.3368 | 2.3368 | 0.59063 | 0.74967 | 0.74967 | 0.74967 | 0.74967 | 0.74967
2020-08-24 22:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.49727 | 0.49727 | 0.49727 | 0.49727 | 0.49727 | 0.49727 | 2.191 | 3.1605 | 3.7957 | 4.13 | 4.7986 | 5.4672 | 0.62111 | 1.6872 | 2.1161 | 2.1161 | 2.1161 | 2.1161 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-08-24 23:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.51156 | 0.51156 | 0.51156 | 0.51156 | 0.51156 | 0.51156 | 1.9231 | 2.774 | 3.3315 | 3.625 | 4.2118 | 4.7987 | 0.58301 | 1.5837 | 1.9863 | 1.9863 | 1.9863 | 1.9863 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-08-25 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.50298 | 0.50298 | 0.50298 | 0.50298 | 0.50298 | 0.50298 | 1.7364 | 2.5047 | 3.0081 | 3.273 | 3.8029 | 4.3327 | 0.57157 | 1.5526 | 1.9474 | 1.9474 | 1.9474 | 1.9474 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-08-25 01:00 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 1.6576 | 2.391 | 2.8715 | 3.1244 | 3.6302 | 4.1361 | 0.54871 | 1.4905 | 1.8695 | 1.8695 | 1.8695 | 1.8695 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-08-25 02:00 | Winter | 1.2194 | 1.8749 | 2.8371 | 2.8371 | 2.8371 | 2.8371 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 1.6766 | 2.4185 | 2.9045 | 3.1603 | 3.672 | 4.1836 | 0.52966 | 1.4388 | 1.8046 | 1.8046 | 1.8046 | 1.8046 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-08-25 03:00 | Winter | 1.2003 | 1.8456 | 2.7928 | 2.7928 | 2.7928 | 2.7928 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 1.6766 | 2.4185 | 2.9045 | 3.1603 | 3.672 | 4.1836 | 0.52204 | 1.4181 | 1.7786 | 1.7786 | 1.7786 | 1.7786 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-08-25 04:00 | Winter | 1.2382 | 1.9039 | 2.8809 | 2.8809 | 2.8809 | 2.8809 | 0.49155 | 0.49155 | 0.49155 | 0.49155 | 0.49155 | 0.49155 | 1.6766 | 2.4185 | 2.9045 | 3.1603 | 3.672 | 4.1836 | 0.51061 | 1.387 | 1.7396 | 1.7396 | 1.7396 | 1.7396 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-08-25 05:00 | Winter | 1.4099 | 2.1679 | 3.2804 | 3.2804 | 3.2804 | 3.2804 | 0.70875 | 0.70875 | 0.70875 | 0.70875 | 0.70875 | 0.70875 | 1.9815 | 2.8582 | 3.4326 | 3.735 | 4.3396 | 4.9443 | 0.67827 | 1.8425 | 2.3109 | 2.3109 | 2.3109 | 2.3109 | 0.724 | 0.91895 | 0.91895 | 0.91895 | 0.91895 | 0.91895
2020-08-25 06:00 | Winter | 1.8862 | 2.9003 | 4.3887 | 4.3887 | 4.3887 | 4.3887 | 0.78306 | 0.78306 | 0.78306 | 0.78306 | 0.78306 | 0.78306 | 2.2832 | 3.2934 | 3.9553 | 4.3037 | 5.0004 | 5.6971 | 0.70875 | 1.9253 | 2.4147 | 2.4147 | 2.4147 | 2.4147 | 1.059 | 1.3442 | 1.3442 | 1.3442 | 1.3442 | 1.3442
2020-08-25 07:00 | Winter | 2.3435 | 3.6034 | 5.4526 | 5.4526 | 5.4526 | 5.4526 | 1.0203 | 1.0203 | 1.0203 | 1.0203 | 1.0203 | 1.0203 | 2.5911 | 3.7377 | 4.4888 | 4.8842 | 5.6749 | 6.4656 | 0.76591 | 2.0805 | 2.6095 | 2.6095 | 2.6095 | 2.6095 | 1.467 | 1.8621 | 1.8621 | 1.8621 | 1.8621 | 1.8621
2020-08-25 08:00 | Winter | 2.5911 | 3.9842 | 6.0289 | 6.0289 | 6.0289 | 6.0289 | 1.2546 | 1.2546 | 1.2546 | 1.2546 | 1.2546 | 1.2546 | 2.8198 | 4.0675 | 4.8849 | 5.3151 | 6.1756 | 7.0361 | 0.87261 | 2.3704 | 2.973 | 2.973 | 2.973 | 2.973 | 1.6195 | 2.0556 | 2.0556 | 2.0556 | 2.0556 | 2.0556
2020-08-25 09:00 | Winter | 2.5149 | 3.867 | 5.8515 | 5.8515 | 5.8515 | 5.8515 | 1.1917 | 1.1917 | 1.1917 | 1.1917 | 1.1917 | 1.1917 | 2.8388 | 4.0949 | 4.9179 | 5.351 | 6.2173 | 7.0836 | 0.83069 | 2.2565 | 2.8302 | 2.8302 | 2.8302 | 2.8302 | 1.6195 | 2.0556 | 2.0556 | 2.0556 | 2.0556 | 2.0556
2020-08-25 10:00 | Winter | 2.534 | 3.8963 | 5.8959 | 5.8959 | 5.8959 | 5.8959 | 1.2117 | 1.2117 | 1.2117 | 1.2117 | 1.2117 | 1.2117 | 2.8579 | 4.1224 | 4.9509 | 5.387 | 6.259 | 7.1311 | 0.83069 | 2.2565 | 2.8302 | 2.8302 | 2.8302 | 2.8302 | 1.6576 | 2.1039 | 2.1039 | 2.1039 | 2.1039 | 2.1039
2020-08-25 11:00 | Winter | 2.4768 | 3.8084 | 5.7629 | 5.7629 | 5.7629 | 5.7629 | 1.1403 | 1.1403 | 1.1403 | 1.1403 | 1.1403 | 1.1403 | 2.7817 | 4.0125 | 4.8189 | 5.2433 | 6.0921 | 6.941 | 0.79258 | 2.153 | 2.7003 | 2.7003 | 2.7003 | 2.7003 | 1.6385 | 2.0797 | 2.0797 | 2.0797 | 2.0797 | 2.0797
2020-08-25 12:00 | Winter | 2.4387 | 3.7498 | 5.6742 | 5.6742 | 5.6742 | 5.6742 | 1.0288 | 1.0288 | 1.0288 | 1.0288 | 1.0288 | 1.0288 | 2.7626 | 3.985 | 4.7859 | 5.2074 | 6.0504 | 6.8934 | 0.85355 | 2.3186 | 2.9081 | 2.9081 | 2.9081 | 2.9081 | 1.6004 | 2.0314 | 2.0314 | 2.0314 | 2.0314 | 2.0314
2020-08-25 13:00 | Winter | 2.3625 | 3.6326 | 5.4969 | 5.4969 | 5.4969 | 5.4969 | 0.97739 | 0.97739 | 0.97739 | 0.97739 | 0.97739 | 0.97739 | 2.7245 | 3.93 | 4.7199 | 5.1356 | 5.967 | 6.7984 | 0.88023 | 2.3911 | 2.9989 | 2.9989 | 2.9989 | 2.9989 | 1.5433 | 1.9588 | 1.9588 | 1.9588 | 1.9588 | 1.9588
2020-08-25 14:00 | Winter | 2.3816 | 3.6619 | 5.5412 | 5.5412 | 5.5412 | 5.5412 | 0.99617 | 0.99617 | 0.99617 | 0.99617 | 0.99617 | 0.99617 | 2.7055 | 3.9026 | 4.6869 | 5.0996 | 5.9252 | 6.7508 | 0.84593 | 2.2979 | 2.8821 | 2.8821 | 2.8821 | 2.8821 | 1.4403 | 1.8282 | 1.8282 | 1.8282 | 1.8282 | 1.8282
2020-08-25 15:00 | Winter | 2.3244 | 3.5741 | 5.4082 | 5.4082 | 5.4082 | 5.4082 | 1.0117 | 1.0117 | 1.0117 | 1.0117 | 1.0117 | 1.0117 | 2.6483 | 3.8201 | 4.5878 | 4.9919 | 5.8 | 6.6082 | 0.81545 | 2.2151 | 2.7782 | 2.7782 | 2.7782 | 2.7782 | 1.4289 | 1.8137 | 1.8137 | 1.8137 | 1.8137 | 1.8137
2020-08-25 16:00 | Winter | 2.2101 | 3.3983 | 5.1423 | 5.1423 | 5.1423 | 5.1423 | 0.96596 | 0.96596 | 0.96596 | 0.96596 | 0.96596 | 0.96596 | 2.553 | 3.6827 | 4.4228 | 4.8123 | 5.5914 | 6.3705 | 0.89547 | 2.4325 | 3.0509 | 3.0509 | 3.0509 | 3.0509 | 1.3527 | 1.717 | 1.717 | 1.717 | 1.717 | 1.717
2020-08-25 17:00 | Winter | 2.063 | 3.1721 | 4.8 | 4.8 | 4.8 | 4.8 | 0.99168 | 0.99168 | 0.99168 | 0.99168 | 0.99168 | 0.99168 | 2.553 | 3.6827 | 4.4228 | 4.8123 | 5.5914 | 6.3705 | 0.82688 | 2.2461 | 2.8172 | 2.8172 | 2.8172 | 2.8172 | 1.2575 | 1.5961 | 1.5961 | 1.5961 | 1.5961 | 1.5961
2020-08-25 18:00 | Winter | 1.6282 | 2.5035 | 3.7884 | 3.7884 | 3.7884 | 3.7884 | 0.84879 | 0.84879 | 0.84879 | 0.84879 | 0.84879 | 0.84879 | 2.7436 | 3.9575 | 4.7529 | 5.1715 | 6.0087 | 6.8459 | 0.84212 | 2.2875 | 2.8691 | 2.8691 | 2.8691 | 2.8691 | 0.89698 | 1.1385 | 1.1385 | 1.1385 | 1.1385 | 1.1385
2020-08-25 19:00 | Winter | 1.1723 | 1.8025 | 2.7275 | 2.7275 | 2.7275 | 2.7275 | 0.59729 | 0.59729 | 0.59729 | 0.59729 | 0.59729 | 0.59729 | 2.5724 | 3.7106 | 4.4563 | 4.8488 | 5.6338 | 6.4187 | 0.81926 | 2.2254 | 2.7912 | 2.7912 | 2.7912 | 2.7912 | 0.68589 | 0.87059 | 0.87059 | 0.87059 | 0.87059 | 0.87059
2020-08-25 20:00 | Winter | 1.1241 | 1.7284 | 2.6155 | 2.6155 | 2.6155 | 2.6155 | 0.55157 | 0.55157 | 0.55157 | 0.55157 | 0.55157 | 0.55157 | 2.4214 | 3.4928 | 4.1948 | 4.5643 | 5.3032 | 6.0421 | 0.7621 | 2.0702 | 2.5965 | 2.5965 | 2.5965 | 2.5965 | 0.66684 | 0.84641 | 0.84641 | 0.84641 | 0.84641 | 0.84641
2020-08-25 21:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 0.52585 | 0.52585 | 0.52585 | 0.52585 | 0.52585 | 0.52585 | 2.3244 | 3.3529 | 4.0267 | 4.3814 | 5.0907 | 5.8 | 0.73924 | 2.0081 | 2.5186 | 2.5186 | 2.5186 | 2.5186 | 0.59374 | 0.75362 | 0.75362 | 0.75362 | 0.75362 | 0.75362
2020-08-25 22:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 2.1154 | 3.0514 | 3.6647 | 3.9874 | 4.633 | 5.2785 | 0.73543 | 1.9977 | 2.5056 | 2.5056 | 2.5056 | 2.5056 | 0.55252 | 0.70131 | 0.70131 | 0.70131 | 0.70131 | 0.70131
2020-08-25 23:00 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 1.8682 | 2.6948 | 3.2364 | 3.5214 | 4.0915 | 4.6615 | 0.64779 | 1.7596 | 2.207 | 2.207 | 2.207 | 2.207 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-08-26 | Winter | 0.95257 | 1.4647 | 2.2164 | 2.2164 | 2.2164 | 2.2164 | 0.51442 | 0.51442 | 0.51442 | 0.51442 | 0.51442 | 0.51442 | 1.7727 | 2.557 | 3.0709 | 3.3414 | 3.8823 | 4.4233 | 0.5792 | 1.5733 | 1.9733 | 1.9733 | 1.9733 | 1.9733 | 0.49537 | 0.62876 | 0.62876 | 0.62876 | 0.62876 | 0.62876
2020-08-26 01:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 1.6723 | 2.4123 | 2.8971 | 3.1523 | 3.6626 | 4.1729 | 0.55633 | 1.5112 | 1.8954 | 1.8954 | 1.8954 | 1.8954 | 0.49528 | 0.62864 | 0.62864 | 0.62864 | 0.62864 | 0.62864
2020-08-26 02:00 | Winter | 1.1622 | 1.787 | 2.7041 | 2.7041 | 2.7041 | 2.7041 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 1.6395 | 2.365 | 2.8403 | 3.0904 | 3.5907 | 4.091 | 0.56014 | 1.5216 | 1.9084 | 1.9084 | 1.9084 | 1.9084 | 0.49537 | 0.62876 | 0.62876 | 0.62876 | 0.62876 | 0.62876
2020-08-26 03:00 | Winter | 1.1432 | 1.7577 | 2.6598 | 2.6598 | 2.6598 | 2.6598 | 0.46869 | 0.46869 | 0.46869 | 0.46869 | 0.46869 | 0.46869 | 1.6957 | 2.446 | 2.9375 | 3.1963 | 3.7137 | 4.2311 | 0.54109 | 1.4698 | 1.8435 | 1.8435 | 1.8435 | 1.8435 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-08-26 04:00 | Winter | 1.2003 | 1.8456 | 2.7928 | 2.7928 | 2.7928 | 2.7928 | 0.48046 | 0.48046 | 0.48046 | 0.48046 | 0.48046 | 0.48046 | 1.7706 | 2.5541 | 3.0674 | 3.3376 | 3.8779 | 4.4182 | 0.56014 | 1.5216 | 1.9084 | 1.9084 | 1.9084 | 1.9084 | 0.54095 | 0.68662 | 0.68662 | 0.68662 | 0.68662 | 0.68662
2020-08-26 05:00 | Winter | 1.5294 | 2.3517 | 3.5585 | 3.5585 | 3.5585 | 3.5585 | 0.63159 | 0.63159 | 0.63159 | 0.63159 | 0.63159 | 0.63159 | 1.9815 | 2.8582 | 3.4326 | 3.735 | 4.3396 | 4.9443 | 0.69732 | 1.8942 | 2.3758 | 2.3758 | 2.3758 | 2.3758 | 0.73542 | 0.93346 | 0.93346 | 0.93346 | 0.93346 | 0.93346
2020-08-26 06:00 | Winter | 1.857 | 2.8554 | 4.3208 | 4.3208 | 4.3208 | 4.3208 | 0.7573 | 0.7573 | 0.7573 | 0.7573 | 0.7573 | 0.7573 | 2.2863 | 3.2979 | 3.9607 | 4.3096 | 5.0072 | 5.7049 | 0.72781 | 1.977 | 2.4796 | 2.4796 | 2.4796 | 2.4796 | 1.05 | 1.3328 | 1.3328 | 1.3328 | 1.3328 | 1.3328
2020-08-26 07:00 | Winter | 2.1529 | 3.3104 | 5.0093 | 5.0093 | 5.0093 | 5.0093 | 1.1832 | 1.1832 | 1.1832 | 1.1832 | 1.1832 | 1.1832 | 2.5911 | 3.7377 | 4.4888 | 4.8842 | 5.6749 | 6.4656 | 0.82307 | 2.2358 | 2.8042 | 2.8042 | 2.8042 | 2.8042 | 1.4289 | 1.8137 | 1.8137 | 1.8137 | 1.8137 | 1.8137
2020-08-26 08:00 | Winter | 2.3625 | 3.6326 | 5.4969 | 5.4969 | 5.4969 | 5.4969 | 1.3118 | 1.3118 | 1.3118 | 1.3118 | 1.3118 | 1.3118 | 2.8007 | 4.04 | 4.8519 | 5.2792 | 6.1339 | 6.9885 | 0.84974 | 2.3082 | 2.8951 | 2.8951 | 2.8951 | 2.8951 | 1.6355 | 2.0759 | 2.0759 | 2.0759 | 2.0759 | 2.0759
2020-08-26 09:00 | Winter | 2.3614 | 3.6309 | 5.4943 | 5.4943 | 5.4943 | 5.4943 | 1.2632 | 1.2632 | 1.2632 | 1.2632 | 1.2632 | 1.2632 | 2.8579 | 4.1224 | 4.9509 | 5.387 | 6.259 | 7.1311 | 0.87642 | 2.3807 | 2.986 | 2.986 | 2.986 | 2.986 | 1.6957 | 2.1523 | 2.1523 | 2.1523 | 2.1523 | 2.1523
2020-08-26 10:00 | Winter | 2.4197 | 3.7205 | 5.6299 | 5.6299 | 5.6299 | 5.6299 | 1.1746 | 1.1746 | 1.1746 | 1.1746 | 1.1746 | 1.1746 | 2.7626 | 3.985 | 4.7859 | 5.2074 | 6.0504 | 6.8934 | 0.80783 | 2.1944 | 2.7523 | 2.7523 | 2.7523 | 2.7523 | 1.6957 | 2.1523 | 2.1523 | 2.1523 | 2.1523 | 2.1523
2020-08-26 11:00 | Winter | 2.2291 | 3.4276 | 5.1866 | 5.1866 | 5.1866 | 5.1866 | 1.1031 | 1.1031 | 1.1031 | 1.1031 | 1.1031 | 1.1031 | 2.8007 | 4.04 | 4.8519 | 5.2792 | 6.1339 | 6.9885 | 0.80402 | 2.184 | 2.7393 | 2.7393 | 2.7393 | 2.7393 | 1.6385 | 2.0797 | 2.0797 | 2.0797 | 2.0797 | 2.0797
2020-08-26 12:00 | Winter | 2.191 | 3.369 | 5.0979 | 5.0979 | 5.0979 | 5.0979 | 1.1289 | 1.1289 | 1.1289 | 1.1289 | 1.1289 | 1.1289 | 2.7817 | 4.0125 | 4.8189 | 5.2433 | 6.0921 | 6.941 | 0.79258 | 2.153 | 2.7003 | 2.7003 | 2.7003 | 2.7003 | 1.5814 | 2.0072 | 2.0072 | 2.0072 | 2.0072 | 2.0072
2020-08-26 13:00 | Winter | 2.2101 | 3.3983 | 5.1423 | 5.1423 | 5.1423 | 5.1423 | 0.98311 | 0.98311 | 0.98311 | 0.98311 | 0.98311 | 0.98311 | 2.7668 | 3.991 | 4.7931 | 5.2152 | 6.0595 | 6.9038 | 0.78021 | 2.1194 | 2.6582 | 2.6582 | 2.6582 | 2.6582 | 1.5433 | 1.9588 | 1.9588 | 1.9588 | 1.9588 | 1.9588
2020-08-26 14:00 | Winter | 2.172 | 3.3397 | 5.0536 | 5.0536 | 5.0536 | 5.0536 | 1.066 | 1.066 | 1.066 | 1.066 | 1.066 | 1.066 | 2.7817 | 4.0125 | 4.8189 | 5.2433 | 6.0921 | 6.941 | 0.79258 | 2.153 | 2.7003 | 2.7003 | 2.7003 | 2.7003 | 1.467 | 1.8621 | 1.8621 | 1.8621 | 1.8621 | 1.8621
2020-08-26 15:00 | Winter | 2.191 | 3.369 | 5.0979 | 5.0979 | 5.0979 | 5.0979 | 0.95739 | 0.95739 | 0.95739 | 0.95739 | 0.95739 | 0.95739 | 2.7245 | 3.93 | 4.7199 | 5.1356 | 5.967 | 6.7984 | 0.77734 | 2.1116 | 2.6484 | 2.6484 | 2.6484 | 2.6484 | 1.3527 | 1.717 | 1.717 | 1.717 | 1.717 | 1.717
2020-08-26 16:00 | Winter | 2.1148 | 3.2518 | 4.9206 | 4.9206 | 4.9206 | 4.9206 | 0.93452 | 0.93452 | 0.93452 | 0.93452 | 0.93452 | 0.93452 | 2.6864 | 3.8751 | 4.6539 | 5.0637 | 5.8835 | 6.7033 | 0.79258 | 2.153 | 2.7003 | 2.7003 | 2.7003 | 2.7003 | 1.2578 | 1.5964 | 1.5964 | 1.5964 | 1.5964 | 1.5964
2020-08-26 17:00 | Winter | 2.0649 | 3.1751 | 4.8045 | 4.8045 | 4.8045 | 4.8045 | 0.88594 | 0.88594 | 0.88594 | 0.88594 | 0.88594 | 0.88594 | 2.6293 | 3.7926 | 4.5548 | 4.956 | 5.7583 | 6.5606 | 0.78618 | 2.1356 | 2.6785 | 2.6785 | 2.6785 | 2.6785 | 1.2765 | 1.6203 | 1.6203 | 1.6203 | 1.6203 | 1.6203
2020-08-26 18:00 | Winter | 1.5928 | 2.449 | 3.7059 | 3.7059 | 3.7059 | 3.7059 | 0.7802 | 0.7802 | 0.7802 | 0.7802 | 0.7802 | 0.7802 | 2.7055 | 3.9026 | 4.6869 | 5.0996 | 5.9252 | 6.7508 | 0.81926 | 2.2254 | 2.7912 | 2.7912 | 2.7912 | 2.7912 | 1.0294 | 1.3066 | 1.3066 | 1.3066 | 1.3066 | 1.3066
2020-08-26 19:00 | Winter | 1.2319 | 1.8941 | 2.8662 | 2.8662 | 2.8662 | 2.8662 | 0.58872 | 0.58872 | 0.58872 | 0.58872 | 0.58872 | 0.58872 | 2.5149 | 3.6277 | 4.3568 | 4.7405 | 5.508 | 6.2754 | 0.78115 | 2.1219 | 2.6614 | 2.6614 | 2.6614 | 2.6614 | 0.70494 | 0.89477 | 0.89477 | 0.89477 | 0.89477 | 0.89477
2020-08-26 20:00 | Winter | 1.1241 | 1.7284 | 2.6155 | 2.6155 | 2.6155 | 2.6155 | 0.54299 | 0.54299 | 0.54299 | 0.54299 | 0.54299 | 0.54299 | 2.4096 | 3.4758 | 4.1743 | 4.5419 | 5.2772 | 6.0125 | 0.78115 | 2.1219 | 2.6614 | 2.6614 | 2.6614 | 2.6614 | 0.62873 | 0.79804 | 0.79804 | 0.79804 | 0.79804 | 0.79804
2020-08-26 21:00 | Winter | 1.0473 | 1.6104 | 2.4369 | 2.4369 | 2.4369 | 2.4369 | 0.51727 | 0.51727 | 0.51727 | 0.51727 | 0.51727 | 0.51727 | 2.2482 | 3.243 | 3.8947 | 4.2377 | 4.9238 | 5.6098 | 0.85355 | 2.3186 | 2.9081 | 2.9081 | 2.9081 | 2.9081 | 0.59063 | 0.74967 | 0.74967 | 0.74967 | 0.74967 | 0.74967
2020-08-26 22:00 | Winter | 0.97349 | 1.4969 | 2.265 | 2.265 | 2.265 | 2.265 | 0.5087 | 0.5087 | 0.5087 | 0.5087 | 0.5087 | 0.5087 | 2.0581 | 2.9688 | 3.5654 | 3.8795 | 4.5075 | 5.1356 | 0.80402 | 2.184 | 2.7393 | 2.7393 | 2.7393 | 2.7393 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-08-26 23:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 1.8672 | 2.6933 | 3.2346 | 3.5195 | 4.0892 | 4.659 | 0.63254 | 1.7182 | 2.1551 | 2.1551 | 2.1551 | 2.1551 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-08-27 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 1.7147 | 2.4735 | 2.9705 | 3.2322 | 3.7554 | 4.2787 | 0.62111 | 1.6872 | 2.1161 | 2.1161 | 2.1161 | 2.1161 | 0.45726 | 0.58039 | 0.58039 | 0.58039 | 0.58039 | 0.58039
2020-08-27 01:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 1.6766 | 2.4185 | 2.9045 | 3.1603 | 3.672 | 4.1836 | 0.54444 | 1.4789 | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 0.45726 | 0.58039 | 0.58039 | 0.58039 | 0.58039 | 0.58039
2020-08-27 02:00 | Winter | 1.1168 | 1.7172 | 2.5985 | 2.5985 | 2.5985 | 2.5985 | 0.50013 | 0.50013 | 0.50013 | 0.50013 | 0.50013 | 0.50013 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.53728 | 1.4595 | 1.8305 | 1.8305 | 1.8305 | 1.8305 | 0.45726 | 0.58039 | 0.58039 | 0.58039 | 0.58039 | 0.58039
2020-08-27 03:00 | Winter | 1.1813 | 1.8163 | 2.7485 | 2.7485 | 2.7485 | 2.7485 | 0.47726 | 0.47726 | 0.47726 | 0.47726 | 0.47726 | 0.47726 | 1.6143 | 2.3286 | 2.7966 | 3.0429 | 3.5356 | 4.0282 | 0.58682 | 1.594 | 1.9993 | 1.9993 | 1.9993 | 1.9993 | 0.45726 | 0.58039 | 0.58039 | 0.58039 | 0.58039 | 0.58039
2020-08-27 04:00 | Winter | 1.2002 | 1.8455 | 2.7926 | 2.7926 | 2.7926 | 2.7926 | 0.48584 | 0.48584 | 0.48584 | 0.48584 | 0.48584 | 0.48584 | 1.7162 | 2.4756 | 2.9732 | 3.235 | 3.7587 | 4.2824 | 0.56395 | 1.5319 | 1.9214 | 1.9214 | 1.9214 | 1.9214 | 0.5629 | 0.71447 | 0.71447 | 0.71447 | 0.71447 | 0.71447
2020-08-27 05:00 | Winter | 1.5433 | 2.3729 | 3.5907 | 3.5907 | 3.5907 | 3.5907 | 0.68303 | 0.68303 | 0.68303 | 0.68303 | 0.68303 | 0.68303 | 1.9815 | 2.8582 | 3.4326 | 3.735 | 4.3396 | 4.9443 | 0.66303 | 1.8011 | 2.2589 | 2.2589 | 2.2589 | 2.2589 | 0.724 | 0.91895 | 0.91895 | 0.91895 | 0.91895 | 0.91895
2020-08-27 06:00 | Winter | 1.7761 | 2.7309 | 4.1324 | 4.1324 | 4.1324 | 4.1324 | 0.7459 | 0.7459 | 0.7459 | 0.7459 | 0.7459 | 0.7459 | 2.2674 | 3.2707 | 3.928 | 4.274 | 4.9659 | 5.6578 | 0.71256 | 1.9356 | 2.4277 | 2.4277 | 2.4277 | 2.4277 | 0.98991 | 1.2565 | 1.2565 | 1.2565 | 1.2565 | 1.2565
2020-08-27 07:00 | Winter | 2.2339 | 3.4349 | 5.1977 | 5.1977 | 5.1977 | 5.1977 | 1.0785 | 1.0785 | 1.0785 | 1.0785 | 1.0785 | 1.0785 | 2.5233 | 3.6398 | 4.3713 | 4.7563 | 5.5263 | 6.2963 | 0.86498 | 2.3496 | 2.947 | 2.947 | 2.947 | 2.947 | 1.3718 | 1.7412 | 1.7412 | 1.7412 | 1.7412 | 1.7412
2020-08-27 08:00 | Winter | 2.3816 | 3.6619 | 5.5412 | 5.5412 | 5.5412 | 5.5412 | 1.2918 | 1.2918 | 1.2918 | 1.2918 | 1.2918 | 1.2918 | 2.7626 | 3.985 | 4.7859 | 5.2074 | 6.0504 | 6.8934 | 0.91071 | 2.4739 | 3.1028 | 3.1028 | 3.1028 | 3.1028 | 1.6385 | 2.0797 | 2.0797 | 2.0797 | 2.0797 | 2.0797
2020-08-27 09:00 | Winter | 2.4959 | 3.8377 | 5.8072 | 5.8072 | 5.8072 | 5.8072 | 1.3032 | 1.3032 | 1.3032 | 1.3032 | 1.3032 | 1.3032 | 2.9341 | 4.2323 | 5.0829 | 5.5306 | 6.426 | 7.3213 | 0.91452 | 2.4842 | 3.1158 | 3.1158 | 3.1158 | 3.1158 | 1.6385 | 2.0797 | 2.0797 | 2.0797 | 2.0797 | 2.0797
2020-08-27 10:00 | Winter | 2.2884 | 3.5186 | 5.3244 | 5.3244 | 5.3244 | 5.3244 | 1.3032 | 1.3032 | 1.3032 | 1.3032 | 1.3032 | 1.3032 | 2.8198 | 4.0675 | 4.8849 | 5.3151 | 6.1756 | 7.0361 | 0.82307 | 2.2358 | 2.8042 | 2.8042 | 2.8042 | 2.8042 | 1.6195 | 2.0556 | 2.0556 | 2.0556 | 2.0556 | 2.0556
2020-08-27 11:00 | Winter | 2.2291 | 3.4276 | 5.1866 | 5.1866 | 5.1866 | 5.1866 | 1.0317 | 1.0317 | 1.0317 | 1.0317 | 1.0317 | 1.0317 | 2.8007 | 4.04 | 4.8519 | 5.2792 | 6.1339 | 6.9885 | 0.89166 | 2.4221 | 3.0379 | 3.0379 | 3.0379 | 3.0379 | 1.6195 | 2.0556 | 2.0556 | 2.0556 | 2.0556 | 2.0556
2020-08-27 12:00 | Winter | 2.2101 | 3.3983 | 5.1423 | 5.1423 | 5.1423 | 5.1423 | 1.0803 | 1.0803 | 1.0803 | 1.0803 | 1.0803 | 1.0803 | 2.7817 | 4.0125 | 4.8189 | 5.2433 | 6.0921 | 6.941 | 0.91833 | 2.4946 | 3.1288 | 3.1288 | 3.1288 | 3.1288 | 1.5623 | 1.983 | 1.983 | 1.983 | 1.983 | 1.983
2020-08-27 13:00 | Winter | 2.2291 | 3.4276 | 5.1866 | 5.1866 | 5.1866 | 5.1866 | 1.0145 | 1.0145 | 1.0145 | 1.0145 | 1.0145 | 1.0145 | 2.6864 | 3.8751 | 4.6539 | 5.0637 | 5.8835 | 6.7033 | 0.84974 | 2.3082 | 2.8951 | 2.8951 | 2.8951 | 2.8951 | 1.5623 | 1.983 | 1.983 | 1.983 | 1.983 | 1.983
2020-08-27 14:00 | Winter | 2.2101 | 3.3983 | 5.1423 | 5.1423 | 5.1423 | 5.1423 | 1.0117 | 1.0117 | 1.0117 | 1.0117 | 1.0117 | 1.0117 | 2.7245 | 3.93 | 4.7199 | 5.1356 | 5.967 | 6.7984 | 0.90309 | 2.4532 | 3.0768 | 3.0768 | 3.0768 | 3.0768 | 1.448 | 1.8379 | 1.8379 | 1.8379 | 1.8379 | 1.8379
2020-08-27 15:00 | Winter | 2.172 | 3.3397 | 5.0536 | 5.0536 | 5.0536 | 5.0536 | 0.96882 | 0.96882 | 0.96882 | 0.96882 | 0.96882 | 0.96882 | 2.6293 | 3.7926 | 4.5548 | 4.956 | 5.7583 | 6.5606 | 0.84974 | 2.3082 | 2.8951 | 2.8951 | 2.8951 | 2.8951 | 1.3349 | 1.6944 | 1.6944 | 1.6944 | 1.6944 | 1.6944
2020-08-27 16:00 | Winter | 2.0767 | 3.1932 | 4.832 | 4.832 | 4.832 | 4.832 | 1.0317 | 1.0317 | 1.0317 | 1.0317 | 1.0317 | 1.0317 | 2.6102 | 3.7651 | 4.5218 | 4.9201 | 5.7166 | 6.5131 | 0.84974 | 2.3082 | 2.8951 | 2.8951 | 2.8951 | 2.8951 | 1.2956 | 1.6444 | 1.6444 | 1.6444 | 1.6444 | 1.6444
2020-08-27 17:00 | Winter | 2.0005 | 3.076 | 4.6546 | 4.6546 | 4.6546 | 4.6546 | 1.0031 | 1.0031 | 1.0031 | 1.0031 | 1.0031 | 1.0031 | 2.6293 | 3.7926 | 4.5548 | 4.956 | 5.7583 | 6.5606 | 0.85355 | 2.3186 | 2.9081 | 2.9081 | 2.9081 | 2.9081 | 1.1813 | 1.4993 | 1.4993 | 1.4993 | 1.4993 | 1.4993
2020-08-27 18:00 | Winter | 1.6808 | 2.5844 | 3.9107 | 3.9107 | 3.9107 | 3.9107 | 0.88022 | 0.88022 | 0.88022 | 0.88022 | 0.88022 | 0.88022 | 2.7055 | 3.9026 | 4.6869 | 5.0996 | 5.9252 | 6.7508 | 0.89547 | 2.4325 | 3.0509 | 3.0509 | 3.0509 | 3.0509 | 0.99073 | 1.2575 | 1.2575 | 1.2575 | 1.2575 | 1.2575
2020-08-27 19:00 | Winter | 1.2384 | 1.9042 | 2.8814 | 2.8814 | 2.8814 | 2.8814 | 0.75162 | 0.75162 | 0.75162 | 0.75162 | 0.75162 | 0.75162 | 2.4908 | 3.5929 | 4.315 | 4.695 | 5.4551 | 6.2151 | 0.83831 | 2.2772 | 2.8561 | 2.8561 | 2.8561 | 2.8561 | 0.71647 | 0.9094 | 0.9094 | 0.9094 | 0.9094 | 0.9094
2020-08-27 20:00 | Winter | 1.1622 | 1.787 | 2.7041 | 2.7041 | 2.7041 | 2.7041 | 0.68017 | 0.68017 | 0.68017 | 0.68017 | 0.68017 | 0.68017 | 2.4197 | 3.4903 | 4.1918 | 4.561 | 5.2993 | 6.0377 | 0.84593 | 2.2979 | 2.8821 | 2.8821 | 2.8821 | 2.8821 | 0.64779 | 0.82222 | 0.82222 | 0.82222 | 0.82222 | 0.82222
2020-08-27 21:00 | Winter | 1.0266 | 1.5785 | 2.3886 | 2.3886 | 2.3886 | 2.3886 | 0.6373 | 0.6373 | 0.6373 | 0.6373 | 0.6373 | 0.6373 | 2.3435 | 3.3804 | 4.0597 | 4.4173 | 5.1324 | 5.8475 | 0.78496 | 2.1323 | 2.6744 | 2.6744 | 2.6744 | 2.6744 | 0.57158 | 0.72549 | 0.72549 | 0.72549 | 0.72549 | 0.72549
2020-08-27 22:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.59158 | 0.59158 | 0.59158 | 0.59158 | 0.59158 | 0.59158 | 2.1339 | 3.0781 | 3.6967 | 4.0223 | 4.6734 | 5.3246 | 0.72781 | 1.977 | 2.4796 | 2.4796 | 2.4796 | 2.4796 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-08-27 23:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 1.8862 | 2.7208 | 3.2676 | 3.5554 | 4.131 | 4.7066 | 0.65922 | 1.7907 | 2.246 | 2.246 | 2.246 | 2.246 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-08-28 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.40582 | 0.40582 | 0.40582 | 0.40582 | 0.40582 | 0.40582 | 1.7528 | 2.5284 | 3.0366 | 3.304 | 3.8389 | 4.3738 | 0.5792 | 1.5733 | 1.9733 | 1.9733 | 1.9733 | 1.9733 | 0.49537 | 0.62876 | 0.62876 | 0.62876 | 0.62876 | 0.62876
2020-08-28 01:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.39153 | 0.39153 | 0.39153 | 0.39153 | 0.39153 | 0.39153 | 1.6576 | 2.391 | 2.8715 | 3.1244 | 3.6302 | 4.1361 | 0.57157 | 1.5526 | 1.9474 | 1.9474 | 1.9474 | 1.9474 | 0.49537 | 0.62876 | 0.62876 | 0.62876 | 0.62876 | 0.62876
2020-08-28 02:00 | Winter | 1.1241 | 1.7284 | 2.6155 | 2.6155 | 2.6155 | 2.6155 | 0.40582 | 0.40582 | 0.40582 | 0.40582 | 0.40582 | 0.40582 | 1.6766 | 2.4185 | 2.9045 | 3.1603 | 3.672 | 4.1836 | 0.58301 | 1.5837 | 1.9863 | 1.9863 | 1.9863 | 1.9863 | 0.45761 | 0.58083 | 0.58083 | 0.58083 | 0.58083 | 0.58083
2020-08-28 03:00 | Winter | 1.1478 | 1.7648 | 2.6705 | 2.6705 | 2.6705 | 2.6705 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 1.6766 | 2.4185 | 2.9045 | 3.1603 | 3.672 | 4.1836 | 0.59063 | 1.6044 | 2.0123 | 2.0123 | 2.0123 | 2.0123 | 0.45726 | 0.58039 | 0.58039 | 0.58039 | 0.58039 | 0.58039
2020-08-28 04:00 | Winter | 1.1813 | 1.8163 | 2.7485 | 2.7485 | 2.7485 | 2.7485 | 0.48584 | 0.48584 | 0.48584 | 0.48584 | 0.48584 | 0.48584 | 1.7165 | 2.476 | 2.9736 | 3.2355 | 3.7592 | 4.283 | 0.64779 | 1.7596 | 2.207 | 2.207 | 2.207 | 2.207 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-08-28 05:00 | Winter | 1.5242 | 2.3436 | 3.5464 | 3.5464 | 3.5464 | 3.5464 | 0.63159 | 0.63159 | 0.63159 | 0.63159 | 0.63159 | 0.63159 | 1.8858 | 2.7202 | 3.2669 | 3.5547 | 4.1301 | 4.7056 | 0.74305 | 2.0184 | 2.5316 | 2.5316 | 2.5316 | 2.5316 | 0.74376 | 0.94404 | 0.94404 | 0.94404 | 0.94404 | 0.94404
2020-08-28 06:00 | Winter | 1.6723 | 2.5714 | 3.8911 | 3.8911 | 3.8911 | 3.8911 | 0.77162 | 0.77162 | 0.77162 | 0.77162 | 0.77162 | 0.77162 | 2.2224 | 3.2058 | 3.8501 | 4.1892 | 4.8674 | 5.5455 | 0.80021 | 2.1737 | 2.7263 | 2.7263 | 2.7263 | 2.7263 | 0.93358 | 1.185 | 1.185 | 1.185 | 1.185 | 1.185
2020-08-28 07:00 | Winter | 2.0005 | 3.076 | 4.6546 | 4.6546 | 4.6546 | 4.6546 | 0.89451 | 0.89451 | 0.89451 | 0.89451 | 0.89451 | 0.89451 | 2.4387 | 3.5178 | 4.2248 | 4.5969 | 5.3411 | 6.0852 | 0.85591 | 2.325 | 2.9161 | 2.9161 | 2.9161 | 2.9161 | 1.3337 | 1.6928 | 1.6928 | 1.6928 | 1.6928 | 1.6928
2020-08-28 08:00 | Winter | 2.191 | 3.369 | 5.0979 | 5.0979 | 5.0979 | 5.0979 | 1.0688 | 1.0688 | 1.0688 | 1.0688 | 1.0688 | 1.0688 | 2.5721 | 3.7102 | 4.4558 | 4.8483 | 5.6331 | 6.418 | 0.89928 | 2.4428 | 3.0639 | 3.0639 | 3.0639 | 3.0639 | 1.448 | 1.8379 | 1.8379 | 1.8379 | 1.8379 | 1.8379
2020-08-28 09:00 | Winter | 2.191 | 3.369 | 5.0979 | 5.0979 | 5.0979 | 5.0979 | 1.046 | 1.046 | 1.046 | 1.046 | 1.046 | 1.046 | 2.6102 | 3.7651 | 4.5218 | 4.9201 | 5.7166 | 6.5131 | 0.84974 | 2.3082 | 2.8951 | 2.8951 | 2.8951 | 2.8951 | 1.504 | 1.909 | 1.909 | 1.909 | 1.909 | 1.909
2020-08-28 10:00 | Winter | 2.172 | 3.3397 | 5.0536 | 5.0536 | 5.0536 | 5.0536 | 1.0088 | 1.0088 | 1.0088 | 1.0088 | 1.0088 | 1.0088 | 2.6483 | 3.8201 | 4.5878 | 4.9919 | 5.8 | 6.6082 | 0.89166 | 2.4221 | 3.0379 | 3.0379 | 3.0379 | 3.0379 | 1.5052 | 1.9105 | 1.9105 | 1.9105 | 1.9105 | 1.9105
2020-08-28 11:00 | Winter | 2.172 | 3.3397 | 5.0536 | 5.0536 | 5.0536 | 5.0536 | 0.98882 | 0.98882 | 0.98882 | 0.98882 | 0.98882 | 0.98882 | 2.6483 | 3.8201 | 4.5878 | 4.9919 | 5.8 | 6.6082 | 0.89166 | 2.4221 | 3.0379 | 3.0379 | 3.0379 | 3.0379 | 1.5052 | 1.9105 | 1.9105 | 1.9105 | 1.9105 | 1.9105
2020-08-28 12:00 | Winter | 2.172 | 3.3397 | 5.0536 | 5.0536 | 5.0536 | 5.0536 | 1.0574 | 1.0574 | 1.0574 | 1.0574 | 1.0574 | 1.0574 | 2.6483 | 3.8201 | 4.5878 | 4.9919 | 5.8 | 6.6082 | 0.85355 | 2.3186 | 2.9081 | 2.9081 | 2.9081 | 2.9081 | 1.448 | 1.8379 | 1.8379 | 1.8379 | 1.8379 | 1.8379
2020-08-28 13:00 | Winter | 2.0958 | 3.2225 | 4.8763 | 4.8763 | 4.8763 | 4.8763 | 1.0231 | 1.0231 | 1.0231 | 1.0231 | 1.0231 | 1.0231 | 2.6293 | 3.7926 | 4.5548 | 4.956 | 5.7583 | 6.5606 | 0.96787 | 2.6291 | 3.2975 | 3.2975 | 3.2975 | 3.2975 | 1.4099 | 1.7895 | 1.7895 | 1.7895 | 1.7895 | 1.7895
2020-08-28 14:00 | Winter | 2.0958 | 3.2225 | 4.8763 | 4.8763 | 4.8763 | 4.8763 | 0.92881 | 0.92881 | 0.92881 | 0.92881 | 0.92881 | 0.92881 | 2.7245 | 3.93 | 4.7199 | 5.1356 | 5.967 | 6.7984 | 0.89928 | 2.4428 | 3.0639 | 3.0639 | 3.0639 | 3.0639 | 1.3337 | 1.6928 | 1.6928 | 1.6928 | 1.6928 | 1.6928
2020-08-28 15:00 | Winter | 2.0577 | 3.1639 | 4.7876 | 4.7876 | 4.7876 | 4.7876 | 0.93452 | 0.93452 | 0.93452 | 0.93452 | 0.93452 | 0.93452 | 2.5911 | 3.7377 | 4.4888 | 4.8842 | 5.6749 | 6.4656 | 0.9069 | 2.4635 | 3.0898 | 3.0898 | 3.0898 | 3.0898 | 1.2575 | 1.5961 | 1.5961 | 1.5961 | 1.5961 | 1.5961
2020-08-28 16:00 | Winter | 2.0767 | 3.1932 | 4.832 | 4.832 | 4.832 | 4.832 | 0.96596 | 0.96596 | 0.96596 | 0.96596 | 0.96596 | 0.96596 | 2.5721 | 3.7102 | 4.4558 | 4.8483 | 5.6331 | 6.418 | 0.89547 | 2.4325 | 3.0509 | 3.0509 | 3.0509 | 3.0509 | 1.2575 | 1.5961 | 1.5961 | 1.5961 | 1.5961 | 1.5961
2020-08-28 17:00 | Winter | 1.9815 | 3.0467 | 4.6103 | 4.6103 | 4.6103 | 4.6103 | 0.9431 | 0.9431 | 0.9431 | 0.9431 | 0.9431 | 0.9431 | 2.5721 | 3.7102 | 4.4558 | 4.8483 | 5.6331 | 6.418 | 0.85736 | 2.3289 | 2.9211 | 2.9211 | 2.9211 | 2.9211 | 1.1539 | 1.4646 | 1.4646 | 1.4646 | 1.4646 | 1.4646
2020-08-28 18:00 | Winter | 1.7344 | 2.6668 | 4.0354 | 4.0354 | 4.0354 | 4.0354 | 0.88022 | 0.88022 | 0.88022 | 0.88022 | 0.88022 | 0.88022 | 2.6674 | 3.8476 | 4.6208 | 5.0278 | 5.8418 | 6.6557 | 0.86498 | 2.3496 | 2.947 | 2.947 | 2.947 | 2.947 | 0.88564 | 1.1241 | 1.1241 | 1.1241 | 1.1241 | 1.1241
2020-08-28 19:00 | Winter | 1.1301 | 1.7377 | 2.6295 | 2.6295 | 2.6295 | 2.6295 | 0.72876 | 0.72876 | 0.72876 | 0.72876 | 0.72876 | 0.72876 | 2.5137 | 3.6259 | 4.3546 | 4.7381 | 5.5051 | 6.2722 | 0.88404 | 2.4014 | 3.0119 | 3.0119 | 3.0119 | 3.0119 | 0.70537 | 0.89531 | 0.89531 | 0.89531 | 0.89531 | 0.89531
2020-08-28 20:00 | Winter | 1.105 | 1.6991 | 2.5711 | 2.5711 | 2.5711 | 2.5711 | 0.65159 | 0.65159 | 0.65159 | 0.65159 | 0.65159 | 0.65159 | 2.3244 | 3.3529 | 4.0267 | 4.3814 | 5.0907 | 5.8 | 0.78115 | 2.1219 | 2.6614 | 2.6614 | 2.6614 | 2.6614 | 0.62873 | 0.79804 | 0.79804 | 0.79804 | 0.79804 | 0.79804
2020-08-28 21:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 0.64302 | 0.64302 | 0.64302 | 0.64302 | 0.64302 | 0.64302 | 2.2482 | 3.243 | 3.8947 | 4.2377 | 4.9238 | 5.6098 | 0.85736 | 2.3289 | 2.9211 | 2.9211 | 2.9211 | 2.9211 | 0.57158 | 0.72549 | 0.72549 | 0.72549 | 0.72549 | 0.72549
2020-08-28 22:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.62016 | 0.62016 | 0.62016 | 0.62016 | 0.62016 | 0.62016 | 2.0386 | 2.9407 | 3.5316 | 3.8427 | 4.4648 | 5.0869 | 0.81164 | 2.2047 | 2.7653 | 2.7653 | 2.7653 | 2.7653 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-08-28 23:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.5287 | 0.5287 | 0.5287 | 0.5287 | 0.5287 | 0.5287 | 1.9243 | 2.7758 | 3.3336 | 3.6272 | 4.2144 | 4.8016 | 0.72781 | 1.977 | 2.4796 | 2.4796 | 2.4796 | 2.4796 | 0.49531 | 0.62868 | 0.62868 | 0.62868 | 0.62868 | 0.62868
2020-08-29 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 1.81 | 2.6109 | 3.1356 | 3.4117 | 3.9641 | 4.5164 | 0.63635 | 1.7286 | 2.1681 | 2.1681 | 2.1681 | 2.1681 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-08-29 01:00 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.48012 | 0.48012 | 0.48012 | 0.48012 | 0.48012 | 0.48012 | 1.7338 | 2.5009 | 3.0036 | 3.2681 | 3.7972 | 4.3262 | 0.59444 | 1.6147 | 2.0253 | 2.0253 | 2.0253 | 2.0253 | 0.49537 | 0.62876 | 0.62876 | 0.62876 | 0.62876 | 0.62876
2020-08-29 02:00 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 1.6576 | 2.391 | 2.8715 | 3.1244 | 3.6302 | 4.1361 | 0.58682 | 1.594 | 1.9993 | 1.9993 | 1.9993 | 1.9993 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-08-29 03:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 1.6575 | 2.3909 | 2.8714 | 3.1243 | 3.6301 | 4.1359 | 0.55633 | 1.5112 | 1.8954 | 1.8954 | 1.8954 | 1.8954 | 0.45446 | 0.57684 | 0.57684 | 0.57684 | 0.57684 | 0.57684
2020-08-29 04:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.48869 | 0.48869 | 0.48869 | 0.48869 | 0.48869 | 0.48869 | 1.7224 | 2.4845 | 2.9838 | 3.2466 | 3.7721 | 4.2977 | 0.59063 | 1.6044 | 2.0123 | 2.0123 | 2.0123 | 2.0123 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-08-29 05:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.563 | 0.563 | 0.563 | 0.563 | 0.563 | 0.563 | 1.7886 | 2.58 | 3.0985 | 3.3714 | 3.9172 | 4.463 | 0.58682 | 1.594 | 1.9993 | 1.9993 | 1.9993 | 1.9993 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-08-29 06:00 | Winter | 1.0288 | 1.582 | 2.3938 | 2.3938 | 2.3938 | 2.3938 | 0.58586 | 0.58586 | 0.58586 | 0.58586 | 0.58586 | 0.58586 | 1.9243 | 2.7758 | 3.3336 | 3.6272 | 4.2144 | 4.8016 | 0.63254 | 1.7182 | 2.1551 | 2.1551 | 2.1551 | 2.1551 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-08-29 07:00 | Winter | 1.0669 | 1.6405 | 2.4825 | 2.4825 | 2.4825 | 2.4825 | 0.68017 | 0.68017 | 0.68017 | 0.68017 | 0.68017 | 0.68017 | 1.979 | 2.8547 | 3.4284 | 3.7303 | 4.3342 | 4.9381 | 0.59063 | 1.6044 | 2.0123 | 2.0123 | 2.0123 | 2.0123 | 0.59063 | 0.74967 | 0.74967 | 0.74967 | 0.74967 | 0.74967
2020-08-29 08:00 | Winter | 1.086 | 1.6698 | 2.5268 | 2.5268 | 2.5268 | 2.5268 | 0.67731 | 0.67731 | 0.67731 | 0.67731 | 0.67731 | 0.67731 | 2.2482 | 3.243 | 3.8947 | 4.2377 | 4.9238 | 5.6098 | 0.64016 | 1.7389 | 2.1811 | 2.1811 | 2.1811 | 2.1811 | 0.57158 | 0.72549 | 0.72549 | 0.72549 | 0.72549 | 0.72549
2020-08-29 09:00 | Winter | 1.0288 | 1.582 | 2.3938 | 2.3938 | 2.3938 | 2.3938 | 0.65731 | 0.65731 | 0.65731 | 0.65731 | 0.65731 | 0.65731 | 2.3598 | 3.404 | 4.0881 | 4.4481 | 5.1683 | 5.8884 | 0.68589 | 1.8632 | 2.3368 | 2.3368 | 2.3368 | 2.3368 | 0.64779 | 0.82222 | 0.82222 | 0.82222 | 0.82222 | 0.82222
2020-08-29 10:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.67446 | 0.67446 | 0.67446 | 0.67446 | 0.67446 | 0.67446 | 2.3625 | 3.4079 | 4.0927 | 4.4532 | 5.1741 | 5.8951 | 0.63254 | 1.7182 | 2.1551 | 2.1551 | 2.1551 | 2.1551 | 0.68589 | 0.87059 | 0.87059 | 0.87059 | 0.87059 | 0.87059
2020-08-29 11:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.62301 | 0.62301 | 0.62301 | 0.62301 | 0.62301 | 0.62301 | 2.3054 | 3.3254 | 3.9937 | 4.3455 | 5.049 | 5.7525 | 0.65541 | 1.7803 | 2.233 | 2.233 | 2.233 | 2.233 | 0.724 | 0.91895 | 0.91895 | 0.91895 | 0.91895 | 0.91895
2020-08-29 12:00 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.57157 | 0.57157 | 0.57157 | 0.57157 | 0.57157 | 0.57157 | 2.2863 | 3.2979 | 3.9607 | 4.3096 | 5.0072 | 5.7049 | 0.6173 | 1.6768 | 2.1032 | 2.1032 | 2.1032 | 2.1032 | 0.68589 | 0.87059 | 0.87059 | 0.87059 | 0.87059 | 0.87059
2020-08-29 13:00 | Winter | 0.91452 | 1.4062 | 2.1278 | 2.1278 | 2.1278 | 2.1278 | 0.51727 | 0.51727 | 0.51727 | 0.51727 | 0.51727 | 0.51727 | 2.2863 | 3.2979 | 3.9607 | 4.3096 | 5.0072 | 5.7049 | 0.63635 | 1.7286 | 2.1681 | 2.1681 | 2.1681 | 2.1681 | 0.66684 | 0.84641 | 0.84641 | 0.84641 | 0.84641 | 0.84641
2020-08-29 14:00 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.54585 | 0.54585 | 0.54585 | 0.54585 | 0.54585 | 0.54585 | 2.2673 | 3.2705 | 3.9277 | 4.2736 | 4.9655 | 5.6574 | 0.58682 | 1.594 | 1.9993 | 1.9993 | 1.9993 | 1.9993 | 0.59063 | 0.74967 | 0.74967 | 0.74967 | 0.74967 | 0.74967
2020-08-29 15:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.51156 | 0.51156 | 0.51156 | 0.51156 | 0.51156 | 0.51156 | 2.3054 | 3.3254 | 3.9937 | 4.3455 | 5.049 | 5.7525 | 0.65541 | 1.7803 | 2.233 | 2.233 | 2.233 | 2.233 | 0.57158 | 0.72549 | 0.72549 | 0.72549 | 0.72549 | 0.72549
2020-08-29 16:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.52401 | 0.52401 | 0.52401 | 0.52401 | 0.52401 | 0.52401 | 2.3054 | 3.3254 | 3.9937 | 4.3455 | 5.049 | 5.7525 | 0.64779 | 1.7596 | 2.207 | 2.207 | 2.207 | 2.207 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-08-29 17:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.55443 | 0.55443 | 0.55443 | 0.55443 | 0.55443 | 0.55443 | 2.3054 | 3.3254 | 3.9937 | 4.3455 | 5.049 | 5.7525 | 0.77353 | 2.1012 | 2.6354 | 2.6354 | 2.6354 | 2.6354 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-08-29 18:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.59444 | 0.59444 | 0.59444 | 0.59444 | 0.59444 | 0.59444 | 2.3054 | 3.3254 | 3.9937 | 4.3455 | 5.049 | 5.7525 | 0.81926 | 2.2254 | 2.7912 | 2.7912 | 2.7912 | 2.7912 | 0.57158 | 0.72549 | 0.72549 | 0.72549 | 0.72549 | 0.72549
2020-08-29 19:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.59158 | 0.59158 | 0.59158 | 0.59158 | 0.59158 | 0.59158 | 2.3054 | 3.3254 | 3.9937 | 4.3455 | 5.049 | 5.7525 | 0.74305 | 2.0184 | 2.5316 | 2.5316 | 2.5316 | 2.5316 | 0.55252 | 0.70131 | 0.70131 | 0.70131 | 0.70131 | 0.70131
2020-08-29 20:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.57157 | 0.57157 | 0.57157 | 0.57157 | 0.57157 | 0.57157 | 2.2678 | 3.2712 | 3.9287 | 4.2747 | 4.9667 | 5.6587 | 0.74686 | 2.0288 | 2.5446 | 2.5446 | 2.5446 | 2.5446 | 0.51664 | 0.65576 | 0.65576 | 0.65576 | 0.65576 | 0.65576
2020-08-29 21:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.60015 | 0.60015 | 0.60015 | 0.60015 | 0.60015 | 0.60015 | 2.0767 | 2.9956 | 3.5977 | 3.9145 | 4.5482 | 5.182 | 0.73162 | 1.9874 | 2.4926 | 2.4926 | 2.4926 | 2.4926 | 0.55252 | 0.70131 | 0.70131 | 0.70131 | 0.70131 | 0.70131
2020-08-29 22:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.50298 | 0.50298 | 0.50298 | 0.50298 | 0.50298 | 0.50298 | 2.0767 | 2.9956 | 3.5977 | 3.9145 | 4.5482 | 5.182 | 0.72018 | 1.9563 | 2.4537 | 2.4537 | 2.4537 | 2.4537 | 0.55252 | 0.70131 | 0.70131 | 0.70131 | 0.70131 | 0.70131
2020-08-29 23:00 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.42296 | 0.42296 | 0.42296 | 0.42296 | 0.42296 | 0.42296 | 1.9624 | 2.8307 | 3.3996 | 3.699 | 4.2979 | 4.8967 | 0.66684 | 1.8114 | 2.2719 | 2.2719 | 2.2719 | 2.2719 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-08-30 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.43419 | 0.43419 | 0.43419 | 0.43419 | 0.43419 | 0.43419 | 1.7532 | 2.529 | 3.0372 | 3.3047 | 3.8397 | 4.3747 | 0.59825 | 1.6251 | 2.0382 | 2.0382 | 2.0382 | 2.0382 | 0.49537 | 0.62876 | 0.62876 | 0.62876 | 0.62876 | 0.62876
2020-08-30 01:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 1.7147 | 2.4735 | 2.9705 | 3.2322 | 3.7554 | 4.2787 | 0.58682 | 1.594 | 1.9993 | 1.9993 | 1.9993 | 1.9993 | 0.49537 | 0.62876 | 0.62876 | 0.62876 | 0.62876 | 0.62876
2020-08-30 02:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.42582 | 0.42582 | 0.42582 | 0.42582 | 0.42582 | 0.42582 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.57157 | 1.5526 | 1.9474 | 1.9474 | 1.9474 | 1.9474 | 0.47753 | 0.60612 | 0.60612 | 0.60612 | 0.60612 | 0.60612
2020-08-30 03:00 | Winter | 0.93358 | 1.4355 | 2.1722 | 2.1722 | 2.1722 | 2.1722 | 0.41153 | 0.41153 | 0.41153 | 0.41153 | 0.41153 | 0.41153 | 1.6576 | 2.391 | 2.8715 | 3.1244 | 3.6302 | 4.1361 | 0.55633 | 1.5112 | 1.8954 | 1.8954 | 1.8954 | 1.8954 | 0.49537 | 0.62876 | 0.62876 | 0.62876 | 0.62876 | 0.62876
2020-08-30 04:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.54109 | 1.4698 | 1.8435 | 1.8435 | 1.8435 | 1.8435 | 0.45814 | 0.58151 | 0.58151 | 0.58151 | 0.58151 | 0.58151
2020-08-30 05:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.49089 | 0.49089 | 0.49089 | 0.49089 | 0.49089 | 0.49089 | 1.7338 | 2.5009 | 3.0036 | 3.2681 | 3.7972 | 4.3262 | 0.56014 | 1.5216 | 1.9084 | 1.9084 | 1.9084 | 1.9084 | 0.51514 | 0.65386 | 0.65386 | 0.65386 | 0.65386 | 0.65386
2020-08-30 06:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.50298 | 0.50298 | 0.50298 | 0.50298 | 0.50298 | 0.50298 | 1.8951 | 2.7336 | 3.283 | 3.5721 | 4.1504 | 4.7287 | 0.59444 | 1.6147 | 2.0253 | 2.0253 | 2.0253 | 2.0253 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-08-30 07:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.66588 | 0.66588 | 0.66588 | 0.66588 | 0.66588 | 0.66588 | 1.9624 | 2.8307 | 3.3996 | 3.699 | 4.2979 | 4.8967 | 0.63254 | 1.7182 | 2.1551 | 2.1551 | 2.1551 | 2.1551 | 0.53314 | 0.6767 | 0.6767 | 0.6767 | 0.6767 | 0.6767
2020-08-30 08:00 | Winter | 0.91452 | 1.4062 | 2.1278 | 2.1278 | 2.1278 | 2.1278 | 0.63159 | 0.63159 | 0.63159 | 0.63159 | 0.63159 | 0.63159 | 2.172 | 3.133 | 3.7627 | 4.0941 | 4.7569 | 5.4197 | 0.70113 | 1.9046 | 2.3888 | 2.3888 | 2.3888 | 2.3888 | 0.55252 | 0.70131 | 0.70131 | 0.70131 | 0.70131 | 0.70131
2020-08-30 09:00 | Winter | 0.89547 | 1.3769 | 2.0835 | 2.0835 | 2.0835 | 2.0835 | 0.58586 | 0.58586 | 0.58586 | 0.58586 | 0.58586 | 0.58586 | 2.2673 | 3.2705 | 3.9277 | 4.2736 | 4.9655 | 5.6574 | 0.70494 | 1.9149 | 2.4018 | 2.4018 | 2.4018 | 2.4018 | 0.57158 | 0.72549 | 0.72549 | 0.72549 | 0.72549 | 0.72549
2020-08-30 10:00 | Winter | 0.88872 | 1.3665 | 2.0678 | 2.0678 | 2.0678 | 2.0678 | 0.5287 | 0.5287 | 0.5287 | 0.5287 | 0.5287 | 0.5287 | 2.191 | 3.1605 | 3.7957 | 4.13 | 4.7986 | 5.4672 | 0.64016 | 1.7389 | 2.1811 | 2.1811 | 2.1811 | 2.1811 | 0.59063 | 0.74967 | 0.74967 | 0.74967 | 0.74967 | 0.74967
2020-08-30 11:00 | Winter | 0.93358 | 1.4355 | 2.1722 | 2.1722 | 2.1722 | 2.1722 | 0.51727 | 0.51727 | 0.51727 | 0.51727 | 0.51727 | 0.51727 | 2.191 | 3.1605 | 3.7957 | 4.13 | 4.7986 | 5.4672 | 0.63254 | 1.7182 | 2.1551 | 2.1551 | 2.1551 | 2.1551 | 0.55566 | 0.70529 | 0.70529 | 0.70529 | 0.70529 | 0.70529
2020-08-30 12:00 | Winter | 0.89547 | 1.3769 | 2.0835 | 2.0835 | 2.0835 | 2.0835 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 0.40867 | 2.2291 | 3.2155 | 3.8617 | 4.2018 | 4.8821 | 5.5623 | 0.57539 | 1.563 | 1.9603 | 1.9603 | 1.9603 | 1.9603 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-08-30 13:00 | Winter | 0.8704 | 1.3383 | 2.0252 | 2.0252 | 2.0252 | 2.0252 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 2.2482 | 3.243 | 3.8947 | 4.2377 | 4.9238 | 5.6098 | 0.55252 | 1.5009 | 1.8825 | 1.8825 | 1.8825 | 1.8825 | 0.55252 | 0.70131 | 0.70131 | 0.70131 | 0.70131 | 0.70131
2020-08-30 14:00 | Winter | 0.91452 | 1.4062 | 2.1278 | 2.1278 | 2.1278 | 2.1278 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 2.2482 | 3.243 | 3.8947 | 4.2377 | 4.9238 | 5.6098 | 0.55252 | 1.5009 | 1.8825 | 1.8825 | 1.8825 | 1.8825 | 0.55252 | 0.70131 | 0.70131 | 0.70131 | 0.70131 | 0.70131
2020-08-30 15:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 2.2482 | 3.243 | 3.8947 | 4.2377 | 4.9238 | 5.6098 | 0.5449 | 1.4802 | 1.8565 | 1.8565 | 1.8565 | 1.8565 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-08-30 16:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 0.41725 | 2.191 | 3.1605 | 3.7957 | 4.13 | 4.7986 | 5.4672 | 0.59444 | 1.6147 | 2.0253 | 2.0253 | 2.0253 | 2.0253 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-08-30 17:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.48584 | 0.48584 | 0.48584 | 0.48584 | 0.48584 | 0.48584 | 2.2101 | 3.188 | 3.8287 | 4.1659 | 4.8403 | 5.5147 | 0.59444 | 1.6147 | 2.0253 | 2.0253 | 2.0253 | 2.0253 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-08-30 18:00 | Winter | 0.98987 | 1.522 | 2.3031 | 2.3031 | 2.3031 | 2.3031 | 0.50298 | 0.50298 | 0.50298 | 0.50298 | 0.50298 | 0.50298 | 2.3435 | 3.3804 | 4.0597 | 4.4173 | 5.1324 | 5.8475 | 0.67827 | 1.8425 | 2.3109 | 2.3109 | 2.3109 | 2.3109 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-08-30 19:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.48869 | 0.48869 | 0.48869 | 0.48869 | 0.48869 | 0.48869 | 2.3054 | 3.3254 | 3.9937 | 4.3455 | 5.049 | 5.7525 | 0.70875 | 1.9253 | 2.4147 | 2.4147 | 2.4147 | 2.4147 | 0.49592 | 0.62945 | 0.62945 | 0.62945 | 0.62945 | 0.62945
2020-08-30 20:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.52013 | 0.52013 | 0.52013 | 0.52013 | 0.52013 | 0.52013 | 2.1529 | 3.1056 | 3.7297 | 4.0582 | 4.7151 | 5.3721 | 0.6897 | 1.8735 | 2.3498 | 2.3498 | 2.3498 | 2.3498 | 0.51219 | 0.65011 | 0.65011 | 0.65011 | 0.65011 | 0.65011
2020-08-30 21:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.4544 | 0.4544 | 0.4544 | 0.4544 | 0.4544 | 0.4544 | 2.058 | 2.9686 | 3.5652 | 3.8792 | 4.5071 | 5.1351 | 0.65541 | 1.7803 | 2.233 | 2.233 | 2.233 | 2.233 | 0.55252 | 0.70131 | 0.70131 | 0.70131 | 0.70131 | 0.70131
2020-08-30 22:00 | Winter | 0.93358 | 1.4355 | 2.1722 | 2.1722 | 2.1722 | 2.1722 | 0.47441 | 0.47441 | 0.47441 | 0.47441 | 0.47441 | 0.47441 | 1.9631 | 2.8317 | 3.4008 | 3.7003 | 4.2994 | 4.8984 | 0.65922 | 1.7907 | 2.246 | 2.246 | 2.246 | 2.246 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-08-30 23:00 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 1.8034 | 2.6014 | 3.1242 | 3.3994 | 3.9497 | 4.5001 | 0.56776 | 1.5423 | 1.9344 | 1.9344 | 1.9344 | 1.9344 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-08-31 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 0.44297 | 1.677 | 2.4191 | 2.9052 | 3.1611 | 3.6729 | 4.1846 | 0.55252 | 1.5009 | 1.8825 | 1.8825 | 1.8825 | 1.8825 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-08-31 01:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.50299 | 1.3663 | 1.7137 | 1.7137 | 1.7137 | 1.7137 | 0.49567 | 0.62914 | 0.62914 | 0.62914 | 0.62914 | 0.62914
2020-08-31 02:00 | Winter | 1.1456 | 1.7615 | 2.6654 | 2.6654 | 2.6654 | 2.6654 | 0.4544 | 0.4544 | 0.4544 | 0.4544 | 0.4544 | 0.4544 | 1.6195 | 2.336 | 2.8055 | 3.0526 | 3.5468 | 4.041 | 0.48012 | 1.3042 | 1.6358 | 1.6358 | 1.6358 | 1.6358 | 0.47633 | 0.6046 | 0.6046 | 0.6046 | 0.6046 | 0.6046
2020-08-31 03:00 | Winter | 1.1622 | 1.787 | 2.7041 | 2.7041 | 2.7041 | 2.7041 | 0.43439 | 0.43439 | 0.43439 | 0.43439 | 0.43439 | 0.43439 | 1.5433 | 2.2261 | 2.6735 | 2.909 | 3.3799 | 3.8508 | 0.51061 | 1.387 | 1.7396 | 1.7396 | 1.7396 | 1.7396 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-08-31 04:00 | Winter | 1.2003 | 1.8456 | 2.7928 | 2.7928 | 2.7928 | 2.7928 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 1.6383 | 2.3631 | 2.8381 | 3.088 | 3.5879 | 4.0879 | 0.49155 | 1.3353 | 1.6747 | 1.6747 | 1.6747 | 1.6747 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-08-31 05:00 | Winter | 1.295 | 1.9912 | 3.0131 | 3.0131 | 3.0131 | 3.0131 | 0.57157 | 0.57157 | 0.57157 | 0.57157 | 0.57157 | 0.57157 | 1.8285 | 2.6376 | 3.1677 | 3.4467 | 4.0046 | 4.5626 | 0.61349 | 1.6665 | 2.0902 | 2.0902 | 2.0902 | 2.0902 | 0.8066 | 1.0238 | 1.0238 | 1.0238 | 1.0238 | 1.0238
2020-08-31 06:00 | Winter | 1.649 | 2.5355 | 3.8367 | 3.8367 | 3.8367 | 3.8367 | 0.74876 | 0.74876 | 0.74876 | 0.74876 | 0.74876 | 0.74876 | 2.1933 | 3.1638 | 3.7996 | 4.1342 | 4.8035 | 5.4728 | 0.67065 | 1.8218 | 2.2849 | 2.2849 | 2.2849 | 2.2849 | 1.0391 | 1.3189 | 1.3189 | 1.3189 | 1.3189 | 1.3189
2020-08-31 07:00 | Winter | 2.0456 | 3.1454 | 4.7596 | 4.7596 | 4.7596 | 4.7596 | 0.9088 | 0.9088 | 0.9088 | 0.9088 | 0.9088 | 0.9088 | 2.3816 | 3.4353 | 4.1258 | 4.4891 | 5.2159 | 5.9426 | 0.78496 | 2.1323 | 2.6744 | 2.6744 | 2.6744 | 2.6744 | 1.3337 | 1.6928 | 1.6928 | 1.6928 | 1.6928 | 1.6928
2020-08-31 08:00 | Winter | 2.191 | 3.369 | 5.0979 | 5.0979 | 5.0979 | 5.0979 | 0.98311 | 0.98311 | 0.98311 | 0.98311 | 0.98311 | 0.98311 | 2.5721 | 3.7102 | 4.4558 | 4.8483 | 5.6331 | 6.418 | 0.84593 | 2.2979 | 2.8821 | 2.8821 | 2.8821 | 2.8821 | 1.4861 | 1.8863 | 1.8863 | 1.8863 | 1.8863 | 1.8863
2020-08-31 09:00 | Winter | 2.3054 | 3.5448 | 5.3639 | 5.3639 | 5.3639 | 5.3639 | 0.97228 | 0.97228 | 0.97228 | 0.97228 | 0.97228 | 0.97228 | 2.5752 | 3.7147 | 4.4613 | 4.8542 | 5.64 | 6.4259 | 0.85355 | 2.3186 | 2.9081 | 2.9081 | 2.9081 | 2.9081 | 1.467 | 1.8621 | 1.8621 | 1.8621 | 1.8621 | 1.8621
2020-08-31 10:00 | Winter | 2.172 | 3.3397 | 5.0536 | 5.0536 | 5.0536 | 5.0536 | 0.95453 | 0.95453 | 0.95453 | 0.95453 | 0.95453 | 0.95453 | 2.5911 | 3.7377 | 4.4888 | 4.8842 | 5.6749 | 6.4656 | 0.79258 | 2.153 | 2.7003 | 2.7003 | 2.7003 | 2.7003 | 1.467 | 1.8621 | 1.8621 | 1.8621 | 1.8621 | 1.8621
2020-08-31 11:00 | Winter | 2.1148 | 3.2518 | 4.9206 | 4.9206 | 4.9206 | 4.9206 | 1.0031 | 1.0031 | 1.0031 | 1.0031 | 1.0031 | 1.0031 | 2.5721 | 3.7102 | 4.4558 | 4.8483 | 5.6331 | 6.418 | 0.77353 | 2.1012 | 2.6354 | 2.6354 | 2.6354 | 2.6354 | 1.448 | 1.8379 | 1.8379 | 1.8379 | 1.8379 | 1.8379
2020-08-31 12:00 | Winter | 2.1339 | 3.2811 | 4.9649 | 4.9649 | 4.9649 | 4.9649 | 0.94596 | 0.94596 | 0.94596 | 0.94596 | 0.94596 | 0.94596 | 2.6483 | 3.8201 | 4.5878 | 4.9919 | 5.8 | 6.6082 | 0.77353 | 2.1012 | 2.6354 | 2.6354 | 2.6354 | 2.6354 | 1.4029 | 1.7807 | 1.7807 | 1.7807 | 1.7807 | 1.7807
2020-08-31 13:00 | Winter | 2.1529 | 3.3104 | 5.0093 | 5.0093 | 5.0093 | 5.0093 | 0.92023 | 0.92023 | 0.92023 | 0.92023 | 0.92023 | 0.92023 | 2.5721 | 3.7102 | 4.4558 | 4.8483 | 5.6331 | 6.418 | 0.81164 | 2.2047 | 2.7653 | 2.7653 | 2.7653 | 2.7653 | 1.4099 | 1.7895 | 1.7895 | 1.7895 | 1.7895 | 1.7895
2020-08-31 14:00 | Winter | 2.2101 | 3.3983 | 5.1423 | 5.1423 | 5.1423 | 5.1423 | 0.84593 | 0.84593 | 0.84593 | 0.84593 | 0.84593 | 0.84593 | 2.4959 | 3.6002 | 4.3238 | 4.7046 | 5.4662 | 6.2279 | 0.75767 | 2.0581 | 2.5814 | 2.5814 | 2.5814 | 2.5814 | 1.3146 | 1.6686 | 1.6686 | 1.6686 | 1.6686 | 1.6686
2020-08-31 15:00 | Winter | 2.0196 | 3.1053 | 4.699 | 4.699 | 4.699 | 4.699 | 0.86022 | 0.86022 | 0.86022 | 0.86022 | 0.86022 | 0.86022 | 2.534 | 3.6552 | 4.3898 | 4.7764 | 5.5497 | 6.3229 | 0.83069 | 2.2565 | 2.8302 | 2.8302 | 2.8302 | 2.8302 | 1.2575 | 1.5961 | 1.5961 | 1.5961 | 1.5961 | 1.5961
2020-08-31 16:00 | Winter | 2.0577 | 3.1639 | 4.7876 | 4.7876 | 4.7876 | 4.7876 | 0.89166 | 0.89166 | 0.89166 | 0.89166 | 0.89166 | 0.89166 | 2.5149 | 3.6277 | 4.3568 | 4.7405 | 5.508 | 6.2754 | 0.76272 | 2.0719 | 2.5986 | 2.5986 | 2.5986 | 2.5986 | 1.2384 | 1.5719 | 1.5719 | 1.5719 | 1.5719 | 1.5719
2020-08-31 17:00 | Winter | 2.0005 | 3.076 | 4.6546 | 4.6546 | 4.6546 | 4.6546 | 0.90023 | 0.90023 | 0.90023 | 0.90023 | 0.90023 | 0.90023 | 2.4768 | 3.5728 | 4.2908 | 4.6687 | 5.4245 | 6.1803 | 0.75448 | 2.0495 | 2.5705 | 2.5705 | 2.5705 | 2.5705 | 1.1622 | 1.4752 | 1.4752 | 1.4752 | 1.4752 | 1.4752
2020-08-31 18:00 | Winter | 1.7258 | 2.6537 | 4.0155 | 4.0155 | 4.0155 | 4.0155 | 0.87451 | 0.87451 | 0.87451 | 0.87451 | 0.87451 | 0.87451 | 2.534 | 3.6552 | 4.3898 | 4.7764 | 5.5497 | 6.3229 | 0.73543 | 1.9977 | 2.5056 | 2.5056 | 2.5056 | 2.5056 | 0.87164 | 1.1064 | 1.1064 | 1.1064 | 1.1064 | 1.1064
2020-08-31 19:00 | Winter | 1.1754 | 1.8073 | 2.7349 | 2.7349 | 2.7349 | 2.7349 | 0.6916 | 0.6916 | 0.6916 | 0.6916 | 0.6916 | 0.6916 | 2.4784 | 3.575 | 4.2934 | 4.6716 | 5.4278 | 6.1841 | 0.71256 | 1.9356 | 2.4277 | 2.4277 | 2.4277 | 2.4277 | 0.64779 | 0.82222 | 0.82222 | 0.82222 | 0.82222 | 0.82222
2020-08-31 20:00 | Winter | 1.0481 | 1.6116 | 2.4387 | 2.4387 | 2.4387 | 2.4387 | 0.58872 | 0.58872 | 0.58872 | 0.58872 | 0.58872 | 0.58872 | 2.2291 | 3.2155 | 3.8617 | 4.2018 | 4.8821 | 5.5623 | 0.62873 | 1.7079 | 2.1421 | 2.1421 | 2.1421 | 2.1421 | 0.59076 | 0.74984 | 0.74984 | 0.74984 | 0.74984 | 0.74984
2020-08-31 21:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.51727 | 0.51727 | 0.51727 | 0.51727 | 0.51727 | 0.51727 | 2.1148 | 3.0506 | 3.6637 | 3.9863 | 4.6317 | 5.277 | 0.67446 | 1.8321 | 2.2979 | 2.2979 | 2.2979 | 2.2979 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-08-31 22:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 2.001 | 2.8863 | 3.4664 | 3.7717 | 4.3823 | 4.9929 | 0.65922 | 1.7907 | 2.246 | 2.246 | 2.246 | 2.246 | 0.49537 | 0.62876 | 0.62876 | 0.62876 | 0.62876 | 0.62876
2020-08-31 23:00 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 0.45154 | 1.8335 | 2.6448 | 3.1764 | 3.4561 | 4.0156 | 4.5751 | 0.54109 | 1.4698 | 1.8435 | 1.8435 | 1.8435 | 1.8435 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-09-01 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 1.6766 | 2.4185 | 2.9045 | 3.1603 | 3.672 | 4.1836 | 0.59825 | 1.6251 | 2.0382 | 2.0382 | 2.0382 | 2.0382 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-09-01 01:00 | Winter | 0.91452 | 1.4062 | 2.1278 | 2.1278 | 2.1278 | 2.1278 | 0.43154 | 0.43154 | 0.43154 | 0.43154 | 0.43154 | 0.43154 | 1.5814 | 2.2811 | 2.7395 | 2.9808 | 3.4633 | 3.9459 | 0.53728 | 1.4595 | 1.8305 | 1.8305 | 1.8305 | 1.8305 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-09-01 02:00 | Winter | 1.086 | 1.6698 | 2.5268 | 2.5268 | 2.5268 | 2.5268 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 1.5814 | 2.2811 | 2.7395 | 2.9808 | 3.4633 | 3.9459 | 0.52585 | 1.4284 | 1.7916 | 1.7916 | 1.7916 | 1.7916 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-09-01 03:00 | Winter | 1.086 | 1.6698 | 2.5268 | 2.5268 | 2.5268 | 2.5268 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 1.5623 | 2.2536 | 2.7065 | 2.9449 | 3.4216 | 3.8984 | 0.54109 | 1.4698 | 1.8435 | 1.8435 | 1.8435 | 1.8435 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-09-01 04:00 | Winter | 1.1432 | 1.7577 | 2.6598 | 2.6598 | 2.6598 | 2.6598 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 1.6193 | 2.3357 | 2.8051 | 3.0522 | 3.5463 | 4.0404 | 0.52966 | 1.4388 | 1.8046 | 1.8046 | 1.8046 | 1.8046 | 0.55252 | 0.70131 | 0.70131 | 0.70131 | 0.70131 | 0.70131
2020-09-01 05:00 | Winter | 1.4023 | 2.1561 | 3.2627 | 3.2627 | 3.2627 | 3.2627 | 0.51637 | 0.51637 | 0.51637 | 0.51637 | 0.51637 | 0.51637 | 1.821 | 2.6268 | 3.1547 | 3.4325 | 3.9882 | 4.5439 | 0.67446 | 1.8321 | 2.2979 | 2.2979 | 2.2979 | 2.2979 | 0.78115 | 0.9915 | 0.9915 | 0.9915 | 0.9915 | 0.9915
2020-09-01 06:00 | Winter | 1.6116 | 2.478 | 3.7497 | 3.7497 | 3.7497 | 3.7497 | 0.70018 | 0.70018 | 0.70018 | 0.70018 | 0.70018 | 0.70018 | 2.0196 | 2.9132 | 3.4986 | 3.8068 | 4.4231 | 5.0393 | 0.68208 | 1.8528 | 2.3239 | 2.3239 | 2.3239 | 2.3239 | 1.0019 | 1.2716 | 1.2716 | 1.2716 | 1.2716 | 1.2716
2020-09-01 07:00 | Winter | 1.9815 | 3.0467 | 4.6103 | 4.6103 | 4.6103 | 4.6103 | 0.84879 | 0.84879 | 0.84879 | 0.84879 | 0.84879 | 0.84879 | 2.3595 | 3.4035 | 4.0875 | 4.4475 | 5.1675 | 5.8875 | 0.85736 | 2.3289 | 2.9211 | 2.9211 | 2.9211 | 2.9211 | 1.2851 | 1.6311 | 1.6311 | 1.6311 | 1.6311 | 1.6311
2020-09-01 08:00 | Winter | 2.2673 | 3.4862 | 5.2753 | 5.2753 | 5.2753 | 5.2753 | 0.9631 | 0.9631 | 0.9631 | 0.9631 | 0.9631 | 0.9631 | 2.5432 | 3.6684 | 4.4057 | 4.7937 | 5.5698 | 6.3458 | 0.88023 | 2.3911 | 2.9989 | 2.9989 | 2.9989 | 2.9989 | 1.3718 | 1.7412 | 1.7412 | 1.7412 | 1.7412 | 1.7412
2020-09-01 09:00 | Winter | 2.2101 | 3.3983 | 5.1423 | 5.1423 | 5.1423 | 5.1423 | 1.026 | 1.026 | 1.026 | 1.026 | 1.026 | 1.026 | 2.6674 | 3.8476 | 4.6208 | 5.0278 | 5.8418 | 6.6557 | 0.87261 | 2.3704 | 2.973 | 2.973 | 2.973 | 2.973 | 1.448 | 1.8379 | 1.8379 | 1.8379 | 1.8379 | 1.8379
2020-09-01 10:00 | Winter | 2.172 | 3.3397 | 5.0536 | 5.0536 | 5.0536 | 5.0536 | 0.99454 | 0.99454 | 0.99454 | 0.99454 | 0.99454 | 0.99454 | 2.7055 | 3.9026 | 4.6869 | 5.0996 | 5.9252 | 6.7508 | 0.81926 | 2.2254 | 2.7912 | 2.7912 | 2.7912 | 2.7912 | 1.448 | 1.8379 | 1.8379 | 1.8379 | 1.8379 | 1.8379
2020-09-01 11:00 | Winter | 2.191 | 3.369 | 5.0979 | 5.0979 | 5.0979 | 5.0979 | 0.96882 | 0.96882 | 0.96882 | 0.96882 | 0.96882 | 0.96882 | 2.6489 | 3.821 | 4.5889 | 4.9931 | 5.8014 | 6.6097 | 0.82307 | 2.2358 | 2.8042 | 2.8042 | 2.8042 | 2.8042 | 1.5433 | 1.9588 | 1.9588 | 1.9588 | 1.9588 | 1.9588
2020-09-01 12:00 | Winter | 2.2291 | 3.4276 | 5.1866 | 5.1866 | 5.1866 | 5.1866 | 0.93738 | 0.93738 | 0.93738 | 0.93738 | 0.93738 | 0.93738 | 2.6674 | 3.8476 | 4.6208 | 5.0278 | 5.8418 | 6.6557 | 0.86879 | 2.36 | 2.96 | 2.96 | 2.96 | 2.96 | 1.467 | 1.8621 | 1.8621 | 1.8621 | 1.8621 | 1.8621
2020-09-01 13:00 | Winter | 2.1148 | 3.2518 | 4.9206 | 4.9206 | 4.9206 | 4.9206 | 0.86308 | 0.86308 | 0.86308 | 0.86308 | 0.86308 | 0.86308 | 2.6293 | 3.7926 | 4.5548 | 4.956 | 5.7583 | 6.5606 | 0.74686 | 2.0288 | 2.5446 | 2.5446 | 2.5446 | 2.5446 | 1.4861 | 1.8863 | 1.8863 | 1.8863 | 1.8863 | 1.8863
2020-09-01 14:00 | Winter | 2.1529 | 3.3104 | 5.0093 | 5.0093 | 5.0093 | 5.0093 | 0.86594 | 0.86594 | 0.86594 | 0.86594 | 0.86594 | 0.86594 | 2.534 | 3.6552 | 4.3898 | 4.7764 | 5.5497 | 6.3229 | 0.76972 | 2.0909 | 2.6225 | 2.6225 | 2.6225 | 2.6225 | 1.3527 | 1.717 | 1.717 | 1.717 | 1.717 | 1.717
2020-09-01 15:00 | Winter | 2.0767 | 3.1932 | 4.832 | 4.832 | 4.832 | 4.832 | 0.89166 | 0.89166 | 0.89166 | 0.89166 | 0.89166 | 0.89166 | 2.4959 | 3.6002 | 4.3238 | 4.7046 | 5.4662 | 6.2279 | 0.76972 | 2.0909 | 2.6225 | 2.6225 | 2.6225 | 2.6225 | 1.333 | 1.6919 | 1.6919 | 1.6919 | 1.6919 | 1.6919
2020-09-01 16:00 | Winter | 2.0958 | 3.2225 | 4.8763 | 4.8763 | 4.8763 | 4.8763 | 0.93167 | 0.93167 | 0.93167 | 0.93167 | 0.93167 | 0.93167 | 2.4768 | 3.5728 | 4.2908 | 4.6687 | 5.4245 | 6.1803 | 0.78115 | 2.1219 | 2.6614 | 2.6614 | 2.6614 | 2.6614 | 1.2003 | 1.5235 | 1.5235 | 1.5235 | 1.5235 | 1.5235
2020-09-01 17:00 | Winter | 1.9815 | 3.0467 | 4.6103 | 4.6103 | 4.6103 | 4.6103 | 0.86022 | 0.86022 | 0.86022 | 0.86022 | 0.86022 | 0.86022 | 2.4578 | 3.5453 | 4.2578 | 4.6328 | 5.3828 | 6.1328 | 0.76972 | 2.0909 | 2.6225 | 2.6225 | 2.6225 | 2.6225 | 1.1433 | 1.4511 | 1.4511 | 1.4511 | 1.4511 | 1.4511
2020-09-01 18:00 | Winter | 1.6371 | 2.5173 | 3.8092 | 3.8092 | 3.8092 | 3.8092 | 0.74019 | 0.74019 | 0.74019 | 0.74019 | 0.74019 | 0.74019 | 2.553 | 3.6827 | 4.4228 | 4.8123 | 5.5914 | 6.3705 | 0.78496 | 2.1323 | 2.6744 | 2.6744 | 2.6744 | 2.6744 | 0.9354 | 1.1873 | 1.1873 | 1.1873 | 1.1873 | 1.1873
2020-09-01 19:00 | Winter | 1.2194 | 1.8749 | 2.8371 | 2.8371 | 2.8371 | 2.8371 | 0.62301 | 0.62301 | 0.62301 | 0.62301 | 0.62301 | 0.62301 | 2.5043 | 3.6124 | 4.3384 | 4.7205 | 5.4848 | 6.249 | 0.74305 | 2.0184 | 2.5316 | 2.5316 | 2.5316 | 2.5316 | 0.67506 | 0.85684 | 0.85684 | 0.85684 | 0.85684 | 0.85684
2020-09-01 20:00 | Winter | 1.1042 | 1.6979 | 2.5692 | 2.5692 | 2.5692 | 2.5692 | 0.55443 | 0.55443 | 0.55443 | 0.55443 | 0.55443 | 0.55443 | 2.3054 | 3.3254 | 3.9937 | 4.3455 | 5.049 | 5.7525 | 0.70494 | 1.9149 | 2.4018 | 2.4018 | 2.4018 | 2.4018 | 0.60968 | 0.77386 | 0.77386 | 0.77386 | 0.77386 | 0.77386
2020-09-01 21:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.50584 | 0.50584 | 0.50584 | 0.50584 | 0.50584 | 0.50584 | 2.1968 | 3.1688 | 3.8056 | 4.1408 | 4.8112 | 5.4815 | 0.64016 | 1.7389 | 2.1811 | 2.1811 | 2.1811 | 2.1811 | 0.55252 | 0.70131 | 0.70131 | 0.70131 | 0.70131 | 0.70131
2020-09-01 22:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.45972 | 0.45972 | 0.45972 | 0.45972 | 0.45972 | 0.45972 | 1.9532 | 2.8174 | 3.3836 | 3.6816 | 4.2776 | 4.8736 | 0.70494 | 1.9149 | 2.4018 | 2.4018 | 2.4018 | 2.4018 | 0.49537 | 0.62876 | 0.62876 | 0.62876 | 0.62876 | 0.62876
2020-09-01 23:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 1.7481 | 2.5216 | 3.0284 | 3.2951 | 3.8286 | 4.362 | 0.54871 | 1.4905 | 1.8695 | 1.8695 | 1.8695 | 1.8695 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-09-02 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.48584 | 0.48584 | 0.48584 | 0.48584 | 0.48584 | 0.48584 | 1.6578 | 2.3913 | 2.8718 | 3.1248 | 3.6307 | 4.1365 | 0.5449 | 1.4802 | 1.8565 | 1.8565 | 1.8565 | 1.8565 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-09-02 01:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 1.6195 | 2.336 | 2.8055 | 3.0526 | 3.5468 | 4.041 | 0.52204 | 1.4181 | 1.7786 | 1.7786 | 1.7786 | 1.7786 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-09-02 02:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 1.5624 | 2.2537 | 2.7067 | 2.9451 | 3.4218 | 3.8986 | 0.51442 | 1.3974 | 1.7526 | 1.7526 | 1.7526 | 1.7526 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-09-02 03:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 0.42011 | 1.6766 | 2.4185 | 2.9045 | 3.1603 | 3.672 | 4.1836 | 0.51061 | 1.387 | 1.7396 | 1.7396 | 1.7396 | 1.7396 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-09-02 04:00 | Winter | 1.1813 | 1.8163 | 2.7485 | 2.7485 | 2.7485 | 2.7485 | 0.52585 | 0.52585 | 0.52585 | 0.52585 | 0.52585 | 0.52585 | 1.6766 | 2.4185 | 2.9045 | 3.1603 | 3.672 | 4.1836 | 0.50299 | 1.3663 | 1.7137 | 1.7137 | 1.7137 | 1.7137 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-09-02 05:00 | Winter | 1.2803 | 1.9687 | 2.979 | 2.979 | 2.979 | 2.979 | 0.65159 | 0.65159 | 0.65159 | 0.65159 | 0.65159 | 0.65159 | 1.8481 | 2.6658 | 3.2016 | 3.4836 | 4.0475 | 4.6115 | 0.6173 | 1.6768 | 2.1032 | 2.1032 | 2.1032 | 2.1032 | 0.7615 | 0.96655 | 0.96655 | 0.96655 | 0.96655 | 0.96655
2020-09-02 06:00 | Winter | 1.5185 | 2.3349 | 3.5332 | 3.5332 | 3.5332 | 3.5332 | 0.68589 | 0.68589 | 0.68589 | 0.68589 | 0.68589 | 0.68589 | 2.1772 | 3.1406 | 3.7718 | 4.104 | 4.7684 | 5.4328 | 0.70875 | 1.9253 | 2.4147 | 2.4147 | 2.4147 | 2.4147 | 1.0546 | 1.3386 | 1.3386 | 1.3386 | 1.3386 | 1.3386
2020-09-02 07:00 | Winter | 2.0176 | 3.1024 | 4.6945 | 4.6945 | 4.6945 | 4.6945 | 0.89451 | 0.89451 | 0.89451 | 0.89451 | 0.89451 | 0.89451 | 2.4197 | 3.4903 | 4.1918 | 4.561 | 5.2993 | 6.0377 | 0.7964 | 2.1633 | 2.7133 | 2.7133 | 2.7133 | 2.7133 | 1.3337 | 1.6928 | 1.6928 | 1.6928 | 1.6928 | 1.6928
2020-09-02 08:00 | Winter | 2.3244 | 3.5741 | 5.4082 | 5.4082 | 5.4082 | 5.4082 | 0.96025 | 0.96025 | 0.96025 | 0.96025 | 0.96025 | 0.96025 | 2.6674 | 3.8476 | 4.6208 | 5.0278 | 5.8418 | 6.6557 | 0.81164 | 2.2047 | 2.7653 | 2.7653 | 2.7653 | 2.7653 | 1.448 | 1.8379 | 1.8379 | 1.8379 | 1.8379 | 1.8379
2020-09-02 09:00 | Winter | 2.1529 | 3.3104 | 5.0093 | 5.0093 | 5.0093 | 5.0093 | 0.96596 | 0.96596 | 0.96596 | 0.96596 | 0.96596 | 0.96596 | 2.7245 | 3.93 | 4.7199 | 5.1356 | 5.967 | 6.7984 | 0.82688 | 2.2461 | 2.8172 | 2.8172 | 2.8172 | 2.8172 | 1.5433 | 1.9588 | 1.9588 | 1.9588 | 1.9588 | 1.9588
2020-09-02 10:00 | Winter | 2.3244 | 3.5741 | 5.4082 | 5.4082 | 5.4082 | 5.4082 | 0.96596 | 0.96596 | 0.96596 | 0.96596 | 0.96596 | 0.96596 | 2.7055 | 3.9026 | 4.6869 | 5.0996 | 5.9252 | 6.7508 | 0.77734 | 2.1116 | 2.6484 | 2.6484 | 2.6484 | 2.6484 | 1.4289 | 1.8137 | 1.8137 | 1.8137 | 1.8137 | 1.8137
2020-09-02 11:00 | Winter | 2.2482 | 3.4569 | 5.2309 | 5.2309 | 5.2309 | 5.2309 | 0.92881 | 0.92881 | 0.92881 | 0.92881 | 0.92881 | 0.92881 | 2.7055 | 3.9026 | 4.6869 | 5.0996 | 5.9252 | 6.7508 | 0.71256 | 1.9356 | 2.4277 | 2.4277 | 2.4277 | 2.4277 | 1.467 | 1.8621 | 1.8621 | 1.8621 | 1.8621 | 1.8621
2020-09-02 12:00 | Winter | 2.2673 | 3.4862 | 5.2753 | 5.2753 | 5.2753 | 5.2753 | 0.96025 | 0.96025 | 0.96025 | 0.96025 | 0.96025 | 0.96025 | 2.6674 | 3.8476 | 4.6208 | 5.0278 | 5.8418 | 6.6557 | 0.71256 | 1.9356 | 2.4277 | 2.4277 | 2.4277 | 2.4277 | 1.448 | 1.8379 | 1.8379 | 1.8379 | 1.8379 | 1.8379
2020-09-02 13:00 | Winter | 2.2101 | 3.3983 | 5.1423 | 5.1423 | 5.1423 | 5.1423 | 0.87165 | 0.87165 | 0.87165 | 0.87165 | 0.87165 | 0.87165 | 2.6483 | 3.8201 | 4.5878 | 4.9919 | 5.8 | 6.6082 | 0.73162 | 1.9874 | 2.4926 | 2.4926 | 2.4926 | 2.4926 | 1.3718 | 1.7412 | 1.7412 | 1.7412 | 1.7412 | 1.7412
2020-09-02 14:00 | Winter | 2.2291 | 3.4276 | 5.1866 | 5.1866 | 5.1866 | 5.1866 | 0.94024 | 0.94024 | 0.94024 | 0.94024 | 0.94024 | 0.94024 | 2.6102 | 3.7651 | 4.5218 | 4.9201 | 5.7166 | 6.5131 | 0.70494 | 1.9149 | 2.4018 | 2.4018 | 2.4018 | 2.4018 | 1.3527 | 1.717 | 1.717 | 1.717 | 1.717 | 1.717
2020-09-02 15:00 | Winter | 2.172 | 3.3397 | 5.0536 | 5.0536 | 5.0536 | 5.0536 | 0.86308 | 0.86308 | 0.86308 | 0.86308 | 0.86308 | 0.86308 | 2.4959 | 3.6002 | 4.3238 | 4.7046 | 5.4662 | 6.2279 | 0.83831 | 2.2772 | 2.8561 | 2.8561 | 2.8561 | 2.8561 | 1.2384 | 1.5719 | 1.5719 | 1.5719 | 1.5719 | 1.5719
2020-09-02 16:00 | Winter | 2.1555 | 3.3144 | 5.0153 | 5.0153 | 5.0153 | 5.0153 | 0.88022 | 0.88022 | 0.88022 | 0.88022 | 0.88022 | 0.88022 | 2.5149 | 3.6277 | 4.3568 | 4.7405 | 5.508 | 6.2754 | 0.78877 | 2.1426 | 2.6874 | 2.6874 | 2.6874 | 2.6874 | 1.1622 | 1.4752 | 1.4752 | 1.4752 | 1.4752 | 1.4752
2020-09-02 17:00 | Winter | 2.0577 | 3.1639 | 4.7876 | 4.7876 | 4.7876 | 4.7876 | 0.92023 | 0.92023 | 0.92023 | 0.92023 | 0.92023 | 0.92023 | 2.4387 | 3.5178 | 4.2248 | 4.5969 | 5.3411 | 6.0852 | 0.69732 | 1.8942 | 2.3758 | 2.3758 | 2.3758 | 2.3758 | 1.1432 | 1.451 | 1.451 | 1.451 | 1.451 | 1.451
2020-09-02 18:00 | Winter | 1.7342 | 2.6666 | 4.035 | 4.035 | 4.035 | 4.035 | 0.74305 | 0.74305 | 0.74305 | 0.74305 | 0.74305 | 0.74305 | 2.534 | 3.6552 | 4.3898 | 4.7764 | 5.5497 | 6.3229 | 0.78115 | 2.1219 | 2.6614 | 2.6614 | 2.6614 | 2.6614 | 0.9528 | 1.2094 | 1.2094 | 1.2094 | 1.2094 | 1.2094
2020-09-02 19:00 | Winter | 1.1411 | 1.7546 | 2.6551 | 2.6551 | 2.6551 | 2.6551 | 0.66588 | 0.66588 | 0.66588 | 0.66588 | 0.66588 | 0.66588 | 2.4166 | 3.4859 | 4.1864 | 4.5552 | 5.2926 | 6.03 | 0.72781 | 1.977 | 2.4796 | 2.4796 | 2.4796 | 2.4796 | 0.6915 | 0.87771 | 0.87771 | 0.87771 | 0.87771 | 0.87771
2020-09-02 20:00 | Winter | 1.086 | 1.6698 | 2.5268 | 2.5268 | 2.5268 | 2.5268 | 0.59444 | 0.59444 | 0.59444 | 0.59444 | 0.59444 | 0.59444 | 2.2863 | 3.2979 | 3.9607 | 4.3096 | 5.0072 | 5.7049 | 0.71637 | 1.946 | 2.4407 | 2.4407 | 2.4407 | 2.4407 | 0.62873 | 0.79804 | 0.79804 | 0.79804 | 0.79804 | 0.79804
2020-09-02 21:00 | Winter | 1.0288 | 1.582 | 2.3938 | 2.3938 | 2.3938 | 2.3938 | 0.52585 | 0.52585 | 0.52585 | 0.52585 | 0.52585 | 0.52585 | 2.0783 | 2.9979 | 3.6004 | 3.9175 | 4.5518 | 5.186 | 0.74305 | 2.0184 | 2.5316 | 2.5316 | 2.5316 | 2.5316 | 0.55252 | 0.70131 | 0.70131 | 0.70131 | 0.70131 | 0.70131
2020-09-02 22:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 1.9624 | 2.8307 | 3.3996 | 3.699 | 4.2979 | 4.8967 | 0.64779 | 1.7596 | 2.207 | 2.207 | 2.207 | 2.207 | 0.49537 | 0.62876 | 0.62876 | 0.62876 | 0.62876 | 0.62876
2020-09-02 23:00 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 0.44011 | 1.7903 | 2.5825 | 3.1015 | 3.3747 | 3.921 | 4.4674 | 0.5852 | 1.5897 | 1.9938 | 1.9938 | 1.9938 | 1.9938 | 0.49537 | 0.62876 | 0.62876 | 0.62876 | 0.62876 | 0.62876
2020-09-03 | Winter | 0.93358 | 1.4355 | 2.1722 | 2.1722 | 2.1722 | 2.1722 | 0.43154 | 0.43154 | 0.43154 | 0.43154 | 0.43154 | 0.43154 | 1.7147 | 2.4735 | 2.9705 | 3.2322 | 3.7554 | 4.2787 | 0.52585 | 1.4284 | 1.7916 | 1.7916 | 1.7916 | 1.7916 | 0.43833 | 0.55636 | 0.55636 | 0.55636 | 0.55636 | 0.55636
2020-09-03 01:00 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 0.43725 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.52966 | 1.4388 | 1.8046 | 1.8046 | 1.8046 | 1.8046 | 0.45726 | 0.58039 | 0.58039 | 0.58039 | 0.58039 | 0.58039
2020-09-03 02:00 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.51061 | 1.387 | 1.7396 | 1.7396 | 1.7396 | 1.7396 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-09-03 03:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 0.44868 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.55252 | 1.5009 | 1.8825 | 1.8825 | 1.8825 | 1.8825 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-09-03 04:00 | Winter | 1.1622 | 1.787 | 2.7041 | 2.7041 | 2.7041 | 2.7041 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 1.6462 | 2.3746 | 2.8518 | 3.103 | 3.6054 | 4.1077 | 0.51442 | 1.3974 | 1.7526 | 1.7526 | 1.7526 | 1.7526 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-09-03 05:00 | Winter | 1.2592 | 1.9362 | 2.9299 | 2.9299 | 2.9299 | 2.9299 | 0.51156 | 0.51156 | 0.51156 | 0.51156 | 0.51156 | 0.51156 | 1.853 | 2.6728 | 3.21 | 3.4927 | 4.0582 | 4.6236 | 0.63635 | 1.7286 | 2.1681 | 2.1681 | 2.1681 | 2.1681 | 0.76523 | 0.97129 | 0.97129 | 0.97129 | 0.97129 | 0.97129
2020-09-03 06:00 | Winter | 1.4052 | 2.1607 | 3.2696 | 3.2696 | 3.2696 | 3.2696 | 0.73447 | 0.73447 | 0.73447 | 0.73447 | 0.73447 | 0.73447 | 2.0386 | 2.9407 | 3.5316 | 3.8427 | 4.4648 | 5.0869 | 0.70113 | 1.9046 | 2.3888 | 2.3888 | 2.3888 | 2.3888 | 0.93865 | 1.1914 | 1.1914 | 1.1914 | 1.1914 | 1.1914
2020-09-03 07:00 | Winter | 1.9426 | 2.9869 | 4.5198 | 4.5198 | 4.5198 | 4.5198 | 0.81735 | 0.81735 | 0.81735 | 0.81735 | 0.81735 | 0.81735 | 2.3625 | 3.4079 | 4.0927 | 4.4532 | 5.1741 | 5.8951 | 0.81926 | 2.2254 | 2.7912 | 2.7912 | 2.7912 | 2.7912 | 1.2384 | 1.5719 | 1.5719 | 1.5719 | 1.5719 | 1.5719
2020-09-03 08:00 | Winter | 2.2291 | 3.4276 | 5.1866 | 5.1866 | 5.1866 | 5.1866 | 0.88594 | 0.88594 | 0.88594 | 0.88594 | 0.88594 | 0.88594 | 2.4768 | 3.5728 | 4.2908 | 4.6687 | 5.4245 | 6.1803 | 0.84212 | 2.2875 | 2.8691 | 2.8691 | 2.8691 | 2.8691 | 1.3146 | 1.6686 | 1.6686 | 1.6686 | 1.6686 | 1.6686
2020-09-03 09:00 | Winter | 2.1403 | 3.2909 | 4.9798 | 4.9798 | 4.9798 | 4.9798 | 0.93167 | 0.93167 | 0.93167 | 0.93167 | 0.93167 | 0.93167 | 2.553 | 3.6827 | 4.4228 | 4.8123 | 5.5914 | 6.3705 | 0.78877 | 2.1426 | 2.6874 | 2.6874 | 2.6874 | 2.6874 | 1.3337 | 1.6928 | 1.6928 | 1.6928 | 1.6928 | 1.6928
2020-09-03 10:00 | Winter | 2.191 | 3.369 | 5.0979 | 5.0979 | 5.0979 | 5.0979 | 0.84021 | 0.84021 | 0.84021 | 0.84021 | 0.84021 | 0.84021 | 2.5911 | 3.7377 | 4.4888 | 4.8842 | 5.6749 | 6.4656 | 0.78496 | 2.1323 | 2.6744 | 2.6744 | 2.6744 | 2.6744 | 1.3527 | 1.717 | 1.717 | 1.717 | 1.717 | 1.717
2020-09-03 11:00 | Winter | 2.172 | 3.3397 | 5.0536 | 5.0536 | 5.0536 | 5.0536 | 0.87165 | 0.87165 | 0.87165 | 0.87165 | 0.87165 | 0.87165 | 2.6102 | 3.7651 | 4.5218 | 4.9201 | 5.7166 | 6.5131 | 0.75448 | 2.0495 | 2.5705 | 2.5705 | 2.5705 | 2.5705 | 1.3337 | 1.6928 | 1.6928 | 1.6928 | 1.6928 | 1.6928
2020-09-03 12:00 | Winter | 2.172 | 3.3397 | 5.0536 | 5.0536 | 5.0536 | 5.0536 | 0.82878 | 0.82878 | 0.82878 | 0.82878 | 0.82878 | 0.82878 | 2.6674 | 3.8476 | 4.6208 | 5.0278 | 5.8418 | 6.6557 | 0.75448 | 2.0495 | 2.5705 | 2.5705 | 2.5705 | 2.5705 | 1.3337 | 1.6928 | 1.6928 | 1.6928 | 1.6928 | 1.6928
2020-09-03 13:00 | Winter | 2.191 | 3.369 | 5.0979 | 5.0979 | 5.0979 | 5.0979 | 0.80592 | 0.80592 | 0.80592 | 0.80592 | 0.80592 | 0.80592 | 2.553 | 3.6827 | 4.4228 | 4.8123 | 5.5914 | 6.3705 | 0.87642 | 2.3807 | 2.986 | 2.986 | 2.986 | 2.986 | 1.3908 | 1.7654 | 1.7654 | 1.7654 | 1.7654 | 1.7654
2020-09-03 14:00 | Winter | 2.2101 | 3.3983 | 5.1423 | 5.1423 | 5.1423 | 5.1423 | 0.89737 | 0.89737 | 0.89737 | 0.89737 | 0.89737 | 0.89737 | 2.553 | 3.6827 | 4.4228 | 4.8123 | 5.5914 | 6.3705 | 0.78115 | 2.1219 | 2.6614 | 2.6614 | 2.6614 | 2.6614 | 1.3146 | 1.6686 | 1.6686 | 1.6686 | 1.6686 | 1.6686
2020-09-03 15:00 | Winter | 2.191 | 3.369 | 5.0979 | 5.0979 | 5.0979 | 5.0979 | 0.88022 | 0.88022 | 0.88022 | 0.88022 | 0.88022 | 0.88022 | 2.5149 | 3.6277 | 4.3568 | 4.7405 | 5.508 | 6.2754 | 0.80402 | 2.184 | 2.7393 | 2.7393 | 2.7393 | 2.7393 | 1.265 | 1.6057 | 1.6057 | 1.6057 | 1.6057 | 1.6057
2020-09-03 16:00 | Winter | 2.191 | 3.369 | 5.0979 | 5.0979 | 5.0979 | 5.0979 | 0.82878 | 0.82878 | 0.82878 | 0.82878 | 0.82878 | 0.82878 | 2.4197 | 3.4903 | 4.1918 | 4.561 | 5.2993 | 6.0377 | 0.81545 | 2.2151 | 2.7782 | 2.7782 | 2.7782 | 2.7782 | 1.1622 | 1.4752 | 1.4752 | 1.4752 | 1.4752 | 1.4752
2020-09-03 17:00 | Winter | 2.0196 | 3.1053 | 4.699 | 4.699 | 4.699 | 4.699 | 0.87165 | 0.87165 | 0.87165 | 0.87165 | 0.87165 | 0.87165 | 2.4387 | 3.5178 | 4.2248 | 4.5969 | 5.3411 | 6.0852 | 0.76972 | 2.0909 | 2.6225 | 2.6225 | 2.6225 | 2.6225 | 1.086 | 1.3784 | 1.3784 | 1.3784 | 1.3784 | 1.3784
2020-09-03 18:00 | Winter | 1.5761 | 2.4234 | 3.667 | 3.667 | 3.667 | 3.667 | 0.82307 | 0.82307 | 0.82307 | 0.82307 | 0.82307 | 0.82307 | 2.4006 | 3.4628 | 4.1588 | 4.525 | 5.2576 | 5.9902 | 0.83069 | 2.2565 | 2.8302 | 2.8302 | 2.8302 | 2.8302 | 0.88071 | 1.1179 | 1.1179 | 1.1179 | 1.1179 | 1.1179
2020-09-03 19:00 | Winter | 1.1241 | 1.7284 | 2.6155 | 2.6155 | 2.6155 | 2.6155 | 0.7459 | 0.7459 | 0.7459 | 0.7459 | 0.7459 | 0.7459 | 2.3484 | 3.3875 | 4.0683 | 4.4266 | 5.1432 | 5.8599 | 0.80021 | 2.1737 | 2.7263 | 2.7263 | 2.7263 | 2.7263 | 0.70494 | 0.89477 | 0.89477 | 0.89477 | 0.89477 | 0.89477
2020-09-03 20:00 | Winter | 1.105 | 1.6991 | 2.5711 | 2.5711 | 2.5711 | 2.5711 | 0.64302 | 0.64302 | 0.64302 | 0.64302 | 0.64302 | 0.64302 | 2.1824 | 3.148 | 3.7807 | 4.1137 | 4.7796 | 5.4456 | 0.71256 | 1.9356 | 2.4277 | 2.4277 | 2.4277 | 2.4277 | 0.59099 | 0.75013 | 0.75013 | 0.75013 | 0.75013 | 0.75013
2020-09-03 21:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.60873 | 0.60873 | 0.60873 | 0.60873 | 0.60873 | 0.60873 | 2.0767 | 2.9956 | 3.5977 | 3.9145 | 4.5482 | 5.182 | 0.6897 | 1.8735 | 2.3498 | 2.3498 | 2.3498 | 2.3498 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-09-03 22:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 1.9624 | 2.8307 | 3.3996 | 3.699 | 4.2979 | 4.8967 | 0.70113 | 1.9046 | 2.3888 | 2.3888 | 2.3888 | 2.3888 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-09-03 23:00 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.47726 | 0.47726 | 0.47726 | 0.47726 | 0.47726 | 0.47726 | 1.8724 | 2.7009 | 3.2437 | 3.5294 | 4.1007 | 4.6721 | 0.60587 | 1.6458 | 2.0642 | 2.0642 | 2.0642 | 2.0642 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-09-04 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 1.6957 | 2.446 | 2.9375 | 3.1963 | 3.7137 | 4.2311 | 0.53728 | 1.4595 | 1.8305 | 1.8305 | 1.8305 | 1.8305 | 0.45759 | 0.58081 | 0.58081 | 0.58081 | 0.58081 | 0.58081
2020-09-04 01:00 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 0.46583 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.53347 | 1.4491 | 1.8175 | 1.8175 | 1.8175 | 1.8175 | 0.45726 | 0.58039 | 0.58039 | 0.58039 | 0.58039 | 0.58039
2020-09-04 02:00 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 0.46297 | 1.6576 | 2.391 | 2.8715 | 3.1244 | 3.6302 | 4.1361 | 0.52204 | 1.4181 | 1.7786 | 1.7786 | 1.7786 | 1.7786 | 0.45726 | 0.58039 | 0.58039 | 0.58039 | 0.58039 | 0.58039
2020-09-04 03:00 | Winter | 0.97466 | 1.4986 | 2.2678 | 2.2678 | 2.2678 | 2.2678 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 0.45726 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.51061 | 1.387 | 1.7396 | 1.7396 | 1.7396 | 1.7396 | 0.49537 | 0.62876 | 0.62876 | 0.62876 | 0.62876 | 0.62876
2020-09-04 04:00 | Winter | 1.1813 | 1.8163 | 2.7485 | 2.7485 | 2.7485 | 2.7485 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.52585 | 1.4284 | 1.7916 | 1.7916 | 1.7916 | 1.7916 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-09-04 05:00 | Winter | 1.2575 | 1.9335 | 2.9258 | 2.9258 | 2.9258 | 2.9258 | 0.57443 | 0.57443 | 0.57443 | 0.57443 | 0.57443 | 0.57443 | 1.8672 | 2.6933 | 3.2346 | 3.5195 | 4.0892 | 4.659 | 0.63254 | 1.7182 | 2.1551 | 2.1551 | 2.1551 | 2.1551 | 0.67111 | 0.85183 | 0.85183 | 0.85183 | 0.85183 | 0.85183
2020-09-04 06:00 | Winter | 1.3267 | 2.04 | 3.0869 | 3.0869 | 3.0869 | 3.0869 | 0.7259 | 0.7259 | 0.7259 | 0.7259 | 0.7259 | 0.7259 | 1.9815 | 2.8582 | 3.4326 | 3.735 | 4.3396 | 4.9443 | 0.66303 | 1.8011 | 2.2589 | 2.2589 | 2.2589 | 2.2589 | 0.88792 | 1.127 | 1.127 | 1.127 | 1.127 | 1.127
2020-09-04 07:00 | Winter | 1.7719 | 2.7245 | 4.1227 | 4.1227 | 4.1227 | 4.1227 | 0.85736 | 0.85736 | 0.85736 | 0.85736 | 0.85736 | 0.85736 | 2.2614 | 3.262 | 3.9176 | 4.2626 | 4.9527 | 5.6428 | 0.83069 | 2.2565 | 2.8302 | 2.8302 | 2.8302 | 2.8302 | 1.105 | 1.4026 | 1.4026 | 1.4026 | 1.4026 | 1.4026
2020-09-04 08:00 | Winter | 2.0577 | 3.1639 | 4.7876 | 4.7876 | 4.7876 | 4.7876 | 0.88022 | 0.88022 | 0.88022 | 0.88022 | 0.88022 | 0.88022 | 2.4387 | 3.5178 | 4.2248 | 4.5969 | 5.3411 | 6.0852 | 0.8345 | 2.2668 | 2.8432 | 2.8432 | 2.8432 | 2.8432 | 1.2194 | 1.5477 | 1.5477 | 1.5477 | 1.5477 | 1.5477
2020-09-04 09:00 | Winter | 2.0577 | 3.1639 | 4.7876 | 4.7876 | 4.7876 | 4.7876 | 0.96882 | 0.96882 | 0.96882 | 0.96882 | 0.96882 | 0.96882 | 2.534 | 3.6552 | 4.3898 | 4.7764 | 5.5497 | 6.3229 | 0.86498 | 2.3496 | 2.947 | 2.947 | 2.947 | 2.947 | 1.3006 | 1.6508 | 1.6508 | 1.6508 | 1.6508 | 1.6508
2020-09-04 10:00 | Winter | 2.1148 | 3.2518 | 4.9206 | 4.9206 | 4.9206 | 4.9206 | 0.87737 | 0.87737 | 0.87737 | 0.87737 | 0.87737 | 0.87737 | 2.6102 | 3.7651 | 4.5218 | 4.9201 | 5.7166 | 6.5131 | 0.78496 | 2.1323 | 2.6744 | 2.6744 | 2.6744 | 2.6744 | 1.3337 | 1.6928 | 1.6928 | 1.6928 | 1.6928 | 1.6928
2020-09-04 11:00 | Winter | 2.0386 | 3.1346 | 4.7433 | 4.7433 | 4.7433 | 4.7433 | 0.8888 | 0.8888 | 0.8888 | 0.8888 | 0.8888 | 0.8888 | 2.5911 | 3.7377 | 4.4888 | 4.8842 | 5.6749 | 6.4656 | 0.75448 | 2.0495 | 2.5705 | 2.5705 | 2.5705 | 2.5705 | 1.3718 | 1.7412 | 1.7412 | 1.7412 | 1.7412 | 1.7412
2020-09-04 12:00 | Winter | 2.0577 | 3.1639 | 4.7876 | 4.7876 | 4.7876 | 4.7876 | 0.84307 | 0.84307 | 0.84307 | 0.84307 | 0.84307 | 0.84307 | 2.5911 | 3.7377 | 4.4888 | 4.8842 | 5.6749 | 6.4656 | 0.76972 | 2.0909 | 2.6225 | 2.6225 | 2.6225 | 2.6225 | 1.2765 | 1.6203 | 1.6203 | 1.6203 | 1.6203 | 1.6203
2020-09-04 13:00 | Winter | 2.1148 | 3.2518 | 4.9206 | 4.9206 | 4.9206 | 4.9206 | 0.78591 | 0.78591 | 0.78591 | 0.78591 | 0.78591 | 0.78591 | 2.4959 | 3.6002 | 4.3238 | 4.7046 | 5.4662 | 6.2279 | 0.75067 | 2.0391 | 2.5575 | 2.5575 | 2.5575 | 2.5575 | 1.2575 | 1.5961 | 1.5961 | 1.5961 | 1.5961 | 1.5961
2020-09-04 14:00 | Winter | 2.1148 | 3.2518 | 4.9206 | 4.9206 | 4.9206 | 4.9206 | 0.78877 | 0.78877 | 0.78877 | 0.78877 | 0.78877 | 0.78877 | 2.4768 | 3.5728 | 4.2908 | 4.6687 | 5.4245 | 6.1803 | 0.73543 | 1.9977 | 2.5056 | 2.5056 | 2.5056 | 2.5056 | 1.2384 | 1.5719 | 1.5719 | 1.5719 | 1.5719 | 1.5719
2020-09-04 15:00 | Winter | 2.0386 | 3.1346 | 4.7433 | 4.7433 | 4.7433 | 4.7433 | 0.76305 | 0.76305 | 0.76305 | 0.76305 | 0.76305 | 0.76305 | 2.4387 | 3.5178 | 4.2248 | 4.5969 | 5.3411 | 6.0852 | 0.78496 | 2.1323 | 2.6744 | 2.6744 | 2.6744 | 2.6744 | 1.1622 | 1.4752 | 1.4752 | 1.4752 | 1.4752 | 1.4752
2020-09-04 16:00 | Winter | 1.9434 | 2.9881 | 4.5216 | 4.5216 | 4.5216 | 4.5216 | 0.87165 | 0.87165 | 0.87165 | 0.87165 | 0.87165 | 0.87165 | 2.4387 | 3.5178 | 4.2248 | 4.5969 | 5.3411 | 6.0852 | 0.74305 | 2.0184 | 2.5316 | 2.5316 | 2.5316 | 2.5316 | 1.1622 | 1.4752 | 1.4752 | 1.4752 | 1.4752 | 1.4752
2020-09-04 17:00 | Winter | 1.829 | 2.8124 | 4.2557 | 4.2557 | 4.2557 | 4.2557 | 0.87165 | 0.87165 | 0.87165 | 0.87165 | 0.87165 | 0.87165 | 2.4006 | 3.4628 | 4.1588 | 4.525 | 5.2576 | 5.9902 | 0.78877 | 2.1426 | 2.6874 | 2.6874 | 2.6874 | 2.6874 | 1.105 | 1.4026 | 1.4026 | 1.4026 | 1.4026 | 1.4026
2020-09-04 18:00 | Winter | 1.6577 | 2.549 | 3.8571 | 3.8571 | 3.8571 | 3.8571 | 0.71447 | 0.71447 | 0.71447 | 0.71447 | 0.71447 | 0.71447 | 2.3244 | 3.3529 | 4.0267 | 4.3814 | 5.0907 | 5.8 | 0.84593 | 2.2979 | 2.8821 | 2.8821 | 2.8821 | 2.8821 | 0.8119 | 1.0305 | 1.0305 | 1.0305 | 1.0305 | 1.0305
2020-09-04 19:00 | Winter | 1.105 | 1.6991 | 2.5711 | 2.5711 | 2.5711 | 2.5711 | 0.66127 | 0.66127 | 0.66127 | 0.66127 | 0.66127 | 0.66127 | 2.2101 | 3.188 | 3.8287 | 4.1659 | 4.8403 | 5.5147 | 0.75829 | 2.0598 | 2.5835 | 2.5835 | 2.5835 | 2.5835 | 0.66684 | 0.84641 | 0.84641 | 0.84641 | 0.84641 | 0.84641
2020-09-04 20:00 | Winter | 1.0288 | 1.582 | 2.3938 | 2.3938 | 2.3938 | 2.3938 | 0.65731 | 0.65731 | 0.65731 | 0.65731 | 0.65731 | 0.65731 | 2.1529 | 3.1056 | 3.7297 | 4.0582 | 4.7151 | 5.3721 | 0.75067 | 2.0391 | 2.5575 | 2.5575 | 2.5575 | 2.5575 | 0.62873 | 0.79804 | 0.79804 | 0.79804 | 0.79804 | 0.79804
2020-09-04 21:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.58015 | 0.58015 | 0.58015 | 0.58015 | 0.58015 | 0.58015 | 2.0767 | 2.9956 | 3.5977 | 3.9145 | 4.5482 | 5.182 | 0.76972 | 2.0909 | 2.6225 | 2.6225 | 2.6225 | 2.6225 | 0.57158 | 0.72549 | 0.72549 | 0.72549 | 0.72549 | 0.72549
2020-09-04 22:00 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.53728 | 0.53728 | 0.53728 | 0.53728 | 0.53728 | 0.53728 | 1.9434 | 2.8032 | 3.3666 | 3.6631 | 4.2562 | 4.8492 | 0.73162 | 1.9874 | 2.4926 | 2.4926 | 2.4926 | 2.4926 | 0.53377 | 0.6775 | 0.6775 | 0.6775 | 0.6775 | 0.6775
2020-09-04 23:00 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 0.42868 | 1.8293 | 2.6387 | 3.1689 | 3.448 | 4.0062 | 4.5645 | 0.62873 | 1.7079 | 2.1421 | 2.1421 | 2.1421 | 2.1421 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-09-05 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.48584 | 0.48584 | 0.48584 | 0.48584 | 0.48584 | 0.48584 | 1.6957 | 2.446 | 2.9375 | 3.1963 | 3.7137 | 4.2311 | 0.5449 | 1.4802 | 1.8565 | 1.8565 | 1.8565 | 1.8565 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-09-05 01:00 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.47441 | 0.47441 | 0.47441 | 0.47441 | 0.47441 | 0.47441 | 1.6576 | 2.391 | 2.8715 | 3.1244 | 3.6302 | 4.1361 | 0.51442 | 1.3974 | 1.7526 | 1.7526 | 1.7526 | 1.7526 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-09-05 02:00 | Winter | 0.93358 | 1.4355 | 2.1722 | 2.1722 | 2.1722 | 2.1722 | 0.47441 | 0.47441 | 0.47441 | 0.47441 | 0.47441 | 0.47441 | 1.6195 | 2.336 | 2.8055 | 3.0526 | 3.5468 | 4.041 | 0.54109 | 1.4698 | 1.8435 | 1.8435 | 1.8435 | 1.8435 | 0.49537 | 0.62876 | 0.62876 | 0.62876 | 0.62876 | 0.62876
2020-09-05 03:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.47726 | 0.47726 | 0.47726 | 0.47726 | 0.47726 | 0.47726 | 1.6195 | 2.336 | 2.8055 | 3.0526 | 3.5468 | 4.041 | 0.5068 | 1.3767 | 1.7267 | 1.7267 | 1.7267 | 1.7267 | 0.45726 | 0.58039 | 0.58039 | 0.58039 | 0.58039 | 0.58039
2020-09-05 04:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 0.47155 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.56395 | 1.5319 | 1.9214 | 1.9214 | 1.9214 | 1.9214 | 0.45726 | 0.58039 | 0.58039 | 0.58039 | 0.58039 | 0.58039
2020-09-05 05:00 | Winter | 0.96184 | 1.4789 | 2.2379 | 2.2379 | 2.2379 | 2.2379 | 0.49155 | 0.49155 | 0.49155 | 0.49155 | 0.49155 | 0.49155 | 1.8085 | 2.6087 | 3.1329 | 3.4089 | 3.9607 | 4.5126 | 0.54871 | 1.4905 | 1.8695 | 1.8695 | 1.8695 | 1.8695 | 0.45726 | 0.58039 | 0.58039 | 0.58039 | 0.58039 | 0.58039
2020-09-05 06:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.54585 | 0.54585 | 0.54585 | 0.54585 | 0.54585 | 0.54585 | 1.8662 | 2.6919 | 3.2329 | 3.5177 | 4.0872 | 4.6566 | 0.55252 | 1.5009 | 1.8825 | 1.8825 | 1.8825 | 1.8825 | 0.50514 | 0.64117 | 0.64117 | 0.64117 | 0.64117 | 0.64117
2020-09-05 07:00 | Winter | 1.0288 | 1.582 | 2.3938 | 2.3938 | 2.3938 | 2.3938 | 0.61158 | 0.61158 | 0.61158 | 0.61158 | 0.61158 | 0.61158 | 1.9494 | 2.812 | 3.3771 | 3.6745 | 4.2694 | 4.8643 | 0.64779 | 1.7596 | 2.207 | 2.207 | 2.207 | 2.207 | 0.55252 | 0.70131 | 0.70131 | 0.70131 | 0.70131 | 0.70131
2020-09-05 08:00 | Winter | 1.0669 | 1.6405 | 2.4825 | 2.4825 | 2.4825 | 2.4825 | 0.64016 | 0.64016 | 0.64016 | 0.64016 | 0.64016 | 0.64016 | 2.0958 | 3.0231 | 3.6307 | 3.9504 | 4.59 | 5.2295 | 0.66684 | 1.8114 | 2.2719 | 2.2719 | 2.2719 | 2.2719 | 0.55252 | 0.70131 | 0.70131 | 0.70131 | 0.70131 | 0.70131
2020-09-05 09:00 | Winter | 1.0188 | 1.5665 | 2.3704 | 2.3704 | 2.3704 | 2.3704 | 0.66303 | 0.66303 | 0.66303 | 0.66303 | 0.66303 | 0.66303 | 2.1148 | 3.0506 | 3.6637 | 3.9863 | 4.6317 | 5.277 | 0.70875 | 1.9253 | 2.4147 | 2.4147 | 2.4147 | 2.4147 | 0.60968 | 0.77386 | 0.77386 | 0.77386 | 0.77386 | 0.77386
2020-09-05 10:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.66017 | 0.66017 | 0.66017 | 0.66017 | 0.66017 | 0.66017 | 2.0958 | 3.0231 | 3.6307 | 3.9504 | 4.59 | 5.2295 | 0.6516 | 1.77 | 2.22 | 2.22 | 2.22 | 2.22 | 0.62873 | 0.79804 | 0.79804 | 0.79804 | 0.79804 | 0.79804
2020-09-05 11:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.62016 | 0.62016 | 0.62016 | 0.62016 | 0.62016 | 0.62016 | 2.1339 | 3.0781 | 3.6967 | 4.0223 | 4.6734 | 5.3246 | 0.65922 | 1.7907 | 2.246 | 2.246 | 2.246 | 2.246 | 0.64779 | 0.82222 | 0.82222 | 0.82222 | 0.82222 | 0.82222
2020-09-05 12:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.64016 | 0.64016 | 0.64016 | 0.64016 | 0.64016 | 0.64016 | 2.1339 | 3.0781 | 3.6967 | 4.0223 | 4.6734 | 5.3246 | 0.5792 | 1.5733 | 1.9733 | 1.9733 | 1.9733 | 1.9733 | 0.64779 | 0.82222 | 0.82222 | 0.82222 | 0.82222 | 0.82222
2020-09-05 13:00 | Winter | 0.90567 | 1.3926 | 2.1072 | 2.1072 | 2.1072 | 2.1072 | 0.60015 | 0.60015 | 0.60015 | 0.60015 | 0.60015 | 0.60015 | 2.172 | 3.133 | 3.7627 | 4.0941 | 4.7569 | 5.4197 | 0.59825 | 1.6251 | 2.0382 | 2.0382 | 2.0382 | 2.0382 | 0.62873 | 0.79804 | 0.79804 | 0.79804 | 0.79804 | 0.79804
2020-09-05 14:00 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.61158 | 0.61158 | 0.61158 | 0.61158 | 0.61158 | 0.61158 | 2.2101 | 3.188 | 3.8287 | 4.1659 | 4.8403 | 5.5147 | 0.59063 | 1.6044 | 2.0123 | 2.0123 | 2.0123 | 2.0123 | 0.55252 | 0.70131 | 0.70131 | 0.70131 | 0.70131 | 0.70131
2020-09-05 15:00 | Winter | 0.91452 | 1.4062 | 2.1278 | 2.1278 | 2.1278 | 2.1278 | 0.64016 | 0.64016 | 0.64016 | 0.64016 | 0.64016 | 0.64016 | 2.1148 | 3.0506 | 3.6637 | 3.9863 | 4.6317 | 5.277 | 0.61349 | 1.6665 | 2.0902 | 2.0902 | 2.0902 | 2.0902 | 0.55252 | 0.70131 | 0.70131 | 0.70131 | 0.70131 | 0.70131
2020-09-05 16:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.62016 | 0.62016 | 0.62016 | 0.62016 | 0.62016 | 0.62016 | 2.191 | 3.1605 | 3.7957 | 4.13 | 4.7986 | 5.4672 | 0.6516 | 1.77 | 2.22 | 2.22 | 2.22 | 2.22 | 0.60968 | 0.77386 | 0.77386 | 0.77386 | 0.77386 | 0.77386
2020-09-05 17:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.58586 | 0.58586 | 0.58586 | 0.58586 | 0.58586 | 0.58586 | 2.191 | 3.1605 | 3.7957 | 4.13 | 4.7986 | 5.4672 | 0.67827 | 1.8425 | 2.3109 | 2.3109 | 2.3109 | 2.3109 | 0.56376 | 0.71557 | 0.71557 | 0.71557 | 0.71557 | 0.71557
2020-09-05 18:00 | Winter | 0.95282 | 1.4651 | 2.2169 | 2.2169 | 2.2169 | 2.2169 | 0.6373 | 0.6373 | 0.6373 | 0.6373 | 0.6373 | 0.6373 | 2.2101 | 3.188 | 3.8287 | 4.1659 | 4.8403 | 5.5147 | 0.76591 | 2.0805 | 2.6095 | 2.6095 | 2.6095 | 2.6095 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-09-05 19:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.6173 | 0.6173 | 0.6173 | 0.6173 | 0.6173 | 0.6173 | 2.191 | 3.1605 | 3.7957 | 4.13 | 4.7986 | 5.4672 | 0.73924 | 2.0081 | 2.5186 | 2.5186 | 2.5186 | 2.5186 | 0.55252 | 0.70131 | 0.70131 | 0.70131 | 0.70131 | 0.70131
2020-09-05 20:00 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.64588 | 0.64588 | 0.64588 | 0.64588 | 0.64588 | 0.64588 | 2.0767 | 2.9956 | 3.5977 | 3.9145 | 4.5482 | 5.182 | 0.724 | 1.9667 | 2.4667 | 2.4667 | 2.4667 | 2.4667 | 0.58685 | 0.74487 | 0.74487 | 0.74487 | 0.74487 | 0.74487
2020-09-05 21:00 | Winter | 0.93358 | 1.4355 | 2.1722 | 2.1722 | 2.1722 | 2.1722 | 0.56149 | 0.56149 | 0.56149 | 0.56149 | 0.56149 | 0.56149 | 2.0389 | 2.9411 | 3.5321 | 3.8432 | 4.4654 | 5.0876 | 0.73142 | 1.9868 | 2.4919 | 2.4919 | 2.4919 | 2.4919 | 0.59063 | 0.74967 | 0.74967 | 0.74967 | 0.74967 | 0.74967
2020-09-05 22:00 | Winter | 0.93358 | 1.4355 | 2.1722 | 2.1722 | 2.1722 | 2.1722 | 0.52299 | 0.52299 | 0.52299 | 0.52299 | 0.52299 | 0.52299 | 2.0005 | 2.8857 | 3.4656 | 3.7709 | 4.3813 | 4.9918 | 0.73924 | 2.0081 | 2.5186 | 2.5186 | 2.5186 | 2.5186 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-09-05 23:00 | Winter | 0.91505 | 1.407 | 2.1291 | 2.1291 | 2.1291 | 2.1291 | 0.47098 | 0.47098 | 0.47098 | 0.47098 | 0.47098 | 0.47098 | 1.7896 | 2.5814 | 3.1002 | 3.3733 | 3.9193 | 4.4654 | 0.64016 | 1.7389 | 2.1811 | 2.1811 | 2.1811 | 2.1811 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-09-06 | Winter | 0.9335 | 1.4354 | 2.172 | 2.172 | 2.172 | 2.172 | 0.48584 | 0.48584 | 0.48584 | 0.48584 | 0.48584 | 0.48584 | 1.7109 | 2.4679 | 2.9638 | 3.2249 | 3.747 | 4.269 | 0.58301 | 1.5837 | 1.9863 | 1.9863 | 1.9863 | 1.9863 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-09-06 01:00 | Winter | 0.93358 | 1.4355 | 2.1722 | 2.1722 | 2.1722 | 2.1722 | 0.47441 | 0.47441 | 0.47441 | 0.47441 | 0.47441 | 0.47441 | 1.6388 | 2.364 | 2.8391 | 3.0891 | 3.5892 | 4.0893 | 0.57539 | 1.563 | 1.9603 | 1.9603 | 1.9603 | 1.9603 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-09-06 02:00 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 0.48298 | 1.6004 | 2.3086 | 2.7725 | 3.0167 | 3.5051 | 3.9934 | 0.56395 | 1.5319 | 1.9214 | 1.9214 | 1.9214 | 1.9214 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-09-06 03:00 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.49727 | 0.49727 | 0.49727 | 0.49727 | 0.49727 | 0.49727 | 1.6004 | 2.3086 | 2.7725 | 3.0167 | 3.5051 | 3.9934 | 0.52585 | 1.4284 | 1.7916 | 1.7916 | 1.7916 | 1.7916 | 0.49537 | 0.62876 | 0.62876 | 0.62876 | 0.62876 | 0.62876
2020-09-06 04:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.47726 | 0.47726 | 0.47726 | 0.47726 | 0.47726 | 0.47726 | 1.6195 | 2.336 | 2.8055 | 3.0526 | 3.5468 | 4.041 | 0.52585 | 1.4284 | 1.7916 | 1.7916 | 1.7916 | 1.7916 | 0.49537 | 0.62876 | 0.62876 | 0.62876 | 0.62876 | 0.62876
2020-09-06 05:00 | Winter | 0.93358 | 1.4355 | 2.1722 | 2.1722 | 2.1722 | 2.1722 | 0.54014 | 0.54014 | 0.54014 | 0.54014 | 0.54014 | 0.54014 | 1.7719 | 2.5559 | 3.0696 | 3.3399 | 3.8806 | 4.4213 | 0.52966 | 1.4388 | 1.8046 | 1.8046 | 1.8046 | 1.8046 | 0.49607 | 0.62965 | 0.62965 | 0.62965 | 0.62965 | 0.62965
2020-09-06 06:00 | Winter | 0.93358 | 1.4355 | 2.1722 | 2.1722 | 2.1722 | 2.1722 | 0.55157 | 0.55157 | 0.55157 | 0.55157 | 0.55157 | 0.55157 | 1.81 | 2.6109 | 3.1356 | 3.4117 | 3.9641 | 4.5164 | 0.5449 | 1.4802 | 1.8565 | 1.8565 | 1.8565 | 1.8565 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-09-06 07:00 | Winter | 0.93358 | 1.4355 | 2.1722 | 2.1722 | 2.1722 | 2.1722 | 0.62301 | 0.62301 | 0.62301 | 0.62301 | 0.62301 | 0.62301 | 1.9243 | 2.7758 | 3.3336 | 3.6272 | 4.2144 | 4.8016 | 0.63635 | 1.7286 | 2.1681 | 2.1681 | 2.1681 | 2.1681 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-09-06 08:00 | Winter | 0.87642 | 1.3476 | 2.0392 | 2.0392 | 2.0392 | 2.0392 | 0.69446 | 0.69446 | 0.69446 | 0.69446 | 0.69446 | 0.69446 | 2.1148 | 3.0506 | 3.6637 | 3.9863 | 4.6317 | 5.277 | 0.63254 | 1.7182 | 2.1551 | 2.1551 | 2.1551 | 2.1551 | 0.55252 | 0.70131 | 0.70131 | 0.70131 | 0.70131 | 0.70131
2020-09-06 09:00 | Winter | 0.85737 | 1.3183 | 1.9948 | 1.9948 | 1.9948 | 1.9948 | 0.59444 | 0.59444 | 0.59444 | 0.59444 | 0.59444 | 0.59444 | 2.1148 | 3.0506 | 3.6637 | 3.9863 | 4.6317 | 5.277 | 0.65922 | 1.7907 | 2.246 | 2.246 | 2.246 | 2.246 | 0.60968 | 0.77386 | 0.77386 | 0.77386 | 0.77386 | 0.77386
2020-09-06 10:00 | Winter | 0.83831 | 1.289 | 1.9505 | 1.9505 | 1.9505 | 1.9505 | 0.52585 | 0.86048 | 1.1792 | 1.4182 | 1.4182 | 1.4182 | 2.1529 | 3.1056 | 3.7297 | 4.0582 | 4.7151 | 5.3721 | 0.68208 | 1.8528 | 2.3239 | 2.3239 | 2.3239 | 2.3239 | 0.62873 | 0.79804 | 0.79804 | 0.79804 | 0.79804 | 0.79804
2020-09-06 11:00 | Winter | 0.89547 | 1.3769 | 2.0835 | 2.0835 | 2.0835 | 2.0835 | 0.49155 | 0.80436 | 1.1023 | 1.3257 | 1.3257 | 1.3257 | 2.172 | 3.133 | 3.7627 | 4.0941 | 4.7569 | 5.4197 | 0.64016 | 1.7389 | 2.1811 | 2.1811 | 2.1811 | 2.1811 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-09-06 12:00 | Winter | 0.85737 | 1.3183 | 1.9948 | 1.9948 | 1.9948 | 1.9948 | 0.44583 | 0.72953 | 0.99973 | 1.2024 | 1.2024 | 1.2024 | 2.191 | 3.1605 | 3.7957 | 4.13 | 4.7986 | 5.4672 | 0.57157 | 1.5526 | 1.9474 | 1.9474 | 1.9474 | 1.9474 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-09-06 13:00 | Winter | 0.83831 | 1.289 | 1.9505 | 1.9505 | 1.9505 | 1.9505 | 0.44011 | 0.72018 | 0.98691 | 1.187 | 1.187 | 1.187 | 2.2101 | 3.188 | 3.8287 | 4.1659 | 4.8403 | 5.5147 | 0.52585 | 1.4284 | 1.7916 | 1.7916 | 1.7916 | 1.7916 | 0.55252 | 0.70131 | 0.70131 | 0.70131 | 0.70131 | 0.70131
2020-09-06 14:00 | Winter | 0.85737 | 1.3183 | 1.9948 | 1.9948 | 1.9948 | 1.9948 | 0.39634 | 0.64856 | 0.88877 | 1.0689 | 1.0689 | 1.0689 | 2.172 | 3.133 | 3.7627 | 4.0941 | 4.7569 | 5.4197 | 0.56395 | 1.5319 | 1.9214 | 1.9214 | 1.9214 | 1.9214 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-09-06 15:00 | Winter | 0.89547 | 1.3769 | 2.0835 | 2.0835 | 2.0835 | 2.0835 | 0.43725 | 0.7155 | 0.98051 | 1.1793 | 1.1793 | 1.1793 | 2.1339 | 3.0781 | 3.6967 | 4.0223 | 4.6734 | 5.3246 | 0.57157 | 1.5526 | 1.9474 | 1.9474 | 1.9474 | 1.9474 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-09-06 16:00 | Winter | 0.93358 | 1.4355 | 2.1722 | 2.1722 | 2.1722 | 2.1722 | 0.47441 | 0.7763 | 1.0638 | 1.2795 | 1.2795 | 1.2795 | 2.1529 | 3.1056 | 3.7297 | 4.0582 | 4.7151 | 5.3721 | 0.60206 | 1.6354 | 2.0512 | 2.0512 | 2.0512 | 2.0512 | 0.52671 | 0.66854 | 0.66854 | 0.66854 | 0.66854 | 0.66854
2020-09-06 17:00 | Winter | 0.93358 | 1.4355 | 2.1722 | 2.1722 | 2.1722 | 2.1722 | 0.52585 | 0.86048 | 1.1792 | 1.4182 | 1.4182 | 1.4182 | 2.1529 | 3.1056 | 3.7297 | 4.0582 | 4.7151 | 5.3721 | 0.59063 | 1.6044 | 2.0123 | 2.0123 | 2.0123 | 2.0123 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-09-06 18:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.54014 | 0.88386 | 1.2112 | 1.4567 | 1.4567 | 1.4567 | 2.191 | 3.1605 | 3.7957 | 4.13 | 4.7986 | 5.4672 | 0.71637 | 1.946 | 2.4407 | 2.4407 | 2.4407 | 2.4407 | 0.49537 | 0.62876 | 0.62876 | 0.62876 | 0.62876 | 0.62876
2020-09-06 19:00 | Winter | 0.93481 | 1.4374 | 2.175 | 2.175 | 2.175 | 2.175 | 0.4924 | 0.80575 | 1.1042 | 1.328 | 1.328 | 1.328 | 2.1339 | 3.0781 | 3.6967 | 4.0223 | 4.6734 | 5.3246 | 0.67827 | 1.8425 | 2.3109 | 2.3109 | 2.3109 | 2.3109 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-09-06 20:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.51156 | 0.83709 | 1.1471 | 1.3797 | 1.3797 | 1.3797 | 2.0767 | 2.9956 | 3.5977 | 3.9145 | 4.5482 | 5.182 | 0.64779 | 1.7596 | 2.207 | 2.207 | 2.207 | 2.207 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-09-06 21:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.48584 | 0.79501 | 1.0895 | 1.3103 | 1.3103 | 1.3103 | 1.9831 | 2.8605 | 3.4354 | 3.738 | 4.3431 | 4.9483 | 0.65922 | 1.7907 | 2.246 | 2.246 | 2.246 | 2.246 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-09-06 22:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.48012 | 0.78565 | 1.0766 | 1.2949 | 1.2949 | 1.2949 | 1.9815 | 2.8582 | 3.4326 | 3.735 | 4.3396 | 4.9443 | 0.6173 | 1.6768 | 2.1032 | 2.1032 | 2.1032 | 2.1032 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-09-06 23:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.48298 | 0.79033 | 1.083 | 1.3026 | 1.3026 | 1.3026 | 1.7528 | 2.5284 | 3.0366 | 3.304 | 3.8389 | 4.3738 | 0.55252 | 1.5009 | 1.8825 | 1.8825 | 1.8825 | 1.8825 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-09-07 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.48869 | 0.79968 | 1.0959 | 1.318 | 1.318 | 1.318 | 1.6576 | 2.391 | 2.8715 | 3.1244 | 3.6302 | 4.1361 | 0.52204 | 1.4181 | 1.7786 | 1.7786 | 1.7786 | 1.7786 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-09-07 01:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.47155 | 0.77162 | 1.0574 | 1.2717 | 1.2717 | 1.2717 | 1.6195 | 2.336 | 2.8055 | 3.0526 | 3.5468 | 4.041 | 0.52204 | 1.4181 | 1.7786 | 1.7786 | 1.7786 | 1.7786 | 0.49537 | 0.62876 | 0.62876 | 0.62876 | 0.62876 | 0.62876
2020-09-07 02:00 | Winter | 1.0856 | 1.6693 | 2.526 | 2.526 | 2.526 | 2.526 | 0.49727 | 0.81371 | 1.1151 | 1.3411 | 1.3411 | 1.3411 | 1.5623 | 2.2536 | 2.7065 | 2.9449 | 3.4216 | 3.8984 | 0.5068 | 1.3767 | 1.7267 | 1.7267 | 1.7267 | 1.7267 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-09-07 03:00 | Winter | 1.105 | 1.6991 | 2.5711 | 2.5711 | 2.5711 | 2.5711 | 0.47726 | 0.78098 | 1.0702 | 1.2872 | 1.2872 | 1.2872 | 1.5371 | 2.2172 | 2.6628 | 2.8974 | 3.3664 | 3.8355 | 0.51823 | 1.4077 | 1.7656 | 1.7656 | 1.7656 | 1.7656 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-09-07 04:00 | Winter | 1.2003 | 1.8456 | 2.7928 | 2.7928 | 2.7928 | 2.7928 | 0.50584 | 0.82774 | 1.1343 | 1.3642 | 1.3642 | 1.3642 | 1.6766 | 2.4185 | 2.9045 | 3.1603 | 3.672 | 4.1836 | 0.53728 | 1.4595 | 1.8305 | 1.8305 | 1.8305 | 1.8305 | 0.55593 | 0.70563 | 0.70563 | 0.70563 | 0.70563 | 0.70563
2020-09-07 05:00 | Winter | 1.3602 | 2.0914 | 3.1647 | 3.1647 | 3.1647 | 3.1647 | 0.55728 | 0.91192 | 1.2497 | 1.503 | 1.503 | 1.503 | 1.8862 | 2.7208 | 3.2676 | 3.5554 | 4.131 | 4.7066 | 0.62111 | 1.6872 | 2.1161 | 2.1161 | 2.1161 | 2.1161 | 0.77792 | 0.98739 | 0.98739 | 0.98739 | 0.98739 | 0.98739
2020-09-07 06:00 | Winter | 1.5951 | 2.4526 | 3.7112 | 3.7112 | 3.7112 | 3.7112 | 0.75162 | 1.2299 | 1.6855 | 2.0271 | 2.0271 | 2.0271 | 2.0386 | 2.9407 | 3.5316 | 3.8427 | 4.4648 | 5.0869 | 0.6173 | 1.6768 | 2.1032 | 2.1032 | 2.1032 | 2.1032 | 0.97883 | 1.2424 | 1.2424 | 1.2424 | 1.2424 | 1.2424
2020-09-07 07:00 | Winter | 1.9818 | 3.0472 | 4.611 | 4.611 | 4.611 | 4.611 | 0.90309 | 1.4778 | 2.0251 | 2.4356 | 2.4356 | 2.4356 | 2.3244 | 3.3529 | 4.0267 | 4.3814 | 5.0907 | 5.8 | 0.80021 | 2.1737 | 2.7263 | 2.7263 | 2.7263 | 2.7263 | 1.2762 | 1.6198 | 1.6198 | 1.6198 | 1.6198 | 1.6198
2020-09-07 08:00 | Winter | 2.2291 | 3.4276 | 5.1866 | 5.1866 | 5.1866 | 5.1866 | 0.95167 | 1.5573 | 2.1341 | 2.5666 | 2.5666 | 2.5666 | 2.4158 | 3.4847 | 4.185 | 4.5536 | 5.2907 | 6.0279 | 0.86117 | 2.3393 | 2.934 | 2.934 | 2.934 | 2.934 | 1.3718 | 1.7412 | 1.7412 | 1.7412 | 1.7412 | 1.7412
2020-09-07 09:00 | Winter | 2.172 | 3.3397 | 5.0536 | 5.0536 | 5.0536 | 5.0536 | 0.95739 | 1.5666 | 2.1469 | 2.582 | 2.582 | 2.582 | 2.553 | 3.6827 | 4.4228 | 4.8123 | 5.5914 | 6.3705 | 0.88023 | 2.3911 | 2.9989 | 2.9989 | 2.9989 | 2.9989 | 1.467 | 1.8621 | 1.8621 | 1.8621 | 1.8621 | 1.8621
2020-09-07 10:00 | Winter | 2.2101 | 3.3983 | 5.1423 | 5.1423 | 5.1423 | 5.1423 | 0.87165 | 1.4263 | 1.9546 | 2.3508 | 2.3508 | 2.3508 | 2.6102 | 3.7651 | 4.5218 | 4.9201 | 5.7166 | 6.5131 | 0.92595 | 2.5153 | 3.1547 | 3.1547 | 3.1547 | 3.1547 | 1.3908 | 1.7654 | 1.7654 | 1.7654 | 1.7654 | 1.7654
2020-09-07 11:00 | Winter | 2.3534 | 3.6186 | 5.4757 | 5.4757 | 5.4757 | 5.4757 | 0.87165 | 1.4263 | 1.9546 | 2.3508 | 2.3508 | 2.3508 | 2.6102 | 3.7651 | 4.5218 | 4.9201 | 5.7166 | 6.5131 | 0.81164 | 2.2047 | 2.7653 | 2.7653 | 2.7653 | 2.7653 | 1.4099 | 1.7895 | 1.7895 | 1.7895 | 1.7895 | 1.7895
2020-09-07 12:00 | Winter | 2.5149 | 3.867 | 5.8515 | 5.8515 | 5.8515 | 5.8515 | 0.86308 | 1.4123 | 1.9354 | 2.3277 | 2.3277 | 2.3277 | 2.553 | 3.6827 | 4.4228 | 4.8123 | 5.5914 | 6.3705 | 0.7621 | 2.0702 | 2.5965 | 2.5965 | 2.5965 | 2.5965 | 1.3718 | 1.7412 | 1.7412 | 1.7412 | 1.7412 | 1.7412
2020-09-07 13:00 | Winter | 2.3435 | 3.6034 | 5.4526 | 5.4526 | 5.4526 | 5.4526 | 0.82307 | 1.3468 | 1.8457 | 2.2198 | 2.2198 | 2.2198 | 2.553 | 3.6827 | 4.4228 | 4.8123 | 5.5914 | 6.3705 | 0.74305 | 2.0184 | 2.5316 | 2.5316 | 2.5316 | 2.5316 | 1.3718 | 1.7412 | 1.7412 | 1.7412 | 1.7412 | 1.7412
2020-09-07 14:00 | Winter | 2.2863 | 3.5155 | 5.3196 | 5.3196 | 5.3196 | 5.3196 | 0.8002 | 1.3094 | 1.7944 | 2.1581 | 2.1581 | 2.1581 | 2.534 | 3.6552 | 4.3898 | 4.7764 | 5.5497 | 6.3229 | 0.7621 | 2.0702 | 2.5965 | 2.5965 | 2.5965 | 2.5965 | 1.3527 | 1.717 | 1.717 | 1.717 | 1.717 | 1.717
2020-09-07 15:00 | Winter | 2.3625 | 3.6326 | 5.4969 | 5.4969 | 5.4969 | 5.4969 | 0.8002 | 1.3094 | 1.7944 | 2.1581 | 2.1581 | 2.1581 | 2.534 | 3.6552 | 4.3898 | 4.7764 | 5.5497 | 6.3229 | 0.75067 | 2.0391 | 2.5575 | 2.5575 | 2.5575 | 2.5575 | 1.3527 | 1.717 | 1.717 | 1.717 | 1.717 | 1.717
2020-09-07 16:00 | Winter | 2.3244 | 3.5741 | 5.4082 | 5.4082 | 5.4082 | 5.4082 | 0.82592 | 1.3515 | 1.8521 | 2.2275 | 2.2275 | 2.2275 | 2.534 | 3.6552 | 4.3898 | 4.7764 | 5.5497 | 6.3229 | 0.74686 | 2.0288 | 2.5446 | 2.5446 | 2.5446 | 2.5446 | 1.2384 | 1.5719 | 1.5719 | 1.5719 | 1.5719 | 1.5719
2020-09-07 17:00 | Winter | 2.172 | 3.3397 | 5.0536 | 5.0536 | 5.0536 | 5.0536 | 0.7802 | 1.2767 | 1.7495 | 2.1042 | 2.1042 | 2.1042 | 2.3625 | 3.4079 | 4.0927 | 4.4532 | 5.1741 | 5.8951 | 0.7621 | 2.0702 | 2.5965 | 2.5965 | 2.5965 | 2.5965 | 1.1813 | 1.4993 | 1.4993 | 1.4993 | 1.4993 | 1.4993
2020-09-07 18:00 | Winter | 1.6383 | 2.5191 | 3.8119 | 3.8119 | 3.8119 | 3.8119 | 0.69446 | 1.1364 | 1.5573 | 1.8729 | 1.8729 | 1.8729 | 2.3435 | 3.3804 | 4.0597 | 4.4173 | 5.1324 | 5.8475 | 0.71637 | 1.946 | 2.4407 | 2.4407 | 2.4407 | 2.4407 | 0.80312 | 1.0194 | 1.0194 | 1.0194 | 1.0194 | 1.0194
2020-09-07 19:00 | Winter | 1.2194 | 1.8749 | 2.8371 | 2.8371 | 2.8371 | 2.8371 | 0.47155 | 0.77162 | 1.0574 | 1.2717 | 1.2717 | 1.2717 | 2.2101 | 3.188 | 3.8287 | 4.1659 | 4.8403 | 5.5147 | 0.73543 | 1.9977 | 2.5056 | 2.5056 | 2.5056 | 2.5056 | 0.62873 | 0.79804 | 0.79804 | 0.79804 | 0.79804 | 0.79804
2020-09-07 20:00 | Winter | 1.105 | 1.6991 | 2.5711 | 2.5711 | 2.5711 | 2.5711 | 0.47441 | 0.7763 | 1.0638 | 1.2795 | 1.2795 | 1.2795 | 2.1529 | 3.1056 | 3.7297 | 4.0582 | 4.7151 | 5.3721 | 0.6897 | 1.8735 | 2.3498 | 2.3498 | 2.3498 | 2.3498 | 0.57158 | 0.72549 | 0.72549 | 0.72549 | 0.72549 | 0.72549
2020-09-07 21:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.43439 | 0.71083 | 0.9741 | 1.1715 | 1.1715 | 1.1715 | 2.0386 | 2.9407 | 3.5316 | 3.8427 | 4.4648 | 5.0869 | 0.66303 | 1.8011 | 2.2589 | 2.2589 | 2.2589 | 2.2589 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-09-07 22:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.48012 | 0.78565 | 1.0766 | 1.2949 | 1.2949 | 1.2949 | 1.829 | 2.6383 | 3.1686 | 3.4477 | 4.0058 | 4.5639 | 0.62111 | 1.6872 | 2.1161 | 2.1161 | 2.1161 | 2.1161 | 0.50218 | 0.6374 | 0.6374 | 0.6374 | 0.6374 | 0.6374
2020-09-07 23:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.4544 | 0.74356 | 1.019 | 1.2255 | 1.2255 | 1.2255 | 1.7199 | 2.4809 | 2.9795 | 3.242 | 3.7668 | 4.2916 | 0.5449 | 1.4802 | 1.8565 | 1.8565 | 1.8565 | 1.8565 | 0.49537 | 0.62876 | 0.62876 | 0.62876 | 0.62876 | 0.62876
2020-09-08 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.44011 | 0.72018 | 0.98691 | 1.187 | 1.187 | 1.187 | 1.6576 | 2.391 | 2.8715 | 3.1244 | 3.6302 | 4.1361 | 0.52656 | 1.4303 | 1.794 | 1.794 | 1.794 | 1.794 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-09-08 01:00 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.42296 | 0.69212 | 0.94846 | 1.1407 | 1.1407 | 1.1407 | 1.5425 | 2.225 | 2.6721 | 2.9074 | 3.3781 | 3.8488 | 0.52966 | 1.4388 | 1.8046 | 1.8046 | 1.8046 | 1.8046 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-09-08 02:00 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.46869 | 0.76695 | 1.051 | 1.264 | 1.264 | 1.264 | 1.5814 | 2.2811 | 2.7395 | 2.9808 | 3.4633 | 3.9459 | 0.48012 | 1.3042 | 1.6358 | 1.6358 | 1.6358 | 1.6358 | 0.49537 | 0.62876 | 0.62876 | 0.62876 | 0.62876 | 0.62876
2020-09-08 03:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.4544 | 0.74356 | 1.019 | 1.2255 | 1.2255 | 1.2255 | 1.6004 | 2.3086 | 2.7725 | 3.0167 | 3.5051 | 3.9934 | 0.49918 | 1.356 | 1.7007 | 1.7007 | 1.7007 | 1.7007 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-09-08 04:00 | Winter | 1.1622 | 1.787 | 2.7041 | 2.7041 | 2.7041 | 2.7041 | 0.48012 | 0.78565 | 1.0766 | 1.2949 | 1.2949 | 1.2949 | 1.6004 | 2.3086 | 2.7725 | 3.0167 | 3.5051 | 3.9934 | 0.50299 | 1.3663 | 1.7137 | 1.7137 | 1.7137 | 1.7137 | 0.55252 | 0.70131 | 0.70131 | 0.70131 | 0.70131 | 0.70131
2020-09-08 05:00 | Winter | 1.2192 | 1.8746 | 2.8367 | 2.8367 | 2.8367 | 2.8367 | 0.62301 | 1.0195 | 1.3971 | 1.6803 | 1.6803 | 1.6803 | 1.7215 | 2.4832 | 2.9823 | 3.2449 | 3.7703 | 4.2956 | 0.59825 | 1.6251 | 2.0382 | 2.0382 | 2.0382 | 2.0382 | 0.74305 | 0.94314 | 0.94314 | 0.94314 | 0.94314 | 0.94314
2020-09-08 06:00 | Winter | 1.4861 | 2.2851 | 3.4577 | 3.4577 | 3.4577 | 3.4577 | 0.74019 | 1.2112 | 1.6598 | 1.9963 | 1.9963 | 1.9963 | 2.0382 | 2.9401 | 3.531 | 3.842 | 4.4639 | 5.0859 | 0.63254 | 1.7182 | 2.1551 | 2.1551 | 2.1551 | 2.1551 | 0.8759 | 1.1118 | 1.1118 | 1.1118 | 1.1118 | 1.1118
2020-09-08 07:00 | Winter | 1.8481 | 2.8417 | 4.3 | 4.3 | 4.3 | 4.3 | 0.83736 | 1.3702 | 1.8777 | 2.2583 | 2.2583 | 2.2583 | 2.3244 | 3.3529 | 4.0267 | 4.3814 | 5.0907 | 5.8 | 0.83069 | 2.2565 | 2.8302 | 2.8302 | 2.8302 | 2.8302 | 1.1432 | 1.451 | 1.451 | 1.451 | 1.451 | 1.451
2020-09-08 08:00 | Winter | 2.2863 | 3.5155 | 5.3196 | 5.3196 | 5.3196 | 5.3196 | 0.91738 | 1.5012 | 2.0571 | 2.4741 | 2.4741 | 2.4741 | 2.4578 | 3.5453 | 4.2578 | 4.6328 | 5.3828 | 6.1328 | 0.81164 | 2.2047 | 2.7653 | 2.7653 | 2.7653 | 2.7653 | 1.3146 | 1.6686 | 1.6686 | 1.6686 | 1.6686 | 1.6686
2020-09-08 09:00 | Winter | 2.3244 | 3.5741 | 5.4082 | 5.4082 | 5.4082 | 5.4082 | 0.88594 | 1.4497 | 1.9867 | 2.3894 | 2.3894 | 2.3894 | 2.534 | 3.6552 | 4.3898 | 4.7764 | 5.5497 | 6.3229 | 0.84974 | 2.3082 | 2.8951 | 2.8951 | 2.8951 | 2.8951 | 1.3146 | 1.6686 | 1.6686 | 1.6686 | 1.6686 | 1.6686
2020-09-08 10:00 | Winter | 2.2863 | 3.5155 | 5.3196 | 5.3196 | 5.3196 | 5.3196 | 0.84307 | 1.3796 | 1.8905 | 2.2737 | 2.2737 | 2.2737 | 2.534 | 3.6552 | 4.3898 | 4.7764 | 5.5497 | 6.3229 | 0.80783 | 2.1944 | 2.7523 | 2.7523 | 2.7523 | 2.7523 | 1.3337 | 1.6928 | 1.6928 | 1.6928 | 1.6928 | 1.6928
2020-09-08 11:00 | Winter | 2.2673 | 3.4862 | 5.2753 | 5.2753 | 5.2753 | 5.2753 | 0.82021 | 1.3422 | 1.8393 | 2.2121 | 2.2121 | 2.2121 | 2.4959 | 3.6002 | 4.3238 | 4.7046 | 5.4662 | 6.2279 | 0.80783 | 2.1944 | 2.7523 | 2.7523 | 2.7523 | 2.7523 | 1.3337 | 1.6928 | 1.6928 | 1.6928 | 1.6928 | 1.6928
2020-09-08 12:00 | Winter | 2.3054 | 3.5448 | 5.3639 | 5.3639 | 5.3639 | 5.3639 | 1.0117 | 1.6555 | 2.2686 | 2.7285 | 2.7285 | 2.7285 | 2.5096 | 3.62 | 4.3475 | 4.7304 | 5.4962 | 6.262 | 0.78362 | 2.1286 | 2.6698 | 2.6698 | 2.6698 | 2.6698 | 1.3218 | 1.6777 | 1.6777 | 1.6777 | 1.6777 | 1.6777
2020-09-08 13:00 | Winter | 2.3244 | 3.5741 | 5.4082 | 5.4082 | 5.4082 | 5.4082 | 0.86879 | 1.4217 | 1.9482 | 2.3431 | 2.3431 | 2.3431 | 2.5149 | 3.6277 | 4.3568 | 4.7405 | 5.508 | 6.2754 | 0.84212 | 2.2875 | 2.8691 | 2.8691 | 2.8691 | 2.8691 | 1.3527 | 1.717 | 1.717 | 1.717 | 1.717 | 1.717
2020-09-08 14:00 | Winter | 2.3435 | 3.6034 | 5.4526 | 5.4526 | 5.4526 | 5.4526 | 0.86022 | 1.4076 | 1.929 | 2.32 | 2.32 | 2.32 | 2.6674 | 3.8476 | 4.6208 | 5.0278 | 5.8418 | 6.6557 | 0.81545 | 2.2151 | 2.7782 | 2.7782 | 2.7782 | 2.7782 | 1.3718 | 1.7412 | 1.7412 | 1.7412 | 1.7412 | 1.7412
2020-09-08 15:00 | Winter | 2.3625 | 3.6326 | 5.4969 | 5.4969 | 5.4969 | 5.4969 | 0.89451 | 1.4638 | 2.0059 | 2.4125 | 2.4125 | 2.4125 | 2.6002 | 3.7507 | 4.5045 | 4.9012 | 5.6946 | 6.4881 | 0.75067 | 2.0391 | 2.5575 | 2.5575 | 2.5575 | 2.5575 | 1.2956 | 1.6444 | 1.6444 | 1.6444 | 1.6444 | 1.6444
2020-09-08 16:00 | Winter | 2.3816 | 3.6619 | 5.5412 | 5.5412 | 5.5412 | 5.5412 | 0.93738 | 1.5339 | 2.102 | 2.5281 | 2.5281 | 2.5281 | 2.6102 | 3.7651 | 4.5218 | 4.9201 | 5.7166 | 6.5131 | 0.93357 | 2.536 | 3.1807 | 3.1807 | 3.1807 | 3.1807 | 1.2194 | 1.5477 | 1.5477 | 1.5477 | 1.5477 | 1.5477
2020-09-08 17:00 | Winter | 2.2802 | 3.506 | 5.3053 | 5.3053 | 5.3053 | 5.3053 | 0.82592 | 1.3515 | 1.8521 | 2.2275 | 2.2275 | 2.2275 | 2.4581 | 3.5457 | 4.2583 | 4.6334 | 5.3835 | 6.1336 | 0.88404 | 2.4014 | 3.0119 | 3.0119 | 3.0119 | 3.0119 | 1.105 | 1.4026 | 1.4026 | 1.4026 | 1.4026 | 1.4026
2020-09-08 18:00 | Winter | 1.6344 | 2.513 | 3.8027 | 3.8027 | 3.8027 | 3.8027 | 0.70461 | 1.153 | 1.58 | 1.9003 | 1.9003 | 1.9003 | 2.3054 | 3.3254 | 3.9937 | 4.3455 | 5.049 | 5.7525 | 0.76591 | 2.0805 | 2.6095 | 2.6095 | 2.6095 | 2.6095 | 0.80521 | 1.022 | 1.022 | 1.022 | 1.022 | 1.022
2020-09-08 19:00 | Winter | 1.1475 | 1.7645 | 2.67 | 2.67 | 2.67 | 2.67 | 0.51442 | 0.84177 | 1.1535 | 1.3874 | 1.3874 | 1.3874 | 2.1339 | 3.0781 | 3.6967 | 4.0223 | 4.6734 | 5.3246 | 0.76972 | 2.0909 | 2.6225 | 2.6225 | 2.6225 | 2.6225 | 0.66684 | 0.84641 | 0.84641 | 0.84641 | 0.84641 | 0.84641
2020-09-08 20:00 | Winter | 1.105 | 1.6991 | 2.5711 | 2.5711 | 2.5711 | 2.5711 | 0.48056 | 0.78637 | 1.0776 | 1.2961 | 1.2961 | 1.2961 | 2.0767 | 2.9956 | 3.5977 | 3.9145 | 4.5482 | 5.182 | 0.7089 | 1.9257 | 2.4152 | 2.4152 | 2.4152 | 2.4152 | 0.59063 | 0.74967 | 0.74967 | 0.74967 | 0.74967 | 0.74967
2020-09-08 21:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 0.52013 | 0.85112 | 1.1664 | 1.4028 | 1.4028 | 1.4028 | 1.9053 | 2.7483 | 3.3006 | 3.5913 | 4.1727 | 4.7541 | 0.74305 | 2.0184 | 2.5316 | 2.5316 | 2.5316 | 2.5316 | 0.49844 | 0.63266 | 0.63266 | 0.63266 | 0.63266 | 0.63266
2020-09-08 22:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.43154 | 0.70615 | 0.96769 | 1.1638 | 1.1638 | 1.1638 | 1.81 | 2.6109 | 3.1356 | 3.4117 | 3.9641 | 4.5164 | 0.74305 | 2.0184 | 2.5316 | 2.5316 | 2.5316 | 2.5316 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-09-08 23:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.46012 | 0.75292 | 1.0318 | 1.2409 | 1.2409 | 1.2409 | 1.7338 | 2.5009 | 3.0036 | 3.2681 | 3.7972 | 4.3262 | 0.60587 | 1.6458 | 2.0642 | 2.0642 | 2.0642 | 2.0642 | 0.45726 | 0.58039 | 0.58039 | 0.58039 | 0.58039 | 0.58039
2020-09-09 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.42868 | 0.70147 | 0.96128 | 1.1561 | 1.1561 | 1.1561 | 1.6576 | 2.391 | 2.8715 | 3.1244 | 3.6302 | 4.1361 | 0.6173 | 1.6768 | 2.1032 | 2.1032 | 2.1032 | 2.1032 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-09-09 01:00 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.37438 | 0.61262 | 0.83952 | 1.0097 | 1.0097 | 1.0097 | 1.5814 | 2.2811 | 2.7395 | 2.9808 | 3.4633 | 3.9459 | 0.57539 | 1.563 | 1.9603 | 1.9603 | 1.9603 | 1.9603 | 0.45726 | 0.58039 | 0.58039 | 0.58039 | 0.58039 | 0.58039
2020-09-09 02:00 | Winter | 0.93358 | 1.4355 | 2.1722 | 2.1722 | 2.1722 | 2.1722 | 0.46583 | 0.76227 | 1.0446 | 1.2563 | 1.2563 | 1.2563 | 1.5814 | 2.2811 | 2.7395 | 2.9808 | 3.4633 | 3.9459 | 0.59063 | 1.6044 | 2.0123 | 2.0123 | 2.0123 | 2.0123 | 0.45726 | 0.58039 | 0.58039 | 0.58039 | 0.58039 | 0.58039
2020-09-09 03:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.43154 | 0.70615 | 0.96769 | 1.1638 | 1.1638 | 1.1638 | 1.5623 | 2.2536 | 2.7065 | 2.9449 | 3.4216 | 3.8984 | 0.5792 | 1.5733 | 1.9733 | 1.9733 | 1.9733 | 1.9733 | 0.45726 | 0.58039 | 0.58039 | 0.58039 | 0.58039 | 0.58039
2020-09-09 04:00 | Winter | 1.1241 | 1.7284 | 2.6155 | 2.6155 | 2.6155 | 2.6155 | 0.43439 | 0.71083 | 0.9741 | 1.1715 | 1.1715 | 1.1715 | 1.6111 | 2.324 | 2.7911 | 3.0369 | 3.5285 | 4.0202 | 0.58682 | 1.594 | 1.9993 | 1.9993 | 1.9993 | 1.9993 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-09-09 05:00 | Winter | 1.186 | 1.8237 | 2.7596 | 2.7596 | 2.7596 | 2.7596 | 0.41153 | 0.67342 | 0.92283 | 1.1099 | 1.1099 | 1.1099 | 1.7719 | 2.5559 | 3.0696 | 3.3399 | 3.8806 | 4.4213 | 0.64397 | 1.7493 | 2.194 | 2.194 | 2.194 | 2.194 | 0.68589 | 0.87059 | 0.87059 | 0.87059 | 0.87059 | 0.87059
2020-09-09 06:00 | Winter | 1.3003 | 1.9993 | 3.0253 | 3.0253 | 3.0253 | 3.0253 | 0.63274 | 1.0354 | 1.4189 | 1.7065 | 1.7065 | 1.7065 | 1.8983 | 2.7382 | 3.2885 | 3.5781 | 4.1574 | 4.7366 | 0.74686 | 2.0288 | 2.5446 | 2.5446 | 2.5446 | 2.5446 | 0.766 | 0.97227 | 0.97227 | 0.97227 | 0.97227 | 0.97227
2020-09-09 07:00 | Winter | 1.8281 | 2.8109 | 4.2535 | 4.2535 | 4.2535 | 4.2535 | 0.7459 | 1.2206 | 1.6726 | 2.0117 | 2.0117 | 2.0117 | 2.172 | 3.133 | 3.7627 | 4.0941 | 4.7569 | 5.4197 | 0.91452 | 2.4842 | 3.1158 | 3.1158 | 3.1158 | 3.1158 | 1.0028 | 1.2728 | 1.2728 | 1.2728 | 1.2728 | 1.2728
2020-09-09 08:00 | Winter | 2.0951 | 3.2214 | 4.8746 | 4.8746 | 4.8746 | 4.8746 | 0.9431 | 1.5433 | 2.1148 | 2.5435 | 2.5435 | 2.5435 | 2.4768 | 3.5728 | 4.2908 | 4.6687 | 5.4245 | 6.1803 | 0.94119 | 2.5567 | 3.2067 | 3.2067 | 3.2067 | 3.2067 | 1.2829 | 1.6283 | 1.6283 | 1.6283 | 1.6283 | 1.6283
2020-09-09 09:00 | Winter | 2.2673 | 3.4862 | 5.2753 | 5.2753 | 5.2753 | 5.2753 | 0.94881 | 1.5526 | 2.1276 | 2.5589 | 2.5589 | 2.5589 | 2.5721 | 3.7102 | 4.4558 | 4.8483 | 5.6331 | 6.418 | 0.93357 | 2.536 | 3.1807 | 3.1807 | 3.1807 | 3.1807 | 1.3527 | 1.717 | 1.717 | 1.717 | 1.717 | 1.717
2020-09-09 10:00 | Winter | 2.2482 | 3.4569 | 5.2309 | 5.2309 | 5.2309 | 5.2309 | 0.9631 | 1.576 | 2.1597 | 2.5975 | 2.5975 | 2.5975 | 2.5721 | 3.7102 | 4.4558 | 4.8483 | 5.6331 | 6.418 | 0.84974 | 2.3082 | 2.8951 | 2.8951 | 2.8951 | 2.8951 | 1.3718 | 1.7412 | 1.7412 | 1.7412 | 1.7412 | 1.7412
2020-09-09 11:00 | Winter | 2.2101 | 3.3983 | 5.1423 | 5.1423 | 5.1423 | 5.1423 | 0.95167 | 1.5573 | 2.1341 | 2.5666 | 2.5666 | 2.5666 | 2.5911 | 3.7377 | 4.4888 | 4.8842 | 5.6749 | 6.4656 | 0.89166 | 2.4221 | 3.0379 | 3.0379 | 3.0379 | 3.0379 | 1.3908 | 1.7654 | 1.7654 | 1.7654 | 1.7654 | 1.7654
2020-09-09 12:00 | Winter | 2.2101 | 3.3983 | 5.1423 | 5.1423 | 5.1423 | 5.1423 | 0.94596 | 1.5479 | 2.1212 | 2.5512 | 2.5512 | 2.5512 | 2.7245 | 3.93 | 4.7199 | 5.1356 | 5.967 | 6.7984 | 0.85736 | 2.3289 | 2.9211 | 2.9211 | 2.9211 | 2.9211 | 1.4099 | 1.7895 | 1.7895 | 1.7895 | 1.7895 | 1.7895
2020-09-09 13:00 | Winter | 2.191 | 3.369 | 5.0979 | 5.0979 | 5.0979 | 5.0979 | 0.85736 | 1.403 | 1.9226 | 2.3123 | 2.3123 | 2.3123 | 2.6293 | 3.7926 | 4.5548 | 4.956 | 5.7583 | 6.5606 | 0.82307 | 2.2358 | 2.8042 | 2.8042 | 2.8042 | 2.8042 | 1.3908 | 1.7654 | 1.7654 | 1.7654 | 1.7654 | 1.7654
2020-09-09 14:00 | Winter | 2.2482 | 3.4569 | 5.2309 | 5.2309 | 5.2309 | 5.2309 | 0.84307 | 1.3796 | 1.8905 | 2.2737 | 2.2737 | 2.2737 | 2.6483 | 3.8201 | 4.5878 | 4.9919 | 5.8 | 6.6082 | 0.81164 | 2.2047 | 2.7653 | 2.7653 | 2.7653 | 2.7653 | 1.3527 | 1.717 | 1.717 | 1.717 | 1.717 | 1.717
2020-09-09 15:00 | Winter | 2.191 | 3.369 | 5.0979 | 5.0979 | 5.0979 | 5.0979 | 0.82307 | 1.3468 | 1.8457 | 2.2198 | 2.2198 | 2.2198 | 2.5911 | 3.7377 | 4.4888 | 4.8842 | 5.6749 | 6.4656 | 0.78115 | 2.1219 | 2.6614 | 2.6614 | 2.6614 | 2.6614 | 1.3146 | 1.6686 | 1.6686 | 1.6686 | 1.6686 | 1.6686
2020-09-09 16:00 | Winter | 2.0958 | 3.2225 | 4.8763 | 4.8763 | 4.8763 | 4.8763 | 0.82021 | 1.3422 | 1.8393 | 2.2121 | 2.2121 | 2.2121 | 2.534 | 3.6552 | 4.3898 | 4.7764 | 5.5497 | 6.3229 | 0.80783 | 2.1944 | 2.7523 | 2.7523 | 2.7523 | 2.7523 | 1.2575 | 1.5961 | 1.5961 | 1.5961 | 1.5961 | 1.5961
2020-09-09 17:00 | Winter | 2.0196 | 3.1053 | 4.699 | 4.699 | 4.699 | 4.699 | 0.85165 | 1.3936 | 1.9098 | 2.2969 | 2.2969 | 2.2969 | 2.4768 | 3.5728 | 4.2908 | 4.6687 | 5.4245 | 6.1803 | 0.75448 | 2.0495 | 2.5705 | 2.5705 | 2.5705 | 2.5705 | 1.1894 | 1.5097 | 1.5097 | 1.5097 | 1.5097 | 1.5097
2020-09-09 18:00 | Winter | 1.6957 | 2.6073 | 3.9454 | 3.9454 | 3.9454 | 3.9454 | 0.69446 | 1.1364 | 1.5573 | 1.8729 | 1.8729 | 1.8729 | 2.4959 | 3.6002 | 4.3238 | 4.7046 | 5.4662 | 6.2279 | 0.79258 | 2.153 | 2.7003 | 2.7003 | 2.7003 | 2.7003 | 0.917 | 1.1639 | 1.1639 | 1.1639 | 1.1639 | 1.1639
2020-09-09 19:00 | Winter | 1.2072 | 1.8561 | 2.8087 | 2.8087 | 2.8087 | 2.8087 | 0.58872 | 0.96336 | 1.3202 | 1.5878 | 1.5878 | 1.5878 | 2.3508 | 3.391 | 4.0725 | 4.4312 | 5.1486 | 5.8659 | 0.79258 | 2.153 | 2.7003 | 2.7003 | 2.7003 | 2.7003 | 0.70494 | 0.89477 | 0.89477 | 0.89477 | 0.89477 | 0.89477
2020-09-09 20:00 | Winter | 1.1241 | 1.7284 | 2.6155 | 2.6155 | 2.6155 | 2.6155 | 0.50298 | 0.82306 | 1.1279 | 1.3565 | 1.3565 | 1.3565 | 2.2101 | 3.188 | 3.8287 | 4.1659 | 4.8403 | 5.5147 | 0.73543 | 1.9977 | 2.5056 | 2.5056 | 2.5056 | 2.5056 | 0.61311 | 0.77821 | 0.77821 | 0.77821 | 0.77821 | 0.77821
2020-09-09 21:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 0.47155 | 0.77162 | 1.0574 | 1.2717 | 1.2717 | 1.2717 | 2.0577 | 2.9681 | 3.5647 | 3.8786 | 4.5065 | 5.1344 | 0.68589 | 1.8632 | 2.3368 | 2.3368 | 2.3368 | 2.3368 | 0.57158 | 0.72549 | 0.72549 | 0.72549 | 0.72549 | 0.72549
2020-09-09 22:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.45154 | 0.73889 | 1.0125 | 1.2178 | 1.2178 | 1.2178 | 1.9019 | 2.7435 | 3.2948 | 3.585 | 4.1654 | 4.7457 | 0.6516 | 1.77 | 2.22 | 2.22 | 2.22 | 2.22 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-09-09 23:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.42011 | 0.68744 | 0.94205 | 1.133 | 1.133 | 1.133 | 1.7338 | 2.5009 | 3.0036 | 3.2681 | 3.7972 | 4.3262 | 0.63635 | 1.7286 | 2.1681 | 2.1681 | 2.1681 | 2.1681 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-09-10 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.4544 | 0.74356 | 1.019 | 1.2255 | 1.2255 | 1.2255 | 1.6957 | 2.446 | 2.9375 | 3.1963 | 3.7137 | 4.2311 | 0.5792 | 1.5733 | 1.9733 | 1.9733 | 1.9733 | 1.9733 | 0.45756 | 0.58076 | 0.58076 | 0.58076 | 0.58076 | 0.58076
2020-09-10 01:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.44011 | 0.72018 | 0.98691 | 1.187 | 1.187 | 1.187 | 1.5814 | 2.2811 | 2.7395 | 2.9808 | 3.4633 | 3.9459 | 0.59444 | 1.6147 | 2.0253 | 2.0253 | 2.0253 | 2.0253 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-09-10 02:00 | Winter | 0.93358 | 1.4355 | 2.1722 | 2.1722 | 2.1722 | 2.1722 | 0.46012 | 0.75292 | 1.0318 | 1.2409 | 1.2409 | 1.2409 | 1.5432 | 2.226 | 2.6733 | 2.9088 | 3.3797 | 3.8506 | 0.57157 | 1.5526 | 1.9474 | 1.9474 | 1.9474 | 1.9474 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-09-10 03:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.41725 | 0.68277 | 0.93565 | 1.1253 | 1.1253 | 1.1253 | 1.5814 | 2.2811 | 2.7395 | 2.9808 | 3.4633 | 3.9459 | 0.56014 | 1.5216 | 1.9084 | 1.9084 | 1.9084 | 1.9084 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-09-10 04:00 | Winter | 1.1761 | 1.8084 | 2.7364 | 2.7364 | 2.7364 | 2.7364 | 0.48012 | 0.78565 | 1.0766 | 1.2949 | 1.2949 | 1.2949 | 1.6328 | 2.3553 | 2.8286 | 3.0778 | 3.576 | 4.0743 | 0.54091 | 1.4693 | 1.8429 | 1.8429 | 1.8429 | 1.8429 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-09-10 05:00 | Winter | 1.2194 | 1.8749 | 2.8371 | 2.8371 | 2.8371 | 2.8371 | 0.50584 | 0.82774 | 1.1343 | 1.3642 | 1.3642 | 1.3642 | 1.771 | 2.5546 | 3.068 | 3.3383 | 3.8787 | 4.4191 | 0.61349 | 1.6665 | 2.0902 | 2.0902 | 2.0902 | 2.0902 | 0.75102 | 0.95325 | 0.95325 | 0.95325 | 0.95325 | 0.95325
2020-09-10 06:00 | Winter | 1.405 | 2.1603 | 3.269 | 3.269 | 3.269 | 3.269 | 0.63159 | 1.0335 | 1.4163 | 1.7034 | 1.7034 | 1.7034 | 1.9815 | 2.8582 | 3.4326 | 3.735 | 4.3396 | 4.9443 | 0.70113 | 1.9046 | 2.3888 | 2.3888 | 2.3888 | 2.3888 | 0.92606 | 1.1754 | 1.1754 | 1.1754 | 1.1754 | 1.1754
2020-09-10 07:00 | Winter | 1.9473 | 2.9943 | 4.5309 | 4.5309 | 4.5309 | 4.5309 | 0.84021 | 1.3749 | 1.8841 | 2.266 | 2.266 | 2.266 | 2.3625 | 3.4079 | 4.0927 | 4.4532 | 5.1741 | 5.8951 | 0.84974 | 2.3082 | 2.8951 | 2.8951 | 2.8951 | 2.8951 | 1.2035 | 1.5276 | 1.5276 | 1.5276 | 1.5276 | 1.5276
2020-09-10 08:00 | Winter | 2.1339 | 3.2811 | 4.9649 | 4.9649 | 4.9649 | 4.9649 | 0.90595 | 1.4825 | 2.0315 | 2.4433 | 2.4433 | 2.4433 | 2.4768 | 3.5728 | 4.2908 | 4.6687 | 5.4245 | 6.1803 | 0.86498 | 2.3496 | 2.947 | 2.947 | 2.947 | 2.947 | 1.3718 | 1.7412 | 1.7412 | 1.7412 | 1.7412 | 1.7412
2020-09-10 09:00 | Winter | 2.2673 | 3.4862 | 5.2753 | 5.2753 | 5.2753 | 5.2753 | 0.92309 | 1.5105 | 2.07 | 2.4896 | 2.4896 | 2.4896 | 2.553 | 3.6827 | 4.4228 | 4.8123 | 5.5914 | 6.3705 | 0.82307 | 2.2358 | 2.8042 | 2.8042 | 2.8042 | 2.8042 | 1.3718 | 1.7412 | 1.7412 | 1.7412 | 1.7412 | 1.7412
2020-09-10 10:00 | Winter | 2.172 | 3.3397 | 5.0536 | 5.0536 | 5.0536 | 5.0536 | 0.88594 | 1.4497 | 1.9867 | 2.3894 | 2.3894 | 2.3894 | 2.553 | 3.6827 | 4.4228 | 4.8123 | 5.5914 | 6.3705 | 0.84974 | 2.3082 | 2.8951 | 2.8951 | 2.8951 | 2.8951 | 1.3718 | 1.7412 | 1.7412 | 1.7412 | 1.7412 | 1.7412
2020-09-10 11:00 | Winter | 2.1339 | 3.2811 | 4.9649 | 4.9649 | 4.9649 | 4.9649 | 1.1317 | 1.8519 | 2.5378 | 3.0522 | 3.0522 | 3.0522 | 2.6102 | 3.7651 | 4.5218 | 4.9201 | 5.7166 | 6.5131 | 0.84593 | 2.2979 | 2.8821 | 2.8821 | 2.8821 | 2.8821 | 1.3718 | 1.7412 | 1.7412 | 1.7412 | 1.7412 | 1.7412
2020-09-10 12:00 | Winter | 2.1148 | 3.2518 | 4.9206 | 4.9206 | 4.9206 | 4.9206 | 0.8888 | 1.4544 | 1.9931 | 2.3971 | 2.3971 | 2.3971 | 2.6293 | 3.7926 | 4.5548 | 4.956 | 5.7583 | 6.5606 | 0.89928 | 2.4428 | 3.0639 | 3.0639 | 3.0639 | 3.0639 | 1.3718 | 1.7412 | 1.7412 | 1.7412 | 1.7412 | 1.7412
2020-09-10 13:00 | Winter | 2.1148 | 3.2518 | 4.9206 | 4.9206 | 4.9206 | 4.9206 | 0.91166 | 1.4918 | 2.0443 | 2.4587 | 2.4587 | 2.4587 | 2.6293 | 3.7926 | 4.5548 | 4.956 | 5.7583 | 6.5606 | 0.89547 | 2.4325 | 3.0509 | 3.0509 | 3.0509 | 3.0509 | 1.3337 | 1.6928 | 1.6928 | 1.6928 | 1.6928 | 1.6928
2020-09-10 14:00 | Winter | 2.1148 | 3.2518 | 4.9206 | 4.9206 | 4.9206 | 4.9206 | 0.84307 | 1.3796 | 1.8905 | 2.2737 | 2.2737 | 2.2737 | 2.4959 | 3.6002 | 4.3238 | 4.7046 | 5.4662 | 6.2279 | 0.86117 | 2.3393 | 2.934 | 2.934 | 2.934 | 2.934 | 1.3146 | 1.6686 | 1.6686 | 1.6686 | 1.6686 | 1.6686
2020-09-10 15:00 | Winter | 2.0767 | 3.1932 | 4.832 | 4.832 | 4.832 | 4.832 | 0.84879 | 1.3889 | 1.9033 | 2.2892 | 2.2892 | 2.2892 | 2.534 | 3.6552 | 4.3898 | 4.7764 | 5.5497 | 6.3229 | 0.86498 | 2.3496 | 2.947 | 2.947 | 2.947 | 2.947 | 1.2956 | 1.6444 | 1.6444 | 1.6444 | 1.6444 | 1.6444
2020-09-10 16:00 | Winter | 2.0958 | 3.2225 | 4.8763 | 4.8763 | 4.8763 | 4.8763 | 0.84021 | 1.3749 | 1.8841 | 2.266 | 2.266 | 2.266 | 2.4578 | 3.5453 | 4.2578 | 4.6328 | 5.3828 | 6.1328 | 0.87261 | 2.3704 | 2.973 | 2.973 | 2.973 | 2.973 | 1.2008 | 1.5241 | 1.5241 | 1.5241 | 1.5241 | 1.5241
2020-09-10 17:00 | Winter | 2.0196 | 3.1053 | 4.699 | 4.699 | 4.699 | 4.699 | 0.78591 | 1.286 | 1.7624 | 2.1196 | 2.1196 | 2.1196 | 2.3816 | 3.4353 | 4.1258 | 4.4891 | 5.2159 | 5.9426 | 0.88023 | 2.3911 | 2.9989 | 2.9989 | 2.9989 | 2.9989 | 1.1432 | 1.451 | 1.451 | 1.451 | 1.451 | 1.451
2020-09-10 18:00 | Winter | 1.7726 | 2.7255 | 4.1243 | 4.1243 | 4.1243 | 4.1243 | 0.72018 | 1.1785 | 1.615 | 1.9423 | 1.9423 | 1.9423 | 2.4387 | 3.5178 | 4.2248 | 4.5969 | 5.3411 | 6.0852 | 0.87642 | 2.3807 | 2.986 | 2.986 | 2.986 | 2.986 | 0.9138 | 1.1599 | 1.1599 | 1.1599 | 1.1599 | 1.1599
2020-09-10 19:00 | Winter | 1.2014 | 1.8473 | 2.7954 | 2.7954 | 2.7954 | 2.7954 | 0.50061 | 0.81918 | 1.1226 | 1.3501 | 1.3501 | 1.3501 | 2.3352 | 3.3684 | 4.0454 | 4.4017 | 5.1143 | 5.8269 | 0.7964 | 2.1633 | 2.7133 | 2.7133 | 2.7133 | 2.7133 | 0.68589 | 0.87059 | 0.87059 | 0.87059 | 0.87059 | 0.87059
2020-09-10 20:00 | Winter | 1.1241 | 1.7284 | 2.6155 | 2.6155 | 2.6155 | 2.6155 | 0.54871 | 0.89789 | 1.2304 | 1.4799 | 1.4799 | 1.4799 | 2.3054 | 3.3254 | 3.9937 | 4.3455 | 5.049 | 5.7525 | 0.80783 | 2.1944 | 2.7523 | 2.7523 | 2.7523 | 2.7523 | 0.60968 | 0.77386 | 0.77386 | 0.77386 | 0.77386 | 0.77386
2020-09-10 21:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 0.55443 | 0.90724 | 1.2433 | 1.4953 | 1.4953 | 1.4953 | 2.2101 | 3.188 | 3.8287 | 4.1659 | 4.8403 | 5.5147 | 0.73924 | 2.0081 | 2.5186 | 2.5186 | 2.5186 | 2.5186 | 0.57174 | 0.72569 | 0.72569 | 0.72569 | 0.72569 | 0.72569
2020-09-10 22:00 | Winter | 0.97407 | 1.4978 | 2.2664 | 2.2664 | 2.2664 | 2.2664 | 0.5287 | 0.86515 | 1.1856 | 1.4259 | 1.4259 | 1.4259 | 1.9624 | 2.8307 | 3.3996 | 3.699 | 4.2979 | 4.8967 | 0.72018 | 1.9563 | 2.4537 | 2.4537 | 2.4537 | 2.4537 | 0.57158 | 0.72549 | 0.72549 | 0.72549 | 0.72549 | 0.72549
2020-09-10 23:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.46869 | 0.76695 | 1.051 | 1.264 | 1.264 | 1.264 | 1.81 | 2.6109 | 3.1356 | 3.4117 | 3.9641 | 4.5164 | 0.65922 | 1.7907 | 2.246 | 2.246 | 2.246 | 2.246 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-09-11 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.45154 | 0.73889 | 1.0125 | 1.2178 | 1.2178 | 1.2178 | 1.6766 | 2.4185 | 2.9045 | 3.1603 | 3.672 | 4.1836 | 0.64779 | 1.7596 | 2.207 | 2.207 | 2.207 | 2.207 | 0.46921 | 0.59555 | 0.59555 | 0.59555 | 0.59555 | 0.59555
2020-09-11 01:00 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.44011 | 0.72018 | 0.98691 | 1.187 | 1.187 | 1.187 | 1.5784 | 2.2769 | 2.7344 | 2.9753 | 3.4569 | 3.9386 | 0.58682 | 1.594 | 1.9993 | 1.9993 | 1.9993 | 1.9993 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-09-11 02:00 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.43144 | 0.706 | 0.96748 | 1.1636 | 1.1636 | 1.1636 | 1.5623 | 2.2536 | 2.7065 | 2.9449 | 3.4216 | 3.8984 | 0.6516 | 1.77 | 2.22 | 2.22 | 2.22 | 2.22 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-09-11 03:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.44868 | 0.73421 | 1.0061 | 1.2101 | 1.2101 | 1.2101 | 1.5623 | 2.2536 | 2.7065 | 2.9449 | 3.4216 | 3.8984 | 0.59444 | 1.6147 | 2.0253 | 2.0253 | 2.0253 | 2.0253 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-09-11 04:00 | Winter | 1.1241 | 1.7284 | 2.6155 | 2.6155 | 2.6155 | 2.6155 | 0.47726 | 0.78098 | 1.0702 | 1.2872 | 1.2872 | 1.2872 | 1.5242 | 2.1986 | 2.6405 | 2.873 | 3.3382 | 3.8033 | 0.59825 | 1.6251 | 2.0382 | 2.0382 | 2.0382 | 2.0382 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-09-11 05:00 | Winter | 1.238 | 1.9035 | 2.8804 | 2.8804 | 2.8804 | 2.8804 | 0.55443 | 0.90724 | 1.2433 | 1.4953 | 1.4953 | 1.4953 | 1.9053 | 2.7483 | 3.3006 | 3.5913 | 4.1727 | 4.7541 | 0.64779 | 1.7596 | 2.207 | 2.207 | 2.207 | 2.207 | 0.72365 | 0.91851 | 0.91851 | 0.91851 | 0.91851 | 0.91851
2020-09-11 06:00 | Winter | 1.4294 | 2.1978 | 3.3258 | 3.3258 | 3.3258 | 3.3258 | 0.71161 | 1.1645 | 1.5957 | 1.9192 | 1.9192 | 1.9192 | 1.9243 | 2.7758 | 3.3336 | 3.6272 | 4.2144 | 4.8016 | 0.72018 | 1.9563 | 2.4537 | 2.4537 | 2.4537 | 2.4537 | 0.91162 | 1.1571 | 1.1571 | 1.1571 | 1.1571 | 1.1571
2020-09-11 07:00 | Winter | 1.9537 | 3.004 | 4.5457 | 4.5457 | 4.5457 | 4.5457 | 0.81735 | 1.3375 | 1.8328 | 2.2044 | 2.2044 | 2.2044 | 2.191 | 3.1605 | 3.7957 | 4.13 | 4.7986 | 5.4672 | 0.84593 | 2.2979 | 2.8821 | 2.8821 | 2.8821 | 2.8821 | 1.1241 | 1.4268 | 1.4268 | 1.4268 | 1.4268 | 1.4268
2020-09-11 08:00 | Winter | 2.2101 | 3.3983 | 5.1423 | 5.1423 | 5.1423 | 5.1423 | 0.95167 | 1.5573 | 2.1341 | 2.5666 | 2.5666 | 2.5666 | 2.4197 | 3.4903 | 4.1918 | 4.561 | 5.2993 | 6.0377 | 0.89166 | 2.4221 | 3.0379 | 3.0379 | 3.0379 | 3.0379 | 1.3146 | 1.6686 | 1.6686 | 1.6686 | 1.6686 | 1.6686
2020-09-11 09:00 | Winter | 2.191 | 3.369 | 5.0979 | 5.0979 | 5.0979 | 5.0979 | 0.95739 | 1.5666 | 2.1469 | 2.582 | 2.582 | 2.582 | 2.4197 | 3.4903 | 4.1918 | 4.561 | 5.2993 | 6.0377 | 0.88023 | 2.3911 | 2.9989 | 2.9989 | 2.9989 | 2.9989 | 1.4099 | 1.7895 | 1.7895 | 1.7895 | 1.7895 | 1.7895
2020-09-11 10:00 | Winter | 2.0767 | 3.1932 | 4.832 | 4.832 | 4.832 | 4.832 | 0.87451 | 1.431 | 1.961 | 2.3585 | 2.3585 | 2.3585 | 2.5721 | 3.7102 | 4.4558 | 4.8483 | 5.6331 | 6.418 | 0.85736 | 2.3289 | 2.9211 | 2.9211 | 2.9211 | 2.9211 | 1.3921 | 1.767 | 1.767 | 1.767 | 1.767 | 1.767
2020-09-11 11:00 | Winter | 2.172 | 3.3397 | 5.0536 | 5.0536 | 5.0536 | 5.0536 | 0.82878 | 1.3562 | 1.8585 | 2.2352 | 2.2352 | 2.2352 | 2.4768 | 3.5728 | 4.2908 | 4.6687 | 5.4245 | 6.1803 | 0.83069 | 2.2565 | 2.8302 | 2.8302 | 2.8302 | 2.8302 | 1.3718 | 1.7412 | 1.7412 | 1.7412 | 1.7412 | 1.7412
2020-09-11 12:00 | Winter | 2.1148 | 3.2518 | 4.9206 | 4.9206 | 4.9206 | 4.9206 | 0.85736 | 1.403 | 1.9226 | 2.3123 | 2.3123 | 2.3123 | 2.4959 | 3.6002 | 4.3238 | 4.7046 | 5.4662 | 6.2279 | 0.78496 | 2.1323 | 2.6744 | 2.6744 | 2.6744 | 2.6744 | 1.3104 | 1.6632 | 1.6632 | 1.6632 | 1.6632 | 1.6632
2020-09-11 13:00 | Winter | 2.2482 | 3.4569 | 5.2309 | 5.2309 | 5.2309 | 5.2309 | 0.85165 | 1.3936 | 1.9098 | 2.2969 | 2.2969 | 2.2969 | 2.6102 | 3.7651 | 4.5218 | 4.9201 | 5.7166 | 6.5131 | 0.7964 | 2.1633 | 2.7133 | 2.7133 | 2.7133 | 2.7133 | 1.2956 | 1.6444 | 1.6444 | 1.6444 | 1.6444 | 1.6444
2020-09-11 14:00 | Winter | 2.1529 | 3.3104 | 5.0093 | 5.0093 | 5.0093 | 5.0093 | 0.80878 | 1.3235 | 1.8136 | 2.1812 | 2.1812 | 2.1812 | 2.553 | 3.6827 | 4.4228 | 4.8123 | 5.5914 | 6.3705 | 0.79258 | 2.153 | 2.7003 | 2.7003 | 2.7003 | 2.7003 | 1.2765 | 1.6203 | 1.6203 | 1.6203 | 1.6203 | 1.6203
2020-09-11 15:00 | Winter | 2.1529 | 3.3104 | 5.0093 | 5.0093 | 5.0093 | 5.0093 | 0.78591 | 1.286 | 1.7624 | 2.1196 | 2.1196 | 2.1196 | 2.553 | 3.6827 | 4.4228 | 4.8123 | 5.5914 | 6.3705 | 0.9069 | 2.4635 | 3.0898 | 3.0898 | 3.0898 | 3.0898 | 1.2384 | 1.5719 | 1.5719 | 1.5719 | 1.5719 | 1.5719
2020-09-11 16:00 | Winter | 2.191 | 3.369 | 5.0979 | 5.0979 | 5.0979 | 5.0979 | 0.86879 | 1.4217 | 1.9482 | 2.3431 | 2.3431 | 2.3431 | 2.4578 | 3.5453 | 4.2578 | 4.6328 | 5.3828 | 6.1328 | 0.83069 | 2.2565 | 2.8302 | 2.8302 | 2.8302 | 2.8302 | 1.1813 | 1.4993 | 1.4993 | 1.4993 | 1.4993 | 1.4993
2020-09-11 17:00 | Winter | 1.9895 | 3.0591 | 4.6291 | 4.6291 | 4.6291 | 4.6291 | 0.84879 | 1.3889 | 1.9033 | 2.2892 | 2.2892 | 2.2892 | 2.3625 | 3.4079 | 4.0927 | 4.4532 | 5.1741 | 5.8951 | 0.81164 | 2.2047 | 2.7653 | 2.7653 | 2.7653 | 2.7653 | 1.0862 | 1.3787 | 1.3787 | 1.3787 | 1.3787 | 1.3787
2020-09-11 18:00 | Winter | 1.7719 | 2.7245 | 4.1227 | 4.1227 | 4.1227 | 4.1227 | 0.7259 | 1.1878 | 1.6278 | 1.9577 | 1.9577 | 1.9577 | 2.3054 | 3.3254 | 3.9937 | 4.3455 | 5.049 | 5.7525 | 0.82688 | 2.2461 | 2.8172 | 2.8172 | 2.8172 | 2.8172 | 0.89588 | 1.1371 | 1.1371 | 1.1371 | 1.1371 | 1.1371
2020-09-11 19:00 | Winter | 1.1631 | 1.7885 | 2.7063 | 2.7063 | 2.7063 | 2.7063 | 0.61444 | 1.0054 | 1.3778 | 1.6571 | 1.6571 | 1.6571 | 2.2291 | 3.2155 | 3.8617 | 4.2018 | 4.8821 | 5.5623 | 0.76972 | 2.0909 | 2.6225 | 2.6225 | 2.6225 | 2.6225 | 0.66684 | 0.84641 | 0.84641 | 0.84641 | 0.84641 | 0.84641
2020-09-11 20:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 0.57729 | 0.94465 | 1.2945 | 1.5569 | 1.5569 | 1.5569 | 2.1529 | 3.1056 | 3.7297 | 4.0582 | 4.7151 | 5.3721 | 0.74686 | 2.0288 | 2.5446 | 2.5446 | 2.5446 | 2.5446 | 0.66684 | 0.84641 | 0.84641 | 0.84641 | 0.84641 | 0.84641
2020-09-11 21:00 | Winter | 1.0288 | 1.582 | 2.3938 | 2.3938 | 2.3938 | 2.3938 | 0.54585 | 0.89321 | 1.224 | 1.4721 | 1.4721 | 1.4721 | 2.0577 | 2.9681 | 3.5647 | 3.8786 | 4.5065 | 5.1344 | 0.71637 | 1.946 | 2.4407 | 2.4407 | 2.4407 | 2.4407 | 0.60968 | 0.77386 | 0.77386 | 0.77386 | 0.77386 | 0.77386
2020-09-11 22:00 | Winter | 0.98284 | 1.5112 | 2.2868 | 2.2868 | 2.2868 | 2.2868 | 0.54585 | 0.89321 | 1.224 | 1.4721 | 1.4721 | 1.4721 | 1.9055 | 2.7487 | 3.3011 | 3.5918 | 4.1733 | 4.7548 | 0.71637 | 1.946 | 2.4407 | 2.4407 | 2.4407 | 2.4407 | 0.59063 | 0.74967 | 0.74967 | 0.74967 | 0.74967 | 0.74967
2020-09-11 23:00 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.48584 | 0.79501 | 1.0895 | 1.3103 | 1.3103 | 1.3103 | 1.7662 | 2.5477 | 3.0597 | 3.3292 | 3.8682 | 4.4071 | 0.67827 | 1.8425 | 2.3109 | 2.3109 | 2.3109 | 2.3109 | 0.55252 | 0.70131 | 0.70131 | 0.70131 | 0.70131 | 0.70131
2020-09-12 | Winter | 0.93358 | 1.4355 | 2.1722 | 2.1722 | 2.1722 | 2.1722 | 0.4544 | 0.74356 | 1.019 | 1.2255 | 1.2255 | 1.2255 | 1.6957 | 2.446 | 2.9375 | 3.1963 | 3.7137 | 4.2311 | 0.60968 | 1.6561 | 2.0772 | 2.0772 | 2.0772 | 2.0772 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-09-12 01:00 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.45726 | 0.74824 | 1.0254 | 1.2332 | 1.2332 | 1.2332 | 1.5623 | 2.2536 | 2.7065 | 2.9449 | 3.4216 | 3.8984 | 0.60968 | 1.6561 | 2.0772 | 2.0772 | 2.0772 | 2.0772 | 0.55252 | 0.70131 | 0.70131 | 0.70131 | 0.70131 | 0.70131
2020-09-12 02:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.42868 | 0.70147 | 0.96128 | 1.1561 | 1.1561 | 1.1561 | 1.5433 | 2.2261 | 2.6735 | 2.909 | 3.3799 | 3.8508 | 0.62111 | 1.6872 | 2.1161 | 2.1161 | 2.1161 | 2.1161 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-09-12 03:00 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.45726 | 0.74824 | 1.0254 | 1.2332 | 1.2332 | 1.2332 | 1.5623 | 2.2536 | 2.7065 | 2.9449 | 3.4216 | 3.8984 | 0.55633 | 1.5112 | 1.8954 | 1.8954 | 1.8954 | 1.8954 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-09-12 04:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.4544 | 0.74356 | 1.019 | 1.2255 | 1.2255 | 1.2255 | 1.5814 | 2.2811 | 2.7395 | 2.9808 | 3.4633 | 3.9459 | 0.59063 | 1.6044 | 2.0123 | 2.0123 | 2.0123 | 2.0123 | 0.49537 | 0.62876 | 0.62876 | 0.62876 | 0.62876 | 0.62876
2020-09-12 05:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.47726 | 0.78098 | 1.0702 | 1.2872 | 1.2872 | 1.2872 | 1.6576 | 2.391 | 2.8715 | 3.1244 | 3.6302 | 4.1361 | 0.57539 | 1.563 | 1.9603 | 1.9603 | 1.9603 | 1.9603 | 0.49537 | 0.62876 | 0.62876 | 0.62876 | 0.62876 | 0.62876
2020-09-12 06:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.54871 | 0.89789 | 1.2304 | 1.4799 | 1.4799 | 1.4799 | 1.7719 | 2.5559 | 3.0696 | 3.3399 | 3.8806 | 4.4213 | 0.52966 | 1.4388 | 1.8046 | 1.8046 | 1.8046 | 1.8046 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-09-12 07:00 | Winter | 1.0288 | 1.582 | 2.3938 | 2.3938 | 2.3938 | 2.3938 | 0.60587 | 0.99142 | 1.3586 | 1.634 | 1.634 | 1.634 | 1.8682 | 2.6948 | 3.2364 | 3.5214 | 4.0915 | 4.6616 | 0.68589 | 1.8632 | 2.3368 | 2.3368 | 2.3368 | 2.3368 | 0.5334 | 0.67703 | 0.67703 | 0.67703 | 0.67703 | 0.67703
2020-09-12 08:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 0.65731 | 1.0756 | 1.474 | 1.7727 | 1.7727 | 1.7727 | 2.0386 | 2.9407 | 3.5316 | 3.8427 | 4.4648 | 5.0869 | 0.6897 | 1.8735 | 2.3498 | 2.3498 | 2.3498 | 2.3498 | 0.57158 | 0.72549 | 0.72549 | 0.72549 | 0.72549 | 0.72549
2020-09-12 09:00 | Winter | 0.9996 | 1.537 | 2.3258 | 2.3258 | 2.3258 | 2.3258 | 0.73733 | 1.2065 | 1.6534 | 1.9886 | 1.9886 | 1.9886 | 2.1529 | 3.1056 | 3.7297 | 4.0582 | 4.7151 | 5.3721 | 0.6897 | 1.8735 | 2.3498 | 2.3498 | 2.3498 | 2.3498 | 0.60968 | 0.77386 | 0.77386 | 0.77386 | 0.77386 | 0.77386
2020-09-12 10:00 | Winter | 0.93358 | 1.4355 | 2.1722 | 2.1722 | 2.1722 | 2.1722 | 0.71733 | 1.1738 | 1.6085 | 1.9346 | 1.9346 | 1.9346 | 2.1339 | 3.0781 | 3.6967 | 4.0223 | 4.6734 | 5.3246 | 0.69351 | 1.8839 | 2.3628 | 2.3628 | 2.3628 | 2.3628 | 0.62091 | 0.78811 | 0.78811 | 0.78811 | 0.78811 | 0.78811
2020-09-12 11:00 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.59158 | 0.96804 | 1.3266 | 1.5955 | 1.5955 | 1.5955 | 2.1142 | 3.0497 | 3.6626 | 3.9852 | 4.6303 | 5.2755 | 0.64397 | 1.7493 | 2.194 | 2.194 | 2.194 | 2.194 | 0.62873 | 0.79804 | 0.79804 | 0.79804 | 0.79804 | 0.79804
2020-09-12 12:00 | Winter | 0.91452 | 1.4062 | 2.1278 | 2.1278 | 2.1278 | 2.1278 | 0.48298 | 0.79033 | 1.083 | 1.3026 | 1.3026 | 1.3026 | 2.1148 | 3.0506 | 3.6637 | 3.9863 | 4.6317 | 5.277 | 0.60206 | 1.6354 | 2.0512 | 2.0512 | 2.0512 | 2.0512 | 0.59063 | 0.74967 | 0.74967 | 0.74967 | 0.74967 | 0.74967
2020-09-12 13:00 | Winter | 0.91452 | 1.4062 | 2.1278 | 2.1278 | 2.1278 | 2.1278 | 0.44583 | 0.72953 | 0.99973 | 1.2024 | 1.2024 | 1.2024 | 2.0005 | 2.8857 | 3.4656 | 3.7709 | 4.3813 | 4.9918 | 0.5792 | 1.5733 | 1.9733 | 1.9733 | 1.9733 | 1.9733 | 0.59063 | 0.74967 | 0.74967 | 0.74967 | 0.74967 | 0.74967
2020-09-12 14:00 | Winter | 0.87642 | 1.3476 | 2.0392 | 2.0392 | 2.0392 | 2.0392 | 0.49441 | 0.80903 | 1.1087 | 1.3334 | 1.3334 | 1.3334 | 2.0386 | 2.9407 | 3.5316 | 3.8427 | 4.4648 | 5.0869 | 0.6516 | 1.77 | 2.22 | 2.22 | 2.22 | 2.22 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-09-12 15:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.50298 | 0.82306 | 1.1279 | 1.3565 | 1.3565 | 1.3565 | 2.0577 | 2.9681 | 3.5647 | 3.8786 | 4.5065 | 5.1344 | 0.6516 | 1.77 | 2.22 | 2.22 | 2.22 | 2.22 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-09-12 16:00 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.51442 | 0.84177 | 1.1535 | 1.3874 | 1.3874 | 1.3874 | 2.0577 | 2.9681 | 3.5647 | 3.8786 | 4.5065 | 5.1344 | 0.67446 | 1.8321 | 2.2979 | 2.2979 | 2.2979 | 2.2979 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-09-12 17:00 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.51156 | 0.83709 | 1.1471 | 1.3797 | 1.3797 | 1.3797 | 2.0182 | 2.9113 | 3.4963 | 3.8043 | 4.4202 | 5.036 | 0.73162 | 1.9874 | 2.4926 | 2.4926 | 2.4926 | 2.4926 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-09-12 18:00 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.54299 | 0.88854 | 1.2176 | 1.4644 | 1.4644 | 1.4644 | 2.1339 | 3.0781 | 3.6967 | 4.0223 | 4.6734 | 5.3246 | 0.8345 | 2.2668 | 2.8432 | 2.8432 | 2.8432 | 2.8432 | 0.55252 | 0.70131 | 0.70131 | 0.70131 | 0.70131 | 0.70131
2020-09-12 19:00 | Winter | 0.93358 | 1.4355 | 2.1722 | 2.1722 | 2.1722 | 2.1722 | 0.56014 | 0.9166 | 1.2561 | 1.5107 | 1.5107 | 1.5107 | 2.1339 | 3.0781 | 3.6967 | 4.0223 | 4.6734 | 5.3246 | 0.82307 | 2.2358 | 2.8042 | 2.8042 | 2.8042 | 2.8042 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-09-12 20:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.52299 | 0.8558 | 1.1728 | 1.4105 | 1.4105 | 1.4105 | 2.0577 | 2.9681 | 3.5647 | 3.8786 | 4.5065 | 5.1344 | 0.75067 | 2.0391 | 2.5575 | 2.5575 | 2.5575 | 2.5575 | 0.55252 | 0.70131 | 0.70131 | 0.70131 | 0.70131 | 0.70131
2020-09-12 21:00 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.48584 | 0.79501 | 1.0895 | 1.3103 | 1.3103 | 1.3103 | 1.9815 | 2.8582 | 3.4326 | 3.735 | 4.3396 | 4.9443 | 0.74305 | 2.0184 | 2.5316 | 2.5316 | 2.5316 | 2.5316 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-09-12 22:00 | Winter | 0.93358 | 1.4355 | 2.1722 | 2.1722 | 2.1722 | 2.1722 | 0.39724 | 0.65003 | 0.89079 | 1.0713 | 1.0713 | 1.0713 | 1.8744 | 2.7037 | 3.2471 | 3.533 | 4.105 | 4.677 | 0.77353 | 2.1012 | 2.6354 | 2.6354 | 2.6354 | 2.6354 | 0.4819 | 0.61167 | 0.61167 | 0.61167 | 0.61167 | 0.61167
2020-09-12 23:00 | Winter | 0.91452 | 1.4062 | 2.1278 | 2.1278 | 2.1278 | 2.1278 | 0.47726 | 0.78098 | 1.0702 | 1.2872 | 1.2872 | 1.2872 | 1.7719 | 2.5559 | 3.0696 | 3.3399 | 3.8806 | 4.4213 | 0.64397 | 1.7493 | 2.194 | 2.194 | 2.194 | 2.194 | 0.49537 | 0.62876 | 0.62876 | 0.62876 | 0.62876 | 0.62876
2020-09-13 | Winter | 0.91452 | 1.4062 | 2.1278 | 2.1278 | 2.1278 | 2.1278 | 0.44583 | 0.72953 | 0.99973 | 1.2024 | 1.2024 | 1.2024 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.60206 | 1.6354 | 2.0512 | 2.0512 | 2.0512 | 2.0512 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-09-13 01:00 | Winter | 0.91452 | 1.4062 | 2.1278 | 2.1278 | 2.1278 | 2.1278 | 0.42011 | 0.68744 | 0.94205 | 1.133 | 1.133 | 1.133 | 1.5015 | 2.1659 | 2.6011 | 2.8302 | 3.2884 | 3.7466 | 0.5792 | 1.5733 | 1.9733 | 1.9733 | 1.9733 | 1.9733 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-09-13 02:00 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.45726 | 0.74824 | 1.0254 | 1.2332 | 1.2332 | 1.2332 | 1.5242 | 2.1986 | 2.6405 | 2.873 | 3.3382 | 3.8033 | 0.53728 | 1.4595 | 1.8305 | 1.8305 | 1.8305 | 1.8305 | 0.49537 | 0.62876 | 0.62876 | 0.62876 | 0.62876 | 0.62876
2020-09-13 03:00 | Winter | 0.93358 | 1.4355 | 2.1722 | 2.1722 | 2.1722 | 2.1722 | 0.41439 | 0.67809 | 0.92924 | 1.1176 | 1.1176 | 1.1176 | 1.5433 | 2.2261 | 2.6735 | 2.909 | 3.3799 | 3.8508 | 0.51823 | 1.4077 | 1.7656 | 1.7656 | 1.7656 | 1.7656 | 0.49537 | 0.62876 | 0.62876 | 0.62876 | 0.62876 | 0.62876
2020-09-13 04:00 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.38581 | 0.63133 | 0.86515 | 1.0405 | 1.0405 | 1.0405 | 1.5052 | 2.1711 | 2.6075 | 2.8371 | 3.2964 | 3.7557 | 0.56776 | 1.5423 | 1.9344 | 1.9344 | 1.9344 | 1.9344 | 0.45726 | 0.58039 | 0.58039 | 0.58039 | 0.58039 | 0.58039
2020-09-13 05:00 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.47441 | 0.7763 | 1.0638 | 1.2795 | 1.2795 | 1.2795 | 1.5623 | 2.2536 | 2.7065 | 2.9449 | 3.4216 | 3.8984 | 0.56395 | 1.5319 | 1.9214 | 1.9214 | 1.9214 | 1.9214 | 0.45726 | 0.58039 | 0.58039 | 0.58039 | 0.58039 | 0.58039
2020-09-13 06:00 | Winter | 0.92445 | 1.4215 | 2.1509 | 2.1509 | 2.1509 | 2.1509 | 0.50298 | 0.82306 | 1.1279 | 1.3565 | 1.3565 | 1.3565 | 1.6957 | 2.446 | 2.9375 | 3.1963 | 3.7137 | 4.2311 | 0.57157 | 1.5526 | 1.9474 | 1.9474 | 1.9474 | 1.9474 | 0.49537 | 0.62876 | 0.62876 | 0.62876 | 0.62876 | 0.62876
2020-09-13 07:00 | Winter | 0.91452 | 1.4062 | 2.1278 | 2.1278 | 2.1278 | 2.1278 | 0.54299 | 0.88854 | 1.2176 | 1.4644 | 1.4644 | 1.4644 | 1.7575 | 2.5351 | 3.0446 | 3.3127 | 3.849 | 4.3853 | 0.59444 | 1.6147 | 2.0253 | 2.0253 | 2.0253 | 2.0253 | 0.48121 | 0.61079 | 0.61079 | 0.61079 | 0.61079 | 0.61079
2020-09-13 08:00 | Winter | 0.93358 | 1.4355 | 2.1722 | 2.1722 | 2.1722 | 2.1722 | 0.51727 | 0.84645 | 1.1599 | 1.3951 | 1.3951 | 1.3951 | 2.0196 | 2.9132 | 3.4986 | 3.8068 | 4.4231 | 5.0393 | 0.63635 | 1.7286 | 2.1681 | 2.1681 | 2.1681 | 2.1681 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-09-13 09:00 | Winter | 0.91452 | 1.4062 | 2.1278 | 2.1278 | 2.1278 | 2.1278 | 0.55443 | 0.90724 | 1.2433 | 1.4953 | 1.4953 | 1.4953 | 2.0958 | 3.0231 | 3.6307 | 3.9504 | 4.59 | 5.2295 | 0.67065 | 1.8218 | 2.2849 | 2.2849 | 2.2849 | 2.2849 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-09-13 10:00 | Winter | 1.0288 | 1.582 | 2.3938 | 2.3938 | 2.3938 | 2.3938 | 0.49155 | 0.80436 | 1.1023 | 1.3257 | 1.3257 | 1.3257 | 2.1675 | 3.1266 | 3.755 | 4.0857 | 4.7471 | 5.4085 | 0.69351 | 1.8839 | 2.3628 | 2.3628 | 2.3628 | 2.3628 | 0.59063 | 0.74967 | 0.74967 | 0.74967 | 0.74967 | 0.74967
2020-09-13 11:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.49441 | 0.80903 | 1.1087 | 1.3334 | 1.3334 | 1.3334 | 2.2291 | 3.2155 | 3.8617 | 4.2018 | 4.8821 | 5.5623 | 0.68208 | 1.8528 | 2.3239 | 2.3239 | 2.3239 | 2.3239 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-09-13 12:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.55157 | 0.90257 | 1.2368 | 1.4876 | 1.4876 | 1.4876 | 2.1948 | 3.166 | 3.8023 | 4.1372 | 4.8069 | 5.4767 | 0.69351 | 1.8839 | 2.3628 | 2.3628 | 2.3628 | 2.3628 | 0.59063 | 0.74967 | 0.74967 | 0.74967 | 0.74967 | 0.74967
2020-09-13 13:00 | Winter | 0.91452 | 1.4062 | 2.1278 | 2.1278 | 2.1278 | 2.1278 | 0.43725 | 0.7155 | 0.98051 | 1.1793 | 1.1793 | 1.1793 | 2.1529 | 3.1056 | 3.7297 | 4.0582 | 4.7151 | 5.3721 | 0.67065 | 1.8218 | 2.2849 | 2.2849 | 2.2849 | 2.2849 | 0.55274 | 0.70158 | 0.70158 | 0.70158 | 0.70158 | 0.70158
2020-09-13 14:00 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.45726 | 0.74824 | 1.0254 | 1.2332 | 1.2332 | 1.2332 | 2.1148 | 3.0506 | 3.6637 | 3.9863 | 4.6317 | 5.277 | 0.61349 | 1.6665 | 2.0902 | 2.0902 | 2.0902 | 2.0902 | 0.55252 | 0.70131 | 0.70131 | 0.70131 | 0.70131 | 0.70131
2020-09-13 15:00 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.46583 | 0.76227 | 1.0446 | 1.2563 | 1.2563 | 1.2563 | 2.1183 | 3.0556 | 3.6697 | 3.9929 | 4.6393 | 5.2857 | 0.64016 | 1.7389 | 2.1811 | 2.1811 | 2.1811 | 2.1811 | 0.55252 | 0.70131 | 0.70131 | 0.70131 | 0.70131 | 0.70131
2020-09-13 16:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.45868 | 0.75058 | 1.0286 | 1.2371 | 1.2371 | 1.2371 | 2.1339 | 3.0781 | 3.6967 | 4.0223 | 4.6734 | 5.3246 | 0.64397 | 1.7493 | 2.194 | 2.194 | 2.194 | 2.194 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-09-13 17:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.47565 | 0.77833 | 1.0666 | 1.2828 | 1.2828 | 1.2828 | 2.1148 | 3.0506 | 3.6637 | 3.9863 | 4.6317 | 5.277 | 0.67827 | 1.8425 | 2.3109 | 2.3109 | 2.3109 | 2.3109 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-09-13 18:00 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.50013 | 0.81839 | 1.1215 | 1.3488 | 1.3488 | 1.3488 | 2.1529 | 3.1056 | 3.7297 | 4.0582 | 4.7151 | 5.3721 | 0.75067 | 2.0391 | 2.5575 | 2.5575 | 2.5575 | 2.5575 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-09-13 19:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.48584 | 0.79501 | 1.0895 | 1.3103 | 1.3103 | 1.3103 | 2.1339 | 3.0781 | 3.6967 | 4.0223 | 4.6734 | 5.3246 | 0.724 | 1.9667 | 2.4667 | 2.4667 | 2.4667 | 2.4667 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-09-13 20:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.46869 | 0.76695 | 1.051 | 1.264 | 1.264 | 1.264 | 2.037 | 2.9384 | 3.5289 | 3.8397 | 4.4613 | 5.0829 | 0.71637 | 1.946 | 2.4407 | 2.4407 | 2.4407 | 2.4407 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-09-13 21:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.46297 | 0.75759 | 1.0382 | 1.2486 | 1.2486 | 1.2486 | 1.9434 | 2.8032 | 3.3666 | 3.6631 | 4.2562 | 4.8492 | 0.68589 | 1.8632 | 2.3368 | 2.3368 | 2.3368 | 2.3368 | 0.55252 | 0.70131 | 0.70131 | 0.70131 | 0.70131 | 0.70131
2020-09-13 22:00 | Winter | 0.94784 | 1.4574 | 2.2054 | 2.2054 | 2.2054 | 2.2054 | 0.44297 | 0.72486 | 0.99332 | 1.1947 | 1.1947 | 1.1947 | 1.81 | 2.6109 | 3.1356 | 3.4117 | 3.9641 | 4.5164 | 0.6897 | 1.8735 | 2.3498 | 2.3498 | 2.3498 | 2.3498 | 0.55252 | 0.70131 | 0.70131 | 0.70131 | 0.70131 | 0.70131
2020-09-13 23:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.43725 | 0.7155 | 0.98051 | 1.1793 | 1.1793 | 1.1793 | 1.6957 | 2.446 | 2.9375 | 3.1963 | 3.7137 | 4.2311 | 0.61349 | 1.6665 | 2.0902 | 2.0902 | 2.0902 | 2.0902 | 0.49537 | 0.62876 | 0.62876 | 0.62876 | 0.62876 | 0.62876
2020-09-14 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.43439 | 0.71083 | 0.9741 | 1.1715 | 1.1715 | 1.1715 | 1.5623 | 2.2536 | 2.7065 | 2.9449 | 3.4216 | 3.8984 | 0.57539 | 1.563 | 1.9603 | 1.9603 | 1.9603 | 1.9603 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-09-14 01:00 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.48298 | 0.79033 | 1.083 | 1.3026 | 1.3026 | 1.3026 | 1.5433 | 2.2261 | 2.6735 | 2.909 | 3.3799 | 3.8508 | 0.5449 | 1.4802 | 1.8565 | 1.8565 | 1.8565 | 1.8565 | 0.53276 | 0.67622 | 0.67622 | 0.67622 | 0.67622 | 0.67622
2020-09-14 02:00 | Winter | 1.0669 | 1.6405 | 2.4825 | 2.4825 | 2.4825 | 2.4825 | 0.46583 | 0.76227 | 1.0446 | 1.2563 | 1.2563 | 1.2563 | 1.5623 | 2.2536 | 2.7065 | 2.9449 | 3.4216 | 3.8984 | 0.53728 | 1.4595 | 1.8305 | 1.8305 | 1.8305 | 1.8305 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-09-14 03:00 | Winter | 1.086 | 1.6698 | 2.5268 | 2.5268 | 2.5268 | 2.5268 | 0.4001 | 0.65471 | 0.89719 | 1.0791 | 1.0791 | 1.0791 | 1.5242 | 2.1986 | 2.6405 | 2.873 | 3.3382 | 3.8033 | 0.54871 | 1.4905 | 1.8695 | 1.8695 | 1.8695 | 1.8695 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-09-14 04:00 | Winter | 1.1241 | 1.7284 | 2.6155 | 2.6155 | 2.6155 | 2.6155 | 0.48869 | 0.79968 | 1.0959 | 1.318 | 1.318 | 1.318 | 1.5832 | 2.2837 | 2.7427 | 2.9842 | 3.4674 | 3.9505 | 0.5792 | 1.5733 | 1.9733 | 1.9733 | 1.9733 | 1.9733 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-09-14 05:00 | Winter | 1.2765 | 1.9628 | 2.9701 | 2.9701 | 2.9701 | 2.9701 | 0.52539 | 0.85972 | 1.1781 | 1.417 | 1.417 | 1.417 | 1.7449 | 2.517 | 3.0228 | 3.2891 | 3.8215 | 4.354 | 0.62492 | 1.6975 | 2.1291 | 2.1291 | 2.1291 | 2.1291 | 0.78316 | 0.99405 | 0.99405 | 0.99405 | 0.99405 | 0.99405
2020-09-14 06:00 | Winter | 1.4476 | 2.2258 | 3.3681 | 3.3681 | 3.3681 | 3.3681 | 0.75734 | 1.2393 | 1.6983 | 2.0425 | 2.0425 | 2.0425 | 2.005 | 2.8921 | 3.4734 | 3.7793 | 4.3911 | 5.0029 | 0.70113 | 1.9046 | 2.3888 | 2.3888 | 2.3888 | 2.3888 | 0.96938 | 1.2304 | 1.2304 | 1.2304 | 1.2304 | 1.2304
2020-09-14 07:00 | Winter | 1.9807 | 3.0456 | 4.6086 | 4.6086 | 4.6086 | 4.6086 | 0.82307 | 1.3468 | 1.8457 | 2.2198 | 2.2198 | 2.2198 | 2.2482 | 3.243 | 3.8947 | 4.2377 | 4.9238 | 5.6098 | 0.88023 | 2.3911 | 2.9989 | 2.9989 | 2.9989 | 2.9989 | 1.2384 | 1.5719 | 1.5719 | 1.5719 | 1.5719 | 1.5719
2020-09-14 08:00 | Winter | 2.2482 | 3.4569 | 5.2309 | 5.2309 | 5.2309 | 5.2309 | 0.94596 | 1.5479 | 2.1212 | 2.5512 | 2.5512 | 2.5512 | 2.3625 | 3.4079 | 4.0927 | 4.4532 | 5.1741 | 5.8951 | 0.81164 | 2.2047 | 2.7653 | 2.7653 | 2.7653 | 2.7653 | 1.467 | 1.8621 | 1.8621 | 1.8621 | 1.8621 | 1.8621
2020-09-14 09:00 | Winter | 2.2291 | 3.4276 | 5.1866 | 5.1866 | 5.1866 | 5.1866 | 0.93167 | 1.5245 | 2.0892 | 2.5127 | 2.5127 | 2.5127 | 2.4578 | 3.5453 | 4.2578 | 4.6328 | 5.3828 | 6.1328 | 0.96025 | 2.6084 | 3.2716 | 3.2716 | 3.2716 | 3.2716 | 1.4289 | 1.8137 | 1.8137 | 1.8137 | 1.8137 | 1.8137
2020-09-14 10:00 | Winter | 2.3625 | 3.6326 | 5.4969 | 5.4969 | 5.4969 | 5.4969 | 0.8002 | 1.3094 | 1.7944 | 2.1581 | 2.1581 | 2.1581 | 2.4768 | 3.5728 | 4.2908 | 4.6687 | 5.4245 | 6.1803 | 0.87201 | 2.3687 | 2.971 | 2.971 | 2.971 | 2.971 | 1.448 | 1.8379 | 1.8379 | 1.8379 | 1.8379 | 1.8379
2020-09-14 11:00 | Winter | 2.3435 | 3.6034 | 5.4526 | 5.4526 | 5.4526 | 5.4526 | 1.0145 | 1.6602 | 2.275 | 2.7362 | 2.7362 | 2.7362 | 2.4768 | 3.5728 | 4.2908 | 4.6687 | 5.4245 | 6.1803 | 0.95644 | 2.5981 | 3.2586 | 3.2586 | 3.2586 | 3.2586 | 1.4289 | 1.8137 | 1.8137 | 1.8137 | 1.8137 | 1.8137
2020-09-14 12:00 | Winter | 2.4006 | 3.6912 | 5.5856 | 5.5856 | 5.5856 | 5.5856 | 0.81164 | 1.3281 | 1.82 | 2.189 | 2.189 | 2.189 | 2.4768 | 3.5728 | 4.2908 | 4.6687 | 5.4245 | 6.1803 | 0.78496 | 2.1323 | 2.6744 | 2.6744 | 2.6744 | 2.6744 | 1.3718 | 1.7412 | 1.7412 | 1.7412 | 1.7412 | 1.7412
2020-09-14 13:00 | Winter | 2.2863 | 3.5155 | 5.3196 | 5.3196 | 5.3196 | 5.3196 | 0.74019 | 1.2112 | 1.6598 | 1.9963 | 1.9963 | 1.9963 | 2.4387 | 3.5178 | 4.2248 | 4.5969 | 5.3411 | 6.0852 | 0.76591 | 2.0805 | 2.6095 | 2.6095 | 2.6095 | 2.6095 | 1.3908 | 1.7654 | 1.7654 | 1.7654 | 1.7654 | 1.7654
2020-09-14 14:00 | Winter | 2.2673 | 3.4862 | 5.2753 | 5.2753 | 5.2753 | 5.2753 | 0.76305 | 1.2486 | 1.7111 | 2.0579 | 2.0579 | 2.0579 | 2.4387 | 3.5178 | 4.2248 | 4.5969 | 5.3411 | 6.0852 | 0.8345 | 2.2668 | 2.8432 | 2.8432 | 2.8432 | 2.8432 | 1.3337 | 1.6928 | 1.6928 | 1.6928 | 1.6928 | 1.6928
2020-09-14 15:00 | Winter | 2.3435 | 3.6034 | 5.4526 | 5.4526 | 5.4526 | 5.4526 | 0.79163 | 1.2954 | 1.7752 | 2.135 | 2.135 | 2.135 | 2.3816 | 3.4353 | 4.1258 | 4.4891 | 5.2159 | 5.9426 | 0.81926 | 2.2254 | 2.7912 | 2.7912 | 2.7912 | 2.7912 | 1.2685 | 1.6101 | 1.6101 | 1.6101 | 1.6101 | 1.6101
2020-09-14 16:00 | Winter | 2.4006 | 3.6912 | 5.5856 | 5.5856 | 5.5856 | 5.5856 | 0.79163 | 1.2954 | 1.7752 | 2.135 | 2.135 | 2.135 | 2.3816 | 3.4353 | 4.1258 | 4.4891 | 5.2159 | 5.9426 | 0.84593 | 2.2979 | 2.8821 | 2.8821 | 2.8821 | 2.8821 | 1.2003 | 1.5235 | 1.5235 | 1.5235 | 1.5235 | 1.5235
2020-09-14 17:00 | Winter | 2.0767 | 3.1932 | 4.832 | 4.832 | 4.832 | 4.832 | 0.81735 | 1.3375 | 1.8328 | 2.2044 | 2.2044 | 2.2044 | 2.2484 | 3.2433 | 3.8951 | 4.2381 | 4.9242 | 5.6103 | 0.86498 | 2.3496 | 2.947 | 2.947 | 2.947 | 2.947 | 1.0669 | 1.3542 | 1.3542 | 1.3542 | 1.3542 | 1.3542
2020-09-14 18:00 | Winter | 1.6157 | 2.4843 | 3.7592 | 3.7592 | 3.7592 | 3.7592 | 0.64302 | 1.0522 | 1.4419 | 1.7342 | 1.7342 | 1.7342 | 2.2863 | 3.2979 | 3.9607 | 4.3096 | 5.0072 | 5.7049 | 0.76972 | 2.0909 | 2.6225 | 2.6225 | 2.6225 | 2.6225 | 0.81979 | 1.0405 | 1.0405 | 1.0405 | 1.0405 | 1.0405
2020-09-14 19:00 | Winter | 1.1432 | 1.7577 | 2.6598 | 2.6598 | 2.6598 | 2.6598 | 0.46869 | 0.76695 | 1.051 | 1.264 | 1.264 | 1.264 | 2.2482 | 3.243 | 3.8947 | 4.2377 | 4.9238 | 5.6098 | 0.77734 | 2.1116 | 2.6484 | 2.6484 | 2.6484 | 2.6484 | 0.60968 | 0.77386 | 0.77386 | 0.77386 | 0.77386 | 0.77386
2020-09-14 20:00 | Winter | 1.0669 | 1.6405 | 2.4825 | 2.4825 | 2.4825 | 2.4825 | 0.58015 | 0.94933 | 1.3009 | 1.5646 | 1.5646 | 1.5646 | 2.0386 | 2.9407 | 3.5316 | 3.8427 | 4.4648 | 5.0869 | 0.69732 | 1.8942 | 2.3758 | 2.3758 | 2.3758 | 2.3758 | 0.57158 | 0.72549 | 0.72549 | 0.72549 | 0.72549 | 0.72549
2020-09-14 21:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.38828 | 0.63536 | 0.87068 | 1.0472 | 1.0472 | 1.0472 | 2.0196 | 2.9132 | 3.4986 | 3.8068 | 4.4231 | 5.0393 | 0.71256 | 1.9356 | 2.4277 | 2.4277 | 2.4277 | 2.4277 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-09-14 22:00 | Winter | 0.93358 | 1.4355 | 2.1722 | 2.1722 | 2.1722 | 2.1722 | 0.45154 | 0.73889 | 1.0125 | 1.2178 | 1.2178 | 1.2178 | 1.829 | 2.6383 | 3.1686 | 3.4477 | 4.0058 | 4.5639 | 0.70875 | 1.9253 | 2.4147 | 2.4147 | 2.4147 | 2.4147 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-09-14 23:00 | Winter | 0.93358 | 1.4355 | 2.1722 | 2.1722 | 2.1722 | 2.1722 | 0.42868 | 0.70147 | 0.96128 | 1.1561 | 1.1561 | 1.1561 | 1.6766 | 2.4185 | 2.9045 | 3.1603 | 3.672 | 4.1836 | 0.60587 | 1.6458 | 2.0642 | 2.0642 | 2.0642 | 2.0642 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-09-15 | Winter | 0.93358 | 1.4355 | 2.1722 | 2.1722 | 2.1722 | 2.1722 | 0.41734 | 0.68292 | 0.93585 | 1.1255 | 1.1255 | 1.1255 | 1.6196 | 2.3362 | 2.8057 | 3.0528 | 3.5471 | 4.0413 | 0.57157 | 1.5526 | 1.9474 | 1.9474 | 1.9474 | 1.9474 | 0.43406 | 0.55094 | 0.55094 | 0.55094 | 0.55094 | 0.55094
2020-09-15 01:00 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.43154 | 0.70615 | 0.96769 | 1.1638 | 1.1638 | 1.1638 | 1.5242 | 2.1986 | 2.6405 | 2.873 | 3.3382 | 3.8033 | 0.57539 | 1.563 | 1.9603 | 1.9603 | 1.9603 | 1.9603 | 0.45726 | 0.58039 | 0.58039 | 0.58039 | 0.58039 | 0.58039
2020-09-15 02:00 | Winter | 0.93358 | 1.4355 | 2.1722 | 2.1722 | 2.1722 | 2.1722 | 0.40582 | 0.66406 | 0.91001 | 1.0945 | 1.0945 | 1.0945 | 1.5052 | 2.1711 | 2.6075 | 2.8371 | 3.2964 | 3.7557 | 0.51061 | 1.387 | 1.7396 | 1.7396 | 1.7396 | 1.7396 | 0.49537 | 0.62876 | 0.62876 | 0.62876 | 0.62876 | 0.62876
2020-09-15 03:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.43725 | 0.7155 | 0.98051 | 1.1793 | 1.1793 | 1.1793 | 1.5242 | 2.1986 | 2.6405 | 2.873 | 3.3382 | 3.8033 | 0.53728 | 1.4595 | 1.8305 | 1.8305 | 1.8305 | 1.8305 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-09-15 04:00 | Winter | 1.144 | 1.759 | 2.6617 | 2.6617 | 2.6617 | 2.6617 | 0.43154 | 0.70615 | 0.96769 | 1.1638 | 1.1638 | 1.1638 | 1.5217 | 2.195 | 2.6361 | 2.8683 | 3.3327 | 3.797 | 0.57157 | 1.5526 | 1.9474 | 1.9474 | 1.9474 | 1.9474 | 0.53257 | 0.67598 | 0.67598 | 0.67598 | 0.67598 | 0.67598
2020-09-15 05:00 | Winter | 1.2575 | 1.9335 | 2.9258 | 2.9258 | 2.9258 | 2.9258 | 0.5087 | 0.83242 | 1.1407 | 1.3719 | 1.3719 | 1.3719 | 1.7338 | 2.5009 | 3.0036 | 3.2681 | 3.7972 | 4.3262 | 0.62111 | 1.6872 | 2.1161 | 2.1161 | 2.1161 | 2.1161 | 0.724 | 0.91895 | 0.91895 | 0.91895 | 0.91895 | 0.91895
2020-09-15 06:00 | Winter | 1.467 | 2.2556 | 3.4132 | 3.4132 | 3.4132 | 3.4132 | 0.68875 | 1.127 | 1.5445 | 1.8575 | 1.8575 | 1.8575 | 1.9434 | 2.8032 | 3.3666 | 3.6631 | 4.2562 | 4.8492 | 0.70113 | 1.9046 | 2.3888 | 2.3888 | 2.3888 | 2.3888 | 0.88522 | 1.1236 | 1.1236 | 1.1236 | 1.1236 | 1.1236
2020-09-15 07:00 | Winter | 1.829 | 2.8124 | 4.2557 | 4.2557 | 4.2557 | 4.2557 | 0.97168 | 1.59 | 2.1789 | 2.6206 | 2.6206 | 2.6206 | 2.2673 | 3.2705 | 3.9277 | 4.2736 | 4.9655 | 5.6574 | 0.85736 | 2.3289 | 2.9211 | 2.9211 | 2.9211 | 2.9211 | 1.1813 | 1.4993 | 1.4993 | 1.4993 | 1.4993 | 1.4993
2020-09-15 08:00 | Winter | 2.0958 | 3.2225 | 4.8763 | 4.8763 | 4.8763 | 4.8763 | 0.9088 | 1.4871 | 2.0379 | 2.451 | 2.451 | 2.451 | 2.3816 | 3.4353 | 4.1258 | 4.4891 | 5.2159 | 5.9426 | 0.86879 | 2.36 | 2.96 | 2.96 | 2.96 | 2.96 | 1.2956 | 1.6444 | 1.6444 | 1.6444 | 1.6444 | 1.6444
2020-09-15 09:00 | Winter | 2.3816 | 3.6619 | 5.5412 | 5.5412 | 5.5412 | 5.5412 | 0.93452 | 1.5292 | 2.0956 | 2.5204 | 2.5204 | 2.5204 | 2.4768 | 3.5728 | 4.2908 | 4.6687 | 5.4245 | 6.1803 | 0.94119 | 2.5567 | 3.2067 | 3.2067 | 3.2067 | 3.2067 | 1.3718 | 1.7412 | 1.7412 | 1.7412 | 1.7412 | 1.7412
2020-09-15 10:00 | Winter | 2.2673 | 3.4862 | 5.2753 | 5.2753 | 5.2753 | 5.2753 | 0.80592 | 1.3188 | 1.8072 | 2.1735 | 2.1735 | 2.1735 | 2.4768 | 3.5728 | 4.2908 | 4.6687 | 5.4245 | 6.1803 | 0.92595 | 2.5153 | 3.1547 | 3.1547 | 3.1547 | 3.1547 | 1.3718 | 1.7412 | 1.7412 | 1.7412 | 1.7412 | 1.7412
2020-09-15 11:00 | Winter | 2.2502 | 3.4599 | 5.2355 | 5.2355 | 5.2355 | 5.2355 | 0.82592 | 1.3515 | 1.8521 | 2.2275 | 2.2275 | 2.2275 | 2.5513 | 3.6802 | 4.4198 | 4.8091 | 5.5876 | 6.3662 | 0.7964 | 2.1633 | 2.7133 | 2.7133 | 2.7133 | 2.7133 | 1.3146 | 1.6686 | 1.6686 | 1.6686 | 1.6686 | 1.6686
2020-09-15 12:00 | Winter | 2.3244 | 3.5741 | 5.4082 | 5.4082 | 5.4082 | 5.4082 | 0.78877 | 1.2907 | 1.7688 | 2.1273 | 2.1273 | 2.1273 | 2.553 | 3.6827 | 4.4228 | 4.8123 | 5.5914 | 6.3705 | 0.80402 | 2.184 | 2.7393 | 2.7393 | 2.7393 | 2.7393 | 1.3908 | 1.7654 | 1.7654 | 1.7654 | 1.7654 | 1.7654
2020-09-15 13:00 | Winter | 2.3435 | 3.6034 | 5.4526 | 5.4526 | 5.4526 | 5.4526 | 0.84307 | 1.3796 | 1.8905 | 2.2737 | 2.2737 | 2.2737 | 2.534 | 3.6552 | 4.3898 | 4.7764 | 5.5497 | 6.3229 | 0.84212 | 2.2875 | 2.8691 | 2.8691 | 2.8691 | 2.8691 | 1.3908 | 1.7654 | 1.7654 | 1.7654 | 1.7654 | 1.7654
2020-09-15 14:00 | Winter | 2.4197 | 3.7205 | 5.6299 | 5.6299 | 5.6299 | 5.6299 | 0.8545 | 1.3983 | 1.9162 | 2.3046 | 2.3046 | 2.3046 | 2.6061 | 3.7592 | 4.5147 | 4.9123 | 5.7076 | 6.5028 | 0.86498 | 2.3496 | 2.947 | 2.947 | 2.947 | 2.947 | 1.3146 | 1.6686 | 1.6686 | 1.6686 | 1.6686 | 1.6686
2020-09-15 15:00 | Winter | 2.4197 | 3.7205 | 5.6299 | 5.6299 | 5.6299 | 5.6299 | 0.84021 | 1.3749 | 1.8841 | 2.266 | 2.266 | 2.266 | 2.6293 | 3.7926 | 4.5548 | 4.956 | 5.7583 | 6.5606 | 0.86879 | 2.36 | 2.96 | 2.96 | 2.96 | 2.96 | 1.2956 | 1.6444 | 1.6444 | 1.6444 | 1.6444 | 1.6444
2020-09-15 16:00 | Winter | 2.3816 | 3.6619 | 5.5412 | 5.5412 | 5.5412 | 5.5412 | 0.84593 | 1.3842 | 1.8969 | 2.2814 | 2.2814 | 2.2814 | 2.4959 | 3.6002 | 4.3238 | 4.7046 | 5.4662 | 6.2279 | 0.8345 | 2.2668 | 2.8432 | 2.8432 | 2.8432 | 2.8432 | 1.2765 | 1.6203 | 1.6203 | 1.6203 | 1.6203 | 1.6203
2020-09-15 17:00 | Winter | 2.1339 | 3.2811 | 4.9649 | 4.9649 | 4.9649 | 4.9649 | 0.80592 | 1.3188 | 1.8072 | 2.1735 | 2.1735 | 2.1735 | 2.3816 | 3.4353 | 4.1258 | 4.4891 | 5.2159 | 5.9426 | 0.81545 | 2.2151 | 2.7782 | 2.7782 | 2.7782 | 2.7782 | 1.1285 | 1.4324 | 1.4324 | 1.4324 | 1.4324 | 1.4324
2020-09-15 18:00 | Winter | 1.6739 | 2.5738 | 3.8946 | 3.8946 | 3.8946 | 3.8946 | 0.60587 | 0.99142 | 1.3586 | 1.634 | 1.634 | 1.634 | 2.2482 | 3.243 | 3.8947 | 4.2377 | 4.9238 | 5.6098 | 0.78115 | 2.1219 | 2.6614 | 2.6614 | 2.6614 | 2.6614 | 0.8797 | 1.1166 | 1.1166 | 1.1166 | 1.1166 | 1.1166
2020-09-15 19:00 | Winter | 1.1813 | 1.8163 | 2.7485 | 2.7485 | 2.7485 | 2.7485 | 0.52013 | 0.85112 | 1.1664 | 1.4028 | 1.4028 | 1.4028 | 2.191 | 3.1605 | 3.7957 | 4.13 | 4.7986 | 5.4672 | 0.76972 | 2.0909 | 2.6225 | 2.6225 | 2.6225 | 2.6225 | 0.65968 | 0.83732 | 0.83732 | 0.83732 | 0.83732 | 0.83732
2020-09-15 20:00 | Winter | 1.0669 | 1.6405 | 2.4825 | 2.4825 | 2.4825 | 2.4825 | 0.52013 | 0.85112 | 1.1664 | 1.4028 | 1.4028 | 1.4028 | 2.0386 | 2.9407 | 3.5316 | 3.8427 | 4.4648 | 5.0869 | 0.72781 | 1.977 | 2.4796 | 2.4796 | 2.4796 | 2.4796 | 0.64779 | 0.82222 | 0.82222 | 0.82222 | 0.82222 | 0.82222
2020-09-15 21:00 | Winter | 1.0288 | 1.582 | 2.3938 | 2.3938 | 2.3938 | 2.3938 | 0.4544 | 0.74356 | 1.019 | 1.2255 | 1.2255 | 1.2255 | 1.9243 | 2.7758 | 3.3336 | 3.6272 | 4.2144 | 4.8016 | 0.71637 | 1.946 | 2.4407 | 2.4407 | 2.4407 | 2.4407 | 0.55252 | 0.70131 | 0.70131 | 0.70131 | 0.70131 | 0.70131
2020-09-15 22:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.46297 | 0.75759 | 1.0382 | 1.2486 | 1.2486 | 1.2486 | 1.829 | 2.6383 | 3.1686 | 3.4477 | 4.0058 | 4.5639 | 0.73162 | 1.9874 | 2.4926 | 2.4926 | 2.4926 | 2.4926 | 0.49537 | 0.62876 | 0.62876 | 0.62876 | 0.62876 | 0.62876
2020-09-15 23:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.35723 | 0.58456 | 0.80107 | 0.96344 | 0.96344 | 0.96344 | 1.6519 | 2.3828 | 2.8617 | 3.1137 | 3.6178 | 4.1218 | 0.63635 | 1.7286 | 2.1681 | 2.1681 | 2.1681 | 2.1681 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-09-16 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.42868 | 0.70147 | 0.96128 | 1.1561 | 1.1561 | 1.1561 | 1.5814 | 2.2811 | 2.7395 | 2.9808 | 3.4633 | 3.9459 | 0.59444 | 1.6147 | 2.0253 | 2.0253 | 2.0253 | 2.0253 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-09-16 01:00 | Winter | 0.96299 | 1.4807 | 2.2406 | 2.2406 | 2.2406 | 2.2406 | 0.34572 | 0.56572 | 0.77524 | 0.93238 | 0.93238 | 0.93238 | 1.5052 | 2.1711 | 2.6075 | 2.8371 | 3.2964 | 3.7557 | 0.58682 | 1.594 | 1.9993 | 1.9993 | 1.9993 | 1.9993 | 0.45726 | 0.58039 | 0.58039 | 0.58039 | 0.58039 | 0.58039
2020-09-16 02:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.45154 | 0.73889 | 1.0125 | 1.2178 | 1.2178 | 1.2178 | 1.5433 | 2.2261 | 2.6735 | 2.909 | 3.3799 | 3.8508 | 0.56776 | 1.5423 | 1.9344 | 1.9344 | 1.9344 | 1.9344 | 0.45361 | 0.57576 | 0.57576 | 0.57576 | 0.57576 | 0.57576
2020-09-16 03:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.4346 | 0.71116 | 0.97455 | 1.1721 | 1.1721 | 1.1721 | 1.5433 | 2.2261 | 2.6735 | 2.909 | 3.3799 | 3.8508 | 0.56014 | 1.5216 | 1.9084 | 1.9084 | 1.9084 | 1.9084 | 0.49533 | 0.62871 | 0.62871 | 0.62871 | 0.62871 | 0.62871
2020-09-16 04:00 | Winter | 1.1432 | 1.7577 | 2.6598 | 2.6598 | 2.6598 | 2.6598 | 0.44011 | 0.72018 | 0.98691 | 1.187 | 1.187 | 1.187 | 1.5052 | 2.1711 | 2.6075 | 2.8371 | 3.2964 | 3.7557 | 0.55633 | 1.5112 | 1.8954 | 1.8954 | 1.8954 | 1.8954 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-09-16 05:00 | Winter | 1.2033 | 1.8502 | 2.7998 | 2.7998 | 2.7998 | 2.7998 | 0.50298 | 0.82306 | 1.1279 | 1.3565 | 1.3565 | 1.3565 | 1.6764 | 2.4182 | 2.9042 | 3.16 | 3.6715 | 4.1831 | 0.60587 | 1.6458 | 2.0642 | 2.0642 | 2.0642 | 2.0642 | 0.68589 | 0.87059 | 0.87059 | 0.87059 | 0.87059 | 0.87059
2020-09-16 06:00 | Winter | 1.4289 | 2.1972 | 3.3247 | 3.3247 | 3.3247 | 3.3247 | 0.6173 | 1.0101 | 1.3842 | 1.6648 | 1.6648 | 1.6648 | 1.9645 | 2.8338 | 3.4033 | 3.703 | 4.3025 | 4.902 | 0.66303 | 1.8011 | 2.2589 | 2.2589 | 2.2589 | 2.2589 | 0.93284 | 1.184 | 1.184 | 1.184 | 1.184 | 1.184
2020-09-16 07:00 | Winter | 1.8379 | 2.826 | 4.2763 | 4.2763 | 4.2763 | 4.2763 | 0.82878 | 1.3562 | 1.8585 | 2.2352 | 2.2352 | 2.2352 | 2.3054 | 3.3254 | 3.9937 | 4.3455 | 5.049 | 5.7525 | 0.86498 | 2.3496 | 2.947 | 2.947 | 2.947 | 2.947 | 1.1039 | 1.4012 | 1.4012 | 1.4012 | 1.4012 | 1.4012
2020-09-16 08:00 | Winter | 2.1148 | 3.2518 | 4.9206 | 4.9206 | 4.9206 | 4.9206 | 1.0145 | 1.6602 | 2.275 | 2.7362 | 2.7362 | 2.7362 | 2.4006 | 3.4628 | 4.1588 | 4.525 | 5.2576 | 5.9902 | 0.96025 | 2.6084 | 3.2716 | 3.2716 | 3.2716 | 3.2716 | 1.2765 | 1.6203 | 1.6203 | 1.6203 | 1.6203 | 1.6203
2020-09-16 09:00 | Winter | 2.2863 | 3.5155 | 5.3196 | 5.3196 | 5.3196 | 5.3196 | 0.9431 | 1.5433 | 2.1148 | 2.5435 | 2.5435 | 2.5435 | 2.4768 | 3.5728 | 4.2908 | 4.6687 | 5.4245 | 6.1803 | 0.93357 | 2.536 | 3.1807 | 3.1807 | 3.1807 | 3.1807 | 1.3527 | 1.717 | 1.717 | 1.717 | 1.717 | 1.717
2020-09-16 10:00 | Winter | 2.4006 | 3.6912 | 5.5856 | 5.5856 | 5.5856 | 5.5856 | 0.94024 | 1.5386 | 2.1084 | 2.5358 | 2.5358 | 2.5358 | 2.5149 | 3.6277 | 4.3568 | 4.7405 | 5.508 | 6.2754 | 0.86879 | 2.36 | 2.96 | 2.96 | 2.96 | 2.96 | 1.3718 | 1.7412 | 1.7412 | 1.7412 | 1.7412 | 1.7412
2020-09-16 11:00 | Winter | 2.3435 | 3.6034 | 5.4526 | 5.4526 | 5.4526 | 5.4526 | 0.79449 | 1.3001 | 1.7816 | 2.1427 | 2.1427 | 2.1427 | 2.4768 | 3.5728 | 4.2908 | 4.6687 | 5.4245 | 6.1803 | 0.84212 | 2.2875 | 2.8691 | 2.8691 | 2.8691 | 2.8691 | 1.4289 | 1.8137 | 1.8137 | 1.8137 | 1.8137 | 1.8137
2020-09-16 12:00 | Winter | 2.3435 | 3.6034 | 5.4526 | 5.4526 | 5.4526 | 5.4526 | 0.7802 | 1.2767 | 1.7495 | 2.1042 | 2.1042 | 2.1042 | 2.553 | 3.6827 | 4.4228 | 4.8123 | 5.5914 | 6.3705 | 0.81926 | 2.2254 | 2.7912 | 2.7912 | 2.7912 | 2.7912 | 1.3527 | 1.717 | 1.717 | 1.717 | 1.717 | 1.717
2020-09-16 13:00 | Winter | 2.3435 | 3.6034 | 5.4526 | 5.4526 | 5.4526 | 5.4526 | 0.89737 | 1.4684 | 2.0123 | 2.4202 | 2.4202 | 2.4202 | 2.553 | 3.6827 | 4.4228 | 4.8123 | 5.5914 | 6.3705 | 0.82307 | 2.2358 | 2.8042 | 2.8042 | 2.8042 | 2.8042 | 1.3146 | 1.6686 | 1.6686 | 1.6686 | 1.6686 | 1.6686
2020-09-16 14:00 | Winter | 2.3244 | 3.5741 | 5.4082 | 5.4082 | 5.4082 | 5.4082 | 0.82592 | 1.3515 | 1.8521 | 2.2275 | 2.2275 | 2.2275 | 2.4959 | 3.6002 | 4.3238 | 4.7046 | 5.4662 | 6.2279 | 0.82307 | 2.2358 | 2.8042 | 2.8042 | 2.8042 | 2.8042 | 1.3337 | 1.6928 | 1.6928 | 1.6928 | 1.6928 | 1.6928
2020-09-16 15:00 | Winter | 2.3054 | 3.5448 | 5.3639 | 5.3639 | 5.3639 | 5.3639 | 0.89166 | 1.4591 | 1.9995 | 2.4048 | 2.4048 | 2.4048 | 2.4768 | 3.5728 | 4.2908 | 4.6687 | 5.4245 | 6.1803 | 0.8345 | 2.2668 | 2.8432 | 2.8432 | 2.8432 | 2.8432 | 1.2765 | 1.6203 | 1.6203 | 1.6203 | 1.6203 | 1.6203
2020-09-16 16:00 | Winter | 2.3625 | 3.6326 | 5.4969 | 5.4969 | 5.4969 | 5.4969 | 0.82021 | 1.3422 | 1.8393 | 2.2121 | 2.2121 | 2.2121 | 2.4387 | 3.5178 | 4.2248 | 4.5969 | 5.3411 | 6.0852 | 0.81545 | 2.2151 | 2.7782 | 2.7782 | 2.7782 | 2.7782 | 1.2765 | 1.6203 | 1.6203 | 1.6203 | 1.6203 | 1.6203
2020-09-16 17:00 | Winter | 2.2482 | 3.4569 | 5.2309 | 5.2309 | 5.2309 | 5.2309 | 0.89737 | 1.4684 | 2.0123 | 2.4202 | 2.4202 | 2.4202 | 2.348 | 3.387 | 4.0677 | 4.4259 | 5.1424 | 5.859 | 0.78877 | 2.1426 | 2.6874 | 2.6874 | 2.6874 | 2.6874 | 1.1622 | 1.4752 | 1.4752 | 1.4752 | 1.4752 | 1.4752
2020-09-16 18:00 | Winter | 1.6175 | 2.4871 | 3.7634 | 3.7634 | 3.7634 | 3.7634 | 0.6328 | 1.0355 | 1.419 | 1.7066 | 1.7066 | 1.7066 | 2.2291 | 3.2155 | 3.8617 | 4.2018 | 4.8821 | 5.5623 | 0.78496 | 2.1323 | 2.6744 | 2.6744 | 2.6744 | 2.6744 | 0.85088 | 1.08 | 1.08 | 1.08 | 1.08 | 1.08
2020-09-16 19:00 | Winter | 1.1815 | 1.8168 | 2.7491 | 2.7491 | 2.7491 | 2.7491 | 0.61444 | 1.0054 | 1.3778 | 1.6571 | 1.6571 | 1.6571 | 2.113 | 3.048 | 3.6605 | 3.9829 | 4.6277 | 5.2725 | 0.78115 | 2.1219 | 2.6614 | 2.6614 | 2.6614 | 2.6614 | 0.66684 | 0.84641 | 0.84641 | 0.84641 | 0.84641 | 0.84641
2020-09-16 20:00 | Winter | 1.105 | 1.6991 | 2.5711 | 2.5711 | 2.5711 | 2.5711 | 0.52299 | 0.8558 | 1.1728 | 1.4105 | 1.4105 | 1.4105 | 2.0386 | 2.9407 | 3.5316 | 3.8427 | 4.4648 | 5.0869 | 0.75067 | 2.0391 | 2.5575 | 2.5575 | 2.5575 | 2.5575 | 0.55311 | 0.70206 | 0.70206 | 0.70206 | 0.70206 | 0.70206
2020-09-16 21:00 | Winter | 1.0288 | 1.582 | 2.3938 | 2.3938 | 2.3938 | 2.3938 | 0.51442 | 0.84177 | 1.1535 | 1.3874 | 1.3874 | 1.3874 | 1.9053 | 2.7483 | 3.3006 | 3.5913 | 4.1727 | 4.7541 | 0.75448 | 2.0495 | 2.5705 | 2.5705 | 2.5705 | 2.5705 | 0.49537 | 0.62876 | 0.62876 | 0.62876 | 0.62876 | 0.62876
2020-09-16 22:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.48298 | 0.79033 | 1.083 | 1.3026 | 1.3026 | 1.3026 | 1.7909 | 2.5834 | 3.1026 | 3.3758 | 3.9223 | 4.4688 | 0.65645 | 1.7832 | 2.2365 | 2.2365 | 2.2365 | 2.2365 | 0.43806 | 0.55602 | 0.55602 | 0.55602 | 0.55602 | 0.55602
2020-09-16 23:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.38581 | 0.63133 | 0.86515 | 1.0405 | 1.0405 | 1.0405 | 1.7719 | 2.5559 | 3.0696 | 3.3399 | 3.8806 | 4.4213 | 0.65541 | 1.7803 | 2.233 | 2.233 | 2.233 | 2.233 | 0.42862 | 0.54403 | 0.54403 | 0.54403 | 0.54403 | 0.54403
2020-09-17 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.33437 | 0.54715 | 0.7498 | 0.90178 | 0.90178 | 0.90178 | 1.5623 | 2.2536 | 2.7065 | 2.9449 | 3.4216 | 3.8984 | 0.60206 | 1.6354 | 2.0512 | 2.0512 | 2.0512 | 2.0512 | 0.45726 | 0.58039 | 0.58039 | 0.58039 | 0.58039 | 0.58039
2020-09-17 01:00 | Winter | 0.95292 | 1.4652 | 2.2172 | 2.2172 | 2.2172 | 2.2172 | 0.32865 | 0.5378 | 0.73698 | 0.88637 | 0.88637 | 0.88637 | 1.5052 | 2.1711 | 2.6075 | 2.8371 | 3.2964 | 3.7557 | 0.57539 | 1.563 | 1.9603 | 1.9603 | 1.9603 | 1.9603 | 0.41506 | 0.52683 | 0.52683 | 0.52683 | 0.52683 | 0.52683
2020-09-17 02:00 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.41439 | 0.67809 | 0.92924 | 1.1176 | 1.1176 | 1.1176 | 1.5433 | 2.2261 | 2.6735 | 2.909 | 3.3799 | 3.8508 | 0.5792 | 1.5733 | 1.9733 | 1.9733 | 1.9733 | 1.9733 | 0.45726 | 0.58039 | 0.58039 | 0.58039 | 0.58039 | 0.58039
2020-09-17 03:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.33437 | 0.54715 | 0.7498 | 0.90178 | 0.90178 | 0.90178 | 1.4759 | 2.129 | 2.5568 | 2.782 | 3.2324 | 3.6828 | 0.56395 | 1.5319 | 1.9214 | 1.9214 | 1.9214 | 1.9214 | 0.45021 | 0.57144 | 0.57144 | 0.57144 | 0.57144 | 0.57144
2020-09-17 04:00 | Winter | 1.1241 | 1.7284 | 2.6155 | 2.6155 | 2.6155 | 2.6155 | 0.38581 | 0.63133 | 0.86515 | 1.0405 | 1.0405 | 1.0405 | 1.5266 | 2.202 | 2.6446 | 2.8775 | 3.3433 | 3.8092 | 0.58301 | 1.5837 | 1.9863 | 1.9863 | 1.9863 | 1.9863 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-09-17 05:00 | Winter | 1.2194 | 1.8749 | 2.8371 | 2.8371 | 2.8371 | 2.8371 | 0.48584 | 0.79501 | 1.0895 | 1.3103 | 1.3103 | 1.3103 | 1.6004 | 2.3086 | 2.7725 | 3.0167 | 3.5051 | 3.9934 | 0.63254 | 1.7182 | 2.1551 | 2.1551 | 2.1551 | 2.1551 | 0.64779 | 0.82222 | 0.82222 | 0.82222 | 0.82222 | 0.82222
2020-09-17 06:00 | Winter | 1.4099 | 2.1679 | 3.2804 | 3.2804 | 3.2804 | 3.2804 | 0.55443 | 0.90724 | 1.2433 | 1.4953 | 1.4953 | 1.4953 | 1.8291 | 2.6385 | 3.1687 | 3.4478 | 4.006 | 4.5641 | 0.6516 | 1.77 | 2.22 | 2.22 | 2.22 | 2.22 | 0.80578 | 1.0228 | 1.0228 | 1.0228 | 1.0228 | 1.0228
2020-09-17 07:00 | Winter | 1.9053 | 2.9296 | 4.433 | 4.433 | 4.433 | 4.433 | 0.7459 | 1.2206 | 1.6726 | 2.0117 | 2.0117 | 2.0117 | 2.1529 | 3.1056 | 3.7297 | 4.0582 | 4.7151 | 5.3721 | 0.80021 | 2.1737 | 2.7263 | 2.7263 | 2.7263 | 2.7263 | 1.1038 | 1.401 | 1.401 | 1.401 | 1.401 | 1.401
2020-09-17 08:00 | Winter | 2.2863 | 3.5155 | 5.3196 | 5.3196 | 5.3196 | 5.3196 | 0.77734 | 1.272 | 1.7431 | 2.0965 | 2.0965 | 2.0965 | 2.3435 | 3.3804 | 4.0597 | 4.4173 | 5.1324 | 5.8475 | 0.88785 | 2.4118 | 3.0249 | 3.0249 | 3.0249 | 3.0249 | 1.2956 | 1.6444 | 1.6444 | 1.6444 | 1.6444 | 1.6444
2020-09-17 09:00 | Winter | 2.4006 | 3.6912 | 5.5856 | 5.5856 | 5.5856 | 5.5856 | 0.75448 | 1.2346 | 1.6919 | 2.0348 | 2.0348 | 2.0348 | 2.4006 | 3.4628 | 4.1588 | 4.525 | 5.2576 | 5.9902 | 0.91071 | 2.4739 | 3.1028 | 3.1028 | 3.1028 | 3.1028 | 1.2956 | 1.6444 | 1.6444 | 1.6444 | 1.6444 | 1.6444
2020-09-17 10:00 | Winter | 2.3054 | 3.5448 | 5.3639 | 5.3639 | 5.3639 | 5.3639 | 0.72304 | 1.1832 | 1.6214 | 1.95 | 1.95 | 1.95 | 2.5721 | 3.7102 | 4.4558 | 4.8483 | 5.6331 | 6.418 | 0.84974 | 2.3082 | 2.8951 | 2.8951 | 2.8951 | 2.8951 | 1.3146 | 1.6686 | 1.6686 | 1.6686 | 1.6686 | 1.6686
2020-09-17 11:00 | Winter | 2.3816 | 3.6619 | 5.5412 | 5.5412 | 5.5412 | 5.5412 | 0.8545 | 1.3983 | 1.9162 | 2.3046 | 2.3046 | 2.3046 | 2.5674 | 3.7034 | 4.4476 | 4.8393 | 5.6228 | 6.4062 | 0.86498 | 2.3496 | 2.947 | 2.947 | 2.947 | 2.947 | 1.3527 | 1.717 | 1.717 | 1.717 | 1.717 | 1.717
2020-09-17 12:00 | Winter | 2.4959 | 3.8377 | 5.8072 | 5.8072 | 5.8072 | 5.8072 | 0.84879 | 1.3889 | 1.9033 | 2.2892 | 2.2892 | 2.2892 | 2.6293 | 3.7926 | 4.5548 | 4.956 | 5.7583 | 6.5606 | 0.86498 | 2.3496 | 2.947 | 2.947 | 2.947 | 2.947 | 1.3337 | 1.6928 | 1.6928 | 1.6928 | 1.6928 | 1.6928
2020-09-17 13:00 | Winter | 2.4578 | 3.7791 | 5.7186 | 5.7186 | 5.7186 | 5.7186 | 0.86308 | 1.4123 | 1.9354 | 2.3277 | 2.3277 | 2.3277 | 2.6864 | 3.8751 | 4.6539 | 5.0637 | 5.8835 | 6.7033 | 0.86498 | 2.3496 | 2.947 | 2.947 | 2.947 | 2.947 | 1.3527 | 1.717 | 1.717 | 1.717 | 1.717 | 1.717
2020-09-17 14:00 | Winter | 2.3625 | 3.6326 | 5.4969 | 5.4969 | 5.4969 | 5.4969 | 0.90309 | 1.4778 | 2.0251 | 2.4356 | 2.4356 | 2.4356 | 2.7055 | 3.9026 | 4.6869 | 5.0996 | 5.9252 | 6.7508 | 0.90309 | 2.4532 | 3.0768 | 3.0768 | 3.0768 | 3.0768 | 1.3337 | 1.6928 | 1.6928 | 1.6928 | 1.6928 | 1.6928
2020-09-17 15:00 | Winter | 2.4387 | 3.7498 | 5.6742 | 5.6742 | 5.6742 | 5.6742 | 0.85165 | 1.3936 | 1.9098 | 2.2969 | 2.2969 | 2.2969 | 2.6293 | 3.7926 | 4.5548 | 4.956 | 5.7583 | 6.5606 | 0.90309 | 2.4532 | 3.0768 | 3.0768 | 3.0768 | 3.0768 | 1.3146 | 1.6686 | 1.6686 | 1.6686 | 1.6686 | 1.6686
2020-09-17 16:00 | Winter | 2.4197 | 3.7205 | 5.6299 | 5.6299 | 5.6299 | 5.6299 | 0.81735 | 1.3375 | 1.8328 | 2.2044 | 2.2044 | 2.2044 | 2.6293 | 3.7926 | 4.5548 | 4.956 | 5.7583 | 6.5606 | 0.89166 | 2.4221 | 3.0379 | 3.0379 | 3.0379 | 3.0379 | 1.2194 | 1.5477 | 1.5477 | 1.5477 | 1.5477 | 1.5477
2020-09-17 17:00 | Winter | 2.2101 | 3.3983 | 5.1423 | 5.1423 | 5.1423 | 5.1423 | 0.83164 | 1.3609 | 1.8649 | 2.2429 | 2.2429 | 2.2429 | 2.5149 | 3.6277 | 4.3568 | 4.7405 | 5.508 | 6.2754 | 0.89928 | 2.4428 | 3.0639 | 3.0639 | 3.0639 | 3.0639 | 1.1059 | 1.4037 | 1.4037 | 1.4037 | 1.4037 | 1.4037
2020-09-17 18:00 | Winter | 1.5808 | 2.4306 | 3.678 | 3.678 | 3.678 | 3.678 | 0.71733 | 1.1738 | 1.6085 | 1.9346 | 1.9346 | 1.9346 | 2.3435 | 3.3804 | 4.0597 | 4.4173 | 5.1324 | 5.8475 | 0.78877 | 2.1426 | 2.6874 | 2.6874 | 2.6874 | 2.6874 | 0.95263 | 1.2092 | 1.2092 | 1.2092 | 1.2092 | 1.2092
2020-09-17 19:00 | Winter | 1.2003 | 1.8456 | 2.7928 | 2.7928 | 2.7928 | 2.7928 | 0.53728 | 0.87918 | 1.2048 | 1.449 | 1.449 | 1.449 | 2.254 | 3.2514 | 3.9048 | 4.2487 | 4.9366 | 5.6244 | 0.78115 | 2.1219 | 2.6614 | 2.6614 | 2.6614 | 2.6614 | 0.66684 | 0.84641 | 0.84641 | 0.84641 | 0.84641 | 0.84641
2020-09-17 20:00 | Winter | 1.105 | 1.6991 | 2.5711 | 2.5711 | 2.5711 | 2.5711 | 0.50298 | 0.82306 | 1.1279 | 1.3565 | 1.3565 | 1.3565 | 2.0958 | 3.0231 | 3.6307 | 3.9504 | 4.59 | 5.2295 | 0.72018 | 1.9563 | 2.4537 | 2.4537 | 2.4537 | 2.4537 | 0.59063 | 0.74967 | 0.74967 | 0.74967 | 0.74967 | 0.74967
2020-09-17 21:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 0.51727 | 0.84645 | 1.1599 | 1.3951 | 1.3951 | 1.3951 | 1.9434 | 2.8032 | 3.3666 | 3.6631 | 4.2562 | 4.8492 | 0.72018 | 1.9563 | 2.4537 | 2.4537 | 2.4537 | 2.4537 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-09-17 22:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.48298 | 0.79033 | 1.083 | 1.3026 | 1.3026 | 1.3026 | 1.7987 | 2.5946 | 3.116 | 3.3904 | 3.9393 | 4.4882 | 0.724 | 1.9667 | 2.4667 | 2.4667 | 2.4667 | 2.4667 | 0.49537 | 0.62876 | 0.62876 | 0.62876 | 0.62876 | 0.62876
2020-09-17 23:00 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.38867 | 0.636 | 0.87156 | 1.0482 | 1.0482 | 1.0482 | 1.6957 | 2.446 | 2.9375 | 3.1963 | 3.7137 | 4.2311 | 0.63635 | 1.7286 | 2.1681 | 2.1681 | 2.1681 | 2.1681 | 0.49537 | 0.62876 | 0.62876 | 0.62876 | 0.62876 | 0.62876
2020-09-18 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.40818 | 0.66793 | 0.91531 | 1.1008 | 1.1008 | 1.1008 | 1.5433 | 2.2261 | 2.6735 | 2.909 | 3.3799 | 3.8508 | 0.59063 | 1.6044 | 2.0123 | 2.0123 | 2.0123 | 2.0123 | 0.437 | 0.55468 | 0.55468 | 0.55468 | 0.55468 | 0.55468
2020-09-18 01:00 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.46012 | 0.75292 | 1.0318 | 1.2409 | 1.2409 | 1.2409 | 1.5623 | 2.2536 | 2.7065 | 2.9449 | 3.4216 | 3.8984 | 0.55633 | 1.5112 | 1.8954 | 1.8954 | 1.8954 | 1.8954 | 0.45726 | 0.58039 | 0.58039 | 0.58039 | 0.58039 | 0.58039
2020-09-18 02:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.33722 | 0.55181 | 0.75618 | 0.90946 | 0.90946 | 0.90946 | 1.5052 | 2.1711 | 2.6075 | 2.8371 | 3.2964 | 3.7557 | 0.53347 | 1.4491 | 1.8175 | 1.8175 | 1.8175 | 1.8175 | 0.43821 | 0.55621 | 0.55621 | 0.55621 | 0.55621 | 0.55621
2020-09-18 03:00 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.41725 | 0.68277 | 0.93565 | 1.1253 | 1.1253 | 1.1253 | 1.5242 | 2.1986 | 2.6405 | 2.873 | 3.3382 | 3.8033 | 0.55633 | 1.5112 | 1.8954 | 1.8954 | 1.8954 | 1.8954 | 0.45726 | 0.58039 | 0.58039 | 0.58039 | 0.58039 | 0.58039
2020-09-18 04:00 | Winter | 1.086 | 1.6698 | 2.5268 | 2.5268 | 2.5268 | 2.5268 | 0.37724 | 0.6173 | 0.84593 | 1.0174 | 1.0174 | 1.0174 | 1.5367 | 2.2167 | 2.6622 | 2.8966 | 3.3656 | 3.8345 | 0.53728 | 1.4595 | 1.8305 | 1.8305 | 1.8305 | 1.8305 | 0.49748 | 0.63144 | 0.63144 | 0.63144 | 0.63144 | 0.63144
2020-09-18 05:00 | Winter | 1.1821 | 1.8176 | 2.7503 | 2.7503 | 2.7503 | 2.7503 | 0.48012 | 0.78565 | 1.0766 | 1.2949 | 1.2949 | 1.2949 | 1.6468 | 2.3755 | 2.8529 | 3.1042 | 3.6068 | 4.1093 | 0.62492 | 1.6975 | 2.1291 | 2.1291 | 2.1291 | 2.1291 | 0.70494 | 0.89477 | 0.89477 | 0.89477 | 0.89477 | 0.89477
2020-09-18 06:00 | Winter | 1.3337 | 2.0507 | 3.1031 | 3.1031 | 3.1031 | 3.1031 | 0.53728 | 0.87918 | 1.2048 | 1.449 | 1.449 | 1.449 | 1.7719 | 2.5559 | 3.0696 | 3.3399 | 3.8806 | 4.4213 | 0.67827 | 1.8425 | 2.3109 | 2.3109 | 2.3109 | 2.3109 | 0.7845 | 0.99576 | 0.99576 | 0.99576 | 0.99576 | 0.99576
2020-09-18 07:00 | Winter | 1.8215 | 2.8008 | 4.2382 | 4.2382 | 4.2382 | 4.2382 | 0.74305 | 1.2159 | 1.6662 | 2.004 | 2.004 | 2.004 | 2.0577 | 2.9681 | 3.5647 | 3.8786 | 4.5065 | 5.1344 | 0.87261 | 2.3704 | 2.973 | 2.973 | 2.973 | 2.973 | 1.0669 | 1.3542 | 1.3542 | 1.3542 | 1.3542 | 1.3542
2020-09-18 08:00 | Winter | 2.0577 | 3.1639 | 4.7876 | 4.7876 | 4.7876 | 4.7876 | 0.78877 | 1.2907 | 1.7688 | 2.1273 | 2.1273 | 2.1273 | 2.3157 | 3.3403 | 4.0117 | 4.365 | 5.0716 | 5.7783 | 0.87261 | 2.3704 | 2.973 | 2.973 | 2.973 | 2.973 | 1.2194 | 1.5477 | 1.5477 | 1.5477 | 1.5477 | 1.5477
2020-09-18 09:00 | Winter | 2.1339 | 3.2811 | 4.9649 | 4.9649 | 4.9649 | 4.9649 | 0.74876 | 1.2252 | 1.679 | 2.0194 | 2.0194 | 2.0194 | 2.4197 | 3.4903 | 4.1918 | 4.561 | 5.2993 | 6.0377 | 0.91833 | 2.4946 | 3.1288 | 3.1288 | 3.1288 | 3.1288 | 1.2956 | 1.6444 | 1.6444 | 1.6444 | 1.6444 | 1.6444
2020-09-18 10:00 | Winter | 2.172 | 3.3397 | 5.0536 | 5.0536 | 5.0536 | 5.0536 | 0.7459 | 1.2206 | 1.6726 | 2.0117 | 2.0117 | 2.0117 | 2.4959 | 3.6002 | 4.3238 | 4.7046 | 5.4662 | 6.2279 | 0.88404 | 2.4014 | 3.0119 | 3.0119 | 3.0119 | 3.0119 | 1.3146 | 1.6686 | 1.6686 | 1.6686 | 1.6686 | 1.6686
2020-09-18 11:00 | Winter | 2.0386 | 3.1346 | 4.7433 | 4.7433 | 4.7433 | 4.7433 | 0.76305 | 1.2486 | 1.7111 | 2.0579 | 2.0579 | 2.0579 | 2.553 | 3.6827 | 4.4228 | 4.8123 | 5.5914 | 6.3705 | 0.84974 | 2.3082 | 2.8951 | 2.8951 | 2.8951 | 2.8951 | 1.3337 | 1.6928 | 1.6928 | 1.6928 | 1.6928 | 1.6928
2020-09-18 12:00 | Winter | 2.0577 | 3.1639 | 4.7876 | 4.7876 | 4.7876 | 4.7876 | 0.71161 | 1.1645 | 1.5957 | 1.9192 | 1.9192 | 1.9192 | 2.534 | 3.6552 | 4.3898 | 4.7764 | 5.5497 | 6.3229 | 0.87642 | 2.3807 | 2.986 | 2.986 | 2.986 | 2.986 | 1.3337 | 1.6928 | 1.6928 | 1.6928 | 1.6928 | 1.6928
2020-09-18 13:00 | Winter | 2.0386 | 3.1346 | 4.7433 | 4.7433 | 4.7433 | 4.7433 | 0.72018 | 1.1785 | 1.615 | 1.9423 | 1.9423 | 1.9423 | 2.4768 | 3.5728 | 4.2908 | 4.6687 | 5.4245 | 6.1803 | 0.79258 | 2.153 | 2.7003 | 2.7003 | 2.7003 | 2.7003 | 1.3146 | 1.6686 | 1.6686 | 1.6686 | 1.6686 | 1.6686
2020-09-18 14:00 | Winter | 2.191 | 3.369 | 5.0979 | 5.0979 | 5.0979 | 5.0979 | 0.70589 | 1.1551 | 1.5829 | 1.9038 | 1.9038 | 1.9038 | 2.4197 | 3.4903 | 4.1918 | 4.561 | 5.2993 | 6.0377 | 0.80783 | 2.1944 | 2.7523 | 2.7523 | 2.7523 | 2.7523 | 1.2265 | 1.5568 | 1.5568 | 1.5568 | 1.5568 | 1.5568
2020-09-18 15:00 | Winter | 2.0767 | 3.1932 | 4.832 | 4.832 | 4.832 | 4.832 | 0.70527 | 1.1541 | 1.5815 | 1.9021 | 1.9021 | 1.9021 | 2.4578 | 3.5453 | 4.2578 | 4.6328 | 5.3828 | 6.1328 | 0.77734 | 2.1116 | 2.6484 | 2.6484 | 2.6484 | 2.6484 | 1.2003 | 1.5235 | 1.5235 | 1.5235 | 1.5235 | 1.5235
2020-09-18 16:00 | Winter | 2.0196 | 3.1053 | 4.699 | 4.699 | 4.699 | 4.699 | 0.73447 | 1.2019 | 1.647 | 1.9808 | 1.9808 | 1.9808 | 2.4959 | 3.6002 | 4.3238 | 4.7046 | 5.4662 | 6.2279 | 0.77353 | 2.1012 | 2.6354 | 2.6354 | 2.6354 | 2.6354 | 1.1813 | 1.4993 | 1.4993 | 1.4993 | 1.4993 | 1.4993
2020-09-18 17:00 | Winter | 1.9067 | 2.9318 | 4.4363 | 4.4363 | 4.4363 | 4.4363 | 0.73447 | 1.2019 | 1.647 | 1.9808 | 1.9808 | 1.9808 | 2.4387 | 3.5178 | 4.2248 | 4.5969 | 5.3411 | 6.0852 | 0.78877 | 2.1426 | 2.6874 | 2.6874 | 2.6874 | 2.6874 | 1.0732 | 1.3621 | 1.3621 | 1.3621 | 1.3621 | 1.3621
2020-09-18 18:00 | Winter | 1.5546 | 2.3904 | 3.6172 | 3.6172 | 3.6172 | 3.6172 | 0.62587 | 1.0242 | 1.4035 | 1.688 | 1.688 | 1.688 | 2.3816 | 3.4353 | 4.1258 | 4.4891 | 5.2159 | 5.9426 | 0.80402 | 2.184 | 2.7393 | 2.7393 | 2.7393 | 2.7393 | 0.85825 | 1.0894 | 1.0894 | 1.0894 | 1.0894 | 1.0894
2020-09-18 19:00 | Winter | 1.1813 | 1.8163 | 2.7485 | 2.7485 | 2.7485 | 2.7485 | 0.563 | 0.92127 | 1.2625 | 1.5184 | 1.5184 | 1.5184 | 2.2032 | 3.178 | 3.8167 | 4.1528 | 4.8251 | 5.4974 | 0.81164 | 2.2047 | 2.7653 | 2.7653 | 2.7653 | 2.7653 | 0.66684 | 0.84641 | 0.84641 | 0.84641 | 0.84641 | 0.84641
2020-09-18 20:00 | Winter | 1.086 | 1.6698 | 2.5268 | 2.5268 | 2.5268 | 2.5268 | 0.50013 | 0.81839 | 1.1215 | 1.3488 | 1.3488 | 1.3488 | 2.0733 | 2.9907 | 3.5917 | 3.908 | 4.5407 | 5.1734 | 0.73924 | 2.0081 | 2.5186 | 2.5186 | 2.5186 | 2.5186 | 0.64779 | 0.82222 | 0.82222 | 0.82222 | 0.82222 | 0.82222
2020-09-18 21:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.47726 | 0.78098 | 1.0702 | 1.2872 | 1.2872 | 1.2872 | 2.0767 | 2.9956 | 3.5977 | 3.9145 | 4.5482 | 5.182 | 0.74305 | 2.0184 | 2.5316 | 2.5316 | 2.5316 | 2.5316 | 0.59063 | 0.74967 | 0.74967 | 0.74967 | 0.74967 | 0.74967
2020-09-18 22:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.43725 | 0.7155 | 0.98051 | 1.1793 | 1.1793 | 1.1793 | 1.9161 | 2.764 | 3.3194 | 3.6118 | 4.1965 | 4.7812 | 0.724 | 1.9667 | 2.4667 | 2.4667 | 2.4667 | 2.4667 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-09-18 23:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.36348 | 0.59479 | 0.81508 | 0.9803 | 0.9803 | 0.9803 | 1.8194 | 2.6245 | 3.1519 | 3.4295 | 3.9847 | 4.5399 | 0.64779 | 1.7596 | 2.207 | 2.207 | 2.207 | 2.207 | 0.49537 | 0.62876 | 0.62876 | 0.62876 | 0.62876 | 0.62876
2020-09-19 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.39438 | 0.64536 | 0.88438 | 1.0636 | 1.0636 | 1.0636 | 1.6766 | 2.4185 | 2.9045 | 3.1603 | 3.672 | 4.1836 | 0.58682 | 1.594 | 1.9993 | 1.9993 | 1.9993 | 1.9993 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-09-19 01:00 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.40867 | 0.66874 | 0.91642 | 1.1022 | 1.1022 | 1.1022 | 1.6134 | 2.3272 | 2.7949 | 3.0411 | 3.5334 | 4.0257 | 0.59444 | 1.6147 | 2.0253 | 2.0253 | 2.0253 | 2.0253 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-09-19 02:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.35437 | 0.57988 | 0.79466 | 0.95574 | 0.95574 | 0.95574 | 1.6195 | 2.336 | 2.8055 | 3.0526 | 3.5468 | 4.041 | 0.57157 | 1.5526 | 1.9474 | 1.9474 | 1.9474 | 1.9474 | 0.45726 | 0.58039 | 0.58039 | 0.58039 | 0.58039 | 0.58039
2020-09-19 03:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.34866 | 0.57053 | 0.78184 | 0.94032 | 0.94032 | 0.94032 | 1.6195 | 2.336 | 2.8055 | 3.0526 | 3.5468 | 4.041 | 0.56079 | 1.5233 | 1.9106 | 1.9106 | 1.9106 | 1.9106 | 0.43821 | 0.55621 | 0.55621 | 0.55621 | 0.55621 | 0.55621
2020-09-19 04:00 | Winter | 0.99673 | 1.5326 | 2.3191 | 2.3191 | 2.3191 | 2.3191 | 0.32299 | 0.52853 | 0.72428 | 0.8711 | 0.8711 | 0.8711 | 1.6745 | 2.4154 | 2.9008 | 3.1562 | 3.6672 | 4.1782 | 0.56395 | 1.5319 | 1.9214 | 1.9214 | 1.9214 | 1.9214 | 0.43821 | 0.55621 | 0.55621 | 0.55621 | 0.55621 | 0.55621
2020-09-19 05:00 | Winter | 1.0288 | 1.582 | 2.3938 | 2.3938 | 2.3938 | 2.3938 | 0.39724 | 0.65003 | 0.89079 | 1.0713 | 1.0713 | 1.0713 | 1.7338 | 2.5009 | 3.0036 | 3.2681 | 3.7972 | 4.3262 | 0.59063 | 1.6044 | 2.0123 | 2.0123 | 2.0123 | 2.0123 | 0.4425 | 0.56165 | 0.56165 | 0.56165 | 0.56165 | 0.56165
2020-09-19 06:00 | Winter | 1.0288 | 1.582 | 2.3938 | 2.3938 | 2.3938 | 2.3938 | 0.40296 | 0.65939 | 0.9036 | 1.0868 | 1.0868 | 1.0868 | 1.7528 | 2.5284 | 3.0366 | 3.304 | 3.8389 | 4.3738 | 0.55633 | 1.5112 | 1.8954 | 1.8954 | 1.8954 | 1.8954 | 0.45724 | 0.58037 | 0.58037 | 0.58037 | 0.58037 | 0.58037
2020-09-19 07:00 | Winter | 1.086 | 1.6698 | 2.5268 | 2.5268 | 2.5268 | 2.5268 | 0.48584 | 0.79501 | 1.0895 | 1.3103 | 1.3103 | 1.3103 | 1.8253 | 2.6329 | 3.162 | 3.4405 | 3.9975 | 4.5545 | 0.68208 | 1.8528 | 2.3239 | 2.3239 | 2.3239 | 2.3239 | 0.55252 | 0.70131 | 0.70131 | 0.70131 | 0.70131 | 0.70131
2020-09-19 08:00 | Winter | 1.1432 | 1.7577 | 2.6598 | 2.6598 | 2.6598 | 2.6598 | 0.49155 | 0.80436 | 1.1023 | 1.3257 | 1.3257 | 1.3257 | 2.0196 | 2.9132 | 3.4986 | 3.8068 | 4.4231 | 5.0393 | 0.65541 | 1.7803 | 2.233 | 2.233 | 2.233 | 2.233 | 0.61523 | 0.7809 | 0.7809 | 0.7809 | 0.7809 | 0.7809
2020-09-19 09:00 | Winter | 1.105 | 1.6991 | 2.5711 | 2.5711 | 2.5711 | 2.5711 | 0.49727 | 0.81371 | 1.1151 | 1.3411 | 1.3411 | 1.3411 | 2.0386 | 2.9407 | 3.5316 | 3.8427 | 4.4648 | 5.0869 | 0.69351 | 1.8839 | 2.3628 | 2.3628 | 2.3628 | 2.3628 | 0.64779 | 0.82222 | 0.82222 | 0.82222 | 0.82222 | 0.82222
2020-09-19 10:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 0.49155 | 0.80436 | 1.1023 | 1.3257 | 1.3257 | 1.3257 | 2.0495 | 2.9564 | 3.5506 | 3.8633 | 4.4887 | 5.1141 | 0.69351 | 1.8839 | 2.3628 | 2.3628 | 2.3628 | 2.3628 | 0.70494 | 0.89477 | 0.89477 | 0.89477 | 0.89477 | 0.89477
2020-09-19 11:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 0.46297 | 0.75759 | 1.0382 | 1.2486 | 1.2486 | 1.2486 | 2.1529 | 3.1056 | 3.7297 | 4.0582 | 4.7151 | 5.3721 | 0.62111 | 1.6872 | 2.1161 | 2.1161 | 2.1161 | 2.1161 | 0.724 | 0.91895 | 0.91895 | 0.91895 | 0.91895 | 0.91895
2020-09-19 12:00 | Winter | 1.0288 | 1.582 | 2.3938 | 2.3938 | 2.3938 | 2.3938 | 0.4001 | 0.65471 | 0.89719 | 1.0791 | 1.0791 | 1.0791 | 2.191 | 3.1605 | 3.7957 | 4.13 | 4.7986 | 5.4672 | 0.64397 | 1.7493 | 2.194 | 2.194 | 2.194 | 2.194 | 0.724 | 0.91895 | 0.91895 | 0.91895 | 0.91895 | 0.91895
2020-09-19 13:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.45154 | 0.73889 | 1.0125 | 1.2178 | 1.2178 | 1.2178 | 2.1339 | 3.0781 | 3.6967 | 4.0223 | 4.6734 | 5.3246 | 0.62111 | 1.6872 | 2.1161 | 2.1161 | 2.1161 | 2.1161 | 0.66684 | 0.84641 | 0.84641 | 0.84641 | 0.84641 | 0.84641
2020-09-19 14:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.43154 | 0.70615 | 0.96769 | 1.1638 | 1.1638 | 1.1638 | 2.2101 | 3.188 | 3.8287 | 4.1659 | 4.8403 | 5.5147 | 0.73543 | 1.9977 | 2.5056 | 2.5056 | 2.5056 | 2.5056 | 0.57158 | 0.72549 | 0.72549 | 0.72549 | 0.72549 | 0.72549
2020-09-19 15:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 0.48584 | 0.79501 | 1.0895 | 1.3103 | 1.3103 | 1.3103 | 2.135 | 3.0797 | 3.6987 | 4.0244 | 4.6759 | 5.3274 | 0.74686 | 2.0288 | 2.5446 | 2.5446 | 2.5446 | 2.5446 | 0.59063 | 0.74967 | 0.74967 | 0.74967 | 0.74967 | 0.74967
2020-09-19 16:00 | Winter | 1.0669 | 1.6405 | 2.4825 | 2.4825 | 2.4825 | 2.4825 | 0.46297 | 0.75759 | 1.0382 | 1.2486 | 1.2486 | 1.2486 | 2.1339 | 3.0781 | 3.6967 | 4.0223 | 4.6734 | 5.3246 | 0.70113 | 1.9046 | 2.3888 | 2.3888 | 2.3888 | 2.3888 | 0.62873 | 0.79804 | 0.79804 | 0.79804 | 0.79804 | 0.79804
2020-09-19 17:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 0.41153 | 0.67342 | 0.92283 | 1.1099 | 1.1099 | 1.1099 | 2.0958 | 3.0231 | 3.6307 | 3.9504 | 4.59 | 5.2295 | 0.74686 | 2.0288 | 2.5446 | 2.5446 | 2.5446 | 2.5446 | 0.51324 | 0.65145 | 0.65145 | 0.65145 | 0.65145 | 0.65145
2020-09-19 18:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.41153 | 0.67342 | 0.92283 | 1.1099 | 1.1099 | 1.1099 | 2.1148 | 3.0506 | 3.6637 | 3.9863 | 4.6317 | 5.277 | 0.82307 | 2.2358 | 2.8042 | 2.8042 | 2.8042 | 2.8042 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-09-19 19:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.43154 | 0.70615 | 0.96769 | 1.1638 | 1.1638 | 1.1638 | 2.0958 | 3.0231 | 3.6307 | 3.9504 | 4.59 | 5.2295 | 0.75829 | 2.0598 | 2.5835 | 2.5835 | 2.5835 | 2.5835 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-09-19 20:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 0.5287 | 0.86515 | 1.1856 | 1.4259 | 1.4259 | 1.4259 | 2.0196 | 2.9132 | 3.4986 | 3.8068 | 4.4231 | 5.0393 | 0.70875 | 1.9253 | 2.4147 | 2.4147 | 2.4147 | 2.4147 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-09-19 21:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.47155 | 0.77162 | 1.0574 | 1.2717 | 1.2717 | 1.2717 | 1.9624 | 2.8307 | 3.3996 | 3.699 | 4.2979 | 4.8967 | 0.724 | 1.9667 | 2.4667 | 2.4667 | 2.4667 | 2.4667 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-09-19 22:00 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.40582 | 0.66406 | 0.91001 | 1.0945 | 1.0945 | 1.0945 | 1.8862 | 2.7208 | 3.2676 | 3.5554 | 4.131 | 4.7066 | 0.81164 | 2.2047 | 2.7653 | 2.7653 | 2.7653 | 2.7653 | 0.47559 | 0.60366 | 0.60366 | 0.60366 | 0.60366 | 0.60366
2020-09-19 23:00 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.38867 | 0.636 | 0.87156 | 1.0482 | 1.0482 | 1.0482 | 1.7684 | 2.5509 | 3.0636 | 3.3334 | 3.8731 | 4.4127 | 0.72781 | 1.977 | 2.4796 | 2.4796 | 2.4796 | 2.4796 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-09-20 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.40867 | 0.66874 | 0.91642 | 1.1022 | 1.1022 | 1.1022 | 1.6576 | 2.391 | 2.8715 | 3.1244 | 3.6302 | 4.1361 | 0.63254 | 1.7182 | 2.1551 | 2.1551 | 2.1551 | 2.1551 | 0.45726 | 0.58039 | 0.58039 | 0.58039 | 0.58039 | 0.58039
2020-09-20 01:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.43725 | 0.7155 | 0.98051 | 1.1793 | 1.1793 | 1.1793 | 1.6004 | 2.3086 | 2.7725 | 3.0167 | 3.5051 | 3.9934 | 0.57157 | 1.5526 | 1.9474 | 1.9474 | 1.9474 | 1.9474 | 0.45726 | 0.58039 | 0.58039 | 0.58039 | 0.58039 | 0.58039
2020-09-20 02:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.4001 | 0.65471 | 0.89719 | 1.0791 | 1.0791 | 1.0791 | 1.6004 | 2.3086 | 2.7725 | 3.0167 | 3.5051 | 3.9934 | 0.57539 | 1.563 | 1.9603 | 1.9603 | 1.9603 | 1.9603 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-09-20 03:00 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.31439 | 0.51446 | 0.70499 | 0.8479 | 0.8479 | 0.8479 | 1.5623 | 2.2536 | 2.7065 | 2.9449 | 3.4216 | 3.8984 | 0.55633 | 1.5112 | 1.8954 | 1.8954 | 1.8954 | 1.8954 | 0.43821 | 0.55621 | 0.55621 | 0.55621 | 0.55621 | 0.55621
2020-09-20 04:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.31728 | 0.51919 | 0.71149 | 0.8557 | 0.8557 | 0.8557 | 1.5623 | 2.2536 | 2.7065 | 2.9449 | 3.4216 | 3.8984 | 0.55633 | 1.5112 | 1.8954 | 1.8954 | 1.8954 | 1.8954 | 0.43821 | 0.55621 | 0.55621 | 0.55621 | 0.55621 | 0.55621
2020-09-20 05:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.33889 | 0.55455 | 0.75994 | 0.91398 | 0.91398 | 0.91398 | 1.6567 | 2.3897 | 2.8699 | 3.1227 | 3.6282 | 4.1338 | 0.59825 | 1.6251 | 2.0382 | 2.0382 | 2.0382 | 2.0382 | 0.44231 | 0.56142 | 0.56142 | 0.56142 | 0.56142 | 0.56142
2020-09-20 06:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.39724 | 0.65003 | 0.89079 | 1.0713 | 1.0713 | 1.0713 | 1.7528 | 2.5284 | 3.0366 | 3.304 | 3.8389 | 4.3738 | 0.57714 | 1.5677 | 1.9663 | 1.9663 | 1.9663 | 1.9663 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-09-20 07:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.4544 | 0.74356 | 1.019 | 1.2255 | 1.2255 | 1.2255 | 1.7959 | 2.5905 | 3.1111 | 3.3851 | 3.9332 | 4.4812 | 0.66684 | 1.8114 | 2.2719 | 2.2719 | 2.2719 | 2.2719 | 0.48835 | 0.61985 | 0.61985 | 0.61985 | 0.61985 | 0.61985
2020-09-20 08:00 | Winter | 1.0288 | 1.582 | 2.3938 | 2.3938 | 2.3938 | 2.3938 | 0.46869 | 0.76695 | 1.051 | 1.264 | 1.264 | 1.264 | 2.0005 | 2.8857 | 3.4656 | 3.7709 | 4.3813 | 4.9918 | 0.65541 | 1.7803 | 2.233 | 2.233 | 2.233 | 2.233 | 0.552 | 0.70065 | 0.70065 | 0.70065 | 0.70065 | 0.70065
2020-09-20 09:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.48584 | 0.79501 | 1.0895 | 1.3103 | 1.3103 | 1.3103 | 2.0577 | 2.9681 | 3.5647 | 3.8786 | 4.5065 | 5.1344 | 0.65541 | 1.7803 | 2.233 | 2.233 | 2.233 | 2.233 | 0.55252 | 0.70131 | 0.70131 | 0.70131 | 0.70131 | 0.70131
2020-09-20 10:00 | Winter | 1.0669 | 1.6405 | 2.4825 | 2.4825 | 2.4825 | 2.4825 | 0.39438 | 0.64536 | 0.88438 | 1.0636 | 1.0636 | 1.0636 | 2.1529 | 3.1056 | 3.7297 | 4.0582 | 4.7151 | 5.3721 | 0.67446 | 1.8321 | 2.2979 | 2.2979 | 2.2979 | 2.2979 | 0.57158 | 0.72549 | 0.72549 | 0.72549 | 0.72549 | 0.72549
2020-09-20 11:00 | Winter | 1.086 | 1.6698 | 2.5268 | 2.5268 | 2.5268 | 2.5268 | 0.42582 | 0.6968 | 0.95487 | 1.1484 | 1.1484 | 1.1484 | 2.2101 | 3.188 | 3.8287 | 4.1659 | 4.8403 | 5.5147 | 0.64779 | 1.7596 | 2.207 | 2.207 | 2.207 | 2.207 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-09-20 12:00 | Winter | 1.0669 | 1.6405 | 2.4825 | 2.4825 | 2.4825 | 2.4825 | 0.38581 | 0.63133 | 0.86515 | 1.0405 | 1.0405 | 1.0405 | 2.2482 | 3.243 | 3.8947 | 4.2377 | 4.9238 | 5.6098 | 0.63254 | 1.7182 | 2.1551 | 2.1551 | 2.1551 | 2.1551 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-09-20 13:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.39438 | 0.64536 | 0.88438 | 1.0636 | 1.0636 | 1.0636 | 2.2101 | 3.188 | 3.8287 | 4.1659 | 4.8403 | 5.5147 | 0.64016 | 1.7389 | 2.1811 | 2.1811 | 2.1811 | 2.1811 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-09-20 14:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.37152 | 0.60794 | 0.83311 | 1.002 | 1.002 | 1.002 | 2.2291 | 3.2155 | 3.8617 | 4.2018 | 4.8821 | 5.5623 | 0.60206 | 1.6354 | 2.0512 | 2.0512 | 2.0512 | 2.0512 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-09-20 15:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.38581 | 0.63133 | 0.86515 | 1.0405 | 1.0405 | 1.0405 | 2.191 | 3.1605 | 3.7957 | 4.13 | 4.7986 | 5.4672 | 0.61349 | 1.6665 | 2.0902 | 2.0902 | 2.0902 | 2.0902 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-09-20 16:00 | Winter | 1.0288 | 1.582 | 2.3938 | 2.3938 | 2.3938 | 2.3938 | 0.44583 | 0.72953 | 0.99973 | 1.2024 | 1.2024 | 1.2024 | 2.1529 | 3.1056 | 3.7297 | 4.0582 | 4.7151 | 5.3721 | 0.74305 | 2.0184 | 2.5316 | 2.5316 | 2.5316 | 2.5316 | 0.49537 | 0.62876 | 0.62876 | 0.62876 | 0.62876 | 0.62876
2020-09-20 17:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.49155 | 0.80436 | 1.1023 | 1.3257 | 1.3257 | 1.3257 | 2.0767 | 2.9956 | 3.5977 | 3.9145 | 4.5482 | 5.182 | 0.65922 | 1.7907 | 2.246 | 2.246 | 2.246 | 2.246 | 0.55252 | 0.70131 | 0.70131 | 0.70131 | 0.70131 | 0.70131
2020-09-20 18:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 0.44583 | 0.72953 | 0.99973 | 1.2024 | 1.2024 | 1.2024 | 2.1339 | 3.0781 | 3.6967 | 4.0223 | 4.6734 | 5.3246 | 0.74686 | 2.0288 | 2.5446 | 2.5446 | 2.5446 | 2.5446 | 0.51982 | 0.6598 | 0.6598 | 0.6598 | 0.6598 | 0.6598
2020-09-20 19:00 | Winter | 1.0288 | 1.582 | 2.3938 | 2.3938 | 2.3938 | 2.3938 | 0.45726 | 0.74824 | 1.0254 | 1.2332 | 1.2332 | 1.2332 | 2.0767 | 2.9956 | 3.5977 | 3.9145 | 4.5482 | 5.182 | 0.73543 | 1.9977 | 2.5056 | 2.5056 | 2.5056 | 2.5056 | 0.49537 | 0.62876 | 0.62876 | 0.62876 | 0.62876 | 0.62876
2020-09-20 20:00 | Winter | 1.0669 | 1.6405 | 2.4825 | 2.4825 | 2.4825 | 2.4825 | 0.48012 | 0.78565 | 1.0766 | 1.2949 | 1.2949 | 1.2949 | 2.0577 | 2.9681 | 3.5647 | 3.8786 | 4.5065 | 5.1344 | 0.71256 | 1.9356 | 2.4277 | 2.4277 | 2.4277 | 2.4277 | 0.49537 | 0.62876 | 0.62876 | 0.62876 | 0.62876 | 0.62876
2020-09-20 21:00 | Winter | 1.0288 | 1.582 | 2.3938 | 2.3938 | 2.3938 | 2.3938 | 0.40582 | 0.66406 | 0.91001 | 1.0945 | 1.0945 | 1.0945 | 1.9624 | 2.8307 | 3.3996 | 3.699 | 4.2979 | 4.8967 | 0.64779 | 1.7596 | 2.207 | 2.207 | 2.207 | 2.207 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-09-20 22:00 | Winter | 1.0288 | 1.582 | 2.3938 | 2.3938 | 2.3938 | 2.3938 | 0.40075 | 0.65578 | 0.89866 | 1.0808 | 1.0808 | 1.0808 | 1.9053 | 2.7483 | 3.3006 | 3.5913 | 4.1727 | 4.7541 | 0.68589 | 1.8632 | 2.3368 | 2.3368 | 2.3368 | 2.3368 | 0.55252 | 0.70131 | 0.70131 | 0.70131 | 0.70131 | 0.70131
2020-09-20 23:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.31192 | 0.51041 | 0.69945 | 0.84123 | 0.84123 | 0.84123 | 1.7353 | 2.5031 | 3.0061 | 3.2709 | 3.8004 | 4.3299 | 0.62111 | 1.6872 | 2.1161 | 2.1161 | 2.1161 | 2.1161 | 0.49537 | 0.62876 | 0.62876 | 0.62876 | 0.62876 | 0.62876
2020-09-21 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.4544 | 0.74356 | 1.019 | 1.2255 | 1.2255 | 1.2255 | 1.6184 | 2.3345 | 2.8037 | 3.0506 | 3.5445 | 4.0384 | 0.57539 | 1.563 | 1.9603 | 1.9603 | 1.9603 | 1.9603 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-09-21 01:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.41153 | 0.67342 | 0.92283 | 1.1099 | 1.1099 | 1.1099 | 1.5623 | 2.2536 | 2.7065 | 2.9449 | 3.4216 | 3.8984 | 0.53728 | 1.4595 | 1.8305 | 1.8305 | 1.8305 | 1.8305 | 0.50522 | 0.64126 | 0.64126 | 0.64126 | 0.64126 | 0.64126
2020-09-21 02:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.46012 | 0.75292 | 1.0318 | 1.2409 | 1.2409 | 1.2409 | 1.5623 | 2.2536 | 2.7065 | 2.9449 | 3.4216 | 3.8984 | 0.54871 | 1.4905 | 1.8695 | 1.8695 | 1.8695 | 1.8695 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-09-21 03:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.47726 | 0.78098 | 1.0702 | 1.2872 | 1.2872 | 1.2872 | 1.5623 | 2.2536 | 2.7065 | 2.9449 | 3.4216 | 3.8984 | 0.5449 | 1.4802 | 1.8565 | 1.8565 | 1.8565 | 1.8565 | 0.49537 | 0.62876 | 0.62876 | 0.62876 | 0.62876 | 0.62876
2020-09-21 04:00 | Winter | 1.1432 | 1.7577 | 2.6598 | 2.6598 | 2.6598 | 2.6598 | 0.44583 | 0.72953 | 0.99973 | 1.2024 | 1.2024 | 1.2024 | 1.6111 | 2.324 | 2.791 | 3.0368 | 3.5285 | 4.0201 | 0.53728 | 1.4595 | 1.8305 | 1.8305 | 1.8305 | 1.8305 | 0.57158 | 0.72549 | 0.72549 | 0.72549 | 0.72549 | 0.72549
2020-09-21 05:00 | Winter | 1.2194 | 1.8749 | 2.8371 | 2.8371 | 2.8371 | 2.8371 | 0.41725 | 0.68277 | 0.93565 | 1.1253 | 1.1253 | 1.1253 | 1.7235 | 2.4861 | 2.9857 | 3.2486 | 3.7746 | 4.3005 | 0.59825 | 1.6251 | 2.0382 | 2.0382 | 2.0382 | 2.0382 | 0.68589 | 0.87059 | 0.87059 | 0.87059 | 0.87059 | 0.87059
2020-09-21 06:00 | Winter | 1.3815 | 2.1242 | 3.2144 | 3.2144 | 3.2144 | 3.2144 | 0.57443 | 0.93998 | 1.2881 | 1.5492 | 1.5492 | 1.5492 | 1.9434 | 2.8032 | 3.3666 | 3.6631 | 4.2562 | 4.8492 | 0.69351 | 1.8839 | 2.3628 | 2.3628 | 2.3628 | 2.3628 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399
2020-09-21 07:00 | Winter | 1.8256 | 2.8071 | 4.2476 | 4.2476 | 4.2476 | 4.2476 | 0.70304 | 1.1504 | 1.5765 | 1.8961 | 1.8961 | 1.8961 | 2.1958 | 3.1674 | 3.8039 | 4.139 | 4.809 | 5.4791 | 0.83831 | 2.2772 | 2.8561 | 2.8561 | 2.8561 | 2.8561 | 1.0592 | 1.3445 | 1.3445 | 1.3445 | 1.3445 | 1.3445
2020-09-21 08:00 | Winter | 2.3054 | 3.5448 | 5.3639 | 5.3639 | 5.3639 | 5.3639 | 0.88022 | 1.4404 | 1.9738 | 2.3739 | 2.3739 | 2.3739 | 2.3345 | 3.3674 | 4.0442 | 4.4004 | 5.1127 | 5.8251 | 0.91071 | 2.4739 | 3.1028 | 3.1028 | 3.1028 | 3.1028 | 1.2575 | 1.5961 | 1.5961 | 1.5961 | 1.5961 | 1.5961
2020-09-21 09:00 | Winter | 2.3244 | 3.5741 | 5.4082 | 5.4082 | 5.4082 | 5.4082 | 0.77734 | 1.272 | 1.7431 | 2.0965 | 2.0965 | 2.0965 | 2.4768 | 3.5728 | 4.2908 | 4.6687 | 5.4245 | 6.1803 | 0.88404 | 2.4014 | 3.0119 | 3.0119 | 3.0119 | 3.0119 | 1.2575 | 1.5961 | 1.5961 | 1.5961 | 1.5961 | 1.5961
2020-09-21 10:00 | Winter | 2.4197 | 3.7205 | 5.6299 | 5.6299 | 5.6299 | 5.6299 | 0.77448 | 1.2673 | 1.7367 | 2.0888 | 2.0888 | 2.0888 | 2.7055 | 3.9026 | 4.6869 | 5.0996 | 5.9252 | 6.7508 | 0.85355 | 2.3186 | 2.9081 | 2.9081 | 2.9081 | 2.9081 | 1.3146 | 1.6686 | 1.6686 | 1.6686 | 1.6686 | 1.6686
2020-09-21 11:00 | Winter | 2.4006 | 3.6912 | 5.5856 | 5.5856 | 5.5856 | 5.5856 | 0.89737 | 1.4684 | 2.0123 | 2.4202 | 2.4202 | 2.4202 | 2.6483 | 3.8201 | 4.5878 | 4.9919 | 5.8 | 6.6082 | 0.91833 | 2.4946 | 3.1288 | 3.1288 | 3.1288 | 3.1288 | 1.3337 | 1.6928 | 1.6928 | 1.6928 | 1.6928 | 1.6928
2020-09-21 12:00 | Winter | 2.4387 | 3.7498 | 5.6742 | 5.6742 | 5.6742 | 5.6742 | 0.90595 | 1.4825 | 2.0315 | 2.4433 | 2.4433 | 2.4433 | 2.7817 | 4.0125 | 4.8189 | 5.2433 | 6.0921 | 6.941 | 0.87261 | 2.3704 | 2.973 | 2.973 | 2.973 | 2.973 | 1.3337 | 1.6928 | 1.6928 | 1.6928 | 1.6928 | 1.6928
2020-09-21 13:00 | Winter | 2.4768 | 3.8084 | 5.7629 | 5.7629 | 5.7629 | 5.7629 | 0.95739 | 1.5666 | 2.1469 | 2.582 | 2.582 | 2.582 | 2.7626 | 3.985 | 4.7859 | 5.2074 | 6.0504 | 6.8934 | 0.91833 | 2.4946 | 3.1288 | 3.1288 | 3.1288 | 3.1288 | 1.3527 | 1.717 | 1.717 | 1.717 | 1.717 | 1.717
2020-09-21 14:00 | Winter | 2.4768 | 3.8084 | 5.7629 | 5.7629 | 5.7629 | 5.7629 | 0.92595 | 1.5152 | 2.0764 | 2.4973 | 2.4973 | 2.4973 | 2.8007 | 4.04 | 4.8519 | 5.2792 | 6.1339 | 6.9885 | 0.93357 | 2.536 | 3.1807 | 3.1807 | 3.1807 | 3.1807 | 1.2575 | 1.5961 | 1.5961 | 1.5961 | 1.5961 | 1.5961
2020-09-21 15:00 | Winter | 2.4197 | 3.7205 | 5.6299 | 5.6299 | 5.6299 | 5.6299 | 0.97453 | 1.5947 | 2.1853 | 2.6283 | 2.6283 | 2.6283 | 2.7055 | 3.9026 | 4.6869 | 5.0996 | 5.9252 | 6.7508 | 0.82307 | 2.2358 | 2.8042 | 2.8042 | 2.8042 | 2.8042 | 1.3337 | 1.6928 | 1.6928 | 1.6928 | 1.6928 | 1.6928
2020-09-21 16:00 | Winter | 2.4197 | 3.7205 | 5.6299 | 5.6299 | 5.6299 | 5.6299 | 0.95739 | 1.5666 | 2.1469 | 2.582 | 2.582 | 2.582 | 2.6674 | 3.8476 | 4.6208 | 5.0278 | 5.8418 | 6.6557 | 0.87642 | 2.3807 | 2.986 | 2.986 | 2.986 | 2.986 | 1.1622 | 1.4752 | 1.4752 | 1.4752 | 1.4752 | 1.4752
2020-09-21 17:00 | Winter | 2.1148 | 3.2518 | 4.9206 | 4.9206 | 4.9206 | 4.9206 | 0.87165 | 1.4263 | 1.9546 | 2.3508 | 2.3508 | 2.3508 | 2.553 | 3.6827 | 4.4228 | 4.8123 | 5.5914 | 6.3705 | 0.91833 | 2.4946 | 3.1288 | 3.1288 | 3.1288 | 3.1288 | 1.0669 | 1.3542 | 1.3542 | 1.3542 | 1.3542 | 1.3542
2020-09-21 18:00 | Winter | 1.5903 | 2.4453 | 3.7002 | 3.7002 | 3.7002 | 3.7002 | 0.62587 | 1.0242 | 1.4035 | 1.688 | 1.688 | 1.688 | 2.2863 | 3.2979 | 3.9607 | 4.3096 | 5.0072 | 5.7049 | 0.87261 | 2.3704 | 2.973 | 2.973 | 2.973 | 2.973 | 0.76508 | 0.9711 | 0.9711 | 0.9711 | 0.9711 | 0.9711
2020-09-21 19:00 | Winter | 1.2062 | 1.8547 | 2.8065 | 2.8065 | 2.8065 | 2.8065 | 0.55728 | 0.91192 | 1.2497 | 1.503 | 1.503 | 1.503 | 2.1453 | 3.0945 | 3.7164 | 4.0437 | 4.6984 | 5.353 | 0.85736 | 2.3289 | 2.9211 | 2.9211 | 2.9211 | 2.9211 | 0.62873 | 0.79804 | 0.79804 | 0.79804 | 0.79804 | 0.79804
2020-09-21 20:00 | Winter | 1.105 | 1.6991 | 2.5711 | 2.5711 | 2.5711 | 2.5711 | 0.53728 | 0.87918 | 1.2048 | 1.449 | 1.449 | 1.449 | 2.0389 | 2.9411 | 3.5322 | 3.8433 | 4.4655 | 5.0877 | 0.76972 | 2.0909 | 2.6225 | 2.6225 | 2.6225 | 2.6225 | 0.60968 | 0.77386 | 0.77386 | 0.77386 | 0.77386 | 0.77386
2020-09-21 21:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 0.52585 | 0.86048 | 1.1792 | 1.4182 | 1.4182 | 1.4182 | 2.0005 | 2.8857 | 3.4656 | 3.7709 | 4.3813 | 4.9918 | 0.724 | 1.9667 | 2.4667 | 2.4667 | 2.4667 | 2.4667 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-09-21 22:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 0.5287 | 0.86515 | 1.1856 | 1.4259 | 1.4259 | 1.4259 | 1.829 | 2.6383 | 3.1686 | 3.4477 | 4.0058 | 4.5639 | 0.69351 | 1.8839 | 2.3628 | 2.3628 | 2.3628 | 2.3628 | 0.49537 | 0.62876 | 0.62876 | 0.62876 | 0.62876 | 0.62876
2020-09-21 23:00 | Winter | 0.98429 | 1.5135 | 2.2902 | 2.2902 | 2.2902 | 2.2902 | 0.48012 | 0.78565 | 1.0766 | 1.2949 | 1.2949 | 1.2949 | 1.7528 | 2.5284 | 3.0366 | 3.304 | 3.8389 | 4.3738 | 0.63635 | 1.7286 | 2.1681 | 2.1681 | 2.1681 | 2.1681 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-09-22 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.51442 | 0.84177 | 1.1535 | 1.3874 | 1.3874 | 1.3874 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.59795 | 1.6243 | 2.0372 | 2.0372 | 2.0372 | 2.0372 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-09-22 01:00 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.43725 | 0.7155 | 0.98051 | 1.1793 | 1.1793 | 1.1793 | 1.585 | 2.2863 | 2.7458 | 2.9876 | 3.4713 | 3.955 | 0.56776 | 1.5423 | 1.9344 | 1.9344 | 1.9344 | 1.9344 | 0.45726 | 0.58039 | 0.58039 | 0.58039 | 0.58039 | 0.58039
2020-09-22 02:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.42582 | 0.6968 | 0.95487 | 1.1484 | 1.1484 | 1.1484 | 1.5433 | 2.2261 | 2.6735 | 2.909 | 3.3799 | 3.8508 | 0.59063 | 1.6044 | 2.0123 | 2.0123 | 2.0123 | 2.0123 | 0.49537 | 0.62876 | 0.62876 | 0.62876 | 0.62876 | 0.62876
2020-09-22 03:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.47441 | 0.7763 | 1.0638 | 1.2795 | 1.2795 | 1.2795 | 1.5623 | 2.2536 | 2.7065 | 2.9449 | 3.4216 | 3.8984 | 0.56014 | 1.5216 | 1.9084 | 1.9084 | 1.9084 | 1.9084 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-09-22 04:00 | Winter | 1.0906 | 1.6769 | 2.5375 | 2.5375 | 2.5375 | 2.5375 | 0.38008 | 0.62194 | 0.85229 | 1.0251 | 1.0251 | 1.0251 | 1.5052 | 2.1711 | 2.6075 | 2.8371 | 3.2964 | 3.7557 | 0.58682 | 1.594 | 1.9993 | 1.9993 | 1.9993 | 1.9993 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-09-22 05:00 | Winter | 1.2002 | 1.8454 | 2.7925 | 2.7925 | 2.7925 | 2.7925 | 0.56586 | 0.92595 | 1.2689 | 1.5261 | 1.5261 | 1.5261 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.59444 | 1.6147 | 2.0253 | 2.0253 | 2.0253 | 2.0253 | 0.69389 | 0.88074 | 0.88074 | 0.88074 | 0.88074 | 0.88074
2020-09-22 06:00 | Winter | 1.3706 | 2.1074 | 3.1889 | 3.1889 | 3.1889 | 3.1889 | 0.58872 | 0.96336 | 1.3202 | 1.5878 | 1.5878 | 1.5878 | 1.8379 | 2.6511 | 3.184 | 3.4644 | 4.0252 | 4.5861 | 0.71637 | 1.946 | 2.4407 | 2.4407 | 2.4407 | 2.4407 | 0.80065 | 1.0162 | 1.0162 | 1.0162 | 1.0162 | 1.0162
2020-09-22 07:00 | Winter | 1.81 | 2.7831 | 4.2113 | 4.2113 | 4.2113 | 4.2113 | 0.8002 | 1.3094 | 1.7944 | 2.1581 | 2.1581 | 2.1581 | 2.1604 | 3.1164 | 3.7427 | 4.0723 | 4.7316 | 5.3908 | 0.8345 | 2.2668 | 2.8432 | 2.8432 | 2.8432 | 2.8432 | 1.0249 | 1.3009 | 1.3009 | 1.3009 | 1.3009 | 1.3009
2020-09-22 08:00 | Winter | 2.0958 | 3.2225 | 4.8763 | 4.8763 | 4.8763 | 4.8763 | 0.84307 | 1.3796 | 1.8905 | 2.2737 | 2.2737 | 2.2737 | 2.4449 | 3.5267 | 4.2355 | 4.6086 | 5.3546 | 6.1007 | 1.0479 | 2.8465 | 3.5702 | 3.5702 | 3.5702 | 3.5702 | 1.1813 | 1.4993 | 1.4993 | 1.4993 | 1.4993 | 1.4993
2020-09-22 09:00 | Winter | 2.3054 | 3.5448 | 5.3639 | 5.3639 | 5.3639 | 5.3639 | 0.87165 | 1.4263 | 1.9546 | 2.3508 | 2.3508 | 2.3508 | 2.4768 | 3.5728 | 4.2908 | 4.6687 | 5.4245 | 6.1803 | 1.0444 | 2.8371 | 3.5584 | 3.5584 | 3.5584 | 3.5584 | 1.2765 | 1.6203 | 1.6203 | 1.6203 | 1.6203 | 1.6203
2020-09-22 10:00 | Winter | 2.3054 | 3.5448 | 5.3639 | 5.3639 | 5.3639 | 5.3639 | 0.77448 | 1.2673 | 1.7367 | 2.0888 | 2.0888 | 2.0888 | 2.4959 | 3.6002 | 4.3238 | 4.7046 | 5.4662 | 6.2279 | 0.9793 | 2.6602 | 3.3365 | 3.3365 | 3.3365 | 3.3365 | 1.2956 | 1.6444 | 1.6444 | 1.6444 | 1.6444 | 1.6444
2020-09-22 11:00 | Winter | 2.2863 | 3.5155 | 5.3196 | 5.3196 | 5.3196 | 5.3196 | 0.79798 | 1.3058 | 1.7894 | 2.1521 | 2.1521 | 2.1521 | 2.6102 | 3.7651 | 4.5218 | 4.9201 | 5.7166 | 6.5131 | 0.91452 | 2.4842 | 3.1158 | 3.1158 | 3.1158 | 3.1158 | 1.2956 | 1.6444 | 1.6444 | 1.6444 | 1.6444 | 1.6444
2020-09-22 12:00 | Winter | 2.3435 | 3.6034 | 5.4526 | 5.4526 | 5.4526 | 5.4526 | 0.8002 | 1.3094 | 1.7944 | 2.1581 | 2.1581 | 2.1581 | 2.4768 | 3.5728 | 4.2908 | 4.6687 | 5.4245 | 6.1803 | 0.89547 | 2.4325 | 3.0509 | 3.0509 | 3.0509 | 3.0509 | 1.3146 | 1.6686 | 1.6686 | 1.6686 | 1.6686 | 1.6686
2020-09-22 13:00 | Winter | 2.3625 | 3.6326 | 5.4969 | 5.4969 | 5.4969 | 5.4969 | 0.77448 | 1.2673 | 1.7367 | 2.0888 | 2.0888 | 2.0888 | 2.4768 | 3.5728 | 4.2908 | 4.6687 | 5.4245 | 6.1803 | 0.90309 | 2.4532 | 3.0768 | 3.0768 | 3.0768 | 3.0768 | 1.2384 | 1.5719 | 1.5719 | 1.5719 | 1.5719 | 1.5719
2020-09-22 14:00 | Winter | 2.2863 | 3.5155 | 5.3196 | 5.3196 | 5.3196 | 5.3196 | 0.74019 | 1.2112 | 1.6598 | 1.9963 | 1.9963 | 1.9963 | 2.4959 | 3.6002 | 4.3238 | 4.7046 | 5.4662 | 6.2279 | 0.80021 | 2.1737 | 2.7263 | 2.7263 | 2.7263 | 2.7263 | 1.2575 | 1.5961 | 1.5961 | 1.5961 | 1.5961 | 1.5961
2020-09-22 15:00 | Winter | 2.2863 | 3.5155 | 5.3196 | 5.3196 | 5.3196 | 5.3196 | 0.80592 | 1.3188 | 1.8072 | 2.1735 | 2.1735 | 2.1735 | 2.4768 | 3.5728 | 4.2908 | 4.6687 | 5.4245 | 6.1803 | 0.89547 | 2.4325 | 3.0509 | 3.0509 | 3.0509 | 3.0509 | 1.2047 | 1.5291 | 1.5291 | 1.5291 | 1.5291 | 1.5291
2020-09-22 16:00 | Winter | 2.2482 | 3.4569 | 5.2309 | 5.2309 | 5.2309 | 5.2309 | 0.75734 | 1.2393 | 1.6983 | 2.0425 | 2.0425 | 2.0425 | 2.4197 | 3.4903 | 4.1918 | 4.561 | 5.2993 | 6.0377 | 0.88785 | 2.4118 | 3.0249 | 3.0249 | 3.0249 | 3.0249 | 1.1432 | 1.451 | 1.451 | 1.451 | 1.451 | 1.451
2020-09-22 17:00 | Winter | 2.0577 | 3.1639 | 4.7876 | 4.7876 | 4.7876 | 4.7876 | 0.76877 | 1.258 | 1.7239 | 2.0733 | 2.0733 | 2.0733 | 2.3054 | 3.3254 | 3.9937 | 4.3455 | 5.049 | 5.7525 | 0.77353 | 2.1012 | 2.6354 | 2.6354 | 2.6354 | 2.6354 | 1.0479 | 1.3301 | 1.3301 | 1.3301 | 1.3301 | 1.3301
2020-09-22 18:00 | Winter | 1.6181 | 2.4881 | 3.765 | 3.765 | 3.765 | 3.765 | 0.64874 | 1.0616 | 1.4547 | 1.7496 | 1.7496 | 1.7496 | 2.2291 | 3.2155 | 3.8617 | 4.2018 | 4.8821 | 5.5623 | 0.75448 | 2.0495 | 2.5705 | 2.5705 | 2.5705 | 2.5705 | 0.73747 | 0.93606 | 0.93606 | 0.93606 | 0.93606 | 0.93606
2020-09-22 19:00 | Winter | 1.1241 | 1.7284 | 2.6155 | 2.6155 | 2.6155 | 2.6155 | 0.58586 | 0.95868 | 1.3138 | 1.5801 | 1.5801 | 1.5801 | 2.1148 | 3.0506 | 3.6637 | 3.9863 | 4.6317 | 5.277 | 0.7964 | 2.1633 | 2.7133 | 2.7133 | 2.7133 | 2.7133 | 0.62816 | 0.79731 | 0.79731 | 0.79731 | 0.79731 | 0.79731
2020-09-22 20:00 | Winter | 1.1241 | 1.7284 | 2.6155 | 2.6155 | 2.6155 | 2.6155 | 0.46869 | 0.76695 | 1.051 | 1.264 | 1.264 | 1.264 | 2.0196 | 2.9132 | 3.4986 | 3.8068 | 4.4231 | 5.0393 | 0.70113 | 1.9046 | 2.3888 | 2.3888 | 2.3888 | 2.3888 | 0.55296 | 0.70186 | 0.70186 | 0.70186 | 0.70186 | 0.70186
2020-09-22 21:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 0.49441 | 0.80903 | 1.1087 | 1.3334 | 1.3334 | 1.3334 | 1.9286 | 2.782 | 3.3411 | 3.6354 | 4.2239 | 4.8125 | 0.65541 | 1.7803 | 2.233 | 2.233 | 2.233 | 2.233 | 0.49542 | 0.62883 | 0.62883 | 0.62883 | 0.62883 | 0.62883
2020-09-22 22:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.4001 | 0.65471 | 0.89719 | 1.0791 | 1.0791 | 1.0791 | 1.7522 | 2.5275 | 3.0355 | 3.3028 | 3.8375 | 4.3722 | 0.69732 | 1.8942 | 2.3758 | 2.3758 | 2.3758 | 2.3758 | 0.4764 | 0.60468 | 0.60468 | 0.60468 | 0.60468 | 0.60468
2020-09-22 23:00 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.47155 | 0.77162 | 1.0574 | 1.2717 | 1.2717 | 1.2717 | 1.6486 | 2.378 | 2.8559 | 3.1074 | 3.6105 | 4.1136 | 0.62111 | 1.6872 | 2.1161 | 2.1161 | 2.1161 | 2.1161 | 0.42821 | 0.54352 | 0.54352 | 0.54352 | 0.54352 | 0.54352
2020-09-23 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.41153 | 0.67342 | 0.92283 | 1.1099 | 1.1099 | 1.1099 | 1.5623 | 2.2536 | 2.7065 | 2.9449 | 3.4216 | 3.8984 | 0.5801 | 1.5758 | 1.9764 | 1.9764 | 1.9764 | 1.9764 | 0.43821 | 0.55621 | 0.55621 | 0.55621 | 0.55621 | 0.55621
2020-09-23 01:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.44011 | 0.72018 | 0.98691 | 1.187 | 1.187 | 1.187 | 1.5052 | 2.1711 | 2.6075 | 2.8371 | 3.2964 | 3.7557 | 0.60587 | 1.6458 | 2.0642 | 2.0642 | 2.0642 | 2.0642 | 0.41682 | 0.52905 | 0.52905 | 0.52905 | 0.52905 | 0.52905
2020-09-23 02:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.4544 | 0.74356 | 1.019 | 1.2255 | 1.2255 | 1.2255 | 1.5242 | 2.1986 | 2.6405 | 2.873 | 3.3382 | 3.8033 | 0.58682 | 1.594 | 1.9993 | 1.9993 | 1.9993 | 1.9993 | 0.41916 | 0.53203 | 0.53203 | 0.53203 | 0.53203 | 0.53203
2020-09-23 03:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.46012 | 0.75292 | 1.0318 | 1.2409 | 1.2409 | 1.2409 | 1.5242 | 2.1986 | 2.6405 | 2.873 | 3.3382 | 3.8033 | 0.51823 | 1.4077 | 1.7656 | 1.7656 | 1.7656 | 1.7656 | 0.49532 | 0.6287 | 0.6287 | 0.6287 | 0.6287 | 0.6287
2020-09-23 04:00 | Winter | 1.1241 | 1.7284 | 2.6155 | 2.6155 | 2.6155 | 2.6155 | 0.46297 | 0.75759 | 1.0382 | 1.2486 | 1.2486 | 1.2486 | 1.4901 | 2.1495 | 2.5815 | 2.8088 | 3.2636 | 3.7183 | 0.59444 | 1.6147 | 2.0253 | 2.0253 | 2.0253 | 2.0253 | 0.49537 | 0.62876 | 0.62876 | 0.62876 | 0.62876 | 0.62876
2020-09-23 05:00 | Winter | 1.2575 | 1.9335 | 2.9258 | 2.9258 | 2.9258 | 2.9258 | 0.50584 | 0.82774 | 1.1343 | 1.3642 | 1.3642 | 1.3642 | 1.6886 | 2.4358 | 2.9253 | 3.1829 | 3.6982 | 4.2135 | 0.58682 | 1.594 | 1.9993 | 1.9993 | 1.9993 | 1.9993 | 0.63132 | 0.80132 | 0.80132 | 0.80132 | 0.80132 | 0.80132
2020-09-23 06:00 | Winter | 1.3231 | 2.0344 | 3.0784 | 3.0784 | 3.0784 | 3.0784 | 0.65445 | 1.0709 | 1.4676 | 1.765 | 1.765 | 1.765 | 1.9719 | 2.8444 | 3.416 | 3.7168 | 4.3186 | 4.9203 | 0.64778 | 1.7596 | 2.207 | 2.207 | 2.207 | 2.207 | 0.83631 | 1.0615 | 1.0615 | 1.0615 | 1.0615 | 1.0615
2020-09-23 07:00 | Winter | 1.7719 | 2.7245 | 4.1227 | 4.1227 | 4.1227 | 4.1227 | 0.79735 | 1.3047 | 1.788 | 2.1504 | 2.1504 | 2.1504 | 2.1742 | 3.1362 | 3.7665 | 4.0982 | 4.7617 | 5.4251 | 0.84212 | 2.2875 | 2.8691 | 2.8691 | 2.8691 | 2.8691 | 1.0669 | 1.3542 | 1.3542 | 1.3542 | 1.3542 | 1.3542
2020-09-23 08:00 | Winter | 2.0958 | 3.2225 | 4.8763 | 4.8763 | 4.8763 | 4.8763 | 0.86308 | 1.4123 | 1.9354 | 2.3277 | 2.3277 | 2.3277 | 2.4006 | 3.4628 | 4.1588 | 4.525 | 5.2576 | 5.9902 | 0.88404 | 2.4014 | 3.0119 | 3.0119 | 3.0119 | 3.0119 | 1.2384 | 1.5719 | 1.5719 | 1.5719 | 1.5719 | 1.5719
2020-09-23 09:00 | Winter | 2.1529 | 3.3104 | 5.0093 | 5.0093 | 5.0093 | 5.0093 | 0.8545 | 1.3983 | 1.9162 | 2.3046 | 2.3046 | 2.3046 | 2.4768 | 3.5728 | 4.2908 | 4.6687 | 5.4245 | 6.1803 | 0.88023 | 2.3911 | 2.9989 | 2.9989 | 2.9989 | 2.9989 | 1.2956 | 1.6444 | 1.6444 | 1.6444 | 1.6444 | 1.6444
2020-09-23 10:00 | Winter | 2.1148 | 3.2518 | 4.9206 | 4.9206 | 4.9206 | 4.9206 | 0.87451 | 1.431 | 1.961 | 2.3585 | 2.3585 | 2.3585 | 2.4768 | 3.5728 | 4.2908 | 4.6687 | 5.4245 | 6.1803 | 0.87261 | 2.3704 | 2.973 | 2.973 | 2.973 | 2.973 | 1.3527 | 1.717 | 1.717 | 1.717 | 1.717 | 1.717
2020-09-23 11:00 | Winter | 2.1043 | 3.2356 | 4.8961 | 4.8961 | 4.8961 | 4.8961 | 0.95453 | 1.562 | 2.1405 | 2.5743 | 2.5743 | 2.5743 | 2.5149 | 3.6277 | 4.3568 | 4.7405 | 5.508 | 6.2754 | 0.81164 | 2.2047 | 2.7653 | 2.7653 | 2.7653 | 2.7653 | 1.3908 | 1.7654 | 1.7654 | 1.7654 | 1.7654 | 1.7654
2020-09-23 12:00 | Winter | 2.0577 | 3.1639 | 4.7876 | 4.7876 | 4.7876 | 4.7876 | 0.8888 | 1.4544 | 1.9931 | 2.3971 | 2.3971 | 2.3971 | 2.5721 | 3.7102 | 4.4558 | 4.8483 | 5.6331 | 6.418 | 0.85736 | 2.3289 | 2.9211 | 2.9211 | 2.9211 | 2.9211 | 1.3527 | 1.717 | 1.717 | 1.717 | 1.717 | 1.717
2020-09-23 13:00 | Winter | 2.0552 | 3.1601 | 4.7818 | 4.7818 | 4.7818 | 4.7818 | 0.8545 | 1.3983 | 1.9162 | 2.3046 | 2.3046 | 2.3046 | 2.4959 | 3.6002 | 4.3238 | 4.7046 | 5.4662 | 6.2279 | 0.80021 | 2.1737 | 2.7263 | 2.7263 | 2.7263 | 2.7263 | 1.3337 | 1.6928 | 1.6928 | 1.6928 | 1.6928 | 1.6928
2020-09-23 14:00 | Winter | 2.0958 | 3.2225 | 4.8763 | 4.8763 | 4.8763 | 4.8763 | 0.87737 | 1.4357 | 1.9674 | 2.3662 | 2.3662 | 2.3662 | 2.553 | 3.6827 | 4.4228 | 4.8123 | 5.5914 | 6.3705 | 0.83831 | 2.2772 | 2.8561 | 2.8561 | 2.8561 | 2.8561 | 1.3146 | 1.6686 | 1.6686 | 1.6686 | 1.6686 | 1.6686
2020-09-23 15:00 | Winter | 2.0767 | 3.1932 | 4.832 | 4.832 | 4.832 | 4.832 | 0.80878 | 1.3235 | 1.8136 | 2.1812 | 2.1812 | 2.1812 | 2.4387 | 3.5178 | 4.2248 | 4.5969 | 5.3411 | 6.0852 | 0.81164 | 2.2047 | 2.7653 | 2.7653 | 2.7653 | 2.7653 | 1.2194 | 1.5477 | 1.5477 | 1.5477 | 1.5477 | 1.5477
2020-09-23 16:00 | Winter | 2.0577 | 3.1639 | 4.7876 | 4.7876 | 4.7876 | 4.7876 | 0.87451 | 1.431 | 1.961 | 2.3585 | 2.3585 | 2.3585 | 2.4197 | 3.4903 | 4.1918 | 4.561 | 5.2993 | 6.0377 | 0.88023 | 2.3911 | 2.9989 | 2.9989 | 2.9989 | 2.9989 | 1.1813 | 1.4993 | 1.4993 | 1.4993 | 1.4993 | 1.4993
2020-09-23 17:00 | Winter | 1.8862 | 2.9003 | 4.3887 | 4.3887 | 4.3887 | 4.3887 | 0.77162 | 1.2627 | 1.7303 | 2.081 | 2.081 | 2.081 | 2.3427 | 3.3792 | 4.0584 | 4.4158 | 5.1307 | 5.8456 | 0.75067 | 2.0391 | 2.5575 | 2.5575 | 2.5575 | 2.5575 | 1.0705 | 1.3587 | 1.3587 | 1.3587 | 1.3587 | 1.3587
2020-09-23 18:00 | Winter | 1.629 | 2.5048 | 3.7903 | 3.7903 | 3.7903 | 3.7903 | 0.69446 | 1.1364 | 1.5573 | 1.8729 | 1.8729 | 1.8729 | 2.4197 | 3.4903 | 4.1918 | 4.561 | 5.2993 | 6.0377 | 0.80402 | 2.184 | 2.7393 | 2.7393 | 2.7393 | 2.7393 | 0.84862 | 1.0771 | 1.0771 | 1.0771 | 1.0771 | 1.0771
2020-09-23 19:00 | Winter | 1.2176 | 1.8722 | 2.833 | 2.833 | 2.833 | 2.833 | 0.59729 | 0.97739 | 1.3394 | 1.6109 | 1.6109 | 1.6109 | 2.3234 | 3.3515 | 4.0251 | 4.3796 | 5.0886 | 5.7976 | 0.81545 | 2.2151 | 2.7782 | 2.7782 | 2.7782 | 2.7782 | 0.65517 | 0.8316 | 0.8316 | 0.8316 | 0.8316 | 0.8316
2020-09-23 20:00 | Winter | 1.105 | 1.6991 | 2.5711 | 2.5711 | 2.5711 | 2.5711 | 0.52013 | 0.85112 | 1.1664 | 1.4028 | 1.4028 | 1.4028 | 2.2863 | 3.2979 | 3.9607 | 4.3096 | 5.0072 | 5.7049 | 0.75067 | 2.0391 | 2.5575 | 2.5575 | 2.5575 | 2.5575 | 0.59063 | 0.74967 | 0.74967 | 0.74967 | 0.74967 | 0.74967
2020-09-23 21:00 | Winter | 1.105 | 1.6991 | 2.5711 | 2.5711 | 2.5711 | 2.5711 | 0.48584 | 0.79501 | 1.0895 | 1.3103 | 1.3103 | 1.3103 | 2.0577 | 2.9681 | 3.5647 | 3.8786 | 4.5065 | 5.1344 | 0.67446 | 1.8321 | 2.2979 | 2.2979 | 2.2979 | 2.2979 | 0.55252 | 0.70131 | 0.70131 | 0.70131 | 0.70131 | 0.70131
2020-09-23 22:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.48012 | 0.78565 | 1.0766 | 1.2949 | 1.2949 | 1.2949 | 1.8481 | 2.6658 | 3.2016 | 3.4836 | 4.0475 | 4.6115 | 0.63635 | 1.7286 | 2.1681 | 2.1681 | 2.1681 | 2.1681 | 0.49537 | 0.62876 | 0.62876 | 0.62876 | 0.62876 | 0.62876
2020-09-23 23:00 | Winter | 0.95354 | 1.4662 | 2.2186 | 2.2186 | 2.2186 | 2.2186 | 0.49155 | 0.80436 | 1.1023 | 1.3257 | 1.3257 | 1.3257 | 1.7528 | 2.5284 | 3.0366 | 3.304 | 3.8389 | 4.3738 | 0.61349 | 1.6665 | 2.0902 | 2.0902 | 2.0902 | 2.0902 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-09-24 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.46012 | 0.75292 | 1.0318 | 1.2409 | 1.2409 | 1.2409 | 1.6195 | 2.336 | 2.8055 | 3.0526 | 3.5468 | 4.041 | 0.58682 | 1.594 | 1.9993 | 1.9993 | 1.9993 | 1.9993 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-09-24 01:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.46012 | 0.75292 | 1.0318 | 1.2409 | 1.2409 | 1.2409 | 1.5433 | 2.2261 | 2.6735 | 2.909 | 3.3799 | 3.8508 | 0.53728 | 1.4595 | 1.8305 | 1.8305 | 1.8305 | 1.8305 | 0.43821 | 0.55621 | 0.55621 | 0.55621 | 0.55621 | 0.55621
2020-09-24 02:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.4544 | 0.74356 | 1.019 | 1.2255 | 1.2255 | 1.2255 | 1.5433 | 2.2261 | 2.6735 | 2.909 | 3.3799 | 3.8508 | 0.52585 | 1.4284 | 1.7916 | 1.7916 | 1.7916 | 1.7916 | 0.45726 | 0.58039 | 0.58039 | 0.58039 | 0.58039 | 0.58039
2020-09-24 03:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.45154 | 0.73889 | 1.0125 | 1.2178 | 1.2178 | 1.2178 | 1.5433 | 2.2261 | 2.6735 | 2.909 | 3.3799 | 3.8508 | 0.5792 | 1.5733 | 1.9733 | 1.9733 | 1.9733 | 1.9733 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-09-24 04:00 | Winter | 1.1432 | 1.7577 | 2.6598 | 2.6598 | 2.6598 | 2.6598 | 0.45154 | 0.73889 | 1.0125 | 1.2178 | 1.2178 | 1.2178 | 1.581 | 2.2806 | 2.7389 | 2.9801 | 3.4626 | 3.9451 | 0.54871 | 1.4905 | 1.8695 | 1.8695 | 1.8695 | 1.8695 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-09-24 05:00 | Winter | 1.2252 | 1.8839 | 2.8508 | 2.8508 | 2.8508 | 2.8508 | 0.53728 | 0.87918 | 1.2048 | 1.449 | 1.449 | 1.449 | 1.7338 | 2.5009 | 3.0036 | 3.2681 | 3.7972 | 4.3262 | 0.58682 | 1.594 | 1.9993 | 1.9993 | 1.9993 | 1.9993 | 0.72264 | 0.91723 | 0.91723 | 0.91723 | 0.91723 | 0.91723
2020-09-24 06:00 | Winter | 1.3521 | 2.0791 | 3.146 | 3.146 | 3.146 | 3.146 | 0.68303 | 1.1177 | 1.5316 | 1.8421 | 1.8421 | 1.8421 | 1.9048 | 2.7477 | 3.2999 | 3.5905 | 4.1718 | 4.753 | 0.65541 | 1.7803 | 2.233 | 2.233 | 2.233 | 2.233 | 0.9238 | 1.1726 | 1.1726 | 1.1726 | 1.1726 | 1.1726
2020-09-24 07:00 | Winter | 1.9243 | 2.9588 | 4.4772 | 4.4772 | 4.4772 | 4.4772 | 0.76877 | 1.258 | 1.7239 | 2.0733 | 2.0733 | 2.0733 | 2.2291 | 3.2155 | 3.8617 | 4.2018 | 4.8821 | 5.5623 | 0.80021 | 2.1737 | 2.7263 | 2.7263 | 2.7263 | 2.7263 | 1.1962 | 1.5183 | 1.5183 | 1.5183 | 1.5183 | 1.5183
2020-09-24 08:00 | Winter | 2.1148 | 3.2518 | 4.9206 | 4.9206 | 4.9206 | 4.9206 | 0.85165 | 1.3936 | 1.9098 | 2.2969 | 2.2969 | 2.2969 | 2.3244 | 3.3529 | 4.0267 | 4.3814 | 5.0907 | 5.8 | 0.85355 | 2.3186 | 2.9081 | 2.9081 | 2.9081 | 2.9081 | 1.3337 | 1.6928 | 1.6928 | 1.6928 | 1.6928 | 1.6928
2020-09-24 09:00 | Winter | 2.191 | 3.369 | 5.0979 | 5.0979 | 5.0979 | 5.0979 | 0.93738 | 1.5339 | 2.102 | 2.5281 | 2.5281 | 2.5281 | 2.4768 | 3.5728 | 4.2908 | 4.6687 | 5.4245 | 6.1803 | 0.86879 | 2.36 | 2.96 | 2.96 | 2.96 | 2.96 | 1.3337 | 1.6928 | 1.6928 | 1.6928 | 1.6928 | 1.6928
2020-09-24 10:00 | Winter | 2.1542 | 3.3124 | 5.0123 | 5.0123 | 5.0123 | 5.0123 | 0.98025 | 1.604 | 2.1981 | 2.6437 | 2.6437 | 2.6437 | 2.4768 | 3.5728 | 4.2908 | 4.6687 | 5.4245 | 6.1803 | 0.82688 | 2.2461 | 2.8172 | 2.8172 | 2.8172 | 2.8172 | 1.4289 | 1.8137 | 1.8137 | 1.8137 | 1.8137 | 1.8137
2020-09-24 11:00 | Winter | 2.1529 | 3.3104 | 5.0093 | 5.0093 | 5.0093 | 5.0093 | 0.98025 | 1.604 | 2.1981 | 2.6437 | 2.6437 | 2.6437 | 2.4006 | 3.4628 | 4.1588 | 4.525 | 5.2576 | 5.9902 | 0.82307 | 2.2358 | 2.8042 | 2.8042 | 2.8042 | 2.8042 | 1.3718 | 1.7412 | 1.7412 | 1.7412 | 1.7412 | 1.7412
2020-09-24 12:00 | Winter | 2.1148 | 3.2518 | 4.9206 | 4.9206 | 4.9206 | 4.9206 | 0.9974 | 1.6321 | 2.2366 | 2.69 | 2.69 | 2.69 | 2.5721 | 3.7102 | 4.4558 | 4.8483 | 5.6331 | 6.418 | 0.78115 | 2.1219 | 2.6614 | 2.6614 | 2.6614 | 2.6614 | 1.3718 | 1.7412 | 1.7412 | 1.7412 | 1.7412 | 1.7412
2020-09-24 13:00 | Winter | 2.191 | 3.369 | 5.0979 | 5.0979 | 5.0979 | 5.0979 | 0.98882 | 1.6181 | 2.2174 | 2.6668 | 2.6668 | 2.6668 | 2.534 | 3.6552 | 4.3898 | 4.7764 | 5.5497 | 6.3229 | 0.78115 | 2.1219 | 2.6614 | 2.6614 | 2.6614 | 2.6614 | 1.3527 | 1.717 | 1.717 | 1.717 | 1.717 | 1.717
2020-09-24 14:00 | Winter | 2.0761 | 3.1922 | 4.8304 | 4.8304 | 4.8304 | 4.8304 | 0.89737 | 1.4684 | 2.0123 | 2.4202 | 2.4202 | 2.4202 | 2.5149 | 3.6277 | 4.3568 | 4.7405 | 5.508 | 6.2754 | 0.80783 | 2.1944 | 2.7523 | 2.7523 | 2.7523 | 2.7523 | 1.2384 | 1.5719 | 1.5719 | 1.5719 | 1.5719 | 1.5719
2020-09-24 15:00 | Winter | 2.0958 | 3.2225 | 4.8763 | 4.8763 | 4.8763 | 4.8763 | 0.89166 | 1.4591 | 1.9995 | 2.4048 | 2.4048 | 2.4048 | 2.534 | 3.6552 | 4.3898 | 4.7764 | 5.5497 | 6.3229 | 0.80783 | 2.1944 | 2.7523 | 2.7523 | 2.7523 | 2.7523 | 1.2384 | 1.5719 | 1.5719 | 1.5719 | 1.5719 | 1.5719
2020-09-24 16:00 | Winter | 2.0577 | 3.1639 | 4.7876 | 4.7876 | 4.7876 | 4.7876 | 0.93167 | 1.5245 | 2.0892 | 2.5127 | 2.5127 | 2.5127 | 2.4959 | 3.6002 | 4.3238 | 4.7046 | 5.4662 | 6.2279 | 0.76591 | 2.0805 | 2.6095 | 2.6095 | 2.6095 | 2.6095 | 1.2003 | 1.5235 | 1.5235 | 1.5235 | 1.5235 | 1.5235
2020-09-24 17:00 | Winter | 1.9629 | 3.0181 | 4.567 | 4.567 | 4.567 | 4.567 | 0.88594 | 1.4497 | 1.9867 | 2.3894 | 2.3894 | 2.3894 | 2.4006 | 3.4628 | 4.1588 | 4.525 | 5.2576 | 5.9902 | 0.76591 | 2.0805 | 2.6095 | 2.6095 | 2.6095 | 2.6095 | 1.1622 | 1.4752 | 1.4752 | 1.4752 | 1.4752 | 1.4752
2020-09-24 18:00 | Winter | 1.5351 | 2.3604 | 3.5717 | 3.5717 | 3.5717 | 3.5717 | 0.70304 | 1.1504 | 1.5765 | 1.8961 | 1.8961 | 1.8961 | 2.4006 | 3.4628 | 4.1588 | 4.525 | 5.2576 | 5.9902 | 0.78877 | 2.1426 | 2.6874 | 2.6874 | 2.6874 | 2.6874 | 0.85961 | 1.0911 | 1.0911 | 1.0911 | 1.0911 | 1.0911
2020-09-24 19:00 | Winter | 1.2384 | 1.9042 | 2.8814 | 2.8814 | 2.8814 | 2.8814 | 0.5287 | 0.86515 | 1.1856 | 1.4259 | 1.4259 | 1.4259 | 2.3244 | 3.3529 | 4.0267 | 4.3814 | 5.0907 | 5.8 | 0.7621 | 2.0702 | 2.5965 | 2.5965 | 2.5965 | 2.5965 | 0.69266 | 0.87917 | 0.87917 | 0.87917 | 0.87917 | 0.87917
2020-09-24 20:00 | Winter | 1.0874 | 1.6719 | 2.53 | 2.53 | 2.53 | 2.53 | 0.56872 | 0.93062 | 1.2753 | 1.5338 | 1.5338 | 1.5338 | 2.2482 | 3.243 | 3.8947 | 4.2377 | 4.9238 | 5.6098 | 0.7621 | 2.0702 | 2.5965 | 2.5965 | 2.5965 | 2.5965 | 0.63786 | 0.80963 | 0.80963 | 0.80963 | 0.80963 | 0.80963
2020-09-24 21:00 | Winter | 1.086 | 1.6698 | 2.5268 | 2.5268 | 2.5268 | 2.5268 | 0.48628 | 0.79573 | 1.0904 | 1.3115 | 1.3115 | 1.3115 | 2.172 | 3.133 | 3.7627 | 4.0941 | 4.7569 | 5.4197 | 0.71256 | 1.9356 | 2.4277 | 2.4277 | 2.4277 | 2.4277 | 0.57158 | 0.72549 | 0.72549 | 0.72549 | 0.72549 | 0.72549
2020-09-24 22:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.50584 | 0.82774 | 1.1343 | 1.3642 | 1.3642 | 1.3642 | 1.9624 | 2.8307 | 3.3996 | 3.699 | 4.2979 | 4.8967 | 0.67827 | 1.8425 | 2.3109 | 2.3109 | 2.3109 | 2.3109 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-09-24 23:00 | Winter | 0.93378 | 1.4358 | 2.1726 | 2.1726 | 2.1726 | 2.1726 | 0.47726 | 0.78098 | 1.0702 | 1.2872 | 1.2872 | 1.2872 | 1.7682 | 2.5506 | 3.0632 | 3.333 | 3.8726 | 4.4121 | 0.64779 | 1.7596 | 2.207 | 2.207 | 2.207 | 2.207 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-09-25 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.46012 | 0.75292 | 1.0318 | 1.2409 | 1.2409 | 1.2409 | 1.7719 | 2.5559 | 3.0696 | 3.3399 | 3.8806 | 4.4213 | 0.58682 | 1.594 | 1.9993 | 1.9993 | 1.9993 | 1.9993 | 0.49537 | 0.62876 | 0.62876 | 0.62876 | 0.62876 | 0.62876
2020-09-25 01:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.43439 | 0.71083 | 0.9741 | 1.1715 | 1.1715 | 1.1715 | 1.5814 | 2.2811 | 2.7395 | 2.9808 | 3.4633 | 3.9459 | 0.60587 | 1.6458 | 2.0642 | 2.0642 | 2.0642 | 2.0642 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-09-25 02:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.46869 | 0.76695 | 1.051 | 1.264 | 1.264 | 1.264 | 1.5814 | 2.2811 | 2.7395 | 2.9808 | 3.4633 | 3.9459 | 0.56395 | 1.5319 | 1.9214 | 1.9214 | 1.9214 | 1.9214 | 0.45726 | 0.58039 | 0.58039 | 0.58039 | 0.58039 | 0.58039
2020-09-25 03:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.43439 | 0.71083 | 0.9741 | 1.1715 | 1.1715 | 1.1715 | 1.5623 | 2.2536 | 2.7065 | 2.9449 | 3.4216 | 3.8984 | 0.58682 | 1.594 | 1.9993 | 1.9993 | 1.9993 | 1.9993 | 0.45726 | 0.58039 | 0.58039 | 0.58039 | 0.58039 | 0.58039
2020-09-25 04:00 | Winter | 1.1633 | 1.7887 | 2.7067 | 2.7067 | 2.7067 | 2.7067 | 0.44868 | 0.73421 | 1.0061 | 1.2101 | 1.2101 | 1.2101 | 1.5814 | 2.2811 | 2.7395 | 2.9808 | 3.4633 | 3.9459 | 0.55633 | 1.5112 | 1.8954 | 1.8954 | 1.8954 | 1.8954 | 0.56377 | 0.71558 | 0.71558 | 0.71558 | 0.71558 | 0.71558
2020-09-25 05:00 | Winter | 1.2194 | 1.875 | 2.8373 | 2.8373 | 2.8373 | 2.8373 | 0.59729 | 0.97739 | 1.3394 | 1.6109 | 1.6109 | 1.6109 | 1.7147 | 2.4735 | 2.9705 | 3.2322 | 3.7554 | 4.2787 | 0.63635 | 1.7286 | 2.1681 | 2.1681 | 2.1681 | 2.1681 | 0.75013 | 0.95212 | 0.95212 | 0.95212 | 0.95212 | 0.95212
2020-09-25 06:00 | Winter | 1.4243 | 2.19 | 3.3139 | 3.3139 | 3.3139 | 3.3139 | 0.70304 | 1.1504 | 1.5765 | 1.8961 | 1.8961 | 1.8961 | 1.9815 | 2.8582 | 3.4326 | 3.735 | 4.3396 | 4.9443 | 0.72781 | 1.977 | 2.4796 | 2.4796 | 2.4796 | 2.4796 | 0.94283 | 1.1967 | 1.1967 | 1.1967 | 1.1967 | 1.1967
2020-09-25 07:00 | Winter | 2.0653 | 3.1756 | 4.8053 | 4.8053 | 4.8053 | 4.8053 | 1.046 | 1.7116 | 2.3455 | 2.821 | 2.821 | 2.821 | 2.3816 | 3.4353 | 4.1258 | 4.4891 | 5.2159 | 5.9426 | 0.84212 | 2.2875 | 2.8691 | 2.8691 | 2.8691 | 2.8691 | 1.2003 | 1.5235 | 1.5235 | 1.5235 | 1.5235 | 1.5235
2020-09-25 08:00 | Winter | 2.3054 | 3.5448 | 5.3639 | 5.3639 | 5.3639 | 5.3639 | 1.0746 | 1.7584 | 2.4096 | 2.8981 | 2.8981 | 2.8981 | 2.5149 | 3.6277 | 4.3568 | 4.7405 | 5.508 | 6.2754 | 0.94119 | 2.5567 | 3.2067 | 3.2067 | 3.2067 | 3.2067 | 1.3789 | 1.7503 | 1.7503 | 1.7503 | 1.7503 | 1.7503
2020-09-25 09:00 | Winter | 2.2673 | 3.4862 | 5.2753 | 5.2753 | 5.2753 | 5.2753 | 1.0517 | 1.721 | 2.3584 | 2.8364 | 2.8364 | 2.8364 | 2.5911 | 3.7377 | 4.4888 | 4.8842 | 5.6749 | 6.4656 | 0.8816 | 2.3948 | 3.0036 | 3.0036 | 3.0036 | 3.0036 | 1.3908 | 1.7654 | 1.7654 | 1.7654 | 1.7654 | 1.7654
2020-09-25 10:00 | Winter | 2.3054 | 3.5448 | 5.3639 | 5.3639 | 5.3639 | 5.3639 | 0.99168 | 1.6228 | 2.2238 | 2.6745 | 2.6745 | 2.6745 | 2.6102 | 3.7651 | 4.5218 | 4.9201 | 5.7166 | 6.5131 | 0.89928 | 2.4428 | 3.0639 | 3.0639 | 3.0639 | 3.0639 | 1.4861 | 1.8863 | 1.8863 | 1.8863 | 1.8863 | 1.8863
2020-09-25 11:00 | Winter | 2.3054 | 3.5448 | 5.3639 | 5.3639 | 5.3639 | 5.3639 | 1.0946 | 1.7911 | 2.4545 | 2.952 | 2.952 | 2.952 | 2.7245 | 3.93 | 4.7199 | 5.1356 | 5.967 | 6.7984 | 0.95263 | 2.5877 | 3.2456 | 3.2456 | 3.2456 | 3.2456 | 1.4861 | 1.8863 | 1.8863 | 1.8863 | 1.8863 | 1.8863
2020-09-25 12:00 | Winter | 2.3244 | 3.5741 | 5.4082 | 5.4082 | 5.4082 | 5.4082 | 1.0603 | 1.735 | 2.3776 | 2.8595 | 2.8595 | 2.8595 | 2.8007 | 4.04 | 4.8519 | 5.2792 | 6.1339 | 6.9885 | 0.94119 | 2.5567 | 3.2067 | 3.2067 | 3.2067 | 3.2067 | 1.4861 | 1.8863 | 1.8863 | 1.8863 | 1.8863 | 1.8863
2020-09-25 13:00 | Winter | 2.3054 | 3.5448 | 5.3639 | 5.3639 | 5.3639 | 5.3639 | 1.0546 | 1.7256 | 2.3648 | 2.8441 | 2.8441 | 2.8441 | 2.8198 | 4.0675 | 4.8849 | 5.3151 | 6.1756 | 7.0361 | 0.91833 | 2.4946 | 3.1288 | 3.1288 | 3.1288 | 3.1288 | 1.467 | 1.8621 | 1.8621 | 1.8621 | 1.8621 | 1.8621
2020-09-25 14:00 | Winter | 2.2291 | 3.4276 | 5.1866 | 5.1866 | 5.1866 | 5.1866 | 1.0479 | 1.7148 | 2.3499 | 2.8262 | 2.8262 | 2.8262 | 2.7436 | 3.9575 | 4.7529 | 5.1715 | 6.0087 | 6.8459 | 0.94882 | 2.5774 | 3.2326 | 3.2326 | 3.2326 | 3.2326 | 1.4289 | 1.8137 | 1.8137 | 1.8137 | 1.8137 | 1.8137
2020-09-25 15:00 | Winter | 2.172 | 3.3397 | 5.0536 | 5.0536 | 5.0536 | 5.0536 | 1.026 | 1.6789 | 2.3007 | 2.767 | 2.767 | 2.767 | 2.8579 | 4.1224 | 4.9509 | 5.387 | 6.259 | 7.1311 | 0.88023 | 2.3911 | 2.9989 | 2.9989 | 2.9989 | 2.9989 | 1.3527 | 1.717 | 1.717 | 1.717 | 1.717 | 1.717
2020-09-25 16:00 | Winter | 2.1148 | 3.2518 | 4.9206 | 4.9206 | 4.9206 | 4.9206 | 1.0688 | 1.749 | 2.3968 | 2.8826 | 2.8826 | 2.8826 | 2.8769 | 4.1499 | 4.9839 | 5.4229 | 6.3008 | 7.1787 | 0.86498 | 2.3496 | 2.947 | 2.947 | 2.947 | 2.947 | 1.2575 | 1.5961 | 1.5961 | 1.5961 | 1.5961 | 1.5961
2020-09-25 17:00 | Winter | 2.0032 | 3.0802 | 4.661 | 4.661 | 4.661 | 4.661 | 1.0088 | 1.6508 | 2.2622 | 2.7208 | 2.7208 | 2.7208 | 2.7436 | 3.9575 | 4.7529 | 5.1715 | 6.0087 | 6.8459 | 0.84212 | 2.2875 | 2.8691 | 2.8691 | 2.8691 | 2.8691 | 1.1813 | 1.4993 | 1.4993 | 1.4993 | 1.4993 | 1.4993
2020-09-25 18:00 | Winter | 1.6386 | 2.5196 | 3.8126 | 3.8126 | 3.8126 | 3.8126 | 0.85736 | 1.403 | 1.9226 | 2.3123 | 2.3123 | 2.3123 | 2.7436 | 3.9575 | 4.7529 | 5.1715 | 6.0087 | 6.8459 | 0.88023 | 2.3911 | 2.9989 | 2.9989 | 2.9989 | 2.9989 | 0.94178 | 1.1954 | 1.1954 | 1.1954 | 1.1954 | 1.1954
2020-09-25 19:00 | Winter | 1.1831 | 1.8192 | 2.7528 | 2.7528 | 2.7528 | 2.7528 | 0.67678 | 1.1075 | 1.5176 | 1.8253 | 1.8253 | 1.8253 | 2.6102 | 3.7651 | 4.5218 | 4.9201 | 5.7166 | 6.5131 | 0.86498 | 2.3496 | 2.947 | 2.947 | 2.947 | 2.947 | 0.78115 | 0.9915 | 0.9915 | 0.9915 | 0.9915 | 0.9915
2020-09-25 20:00 | Winter | 1.086 | 1.6698 | 2.5268 | 2.5268 | 2.5268 | 2.5268 | 0.6373 | 1.0429 | 1.4291 | 1.7188 | 1.7188 | 1.7188 | 2.5911 | 3.7377 | 4.4888 | 4.8842 | 5.6749 | 6.4656 | 0.80783 | 2.1944 | 2.7523 | 2.7523 | 2.7523 | 2.7523 | 0.68589 | 0.87059 | 0.87059 | 0.87059 | 0.87059 | 0.87059
2020-09-25 21:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 0.62873 | 1.0288 | 1.4099 | 1.6957 | 1.6957 | 1.6957 | 2.4624 | 3.552 | 4.2659 | 4.6416 | 5.393 | 6.1444 | 0.7964 | 2.1633 | 2.7133 | 2.7133 | 2.7133 | 2.7133 | 0.64779 | 0.82222 | 0.82222 | 0.82222 | 0.82222 | 0.82222
2020-09-25 22:00 | Winter | 1.0288 | 1.582 | 2.3938 | 2.3938 | 2.3938 | 2.3938 | 0.59444 | 0.97271 | 1.333 | 1.6032 | 1.6032 | 1.6032 | 2.2482 | 3.243 | 3.8947 | 4.2377 | 4.9238 | 5.6098 | 0.76591 | 2.0805 | 2.6095 | 2.6095 | 2.6095 | 2.6095 | 0.60968 | 0.77386 | 0.77386 | 0.77386 | 0.77386 | 0.77386
2020-09-25 23:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.45726 | 0.74824 | 1.0254 | 1.2332 | 1.2332 | 1.2332 | 2.0577 | 2.9681 | 3.5647 | 3.8786 | 4.5065 | 5.1344 | 0.63254 | 1.7182 | 2.1551 | 2.1551 | 2.1551 | 2.1551 | 0.55252 | 0.70131 | 0.70131 | 0.70131 | 0.70131 | 0.70131
2020-09-26 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.45726 | 0.74824 | 1.0254 | 1.2332 | 1.2332 | 1.2332 | 1.8862 | 2.7208 | 3.2676 | 3.5554 | 4.131 | 4.7066 | 0.60206 | 1.6354 | 2.0512 | 2.0512 | 2.0512 | 2.0512 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-09-26 01:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.45726 | 0.74824 | 1.0254 | 1.2332 | 1.2332 | 1.2332 | 1.7909 | 2.5834 | 3.1026 | 3.3758 | 3.9223 | 4.4688 | 0.56395 | 1.5319 | 1.9214 | 1.9214 | 1.9214 | 1.9214 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-09-26 02:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.44011 | 0.72018 | 0.98691 | 1.187 | 1.187 | 1.187 | 1.7338 | 2.5009 | 3.0036 | 3.2681 | 3.7972 | 4.3262 | 0.62111 | 1.6872 | 2.1161 | 2.1161 | 2.1161 | 2.1161 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-09-26 03:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.48765 | 0.79797 | 1.0935 | 1.3152 | 1.3152 | 1.3152 | 1.7338 | 2.5009 | 3.0036 | 3.2681 | 3.7972 | 4.3262 | 0.57157 | 1.5526 | 1.9474 | 1.9474 | 1.9474 | 1.9474 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-09-26 04:00 | Winter | 1.0288 | 1.582 | 2.3938 | 2.3938 | 2.3938 | 2.3938 | 0.49441 | 0.80903 | 1.1087 | 1.3334 | 1.3334 | 1.3334 | 1.7578 | 2.5356 | 3.0451 | 3.3133 | 3.8497 | 4.3861 | 0.6173 | 1.6768 | 2.1032 | 2.1032 | 2.1032 | 2.1032 | 0.49537 | 0.62876 | 0.62876 | 0.62876 | 0.62876 | 0.62876
2020-09-26 05:00 | Winter | 1.0288 | 1.582 | 2.3938 | 2.3938 | 2.3938 | 2.3938 | 0.48012 | 0.78565 | 1.0766 | 1.2949 | 1.2949 | 1.2949 | 1.829 | 2.6383 | 3.1686 | 3.4477 | 4.0058 | 4.5639 | 0.58682 | 1.594 | 1.9993 | 1.9993 | 1.9993 | 1.9993 | 0.49537 | 0.62876 | 0.62876 | 0.62876 | 0.62876 | 0.62876
2020-09-26 06:00 | Winter | 1.0288 | 1.582 | 2.3938 | 2.3938 | 2.3938 | 2.3938 | 0.5087 | 0.83242 | 1.1407 | 1.3719 | 1.3719 | 1.3719 | 2.0571 | 2.9673 | 3.5636 | 3.8775 | 4.5052 | 5.1329 | 0.6173 | 1.6768 | 2.1032 | 2.1032 | 2.1032 | 2.1032 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-09-26 07:00 | Winter | 1.1241 | 1.7284 | 2.6155 | 2.6155 | 2.6155 | 2.6155 | 0.63159 | 1.0335 | 1.4163 | 1.7034 | 1.7034 | 1.7034 | 2.0958 | 3.0231 | 3.6307 | 3.9504 | 4.59 | 5.2295 | 0.68208 | 1.8528 | 2.3239 | 2.3239 | 2.3239 | 2.3239 | 0.55252 | 0.70131 | 0.70131 | 0.70131 | 0.70131 | 0.70131
2020-09-26 08:00 | Winter | 1.086 | 1.6698 | 2.5268 | 2.5268 | 2.5268 | 2.5268 | 0.63159 | 1.0335 | 1.4163 | 1.7034 | 1.7034 | 1.7034 | 2.2673 | 3.2705 | 3.9277 | 4.2736 | 4.9655 | 5.6574 | 0.71256 | 1.9356 | 2.4277 | 2.4277 | 2.4277 | 2.4277 | 0.55252 | 0.70131 | 0.70131 | 0.70131 | 0.70131 | 0.70131
2020-09-26 09:00 | Winter | 1.086 | 1.6698 | 2.5268 | 2.5268 | 2.5268 | 2.5268 | 0.68589 | 1.1224 | 1.5381 | 1.8498 | 1.8498 | 1.8498 | 2.3625 | 3.4079 | 4.0927 | 4.4532 | 5.1741 | 5.8951 | 0.71637 | 1.946 | 2.4407 | 2.4407 | 2.4407 | 2.4407 | 0.60968 | 0.77386 | 0.77386 | 0.77386 | 0.77386 | 0.77386
2020-09-26 10:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 0.64588 | 1.0569 | 1.4483 | 1.7419 | 1.7419 | 1.7419 | 2.2291 | 3.2155 | 3.8617 | 4.2018 | 4.8821 | 5.5623 | 0.73543 | 1.9977 | 2.5056 | 2.5056 | 2.5056 | 2.5056 | 0.62873 | 0.79804 | 0.79804 | 0.79804 | 0.79804 | 0.79804
2020-09-26 11:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 0.68303 | 1.1177 | 1.5316 | 1.8421 | 1.8421 | 1.8421 | 2.2482 | 3.243 | 3.8947 | 4.2377 | 4.9238 | 5.6098 | 0.71637 | 1.946 | 2.4407 | 2.4407 | 2.4407 | 2.4407 | 0.62873 | 0.79804 | 0.79804 | 0.79804 | 0.79804 | 0.79804
2020-09-26 12:00 | Winter | 1.0288 | 1.582 | 2.3938 | 2.3938 | 2.3938 | 2.3938 | 0.64016 | 1.0475 | 1.4355 | 1.7265 | 1.7265 | 1.7265 | 2.3244 | 3.3529 | 4.0267 | 4.3814 | 5.0907 | 5.8 | 0.67827 | 1.8425 | 2.3109 | 2.3109 | 2.3109 | 2.3109 | 0.62873 | 0.79804 | 0.79804 | 0.79804 | 0.79804 | 0.79804
2020-09-26 13:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.63159 | 1.0335 | 1.4163 | 1.7034 | 1.7034 | 1.7034 | 2.3816 | 3.4353 | 4.1258 | 4.4891 | 5.2159 | 5.9426 | 0.67446 | 1.8321 | 2.2979 | 2.2979 | 2.2979 | 2.2979 | 0.60968 | 0.77386 | 0.77386 | 0.77386 | 0.77386 | 0.77386
2020-09-26 14:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 0.59444 | 0.97271 | 1.333 | 1.6032 | 1.6032 | 1.6032 | 2.3244 | 3.3529 | 4.0267 | 4.3814 | 5.0907 | 5.8 | 0.74686 | 2.0288 | 2.5446 | 2.5446 | 2.5446 | 2.5446 | 0.62873 | 0.79804 | 0.79804 | 0.79804 | 0.79804 | 0.79804
2020-09-26 15:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.63159 | 1.0335 | 1.4163 | 1.7034 | 1.7034 | 1.7034 | 2.2673 | 3.2705 | 3.9277 | 4.2736 | 4.9655 | 5.6574 | 0.72018 | 1.9563 | 2.4537 | 2.4537 | 2.4537 | 2.4537 | 0.60968 | 0.77386 | 0.77386 | 0.77386 | 0.77386 | 0.77386
2020-09-26 16:00 | Winter | 1.086 | 1.6698 | 2.5268 | 2.5268 | 2.5268 | 2.5268 | 0.64874 | 1.0616 | 1.4547 | 1.7496 | 1.7496 | 1.7496 | 2.2673 | 3.2705 | 3.9277 | 4.2736 | 4.9655 | 5.6574 | 0.78496 | 2.1323 | 2.6744 | 2.6744 | 2.6744 | 2.6744 | 0.59063 | 0.74967 | 0.74967 | 0.74967 | 0.74967 | 0.74967
2020-09-26 17:00 | Winter | 1.0288 | 1.582 | 2.3938 | 2.3938 | 2.3938 | 2.3938 | 0.66017 | 1.0803 | 1.4804 | 1.7805 | 1.7805 | 1.7805 | 2.3816 | 3.4353 | 4.1258 | 4.4891 | 5.2159 | 5.9426 | 0.78496 | 2.1323 | 2.6744 | 2.6744 | 2.6744 | 2.6744 | 0.57158 | 0.72549 | 0.72549 | 0.72549 | 0.72549 | 0.72549
2020-09-26 18:00 | Winter | 1.0288 | 1.582 | 2.3938 | 2.3938 | 2.3938 | 2.3938 | 0.68589 | 1.1224 | 1.5381 | 1.8498 | 1.8498 | 1.8498 | 2.534 | 3.6552 | 4.3898 | 4.7764 | 5.5497 | 6.3229 | 0.9069 | 2.4635 | 3.0898 | 3.0898 | 3.0898 | 3.0898 | 0.62873 | 0.79804 | 0.79804 | 0.79804 | 0.79804 | 0.79804
2020-09-26 19:00 | Winter | 0.99852 | 1.5353 | 2.3233 | 2.3233 | 2.3233 | 2.3233 | 0.61158 | 1.0008 | 1.3714 | 1.6494 | 1.6494 | 1.6494 | 2.5149 | 3.6277 | 4.3568 | 4.7405 | 5.508 | 6.2754 | 0.92214 | 2.5049 | 3.1418 | 3.1418 | 3.1418 | 3.1418 | 0.62873 | 0.79804 | 0.79804 | 0.79804 | 0.79804 | 0.79804
2020-09-26 20:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 0.62016 | 1.0148 | 1.3907 | 1.6725 | 1.6725 | 1.6725 | 2.4392 | 3.5184 | 4.2255 | 4.5977 | 5.342 | 6.0863 | 0.89928 | 2.4428 | 3.0639 | 3.0639 | 3.0639 | 3.0639 | 0.60968 | 0.77386 | 0.77386 | 0.77386 | 0.77386 | 0.77386
2020-09-26 21:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.55443 | 0.90724 | 1.2433 | 1.4953 | 1.4953 | 1.4953 | 2.4578 | 3.5453 | 4.2578 | 4.6328 | 5.3828 | 6.1328 | 0.89928 | 2.4428 | 3.0639 | 3.0639 | 3.0639 | 3.0639 | 0.60968 | 0.77386 | 0.77386 | 0.77386 | 0.77386 | 0.77386
2020-09-26 22:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.51442 | 0.84177 | 1.1535 | 1.3874 | 1.3874 | 1.3874 | 2.2294 | 3.2159 | 3.8622 | 4.2023 | 4.8826 | 5.563 | 0.78877 | 2.1426 | 2.6874 | 2.6874 | 2.6874 | 2.6874 | 0.59063 | 0.74967 | 0.74967 | 0.74967 | 0.74967 | 0.74967
2020-09-26 23:00 | Winter | 0.94157 | 1.4478 | 2.1908 | 2.1908 | 2.1908 | 2.1908 | 0.41153 | 0.67342 | 0.92283 | 1.1099 | 1.1099 | 1.1099 | 1.9815 | 2.8582 | 3.4326 | 3.735 | 4.3396 | 4.9443 | 0.72781 | 1.977 | 2.4796 | 2.4796 | 2.4796 | 2.4796 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-09-27 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.44583 | 0.72953 | 0.99973 | 1.2024 | 1.2024 | 1.2024 | 1.9243 | 2.7758 | 3.3336 | 3.6272 | 4.2144 | 4.8016 | 0.62111 | 1.6872 | 2.1161 | 2.1161 | 2.1161 | 2.1161 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-09-27 01:00 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.40296 | 0.65939 | 0.9036 | 1.0868 | 1.0868 | 1.0868 | 1.8133 | 2.6157 | 3.1413 | 3.418 | 3.9714 | 4.5247 | 0.61349 | 1.6665 | 2.0902 | 2.0902 | 2.0902 | 2.0902 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-09-27 02:00 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.40867 | 0.66874 | 0.91642 | 1.1022 | 1.1022 | 1.1022 | 1.6957 | 2.446 | 2.9375 | 3.1963 | 3.7137 | 4.2311 | 0.55484 | 1.5072 | 1.8904 | 1.8904 | 1.8904 | 1.8904 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-09-27 03:00 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.40867 | 0.66874 | 0.91642 | 1.1022 | 1.1022 | 1.1022 | 1.7528 | 2.5284 | 3.0366 | 3.304 | 3.8389 | 4.3738 | 0.60587 | 1.6458 | 2.0642 | 2.0642 | 2.0642 | 2.0642 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-09-27 04:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.43381 | 0.70986 | 0.97277 | 1.17 | 1.17 | 1.17 | 1.7 | 2.4522 | 2.945 | 3.2044 | 3.7231 | 4.2419 | 0.58682 | 1.594 | 1.9993 | 1.9993 | 1.9993 | 1.9993 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-09-27 05:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.49727 | 0.81371 | 1.1151 | 1.3411 | 1.3411 | 1.3411 | 1.7909 | 2.5834 | 3.1026 | 3.3758 | 3.9223 | 4.4688 | 0.58682 | 1.594 | 1.9993 | 1.9993 | 1.9993 | 1.9993 | 0.45738 | 0.58054 | 0.58054 | 0.58054 | 0.58054 | 0.58054
2020-09-27 06:00 | Winter | 0.93358 | 1.4355 | 2.1722 | 2.1722 | 2.1722 | 2.1722 | 0.48298 | 0.79033 | 1.083 | 1.3026 | 1.3026 | 1.3026 | 1.9022 | 2.7438 | 3.2953 | 3.5855 | 4.166 | 4.7464 | 0.60206 | 1.6354 | 2.0512 | 2.0512 | 2.0512 | 2.0512 | 0.49299 | 0.62574 | 0.62574 | 0.62574 | 0.62574 | 0.62574
2020-09-27 07:00 | Winter | 0.93358 | 1.4355 | 2.1722 | 2.1722 | 2.1722 | 2.1722 | 0.56586 | 0.92595 | 1.2689 | 1.5261 | 1.5261 | 1.5261 | 1.9441 | 2.8043 | 3.3679 | 3.6646 | 4.2578 | 4.8511 | 0.66684 | 1.8114 | 2.2719 | 2.2719 | 2.2719 | 2.2719 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-09-27 08:00 | Winter | 0.89547 | 1.3769 | 2.0835 | 2.0835 | 2.0835 | 2.0835 | 0.56586 | 0.92595 | 1.2689 | 1.5261 | 1.5261 | 1.5261 | 2.191 | 3.1605 | 3.7957 | 4.13 | 4.7986 | 5.4672 | 0.71637 | 1.946 | 2.4407 | 2.4407 | 2.4407 | 2.4407 | 0.55252 | 0.70131 | 0.70131 | 0.70131 | 0.70131 | 0.70131
2020-09-27 09:00 | Winter | 0.85737 | 1.3183 | 1.9948 | 1.9948 | 1.9948 | 1.9948 | 0.52772 | 0.86355 | 1.1834 | 1.4233 | 1.4233 | 1.4233 | 2.2101 | 3.188 | 3.8287 | 4.1659 | 4.8403 | 5.5147 | 0.70113 | 1.9046 | 2.3888 | 2.3888 | 2.3888 | 2.3888 | 0.59063 | 0.74967 | 0.74967 | 0.74967 | 0.74967 | 0.74967
2020-09-27 10:00 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.52585 | 0.86048 | 1.1792 | 1.4182 | 1.4182 | 1.4182 | 2.2291 | 3.2155 | 3.8617 | 4.2018 | 4.8821 | 5.5623 | 0.73162 | 1.9874 | 2.4926 | 2.4926 | 2.4926 | 2.4926 | 0.57158 | 0.72549 | 0.72549 | 0.72549 | 0.72549 | 0.72549
2020-09-27 11:00 | Winter | 0.93358 | 1.4355 | 2.1722 | 2.1722 | 2.1722 | 2.1722 | 0.56014 | 0.9166 | 1.2561 | 1.5107 | 1.5107 | 1.5107 | 2.2673 | 3.2705 | 3.9277 | 4.2736 | 4.9655 | 5.6574 | 0.72018 | 1.9563 | 2.4537 | 2.4537 | 2.4537 | 2.4537 | 0.55252 | 0.70131 | 0.70131 | 0.70131 | 0.70131 | 0.70131
2020-09-27 12:00 | Winter | 0.93358 | 1.4355 | 2.1722 | 2.1722 | 2.1722 | 2.1722 | 0.66303 | 1.085 | 1.4868 | 1.7882 | 1.7882 | 1.7882 | 2.2473 | 3.2417 | 3.8932 | 4.2361 | 4.9218 | 5.6076 | 0.66684 | 1.8114 | 2.2719 | 2.2719 | 2.2719 | 2.2719 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-09-27 13:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.4544 | 0.74356 | 1.019 | 1.2255 | 1.2255 | 1.2255 | 2.2673 | 3.2705 | 3.9277 | 4.2736 | 4.9655 | 5.6574 | 0.65541 | 1.7803 | 2.233 | 2.233 | 2.233 | 2.233 | 0.55252 | 0.70131 | 0.70131 | 0.70131 | 0.70131 | 0.70131
2020-09-27 14:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 0.45154 | 0.73889 | 1.0125 | 1.2178 | 1.2178 | 1.2178 | 2.191 | 3.1605 | 3.7957 | 4.13 | 4.7986 | 5.4672 | 0.65541 | 1.7803 | 2.233 | 2.233 | 2.233 | 2.233 | 0.59063 | 0.74967 | 0.74967 | 0.74967 | 0.74967 | 0.74967
2020-09-27 15:00 | Winter | 1.0288 | 1.582 | 2.3938 | 2.3938 | 2.3938 | 2.3938 | 0.44583 | 0.72953 | 0.99973 | 1.2024 | 1.2024 | 1.2024 | 2.191 | 3.1605 | 3.7957 | 4.13 | 4.7986 | 5.4672 | 0.724 | 1.9667 | 2.4667 | 2.4667 | 2.4667 | 2.4667 | 0.57158 | 0.72549 | 0.72549 | 0.72549 | 0.72549 | 0.72549
2020-09-27 16:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.47334 | 0.77456 | 1.0614 | 1.2766 | 1.2766 | 1.2766 | 2.2291 | 3.2155 | 3.8617 | 4.2018 | 4.8821 | 5.5623 | 0.68589 | 1.8632 | 2.3368 | 2.3368 | 2.3368 | 2.3368 | 0.55252 | 0.70131 | 0.70131 | 0.70131 | 0.70131 | 0.70131
2020-09-27 17:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.5087 | 0.83242 | 1.1407 | 1.3719 | 1.3719 | 1.3719 | 2.177 | 3.1403 | 3.7714 | 4.1036 | 4.7679 | 5.4322 | 0.70494 | 1.9149 | 2.4018 | 2.4018 | 2.4018 | 2.4018 | 0.55252 | 0.70131 | 0.70131 | 0.70131 | 0.70131 | 0.70131
2020-09-27 18:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.56014 | 0.9166 | 1.2561 | 1.5107 | 1.5107 | 1.5107 | 2.3054 | 3.3254 | 3.9937 | 4.3455 | 5.049 | 5.7525 | 0.80402 | 2.184 | 2.7393 | 2.7393 | 2.7393 | 2.7393 | 0.57158 | 0.72549 | 0.72549 | 0.72549 | 0.72549 | 0.72549
2020-09-27 19:00 | Winter | 0.99828 | 1.535 | 2.3227 | 2.3227 | 2.3227 | 2.3227 | 0.57443 | 0.93998 | 1.2881 | 1.5492 | 1.5492 | 1.5492 | 2.3054 | 3.3254 | 3.9937 | 4.3455 | 5.049 | 5.7525 | 0.81545 | 2.2151 | 2.7782 | 2.7782 | 2.7782 | 2.7782 | 0.57158 | 0.72549 | 0.72549 | 0.72549 | 0.72549 | 0.72549
2020-09-27 20:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 0.59444 | 0.97271 | 1.333 | 1.6032 | 1.6032 | 1.6032 | 2.2863 | 3.2979 | 3.9607 | 4.3096 | 5.0072 | 5.7049 | 0.77734 | 2.1116 | 2.6484 | 2.6484 | 2.6484 | 2.6484 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-09-27 21:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.48012 | 0.78565 | 1.0766 | 1.2949 | 1.2949 | 1.2949 | 2.191 | 3.1605 | 3.7957 | 4.13 | 4.7986 | 5.4672 | 0.81545 | 2.2151 | 2.7782 | 2.7782 | 2.7782 | 2.7782 | 0.55252 | 0.70131 | 0.70131 | 0.70131 | 0.70131 | 0.70131
2020-09-27 22:00 | Winter | 0.97464 | 1.4986 | 2.2677 | 2.2677 | 2.2677 | 2.2677 | 0.49155 | 0.80436 | 1.1023 | 1.3257 | 1.3257 | 1.3257 | 2.0958 | 3.0231 | 3.6307 | 3.9504 | 4.59 | 5.2295 | 0.77734 | 2.1116 | 2.6484 | 2.6484 | 2.6484 | 2.6484 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-09-27 23:00 | Winter | 0.98953 | 1.5215 | 2.3024 | 2.3024 | 2.3024 | 2.3024 | 0.44011 | 0.72018 | 0.98691 | 1.187 | 1.187 | 1.187 | 1.8862 | 2.7208 | 3.2676 | 3.5554 | 4.131 | 4.7066 | 0.71256 | 1.9356 | 2.4277 | 2.4277 | 2.4277 | 2.4277 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-09-28 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.44583 | 0.72953 | 0.99973 | 1.2024 | 1.2024 | 1.2024 | 1.81 | 2.6109 | 3.1356 | 3.4117 | 3.9641 | 4.5164 | 0.6516 | 1.77 | 2.22 | 2.22 | 2.22 | 2.22 | 0.49537 | 0.62876 | 0.62876 | 0.62876 | 0.62876 | 0.62876
2020-09-28 01:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.37724 | 0.6173 | 0.84593 | 1.0174 | 1.0174 | 1.0174 | 1.6957 | 2.446 | 2.9375 | 3.1963 | 3.7137 | 4.2311 | 0.58301 | 1.5837 | 1.9863 | 1.9863 | 1.9863 | 1.9863 | 0.49537 | 0.62876 | 0.62876 | 0.62876 | 0.62876 | 0.62876
2020-09-28 02:00 | Winter | 1.2003 | 1.8456 | 2.7928 | 2.7928 | 2.7928 | 2.7928 | 0.49441 | 0.80903 | 1.1087 | 1.3334 | 1.3334 | 1.3334 | 1.6766 | 2.4185 | 2.9045 | 3.1603 | 3.672 | 4.1836 | 0.56395 | 1.5319 | 1.9214 | 1.9214 | 1.9214 | 1.9214 | 0.49464 | 0.62784 | 0.62784 | 0.62784 | 0.62784 | 0.62784
2020-09-28 03:00 | Winter | 1.1807 | 1.8154 | 2.7471 | 2.7471 | 2.7471 | 2.7471 | 0.48298 | 0.79033 | 1.083 | 1.3026 | 1.3026 | 1.3026 | 1.686 | 2.4321 | 2.9208 | 3.1781 | 3.6926 | 4.2071 | 0.57157 | 1.5526 | 1.9474 | 1.9474 | 1.9474 | 1.9474 | 0.49537 | 0.62876 | 0.62876 | 0.62876 | 0.62876 | 0.62876
2020-09-28 04:00 | Winter | 1.2575 | 1.9335 | 2.9258 | 2.9258 | 2.9258 | 2.9258 | 0.54299 | 0.88854 | 1.2176 | 1.4644 | 1.4644 | 1.4644 | 1.7719 | 2.5559 | 3.0696 | 3.3399 | 3.8806 | 4.4213 | 0.5792 | 1.5733 | 1.9733 | 1.9733 | 1.9733 | 1.9733 | 0.49537 | 0.62876 | 0.62876 | 0.62876 | 0.62876 | 0.62876
2020-09-28 05:00 | Winter | 1.373 | 2.1112 | 3.1947 | 3.1947 | 3.1947 | 3.1947 | 0.90023 | 1.4731 | 2.0187 | 2.4279 | 2.4279 | 2.4279 | 1.9419 | 2.8011 | 3.3641 | 3.6604 | 4.2529 | 4.8455 | 0.73162 | 1.9874 | 2.4926 | 2.4926 | 2.4926 | 2.4926 | 0.75177 | 0.9542 | 0.9542 | 0.9542 | 0.9542 | 0.9542
2020-09-28 06:00 | Winter | 1.7843 | 2.7435 | 4.1515 | 4.1515 | 4.1515 | 4.1515 | 0.93915 | 1.5368 | 2.106 | 2.5328 | 2.5328 | 2.5328 | 2.172 | 3.133 | 3.7627 | 4.0941 | 4.7569 | 5.4197 | 0.72781 | 1.977 | 2.4796 | 2.4796 | 2.4796 | 2.4796 | 0.99073 | 1.2575 | 1.2575 | 1.2575 | 1.2575 | 1.2575
2020-09-28 07:00 | Winter | 2.1219 | 3.2627 | 4.9371 | 4.9371 | 4.9371 | 4.9371 | 1.0974 | 1.7958 | 2.4609 | 2.9597 | 2.9597 | 2.9597 | 2.4578 | 3.5453 | 4.2578 | 4.6328 | 5.3828 | 6.1328 | 0.91833 | 2.4946 | 3.1288 | 3.1288 | 3.1288 | 3.1288 | 1.3717 | 1.741 | 1.741 | 1.741 | 1.741 | 1.741
2020-09-28 08:00 | Winter | 2.3244 | 3.5741 | 5.4082 | 5.4082 | 5.4082 | 5.4082 | 1.1974 | 1.9595 | 2.6852 | 3.2295 | 3.2295 | 3.2295 | 2.5911 | 3.7377 | 4.4888 | 4.8842 | 5.6749 | 6.4656 | 0.97549 | 2.6498 | 3.3235 | 3.3235 | 3.3235 | 3.3235 | 1.467 | 1.8621 | 1.8621 | 1.8621 | 1.8621 | 1.8621
2020-09-28 09:00 | Winter | 2.2863 | 3.5155 | 5.3196 | 5.3196 | 5.3196 | 5.3196 | 1.1717 | 1.9174 | 2.6275 | 3.1601 | 3.1601 | 3.1601 | 2.6102 | 3.7651 | 4.5218 | 4.9201 | 5.7166 | 6.5131 | 0.95263 | 2.5877 | 3.2456 | 3.2456 | 3.2456 | 3.2456 | 1.5166 | 1.925 | 1.925 | 1.925 | 1.925 | 1.925
2020-09-28 10:00 | Winter | 2.2673 | 3.4862 | 5.2753 | 5.2753 | 5.2753 | 5.2753 | 0.99454 | 1.6274 | 2.2302 | 2.6822 | 2.6822 | 2.6822 | 2.6102 | 3.7651 | 4.5218 | 4.9201 | 5.7166 | 6.5131 | 0.89547 | 2.4325 | 3.0509 | 3.0509 | 3.0509 | 3.0509 | 1.5623 | 1.983 | 1.983 | 1.983 | 1.983 | 1.983
2020-09-28 11:00 | Winter | 2.4006 | 3.6912 | 5.5856 | 5.5856 | 5.5856 | 5.5856 | 0.88022 | 1.4404 | 1.9738 | 2.3739 | 2.3739 | 2.3739 | 2.553 | 3.6827 | 4.4228 | 4.8123 | 5.5914 | 6.3705 | 0.88023 | 2.3911 | 2.9989 | 2.9989 | 2.9989 | 2.9989 | 1.5623 | 1.983 | 1.983 | 1.983 | 1.983 | 1.983
2020-09-28 12:00 | Winter | 2.3578 | 3.6254 | 5.486 | 5.486 | 5.486 | 5.486 | 0.81449 | 1.3328 | 1.8264 | 2.1967 | 2.1967 | 2.1967 | 2.6102 | 3.7651 | 4.5218 | 4.9201 | 5.7166 | 6.5131 | 0.87261 | 2.3704 | 2.973 | 2.973 | 2.973 | 2.973 | 1.5814 | 2.0072 | 2.0072 | 2.0072 | 2.0072 | 2.0072
2020-09-28 13:00 | Winter | 2.1339 | 3.2811 | 4.9649 | 4.9649 | 4.9649 | 4.9649 | 0.83736 | 1.3702 | 1.8777 | 2.2583 | 2.2583 | 2.2583 | 2.5911 | 3.7377 | 4.4888 | 4.8842 | 5.6749 | 6.4656 | 0.84212 | 2.2875 | 2.8691 | 2.8691 | 2.8691 | 2.8691 | 1.4861 | 1.8863 | 1.8863 | 1.8863 | 1.8863 | 1.8863
2020-09-28 14:00 | Winter | 2.3244 | 3.5741 | 5.4082 | 5.4082 | 5.4082 | 5.4082 | 0.83164 | 1.3609 | 1.8649 | 2.2429 | 2.2429 | 2.2429 | 2.4959 | 3.6002 | 4.3238 | 4.7046 | 5.4662 | 6.2279 | 0.86498 | 2.3496 | 2.947 | 2.947 | 2.947 | 2.947 | 1.3527 | 1.717 | 1.717 | 1.717 | 1.717 | 1.717
2020-09-28 15:00 | Winter | 2.191 | 3.369 | 5.0979 | 5.0979 | 5.0979 | 5.0979 | 0.86879 | 1.4217 | 1.9482 | 2.3431 | 2.3431 | 2.3431 | 2.4578 | 3.5453 | 4.2578 | 4.6328 | 5.3828 | 6.1328 | 0.83069 | 2.2565 | 2.8302 | 2.8302 | 2.8302 | 2.8302 | 1.2765 | 1.6203 | 1.6203 | 1.6203 | 1.6203 | 1.6203
2020-09-28 16:00 | Winter | 2.191 | 3.369 | 5.0979 | 5.0979 | 5.0979 | 5.0979 | 0.82592 | 1.3515 | 1.8521 | 2.2275 | 2.2275 | 2.2275 | 2.4387 | 3.5178 | 4.2248 | 4.5969 | 5.3411 | 6.0852 | 0.84974 | 2.3082 | 2.8951 | 2.8951 | 2.8951 | 2.8951 | 1.2194 | 1.5477 | 1.5477 | 1.5477 | 1.5477 | 1.5477
2020-09-28 17:00 | Winter | 2.1148 | 3.2518 | 4.9206 | 4.9206 | 4.9206 | 4.9206 | 0.86879 | 1.4217 | 1.9482 | 2.3431 | 2.3431 | 2.3431 | 2.3816 | 3.4353 | 4.1258 | 4.4891 | 5.2159 | 5.9426 | 0.80783 | 2.1944 | 2.7523 | 2.7523 | 2.7523 | 2.7523 | 1.1432 | 1.451 | 1.451 | 1.451 | 1.451 | 1.451
2020-09-28 18:00 | Winter | 1.7006 | 2.6149 | 3.9569 | 3.9569 | 3.9569 | 3.9569 | 0.74019 | 1.2112 | 1.6598 | 1.9963 | 1.9963 | 1.9963 | 2.4578 | 3.5453 | 4.2578 | 4.6328 | 5.3828 | 6.1328 | 0.85736 | 2.3289 | 2.9211 | 2.9211 | 2.9211 | 2.9211 | 0.83568 | 1.0607 | 1.0607 | 1.0607 | 1.0607 | 1.0607
2020-09-28 19:00 | Winter | 1.1813 | 1.8163 | 2.7485 | 2.7485 | 2.7485 | 2.7485 | 0.60301 | 0.98674 | 1.3522 | 1.6263 | 1.6263 | 1.6263 | 2.3054 | 3.3254 | 3.9937 | 4.3455 | 5.049 | 5.7525 | 0.78496 | 2.1323 | 2.6744 | 2.6744 | 2.6744 | 2.6744 | 0.724 | 0.91895 | 0.91895 | 0.91895 | 0.91895 | 0.91895
2020-09-28 20:00 | Winter | 1.0872 | 1.6717 | 2.5295 | 2.5295 | 2.5295 | 2.5295 | 0.49727 | 0.81371 | 1.1151 | 1.3411 | 1.3411 | 1.3411 | 2.2101 | 3.188 | 3.8287 | 4.1659 | 4.8403 | 5.5147 | 0.75448 | 2.0495 | 2.5705 | 2.5705 | 2.5705 | 2.5705 | 0.64779 | 0.82222 | 0.82222 | 0.82222 | 0.82222 | 0.82222
2020-09-28 21:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.5087 | 0.83242 | 1.1407 | 1.3719 | 1.3719 | 1.3719 | 2.1148 | 3.0506 | 3.6637 | 3.9863 | 4.6317 | 5.277 | 0.7621 | 2.0702 | 2.5965 | 2.5965 | 2.5965 | 2.5965 | 0.57158 | 0.72549 | 0.72549 | 0.72549 | 0.72549 | 0.72549
2020-09-28 22:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.48869 | 0.79968 | 1.0959 | 1.318 | 1.318 | 1.318 | 1.9624 | 2.8307 | 3.3996 | 3.699 | 4.2979 | 4.8967 | 0.72018 | 1.9563 | 2.4537 | 2.4537 | 2.4537 | 2.4537 | 0.53347 | 0.67712 | 0.67712 | 0.67712 | 0.67712 | 0.67712
2020-09-28 23:00 | Winter | 0.99073 | 1.5234 | 2.3052 | 2.3052 | 2.3052 | 2.3052 | 0.42868 | 0.70147 | 0.96128 | 1.1561 | 1.1561 | 1.1561 | 1.8481 | 2.6658 | 3.2016 | 3.4836 | 4.0475 | 4.6115 | 0.67827 | 1.8425 | 2.3109 | 2.3109 | 2.3109 | 2.3109 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-09-29 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.37724 | 0.6173 | 0.84593 | 1.0174 | 1.0174 | 1.0174 | 1.7147 | 2.4735 | 2.9705 | 3.2322 | 3.7554 | 4.2787 | 0.57539 | 1.563 | 1.9603 | 1.9603 | 1.9603 | 1.9603 | 0.45919 | 0.58283 | 0.58283 | 0.58283 | 0.58283 | 0.58283
2020-09-29 01:00 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.46583 | 0.76227 | 1.0446 | 1.2563 | 1.2563 | 1.2563 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.57157 | 1.5526 | 1.9474 | 1.9474 | 1.9474 | 1.9474 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-09-29 02:00 | Winter | 1.1241 | 1.7284 | 2.6155 | 2.6155 | 2.6155 | 2.6155 | 0.45154 | 0.73889 | 1.0125 | 1.2178 | 1.2178 | 1.2178 | 1.6004 | 2.3086 | 2.7725 | 3.0167 | 3.5051 | 3.9934 | 0.57157 | 1.5526 | 1.9474 | 1.9474 | 1.9474 | 1.9474 | 0.49537 | 0.62876 | 0.62876 | 0.62876 | 0.62876 | 0.62876
2020-09-29 03:00 | Winter | 1.1622 | 1.787 | 2.7041 | 2.7041 | 2.7041 | 2.7041 | 0.44011 | 0.72018 | 0.98691 | 1.187 | 1.187 | 1.187 | 1.6195 | 2.336 | 2.8055 | 3.0526 | 3.5468 | 4.041 | 0.59825 | 1.6251 | 2.0382 | 2.0382 | 2.0382 | 2.0382 | 0.49537 | 0.62876 | 0.62876 | 0.62876 | 0.62876 | 0.62876
2020-09-29 04:00 | Winter | 1.1813 | 1.8163 | 2.7485 | 2.7485 | 2.7485 | 2.7485 | 0.46012 | 0.75292 | 1.0318 | 1.2409 | 1.2409 | 1.2409 | 1.6226 | 2.3406 | 2.811 | 3.0585 | 3.5537 | 4.0488 | 0.57157 | 1.5526 | 1.9474 | 1.9474 | 1.9474 | 1.9474 | 0.49537 | 0.62876 | 0.62876 | 0.62876 | 0.62876 | 0.62876
2020-09-29 05:00 | Winter | 1.448 | 2.2265 | 3.3691 | 3.3691 | 3.3691 | 3.3691 | 0.49694 | 0.81318 | 1.1144 | 1.3402 | 1.3402 | 1.3402 | 1.7909 | 2.5834 | 3.1026 | 3.3758 | 3.9223 | 4.4688 | 0.67446 | 1.8321 | 2.2979 | 2.2979 | 2.2979 | 2.2979 | 0.72366 | 0.91852 | 0.91852 | 0.91852 | 0.91852 | 0.91852
2020-09-29 06:00 | Winter | 1.6904 | 2.5992 | 3.9331 | 3.9331 | 3.9331 | 3.9331 | 0.72018 | 1.1785 | 1.615 | 1.9423 | 1.9423 | 1.9423 | 2.0005 | 2.8857 | 3.4656 | 3.7709 | 4.3813 | 4.9918 | 0.76972 | 2.0909 | 2.6225 | 2.6225 | 2.6225 | 2.6225 | 0.96489 | 1.2247 | 1.2247 | 1.2247 | 1.2247 | 1.2247
2020-09-29 07:00 | Winter | 1.9434 | 2.9881 | 4.5216 | 4.5216 | 4.5216 | 4.5216 | 0.9431 | 1.5433 | 2.1148 | 2.5435 | 2.5435 | 2.5435 | 2.3435 | 3.3804 | 4.0597 | 4.4173 | 5.1324 | 5.8475 | 0.88404 | 2.4014 | 3.0119 | 3.0119 | 3.0119 | 3.0119 | 1.3337 | 1.6928 | 1.6928 | 1.6928 | 1.6928 | 1.6928
2020-09-29 08:00 | Winter | 2.191 | 3.369 | 5.0979 | 5.0979 | 5.0979 | 5.0979 | 1.0403 | 1.7023 | 2.3327 | 2.8056 | 2.8056 | 2.8056 | 2.4768 | 3.5728 | 4.2908 | 4.6687 | 5.4245 | 6.1803 | 0.99454 | 2.7016 | 3.3884 | 3.3884 | 3.3884 | 3.3884 | 1.467 | 1.8621 | 1.8621 | 1.8621 | 1.8621 | 1.8621
2020-09-29 09:00 | Winter | 2.2863 | 3.5155 | 5.3196 | 5.3196 | 5.3196 | 5.3196 | 0.98025 | 1.604 | 2.1981 | 2.6437 | 2.6437 | 2.6437 | 2.553 | 3.6827 | 4.4228 | 4.8123 | 5.5914 | 6.3705 | 0.9793 | 2.6602 | 3.3365 | 3.3365 | 3.3365 | 3.3365 | 1.5242 | 1.9346 | 1.9346 | 1.9346 | 1.9346 | 1.9346
2020-09-29 10:00 | Winter | 2.2291 | 3.4276 | 5.1866 | 5.1866 | 5.1866 | 5.1866 | 0.78877 | 1.2907 | 1.7688 | 2.1273 | 2.1273 | 2.1273 | 2.5911 | 3.7377 | 4.4888 | 4.8842 | 5.6749 | 6.4656 | 0.83831 | 2.2772 | 2.8561 | 2.8561 | 2.8561 | 2.8561 | 1.448 | 1.8379 | 1.8379 | 1.8379 | 1.8379 | 1.8379
2020-09-29 11:00 | Winter | 2.4387 | 3.7498 | 5.6742 | 5.6742 | 5.6742 | 5.6742 | 0.91738 | 1.5012 | 2.0571 | 2.4741 | 2.4741 | 2.4741 | 2.6483 | 3.8201 | 4.5878 | 4.9919 | 5.8 | 6.6082 | 0.74305 | 2.0184 | 2.5316 | 2.5316 | 2.5316 | 2.5316 | 1.448 | 1.8379 | 1.8379 | 1.8379 | 1.8379 | 1.8379
2020-09-29 12:00 | Winter | 2.4335 | 3.7418 | 5.6621 | 5.6621 | 5.6621 | 5.6621 | 0.80878 | 1.3235 | 1.8136 | 2.1812 | 2.1812 | 2.1812 | 2.6674 | 3.8476 | 4.6208 | 5.0278 | 5.8418 | 6.6557 | 0.80402 | 2.184 | 2.7393 | 2.7393 | 2.7393 | 2.7393 | 1.3718 | 1.7412 | 1.7412 | 1.7412 | 1.7412 | 1.7412
2020-09-29 13:00 | Winter | 2.2673 | 3.4862 | 5.2753 | 5.2753 | 5.2753 | 5.2753 | 0.84879 | 1.3889 | 1.9033 | 2.2892 | 2.2892 | 2.2892 | 2.6293 | 3.7926 | 4.5548 | 4.956 | 5.7583 | 6.5606 | 0.78115 | 2.1219 | 2.6614 | 2.6614 | 2.6614 | 2.6614 | 1.3544 | 1.7191 | 1.7191 | 1.7191 | 1.7191 | 1.7191
2020-09-29 14:00 | Winter | 2.3244 | 3.5741 | 5.4082 | 5.4082 | 5.4082 | 5.4082 | 0.87451 | 1.431 | 1.961 | 2.3585 | 2.3585 | 2.3585 | 2.5721 | 3.7102 | 4.4558 | 4.8483 | 5.6331 | 6.418 | 0.76591 | 2.0805 | 2.6095 | 2.6095 | 2.6095 | 2.6095 | 1.3527 | 1.717 | 1.717 | 1.717 | 1.717 | 1.717
2020-09-29 15:00 | Winter | 2.3054 | 3.5448 | 5.3639 | 5.3639 | 5.3639 | 5.3639 | 0.90309 | 1.4778 | 2.0251 | 2.4356 | 2.4356 | 2.4356 | 2.4978 | 3.603 | 4.3271 | 4.7082 | 5.4704 | 6.2326 | 0.76591 | 2.0805 | 2.6095 | 2.6095 | 2.6095 | 2.6095 | 1.2956 | 1.6444 | 1.6444 | 1.6444 | 1.6444 | 1.6444
2020-09-29 16:00 | Winter | 2.3054 | 3.5448 | 5.3639 | 5.3639 | 5.3639 | 5.3639 | 0.90309 | 1.4778 | 2.0251 | 2.4356 | 2.4356 | 2.4356 | 2.553 | 3.6827 | 4.4228 | 4.8123 | 5.5914 | 6.3705 | 0.79258 | 2.153 | 2.7003 | 2.7003 | 2.7003 | 2.7003 | 1.1813 | 1.4993 | 1.4993 | 1.4993 | 1.4993 | 1.4993
2020-09-29 17:00 | Winter | 2.0958 | 3.2225 | 4.8763 | 4.8763 | 4.8763 | 4.8763 | 0.87165 | 1.4263 | 1.9546 | 2.3508 | 2.3508 | 2.3508 | 2.38 | 3.4331 | 4.1231 | 4.4862 | 5.2125 | 5.9388 | 0.80402 | 2.184 | 2.7393 | 2.7393 | 2.7393 | 2.7393 | 1.1241 | 1.4268 | 1.4268 | 1.4268 | 1.4268 | 1.4268
2020-09-29 18:00 | Winter | 1.63 | 2.5063 | 3.7925 | 3.7925 | 3.7925 | 3.7925 | 0.68875 | 1.127 | 1.5445 | 1.8575 | 1.8575 | 1.8575 | 2.3816 | 3.4353 | 4.1258 | 4.4891 | 5.2159 | 5.9426 | 0.81926 | 2.2254 | 2.7912 | 2.7912 | 2.7912 | 2.7912 | 0.82844 | 1.0515 | 1.0515 | 1.0515 | 1.0515 | 1.0515
2020-09-29 19:00 | Winter | 1.1622 | 1.787 | 2.7041 | 2.7041 | 2.7041 | 2.7041 | 0.52013 | 0.85112 | 1.1664 | 1.4028 | 1.4028 | 1.4028 | 2.3335 | 3.366 | 4.0424 | 4.3985 | 5.1105 | 5.8226 | 0.86498 | 2.3496 | 2.947 | 2.947 | 2.947 | 2.947 | 0.68629 | 0.8711 | 0.8711 | 0.8711 | 0.8711 | 0.8711
2020-09-29 20:00 | Winter | 1.105 | 1.6991 | 2.5711 | 2.5711 | 2.5711 | 2.5711 | 0.6173 | 1.0101 | 1.3842 | 1.6648 | 1.6648 | 1.6648 | 2.1455 | 3.0948 | 3.7167 | 4.0441 | 4.6988 | 5.3535 | 0.73162 | 1.9874 | 2.4926 | 2.4926 | 2.4926 | 2.4926 | 0.64779 | 0.82222 | 0.82222 | 0.82222 | 0.82222 | 0.82222
2020-09-29 21:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 0.43964 | 0.71941 | 0.98586 | 1.1857 | 1.1857 | 1.1857 | 2.0394 | 2.9418 | 3.533 | 3.8442 | 4.4665 | 5.0889 | 0.67446 | 1.8321 | 2.2979 | 2.2979 | 2.2979 | 2.2979 | 0.57158 | 0.72549 | 0.72549 | 0.72549 | 0.72549 | 0.72549
2020-09-29 22:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.47726 | 0.78098 | 1.0702 | 1.2872 | 1.2872 | 1.2872 | 1.8799 | 2.7117 | 3.2567 | 3.5435 | 4.1172 | 4.6909 | 0.66684 | 1.8114 | 2.2719 | 2.2719 | 2.2719 | 2.2719 | 0.51451 | 0.65305 | 0.65305 | 0.65305 | 0.65305 | 0.65305
2020-09-29 23:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.34321 | 0.56162 | 0.76963 | 0.92563 | 0.92563 | 0.92563 | 1.7338 | 2.5009 | 3.0036 | 3.2681 | 3.7972 | 4.3262 | 0.57539 | 1.563 | 1.9603 | 1.9603 | 1.9603 | 1.9603 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-09-30 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.4001 | 0.65471 | 0.89719 | 1.0791 | 1.0791 | 1.0791 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.52204 | 1.4181 | 1.7786 | 1.7786 | 1.7786 | 1.7786 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-09-30 01:00 | Winter | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.42868 | 0.70147 | 0.96128 | 1.1561 | 1.1561 | 1.1561 | 1.6004 | 2.3086 | 2.7725 | 3.0167 | 3.5051 | 3.9934 | 0.52204 | 1.4181 | 1.7786 | 1.7786 | 1.7786 | 1.7786 | 0.45726 | 0.58039 | 0.58039 | 0.58039 | 0.58039 | 0.58039
2020-09-30 02:00 | Winter | 0.95263 | 1.4648 | 2.2165 | 2.2165 | 2.2165 | 2.2165 | 0.36295 | 0.59391 | 0.81388 | 0.97886 | 0.97886 | 0.97886 | 1.581 | 2.2806 | 2.7389 | 2.9801 | 3.4626 | 3.945 | 0.52585 | 1.4284 | 1.7916 | 1.7916 | 1.7916 | 1.7916 | 0.45726 | 0.58039 | 0.58039 | 0.58039 | 0.58039 | 0.58039
2020-09-30 03:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 0.42296 | 0.69212 | 0.94846 | 1.1407 | 1.1407 | 1.1407 | 1.5814 | 2.2811 | 2.7395 | 2.9808 | 3.4633 | 3.9459 | 0.49155 | 1.3353 | 1.6747 | 1.6747 | 1.6747 | 1.6747 | 0.49537 | 0.62876 | 0.62876 | 0.62876 | 0.62876 | 0.62876
2020-09-30 04:00 | Winter | 1.1432 | 1.7577 | 2.6598 | 2.6598 | 2.6598 | 2.6598 | 0.45726 | 0.74824 | 1.0254 | 1.2332 | 1.2332 | 1.2332 | 1.5814 | 2.2811 | 2.7395 | 2.9808 | 3.4633 | 3.9459 | 0.5068 | 1.3767 | 1.7267 | 1.7267 | 1.7267 | 1.7267 | 0.51442 | 0.65294 | 0.65294 | 0.65294 | 0.65294 | 0.65294
2020-09-30 05:00 | Winter | 1.2798 | 1.9678 | 2.9776 | 2.9776 | 2.9776 | 2.9776 | 0.43537 | 0.71242 | 0.97629 | 1.1742 | 1.1742 | 1.1742 | 1.7379 | 2.5068 | 3.0106 | 3.2758 | 3.8061 | 4.3364 | 0.58682 | 1.594 | 1.9993 | 1.9993 | 1.9993 | 1.9993 | 0.64765 | 0.82205 | 0.82205 | 0.82205 | 0.82205 | 0.82205
2020-09-30 06:00 | Winter | 1.4099 | 2.1679 | 3.2804 | 3.2804 | 3.2804 | 3.2804 | 0.69732 | 1.1411 | 1.5637 | 1.8807 | 1.8807 | 1.8807 | 1.9873 | 2.8666 | 3.4428 | 3.746 | 4.3524 | 4.9589 | 0.6516 | 1.77 | 2.22 | 2.22 | 2.22 | 2.22 | 0.90531 | 1.1491 | 1.1491 | 1.1491 | 1.1491 | 1.1491
2020-09-30 07:00 | Winter | 2.0682 | 3.1802 | 4.8122 | 4.8122 | 4.8122 | 4.8122 | 1.0145 | 1.6602 | 2.275 | 2.7362 | 2.7362 | 2.7362 | 2.2482 | 3.243 | 3.8947 | 4.2377 | 4.9238 | 5.6098 | 0.86879 | 2.36 | 2.96 | 2.96 | 2.96 | 2.96 | 1.1469 | 1.4557 | 1.4557 | 1.4557 | 1.4557 | 1.4557
2020-09-30 08:00 | Winter | 2.172 | 3.3397 | 5.0536 | 5.0536 | 5.0536 | 5.0536 | 0.92595 | 1.5152 | 2.0764 | 2.4973 | 2.4973 | 2.4973 | 2.4959 | 3.6002 | 4.3238 | 4.7046 | 5.4662 | 6.2279 | 0.91452 | 2.4842 | 3.1158 | 3.1158 | 3.1158 | 3.1158 | 1.3337 | 1.6928 | 1.6928 | 1.6928 | 1.6928 | 1.6928
2020-09-30 09:00 | Winter | 2.172 | 3.3397 | 5.0536 | 5.0536 | 5.0536 | 5.0536 | 1.0231 | 1.6742 | 2.2943 | 2.7593 | 2.7593 | 2.7593 | 2.534 | 3.6552 | 4.3898 | 4.7764 | 5.5497 | 6.3229 | 0.8345 | 2.2668 | 2.8432 | 2.8432 | 2.8432 | 2.8432 | 1.3337 | 1.6928 | 1.6928 | 1.6928 | 1.6928 | 1.6928
2020-09-30 10:00 | Winter | 2.3435 | 3.6034 | 5.4526 | 5.4526 | 5.4526 | 5.4526 | 0.95739 | 1.5666 | 2.1469 | 2.582 | 2.582 | 2.582 | 2.534 | 3.6552 | 4.3898 | 4.7764 | 5.5497 | 6.3229 | 0.81164 | 2.2047 | 2.7653 | 2.7653 | 2.7653 | 2.7653 | 1.3718 | 1.7412 | 1.7412 | 1.7412 | 1.7412 | 1.7412
2020-09-30 11:00 | Winter | 2.3054 | 3.5448 | 5.3639 | 5.3639 | 5.3639 | 5.3639 | 0.9389 | 1.5364 | 2.1054 | 2.5322 | 2.5322 | 2.5322 | 2.6102 | 3.7651 | 4.5218 | 4.9201 | 5.7166 | 6.5131 | 0.78877 | 2.1426 | 2.6874 | 2.6874 | 2.6874 | 2.6874 | 1.3527 | 1.717 | 1.717 | 1.717 | 1.717 | 1.717
2020-09-30 12:00 | Winter | 2.2101 | 3.3983 | 5.1423 | 5.1423 | 5.1423 | 5.1423 | 0.95453 | 1.562 | 2.1405 | 2.5743 | 2.5743 | 2.5743 | 2.5911 | 3.7377 | 4.4888 | 4.8842 | 5.6749 | 6.4656 | 0.81926 | 2.2254 | 2.7912 | 2.7912 | 2.7912 | 2.7912 | 1.448 | 1.8379 | 1.8379 | 1.8379 | 1.8379 | 1.8379
2020-09-30 13:00 | Winter | 2.2291 | 3.4276 | 5.1866 | 5.1866 | 5.1866 | 5.1866 | 0.95739 | 1.5666 | 2.1469 | 2.582 | 2.582 | 2.582 | 2.5911 | 3.7377 | 4.4888 | 4.8842 | 5.6749 | 6.4656 | 0.83069 | 2.2565 | 2.8302 | 2.8302 | 2.8302 | 2.8302 | 1.3527 | 1.717 | 1.717 | 1.717 | 1.717 | 1.717
2020-09-30 14:00 | Winter | 2.2482 | 3.4569 | 5.2309 | 5.2309 | 5.2309 | 5.2309 | 0.94024 | 1.5386 | 2.1084 | 2.5358 | 2.5358 | 2.5358 | 2.5721 | 3.7102 | 4.4558 | 4.8483 | 5.6331 | 6.418 | 0.79258 | 2.153 | 2.7003 | 2.7003 | 2.7003 | 2.7003 | 1.2956 | 1.6444 | 1.6444 | 1.6444 | 1.6444 | 1.6444
2020-09-30 15:00 | Winter | 2.1529 | 3.3104 | 5.0093 | 5.0093 | 5.0093 | 5.0093 | 0.91166 | 1.4918 | 2.0443 | 2.4587 | 2.4587 | 2.4587 | 2.6674 | 3.8476 | 4.6208 | 5.0278 | 5.8418 | 6.6557 | 0.79258 | 2.153 | 2.7003 | 2.7003 | 2.7003 | 2.7003 | 1.2956 | 1.6444 | 1.6444 | 1.6444 | 1.6444 | 1.6444
2020-09-30 16:00 | Winter | 2.172 | 3.3397 | 5.0536 | 5.0536 | 5.0536 | 5.0536 | 0.91738 | 1.5012 | 2.0571 | 2.4741 | 2.4741 | 2.4741 | 2.5766 | 3.7167 | 4.4636 | 4.8567 | 5.643 | 6.4293 | 0.80402 | 2.184 | 2.7393 | 2.7393 | 2.7393 | 2.7393 | 1.2194 | 1.5477 | 1.5477 | 1.5477 | 1.5477 | 1.5477
2020-09-30 17:00 | Winter | 2.0577 | 3.1639 | 4.7876 | 4.7876 | 4.7876 | 4.7876 | 0.89166 | 1.4591 | 1.9995 | 2.4048 | 2.4048 | 2.4048 | 2.6293 | 3.7926 | 4.5548 | 4.956 | 5.7583 | 6.5606 | 0.77734 | 2.1116 | 2.6484 | 2.6484 | 2.6484 | 2.6484 | 1.1813 | 1.4993 | 1.4993 | 1.4993 | 1.4993 | 1.4993
2020-09-30 18:00 | Winter | 1.715 | 2.6371 | 3.9904 | 3.9904 | 3.9904 | 3.9904 | 0.80306 | 1.3141 | 1.8008 | 2.1658 | 2.1658 | 2.1658 | 2.6054 | 3.7582 | 4.5135 | 4.911 | 5.7061 | 6.5011 | 0.80783 | 2.1944 | 2.7523 | 2.7523 | 2.7523 | 2.7523 | 0.89036 | 1.1301 | 1.1301 | 1.1301 | 1.1301 | 1.1301
2020-09-30 19:00 | Winter | 1.2003 | 1.8456 | 2.7928 | 2.7928 | 2.7928 | 2.7928 | 0.57157 | 0.9353 | 1.2817 | 1.5415 | 1.5415 | 1.5415 | 2.4768 | 3.5728 | 4.2908 | 4.6687 | 5.4245 | 6.1803 | 0.81926 | 2.2254 | 2.7912 | 2.7912 | 2.7912 | 2.7912 | 0.70494 | 0.89477 | 0.89477 | 0.89477 | 0.89477 | 0.89477
2020-09-30 20:00 | Winter | 1.086 | 1.6698 | 2.5268 | 2.5268 | 2.5268 | 2.5268 | 0.59158 | 0.96804 | 1.3266 | 1.5955 | 1.5955 | 1.5955 | 2.2676 | 3.271 | 3.9284 | 4.2743 | 4.9663 | 5.6583 | 0.75067 | 2.0391 | 2.5575 | 2.5575 | 2.5575 | 2.5575 | 0.60968 | 0.77386 | 0.77386 | 0.77386 | 0.77386 | 0.77386
2020-09-30 21:00 | Winter | 1.0479 | 1.6113 | 2.4381 | 2.4381 | 2.4381 | 2.4381 | 0.6173 | 1.0101 | 1.3842 | 1.6648 | 1.6648 | 1.6648 | 2.1148 | 3.0506 | 3.6637 | 3.9863 | 4.6317 | 5.277 | 0.69351 | 1.8839 | 2.3628 | 2.3628 | 2.3628 | 2.3628 | 0.59063 | 0.74967 | 0.74967 | 0.74967 | 0.74967 | 0.74967
2020-09-30 22:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.52169 | 0.85368 | 1.1699 | 1.407 | 1.407 | 1.407 | 1.9434 | 2.8032 | 3.3666 | 3.6631 | 4.2562 | 4.8492 | 0.66303 | 1.8011 | 2.2589 | 2.2589 | 2.2589 | 2.2589 | 0.55252 | 0.70131 | 0.70131 | 0.70131 | 0.70131 | 0.70131
2020-09-30 23:00 | Winter | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.57157 | 0.9353 | 1.2817 | 1.5415 | 1.5415 | 1.5415 | 1.8672 | 2.6933 | 3.2346 | 3.5195 | 4.0892 | 4.659 | 0.62492 | 1.6975 | 2.1291 | 2.1291 | 2.1291 | 2.1291 | 0.47631 | 0.60458 | 0.60458 | 0.60458 | 0.60458 | 0.60458
2020-10-01 | Summer | 0.95637 | 1.3687 | 1.9751 | 1.9751 | 1.9751 | 1.9751 | 0.49727 | 0.81371 | 1.1151 | 1.3411 | 1.3411 | 1.3411 | 1.6767 | 2.1638 | 2.4829 | 2.6508 | 2.9867 | 3.3226 | 0.56776 | 1.1206 | 1.3447 | 1.3447 | 1.3447 | 1.3447 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-10-01 01:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.42011 | 0.68744 | 0.94205 | 1.133 | 1.133 | 1.133 | 1.6385 | 2.1145 | 2.4263 | 2.5904 | 2.9187 | 3.2469 | 0.52204 | 1.0303 | 1.2364 | 1.2364 | 1.2364 | 1.2364 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-10-01 02:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.42011 | 0.68744 | 0.94205 | 1.133 | 1.133 | 1.133 | 1.6195 | 2.0899 | 2.3981 | 2.5603 | 2.8847 | 3.2092 | 0.52204 | 1.0303 | 1.2364 | 1.2364 | 1.2364 | 1.2364 | 0.4386 | 0.51021 | 0.51021 | 0.51021 | 0.51021 | 0.51021
2020-10-01 03:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.43154 | 0.70615 | 0.96769 | 1.1638 | 1.1638 | 1.1638 | 1.5623 | 2.0161 | 2.3135 | 2.4699 | 2.7829 | 3.0959 | 0.51061 | 1.0078 | 1.2093 | 1.2093 | 1.2093 | 1.2093 | 0.41921 | 0.48766 | 0.48766 | 0.48766 | 0.48766 | 0.48766
2020-10-01 04:00 | Summer | 1.1236 | 1.6081 | 2.3205 | 2.3205 | 2.3205 | 2.3205 | 0.46869 | 0.76695 | 1.051 | 1.264 | 1.264 | 1.264 | 1.642 | 2.119 | 2.4315 | 2.5959 | 2.9249 | 3.2538 | 0.54871 | 1.083 | 1.2996 | 1.2996 | 1.2996 | 1.2996 | 0.53347 | 0.62057 | 0.62057 | 0.62057 | 0.62057 | 0.62057
2020-10-01 05:00 | Summer | 1.2684 | 1.8153 | 2.6195 | 2.6195 | 2.6195 | 2.6195 | 0.5087 | 0.83242 | 1.1407 | 1.3719 | 1.3719 | 1.3719 | 1.7526 | 2.2616 | 2.5952 | 2.7707 | 3.1218 | 3.4729 | 0.57559 | 1.136 | 1.3632 | 1.3632 | 1.3632 | 1.3632 | 0.68589 | 0.79787 | 0.79787 | 0.79787 | 0.79787 | 0.79787
2020-10-01 06:00 | Summer | 1.3777 | 1.9718 | 2.8453 | 2.8453 | 2.8453 | 2.8453 | 0.6916 | 1.1317 | 1.5509 | 1.8652 | 1.8652 | 1.8652 | 1.9434 | 2.5079 | 2.8777 | 3.0724 | 3.4617 | 3.851 | 0.64397 | 1.271 | 1.5252 | 1.5252 | 1.5252 | 1.5252 | 0.8839 | 1.0282 | 1.0282 | 1.0282 | 1.0282 | 1.0282
2020-10-01 07:00 | Summer | 1.8722 | 2.6795 | 3.8666 | 3.8666 | 3.8666 | 3.8666 | 0.84879 | 1.3889 | 1.9033 | 2.2892 | 2.2892 | 2.2892 | 2.3244 | 2.9996 | 3.442 | 3.6748 | 4.1404 | 4.6061 | 0.81926 | 1.617 | 1.9403 | 1.9403 | 1.9403 | 1.9403 | 1.086 | 1.2633 | 1.2633 | 1.2633 | 1.2633 | 1.2633
2020-10-01 08:00 | Summer | 2.1339 | 3.0539 | 4.4069 | 4.4069 | 4.4069 | 4.4069 | 0.87451 | 1.431 | 1.961 | 2.3585 | 2.3585 | 2.3585 | 2.4768 | 3.1963 | 3.6677 | 3.9158 | 4.4119 | 4.9081 | 0.88404 | 1.7448 | 2.0938 | 2.0938 | 2.0938 | 2.0938 | 1.2575 | 1.4628 | 1.4628 | 1.4628 | 1.4628 | 1.4628
2020-10-01 09:00 | Summer | 2.172 | 3.1085 | 4.4856 | 4.4856 | 4.4856 | 4.4856 | 0.90309 | 1.4778 | 2.0251 | 2.4356 | 2.4356 | 2.4356 | 2.5721 | 3.3192 | 3.8087 | 4.0664 | 4.5816 | 5.0969 | 0.97549 | 1.9253 | 2.3104 | 2.3104 | 2.3104 | 2.3104 | 1.2575 | 1.4628 | 1.4628 | 1.4628 | 1.4628 | 1.4628
2020-10-01 10:00 | Summer | 2.1339 | 3.0539 | 4.4069 | 4.4069 | 4.4069 | 4.4069 | 0.92881 | 1.5199 | 2.0828 | 2.505 | 2.505 | 2.505 | 2.5911 | 3.3438 | 3.8369 | 4.0965 | 4.6156 | 5.1347 | 0.80402 | 1.5869 | 1.9042 | 1.9042 | 1.9042 | 1.9042 | 1.2956 | 1.5071 | 1.5071 | 1.5071 | 1.5071 | 1.5071
2020-10-01 11:00 | Summer | 2.1148 | 3.0267 | 4.3676 | 4.3676 | 4.3676 | 4.3676 | 0.92023 | 1.5058 | 2.0636 | 2.4818 | 2.4818 | 2.4818 | 2.6293 | 3.393 | 3.8934 | 4.1567 | 4.6835 | 5.2102 | 0.76972 | 1.5192 | 1.823 | 1.823 | 1.823 | 1.823 | 1.2956 | 1.5071 | 1.5071 | 1.5071 | 1.5071 | 1.5071
2020-10-01 12:00 | Summer | 2.4006 | 3.4357 | 4.9578 | 4.9578 | 4.9578 | 4.9578 | 0.9088 | 1.4871 | 2.0379 | 2.451 | 2.451 | 2.451 | 2.6483 | 3.4176 | 3.9216 | 4.1869 | 4.7174 | 5.2479 | 0.76591 | 1.5117 | 1.814 | 1.814 | 1.814 | 1.814 | 1.3337 | 1.5514 | 1.5514 | 1.5514 | 1.5514 | 1.5514
2020-10-01 13:00 | Summer | 2.2673 | 3.2448 | 4.6824 | 4.6824 | 4.6824 | 4.6824 | 0.80306 | 1.3141 | 1.8008 | 2.1658 | 2.1658 | 2.1658 | 2.7626 | 3.5651 | 4.0909 | 4.3676 | 4.921 | 5.4745 | 0.75448 | 1.4891 | 1.7869 | 1.7869 | 1.7869 | 1.7869 | 1.3146 | 1.5293 | 1.5293 | 1.5293 | 1.5293 | 1.5293
2020-10-01 14:00 | Summer | 2.2673 | 3.2448 | 4.6824 | 4.6824 | 4.6824 | 4.6824 | 0.92881 | 1.5199 | 2.0828 | 2.505 | 2.505 | 2.505 | 2.7436 | 3.5405 | 4.0627 | 4.3375 | 4.8871 | 5.4367 | 0.84593 | 1.6696 | 2.0035 | 2.0035 | 2.0035 | 2.0035 | 1.2003 | 1.3963 | 1.3963 | 1.3963 | 1.3963 | 1.3963
2020-10-01 15:00 | Summer | 2.3625 | 3.3811 | 4.8791 | 4.8791 | 4.8791 | 4.8791 | 0.86879 | 1.4217 | 1.9482 | 2.3431 | 2.3431 | 2.3431 | 2.5721 | 3.3192 | 3.8087 | 4.0664 | 4.5816 | 5.0969 | 0.83831 | 1.6546 | 1.9855 | 1.9855 | 1.9855 | 1.9855 | 1.1813 | 1.3741 | 1.3741 | 1.3741 | 1.3741 | 1.3741
2020-10-01 16:00 | Summer | 2.2291 | 3.1903 | 4.6037 | 4.6037 | 4.6037 | 4.6037 | 0.9088 | 1.4871 | 2.0379 | 2.451 | 2.451 | 2.451 | 2.5149 | 3.2455 | 3.7241 | 3.976 | 4.4798 | 4.9836 | 0.72781 | 1.4365 | 1.7238 | 1.7238 | 1.7238 | 1.7238 | 1.1622 | 1.352 | 1.352 | 1.352 | 1.352 | 1.352
2020-10-01 17:00 | Summer | 2.0767 | 2.9721 | 4.2889 | 4.2889 | 4.2889 | 4.2889 | 0.89451 | 1.4638 | 2.0059 | 2.4125 | 2.4125 | 2.4125 | 2.4387 | 3.1471 | 3.6112 | 3.8555 | 4.3441 | 4.8326 | 0.67065 | 1.3236 | 1.5884 | 1.5884 | 1.5884 | 1.5884 | 1.1241 | 1.3076 | 1.3076 | 1.3076 | 1.3076 | 1.3076
2020-10-01 18:00 | Summer | 1.6533 | 2.3662 | 3.4145 | 3.4145 | 3.4145 | 3.4145 | 0.69514 | 1.1375 | 1.5588 | 1.8748 | 1.8748 | 1.8748 | 2.4197 | 3.1225 | 3.583 | 3.8254 | 4.3101 | 4.7949 | 0.78877 | 1.5568 | 1.8681 | 1.8681 | 1.8681 | 1.8681 | 0.85292 | 0.99217 | 0.99217 | 0.99217 | 0.99217 | 0.99217
2020-10-01 19:00 | Summer | 1.1813 | 1.6906 | 2.4396 | 2.4396 | 2.4396 | 2.4396 | 0.55728 | 0.91192 | 1.2497 | 1.503 | 1.503 | 1.503 | 2.3625 | 3.0488 | 3.4984 | 3.735 | 4.2083 | 4.6816 | 0.73924 | 1.459 | 1.7508 | 1.7508 | 1.7508 | 1.7508 | 0.63455 | 0.73815 | 0.73815 | 0.73815 | 0.73815 | 0.73815
2020-10-01 20:00 | Summer | 1.105 | 1.5815 | 2.2822 | 2.2822 | 2.2822 | 2.2822 | 0.56014 | 0.9166 | 1.2561 | 1.5107 | 1.5107 | 1.5107 | 2.2673 | 2.9258 | 3.3573 | 3.5844 | 4.0386 | 4.4928 | 0.71637 | 1.4139 | 1.6967 | 1.6967 | 1.6967 | 1.6967 | 0.60968 | 0.70922 | 0.70922 | 0.70922 | 0.70922 | 0.70922
2020-10-01 21:00 | Summer | 1.0288 | 1.4724 | 2.1248 | 2.1248 | 2.1248 | 2.1248 | 0.53156 | 0.86983 | 1.192 | 1.4336 | 1.4336 | 1.4336 | 2.1328 | 2.7524 | 3.1583 | 3.3719 | 3.7992 | 4.2265 | 0.71256 | 1.4064 | 1.6877 | 1.6877 | 1.6877 | 1.6877 | 0.53347 | 0.62057 | 0.62057 | 0.62057 | 0.62057 | 0.62057
2020-10-01 22:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.55443 | 0.90724 | 1.2433 | 1.4953 | 1.4953 | 1.4953 | 2.0386 | 2.6308 | 3.0188 | 3.223 | 3.6314 | 4.0398 | 0.65922 | 1.3011 | 1.5613 | 1.5613 | 1.5613 | 1.5613 | 0.47634 | 0.55411 | 0.55411 | 0.55411 | 0.55411 | 0.55411
2020-10-01 23:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.49155 | 0.80436 | 1.1023 | 1.3257 | 1.3257 | 1.3257 | 1.852 | 2.39 | 2.7425 | 2.928 | 3.299 | 3.67 | 0.61919 | 1.2221 | 1.4665 | 1.4665 | 1.4665 | 1.4665 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-10-02 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.35437 | 0.57988 | 0.79466 | 0.95574 | 0.95574 | 0.95574 | 1.7147 | 2.2128 | 2.5392 | 2.7109 | 3.0544 | 3.3979 | 0.54871 | 1.083 | 1.2996 | 1.2996 | 1.2996 | 1.2996 | 0.46928 | 0.5459 | 0.5459 | 0.5459 | 0.5459 | 0.5459
2020-10-02 01:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.3401 | 0.55653 | 0.76265 | 0.91725 | 0.91725 | 0.91725 | 1.6766 | 2.1636 | 2.4827 | 2.6507 | 2.9865 | 3.3224 | 0.52585 | 1.0379 | 1.2454 | 1.2454 | 1.2454 | 1.2454 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-10-02 02:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.45726 | 0.74824 | 1.0254 | 1.2332 | 1.2332 | 1.2332 | 1.6576 | 2.1391 | 2.4545 | 2.6205 | 2.9526 | 3.2847 | 0.51442 | 1.0153 | 1.2184 | 1.2184 | 1.2184 | 1.2184 | 0.43821 | 0.50975 | 0.50975 | 0.50975 | 0.50975 | 0.50975
2020-10-02 03:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.39438 | 0.64536 | 0.88438 | 1.0636 | 1.0636 | 1.0636 | 1.6385 | 2.1145 | 2.4263 | 2.5904 | 2.9187 | 3.2469 | 0.54871 | 1.083 | 1.2996 | 1.2996 | 1.2996 | 1.2996 | 0.46885 | 0.54539 | 0.54539 | 0.54539 | 0.54539 | 0.54539
2020-10-02 04:00 | Summer | 1.1241 | 1.6088 | 2.3215 | 2.3215 | 2.3215 | 2.3215 | 0.46583 | 0.76227 | 1.0446 | 1.2563 | 1.2563 | 1.2563 | 1.7147 | 2.2128 | 2.5392 | 2.7109 | 3.0544 | 3.3979 | 0.58682 | 1.1582 | 1.3898 | 1.3898 | 1.3898 | 1.3898 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-10-02 05:00 | Summer | 1.2703 | 1.818 | 2.6234 | 2.6234 | 2.6234 | 2.6234 | 0.54014 | 0.88386 | 1.2112 | 1.4567 | 1.4567 | 1.4567 | 1.81 | 2.3358 | 2.6802 | 2.8615 | 3.2241 | 3.5867 | 0.58301 | 1.1507 | 1.3808 | 1.3808 | 1.3808 | 1.3808 | 0.74115 | 0.86216 | 0.86216 | 0.86216 | 0.86216 | 0.86216
2020-10-02 06:00 | Summer | 1.4818 | 2.1207 | 3.0602 | 3.0602 | 3.0602 | 3.0602 | 0.67731 | 1.1083 | 1.5188 | 1.8267 | 1.8267 | 1.8267 | 2.0011 | 2.5823 | 2.9631 | 3.1636 | 3.5645 | 3.9653 | 0.64601 | 1.275 | 1.53 | 1.53 | 1.53 | 1.53 | 0.95147 | 1.1068 | 1.1068 | 1.1068 | 1.1068 | 1.1068
2020-10-02 07:00 | Summer | 1.8468 | 2.6431 | 3.8141 | 3.8141 | 3.8141 | 3.8141 | 0.75734 | 1.2393 | 1.6983 | 2.0425 | 2.0425 | 2.0425 | 2.3151 | 2.9876 | 3.4282 | 3.6601 | 4.1239 | 4.5877 | 0.86498 | 1.7072 | 2.0486 | 2.0486 | 2.0486 | 2.0486 | 1.143 | 1.3297 | 1.3297 | 1.3297 | 1.3297 | 1.3297
2020-10-02 08:00 | Summer | 2.1339 | 3.0539 | 4.4069 | 4.4069 | 4.4069 | 4.4069 | 0.80592 | 1.3188 | 1.8072 | 2.1735 | 2.1735 | 2.1735 | 2.534 | 3.2701 | 3.7523 | 4.0061 | 4.5138 | 5.0214 | 0.93738 | 1.8501 | 2.2201 | 2.2201 | 2.2201 | 2.2201 | 1.2956 | 1.5071 | 1.5071 | 1.5071 | 1.5071 | 1.5071
2020-10-02 09:00 | Summer | 2.0386 | 2.9176 | 4.2102 | 4.2102 | 4.2102 | 4.2102 | 0.93452 | 1.5292 | 2.0956 | 2.5204 | 2.5204 | 2.5204 | 2.6293 | 3.393 | 3.8934 | 4.1567 | 4.6835 | 5.2102 | 0.88023 | 1.7373 | 2.0847 | 2.0847 | 2.0847 | 2.0847 | 1.3718 | 1.5957 | 1.5957 | 1.5957 | 1.5957 | 1.5957
2020-10-02 10:00 | Summer | 2.3816 | 3.4084 | 4.9185 | 4.9185 | 4.9185 | 4.9185 | 0.88594 | 1.4497 | 1.9867 | 2.3894 | 2.3894 | 2.3894 | 2.6098 | 3.3679 | 3.8645 | 4.126 | 4.6488 | 5.1716 | 0.85736 | 1.6922 | 2.0306 | 2.0306 | 2.0306 | 2.0306 | 1.3146 | 1.5293 | 1.5293 | 1.5293 | 1.5293 | 1.5293
2020-10-02 11:00 | Summer | 2.2482 | 3.2175 | 4.643 | 4.643 | 4.643 | 4.643 | 0.88594 | 1.4497 | 1.9867 | 2.3894 | 2.3894 | 2.3894 | 2.6864 | 3.4668 | 3.978 | 4.2471 | 4.7853 | 5.3234 | 0.86117 | 1.6997 | 2.0396 | 2.0396 | 2.0396 | 2.0396 | 1.3337 | 1.5514 | 1.5514 | 1.5514 | 1.5514 | 1.5514
2020-10-02 12:00 | Summer | 2.2204 | 3.1778 | 4.5856 | 4.5856 | 4.5856 | 4.5856 | 0.92881 | 1.5199 | 2.0828 | 2.505 | 2.505 | 2.505 | 2.5721 | 3.3192 | 3.8087 | 4.0664 | 4.5816 | 5.0969 | 0.81164 | 1.6019 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 1.2384 | 1.4406 | 1.4406 | 1.4406 | 1.4406 | 1.4406
2020-10-02 13:00 | Summer | 2.2482 | 3.2175 | 4.643 | 4.643 | 4.643 | 4.643 | 1.0003 | 1.6368 | 2.243 | 2.6977 | 2.6977 | 2.6977 | 2.6483 | 3.4176 | 3.9216 | 4.1869 | 4.7174 | 5.2479 | 0.92214 | 1.82 | 2.184 | 2.184 | 2.184 | 2.184 | 1.2384 | 1.4406 | 1.4406 | 1.4406 | 1.4406 | 1.4406
2020-10-02 14:00 | Summer | 2.2673 | 3.2448 | 4.6824 | 4.6824 | 4.6824 | 4.6824 | 0.96464 | 1.5785 | 2.1631 | 2.6016 | 2.6016 | 2.6016 | 2.7055 | 3.4913 | 4.0062 | 4.2772 | 4.8192 | 5.3612 | 0.95263 | 1.8802 | 2.2562 | 2.2562 | 2.2562 | 2.2562 | 1.1813 | 1.3741 | 1.3741 | 1.3741 | 1.3741 | 1.3741
2020-10-02 15:00 | Summer | 2.2863 | 3.2721 | 4.7217 | 4.7217 | 4.7217 | 4.7217 | 0.94881 | 1.5526 | 2.1276 | 2.5589 | 2.5589 | 2.5589 | 2.6674 | 3.4422 | 3.9498 | 4.217 | 4.7513 | 5.2857 | 0.83831 | 1.6546 | 1.9855 | 1.9855 | 1.9855 | 1.9855 | 1.105 | 1.2855 | 1.2855 | 1.2855 | 1.2855 | 1.2855
2020-10-02 16:00 | Summer | 2.2291 | 3.1903 | 4.6037 | 4.6037 | 4.6037 | 4.6037 | 0.87165 | 1.4263 | 1.9546 | 2.3508 | 2.3508 | 2.3508 | 2.5911 | 3.3438 | 3.8369 | 4.0965 | 4.6156 | 5.1347 | 0.85355 | 1.6846 | 2.0216 | 2.0216 | 2.0216 | 2.0216 | 1.0669 | 1.2411 | 1.2411 | 1.2411 | 1.2411 | 1.2411
2020-10-02 17:00 | Summer | 2.1347 | 3.0551 | 4.4086 | 4.4086 | 4.4086 | 4.4086 | 0.78877 | 1.2907 | 1.7688 | 2.1273 | 2.1273 | 2.1273 | 2.3916 | 3.0863 | 3.5415 | 3.781 | 4.2601 | 4.7392 | 0.84212 | 1.6621 | 1.9945 | 1.9945 | 1.9945 | 1.9945 | 1.0068 | 1.1711 | 1.1711 | 1.1711 | 1.1711 | 1.1711
2020-10-02 18:00 | Summer | 1.5969 | 2.2854 | 3.2979 | 3.2979 | 3.2979 | 3.2979 | 0.65445 | 1.0709 | 1.4676 | 1.765 | 1.765 | 1.765 | 2.3086 | 2.9792 | 3.4185 | 3.6497 | 4.1122 | 4.5747 | 0.81545 | 1.6094 | 1.9313 | 1.9313 | 1.9313 | 1.9313 | 0.80725 | 0.93904 | 0.93904 | 0.93904 | 0.93904 | 0.93904
2020-10-02 19:00 | Summer | 1.106 | 1.5829 | 2.2841 | 2.2841 | 2.2841 | 2.2841 | 0.61168 | 1.0009 | 1.3717 | 1.6497 | 1.6497 | 1.6497 | 2.278 | 2.9397 | 3.3733 | 3.6014 | 4.0578 | 4.5142 | 0.7964 | 1.5718 | 1.8862 | 1.8862 | 1.8862 | 1.8862 | 0.62873 | 0.73138 | 0.73138 | 0.73138 | 0.73138 | 0.73138
2020-10-02 20:00 | Summer | 1.0479 | 1.4997 | 2.1641 | 2.1641 | 2.1641 | 2.1641 | 0.53728 | 0.87918 | 1.2048 | 1.449 | 1.449 | 1.449 | 2.2101 | 2.8521 | 3.2727 | 3.4941 | 3.9368 | 4.3796 | 0.79258 | 1.5643 | 1.8772 | 1.8772 | 1.8772 | 1.8772 | 0.54979 | 0.63956 | 0.63956 | 0.63956 | 0.63956 | 0.63956
2020-10-02 21:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.53728 | 0.87918 | 1.2048 | 1.449 | 1.449 | 1.449 | 2.0958 | 2.7046 | 3.1034 | 3.3133 | 3.7332 | 4.153 | 0.77734 | 1.5342 | 1.8411 | 1.8411 | 1.8411 | 1.8411 | 0.55252 | 0.64273 | 0.64273 | 0.64273 | 0.64273 | 0.64273
2020-10-02 22:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.47155 | 0.77162 | 1.0574 | 1.2717 | 1.2717 | 1.2717 | 1.9815 | 2.557 | 2.9341 | 3.1326 | 3.5296 | 3.9265 | 0.76972 | 1.5192 | 1.823 | 1.823 | 1.823 | 1.823 | 0.53347 | 0.62057 | 0.62057 | 0.62057 | 0.62057 | 0.62057
2020-10-02 23:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.372 | 0.60872 | 0.83418 | 1.0033 | 1.0033 | 1.0033 | 1.8481 | 2.3849 | 2.7366 | 2.9218 | 3.292 | 3.6622 | 0.6897 | 1.3613 | 1.6335 | 1.6335 | 1.6335 | 1.6335 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-10-03 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.35251 | 0.57683 | 0.79047 | 0.9507 | 0.9507 | 0.9507 | 1.7534 | 2.2627 | 2.5964 | 2.772 | 3.1233 | 3.4745 | 0.59825 | 1.1808 | 1.4169 | 1.4169 | 1.4169 | 1.4169 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-10-03 01:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.42582 | 0.6968 | 0.95487 | 1.1484 | 1.1484 | 1.1484 | 1.6576 | 2.1391 | 2.4545 | 2.6205 | 2.9526 | 3.2847 | 0.57157 | 1.1281 | 1.3537 | 1.3537 | 1.3537 | 1.3537 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-10-03 02:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.42868 | 0.70147 | 0.96128 | 1.1561 | 1.1561 | 1.1561 | 1.6385 | 2.1145 | 2.4263 | 2.5904 | 2.9187 | 3.2469 | 0.55252 | 1.0905 | 1.3086 | 1.3086 | 1.3086 | 1.3086 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-10-03 03:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.43154 | 0.70615 | 0.96769 | 1.1638 | 1.1638 | 1.1638 | 1.6004 | 2.0653 | 2.3699 | 2.5302 | 2.8508 | 3.1714 | 0.54109 | 1.0679 | 1.2815 | 1.2815 | 1.2815 | 1.2815 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-10-03 04:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.33723 | 0.55183 | 0.75621 | 0.90949 | 0.90949 | 0.90949 | 1.6625 | 2.1455 | 2.4619 | 2.6284 | 2.9615 | 3.2945 | 0.51442 | 1.0153 | 1.2184 | 1.2184 | 1.2184 | 1.2184 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-10-03 05:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.43439 | 0.71083 | 0.9741 | 1.1715 | 1.1715 | 1.1715 | 1.6957 | 2.1882 | 2.5109 | 2.6808 | 3.0205 | 3.3602 | 0.5068 | 1.0003 | 1.2003 | 1.2003 | 1.2003 | 1.2003 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-10-03 06:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.52585 | 0.86048 | 1.1792 | 1.4182 | 1.4182 | 1.4182 | 1.81 | 2.3358 | 2.6802 | 2.8615 | 3.2241 | 3.5867 | 0.56395 | 1.1131 | 1.3357 | 1.3357 | 1.3357 | 1.3357 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-10-03 07:00 | Summer | 1.0288 | 1.4724 | 2.1248 | 2.1248 | 2.1248 | 2.1248 | 0.49441 | 0.80903 | 1.1087 | 1.3334 | 1.3334 | 1.3334 | 1.8866 | 2.4346 | 2.7936 | 2.9826 | 3.3605 | 3.7384 | 0.60206 | 1.1883 | 1.4259 | 1.4259 | 1.4259 | 1.4259 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-10-03 08:00 | Summer | 1.0479 | 1.4997 | 2.1641 | 2.1641 | 2.1641 | 2.1641 | 0.56586 | 0.92595 | 1.2689 | 1.5261 | 1.5261 | 1.5261 | 2.0196 | 2.6062 | 2.9906 | 3.1929 | 3.5974 | 4.002 | 0.69732 | 1.3763 | 1.6516 | 1.6516 | 1.6516 | 1.6516 | 0.53347 | 0.62057 | 0.62057 | 0.62057 | 0.62057 | 0.62057
2020-10-03 09:00 | Summer | 0.985 | 1.4097 | 2.0342 | 2.0342 | 2.0342 | 2.0342 | 0.6716 | 1.099 | 1.506 | 1.8113 | 1.8113 | 1.8113 | 2.0958 | 2.7046 | 3.1034 | 3.3133 | 3.7332 | 4.153 | 0.78877 | 1.5568 | 1.8681 | 1.8681 | 1.8681 | 1.8681 | 0.60968 | 0.70922 | 0.70922 | 0.70922 | 0.70922 | 0.70922
2020-10-03 10:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.58278 | 0.95364 | 1.3068 | 1.5717 | 1.5717 | 1.5717 | 2.191 | 2.8275 | 3.2445 | 3.4639 | 3.9029 | 4.3418 | 0.77353 | 1.5267 | 1.832 | 1.832 | 1.832 | 1.832 | 0.62873 | 0.73138 | 0.73138 | 0.73138 | 0.73138 | 0.73138
2020-10-03 11:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.62301 | 1.0195 | 1.3971 | 1.6803 | 1.6803 | 1.6803 | 2.2101 | 2.8521 | 3.2727 | 3.4941 | 3.9368 | 4.3796 | 0.72018 | 1.4214 | 1.7057 | 1.7057 | 1.7057 | 1.7057 | 0.62873 | 0.73138 | 0.73138 | 0.73138 | 0.73138 | 0.73138
2020-10-03 12:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.70875 | 1.1598 | 1.5893 | 1.9115 | 1.9115 | 1.9115 | 2.2482 | 2.9013 | 3.3291 | 3.5543 | 4.0047 | 4.4551 | 0.6363 | 1.2559 | 1.507 | 1.507 | 1.507 | 1.507 | 0.58922 | 0.68542 | 0.68542 | 0.68542 | 0.68542 | 0.68542
2020-10-03 13:00 | Summer | 0.94083 | 1.3465 | 1.943 | 1.943 | 1.943 | 1.943 | 0.6173 | 1.0101 | 1.3842 | 1.6648 | 1.6648 | 1.6648 | 2.2101 | 2.8521 | 3.2727 | 3.4941 | 3.9368 | 4.3796 | 0.60069 | 1.1856 | 1.4227 | 1.4227 | 1.4227 | 1.4227 | 0.57158 | 0.6649 | 0.6649 | 0.6649 | 0.6649 | 0.6649
2020-10-03 14:00 | Summer | 0.91452 | 1.3088 | 1.8887 | 1.8887 | 1.8887 | 1.8887 | 0.64016 | 1.0475 | 1.4355 | 1.7265 | 1.7265 | 1.7265 | 2.2673 | 2.9258 | 3.3573 | 3.5844 | 4.0386 | 4.4928 | 0.62873 | 1.2409 | 1.4891 | 1.4891 | 1.4891 | 1.4891 | 0.53341 | 0.6205 | 0.6205 | 0.6205 | 0.6205 | 0.6205
2020-10-03 15:00 | Summer | 1.0479 | 1.4997 | 2.1641 | 2.1641 | 2.1641 | 2.1641 | 0.66017 | 1.0803 | 1.4804 | 1.7805 | 1.7805 | 1.7805 | 2.1339 | 2.7537 | 3.1598 | 3.3736 | 3.8011 | 4.2285 | 0.7964 | 1.5718 | 1.8862 | 1.8862 | 1.8862 | 1.8862 | 0.53347 | 0.62057 | 0.62057 | 0.62057 | 0.62057 | 0.62057
2020-10-03 16:00 | Summer | 1.0479 | 1.4997 | 2.1641 | 2.1641 | 2.1641 | 2.1641 | 0.73447 | 1.2019 | 1.647 | 1.9808 | 1.9808 | 1.9808 | 2.191 | 2.8275 | 3.2445 | 3.4639 | 3.9029 | 4.3418 | 0.81545 | 1.6094 | 1.9313 | 1.9313 | 1.9313 | 1.9313 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-10-03 17:00 | Summer | 1.0479 | 1.4997 | 2.1641 | 2.1641 | 2.1641 | 2.1641 | 0.64588 | 1.0569 | 1.4483 | 1.7419 | 1.7419 | 1.7419 | 2.172 | 2.8029 | 3.2163 | 3.4338 | 3.8689 | 4.3041 | 0.81926 | 1.617 | 1.9403 | 1.9403 | 1.9403 | 1.9403 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-10-03 18:00 | Summer | 1.0479 | 1.4997 | 2.1641 | 2.1641 | 2.1641 | 2.1641 | 0.55443 | 0.90724 | 1.2433 | 1.4953 | 1.4953 | 1.4953 | 2.0577 | 2.6554 | 3.047 | 3.2531 | 3.6653 | 4.0775 | 0.89928 | 1.7749 | 2.1299 | 2.1299 | 2.1299 | 2.1299 | 0.53347 | 0.62057 | 0.62057 | 0.62057 | 0.62057 | 0.62057
2020-10-03 19:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.45726 | 0.74824 | 1.0254 | 1.2332 | 1.2332 | 1.2332 | 2.0005 | 2.5816 | 2.9624 | 3.1627 | 3.5635 | 3.9643 | 0.83831 | 1.6546 | 1.9855 | 1.9855 | 1.9855 | 1.9855 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-10-03 20:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.47155 | 0.77162 | 1.0574 | 1.2717 | 1.2717 | 1.2717 | 2.0005 | 2.5816 | 2.9624 | 3.1627 | 3.5635 | 3.9643 | 0.85355 | 1.6846 | 2.0216 | 2.0216 | 2.0216 | 2.0216 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-10-03 21:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.47155 | 0.77162 | 1.0574 | 1.2717 | 1.2717 | 1.2717 | 1.9243 | 2.4833 | 2.8495 | 3.0422 | 3.4277 | 3.8132 | 0.82688 | 1.632 | 1.9584 | 1.9584 | 1.9584 | 1.9584 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-10-03 22:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.38009 | 0.62197 | 0.85233 | 1.0251 | 1.0251 | 1.0251 | 1.81 | 2.3358 | 2.6802 | 2.8615 | 3.2241 | 3.5867 | 0.77297 | 1.5256 | 1.8307 | 1.8307 | 1.8307 | 1.8307 | 0.45459 | 0.52881 | 0.52881 | 0.52881 | 0.52881 | 0.52881
2020-10-03 23:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.46869 | 0.76695 | 1.051 | 1.264 | 1.264 | 1.264 | 1.7338 | 2.2374 | 2.5674 | 2.741 | 3.0884 | 3.4357 | 0.72781 | 1.4365 | 1.7238 | 1.7238 | 1.7238 | 1.7238 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-10-04 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.35437 | 0.57988 | 0.79466 | 0.95574 | 0.95574 | 0.95574 | 1.6372 | 2.1128 | 2.4243 | 2.5883 | 2.9163 | 3.2443 | 0.58301 | 1.1507 | 1.3808 | 1.3808 | 1.3808 | 1.3808 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-10-04 01:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.37152 | 0.60794 | 0.83311 | 1.002 | 1.002 | 1.002 | 1.5623 | 2.0161 | 2.3135 | 2.4699 | 2.7829 | 3.0959 | 0.53728 | 1.0604 | 1.2725 | 1.2725 | 1.2725 | 1.2725 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-10-04 03:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.42011 | 0.68744 | 0.94205 | 1.133 | 1.133 | 1.133 | 1.5242 | 1.967 | 2.257 | 2.4097 | 2.715 | 3.0204 | 0.59444 | 1.1732 | 1.4079 | 1.4079 | 1.4079 | 1.4079 | 0.43499 | 0.50601 | 0.50601 | 0.50601 | 0.50601 | 0.50601
2020-10-04 04:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.42868 | 0.70147 | 0.96128 | 1.1561 | 1.1561 | 1.1561 | 1.5434 | 1.9917 | 2.2855 | 2.4401 | 2.7493 | 3.0584 | 0.51061 | 1.0078 | 1.2093 | 1.2093 | 1.2093 | 1.2093 | 0.41861 | 0.48695 | 0.48695 | 0.48695 | 0.48695 | 0.48695
2020-10-04 05:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.41725 | 0.68277 | 0.93565 | 1.1253 | 1.1253 | 1.1253 | 1.6385 | 2.1145 | 2.4263 | 2.5904 | 2.9187 | 3.2469 | 0.50299 | 0.99273 | 1.1913 | 1.1913 | 1.1913 | 1.1913 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-10-04 06:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.41153 | 0.67342 | 0.92283 | 1.1099 | 1.1099 | 1.1099 | 1.6385 | 2.1145 | 2.4263 | 2.5904 | 2.9187 | 3.2469 | 0.5792 | 1.1431 | 1.3718 | 1.3718 | 1.3718 | 1.3718 | 0.47461 | 0.5521 | 0.5521 | 0.5521 | 0.5521 | 0.5521
2020-10-04 07:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.44011 | 0.72018 | 0.98691 | 1.187 | 1.187 | 1.187 | 1.7909 | 2.3112 | 2.652 | 2.8314 | 3.1902 | 3.549 | 0.5792 | 1.1431 | 1.3718 | 1.3718 | 1.3718 | 1.3718 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-10-04 08:00 | Summer | 0.87742 | 1.2557 | 1.8121 | 1.8121 | 1.8121 | 1.8121 | 0.42582 | 0.6968 | 0.95487 | 1.1484 | 1.1484 | 1.1484 | 1.9264 | 2.4859 | 2.8525 | 3.0455 | 3.4314 | 3.8173 | 0.73162 | 1.444 | 1.7328 | 1.7328 | 1.7328 | 1.7328 | 0.47931 | 0.55757 | 0.55757 | 0.55757 | 0.55757 | 0.55757
2020-10-04 09:00 | Summer | 0.89547 | 1.2816 | 1.8493 | 1.8493 | 1.8493 | 1.8493 | 0.56014 | 0.9166 | 1.2561 | 1.5107 | 1.5107 | 1.5107 | 2.0005 | 2.5816 | 2.9624 | 3.1627 | 3.5635 | 3.9643 | 0.80783 | 1.5944 | 1.9133 | 1.9133 | 1.9133 | 1.9133 | 0.53347 | 0.62057 | 0.62057 | 0.62057 | 0.62057 | 0.62057
2020-10-04 10:00 | Summer | 0.87642 | 1.2543 | 1.81 | 1.81 | 1.81 | 1.81 | 0.44011 | 0.72018 | 0.98691 | 1.187 | 1.187 | 1.187 | 2.172 | 2.8029 | 3.2163 | 3.4338 | 3.8689 | 4.3041 | 0.79258 | 1.5643 | 1.8772 | 1.8772 | 1.8772 | 1.8772 | 0.56294 | 0.65485 | 0.65485 | 0.65485 | 0.65485 | 0.65485
2020-10-04 11:00 | Summer | 0.87642 | 1.2543 | 1.81 | 1.81 | 1.81 | 1.81 | 0.38295 | 0.62665 | 0.85874 | 1.0328 | 1.0328 | 1.0328 | 2.0958 | 2.7046 | 3.1034 | 3.3133 | 3.7332 | 4.153 | 0.76215 | 1.5043 | 1.8051 | 1.8051 | 1.8051 | 1.8051 | 0.57158 | 0.6649 | 0.6649 | 0.6649 | 0.6649 | 0.6649
2020-10-04 12:00 | Summer | 0.85737 | 1.227 | 1.7706 | 1.7706 | 1.7706 | 1.7706 | 0.42868 | 0.70147 | 0.96128 | 1.1561 | 1.1561 | 1.1561 | 2.191 | 2.8275 | 3.2445 | 3.4639 | 3.9029 | 4.3418 | 0.69351 | 1.3688 | 1.6425 | 1.6425 | 1.6425 | 1.6425 | 0.51361 | 0.59747 | 0.59747 | 0.59747 | 0.59747 | 0.59747
2020-10-04 13:00 | Summer | 0.91452 | 1.3088 | 1.8887 | 1.8887 | 1.8887 | 1.8887 | 0.46869 | 0.76695 | 1.051 | 1.264 | 1.264 | 1.264 | 2.3054 | 2.975 | 3.4138 | 3.6447 | 4.1065 | 4.5683 | 0.73924 | 1.459 | 1.7508 | 1.7508 | 1.7508 | 1.7508 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-10-04 14:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.42011 | 0.68744 | 0.94205 | 1.133 | 1.133 | 1.133 | 2.2101 | 2.8521 | 3.2727 | 3.4941 | 3.9368 | 4.3796 | 0.75067 | 1.4816 | 1.7779 | 1.7779 | 1.7779 | 1.7779 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-10-04 15:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.43154 | 0.70615 | 0.96769 | 1.1638 | 1.1638 | 1.1638 | 2.2101 | 2.8521 | 3.2727 | 3.4941 | 3.9368 | 4.3796 | 0.75448 | 1.4891 | 1.7869 | 1.7869 | 1.7869 | 1.7869 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-10-04 16:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.47155 | 0.77162 | 1.0574 | 1.2717 | 1.2717 | 1.2717 | 2.2863 | 2.9504 | 3.3855 | 3.6146 | 4.0726 | 4.5306 | 0.78115 | 1.5417 | 1.8501 | 1.8501 | 1.8501 | 1.8501 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-10-04 17:00 | Summer | 1.0288 | 1.4724 | 2.1248 | 2.1248 | 2.1248 | 2.1248 | 0.45726 | 0.74824 | 1.0254 | 1.2332 | 1.2332 | 1.2332 | 2.2434 | 2.895 | 3.3219 | 3.5466 | 3.996 | 4.4455 | 0.80783 | 1.5944 | 1.9133 | 1.9133 | 1.9133 | 1.9133 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-10-04 18:00 | Summer | 1.086 | 1.5542 | 2.2428 | 2.2428 | 2.2428 | 2.2428 | 0.45726 | 0.74824 | 1.0254 | 1.2332 | 1.2332 | 1.2332 | 2.0958 | 2.7046 | 3.1034 | 3.3133 | 3.7332 | 4.153 | 0.83069 | 1.6395 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.48057 | 0.55903 | 0.55903 | 0.55903 | 0.55903 | 0.55903
2020-10-04 19:00 | Summer | 1.0479 | 1.4997 | 2.1641 | 2.1641 | 2.1641 | 2.1641 | 0.42232 | 0.69106 | 0.94701 | 1.139 | 1.139 | 1.139 | 2.02 | 2.6068 | 2.9912 | 3.1936 | 3.5982 | 4.0029 | 0.87261 | 1.7222 | 2.0667 | 2.0667 | 2.0667 | 2.0667 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-10-04 20:00 | Summer | 1.0288 | 1.4724 | 2.1248 | 2.1248 | 2.1248 | 2.1248 | 0.44297 | 0.72486 | 0.99332 | 1.1947 | 1.1947 | 1.1947 | 2.0386 | 2.6308 | 3.0188 | 3.223 | 3.6314 | 4.0398 | 0.87261 | 1.7222 | 2.0667 | 2.0667 | 2.0667 | 2.0667 | 0.53347 | 0.62057 | 0.62057 | 0.62057 | 0.62057 | 0.62057
2020-10-04 21:00 | Summer | 1.0288 | 1.4724 | 2.1248 | 2.1248 | 2.1248 | 2.1248 | 0.42099 | 0.68889 | 0.94403 | 1.1354 | 1.1354 | 1.1354 | 1.9053 | 2.4587 | 2.8213 | 3.0121 | 3.3938 | 3.7755 | 0.82688 | 1.632 | 1.9584 | 1.9584 | 1.9584 | 1.9584 | 0.46828 | 0.54473 | 0.54473 | 0.54473 | 0.54473 | 0.54473
2020-10-04 22:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.36295 | 0.59391 | 0.81388 | 0.97886 | 0.97886 | 0.97886 | 1.9053 | 2.4587 | 2.8213 | 3.0121 | 3.3938 | 3.7755 | 0.92976 | 1.8351 | 2.2021 | 2.2021 | 2.2021 | 2.2021 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-10-04 23:00 | Summer | 0.9919 | 1.4196 | 2.0485 | 2.0485 | 2.0485 | 2.0485 | 0.33738 | 0.55208 | 0.75655 | 0.90991 | 0.90991 | 0.90991 | 1.829 | 2.3603 | 2.7084 | 2.8916 | 3.2581 | 3.6245 | 0.70875 | 1.3989 | 1.6786 | 1.6786 | 1.6786 | 1.6786 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-10-05 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.38581 | 0.63133 | 0.86515 | 1.0405 | 1.0405 | 1.0405 | 1.6489 | 2.1279 | 2.4417 | 2.6068 | 2.9372 | 3.2675 | 0.64016 | 1.2635 | 1.5162 | 1.5162 | 1.5162 | 1.5162 | 0.42766 | 0.49748 | 0.49748 | 0.49748 | 0.49748 | 0.49748
2020-10-05 01:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.40867 | 0.66874 | 0.91642 | 1.1022 | 1.1022 | 1.1022 | 1.6004 | 2.0653 | 2.3699 | 2.5302 | 2.8508 | 3.1714 | 0.60587 | 1.1958 | 1.435 | 1.435 | 1.435 | 1.435 | 0.43293 | 0.50361 | 0.50361 | 0.50361 | 0.50361 | 0.50361
2020-10-05 02:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.39153 | 0.64068 | 0.87797 | 1.0559 | 1.0559 | 1.0559 | 1.5242 | 1.967 | 2.257 | 2.4097 | 2.715 | 3.0204 | 0.52585 | 1.0379 | 1.2454 | 1.2454 | 1.2454 | 1.2454 | 0.4382 | 0.50974 | 0.50974 | 0.50974 | 0.50974 | 0.50974
2020-10-05 03:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.4001 | 0.65471 | 0.89719 | 1.0791 | 1.0791 | 1.0791 | 1.5623 | 2.0161 | 2.3135 | 2.4699 | 2.7829 | 3.0959 | 0.50299 | 0.99273 | 1.1913 | 1.1913 | 1.1913 | 1.1913 | 0.43821 | 0.50975 | 0.50975 | 0.50975 | 0.50975 | 0.50975
2020-10-05 04:00 | Summer | 1.0288 | 1.4724 | 2.1248 | 2.1248 | 2.1248 | 2.1248 | 0.36009 | 0.58924 | 0.80747 | 0.97115 | 0.97115 | 0.97115 | 1.5236 | 1.9662 | 2.2561 | 2.4087 | 2.7139 | 3.0192 | 0.49536 | 0.97769 | 1.1732 | 1.1732 | 1.1732 | 1.1732 | 0.41913 | 0.48756 | 0.48756 | 0.48756 | 0.48756 | 0.48756
2020-10-05 05:00 | Summer | 1.1241 | 1.6088 | 2.3215 | 2.3215 | 2.3215 | 2.3215 | 0.4001 | 0.65471 | 0.89719 | 1.0791 | 1.0791 | 1.0791 | 1.6576 | 2.1391 | 2.4545 | 2.6205 | 2.9526 | 3.2847 | 0.6897 | 1.3613 | 1.6335 | 1.6335 | 1.6335 | 1.6335 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-10-05 06:00 | Summer | 1.1432 | 1.636 | 2.3609 | 2.3609 | 2.3609 | 2.3609 | 0.40719 | 0.66632 | 0.9131 | 1.0982 | 1.0982 | 1.0982 | 1.6576 | 2.1391 | 2.4545 | 2.6205 | 2.9526 | 3.2847 | 0.77353 | 1.5267 | 1.832 | 1.832 | 1.832 | 1.832 | 0.60968 | 0.70922 | 0.70922 | 0.70922 | 0.70922 | 0.70922
2020-10-05 07:00 | Summer | 1.2956 | 1.8542 | 2.6756 | 2.6756 | 2.6756 | 2.6756 | 0.46869 | 0.76695 | 1.051 | 1.264 | 1.264 | 1.264 | 1.7871 | 2.3062 | 2.6463 | 2.8253 | 3.1833 | 3.5413 | 0.73543 | 1.4515 | 1.7418 | 1.7418 | 1.7418 | 1.7418 | 0.60968 | 0.70922 | 0.70922 | 0.70922 | 0.70922 | 0.70922
2020-10-05 08:00 | Summer | 1.2956 | 1.8542 | 2.6756 | 2.6756 | 2.6756 | 2.6756 | 0.53442 | 0.87451 | 1.1984 | 1.4413 | 1.4413 | 1.4413 | 2.0196 | 2.6062 | 2.9906 | 3.1929 | 3.5974 | 4.002 | 1.0326 | 2.0381 | 2.4457 | 2.4457 | 2.4457 | 2.4457 | 0.66684 | 0.77571 | 0.77571 | 0.77571 | 0.77571 | 0.77571
2020-10-05 09:00 | Summer | 1.2956 | 1.8542 | 2.6756 | 2.6756 | 2.6756 | 2.6756 | 0.53728 | 0.87918 | 1.2048 | 1.449 | 1.449 | 1.449 | 2.0767 | 2.68 | 3.0752 | 3.2832 | 3.6992 | 4.1153 | 0.92976 | 1.8351 | 2.2021 | 2.2021 | 2.2021 | 2.2021 | 0.66203 | 0.77012 | 0.77012 | 0.77012 | 0.77012 | 0.77012
2020-10-05 10:00 | Summer | 1.4099 | 2.0178 | 2.9117 | 2.9117 | 2.9117 | 2.9117 | 0.50584 | 0.82774 | 1.1343 | 1.3642 | 1.3642 | 1.3642 | 2.0767 | 2.68 | 3.0752 | 3.2832 | 3.6992 | 4.1153 | 0.89547 | 1.7674 | 2.1208 | 2.1208 | 2.1208 | 2.1208 | 0.70494 | 0.82004 | 0.82004 | 0.82004 | 0.82004 | 0.82004
2020-10-05 11:00 | Summer | 1.3527 | 1.936 | 2.7937 | 2.7937 | 2.7937 | 2.7937 | 0.48298 | 0.79033 | 1.083 | 1.3026 | 1.3026 | 1.3026 | 2.2482 | 2.9013 | 3.3291 | 3.5543 | 4.0047 | 4.4551 | 0.87642 | 1.7298 | 2.0757 | 2.0757 | 2.0757 | 2.0757 | 0.724 | 0.8422 | 0.8422 | 0.8422 | 0.8422 | 0.8422
2020-10-05 12:00 | Summer | 1.3146 | 1.8814 | 2.715 | 2.715 | 2.715 | 2.715 | 0.53156 | 0.86983 | 1.192 | 1.4336 | 1.4336 | 1.4336 | 2.2673 | 2.9258 | 3.3573 | 3.5844 | 4.0386 | 4.4928 | 0.84974 | 1.6771 | 2.0125 | 2.0125 | 2.0125 | 2.0125 | 0.7621 | 0.88653 | 0.88653 | 0.88653 | 0.88653 | 0.88653
2020-10-05 13:00 | Summer | 1.3337 | 1.9087 | 2.7543 | 2.7543 | 2.7543 | 2.7543 | 0.5087 | 0.83242 | 1.1407 | 1.3719 | 1.3719 | 1.3719 | 2.3435 | 3.0242 | 3.4702 | 3.7049 | 4.1744 | 4.6438 | 0.84212 | 1.6621 | 1.9945 | 1.9945 | 1.9945 | 1.9945 | 0.74305 | 0.86436 | 0.86436 | 0.86436 | 0.86436 | 0.86436
2020-10-05 14:00 | Summer | 1.3527 | 1.936 | 2.7937 | 2.7937 | 2.7937 | 2.7937 | 0.44011 | 0.72018 | 0.98691 | 1.187 | 1.187 | 1.187 | 2.2673 | 2.9258 | 3.3573 | 3.5844 | 4.0386 | 4.4928 | 0.86498 | 1.7072 | 2.0486 | 2.0486 | 2.0486 | 2.0486 | 0.67952 | 0.79046 | 0.79046 | 0.79046 | 0.79046 | 0.79046
2020-10-05 15:00 | Summer | 1.3337 | 1.9087 | 2.7543 | 2.7543 | 2.7543 | 2.7543 | 0.47726 | 0.78098 | 1.0702 | 1.2872 | 1.2872 | 1.2872 | 2.2291 | 2.8767 | 3.3009 | 3.5242 | 3.9708 | 4.4173 | 0.86498 | 1.7072 | 2.0486 | 2.0486 | 2.0486 | 2.0486 | 0.67092 | 0.78046 | 0.78046 | 0.78046 | 0.78046 | 0.78046
2020-10-05 16:00 | Summer | 1.4099 | 2.0178 | 2.9117 | 2.9117 | 2.9117 | 2.9117 | 0.51156 | 0.83709 | 1.1471 | 1.3797 | 1.3797 | 1.3797 | 2.286 | 2.95 | 3.3851 | 3.6141 | 4.072 | 4.53 | 0.84593 | 1.6696 | 2.0035 | 2.0035 | 2.0035 | 2.0035 | 0.70494 | 0.82004 | 0.82004 | 0.82004 | 0.82004 | 0.82004
2020-10-05 17:00 | Summer | 1.3527 | 1.936 | 2.7937 | 2.7937 | 2.7937 | 2.7937 | 0.48012 | 0.78565 | 1.0766 | 1.2949 | 1.2949 | 1.2949 | 2.2863 | 2.9504 | 3.3855 | 3.6146 | 4.0726 | 4.5306 | 0.83069 | 1.6395 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.62398 | 0.72586 | 0.72586 | 0.72586 | 0.72586 | 0.72586
2020-10-05 18:00 | Summer | 1.2451 | 1.782 | 2.5715 | 2.5715 | 2.5715 | 2.5715 | 0.47441 | 0.7763 | 1.0638 | 1.2795 | 1.2795 | 1.2795 | 2.0577 | 2.6554 | 3.047 | 3.2531 | 3.6653 | 4.0775 | 0.76591 | 1.5117 | 1.814 | 1.814 | 1.814 | 1.814 | 0.62873 | 0.73138 | 0.73138 | 0.73138 | 0.73138 | 0.73138
2020-10-05 19:00 | Summer | 1.0669 | 1.527 | 2.2035 | 2.2035 | 2.2035 | 2.2035 | 0.40848 | 0.66843 | 0.91599 | 1.1017 | 1.1017 | 1.1017 | 2.0958 | 2.7046 | 3.1034 | 3.3133 | 3.7332 | 4.153 | 0.7621 | 1.5041 | 1.805 | 1.805 | 1.805 | 1.805 | 0.52303 | 0.60842 | 0.60842 | 0.60842 | 0.60842 | 0.60842
2020-10-05 20:00 | Summer | 1.0479 | 1.4997 | 2.1641 | 2.1641 | 2.1641 | 2.1641 | 0.40867 | 0.66874 | 0.91642 | 1.1022 | 1.1022 | 1.1022 | 2.0005 | 2.5816 | 2.9624 | 3.1627 | 3.5635 | 3.9643 | 0.78496 | 1.5493 | 1.8591 | 1.8591 | 1.8591 | 1.8591 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-10-05 21:00 | Summer | 1.0479 | 1.4997 | 2.1641 | 2.1641 | 2.1641 | 2.1641 | 0.36866 | 0.60327 | 0.8267 | 0.99427 | 0.99427 | 0.99427 | 1.9624 | 2.5325 | 2.9059 | 3.1025 | 3.4956 | 3.8887 | 0.77627 | 1.5321 | 1.8385 | 1.8385 | 1.8385 | 1.8385 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-10-05 22:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.38009 | 0.62197 | 0.85233 | 1.0251 | 1.0251 | 1.0251 | 1.8672 | 2.4095 | 2.7649 | 2.9519 | 3.3259 | 3.7 | 0.72975 | 1.4403 | 1.7284 | 1.7284 | 1.7284 | 1.7284 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-10-05 23:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.36581 | 0.59859 | 0.82029 | 0.98657 | 0.98657 | 0.98657 | 1.8481 | 2.3849 | 2.7366 | 2.9218 | 3.292 | 3.6622 | 0.56776 | 1.1206 | 1.3447 | 1.3447 | 1.3447 | 1.3447 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-10-06 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.45154 | 0.73889 | 1.0125 | 1.2178 | 1.2178 | 1.2178 | 1.7147 | 2.2128 | 2.5392 | 2.7109 | 3.0544 | 3.3979 | 0.54109 | 1.0679 | 1.2815 | 1.2815 | 1.2815 | 1.2815 | 0.43821 | 0.50975 | 0.50975 | 0.50975 | 0.50975 | 0.50975
2020-10-06 01:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.37152 | 0.60794 | 0.83311 | 1.002 | 1.002 | 1.002 | 1.6195 | 2.0899 | 2.3981 | 2.5603 | 2.8847 | 3.2092 | 0.57539 | 1.1356 | 1.3628 | 1.3628 | 1.3628 | 1.3628 | 0.43821 | 0.50975 | 0.50975 | 0.50975 | 0.50975 | 0.50975
2020-10-06 02:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.38295 | 0.62665 | 0.85874 | 1.0328 | 1.0328 | 1.0328 | 1.6957 | 2.1882 | 2.5109 | 2.6808 | 3.0205 | 3.3602 | 0.50299 | 0.99273 | 1.1913 | 1.1913 | 1.1913 | 1.1913 | 0.41931 | 0.48776 | 0.48776 | 0.48776 | 0.48776 | 0.48776
2020-10-06 03:00 | Summer | 0.96519 | 1.3813 | 1.9933 | 1.9933 | 1.9933 | 1.9933 | 0.39438 | 0.64536 | 0.88438 | 1.0636 | 1.0636 | 1.0636 | 1.6004 | 2.0653 | 2.3699 | 2.5302 | 2.8508 | 3.1714 | 0.52966 | 1.0454 | 1.2545 | 1.2545 | 1.2545 | 1.2545 | 0.42023 | 0.48884 | 0.48884 | 0.48884 | 0.48884 | 0.48884
2020-10-06 04:00 | Summer | 1.1165 | 1.5979 | 2.3059 | 2.3059 | 2.3059 | 2.3059 | 0.39438 | 0.64536 | 0.88438 | 1.0636 | 1.0636 | 1.0636 | 1.6957 | 2.1882 | 2.5109 | 2.6808 | 3.0205 | 3.3602 | 0.51823 | 1.0228 | 1.2274 | 1.2274 | 1.2274 | 1.2274 | 0.43814 | 0.50968 | 0.50968 | 0.50968 | 0.50968 | 0.50968
2020-10-06 05:00 | Summer | 1.4137 | 2.0232 | 2.9196 | 2.9196 | 2.9196 | 2.9196 | 0.46012 | 0.75292 | 1.0318 | 1.2409 | 1.2409 | 1.2409 | 1.7577 | 2.2683 | 2.6028 | 2.7789 | 3.131 | 3.4831 | 0.70654 | 1.3945 | 1.6734 | 1.6734 | 1.6734 | 1.6734 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-10-06 06:00 | Summer | 1.4289 | 2.045 | 2.9511 | 2.9511 | 2.9511 | 2.9511 | 0.63159 | 1.0335 | 1.4163 | 1.7034 | 1.7034 | 1.7034 | 1.9243 | 2.4833 | 2.8495 | 3.0422 | 3.4277 | 3.8132 | 0.70875 | 1.3989 | 1.6786 | 1.6786 | 1.6786 | 1.6786 | 0.68589 | 0.79787 | 0.79787 | 0.79787 | 0.79787 | 0.79787
2020-10-06 07:00 | Summer | 1.8079 | 2.5874 | 3.7336 | 3.7336 | 3.7336 | 3.7336 | 0.80059 | 1.3101 | 1.7953 | 2.1592 | 2.1592 | 2.1592 | 2.223 | 2.8687 | 3.2918 | 3.5144 | 3.9598 | 4.4051 | 0.85736 | 1.6922 | 2.0306 | 2.0306 | 2.0306 | 2.0306 | 0.86065 | 1.0012 | 1.0012 | 1.0012 | 1.0012 | 1.0012
2020-10-06 08:00 | Summer | 2.2101 | 3.163 | 4.5643 | 4.5643 | 4.5643 | 4.5643 | 0.88594 | 1.4497 | 1.9867 | 2.3894 | 2.3894 | 2.3894 | 2.4768 | 3.1963 | 3.6677 | 3.9158 | 4.4119 | 4.9081 | 0.86879 | 1.7147 | 2.0577 | 2.0577 | 2.0577 | 2.0577 | 1.105 | 1.2855 | 1.2855 | 1.2855 | 1.2855 | 1.2855
2020-10-06 09:00 | Summer | 2.2101 | 3.163 | 4.5643 | 4.5643 | 4.5643 | 4.5643 | 0.8888 | 1.4544 | 1.9931 | 2.3971 | 2.3971 | 2.3971 | 2.6674 | 3.4422 | 3.9498 | 4.217 | 4.7513 | 5.2857 | 0.96406 | 1.9027 | 2.2833 | 2.2833 | 2.2833 | 2.2833 | 1.2003 | 1.3963 | 1.3963 | 1.3963 | 1.3963 | 1.3963
2020-10-06 10:00 | Summer | 2.191 | 3.1357 | 4.525 | 4.525 | 4.525 | 4.525 | 0.88022 | 1.4404 | 1.9738 | 2.3739 | 2.3739 | 2.3739 | 2.6293 | 3.393 | 3.8934 | 4.1567 | 4.6835 | 5.2102 | 0.99454 | 1.9629 | 2.3555 | 2.3555 | 2.3555 | 2.3555 | 1.3146 | 1.5293 | 1.5293 | 1.5293 | 1.5293 | 1.5293
2020-10-06 11:00 | Summer | 2.172 | 3.1085 | 4.4856 | 4.4856 | 4.4856 | 4.4856 | 0.88308 | 1.445 | 1.9802 | 2.3816 | 2.3816 | 2.3816 | 2.6674 | 3.4422 | 3.9498 | 4.217 | 4.7513 | 5.2857 | 0.88785 | 1.7523 | 2.1028 | 2.1028 | 2.1028 | 2.1028 | 1.3337 | 1.5514 | 1.5514 | 1.5514 | 1.5514 | 1.5514
2020-10-06 12:00 | Summer | 2.3562 | 3.3721 | 4.866 | 4.866 | 4.866 | 4.866 | 0.87737 | 1.4357 | 1.9674 | 2.3662 | 2.3662 | 2.3662 | 2.6864 | 3.4668 | 3.978 | 4.2471 | 4.7853 | 5.3234 | 0.96025 | 1.8952 | 2.2743 | 2.2743 | 2.2743 | 2.2743 | 1.3908 | 1.6179 | 1.6179 | 1.6179 | 1.6179 | 1.6179
2020-10-06 13:00 | Summer | 2.4006 | 3.4357 | 4.9578 | 4.9578 | 4.9578 | 4.9578 | 0.90309 | 1.4778 | 2.0251 | 2.4356 | 2.4356 | 2.4356 | 2.6674 | 3.4422 | 3.9498 | 4.217 | 4.7513 | 5.2857 | 0.98311 | 1.9403 | 2.3284 | 2.3284 | 2.3284 | 2.3284 | 1.3337 | 1.5514 | 1.5514 | 1.5514 | 1.5514 | 1.5514
2020-10-06 14:00 | Summer | 2.2863 | 3.2721 | 4.7217 | 4.7217 | 4.7217 | 4.7217 | 0.87451 | 1.431 | 1.961 | 2.3585 | 2.3585 | 2.3585 | 2.5721 | 3.3192 | 3.8087 | 4.0664 | 4.5816 | 5.0969 | 0.89547 | 1.7674 | 2.1208 | 2.1208 | 2.1208 | 2.1208 | 1.3077 | 1.5212 | 1.5212 | 1.5212 | 1.5212 | 1.5212
2020-10-06 15:00 | Summer | 2.2291 | 3.1903 | 4.6037 | 4.6037 | 4.6037 | 4.6037 | 0.8345 | 1.3655 | 1.8713 | 2.2506 | 2.2506 | 2.2506 | 2.5721 | 3.3192 | 3.8087 | 4.0664 | 4.5816 | 5.0969 | 1.0098 | 1.993 | 2.3916 | 2.3916 | 2.3916 | 2.3916 | 1.2765 | 1.4849 | 1.4849 | 1.4849 | 1.4849 | 1.4849
2020-10-06 16:00 | Summer | 2.3054 | 3.2993 | 4.7611 | 4.7611 | 4.7611 | 4.7611 | 0.78306 | 1.2814 | 1.7559 | 2.1119 | 2.1119 | 2.1119 | 2.6102 | 3.3684 | 3.8652 | 4.1266 | 4.6495 | 5.1724 | 0.96504 | 1.9047 | 2.2856 | 2.2856 | 2.2856 | 2.2856 | 1.2384 | 1.4406 | 1.4406 | 1.4406 | 1.4406 | 1.4406
2020-10-06 17:00 | Summer | 2.1529 | 3.0812 | 4.4463 | 4.4463 | 4.4463 | 4.4463 | 0.7459 | 1.2206 | 1.6726 | 2.0117 | 2.0117 | 2.0117 | 2.4638 | 3.1794 | 3.6483 | 3.8951 | 4.3887 | 4.8823 | 0.82307 | 1.6245 | 1.9494 | 1.9494 | 1.9494 | 1.9494 | 1.0573 | 1.23 | 1.23 | 1.23 | 1.23 | 1.23
2020-10-06 18:00 | Summer | 1.6149 | 2.3111 | 3.335 | 3.335 | 3.335 | 3.335 | 0.63445 | 1.0382 | 1.4227 | 1.7111 | 1.7111 | 1.7111 | 2.4006 | 3.098 | 3.5548 | 3.7953 | 4.2762 | 4.7571 | 0.71637 | 1.4139 | 1.6967 | 1.6967 | 1.6967 | 1.6967 | 0.89257 | 1.0383 | 1.0383 | 1.0383 | 1.0383 | 1.0383
2020-10-06 19:00 | Summer | 1.1622 | 1.6633 | 2.4002 | 2.4002 | 2.4002 | 2.4002 | 0.52299 | 0.8558 | 1.1728 | 1.4105 | 1.4105 | 1.4105 | 2.1827 | 2.8167 | 3.2321 | 3.4508 | 3.888 | 4.3253 | 0.7621 | 1.5041 | 1.805 | 1.805 | 1.805 | 1.805 | 0.71764 | 0.83481 | 0.83481 | 0.83481 | 0.83481 | 0.83481
2020-10-06 20:00 | Summer | 1.105 | 1.5815 | 2.2822 | 2.2822 | 2.2822 | 2.2822 | 0.52013 | 0.85112 | 1.1664 | 1.4028 | 1.4028 | 1.4028 | 2.0958 | 2.7046 | 3.1034 | 3.3133 | 3.7332 | 4.153 | 0.7964 | 1.5718 | 1.8862 | 1.8862 | 1.8862 | 1.8862 | 0.59063 | 0.68706 | 0.68706 | 0.68706 | 0.68706 | 0.68706
2020-10-06 21:00 | Summer | 1.0669 | 1.527 | 2.2035 | 2.2035 | 2.2035 | 2.2035 | 0.49727 | 0.81371 | 1.1151 | 1.3411 | 1.3411 | 1.3411 | 2.0246 | 2.6126 | 2.9979 | 3.2007 | 3.6063 | 4.0119 | 0.7621 | 1.5041 | 1.805 | 1.805 | 1.805 | 1.805 | 0.55252 | 0.64273 | 0.64273 | 0.64273 | 0.64273 | 0.64273
2020-10-06 22:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.55443 | 0.90724 | 1.2433 | 1.4953 | 1.4953 | 1.4953 | 1.9243 | 2.4833 | 2.8495 | 3.0422 | 3.4277 | 3.8132 | 0.76972 | 1.5192 | 1.823 | 1.823 | 1.823 | 1.823 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-10-06 23:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.4544 | 0.74356 | 1.019 | 1.2255 | 1.2255 | 1.2255 | 1.829 | 2.3603 | 2.7084 | 2.8916 | 3.2581 | 3.6245 | 0.66684 | 1.3161 | 1.5794 | 1.5794 | 1.5794 | 1.5794 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-10-07 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.43439 | 0.71083 | 0.9741 | 1.1715 | 1.1715 | 1.1715 | 1.6957 | 2.1882 | 2.5109 | 2.6808 | 3.0205 | 3.3602 | 0.58682 | 1.1582 | 1.3898 | 1.3898 | 1.3898 | 1.3898 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-10-07 01:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.41725 | 0.68277 | 0.93565 | 1.1253 | 1.1253 | 1.1253 | 1.6195 | 2.0899 | 2.3981 | 2.5603 | 2.8847 | 3.2092 | 0.56014 | 1.1055 | 1.3267 | 1.3267 | 1.3267 | 1.3267 | 0.43821 | 0.50975 | 0.50975 | 0.50975 | 0.50975 | 0.50975
2020-10-07 02:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.45154 | 0.73889 | 1.0125 | 1.2178 | 1.2178 | 1.2178 | 1.5897 | 2.0515 | 2.3541 | 2.5133 | 2.8318 | 3.1502 | 0.53784 | 1.0615 | 1.2738 | 1.2738 | 1.2738 | 1.2738 | 0.43821 | 0.50975 | 0.50975 | 0.50975 | 0.50975 | 0.50975
2020-10-07 03:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.48869 | 0.79968 | 1.0959 | 1.318 | 1.318 | 1.318 | 1.6195 | 2.0899 | 2.3981 | 2.5603 | 2.8847 | 3.2092 | 0.5449 | 1.0755 | 1.2906 | 1.2906 | 1.2906 | 1.2906 | 0.43821 | 0.50975 | 0.50975 | 0.50975 | 0.50975 | 0.50975
2020-10-07 04:00 | Summer | 1.086 | 1.5542 | 2.2428 | 2.2428 | 2.2428 | 2.2428 | 0.45154 | 0.73889 | 1.0125 | 1.2178 | 1.2178 | 1.2178 | 1.6147 | 2.0837 | 2.391 | 2.5527 | 2.8762 | 3.1997 | 0.53728 | 1.0604 | 1.2725 | 1.2725 | 1.2725 | 1.2725 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-10-07 05:00 | Summer | 1.2575 | 1.7996 | 2.5969 | 2.5969 | 2.5969 | 2.5969 | 0.46012 | 0.75292 | 1.0318 | 1.2409 | 1.2409 | 1.2409 | 1.7454 | 2.2524 | 2.5846 | 2.7594 | 3.1091 | 3.4587 | 0.75976 | 1.4995 | 1.7994 | 1.7994 | 1.7994 | 1.7994 | 0.5176 | 0.60211 | 0.60211 | 0.60211 | 0.60211 | 0.60211
2020-10-07 06:00 | Summer | 1.3337 | 1.9087 | 2.7543 | 2.7543 | 2.7543 | 2.7543 | 0.56586 | 0.92595 | 1.2689 | 1.5261 | 1.5261 | 1.5261 | 1.8481 | 2.3849 | 2.7366 | 2.9218 | 3.292 | 3.6622 | 0.7621 | 1.5041 | 1.805 | 1.805 | 1.805 | 1.805 | 0.779 | 0.90618 | 0.90618 | 0.90618 | 0.90618 | 0.90618
2020-10-07 07:00 | Summer | 1.8449 | 2.6403 | 3.8101 | 3.8101 | 3.8101 | 3.8101 | 0.8002 | 1.3094 | 1.7944 | 2.1581 | 2.1581 | 2.1581 | 2.1857 | 2.8206 | 3.2366 | 3.4555 | 3.8934 | 4.3312 | 0.92976 | 1.8351 | 2.2021 | 2.2021 | 2.2021 | 2.2021 | 0.95263 | 1.1082 | 1.1082 | 1.1082 | 1.1082 | 1.1082
2020-10-07 08:00 | Summer | 2.1529 | 3.0812 | 4.4463 | 4.4463 | 4.4463 | 4.4463 | 0.89166 | 1.4591 | 1.9995 | 2.4048 | 2.4048 | 2.4048 | 2.4768 | 3.1963 | 3.6677 | 3.9158 | 4.4119 | 4.9081 | 0.9793 | 1.9328 | 2.3194 | 2.3194 | 2.3194 | 2.3194 | 1.1813 | 1.3741 | 1.3741 | 1.3741 | 1.3741 | 1.3741
2020-10-07 09:00 | Summer | 2.3625 | 3.3811 | 4.8791 | 4.8791 | 4.8791 | 4.8791 | 0.91166 | 1.4918 | 2.0443 | 2.4587 | 2.4587 | 2.4587 | 2.534 | 3.2701 | 3.7523 | 4.0061 | 4.5138 | 5.0214 | 0.9793 | 1.9328 | 2.3194 | 2.3194 | 2.3194 | 2.3194 | 1.2194 | 1.4184 | 1.4184 | 1.4184 | 1.4184 | 1.4184
2020-10-07 10:00 | Summer | 2.3054 | 3.2993 | 4.7611 | 4.7611 | 4.7611 | 4.7611 | 0.93738 | 1.5339 | 2.102 | 2.5281 | 2.5281 | 2.5281 | 2.5721 | 3.3192 | 3.8087 | 4.0664 | 4.5816 | 5.0969 | 0.99454 | 1.9629 | 2.3555 | 2.3555 | 2.3555 | 2.3555 | 1.2384 | 1.4406 | 1.4406 | 1.4406 | 1.4406 | 1.4406
2020-10-07 11:00 | Summer | 2.2863 | 3.2721 | 4.7217 | 4.7217 | 4.7217 | 4.7217 | 0.93167 | 1.5245 | 2.0892 | 2.5127 | 2.5127 | 2.5127 | 2.648 | 3.4172 | 3.9212 | 4.1864 | 4.7169 | 5.2474 | 0.93738 | 1.8501 | 2.2201 | 2.2201 | 2.2201 | 2.2201 | 1.3146 | 1.5293 | 1.5293 | 1.5293 | 1.5293 | 1.5293
2020-10-07 12:00 | Summer | 2.3244 | 3.3266 | 4.8004 | 4.8004 | 4.8004 | 4.8004 | 0.98025 | 1.604 | 2.1981 | 2.6437 | 2.6437 | 2.6437 | 2.7055 | 3.4913 | 4.0062 | 4.2772 | 4.8192 | 5.3612 | 0.95263 | 1.8802 | 2.2562 | 2.2562 | 2.2562 | 2.2562 | 1.2956 | 1.5071 | 1.5071 | 1.5071 | 1.5071 | 1.5071
2020-10-07 13:00 | Summer | 2.3625 | 3.3811 | 4.8791 | 4.8791 | 4.8791 | 4.8791 | 0.98025 | 1.604 | 2.1981 | 2.6437 | 2.6437 | 2.6437 | 2.6674 | 3.4422 | 3.9498 | 4.217 | 4.7513 | 5.2857 | 0.94119 | 1.8576 | 2.2291 | 2.2291 | 2.2291 | 2.2291 | 1.2575 | 1.4628 | 1.4628 | 1.4628 | 1.4628 | 1.4628
2020-10-07 14:00 | Summer | 2.2101 | 3.163 | 4.5643 | 4.5643 | 4.5643 | 4.5643 | 0.83736 | 1.3702 | 1.8777 | 2.2583 | 2.2583 | 2.2583 | 2.6293 | 3.393 | 3.8934 | 4.1567 | 4.6835 | 5.2102 | 0.91071 | 1.7975 | 2.1569 | 2.1569 | 2.1569 | 2.1569 | 1.2575 | 1.4628 | 1.4628 | 1.4628 | 1.4628 | 1.4628
2020-10-07 15:00 | Summer | 2.191 | 3.1357 | 4.525 | 4.525 | 4.525 | 4.525 | 0.84021 | 1.3749 | 1.8841 | 2.266 | 2.266 | 2.266 | 2.6293 | 3.393 | 3.8934 | 4.1567 | 4.6835 | 5.2102 | 0.95644 | 1.8877 | 2.2652 | 2.2652 | 2.2652 | 2.2652 | 1.1432 | 1.3298 | 1.3298 | 1.3298 | 1.3298 | 1.3298
2020-10-07 16:00 | Summer | 2.1529 | 3.0812 | 4.4463 | 4.4463 | 4.4463 | 4.4463 | 0.83164 | 1.3609 | 1.8649 | 2.2429 | 2.2429 | 2.2429 | 2.6102 | 3.3684 | 3.8652 | 4.1266 | 4.6495 | 5.1724 | 0.98311 | 1.9403 | 2.3284 | 2.3284 | 2.3284 | 2.3284 | 1.1432 | 1.3298 | 1.3298 | 1.3298 | 1.3298 | 1.3298
2020-10-07 17:00 | Summer | 2.0005 | 2.8631 | 4.1315 | 4.1315 | 4.1315 | 4.1315 | 0.78306 | 1.2814 | 1.7559 | 2.1119 | 2.1119 | 2.1119 | 2.5892 | 3.3413 | 3.834 | 4.0934 | 4.612 | 5.1307 | 0.9793 | 1.9328 | 2.3194 | 2.3194 | 2.3194 | 2.3194 | 1.0669 | 1.2411 | 1.2411 | 1.2411 | 1.2411 | 1.2411
2020-10-07 18:00 | Summer | 1.6521 | 2.3644 | 3.4119 | 3.4119 | 3.4119 | 3.4119 | 0.61751 | 1.0105 | 1.3847 | 1.6654 | 1.6654 | 1.6654 | 2.4387 | 3.1471 | 3.6112 | 3.8555 | 4.3441 | 4.8326 | 0.80783 | 1.5944 | 1.9133 | 1.9133 | 1.9133 | 1.9133 | 0.89668 | 1.0431 | 1.0431 | 1.0431 | 1.0431 | 1.0431
2020-10-07 19:00 | Summer | 1.2003 | 1.7178 | 2.4789 | 2.4789 | 2.4789 | 2.4789 | 0.4806 | 0.78643 | 1.0777 | 1.2962 | 1.2962 | 1.2962 | 2.4036 | 3.1018 | 3.5592 | 3.8 | 4.2815 | 4.763 | 0.84974 | 1.6771 | 2.0125 | 2.0125 | 2.0125 | 2.0125 | 0.68589 | 0.79787 | 0.79787 | 0.79787 | 0.79787 | 0.79787
2020-10-07 20:00 | Summer | 1.086 | 1.5542 | 2.2428 | 2.2428 | 2.2428 | 2.2428 | 0.49155 | 0.80436 | 1.1023 | 1.3257 | 1.3257 | 1.3257 | 2.3244 | 2.9996 | 3.442 | 3.6748 | 4.1404 | 4.6061 | 0.81164 | 1.6019 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 0.59063 | 0.68706 | 0.68706 | 0.68706 | 0.68706 | 0.68706
2020-10-07 21:00 | Summer | 1.0669 | 1.527 | 2.2035 | 2.2035 | 2.2035 | 2.2035 | 0.46012 | 0.75292 | 1.0318 | 1.2409 | 1.2409 | 1.2409 | 2.0958 | 2.7046 | 3.1034 | 3.3133 | 3.7332 | 4.153 | 0.7964 | 1.5718 | 1.8862 | 1.8862 | 1.8862 | 1.8862 | 0.53347 | 0.62057 | 0.62057 | 0.62057 | 0.62057 | 0.62057
2020-10-07 22:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.42011 | 0.68744 | 0.94205 | 1.133 | 1.133 | 1.133 | 2.0005 | 2.5816 | 2.9624 | 3.1627 | 3.5635 | 3.9643 | 0.78355 | 1.5465 | 1.8558 | 1.8558 | 1.8558 | 1.8558 | 0.47648 | 0.55428 | 0.55428 | 0.55428 | 0.55428 | 0.55428
2020-10-07 23:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.37438 | 0.61262 | 0.83952 | 1.0097 | 1.0097 | 1.0097 | 1.8385 | 2.3726 | 2.7225 | 2.9066 | 3.275 | 3.6433 | 0.73162 | 1.444 | 1.7328 | 1.7328 | 1.7328 | 1.7328 | 0.45725 | 0.5319 | 0.5319 | 0.5319 | 0.5319 | 0.5319
2020-10-08 | Summer | 1.0288 | 1.4724 | 2.1248 | 2.1248 | 2.1248 | 2.1248 | 0.39438 | 0.64536 | 0.88438 | 1.0636 | 1.0636 | 1.0636 | 1.7528 | 2.262 | 2.5956 | 2.7712 | 3.1223 | 3.4734 | 0.64269 | 1.2685 | 1.5222 | 1.5222 | 1.5222 | 1.5222 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-10-08 01:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.38867 | 0.636 | 0.87156 | 1.0482 | 1.0482 | 1.0482 | 1.6399 | 2.1163 | 2.4283 | 2.5926 | 2.9211 | 3.2496 | 0.60968 | 1.2033 | 1.444 | 1.444 | 1.444 | 1.444 | 0.41827 | 0.48656 | 0.48656 | 0.48656 | 0.48656 | 0.48656
2020-10-08 02:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.41725 | 0.68277 | 0.93565 | 1.1253 | 1.1253 | 1.1253 | 1.6385 | 2.1145 | 2.4263 | 2.5904 | 2.9187 | 3.2469 | 0.60587 | 1.1958 | 1.435 | 1.435 | 1.435 | 1.435 | 0.43731 | 0.50871 | 0.50871 | 0.50871 | 0.50871 | 0.50871
2020-10-08 03:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.40582 | 0.66406 | 0.91001 | 1.0945 | 1.0945 | 1.0945 | 1.6169 | 2.0866 | 2.3944 | 2.5563 | 2.8802 | 3.2042 | 0.6173 | 1.2184 | 1.462 | 1.462 | 1.462 | 1.462 | 0.43821 | 0.50975 | 0.50975 | 0.50975 | 0.50975 | 0.50975
2020-10-08 04:00 | Summer | 1.0929 | 1.5641 | 2.257 | 2.257 | 2.257 | 2.257 | 0.39438 | 0.64536 | 0.88438 | 1.0636 | 1.0636 | 1.0636 | 1.6766 | 2.1636 | 2.4827 | 2.6507 | 2.9865 | 3.3224 | 0.57539 | 1.1356 | 1.3628 | 1.3628 | 1.3628 | 1.3628 | 0.45694 | 0.53154 | 0.53154 | 0.53154 | 0.53154 | 0.53154
2020-10-08 05:00 | Summer | 1.2765 | 1.8269 | 2.6363 | 2.6363 | 2.6363 | 2.6363 | 0.45726 | 0.74824 | 1.0254 | 1.2332 | 1.2332 | 1.2332 | 1.7422 | 2.2482 | 2.5798 | 2.7543 | 3.1033 | 3.4523 | 0.66303 | 1.3086 | 1.5703 | 1.5703 | 1.5703 | 1.5703 | 0.53495 | 0.62229 | 0.62229 | 0.62229 | 0.62229 | 0.62229
2020-10-08 06:00 | Summer | 1.3527 | 1.936 | 2.7937 | 2.7937 | 2.7937 | 2.7937 | 0.62016 | 1.0148 | 1.3907 | 1.6725 | 1.6725 | 1.6725 | 1.9053 | 2.4587 | 2.8213 | 3.0121 | 3.3938 | 3.7755 | 0.71256 | 1.4064 | 1.6877 | 1.6877 | 1.6877 | 1.6877 | 0.85617 | 0.99596 | 0.99596 | 0.99596 | 0.99596 | 0.99596
2020-10-08 07:00 | Summer | 1.81 | 2.5904 | 3.738 | 3.738 | 3.738 | 3.738 | 0.76877 | 1.258 | 1.7239 | 2.0733 | 2.0733 | 2.0733 | 2.2673 | 2.9258 | 3.3573 | 3.5844 | 4.0386 | 4.4928 | 0.96406 | 1.9027 | 2.2833 | 2.2833 | 2.2833 | 2.2833 | 1.0463 | 1.2171 | 1.2171 | 1.2171 | 1.2171 | 1.2171
2020-10-08 08:00 | Summer | 2.3244 | 3.3266 | 4.8004 | 4.8004 | 4.8004 | 4.8004 | 0.80592 | 1.3188 | 1.8072 | 2.1735 | 2.1735 | 2.1735 | 2.5385 | 3.2759 | 3.759 | 4.0133 | 4.5218 | 5.0303 | 1.0631 | 2.0983 | 2.5179 | 2.5179 | 2.5179 | 2.5179 | 1.2384 | 1.4406 | 1.4406 | 1.4406 | 1.4406 | 1.4406
2020-10-08 09:00 | Summer | 2.2863 | 3.2721 | 4.7217 | 4.7217 | 4.7217 | 4.7217 | 0.89166 | 1.4591 | 1.9995 | 2.4048 | 2.4048 | 2.4048 | 2.6053 | 3.3621 | 3.858 | 4.1189 | 4.6408 | 5.1628 | 1.0936 | 2.1585 | 2.5901 | 2.5901 | 2.5901 | 2.5901 | 1.3527 | 1.5736 | 1.5736 | 1.5736 | 1.5736 | 1.5736
2020-10-08 10:00 | Summer | 2.3054 | 3.2993 | 4.7611 | 4.7611 | 4.7611 | 4.7611 | 0.88594 | 1.4497 | 1.9867 | 2.3894 | 2.3894 | 2.3894 | 2.7245 | 3.5159 | 4.0344 | 4.3073 | 4.8531 | 5.3989 | 1.0593 | 2.0908 | 2.5089 | 2.5089 | 2.5089 | 2.5089 | 1.3146 | 1.5293 | 1.5293 | 1.5293 | 1.5293 | 1.5293
2020-10-08 11:00 | Summer | 2.2482 | 3.2175 | 4.643 | 4.643 | 4.643 | 4.643 | 0.85736 | 1.403 | 1.9226 | 2.3123 | 2.3123 | 2.3123 | 2.6674 | 3.4422 | 3.9498 | 4.217 | 4.7513 | 5.2857 | 0.9069 | 1.7899 | 2.1479 | 2.1479 | 2.1479 | 2.1479 | 1.3146 | 1.5293 | 1.5293 | 1.5293 | 1.5293 | 1.5293
2020-10-08 12:00 | Summer | 2.3244 | 3.3266 | 4.8004 | 4.8004 | 4.8004 | 4.8004 | 0.85736 | 1.403 | 1.9226 | 2.3123 | 2.3123 | 2.3123 | 2.6864 | 3.4668 | 3.978 | 4.2471 | 4.7853 | 5.3234 | 0.88023 | 1.7373 | 2.0847 | 2.0847 | 2.0847 | 2.0847 | 1.3527 | 1.5736 | 1.5736 | 1.5736 | 1.5736 | 1.5736
2020-10-08 13:00 | Summer | 2.3244 | 3.3266 | 4.8004 | 4.8004 | 4.8004 | 4.8004 | 0.93452 | 1.5292 | 2.0956 | 2.5204 | 2.5204 | 2.5204 | 2.7245 | 3.5159 | 4.0344 | 4.3073 | 4.8531 | 5.3989 | 0.91452 | 1.805 | 2.166 | 2.166 | 2.166 | 2.166 | 1.3146 | 1.5293 | 1.5293 | 1.5293 | 1.5293 | 1.5293
2020-10-08 14:00 | Summer | 2.2505 | 3.2208 | 4.6478 | 4.6478 | 4.6478 | 4.6478 | 0.76877 | 1.258 | 1.7239 | 2.0733 | 2.0733 | 2.0733 | 2.6293 | 3.393 | 3.8934 | 4.1567 | 4.6835 | 5.2102 | 0.84593 | 1.6696 | 2.0035 | 2.0035 | 2.0035 | 2.0035 | 1.2956 | 1.5071 | 1.5071 | 1.5071 | 1.5071 | 1.5071
2020-10-08 15:00 | Summer | 2.2863 | 3.2721 | 4.7217 | 4.7217 | 4.7217 | 4.7217 | 0.85165 | 1.3936 | 1.9098 | 2.2969 | 2.2969 | 2.2969 | 2.5721 | 3.3192 | 3.8087 | 4.0664 | 4.5816 | 5.0969 | 0.86498 | 1.7072 | 2.0486 | 2.0486 | 2.0486 | 2.0486 | 1.3337 | 1.5514 | 1.5514 | 1.5514 | 1.5514 | 1.5514
2020-10-08 16:00 | Summer | 2.1987 | 3.1466 | 4.5407 | 4.5407 | 4.5407 | 4.5407 | 0.87451 | 1.431 | 1.961 | 2.3585 | 2.3585 | 2.3585 | 2.4959 | 3.2209 | 3.6959 | 3.9459 | 4.4459 | 4.9459 | 0.89547 | 1.7674 | 2.1208 | 2.1208 | 2.1208 | 2.1208 | 1.2575 | 1.4628 | 1.4628 | 1.4628 | 1.4628 | 1.4628
2020-10-08 17:00 | Summer | 2.0134 | 2.8815 | 4.1581 | 4.1581 | 4.1581 | 4.1581 | 0.8345 | 1.3655 | 1.8713 | 2.2506 | 2.2506 | 2.2506 | 2.4387 | 3.1471 | 3.6112 | 3.8555 | 4.3441 | 4.8326 | 0.7964 | 1.5718 | 1.8862 | 1.8862 | 1.8862 | 1.8862 | 1.1241 | 1.3076 | 1.3076 | 1.3076 | 1.3076 | 1.3076
2020-10-08 18:00 | Summer | 1.5939 | 2.2811 | 3.2917 | 3.2917 | 3.2917 | 3.2917 | 0.57729 | 0.94465 | 1.2945 | 1.5569 | 1.5569 | 1.5569 | 2.191 | 2.8275 | 3.2445 | 3.4639 | 3.9029 | 4.3418 | 0.77353 | 1.5267 | 1.832 | 1.832 | 1.832 | 1.832 | 0.86108 | 1.0017 | 1.0017 | 1.0017 | 1.0017 | 1.0017
2020-10-08 19:00 | Summer | 1.1622 | 1.6633 | 2.4002 | 2.4002 | 2.4002 | 2.4002 | 0.46583 | 0.76227 | 1.0446 | 1.2563 | 1.2563 | 1.2563 | 2.1148 | 2.7291 | 3.1316 | 3.3435 | 3.7671 | 4.1908 | 0.78877 | 1.5568 | 1.8681 | 1.8681 | 1.8681 | 1.8681 | 0.68589 | 0.79787 | 0.79787 | 0.79787 | 0.79787 | 0.79787
2020-10-08 20:00 | Summer | 1.105 | 1.5815 | 2.2822 | 2.2822 | 2.2822 | 2.2822 | 0.57157 | 0.9353 | 1.2817 | 1.5415 | 1.5415 | 1.5415 | 2.1339 | 2.7537 | 3.1598 | 3.3736 | 3.8011 | 4.2285 | 0.78115 | 1.5417 | 1.8501 | 1.8501 | 1.8501 | 1.8501 | 0.64779 | 0.75355 | 0.75355 | 0.75355 | 0.75355 | 0.75355
2020-10-08 21:00 | Summer | 1.0479 | 1.4997 | 2.1641 | 2.1641 | 2.1641 | 2.1641 | 0.51442 | 0.84177 | 1.1535 | 1.3874 | 1.3874 | 1.3874 | 1.9857 | 2.5625 | 2.9404 | 3.1393 | 3.537 | 3.9348 | 0.78115 | 1.5417 | 1.8501 | 1.8501 | 1.8501 | 1.8501 | 0.57158 | 0.6649 | 0.6649 | 0.6649 | 0.6649 | 0.6649
2020-10-08 22:00 | Summer | 1.0479 | 1.4997 | 2.1641 | 2.1641 | 2.1641 | 2.1641 | 0.47441 | 0.7763 | 1.0638 | 1.2795 | 1.2795 | 1.2795 | 1.8862 | 2.4341 | 2.7931 | 2.982 | 3.3599 | 3.7377 | 0.70494 | 1.3913 | 1.6696 | 1.6696 | 1.6696 | 1.6696 | 0.51364 | 0.5975 | 0.5975 | 0.5975 | 0.5975 | 0.5975
2020-10-08 23:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.30873 | 0.50519 | 0.69229 | 0.83262 | 0.83262 | 0.83262 | 1.7528 | 2.262 | 2.5956 | 2.7712 | 3.1223 | 3.4734 | 0.66303 | 1.3086 | 1.5703 | 1.5703 | 1.5703 | 1.5703 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-10-09 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.2915 | 0.477 | 0.65367 | 0.78617 | 0.78617 | 0.78617 | 1.6385 | 2.1145 | 2.4263 | 2.5904 | 2.9187 | 3.2469 | 0.57539 | 1.1356 | 1.3628 | 1.3628 | 1.3628 | 1.3628 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-10-09 01:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.32004 | 0.52369 | 0.71766 | 0.86313 | 0.86313 | 0.86313 | 1.5436 | 1.992 | 2.2858 | 2.4404 | 2.7496 | 3.0589 | 0.59444 | 1.1732 | 1.4079 | 1.4079 | 1.4079 | 1.4079 | 0.45745 | 0.53213 | 0.53213 | 0.53213 | 0.53213 | 0.53213
2020-10-09 02:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.34866 | 0.57053 | 0.78184 | 0.94032 | 0.94032 | 0.94032 | 1.5433 | 1.9915 | 2.2852 | 2.4398 | 2.749 | 3.0581 | 0.56014 | 1.1055 | 1.3267 | 1.3267 | 1.3267 | 1.3267 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-10-09 03:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.40582 | 0.66406 | 0.91001 | 1.0945 | 1.0945 | 1.0945 | 1.5231 | 1.9655 | 2.2553 | 2.4079 | 2.713 | 3.0181 | 0.54871 | 1.083 | 1.2996 | 1.2996 | 1.2996 | 1.2996 | 0.45682 | 0.5314 | 0.5314 | 0.5314 | 0.5314 | 0.5314
2020-10-09 04:00 | Summer | 1.0857 | 1.5538 | 2.2422 | 2.2422 | 2.2422 | 2.2422 | 0.49155 | 0.80436 | 1.1023 | 1.3257 | 1.3257 | 1.3257 | 1.57 | 2.0261 | 2.3249 | 2.4821 | 2.7967 | 3.1112 | 0.52966 | 1.0454 | 1.2545 | 1.2545 | 1.2545 | 1.2545 | 0.53347 | 0.62057 | 0.62057 | 0.62057 | 0.62057 | 0.62057
2020-10-09 05:00 | Summer | 1.2388 | 1.7729 | 2.5583 | 2.5583 | 2.5583 | 2.5583 | 0.43154 | 0.70615 | 0.96769 | 1.1638 | 1.1638 | 1.1638 | 1.7338 | 2.2374 | 2.5674 | 2.741 | 3.0884 | 3.4357 | 0.58301 | 1.1507 | 1.3808 | 1.3808 | 1.3808 | 1.3808 | 0.59372 | 0.69065 | 0.69065 | 0.69065 | 0.69065 | 0.69065
2020-10-09 06:00 | Summer | 1.335 | 1.9106 | 2.7571 | 2.7571 | 2.7571 | 2.7571 | 0.61158 | 1.0008 | 1.3714 | 1.6494 | 1.6494 | 1.6494 | 1.7909 | 2.3112 | 2.652 | 2.8314 | 3.1902 | 3.549 | 0.69732 | 1.3763 | 1.6516 | 1.6516 | 1.6516 | 1.6516 | 0.83831 | 0.97518 | 0.97518 | 0.97518 | 0.97518 | 0.97518
2020-10-09 07:00 | Summer | 1.7685 | 2.5311 | 3.6524 | 3.6524 | 3.6524 | 3.6524 | 0.81164 | 1.3281 | 1.82 | 2.189 | 2.189 | 2.189 | 2.1339 | 2.7537 | 3.1598 | 3.3736 | 3.8011 | 4.2285 | 0.8935 | 1.7635 | 2.1162 | 2.1162 | 2.1162 | 2.1162 | 0.99073 | 1.1525 | 1.1525 | 1.1525 | 1.1525 | 1.1525
2020-10-09 08:00 | Summer | 2.0386 | 2.9176 | 4.2102 | 4.2102 | 4.2102 | 4.2102 | 0.83164 | 1.3609 | 1.8649 | 2.2429 | 2.2429 | 2.2429 | 2.3625 | 3.0488 | 3.4984 | 3.735 | 4.2083 | 4.6816 | 0.90309 | 1.7824 | 2.1389 | 2.1389 | 2.1389 | 2.1389 | 1.2003 | 1.3963 | 1.3963 | 1.3963 | 1.3963 | 1.3963
2020-10-09 09:00 | Summer | 2.0958 | 2.9994 | 4.3282 | 4.3282 | 4.3282 | 4.3282 | 0.88308 | 1.445 | 1.9802 | 2.3816 | 2.3816 | 2.3816 | 2.5149 | 3.2455 | 3.7241 | 3.976 | 4.4798 | 4.9836 | 0.89166 | 1.7599 | 2.1118 | 2.1118 | 2.1118 | 2.1118 | 1.3146 | 1.5293 | 1.5293 | 1.5293 | 1.5293 | 1.5293
2020-10-09 10:00 | Summer | 2.0767 | 2.9721 | 4.2889 | 4.2889 | 4.2889 | 4.2889 | 0.86308 | 1.4123 | 1.9354 | 2.3277 | 2.3277 | 2.3277 | 2.5241 | 3.2572 | 3.7376 | 3.9904 | 4.4961 | 5.0017 | 0.86879 | 1.7147 | 2.0577 | 2.0577 | 2.0577 | 2.0577 | 1.2956 | 1.5071 | 1.5071 | 1.5071 | 1.5071 | 1.5071
2020-10-09 11:00 | Summer | 2.0577 | 2.9449 | 4.2495 | 4.2495 | 4.2495 | 4.2495 | 0.85736 | 1.403 | 1.9226 | 2.3123 | 2.3123 | 2.3123 | 2.553 | 3.2946 | 3.7805 | 4.0362 | 4.5477 | 5.0591 | 0.83831 | 1.6546 | 1.9855 | 1.9855 | 1.9855 | 1.9855 | 1.3337 | 1.5514 | 1.5514 | 1.5514 | 1.5514 | 1.5514
2020-10-09 12:00 | Summer | 2.1196 | 3.0334 | 4.3774 | 4.3774 | 4.3774 | 4.3774 | 0.88356 | 1.4458 | 1.9813 | 2.3829 | 2.3829 | 2.3829 | 2.6483 | 3.4176 | 3.9216 | 4.1869 | 4.7174 | 5.2479 | 0.84593 | 1.6696 | 2.0035 | 2.0035 | 2.0035 | 2.0035 | 1.2956 | 1.5071 | 1.5071 | 1.5071 | 1.5071 | 1.5071
2020-10-09 13:00 | Summer | 2.172 | 3.1085 | 4.4856 | 4.4856 | 4.4856 | 4.4856 | 0.89451 | 1.4638 | 2.0059 | 2.4125 | 2.4125 | 2.4125 | 2.6102 | 3.3684 | 3.8652 | 4.1266 | 4.6495 | 5.1724 | 0.85355 | 1.6846 | 2.0216 | 2.0216 | 2.0216 | 2.0216 | 1.2575 | 1.4628 | 1.4628 | 1.4628 | 1.4628 | 1.4628
2020-10-09 14:00 | Summer | 2.0716 | 2.9647 | 4.2782 | 4.2782 | 4.2782 | 4.2782 | 0.84593 | 1.3842 | 1.8969 | 2.2814 | 2.2814 | 2.2814 | 2.5149 | 3.2455 | 3.7241 | 3.976 | 4.4798 | 4.9836 | 0.86117 | 1.6997 | 2.0396 | 2.0396 | 2.0396 | 2.0396 | 1.1813 | 1.3741 | 1.3741 | 1.3741 | 1.3741 | 1.3741
2020-10-09 15:00 | Summer | 1.9815 | 2.8358 | 4.0922 | 4.0922 | 4.0922 | 4.0922 | 0.80878 | 1.3235 | 1.8136 | 2.1812 | 2.1812 | 2.1812 | 2.4768 | 3.1963 | 3.6677 | 3.9158 | 4.4119 | 4.9081 | 0.84974 | 1.6771 | 2.0125 | 2.0125 | 2.0125 | 2.0125 | 1.1241 | 1.3076 | 1.3076 | 1.3076 | 1.3076 | 1.3076
2020-10-09 16:00 | Summer | 1.8862 | 2.6995 | 3.8954 | 3.8954 | 3.8954 | 3.8954 | 0.81449 | 1.3328 | 1.8264 | 2.1967 | 2.1967 | 2.1967 | 2.4578 | 3.1717 | 3.6395 | 3.8856 | 4.378 | 4.8704 | 0.82307 | 1.6245 | 1.9494 | 1.9494 | 1.9494 | 1.9494 | 1.1241 | 1.3076 | 1.3076 | 1.3076 | 1.3076 | 1.3076
2020-10-09 17:00 | Summer | 1.7528 | 2.5086 | 3.62 | 3.62 | 3.62 | 3.62 | 0.73733 | 1.2065 | 1.6534 | 1.9886 | 1.9886 | 1.9886 | 2.3054 | 2.975 | 3.4138 | 3.6447 | 4.1065 | 4.5683 | 0.82688 | 1.632 | 1.9584 | 1.9584 | 1.9584 | 1.9584 | 1.086 | 1.2633 | 1.2633 | 1.2633 | 1.2633 | 1.2633
2020-10-09 18:00 | Summer | 1.5196 | 2.1748 | 3.1383 | 3.1383 | 3.1383 | 3.1383 | 0.6373 | 1.0429 | 1.4291 | 1.7188 | 1.7188 | 1.7188 | 2.172 | 2.8029 | 3.2163 | 3.4338 | 3.8689 | 4.3041 | 0.7964 | 1.5718 | 1.8862 | 1.8862 | 1.8862 | 1.8862 | 0.81731 | 0.95075 | 0.95075 | 0.95075 | 0.95075 | 0.95075
2020-10-09 19:00 | Summer | 1.086 | 1.5542 | 2.2428 | 2.2428 | 2.2428 | 2.2428 | 0.54416 | 0.89045 | 1.2202 | 1.4676 | 1.4676 | 1.4676 | 2.1529 | 2.7783 | 3.1881 | 3.4037 | 3.835 | 4.2663 | 0.78877 | 1.5568 | 1.8681 | 1.8681 | 1.8681 | 1.8681 | 0.59494 | 0.69208 | 0.69208 | 0.69208 | 0.69208 | 0.69208
2020-10-09 20:00 | Summer | 1.0669 | 1.527 | 2.2035 | 2.2035 | 2.2035 | 2.2035 | 0.5087 | 0.83242 | 1.1407 | 1.3719 | 1.3719 | 1.3719 | 2.0987 | 2.7084 | 3.1078 | 3.318 | 3.7384 | 4.1589 | 0.78877 | 1.5568 | 1.8681 | 1.8681 | 1.8681 | 1.8681 | 0.60968 | 0.70922 | 0.70922 | 0.70922 | 0.70922 | 0.70922
2020-10-09 21:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.50013 | 0.81839 | 1.1215 | 1.3488 | 1.3488 | 1.3488 | 2.0386 | 2.6308 | 3.0188 | 3.223 | 3.6314 | 4.0398 | 0.78115 | 1.5417 | 1.8501 | 1.8501 | 1.8501 | 1.8501 | 0.55252 | 0.64273 | 0.64273 | 0.64273 | 0.64273 | 0.64273
2020-10-09 22:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.47155 | 0.77162 | 1.0574 | 1.2717 | 1.2717 | 1.2717 | 1.9053 | 2.4587 | 2.8213 | 3.0121 | 3.3938 | 3.7755 | 0.75829 | 1.4966 | 1.796 | 1.796 | 1.796 | 1.796 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-10-09 23:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.37668 | 0.61638 | 0.84467 | 1.0159 | 1.0159 | 1.0159 | 1.81 | 2.3358 | 2.6802 | 2.8615 | 3.2241 | 3.5867 | 0.69732 | 1.3763 | 1.6516 | 1.6516 | 1.6516 | 1.6516 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-10-10 | Summer | 0.94991 | 1.3595 | 1.9618 | 1.9618 | 1.9618 | 1.9618 | 0.31722 | 0.51909 | 0.71134 | 0.85554 | 0.85554 | 0.85554 | 1.6957 | 2.1882 | 2.5109 | 2.6808 | 3.0205 | 3.3602 | 0.62111 | 1.2259 | 1.4711 | 1.4711 | 1.4711 | 1.4711 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-10-10 01:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.30576 | 0.50034 | 0.68565 | 0.82463 | 0.82463 | 0.82463 | 1.5718 | 2.0284 | 2.3276 | 2.485 | 2.7999 | 3.1148 | 0.59825 | 1.1808 | 1.4169 | 1.4169 | 1.4169 | 1.4169 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-10-10 02:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.36009 | 0.58924 | 0.80747 | 0.97115 | 0.97115 | 0.97115 | 1.5814 | 2.0407 | 2.3417 | 2.5001 | 2.8169 | 3.1337 | 0.5449 | 1.0755 | 1.2906 | 1.2906 | 1.2906 | 1.2906 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-10-10 03:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.42011 | 0.68744 | 0.94205 | 1.133 | 1.133 | 1.133 | 1.4861 | 1.9178 | 2.2006 | 2.3495 | 2.6472 | 2.9449 | 0.55252 | 1.0905 | 1.3086 | 1.3086 | 1.3086 | 1.3086 | 0.43752 | 0.50896 | 0.50896 | 0.50896 | 0.50896 | 0.50896
2020-10-10 04:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.33707 | 0.55157 | 0.75585 | 0.90906 | 0.90906 | 0.90906 | 1.5529 | 2.0039 | 2.2995 | 2.455 | 2.7661 | 3.0772 | 0.5449 | 1.0755 | 1.2906 | 1.2906 | 1.2906 | 1.2906 | 0.43821 | 0.50975 | 0.50975 | 0.50975 | 0.50975 | 0.50975
2020-10-10 05:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.46869 | 0.76695 | 1.051 | 1.264 | 1.264 | 1.264 | 1.6195 | 2.0899 | 2.3981 | 2.5603 | 2.8847 | 3.2092 | 0.53728 | 1.0604 | 1.2725 | 1.2725 | 1.2725 | 1.2725 | 0.43821 | 0.50975 | 0.50975 | 0.50975 | 0.50975 | 0.50975
2020-10-10 06:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.51442 | 0.84177 | 1.1535 | 1.3874 | 1.3874 | 1.3874 | 1.6766 | 2.1636 | 2.4827 | 2.6507 | 2.9865 | 3.3224 | 0.5792 | 1.1431 | 1.3718 | 1.3718 | 1.3718 | 1.3718 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-10-10 07:00 | Summer | 1.0072 | 1.4415 | 2.0801 | 2.0801 | 2.0801 | 2.0801 | 0.54585 | 0.89321 | 1.224 | 1.4721 | 1.4721 | 1.4721 | 1.7856 | 2.3043 | 2.6441 | 2.823 | 3.1807 | 3.5384 | 0.58682 | 1.1582 | 1.3898 | 1.3898 | 1.3898 | 1.3898 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-10-10 08:00 | Summer | 1.0479 | 1.4997 | 2.1641 | 2.1641 | 2.1641 | 2.1641 | 0.59444 | 0.97271 | 1.333 | 1.6032 | 1.6032 | 1.6032 | 1.9434 | 2.5079 | 2.8777 | 3.0724 | 3.4617 | 3.851 | 0.68208 | 1.3462 | 1.6155 | 1.6155 | 1.6155 | 1.6155 | 0.57158 | 0.6649 | 0.6649 | 0.6649 | 0.6649 | 0.6649
2020-10-10 09:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.57443 | 0.93998 | 1.2881 | 1.5492 | 1.5492 | 1.5492 | 2.0005 | 2.5816 | 2.9624 | 3.1627 | 3.5635 | 3.9643 | 0.73543 | 1.4515 | 1.7418 | 1.7418 | 1.7418 | 1.7418 | 0.55252 | 0.64273 | 0.64273 | 0.64273 | 0.64273 | 0.64273
2020-10-10 10:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.55728 | 0.91192 | 1.2497 | 1.503 | 1.503 | 1.503 | 1.9624 | 2.5325 | 2.9059 | 3.1025 | 3.4956 | 3.8887 | 0.69351 | 1.3688 | 1.6425 | 1.6425 | 1.6425 | 1.6425 | 0.57158 | 0.6649 | 0.6649 | 0.6649 | 0.6649 | 0.6649
2020-10-10 11:00 | Summer | 0.91452 | 1.3088 | 1.8887 | 1.8887 | 1.8887 | 1.8887 | 0.52299 | 0.8558 | 1.1728 | 1.4105 | 1.4105 | 1.4105 | 2.0958 | 2.7046 | 3.1034 | 3.3133 | 3.7332 | 4.153 | 0.67446 | 1.3312 | 1.5974 | 1.5974 | 1.5974 | 1.5974 | 0.59063 | 0.68706 | 0.68706 | 0.68706 | 0.68706 | 0.68706
2020-10-10 12:00 | Summer | 1.0479 | 1.4997 | 2.1641 | 2.1641 | 2.1641 | 2.1641 | 0.5287 | 0.86515 | 1.1856 | 1.4259 | 1.4259 | 1.4259 | 2.0577 | 2.6554 | 3.047 | 3.2531 | 3.6653 | 4.0775 | 0.6516 | 1.286 | 1.5433 | 1.5433 | 1.5433 | 1.5433 | 0.53347 | 0.62057 | 0.62057 | 0.62057 | 0.62057 | 0.62057
2020-10-10 13:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.48869 | 0.79968 | 1.0959 | 1.318 | 1.318 | 1.318 | 2.0577 | 2.6554 | 3.047 | 3.2531 | 3.6653 | 4.0775 | 0.60587 | 1.1958 | 1.435 | 1.435 | 1.435 | 1.435 | 0.53347 | 0.62057 | 0.62057 | 0.62057 | 0.62057 | 0.62057
2020-10-10 14:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.46297 | 0.75759 | 1.0382 | 1.2486 | 1.2486 | 1.2486 | 2.0386 | 2.6308 | 3.0188 | 3.223 | 3.6314 | 4.0398 | 0.65922 | 1.3011 | 1.5613 | 1.5613 | 1.5613 | 1.5613 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-10-10 15:00 | Summer | 1.0479 | 1.4997 | 2.1641 | 2.1641 | 2.1641 | 2.1641 | 0.5287 | 0.86515 | 1.1856 | 1.4259 | 1.4259 | 1.4259 | 2.0005 | 2.5816 | 2.9624 | 3.1627 | 3.5635 | 3.9643 | 0.76591 | 1.5117 | 1.814 | 1.814 | 1.814 | 1.814 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-10-10 16:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.5087 | 0.83242 | 1.1407 | 1.3719 | 1.3719 | 1.3719 | 2.0767 | 2.68 | 3.0752 | 3.2832 | 3.6992 | 4.1153 | 0.74686 | 1.4741 | 1.7689 | 1.7689 | 1.7689 | 1.7689 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-10-10 17:00 | Summer | 1.0479 | 1.4997 | 2.1641 | 2.1641 | 2.1641 | 2.1641 | 0.53353 | 0.87305 | 1.1964 | 1.4389 | 1.4389 | 1.4389 | 2.0196 | 2.6062 | 2.9906 | 3.1929 | 3.5974 | 4.002 | 0.72018 | 1.4214 | 1.7057 | 1.7057 | 1.7057 | 1.7057 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-10-10 18:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.53442 | 0.87451 | 1.1984 | 1.4413 | 1.4413 | 1.4413 | 1.8862 | 2.4341 | 2.7931 | 2.982 | 3.3599 | 3.7377 | 0.85355 | 1.6846 | 2.0216 | 2.0216 | 2.0216 | 2.0216 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-10-10 19:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.52013 | 0.85112 | 1.1664 | 1.4028 | 1.4028 | 1.4028 | 1.9815 | 2.557 | 2.9341 | 3.1326 | 3.5296 | 3.9265 | 0.76591 | 1.5117 | 1.814 | 1.814 | 1.814 | 1.814 | 0.53347 | 0.62057 | 0.62057 | 0.62057 | 0.62057 | 0.62057
2020-10-10 20:00 | Summer | 0.95331 | 1.3643 | 1.9688 | 1.9688 | 1.9688 | 1.9688 | 0.51156 | 0.83709 | 1.1471 | 1.3797 | 1.3797 | 1.3797 | 1.9434 | 2.5079 | 2.8777 | 3.0724 | 3.4617 | 3.851 | 0.81545 | 1.6094 | 1.9313 | 1.9313 | 1.9313 | 1.9313 | 0.55252 | 0.64273 | 0.64273 | 0.64273 | 0.64273 | 0.64273
2020-10-10 21:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.48298 | 0.79033 | 1.083 | 1.3026 | 1.3026 | 1.3026 | 1.9053 | 2.4587 | 2.8213 | 3.0121 | 3.3938 | 3.7755 | 0.75829 | 1.4966 | 1.796 | 1.796 | 1.796 | 1.796 | 0.53347 | 0.62057 | 0.62057 | 0.62057 | 0.62057 | 0.62057
2020-10-10 22:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.35437 | 0.57988 | 0.79466 | 0.95574 | 0.95574 | 0.95574 | 1.8481 | 2.3849 | 2.7366 | 2.9218 | 3.292 | 3.6622 | 0.81926 | 1.617 | 1.9403 | 1.9403 | 1.9403 | 1.9403 | 0.51552 | 0.59969 | 0.59969 | 0.59969 | 0.59969 | 0.59969
2020-10-10 23:00 | Summer | 0.94902 | 1.3582 | 1.9599 | 1.9599 | 1.9599 | 1.9599 | 0.35437 | 0.57988 | 0.79466 | 0.95574 | 0.95574 | 0.95574 | 1.7528 | 2.262 | 2.5956 | 2.7712 | 3.1223 | 3.4734 | 0.72018 | 1.4214 | 1.7057 | 1.7057 | 1.7057 | 1.7057 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-10-11 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.3201 | 0.52381 | 0.71781 | 0.86331 | 0.86331 | 0.86331 | 1.6695 | 2.1544 | 2.4722 | 2.6394 | 2.9738 | 3.3083 | 0.724 | 1.4289 | 1.7147 | 1.7147 | 1.7147 | 1.7147 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-10-11 01:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.44011 | 0.72018 | 0.98691 | 1.187 | 1.187 | 1.187 | 1.5433 | 1.9915 | 2.2852 | 2.4398 | 2.749 | 3.0581 | 0.5792 | 1.1431 | 1.3718 | 1.3718 | 1.3718 | 1.3718 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-10-11 02:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.32295 | 0.52847 | 0.7242 | 0.871 | 0.871 | 0.871 | 1.5052 | 1.9424 | 2.2288 | 2.3796 | 2.6811 | 2.9826 | 0.54871 | 1.083 | 1.2996 | 1.2996 | 1.2996 | 1.2996 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-10-11 03:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.43154 | 0.70615 | 0.96769 | 1.1638 | 1.1638 | 1.1638 | 1.5242 | 1.967 | 2.257 | 2.4097 | 2.715 | 3.0204 | 0.55633 | 1.098 | 1.3176 | 1.3176 | 1.3176 | 1.3176 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-10-11 04:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.33722 | 0.55181 | 0.75618 | 0.90946 | 0.90946 | 0.90946 | 1.5052 | 1.9424 | 2.2288 | 2.3796 | 2.6811 | 2.9826 | 0.54109 | 1.0679 | 1.2815 | 1.2815 | 1.2815 | 1.2815 | 0.4385 | 0.5101 | 0.5101 | 0.5101 | 0.5101 | 0.5101
2020-10-11 05:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.42582 | 0.6968 | 0.95487 | 1.1484 | 1.1484 | 1.1484 | 1.6004 | 2.0653 | 2.3699 | 2.5302 | 2.8508 | 3.1714 | 0.55633 | 1.098 | 1.3176 | 1.3176 | 1.3176 | 1.3176 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-10-11 06:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.45726 | 0.74824 | 1.0254 | 1.2332 | 1.2332 | 1.2332 | 1.6195 | 2.0899 | 2.3981 | 2.5603 | 2.8847 | 3.2092 | 0.56395 | 1.1131 | 1.3357 | 1.3357 | 1.3357 | 1.3357 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-10-11 07:00 | Summer | 0.91452 | 1.3088 | 1.8887 | 1.8887 | 1.8887 | 1.8887 | 0.48869 | 0.79968 | 1.0959 | 1.318 | 1.318 | 1.318 | 1.7625 | 2.2744 | 2.6098 | 2.7864 | 3.1395 | 3.4925 | 0.5792 | 1.1431 | 1.3718 | 1.3718 | 1.3718 | 1.3718 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-10-11 08:00 | Summer | 0.89547 | 1.2816 | 1.8493 | 1.8493 | 1.8493 | 1.8493 | 0.45726 | 0.74824 | 1.0254 | 1.2332 | 1.2332 | 1.2332 | 1.9624 | 2.5325 | 2.9059 | 3.1025 | 3.4956 | 3.8887 | 0.68589 | 1.3537 | 1.6245 | 1.6245 | 1.6245 | 1.6245 | 0.47619 | 0.55394 | 0.55394 | 0.55394 | 0.55394 | 0.55394
2020-10-11 09:00 | Summer | 0.85737 | 1.227 | 1.7706 | 1.7706 | 1.7706 | 1.7706 | 0.54871 | 0.89789 | 1.2304 | 1.4799 | 1.4799 | 1.4799 | 1.9815 | 2.557 | 2.9341 | 3.1326 | 3.5296 | 3.9265 | 0.63254 | 1.2484 | 1.4981 | 1.4981 | 1.4981 | 1.4981 | 0.53316 | 0.62021 | 0.62021 | 0.62021 | 0.62021 | 0.62021
2020-10-11 10:00 | Summer | 0.85737 | 1.227 | 1.7706 | 1.7706 | 1.7706 | 1.7706 | 0.48012 | 0.78565 | 1.0766 | 1.2949 | 1.2949 | 1.2949 | 2.0386 | 2.6308 | 3.0188 | 3.223 | 3.6314 | 4.0398 | 0.73924 | 1.459 | 1.7508 | 1.7508 | 1.7508 | 1.7508 | 0.55252 | 0.64273 | 0.64273 | 0.64273 | 0.64273 | 0.64273
2020-10-11 11:00 | Summer | 0.89547 | 1.2816 | 1.8493 | 1.8493 | 1.8493 | 1.8493 | 0.4001 | 0.65471 | 0.89719 | 1.0791 | 1.0791 | 1.0791 | 2.0767 | 2.68 | 3.0752 | 3.2832 | 3.6992 | 4.1153 | 0.60968 | 1.2033 | 1.444 | 1.444 | 1.444 | 1.444 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-10-11 12:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.40867 | 0.66874 | 0.91642 | 1.1022 | 1.1022 | 1.1022 | 2.1148 | 2.7291 | 3.1316 | 3.3435 | 3.7671 | 4.1908 | 0.59444 | 1.1732 | 1.4079 | 1.4079 | 1.4079 | 1.4079 | 0.53347 | 0.62057 | 0.62057 | 0.62057 | 0.62057 | 0.62057
2020-10-11 13:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.38581 | 0.63133 | 0.86515 | 1.0405 | 1.0405 | 1.0405 | 2.0969 | 2.706 | 3.1051 | 3.3152 | 3.7352 | 4.1553 | 0.67017 | 1.3227 | 1.5872 | 1.5872 | 1.5872 | 1.5872 | 0.62873 | 0.73138 | 0.73138 | 0.73138 | 0.73138 | 0.73138
2020-10-11 14:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.41153 | 0.67342 | 0.92283 | 1.1099 | 1.1099 | 1.1099 | 2.1529 | 2.7783 | 3.1881 | 3.4037 | 3.835 | 4.2663 | 0.67065 | 1.3236 | 1.5884 | 1.5884 | 1.5884 | 1.5884 | 0.57158 | 0.6649 | 0.6649 | 0.6649 | 0.6649 | 0.6649
2020-10-11 15:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.47726 | 0.78098 | 1.0702 | 1.2872 | 1.2872 | 1.2872 | 2.1148 | 2.7291 | 3.1316 | 3.3435 | 3.7671 | 4.1908 | 0.63254 | 1.2484 | 1.4981 | 1.4981 | 1.4981 | 1.4981 | 0.50914 | 0.59226 | 0.59226 | 0.59226 | 0.59226 | 0.59226
2020-10-11 16:00 | Summer | 1.0479 | 1.4997 | 2.1641 | 2.1641 | 2.1641 | 2.1641 | 0.46012 | 0.75292 | 1.0318 | 1.2409 | 1.2409 | 1.2409 | 2.1529 | 2.7783 | 3.1881 | 3.4037 | 3.835 | 4.2663 | 0.84974 | 1.6771 | 2.0125 | 2.0125 | 2.0125 | 2.0125 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-10-11 17:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.47441 | 0.7763 | 1.0638 | 1.2795 | 1.2795 | 1.2795 | 2.0526 | 2.6489 | 3.0395 | 3.2451 | 3.6563 | 4.0675 | 0.63254 | 1.2484 | 1.4981 | 1.4981 | 1.4981 | 1.4981 | 0.53347 | 0.62057 | 0.62057 | 0.62057 | 0.62057 | 0.62057
2020-10-11 18:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.43154 | 0.70615 | 0.96769 | 1.1638 | 1.1638 | 1.1638 | 1.9182 | 2.4754 | 2.8404 | 3.0325 | 3.4168 | 3.8011 | 0.67827 | 1.3387 | 1.6064 | 1.6064 | 1.6064 | 1.6064 | 0.53347 | 0.62057 | 0.62057 | 0.62057 | 0.62057 | 0.62057
2020-10-11 19:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.44297 | 0.72486 | 0.99332 | 1.1947 | 1.1947 | 1.1947 | 1.9624 | 2.5325 | 2.9059 | 3.1025 | 3.4956 | 3.8887 | 0.81164 | 1.6019 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 0.51145 | 0.59495 | 0.59495 | 0.59495 | 0.59495 | 0.59495
2020-10-11 20:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.42868 | 0.70147 | 0.96128 | 1.1561 | 1.1561 | 1.1561 | 1.9624 | 2.5325 | 2.9059 | 3.1025 | 3.4956 | 3.8887 | 0.75067 | 1.4816 | 1.7779 | 1.7779 | 1.7779 | 1.7779 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-10-11 21:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.41439 | 0.67809 | 0.92924 | 1.1176 | 1.1176 | 1.1176 | 1.9053 | 2.4587 | 2.8213 | 3.0121 | 3.3938 | 3.7755 | 0.70875 | 1.3989 | 1.6786 | 1.6786 | 1.6786 | 1.6786 | 0.55252 | 0.64273 | 0.64273 | 0.64273 | 0.64273 | 0.64273
2020-10-11 22:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.38581 | 0.63133 | 0.86515 | 1.0405 | 1.0405 | 1.0405 | 1.7909 | 2.3112 | 2.652 | 2.8314 | 3.1902 | 3.549 | 0.72781 | 1.4365 | 1.7238 | 1.7238 | 1.7238 | 1.7238 | 0.5007 | 0.58244 | 0.58244 | 0.58244 | 0.58244 | 0.58244
2020-10-11 23:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.35152 | 0.57521 | 0.78825 | 0.94803 | 0.94803 | 0.94803 | 1.6576 | 2.1391 | 2.4545 | 2.6205 | 2.9526 | 3.2847 | 0.65541 | 1.2936 | 1.5523 | 1.5523 | 1.5523 | 1.5523 | 0.5142 | 0.59815 | 0.59815 | 0.59815 | 0.59815 | 0.59815
2020-10-12 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.36581 | 0.59859 | 0.82029 | 0.98657 | 0.98657 | 0.98657 | 1.5814 | 2.0407 | 2.3417 | 2.5001 | 2.8169 | 3.1337 | 0.59063 | 1.1657 | 1.3989 | 1.3989 | 1.3989 | 1.3989 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-10-12 01:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.30862 | 0.50502 | 0.69207 | 0.83235 | 0.83235 | 0.83235 | 1.5242 | 1.967 | 2.257 | 2.4097 | 2.715 | 3.0204 | 0.57539 | 1.1356 | 1.3628 | 1.3628 | 1.3628 | 1.3628 | 0.47499 | 0.55254 | 0.55254 | 0.55254 | 0.55254 | 0.55254
2020-10-12 02:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.30865 | 0.50506 | 0.69212 | 0.83241 | 0.83241 | 0.83241 | 1.4861 | 1.9178 | 2.2006 | 2.3495 | 2.6472 | 2.9449 | 0.57157 | 1.1281 | 1.3537 | 1.3537 | 1.3537 | 1.3537 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-10-12 03:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.41725 | 0.68277 | 0.93565 | 1.1253 | 1.1253 | 1.1253 | 1.467 | 1.8932 | 2.1724 | 2.3193 | 2.6132 | 2.9071 | 0.57539 | 1.1356 | 1.3628 | 1.3628 | 1.3628 | 1.3628 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-10-12 04:00 | Summer | 1.1632 | 1.6647 | 2.4022 | 2.4022 | 2.4022 | 2.4022 | 0.41439 | 0.67809 | 0.92924 | 1.1176 | 1.1176 | 1.1176 | 1.5052 | 1.9424 | 2.2288 | 2.3796 | 2.6811 | 2.9826 | 0.56014 | 1.1055 | 1.3267 | 1.3267 | 1.3267 | 1.3267 | 0.52414 | 0.60971 | 0.60971 | 0.60971 | 0.60971 | 0.60971
2020-10-12 05:00 | Summer | 1.2573 | 1.7993 | 2.5965 | 2.5965 | 2.5965 | 2.5965 | 0.47155 | 0.77162 | 1.0574 | 1.2717 | 1.2717 | 1.2717 | 1.6843 | 2.1735 | 2.4941 | 2.6628 | 3.0002 | 3.3376 | 0.63254 | 1.2484 | 1.4981 | 1.4981 | 1.4981 | 1.4981 | 0.62839 | 0.73098 | 0.73098 | 0.73098 | 0.73098 | 0.73098
2020-10-12 06:00 | Summer | 1.506 | 2.1553 | 3.1102 | 3.1102 | 3.1102 | 3.1102 | 0.57443 | 0.93998 | 1.2881 | 1.5492 | 1.5492 | 1.5492 | 1.81 | 2.3358 | 2.6802 | 2.8615 | 3.2241 | 3.5867 | 0.67065 | 1.3236 | 1.5884 | 1.5884 | 1.5884 | 1.5884 | 0.90173 | 1.0489 | 1.0489 | 1.0489 | 1.0489 | 1.0489
2020-10-12 07:00 | Summer | 1.8538 | 2.6531 | 3.8285 | 3.8285 | 3.8285 | 3.8285 | 0.77734 | 1.272 | 1.7431 | 2.0965 | 2.0965 | 2.0965 | 2.1529 | 2.7783 | 3.1881 | 3.4037 | 3.835 | 4.2663 | 0.91452 | 1.805 | 2.166 | 2.166 | 2.166 | 2.166 | 1.0288 | 1.1968 | 1.1968 | 1.1968 | 1.1968 | 1.1968
2020-10-12 08:00 | Summer | 2.2291 | 3.1903 | 4.6037 | 4.6037 | 4.6037 | 4.6037 | 0.76305 | 1.2486 | 1.7111 | 2.0579 | 2.0579 | 2.0579 | 2.4197 | 3.1225 | 3.583 | 3.8254 | 4.3101 | 4.7949 | 0.85736 | 1.6922 | 2.0306 | 2.0306 | 2.0306 | 2.0306 | 1.1813 | 1.3741 | 1.3741 | 1.3741 | 1.3741 | 1.3741
2020-10-12 09:00 | Summer | 2.2863 | 3.2721 | 4.7217 | 4.7217 | 4.7217 | 4.7217 | 0.78306 | 1.2814 | 1.7559 | 2.1119 | 2.1119 | 2.1119 | 2.4959 | 3.2209 | 3.6959 | 3.9459 | 4.4459 | 4.9459 | 0.84212 | 1.6621 | 1.9945 | 1.9945 | 1.9945 | 1.9945 | 1.3337 | 1.5514 | 1.5514 | 1.5514 | 1.5514 | 1.5514
2020-10-12 10:00 | Summer | 2.3816 | 3.4084 | 4.9185 | 4.9185 | 4.9185 | 4.9185 | 0.84593 | 1.3842 | 1.8969 | 2.2814 | 2.2814 | 2.2814 | 2.4768 | 3.1963 | 3.6677 | 3.9158 | 4.4119 | 4.9081 | 0.94882 | 1.8727 | 2.2472 | 2.2472 | 2.2472 | 2.2472 | 1.3313 | 1.5487 | 1.5487 | 1.5487 | 1.5487 | 1.5487
2020-10-12 11:00 | Summer | 2.4197 | 3.4629 | 4.9972 | 4.9972 | 4.9972 | 4.9972 | 0.74305 | 1.2159 | 1.6662 | 2.004 | 2.004 | 2.004 | 2.7347 | 3.529 | 4.0495 | 4.3234 | 4.8712 | 5.419 | 0.78115 | 1.5417 | 1.8501 | 1.8501 | 1.8501 | 1.8501 | 1.3718 | 1.5957 | 1.5957 | 1.5957 | 1.5957 | 1.5957
2020-10-12 12:00 | Summer | 2.4578 | 3.5175 | 5.0759 | 5.0759 | 5.0759 | 5.0759 | 0.74305 | 1.2159 | 1.6662 | 2.004 | 2.004 | 2.004 | 2.8198 | 3.6389 | 4.1755 | 4.4579 | 5.0228 | 5.5877 | 0.81164 | 1.6019 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 1.4099 | 1.6401 | 1.6401 | 1.6401 | 1.6401 | 1.6401
2020-10-12 13:00 | Summer | 2.4197 | 3.4629 | 4.9972 | 4.9972 | 4.9972 | 4.9972 | 0.90595 | 1.4825 | 2.0315 | 2.4433 | 2.4433 | 2.4433 | 2.8198 | 3.6389 | 4.1755 | 4.4579 | 5.0228 | 5.5877 | 0.84593 | 1.6696 | 2.0035 | 2.0035 | 2.0035 | 2.0035 | 1.4056 | 1.6351 | 1.6351 | 1.6351 | 1.6351 | 1.6351
2020-10-12 14:00 | Summer | 2.4768 | 3.5447 | 5.1152 | 5.1152 | 5.1152 | 5.1152 | 0.88308 | 1.445 | 1.9802 | 2.3816 | 2.3816 | 2.3816 | 2.8198 | 3.6389 | 4.1755 | 4.4579 | 5.0228 | 5.5877 | 0.9069 | 1.7899 | 2.1479 | 2.1479 | 2.1479 | 2.1479 | 1.4099 | 1.6401 | 1.6401 | 1.6401 | 1.6401 | 1.6401
2020-10-12 15:00 | Summer | 2.4197 | 3.4629 | 4.9972 | 4.9972 | 4.9972 | 4.9972 | 0.8345 | 1.3655 | 1.8713 | 2.2506 | 2.2506 | 2.2506 | 2.6483 | 3.4176 | 3.9216 | 4.1869 | 4.7174 | 5.2479 | 0.89547 | 1.7674 | 2.1208 | 2.1208 | 2.1208 | 2.1208 | 1.3146 | 1.5293 | 1.5293 | 1.5293 | 1.5293 | 1.5293
2020-10-12 16:00 | Summer | 2.4768 | 3.5447 | 5.1152 | 5.1152 | 5.1152 | 5.1152 | 0.97739 | 1.5994 | 2.1917 | 2.636 | 2.636 | 2.636 | 2.6674 | 3.4422 | 3.9498 | 4.217 | 4.7513 | 5.2857 | 0.87261 | 1.7222 | 2.0667 | 2.0667 | 2.0667 | 2.0667 | 1.2765 | 1.4849 | 1.4849 | 1.4849 | 1.4849 | 1.4849
2020-10-12 17:00 | Summer | 2.3816 | 3.4084 | 4.9185 | 4.9185 | 4.9185 | 4.9185 | 0.92881 | 1.5199 | 2.0828 | 2.505 | 2.505 | 2.505 | 2.5149 | 3.2455 | 3.7241 | 3.976 | 4.4798 | 4.9836 | 0.84212 | 1.6621 | 1.9945 | 1.9945 | 1.9945 | 1.9945 | 1.1813 | 1.3741 | 1.3741 | 1.3741 | 1.3741 | 1.3741
2020-10-12 18:00 | Summer | 1.8602 | 2.6622 | 3.8416 | 3.8416 | 3.8416 | 3.8416 | 0.73147 | 1.197 | 1.6403 | 1.9728 | 1.9728 | 1.9728 | 2.3424 | 3.0229 | 3.4687 | 3.7033 | 4.1726 | 4.6418 | 0.86117 | 1.6997 | 2.0396 | 2.0396 | 2.0396 | 2.0396 | 0.87441 | 1.0172 | 1.0172 | 1.0172 | 1.0172 | 1.0172
2020-10-12 19:00 | Summer | 1.1813 | 1.6906 | 2.4396 | 2.4396 | 2.4396 | 2.4396 | 0.59729 | 0.97739 | 1.3394 | 1.6109 | 1.6109 | 1.6109 | 2.0886 | 2.6953 | 3.0928 | 3.302 | 3.7204 | 4.1388 | 0.74305 | 1.4665 | 1.7599 | 1.7599 | 1.7599 | 1.7599 | 0.64842 | 0.75428 | 0.75428 | 0.75428 | 0.75428 | 0.75428
2020-10-12 20:00 | Summer | 1.1241 | 1.6088 | 2.3215 | 2.3215 | 2.3215 | 2.3215 | 0.4544 | 0.74356 | 1.019 | 1.2255 | 1.2255 | 1.2255 | 2.0196 | 2.6062 | 2.9906 | 3.1929 | 3.5974 | 4.002 | 0.73162 | 1.444 | 1.7328 | 1.7328 | 1.7328 | 1.7328 | 0.57158 | 0.6649 | 0.6649 | 0.6649 | 0.6649 | 0.6649
2020-10-12 21:00 | Summer | 1.086 | 1.5542 | 2.2428 | 2.2428 | 2.2428 | 2.2428 | 0.53728 | 0.87918 | 1.2048 | 1.449 | 1.449 | 1.449 | 1.8862 | 2.4341 | 2.7931 | 2.982 | 3.3599 | 3.7377 | 0.70875 | 1.3989 | 1.6786 | 1.6786 | 1.6786 | 1.6786 | 0.47653 | 0.55434 | 0.55434 | 0.55434 | 0.55434 | 0.55434
2020-10-12 22:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.50298 | 0.82306 | 1.1279 | 1.3565 | 1.3565 | 1.3565 | 1.8481 | 2.3849 | 2.7366 | 2.9218 | 3.292 | 3.6622 | 0.66303 | 1.3086 | 1.5703 | 1.5703 | 1.5703 | 1.5703 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-10-12 23:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.44011 | 0.72018 | 0.98691 | 1.187 | 1.187 | 1.187 | 1.81 | 2.3358 | 2.6802 | 2.8615 | 3.2241 | 3.5867 | 0.63254 | 1.2484 | 1.4981 | 1.4981 | 1.4981 | 1.4981 | 0.43821 | 0.50975 | 0.50975 | 0.50975 | 0.50975 | 0.50975
2020-10-13 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.40867 | 0.66874 | 0.91642 | 1.1022 | 1.1022 | 1.1022 | 1.7147 | 2.2128 | 2.5392 | 2.7109 | 3.0544 | 3.3979 | 0.5792 | 1.1431 | 1.3718 | 1.3718 | 1.3718 | 1.3718 | 0.4462 | 0.51904 | 0.51904 | 0.51904 | 0.51904 | 0.51904
2020-10-13 01:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.41725 | 0.68277 | 0.93565 | 1.1253 | 1.1253 | 1.1253 | 1.5433 | 1.9915 | 2.2852 | 2.4398 | 2.749 | 3.0581 | 0.5068 | 1.0003 | 1.2003 | 1.2003 | 1.2003 | 1.2003 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-10-13 02:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.48584 | 0.79501 | 1.0895 | 1.3103 | 1.3103 | 1.3103 | 1.5623 | 2.0161 | 2.3135 | 2.4699 | 2.7829 | 3.0959 | 0.53686 | 1.0596 | 1.2715 | 1.2715 | 1.2715 | 1.2715 | 0.4675 | 0.54382 | 0.54382 | 0.54382 | 0.54382 | 0.54382
2020-10-13 03:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.39438 | 0.64536 | 0.88438 | 1.0636 | 1.0636 | 1.0636 | 1.5623 | 2.0161 | 2.3135 | 2.4699 | 2.7829 | 3.0959 | 0.53728 | 1.0604 | 1.2725 | 1.2725 | 1.2725 | 1.2725 | 0.48984 | 0.56982 | 0.56982 | 0.56982 | 0.56982 | 0.56982
2020-10-13 04:00 | Summer | 1.0564 | 1.5119 | 2.1818 | 2.1818 | 2.1818 | 2.1818 | 0.38867 | 0.636 | 0.87156 | 1.0482 | 1.0482 | 1.0482 | 1.5909 | 2.053 | 2.3558 | 2.5151 | 2.8338 | 3.1525 | 0.51823 | 1.0228 | 1.2274 | 1.2274 | 1.2274 | 1.2274 | 0.51036 | 0.59368 | 0.59368 | 0.59368 | 0.59368 | 0.59368
2020-10-13 05:00 | Summer | 1.2666 | 1.8127 | 2.6158 | 2.6158 | 2.6158 | 2.6158 | 0.49155 | 0.80436 | 1.1023 | 1.3257 | 1.3257 | 1.3257 | 1.7417 | 2.2476 | 2.5791 | 2.7535 | 3.1024 | 3.4513 | 0.56395 | 1.1131 | 1.3357 | 1.3357 | 1.3357 | 1.3357 | 0.57337 | 0.66698 | 0.66698 | 0.66698 | 0.66698 | 0.66698
2020-10-13 06:00 | Summer | 1.3884 | 1.987 | 2.8673 | 2.8673 | 2.8673 | 2.8673 | 0.54871 | 0.89789 | 1.2304 | 1.4799 | 1.4799 | 1.4799 | 1.829 | 2.3603 | 2.7084 | 2.8916 | 3.2581 | 3.6245 | 0.64397 | 1.271 | 1.5252 | 1.5252 | 1.5252 | 1.5252 | 0.80021 | 0.93085 | 0.93085 | 0.93085 | 0.93085 | 0.93085
2020-10-13 07:00 | Summer | 1.81 | 2.5904 | 3.738 | 3.738 | 3.738 | 3.738 | 0.72304 | 1.1832 | 1.6214 | 1.95 | 1.95 | 1.95 | 2.2101 | 2.8521 | 3.2727 | 3.4941 | 3.9368 | 4.3796 | 1.6499 | 3.2565 | 3.9078 | 3.9078 | 3.9078 | 3.9078 | 1.0098 | 1.1746 | 1.1746 | 1.1746 | 1.1746 | 1.1746
2020-10-13 08:00 | Summer | 2.191 | 3.1357 | 4.525 | 4.525 | 4.525 | 4.525 | 0.81449 | 1.3328 | 1.8264 | 2.1967 | 2.1967 | 2.1967 | 2.3952 | 3.0909 | 3.5468 | 3.7867 | 4.2665 | 4.7463 | 1.7947 | 3.5423 | 4.2507 | 4.2507 | 4.2507 | 4.2507 | 1.2384 | 1.4406 | 1.4406 | 1.4406 | 1.4406 | 1.4406
2020-10-13 09:00 | Summer | 2.4197 | 3.4629 | 4.9972 | 4.9972 | 4.9972 | 4.9972 | 0.87737 | 1.4357 | 1.9674 | 2.3662 | 2.3662 | 2.3662 | 2.4387 | 3.1471 | 3.6112 | 3.8555 | 4.3441 | 4.8326 | 1.8138 | 3.5799 | 4.2958 | 4.2958 | 4.2958 | 4.2958 | 1.2907 | 1.5014 | 1.5014 | 1.5014 | 1.5014 | 1.5014
2020-10-13 10:00 | Summer | 2.4959 | 3.572 | 5.1545 | 5.1545 | 5.1545 | 5.1545 | 0.80306 | 1.3141 | 1.8008 | 2.1658 | 2.1658 | 2.1658 | 2.6293 | 3.393 | 3.8934 | 4.1567 | 4.6835 | 5.2102 | 1.8024 | 3.5573 | 4.2688 | 4.2688 | 4.2688 | 4.2688 | 1.3527 | 1.5736 | 1.5736 | 1.5736 | 1.5736 | 1.5736
2020-10-13 11:00 | Summer | 2.5149 | 3.5993 | 5.1939 | 5.1939 | 5.1939 | 5.1939 | 0.82878 | 1.3562 | 1.8585 | 2.2352 | 2.2352 | 2.2352 | 2.6483 | 3.4176 | 3.9216 | 4.1869 | 4.7174 | 5.2479 | 1.7452 | 3.4445 | 4.1334 | 4.1334 | 4.1334 | 4.1334 | 1.4099 | 1.6401 | 1.6401 | 1.6401 | 1.6401 | 1.6401
2020-10-13 12:00 | Summer | 2.5149 | 3.5993 | 5.1939 | 5.1939 | 5.1939 | 5.1939 | 0.87451 | 1.431 | 1.961 | 2.3585 | 2.3585 | 2.3585 | 3.1246 | 4.0323 | 4.6269 | 4.9399 | 5.5658 | 6.1918 | 1.9014 | 3.75 | 4.5 | 4.5 | 4.5 | 4.5 | 1.4099 | 1.6401 | 1.6401 | 1.6401 | 1.6401 | 1.6401
2020-10-13 13:00 | Summer | 2.6102 | 3.7356 | 5.3906 | 5.3906 | 5.3906 | 5.3906 | 0.98311 | 1.6087 | 2.2045 | 2.6514 | 2.6514 | 2.6514 | 3.1013 | 4.0022 | 4.5924 | 4.903 | 5.5243 | 6.1456 | 1.7947 | 3.5423 | 4.2507 | 4.2507 | 4.2507 | 4.2507 | 1.448 | 1.6844 | 1.6844 | 1.6844 | 1.6844 | 1.6844
2020-10-13 14:00 | Summer | 2.5911 | 3.7083 | 5.3513 | 5.3513 | 5.3513 | 5.3513 | 0.92309 | 1.5105 | 2.07 | 2.4896 | 2.4896 | 2.4896 | 2.915 | 3.7618 | 4.3166 | 4.6086 | 5.1925 | 5.7765 | 1.8748 | 3.7002 | 4.4402 | 4.4402 | 4.4402 | 4.4402 | 1.4289 | 1.6622 | 1.6622 | 1.6622 | 1.6622 | 1.6622
2020-10-13 15:00 | Summer | 2.6483 | 3.7901 | 5.4693 | 5.4693 | 5.4693 | 5.4693 | 0.9088 | 1.4871 | 2.0379 | 2.451 | 2.451 | 2.451 | 2.8388 | 3.6634 | 4.2037 | 4.4881 | 5.0568 | 5.6255 | 1.7185 | 3.3919 | 4.0702 | 4.0702 | 4.0702 | 4.0702 | 1.3527 | 1.5736 | 1.5736 | 1.5736 | 1.5736 | 1.5736
2020-10-13 16:00 | Summer | 2.5721 | 3.6811 | 5.3119 | 5.3119 | 5.3119 | 5.3119 | 0.92023 | 1.5058 | 2.0636 | 2.4818 | 2.4818 | 2.4818 | 2.8216 | 3.6412 | 4.1782 | 4.4608 | 5.0261 | 5.5913 | 1.0441 | 2.0607 | 2.4728 | 2.4728 | 2.4728 | 2.4728 | 1.2765 | 1.4849 | 1.4849 | 1.4849 | 1.4849 | 1.4849
2020-10-13 17:00 | Summer | 2.3816 | 3.4084 | 4.9185 | 4.9185 | 4.9185 | 4.9185 | 0.94024 | 1.5386 | 2.1084 | 2.5358 | 2.5358 | 2.5358 | 2.645 | 3.4134 | 3.9167 | 4.1817 | 4.7116 | 5.2414 | 0.89415 | 1.7648 | 2.1177 | 2.1177 | 2.1177 | 2.1177 | 1.3146 | 1.5293 | 1.5293 | 1.5293 | 1.5293 | 1.5293
2020-10-13 18:00 | Summer | 1.6773 | 2.4005 | 3.464 | 3.464 | 3.464 | 3.464 | 0.64302 | 1.0522 | 1.4419 | 1.7342 | 1.7342 | 1.7342 | 2.4197 | 3.1225 | 3.583 | 3.8254 | 4.3101 | 4.7949 | 0.83831 | 1.6546 | 1.9855 | 1.9855 | 1.9855 | 1.9855 | 0.97773 | 1.1374 | 1.1374 | 1.1374 | 1.1374 | 1.1374
2020-10-13 19:00 | Summer | 1.18 | 1.6887 | 2.4369 | 2.4369 | 2.4369 | 2.4369 | 0.54585 | 0.89321 | 1.224 | 1.4721 | 1.4721 | 1.4721 | 2.1339 | 2.7537 | 3.1598 | 3.3736 | 3.8011 | 4.2285 | 0.78496 | 1.5493 | 1.8591 | 1.8591 | 1.8591 | 1.8591 | 0.6569 | 0.76415 | 0.76415 | 0.76415 | 0.76415 | 0.76415
2020-10-13 20:00 | Summer | 1.105 | 1.5815 | 2.2822 | 2.2822 | 2.2822 | 2.2822 | 0.47726 | 0.78098 | 1.0702 | 1.2872 | 1.2872 | 1.2872 | 2.0632 | 2.6626 | 3.0552 | 3.2619 | 3.6752 | 4.0886 | 0.81926 | 1.617 | 1.9403 | 1.9403 | 1.9403 | 1.9403 | 0.57158 | 0.6649 | 0.6649 | 0.6649 | 0.6649 | 0.6649
2020-10-13 21:00 | Summer | 1.105 | 1.5815 | 2.2822 | 2.2822 | 2.2822 | 2.2822 | 0.46869 | 0.76695 | 1.051 | 1.264 | 1.264 | 1.264 | 1.9624 | 2.5325 | 2.9059 | 3.1025 | 3.4956 | 3.8887 | 0.76591 | 1.5117 | 1.814 | 1.814 | 1.814 | 1.814 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-10-13 22:00 | Summer | 1.0479 | 1.4997 | 2.1641 | 2.1641 | 2.1641 | 2.1641 | 0.42868 | 0.70147 | 0.96128 | 1.1561 | 1.1561 | 1.1561 | 1.8481 | 2.3849 | 2.7366 | 2.9218 | 3.292 | 3.6622 | 0.84593 | 1.6696 | 2.0035 | 2.0035 | 2.0035 | 2.0035 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-10-13 23:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.46012 | 0.75292 | 1.0318 | 1.2409 | 1.2409 | 1.2409 | 1.7909 | 2.3112 | 2.652 | 2.8314 | 3.1902 | 3.549 | 0.58357 | 1.1518 | 1.3821 | 1.3821 | 1.3821 | 1.3821 | 0.42746 | 0.49724 | 0.49724 | 0.49724 | 0.49724 | 0.49724
2020-10-14 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.36866 | 0.60327 | 0.8267 | 0.99427 | 0.99427 | 0.99427 | 1.6957 | 2.1882 | 2.5109 | 2.6808 | 3.0205 | 3.3602 | 0.52585 | 1.0379 | 1.2454 | 1.2454 | 1.2454 | 1.2454 | 0.43821 | 0.50975 | 0.50975 | 0.50975 | 0.50975 | 0.50975
2020-10-14 01:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.39724 | 0.65003 | 0.89079 | 1.0713 | 1.0713 | 1.0713 | 1.5839 | 2.0439 | 2.3454 | 2.504 | 2.8213 | 3.1386 | 0.53347 | 1.0529 | 1.2635 | 1.2635 | 1.2635 | 1.2635 | 0.43821 | 0.50975 | 0.50975 | 0.50975 | 0.50975 | 0.50975
2020-10-14 02:00 | Summer | 0.91452 | 1.3088 | 1.8887 | 1.8887 | 1.8887 | 1.8887 | 0.35152 | 0.57521 | 0.78825 | 0.94803 | 0.94803 | 0.94803 | 1.6004 | 2.0653 | 2.3699 | 2.5302 | 2.8508 | 3.1714 | 0.52966 | 1.0454 | 1.2545 | 1.2545 | 1.2545 | 1.2545 | 0.43821 | 0.50975 | 0.50975 | 0.50975 | 0.50975 | 0.50975
2020-10-14 03:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.35723 | 0.58456 | 0.80107 | 0.96344 | 0.96344 | 0.96344 | 1.5814 | 2.0407 | 2.3417 | 2.5001 | 2.8169 | 3.1337 | 0.51061 | 1.0078 | 1.2093 | 1.2093 | 1.2093 | 1.2093 | 0.4762 | 0.55395 | 0.55395 | 0.55395 | 0.55395 | 0.55395
2020-10-14 04:00 | Summer | 1.0471 | 1.4986 | 2.1626 | 2.1626 | 2.1626 | 2.1626 | 0.33151 | 0.54247 | 0.74339 | 0.89407 | 0.89407 | 0.89407 | 1.5814 | 2.0407 | 2.3417 | 2.5001 | 2.8169 | 3.1337 | 0.51442 | 1.0153 | 1.2184 | 1.2184 | 1.2184 | 1.2184 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-10-14 05:00 | Summer | 1.2575 | 1.7996 | 2.5969 | 2.5969 | 2.5969 | 2.5969 | 0.44868 | 0.73421 | 1.0061 | 1.2101 | 1.2101 | 1.2101 | 1.6957 | 2.1882 | 2.5109 | 2.6808 | 3.0205 | 3.3602 | 0.63635 | 1.256 | 1.5072 | 1.5072 | 1.5072 | 1.5072 | 0.55301 | 0.6433 | 0.6433 | 0.6433 | 0.6433 | 0.6433
2020-10-14 06:00 | Summer | 1.2765 | 1.8269 | 2.6363 | 2.6363 | 2.6363 | 2.6363 | 0.55157 | 0.90257 | 1.2368 | 1.4876 | 1.4876 | 1.4876 | 1.8481 | 2.3849 | 2.7366 | 2.9218 | 3.292 | 3.6622 | 0.58682 | 1.1582 | 1.3898 | 1.3898 | 1.3898 | 1.3898 | 0.80766 | 0.93952 | 0.93952 | 0.93952 | 0.93952 | 0.93952
2020-10-14 07:00 | Summer | 1.6385 | 2.345 | 3.3839 | 3.3839 | 3.3839 | 3.3839 | 0.68303 | 1.1177 | 1.5316 | 1.8421 | 1.8421 | 1.8421 | 2.1148 | 2.7291 | 3.1316 | 3.3435 | 3.7671 | 4.1908 | 0.89547 | 1.7674 | 2.1208 | 2.1208 | 2.1208 | 2.1208 | 0.97168 | 1.1303 | 1.1303 | 1.1303 | 1.1303 | 1.1303
2020-10-14 08:00 | Summer | 2.1199 | 3.0339 | 4.3781 | 4.3781 | 4.3781 | 4.3781 | 0.75162 | 1.2299 | 1.6855 | 2.0271 | 2.0271 | 2.0271 | 2.3435 | 3.0242 | 3.4702 | 3.7049 | 4.1744 | 4.6438 | 1.0174 | 2.008 | 2.4096 | 2.4096 | 2.4096 | 2.4096 | 1.1999 | 1.3958 | 1.3958 | 1.3958 | 1.3958 | 1.3958
2020-10-14 09:00 | Summer | 2.2101 | 3.163 | 4.5643 | 4.5643 | 4.5643 | 4.5643 | 0.84021 | 1.3749 | 1.8841 | 2.266 | 2.266 | 2.266 | 2.472 | 3.1901 | 3.6606 | 3.9082 | 4.4034 | 4.8986 | 0.99454 | 1.9629 | 2.3555 | 2.3555 | 2.3555 | 2.3555 | 1.3042 | 1.5171 | 1.5171 | 1.5171 | 1.5171 | 1.5171
2020-10-14 10:00 | Summer | 2.2863 | 3.2721 | 4.7217 | 4.7217 | 4.7217 | 4.7217 | 0.79735 | 1.3047 | 1.788 | 2.1504 | 2.1504 | 2.1504 | 2.553 | 3.2946 | 3.7805 | 4.0362 | 4.5477 | 5.0591 | 0.96025 | 1.8952 | 2.2743 | 2.2743 | 2.2743 | 2.2743 | 1.3337 | 1.5514 | 1.5514 | 1.5514 | 1.5514 | 1.5514
2020-10-14 11:00 | Summer | 2.172 | 3.1085 | 4.4856 | 4.4856 | 4.4856 | 4.4856 | 0.89737 | 1.4684 | 2.0123 | 2.4202 | 2.4202 | 2.4202 | 2.5911 | 3.3438 | 3.8369 | 4.0965 | 4.6156 | 5.1347 | 1.1127 | 2.1961 | 2.6353 | 2.6353 | 2.6353 | 2.6353 | 1.3718 | 1.5957 | 1.5957 | 1.5957 | 1.5957 | 1.5957
2020-10-14 12:00 | Summer | 2.2673 | 3.2448 | 4.6824 | 4.6824 | 4.6824 | 4.6824 | 0.86879 | 1.4217 | 1.9482 | 2.3431 | 2.3431 | 2.3431 | 2.6674 | 3.4422 | 3.9498 | 4.217 | 4.7513 | 5.2857 | 0.91071 | 1.7975 | 2.1569 | 2.1569 | 2.1569 | 2.1569 | 1.3527 | 1.5736 | 1.5736 | 1.5736 | 1.5736 | 1.5736
2020-10-14 13:00 | Summer | 2.4343 | 3.4838 | 5.0273 | 5.0273 | 5.0273 | 5.0273 | 0.88594 | 1.4497 | 1.9867 | 2.3894 | 2.3894 | 2.3894 | 2.6293 | 3.393 | 3.8934 | 4.1567 | 4.6835 | 5.2102 | 0.92976 | 1.8351 | 2.2021 | 2.2021 | 2.2021 | 2.2021 | 1.3908 | 1.6179 | 1.6179 | 1.6179 | 1.6179 | 1.6179
2020-10-14 14:00 | Summer | 2.5721 | 3.6811 | 5.3119 | 5.3119 | 5.3119 | 5.3119 | 0.90309 | 1.4778 | 2.0251 | 2.4356 | 2.4356 | 2.4356 | 2.8007 | 3.6143 | 4.1473 | 4.4278 | 4.9889 | 5.55 | 0.91833 | 1.8125 | 2.175 | 2.175 | 2.175 | 2.175 | 1.467 | 1.7066 | 1.7066 | 1.7066 | 1.7066 | 1.7066
2020-10-14 15:00 | Summer | 2.4768 | 3.5447 | 5.1152 | 5.1152 | 5.1152 | 5.1152 | 0.89737 | 1.4684 | 2.0123 | 2.4202 | 2.4202 | 2.4202 | 2.6483 | 3.4176 | 3.9216 | 4.1869 | 4.7174 | 5.2479 | 0.99835 | 1.9704 | 2.3645 | 2.3645 | 2.3645 | 2.3645 | 1.4099 | 1.6401 | 1.6401 | 1.6401 | 1.6401 | 1.6401
2020-10-14 16:00 | Summer | 2.4387 | 3.4902 | 5.0365 | 5.0365 | 5.0365 | 5.0365 | 0.87451 | 1.431 | 1.961 | 2.3585 | 2.3585 | 2.3585 | 2.6102 | 3.3684 | 3.8652 | 4.1266 | 4.6495 | 5.1724 | 1.0212 | 2.0156 | 2.4187 | 2.4187 | 2.4187 | 2.4187 | 1.3337 | 1.5514 | 1.5514 | 1.5514 | 1.5514 | 1.5514
2020-10-14 17:00 | Summer | 2.314 | 3.3117 | 4.7789 | 4.7789 | 4.7789 | 4.7789 | 0.83674 | 1.3692 | 1.8763 | 2.2567 | 2.2567 | 2.2567 | 2.5915 | 3.3442 | 3.8374 | 4.097 | 4.6162 | 5.1353 | 0.96787 | 1.9103 | 2.2923 | 2.2923 | 2.2923 | 2.2923 | 1.3337 | 1.5514 | 1.5514 | 1.5514 | 1.5514 | 1.5514
2020-10-14 18:00 | Summer | 2.0199 | 2.8907 | 4.1714 | 4.1714 | 4.1714 | 4.1714 | 0.63159 | 1.0335 | 1.4163 | 1.7034 | 1.7034 | 1.7034 | 2.3435 | 3.0242 | 3.4702 | 3.7049 | 4.1744 | 4.6438 | 0.82688 | 1.632 | 1.9584 | 1.9584 | 1.9584 | 1.9584 | 0.95491 | 1.1108 | 1.1108 | 1.1108 | 1.1108 | 1.1108
2020-10-14 19:00 | Summer | 1.1997 | 1.717 | 2.4777 | 2.4777 | 2.4777 | 2.4777 | 0.45726 | 0.74824 | 1.0254 | 1.2332 | 1.2332 | 1.2332 | 2.2138 | 2.8569 | 3.2782 | 3.4999 | 3.9434 | 4.3869 | 0.81545 | 1.6094 | 1.9313 | 1.9313 | 1.9313 | 1.9313 | 0.72453 | 0.84282 | 0.84282 | 0.84282 | 0.84282 | 0.84282
2020-10-14 20:00 | Summer | 1.1241 | 1.6088 | 2.3215 | 2.3215 | 2.3215 | 2.3215 | 0.47155 | 0.77162 | 1.0574 | 1.2717 | 1.2717 | 1.2717 | 2.1339 | 2.7537 | 3.1598 | 3.3736 | 3.8011 | 4.2285 | 0.72781 | 1.4365 | 1.7238 | 1.7238 | 1.7238 | 1.7238 | 0.59063 | 0.68706 | 0.68706 | 0.68706 | 0.68706 | 0.68706
2020-10-14 21:00 | Summer | 1.0669 | 1.527 | 2.2035 | 2.2035 | 2.2035 | 2.2035 | 0.49155 | 0.80436 | 1.1023 | 1.3257 | 1.3257 | 1.3257 | 1.9624 | 2.5325 | 2.9059 | 3.1025 | 3.4956 | 3.8887 | 0.78496 | 1.5493 | 1.8591 | 1.8591 | 1.8591 | 1.8591 | 0.53347 | 0.62057 | 0.62057 | 0.62057 | 0.62057 | 0.62057
2020-10-14 22:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.40296 | 0.65939 | 0.9036 | 1.0868 | 1.0868 | 1.0868 | 1.8481 | 2.3849 | 2.7366 | 2.9218 | 3.292 | 3.6622 | 0.73952 | 1.4596 | 1.7515 | 1.7515 | 1.7515 | 1.7515 | 0.49541 | 0.57629 | 0.57629 | 0.57629 | 0.57629 | 0.57629
2020-10-14 23:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.37724 | 0.6173 | 0.84593 | 1.0174 | 1.0174 | 1.0174 | 1.7909 | 2.3112 | 2.652 | 2.8314 | 3.1902 | 3.549 | 0.73162 | 1.444 | 1.7328 | 1.7328 | 1.7328 | 1.7328 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-10-15 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.37438 | 0.61262 | 0.83952 | 1.0097 | 1.0097 | 1.0097 | 1.6383 | 2.1141 | 2.4259 | 2.59 | 2.9182 | 3.2464 | 0.5792 | 1.1431 | 1.3718 | 1.3718 | 1.3718 | 1.3718 | 0.43821 | 0.50975 | 0.50975 | 0.50975 | 0.50975 | 0.50975
2020-10-15 01:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.43439 | 0.71083 | 0.9741 | 1.1715 | 1.1715 | 1.1715 | 1.6195 | 2.0899 | 2.3981 | 2.5603 | 2.8847 | 3.2092 | 0.56014 | 1.1055 | 1.3267 | 1.3267 | 1.3267 | 1.3267 | 0.43821 | 0.50975 | 0.50975 | 0.50975 | 0.50975 | 0.50975
2020-10-15 02:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.43439 | 0.71083 | 0.9741 | 1.1715 | 1.1715 | 1.1715 | 1.6195 | 2.0899 | 2.3981 | 2.5603 | 2.8847 | 3.2092 | 0.51823 | 1.0228 | 1.2274 | 1.2274 | 1.2274 | 1.2274 | 0.41916 | 0.48759 | 0.48759 | 0.48759 | 0.48759 | 0.48759
2020-10-15 03:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.40296 | 0.65939 | 0.9036 | 1.0868 | 1.0868 | 1.0868 | 1.5623 | 2.0161 | 2.3135 | 2.4699 | 2.7829 | 3.0959 | 0.5853 | 1.1552 | 1.3862 | 1.3862 | 1.3862 | 1.3862 | 0.43821 | 0.50975 | 0.50975 | 0.50975 | 0.50975 | 0.50975
2020-10-15 04:00 | Summer | 1.086 | 1.5542 | 2.2428 | 2.2428 | 2.2428 | 2.2428 | 0.43725 | 0.7155 | 0.98051 | 1.1793 | 1.1793 | 1.1793 | 1.5623 | 2.0161 | 2.3135 | 2.4699 | 2.7829 | 3.0959 | 0.58682 | 1.1582 | 1.3898 | 1.3898 | 1.3898 | 1.3898 | 0.43812 | 0.50966 | 0.50966 | 0.50966 | 0.50966 | 0.50966
2020-10-15 05:00 | Summer | 1.2384 | 1.7724 | 2.5576 | 2.5576 | 2.5576 | 2.5576 | 0.40296 | 0.65939 | 0.9036 | 1.0868 | 1.0868 | 1.0868 | 1.6956 | 2.1881 | 2.5108 | 2.6806 | 3.0203 | 3.36 | 0.56014 | 1.1055 | 1.3267 | 1.3267 | 1.3267 | 1.3267 | 0.59063 | 0.68706 | 0.68706 | 0.68706 | 0.68706 | 0.68706
2020-10-15 06:00 | Summer | 1.3115 | 1.8769 | 2.7085 | 2.7085 | 2.7085 | 2.7085 | 0.57729 | 0.94465 | 1.2945 | 1.5569 | 1.5569 | 1.5569 | 1.9434 | 2.5079 | 2.8777 | 3.0724 | 3.4617 | 3.851 | 0.60587 | 1.1958 | 1.435 | 1.435 | 1.435 | 1.435 | 0.7889 | 0.91771 | 0.91771 | 0.91771 | 0.91771 | 0.91771
2020-10-15 07:00 | Summer | 1.7528 | 2.5086 | 3.62 | 3.62 | 3.62 | 3.62 | 0.72304 | 1.1832 | 1.6214 | 1.95 | 1.95 | 1.95 | 2.1719 | 2.8027 | 3.2161 | 3.4336 | 3.8687 | 4.3038 | 0.96025 | 1.8952 | 2.2743 | 2.2743 | 2.2743 | 2.2743 | 0.95896 | 1.1155 | 1.1155 | 1.1155 | 1.1155 | 1.1155
2020-10-15 08:00 | Summer | 2.2863 | 3.2721 | 4.7217 | 4.7217 | 4.7217 | 4.7217 | 0.83164 | 1.3609 | 1.8649 | 2.2429 | 2.2429 | 2.2429 | 2.4006 | 3.098 | 3.5548 | 3.7953 | 4.2762 | 4.7571 | 1.0212 | 2.0156 | 2.4187 | 2.4187 | 2.4187 | 2.4187 | 1.2575 | 1.4628 | 1.4628 | 1.4628 | 1.4628 | 1.4628
2020-10-15 09:00 | Summer | 2.4197 | 3.4629 | 4.9972 | 4.9972 | 4.9972 | 4.9972 | 0.8002 | 1.3094 | 1.7944 | 2.1581 | 2.1581 | 2.1581 | 2.5721 | 3.3192 | 3.8087 | 4.0664 | 4.5816 | 5.0969 | 0.99835 | 1.9704 | 2.3645 | 2.3645 | 2.3645 | 2.3645 | 1.3908 | 1.6179 | 1.6179 | 1.6179 | 1.6179 | 1.6179
2020-10-15 10:00 | Summer | 2.4387 | 3.4902 | 5.0365 | 5.0365 | 5.0365 | 5.0365 | 0.98311 | 1.6087 | 2.2045 | 2.6514 | 2.6514 | 2.6514 | 2.6107 | 3.3691 | 3.866 | 4.1275 | 4.6505 | 5.1735 | 1.0517 | 2.0757 | 2.4909 | 2.4909 | 2.4909 | 2.4909 | 1.448 | 1.6844 | 1.6844 | 1.6844 | 1.6844 | 1.6844
2020-10-15 11:00 | Summer | 2.5149 | 3.5993 | 5.1939 | 5.1939 | 5.1939 | 5.1939 | 0.89737 | 1.4684 | 2.0123 | 2.4202 | 2.4202 | 2.4202 | 2.7245 | 3.5159 | 4.0344 | 4.3073 | 4.8531 | 5.3989 | 1.0593 | 2.0908 | 2.5089 | 2.5089 | 2.5089 | 2.5089 | 1.448 | 1.6844 | 1.6844 | 1.6844 | 1.6844 | 1.6844
2020-10-15 12:00 | Summer | 2.4959 | 3.572 | 5.1545 | 5.1545 | 5.1545 | 5.1545 | 1.0088 | 1.6508 | 2.2622 | 2.7208 | 2.7208 | 2.7208 | 2.8579 | 3.688 | 4.2319 | 4.5182 | 5.0907 | 5.6632 | 1.0479 | 2.0682 | 2.4818 | 2.4818 | 2.4818 | 2.4818 | 1.4861 | 1.7287 | 1.7287 | 1.7287 | 1.7287 | 1.7287
2020-10-15 13:00 | Summer | 2.6674 | 3.8174 | 5.5087 | 5.5087 | 5.5087 | 5.5087 | 1.066 | 1.7443 | 2.3904 | 2.8749 | 2.8749 | 2.8749 | 2.8223 | 3.6421 | 4.1793 | 4.462 | 5.0274 | 5.5927 | 1.0517 | 2.0757 | 2.4909 | 2.4909 | 2.4909 | 2.4909 | 1.467 | 1.7066 | 1.7066 | 1.7066 | 1.7066 | 1.7066
2020-10-15 14:00 | Summer | 2.6293 | 3.7629 | 5.43 | 5.43 | 5.43 | 5.43 | 1.1089 | 1.8145 | 2.4865 | 2.9905 | 2.9905 | 2.9905 | 2.9531 | 3.811 | 4.373 | 4.6688 | 5.2604 | 5.852 | 1.0174 | 2.008 | 2.4096 | 2.4096 | 2.4096 | 2.4096 | 1.448 | 1.6844 | 1.6844 | 1.6844 | 1.6844 | 1.6844
2020-10-15 15:00 | Summer | 2.6483 | 3.7901 | 5.4693 | 5.4693 | 5.4693 | 5.4693 | 1.0803 | 1.7677 | 2.4224 | 2.9135 | 2.9135 | 2.9135 | 2.8321 | 3.6547 | 4.1937 | 4.4774 | 5.0447 | 5.6121 | 0.91071 | 1.7975 | 2.1569 | 2.1569 | 2.1569 | 2.1569 | 1.3718 | 1.5957 | 1.5957 | 1.5957 | 1.5957 | 1.5957
2020-10-15 16:00 | Summer | 2.6483 | 3.7901 | 5.4693 | 5.4693 | 5.4693 | 5.4693 | 1.166 | 1.908 | 2.6147 | 3.1447 | 3.1447 | 3.1447 | 2.9341 | 3.7864 | 4.3448 | 4.6387 | 5.2265 | 5.8142 | 0.96406 | 1.9027 | 2.2833 | 2.2833 | 2.2833 | 2.2833 | 1.3337 | 1.5514 | 1.5514 | 1.5514 | 1.5514 | 1.5514
2020-10-15 17:00 | Summer | 2.4768 | 3.5447 | 5.1152 | 5.1152 | 5.1152 | 5.1152 | 1.0631 | 1.7397 | 2.384 | 2.8672 | 2.8672 | 2.8672 | 2.7626 | 3.5651 | 4.0909 | 4.3676 | 4.921 | 5.4745 | 0.91071 | 1.7975 | 2.1569 | 2.1569 | 2.1569 | 2.1569 | 1.3146 | 1.5293 | 1.5293 | 1.5293 | 1.5293 | 1.5293
2020-10-15 18:00 | Summer | 1.9243 | 2.754 | 3.9741 | 3.9741 | 3.9741 | 3.9741 | 0.98597 | 1.6134 | 2.211 | 2.6591 | 2.6591 | 2.6591 | 2.5721 | 3.3192 | 3.8087 | 4.0664 | 4.5816 | 5.0969 | 0.87261 | 1.7222 | 2.0667 | 2.0667 | 2.0667 | 2.0667 | 0.93056 | 1.0825 | 1.0825 | 1.0825 | 1.0825 | 1.0825
2020-10-15 19:00 | Summer | 1.3908 | 1.9905 | 2.8724 | 2.8724 | 2.8724 | 2.8724 | 0.6373 | 1.0429 | 1.4291 | 1.7188 | 1.7188 | 1.7188 | 2.1632 | 2.7916 | 3.2033 | 3.42 | 3.8533 | 4.2867 | 0.83831 | 1.6546 | 1.9855 | 1.9855 | 1.9855 | 1.9855 | 0.67429 | 0.78437 | 0.78437 | 0.78437 | 0.78437 | 0.78437
2020-10-15 20:00 | Summer | 1.2765 | 1.8269 | 2.6363 | 2.6363 | 2.6363 | 2.6363 | 0.66874 | 1.0943 | 1.4996 | 1.8036 | 1.8036 | 1.8036 | 2.0767 | 2.68 | 3.0752 | 3.2832 | 3.6992 | 4.1153 | 0.84593 | 1.6696 | 2.0035 | 2.0035 | 2.0035 | 2.0035 | 0.62873 | 0.73138 | 0.73138 | 0.73138 | 0.73138 | 0.73138
2020-10-15 21:00 | Summer | 1.105 | 1.5815 | 2.2822 | 2.2822 | 2.2822 | 2.2822 | 0.563 | 0.92127 | 1.2625 | 1.5184 | 1.5184 | 1.5184 | 2.0767 | 2.68 | 3.0752 | 3.2832 | 3.6992 | 4.1153 | 0.82688 | 1.632 | 1.9584 | 1.9584 | 1.9584 | 1.9584 | 0.53162 | 0.61841 | 0.61841 | 0.61841 | 0.61841 | 0.61841
2020-10-15 22:00 | Summer | 1.0669 | 1.527 | 2.2035 | 2.2035 | 2.2035 | 2.2035 | 0.55157 | 0.90257 | 1.2368 | 1.4876 | 1.4876 | 1.4876 | 1.83 | 2.3615 | 2.7098 | 2.8931 | 3.2597 | 3.6263 | 0.98311 | 1.9403 | 2.3284 | 2.3284 | 2.3284 | 2.3284 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-10-15 23:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.50013 | 0.81839 | 1.1215 | 1.3488 | 1.3488 | 1.3488 | 1.7528 | 2.262 | 2.5956 | 2.7712 | 3.1223 | 3.4734 | 0.68589 | 1.3537 | 1.6245 | 1.6245 | 1.6245 | 1.6245 | 0.4869 | 0.56639 | 0.56639 | 0.56639 | 0.56639 | 0.56639
2020-10-16 | Summer | 1.0288 | 1.4724 | 2.1248 | 2.1248 | 2.1248 | 2.1248 | 0.35437 | 0.57988 | 0.79466 | 0.95574 | 0.95574 | 0.95574 | 1.6385 | 2.1145 | 2.4263 | 2.5904 | 2.9187 | 3.2469 | 0.64016 | 1.2635 | 1.5162 | 1.5162 | 1.5162 | 1.5162 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-10-16 01:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.36581 | 0.59859 | 0.82029 | 0.98657 | 0.98657 | 0.98657 | 1.6004 | 2.0653 | 2.3699 | 2.5302 | 2.8508 | 3.1714 | 0.67827 | 1.3387 | 1.6064 | 1.6064 | 1.6064 | 1.6064 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-10-16 02:00 | Summer | 1.0288 | 1.4724 | 2.1248 | 2.1248 | 2.1248 | 2.1248 | 0.33151 | 0.54247 | 0.74339 | 0.89407 | 0.89407 | 0.89407 | 1.6004 | 2.0653 | 2.3699 | 2.5302 | 2.8508 | 3.1714 | 0.53728 | 1.0604 | 1.2725 | 1.2725 | 1.2725 | 1.2725 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-10-16 03:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.3294 | 0.53901 | 0.73865 | 0.88838 | 0.88838 | 0.88838 | 1.5825 | 2.0422 | 2.3434 | 2.5019 | 2.8189 | 3.1359 | 0.5449 | 1.0755 | 1.2906 | 1.2906 | 1.2906 | 1.2906 | 0.46634 | 0.54248 | 0.54248 | 0.54248 | 0.54248 | 0.54248
2020-10-16 04:00 | Summer | 1.0288 | 1.4724 | 2.1248 | 2.1248 | 2.1248 | 2.1248 | 0.44583 | 0.72953 | 0.99973 | 1.2024 | 1.2024 | 1.2024 | 1.6004 | 2.0653 | 2.3699 | 2.5302 | 2.8508 | 3.1714 | 0.57539 | 1.1356 | 1.3628 | 1.3628 | 1.3628 | 1.3628 | 0.52251 | 0.60781 | 0.60781 | 0.60781 | 0.60781 | 0.60781
2020-10-16 05:00 | Summer | 1.2184 | 1.7437 | 2.5163 | 2.5163 | 2.5163 | 2.5163 | 0.4001 | 0.65471 | 0.89719 | 1.0791 | 1.0791 | 1.0791 | 1.7378 | 2.2426 | 2.5734 | 2.7475 | 3.0956 | 3.4437 | 0.67827 | 1.3387 | 1.6064 | 1.6064 | 1.6064 | 1.6064 | 0.58694 | 0.68276 | 0.68276 | 0.68276 | 0.68276 | 0.68276
2020-10-16 06:00 | Summer | 1.2956 | 1.8542 | 2.6756 | 2.6756 | 2.6756 | 2.6756 | 0.44583 | 0.72953 | 0.99973 | 1.2024 | 1.2024 | 1.2024 | 1.81 | 2.3358 | 2.6802 | 2.8615 | 3.2241 | 3.5867 | 0.75448 | 1.4891 | 1.7869 | 1.7869 | 1.7869 | 1.7869 | 0.77036 | 0.89614 | 0.89614 | 0.89614 | 0.89614 | 0.89614
2020-10-16 07:00 | Summer | 1.6925 | 2.4222 | 3.4953 | 3.4953 | 3.4953 | 3.4953 | 0.583 | 0.95401 | 1.3073 | 1.5723 | 1.5723 | 1.5723 | 2.1339 | 2.7537 | 3.1598 | 3.3736 | 3.8011 | 4.2285 | 0.99835 | 1.9704 | 2.3645 | 2.3645 | 2.3645 | 2.3645 | 0.93358 | 1.086 | 1.086 | 1.086 | 1.086 | 1.086
2020-10-16 08:00 | Summer | 2.2673 | 3.2448 | 4.6824 | 4.6824 | 4.6824 | 4.6824 | 0.68875 | 1.127 | 1.5445 | 1.8575 | 1.8575 | 1.8575 | 2.4006 | 3.098 | 3.5548 | 3.7953 | 4.2762 | 4.7571 | 1.0174 | 2.008 | 2.4096 | 2.4096 | 2.4096 | 2.4096 | 1.1813 | 1.3741 | 1.3741 | 1.3741 | 1.3741 | 1.3741
2020-10-16 09:00 | Summer | 2.3625 | 3.3811 | 4.8791 | 4.8791 | 4.8791 | 4.8791 | 0.92023 | 1.5058 | 2.0636 | 2.4818 | 2.4818 | 2.4818 | 2.5721 | 3.3192 | 3.8087 | 4.0664 | 4.5816 | 5.0969 | 1.0593 | 2.0908 | 2.5089 | 2.5089 | 2.5089 | 2.5089 | 1.2956 | 1.5071 | 1.5071 | 1.5071 | 1.5071 | 1.5071
2020-10-16 10:00 | Summer | 2.3816 | 3.4084 | 4.9185 | 4.9185 | 4.9185 | 4.9185 | 0.8888 | 1.4544 | 1.9931 | 2.3971 | 2.3971 | 2.3971 | 2.6674 | 3.4422 | 3.9498 | 4.217 | 4.7513 | 5.2857 | 1.0288 | 2.0306 | 2.4367 | 2.4367 | 2.4367 | 2.4367 | 1.3908 | 1.6179 | 1.6179 | 1.6179 | 1.6179 | 1.6179
2020-10-16 11:00 | Summer | 2.553 | 3.6538 | 5.2726 | 5.2726 | 5.2726 | 5.2726 | 0.86308 | 1.4123 | 1.9354 | 2.3277 | 2.3277 | 2.3277 | 2.6864 | 3.4668 | 3.978 | 4.2471 | 4.7853 | 5.3234 | 1.0212 | 2.0156 | 2.4187 | 2.4187 | 2.4187 | 2.4187 | 1.4289 | 1.6622 | 1.6622 | 1.6622 | 1.6622 | 1.6622
2020-10-16 12:00 | Summer | 2.6674 | 3.8174 | 5.5087 | 5.5087 | 5.5087 | 5.5087 | 0.92881 | 1.5199 | 2.0828 | 2.505 | 2.505 | 2.505 | 2.8007 | 3.6143 | 4.1473 | 4.4278 | 4.9889 | 5.55 | 1.0784 | 2.1284 | 2.554 | 2.554 | 2.554 | 2.554 | 1.467 | 1.7066 | 1.7066 | 1.7066 | 1.7066 | 1.7066
2020-10-16 13:00 | Summer | 2.6674 | 3.8174 | 5.5087 | 5.5087 | 5.5087 | 5.5087 | 0.91452 | 1.4965 | 2.0507 | 2.4664 | 2.4664 | 2.4664 | 2.7698 | 3.5744 | 4.1015 | 4.379 | 4.9338 | 5.4887 | 1.1432 | 2.2562 | 2.7075 | 2.7075 | 2.7075 | 2.7075 | 1.467 | 1.7066 | 1.7066 | 1.7066 | 1.7066 | 1.7066
2020-10-16 14:00 | Summer | 2.6293 | 3.7629 | 5.43 | 5.43 | 5.43 | 5.43 | 1.0517 | 1.721 | 2.3584 | 2.8364 | 2.8364 | 2.8364 | 2.7817 | 3.5897 | 4.1191 | 4.3977 | 4.955 | 5.5122 | 1.1851 | 2.3389 | 2.8067 | 2.8067 | 2.8067 | 2.8067 | 1.4099 | 1.6401 | 1.6401 | 1.6401 | 1.6401 | 1.6401
2020-10-16 15:00 | Summer | 2.5911 | 3.7083 | 5.3513 | 5.3513 | 5.3513 | 5.3513 | 0.95453 | 1.562 | 2.1405 | 2.5743 | 2.5743 | 2.5743 | 2.7055 | 3.4913 | 4.0062 | 4.2772 | 4.8192 | 5.3612 | 1.1012 | 2.1735 | 2.6082 | 2.6082 | 2.6082 | 2.6082 | 1.3908 | 1.6179 | 1.6179 | 1.6179 | 1.6179 | 1.6179
2020-10-16 16:00 | Summer | 2.3244 | 3.3266 | 4.8004 | 4.8004 | 4.8004 | 4.8004 | 0.95453 | 1.562 | 2.1405 | 2.5743 | 2.5743 | 2.5743 | 2.5721 | 3.3192 | 3.8087 | 4.0664 | 4.5816 | 5.0969 | 1.0212 | 2.0156 | 2.4187 | 2.4187 | 2.4187 | 2.4187 | 1.2575 | 1.4628 | 1.4628 | 1.4628 | 1.4628 | 1.4628
2020-10-16 17:00 | Summer | 1.9823 | 2.837 | 4.0939 | 4.0939 | 4.0939 | 4.0939 | 0.88594 | 1.4497 | 1.9867 | 2.3894 | 2.3894 | 2.3894 | 2.4909 | 3.2144 | 3.6885 | 3.938 | 4.437 | 4.936 | 0.99073 | 1.9554 | 2.3465 | 2.3465 | 2.3465 | 2.3465 | 1.1053 | 1.2857 | 1.2857 | 1.2857 | 1.2857 | 1.2857
2020-10-16 18:00 | Summer | 1.4667 | 2.099 | 3.029 | 3.029 | 3.029 | 3.029 | 0.7548 | 1.2351 | 1.6926 | 2.0357 | 2.0357 | 2.0357 | 2.191 | 2.8275 | 3.2445 | 3.4639 | 3.9029 | 4.3418 | 0.82307 | 1.6245 | 1.9494 | 1.9494 | 1.9494 | 1.9494 | 0.81894 | 0.95265 | 0.95265 | 0.95265 | 0.95265 | 0.95265
2020-10-16 19:00 | Summer | 1.1241 | 1.6088 | 2.3215 | 2.3215 | 2.3215 | 2.3215 | 0.51159 | 0.83715 | 1.1472 | 1.3798 | 1.3798 | 1.3798 | 2.172 | 2.8029 | 3.2163 | 3.4338 | 3.8689 | 4.3041 | 0.81926 | 1.617 | 1.9403 | 1.9403 | 1.9403 | 1.9403 | 0.68589 | 0.79787 | 0.79787 | 0.79787 | 0.79787 | 0.79787
2020-10-16 20:00 | Summer | 1.0669 | 1.527 | 2.2035 | 2.2035 | 2.2035 | 2.2035 | 0.48298 | 0.79033 | 1.083 | 1.3026 | 1.3026 | 1.3026 | 2.0005 | 2.5816 | 2.9624 | 3.1627 | 3.5635 | 3.9643 | 0.79258 | 1.5643 | 1.8772 | 1.8772 | 1.8772 | 1.8772 | 0.60968 | 0.70922 | 0.70922 | 0.70922 | 0.70922 | 0.70922
2020-10-16 21:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.47155 | 0.77162 | 1.0574 | 1.2717 | 1.2717 | 1.2717 | 1.9624 | 2.5325 | 2.9059 | 3.1025 | 3.4956 | 3.8887 | 0.83831 | 1.6546 | 1.9855 | 1.9855 | 1.9855 | 1.9855 | 0.55252 | 0.64273 | 0.64273 | 0.64273 | 0.64273 | 0.64273
2020-10-16 22:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.43725 | 0.7155 | 0.98051 | 1.1793 | 1.1793 | 1.1793 | 1.8334 | 2.366 | 2.7149 | 2.8985 | 3.2658 | 3.6331 | 0.73543 | 1.4515 | 1.7418 | 1.7418 | 1.7418 | 1.7418 | 0.53347 | 0.62057 | 0.62057 | 0.62057 | 0.62057 | 0.62057
2020-10-16 23:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.36588 | 0.59871 | 0.82045 | 0.98676 | 0.98676 | 0.98676 | 1.6718 | 2.1574 | 2.4756 | 2.643 | 2.978 | 3.3129 | 0.77353 | 1.5267 | 1.832 | 1.832 | 1.832 | 1.832 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-10-17 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.30298 | 0.49579 | 0.67941 | 0.81713 | 0.81713 | 0.81713 | 1.6385 | 2.1145 | 2.4263 | 2.5904 | 2.9187 | 3.2469 | 0.6897 | 1.3613 | 1.6335 | 1.6335 | 1.6335 | 1.6335 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-10-17 01:00 | Summer | 0.95927 | 1.3729 | 1.9811 | 1.9811 | 1.9811 | 1.9811 | 0.3086 | 0.50498 | 0.69201 | 0.83228 | 0.83228 | 0.83228 | 1.5433 | 1.9915 | 2.2852 | 2.4398 | 2.749 | 3.0581 | 0.59825 | 1.1808 | 1.4169 | 1.4169 | 1.4169 | 1.4169 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-10-17 02:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.30865 | 0.50506 | 0.69212 | 0.83241 | 0.83241 | 0.83241 | 1.5433 | 1.9915 | 2.2852 | 2.4398 | 2.749 | 3.0581 | 0.61349 | 1.2108 | 1.453 | 1.453 | 1.453 | 1.453 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-10-17 03:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.29881 | 0.48896 | 0.67005 | 0.80588 | 0.80588 | 0.80588 | 1.4861 | 1.9178 | 2.2006 | 2.3495 | 2.6472 | 2.9449 | 0.61522 | 1.2143 | 1.4571 | 1.4571 | 1.4571 | 1.4571 | 0.43821 | 0.50975 | 0.50975 | 0.50975 | 0.50975 | 0.50975
2020-10-17 04:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.29658 | 0.48532 | 0.66507 | 0.79988 | 0.79988 | 0.79988 | 1.467 | 1.8932 | 2.1724 | 2.3193 | 2.6132 | 2.9071 | 0.62111 | 1.2259 | 1.4711 | 1.4711 | 1.4711 | 1.4711 | 0.43821 | 0.50975 | 0.50975 | 0.50975 | 0.50975 | 0.50975
2020-10-17 05:00 | Summer | 0.99156 | 1.4191 | 2.0478 | 2.0478 | 2.0478 | 2.0478 | 0.33723 | 0.55183 | 0.75621 | 0.90949 | 0.90949 | 0.90949 | 1.5814 | 2.0407 | 2.3417 | 2.5001 | 2.8169 | 3.1337 | 0.65541 | 1.2936 | 1.5523 | 1.5523 | 1.5523 | 1.5523 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-10-17 06:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.34008 | 0.5565 | 0.76261 | 0.9172 | 0.9172 | 0.9172 | 1.6766 | 2.1636 | 2.4827 | 2.6507 | 2.9865 | 3.3224 | 0.69732 | 1.3763 | 1.6516 | 1.6516 | 1.6516 | 1.6516 | 0.47681 | 0.55466 | 0.55466 | 0.55466 | 0.55466 | 0.55466
2020-10-17 07:00 | Summer | 1.0479 | 1.4997 | 2.1641 | 2.1641 | 2.1641 | 2.1641 | 0.3789 | 0.62002 | 0.84966 | 1.0219 | 1.0219 | 1.0219 | 1.7338 | 2.2374 | 2.5674 | 2.741 | 3.0884 | 3.4357 | 0.71637 | 1.4139 | 1.6967 | 1.6967 | 1.6967 | 1.6967 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-10-17 08:00 | Summer | 1.0479 | 1.4997 | 2.1641 | 2.1641 | 2.1641 | 2.1641 | 0.41411 | 0.67763 | 0.9286 | 1.1168 | 1.1168 | 1.1168 | 1.9243 | 2.4833 | 2.8495 | 3.0422 | 3.4277 | 3.8132 | 0.72781 | 1.4365 | 1.7238 | 1.7238 | 1.7238 | 1.7238 | 0.53347 | 0.62057 | 0.62057 | 0.62057 | 0.62057 | 0.62057
2020-10-17 09:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.48012 | 0.78565 | 1.0766 | 1.2949 | 1.2949 | 1.2949 | 1.9434 | 2.5079 | 2.8777 | 3.0724 | 3.4617 | 3.851 | 0.75067 | 1.4816 | 1.7779 | 1.7779 | 1.7779 | 1.7779 | 0.57158 | 0.6649 | 0.6649 | 0.6649 | 0.6649 | 0.6649
2020-10-17 10:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.46297 | 0.75759 | 1.0382 | 1.2486 | 1.2486 | 1.2486 | 2.0196 | 2.6062 | 2.9906 | 3.1929 | 3.5974 | 4.002 | 0.96406 | 1.9027 | 2.2833 | 2.2833 | 2.2833 | 2.2833 | 0.57158 | 0.6649 | 0.6649 | 0.6649 | 0.6649 | 0.6649
2020-10-17 11:00 | Summer | 1.0479 | 1.4997 | 2.1641 | 2.1641 | 2.1641 | 2.1641 | 0.563 | 0.92127 | 1.2625 | 1.5184 | 1.5184 | 1.5184 | 2.0577 | 2.6554 | 3.047 | 3.2531 | 3.6653 | 4.0775 | 0.75448 | 1.4891 | 1.7869 | 1.7869 | 1.7869 | 1.7869 | 0.59063 | 0.68706 | 0.68706 | 0.68706 | 0.68706 | 0.68706
2020-10-17 12:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.56872 | 0.93062 | 1.2753 | 1.5338 | 1.5338 | 1.5338 | 2.1148 | 2.7291 | 3.1316 | 3.3435 | 3.7671 | 4.1908 | 0.91833 | 1.8125 | 2.175 | 2.175 | 2.175 | 2.175 | 0.59784 | 0.69545 | 0.69545 | 0.69545 | 0.69545 | 0.69545
2020-10-17 13:00 | Summer | 1.0479 | 1.4997 | 2.1641 | 2.1641 | 2.1641 | 2.1641 | 0.54299 | 0.88854 | 1.2176 | 1.4644 | 1.4644 | 1.4644 | 2.2101 | 2.8521 | 3.2727 | 3.4941 | 3.9368 | 4.3796 | 0.85736 | 1.6922 | 2.0306 | 2.0306 | 2.0306 | 2.0306 | 0.62873 | 0.73138 | 0.73138 | 0.73138 | 0.73138 | 0.73138
2020-10-17 14:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.55157 | 0.90257 | 1.2368 | 1.4876 | 1.4876 | 1.4876 | 2.1613 | 2.7891 | 3.2005 | 3.4169 | 3.8499 | 4.2829 | 0.95644 | 1.8877 | 2.2652 | 2.2652 | 2.2652 | 2.2652 | 0.59063 | 0.68706 | 0.68706 | 0.68706 | 0.68706 | 0.68706
2020-10-17 15:00 | Summer | 1.0669 | 1.527 | 2.2035 | 2.2035 | 2.2035 | 2.2035 | 0.70875 | 1.1598 | 1.5893 | 1.9115 | 1.9115 | 1.9115 | 2.172 | 2.8029 | 3.2163 | 3.4338 | 3.8689 | 4.3041 | 0.95263 | 1.8802 | 2.2562 | 2.2562 | 2.2562 | 2.2562 | 0.53347 | 0.62057 | 0.62057 | 0.62057 | 0.62057 | 0.62057
2020-10-17 16:00 | Summer | 1.086 | 1.5542 | 2.2428 | 2.2428 | 2.2428 | 2.2428 | 0.79449 | 1.3001 | 1.7816 | 2.1427 | 2.1427 | 2.1427 | 2.1272 | 2.7451 | 3.1499 | 3.363 | 3.7891 | 4.2153 | 1.0403 | 2.0532 | 2.4638 | 2.4638 | 2.4638 | 2.4638 | 0.47759 | 0.55556 | 0.55556 | 0.55556 | 0.55556 | 0.55556
2020-10-17 17:00 | Summer | 1.0288 | 1.4724 | 2.1248 | 2.1248 | 2.1248 | 2.1248 | 0.78877 | 1.2907 | 1.7688 | 2.1273 | 2.1273 | 2.1273 | 2.0767 | 2.68 | 3.0752 | 3.2832 | 3.6992 | 4.1153 | 0.98311 | 1.9403 | 2.3284 | 2.3284 | 2.3284 | 2.3284 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-10-17 18:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.64588 | 1.0569 | 1.4483 | 1.7419 | 1.7419 | 1.7419 | 2.1148 | 2.7291 | 3.1316 | 3.3435 | 3.7671 | 4.1908 | 1.0746 | 2.1208 | 2.545 | 2.545 | 2.545 | 2.545 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-10-17 19:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.55728 | 0.91192 | 1.2497 | 1.503 | 1.503 | 1.503 | 2.1148 | 2.7291 | 3.1316 | 3.3435 | 3.7671 | 4.1908 | 0.94119 | 1.8576 | 2.2291 | 2.2291 | 2.2291 | 2.2291 | 0.53347 | 0.62057 | 0.62057 | 0.62057 | 0.62057 | 0.62057
2020-10-17 20:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.51442 | 0.84177 | 1.1535 | 1.3874 | 1.3874 | 1.3874 | 2.0958 | 2.7046 | 3.1034 | 3.3133 | 3.7332 | 4.153 | 1.1127 | 2.1961 | 2.6353 | 2.6353 | 2.6353 | 2.6353 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-10-17 21:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.51727 | 0.84645 | 1.1599 | 1.3951 | 1.3951 | 1.3951 | 2.0386 | 2.6308 | 3.0188 | 3.223 | 3.6314 | 4.0398 | 0.94472 | 1.8646 | 2.2375 | 2.2375 | 2.2375 | 2.2375 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-10-17 22:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.47155 | 0.77162 | 1.0574 | 1.2717 | 1.2717 | 1.2717 | 1.9434 | 2.5079 | 2.8777 | 3.0724 | 3.4617 | 3.851 | 0.85736 | 1.6922 | 2.0306 | 2.0306 | 2.0306 | 2.0306 | 0.48406 | 0.56309 | 0.56309 | 0.56309 | 0.56309 | 0.56309
2020-10-17 23:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.42011 | 0.68744 | 0.94205 | 1.133 | 1.133 | 1.133 | 1.7719 | 2.2866 | 2.6238 | 2.8013 | 3.1562 | 3.5112 | 0.81164 | 1.6019 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-10-18 | Summer | 0.93604 | 1.3396 | 1.9331 | 1.9331 | 1.9331 | 1.9331 | 0.32033 | 0.52417 | 0.71831 | 0.86391 | 0.86391 | 0.86391 | 1.6954 | 2.1879 | 2.5106 | 2.6804 | 3.0201 | 3.3597 | 0.78496 | 1.5493 | 1.8591 | 1.8591 | 1.8591 | 1.8591 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-10-18 01:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.30997 | 0.50722 | 0.69507 | 0.83597 | 0.83597 | 0.83597 | 1.6004 | 2.0653 | 2.3699 | 2.5302 | 2.8508 | 3.1714 | 0.66303 | 1.3086 | 1.5703 | 1.5703 | 1.5703 | 1.5703 | 0.43821 | 0.50975 | 0.50975 | 0.50975 | 0.50975 | 0.50975
2020-10-18 02:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.31067 | 0.50836 | 0.69665 | 0.83786 | 0.83786 | 0.83786 | 1.5242 | 1.967 | 2.257 | 2.4097 | 2.715 | 3.0204 | 0.59825 | 1.1808 | 1.4169 | 1.4169 | 1.4169 | 1.4169 | 0.43821 | 0.50975 | 0.50975 | 0.50975 | 0.50975 | 0.50975
2020-10-18 03:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.31694 | 0.51863 | 0.71072 | 0.85479 | 0.85479 | 0.85479 | 1.5242 | 1.967 | 2.257 | 2.4097 | 2.715 | 3.0204 | 0.6516 | 1.286 | 1.5433 | 1.5433 | 1.5433 | 1.5433 | 0.41916 | 0.48759 | 0.48759 | 0.48759 | 0.48759 | 0.48759
2020-10-18 04:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.31722 | 0.51909 | 0.71134 | 0.85554 | 0.85554 | 0.85554 | 1.5113 | 1.9503 | 2.2379 | 2.3893 | 2.6921 | 2.9948 | 0.60587 | 1.1958 | 1.435 | 1.435 | 1.435 | 1.435 | 0.41916 | 0.48759 | 0.48759 | 0.48759 | 0.48759 | 0.48759
2020-10-18 05:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.31151 | 0.50974 | 0.69853 | 0.84012 | 0.84012 | 0.84012 | 1.6004 | 2.0653 | 2.3699 | 2.5302 | 2.8508 | 3.1714 | 0.64779 | 1.2785 | 1.5342 | 1.5342 | 1.5342 | 1.5342 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-10-18 06:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.35437 | 0.57988 | 0.79466 | 0.95574 | 0.95574 | 0.95574 | 1.6424 | 2.1194 | 2.432 | 2.5965 | 2.9255 | 3.2545 | 0.76972 | 1.5192 | 1.823 | 1.823 | 1.823 | 1.823 | 0.43821 | 0.50975 | 0.50975 | 0.50975 | 0.50975 | 0.50975
2020-10-18 07:00 | Summer | 0.91452 | 1.3088 | 1.8887 | 1.8887 | 1.8887 | 1.8887 | 0.3487 | 0.57061 | 0.78194 | 0.94045 | 0.94045 | 0.94045 | 1.8253 | 2.3555 | 2.7029 | 2.8857 | 3.2514 | 3.6171 | 0.72018 | 1.4214 | 1.7057 | 1.7057 | 1.7057 | 1.7057 | 0.4285 | 0.49846 | 0.49846 | 0.49846 | 0.49846 | 0.49846
2020-10-18 08:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.38009 | 0.62197 | 0.85233 | 1.0251 | 1.0251 | 1.0251 | 1.9815 | 2.557 | 2.9341 | 3.1326 | 3.5296 | 3.9265 | 0.80402 | 1.5869 | 1.9042 | 1.9042 | 1.9042 | 1.9042 | 0.45038 | 0.52391 | 0.52391 | 0.52391 | 0.52391 | 0.52391
2020-10-18 09:00 | Summer | 0.91452 | 1.3088 | 1.8887 | 1.8887 | 1.8887 | 1.8887 | 0.39724 | 0.65003 | 0.89079 | 1.0713 | 1.0713 | 1.0713 | 2.0958 | 2.7046 | 3.1034 | 3.3133 | 3.7332 | 4.153 | 0.76972 | 1.5192 | 1.823 | 1.823 | 1.823 | 1.823 | 0.49517 | 0.57601 | 0.57601 | 0.57601 | 0.57601 | 0.57601
2020-10-18 10:00 | Summer | 0.90737 | 1.2986 | 1.8739 | 1.8739 | 1.8739 | 1.8739 | 0.38581 | 0.63133 | 0.86515 | 1.0405 | 1.0405 | 1.0405 | 2.0577 | 2.6554 | 3.047 | 3.2531 | 3.6653 | 4.0775 | 0.91833 | 1.8125 | 2.175 | 2.175 | 2.175 | 2.175 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-10-18 11:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.45154 | 0.73889 | 1.0125 | 1.2178 | 1.2178 | 1.2178 | 2.0958 | 2.7046 | 3.1034 | 3.3133 | 3.7332 | 4.153 | 0.85736 | 1.6922 | 2.0306 | 2.0306 | 2.0306 | 2.0306 | 0.47778 | 0.55579 | 0.55579 | 0.55579 | 0.55579 | 0.55579
2020-10-18 12:00 | Summer | 0.91452 | 1.3088 | 1.8887 | 1.8887 | 1.8887 | 1.8887 | 0.34294 | 0.56118 | 0.76902 | 0.92491 | 0.92491 | 0.92491 | 2.0958 | 2.7046 | 3.1034 | 3.3133 | 3.7332 | 4.153 | 0.81926 | 1.617 | 1.9403 | 1.9403 | 1.9403 | 1.9403 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-10-18 13:00 | Summer | 0.91452 | 1.3088 | 1.8887 | 1.8887 | 1.8887 | 1.8887 | 0.38867 | 0.636 | 0.87156 | 1.0482 | 1.0482 | 1.0482 | 2.1339 | 2.7537 | 3.1598 | 3.3736 | 3.8011 | 4.2285 | 0.86879 | 1.7147 | 2.0577 | 2.0577 | 2.0577 | 2.0577 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-10-18 14:00 | Summer | 0.91452 | 1.3088 | 1.8887 | 1.8887 | 1.8887 | 1.8887 | 0.42011 | 0.68744 | 0.94205 | 1.133 | 1.133 | 1.133 | 2.1529 | 2.7783 | 3.1881 | 3.4037 | 3.835 | 4.2663 | 0.75067 | 1.4816 | 1.7779 | 1.7779 | 1.7779 | 1.7779 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-10-18 15:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.44011 | 0.72018 | 0.98691 | 1.187 | 1.187 | 1.187 | 2.0386 | 2.6308 | 3.0188 | 3.223 | 3.6314 | 4.0398 | 0.80783 | 1.5944 | 1.9133 | 1.9133 | 1.9133 | 1.9133 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-10-18 16:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.47441 | 0.7763 | 1.0638 | 1.2795 | 1.2795 | 1.2795 | 2.1148 | 2.7291 | 3.1316 | 3.3435 | 3.7671 | 4.1908 | 0.83831 | 1.6546 | 1.9855 | 1.9855 | 1.9855 | 1.9855 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-10-18 17:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.41168 | 0.67367 | 0.92317 | 1.1103 | 1.1103 | 1.1103 | 2.0583 | 2.6562 | 3.0479 | 3.2541 | 3.6664 | 4.0788 | 0.96406 | 1.9027 | 2.2833 | 2.2833 | 2.2833 | 2.2833 | 0.5139 | 0.5978 | 0.5978 | 0.5978 | 0.5978 | 0.5978
2020-10-18 18:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.37724 | 0.6173 | 0.84593 | 1.0174 | 1.0174 | 1.0174 | 1.9243 | 2.4833 | 2.8495 | 3.0422 | 3.4277 | 3.8132 | 0.74706 | 1.4745 | 1.7694 | 1.7694 | 1.7694 | 1.7694 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-10-18 19:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.38867 | 0.636 | 0.87156 | 1.0482 | 1.0482 | 1.0482 | 1.9815 | 2.557 | 2.9341 | 3.1326 | 3.5296 | 3.9265 | 0.85355 | 1.6846 | 2.0216 | 2.0216 | 2.0216 | 2.0216 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-10-18 20:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.37438 | 0.61262 | 0.83952 | 1.0097 | 1.0097 | 1.0097 | 1.9245 | 2.4836 | 2.8498 | 3.0426 | 3.4282 | 3.8137 | 0.92976 | 1.8351 | 2.2021 | 2.2021 | 2.2021 | 2.2021 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-10-18 21:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.33531 | 0.54869 | 0.75191 | 0.90432 | 0.90432 | 0.90432 | 1.829 | 2.3603 | 2.7084 | 2.8916 | 3.2581 | 3.6245 | 0.79258 | 1.5643 | 1.8772 | 1.8772 | 1.8772 | 1.8772 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-10-18 22:00 | Summer | 0.97639 | 1.3974 | 2.0165 | 2.0165 | 2.0165 | 2.0165 | 0.33437 | 0.54715 | 0.7498 | 0.90178 | 0.90178 | 0.90178 | 1.7719 | 2.2866 | 2.6238 | 2.8013 | 3.1562 | 3.5112 | 0.7621 | 1.5041 | 1.805 | 1.805 | 1.805 | 1.805 | 0.43821 | 0.50975 | 0.50975 | 0.50975 | 0.50975 | 0.50975
2020-10-18 23:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.32294 | 0.52844 | 0.72416 | 0.87095 | 0.87095 | 0.87095 | 1.6576 | 2.1391 | 2.4545 | 2.6205 | 2.9526 | 3.2847 | 0.79258 | 1.5643 | 1.8772 | 1.8772 | 1.8772 | 1.8772 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-10-19 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.29957 | 0.4902 | 0.67176 | 0.80793 | 0.80793 | 0.80793 | 1.582 | 2.0415 | 2.3426 | 2.501 | 2.818 | 3.1349 | 0.62111 | 1.2259 | 1.4711 | 1.4711 | 1.4711 | 1.4711 | 0.45659 | 0.53113 | 0.53113 | 0.53113 | 0.53113 | 0.53113
2020-10-19 01:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.30351 | 0.49666 | 0.6806 | 0.81856 | 0.81856 | 0.81856 | 1.5433 | 1.9915 | 2.2852 | 2.4398 | 2.749 | 3.0581 | 0.60968 | 1.2033 | 1.444 | 1.444 | 1.444 | 1.444 | 0.41916 | 0.48759 | 0.48759 | 0.48759 | 0.48759 | 0.48759
2020-10-19 02:00 | Summer | 0.97148 | 1.3903 | 2.0063 | 2.0063 | 2.0063 | 2.0063 | 0.33437 | 0.54715 | 0.7498 | 0.90178 | 0.90178 | 0.90178 | 1.5433 | 1.9915 | 2.2852 | 2.4398 | 2.749 | 3.0581 | 0.55633 | 1.098 | 1.3176 | 1.3176 | 1.3176 | 1.3176 | 0.43821 | 0.50975 | 0.50975 | 0.50975 | 0.50975 | 0.50975
2020-10-19 03:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.31722 | 0.51909 | 0.71134 | 0.85554 | 0.85554 | 0.85554 | 1.4861 | 1.9178 | 2.2006 | 2.3495 | 2.6472 | 2.9449 | 0.61349 | 1.2108 | 1.453 | 1.453 | 1.453 | 1.453 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-10-19 04:00 | Summer | 1.162 | 1.663 | 2.3998 | 2.3998 | 2.3998 | 2.3998 | 0.31436 | 0.51441 | 0.70494 | 0.84783 | 0.84783 | 0.84783 | 1.5812 | 2.0405 | 2.3414 | 2.4998 | 2.8165 | 3.1333 | 0.60587 | 1.1958 | 1.435 | 1.435 | 1.435 | 1.435 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-10-19 05:00 | Summer | 1.3146 | 1.8814 | 2.715 | 2.715 | 2.715 | 2.715 | 0.40582 | 0.66406 | 0.91001 | 1.0945 | 1.0945 | 1.0945 | 1.6385 | 2.1145 | 2.4263 | 2.5904 | 2.9187 | 3.2469 | 0.58682 | 1.1582 | 1.3898 | 1.3898 | 1.3898 | 1.3898 | 0.57032 | 0.66344 | 0.66344 | 0.66344 | 0.66344 | 0.66344
2020-10-19 06:00 | Summer | 1.4078 | 2.0148 | 2.9075 | 2.9075 | 2.9075 | 2.9075 | 0.54299 | 0.88853 | 1.2176 | 1.4644 | 1.4644 | 1.4644 | 1.8085 | 2.3338 | 2.678 | 2.8591 | 3.2214 | 3.5837 | 0.67827 | 1.3387 | 1.6064 | 1.6064 | 1.6064 | 1.6064 | 0.76146 | 0.88578 | 0.88578 | 0.88578 | 0.88578 | 0.88578
2020-10-19 07:00 | Summer | 1.89 | 2.7049 | 3.9032 | 3.9032 | 3.9032 | 3.9032 | 0.66017 | 1.0803 | 1.4804 | 1.7805 | 1.7805 | 1.7805 | 2.0958 | 2.7046 | 3.1034 | 3.3133 | 3.7332 | 4.153 | 0.94501 | 1.8651 | 2.2382 | 2.2382 | 2.2382 | 2.2382 | 0.95263 | 1.1082 | 1.1082 | 1.1082 | 1.1082 | 1.1082
2020-10-19 08:00 | Summer | 2.191 | 3.1357 | 4.525 | 4.525 | 4.525 | 4.525 | 0.72832 | 1.1918 | 1.6332 | 1.9643 | 1.9643 | 1.9643 | 2.3625 | 3.0488 | 3.4984 | 3.735 | 4.2083 | 4.6816 | 0.99454 | 1.9629 | 2.3555 | 2.3555 | 2.3555 | 2.3555 | 1.105 | 1.2855 | 1.2855 | 1.2855 | 1.2855 | 1.2855
2020-10-19 09:00 | Summer | 2.191 | 3.1357 | 4.525 | 4.525 | 4.525 | 4.525 | 0.8002 | 1.3094 | 1.7944 | 2.1581 | 2.1581 | 2.1581 | 2.3816 | 3.0734 | 3.5266 | 3.7652 | 4.2423 | 4.7194 | 0.87261 | 1.7222 | 2.0667 | 2.0667 | 2.0667 | 2.0667 | 1.1813 | 1.3741 | 1.3741 | 1.3741 | 1.3741 | 1.3741
2020-10-19 10:00 | Summer | 2.191 | 3.1357 | 4.525 | 4.525 | 4.525 | 4.525 | 0.79735 | 1.3047 | 1.788 | 2.1504 | 2.1504 | 2.1504 | 2.4743 | 3.1931 | 3.6639 | 3.9118 | 4.4075 | 4.9031 | 1.006 | 1.9855 | 2.3826 | 2.3826 | 2.3826 | 2.3826 | 1.2575 | 1.4628 | 1.4628 | 1.4628 | 1.4628 | 1.4628
2020-10-19 11:00 | Summer | 2.172 | 3.1085 | 4.4856 | 4.4856 | 4.4856 | 4.4856 | 0.80592 | 1.3188 | 1.8072 | 2.1735 | 2.1735 | 2.1735 | 2.6483 | 3.4176 | 3.9216 | 4.1869 | 4.7174 | 5.2479 | 1.025 | 2.0231 | 2.4277 | 2.4277 | 2.4277 | 2.4277 | 1.2956 | 1.5071 | 1.5071 | 1.5071 | 1.5071 | 1.5071
2020-10-19 12:00 | Summer | 2.2482 | 3.2175 | 4.643 | 4.643 | 4.643 | 4.643 | 0.80878 | 1.3235 | 1.8136 | 2.1812 | 2.1812 | 2.1812 | 2.5911 | 3.3438 | 3.8369 | 4.0965 | 4.6156 | 5.1347 | 0.86879 | 1.7147 | 2.0577 | 2.0577 | 2.0577 | 2.0577 | 1.2575 | 1.4628 | 1.4628 | 1.4628 | 1.4628 | 1.4628
2020-10-19 13:00 | Summer | 2.235 | 3.1986 | 4.6158 | 4.6158 | 4.6158 | 4.6158 | 0.89451 | 1.4638 | 2.0059 | 2.4125 | 2.4125 | 2.4125 | 2.6293 | 3.393 | 3.8934 | 4.1567 | 4.6835 | 5.2102 | 0.87261 | 1.7222 | 2.0667 | 2.0667 | 2.0667 | 2.0667 | 1.2575 | 1.4628 | 1.4628 | 1.4628 | 1.4628 | 1.4628
2020-10-19 14:00 | Summer | 2.3435 | 3.3539 | 4.8398 | 4.8398 | 4.8398 | 4.8398 | 0.88594 | 1.4497 | 1.9867 | 2.3894 | 2.3894 | 2.3894 | 2.6864 | 3.4668 | 3.978 | 4.2471 | 4.7853 | 5.3234 | 0.91452 | 1.805 | 2.166 | 2.166 | 2.166 | 2.166 | 1.2384 | 1.4406 | 1.4406 | 1.4406 | 1.4406 | 1.4406
2020-10-19 15:00 | Summer | 2.4197 | 3.4629 | 4.9972 | 4.9972 | 4.9972 | 4.9972 | 0.86879 | 1.4217 | 1.9482 | 2.3431 | 2.3431 | 2.3431 | 2.5721 | 3.3192 | 3.8087 | 4.0664 | 4.5816 | 5.0969 | 0.98311 | 1.9403 | 2.3284 | 2.3284 | 2.3284 | 2.3284 | 1.2575 | 1.4628 | 1.4628 | 1.4628 | 1.4628 | 1.4628
2020-10-19 16:00 | Summer | 2.6102 | 3.7356 | 5.3906 | 5.3906 | 5.3906 | 5.3906 | 0.93167 | 1.5245 | 2.0892 | 2.5127 | 2.5127 | 2.5127 | 2.534 | 3.2701 | 3.7523 | 4.0061 | 4.5138 | 5.0214 | 0.96406 | 1.9027 | 2.2833 | 2.2833 | 2.2833 | 2.2833 | 1.1813 | 1.3741 | 1.3741 | 1.3741 | 1.3741 | 1.3741
2020-10-19 17:00 | Summer | 2.3625 | 3.3811 | 4.8791 | 4.8791 | 4.8791 | 4.8791 | 0.86879 | 1.4217 | 1.9482 | 2.3431 | 2.3431 | 2.3431 | 2.4777 | 3.1974 | 3.669 | 3.9172 | 4.4135 | 4.9099 | 0.80402 | 1.5869 | 1.9042 | 1.9042 | 1.9042 | 1.9042 | 1.1432 | 1.3298 | 1.3298 | 1.3298 | 1.3298 | 1.3298
2020-10-19 18:00 | Summer | 1.7956 | 2.5698 | 3.7083 | 3.7083 | 3.7083 | 3.7083 | 0.62016 | 1.0148 | 1.3907 | 1.6725 | 1.6725 | 1.6725 | 2.3054 | 2.975 | 3.4138 | 3.6447 | 4.1065 | 4.5683 | 0.76972 | 1.5192 | 1.823 | 1.823 | 1.823 | 1.823 | 0.83251 | 0.96843 | 0.96843 | 0.96843 | 0.96843 | 0.96843
2020-10-19 19:00 | Summer | 1.1622 | 1.6633 | 2.4002 | 2.4002 | 2.4002 | 2.4002 | 0.44314 | 0.72513 | 0.9937 | 1.1951 | 1.1951 | 1.1951 | 2.0914 | 2.699 | 3.097 | 3.3065 | 3.7254 | 4.1444 | 0.88785 | 1.7523 | 2.1028 | 2.1028 | 2.1028 | 2.1028 | 0.66721 | 0.77614 | 0.77614 | 0.77614 | 0.77614 | 0.77614
2020-10-19 20:00 | Summer | 1.0479 | 1.4997 | 2.1641 | 2.1641 | 2.1641 | 2.1641 | 0.35487 | 0.5807 | 0.79577 | 0.95708 | 0.95708 | 0.95708 | 1.9624 | 2.5325 | 2.9059 | 3.1025 | 3.4956 | 3.8887 | 0.71256 | 1.4064 | 1.6877 | 1.6877 | 1.6877 | 1.6877 | 0.55252 | 0.64273 | 0.64273 | 0.64273 | 0.64273 | 0.64273
2020-10-19 21:00 | Summer | 1.0288 | 1.4724 | 2.1248 | 2.1248 | 2.1248 | 2.1248 | 0.38009 | 0.62197 | 0.85233 | 1.0251 | 1.0251 | 1.0251 | 1.8862 | 2.4341 | 2.7931 | 2.982 | 3.3599 | 3.7377 | 0.70875 | 1.3989 | 1.6786 | 1.6786 | 1.6786 | 1.6786 | 0.46549 | 0.54149 | 0.54149 | 0.54149 | 0.54149 | 0.54149
2020-10-19 22:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.34008 | 0.5565 | 0.76261 | 0.9172 | 0.9172 | 0.9172 | 1.8481 | 2.3849 | 2.7366 | 2.9218 | 3.292 | 3.6622 | 0.64016 | 1.2635 | 1.5162 | 1.5162 | 1.5162 | 1.5162 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-10-19 23:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.32871 | 0.53789 | 0.7371 | 0.88652 | 0.88652 | 0.88652 | 1.7528 | 2.262 | 2.5956 | 2.7712 | 3.1223 | 3.4734 | 0.60587 | 1.1958 | 1.435 | 1.435 | 1.435 | 1.435 | 0.41919 | 0.48763 | 0.48763 | 0.48763 | 0.48763 | 0.48763
2020-10-20 | Summer | 0.91452 | 1.3088 | 1.8887 | 1.8887 | 1.8887 | 1.8887 | 0.30578 | 0.50037 | 0.68569 | 0.82468 | 0.82468 | 0.82468 | 1.6672 | 2.1515 | 2.4688 | 2.6358 | 2.9698 | 3.3038 | 0.59825 | 1.1808 | 1.4169 | 1.4169 | 1.4169 | 1.4169 | 0.43821 | 0.50975 | 0.50975 | 0.50975 | 0.50975 | 0.50975
2020-10-20 01:00 | Summer | 0.91452 | 1.3088 | 1.8887 | 1.8887 | 1.8887 | 1.8887 | 0.31722 | 0.51909 | 0.71134 | 0.85554 | 0.85554 | 0.85554 | 1.6385 | 2.1145 | 2.4263 | 2.5904 | 2.9187 | 3.2469 | 0.56395 | 1.1131 | 1.3357 | 1.3357 | 1.3357 | 1.3357 | 0.41104 | 0.47815 | 0.47815 | 0.47815 | 0.47815 | 0.47815
2020-10-20 02:00 | Summer | 0.89547 | 1.2816 | 1.8493 | 1.8493 | 1.8493 | 1.8493 | 0.30579 | 0.50038 | 0.68571 | 0.82471 | 0.82471 | 0.82471 | 1.5623 | 2.0161 | 2.3135 | 2.4699 | 2.7829 | 3.0959 | 0.54871 | 1.083 | 1.2996 | 1.2996 | 1.2996 | 1.2996 | 0.41896 | 0.48736 | 0.48736 | 0.48736 | 0.48736 | 0.48736
2020-10-20 03:00 | Summer | 0.91452 | 1.3088 | 1.8887 | 1.8887 | 1.8887 | 1.8887 | 0.3037 | 0.49697 | 0.68103 | 0.81908 | 0.81908 | 0.81908 | 1.5623 | 2.0161 | 2.3135 | 2.4699 | 2.7829 | 3.0959 | 0.55252 | 1.0905 | 1.3086 | 1.3086 | 1.3086 | 1.3086 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-10-20 04:00 | Summer | 1.0552 | 1.5101 | 2.1791 | 2.1791 | 2.1791 | 2.1791 | 0.33151 | 0.54247 | 0.74339 | 0.89407 | 0.89407 | 0.89407 | 1.5444 | 1.993 | 2.2869 | 2.4416 | 2.751 | 3.0604 | 0.6173 | 1.2184 | 1.462 | 1.462 | 1.462 | 1.462 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-10-20 05:00 | Summer | 1.2575 | 1.7996 | 2.5969 | 2.5969 | 2.5969 | 2.5969 | 0.38828 | 0.63537 | 0.87069 | 1.0472 | 1.0472 | 1.0472 | 1.6766 | 2.1636 | 2.4827 | 2.6507 | 2.9865 | 3.3224 | 0.66684 | 1.3161 | 1.5794 | 1.5794 | 1.5794 | 1.5794 | 0.55584 | 0.64659 | 0.64659 | 0.64659 | 0.64659 | 0.64659
2020-10-20 06:00 | Summer | 1.352 | 1.935 | 2.7923 | 2.7923 | 2.7923 | 2.7923 | 0.48012 | 0.78565 | 1.0766 | 1.2949 | 1.2949 | 1.2949 | 1.7876 | 2.3069 | 2.6471 | 2.8261 | 3.1842 | 3.5424 | 0.68208 | 1.3462 | 1.6155 | 1.6155 | 1.6155 | 1.6155 | 0.79472 | 0.92447 | 0.92447 | 0.92447 | 0.92447 | 0.92447
2020-10-20 07:00 | Summer | 1.7719 | 2.5359 | 3.6593 | 3.6593 | 3.6593 | 3.6593 | 0.57729 | 0.94465 | 1.2945 | 1.5569 | 1.5569 | 1.5569 | 2.138 | 2.7591 | 3.1659 | 3.3801 | 3.8084 | 4.2367 | 0.99454 | 1.9629 | 2.3555 | 2.3555 | 2.3555 | 2.3555 | 0.93611 | 1.0889 | 1.0889 | 1.0889 | 1.0889 | 1.0889
2020-10-20 08:00 | Summer | 2.191 | 3.1357 | 4.525 | 4.525 | 4.525 | 4.525 | 0.6916 | 1.1317 | 1.5509 | 1.8652 | 1.8652 | 1.8652 | 2.3435 | 3.0242 | 3.4702 | 3.7049 | 4.1744 | 4.6438 | 1.0174 | 2.008 | 2.4096 | 2.4096 | 2.4096 | 2.4096 | 1.1622 | 1.352 | 1.352 | 1.352 | 1.352 | 1.352
2020-10-20 09:00 | Summer | 2.5149 | 3.5993 | 5.1939 | 5.1939 | 5.1939 | 5.1939 | 0.75734 | 1.2393 | 1.6983 | 2.0425 | 2.0425 | 2.0425 | 2.4768 | 3.1963 | 3.6677 | 3.9158 | 4.4119 | 4.9081 | 1.1165 | 2.2036 | 2.6443 | 2.6443 | 2.6443 | 2.6443 | 1.2194 | 1.4184 | 1.4184 | 1.4184 | 1.4184 | 1.4184
2020-10-20 10:00 | Summer | 2.3054 | 3.2993 | 4.7611 | 4.7611 | 4.7611 | 4.7611 | 0.76591 | 1.2533 | 1.7175 | 2.0656 | 2.0656 | 2.0656 | 2.4768 | 3.1963 | 3.6677 | 3.9158 | 4.4119 | 4.9081 | 1.0098 | 1.993 | 2.3916 | 2.3916 | 2.3916 | 2.3916 | 1.2956 | 1.5071 | 1.5071 | 1.5071 | 1.5071 | 1.5071
2020-10-20 11:00 | Summer | 2.3054 | 3.2993 | 4.7611 | 4.7611 | 4.7611 | 4.7611 | 0.7802 | 1.2767 | 1.7495 | 2.1042 | 2.1042 | 2.1042 | 2.4578 | 3.1717 | 3.6395 | 3.8856 | 4.378 | 4.8704 | 1.0212 | 2.0156 | 2.4187 | 2.4187 | 2.4187 | 2.4187 | 1.2575 | 1.4628 | 1.4628 | 1.4628 | 1.4628 | 1.4628
2020-10-20 12:00 | Summer | 2.4387 | 3.4902 | 5.0365 | 5.0365 | 5.0365 | 5.0365 | 0.8545 | 1.3983 | 1.9162 | 2.3046 | 2.3046 | 2.3046 | 2.6483 | 3.4176 | 3.9216 | 4.1869 | 4.7174 | 5.2479 | 0.92976 | 1.8351 | 2.2021 | 2.2021 | 2.2021 | 2.2021 | 1.2956 | 1.5071 | 1.5071 | 1.5071 | 1.5071 | 1.5071
2020-10-20 13:00 | Summer | 2.4006 | 3.4357 | 4.9578 | 4.9578 | 4.9578 | 4.9578 | 0.88594 | 1.4497 | 1.9867 | 2.3894 | 2.3894 | 2.3894 | 2.6293 | 3.393 | 3.8934 | 4.1567 | 4.6835 | 5.2102 | 0.93738 | 1.8501 | 2.2201 | 2.2201 | 2.2201 | 2.2201 | 1.3146 | 1.5293 | 1.5293 | 1.5293 | 1.5293 | 1.5293
2020-10-20 14:00 | Summer | 2.3435 | 3.3539 | 4.8398 | 4.8398 | 4.8398 | 4.8398 | 0.97168 | 1.59 | 2.1789 | 2.6206 | 2.6206 | 2.6206 | 2.6864 | 3.4668 | 3.978 | 4.2471 | 4.7853 | 5.3234 | 0.91452 | 1.805 | 2.166 | 2.166 | 2.166 | 2.166 | 1.2575 | 1.4628 | 1.4628 | 1.4628 | 1.4628 | 1.4628
2020-10-20 15:00 | Summer | 2.3755 | 3.3997 | 4.9059 | 4.9059 | 4.9059 | 4.9059 | 1.0803 | 1.7677 | 2.4224 | 2.9135 | 2.9135 | 2.9135 | 2.6483 | 3.4176 | 3.9216 | 4.1869 | 4.7174 | 5.2479 | 0.91071 | 1.7975 | 2.1569 | 2.1569 | 2.1569 | 2.1569 | 1.3527 | 1.5736 | 1.5736 | 1.5736 | 1.5736 | 1.5736
2020-10-20 16:00 | Summer | 2.4768 | 3.5447 | 5.1152 | 5.1152 | 5.1152 | 5.1152 | 1.0574 | 1.7303 | 2.3712 | 2.8518 | 2.8518 | 2.8518 | 2.6102 | 3.3684 | 3.8652 | 4.1266 | 4.6495 | 5.1724 | 0.94501 | 1.8651 | 2.2382 | 2.2382 | 2.2382 | 2.2382 | 1.2194 | 1.4184 | 1.4184 | 1.4184 | 1.4184 | 1.4184
2020-10-20 17:00 | Summer | 2.3539 | 3.3687 | 4.8612 | 4.8612 | 4.8612 | 4.8612 | 1.0946 | 1.7911 | 2.4545 | 2.952 | 2.952 | 2.952 | 2.5324 | 3.268 | 3.75 | 4.0036 | 4.511 | 5.0183 | 0.88854 | 1.7537 | 2.1044 | 2.1044 | 2.1044 | 2.1044 | 1.2194 | 1.4184 | 1.4184 | 1.4184 | 1.4184 | 1.4184
2020-10-20 18:00 | Summer | 1.7 | 2.433 | 3.5109 | 3.5109 | 3.5109 | 3.5109 | 0.69732 | 1.1411 | 1.5637 | 1.8807 | 1.8807 | 1.8807 | 2.2866 | 2.9508 | 3.3859 | 3.615 | 4.073 | 4.5311 | 0.84212 | 1.6621 | 1.9945 | 1.9945 | 1.9945 | 1.9945 | 0.89607 | 1.0424 | 1.0424 | 1.0424 | 1.0424 | 1.0424
2020-10-20 19:00 | Summer | 1.2007 | 1.7184 | 2.4797 | 2.4797 | 2.4797 | 2.4797 | 0.61158 | 1.0008 | 1.3714 | 1.6494 | 1.6494 | 1.6494 | 2.0623 | 2.6614 | 3.0539 | 3.2604 | 3.6736 | 4.0867 | 0.74227 | 1.465 | 1.758 | 1.758 | 1.758 | 1.758 | 0.63833 | 0.74254 | 0.74254 | 0.74254 | 0.74254 | 0.74254
2020-10-20 20:00 | Summer | 1.105 | 1.5815 | 2.2822 | 2.2822 | 2.2822 | 2.2822 | 0.55443 | 0.90724 | 1.2433 | 1.4953 | 1.4953 | 1.4953 | 2.0005 | 2.5816 | 2.9624 | 3.1627 | 3.5635 | 3.9643 | 0.76972 | 1.5192 | 1.823 | 1.823 | 1.823 | 1.823 | 0.60968 | 0.70922 | 0.70922 | 0.70922 | 0.70922 | 0.70922
2020-10-20 21:00 | Summer | 1.0288 | 1.4724 | 2.1248 | 2.1248 | 2.1248 | 2.1248 | 0.51727 | 0.84645 | 1.1599 | 1.3951 | 1.3951 | 1.3951 | 1.8862 | 2.4341 | 2.7931 | 2.982 | 3.3599 | 3.7377 | 0.84974 | 1.6771 | 2.0125 | 2.0125 | 2.0125 | 2.0125 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-10-20 22:00 | Summer | 0.99784 | 1.4281 | 2.0608 | 2.0608 | 2.0608 | 2.0608 | 0.44011 | 0.72018 | 0.98691 | 1.187 | 1.187 | 1.187 | 1.81 | 2.3358 | 2.6802 | 2.8615 | 3.2241 | 3.5867 | 0.76659 | 1.513 | 1.8156 | 1.8156 | 1.8156 | 1.8156 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-10-20 23:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.35152 | 0.57521 | 0.78825 | 0.94803 | 0.94803 | 0.94803 | 1.6576 | 2.1391 | 2.4545 | 2.6205 | 2.9526 | 3.2847 | 0.67827 | 1.3387 | 1.6064 | 1.6064 | 1.6064 | 1.6064 | 0.43832 | 0.50989 | 0.50989 | 0.50989 | 0.50989 | 0.50989
2020-10-21 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.31741 | 0.51939 | 0.71176 | 0.85604 | 0.85604 | 0.85604 | 1.5814 | 2.0407 | 2.3417 | 2.5001 | 2.8169 | 3.1337 | 0.5792 | 1.1431 | 1.3718 | 1.3718 | 1.3718 | 1.3718 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-10-21 01:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.33179 | 0.54292 | 0.744 | 0.89481 | 0.89481 | 0.89481 | 1.6576 | 2.1391 | 2.4545 | 2.6205 | 2.9526 | 3.2847 | 0.59063 | 1.1657 | 1.3989 | 1.3989 | 1.3989 | 1.3989 | 0.43821 | 0.50975 | 0.50975 | 0.50975 | 0.50975 | 0.50975
2020-10-21 02:00 | Summer | 0.91452 | 1.3088 | 1.8887 | 1.8887 | 1.8887 | 1.8887 | 0.35152 | 0.57521 | 0.78825 | 0.94803 | 0.94803 | 0.94803 | 1.5623 | 2.0161 | 2.3135 | 2.4699 | 2.7829 | 3.0959 | 0.55633 | 1.098 | 1.3176 | 1.3176 | 1.3176 | 1.3176 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-10-21 03:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.32307 | 0.52866 | 0.72446 | 0.87131 | 0.87131 | 0.87131 | 1.5623 | 2.0161 | 2.3135 | 2.4699 | 2.7829 | 3.0959 | 0.77353 | 1.5267 | 1.832 | 1.832 | 1.832 | 1.832 | 0.43466 | 0.50562 | 0.50562 | 0.50562 | 0.50562 | 0.50562
2020-10-21 04:00 | Summer | 1.0149 | 1.4524 | 2.0959 | 2.0959 | 2.0959 | 2.0959 | 0.31722 | 0.51909 | 0.71134 | 0.85554 | 0.85554 | 0.85554 | 1.5814 | 2.0407 | 2.3417 | 2.5001 | 2.8169 | 3.1337 | 0.56014 | 1.1055 | 1.3267 | 1.3267 | 1.3267 | 1.3267 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-10-21 05:00 | Summer | 1.24 | 1.7747 | 2.561 | 2.561 | 2.561 | 2.561 | 0.40867 | 0.66874 | 0.91642 | 1.1022 | 1.1022 | 1.1022 | 1.6957 | 2.1882 | 2.5109 | 2.6808 | 3.0205 | 3.3602 | 0.62111 | 1.2259 | 1.4711 | 1.4711 | 1.4711 | 1.4711 | 0.57158 | 0.6649 | 0.6649 | 0.6649 | 0.6649 | 0.6649
2020-10-21 06:00 | Summer | 1.3337 | 1.9087 | 2.7543 | 2.7543 | 2.7543 | 2.7543 | 0.5287 | 0.86515 | 1.1856 | 1.4259 | 1.4259 | 1.4259 | 1.8656 | 2.4075 | 2.7625 | 2.9494 | 3.3231 | 3.6968 | 0.67446 | 1.3312 | 1.5974 | 1.5974 | 1.5974 | 1.5974 | 0.80021 | 0.93085 | 0.93085 | 0.93085 | 0.93085 | 0.93085
2020-10-21 07:00 | Summer | 1.839 | 2.6319 | 3.798 | 3.798 | 3.798 | 3.798 | 0.6716 | 1.099 | 1.506 | 1.8113 | 1.8113 | 1.8113 | 2.1494 | 2.7737 | 3.1828 | 3.3981 | 3.8287 | 4.2593 | 0.89547 | 1.7674 | 2.1208 | 2.1208 | 2.1208 | 2.1208 | 0.97134 | 1.1299 | 1.1299 | 1.1299 | 1.1299 | 1.1299
2020-10-21 08:00 | Summer | 2.2482 | 3.2175 | 4.643 | 4.643 | 4.643 | 4.643 | 0.81735 | 1.3375 | 1.8328 | 2.2044 | 2.2044 | 2.2044 | 2.5156 | 3.2463 | 3.7251 | 3.9771 | 4.481 | 4.985 | 0.91833 | 1.8125 | 2.175 | 2.175 | 2.175 | 2.175 | 1.1622 | 1.352 | 1.352 | 1.352 | 1.352 | 1.352
2020-10-21 09:00 | Summer | 2.4182 | 3.4608 | 4.9941 | 4.9941 | 4.9941 | 4.9941 | 0.76305 | 1.2486 | 1.7111 | 2.0579 | 2.0579 | 2.0579 | 2.6663 | 3.4408 | 3.9482 | 4.2153 | 4.7494 | 5.2835 | 0.91071 | 1.7975 | 2.1569 | 2.1569 | 2.1569 | 2.1569 | 1.2956 | 1.5071 | 1.5071 | 1.5071 | 1.5071 | 1.5071
2020-10-21 10:00 | Summer | 2.4578 | 3.5175 | 5.0759 | 5.0759 | 5.0759 | 5.0759 | 0.79735 | 1.3047 | 1.788 | 2.1504 | 2.1504 | 2.1504 | 2.7626 | 3.5651 | 4.0909 | 4.3676 | 4.921 | 5.4745 | 0.91452 | 1.805 | 2.166 | 2.166 | 2.166 | 2.166 | 1.3908 | 1.6179 | 1.6179 | 1.6179 | 1.6179 | 1.6179
2020-10-21 11:00 | Summer | 2.4578 | 3.5175 | 5.0759 | 5.0759 | 5.0759 | 5.0759 | 1.126 | 1.8425 | 2.525 | 3.0368 | 3.0368 | 3.0368 | 2.7245 | 3.5159 | 4.0344 | 4.3073 | 4.8531 | 5.3989 | 0.88785 | 1.7523 | 2.1028 | 2.1028 | 2.1028 | 2.1028 | 1.448 | 1.6844 | 1.6844 | 1.6844 | 1.6844 | 1.6844
2020-10-21 12:00 | Summer | 2.553 | 3.6538 | 5.2726 | 5.2726 | 5.2726 | 5.2726 | 1.1774 | 1.9267 | 2.6403 | 3.1755 | 3.1755 | 3.1755 | 2.7626 | 3.5651 | 4.0909 | 4.3676 | 4.921 | 5.4745 | 0.90309 | 1.7824 | 2.1389 | 2.1389 | 2.1389 | 2.1389 | 1.467 | 1.7066 | 1.7066 | 1.7066 | 1.7066 | 1.7066
2020-10-21 13:00 | Summer | 2.7245 | 3.8992 | 5.6267 | 5.6267 | 5.6267 | 5.6267 | 1.0546 | 1.7256 | 2.3648 | 2.8441 | 2.8441 | 2.8441 | 2.8198 | 3.6389 | 4.1755 | 4.4579 | 5.0228 | 5.5877 | 0.90309 | 1.7824 | 2.1389 | 2.1389 | 2.1389 | 2.1389 | 1.448 | 1.6844 | 1.6844 | 1.6844 | 1.6844 | 1.6844
2020-10-21 14:00 | Summer | 2.5911 | 3.7083 | 5.3513 | 5.3513 | 5.3513 | 5.3513 | 1.1146 | 1.8238 | 2.4993 | 3.006 | 3.006 | 3.006 | 2.8388 | 3.6634 | 4.2037 | 4.4881 | 5.0568 | 5.6255 | 1.0784 | 2.1284 | 2.554 | 2.554 | 2.554 | 2.554 | 1.3718 | 1.5957 | 1.5957 | 1.5957 | 1.5957 | 1.5957
2020-10-21 15:00 | Summer | 2.553 | 3.6538 | 5.2726 | 5.2726 | 5.2726 | 5.2726 | 1.0631 | 1.7397 | 2.384 | 2.8672 | 2.8672 | 2.8672 | 2.8193 | 3.6383 | 4.1749 | 4.4573 | 5.0221 | 5.5869 | 1.0555 | 2.0832 | 2.4999 | 2.4999 | 2.4999 | 2.4999 | 1.3146 | 1.5293 | 1.5293 | 1.5293 | 1.5293 | 1.5293
2020-10-21 16:00 | Summer | 2.4578 | 3.5175 | 5.0759 | 5.0759 | 5.0759 | 5.0759 | 1.0688 | 1.749 | 2.3968 | 2.8826 | 2.8826 | 2.8826 | 2.8388 | 3.6634 | 4.2037 | 4.4881 | 5.0568 | 5.6255 | 0.93357 | 1.8426 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 1.2956 | 1.5071 | 1.5071 | 1.5071 | 1.5071 | 1.5071
2020-10-21 17:00 | Summer | 2.2374 | 3.2021 | 4.6208 | 4.6208 | 4.6208 | 4.6208 | 0.94596 | 1.5479 | 2.1212 | 2.5512 | 2.5512 | 2.5512 | 2.63 | 3.3939 | 3.8944 | 4.1579 | 4.6847 | 5.2116 | 0.80783 | 1.5944 | 1.9133 | 1.9133 | 1.9133 | 1.9133 | 1.2384 | 1.4406 | 1.4406 | 1.4406 | 1.4406 | 1.4406
2020-10-21 18:00 | Summer | 1.7248 | 2.4684 | 3.562 | 3.562 | 3.562 | 3.562 | 0.74019 | 1.2112 | 1.6598 | 1.9963 | 1.9963 | 1.9963 | 2.4186 | 3.1211 | 3.5814 | 3.8237 | 4.3082 | 4.7927 | 0.70113 | 1.3838 | 1.6606 | 1.6606 | 1.6606 | 1.6606 | 0.90933 | 1.0578 | 1.0578 | 1.0578 | 1.0578 | 1.0578
2020-10-21 19:00 | Summer | 1.1432 | 1.636 | 2.3609 | 2.3609 | 2.3609 | 2.3609 | 0.58015 | 0.94933 | 1.3009 | 1.5646 | 1.5646 | 1.5646 | 2.3435 | 3.0242 | 3.4702 | 3.7049 | 4.1744 | 4.6438 | 0.93738 | 1.8501 | 2.2201 | 2.2201 | 2.2201 | 2.2201 | 0.724 | 0.8422 | 0.8422 | 0.8422 | 0.8422 | 0.8422
2020-10-21 20:00 | Summer | 1.105 | 1.5815 | 2.2822 | 2.2822 | 2.2822 | 2.2822 | 0.55443 | 0.90724 | 1.2433 | 1.4953 | 1.4953 | 1.4953 | 2.1709 | 2.8015 | 3.2147 | 3.4321 | 3.867 | 4.3019 | 0.86879 | 1.7147 | 2.0577 | 2.0577 | 2.0577 | 2.0577 | 0.5718 | 0.66515 | 0.66515 | 0.66515 | 0.66515 | 0.66515
2020-10-21 21:00 | Summer | 1.0592 | 1.5159 | 2.1876 | 2.1876 | 2.1876 | 2.1876 | 0.54871 | 0.89789 | 1.2304 | 1.4799 | 1.4799 | 1.4799 | 2.0577 | 2.6554 | 3.047 | 3.2531 | 3.6653 | 4.0775 | 0.86117 | 1.6997 | 2.0396 | 2.0396 | 2.0396 | 2.0396 | 0.55265 | 0.64288 | 0.64288 | 0.64288 | 0.64288 | 0.64288
2020-10-21 22:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.50584 | 0.82774 | 1.1343 | 1.3642 | 1.3642 | 1.3642 | 1.8672 | 2.4095 | 2.7649 | 2.9519 | 3.3259 | 3.7 | 0.84212 | 1.6621 | 1.9945 | 1.9945 | 1.9945 | 1.9945 | 0.47124 | 0.54818 | 0.54818 | 0.54818 | 0.54818 | 0.54818
2020-10-21 23:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.44011 | 0.72018 | 0.98691 | 1.187 | 1.187 | 1.187 | 1.7528 | 2.262 | 2.5956 | 2.7712 | 3.1223 | 3.4734 | 0.62492 | 1.2334 | 1.4801 | 1.4801 | 1.4801 | 1.4801 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-10-22 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.32239 | 0.52755 | 0.72293 | 0.86947 | 0.86947 | 0.86947 | 1.6576 | 2.1391 | 2.4545 | 2.6205 | 2.9526 | 3.2847 | 0.65922 | 1.3011 | 1.5613 | 1.5613 | 1.5613 | 1.5613 | 0.43863 | 0.51024 | 0.51024 | 0.51024 | 0.51024 | 0.51024
2020-10-22 01:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.32294 | 0.52844 | 0.72416 | 0.87095 | 0.87095 | 0.87095 | 1.5814 | 2.0407 | 2.3417 | 2.5001 | 2.8169 | 3.1337 | 0.78115 | 1.5417 | 1.8501 | 1.8501 | 1.8501 | 1.8501 | 0.43821 | 0.50975 | 0.50975 | 0.50975 | 0.50975 | 0.50975
2020-10-22 02:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.30579 | 0.50038 | 0.68571 | 0.82471 | 0.82471 | 0.82471 | 1.6004 | 2.0653 | 2.3699 | 2.5302 | 2.8508 | 3.1714 | 0.52585 | 1.0379 | 1.2454 | 1.2454 | 1.2454 | 1.2454 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-10-22 03:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.30579 | 0.50038 | 0.68571 | 0.82471 | 0.82471 | 0.82471 | 1.5433 | 1.9915 | 2.2852 | 2.4398 | 2.749 | 3.0581 | 0.53728 | 1.0604 | 1.2725 | 1.2725 | 1.2725 | 1.2725 | 0.41919 | 0.48763 | 0.48763 | 0.48763 | 0.48763 | 0.48763
2020-10-22 04:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.33151 | 0.54247 | 0.74339 | 0.89407 | 0.89407 | 0.89407 | 1.6576 | 2.1391 | 2.4545 | 2.6205 | 2.9526 | 3.2847 | 0.52204 | 1.0303 | 1.2364 | 1.2364 | 1.2364 | 1.2364 | 0.46666 | 0.54284 | 0.54284 | 0.54284 | 0.54284 | 0.54284
2020-10-22 05:00 | Summer | 1.1824 | 1.6922 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 0.35152 | 0.57521 | 0.78825 | 0.94803 | 0.94803 | 0.94803 | 1.7558 | 2.2658 | 2.6 | 2.7758 | 3.1276 | 3.4793 | 0.56776 | 1.1206 | 1.3447 | 1.3447 | 1.3447 | 1.3447 | 0.58986 | 0.68616 | 0.68616 | 0.68616 | 0.68616 | 0.68616
2020-10-22 06:00 | Summer | 1.3238 | 1.8946 | 2.7339 | 2.7339 | 2.7339 | 2.7339 | 0.54585 | 0.89321 | 1.224 | 1.4721 | 1.4721 | 1.4721 | 1.8273 | 2.3581 | 2.7059 | 2.8889 | 3.255 | 3.621 | 0.87642 | 1.7298 | 2.0757 | 2.0757 | 2.0757 | 2.0757 | 0.75831 | 0.88211 | 0.88211 | 0.88211 | 0.88211 | 0.88211
2020-10-22 07:00 | Summer | 1.6957 | 2.4268 | 3.5019 | 3.5019 | 3.5019 | 3.5019 | 0.62587 | 1.0242 | 1.4035 | 1.688 | 1.688 | 1.688 | 2.2482 | 2.9013 | 3.3291 | 3.5543 | 4.0047 | 4.4551 | 0.92976 | 1.8351 | 2.2021 | 2.2021 | 2.2021 | 2.2021 | 0.9645 | 1.122 | 1.122 | 1.122 | 1.122 | 1.122
2020-10-22 08:00 | Summer | 2.2863 | 3.2721 | 4.7217 | 4.7217 | 4.7217 | 4.7217 | 0.65731 | 1.0756 | 1.474 | 1.7727 | 1.7727 | 1.7727 | 2.4959 | 3.2209 | 3.6959 | 3.9459 | 4.4459 | 4.9459 | 1.0136 | 2.0005 | 2.4006 | 2.4006 | 2.4006 | 2.4006 | 1.2575 | 1.4628 | 1.4628 | 1.4628 | 1.4628 | 1.4628
2020-10-22 09:00 | Summer | 2.4387 | 3.4902 | 5.0365 | 5.0365 | 5.0365 | 5.0365 | 0.74305 | 1.2159 | 1.6662 | 2.004 | 2.004 | 2.004 | 2.6102 | 3.3684 | 3.8652 | 4.1266 | 4.6495 | 5.1724 | 0.98692 | 1.9479 | 2.3374 | 2.3374 | 2.3374 | 2.3374 | 1.3146 | 1.5293 | 1.5293 | 1.5293 | 1.5293 | 1.5293
2020-10-22 10:00 | Summer | 2.5149 | 3.5993 | 5.1939 | 5.1939 | 5.1939 | 5.1939 | 0.79163 | 1.2954 | 1.7752 | 2.135 | 2.135 | 2.135 | 2.6102 | 3.3684 | 3.8652 | 4.1266 | 4.6495 | 5.1724 | 0.97168 | 1.9178 | 2.3013 | 2.3013 | 2.3013 | 2.3013 | 1.3908 | 1.6179 | 1.6179 | 1.6179 | 1.6179 | 1.6179
2020-10-22 11:00 | Summer | 2.4768 | 3.5447 | 5.1152 | 5.1152 | 5.1152 | 5.1152 | 0.79735 | 1.3047 | 1.788 | 2.1504 | 2.1504 | 2.1504 | 2.8002 | 3.6136 | 4.1465 | 4.427 | 4.9879 | 5.5489 | 1.0212 | 2.0156 | 2.4187 | 2.4187 | 2.4187 | 2.4187 | 1.5052 | 1.7509 | 1.7509 | 1.7509 | 1.7509 | 1.7509
2020-10-22 12:00 | Summer | 2.5911 | 3.7083 | 5.3513 | 5.3513 | 5.3513 | 5.3513 | 0.85165 | 1.3936 | 1.9098 | 2.2969 | 2.2969 | 2.2969 | 2.8392 | 3.6639 | 4.2043 | 4.4887 | 5.0574 | 5.6262 | 1.0174 | 2.008 | 2.4096 | 2.4096 | 2.4096 | 2.4096 | 1.467 | 1.7066 | 1.7066 | 1.7066 | 1.7066 | 1.7066
2020-10-22 13:00 | Summer | 2.6483 | 3.7901 | 5.4693 | 5.4693 | 5.4693 | 5.4693 | 0.85165 | 1.3936 | 1.9098 | 2.2969 | 2.2969 | 2.2969 | 2.9341 | 3.7864 | 4.3448 | 4.6387 | 5.2265 | 5.8142 | 1.0288 | 2.0306 | 2.4367 | 2.4367 | 2.4367 | 2.4367 | 1.4861 | 1.7287 | 1.7287 | 1.7287 | 1.7287 | 1.7287
2020-10-22 14:00 | Summer | 2.5664 | 3.6729 | 5.3002 | 5.3002 | 5.3002 | 5.3002 | 0.80592 | 1.3188 | 1.8072 | 2.1735 | 2.1735 | 2.1735 | 2.8579 | 3.688 | 4.2319 | 4.5182 | 5.0907 | 5.6632 | 0.86879 | 1.7147 | 2.0577 | 2.0577 | 2.0577 | 2.0577 | 1.448 | 1.6844 | 1.6844 | 1.6844 | 1.6844 | 1.6844
2020-10-22 15:00 | Summer | 2.5911 | 3.7083 | 5.3513 | 5.3513 | 5.3513 | 5.3513 | 1.0774 | 1.763 | 2.416 | 2.9058 | 2.9058 | 2.9058 | 2.8388 | 3.6634 | 4.2037 | 4.4881 | 5.0568 | 5.6255 | 0.80783 | 1.5944 | 1.9133 | 1.9133 | 1.9133 | 1.9133 | 1.3908 | 1.6179 | 1.6179 | 1.6179 | 1.6179 | 1.6179
2020-10-22 16:00 | Summer | 2.5911 | 3.7083 | 5.3513 | 5.3513 | 5.3513 | 5.3513 | 1.0586 | 1.7322 | 2.3737 | 2.8549 | 2.8549 | 2.8549 | 2.896 | 3.7372 | 4.2884 | 4.5784 | 5.1586 | 5.7387 | 0.85736 | 1.6922 | 2.0306 | 2.0306 | 2.0306 | 2.0306 | 1.3374 | 1.5557 | 1.5557 | 1.5557 | 1.5557 | 1.5557
2020-10-22 17:00 | Summer | 2.4959 | 3.572 | 5.1545 | 5.1545 | 5.1545 | 5.1545 | 1.246 | 2.039 | 2.7941 | 3.3605 | 3.3605 | 3.3605 | 2.7467 | 3.5446 | 4.0673 | 4.3424 | 4.8927 | 5.4429 | 0.80783 | 1.5944 | 1.9133 | 1.9133 | 1.9133 | 1.9133 | 1.3527 | 1.5736 | 1.5736 | 1.5736 | 1.5736 | 1.5736
2020-10-22 18:00 | Summer | 1.9618 | 2.8077 | 4.0516 | 4.0516 | 4.0516 | 4.0516 | 1.0488 | 1.7163 | 2.3519 | 2.8287 | 2.8287 | 2.8287 | 2.4197 | 3.1225 | 3.583 | 3.8254 | 4.3101 | 4.7949 | 0.79258 | 1.5643 | 1.8772 | 1.8772 | 1.8772 | 1.8772 | 0.91125 | 1.06 | 1.06 | 1.06 | 1.06 | 1.06
2020-10-22 19:00 | Summer | 1.5433 | 2.2086 | 3.1872 | 3.1872 | 3.1872 | 3.1872 | 0.67743 | 1.1085 | 1.5191 | 1.827 | 1.827 | 1.827 | 2.3203 | 2.9943 | 3.4359 | 3.6683 | 4.1331 | 4.598 | 0.73924 | 1.459 | 1.7508 | 1.7508 | 1.7508 | 1.7508 | 0.70494 | 0.82004 | 0.82004 | 0.82004 | 0.82004 | 0.82004
2020-10-22 20:00 | Summer | 1.431 | 2.0479 | 2.9553 | 2.9553 | 2.9553 | 2.9553 | 0.6173 | 1.0101 | 1.3842 | 1.6648 | 1.6648 | 1.6648 | 2.0958 | 2.7046 | 3.1034 | 3.3133 | 3.7332 | 4.153 | 0.80021 | 1.5794 | 1.8952 | 1.8952 | 1.8952 | 1.8952 | 0.59189 | 0.68853 | 0.68853 | 0.68853 | 0.68853 | 0.68853
2020-10-22 21:00 | Summer | 1.2765 | 1.8269 | 2.6363 | 2.6363 | 2.6363 | 2.6363 | 0.65445 | 1.0709 | 1.4676 | 1.765 | 1.765 | 1.765 | 2.0577 | 2.6554 | 3.047 | 3.2531 | 3.6653 | 4.0775 | 0.76972 | 1.5192 | 1.823 | 1.823 | 1.823 | 1.823 | 0.57158 | 0.6649 | 0.6649 | 0.6649 | 0.6649 | 0.6649
2020-10-22 22:00 | Summer | 1.1622 | 1.6633 | 2.4002 | 2.4002 | 2.4002 | 2.4002 | 0.48584 | 0.79501 | 1.0895 | 1.3103 | 1.3103 | 1.3103 | 1.9624 | 2.5325 | 2.9059 | 3.1025 | 3.4956 | 3.8887 | 0.75067 | 1.4816 | 1.7779 | 1.7779 | 1.7779 | 1.7779 | 0.47636 | 0.55414 | 0.55414 | 0.55414 | 0.55414 | 0.55414
2020-10-22 23:00 | Summer | 1.0484 | 1.5005 | 2.1653 | 2.1653 | 2.1653 | 2.1653 | 0.44011 | 0.72018 | 0.98691 | 1.187 | 1.187 | 1.187 | 1.81 | 2.3358 | 2.6802 | 2.8615 | 3.2241 | 3.5867 | 0.64397 | 1.271 | 1.5252 | 1.5252 | 1.5252 | 1.5252 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-10-23 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.44297 | 0.72486 | 0.99332 | 1.1947 | 1.1947 | 1.1947 | 1.6957 | 2.1882 | 2.5109 | 2.6808 | 3.0205 | 3.3602 | 0.60019 | 1.1846 | 1.4215 | 1.4215 | 1.4215 | 1.4215 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-10-23 01:00 | Summer | 0.89595 | 1.2823 | 1.8503 | 1.8503 | 1.8503 | 1.8503 | 0.39153 | 0.64068 | 0.87797 | 1.0559 | 1.0559 | 1.0559 | 1.6385 | 2.1145 | 2.4263 | 2.5904 | 2.9187 | 3.2469 | 0.60587 | 1.1958 | 1.435 | 1.435 | 1.435 | 1.435 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-10-23 02:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.4544 | 0.74356 | 1.019 | 1.2255 | 1.2255 | 1.2255 | 1.6195 | 2.0899 | 2.3981 | 2.5603 | 2.8847 | 3.2092 | 0.56776 | 1.1206 | 1.3447 | 1.3447 | 1.3447 | 1.3447 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-10-23 03:00 | Summer | 0.92191 | 1.3194 | 1.9039 | 1.9039 | 1.9039 | 1.9039 | 0.37724 | 0.6173 | 0.84593 | 1.0174 | 1.0174 | 1.0174 | 1.6195 | 2.0899 | 2.3981 | 2.5603 | 2.8847 | 3.2092 | 0.56776 | 1.1206 | 1.3447 | 1.3447 | 1.3447 | 1.3447 | 0.45724 | 0.5319 | 0.5319 | 0.5319 | 0.5319 | 0.5319
2020-10-23 04:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.40867 | 0.66874 | 0.91642 | 1.1022 | 1.1022 | 1.1022 | 1.6385 | 2.1145 | 2.4263 | 2.5904 | 2.9187 | 3.2469 | 0.56395 | 1.1131 | 1.3357 | 1.3357 | 1.3357 | 1.3357 | 0.47526 | 0.55285 | 0.55285 | 0.55285 | 0.55285 | 0.55285
2020-10-23 05:00 | Summer | 1.1622 | 1.6633 | 2.4002 | 2.4002 | 2.4002 | 2.4002 | 0.43154 | 0.70615 | 0.96769 | 1.1638 | 1.1638 | 1.1638 | 1.7719 | 2.2866 | 2.6238 | 2.8013 | 3.1562 | 3.5112 | 0.59063 | 1.1657 | 1.3989 | 1.3989 | 1.3989 | 1.3989 | 0.60968 | 0.70922 | 0.70922 | 0.70922 | 0.70922 | 0.70922
2020-10-23 06:00 | Summer | 1.3034 | 1.8654 | 2.6918 | 2.6918 | 2.6918 | 2.6918 | 0.62587 | 1.0242 | 1.4035 | 1.688 | 1.688 | 1.688 | 1.81 | 2.3358 | 2.6802 | 2.8615 | 3.2241 | 3.5867 | 0.6516 | 1.286 | 1.5433 | 1.5433 | 1.5433 | 1.5433 | 0.75733 | 0.88098 | 0.88098 | 0.88098 | 0.88098 | 0.88098
2020-10-23 07:00 | Summer | 1.7685 | 2.5311 | 3.6524 | 3.6524 | 3.6524 | 3.6524 | 0.70018 | 1.1457 | 1.5701 | 1.8884 | 1.8884 | 1.8884 | 2.0958 | 2.7046 | 3.1034 | 3.3133 | 3.7332 | 4.153 | 0.92595 | 1.8275 | 2.193 | 2.193 | 2.193 | 2.193 | 1.0503 | 1.2218 | 1.2218 | 1.2218 | 1.2218 | 1.2218
2020-10-23 08:00 | Summer | 2.2291 | 3.1903 | 4.6037 | 4.6037 | 4.6037 | 4.6037 | 0.75448 | 1.2346 | 1.6919 | 2.0348 | 2.0348 | 2.0348 | 2.4355 | 3.143 | 3.6065 | 3.8505 | 4.3384 | 4.8263 | 0.91833 | 1.8125 | 2.175 | 2.175 | 2.175 | 2.175 | 1.1622 | 1.352 | 1.352 | 1.352 | 1.352 | 1.352
2020-10-23 09:00 | Summer | 2.4578 | 3.5175 | 5.0759 | 5.0759 | 5.0759 | 5.0759 | 0.80878 | 1.3235 | 1.8136 | 2.1812 | 2.1812 | 2.1812 | 2.6067 | 3.3639 | 3.86 | 4.1211 | 4.6433 | 5.1655 | 0.96787 | 1.9103 | 2.2923 | 2.2923 | 2.2923 | 2.2923 | 1.3611 | 1.5833 | 1.5833 | 1.5833 | 1.5833 | 1.5833
2020-10-23 10:00 | Summer | 2.4959 | 3.572 | 5.1545 | 5.1545 | 5.1545 | 5.1545 | 0.76305 | 1.2486 | 1.7111 | 2.0579 | 2.0579 | 2.0579 | 2.7436 | 3.5405 | 4.0627 | 4.3375 | 4.8871 | 5.4367 | 0.9793 | 1.9328 | 2.3194 | 2.3194 | 2.3194 | 2.3194 | 1.448 | 1.6844 | 1.6844 | 1.6844 | 1.6844 | 1.6844
2020-10-23 11:00 | Summer | 2.6483 | 3.7901 | 5.4693 | 5.4693 | 5.4693 | 5.4693 | 0.94596 | 1.5479 | 2.1212 | 2.5512 | 2.5512 | 2.5512 | 3.0675 | 3.9585 | 4.5423 | 4.8495 | 5.464 | 6.0785 | 0.9069 | 1.7899 | 2.1479 | 2.1479 | 2.1479 | 2.1479 | 1.6576 | 1.9282 | 1.9282 | 1.9282 | 1.9282 | 1.9282
2020-10-23 12:00 | Summer | 2.6674 | 3.8174 | 5.5087 | 5.5087 | 5.5087 | 5.5087 | 1.0174 | 1.6648 | 2.2814 | 2.7439 | 2.7439 | 2.7439 | 3.0332 | 3.9142 | 4.4915 | 4.7953 | 5.4029 | 6.0106 | 0.84212 | 1.6621 | 1.9945 | 1.9945 | 1.9945 | 1.9945 | 1.5242 | 1.7731 | 1.7731 | 1.7731 | 1.7731 | 1.7731
2020-10-23 13:00 | Summer | 2.7245 | 3.8992 | 5.6267 | 5.6267 | 5.6267 | 5.6267 | 0.98882 | 1.6181 | 2.2174 | 2.6668 | 2.6668 | 2.6668 | 3.2008 | 4.1306 | 4.7398 | 5.0604 | 5.7016 | 6.3428 | 0.83069 | 1.6395 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 1.5814 | 1.8395 | 1.8395 | 1.8395 | 1.8395 | 1.8395
2020-10-23 14:00 | Summer | 2.7952 | 4.0003 | 5.7726 | 5.7726 | 5.7726 | 5.7726 | 1.1317 | 1.8519 | 2.5378 | 3.0522 | 3.0522 | 3.0522 | 3.1246 | 4.0323 | 4.6269 | 4.9399 | 5.5658 | 6.1918 | 0.84974 | 1.6771 | 2.0125 | 2.0125 | 2.0125 | 2.0125 | 1.467 | 1.7066 | 1.7066 | 1.7066 | 1.7066 | 1.7066
2020-10-23 15:00 | Summer | 2.8579 | 4.0901 | 5.9022 | 5.9022 | 5.9022 | 5.9022 | 1.1803 | 1.9314 | 2.6467 | 3.1832 | 3.1832 | 3.1832 | 3.1056 | 4.0077 | 4.5987 | 4.9098 | 5.5319 | 6.154 | 0.82307 | 1.6245 | 1.9494 | 1.9494 | 1.9494 | 1.9494 | 1.467 | 1.7066 | 1.7066 | 1.7066 | 1.7066 | 1.7066
2020-10-23 16:00 | Summer | 2.7258 | 3.901 | 5.6293 | 5.6293 | 5.6293 | 5.6293 | 1.126 | 1.8425 | 2.525 | 3.0368 | 3.0368 | 3.0368 | 2.9341 | 3.7864 | 4.3448 | 4.6387 | 5.2265 | 5.8142 | 0.87642 | 1.7298 | 2.0757 | 2.0757 | 2.0757 | 2.0757 | 1.3527 | 1.5736 | 1.5736 | 1.5736 | 1.5736 | 1.5736
2020-10-23 17:00 | Summer | 2.5721 | 3.6811 | 5.3119 | 5.3119 | 5.3119 | 5.3119 | 1.0117 | 1.6555 | 2.2686 | 2.7285 | 2.7285 | 2.7285 | 2.8198 | 3.6389 | 4.1755 | 4.4579 | 5.0228 | 5.5877 | 0.80402 | 1.5869 | 1.9042 | 1.9042 | 1.9042 | 1.9042 | 1.2765 | 1.4849 | 1.4849 | 1.4849 | 1.4849 | 1.4849
2020-10-23 18:00 | Summer | 1.6765 | 2.3993 | 3.4623 | 3.4623 | 3.4623 | 3.4623 | 0.88594 | 1.4497 | 1.9867 | 2.3894 | 2.3894 | 2.3894 | 2.5149 | 3.2455 | 3.7241 | 3.976 | 4.4798 | 4.9836 | 0.80402 | 1.5869 | 1.9042 | 1.9042 | 1.9042 | 1.9042 | 1.0098 | 1.1746 | 1.1746 | 1.1746 | 1.1746 | 1.1746
2020-10-23 19:00 | Summer | 1.2003 | 1.7178 | 2.4789 | 2.4789 | 2.4789 | 2.4789 | 0.78591 | 1.286 | 1.7624 | 2.1196 | 2.1196 | 2.1196 | 2.3625 | 3.0488 | 3.4984 | 3.735 | 4.2083 | 4.6816 | 0.80783 | 1.5944 | 1.9133 | 1.9133 | 1.9133 | 1.9133 | 0.724 | 0.8422 | 0.8422 | 0.8422 | 0.8422 | 0.8422
2020-10-23 20:00 | Summer | 1.1241 | 1.6088 | 2.3215 | 2.3215 | 2.3215 | 2.3215 | 0.62873 | 1.0288 | 1.4099 | 1.6957 | 1.6957 | 1.6957 | 2.2101 | 2.8521 | 3.2727 | 3.4941 | 3.9368 | 4.3796 | 0.83831 | 1.6546 | 1.9855 | 1.9855 | 1.9855 | 1.9855 | 0.62873 | 0.73138 | 0.73138 | 0.73138 | 0.73138 | 0.73138
2020-10-23 21:00 | Summer | 1.0669 | 1.527 | 2.2035 | 2.2035 | 2.2035 | 2.2035 | 0.60587 | 0.99142 | 1.3586 | 1.634 | 1.634 | 1.634 | 2.0958 | 2.7046 | 3.1034 | 3.3133 | 3.7332 | 4.153 | 0.76972 | 1.5192 | 1.823 | 1.823 | 1.823 | 1.823 | 0.59063 | 0.68706 | 0.68706 | 0.68706 | 0.68706 | 0.68706
2020-10-23 22:00 | Summer | 1.0288 | 1.4724 | 2.1248 | 2.1248 | 2.1248 | 2.1248 | 0.59444 | 0.97271 | 1.333 | 1.6032 | 1.6032 | 1.6032 | 2.0005 | 2.5816 | 2.9624 | 3.1627 | 3.5635 | 3.9643 | 0.80783 | 1.5944 | 1.9133 | 1.9133 | 1.9133 | 1.9133 | 0.55252 | 0.64273 | 0.64273 | 0.64273 | 0.64273 | 0.64273
2020-10-23 23:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.54299 | 0.88854 | 1.2176 | 1.4644 | 1.4644 | 1.4644 | 1.8862 | 2.4341 | 2.7931 | 2.982 | 3.3599 | 3.7377 | 0.71637 | 1.4139 | 1.6967 | 1.6967 | 1.6967 | 1.6967 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-10-24 | Summer | 0.91613 | 1.3111 | 1.892 | 1.892 | 1.892 | 1.892 | 0.42582 | 0.6968 | 0.95487 | 1.1484 | 1.1484 | 1.1484 | 1.8284 | 2.3595 | 2.7075 | 2.8906 | 3.2569 | 3.6232 | 0.6701 | 1.3226 | 1.5871 | 1.5871 | 1.5871 | 1.5871 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-10-24 01:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.51156 | 0.83709 | 1.1471 | 1.3797 | 1.3797 | 1.3797 | 1.6576 | 2.1391 | 2.4545 | 2.6205 | 2.9526 | 3.2847 | 0.67065 | 1.3236 | 1.5884 | 1.5884 | 1.5884 | 1.5884 | 0.47519 | 0.55277 | 0.55277 | 0.55277 | 0.55277 | 0.55277
2020-10-24 02:00 | Summer | 0.90469 | 1.2948 | 1.8684 | 1.8684 | 1.8684 | 1.8684 | 0.41439 | 0.67809 | 0.92924 | 1.1176 | 1.1176 | 1.1176 | 1.6766 | 2.1636 | 2.4827 | 2.6507 | 2.9865 | 3.3224 | 0.62873 | 1.2409 | 1.4891 | 1.4891 | 1.4891 | 1.4891 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-10-24 03:00 | Summer | 0.91452 | 1.3088 | 1.8887 | 1.8887 | 1.8887 | 1.8887 | 0.42868 | 0.70147 | 0.96128 | 1.1561 | 1.1561 | 1.1561 | 1.6004 | 2.0653 | 2.3699 | 2.5302 | 2.8508 | 3.1714 | 0.63254 | 1.2484 | 1.4981 | 1.4981 | 1.4981 | 1.4981 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-10-24 04:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.42011 | 0.68744 | 0.94205 | 1.133 | 1.133 | 1.133 | 1.6385 | 2.1145 | 2.4263 | 2.5904 | 2.9187 | 3.2469 | 0.60587 | 1.1958 | 1.435 | 1.435 | 1.435 | 1.435 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-10-24 05:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.41439 | 0.67809 | 0.92924 | 1.1176 | 1.1176 | 1.1176 | 1.7138 | 2.2116 | 2.5378 | 2.7094 | 3.0528 | 3.3961 | 0.62492 | 1.2334 | 1.4801 | 1.4801 | 1.4801 | 1.4801 | 0.47578 | 0.55346 | 0.55346 | 0.55346 | 0.55346 | 0.55346
2020-10-24 06:00 | Summer | 0.98168 | 1.4049 | 2.0274 | 2.0274 | 2.0274 | 2.0274 | 0.43725 | 0.7155 | 0.98051 | 1.1793 | 1.1793 | 1.1793 | 1.7909 | 2.3112 | 2.652 | 2.8314 | 3.1902 | 3.549 | 0.65922 | 1.3011 | 1.5613 | 1.5613 | 1.5613 | 1.5613 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-10-24 07:00 | Summer | 1.105 | 1.5815 | 2.2822 | 2.2822 | 2.2822 | 2.2822 | 0.50584 | 0.82774 | 1.1343 | 1.3642 | 1.3642 | 1.3642 | 1.8481 | 2.3849 | 2.7366 | 2.9218 | 3.292 | 3.6622 | 0.78496 | 1.5493 | 1.8591 | 1.8591 | 1.8591 | 1.8591 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-10-24 08:00 | Summer | 1.105 | 1.5815 | 2.2822 | 2.2822 | 2.2822 | 2.2822 | 0.43439 | 0.71083 | 0.9741 | 1.1715 | 1.1715 | 1.1715 | 2.0386 | 2.6308 | 3.0188 | 3.223 | 3.6314 | 4.0398 | 0.81926 | 1.617 | 1.9403 | 1.9403 | 1.9403 | 1.9403 | 0.53337 | 0.62045 | 0.62045 | 0.62045 | 0.62045 | 0.62045
2020-10-24 09:00 | Summer | 1.1622 | 1.6633 | 2.4002 | 2.4002 | 2.4002 | 2.4002 | 0.61444 | 1.0054 | 1.3778 | 1.6571 | 1.6571 | 1.6571 | 2.191 | 2.8275 | 3.2445 | 3.4639 | 3.9029 | 4.3418 | 0.81545 | 1.6094 | 1.9313 | 1.9313 | 1.9313 | 1.9313 | 0.53347 | 0.62057 | 0.62057 | 0.62057 | 0.62057 | 0.62057
2020-10-24 10:00 | Summer | 1.2956 | 1.8542 | 2.6756 | 2.6756 | 2.6756 | 2.6756 | 0.70589 | 1.1551 | 1.5829 | 1.9038 | 1.9038 | 1.9038 | 2.2482 | 2.9013 | 3.3291 | 3.5543 | 4.0047 | 4.4551 | 0.78115 | 1.5417 | 1.8501 | 1.8501 | 1.8501 | 1.8501 | 0.57158 | 0.6649 | 0.6649 | 0.6649 | 0.6649 | 0.6649
2020-10-24 11:00 | Summer | 1.1241 | 1.6088 | 2.3215 | 2.3215 | 2.3215 | 2.3215 | 0.57729 | 0.94465 | 1.2945 | 1.5569 | 1.5569 | 1.5569 | 2.2673 | 2.9258 | 3.3573 | 3.5844 | 4.0386 | 4.4928 | 0.74686 | 1.4741 | 1.7689 | 1.7689 | 1.7689 | 1.7689 | 0.59063 | 0.68706 | 0.68706 | 0.68706 | 0.68706 | 0.68706
2020-10-24 12:00 | Summer | 1.0288 | 1.4724 | 2.1248 | 2.1248 | 2.1248 | 2.1248 | 0.59729 | 0.97739 | 1.3394 | 1.6109 | 1.6109 | 1.6109 | 2.3244 | 2.9996 | 3.442 | 3.6748 | 4.1404 | 4.6061 | 0.74686 | 1.4741 | 1.7689 | 1.7689 | 1.7689 | 1.7689 | 0.60968 | 0.70922 | 0.70922 | 0.70922 | 0.70922 | 0.70922
2020-10-24 13:00 | Summer | 1.0479 | 1.4997 | 2.1641 | 2.1641 | 2.1641 | 2.1641 | 0.59158 | 0.96804 | 1.3266 | 1.5955 | 1.5955 | 1.5955 | 2.3435 | 3.0242 | 3.4702 | 3.7049 | 4.1744 | 4.6438 | 0.75829 | 1.4966 | 1.796 | 1.796 | 1.796 | 1.796 | 0.60968 | 0.70922 | 0.70922 | 0.70922 | 0.70922 | 0.70922
2020-10-24 14:00 | Summer | 1.0479 | 1.4997 | 2.1641 | 2.1641 | 2.1641 | 2.1641 | 0.58872 | 0.96336 | 1.3202 | 1.5878 | 1.5878 | 1.5878 | 2.2863 | 2.9504 | 3.3855 | 3.6146 | 4.0726 | 4.5306 | 0.84212 | 1.6621 | 1.9945 | 1.9945 | 1.9945 | 1.9945 | 0.55252 | 0.64273 | 0.64273 | 0.64273 | 0.64273 | 0.64273
2020-10-24 15:00 | Summer | 1.105 | 1.5815 | 2.2822 | 2.2822 | 2.2822 | 2.2822 | 0.60873 | 0.9961 | 1.365 | 1.6417 | 1.6417 | 1.6417 | 2.3244 | 2.9996 | 3.442 | 3.6748 | 4.1404 | 4.6061 | 0.80783 | 1.5944 | 1.9133 | 1.9133 | 1.9133 | 1.9133 | 0.55252 | 0.64273 | 0.64273 | 0.64273 | 0.64273 | 0.64273
2020-10-24 16:00 | Summer | 1.086 | 1.5542 | 2.2428 | 2.2428 | 2.2428 | 2.2428 | 0.64016 | 1.0475 | 1.4355 | 1.7265 | 1.7265 | 1.7265 | 2.3244 | 2.9996 | 3.442 | 3.6748 | 4.1404 | 4.6061 | 0.77734 | 1.5342 | 1.8411 | 1.8411 | 1.8411 | 1.8411 | 0.55252 | 0.64273 | 0.64273 | 0.64273 | 0.64273 | 0.64273
2020-10-24 17:00 | Summer | 1.0479 | 1.4997 | 2.1641 | 2.1641 | 2.1641 | 2.1641 | 0.73733 | 1.2065 | 1.6534 | 1.9886 | 1.9886 | 1.9886 | 2.2434 | 2.8951 | 3.322 | 3.5468 | 3.9962 | 4.4456 | 0.83069 | 1.6395 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-10-24 18:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.60587 | 0.99142 | 1.3586 | 1.634 | 1.634 | 1.634 | 2.0958 | 2.7046 | 3.1034 | 3.3133 | 3.7332 | 4.153 | 0.82688 | 1.632 | 1.9584 | 1.9584 | 1.9584 | 1.9584 | 0.53347 | 0.62057 | 0.62057 | 0.62057 | 0.62057 | 0.62057
2020-10-24 19:00 | Summer | 1.0288 | 1.4724 | 2.1248 | 2.1248 | 2.1248 | 2.1248 | 0.54014 | 0.88386 | 1.2112 | 1.4567 | 1.4567 | 1.4567 | 2.172 | 2.8029 | 3.2163 | 3.4338 | 3.8689 | 4.3041 | 0.89547 | 1.7674 | 2.1208 | 2.1208 | 2.1208 | 2.1208 | 0.53347 | 0.62057 | 0.62057 | 0.62057 | 0.62057 | 0.62057
2020-10-24 20:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.57729 | 0.94465 | 1.2945 | 1.5569 | 1.5569 | 1.5569 | 2.0958 | 2.7046 | 3.1034 | 3.3133 | 3.7332 | 4.153 | 0.86117 | 1.6997 | 2.0396 | 2.0396 | 2.0396 | 2.0396 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-10-24 21:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.54585 | 0.89321 | 1.224 | 1.4721 | 1.4721 | 1.4721 | 2.0005 | 2.5816 | 2.9624 | 3.1627 | 3.5635 | 3.9643 | 0.82688 | 1.632 | 1.9584 | 1.9584 | 1.9584 | 1.9584 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-10-24 22:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.49727 | 0.81371 | 1.1151 | 1.3411 | 1.3411 | 1.3411 | 1.9053 | 2.4587 | 2.8213 | 3.0121 | 3.3938 | 3.7755 | 0.81164 | 1.6019 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-10-24 23:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.42011 | 0.68744 | 0.94205 | 1.133 | 1.133 | 1.133 | 1.81 | 2.3358 | 2.6802 | 2.8615 | 3.2241 | 3.5867 | 0.64779 | 1.2785 | 1.5342 | 1.5342 | 1.5342 | 1.5342 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-10-25 | Summer | 0.91452 | 1.3088 | 1.8887 | 1.8887 | 1.8887 | 1.8887 | 0.35575 | 0.58214 | 0.79775 | 0.95946 | 0.95946 | 0.95946 | 1.6576 | 2.1391 | 2.4545 | 2.6205 | 2.9526 | 3.2847 | 0.62111 | 1.2259 | 1.4711 | 1.4711 | 1.4711 | 1.4711 | 0.43416 | 0.50504 | 0.50504 | 0.50504 | 0.50504 | 0.50504
2020-10-25 01:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.40296 | 0.65939 | 0.9036 | 1.0868 | 1.0868 | 1.0868 | 1.5433 | 1.9915 | 2.2852 | 2.4398 | 2.749 | 3.0581 | 0.64397 | 1.271 | 1.5252 | 1.5252 | 1.5252 | 1.5252 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-10-25 02:00 | Summer | 0.91452 | 1.3088 | 1.8887 | 1.8887 | 1.8887 | 1.8887 | 0.4001 | 0.65471 | 0.89719 | 1.0791 | 1.0791 | 1.0791 | 1.5242 | 1.967 | 2.257 | 2.4097 | 2.715 | 3.0204 | 0.76972 | 1.5192 | 1.823 | 1.823 | 1.823 | 1.823 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-10-25 03:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.38581 | 0.63133 | 0.86515 | 1.0405 | 1.0405 | 1.0405 | 1.467 | 1.8932 | 2.1724 | 2.3193 | 2.6132 | 2.9071 | 0.57157 | 1.1281 | 1.3537 | 1.3537 | 1.3537 | 1.3537 | 0.43821 | 0.50975 | 0.50975 | 0.50975 | 0.50975 | 0.50975
2020-10-25 04:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.40867 | 0.66874 | 0.91642 | 1.1022 | 1.1022 | 1.1022 | 1.4667 | 1.8928 | 2.1719 | 2.3188 | 2.6126 | 2.9065 | 0.56776 | 1.1206 | 1.3447 | 1.3447 | 1.3447 | 1.3447 | 0.43924 | 0.51095 | 0.51095 | 0.51095 | 0.51095 | 0.51095
2020-10-25 05:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.32126 | 0.5257 | 0.72041 | 0.86644 | 0.86644 | 0.86644 | 1.5623 | 2.0161 | 2.3135 | 2.4699 | 2.7829 | 3.0959 | 0.49918 | 0.98521 | 1.1823 | 1.1823 | 1.1823 | 1.1823 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-10-25 06:00 | Summer | 0.91452 | 1.3088 | 1.8887 | 1.8887 | 1.8887 | 1.8887 | 0.52585 | 0.86048 | 1.1792 | 1.4182 | 1.4182 | 1.4182 | 1.5623 | 2.0161 | 2.3135 | 2.4699 | 2.7829 | 3.0959 | 0.58682 | 1.1582 | 1.3898 | 1.3898 | 1.3898 | 1.3898 | 0.43821 | 0.50975 | 0.50975 | 0.50975 | 0.50975 | 0.50975
2020-10-25 07:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.54014 | 0.88386 | 1.2112 | 1.4567 | 1.4567 | 1.4567 | 1.6954 | 2.1879 | 2.5105 | 2.6804 | 3.02 | 3.3596 | 0.67827 | 1.3387 | 1.6064 | 1.6064 | 1.6064 | 1.6064 | 0.43821 | 0.50975 | 0.50975 | 0.50975 | 0.50975 | 0.50975
2020-10-25 08:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.52585 | 0.86048 | 1.1792 | 1.4182 | 1.4182 | 1.4182 | 1.9815 | 2.557 | 2.9341 | 3.1326 | 3.5296 | 3.9265 | 0.62492 | 1.2334 | 1.4801 | 1.4801 | 1.4801 | 1.4801 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-10-25 09:00 | Summer | 0.91452 | 1.3088 | 1.8887 | 1.8887 | 1.8887 | 1.8887 | 0.56586 | 0.92595 | 1.2689 | 1.5261 | 1.5261 | 1.5261 | 1.9815 | 2.557 | 2.9341 | 3.1326 | 3.5296 | 3.9265 | 0.73924 | 1.459 | 1.7508 | 1.7508 | 1.7508 | 1.7508 | 0.48288 | 0.56172 | 0.56172 | 0.56172 | 0.56172 | 0.56172
2020-10-25 10:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.55728 | 0.91192 | 1.2497 | 1.503 | 1.503 | 1.503 | 2.0005 | 2.5816 | 2.9624 | 3.1627 | 3.5635 | 3.9643 | 0.78115 | 1.5417 | 1.8501 | 1.8501 | 1.8501 | 1.8501 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-10-25 11:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.563 | 0.92127 | 1.2625 | 1.5184 | 1.5184 | 1.5184 | 2.0767 | 2.68 | 3.0752 | 3.2832 | 3.6992 | 4.1153 | 0.69323 | 1.3682 | 1.6419 | 1.6419 | 1.6419 | 1.6419 | 0.57158 | 0.6649 | 0.6649 | 0.6649 | 0.6649 | 0.6649
2020-10-25 12:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.45726 | 0.74824 | 1.0254 | 1.2332 | 1.2332 | 1.2332 | 2.1339 | 2.7537 | 3.1598 | 3.3736 | 3.8011 | 4.2285 | 0.74686 | 1.4741 | 1.7689 | 1.7689 | 1.7689 | 1.7689 | 0.5498 | 0.63956 | 0.63956 | 0.63956 | 0.63956 | 0.63956
2020-10-25 13:00 | Summer | 0.89547 | 1.2816 | 1.8493 | 1.8493 | 1.8493 | 1.8493 | 0.43725 | 0.7155 | 0.98051 | 1.1793 | 1.1793 | 1.1793 | 2.0958 | 2.7046 | 3.1034 | 3.3133 | 3.7332 | 4.153 | 0.72018 | 1.4214 | 1.7057 | 1.7057 | 1.7057 | 1.7057 | 0.53347 | 0.62057 | 0.62057 | 0.62057 | 0.62057 | 0.62057
2020-10-25 14:00 | Summer | 0.91452 | 1.3088 | 1.8887 | 1.8887 | 1.8887 | 1.8887 | 0.42582 | 0.6968 | 0.95487 | 1.1484 | 1.1484 | 1.1484 | 2.1148 | 2.7291 | 3.1316 | 3.3435 | 3.7671 | 4.1908 | 0.66684 | 1.3161 | 1.5794 | 1.5794 | 1.5794 | 1.5794 | 0.54935 | 0.63904 | 0.63904 | 0.63904 | 0.63904 | 0.63904
2020-10-25 15:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.48298 | 0.79033 | 1.083 | 1.3026 | 1.3026 | 1.3026 | 2.0386 | 2.6308 | 3.0188 | 3.223 | 3.6314 | 4.0398 | 0.68589 | 1.3537 | 1.6245 | 1.6245 | 1.6245 | 1.6245 | 0.55252 | 0.64273 | 0.64273 | 0.64273 | 0.64273 | 0.64273
2020-10-25 16:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.51156 | 0.83709 | 1.1471 | 1.3797 | 1.3797 | 1.3797 | 2.0958 | 2.7046 | 3.1034 | 3.3133 | 3.7332 | 4.153 | 0.71637 | 1.4139 | 1.6967 | 1.6967 | 1.6967 | 1.6967 | 0.55252 | 0.64273 | 0.64273 | 0.64273 | 0.64273 | 0.64273
2020-10-25 17:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.45154 | 0.73889 | 1.0125 | 1.2178 | 1.2178 | 1.2178 | 2.0519 | 2.648 | 3.0385 | 3.244 | 3.6551 | 4.0661 | 0.72018 | 1.4214 | 1.7057 | 1.7057 | 1.7057 | 1.7057 | 0.53347 | 0.62057 | 0.62057 | 0.62057 | 0.62057 | 0.62057
2020-10-25 18:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.49155 | 0.80436 | 1.1023 | 1.3257 | 1.3257 | 1.3257 | 1.9055 | 2.459 | 2.8217 | 3.0125 | 3.3943 | 3.776 | 0.72018 | 1.4214 | 1.7057 | 1.7057 | 1.7057 | 1.7057 | 0.57158 | 0.6649 | 0.6649 | 0.6649 | 0.6649 | 0.6649
2020-10-25 19:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.52013 | 0.85112 | 1.1664 | 1.4028 | 1.4028 | 1.4028 | 2.0196 | 2.6062 | 2.9906 | 3.1929 | 3.5974 | 4.002 | 0.724 | 1.4289 | 1.7147 | 1.7147 | 1.7147 | 1.7147 | 0.51478 | 0.59883 | 0.59883 | 0.59883 | 0.59883 | 0.59883
2020-10-25 20:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.51727 | 0.84645 | 1.1599 | 1.3951 | 1.3951 | 1.3951 | 2.0196 | 2.6062 | 2.9906 | 3.1929 | 3.5974 | 4.002 | 0.76591 | 1.5117 | 1.814 | 1.814 | 1.814 | 1.814 | 0.53347 | 0.62057 | 0.62057 | 0.62057 | 0.62057 | 0.62057
2020-10-25 21:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.51727 | 0.84645 | 1.1599 | 1.3951 | 1.3951 | 1.3951 | 1.9434 | 2.5079 | 2.8777 | 3.0724 | 3.4617 | 3.851 | 0.69351 | 1.3688 | 1.6425 | 1.6425 | 1.6425 | 1.6425 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-10-25 22:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.35152 | 0.57521 | 0.78825 | 0.94803 | 0.94803 | 0.94803 | 1.8236 | 2.3533 | 2.7003 | 2.883 | 3.2483 | 3.6136 | 0.73543 | 1.4515 | 1.7418 | 1.7418 | 1.7418 | 1.7418 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-10-25 23:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.43154 | 0.70615 | 0.96769 | 1.1638 | 1.1638 | 1.1638 | 1.7644 | 2.2769 | 2.6126 | 2.7894 | 3.1428 | 3.4963 | 0.64397 | 1.271 | 1.5252 | 1.5252 | 1.5252 | 1.5252 | 0.47995 | 0.55831 | 0.55831 | 0.55831 | 0.55831 | 0.55831
2020-10-26 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.38009 | 0.62197 | 0.85233 | 1.0251 | 1.0251 | 1.0251 | 1.6576 | 2.1391 | 2.4545 | 2.6205 | 2.9526 | 3.2847 | 0.52204 | 1.0303 | 1.2364 | 1.2364 | 1.2364 | 1.2364 | 0.47268 | 0.54985 | 0.54985 | 0.54985 | 0.54985 | 0.54985
2020-10-26 01:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.41153 | 0.67342 | 0.92283 | 1.1099 | 1.1099 | 1.1099 | 1.5814 | 2.0407 | 2.3417 | 2.5001 | 2.8169 | 3.1337 | 0.59444 | 1.1732 | 1.4079 | 1.4079 | 1.4079 | 1.4079 | 0.49902 | 0.58049 | 0.58049 | 0.58049 | 0.58049 | 0.58049
2020-10-26 02:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.46012 | 0.75292 | 1.0318 | 1.2409 | 1.2409 | 1.2409 | 1.5814 | 2.0407 | 2.3417 | 2.5001 | 2.8169 | 3.1337 | 0.80783 | 1.5944 | 1.9133 | 1.9133 | 1.9133 | 1.9133 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-10-26 03:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.47155 | 0.77162 | 1.0574 | 1.2717 | 1.2717 | 1.2717 | 1.5814 | 2.0407 | 2.3417 | 2.5001 | 2.8169 | 3.1337 | 0.56014 | 1.1055 | 1.3267 | 1.3267 | 1.3267 | 1.3267 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-10-26 04:00 | Summer | 1.105 | 1.5815 | 2.2822 | 2.2822 | 2.2822 | 2.2822 | 0.44583 | 0.72953 | 0.99973 | 1.2024 | 1.2024 | 1.2024 | 1.5893 | 2.051 | 2.3534 | 2.5126 | 2.831 | 3.1494 | 0.57539 | 1.1356 | 1.3628 | 1.3628 | 1.3628 | 1.3628 | 0.54943 | 0.63914 | 0.63914 | 0.63914 | 0.63914 | 0.63914
2020-10-26 05:00 | Summer | 1.2194 | 1.7451 | 2.5183 | 2.5183 | 2.5183 | 2.5183 | 0.5087 | 0.83242 | 1.1407 | 1.3719 | 1.3719 | 1.3719 | 1.7178 | 2.2168 | 2.5437 | 2.7158 | 3.0599 | 3.4041 | 0.59444 | 1.1732 | 1.4079 | 1.4079 | 1.4079 | 1.4079 | 0.66684 | 0.77571 | 0.77571 | 0.77571 | 0.77571 | 0.77571
2020-10-26 06:00 | Summer | 1.3566 | 1.9415 | 2.8017 | 2.8017 | 2.8017 | 2.8017 | 0.56872 | 0.93062 | 1.2753 | 1.5338 | 1.5338 | 1.5338 | 1.8862 | 2.4341 | 2.7931 | 2.982 | 3.3599 | 3.7377 | 0.71637 | 1.4139 | 1.6967 | 1.6967 | 1.6967 | 1.6967 | 0.88413 | 1.0285 | 1.0285 | 1.0285 | 1.0285 | 1.0285
2020-10-26 07:00 | Summer | 2.03 | 2.9052 | 4.1924 | 4.1924 | 4.1924 | 4.1924 | 0.81164 | 1.3281 | 1.82 | 2.189 | 2.189 | 2.189 | 2.178 | 2.8106 | 3.2251 | 3.4433 | 3.8796 | 4.3159 | 0.94501 | 1.8651 | 2.2382 | 2.2382 | 2.2382 | 2.2382 | 1.1813 | 1.3741 | 1.3741 | 1.3741 | 1.3741 | 1.3741
2020-10-26 08:00 | Summer | 2.2291 | 3.1903 | 4.6037 | 4.6037 | 4.6037 | 4.6037 | 0.92309 | 1.5105 | 2.07 | 2.4896 | 2.4896 | 2.4896 | 2.3816 | 3.0734 | 3.5266 | 3.7652 | 4.2423 | 4.7194 | 0.96787 | 1.9103 | 2.2923 | 2.2923 | 2.2923 | 2.2923 | 1.3908 | 1.6179 | 1.6179 | 1.6179 | 1.6179 | 1.6179
2020-10-26 09:00 | Summer | 2.3054 | 3.2993 | 4.7611 | 4.7611 | 4.7611 | 4.7611 | 0.98311 | 1.6087 | 2.2045 | 2.6514 | 2.6514 | 2.6514 | 2.58 | 3.3294 | 3.8204 | 4.0788 | 4.5957 | 5.1125 | 0.95644 | 1.8877 | 2.2652 | 2.2652 | 2.2652 | 2.2652 | 1.4099 | 1.6401 | 1.6401 | 1.6401 | 1.6401 | 1.6401
2020-10-26 10:00 | Summer | 2.2673 | 3.2448 | 4.6824 | 4.6824 | 4.6824 | 4.6824 | 1.0003 | 1.6368 | 2.243 | 2.6977 | 2.6977 | 2.6977 | 2.6102 | 3.3684 | 3.8652 | 4.1266 | 4.6495 | 5.1724 | 0.90309 | 1.7824 | 2.1389 | 2.1389 | 2.1389 | 2.1389 | 1.4099 | 1.6401 | 1.6401 | 1.6401 | 1.6401 | 1.6401
2020-10-26 11:00 | Summer | 2.2482 | 3.2175 | 4.643 | 4.643 | 4.643 | 4.643 | 0.98025 | 1.604 | 2.1981 | 2.6437 | 2.6437 | 2.6437 | 2.6674 | 3.4422 | 3.9498 | 4.217 | 4.7513 | 5.2857 | 0.87642 | 1.7298 | 2.0757 | 2.0757 | 2.0757 | 2.0757 | 1.448 | 1.6844 | 1.6844 | 1.6844 | 1.6844 | 1.6844
2020-10-26 12:00 | Summer | 2.2673 | 3.2448 | 4.6824 | 4.6824 | 4.6824 | 4.6824 | 0.97168 | 1.59 | 2.1789 | 2.6206 | 2.6206 | 2.6206 | 2.7055 | 3.4913 | 4.0062 | 4.2772 | 4.8192 | 5.3612 | 0.93738 | 1.8501 | 2.2201 | 2.2201 | 2.2201 | 2.2201 | 1.5242 | 1.7731 | 1.7731 | 1.7731 | 1.7731 | 1.7731
2020-10-26 13:00 | Summer | 2.191 | 3.1357 | 4.525 | 4.525 | 4.525 | 4.525 | 0.9631 | 1.576 | 2.1597 | 2.5975 | 2.5975 | 2.5975 | 2.6864 | 3.4668 | 3.978 | 4.2471 | 4.7853 | 5.3234 | 0.83831 | 1.6546 | 1.9855 | 1.9855 | 1.9855 | 1.9855 | 1.4289 | 1.6622 | 1.6622 | 1.6622 | 1.6622 | 1.6622
2020-10-26 14:00 | Summer | 2.1148 | 3.0267 | 4.3676 | 4.3676 | 4.3676 | 4.3676 | 0.92023 | 1.5058 | 2.0636 | 2.4818 | 2.4818 | 2.4818 | 2.5911 | 3.3438 | 3.8369 | 4.0965 | 4.6156 | 5.1347 | 0.86879 | 1.7147 | 2.0577 | 2.0577 | 2.0577 | 2.0577 | 1.3337 | 1.5514 | 1.5514 | 1.5514 | 1.5514 | 1.5514
2020-10-26 15:00 | Summer | 2.0577 | 2.9449 | 4.2495 | 4.2495 | 4.2495 | 4.2495 | 0.83164 | 1.3609 | 1.8649 | 2.2429 | 2.2429 | 2.2429 | 2.6102 | 3.3684 | 3.8652 | 4.1266 | 4.6495 | 5.1724 | 0.91071 | 1.7975 | 2.1569 | 2.1569 | 2.1569 | 2.1569 | 1.2575 | 1.4628 | 1.4628 | 1.4628 | 1.4628 | 1.4628
2020-10-26 16:00 | Summer | 2.0425 | 2.9232 | 4.2183 | 4.2183 | 4.2183 | 4.2183 | 0.78877 | 1.2907 | 1.7688 | 2.1273 | 2.1273 | 2.1273 | 2.4387 | 3.1471 | 3.6112 | 3.8555 | 4.3441 | 4.8326 | 0.86117 | 1.6997 | 2.0396 | 2.0396 | 2.0396 | 2.0396 | 1.1996 | 1.3955 | 1.3955 | 1.3955 | 1.3955 | 1.3955
2020-10-26 17:00 | Summer | 2.0196 | 2.8903 | 4.1709 | 4.1709 | 4.1709 | 4.1709 | 0.80592 | 1.3188 | 1.8072 | 2.1735 | 2.1735 | 2.1735 | 2.3435 | 3.0242 | 3.4702 | 3.7049 | 4.1744 | 4.6438 | 0.88785 | 1.7523 | 2.1028 | 2.1028 | 2.1028 | 2.1028 | 1.0987 | 1.278 | 1.278 | 1.278 | 1.278 | 1.278
2020-10-26 18:00 | Summer | 1.6516 | 2.3637 | 3.4109 | 3.4109 | 3.4109 | 3.4109 | 0.68999 | 1.1291 | 1.5473 | 1.8609 | 1.8609 | 1.8609 | 2.3244 | 2.9996 | 3.442 | 3.6748 | 4.1404 | 4.6061 | 0.82688 | 1.632 | 1.9584 | 1.9584 | 1.9584 | 1.9584 | 0.8957 | 1.0419 | 1.0419 | 1.0419 | 1.0419 | 1.0419
2020-10-26 19:00 | Summer | 1.1149 | 1.5956 | 2.3025 | 2.3025 | 2.3025 | 2.3025 | 0.52585 | 0.86048 | 1.1792 | 1.4182 | 1.4182 | 1.4182 | 2.2863 | 2.9504 | 3.3855 | 3.6146 | 4.0726 | 4.5306 | 0.78877 | 1.5568 | 1.8681 | 1.8681 | 1.8681 | 1.8681 | 0.68589 | 0.79787 | 0.79787 | 0.79787 | 0.79787 | 0.79787
2020-10-26 20:00 | Summer | 1.1241 | 1.6088 | 2.3215 | 2.3215 | 2.3215 | 2.3215 | 0.50584 | 0.82774 | 1.1343 | 1.3642 | 1.3642 | 1.3642 | 2.1148 | 2.7291 | 3.1316 | 3.3435 | 3.7671 | 4.1908 | 0.73543 | 1.4515 | 1.7418 | 1.7418 | 1.7418 | 1.7418 | 0.64779 | 0.75355 | 0.75355 | 0.75355 | 0.75355 | 0.75355
2020-10-26 21:00 | Summer | 1.0479 | 1.4997 | 2.1641 | 2.1641 | 2.1641 | 2.1641 | 0.47726 | 0.78098 | 1.0702 | 1.2872 | 1.2872 | 1.2872 | 2.0767 | 2.68 | 3.0752 | 3.2832 | 3.6992 | 4.1153 | 0.77353 | 1.5267 | 1.832 | 1.832 | 1.832 | 1.832 | 0.54253 | 0.63111 | 0.63111 | 0.63111 | 0.63111 | 0.63111
2020-10-26 22:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.39153 | 0.64068 | 0.87797 | 1.0559 | 1.0559 | 1.0559 | 1.9624 | 2.5325 | 2.9059 | 3.1025 | 3.4956 | 3.8887 | 0.67065 | 1.3236 | 1.5884 | 1.5884 | 1.5884 | 1.5884 | 0.53347 | 0.62057 | 0.62057 | 0.62057 | 0.62057 | 0.62057
2020-10-26 23:00 | Summer | 0.93493 | 1.338 | 1.9308 | 1.9308 | 1.9308 | 1.9308 | 0.42296 | 0.69212 | 0.94846 | 1.1407 | 1.1407 | 1.1407 | 1.7909 | 2.3112 | 2.652 | 2.8314 | 3.1902 | 3.549 | 0.57157 | 1.1281 | 1.3537 | 1.3537 | 1.3537 | 1.3537 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-10-27 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.41725 | 0.68277 | 0.93565 | 1.1253 | 1.1253 | 1.1253 | 1.6576 | 2.1391 | 2.4545 | 2.6205 | 2.9526 | 3.2847 | 0.59063 | 1.1657 | 1.3989 | 1.3989 | 1.3989 | 1.3989 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-10-27 01:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.44011 | 0.72018 | 0.98691 | 1.187 | 1.187 | 1.187 | 1.6004 | 2.0653 | 2.3699 | 2.5302 | 2.8508 | 3.1714 | 0.56699 | 1.1191 | 1.3429 | 1.3429 | 1.3429 | 1.3429 | 0.43821 | 0.50975 | 0.50975 | 0.50975 | 0.50975 | 0.50975
2020-10-27 02:00 | Summer | 0.97106 | 1.3897 | 2.0055 | 2.0055 | 2.0055 | 2.0055 | 0.41725 | 0.68277 | 0.93565 | 1.1253 | 1.1253 | 1.1253 | 1.5814 | 2.0407 | 2.3417 | 2.5001 | 2.8169 | 3.1337 | 0.56776 | 1.1206 | 1.3447 | 1.3447 | 1.3447 | 1.3447 | 0.44364 | 0.51607 | 0.51607 | 0.51607 | 0.51607 | 0.51607
2020-10-27 03:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.40582 | 0.66406 | 0.91001 | 1.0945 | 1.0945 | 1.0945 | 1.5623 | 2.0161 | 2.3135 | 2.4699 | 2.7829 | 3.0959 | 0.56395 | 1.1131 | 1.3357 | 1.3357 | 1.3357 | 1.3357 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-10-27 04:00 | Summer | 1.096 | 1.5686 | 2.2635 | 2.2635 | 2.2635 | 2.2635 | 0.43725 | 0.7155 | 0.98051 | 1.1793 | 1.1793 | 1.1793 | 1.6087 | 2.076 | 2.3821 | 2.5433 | 2.8655 | 3.1878 | 0.5792 | 1.1431 | 1.3718 | 1.3718 | 1.3718 | 1.3718 | 0.52466 | 0.61032 | 0.61032 | 0.61032 | 0.61032 | 0.61032
2020-10-27 05:00 | Summer | 1.2691 | 1.8163 | 2.6209 | 2.6209 | 2.6209 | 2.6209 | 0.55443 | 0.90724 | 1.2433 | 1.4953 | 1.4953 | 1.4953 | 1.8041 | 2.3281 | 2.6714 | 2.8521 | 3.2136 | 3.575 | 0.61995 | 1.2236 | 1.4683 | 1.4683 | 1.4683 | 1.4683 | 0.60968 | 0.70922 | 0.70922 | 0.70922 | 0.70922 | 0.70922
2020-10-27 06:00 | Summer | 1.5592 | 2.2315 | 3.2201 | 3.2201 | 3.2201 | 3.2201 | 0.64874 | 1.0616 | 1.4547 | 1.7496 | 1.7496 | 1.7496 | 2.012 | 2.5964 | 2.9793 | 3.1808 | 3.5839 | 3.987 | 0.73162 | 1.444 | 1.7328 | 1.7328 | 1.7328 | 1.7328 | 0.77502 | 0.90155 | 0.90155 | 0.90155 | 0.90155 | 0.90155
2020-10-27 07:00 | Summer | 1.8915 | 2.707 | 3.9063 | 3.9063 | 3.9063 | 3.9063 | 0.68907 | 1.1276 | 1.5452 | 1.8584 | 1.8584 | 1.8584 | 2.2428 | 2.8943 | 3.3211 | 3.5458 | 3.9951 | 4.4444 | 0.79374 | 1.5666 | 1.8799 | 1.8799 | 1.8799 | 1.8799 | 1.0416 | 1.2116 | 1.2116 | 1.2116 | 1.2116 | 1.2116
2020-10-27 08:00 | Summer | 2.191 | 3.1357 | 4.525 | 4.525 | 4.525 | 4.525 | 0.8553 | 1.3996 | 1.918 | 2.3067 | 2.3067 | 2.3067 | 2.4387 | 3.1471 | 3.6112 | 3.8555 | 4.3441 | 4.8326 | 0.98692 | 1.9479 | 2.3374 | 2.3374 | 2.3374 | 2.3374 | 1.3146 | 1.5293 | 1.5293 | 1.5293 | 1.5293 | 1.5293
2020-10-27 09:00 | Summer | 2.2101 | 3.163 | 4.5643 | 4.5643 | 4.5643 | 4.5643 | 0.94024 | 1.5386 | 2.1084 | 2.5358 | 2.5358 | 2.5358 | 2.6102 | 3.3684 | 3.8652 | 4.1266 | 4.6495 | 5.1724 | 0.99454 | 1.9629 | 2.3555 | 2.3555 | 2.3555 | 2.3555 | 1.3908 | 1.6179 | 1.6179 | 1.6179 | 1.6179 | 1.6179
2020-10-27 10:00 | Summer | 2.191 | 3.1357 | 4.525 | 4.525 | 4.525 | 4.525 | 0.84307 | 1.3796 | 1.8905 | 2.2737 | 2.2737 | 2.2737 | 2.5721 | 3.3192 | 3.8087 | 4.0664 | 4.5816 | 5.0969 | 0.96025 | 1.8952 | 2.2743 | 2.2743 | 2.2743 | 2.2743 | 1.4289 | 1.6622 | 1.6622 | 1.6622 | 1.6622 | 1.6622
2020-10-27 11:00 | Summer | 2.1339 | 3.0539 | 4.4069 | 4.4069 | 4.4069 | 4.4069 | 0.79735 | 1.3047 | 1.788 | 2.1504 | 2.1504 | 2.1504 | 2.6483 | 3.4176 | 3.9216 | 4.1869 | 4.7174 | 5.2479 | 0.95263 | 1.8802 | 2.2562 | 2.2562 | 2.2562 | 2.2562 | 1.3718 | 1.5957 | 1.5957 | 1.5957 | 1.5957 | 1.5957
2020-10-27 12:00 | Summer | 2.3625 | 3.3811 | 4.8791 | 4.8791 | 4.8791 | 4.8791 | 0.88022 | 1.4404 | 1.9738 | 2.3739 | 2.3739 | 2.3739 | 2.6864 | 3.4668 | 3.978 | 4.2471 | 4.7853 | 5.3234 | 0.92595 | 1.8275 | 2.193 | 2.193 | 2.193 | 2.193 | 1.3527 | 1.5736 | 1.5736 | 1.5736 | 1.5736 | 1.5736
2020-10-27 13:00 | Summer | 2.2673 | 3.2448 | 4.6824 | 4.6824 | 4.6824 | 4.6824 | 0.80306 | 1.3141 | 1.8008 | 2.1658 | 2.1658 | 2.1658 | 2.6864 | 3.4668 | 3.978 | 4.2471 | 4.7853 | 5.3234 | 0.93738 | 1.8501 | 2.2201 | 2.2201 | 2.2201 | 2.2201 | 1.3146 | 1.5293 | 1.5293 | 1.5293 | 1.5293 | 1.5293
2020-10-27 14:00 | Summer | 2.2482 | 3.2175 | 4.643 | 4.643 | 4.643 | 4.643 | 0.79449 | 1.3001 | 1.7816 | 2.1427 | 2.1427 | 2.1427 | 2.5721 | 3.3192 | 3.8087 | 4.0664 | 4.5816 | 5.0969 | 1.2308 | 2.4292 | 2.915 | 2.915 | 2.915 | 2.915 | 1.3337 | 1.5514 | 1.5514 | 1.5514 | 1.5514 | 1.5514
2020-10-27 15:00 | Summer | 2.191 | 3.1357 | 4.525 | 4.525 | 4.525 | 4.525 | 0.80592 | 1.3188 | 1.8072 | 2.1735 | 2.1735 | 2.1735 | 2.6102 | 3.3684 | 3.8652 | 4.1266 | 4.6495 | 5.1724 | 0.93357 | 1.8426 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 1.2956 | 1.5071 | 1.5071 | 1.5071 | 1.5071 | 1.5071
2020-10-27 16:00 | Summer | 2.1339 | 3.0539 | 4.4069 | 4.4069 | 4.4069 | 4.4069 | 0.83736 | 1.3702 | 1.8777 | 2.2583 | 2.2583 | 2.2583 | 2.553 | 3.2946 | 3.7805 | 4.0362 | 4.5477 | 5.0591 | 0.92595 | 1.8275 | 2.193 | 2.193 | 2.193 | 2.193 | 1.2384 | 1.4406 | 1.4406 | 1.4406 | 1.4406 | 1.4406
2020-10-27 17:00 | Summer | 2.0577 | 2.9449 | 4.2495 | 4.2495 | 4.2495 | 4.2495 | 0.7259 | 1.1878 | 1.6278 | 1.9577 | 1.9577 | 1.9577 | 2.553 | 3.2946 | 3.7805 | 4.0362 | 4.5477 | 5.0591 | 0.89166 | 1.7599 | 2.1118 | 2.1118 | 2.1118 | 2.1118 | 1.1622 | 1.352 | 1.352 | 1.352 | 1.352 | 1.352
2020-10-27 18:00 | Summer | 1.6135 | 2.3091 | 3.3322 | 3.3322 | 3.3322 | 3.3322 | 0.63445 | 1.0382 | 1.4227 | 1.7111 | 1.7111 | 1.7111 | 2.3435 | 3.0242 | 3.4702 | 3.7049 | 4.1744 | 4.6438 | 0.81926 | 1.617 | 1.9403 | 1.9403 | 1.9403 | 1.9403 | 0.88814 | 1.0331 | 1.0331 | 1.0331 | 1.0331 | 1.0331
2020-10-27 19:00 | Summer | 1.1432 | 1.636 | 2.3609 | 2.3609 | 2.3609 | 2.3609 | 0.5087 | 0.83242 | 1.1407 | 1.3719 | 1.3719 | 1.3719 | 2.2863 | 2.9504 | 3.3855 | 3.6146 | 4.0726 | 4.5306 | 0.90309 | 1.7824 | 2.1389 | 2.1389 | 2.1389 | 2.1389 | 0.68619 | 0.79822 | 0.79822 | 0.79822 | 0.79822 | 0.79822
2020-10-27 20:00 | Summer | 1.0479 | 1.4997 | 2.1641 | 2.1641 | 2.1641 | 2.1641 | 0.44297 | 0.72486 | 0.99332 | 1.1947 | 1.1947 | 1.1947 | 2.2673 | 2.9258 | 3.3573 | 3.5844 | 4.0386 | 4.4928 | 0.82307 | 1.6245 | 1.9494 | 1.9494 | 1.9494 | 1.9494 | 0.62873 | 0.73138 | 0.73138 | 0.73138 | 0.73138 | 0.73138
2020-10-27 21:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.46297 | 0.75759 | 1.0382 | 1.2486 | 1.2486 | 1.2486 | 2.0958 | 2.7046 | 3.1034 | 3.3133 | 3.7332 | 4.153 | 0.80402 | 1.5869 | 1.9042 | 1.9042 | 1.9042 | 1.9042 | 0.57158 | 0.6649 | 0.6649 | 0.6649 | 0.6649 | 0.6649
2020-10-27 22:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.38581 | 0.63133 | 0.86515 | 1.0405 | 1.0405 | 1.0405 | 1.8879 | 2.4363 | 2.7956 | 2.9847 | 3.3629 | 3.7411 | 0.73162 | 1.444 | 1.7328 | 1.7328 | 1.7328 | 1.7328 | 0.5011 | 0.58291 | 0.58291 | 0.58291 | 0.58291 | 0.58291
2020-10-27 23:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.43154 | 0.70615 | 0.96769 | 1.1638 | 1.1638 | 1.1638 | 1.7719 | 2.2866 | 2.6238 | 2.8013 | 3.1562 | 3.5112 | 0.58682 | 1.1582 | 1.3898 | 1.3898 | 1.3898 | 1.3898 | 0.4573 | 0.53196 | 0.53196 | 0.53196 | 0.53196 | 0.53196
2020-10-28 | Summer | 0.91452 | 1.3088 | 1.8887 | 1.8887 | 1.8887 | 1.8887 | 0.35437 | 0.57988 | 0.79466 | 0.95574 | 0.95574 | 0.95574 | 1.6576 | 2.1391 | 2.4545 | 2.6205 | 2.9526 | 3.2847 | 0.64779 | 1.2785 | 1.5342 | 1.5342 | 1.5342 | 1.5342 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-10-28 01:00 | Summer | 0.89547 | 1.2816 | 1.8493 | 1.8493 | 1.8493 | 1.8493 | 0.41153 | 0.67342 | 0.92283 | 1.1099 | 1.1099 | 1.1099 | 1.6385 | 2.1145 | 2.4263 | 2.5904 | 2.9187 | 3.2469 | 0.52204 | 1.0303 | 1.2364 | 1.2364 | 1.2364 | 1.2364 | 0.43821 | 0.50975 | 0.50975 | 0.50975 | 0.50975 | 0.50975
2020-10-28 02:00 | Summer | 0.91452 | 1.3088 | 1.8887 | 1.8887 | 1.8887 | 1.8887 | 0.45154 | 0.73889 | 1.0125 | 1.2178 | 1.2178 | 1.2178 | 1.6195 | 2.0899 | 2.3981 | 2.5603 | 2.8847 | 3.2092 | 0.60968 | 1.2033 | 1.444 | 1.444 | 1.444 | 1.444 | 0.42939 | 0.49949 | 0.49949 | 0.49949 | 0.49949 | 0.49949
2020-10-28 03:00 | Summer | 0.91452 | 1.3088 | 1.8887 | 1.8887 | 1.8887 | 1.8887 | 0.38295 | 0.62665 | 0.85874 | 1.0328 | 1.0328 | 1.0328 | 1.6004 | 2.0653 | 2.3699 | 2.5302 | 2.8508 | 3.1714 | 0.60493 | 1.1939 | 1.4327 | 1.4327 | 1.4327 | 1.4327 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-10-28 04:00 | Summer | 1.0479 | 1.4997 | 2.1641 | 2.1641 | 2.1641 | 2.1641 | 0.37152 | 0.60794 | 0.83311 | 1.002 | 1.002 | 1.002 | 1.6485 | 2.1274 | 2.4411 | 2.6062 | 2.9365 | 3.2667 | 0.60587 | 1.1958 | 1.435 | 1.435 | 1.435 | 1.435 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-10-28 05:00 | Summer | 1.1241 | 1.6088 | 2.3215 | 2.3215 | 2.3215 | 2.3215 | 0.45154 | 0.73889 | 1.0125 | 1.2178 | 1.2178 | 1.2178 | 1.829 | 2.3603 | 2.7084 | 2.8916 | 3.2581 | 3.6245 | 0.65541 | 1.2936 | 1.5523 | 1.5523 | 1.5523 | 1.5523 | 0.66682 | 0.77569 | 0.77569 | 0.77569 | 0.77569 | 0.77569
2020-10-28 06:00 | Summer | 1.3201 | 1.8893 | 2.7264 | 2.7264 | 2.7264 | 2.7264 | 0.53156 | 0.86983 | 1.192 | 1.4336 | 1.4336 | 1.4336 | 1.9434 | 2.5079 | 2.8777 | 3.0724 | 3.4617 | 3.851 | 0.67827 | 1.3387 | 1.6064 | 1.6064 | 1.6064 | 1.6064 | 0.90565 | 1.0535 | 1.0535 | 1.0535 | 1.0535 | 1.0535
2020-10-28 07:00 | Summer | 1.7524 | 2.508 | 3.6192 | 3.6192 | 3.6192 | 3.6192 | 0.76305 | 1.2486 | 1.7111 | 2.0579 | 2.0579 | 2.0579 | 2.2291 | 2.8767 | 3.3009 | 3.5242 | 3.9708 | 4.4173 | 1.0288 | 2.0306 | 2.4367 | 2.4367 | 2.4367 | 2.4367 | 1.0836 | 1.2605 | 1.2605 | 1.2605 | 1.2605 | 1.2605
2020-10-28 08:00 | Summer | 2.1658 | 3.0997 | 4.4729 | 4.4729 | 4.4729 | 4.4729 | 0.86308 | 1.4123 | 1.9354 | 2.3277 | 2.3277 | 2.3277 | 2.4387 | 3.1471 | 3.6112 | 3.8555 | 4.3441 | 4.8326 | 1.006 | 1.9855 | 2.3826 | 2.3826 | 2.3826 | 2.3826 | 1.2575 | 1.4628 | 1.4628 | 1.4628 | 1.4628 | 1.4628
2020-10-28 09:00 | Summer | 2.191 | 3.1357 | 4.525 | 4.525 | 4.525 | 4.525 | 0.81735 | 1.3375 | 1.8328 | 2.2044 | 2.2044 | 2.2044 | 2.5149 | 3.2455 | 3.7241 | 3.976 | 4.4798 | 4.9836 | 0.95644 | 1.8877 | 2.2652 | 2.2652 | 2.2652 | 2.2652 | 1.2765 | 1.4849 | 1.4849 | 1.4849 | 1.4849 | 1.4849
2020-10-28 10:00 | Summer | 2.172 | 3.1085 | 4.4856 | 4.4856 | 4.4856 | 4.4856 | 0.86022 | 1.4076 | 1.929 | 2.32 | 2.32 | 2.32 | 2.553 | 3.2946 | 3.7805 | 4.0362 | 4.5477 | 5.0591 | 1.0174 | 2.008 | 2.4096 | 2.4096 | 2.4096 | 2.4096 | 1.3337 | 1.5514 | 1.5514 | 1.5514 | 1.5514 | 1.5514
2020-10-28 11:00 | Summer | 2.3244 | 3.3266 | 4.8004 | 4.8004 | 4.8004 | 4.8004 | 0.90309 | 1.4778 | 2.0251 | 2.4356 | 2.4356 | 2.4356 | 2.5721 | 3.3192 | 3.8087 | 4.0664 | 4.5816 | 5.0969 | 1.1012 | 2.1735 | 2.6082 | 2.6082 | 2.6082 | 2.6082 | 1.3337 | 1.5514 | 1.5514 | 1.5514 | 1.5514 | 1.5514
2020-10-28 12:00 | Summer | 2.2673 | 3.2448 | 4.6824 | 4.6824 | 4.6824 | 4.6824 | 0.89737 | 1.4684 | 2.0123 | 2.4202 | 2.4202 | 2.4202 | 2.6864 | 3.4668 | 3.978 | 4.2471 | 4.7853 | 5.3234 | 0.95644 | 1.8877 | 2.2652 | 2.2652 | 2.2652 | 2.2652 | 1.3146 | 1.5293 | 1.5293 | 1.5293 | 1.5293 | 1.5293
2020-10-28 13:00 | Summer | 2.2101 | 3.163 | 4.5643 | 4.5643 | 4.5643 | 4.5643 | 0.8002 | 1.3094 | 1.7944 | 2.1581 | 2.1581 | 2.1581 | 2.6674 | 3.4422 | 3.9498 | 4.217 | 4.7513 | 5.2857 | 0.96406 | 1.9027 | 2.2833 | 2.2833 | 2.2833 | 2.2833 | 1.2765 | 1.4849 | 1.4849 | 1.4849 | 1.4849 | 1.4849
2020-10-28 14:00 | Summer | 2.3054 | 3.2993 | 4.7611 | 4.7611 | 4.7611 | 4.7611 | 0.74019 | 1.2112 | 1.6598 | 1.9963 | 1.9963 | 1.9963 | 2.6674 | 3.4422 | 3.9498 | 4.217 | 4.7513 | 5.2857 | 0.9793 | 1.9328 | 2.3194 | 2.3194 | 2.3194 | 2.3194 | 1.2384 | 1.4406 | 1.4406 | 1.4406 | 1.4406 | 1.4406
2020-10-28 15:00 | Summer | 2.3054 | 3.2993 | 4.7611 | 4.7611 | 4.7611 | 4.7611 | 0.73161 | 1.1972 | 1.6406 | 1.9731 | 1.9731 | 1.9731 | 2.6864 | 3.4668 | 3.978 | 4.2471 | 4.7853 | 5.3234 | 0.94882 | 1.8727 | 2.2472 | 2.2472 | 2.2472 | 2.2472 | 1.2194 | 1.4184 | 1.4184 | 1.4184 | 1.4184 | 1.4184
2020-10-28 16:00 | Summer | 2.2863 | 3.2721 | 4.7217 | 4.7217 | 4.7217 | 4.7217 | 0.74019 | 1.2112 | 1.6598 | 1.9963 | 1.9963 | 1.9963 | 2.5149 | 3.2455 | 3.7241 | 3.976 | 4.4798 | 4.9836 | 0.95263 | 1.8802 | 2.2562 | 2.2562 | 2.2562 | 2.2562 | 1.1813 | 1.3741 | 1.3741 | 1.3741 | 1.3741 | 1.3741
2020-10-28 17:00 | Summer | 2.0577 | 2.9449 | 4.2495 | 4.2495 | 4.2495 | 4.2495 | 0.72876 | 1.1925 | 1.6342 | 1.9654 | 1.9654 | 1.9654 | 2.4578 | 3.1717 | 3.6395 | 3.8856 | 4.378 | 4.8704 | 0.89547 | 1.7674 | 2.1208 | 2.1208 | 2.1208 | 2.1208 | 1.105 | 1.2855 | 1.2855 | 1.2855 | 1.2855 | 1.2855
2020-10-28 18:00 | Summer | 1.7528 | 2.5086 | 3.62 | 3.62 | 3.62 | 3.62 | 0.54871 | 0.89789 | 1.2304 | 1.4799 | 1.4799 | 1.4799 | 2.354 | 3.0378 | 3.4858 | 3.7216 | 4.1931 | 4.6647 | 0.81164 | 1.6019 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 0.81196 | 0.94452 | 0.94452 | 0.94452 | 0.94452 | 0.94452
2020-10-28 19:00 | Summer | 1.1622 | 1.6633 | 2.4002 | 2.4002 | 2.4002 | 2.4002 | 0.46297 | 0.75759 | 1.0382 | 1.2486 | 1.2486 | 1.2486 | 2.2673 | 2.9258 | 3.3573 | 3.5844 | 4.0386 | 4.4928 | 0.81545 | 1.6094 | 1.9313 | 1.9313 | 1.9313 | 1.9313 | 0.70494 | 0.82004 | 0.82004 | 0.82004 | 0.82004 | 0.82004
2020-10-28 20:00 | Summer | 1.0288 | 1.4724 | 2.1248 | 2.1248 | 2.1248 | 2.1248 | 0.42296 | 0.69212 | 0.94846 | 1.1407 | 1.1407 | 1.1407 | 2.191 | 2.8275 | 3.2445 | 3.4639 | 3.9029 | 4.3418 | 0.85355 | 1.6846 | 2.0216 | 2.0216 | 2.0216 | 2.0216 | 0.61093 | 0.71068 | 0.71068 | 0.71068 | 0.71068 | 0.71068
2020-10-28 21:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.46869 | 0.76695 | 1.051 | 1.264 | 1.264 | 1.264 | 2.1339 | 2.7537 | 3.1598 | 3.3736 | 3.8011 | 4.2285 | 0.78115 | 1.5417 | 1.8501 | 1.8501 | 1.8501 | 1.8501 | 0.57158 | 0.6649 | 0.6649 | 0.6649 | 0.6649 | 0.6649
2020-10-28 22:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.3405 | 0.55718 | 0.76354 | 0.91831 | 0.91831 | 0.91831 | 1.8833 | 2.4304 | 2.7888 | 2.9775 | 3.3547 | 3.732 | 0.73162 | 1.444 | 1.7328 | 1.7328 | 1.7328 | 1.7328 | 0.55252 | 0.64273 | 0.64273 | 0.64273 | 0.64273 | 0.64273
2020-10-28 23:00 | Summer | 0.91452 | 1.3088 | 1.8887 | 1.8887 | 1.8887 | 1.8887 | 0.33437 | 0.54715 | 0.7498 | 0.90178 | 0.90178 | 0.90178 | 1.7528 | 2.262 | 2.5956 | 2.7712 | 3.1223 | 3.4734 | 0.67827 | 1.3387 | 1.6064 | 1.6064 | 1.6064 | 1.6064 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-10-29 | Summer | 0.91452 | 1.3088 | 1.8887 | 1.8887 | 1.8887 | 1.8887 | 0.30409 | 0.4976 | 0.6819 | 0.82012 | 0.82012 | 0.82012 | 1.6576 | 2.1391 | 2.4545 | 2.6205 | 2.9526 | 3.2847 | 0.64397 | 1.271 | 1.5252 | 1.5252 | 1.5252 | 1.5252 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-10-29 01:00 | Summer | 0.91452 | 1.3088 | 1.8887 | 1.8887 | 1.8887 | 1.8887 | 0.41935 | 0.6862 | 0.94035 | 1.131 | 1.131 | 1.131 | 1.6576 | 2.1391 | 2.4545 | 2.6205 | 2.9526 | 3.2847 | 0.64779 | 1.2785 | 1.5342 | 1.5342 | 1.5342 | 1.5342 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-10-29 02:00 | Summer | 0.91452 | 1.3088 | 1.8887 | 1.8887 | 1.8887 | 1.8887 | 0.42868 | 0.70147 | 0.96128 | 1.1561 | 1.1561 | 1.1561 | 1.5814 | 2.0407 | 2.3417 | 2.5001 | 2.8169 | 3.1337 | 0.59825 | 1.1808 | 1.4169 | 1.4169 | 1.4169 | 1.4169 | 0.45669 | 0.53126 | 0.53126 | 0.53126 | 0.53126 | 0.53126
2020-10-29 03:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.39438 | 0.64536 | 0.88438 | 1.0636 | 1.0636 | 1.0636 | 1.5623 | 2.0161 | 2.3135 | 2.4699 | 2.7829 | 3.0959 | 0.55252 | 1.0905 | 1.3086 | 1.3086 | 1.3086 | 1.3086 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-10-29 04:00 | Summer | 1.0479 | 1.4997 | 2.1641 | 2.1641 | 2.1641 | 2.1641 | 0.36412 | 0.59583 | 0.81651 | 0.98201 | 0.98201 | 0.98201 | 1.5814 | 2.0407 | 2.3417 | 2.5001 | 2.8169 | 3.1337 | 0.61349 | 1.2108 | 1.453 | 1.453 | 1.453 | 1.453 | 0.54812 | 0.63761 | 0.63761 | 0.63761 | 0.63761 | 0.63761
2020-10-29 05:00 | Summer | 1.1281 | 1.6145 | 2.3297 | 2.3297 | 2.3297 | 2.3297 | 0.54585 | 0.89321 | 1.224 | 1.4721 | 1.4721 | 1.4721 | 1.6957 | 2.1882 | 2.5109 | 2.6808 | 3.0205 | 3.3602 | 0.67065 | 1.3236 | 1.5884 | 1.5884 | 1.5884 | 1.5884 | 0.70485 | 0.81993 | 0.81993 | 0.81993 | 0.81993 | 0.81993
2020-10-29 06:00 | Summer | 1.2572 | 1.7992 | 2.5963 | 2.5963 | 2.5963 | 2.5963 | 0.61158 | 1.0008 | 1.3714 | 1.6494 | 1.6494 | 1.6494 | 1.8672 | 2.4095 | 2.7649 | 2.9519 | 3.3259 | 3.7 | 0.68589 | 1.3537 | 1.6245 | 1.6245 | 1.6245 | 1.6245 | 0.86215 | 1.0029 | 1.0029 | 1.0029 | 1.0029 | 1.0029
2020-10-29 07:00 | Summer | 1.6766 | 2.3995 | 3.4626 | 3.4626 | 3.4626 | 3.4626 | 0.78877 | 1.2907 | 1.7688 | 2.1273 | 2.1273 | 2.1273 | 2.3054 | 2.975 | 3.4138 | 3.6447 | 4.1065 | 4.5683 | 0.98311 | 1.9403 | 2.3284 | 2.3284 | 2.3284 | 2.3284 | 1.0694 | 1.244 | 1.244 | 1.244 | 1.244 | 1.244
2020-10-29 08:00 | Summer | 2.2101 | 3.163 | 4.5643 | 4.5643 | 4.5643 | 4.5643 | 0.8345 | 1.3655 | 1.8713 | 2.2506 | 2.2506 | 2.2506 | 2.4197 | 3.1225 | 3.583 | 3.8254 | 4.3101 | 4.7949 | 1.006 | 1.9855 | 2.3826 | 2.3826 | 2.3826 | 2.3826 | 1.2384 | 1.4406 | 1.4406 | 1.4406 | 1.4406 | 1.4406
2020-10-29 09:00 | Summer | 2.2673 | 3.2448 | 4.6824 | 4.6824 | 4.6824 | 4.6824 | 0.8002 | 1.3094 | 1.7944 | 2.1581 | 2.1581 | 2.1581 | 2.5149 | 3.2455 | 3.7241 | 3.976 | 4.4798 | 4.9836 | 1.006 | 1.9855 | 2.3826 | 2.3826 | 2.3826 | 2.3826 | 1.3146 | 1.5293 | 1.5293 | 1.5293 | 1.5293 | 1.5293
2020-10-29 10:00 | Summer | 2.2681 | 3.246 | 4.6841 | 4.6841 | 4.6841 | 4.6841 | 0.82307 | 1.3468 | 1.8457 | 2.2198 | 2.2198 | 2.2198 | 2.6293 | 3.393 | 3.8934 | 4.1567 | 4.6835 | 5.2102 | 1.0708 | 2.1133 | 2.536 | 2.536 | 2.536 | 2.536 | 1.2956 | 1.5071 | 1.5071 | 1.5071 | 1.5071 | 1.5071
2020-10-29 11:00 | Summer | 2.3625 | 3.3811 | 4.8791 | 4.8791 | 4.8791 | 4.8791 | 0.79163 | 1.2954 | 1.7752 | 2.135 | 2.135 | 2.135 | 2.6864 | 3.4668 | 3.978 | 4.2471 | 4.7853 | 5.3234 | 0.95263 | 1.8802 | 2.2562 | 2.2562 | 2.2562 | 2.2562 | 1.3337 | 1.5514 | 1.5514 | 1.5514 | 1.5514 | 1.5514
2020-10-29 12:00 | Summer | 2.3625 | 3.3811 | 4.8791 | 4.8791 | 4.8791 | 4.8791 | 0.84879 | 1.3889 | 1.9033 | 2.2892 | 2.2892 | 2.2892 | 2.6293 | 3.393 | 3.8934 | 4.1567 | 4.6835 | 5.2102 | 1.025 | 2.0231 | 2.4277 | 2.4277 | 2.4277 | 2.4277 | 1.3337 | 1.5514 | 1.5514 | 1.5514 | 1.5514 | 1.5514
2020-10-29 13:00 | Summer | 2.3816 | 3.4084 | 4.9185 | 4.9185 | 4.9185 | 4.9185 | 0.9431 | 1.5433 | 2.1148 | 2.5435 | 2.5435 | 2.5435 | 2.6102 | 3.3684 | 3.8652 | 4.1266 | 4.6495 | 5.1724 | 1.0326 | 2.0381 | 2.4457 | 2.4457 | 2.4457 | 2.4457 | 1.3527 | 1.5736 | 1.5736 | 1.5736 | 1.5736 | 1.5736
2020-10-29 14:00 | Summer | 2.2482 | 3.2175 | 4.643 | 4.643 | 4.643 | 4.643 | 0.90427 | 1.4797 | 2.0277 | 2.4388 | 2.4388 | 2.4388 | 2.5149 | 3.2455 | 3.7241 | 3.976 | 4.4798 | 4.9836 | 0.94119 | 1.8576 | 2.2291 | 2.2291 | 2.2291 | 2.2291 | 1.2765 | 1.4849 | 1.4849 | 1.4849 | 1.4849 | 1.4849
2020-10-29 15:00 | Summer | 2.1529 | 3.0812 | 4.4463 | 4.4463 | 4.4463 | 4.4463 | 0.86308 | 1.4123 | 1.9354 | 2.3277 | 2.3277 | 2.3277 | 2.5721 | 3.3192 | 3.8087 | 4.0664 | 4.5816 | 5.0969 | 0.91071 | 1.7975 | 2.1569 | 2.1569 | 2.1569 | 2.1569 | 1.2384 | 1.4406 | 1.4406 | 1.4406 | 1.4406 | 1.4406
2020-10-29 16:00 | Summer | 1.9243 | 2.754 | 3.9741 | 3.9741 | 3.9741 | 3.9741 | 0.81164 | 1.3281 | 1.82 | 2.189 | 2.189 | 2.189 | 2.534 | 3.2701 | 3.7523 | 4.0061 | 4.5138 | 5.0214 | 0.97168 | 1.9178 | 2.3013 | 2.3013 | 2.3013 | 2.3013 | 1.1432 | 1.3298 | 1.3298 | 1.3298 | 1.3298 | 1.3298
2020-10-29 17:00 | Summer | 1.81 | 2.5904 | 3.738 | 3.738 | 3.738 | 3.738 | 0.76591 | 1.2533 | 1.7175 | 2.0656 | 2.0656 | 2.0656 | 2.4771 | 3.1967 | 3.6681 | 3.9162 | 4.4124 | 4.9087 | 0.80402 | 1.5869 | 1.9042 | 1.9042 | 1.9042 | 1.9042 | 1.086 | 1.2633 | 1.2633 | 1.2633 | 1.2633 | 1.2633
2020-10-29 18:00 | Summer | 1.5195 | 2.1747 | 3.1382 | 3.1382 | 3.1382 | 3.1382 | 0.62016 | 1.0148 | 1.3907 | 1.6725 | 1.6725 | 1.6725 | 2.2863 | 2.9504 | 3.3855 | 3.6146 | 4.0726 | 4.5306 | 0.82688 | 1.632 | 1.9584 | 1.9584 | 1.9584 | 1.9584 | 0.93358 | 1.086 | 1.086 | 1.086 | 1.086 | 1.086
2020-10-29 19:00 | Summer | 1.1673 | 1.6706 | 2.4108 | 2.4108 | 2.4108 | 2.4108 | 0.52585 | 0.86048 | 1.1792 | 1.4182 | 1.4182 | 1.4182 | 2.1364 | 2.757 | 3.1636 | 3.3776 | 3.8056 | 4.2336 | 0.85736 | 1.6922 | 2.0306 | 2.0306 | 2.0306 | 2.0306 | 0.66684 | 0.77571 | 0.77571 | 0.77571 | 0.77571 | 0.77571
2020-10-29 20:00 | Summer | 1.086 | 1.5542 | 2.2428 | 2.2428 | 2.2428 | 2.2428 | 0.55728 | 0.91192 | 1.2497 | 1.503 | 1.503 | 1.503 | 2.0577 | 2.6554 | 3.047 | 3.2531 | 3.6653 | 4.0775 | 0.81164 | 1.6019 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 0.59063 | 0.68706 | 0.68706 | 0.68706 | 0.68706 | 0.68706
2020-10-29 21:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.50298 | 0.82306 | 1.1279 | 1.3565 | 1.3565 | 1.3565 | 2.0196 | 2.6062 | 2.9906 | 3.1929 | 3.5974 | 4.002 | 0.81164 | 1.6019 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 0.55252 | 0.64273 | 0.64273 | 0.64273 | 0.64273 | 0.64273
2020-10-29 22:00 | Summer | 0.96945 | 1.3874 | 2.0021 | 2.0021 | 2.0021 | 2.0021 | 0.47726 | 0.78098 | 1.0702 | 1.2872 | 1.2872 | 1.2872 | 1.8481 | 2.3849 | 2.7366 | 2.9218 | 3.292 | 3.6622 | 0.6897 | 1.3613 | 1.6335 | 1.6335 | 1.6335 | 1.6335 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-10-29 23:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.31151 | 0.50974 | 0.69853 | 0.84012 | 0.84012 | 0.84012 | 1.7147 | 2.2128 | 2.5392 | 2.7109 | 3.0544 | 3.3979 | 0.70494 | 1.3913 | 1.6696 | 1.6696 | 1.6696 | 1.6696 | 0.4572 | 0.53184 | 0.53184 | 0.53184 | 0.53184 | 0.53184
2020-10-30 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.30865 | 0.50506 | 0.69212 | 0.83241 | 0.83241 | 0.83241 | 1.6195 | 2.0899 | 2.3981 | 2.5603 | 2.8847 | 3.2092 | 0.65541 | 1.2936 | 1.5523 | 1.5523 | 1.5523 | 1.5523 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-10-30 01:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.3458 | 0.56585 | 0.77543 | 0.93261 | 0.93261 | 0.93261 | 1.5433 | 1.9915 | 2.2852 | 2.4398 | 2.749 | 3.0581 | 0.56014 | 1.1055 | 1.3267 | 1.3267 | 1.3267 | 1.3267 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-10-30 02:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.31812 | 0.52056 | 0.71336 | 0.85796 | 0.85796 | 0.85796 | 1.5623 | 2.0161 | 2.3135 | 2.4699 | 2.7829 | 3.0959 | 0.61349 | 1.2108 | 1.453 | 1.453 | 1.453 | 1.453 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-10-30 03:00 | Summer | 0.96535 | 1.3816 | 1.9937 | 1.9937 | 1.9937 | 1.9937 | 0.4001 | 0.65471 | 0.89719 | 1.0791 | 1.0791 | 1.0791 | 1.5623 | 2.0161 | 2.3135 | 2.4699 | 2.7829 | 3.0959 | 0.61349 | 1.2108 | 1.453 | 1.453 | 1.453 | 1.453 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-10-30 04:00 | Summer | 1.0479 | 1.4997 | 2.1641 | 2.1641 | 2.1641 | 2.1641 | 0.36581 | 0.59859 | 0.82029 | 0.98657 | 0.98657 | 0.98657 | 1.5623 | 2.0161 | 2.3135 | 2.4699 | 2.7829 | 3.0959 | 0.60587 | 1.1958 | 1.435 | 1.435 | 1.435 | 1.435 | 0.52976 | 0.61625 | 0.61625 | 0.61625 | 0.61625 | 0.61625
2020-10-30 05:00 | Summer | 1.1813 | 1.6906 | 2.4396 | 2.4396 | 2.4396 | 2.4396 | 0.47155 | 0.77162 | 1.0574 | 1.2717 | 1.2717 | 1.2717 | 1.6576 | 2.1391 | 2.4545 | 2.6205 | 2.9526 | 3.2847 | 0.60587 | 1.1958 | 1.435 | 1.435 | 1.435 | 1.435 | 0.70429 | 0.81927 | 0.81927 | 0.81927 | 0.81927 | 0.81927
2020-10-30 06:00 | Summer | 1.2809 | 1.8331 | 2.6453 | 2.6453 | 2.6453 | 2.6453 | 0.59158 | 0.96804 | 1.3266 | 1.5955 | 1.5955 | 1.5955 | 1.81 | 2.3358 | 2.6802 | 2.8615 | 3.2241 | 3.5867 | 0.69732 | 1.3763 | 1.6516 | 1.6516 | 1.6516 | 1.6516 | 0.86846 | 1.0103 | 1.0103 | 1.0103 | 1.0103 | 1.0103
2020-10-30 07:00 | Summer | 1.7808 | 2.5486 | 3.6778 | 3.6778 | 3.6778 | 3.6778 | 0.74876 | 1.2252 | 1.679 | 2.0194 | 2.0194 | 2.0194 | 2.1486 | 2.7727 | 3.1817 | 3.3969 | 3.8273 | 4.2577 | 1.0288 | 2.0306 | 2.4367 | 2.4367 | 2.4367 | 2.4367 | 0.99019 | 1.1519 | 1.1519 | 1.1519 | 1.1519 | 1.1519
2020-10-30 08:00 | Summer | 2.2291 | 3.1903 | 4.6037 | 4.6037 | 4.6037 | 4.6037 | 0.77734 | 1.272 | 1.7431 | 2.0965 | 2.0965 | 2.0965 | 2.2673 | 2.9258 | 3.3573 | 3.5844 | 4.0386 | 4.4928 | 1.025 | 2.0231 | 2.4277 | 2.4277 | 2.4277 | 2.4277 | 1.2003 | 1.3963 | 1.3963 | 1.3963 | 1.3963 | 1.3963
2020-10-30 09:00 | Summer | 2.1339 | 3.0539 | 4.4069 | 4.4069 | 4.4069 | 4.4069 | 0.87165 | 1.4263 | 1.9546 | 2.3508 | 2.3508 | 2.3508 | 2.4578 | 3.1717 | 3.6395 | 3.8856 | 4.378 | 4.8704 | 0.95263 | 1.8802 | 2.2562 | 2.2562 | 2.2562 | 2.2562 | 1.2765 | 1.4849 | 1.4849 | 1.4849 | 1.4849 | 1.4849
2020-10-30 10:00 | Summer | 2.15 | 3.077 | 4.4403 | 4.4403 | 4.4403 | 4.4403 | 0.78306 | 1.2814 | 1.7559 | 2.1119 | 2.1119 | 2.1119 | 2.4481 | 3.1592 | 3.6251 | 3.8703 | 4.3607 | 4.8511 | 0.89166 | 1.7599 | 2.1118 | 2.1118 | 2.1118 | 2.1118 | 1.3146 | 1.5293 | 1.5293 | 1.5293 | 1.5293 | 1.5293
2020-10-30 11:00 | Summer | 2.2863 | 3.2721 | 4.7217 | 4.7217 | 4.7217 | 4.7217 | 0.76877 | 1.258 | 1.7239 | 2.0733 | 2.0733 | 2.0733 | 2.6293 | 3.393 | 3.8934 | 4.1567 | 4.6835 | 5.2102 | 0.99454 | 1.9629 | 2.3555 | 2.3555 | 2.3555 | 2.3555 | 1.2956 | 1.5071 | 1.5071 | 1.5071 | 1.5071 | 1.5071
2020-10-30 12:00 | Summer | 2.3054 | 3.2993 | 4.7611 | 4.7611 | 4.7611 | 4.7611 | 0.77734 | 1.272 | 1.7431 | 2.0965 | 2.0965 | 2.0965 | 2.6102 | 3.3684 | 3.8652 | 4.1266 | 4.6495 | 5.1724 | 0.94119 | 1.8576 | 2.2291 | 2.2291 | 2.2291 | 2.2291 | 1.3527 | 1.5736 | 1.5736 | 1.5736 | 1.5736 | 1.5736
2020-10-30 13:00 | Summer | 2.2863 | 3.2721 | 4.7217 | 4.7217 | 4.7217 | 4.7217 | 0.8888 | 1.4544 | 1.9931 | 2.3971 | 2.3971 | 2.3971 | 2.6483 | 3.4176 | 3.9216 | 4.1869 | 4.7174 | 5.2479 | 0.91833 | 1.8125 | 2.175 | 2.175 | 2.175 | 2.175 | 1.3337 | 1.5514 | 1.5514 | 1.5514 | 1.5514 | 1.5514
2020-10-30 14:00 | Summer | 2.3435 | 3.3539 | 4.8398 | 4.8398 | 4.8398 | 4.8398 | 0.87451 | 1.431 | 1.961 | 2.3585 | 2.3585 | 2.3585 | 2.5911 | 3.3438 | 3.8369 | 4.0965 | 4.6156 | 5.1347 | 0.94119 | 1.8576 | 2.2291 | 2.2291 | 2.2291 | 2.2291 | 1.2765 | 1.4849 | 1.4849 | 1.4849 | 1.4849 | 1.4849
2020-10-30 15:00 | Summer | 2.2673 | 3.2448 | 4.6824 | 4.6824 | 4.6824 | 4.6824 | 1.0003 | 1.6368 | 2.243 | 2.6977 | 2.6977 | 2.6977 | 2.6293 | 3.393 | 3.8934 | 4.1567 | 4.6835 | 5.2102 | 0.93738 | 1.8501 | 2.2201 | 2.2201 | 2.2201 | 2.2201 | 1.2194 | 1.4184 | 1.4184 | 1.4184 | 1.4184 | 1.4184
2020-10-30 16:00 | Summer | 2.2673 | 3.2448 | 4.6824 | 4.6824 | 4.6824 | 4.6824 | 0.93738 | 1.5339 | 2.102 | 2.5281 | 2.5281 | 2.5281 | 2.5721 | 3.3192 | 3.8087 | 4.0664 | 4.5816 | 5.0969 | 0.91804 | 1.8119 | 2.1743 | 2.1743 | 2.1743 | 2.1743 | 1.2384 | 1.4406 | 1.4406 | 1.4406 | 1.4406 | 1.4406
2020-10-30 17:00 | Summer | 2.1339 | 3.0539 | 4.4069 | 4.4069 | 4.4069 | 4.4069 | 0.82307 | 1.3468 | 1.8457 | 2.2198 | 2.2198 | 2.2198 | 2.3948 | 3.0904 | 3.5462 | 3.7861 | 4.2658 | 4.7456 | 0.91833 | 1.8125 | 2.175 | 2.175 | 2.175 | 2.175 | 1.1622 | 1.352 | 1.352 | 1.352 | 1.352 | 1.352
2020-10-30 18:00 | Summer | 1.5478 | 2.2152 | 3.1966 | 3.1966 | 3.1966 | 3.1966 | 0.66022 | 1.0804 | 1.4805 | 1.7806 | 1.7806 | 1.7806 | 2.2673 | 2.9258 | 3.3573 | 3.5844 | 4.0386 | 4.4928 | 0.74305 | 1.4665 | 1.7599 | 1.7599 | 1.7599 | 1.7599 | 0.80307 | 0.93419 | 0.93419 | 0.93419 | 0.93419 | 0.93419
2020-10-30 19:00 | Summer | 1.105 | 1.5815 | 2.2822 | 2.2822 | 2.2822 | 2.2822 | 0.57729 | 0.94465 | 1.2945 | 1.5569 | 1.5569 | 1.5569 | 2.191 | 2.8275 | 3.2445 | 3.4639 | 3.9029 | 4.3418 | 0.7964 | 1.5718 | 1.8862 | 1.8862 | 1.8862 | 1.8862 | 0.62873 | 0.73138 | 0.73138 | 0.73138 | 0.73138 | 0.73138
2020-10-30 20:00 | Summer | 1.086 | 1.5542 | 2.2428 | 2.2428 | 2.2428 | 2.2428 | 0.54871 | 0.89789 | 1.2304 | 1.4799 | 1.4799 | 1.4799 | 2.1148 | 2.7291 | 3.1316 | 3.3435 | 3.7671 | 4.1908 | 0.80402 | 1.5869 | 1.9042 | 1.9042 | 1.9042 | 1.9042 | 0.60968 | 0.70922 | 0.70922 | 0.70922 | 0.70922 | 0.70922
2020-10-30 21:00 | Summer | 1.0288 | 1.4724 | 2.1248 | 2.1248 | 2.1248 | 2.1248 | 0.54871 | 0.89789 | 1.2304 | 1.4799 | 1.4799 | 1.4799 | 2.0958 | 2.7046 | 3.1034 | 3.3133 | 3.7332 | 4.153 | 0.84212 | 1.6621 | 1.9945 | 1.9945 | 1.9945 | 1.9945 | 0.55252 | 0.64273 | 0.64273 | 0.64273 | 0.64273 | 0.64273
2020-10-30 22:00 | Summer | 1.0043 | 1.4373 | 2.0741 | 2.0741 | 2.0741 | 2.0741 | 0.60015 | 0.98207 | 1.3458 | 1.6186 | 1.6186 | 1.6186 | 2.0386 | 2.6308 | 3.0188 | 3.223 | 3.6314 | 4.0398 | 0.76591 | 1.5117 | 1.814 | 1.814 | 1.814 | 1.814 | 0.49531 | 0.57617 | 0.57617 | 0.57617 | 0.57617 | 0.57617
2020-10-30 23:00 | Summer | 0.97211 | 1.3912 | 2.0076 | 2.0076 | 2.0076 | 2.0076 | 0.48584 | 0.79501 | 1.0895 | 1.3103 | 1.3103 | 1.3103 | 1.8443 | 2.3801 | 2.7311 | 2.9158 | 3.2853 | 3.6547 | 0.73162 | 1.444 | 1.7328 | 1.7328 | 1.7328 | 1.7328 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-10-31 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.33723 | 0.55183 | 0.75621 | 0.90949 | 0.90949 | 0.90949 | 1.7719 | 2.2866 | 2.6238 | 2.8013 | 3.1562 | 3.5112 | 0.6897 | 1.3613 | 1.6335 | 1.6335 | 1.6335 | 1.6335 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-10-31 01:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.3859 | 0.63148 | 0.86536 | 1.0408 | 1.0408 | 1.0408 | 1.6957 | 2.1882 | 2.5109 | 2.6808 | 3.0205 | 3.3602 | 0.82307 | 1.6245 | 1.9494 | 1.9494 | 1.9494 | 1.9494 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-10-31 02:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.40867 | 0.66874 | 0.91642 | 1.1022 | 1.1022 | 1.1022 | 1.6385 | 2.1145 | 2.4263 | 2.5904 | 2.9187 | 3.2469 | 0.64016 | 1.2635 | 1.5162 | 1.5162 | 1.5162 | 1.5162 | 0.45703 | 0.53165 | 0.53165 | 0.53165 | 0.53165 | 0.53165
2020-10-31 03:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.27994 | 0.45808 | 0.62774 | 0.75498 | 0.75498 | 0.75498 | 1.6195 | 2.0899 | 2.3981 | 2.5603 | 2.8847 | 3.2092 | 0.62873 | 1.2409 | 1.4891 | 1.4891 | 1.4891 | 1.4891 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-10-31 04:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.28007 | 0.45829 | 0.62803 | 0.75534 | 0.75534 | 0.75534 | 1.5814 | 2.0407 | 2.3417 | 2.5001 | 2.8169 | 3.1337 | 0.60587 | 1.1958 | 1.435 | 1.435 | 1.435 | 1.435 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-10-31 05:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.39153 | 0.64068 | 0.87797 | 1.0559 | 1.0559 | 1.0559 | 1.7338 | 2.2374 | 2.5674 | 2.741 | 3.0884 | 3.4357 | 0.71637 | 1.4139 | 1.6967 | 1.6967 | 1.6967 | 1.6967 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-10-31 06:00 | Summer | 1.0288 | 1.4724 | 2.1248 | 2.1248 | 2.1248 | 2.1248 | 0.44868 | 0.73421 | 1.0061 | 1.2101 | 1.2101 | 1.2101 | 1.6766 | 2.1636 | 2.4827 | 2.6507 | 2.9865 | 3.3224 | 0.58682 | 1.1582 | 1.3898 | 1.3898 | 1.3898 | 1.3898 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-10-31 07:00 | Summer | 1.0479 | 1.4997 | 2.1641 | 2.1641 | 2.1641 | 2.1641 | 0.52013 | 0.85112 | 1.1664 | 1.4028 | 1.4028 | 1.4028 | 1.7528 | 2.262 | 2.5956 | 2.7712 | 3.1223 | 3.4734 | 0.70113 | 1.3838 | 1.6606 | 1.6606 | 1.6606 | 1.6606 | 0.49179 | 0.57208 | 0.57208 | 0.57208 | 0.57208 | 0.57208
2020-10-31 08:00 | Summer | 1.1432 | 1.636 | 2.3609 | 2.3609 | 2.3609 | 2.3609 | 0.44297 | 0.72486 | 0.99332 | 1.1947 | 1.1947 | 1.1947 | 1.9053 | 2.4587 | 2.8213 | 3.0121 | 3.3938 | 3.7755 | 0.80402 | 1.5869 | 1.9042 | 1.9042 | 1.9042 | 1.9042 | 0.57158 | 0.6649 | 0.6649 | 0.6649 | 0.6649 | 0.6649
2020-10-31 09:00 | Summer | 1.1813 | 1.6906 | 2.4396 | 2.4396 | 2.4396 | 2.4396 | 0.583 | 0.95401 | 1.3073 | 1.5723 | 1.5723 | 1.5723 | 2.0577 | 2.6554 | 3.047 | 3.2531 | 3.6653 | 4.0775 | 0.76591 | 1.5117 | 1.814 | 1.814 | 1.814 | 1.814 | 0.60952 | 0.70904 | 0.70904 | 0.70904 | 0.70904 | 0.70904
2020-10-31 10:00 | Summer | 1.086 | 1.5542 | 2.2428 | 2.2428 | 2.2428 | 2.2428 | 0.60873 | 0.9961 | 1.365 | 1.6417 | 1.6417 | 1.6417 | 2.172 | 2.8029 | 3.2163 | 3.4338 | 3.8689 | 4.3041 | 0.7964 | 1.5718 | 1.8862 | 1.8862 | 1.8862 | 1.8862 | 0.62873 | 0.73138 | 0.73138 | 0.73138 | 0.73138 | 0.73138
2020-10-31 11:00 | Summer | 1.105 | 1.5815 | 2.2822 | 2.2822 | 2.2822 | 2.2822 | 0.57157 | 0.9353 | 1.2817 | 1.5415 | 1.5415 | 1.5415 | 2.1529 | 2.7783 | 3.1881 | 3.4037 | 3.835 | 4.2663 | 0.79258 | 1.5643 | 1.8772 | 1.8772 | 1.8772 | 1.8772 | 0.62873 | 0.73138 | 0.73138 | 0.73138 | 0.73138 | 0.73138
2020-10-31 12:00 | Summer | 1.1432 | 1.636 | 2.3609 | 2.3609 | 2.3609 | 2.3609 | 0.6373 | 1.0429 | 1.4291 | 1.7188 | 1.7188 | 1.7188 | 2.172 | 2.8029 | 3.2163 | 3.4338 | 3.8689 | 4.3041 | 0.76591 | 1.5117 | 1.814 | 1.814 | 1.814 | 1.814 | 0.62873 | 0.73138 | 0.73138 | 0.73138 | 0.73138 | 0.73138
2020-10-31 13:00 | Summer | 1.086 | 1.5542 | 2.2428 | 2.2428 | 2.2428 | 2.2428 | 0.62301 | 1.0195 | 1.3971 | 1.6803 | 1.6803 | 1.6803 | 2.1339 | 2.7537 | 3.1598 | 3.3736 | 3.8011 | 4.2285 | 0.78496 | 1.5493 | 1.8591 | 1.8591 | 1.8591 | 1.8591 | 0.57158 | 0.6649 | 0.6649 | 0.6649 | 0.6649 | 0.6649
2020-10-31 14:00 | Summer | 1.086 | 1.5542 | 2.2428 | 2.2428 | 2.2428 | 2.2428 | 0.583 | 0.95401 | 1.3073 | 1.5723 | 1.5723 | 1.5723 | 2.2101 | 2.8521 | 3.2727 | 3.4941 | 3.9368 | 4.3796 | 0.78115 | 1.5417 | 1.8501 | 1.8501 | 1.8501 | 1.8501 | 0.57158 | 0.6649 | 0.6649 | 0.6649 | 0.6649 | 0.6649
2020-10-31 15:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.62301 | 1.0195 | 1.3971 | 1.6803 | 1.6803 | 1.6803 | 2.191 | 2.8275 | 3.2445 | 3.4639 | 3.9029 | 4.3418 | 0.78115 | 1.5417 | 1.8501 | 1.8501 | 1.8501 | 1.8501 | 0.60968 | 0.70922 | 0.70922 | 0.70922 | 0.70922 | 0.70922
2020-10-31 16:00 | Summer | 1.0288 | 1.4724 | 2.1248 | 2.1248 | 2.1248 | 2.1248 | 0.64302 | 1.0522 | 1.4419 | 1.7342 | 1.7342 | 1.7342 | 2.191 | 2.8275 | 3.2445 | 3.4639 | 3.9029 | 4.3418 | 0.78877 | 1.5568 | 1.8681 | 1.8681 | 1.8681 | 1.8681 | 0.53347 | 0.62057 | 0.62057 | 0.62057 | 0.62057 | 0.62057
2020-10-31 17:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.62873 | 1.0288 | 1.4099 | 1.6957 | 1.6957 | 1.6957 | 2.1529 | 2.7783 | 3.1881 | 3.4037 | 3.835 | 4.2663 | 0.78115 | 1.5417 | 1.8501 | 1.8501 | 1.8501 | 1.8501 | 0.55252 | 0.64273 | 0.64273 | 0.64273 | 0.64273 | 0.64273
2020-10-31 18:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.60587 | 0.99142 | 1.3586 | 1.634 | 1.634 | 1.634 | 2.1148 | 2.7291 | 3.1316 | 3.3435 | 3.7671 | 4.1908 | 0.89547 | 1.7674 | 2.1208 | 2.1208 | 2.1208 | 2.1208 | 0.55252 | 0.64273 | 0.64273 | 0.64273 | 0.64273 | 0.64273
2020-10-31 19:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.64874 | 1.0616 | 1.4547 | 1.7496 | 1.7496 | 1.7496 | 2.1339 | 2.7537 | 3.1598 | 3.3736 | 3.8011 | 4.2285 | 0.85736 | 1.6922 | 2.0306 | 2.0306 | 2.0306 | 2.0306 | 0.54869 | 0.63828 | 0.63828 | 0.63828 | 0.63828 | 0.63828
2020-10-31 20:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.6373 | 1.0429 | 1.4291 | 1.7188 | 1.7188 | 1.7188 | 2.172 | 2.8029 | 3.2163 | 3.4338 | 3.8689 | 4.3041 | 0.89928 | 1.7749 | 2.1299 | 2.1299 | 2.1299 | 2.1299 | 0.55252 | 0.64273 | 0.64273 | 0.64273 | 0.64273 | 0.64273
2020-10-31 21:00 | Summer | 0.97886 | 1.4009 | 2.0216 | 2.0216 | 2.0216 | 2.0216 | 0.60015 | 0.98207 | 1.3458 | 1.6186 | 1.6186 | 1.6186 | 2.0005 | 2.5816 | 2.9624 | 3.1627 | 3.5635 | 3.9643 | 0.84974 | 1.6771 | 2.0125 | 2.0125 | 2.0125 | 2.0125 | 0.49997 | 0.58159 | 0.58159 | 0.58159 | 0.58159 | 0.58159
2020-10-31 22:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.43439 | 0.71083 | 0.9741 | 1.1715 | 1.1715 | 1.1715 | 1.8862 | 2.4341 | 2.7931 | 2.982 | 3.3599 | 3.7377 | 0.74686 | 1.4741 | 1.7689 | 1.7689 | 1.7689 | 1.7689 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-10-31 23:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.34866 | 0.57053 | 0.78184 | 0.94032 | 0.94032 | 0.94032 | 1.81 | 2.3358 | 2.6802 | 2.8615 | 3.2241 | 3.5867 | 0.73924 | 1.459 | 1.7508 | 1.7508 | 1.7508 | 1.7508 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-11-01 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.38581 | 0.63133 | 0.86515 | 1.0405 | 1.0405 | 1.0405 | 1.7528 | 2.262 | 2.5956 | 2.7712 | 3.1223 | 3.4734 | 0.69732 | 1.3763 | 1.6516 | 1.6516 | 1.6516 | 1.6516 | 0.4535 | 0.52754 | 0.52754 | 0.52754 | 0.52754 | 0.52754
2020-11-01 01:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.31004 | 0.50734 | 0.69524 | 0.83617 | 0.83617 | 0.83617 | 1.5626 | 2.0165 | 2.3139 | 2.4704 | 2.7835 | 3.0965 | 0.61575 | 1.2153 | 1.4584 | 1.4584 | 1.4584 | 1.4584 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-11-01 02:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.34866 | 0.57053 | 0.78184 | 0.94032 | 0.94032 | 0.94032 | 1.5623 | 2.0161 | 2.3135 | 2.4699 | 2.7829 | 3.0959 | 0.64779 | 1.2785 | 1.5342 | 1.5342 | 1.5342 | 1.5342 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-11-01 03:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.47441 | 0.7763 | 1.0638 | 1.2795 | 1.2795 | 1.2795 | 1.5428 | 1.9909 | 2.2845 | 2.4391 | 2.7481 | 3.0572 | 0.58682 | 1.1582 | 1.3898 | 1.3898 | 1.3898 | 1.3898 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-11-01 04:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.40653 | 0.66523 | 0.91161 | 1.0964 | 1.0964 | 1.0964 | 1.5433 | 1.9915 | 2.2852 | 2.4398 | 2.749 | 3.0581 | 0.61349 | 1.2108 | 1.453 | 1.453 | 1.453 | 1.453 | 0.43648 | 0.50774 | 0.50774 | 0.50774 | 0.50774 | 0.50774
2020-11-01 05:00 | Summer | 0.96021 | 1.3742 | 1.983 | 1.983 | 1.983 | 1.983 | 0.40867 | 0.66874 | 0.91642 | 1.1022 | 1.1022 | 1.1022 | 1.5814 | 2.0407 | 2.3417 | 2.5001 | 2.8169 | 3.1337 | 0.7621 | 1.5041 | 1.805 | 1.805 | 1.805 | 1.805 | 0.45385 | 0.52795 | 0.52795 | 0.52795 | 0.52795 | 0.52795
2020-11-01 06:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.51442 | 0.84177 | 1.1535 | 1.3874 | 1.3874 | 1.3874 | 1.6576 | 2.1391 | 2.4545 | 2.6205 | 2.9526 | 3.2847 | 0.6173 | 1.2184 | 1.462 | 1.462 | 1.462 | 1.462 | 0.47123 | 0.54817 | 0.54817 | 0.54817 | 0.54817 | 0.54817
2020-11-01 07:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.53728 | 0.87918 | 1.2048 | 1.449 | 1.449 | 1.449 | 1.7847 | 2.3031 | 2.6427 | 2.8215 | 3.179 | 3.5365 | 0.71256 | 1.4064 | 1.6877 | 1.6877 | 1.6877 | 1.6877 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-11-01 08:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.5287 | 0.86515 | 1.1856 | 1.4259 | 1.4259 | 1.4259 | 1.9434 | 2.5079 | 2.8777 | 3.0724 | 3.4617 | 3.851 | 0.70875 | 1.3989 | 1.6786 | 1.6786 | 1.6786 | 1.6786 | 0.49533 | 0.5762 | 0.5762 | 0.5762 | 0.5762 | 0.5762
2020-11-01 09:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.56014 | 0.9166 | 1.2561 | 1.5107 | 1.5107 | 1.5107 | 2.0767 | 2.68 | 3.0752 | 3.2832 | 3.6992 | 4.1153 | 0.7964 | 1.5718 | 1.8862 | 1.8862 | 1.8862 | 1.8862 | 0.51121 | 0.59467 | 0.59467 | 0.59467 | 0.59467 | 0.59467
2020-11-01 10:00 | Summer | 0.89547 | 1.2816 | 1.8493 | 1.8493 | 1.8493 | 1.8493 | 0.45154 | 0.73889 | 1.0125 | 1.2178 | 1.2178 | 1.2178 | 2.0386 | 2.6308 | 3.0188 | 3.223 | 3.6314 | 4.0398 | 0.76591 | 1.5117 | 1.814 | 1.814 | 1.814 | 1.814 | 0.54244 | 0.63101 | 0.63101 | 0.63101 | 0.63101 | 0.63101
2020-11-01 11:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.42011 | 0.68744 | 0.94205 | 1.133 | 1.133 | 1.133 | 2.0386 | 2.6308 | 3.0188 | 3.223 | 3.6314 | 4.0398 | 0.72018 | 1.4214 | 1.7057 | 1.7057 | 1.7057 | 1.7057 | 0.55252 | 0.64273 | 0.64273 | 0.64273 | 0.64273 | 0.64273
2020-11-01 12:00 | Summer | 0.95398 | 1.3653 | 1.9702 | 1.9702 | 1.9702 | 1.9702 | 0.44011 | 0.72018 | 0.98691 | 1.187 | 1.187 | 1.187 | 2.0577 | 2.6554 | 3.047 | 3.2531 | 3.6653 | 4.0775 | 0.74686 | 1.4741 | 1.7689 | 1.7689 | 1.7689 | 1.7689 | 0.53347 | 0.62057 | 0.62057 | 0.62057 | 0.62057 | 0.62057
2020-11-01 13:00 | Summer | 0.91452 | 1.3088 | 1.8887 | 1.8887 | 1.8887 | 1.8887 | 0.39724 | 0.65003 | 0.89079 | 1.0713 | 1.0713 | 1.0713 | 2.0196 | 2.6062 | 2.9906 | 3.1929 | 3.5974 | 4.002 | 0.70875 | 1.3989 | 1.6786 | 1.6786 | 1.6786 | 1.6786 | 0.53347 | 0.62057 | 0.62057 | 0.62057 | 0.62057 | 0.62057
2020-11-01 14:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.39724 | 0.65003 | 0.89079 | 1.0713 | 1.0713 | 1.0713 | 2.0577 | 2.6554 | 3.047 | 3.2531 | 3.6653 | 4.0775 | 0.78115 | 1.5417 | 1.8501 | 1.8501 | 1.8501 | 1.8501 | 0.53347 | 0.62057 | 0.62057 | 0.62057 | 0.62057 | 0.62057
2020-11-01 15:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.39724 | 0.65003 | 0.89079 | 1.0713 | 1.0713 | 1.0713 | 2.0005 | 2.5816 | 2.9624 | 3.1627 | 3.5635 | 3.9643 | 0.75829 | 1.4966 | 1.796 | 1.796 | 1.796 | 1.796 | 0.55252 | 0.64273 | 0.64273 | 0.64273 | 0.64273 | 0.64273
2020-11-01 16:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.38581 | 0.63133 | 0.86515 | 1.0405 | 1.0405 | 1.0405 | 2.0577 | 2.6554 | 3.047 | 3.2531 | 3.6653 | 4.0775 | 0.83831 | 1.6546 | 1.9855 | 1.9855 | 1.9855 | 1.9855 | 0.59063 | 0.68706 | 0.68706 | 0.68706 | 0.68706 | 0.68706
2020-11-01 17:00 | Summer | 0.95186 | 1.3623 | 1.9658 | 1.9658 | 1.9658 | 1.9658 | 0.41439 | 0.67809 | 0.92924 | 1.1176 | 1.1176 | 1.1176 | 2.039 | 2.6312 | 3.0193 | 3.2235 | 3.632 | 4.0404 | 0.77353 | 1.5267 | 1.832 | 1.832 | 1.832 | 1.832 | 0.53347 | 0.62057 | 0.62057 | 0.62057 | 0.62057 | 0.62057
2020-11-01 18:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.42011 | 0.68744 | 0.94205 | 1.133 | 1.133 | 1.133 | 2.0005 | 2.5816 | 2.9624 | 3.1627 | 3.5635 | 3.9643 | 0.88023 | 1.7373 | 2.0847 | 2.0847 | 2.0847 | 2.0847 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-11-01 19:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.37724 | 0.6173 | 0.84593 | 1.0174 | 1.0174 | 1.0174 | 1.9434 | 2.5079 | 2.8777 | 3.0724 | 3.4617 | 3.851 | 0.84974 | 1.6771 | 2.0125 | 2.0125 | 2.0125 | 2.0125 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-11-01 20:00 | Summer | 1.0288 | 1.4724 | 2.1248 | 2.1248 | 2.1248 | 2.1248 | 0.40296 | 0.65939 | 0.9036 | 1.0868 | 1.0868 | 1.0868 | 2.0005 | 2.5816 | 2.9624 | 3.1627 | 3.5635 | 3.9643 | 0.88785 | 1.7523 | 2.1028 | 2.1028 | 2.1028 | 2.1028 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-11-01 21:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.43154 | 0.70615 | 0.96769 | 1.1638 | 1.1638 | 1.1638 | 1.9474 | 2.5131 | 2.8838 | 3.0788 | 3.4689 | 3.8591 | 0.80783 | 1.5944 | 1.9133 | 1.9133 | 1.9133 | 1.9133 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-11-01 22:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.30865 | 0.50506 | 0.69212 | 0.83241 | 0.83241 | 0.83241 | 1.8173 | 2.3452 | 2.691 | 2.873 | 3.2371 | 3.6012 | 0.79258 | 1.5643 | 1.8772 | 1.8772 | 1.8772 | 1.8772 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-11-01 23:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.2973 | 0.48649 | 0.66667 | 0.80181 | 0.80181 | 0.80181 | 1.829 | 2.3603 | 2.7084 | 2.8916 | 3.2581 | 3.6245 | 0.63254 | 1.2484 | 1.4981 | 1.4981 | 1.4981 | 1.4981 | 0.47089 | 0.54777 | 0.54777 | 0.54777 | 0.54777 | 0.54777
2020-11-02 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.29143 | 0.47689 | 0.65352 | 0.78599 | 0.78599 | 0.78599 | 1.6766 | 2.1636 | 2.4827 | 2.6507 | 2.9865 | 3.3224 | 0.62873 | 1.2409 | 1.4891 | 1.4891 | 1.4891 | 1.4891 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-11-02 01:00 | Summer | 0.95375 | 1.365 | 1.9697 | 1.9697 | 1.9697 | 1.9697 | 0.39438 | 0.64536 | 0.88438 | 1.0636 | 1.0636 | 1.0636 | 1.6766 | 2.1636 | 2.4827 | 2.6507 | 2.9865 | 3.3224 | 0.59063 | 1.1657 | 1.3989 | 1.3989 | 1.3989 | 1.3989 | 0.47407 | 0.55147 | 0.55147 | 0.55147 | 0.55147 | 0.55147
2020-11-02 02:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.28578 | 0.46765 | 0.64085 | 0.77075 | 0.77075 | 0.77075 | 1.5814 | 2.0407 | 2.3417 | 2.5001 | 2.8169 | 3.1337 | 0.62111 | 1.2259 | 1.4711 | 1.4711 | 1.4711 | 1.4711 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-11-02 03:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.39438 | 0.64536 | 0.88438 | 1.0636 | 1.0636 | 1.0636 | 1.5433 | 1.9915 | 2.2852 | 2.4398 | 2.749 | 3.0581 | 0.57419 | 1.1333 | 1.3599 | 1.3599 | 1.3599 | 1.3599 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-11-02 04:00 | Summer | 1.105 | 1.5815 | 2.2822 | 2.2822 | 2.2822 | 2.2822 | 0.41725 | 0.68277 | 0.93565 | 1.1253 | 1.1253 | 1.1253 | 1.5722 | 2.0289 | 2.3281 | 2.4856 | 2.8006 | 3.1155 | 0.57539 | 1.1356 | 1.3628 | 1.3628 | 1.3628 | 1.3628 | 0.53347 | 0.62057 | 0.62057 | 0.62057 | 0.62057 | 0.62057
2020-11-02 05:00 | Summer | 1.164 | 1.6659 | 2.404 | 2.404 | 2.404 | 2.404 | 0.49727 | 0.81371 | 1.1151 | 1.3411 | 1.3411 | 1.3411 | 1.6766 | 2.1636 | 2.4827 | 2.6507 | 2.9865 | 3.3224 | 0.66256 | 1.3077 | 1.5692 | 1.5692 | 1.5692 | 1.5692 | 0.64779 | 0.75355 | 0.75355 | 0.75355 | 0.75355 | 0.75355
2020-11-02 06:00 | Summer | 1.3586 | 1.9444 | 2.8058 | 2.8058 | 2.8058 | 2.8058 | 0.70018 | 1.1457 | 1.5701 | 1.8884 | 1.8884 | 1.8884 | 1.8826 | 2.4294 | 2.7877 | 2.9763 | 3.3534 | 3.7306 | 0.6897 | 1.3613 | 1.6335 | 1.6335 | 1.6335 | 1.6335 | 0.87024 | 1.0123 | 1.0123 | 1.0123 | 1.0123 | 1.0123
2020-11-02 07:00 | Summer | 1.9053 | 2.7267 | 3.9348 | 3.9348 | 3.9348 | 3.9348 | 0.78591 | 1.286 | 1.7624 | 2.1196 | 2.1196 | 2.1196 | 2.1339 | 2.7537 | 3.1598 | 3.3736 | 3.8011 | 4.2285 | 0.95263 | 1.8802 | 2.2562 | 2.2562 | 2.2562 | 2.2562 | 1.0274 | 1.1952 | 1.1952 | 1.1952 | 1.1952 | 1.1952
2020-11-02 08:00 | Summer | 2.3625 | 3.3811 | 4.8791 | 4.8791 | 4.8791 | 4.8791 | 0.83736 | 1.3702 | 1.8777 | 2.2583 | 2.2583 | 2.2583 | 2.3435 | 3.0242 | 3.4702 | 3.7049 | 4.1744 | 4.6438 | 0.93738 | 1.8501 | 2.2201 | 2.2201 | 2.2201 | 2.2201 | 1.2384 | 1.4406 | 1.4406 | 1.4406 | 1.4406 | 1.4406
2020-11-02 09:00 | Summer | 2.2673 | 3.2448 | 4.6824 | 4.6824 | 4.6824 | 4.6824 | 0.83736 | 1.3702 | 1.8777 | 2.2583 | 2.2583 | 2.2583 | 2.3435 | 3.0242 | 3.4702 | 3.7049 | 4.1744 | 4.6438 | 0.9793 | 1.9328 | 2.3194 | 2.3194 | 2.3194 | 2.3194 | 1.2384 | 1.4406 | 1.4406 | 1.4406 | 1.4406 | 1.4406
2020-11-02 10:00 | Summer | 2.3816 | 3.4084 | 4.9185 | 4.9185 | 4.9185 | 4.9185 | 0.77734 | 1.272 | 1.7431 | 2.0965 | 2.0965 | 2.0965 | 2.4959 | 3.2209 | 3.6959 | 3.9459 | 4.4459 | 4.9459 | 1.0098 | 1.993 | 2.3916 | 2.3916 | 2.3916 | 2.3916 | 1.3337 | 1.5514 | 1.5514 | 1.5514 | 1.5514 | 1.5514
2020-11-02 11:00 | Summer | 2.4006 | 3.4357 | 4.9578 | 4.9578 | 4.9578 | 4.9578 | 0.71733 | 1.1738 | 1.6085 | 1.9346 | 1.9346 | 1.9346 | 2.5911 | 3.3438 | 3.8369 | 4.0965 | 4.6156 | 5.1347 | 0.91452 | 1.805 | 2.166 | 2.166 | 2.166 | 2.166 | 1.3527 | 1.5736 | 1.5736 | 1.5736 | 1.5736 | 1.5736
2020-11-02 12:00 | Summer | 2.3816 | 3.4084 | 4.9185 | 4.9185 | 4.9185 | 4.9185 | 0.8545 | 1.3983 | 1.9162 | 2.3046 | 2.3046 | 2.3046 | 2.534 | 3.2701 | 3.7523 | 4.0061 | 4.5138 | 5.0214 | 0.93357 | 1.8426 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 1.2956 | 1.5071 | 1.5071 | 1.5071 | 1.5071 | 1.5071
2020-11-02 13:00 | Summer | 2.3435 | 3.3539 | 4.8398 | 4.8398 | 4.8398 | 4.8398 | 0.79163 | 1.2954 | 1.7752 | 2.135 | 2.135 | 2.135 | 2.6674 | 3.4422 | 3.9498 | 4.217 | 4.7513 | 5.2857 | 0.96025 | 1.8952 | 2.2743 | 2.2743 | 2.2743 | 2.2743 | 1.2765 | 1.4849 | 1.4849 | 1.4849 | 1.4849 | 1.4849
2020-11-02 14:00 | Summer | 2.4578 | 3.5175 | 5.0759 | 5.0759 | 5.0759 | 5.0759 | 0.84879 | 1.3889 | 1.9033 | 2.2892 | 2.2892 | 2.2892 | 2.6528 | 3.4234 | 3.9282 | 4.1939 | 4.7254 | 5.2568 | 1.1432 | 2.2562 | 2.7075 | 2.7075 | 2.7075 | 2.7075 | 1.3146 | 1.5293 | 1.5293 | 1.5293 | 1.5293 | 1.5293
2020-11-02 15:00 | Summer | 2.3816 | 3.4084 | 4.9185 | 4.9185 | 4.9185 | 4.9185 | 0.86308 | 1.4123 | 1.9354 | 2.3277 | 2.3277 | 2.3277 | 2.5721 | 3.3192 | 3.8087 | 4.0664 | 4.5816 | 5.0969 | 0.99073 | 1.9554 | 2.3465 | 2.3465 | 2.3465 | 2.3465 | 1.2956 | 1.5071 | 1.5071 | 1.5071 | 1.5071 | 1.5071
2020-11-02 16:00 | Summer | 2.3244 | 3.3266 | 4.8004 | 4.8004 | 4.8004 | 4.8004 | 0.97739 | 1.5994 | 2.1917 | 2.636 | 2.636 | 2.636 | 2.6102 | 3.3684 | 3.8652 | 4.1266 | 4.6495 | 5.1724 | 0.98692 | 1.9479 | 2.3374 | 2.3374 | 2.3374 | 2.3374 | 1.2575 | 1.4628 | 1.4628 | 1.4628 | 1.4628 | 1.4628
2020-11-02 17:00 | Summer | 2.3025 | 3.2953 | 4.7552 | 4.7552 | 4.7552 | 4.7552 | 0.77162 | 1.2627 | 1.7303 | 2.081 | 2.081 | 2.081 | 2.534 | 3.2701 | 3.7523 | 4.0061 | 4.5138 | 5.0214 | 1.0022 | 1.978 | 2.3735 | 2.3735 | 2.3735 | 2.3735 | 1.2575 | 1.4628 | 1.4628 | 1.4628 | 1.4628 | 1.4628
2020-11-02 18:00 | Summer | 1.8674 | 2.6726 | 3.8566 | 3.8566 | 3.8566 | 3.8566 | 0.50769 | 0.83077 | 1.1385 | 1.3692 | 1.3692 | 1.3692 | 2.2863 | 2.9504 | 3.3855 | 3.6146 | 4.0726 | 4.5306 | 0.82307 | 1.6245 | 1.9494 | 1.9494 | 1.9494 | 1.9494 | 0.84462 | 0.98252 | 0.98252 | 0.98252 | 0.98252 | 0.98252
2020-11-02 19:00 | Summer | 1.1822 | 1.6919 | 2.4414 | 2.4414 | 2.4414 | 2.4414 | 0.43725 | 0.7155 | 0.98051 | 1.1793 | 1.1793 | 1.1793 | 2.1299 | 2.7486 | 3.154 | 3.3673 | 3.794 | 4.2207 | 0.82307 | 1.6245 | 1.9494 | 1.9494 | 1.9494 | 1.9494 | 0.60896 | 0.70838 | 0.70838 | 0.70838 | 0.70838 | 0.70838
2020-11-02 20:00 | Summer | 1.1212 | 1.6046 | 2.3155 | 2.3155 | 2.3155 | 2.3155 | 0.39724 | 0.65003 | 0.89079 | 1.0713 | 1.0713 | 1.0713 | 2.1148 | 2.7291 | 3.1316 | 3.3435 | 3.7671 | 4.1908 | 0.73543 | 1.4515 | 1.7418 | 1.7418 | 1.7418 | 1.7418 | 0.59063 | 0.68706 | 0.68706 | 0.68706 | 0.68706 | 0.68706
2020-11-02 21:00 | Summer | 1.0479 | 1.4997 | 2.1641 | 2.1641 | 2.1641 | 2.1641 | 0.42011 | 0.68744 | 0.94205 | 1.133 | 1.133 | 1.133 | 1.9426 | 2.5068 | 2.8765 | 3.0711 | 3.4602 | 3.8494 | 0.724 | 1.4289 | 1.7147 | 1.7147 | 1.7147 | 1.7147 | 0.53347 | 0.62057 | 0.62057 | 0.62057 | 0.62057 | 0.62057
2020-11-02 22:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.39724 | 0.65003 | 0.89079 | 1.0713 | 1.0713 | 1.0713 | 1.9434 | 2.5079 | 2.8777 | 3.0724 | 3.4617 | 3.851 | 0.71256 | 1.4064 | 1.6877 | 1.6877 | 1.6877 | 1.6877 | 0.48059 | 0.55906 | 0.55906 | 0.55906 | 0.55906 | 0.55906
2020-11-02 23:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.32865 | 0.5378 | 0.73698 | 0.88637 | 0.88637 | 0.88637 | 1.7147 | 2.2128 | 2.5392 | 2.7109 | 3.0544 | 3.3979 | 0.70122 | 1.384 | 1.6608 | 1.6608 | 1.6608 | 1.6608 | 0.45725 | 0.5319 | 0.5319 | 0.5319 | 0.5319 | 0.5319
2020-11-03 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.34008 | 0.5565 | 0.76261 | 0.9172 | 0.9172 | 0.9172 | 1.7078 | 2.2038 | 2.5289 | 2.6999 | 3.042 | 3.3841 | 0.60587 | 1.1958 | 1.435 | 1.435 | 1.435 | 1.435 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-11-03 01:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.2915 | 0.477 | 0.65367 | 0.78617 | 0.78617 | 0.78617 | 1.6301 | 2.1036 | 2.4138 | 2.5771 | 2.9037 | 3.2302 | 0.53728 | 1.0604 | 1.2725 | 1.2725 | 1.2725 | 1.2725 | 0.43821 | 0.50975 | 0.50975 | 0.50975 | 0.50975 | 0.50975
2020-11-03 02:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.39438 | 0.64536 | 0.88438 | 1.0636 | 1.0636 | 1.0636 | 1.6385 | 2.1145 | 2.4263 | 2.5904 | 2.9187 | 3.2469 | 0.76972 | 1.5192 | 1.823 | 1.823 | 1.823 | 1.823 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-11-03 03:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.37438 | 0.61262 | 0.83952 | 1.0097 | 1.0097 | 1.0097 | 1.638 | 2.1138 | 2.4255 | 2.5896 | 2.9177 | 3.2458 | 0.5449 | 1.0755 | 1.2906 | 1.2906 | 1.2906 | 1.2906 | 0.47776 | 0.55577 | 0.55577 | 0.55577 | 0.55577 | 0.55577
2020-11-03 04:00 | Summer | 1.0669 | 1.527 | 2.2035 | 2.2035 | 2.2035 | 2.2035 | 0.29436 | 0.48168 | 0.66008 | 0.79388 | 0.79388 | 0.79388 | 1.6385 | 2.1145 | 2.4263 | 2.5904 | 2.9187 | 3.2469 | 0.62492 | 1.2334 | 1.4801 | 1.4801 | 1.4801 | 1.4801 | 0.54947 | 0.63918 | 0.63918 | 0.63918 | 0.63918 | 0.63918
2020-11-03 05:00 | Summer | 1.2003 | 1.7178 | 2.4789 | 2.4789 | 2.4789 | 2.4789 | 0.4544 | 0.74356 | 1.019 | 1.2255 | 1.2255 | 1.2255 | 1.6957 | 2.1882 | 2.5109 | 2.6808 | 3.0205 | 3.3602 | 0.63635 | 1.256 | 1.5072 | 1.5072 | 1.5072 | 1.5072 | 0.58367 | 0.67896 | 0.67896 | 0.67896 | 0.67896 | 0.67896
2020-11-03 06:00 | Summer | 1.2764 | 1.8267 | 2.636 | 2.636 | 2.636 | 2.636 | 0.5287 | 0.86515 | 1.1856 | 1.4259 | 1.4259 | 1.4259 | 1.81 | 2.3358 | 2.6802 | 2.8615 | 3.2241 | 3.5867 | 0.68589 | 1.3537 | 1.6245 | 1.6245 | 1.6245 | 1.6245 | 0.77314 | 0.89937 | 0.89937 | 0.89937 | 0.89937 | 0.89937
2020-11-03 07:00 | Summer | 1.8467 | 2.6429 | 3.8138 | 3.8138 | 3.8138 | 3.8138 | 0.66303 | 1.085 | 1.4868 | 1.7882 | 1.7882 | 1.7882 | 2.172 | 2.8029 | 3.2163 | 3.4338 | 3.8689 | 4.3041 | 0.98609 | 1.9462 | 2.3355 | 2.3355 | 2.3355 | 2.3355 | 1.0275 | 1.1952 | 1.1952 | 1.1952 | 1.1952 | 1.1952
2020-11-03 08:00 | Summer | 2.2482 | 3.2175 | 4.643 | 4.643 | 4.643 | 4.643 | 0.77734 | 1.272 | 1.7431 | 2.0965 | 2.0965 | 2.0965 | 2.4578 | 3.1717 | 3.6395 | 3.8856 | 4.378 | 4.8704 | 1.0212 | 2.0156 | 2.4187 | 2.4187 | 2.4187 | 2.4187 | 1.1432 | 1.3298 | 1.3298 | 1.3298 | 1.3298 | 1.3298
2020-11-03 09:00 | Summer | 2.3816 | 3.4084 | 4.9185 | 4.9185 | 4.9185 | 4.9185 | 0.87737 | 1.4357 | 1.9674 | 2.3662 | 2.3662 | 2.3662 | 2.553 | 3.2946 | 3.7805 | 4.0362 | 4.5477 | 5.0591 | 1.0212 | 2.0156 | 2.4187 | 2.4187 | 2.4187 | 2.4187 | 1.1813 | 1.3741 | 1.3741 | 1.3741 | 1.3741 | 1.3741
2020-11-03 10:00 | Summer | 2.4006 | 3.4357 | 4.9578 | 4.9578 | 4.9578 | 4.9578 | 0.84021 | 1.3749 | 1.8841 | 2.266 | 2.266 | 2.266 | 2.534 | 3.2701 | 3.7523 | 4.0061 | 4.5138 | 5.0214 | 0.98692 | 1.9479 | 2.3374 | 2.3374 | 2.3374 | 2.3374 | 1.3527 | 1.5736 | 1.5736 | 1.5736 | 1.5736 | 1.5736
2020-11-03 11:00 | Summer | 2.4197 | 3.4629 | 4.9972 | 4.9972 | 4.9972 | 4.9972 | 0.76305 | 1.2486 | 1.7111 | 2.0579 | 2.0579 | 2.0579 | 2.5911 | 3.3438 | 3.8369 | 4.0965 | 4.6156 | 5.1347 | 0.96787 | 1.9103 | 2.2923 | 2.2923 | 2.2923 | 2.2923 | 1.3908 | 1.6179 | 1.6179 | 1.6179 | 1.6179 | 1.6179
2020-11-03 12:00 | Summer | 2.4959 | 3.572 | 5.1545 | 5.1545 | 5.1545 | 5.1545 | 0.80878 | 1.3235 | 1.8136 | 2.1812 | 2.1812 | 2.1812 | 2.7245 | 3.5159 | 4.0344 | 4.3073 | 4.8531 | 5.3989 | 0.96787 | 1.9103 | 2.2923 | 2.2923 | 2.2923 | 2.2923 | 1.3718 | 1.5957 | 1.5957 | 1.5957 | 1.5957 | 1.5957
2020-11-03 13:00 | Summer | 2.4959 | 3.572 | 5.1545 | 5.1545 | 5.1545 | 5.1545 | 0.88022 | 1.4404 | 1.9738 | 2.3739 | 2.3739 | 2.3739 | 2.7436 | 3.5405 | 4.0627 | 4.3375 | 4.8871 | 5.4367 | 1.0479 | 2.0682 | 2.4818 | 2.4818 | 2.4818 | 2.4818 | 1.3908 | 1.6179 | 1.6179 | 1.6179 | 1.6179 | 1.6179
2020-11-03 14:00 | Summer | 2.4959 | 3.572 | 5.1545 | 5.1545 | 5.1545 | 5.1545 | 0.9088 | 1.4871 | 2.0379 | 2.451 | 2.451 | 2.451 | 2.7245 | 3.5159 | 4.0344 | 4.3073 | 4.8531 | 5.3989 | 1.0593 | 2.0908 | 2.5089 | 2.5089 | 2.5089 | 2.5089 | 1.3718 | 1.5957 | 1.5957 | 1.5957 | 1.5957 | 1.5957
2020-11-03 15:00 | Summer | 2.6102 | 3.7356 | 5.3906 | 5.3906 | 5.3906 | 5.3906 | 0.92595 | 1.5152 | 2.0764 | 2.4973 | 2.4973 | 2.4973 | 2.7626 | 3.5651 | 4.0909 | 4.3676 | 4.921 | 5.4745 | 1.1965 | 2.3615 | 2.8338 | 2.8338 | 2.8338 | 2.8338 | 1.3146 | 1.5293 | 1.5293 | 1.5293 | 1.5293 | 1.5293
2020-11-03 16:00 | Summer | 2.6102 | 3.7356 | 5.3906 | 5.3906 | 5.3906 | 5.3906 | 1.046 | 1.7116 | 2.3455 | 2.821 | 2.821 | 2.821 | 2.8007 | 3.6143 | 4.1473 | 4.4278 | 4.9889 | 5.55 | 1.1927 | 2.354 | 2.8248 | 2.8248 | 2.8248 | 2.8248 | 1.2956 | 1.5071 | 1.5071 | 1.5071 | 1.5071 | 1.5071
2020-11-03 17:00 | Summer | 2.553 | 3.6538 | 5.2726 | 5.2726 | 5.2726 | 5.2726 | 0.91738 | 1.5012 | 2.0571 | 2.4741 | 2.4741 | 2.4741 | 2.5721 | 3.3192 | 3.8087 | 4.0664 | 4.5816 | 5.0969 | 1.0936 | 2.1585 | 2.5901 | 2.5901 | 2.5901 | 2.5901 | 1.2575 | 1.4628 | 1.4628 | 1.4628 | 1.4628 | 1.4628
2020-11-03 18:00 | Summer | 1.7468 | 2.5 | 3.6075 | 3.6075 | 3.6075 | 3.6075 | 0.67189 | 1.0995 | 1.5067 | 1.8121 | 1.8121 | 1.8121 | 2.4197 | 3.1225 | 3.583 | 3.8254 | 4.3101 | 4.7949 | 0.89928 | 1.7749 | 2.1299 | 2.1299 | 2.1299 | 2.1299 | 0.92206 | 1.0726 | 1.0726 | 1.0726 | 1.0726 | 1.0726
2020-11-03 19:00 | Summer | 1.2194 | 1.7451 | 2.5183 | 2.5183 | 2.5183 | 2.5183 | 0.48869 | 0.79968 | 1.0959 | 1.318 | 1.318 | 1.318 | 2.1498 | 2.7742 | 3.1833 | 3.3987 | 3.8293 | 4.26 | 0.88023 | 1.7373 | 2.0847 | 2.0847 | 2.0847 | 2.0847 | 0.66093 | 0.76884 | 0.76884 | 0.76884 | 0.76884 | 0.76884
2020-11-03 20:00 | Summer | 1.1789 | 1.6873 | 2.4348 | 2.4348 | 2.4348 | 2.4348 | 0.46583 | 0.76227 | 1.0446 | 1.2563 | 1.2563 | 1.2563 | 2.0577 | 2.6554 | 3.047 | 3.2531 | 3.6653 | 4.0775 | 0.88023 | 1.7373 | 2.0847 | 2.0847 | 2.0847 | 2.0847 | 0.59063 | 0.68706 | 0.68706 | 0.68706 | 0.68706 | 0.68706
2020-11-03 21:00 | Summer | 1.0669 | 1.527 | 2.2035 | 2.2035 | 2.2035 | 2.2035 | 0.50584 | 0.82774 | 1.1343 | 1.3642 | 1.3642 | 1.3642 | 1.9624 | 2.5325 | 2.9059 | 3.1025 | 3.4956 | 3.8887 | 0.84212 | 1.6621 | 1.9945 | 1.9945 | 1.9945 | 1.9945 | 0.55252 | 0.64273 | 0.64273 | 0.64273 | 0.64273 | 0.64273
2020-11-03 22:00 | Summer | 1.0288 | 1.4724 | 2.1248 | 2.1248 | 2.1248 | 2.1248 | 0.38867 | 0.636 | 0.87156 | 1.0482 | 1.0482 | 1.0482 | 1.829 | 2.3603 | 2.7084 | 2.8916 | 3.2581 | 3.6245 | 0.78115 | 1.5417 | 1.8501 | 1.8501 | 1.8501 | 1.8501 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-11-03 23:00 | Summer | 1.0288 | 1.4724 | 2.1248 | 2.1248 | 2.1248 | 2.1248 | 0.39724 | 0.65003 | 0.89079 | 1.0713 | 1.0713 | 1.0713 | 1.6961 | 2.1888 | 2.5115 | 2.6814 | 3.0212 | 3.361 | 0.63635 | 1.256 | 1.5072 | 1.5072 | 1.5072 | 1.5072 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-11-04 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.39153 | 0.64068 | 0.87797 | 1.0559 | 1.0559 | 1.0559 | 1.6766 | 2.1636 | 2.4827 | 2.6507 | 2.9865 | 3.3224 | 0.64016 | 1.2635 | 1.5162 | 1.5162 | 1.5162 | 1.5162 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-11-04 01:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.35437 | 0.57988 | 0.79466 | 0.95574 | 0.95574 | 0.95574 | 1.5814 | 2.0407 | 2.3417 | 2.5001 | 2.8169 | 3.1337 | 0.55252 | 1.0905 | 1.3086 | 1.3086 | 1.3086 | 1.3086 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-11-04 02:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.38581 | 0.63133 | 0.86515 | 1.0405 | 1.0405 | 1.0405 | 1.5433 | 1.9915 | 2.2852 | 2.4398 | 2.749 | 3.0581 | 0.59825 | 1.1808 | 1.4169 | 1.4169 | 1.4169 | 1.4169 | 0.46829 | 0.54474 | 0.54474 | 0.54474 | 0.54474 | 0.54474
2020-11-04 03:00 | Summer | 0.95573 | 1.3678 | 1.9738 | 1.9738 | 1.9738 | 1.9738 | 0.28293 | 0.46297 | 0.63444 | 0.76304 | 0.76304 | 0.76304 | 1.5242 | 1.967 | 2.257 | 2.4097 | 2.715 | 3.0204 | 0.54109 | 1.0679 | 1.2815 | 1.2815 | 1.2815 | 1.2815 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-11-04 04:00 | Summer | 1.0479 | 1.4997 | 2.1641 | 2.1641 | 2.1641 | 2.1641 | 0.4001 | 0.65471 | 0.89719 | 1.0791 | 1.0791 | 1.0791 | 1.5814 | 2.0407 | 2.3417 | 2.5001 | 2.8169 | 3.1337 | 0.62111 | 1.2259 | 1.4711 | 1.4711 | 1.4711 | 1.4711 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-11-04 05:00 | Summer | 1.2003 | 1.7178 | 2.4789 | 2.4789 | 2.4789 | 2.4789 | 0.44297 | 0.72486 | 0.99332 | 1.1947 | 1.1947 | 1.1947 | 1.6385 | 2.1145 | 2.4263 | 2.5904 | 2.9187 | 3.2469 | 0.66684 | 1.3161 | 1.5794 | 1.5794 | 1.5794 | 1.5794 | 0.57158 | 0.6649 | 0.6649 | 0.6649 | 0.6649 | 0.6649
2020-11-04 06:00 | Summer | 1.3146 | 1.8814 | 2.715 | 2.715 | 2.715 | 2.715 | 0.53156 | 0.86983 | 1.192 | 1.4336 | 1.4336 | 1.4336 | 1.8105 | 2.3364 | 2.681 | 2.8623 | 3.225 | 3.5877 | 0.71256 | 1.4064 | 1.6877 | 1.6877 | 1.6877 | 1.6877 | 0.76383 | 0.88853 | 0.88853 | 0.88853 | 0.88853 | 0.88853
2020-11-04 07:00 | Summer | 1.8063 | 2.5852 | 3.7305 | 3.7305 | 3.7305 | 3.7305 | 0.70018 | 1.1457 | 1.5701 | 1.8884 | 1.8884 | 1.8884 | 2.0767 | 2.68 | 3.0752 | 3.2832 | 3.6992 | 4.1153 | 0.96025 | 1.8952 | 2.2743 | 2.2743 | 2.2743 | 2.2743 | 1.0098 | 1.1746 | 1.1746 | 1.1746 | 1.1746 | 1.1746
2020-11-04 08:00 | Summer | 2.3549 | 3.3702 | 4.8634 | 4.8634 | 4.8634 | 4.8634 | 0.78877 | 1.2907 | 1.7688 | 2.1273 | 2.1273 | 2.1273 | 2.4387 | 3.1471 | 3.6112 | 3.8555 | 4.3441 | 4.8326 | 0.94119 | 1.8576 | 2.2291 | 2.2291 | 2.2291 | 2.2291 | 1.1813 | 1.3741 | 1.3741 | 1.3741 | 1.3741 | 1.3741
2020-11-04 09:00 | Summer | 2.553 | 3.6538 | 5.2726 | 5.2726 | 5.2726 | 5.2726 | 1.0174 | 1.6648 | 2.2814 | 2.7439 | 2.7439 | 2.7439 | 2.5149 | 3.2455 | 3.7241 | 3.976 | 4.4798 | 4.9836 | 1.0326 | 2.0381 | 2.4457 | 2.4457 | 2.4457 | 2.4457 | 1.3337 | 1.5514 | 1.5514 | 1.5514 | 1.5514 | 1.5514
2020-11-04 10:00 | Summer | 2.6483 | 3.7901 | 5.4693 | 5.4693 | 5.4693 | 5.4693 | 0.98882 | 1.6181 | 2.2174 | 2.6668 | 2.6668 | 2.6668 | 2.6102 | 3.3684 | 3.8652 | 4.1266 | 4.6495 | 5.1724 | 1.0669 | 2.1058 | 2.527 | 2.527 | 2.527 | 2.527 | 1.4289 | 1.6622 | 1.6622 | 1.6622 | 1.6622 | 1.6622
2020-11-04 11:00 | Summer | 2.6864 | 3.8447 | 5.548 | 5.548 | 5.548 | 5.548 | 0.96596 | 1.5807 | 2.1661 | 2.6052 | 2.6052 | 2.6052 | 2.6674 | 3.4422 | 3.9498 | 4.217 | 4.7513 | 5.2857 | 1.0136 | 2.0005 | 2.4006 | 2.4006 | 2.4006 | 2.4006 | 1.4861 | 1.7287 | 1.7287 | 1.7287 | 1.7287 | 1.7287
2020-11-04 12:00 | Summer | 2.6293 | 3.7629 | 5.43 | 5.43 | 5.43 | 5.43 | 1.1632 | 1.9033 | 2.6083 | 3.137 | 3.137 | 3.137 | 2.8007 | 3.6143 | 4.1473 | 4.4278 | 4.9889 | 5.55 | 1.0555 | 2.0832 | 2.4999 | 2.4999 | 2.4999 | 2.4999 | 1.4861 | 1.7287 | 1.7287 | 1.7287 | 1.7287 | 1.7287
2020-11-04 13:00 | Summer | 2.6674 | 3.8174 | 5.5087 | 5.5087 | 5.5087 | 5.5087 | 1.1003 | 1.8005 | 2.4673 | 2.9674 | 2.9674 | 2.9674 | 2.896 | 3.7372 | 4.2884 | 4.5784 | 5.1586 | 5.7387 | 0.9069 | 1.7899 | 2.1479 | 2.1479 | 2.1479 | 2.1479 | 1.4651 | 1.7043 | 1.7043 | 1.7043 | 1.7043 | 1.7043
2020-11-04 14:00 | Summer | 2.8388 | 4.0628 | 5.8628 | 5.8628 | 5.8628 | 5.8628 | 1.0717 | 1.7537 | 2.4032 | 2.8903 | 2.8903 | 2.8903 | 2.896 | 3.7372 | 4.2884 | 4.5784 | 5.1586 | 5.7387 | 0.92214 | 1.82 | 2.184 | 2.184 | 2.184 | 2.184 | 1.4289 | 1.6622 | 1.6622 | 1.6622 | 1.6622 | 1.6622
2020-11-04 15:00 | Summer | 2.8579 | 4.0901 | 5.9022 | 5.9022 | 5.9022 | 5.9022 | 1.2489 | 2.0436 | 2.8005 | 3.3682 | 3.3682 | 3.3682 | 2.8888 | 3.7279 | 4.2777 | 4.567 | 5.1457 | 5.7244 | 0.93357 | 1.8426 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 1.4098 | 1.64 | 1.64 | 1.64 | 1.64 | 1.64
2020-11-04 16:00 | Summer | 2.7935 | 3.9979 | 5.7691 | 5.7691 | 5.7691 | 5.7691 | 1.1574 | 1.894 | 2.5955 | 3.1216 | 3.1216 | 3.1216 | 2.7436 | 3.5405 | 4.0627 | 4.3375 | 4.8871 | 5.4367 | 0.92214 | 1.82 | 2.184 | 2.184 | 2.184 | 2.184 | 1.4099 | 1.6401 | 1.6401 | 1.6401 | 1.6401 | 1.6401
2020-11-04 17:00 | Summer | 2.5744 | 3.6844 | 5.3167 | 5.3167 | 5.3167 | 5.3167 | 1.0946 | 1.7911 | 2.4545 | 2.952 | 2.952 | 2.952 | 2.6102 | 3.3684 | 3.8652 | 4.1266 | 4.6495 | 5.1724 | 0.91833 | 1.8125 | 2.175 | 2.175 | 2.175 | 2.175 | 1.2676 | 1.4746 | 1.4746 | 1.4746 | 1.4746 | 1.4746
2020-11-04 18:00 | Summer | 1.678 | 2.4015 | 3.4654 | 3.4654 | 3.4654 | 3.4654 | 0.82307 | 1.3468 | 1.8457 | 2.2198 | 2.2198 | 2.2198 | 2.4197 | 3.1225 | 3.583 | 3.8254 | 4.3101 | 4.7949 | 0.86879 | 1.7147 | 2.0577 | 2.0577 | 2.0577 | 2.0577 | 0.95788 | 1.1143 | 1.1143 | 1.1143 | 1.1143 | 1.1143
2020-11-04 19:00 | Summer | 1.2384 | 1.7724 | 2.5576 | 2.5576 | 2.5576 | 2.5576 | 0.58586 | 0.95868 | 1.3138 | 1.5801 | 1.5801 | 1.5801 | 2.1929 | 2.8299 | 3.2472 | 3.4669 | 3.9062 | 4.3455 | 0.86879 | 1.7147 | 2.0577 | 2.0577 | 2.0577 | 2.0577 | 0.70494 | 0.82004 | 0.82004 | 0.82004 | 0.82004 | 0.82004
2020-11-04 20:00 | Summer | 1.1432 | 1.636 | 2.3609 | 2.3609 | 2.3609 | 2.3609 | 0.60015 | 0.98207 | 1.3458 | 1.6186 | 1.6186 | 1.6186 | 2.0958 | 2.7046 | 3.1034 | 3.3133 | 3.7332 | 4.153 | 0.93357 | 1.8426 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 0.60968 | 0.70922 | 0.70922 | 0.70922 | 0.70922 | 0.70922
2020-11-04 21:00 | Summer | 1.1241 | 1.6088 | 2.3215 | 2.3215 | 2.3215 | 2.3215 | 0.56586 | 0.92595 | 1.2689 | 1.5261 | 1.5261 | 1.5261 | 2.0005 | 2.5816 | 2.9624 | 3.1627 | 3.5635 | 3.9643 | 0.83404 | 1.6461 | 1.9754 | 1.9754 | 1.9754 | 1.9754 | 0.57158 | 0.6649 | 0.6649 | 0.6649 | 0.6649 | 0.6649
2020-11-04 22:00 | Summer | 1.0669 | 1.527 | 2.2035 | 2.2035 | 2.2035 | 2.2035 | 0.4602 | 0.75306 | 1.032 | 1.2411 | 1.2411 | 1.2411 | 1.9434 | 2.5079 | 2.8777 | 3.0724 | 3.4617 | 3.851 | 0.83831 | 1.6546 | 1.9855 | 1.9855 | 1.9855 | 1.9855 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-11-04 23:00 | Summer | 1.0288 | 1.4724 | 2.1248 | 2.1248 | 2.1248 | 2.1248 | 0.38295 | 0.62665 | 0.85874 | 1.0328 | 1.0328 | 1.0328 | 1.6957 | 2.1882 | 2.5109 | 2.6808 | 3.0205 | 3.3602 | 0.72781 | 1.4365 | 1.7238 | 1.7238 | 1.7238 | 1.7238 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-11-05 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.4544 | 0.74356 | 1.019 | 1.2255 | 1.2255 | 1.2255 | 1.7147 | 2.2128 | 2.5392 | 2.7109 | 3.0544 | 3.3979 | 0.68208 | 1.3462 | 1.6155 | 1.6155 | 1.6155 | 1.6155 | 0.48995 | 0.56994 | 0.56994 | 0.56994 | 0.56994 | 0.56994
2020-11-05 01:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.44297 | 0.72486 | 0.99332 | 1.1947 | 1.1947 | 1.1947 | 1.6195 | 2.0899 | 2.3981 | 2.5603 | 2.8847 | 3.2092 | 0.71256 | 1.4064 | 1.6877 | 1.6877 | 1.6877 | 1.6877 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-11-05 02:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.41725 | 0.68277 | 0.93565 | 1.1253 | 1.1253 | 1.1253 | 1.5814 | 2.0407 | 2.3417 | 2.5001 | 2.8169 | 3.1337 | 0.64779 | 1.2785 | 1.5342 | 1.5342 | 1.5342 | 1.5342 | 0.43821 | 0.50975 | 0.50975 | 0.50975 | 0.50975 | 0.50975
2020-11-05 03:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.44011 | 0.72018 | 0.98691 | 1.187 | 1.187 | 1.187 | 1.5814 | 2.0407 | 2.3417 | 2.5001 | 2.8169 | 3.1337 | 0.57539 | 1.1356 | 1.3628 | 1.3628 | 1.3628 | 1.3628 | 0.45436 | 0.52854 | 0.52854 | 0.52854 | 0.52854 | 0.52854
2020-11-05 04:00 | Summer | 1.0714 | 1.5333 | 2.2127 | 2.2127 | 2.2127 | 2.2127 | 0.50013 | 0.81839 | 1.1215 | 1.3488 | 1.3488 | 1.3488 | 1.5698 | 2.0258 | 2.3246 | 2.4818 | 2.7963 | 3.1108 | 0.65541 | 1.2936 | 1.5523 | 1.5523 | 1.5523 | 1.5523 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-11-05 05:00 | Summer | 1.1797 | 1.6883 | 2.4363 | 2.4363 | 2.4363 | 2.4363 | 0.5287 | 0.86515 | 1.1856 | 1.4259 | 1.4259 | 1.4259 | 1.6766 | 2.1636 | 2.4827 | 2.6507 | 2.9865 | 3.3224 | 0.74977 | 1.4798 | 1.7758 | 1.7758 | 1.7758 | 1.7758 | 0.6081 | 0.70738 | 0.70738 | 0.70738 | 0.70738 | 0.70738
2020-11-05 06:00 | Summer | 1.3565 | 1.9414 | 2.8015 | 2.8015 | 2.8015 | 2.8015 | 0.54299 | 0.88854 | 1.2176 | 1.4644 | 1.4644 | 1.4644 | 1.829 | 2.3603 | 2.7084 | 2.8916 | 3.2581 | 3.6245 | 0.83069 | 1.6395 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.795 | 0.9248 | 0.9248 | 0.9248 | 0.9248 | 0.9248
2020-11-05 07:00 | Summer | 1.7719 | 2.5359 | 3.6593 | 3.6593 | 3.6593 | 3.6593 | 0.73733 | 1.2065 | 1.6534 | 1.9886 | 1.9886 | 1.9886 | 2.2023 | 2.842 | 3.2611 | 3.4817 | 3.9228 | 4.364 | 1.0403 | 2.0532 | 2.4638 | 2.4638 | 2.4638 | 2.4638 | 1.0669 | 1.2411 | 1.2411 | 1.2411 | 1.2411 | 1.2411
2020-11-05 08:00 | Summer | 2.191 | 3.1357 | 4.525 | 4.525 | 4.525 | 4.525 | 0.82021 | 1.3422 | 1.8393 | 2.2121 | 2.2121 | 2.2121 | 2.3625 | 3.0488 | 3.4984 | 3.735 | 4.2083 | 4.6816 | 1.0479 | 2.0682 | 2.4818 | 2.4818 | 2.4818 | 2.4818 | 1.2575 | 1.4628 | 1.4628 | 1.4628 | 1.4628 | 1.4628
2020-11-05 09:00 | Summer | 2.259 | 3.2331 | 4.6654 | 4.6654 | 4.6654 | 4.6654 | 0.92595 | 1.5152 | 2.0764 | 2.4973 | 2.4973 | 2.4973 | 2.4768 | 3.1963 | 3.6677 | 3.9158 | 4.4119 | 4.9081 | 1.0593 | 2.0908 | 2.5089 | 2.5089 | 2.5089 | 2.5089 | 1.3146 | 1.5293 | 1.5293 | 1.5293 | 1.5293 | 1.5293
2020-11-05 10:00 | Summer | 2.2673 | 3.2448 | 4.6824 | 4.6824 | 4.6824 | 4.6824 | 0.92023 | 1.5058 | 2.0636 | 2.4818 | 2.4818 | 2.4818 | 2.553 | 3.2946 | 3.7805 | 4.0362 | 4.5477 | 5.0591 | 0.96787 | 1.9103 | 2.2923 | 2.2923 | 2.2923 | 2.2923 | 1.3718 | 1.5957 | 1.5957 | 1.5957 | 1.5957 | 1.5957
2020-11-05 11:00 | Summer | 2.2101 | 3.163 | 4.5643 | 4.5643 | 4.5643 | 4.5643 | 1.0031 | 1.6415 | 2.2494 | 2.7054 | 2.7054 | 2.7054 | 2.4959 | 3.2209 | 3.6959 | 3.9459 | 4.4459 | 4.9459 | 0.93357 | 1.8426 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 1.3718 | 1.5957 | 1.5957 | 1.5957 | 1.5957 | 1.5957
2020-11-05 12:00 | Summer | 2.2101 | 3.163 | 4.5643 | 4.5643 | 4.5643 | 4.5643 | 0.92595 | 1.5152 | 2.0764 | 2.4973 | 2.4973 | 2.4973 | 2.534 | 3.2701 | 3.7523 | 4.0061 | 4.5138 | 5.0214 | 1.0631 | 2.0983 | 2.5179 | 2.5179 | 2.5179 | 2.5179 | 1.3908 | 1.6179 | 1.6179 | 1.6179 | 1.6179 | 1.6179
2020-11-05 13:00 | Summer | 2.2482 | 3.2175 | 4.643 | 4.643 | 4.643 | 4.643 | 0.91452 | 1.4965 | 2.0507 | 2.4664 | 2.4664 | 2.4664 | 2.5596 | 3.3032 | 3.7903 | 4.0467 | 4.5595 | 5.0722 | 0.96025 | 1.8952 | 2.2743 | 2.2743 | 2.2743 | 2.2743 | 1.3527 | 1.5736 | 1.5736 | 1.5736 | 1.5736 | 1.5736
2020-11-05 14:00 | Summer | 2.2101 | 3.163 | 4.5643 | 4.5643 | 4.5643 | 4.5643 | 0.85381 | 1.3971 | 1.9146 | 2.3027 | 2.3027 | 2.3027 | 2.5911 | 3.3438 | 3.8369 | 4.0965 | 4.6156 | 5.1347 | 0.91071 | 1.7975 | 2.1569 | 2.1569 | 2.1569 | 2.1569 | 1.3337 | 1.5514 | 1.5514 | 1.5514 | 1.5514 | 1.5514
2020-11-05 15:00 | Summer | 2.191 | 3.1357 | 4.525 | 4.525 | 4.525 | 4.525 | 0.8545 | 1.3983 | 1.9162 | 2.3046 | 2.3046 | 2.3046 | 2.4768 | 3.1963 | 3.6677 | 3.9158 | 4.4119 | 4.9081 | 0.91833 | 1.8125 | 2.175 | 2.175 | 2.175 | 2.175 | 1.2956 | 1.5071 | 1.5071 | 1.5071 | 1.5071 | 1.5071
2020-11-05 16:00 | Summer | 2.1148 | 3.0267 | 4.3676 | 4.3676 | 4.3676 | 4.3676 | 0.86308 | 1.4123 | 1.9354 | 2.3277 | 2.3277 | 2.3277 | 2.4768 | 3.1963 | 3.6677 | 3.9158 | 4.4119 | 4.9081 | 0.95263 | 1.8802 | 2.2562 | 2.2562 | 2.2562 | 2.2562 | 1.1656 | 1.3559 | 1.3559 | 1.3559 | 1.3559 | 1.3559
2020-11-05 17:00 | Summer | 2.0386 | 2.9176 | 4.2102 | 4.2102 | 4.2102 | 4.2102 | 0.86594 | 1.417 | 1.9418 | 2.3354 | 2.3354 | 2.3354 | 2.4006 | 3.098 | 3.5548 | 3.7953 | 4.2762 | 4.7571 | 0.87261 | 1.7222 | 2.0667 | 2.0667 | 2.0667 | 2.0667 | 1.1813 | 1.3741 | 1.3741 | 1.3741 | 1.3741 | 1.3741
2020-11-05 18:00 | Summer | 1.7596 | 2.5182 | 3.6339 | 3.6339 | 3.6339 | 3.6339 | 0.72304 | 1.1832 | 1.6214 | 1.95 | 1.95 | 1.95 | 2.2482 | 2.9013 | 3.3291 | 3.5543 | 4.0047 | 4.4551 | 0.82125 | 1.6209 | 1.9451 | 1.9451 | 1.9451 | 1.9451 | 0.88761 | 1.0325 | 1.0325 | 1.0325 | 1.0325 | 1.0325
2020-11-05 19:00 | Summer | 1.2194 | 1.7451 | 2.5183 | 2.5183 | 2.5183 | 2.5183 | 0.61158 | 1.0008 | 1.3714 | 1.6494 | 1.6494 | 1.6494 | 2.1496 | 2.7741 | 3.1832 | 3.3985 | 3.8291 | 4.2597 | 0.80021 | 1.5794 | 1.8952 | 1.8952 | 1.8952 | 1.8952 | 0.62013 | 0.72138 | 0.72138 | 0.72138 | 0.72138 | 0.72138
2020-11-05 20:00 | Summer | 1.1432 | 1.636 | 2.3609 | 2.3609 | 2.3609 | 2.3609 | 0.6373 | 1.0429 | 1.4291 | 1.7188 | 1.7188 | 1.7188 | 2.1148 | 2.7291 | 3.1316 | 3.3435 | 3.7671 | 4.1908 | 1.0098 | 1.993 | 2.3916 | 2.3916 | 2.3916 | 2.3916 | 0.60968 | 0.70922 | 0.70922 | 0.70922 | 0.70922 | 0.70922
2020-11-05 21:00 | Summer | 1.0669 | 1.527 | 2.2035 | 2.2035 | 2.2035 | 2.2035 | 0.62016 | 1.0148 | 1.3907 | 1.6725 | 1.6725 | 1.6725 | 1.9744 | 2.5479 | 2.9237 | 3.1214 | 3.517 | 3.9125 | 0.78024 | 1.5399 | 1.8479 | 1.8479 | 1.8479 | 1.8479 | 0.51643 | 0.60074 | 0.60074 | 0.60074 | 0.60074 | 0.60074
2020-11-05 22:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.59444 | 0.97271 | 1.333 | 1.6032 | 1.6032 | 1.6032 | 1.8299 | 2.3615 | 2.7098 | 2.8931 | 3.2596 | 3.6262 | 0.73543 | 1.4515 | 1.7418 | 1.7418 | 1.7418 | 1.7418 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-11-05 23:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.54014 | 0.88386 | 1.2112 | 1.4567 | 1.4567 | 1.4567 | 1.7528 | 2.262 | 2.5956 | 2.7712 | 3.1223 | 3.4734 | 0.66684 | 1.3161 | 1.5794 | 1.5794 | 1.5794 | 1.5794 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-11-06 | Summer | 0.93457 | 1.3375 | 1.9301 | 1.9301 | 1.9301 | 1.9301 | 0.47155 | 0.77162 | 1.0574 | 1.2717 | 1.2717 | 1.2717 | 1.6004 | 2.0653 | 2.3699 | 2.5302 | 2.8508 | 3.1714 | 0.63669 | 1.2566 | 1.508 | 1.508 | 1.508 | 1.508 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-11-06 01:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.36573 | 0.59847 | 0.82013 | 0.98637 | 0.98637 | 0.98637 | 1.6004 | 2.0653 | 2.3699 | 2.5302 | 2.8508 | 3.1714 | 0.62873 | 1.2409 | 1.4891 | 1.4891 | 1.4891 | 1.4891 | 0.41598 | 0.48389 | 0.48389 | 0.48389 | 0.48389 | 0.48389
2020-11-06 02:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.48298 | 0.79033 | 1.083 | 1.3026 | 1.3026 | 1.3026 | 1.5623 | 2.0161 | 2.3135 | 2.4699 | 2.7829 | 3.0959 | 0.52204 | 1.0303 | 1.2364 | 1.2364 | 1.2364 | 1.2364 | 0.41733 | 0.48547 | 0.48547 | 0.48547 | 0.48547 | 0.48547
2020-11-06 03:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.46869 | 0.76695 | 1.051 | 1.264 | 1.264 | 1.264 | 1.5052 | 1.9424 | 2.2288 | 2.3796 | 2.6811 | 2.9826 | 0.77734 | 1.5342 | 1.8411 | 1.8411 | 1.8411 | 1.8411 | 0.43821 | 0.50975 | 0.50975 | 0.50975 | 0.50975 | 0.50975
2020-11-06 04:00 | Summer | 1.086 | 1.5542 | 2.2428 | 2.2428 | 2.2428 | 2.2428 | 0.45154 | 0.73889 | 1.0125 | 1.2178 | 1.2178 | 1.2178 | 1.5432 | 1.9915 | 2.2852 | 2.4398 | 2.7489 | 3.0581 | 0.52585 | 1.0379 | 1.2454 | 1.2454 | 1.2454 | 1.2454 | 0.52615 | 0.61206 | 0.61206 | 0.61206 | 0.61206 | 0.61206
2020-11-06 05:00 | Summer | 1.1813 | 1.6906 | 2.4396 | 2.4396 | 2.4396 | 2.4396 | 0.57157 | 0.9353 | 1.2817 | 1.5415 | 1.5415 | 1.5415 | 1.724 | 2.2248 | 2.5529 | 2.7256 | 3.071 | 3.4164 | 0.6897 | 1.3613 | 1.6335 | 1.6335 | 1.6335 | 1.6335 | 0.61673 | 0.71742 | 0.71742 | 0.71742 | 0.71742 | 0.71742
2020-11-06 06:00 | Summer | 1.3126 | 1.8786 | 2.7108 | 2.7108 | 2.7108 | 2.7108 | 0.66303 | 1.085 | 1.4868 | 1.7882 | 1.7882 | 1.7882 | 1.8672 | 2.4095 | 2.7649 | 2.9519 | 3.3259 | 3.7 | 0.75067 | 1.4816 | 1.7779 | 1.7779 | 1.7779 | 1.7779 | 0.88255 | 1.0266 | 1.0266 | 1.0266 | 1.0266 | 1.0266
2020-11-06 07:00 | Summer | 1.8285 | 2.6169 | 3.7763 | 3.7763 | 3.7763 | 3.7763 | 0.89737 | 1.4684 | 2.0123 | 2.4202 | 2.4202 | 2.4202 | 2.1339 | 2.7537 | 3.1598 | 3.3736 | 3.8011 | 4.2285 | 0.9069 | 1.7899 | 2.1479 | 2.1479 | 2.1479 | 2.1479 | 1.105 | 1.2855 | 1.2855 | 1.2855 | 1.2855 | 1.2855
2020-11-06 08:00 | Summer | 2.1148 | 3.0267 | 4.3676 | 4.3676 | 4.3676 | 4.3676 | 0.92309 | 1.5105 | 2.07 | 2.4896 | 2.4896 | 2.4896 | 2.3244 | 2.9996 | 3.442 | 3.6748 | 4.1404 | 4.6061 | 1.0517 | 2.0757 | 2.4909 | 2.4909 | 2.4909 | 2.4909 | 1.2194 | 1.4184 | 1.4184 | 1.4184 | 1.4184 | 1.4184
2020-11-06 09:00 | Summer | 2.3244 | 3.3266 | 4.8004 | 4.8004 | 4.8004 | 4.8004 | 0.8888 | 1.4544 | 1.9931 | 2.3971 | 2.3971 | 2.3971 | 2.4197 | 3.1225 | 3.583 | 3.8254 | 4.3101 | 4.7949 | 0.95644 | 1.8877 | 2.2652 | 2.2652 | 2.2652 | 2.2652 | 1.3146 | 1.5293 | 1.5293 | 1.5293 | 1.5293 | 1.5293
2020-11-06 10:00 | Summer | 2.2482 | 3.2175 | 4.643 | 4.643 | 4.643 | 4.643 | 0.80592 | 1.3188 | 1.8072 | 2.1735 | 2.1735 | 2.1735 | 2.3625 | 3.0488 | 3.4984 | 3.735 | 4.2083 | 4.6816 | 0.93932 | 1.8539 | 2.2247 | 2.2247 | 2.2247 | 2.2247 | 1.3337 | 1.5514 | 1.5514 | 1.5514 | 1.5514 | 1.5514
2020-11-06 11:00 | Summer | 2.2097 | 3.1624 | 4.5635 | 4.5635 | 4.5635 | 4.5635 | 0.84593 | 1.3842 | 1.8969 | 2.2814 | 2.2814 | 2.2814 | 2.4768 | 3.1963 | 3.6677 | 3.9158 | 4.4119 | 4.9081 | 0.97549 | 1.9253 | 2.3104 | 2.3104 | 2.3104 | 2.3104 | 1.3908 | 1.6179 | 1.6179 | 1.6179 | 1.6179 | 1.6179
2020-11-06 12:00 | Summer | 2.3054 | 3.2993 | 4.7611 | 4.7611 | 4.7611 | 4.7611 | 0.85165 | 1.3936 | 1.9098 | 2.2969 | 2.2969 | 2.2969 | 2.5149 | 3.2455 | 3.7241 | 3.976 | 4.4798 | 4.9836 | 1.0669 | 2.1058 | 2.527 | 2.527 | 2.527 | 2.527 | 1.2956 | 1.5071 | 1.5071 | 1.5071 | 1.5071 | 1.5071
2020-11-06 13:00 | Summer | 2.3054 | 3.2993 | 4.7611 | 4.7611 | 4.7611 | 4.7611 | 0.89166 | 1.4591 | 1.9995 | 2.4048 | 2.4048 | 2.4048 | 2.4967 | 3.2219 | 3.6971 | 3.9472 | 4.4474 | 4.9475 | 1.1393 | 2.2487 | 2.6984 | 2.6984 | 2.6984 | 2.6984 | 1.3718 | 1.5957 | 1.5957 | 1.5957 | 1.5957 | 1.5957
2020-11-06 14:00 | Summer | 2.2863 | 3.2721 | 4.7217 | 4.7217 | 4.7217 | 4.7217 | 0.83736 | 1.3702 | 1.8777 | 2.2583 | 2.2583 | 2.2583 | 2.534 | 3.2701 | 3.7523 | 4.0061 | 4.5138 | 5.0214 | 0.94882 | 1.8727 | 2.2472 | 2.2472 | 2.2472 | 2.2472 | 1.3527 | 1.5736 | 1.5736 | 1.5736 | 1.5736 | 1.5736
2020-11-06 15:00 | Summer | 2.2863 | 3.2721 | 4.7217 | 4.7217 | 4.7217 | 4.7217 | 1.0517 | 1.721 | 2.3584 | 2.8364 | 2.8364 | 2.8364 | 2.4947 | 3.2194 | 3.6942 | 3.9441 | 4.4438 | 4.9436 | 0.98311 | 1.9403 | 2.3284 | 2.3284 | 2.3284 | 2.3284 | 1.2956 | 1.5071 | 1.5071 | 1.5071 | 1.5071 | 1.5071
2020-11-06 16:00 | Summer | 2.282 | 3.266 | 4.7129 | 4.7129 | 4.7129 | 4.7129 | 0.90595 | 1.4825 | 2.0315 | 2.4433 | 2.4433 | 2.4433 | 2.553 | 3.2946 | 3.7805 | 4.0362 | 4.5477 | 5.0591 | 0.97168 | 1.9178 | 2.3013 | 2.3013 | 2.3013 | 2.3013 | 1.2194 | 1.4184 | 1.4184 | 1.4184 | 1.4184 | 1.4184
2020-11-06 17:00 | Summer | 2.191 | 3.1357 | 4.525 | 4.525 | 4.525 | 4.525 | 0.87165 | 1.4263 | 1.9546 | 2.3508 | 2.3508 | 2.3508 | 2.4768 | 3.1963 | 3.6677 | 3.9158 | 4.4119 | 4.9081 | 0.94119 | 1.8576 | 2.2291 | 2.2291 | 2.2291 | 2.2291 | 1.1241 | 1.3076 | 1.3076 | 1.3076 | 1.3076 | 1.3076
2020-11-06 18:00 | Summer | 1.513 | 2.1654 | 3.1247 | 3.1247 | 3.1247 | 3.1247 | 0.73823 | 1.208 | 1.6554 | 1.991 | 1.991 | 1.991 | 2.2863 | 2.9504 | 3.3855 | 3.6146 | 4.0726 | 4.5306 | 0.84593 | 1.6696 | 2.0035 | 2.0035 | 2.0035 | 2.0035 | 0.87837 | 1.0218 | 1.0218 | 1.0218 | 1.0218 | 1.0218
2020-11-06 19:00 | Summer | 1.1633 | 1.6648 | 2.4024 | 2.4024 | 2.4024 | 2.4024 | 0.60015 | 0.98207 | 1.3458 | 1.6186 | 1.6186 | 1.6186 | 2.1096 | 2.7224 | 3.1239 | 3.3352 | 3.7578 | 4.1805 | 0.88502 | 1.7468 | 2.0961 | 2.0961 | 2.0961 | 2.0961 | 0.74904 | 0.87133 | 0.87133 | 0.87133 | 0.87133 | 0.87133
2020-11-06 20:00 | Summer | 1.0481 | 1.5 | 2.1646 | 2.1646 | 2.1646 | 2.1646 | 0.53728 | 0.87918 | 1.2048 | 1.449 | 1.449 | 1.449 | 2.0767 | 2.68 | 3.0752 | 3.2832 | 3.6992 | 4.1153 | 0.88785 | 1.7523 | 2.1028 | 2.1028 | 2.1028 | 2.1028 | 0.64779 | 0.75355 | 0.75355 | 0.75355 | 0.75355 | 0.75355
2020-11-06 21:00 | Summer | 1.0288 | 1.4724 | 2.1248 | 2.1248 | 2.1248 | 2.1248 | 0.55157 | 0.90257 | 1.2368 | 1.4876 | 1.4876 | 1.4876 | 1.979 | 2.5539 | 2.9305 | 3.1287 | 3.5252 | 3.9216 | 0.82688 | 1.632 | 1.9584 | 1.9584 | 1.9584 | 1.9584 | 0.60968 | 0.70922 | 0.70922 | 0.70922 | 0.70922 | 0.70922
2020-11-06 22:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.563 | 0.92127 | 1.2625 | 1.5184 | 1.5184 | 1.5184 | 1.81 | 2.3358 | 2.6802 | 2.8615 | 3.2241 | 3.5867 | 0.81164 | 1.6019 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 0.51324 | 0.59703 | 0.59703 | 0.59703 | 0.59703 | 0.59703
2020-11-06 23:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.46869 | 0.76695 | 1.051 | 1.264 | 1.264 | 1.264 | 1.7719 | 2.2866 | 2.6238 | 2.8013 | 3.1562 | 3.5112 | 0.70494 | 1.3913 | 1.6696 | 1.6696 | 1.6696 | 1.6696 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-11-07 | Summer | 0.91452 | 1.3088 | 1.8887 | 1.8887 | 1.8887 | 1.8887 | 0.36009 | 0.58924 | 0.80747 | 0.97115 | 0.97115 | 0.97115 | 1.6385 | 2.1145 | 2.4263 | 2.5904 | 2.9187 | 3.2469 | 0.6509 | 1.2847 | 1.5416 | 1.5416 | 1.5416 | 1.5416 | 0.45644 | 0.53096 | 0.53096 | 0.53096 | 0.53096 | 0.53096
2020-11-07 01:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.42011 | 0.68744 | 0.94205 | 1.133 | 1.133 | 1.133 | 1.5623 | 2.0161 | 2.3135 | 2.4699 | 2.7829 | 3.0959 | 0.66684 | 1.3161 | 1.5794 | 1.5794 | 1.5794 | 1.5794 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-11-07 02:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.40867 | 0.66874 | 0.91642 | 1.1022 | 1.1022 | 1.1022 | 1.5433 | 1.9915 | 2.2852 | 2.4398 | 2.749 | 3.0581 | 0.56395 | 1.1131 | 1.3357 | 1.3357 | 1.3357 | 1.3357 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-11-07 03:00 | Summer | 0.93965 | 1.3448 | 1.9406 | 1.9406 | 1.9406 | 1.9406 | 0.30337 | 0.49643 | 0.68029 | 0.81819 | 0.81819 | 0.81819 | 1.5623 | 2.0161 | 2.3135 | 2.4699 | 2.7829 | 3.0959 | 0.5792 | 1.1431 | 1.3718 | 1.3718 | 1.3718 | 1.3718 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-11-07 04:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.41153 | 0.67342 | 0.92283 | 1.1099 | 1.1099 | 1.1099 | 1.5814 | 2.0407 | 2.3417 | 2.5001 | 2.8169 | 3.1337 | 0.5792 | 1.1431 | 1.3718 | 1.3718 | 1.3718 | 1.3718 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-11-07 05:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.39724 | 0.65003 | 0.89079 | 1.0713 | 1.0713 | 1.0713 | 1.6195 | 2.0899 | 2.3981 | 2.5603 | 2.8847 | 3.2092 | 0.54109 | 1.0679 | 1.2815 | 1.2815 | 1.2815 | 1.2815 | 0.44681 | 0.51976 | 0.51976 | 0.51976 | 0.51976 | 0.51976
2020-11-07 06:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.47155 | 0.77162 | 1.0574 | 1.2717 | 1.2717 | 1.2717 | 1.6766 | 2.1636 | 2.4827 | 2.6507 | 2.9865 | 3.3224 | 0.54109 | 1.0679 | 1.2815 | 1.2815 | 1.2815 | 1.2815 | 0.45543 | 0.52979 | 0.52979 | 0.52979 | 0.52979 | 0.52979
2020-11-07 07:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.53156 | 0.86983 | 1.192 | 1.4336 | 1.4336 | 1.4336 | 1.829 | 2.3603 | 2.7084 | 2.8916 | 3.2581 | 3.6245 | 0.58348 | 1.1516 | 1.3819 | 1.3819 | 1.3819 | 1.3819 | 0.48764 | 0.56726 | 0.56726 | 0.56726 | 0.56726 | 0.56726
2020-11-07 08:00 | Summer | 1.0288 | 1.4724 | 2.1248 | 2.1248 | 2.1248 | 2.1248 | 0.56586 | 0.92595 | 1.2689 | 1.5261 | 1.5261 | 1.5261 | 1.9243 | 2.4833 | 2.8495 | 3.0422 | 3.4277 | 3.8132 | 0.75829 | 1.4966 | 1.796 | 1.796 | 1.796 | 1.796 | 0.53347 | 0.62057 | 0.62057 | 0.62057 | 0.62057 | 0.62057
2020-11-07 09:00 | Summer | 1.086 | 1.5542 | 2.2428 | 2.2428 | 2.2428 | 2.2428 | 0.54299 | 0.88854 | 1.2176 | 1.4644 | 1.4644 | 1.4644 | 2.1148 | 2.7291 | 3.1316 | 3.3435 | 3.7671 | 4.1908 | 0.80402 | 1.5869 | 1.9042 | 1.9042 | 1.9042 | 1.9042 | 0.57158 | 0.6649 | 0.6649 | 0.6649 | 0.6649 | 0.6649
2020-11-07 10:00 | Summer | 0.94447 | 1.3517 | 1.9505 | 1.9505 | 1.9505 | 1.9505 | 0.62016 | 1.0148 | 1.3907 | 1.6725 | 1.6725 | 1.6725 | 2.0767 | 2.68 | 3.0752 | 3.2832 | 3.6992 | 4.1153 | 0.78496 | 1.5493 | 1.8591 | 1.8591 | 1.8591 | 1.8591 | 0.64779 | 0.75355 | 0.75355 | 0.75355 | 0.75355 | 0.75355
2020-11-07 11:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.6173 | 1.0101 | 1.3842 | 1.6648 | 1.6648 | 1.6648 | 2.1529 | 2.7783 | 3.1881 | 3.4037 | 3.835 | 4.2663 | 0.7621 | 1.5041 | 1.805 | 1.805 | 1.805 | 1.805 | 0.66684 | 0.77571 | 0.77571 | 0.77571 | 0.77571 | 0.77571
2020-11-07 12:00 | Summer | 0.91452 | 1.3088 | 1.8887 | 1.8887 | 1.8887 | 1.8887 | 0.47441 | 0.7763 | 1.0638 | 1.2795 | 1.2795 | 1.2795 | 2.191 | 2.8275 | 3.2445 | 3.4639 | 3.9029 | 4.3418 | 0.74911 | 1.4785 | 1.7742 | 1.7742 | 1.7742 | 1.7742 | 0.64779 | 0.75355 | 0.75355 | 0.75355 | 0.75355 | 0.75355
2020-11-07 13:00 | Summer | 0.91432 | 1.3085 | 1.8883 | 1.8883 | 1.8883 | 1.8883 | 0.62587 | 1.0242 | 1.4035 | 1.688 | 1.688 | 1.688 | 2.3054 | 2.975 | 3.4138 | 3.6447 | 4.1065 | 4.5683 | 0.81926 | 1.617 | 1.9403 | 1.9403 | 1.9403 | 1.9403 | 0.64779 | 0.75355 | 0.75355 | 0.75355 | 0.75355 | 0.75355
2020-11-07 14:00 | Summer | 0.91452 | 1.3088 | 1.8887 | 1.8887 | 1.8887 | 1.8887 | 0.67731 | 1.1083 | 1.5188 | 1.8267 | 1.8267 | 1.8267 | 2.2482 | 2.9013 | 3.3291 | 3.5543 | 4.0047 | 4.4551 | 0.73543 | 1.4515 | 1.7418 | 1.7418 | 1.7418 | 1.7418 | 0.57179 | 0.66514 | 0.66514 | 0.66514 | 0.66514 | 0.66514
2020-11-07 15:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.64302 | 1.0522 | 1.4419 | 1.7342 | 1.7342 | 1.7342 | 2.2291 | 2.8767 | 3.3009 | 3.5242 | 3.9708 | 4.4173 | 0.74305 | 1.4665 | 1.7599 | 1.7599 | 1.7599 | 1.7599 | 0.55252 | 0.64273 | 0.64273 | 0.64273 | 0.64273 | 0.64273
2020-11-07 16:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.65159 | 1.0662 | 1.4611 | 1.7573 | 1.7573 | 1.7573 | 2.2291 | 2.8767 | 3.3009 | 3.5242 | 3.9708 | 4.4173 | 0.76591 | 1.5117 | 1.814 | 1.814 | 1.814 | 1.814 | 0.55252 | 0.64273 | 0.64273 | 0.64273 | 0.64273 | 0.64273
2020-11-07 17:00 | Summer | 1.0288 | 1.4724 | 2.1248 | 2.1248 | 2.1248 | 2.1248 | 0.54299 | 0.88854 | 1.2176 | 1.4644 | 1.4644 | 1.4644 | 2.0577 | 2.6554 | 3.047 | 3.2531 | 3.6653 | 4.0775 | 0.83069 | 1.6395 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.57158 | 0.6649 | 0.6649 | 0.6649 | 0.6649 | 0.6649
2020-11-07 18:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.43154 | 0.70615 | 0.96769 | 1.1638 | 1.1638 | 1.1638 | 1.9434 | 2.5079 | 2.8777 | 3.0724 | 3.4617 | 3.851 | 0.80783 | 1.5944 | 1.9133 | 1.9133 | 1.9133 | 1.9133 | 0.55252 | 0.64273 | 0.64273 | 0.64273 | 0.64273 | 0.64273
2020-11-07 19:00 | Summer | 1.0288 | 1.4724 | 2.1248 | 2.1248 | 2.1248 | 2.1248 | 0.40867 | 0.66874 | 0.91642 | 1.1022 | 1.1022 | 1.1022 | 1.9624 | 2.5325 | 2.9059 | 3.1025 | 3.4956 | 3.8887 | 0.79258 | 1.5643 | 1.8772 | 1.8772 | 1.8772 | 1.8772 | 0.57158 | 0.6649 | 0.6649 | 0.6649 | 0.6649 | 0.6649
2020-11-07 20:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.49155 | 0.80436 | 1.1023 | 1.3257 | 1.3257 | 1.3257 | 2.0386 | 2.6308 | 3.0188 | 3.223 | 3.6314 | 4.0398 | 0.81545 | 1.6094 | 1.9313 | 1.9313 | 1.9313 | 1.9313 | 0.57158 | 0.6649 | 0.6649 | 0.6649 | 0.6649 | 0.6649
2020-11-07 21:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.44011 | 0.72018 | 0.98691 | 1.187 | 1.187 | 1.187 | 1.9243 | 2.4833 | 2.8495 | 3.0422 | 3.4277 | 3.8132 | 0.81545 | 1.6094 | 1.9313 | 1.9313 | 1.9313 | 1.9313 | 0.57158 | 0.6649 | 0.6649 | 0.6649 | 0.6649 | 0.6649
2020-11-07 22:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.38295 | 0.62665 | 0.85874 | 1.0328 | 1.0328 | 1.0328 | 1.8391 | 2.3733 | 2.7233 | 2.9075 | 3.2759 | 3.6444 | 0.74686 | 1.4741 | 1.7689 | 1.7689 | 1.7689 | 1.7689 | 0.48991 | 0.5699 | 0.5699 | 0.5699 | 0.5699 | 0.5699
2020-11-07 23:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.34008 | 0.5565 | 0.76261 | 0.9172 | 0.9172 | 0.9172 | 1.81 | 2.3358 | 2.6802 | 2.8615 | 3.2241 | 3.5867 | 0.70875 | 1.3989 | 1.6786 | 1.6786 | 1.6786 | 1.6786 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-11-08 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.43725 | 0.7155 | 0.98051 | 1.1793 | 1.1793 | 1.1793 | 1.7147 | 2.2128 | 2.5392 | 2.7109 | 3.0544 | 3.3979 | 0.66303 | 1.3086 | 1.5703 | 1.5703 | 1.5703 | 1.5703 | 0.45728 | 0.53194 | 0.53194 | 0.53194 | 0.53194 | 0.53194
2020-11-08 01:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.43154 | 0.70615 | 0.96769 | 1.1638 | 1.1638 | 1.1638 | 1.562 | 2.0158 | 2.313 | 2.4695 | 2.7824 | 3.0953 | 0.64397 | 1.271 | 1.5252 | 1.5252 | 1.5252 | 1.5252 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-11-08 02:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.33149 | 0.54243 | 0.74334 | 0.89401 | 0.89401 | 0.89401 | 1.6004 | 2.0653 | 2.3699 | 2.5302 | 2.8508 | 3.1714 | 0.56395 | 1.1131 | 1.3357 | 1.3357 | 1.3357 | 1.3357 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-11-08 03:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.42868 | 0.70147 | 0.96128 | 1.1561 | 1.1561 | 1.1561 | 1.5242 | 1.967 | 2.257 | 2.4097 | 2.715 | 3.0204 | 0.59444 | 1.1732 | 1.4079 | 1.4079 | 1.4079 | 1.4079 | 0.43821 | 0.50975 | 0.50975 | 0.50975 | 0.50975 | 0.50975
2020-11-08 04:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.41439 | 0.67809 | 0.92924 | 1.1176 | 1.1176 | 1.1176 | 1.5433 | 1.9915 | 2.2852 | 2.4398 | 2.749 | 3.0581 | 0.54291 | 1.0715 | 1.2858 | 1.2858 | 1.2858 | 1.2858 | 0.45713 | 0.53177 | 0.53177 | 0.53177 | 0.53177 | 0.53177
2020-11-08 05:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.41725 | 0.68277 | 0.93565 | 1.1253 | 1.1253 | 1.1253 | 1.5672 | 2.0224 | 2.3207 | 2.4777 | 2.7916 | 3.1056 | 0.59063 | 1.1657 | 1.3989 | 1.3989 | 1.3989 | 1.3989 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-11-08 06:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.45726 | 0.74824 | 1.0254 | 1.2332 | 1.2332 | 1.2332 | 1.6245 | 2.0963 | 2.4055 | 2.5682 | 2.8936 | 3.2191 | 0.59825 | 1.1808 | 1.4169 | 1.4169 | 1.4169 | 1.4169 | 0.43821 | 0.50975 | 0.50975 | 0.50975 | 0.50975 | 0.50975
2020-11-08 07:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.49727 | 0.81371 | 1.1151 | 1.3411 | 1.3411 | 1.3411 | 1.7528 | 2.262 | 2.5956 | 2.7712 | 3.1223 | 3.4734 | 0.68065 | 1.3434 | 1.6121 | 1.6121 | 1.6121 | 1.6121 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-11-08 08:00 | Summer | 0.91452 | 1.3088 | 1.8887 | 1.8887 | 1.8887 | 1.8887 | 0.43154 | 0.70615 | 0.96769 | 1.1638 | 1.1638 | 1.1638 | 1.9434 | 2.5079 | 2.8777 | 3.0724 | 3.4617 | 3.851 | 0.68208 | 1.3462 | 1.6155 | 1.6155 | 1.6155 | 1.6155 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-11-08 09:00 | Summer | 0.91452 | 1.3088 | 1.8887 | 1.8887 | 1.8887 | 1.8887 | 0.45726 | 0.74824 | 1.0254 | 1.2332 | 1.2332 | 1.2332 | 2.0386 | 2.6308 | 3.0188 | 3.223 | 3.6314 | 4.0398 | 0.72781 | 1.4365 | 1.7238 | 1.7238 | 1.7238 | 1.7238 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-11-08 10:00 | Summer | 0.89547 | 1.2816 | 1.8493 | 1.8493 | 1.8493 | 1.8493 | 0.43439 | 0.71083 | 0.9741 | 1.1715 | 1.1715 | 1.1715 | 1.9815 | 2.557 | 2.9341 | 3.1326 | 3.5296 | 3.9265 | 0.67446 | 1.3312 | 1.5974 | 1.5974 | 1.5974 | 1.5974 | 0.53347 | 0.62057 | 0.62057 | 0.62057 | 0.62057 | 0.62057
2020-11-08 11:00 | Summer | 0.87642 | 1.2543 | 1.81 | 1.81 | 1.81 | 1.81 | 0.40582 | 0.66406 | 0.91001 | 1.0945 | 1.0945 | 1.0945 | 2.0958 | 2.7046 | 3.1034 | 3.3133 | 3.7332 | 4.153 | 0.67065 | 1.3236 | 1.5884 | 1.5884 | 1.5884 | 1.5884 | 0.53347 | 0.62057 | 0.62057 | 0.62057 | 0.62057 | 0.62057
2020-11-08 12:00 | Summer | 0.87642 | 1.2543 | 1.81 | 1.81 | 1.81 | 1.81 | 0.40867 | 0.66874 | 0.91642 | 1.1022 | 1.1022 | 1.1022 | 2.1339 | 2.7537 | 3.1598 | 3.3736 | 3.8011 | 4.2285 | 0.68208 | 1.3462 | 1.6155 | 1.6155 | 1.6155 | 1.6155 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-11-08 13:00 | Summer | 0.87642 | 1.2543 | 1.81 | 1.81 | 1.81 | 1.81 | 0.34294 | 0.56118 | 0.76902 | 0.92491 | 0.92491 | 0.92491 | 2.0767 | 2.68 | 3.0752 | 3.2832 | 3.6992 | 4.1153 | 0.68208 | 1.3462 | 1.6155 | 1.6155 | 1.6155 | 1.6155 | 0.55252 | 0.64273 | 0.64273 | 0.64273 | 0.64273 | 0.64273
2020-11-08 14:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.38581 | 0.63133 | 0.86515 | 1.0405 | 1.0405 | 1.0405 | 2.1148 | 2.7291 | 3.1316 | 3.3435 | 3.7671 | 4.1908 | 0.67446 | 1.3312 | 1.5974 | 1.5974 | 1.5974 | 1.5974 | 0.53347 | 0.62057 | 0.62057 | 0.62057 | 0.62057 | 0.62057
2020-11-08 15:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.40582 | 0.66406 | 0.91001 | 1.0945 | 1.0945 | 1.0945 | 2.0958 | 2.7046 | 3.1034 | 3.3133 | 3.7332 | 4.153 | 0.82307 | 1.6245 | 1.9494 | 1.9494 | 1.9494 | 1.9494 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-11-08 16:00 | Summer | 0.91452 | 1.3088 | 1.8887 | 1.8887 | 1.8887 | 1.8887 | 0.37724 | 0.6173 | 0.84593 | 1.0174 | 1.0174 | 1.0174 | 2.0958 | 2.7046 | 3.1034 | 3.3133 | 3.7332 | 4.153 | 0.71637 | 1.4139 | 1.6967 | 1.6967 | 1.6967 | 1.6967 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-11-08 17:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.38581 | 0.63133 | 0.86515 | 1.0405 | 1.0405 | 1.0405 | 2.0386 | 2.6308 | 3.0188 | 3.223 | 3.6314 | 4.0398 | 0.75067 | 1.4816 | 1.7779 | 1.7779 | 1.7779 | 1.7779 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-11-08 18:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.38009 | 0.62197 | 0.85233 | 1.0251 | 1.0251 | 1.0251 | 1.9053 | 2.4587 | 2.8213 | 3.0121 | 3.3938 | 3.7755 | 0.89547 | 1.7674 | 2.1208 | 2.1208 | 2.1208 | 2.1208 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-11-08 19:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.38581 | 0.63133 | 0.86515 | 1.0405 | 1.0405 | 1.0405 | 1.9624 | 2.5325 | 2.9059 | 3.1025 | 3.4956 | 3.8887 | 0.78115 | 1.5417 | 1.8501 | 1.8501 | 1.8501 | 1.8501 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-11-08 20:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.40867 | 0.66874 | 0.91642 | 1.1022 | 1.1022 | 1.1022 | 2.0386 | 2.6308 | 3.0188 | 3.223 | 3.6314 | 4.0398 | 0.79258 | 1.5643 | 1.8772 | 1.8772 | 1.8772 | 1.8772 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-11-08 21:00 | Summer | 0.97152 | 1.3904 | 2.0064 | 2.0064 | 2.0064 | 2.0064 | 0.41153 | 0.67342 | 0.92283 | 1.1099 | 1.1099 | 1.1099 | 1.9053 | 2.4587 | 2.8213 | 3.0121 | 3.3938 | 3.7755 | 0.94501 | 1.8651 | 2.2382 | 2.2382 | 2.2382 | 2.2382 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-11-08 22:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.32861 | 0.53772 | 0.73688 | 0.88624 | 0.88624 | 0.88624 | 1.829 | 2.3603 | 2.7084 | 2.8916 | 3.2581 | 3.6245 | 0.77353 | 1.5267 | 1.832 | 1.832 | 1.832 | 1.832 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-11-08 23:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.32865 | 0.5378 | 0.73698 | 0.88637 | 0.88637 | 0.88637 | 1.7814 | 2.2988 | 2.6378 | 2.8163 | 3.1731 | 3.53 | 0.66303 | 1.3086 | 1.5703 | 1.5703 | 1.5703 | 1.5703 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-11-09 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.30012 | 0.49111 | 0.673 | 0.80942 | 0.80942 | 0.80942 | 1.6195 | 2.0899 | 2.3981 | 2.5603 | 2.8847 | 3.2092 | 0.64101 | 1.2652 | 1.5182 | 1.5182 | 1.5182 | 1.5182 | 0.44635 | 0.51922 | 0.51922 | 0.51922 | 0.51922 | 0.51922
2020-11-09 01:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.32865 | 0.5378 | 0.73698 | 0.88637 | 0.88637 | 0.88637 | 1.5242 | 1.967 | 2.257 | 2.4097 | 2.715 | 3.0204 | 0.62111 | 1.2259 | 1.4711 | 1.4711 | 1.4711 | 1.4711 | 0.47482 | 0.55234 | 0.55234 | 0.55234 | 0.55234 | 0.55234
2020-11-09 02:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.40867 | 0.66874 | 0.91642 | 1.1022 | 1.1022 | 1.1022 | 1.5242 | 1.967 | 2.257 | 2.4097 | 2.715 | 3.0204 | 0.54109 | 1.0679 | 1.2815 | 1.2815 | 1.2815 | 1.2815 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-11-09 03:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.29177 | 0.47744 | 0.65427 | 0.78689 | 0.78689 | 0.78689 | 1.4861 | 1.9178 | 2.2006 | 2.3495 | 2.6472 | 2.9449 | 0.58301 | 1.1507 | 1.3808 | 1.3808 | 1.3808 | 1.3808 | 0.49757 | 0.5788 | 0.5788 | 0.5788 | 0.5788 | 0.5788
2020-11-09 04:00 | Summer | 1.1432 | 1.636 | 2.3609 | 2.3609 | 2.3609 | 2.3609 | 0.42296 | 0.69212 | 0.94846 | 1.1407 | 1.1407 | 1.1407 | 1.5052 | 1.9424 | 2.2288 | 2.3796 | 2.6811 | 2.9826 | 0.53347 | 1.0529 | 1.2635 | 1.2635 | 1.2635 | 1.2635 | 0.53851 | 0.62643 | 0.62643 | 0.62643 | 0.62643 | 0.62643
2020-11-09 05:00 | Summer | 1.2191 | 1.7448 | 2.5177 | 2.5177 | 2.5177 | 2.5177 | 0.49155 | 0.80436 | 1.1023 | 1.3257 | 1.3257 | 1.3257 | 1.6385 | 2.1145 | 2.4263 | 2.5904 | 2.9187 | 3.2469 | 0.58301 | 1.1507 | 1.3808 | 1.3808 | 1.3808 | 1.3808 | 0.59043 | 0.68683 | 0.68683 | 0.68683 | 0.68683 | 0.68683
2020-11-09 06:00 | Summer | 1.381 | 1.9764 | 2.852 | 2.852 | 2.852 | 2.852 | 0.64874 | 1.0616 | 1.4547 | 1.7496 | 1.7496 | 1.7496 | 1.8481 | 2.3849 | 2.7366 | 2.9218 | 3.292 | 3.6622 | 0.72781 | 1.4365 | 1.7238 | 1.7238 | 1.7238 | 1.7238 | 0.81877 | 0.95245 | 0.95245 | 0.95245 | 0.95245 | 0.95245
2020-11-09 07:00 | Summer | 1.8862 | 2.6995 | 3.8954 | 3.8954 | 3.8954 | 3.8954 | 0.72876 | 1.1925 | 1.6342 | 1.9654 | 1.9654 | 1.9654 | 2.0577 | 2.6554 | 3.047 | 3.2531 | 3.6653 | 4.0775 | 0.93738 | 1.8501 | 2.2201 | 2.2201 | 2.2201 | 2.2201 | 1.0098 | 1.1746 | 1.1746 | 1.1746 | 1.1746 | 1.1746
2020-11-09 08:00 | Summer | 2.0958 | 2.9994 | 4.3282 | 4.3282 | 4.3282 | 4.3282 | 0.89451 | 1.4638 | 2.0059 | 2.4125 | 2.4125 | 2.4125 | 2.3625 | 3.0488 | 3.4984 | 3.735 | 4.2083 | 4.6816 | 0.98692 | 1.9479 | 2.3374 | 2.3374 | 2.3374 | 2.3374 | 1.2194 | 1.4184 | 1.4184 | 1.4184 | 1.4184 | 1.4184
2020-11-09 09:00 | Summer | 2.3435 | 3.3539 | 4.8398 | 4.8398 | 4.8398 | 4.8398 | 0.82592 | 1.3515 | 1.8521 | 2.2275 | 2.2275 | 2.2275 | 2.4006 | 3.098 | 3.5548 | 3.7953 | 4.2762 | 4.7571 | 0.94501 | 1.8651 | 2.2382 | 2.2382 | 2.2382 | 2.2382 | 1.3527 | 1.5736 | 1.5736 | 1.5736 | 1.5736 | 1.5736
2020-11-09 10:00 | Summer | 2.2673 | 3.2448 | 4.6824 | 4.6824 | 4.6824 | 4.6824 | 0.82021 | 1.3422 | 1.8393 | 2.2121 | 2.2121 | 2.2121 | 2.4197 | 3.1225 | 3.583 | 3.8254 | 4.3101 | 4.7949 | 0.90309 | 1.7824 | 2.1389 | 2.1389 | 2.1389 | 2.1389 | 1.2575 | 1.4628 | 1.4628 | 1.4628 | 1.4628 | 1.4628
2020-11-09 11:00 | Summer | 2.4006 | 3.4357 | 4.9578 | 4.9578 | 4.9578 | 4.9578 | 0.85736 | 1.403 | 1.9226 | 2.3123 | 2.3123 | 2.3123 | 2.4959 | 3.2209 | 3.6959 | 3.9459 | 4.4459 | 4.9459 | 0.90382 | 1.7839 | 2.1406 | 2.1406 | 2.1406 | 2.1406 | 1.3527 | 1.5736 | 1.5736 | 1.5736 | 1.5736 | 1.5736
2020-11-09 12:00 | Summer | 2.3816 | 3.4084 | 4.9185 | 4.9185 | 4.9185 | 4.9185 | 0.88594 | 1.4497 | 1.9867 | 2.3894 | 2.3894 | 2.3894 | 2.6293 | 3.393 | 3.8934 | 4.1567 | 4.6835 | 5.2102 | 0.9793 | 1.9328 | 2.3194 | 2.3194 | 2.3194 | 2.3194 | 1.3337 | 1.5514 | 1.5514 | 1.5514 | 1.5514 | 1.5514
2020-11-09 13:00 | Summer | 2.3625 | 3.3811 | 4.8791 | 4.8791 | 4.8791 | 4.8791 | 0.77734 | 1.272 | 1.7431 | 2.0965 | 2.0965 | 2.0965 | 2.6293 | 3.393 | 3.8934 | 4.1567 | 4.6835 | 5.2102 | 0.9069 | 1.7899 | 2.1479 | 2.1479 | 2.1479 | 2.1479 | 1.3146 | 1.5293 | 1.5293 | 1.5293 | 1.5293 | 1.5293
2020-11-09 14:00 | Summer | 2.4578 | 3.5175 | 5.0759 | 5.0759 | 5.0759 | 5.0759 | 0.91166 | 1.4918 | 2.0443 | 2.4587 | 2.4587 | 2.4587 | 2.4959 | 3.2209 | 3.6959 | 3.9459 | 4.4459 | 4.9459 | 1.0022 | 1.978 | 2.3735 | 2.3735 | 2.3735 | 2.3735 | 1.3146 | 1.5293 | 1.5293 | 1.5293 | 1.5293 | 1.5293
2020-11-09 15:00 | Summer | 2.4197 | 3.4629 | 4.9972 | 4.9972 | 4.9972 | 4.9972 | 0.88594 | 1.4497 | 1.9867 | 2.3894 | 2.3894 | 2.3894 | 2.5721 | 3.3192 | 3.8087 | 4.0664 | 4.5816 | 5.0969 | 0.9069 | 1.7899 | 2.1479 | 2.1479 | 2.1479 | 2.1479 | 1.3146 | 1.5293 | 1.5293 | 1.5293 | 1.5293 | 1.5293
2020-11-09 16:00 | Summer | 2.4387 | 3.4902 | 5.0365 | 5.0365 | 5.0365 | 5.0365 | 0.81735 | 1.3375 | 1.8328 | 2.2044 | 2.2044 | 2.2044 | 2.6293 | 3.393 | 3.8934 | 4.1567 | 4.6835 | 5.2102 | 0.95644 | 1.8877 | 2.2652 | 2.2652 | 2.2652 | 2.2652 | 1.3337 | 1.5514 | 1.5514 | 1.5514 | 1.5514 | 1.5514
2020-11-09 17:00 | Summer | 2.3625 | 3.3811 | 4.8791 | 4.8791 | 4.8791 | 4.8791 | 0.81164 | 1.3281 | 1.82 | 2.189 | 2.189 | 2.189 | 2.5352 | 3.2717 | 3.7542 | 4.0081 | 4.516 | 5.0239 | 0.8345 | 1.647 | 1.9764 | 1.9764 | 1.9764 | 1.9764 | 1.2384 | 1.4406 | 1.4406 | 1.4406 | 1.4406 | 1.4406
2020-11-09 18:00 | Summer | 1.6649 | 2.3828 | 3.4385 | 3.4385 | 3.4385 | 3.4385 | 0.55991 | 0.91622 | 1.2556 | 1.5101 | 1.5101 | 1.5101 | 2.3054 | 2.975 | 3.4138 | 3.6447 | 4.1065 | 4.5683 | 0.82307 | 1.6245 | 1.9494 | 1.9494 | 1.9494 | 1.9494 | 0.90203 | 1.0493 | 1.0493 | 1.0493 | 1.0493 | 1.0493
2020-11-09 19:00 | Summer | 1.1813 | 1.6906 | 2.4396 | 2.4396 | 2.4396 | 2.4396 | 0.42582 | 0.6968 | 0.95487 | 1.1484 | 1.1484 | 1.1484 | 2.115 | 2.7294 | 3.1319 | 3.3438 | 3.7675 | 4.1912 | 0.80783 | 1.5944 | 1.9133 | 1.9133 | 1.9133 | 1.9133 | 0.64779 | 0.75355 | 0.75355 | 0.75355 | 0.75355 | 0.75355
2020-11-09 20:00 | Summer | 1.1432 | 1.636 | 2.3609 | 2.3609 | 2.3609 | 2.3609 | 0.31722 | 0.51909 | 0.71134 | 0.85554 | 0.85554 | 0.85554 | 1.9815 | 2.557 | 2.9341 | 3.1326 | 3.5296 | 3.9265 | 0.73162 | 1.444 | 1.7328 | 1.7328 | 1.7328 | 1.7328 | 0.57158 | 0.6649 | 0.6649 | 0.6649 | 0.6649 | 0.6649
2020-11-09 21:00 | Summer | 1.0479 | 1.4997 | 2.1641 | 2.1641 | 2.1641 | 2.1641 | 0.3458 | 0.56585 | 0.77543 | 0.93261 | 0.93261 | 0.93261 | 1.9434 | 2.5079 | 2.8777 | 3.0724 | 3.4617 | 3.851 | 0.79258 | 1.5643 | 1.8772 | 1.8772 | 1.8772 | 1.8772 | 0.53347 | 0.62057 | 0.62057 | 0.62057 | 0.62057 | 0.62057
2020-11-09 22:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.37152 | 0.60794 | 0.83311 | 1.002 | 1.002 | 1.002 | 1.829 | 2.3603 | 2.7084 | 2.8916 | 3.2581 | 3.6245 | 0.78115 | 1.5417 | 1.8501 | 1.8501 | 1.8501 | 1.8501 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-11-09 23:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.32865 | 0.5378 | 0.73698 | 0.88637 | 0.88637 | 0.88637 | 1.6581 | 2.1397 | 2.4553 | 2.6213 | 2.9535 | 3.2857 | 0.61349 | 1.2108 | 1.453 | 1.453 | 1.453 | 1.453 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-11-10 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.37152 | 0.60794 | 0.83311 | 1.002 | 1.002 | 1.002 | 1.6004 | 2.0653 | 2.3699 | 2.5302 | 2.8508 | 3.1714 | 0.6173 | 1.2184 | 1.462 | 1.462 | 1.462 | 1.462 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-11-10 01:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.36581 | 0.59859 | 0.82029 | 0.98657 | 0.98657 | 0.98657 | 1.5433 | 1.9915 | 2.2852 | 2.4398 | 2.749 | 3.0581 | 0.53728 | 1.0604 | 1.2725 | 1.2725 | 1.2725 | 1.2725 | 0.43506 | 0.50609 | 0.50609 | 0.50609 | 0.50609 | 0.50609
2020-11-10 02:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.27719 | 0.45358 | 0.62157 | 0.74756 | 0.74756 | 0.74756 | 1.5242 | 1.967 | 2.257 | 2.4097 | 2.715 | 3.0204 | 0.59444 | 1.1732 | 1.4079 | 1.4079 | 1.4079 | 1.4079 | 0.42711 | 0.49685 | 0.49685 | 0.49685 | 0.49685 | 0.49685
2020-11-10 03:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.37438 | 0.61262 | 0.83952 | 1.0097 | 1.0097 | 1.0097 | 1.4861 | 1.9178 | 2.2006 | 2.3495 | 2.6472 | 2.9449 | 0.60587 | 1.1958 | 1.435 | 1.435 | 1.435 | 1.435 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-11-10 04:00 | Summer | 1.0357 | 1.4822 | 2.1389 | 2.1389 | 2.1389 | 2.1389 | 0.40116 | 0.65644 | 0.89957 | 1.0819 | 1.0819 | 1.0819 | 1.5614 | 2.0149 | 2.3121 | 2.4685 | 2.7813 | 3.0941 | 0.59444 | 1.1732 | 1.4079 | 1.4079 | 1.4079 | 1.4079 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-11-10 05:00 | Summer | 1.2169 | 1.7416 | 2.5132 | 2.5132 | 2.5132 | 2.5132 | 0.40582 | 0.66406 | 0.91001 | 1.0945 | 1.0945 | 1.0945 | 1.6385 | 2.1145 | 2.4263 | 2.5904 | 2.9187 | 3.2469 | 0.6173 | 1.2184 | 1.462 | 1.462 | 1.462 | 1.462 | 0.57158 | 0.6649 | 0.6649 | 0.6649 | 0.6649 | 0.6649
2020-11-10 06:00 | Summer | 1.3396 | 1.9172 | 2.7666 | 2.7666 | 2.7666 | 2.7666 | 0.59444 | 0.97271 | 1.333 | 1.6032 | 1.6032 | 1.6032 | 1.7909 | 2.3112 | 2.652 | 2.8314 | 3.1902 | 3.549 | 0.76591 | 1.5117 | 1.814 | 1.814 | 1.814 | 1.814 | 0.80289 | 0.93398 | 0.93398 | 0.93398 | 0.93398 | 0.93398
2020-11-10 07:00 | Summer | 1.9908 | 2.8491 | 4.1114 | 4.1114 | 4.1114 | 4.1114 | 0.68589 | 1.1224 | 1.5381 | 1.8498 | 1.8498 | 1.8498 | 2.1339 | 2.7537 | 3.1598 | 3.3736 | 3.8011 | 4.2285 | 1.0441 | 2.0607 | 2.4728 | 2.4728 | 2.4728 | 2.4728 | 1.0479 | 1.219 | 1.219 | 1.219 | 1.219 | 1.219
2020-11-10 08:00 | Summer | 2.3244 | 3.3266 | 4.8004 | 4.8004 | 4.8004 | 4.8004 | 0.7482 | 1.2243 | 1.6778 | 2.0179 | 2.0179 | 2.0179 | 2.3435 | 3.0242 | 3.4702 | 3.7049 | 4.1744 | 4.6438 | 1.0441 | 2.0607 | 2.4728 | 2.4728 | 2.4728 | 2.4728 | 1.1622 | 1.352 | 1.352 | 1.352 | 1.352 | 1.352
2020-11-10 09:00 | Summer | 2.4768 | 3.5447 | 5.1152 | 5.1152 | 5.1152 | 5.1152 | 0.77734 | 1.272 | 1.7431 | 2.0965 | 2.0965 | 2.0965 | 2.4768 | 3.1963 | 3.6677 | 3.9158 | 4.4119 | 4.9081 | 0.93738 | 1.8501 | 2.2201 | 2.2201 | 2.2201 | 2.2201 | 1.2575 | 1.4628 | 1.4628 | 1.4628 | 1.4628 | 1.4628
2020-11-10 10:00 | Summer | 2.553 | 3.6538 | 5.2726 | 5.2726 | 5.2726 | 5.2726 | 0.76019 | 1.244 | 1.7047 | 2.0502 | 2.0502 | 2.0502 | 2.5911 | 3.3438 | 3.8369 | 4.0965 | 4.6156 | 5.1347 | 0.81545 | 1.6094 | 1.9313 | 1.9313 | 1.9313 | 1.9313 | 1.3715 | 1.5954 | 1.5954 | 1.5954 | 1.5954 | 1.5954
2020-11-10 11:00 | Summer | 2.5721 | 3.6811 | 5.3119 | 5.3119 | 5.3119 | 5.3119 | 0.76591 | 1.2533 | 1.7175 | 2.0656 | 2.0656 | 2.0656 | 2.7055 | 3.4913 | 4.0062 | 4.2772 | 4.8192 | 5.3612 | 0.84974 | 1.6771 | 2.0125 | 2.0125 | 2.0125 | 2.0125 | 1.4099 | 1.6401 | 1.6401 | 1.6401 | 1.6401 | 1.6401
2020-11-10 12:00 | Summer | 2.5721 | 3.6811 | 5.3119 | 5.3119 | 5.3119 | 5.3119 | 0.9088 | 1.4871 | 2.0379 | 2.451 | 2.451 | 2.451 | 2.8198 | 3.6389 | 4.1755 | 4.4579 | 5.0228 | 5.5877 | 0.94119 | 1.8576 | 2.2291 | 2.2291 | 2.2291 | 2.2291 | 1.3718 | 1.5957 | 1.5957 | 1.5957 | 1.5957 | 1.5957
2020-11-10 13:00 | Summer | 2.6674 | 3.8174 | 5.5087 | 5.5087 | 5.5087 | 5.5087 | 0.92595 | 1.5152 | 2.0764 | 2.4973 | 2.4973 | 2.4973 | 2.9531 | 3.811 | 4.373 | 4.6688 | 5.2604 | 5.852 | 0.96025 | 1.8952 | 2.2743 | 2.2743 | 2.2743 | 2.2743 | 1.4099 | 1.6401 | 1.6401 | 1.6401 | 1.6401 | 1.6401
2020-11-10 14:00 | Summer | 2.6146 | 3.7419 | 5.3997 | 5.3997 | 5.3997 | 5.3997 | 1.0088 | 1.6508 | 2.2622 | 2.7208 | 2.7208 | 2.7208 | 2.9345 | 3.787 | 4.3455 | 4.6394 | 5.2273 | 5.8151 | 0.97549 | 1.9253 | 2.3104 | 2.3104 | 2.3104 | 2.3104 | 1.4289 | 1.6622 | 1.6622 | 1.6622 | 1.6622 | 1.6622
2020-11-10 15:00 | Summer | 2.6293 | 3.7629 | 5.43 | 5.43 | 5.43 | 5.43 | 1.0488 | 1.7163 | 2.3519 | 2.8287 | 2.8287 | 2.8287 | 2.9913 | 3.8601 | 4.4294 | 4.729 | 5.3283 | 5.9275 | 0.81926 | 1.617 | 1.9403 | 1.9403 | 1.9403 | 1.9403 | 1.3527 | 1.5736 | 1.5736 | 1.5736 | 1.5736 | 1.5736
2020-11-10 16:00 | Summer | 2.6483 | 3.7901 | 5.4693 | 5.4693 | 5.4693 | 5.4693 | 0.98597 | 1.6134 | 2.211 | 2.6591 | 2.6591 | 2.6591 | 2.9531 | 3.811 | 4.373 | 4.6688 | 5.2604 | 5.852 | 0.86117 | 1.6997 | 2.0396 | 2.0396 | 2.0396 | 2.0396 | 1.3146 | 1.5293 | 1.5293 | 1.5293 | 1.5293 | 1.5293
2020-11-10 17:00 | Summer | 2.534 | 3.6265 | 5.2332 | 5.2332 | 5.2332 | 5.2332 | 0.94881 | 1.5526 | 2.1276 | 2.5589 | 2.5589 | 2.5589 | 2.9531 | 3.811 | 4.373 | 4.6688 | 5.2604 | 5.852 | 0.80402 | 1.5869 | 1.9042 | 1.9042 | 1.9042 | 1.9042 | 1.2956 | 1.5071 | 1.5071 | 1.5071 | 1.5071 | 1.5071
2020-11-10 18:00 | Summer | 1.8345 | 2.6254 | 3.7886 | 3.7886 | 3.7886 | 3.7886 | 0.72876 | 1.1925 | 1.6342 | 1.9654 | 1.9654 | 1.9654 | 2.6483 | 3.4176 | 3.9216 | 4.1869 | 4.7174 | 5.2479 | 0.88023 | 1.7373 | 2.0847 | 2.0847 | 2.0847 | 2.0847 | 0.96683 | 1.1247 | 1.1247 | 1.1247 | 1.1247 | 1.1247
2020-11-10 19:00 | Summer | 1.2003 | 1.7178 | 2.4789 | 2.4789 | 2.4789 | 2.4789 | 0.48066 | 0.78654 | 1.0779 | 1.2963 | 1.2963 | 1.2963 | 2.4387 | 3.1471 | 3.6112 | 3.8555 | 4.3441 | 4.8326 | 0.82688 | 1.632 | 1.9584 | 1.9584 | 1.9584 | 1.9584 | 0.65469 | 0.76157 | 0.76157 | 0.76157 | 0.76157 | 0.76157
2020-11-10 20:00 | Summer | 1.1509 | 1.6471 | 2.3769 | 2.3769 | 2.3769 | 2.3769 | 0.42011 | 0.68744 | 0.94205 | 1.133 | 1.133 | 1.133 | 2.2863 | 2.9504 | 3.3855 | 3.6146 | 4.0726 | 4.5306 | 0.81545 | 1.6094 | 1.9313 | 1.9313 | 1.9313 | 1.9313 | 0.60968 | 0.70922 | 0.70922 | 0.70922 | 0.70922 | 0.70922
2020-11-10 21:00 | Summer | 1.0669 | 1.527 | 2.2035 | 2.2035 | 2.2035 | 2.2035 | 0.45726 | 0.74824 | 1.0254 | 1.2332 | 1.2332 | 1.2332 | 2.0958 | 2.7046 | 3.1034 | 3.3133 | 3.7332 | 4.153 | 0.80783 | 1.5944 | 1.9133 | 1.9133 | 1.9133 | 1.9133 | 0.55252 | 0.64273 | 0.64273 | 0.64273 | 0.64273 | 0.64273
2020-11-10 22:00 | Summer | 1.0669 | 1.527 | 2.2035 | 2.2035 | 2.2035 | 2.2035 | 0.36581 | 0.59859 | 0.82029 | 0.98657 | 0.98657 | 0.98657 | 1.9503 | 2.5169 | 2.888 | 3.0834 | 3.4741 | 3.8648 | 0.69351 | 1.3688 | 1.6425 | 1.6425 | 1.6425 | 1.6425 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-11-10 23:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.38295 | 0.62665 | 0.85874 | 1.0328 | 1.0328 | 1.0328 | 1.6958 | 2.1884 | 2.5111 | 2.6809 | 3.0206 | 3.3604 | 0.66684 | 1.3161 | 1.5794 | 1.5794 | 1.5794 | 1.5794 | 0.45743 | 0.53211 | 0.53211 | 0.53211 | 0.53211 | 0.53211
2020-11-11 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.37724 | 0.6173 | 0.84593 | 1.0174 | 1.0174 | 1.0174 | 1.6385 | 2.1145 | 2.4263 | 2.5904 | 2.9187 | 3.2469 | 0.56014 | 1.1055 | 1.3267 | 1.3267 | 1.3267 | 1.3267 | 0.43821 | 0.50975 | 0.50975 | 0.50975 | 0.50975 | 0.50975
2020-11-11 01:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.34294 | 0.56118 | 0.76902 | 0.92491 | 0.92491 | 0.92491 | 1.5623 | 2.0161 | 2.3135 | 2.4699 | 2.7829 | 3.0959 | 0.49155 | 0.97017 | 1.1642 | 1.1642 | 1.1642 | 1.1642 | 0.43816 | 0.5097 | 0.5097 | 0.5097 | 0.5097 | 0.5097
2020-11-11 02:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.39153 | 0.64068 | 0.87797 | 1.0559 | 1.0559 | 1.0559 | 1.5814 | 2.0407 | 2.3417 | 2.5001 | 2.8169 | 3.1337 | 0.724 | 1.4289 | 1.7147 | 1.7147 | 1.7147 | 1.7147 | 0.43848 | 0.51007 | 0.51007 | 0.51007 | 0.51007 | 0.51007
2020-11-11 03:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.36581 | 0.59859 | 0.82029 | 0.98657 | 0.98657 | 0.98657 | 1.4861 | 1.9178 | 2.2006 | 2.3495 | 2.6472 | 2.9449 | 0.49918 | 0.98521 | 1.1823 | 1.1823 | 1.1823 | 1.1823 | 0.46168 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706
2020-11-11 04:00 | Summer | 1.0479 | 1.4997 | 2.1641 | 2.1641 | 2.1641 | 2.1641 | 0.37724 | 0.6173 | 0.84593 | 1.0174 | 1.0174 | 1.0174 | 1.5433 | 1.9915 | 2.2852 | 2.4398 | 2.749 | 3.0581 | 0.5792 | 1.1431 | 1.3718 | 1.3718 | 1.3718 | 1.3718 | 0.54419 | 0.63303 | 0.63303 | 0.63303 | 0.63303 | 0.63303
2020-11-11 05:00 | Summer | 1.1769 | 1.6843 | 2.4306 | 2.4306 | 2.4306 | 2.4306 | 0.36568 | 0.59838 | 0.82 | 0.98622 | 0.98622 | 0.98622 | 1.6576 | 2.1391 | 2.4545 | 2.6205 | 2.9526 | 3.2847 | 0.61246 | 1.2088 | 1.4506 | 1.4506 | 1.4506 | 1.4506 | 0.5715 | 0.6648 | 0.6648 | 0.6648 | 0.6648 | 0.6648
2020-11-11 06:00 | Summer | 1.365 | 1.9535 | 2.819 | 2.819 | 2.819 | 2.819 | 0.6716 | 1.099 | 1.506 | 1.8113 | 1.8113 | 1.8113 | 1.81 | 2.3358 | 2.6802 | 2.8615 | 3.2241 | 3.5867 | 0.68589 | 1.3537 | 1.6245 | 1.6245 | 1.6245 | 1.6245 | 0.81926 | 0.95302 | 0.95302 | 0.95302 | 0.95302 | 0.95302
2020-11-11 07:00 | Summer | 1.7525 | 2.5081 | 3.6193 | 3.6193 | 3.6193 | 3.6193 | 0.76305 | 1.2486 | 1.7111 | 2.0579 | 2.0579 | 2.0579 | 2.2863 | 2.9504 | 3.3855 | 3.6146 | 4.0726 | 4.5306 | 0.9069 | 1.7899 | 2.1479 | 2.1479 | 2.1479 | 2.1479 | 0.98755 | 1.1488 | 1.1488 | 1.1488 | 1.1488 | 1.1488
2020-11-11 08:00 | Summer | 2.4909 | 3.5649 | 5.1443 | 5.1443 | 5.1443 | 5.1443 | 0.86022 | 1.4076 | 1.929 | 2.32 | 2.32 | 2.32 | 2.4959 | 3.2209 | 3.6959 | 3.9459 | 4.4459 | 4.9459 | 0.97168 | 1.9178 | 2.3013 | 2.3013 | 2.3013 | 2.3013 | 1.3126 | 1.5269 | 1.5269 | 1.5269 | 1.5269 | 1.5269
2020-11-11 09:00 | Summer | 2.6864 | 3.8447 | 5.548 | 5.548 | 5.548 | 5.548 | 0.81014 | 1.3257 | 1.8167 | 2.1849 | 2.1849 | 2.1849 | 2.534 | 3.2701 | 3.7523 | 4.0061 | 4.5138 | 5.0214 | 1.0174 | 2.008 | 2.4096 | 2.4096 | 2.4096 | 2.4096 | 1.3337 | 1.5514 | 1.5514 | 1.5514 | 1.5514 | 1.5514
2020-11-11 10:00 | Summer | 2.8007 | 4.0083 | 5.7841 | 5.7841 | 5.7841 | 5.7841 | 0.85165 | 1.3936 | 1.9098 | 2.2969 | 2.2969 | 2.2969 | 2.8388 | 3.6634 | 4.2037 | 4.4881 | 5.0568 | 5.6255 | 1.0212 | 2.0156 | 2.4187 | 2.4187 | 2.4187 | 2.4187 | 1.4289 | 1.6622 | 1.6622 | 1.6622 | 1.6622 | 1.6622
2020-11-11 11:00 | Summer | 2.7436 | 3.9265 | 5.6661 | 5.6661 | 5.6661 | 5.6661 | 0.95167 | 1.5573 | 2.1341 | 2.5666 | 2.5666 | 2.5666 | 2.9531 | 3.811 | 4.373 | 4.6688 | 5.2604 | 5.852 | 1.006 | 1.9855 | 2.3826 | 2.3826 | 2.3826 | 2.3826 | 1.4861 | 1.7287 | 1.7287 | 1.7287 | 1.7287 | 1.7287
2020-11-11 12:00 | Summer | 2.7245 | 3.8992 | 5.6267 | 5.6267 | 5.6267 | 5.6267 | 0.99168 | 1.6228 | 2.2238 | 2.6745 | 2.6745 | 2.6745 | 3.0103 | 3.8847 | 4.4576 | 4.7592 | 5.3622 | 5.9653 | 0.9069 | 1.7899 | 2.1479 | 2.1479 | 2.1479 | 2.1479 | 1.4861 | 1.7287 | 1.7287 | 1.7287 | 1.7287 | 1.7287
2020-11-11 13:00 | Summer | 2.7245 | 3.8992 | 5.6267 | 5.6267 | 5.6267 | 5.6267 | 0.99168 | 1.6228 | 2.2238 | 2.6745 | 2.6745 | 2.6745 | 3.0675 | 3.9585 | 4.5423 | 4.8495 | 5.464 | 6.0785 | 0.86498 | 1.7072 | 2.0486 | 2.0486 | 2.0486 | 2.0486 | 1.467 | 1.7066 | 1.7066 | 1.7066 | 1.7066 | 1.7066
2020-11-11 14:00 | Summer | 2.896 | 4.1446 | 5.9808 | 5.9808 | 5.9808 | 5.9808 | 0.98597 | 1.6134 | 2.211 | 2.6591 | 2.6591 | 2.6591 | 2.9722 | 3.8356 | 4.4012 | 4.6989 | 5.2943 | 5.8898 | 0.83831 | 1.6546 | 1.9855 | 1.9855 | 1.9855 | 1.9855 | 1.4099 | 1.6401 | 1.6401 | 1.6401 | 1.6401 | 1.6401
2020-11-11 15:00 | Summer | 2.8388 | 4.0628 | 5.8628 | 5.8628 | 5.8628 | 5.8628 | 1.0145 | 1.6602 | 2.275 | 2.7362 | 2.7362 | 2.7362 | 3.0484 | 3.9339 | 4.5141 | 4.8194 | 5.4301 | 6.0408 | 0.89166 | 1.7599 | 2.1118 | 2.1118 | 2.1118 | 2.1118 | 1.4289 | 1.6622 | 1.6622 | 1.6622 | 1.6622 | 1.6622
2020-11-11 16:00 | Summer | 2.8769 | 4.1174 | 5.9415 | 5.9415 | 5.9415 | 5.9415 | 1.0088 | 1.6508 | 2.2622 | 2.7208 | 2.7208 | 2.7208 | 3.0103 | 3.8847 | 4.4576 | 4.7592 | 5.3622 | 5.9653 | 0.87261 | 1.7222 | 2.0667 | 2.0667 | 2.0667 | 2.0667 | 1.3908 | 1.6179 | 1.6179 | 1.6179 | 1.6179 | 1.6179
2020-11-11 17:00 | Summer | 2.7447 | 3.9281 | 5.6684 | 5.6684 | 5.6684 | 5.6684 | 0.99796 | 1.633 | 2.2379 | 2.6915 | 2.6915 | 2.6915 | 2.9823 | 3.8486 | 4.4161 | 4.7148 | 5.3123 | 5.9097 | 0.88023 | 1.7373 | 2.0847 | 2.0847 | 2.0847 | 2.0847 | 1.3527 | 1.5736 | 1.5736 | 1.5736 | 1.5736 | 1.5736
2020-11-11 18:00 | Summer | 1.8555 | 2.6555 | 3.832 | 3.832 | 3.832 | 3.832 | 0.73701 | 1.206 | 1.6527 | 1.9877 | 1.9877 | 1.9877 | 2.6492 | 3.4188 | 3.9229 | 4.1883 | 4.719 | 5.2497 | 0.89166 | 1.7599 | 2.1118 | 2.1118 | 2.1118 | 2.1118 | 0.94891 | 1.1038 | 1.1038 | 1.1038 | 1.1038 | 1.1038
2020-11-11 19:00 | Summer | 1.2956 | 1.8542 | 2.6756 | 2.6756 | 2.6756 | 2.6756 | 0.49576 | 0.81124 | 1.1117 | 1.337 | 1.337 | 1.337 | 2.5722 | 3.3194 | 3.8089 | 4.0666 | 4.5818 | 5.0971 | 0.84974 | 1.6771 | 2.0125 | 2.0125 | 2.0125 | 2.0125 | 0.72401 | 0.84222 | 0.84222 | 0.84222 | 0.84222 | 0.84222
2020-11-11 20:00 | Summer | 1.467 | 2.0996 | 3.0298 | 3.0298 | 3.0298 | 3.0298 | 0.52013 | 0.85112 | 1.1664 | 1.4028 | 1.4028 | 1.4028 | 2.2291 | 2.8767 | 3.3009 | 3.5242 | 3.9708 | 4.4173 | 0.86117 | 1.6997 | 2.0396 | 2.0396 | 2.0396 | 2.0396 | 0.60985 | 0.70941 | 0.70941 | 0.70941 | 0.70941 | 0.70941
2020-11-11 21:00 | Summer | 1.2575 | 1.7996 | 2.5969 | 2.5969 | 2.5969 | 2.5969 | 0.37724 | 0.6173 | 0.84593 | 1.0174 | 1.0174 | 1.0174 | 2.2482 | 2.9013 | 3.3291 | 3.5543 | 4.0047 | 4.4551 | 0.74686 | 1.4741 | 1.7689 | 1.7689 | 1.7689 | 1.7689 | 0.57158 | 0.6649 | 0.6649 | 0.6649 | 0.6649 | 0.6649
2020-11-11 22:00 | Summer | 1.105 | 1.5815 | 2.2822 | 2.2822 | 2.2822 | 2.2822 | 0.42868 | 0.70147 | 0.96128 | 1.1561 | 1.1561 | 1.1561 | 1.9053 | 2.4587 | 2.8213 | 3.0121 | 3.3938 | 3.7755 | 0.75448 | 1.4891 | 1.7869 | 1.7869 | 1.7869 | 1.7869 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-11-11 23:00 | Summer | 1.105 | 1.5815 | 2.2822 | 2.2822 | 2.2822 | 2.2822 | 0.38867 | 0.636 | 0.87156 | 1.0482 | 1.0482 | 1.0482 | 1.81 | 2.3358 | 2.6802 | 2.8615 | 3.2241 | 3.5867 | 0.75829 | 1.4966 | 1.796 | 1.796 | 1.796 | 1.796 | 0.49651 | 0.57757 | 0.57757 | 0.57757 | 0.57757 | 0.57757
2020-11-12 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.33437 | 0.54715 | 0.7498 | 0.90178 | 0.90178 | 0.90178 | 1.6957 | 2.1882 | 2.5109 | 2.6808 | 3.0205 | 3.3602 | 0.69351 | 1.3688 | 1.6425 | 1.6425 | 1.6425 | 1.6425 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-11-12 01:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.38867 | 0.636 | 0.87156 | 1.0482 | 1.0482 | 1.0482 | 1.6195 | 2.0899 | 2.3981 | 2.5603 | 2.8847 | 3.2092 | 0.65922 | 1.3011 | 1.5613 | 1.5613 | 1.5613 | 1.5613 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-11-12 02:00 | Summer | 1.0479 | 1.4997 | 2.1641 | 2.1641 | 2.1641 | 2.1641 | 0.40582 | 0.66406 | 0.91001 | 1.0945 | 1.0945 | 1.0945 | 1.5814 | 2.0407 | 2.3417 | 2.5001 | 2.8169 | 3.1337 | 0.49918 | 0.98521 | 1.1823 | 1.1823 | 1.1823 | 1.1823 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-11-12 03:00 | Summer | 1.0669 | 1.527 | 2.2035 | 2.2035 | 2.2035 | 2.2035 | 0.38581 | 0.63133 | 0.86515 | 1.0405 | 1.0405 | 1.0405 | 1.5814 | 2.0407 | 2.3417 | 2.5001 | 2.8169 | 3.1337 | 0.55633 | 1.098 | 1.3176 | 1.3176 | 1.3176 | 1.3176 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-11-12 04:00 | Summer | 1.0669 | 1.527 | 2.2035 | 2.2035 | 2.2035 | 2.2035 | 0.41153 | 0.67342 | 0.92283 | 1.1099 | 1.1099 | 1.1099 | 1.6098 | 2.0774 | 2.3837 | 2.545 | 2.8675 | 3.1899 | 0.56395 | 1.1131 | 1.3357 | 1.3357 | 1.3357 | 1.3357 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-11-12 05:00 | Summer | 1.0669 | 1.527 | 2.2035 | 2.2035 | 2.2035 | 2.2035 | 0.4001 | 0.65471 | 0.89719 | 1.0791 | 1.0791 | 1.0791 | 1.6576 | 2.1391 | 2.4545 | 2.6205 | 2.9526 | 3.2847 | 0.62873 | 1.2409 | 1.4891 | 1.4891 | 1.4891 | 1.4891 | 0.62873 | 0.73138 | 0.73138 | 0.73138 | 0.73138 | 0.73138
2020-11-12 06:00 | Summer | 1.4305 | 2.0473 | 2.9543 | 2.9543 | 2.9543 | 2.9543 | 0.60873 | 0.9961 | 1.365 | 1.6417 | 1.6417 | 1.6417 | 1.8087 | 2.3341 | 2.6784 | 2.8595 | 3.2219 | 3.5842 | 0.63635 | 1.256 | 1.5072 | 1.5072 | 1.5072 | 1.5072 | 0.77464 | 0.90112 | 0.90112 | 0.90112 | 0.90112 | 0.90112
2020-11-12 07:00 | Summer | 1.8862 | 2.6995 | 3.8954 | 3.8954 | 3.8954 | 3.8954 | 0.76877 | 1.258 | 1.7239 | 2.0733 | 2.0733 | 2.0733 | 2.3054 | 2.975 | 3.4138 | 3.6447 | 4.1065 | 4.5683 | 1.2346 | 2.4367 | 2.9241 | 2.9241 | 2.9241 | 2.9241 | 1.1041 | 1.2844 | 1.2844 | 1.2844 | 1.2844 | 1.2844
2020-11-12 08:00 | Summer | 2.553 | 3.6538 | 5.2726 | 5.2726 | 5.2726 | 5.2726 | 0.80878 | 1.3235 | 1.8136 | 2.1812 | 2.1812 | 2.1812 | 2.4578 | 3.1717 | 3.6395 | 3.8856 | 4.378 | 4.8704 | 1.0403 | 2.0532 | 2.4638 | 2.4638 | 2.4638 | 2.4638 | 1.2765 | 1.4849 | 1.4849 | 1.4849 | 1.4849 | 1.4849
2020-11-12 09:00 | Summer | 2.6483 | 3.7901 | 5.4693 | 5.4693 | 5.4693 | 5.4693 | 1.066 | 1.7443 | 2.3904 | 2.8749 | 2.8749 | 2.8749 | 2.6674 | 3.4422 | 3.9498 | 4.217 | 4.7513 | 5.2857 | 1.006 | 1.9855 | 2.3826 | 2.3826 | 2.3826 | 2.3826 | 1.3718 | 1.5957 | 1.5957 | 1.5957 | 1.5957 | 1.5957
2020-11-12 10:00 | Summer | 2.6102 | 3.7356 | 5.3906 | 5.3906 | 5.3906 | 5.3906 | 0.93488 | 1.5298 | 2.0964 | 2.5213 | 2.5213 | 2.5213 | 2.7817 | 3.5897 | 4.1191 | 4.3977 | 4.955 | 5.5122 | 0.96787 | 1.9103 | 2.2923 | 2.2923 | 2.2923 | 2.2923 | 1.448 | 1.6844 | 1.6844 | 1.6844 | 1.6844 | 1.6844
2020-11-12 11:00 | Summer | 2.6674 | 3.8174 | 5.5087 | 5.5087 | 5.5087 | 5.5087 | 1.0488 | 1.7163 | 2.3519 | 2.8287 | 2.8287 | 2.8287 | 2.8769 | 3.7126 | 4.2601 | 4.5483 | 5.1246 | 5.701 | 1.1432 | 2.2562 | 2.7075 | 2.7075 | 2.7075 | 2.7075 | 1.467 | 1.7066 | 1.7066 | 1.7066 | 1.7066 | 1.7066
2020-11-12 12:00 | Summer | 2.6674 | 3.8174 | 5.5087 | 5.5087 | 5.5087 | 5.5087 | 0.99454 | 1.6274 | 2.2302 | 2.6822 | 2.6822 | 2.6822 | 2.9722 | 3.8356 | 4.4012 | 4.6989 | 5.2943 | 5.8898 | 1.0441 | 2.0607 | 2.4728 | 2.4728 | 2.4728 | 2.4728 | 1.4861 | 1.7287 | 1.7287 | 1.7287 | 1.7287 | 1.7287
2020-11-12 13:00 | Summer | 2.7055 | 3.8719 | 5.5874 | 5.5874 | 5.5874 | 5.5874 | 1.186 | 1.9408 | 2.6596 | 3.1987 | 3.1987 | 3.1987 | 2.896 | 3.7372 | 4.2884 | 4.5784 | 5.1586 | 5.7387 | 1.105 | 2.181 | 2.6172 | 2.6172 | 2.6172 | 2.6172 | 1.5433 | 1.7952 | 1.7952 | 1.7952 | 1.7952 | 1.7952
2020-11-12 14:00 | Summer | 2.6102 | 3.7356 | 5.3906 | 5.3906 | 5.3906 | 5.3906 | 1.0231 | 1.6742 | 2.2943 | 2.7593 | 2.7593 | 2.7593 | 2.9722 | 3.8356 | 4.4012 | 4.6989 | 5.2943 | 5.8898 | 1.1241 | 2.2186 | 2.6623 | 2.6623 | 2.6623 | 2.6623 | 1.4861 | 1.7287 | 1.7287 | 1.7287 | 1.7287 | 1.7287
2020-11-12 15:00 | Summer | 2.6483 | 3.7901 | 5.4693 | 5.4693 | 5.4693 | 5.4693 | 1.0203 | 1.6695 | 2.2879 | 2.7516 | 2.7516 | 2.7516 | 2.9722 | 3.8356 | 4.4012 | 4.6989 | 5.2943 | 5.8898 | 1.1546 | 2.2788 | 2.7345 | 2.7345 | 2.7345 | 2.7345 | 1.467 | 1.7066 | 1.7066 | 1.7066 | 1.7066 | 1.7066
2020-11-12 16:00 | Summer | 2.5149 | 3.5993 | 5.1939 | 5.1939 | 5.1939 | 5.1939 | 1.0374 | 1.6976 | 2.3263 | 2.7979 | 2.7979 | 2.7979 | 2.8007 | 3.6143 | 4.1473 | 4.4278 | 4.9889 | 5.55 | 1.1089 | 2.1885 | 2.6262 | 2.6262 | 2.6262 | 2.6262 | 1.4289 | 1.6622 | 1.6622 | 1.6622 | 1.6622 | 1.6622
2020-11-12 17:00 | Summer | 2.3063 | 3.3007 | 4.763 | 4.763 | 4.763 | 4.763 | 0.89451 | 1.4638 | 2.0059 | 2.4125 | 2.4125 | 2.4125 | 2.7626 | 3.5651 | 4.0909 | 4.3676 | 4.921 | 5.4745 | 1.0936 | 2.1585 | 2.5901 | 2.5901 | 2.5901 | 2.5901 | 1.2384 | 1.4406 | 1.4406 | 1.4406 | 1.4406 | 1.4406
2020-11-12 18:00 | Summer | 1.7664 | 2.528 | 3.6479 | 3.6479 | 3.6479 | 3.6479 | 0.70967 | 1.1613 | 1.5914 | 1.914 | 1.914 | 1.914 | 2.6102 | 3.3684 | 3.8652 | 4.1266 | 4.6495 | 5.1724 | 0.87261 | 1.7222 | 2.0667 | 2.0667 | 2.0667 | 2.0667 | 0.91178 | 1.0606 | 1.0606 | 1.0606 | 1.0606 | 1.0606
2020-11-12 19:00 | Summer | 1.2765 | 1.8269 | 2.6363 | 2.6363 | 2.6363 | 2.6363 | 0.57443 | 0.93998 | 1.2881 | 1.5492 | 1.5492 | 1.5492 | 2.3446 | 3.0257 | 3.4719 | 3.7067 | 4.1764 | 4.6461 | 0.85736 | 1.6922 | 2.0306 | 2.0306 | 2.0306 | 2.0306 | 0.68614 | 0.79816 | 0.79816 | 0.79816 | 0.79816 | 0.79816
2020-11-12 20:00 | Summer | 1.1622 | 1.6633 | 2.4002 | 2.4002 | 2.4002 | 2.4002 | 0.50584 | 0.82774 | 1.1343 | 1.3642 | 1.3642 | 1.3642 | 2.2482 | 2.9013 | 3.3291 | 3.5543 | 4.0047 | 4.4551 | 0.85736 | 1.6922 | 2.0306 | 2.0306 | 2.0306 | 2.0306 | 0.62873 | 0.73138 | 0.73138 | 0.73138 | 0.73138 | 0.73138
2020-11-12 21:00 | Summer | 1.1459 | 1.64 | 2.3665 | 2.3665 | 2.3665 | 2.3665 | 0.54871 | 0.89789 | 1.2304 | 1.4799 | 1.4799 | 1.4799 | 2.1339 | 2.7537 | 3.1598 | 3.3736 | 3.8011 | 4.2285 | 0.81545 | 1.6094 | 1.9313 | 1.9313 | 1.9313 | 1.9313 | 0.57158 | 0.6649 | 0.6649 | 0.6649 | 0.6649 | 0.6649
2020-11-12 22:00 | Summer | 1.0342 | 1.4801 | 2.1358 | 2.1358 | 2.1358 | 2.1358 | 0.52299 | 0.8558 | 1.1728 | 1.4105 | 1.4105 | 1.4105 | 2.0005 | 2.5816 | 2.9624 | 3.1627 | 3.5635 | 3.9643 | 0.80021 | 1.5794 | 1.8952 | 1.8952 | 1.8952 | 1.8952 | 0.51488 | 0.59894 | 0.59894 | 0.59894 | 0.59894 | 0.59894
2020-11-12 23:00 | Summer | 1.0288 | 1.4724 | 2.1248 | 2.1248 | 2.1248 | 2.1248 | 0.4001 | 0.65471 | 0.89719 | 1.0791 | 1.0791 | 1.0791 | 1.7909 | 2.3112 | 2.652 | 2.8314 | 3.1902 | 3.549 | 0.78877 | 1.5568 | 1.8681 | 1.8681 | 1.8681 | 1.8681 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-11-13 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.44868 | 0.73421 | 1.0061 | 1.2101 | 1.2101 | 1.2101 | 1.6576 | 2.1391 | 2.4545 | 2.6205 | 2.9526 | 3.2847 | 0.85736 | 1.6922 | 2.0306 | 2.0306 | 2.0306 | 2.0306 | 0.45734 | 0.53201 | 0.53201 | 0.53201 | 0.53201 | 0.53201
2020-11-13 01:00 | Summer | 0.98697 | 1.4125 | 2.0383 | 2.0383 | 2.0383 | 2.0383 | 0.38009 | 0.62197 | 0.85233 | 1.0251 | 1.0251 | 1.0251 | 1.6227 | 2.094 | 2.4028 | 2.5654 | 2.8904 | 3.2155 | 0.6516 | 1.286 | 1.5433 | 1.5433 | 1.5433 | 1.5433 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-11-13 02:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.4001 | 0.65471 | 0.89719 | 1.0791 | 1.0791 | 1.0791 | 1.6004 | 2.0653 | 2.3699 | 2.5302 | 2.8508 | 3.1714 | 0.54366 | 1.073 | 1.2876 | 1.2876 | 1.2876 | 1.2876 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-11-13 03:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.38581 | 0.63133 | 0.86515 | 1.0405 | 1.0405 | 1.0405 | 1.6004 | 2.0653 | 2.3699 | 2.5302 | 2.8508 | 3.1714 | 0.60587 | 1.1958 | 1.435 | 1.435 | 1.435 | 1.435 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-11-13 04:00 | Summer | 1.1181 | 1.6002 | 2.3091 | 2.3091 | 2.3091 | 2.3091 | 0.43725 | 0.7155 | 0.98051 | 1.1793 | 1.1793 | 1.1793 | 1.6576 | 2.1391 | 2.4545 | 2.6205 | 2.9526 | 3.2847 | 0.60206 | 1.1883 | 1.4259 | 1.4259 | 1.4259 | 1.4259 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-11-13 05:00 | Summer | 1.1813 | 1.6906 | 2.4396 | 2.4396 | 2.4396 | 2.4396 | 0.42296 | 0.69212 | 0.94846 | 1.1407 | 1.1407 | 1.1407 | 1.7719 | 2.2866 | 2.6238 | 2.8013 | 3.1562 | 3.5112 | 0.6173 | 1.2184 | 1.462 | 1.462 | 1.462 | 1.462 | 0.64779 | 0.75355 | 0.75355 | 0.75355 | 0.75355 | 0.75355
2020-11-13 06:00 | Summer | 1.3485 | 1.93 | 2.785 | 2.785 | 2.785 | 2.785 | 0.73733 | 1.2065 | 1.6534 | 1.9886 | 1.9886 | 1.9886 | 1.9815 | 2.557 | 2.9341 | 3.1326 | 3.5296 | 3.9265 | 0.72781 | 1.4365 | 1.7238 | 1.7238 | 1.7238 | 1.7238 | 0.80021 | 0.93085 | 0.93085 | 0.93085 | 0.93085 | 0.93085
2020-11-13 07:00 | Summer | 1.7739 | 2.5387 | 3.6635 | 3.6635 | 3.6635 | 3.6635 | 0.69446 | 1.1364 | 1.5573 | 1.8729 | 1.8729 | 1.8729 | 2.1922 | 2.829 | 3.2462 | 3.4658 | 3.9049 | 4.3441 | 1.0974 | 2.166 | 2.5992 | 2.5992 | 2.5992 | 2.5992 | 0.97168 | 1.1303 | 1.1303 | 1.1303 | 1.1303 | 1.1303
2020-11-13 08:00 | Summer | 2.0577 | 2.9449 | 4.2495 | 4.2495 | 4.2495 | 4.2495 | 0.82592 | 1.3515 | 1.8521 | 2.2275 | 2.2275 | 2.2275 | 2.553 | 3.2946 | 3.7805 | 4.0362 | 4.5477 | 5.0591 | 1.0708 | 2.1133 | 2.536 | 2.536 | 2.536 | 2.536 | 1.1813 | 1.3741 | 1.3741 | 1.3741 | 1.3741 | 1.3741
2020-11-13 09:00 | Summer | 2.2291 | 3.1903 | 4.6037 | 4.6037 | 4.6037 | 4.6037 | 0.86308 | 1.4123 | 1.9354 | 2.3277 | 2.3277 | 2.3277 | 2.5721 | 3.3192 | 3.8087 | 4.0664 | 4.5816 | 5.0969 | 1.0555 | 2.0832 | 2.4999 | 2.4999 | 2.4999 | 2.4999 | 1.2765 | 1.4849 | 1.4849 | 1.4849 | 1.4849 | 1.4849
2020-11-13 10:00 | Summer | 2.2673 | 3.2448 | 4.6824 | 4.6824 | 4.6824 | 4.6824 | 1.0517 | 1.721 | 2.3584 | 2.8364 | 2.8364 | 2.8364 | 2.6864 | 3.4668 | 3.978 | 4.2471 | 4.7853 | 5.3234 | 1.1241 | 2.2186 | 2.6623 | 2.6623 | 2.6623 | 2.6623 | 1.3908 | 1.6179 | 1.6179 | 1.6179 | 1.6179 | 1.6179
2020-11-13 11:00 | Summer | 2.3244 | 3.3266 | 4.8004 | 4.8004 | 4.8004 | 4.8004 | 1.0316 | 1.688 | 2.3132 | 2.7821 | 2.7821 | 2.7821 | 2.8198 | 3.6389 | 4.1755 | 4.4579 | 5.0228 | 5.5877 | 1.0822 | 2.1359 | 2.5631 | 2.5631 | 2.5631 | 2.5631 | 1.4861 | 1.7287 | 1.7287 | 1.7287 | 1.7287 | 1.7287
2020-11-13 12:00 | Summer | 2.4006 | 3.4357 | 4.9578 | 4.9578 | 4.9578 | 4.9578 | 0.9631 | 1.576 | 2.1597 | 2.5975 | 2.5975 | 2.5975 | 2.8237 | 3.644 | 4.1813 | 4.4642 | 5.0299 | 5.5955 | 0.9793 | 1.9328 | 2.3194 | 2.3194 | 2.3194 | 2.3194 | 1.467 | 1.7066 | 1.7066 | 1.7066 | 1.7066 | 1.7066
2020-11-13 13:00 | Summer | 2.3435 | 3.3539 | 4.8398 | 4.8398 | 4.8398 | 4.8398 | 1.0546 | 1.7256 | 2.3648 | 2.8441 | 2.8441 | 2.8441 | 3.0865 | 3.9831 | 4.5705 | 4.8796 | 5.498 | 6.1163 | 0.97168 | 1.9178 | 2.3013 | 2.3013 | 2.3013 | 2.3013 | 1.4289 | 1.6622 | 1.6622 | 1.6622 | 1.6622 | 1.6622
2020-11-13 14:00 | Summer | 2.3054 | 3.2993 | 4.7611 | 4.7611 | 4.7611 | 4.7611 | 0.94024 | 1.5386 | 2.1084 | 2.5358 | 2.5358 | 2.5358 | 2.9341 | 3.7864 | 4.3448 | 4.6387 | 5.2265 | 5.8142 | 0.92976 | 1.8351 | 2.2021 | 2.2021 | 2.2021 | 2.2021 | 1.3908 | 1.6179 | 1.6179 | 1.6179 | 1.6179 | 1.6179
2020-11-13 15:00 | Summer | 2.2641 | 3.2403 | 4.6759 | 4.6759 | 4.6759 | 4.6759 | 0.84307 | 1.3796 | 1.8905 | 2.2737 | 2.2737 | 2.2737 | 2.9531 | 3.811 | 4.373 | 4.6688 | 5.2604 | 5.852 | 1.025 | 2.0231 | 2.4277 | 2.4277 | 2.4277 | 2.4277 | 1.3146 | 1.5293 | 1.5293 | 1.5293 | 1.5293 | 1.5293
2020-11-13 16:00 | Summer | 2.191 | 3.1357 | 4.525 | 4.525 | 4.525 | 4.525 | 1.0631 | 1.7397 | 2.384 | 2.8672 | 2.8672 | 2.8672 | 2.8579 | 3.688 | 4.2319 | 4.5182 | 5.0907 | 5.6632 | 0.97168 | 1.9178 | 2.3013 | 2.3013 | 2.3013 | 2.3013 | 1.2956 | 1.5071 | 1.5071 | 1.5071 | 1.5071 | 1.5071
2020-11-13 17:00 | Summer | 2.1481 | 3.0742 | 4.4362 | 4.4362 | 4.4362 | 4.4362 | 0.8345 | 1.3655 | 1.8713 | 2.2506 | 2.2506 | 2.2506 | 2.7817 | 3.5897 | 4.1191 | 4.3977 | 4.955 | 5.5122 | 0.94882 | 1.8727 | 2.2472 | 2.2472 | 2.2472 | 2.2472 | 1.2387 | 1.441 | 1.441 | 1.441 | 1.441 | 1.441
2020-11-13 18:00 | Summer | 1.829 | 2.6177 | 3.7774 | 3.7774 | 3.7774 | 3.7774 | 0.70975 | 1.1614 | 1.5916 | 1.9142 | 1.9142 | 1.9142 | 2.4768 | 3.1963 | 3.6677 | 3.9158 | 4.4119 | 4.9081 | 0.79258 | 1.5643 | 1.8772 | 1.8772 | 1.8772 | 1.8772 | 0.83778 | 0.97456 | 0.97456 | 0.97456 | 0.97456 | 0.97456
2020-11-13 19:00 | Summer | 1.5052 | 2.1541 | 3.1085 | 3.1085 | 3.1085 | 3.1085 | 0.48298 | 0.79033 | 1.083 | 1.3026 | 1.3026 | 1.3026 | 2.2198 | 2.8646 | 3.2871 | 3.5095 | 3.9541 | 4.3988 | 0.83831 | 1.6546 | 1.9855 | 1.9855 | 1.9855 | 1.9855 | 0.70494 | 0.82004 | 0.82004 | 0.82004 | 0.82004 | 0.82004
2020-11-13 20:00 | Summer | 1.3346 | 1.91 | 2.7562 | 2.7562 | 2.7562 | 2.7562 | 0.52585 | 0.86048 | 1.1792 | 1.4182 | 1.4182 | 1.4182 | 2.0767 | 2.68 | 3.0752 | 3.2832 | 3.6992 | 4.1153 | 0.77353 | 1.5267 | 1.832 | 1.832 | 1.832 | 1.832 | 0.59063 | 0.68706 | 0.68706 | 0.68706 | 0.68706 | 0.68706
2020-11-13 21:00 | Summer | 1.2194 | 1.7451 | 2.5183 | 2.5183 | 2.5183 | 2.5183 | 0.48012 | 0.78565 | 1.0766 | 1.2949 | 1.2949 | 1.2949 | 2.0005 | 2.5816 | 2.9624 | 3.1627 | 3.5635 | 3.9643 | 0.79258 | 1.5643 | 1.8772 | 1.8772 | 1.8772 | 1.8772 | 0.57158 | 0.6649 | 0.6649 | 0.6649 | 0.6649 | 0.6649
2020-11-13 22:00 | Summer | 1.2003 | 1.7178 | 2.4789 | 2.4789 | 2.4789 | 2.4789 | 0.44868 | 0.73421 | 1.0061 | 1.2101 | 1.2101 | 1.2101 | 1.9434 | 2.5079 | 2.8777 | 3.0724 | 3.4617 | 3.851 | 0.71229 | 1.4058 | 1.687 | 1.687 | 1.687 | 1.687 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-11-13 23:00 | Summer | 1.1432 | 1.636 | 2.3609 | 2.3609 | 2.3609 | 2.3609 | 0.36866 | 0.60327 | 0.8267 | 0.99427 | 0.99427 | 0.99427 | 1.829 | 2.3603 | 2.7084 | 2.8916 | 3.2581 | 3.6245 | 0.74686 | 1.4741 | 1.7689 | 1.7689 | 1.7689 | 1.7689 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-11-14 | Summer | 1.086 | 1.5542 | 2.2428 | 2.2428 | 2.2428 | 2.2428 | 0.39724 | 0.65003 | 0.89079 | 1.0713 | 1.0713 | 1.0713 | 1.6766 | 2.1636 | 2.4827 | 2.6507 | 2.9865 | 3.3224 | 0.6516 | 1.286 | 1.5433 | 1.5433 | 1.5433 | 1.5433 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-11-14 01:00 | Summer | 1.1241 | 1.6088 | 2.3215 | 2.3215 | 2.3215 | 2.3215 | 0.31722 | 0.51909 | 0.71134 | 0.85553 | 0.85553 | 0.85553 | 1.5623 | 2.0161 | 2.3135 | 2.4699 | 2.7829 | 3.0959 | 0.62873 | 1.2409 | 1.4891 | 1.4891 | 1.4891 | 1.4891 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-11-14 02:00 | Summer | 1.1622 | 1.6633 | 2.4002 | 2.4002 | 2.4002 | 2.4002 | 0.34008 | 0.5565 | 0.76261 | 0.9172 | 0.9172 | 0.9172 | 1.5623 | 2.0161 | 2.3135 | 2.4699 | 2.7829 | 3.0959 | 0.56827 | 1.1216 | 1.3459 | 1.3459 | 1.3459 | 1.3459 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-11-14 03:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.38009 | 0.62197 | 0.85233 | 1.0251 | 1.0251 | 1.0251 | 1.5316 | 1.9765 | 2.268 | 2.4214 | 2.7282 | 3.0351 | 0.58301 | 1.1507 | 1.3808 | 1.3808 | 1.3808 | 1.3808 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-11-14 04:00 | Summer | 1.0479 | 1.4997 | 2.1641 | 2.1641 | 2.1641 | 2.1641 | 0.38581 | 0.63133 | 0.86515 | 1.0405 | 1.0405 | 1.0405 | 1.5577 | 2.0101 | 2.3066 | 2.4626 | 2.7747 | 3.0867 | 0.51442 | 1.0153 | 1.2184 | 1.2184 | 1.2184 | 1.2184 | 0.46486 | 0.54076 | 0.54076 | 0.54076 | 0.54076 | 0.54076
2020-11-14 05:00 | Summer | 1.0479 | 1.4997 | 2.1641 | 2.1641 | 2.1641 | 2.1641 | 0.36581 | 0.59859 | 0.82029 | 0.98657 | 0.98657 | 0.98657 | 1.6195 | 2.0899 | 2.3981 | 2.5603 | 2.8847 | 3.2092 | 0.56776 | 1.1206 | 1.3447 | 1.3447 | 1.3447 | 1.3447 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-11-14 06:00 | Summer | 1.086 | 1.5542 | 2.2428 | 2.2428 | 2.2428 | 2.2428 | 0.39724 | 0.65003 | 0.89079 | 1.0713 | 1.0713 | 1.0713 | 1.6576 | 2.1391 | 2.4545 | 2.6205 | 2.9526 | 3.2847 | 0.60206 | 1.1883 | 1.4259 | 1.4259 | 1.4259 | 1.4259 | 0.49505 | 0.57587 | 0.57587 | 0.57587 | 0.57587 | 0.57587
2020-11-14 07:00 | Summer | 1.2956 | 1.8542 | 2.6756 | 2.6756 | 2.6756 | 2.6756 | 0.42582 | 0.6968 | 0.95487 | 1.1484 | 1.1484 | 1.1484 | 1.7909 | 2.3112 | 2.652 | 2.8314 | 3.1902 | 3.549 | 0.80021 | 1.5794 | 1.8952 | 1.8952 | 1.8952 | 1.8952 | 0.53347 | 0.62057 | 0.62057 | 0.62057 | 0.62057 | 0.62057
2020-11-14 08:00 | Summer | 1.3337 | 1.9087 | 2.7543 | 2.7543 | 2.7543 | 2.7543 | 0.37379 | 0.61166 | 0.8382 | 1.0081 | 1.0081 | 1.0081 | 1.9436 | 2.5082 | 2.8781 | 3.0728 | 3.4622 | 3.8515 | 0.75448 | 1.4891 | 1.7869 | 1.7869 | 1.7869 | 1.7869 | 0.55252 | 0.64273 | 0.64273 | 0.64273 | 0.64273 | 0.64273
2020-11-14 09:00 | Summer | 1.3527 | 1.936 | 2.7937 | 2.7937 | 2.7937 | 2.7937 | 0.48584 | 0.79501 | 1.0895 | 1.3103 | 1.3103 | 1.3103 | 2.0767 | 2.68 | 3.0752 | 3.2832 | 3.6992 | 4.1153 | 0.75829 | 1.4966 | 1.796 | 1.796 | 1.796 | 1.796 | 0.60968 | 0.70922 | 0.70922 | 0.70922 | 0.70922 | 0.70922
2020-11-14 10:00 | Summer | 1.3718 | 1.9632 | 2.833 | 2.833 | 2.833 | 2.833 | 0.44011 | 0.72018 | 0.98691 | 1.187 | 1.187 | 1.187 | 2.172 | 2.8029 | 3.2163 | 3.4338 | 3.8689 | 4.3041 | 0.75448 | 1.4891 | 1.7869 | 1.7869 | 1.7869 | 1.7869 | 0.64779 | 0.75355 | 0.75355 | 0.75355 | 0.75355 | 0.75355
2020-11-14 11:00 | Summer | 1.3908 | 1.9905 | 2.8724 | 2.8724 | 2.8724 | 2.8724 | 0.46869 | 0.76695 | 1.051 | 1.264 | 1.264 | 1.264 | 2.191 | 2.8275 | 3.2445 | 3.4639 | 3.9029 | 4.3418 | 0.73543 | 1.4515 | 1.7418 | 1.7418 | 1.7418 | 1.7418 | 0.66684 | 0.77571 | 0.77571 | 0.77571 | 0.77571 | 0.77571
2020-11-14 12:00 | Summer | 1.3337 | 1.9087 | 2.7543 | 2.7543 | 2.7543 | 2.7543 | 0.49155 | 0.80436 | 1.1023 | 1.3257 | 1.3257 | 1.3257 | 2.2291 | 2.8767 | 3.3009 | 3.5242 | 3.9708 | 4.4173 | 0.69351 | 1.3688 | 1.6425 | 1.6425 | 1.6425 | 1.6425 | 0.64779 | 0.75355 | 0.75355 | 0.75355 | 0.75355 | 0.75355
2020-11-14 13:00 | Summer | 1.4099 | 2.0178 | 2.9117 | 2.9117 | 2.9117 | 2.9117 | 0.52299 | 0.8558 | 1.1728 | 1.4105 | 1.4105 | 1.4105 | 2.1725 | 2.8036 | 3.2171 | 3.4347 | 3.8699 | 4.3051 | 0.68208 | 1.3462 | 1.6155 | 1.6155 | 1.6155 | 1.6155 | 0.60968 | 0.70922 | 0.70922 | 0.70922 | 0.70922 | 0.70922
2020-11-14 14:00 | Summer | 1.3718 | 1.9632 | 2.833 | 2.833 | 2.833 | 2.833 | 0.5087 | 0.83242 | 1.1407 | 1.3719 | 1.3719 | 1.3719 | 2.2482 | 2.9013 | 3.3291 | 3.5543 | 4.0047 | 4.4551 | 0.71256 | 1.4064 | 1.6877 | 1.6877 | 1.6877 | 1.6877 | 0.60968 | 0.70922 | 0.70922 | 0.70922 | 0.70922 | 0.70922
2020-11-14 15:00 | Summer | 1.3718 | 1.9632 | 2.833 | 2.833 | 2.833 | 2.833 | 0.52013 | 0.85112 | 1.1664 | 1.4028 | 1.4028 | 1.4028 | 2.2101 | 2.8521 | 3.2727 | 3.4941 | 3.9368 | 4.3796 | 0.75448 | 1.4891 | 1.7869 | 1.7869 | 1.7869 | 1.7869 | 0.59063 | 0.68706 | 0.68706 | 0.68706 | 0.68706 | 0.68706
2020-11-14 16:00 | Summer | 1.3718 | 1.9632 | 2.833 | 2.833 | 2.833 | 2.833 | 0.49155 | 0.80436 | 1.1023 | 1.3257 | 1.3257 | 1.3257 | 2.172 | 2.8029 | 3.2163 | 3.4338 | 3.8689 | 4.3041 | 0.87642 | 1.7298 | 2.0757 | 2.0757 | 2.0757 | 2.0757 | 0.60968 | 0.70922 | 0.70922 | 0.70922 | 0.70922 | 0.70922
2020-11-14 17:00 | Summer | 1.3718 | 1.9632 | 2.833 | 2.833 | 2.833 | 2.833 | 0.47726 | 0.78098 | 1.0702 | 1.2872 | 1.2872 | 1.2872 | 2.1529 | 2.7783 | 3.1881 | 3.4037 | 3.835 | 4.2663 | 0.88404 | 1.7448 | 2.0938 | 2.0938 | 2.0938 | 2.0938 | 0.56916 | 0.66209 | 0.66209 | 0.66209 | 0.66209 | 0.66209
2020-11-14 18:00 | Summer | 1.3908 | 1.9905 | 2.8724 | 2.8724 | 2.8724 | 2.8724 | 0.46297 | 0.75759 | 1.0382 | 1.2486 | 1.2486 | 1.2486 | 2.0577 | 2.6554 | 3.047 | 3.2531 | 3.6653 | 4.0775 | 0.88404 | 1.7448 | 2.0938 | 2.0938 | 2.0938 | 2.0938 | 0.57158 | 0.6649 | 0.6649 | 0.6649 | 0.6649 | 0.6649
2020-11-14 19:00 | Summer | 1.3527 | 1.936 | 2.7937 | 2.7937 | 2.7937 | 2.7937 | 0.4001 | 0.65471 | 0.89719 | 1.0791 | 1.0791 | 1.0791 | 1.9626 | 2.5327 | 2.9062 | 3.1028 | 3.496 | 3.8892 | 0.84196 | 1.6618 | 1.9941 | 1.9941 | 1.9941 | 1.9941 | 0.57158 | 0.6649 | 0.6649 | 0.6649 | 0.6649 | 0.6649
2020-11-14 20:00 | Summer | 1.264 | 1.809 | 2.6105 | 2.6105 | 2.6105 | 2.6105 | 0.42011 | 0.68744 | 0.94205 | 1.133 | 1.133 | 1.133 | 1.9815 | 2.557 | 2.9341 | 3.1326 | 3.5296 | 3.9265 | 0.86498 | 1.7072 | 2.0486 | 2.0486 | 2.0486 | 2.0486 | 0.55252 | 0.64273 | 0.64273 | 0.64273 | 0.64273 | 0.64273
2020-11-14 21:00 | Summer | 1.1685 | 1.6723 | 2.4132 | 2.4132 | 2.4132 | 2.4132 | 0.38009 | 0.62197 | 0.85233 | 1.0251 | 1.0251 | 1.0251 | 1.9434 | 2.5079 | 2.8777 | 3.0724 | 3.4617 | 3.851 | 0.8345 | 1.647 | 1.9764 | 1.9764 | 1.9764 | 1.9764 | 0.55252 | 0.64273 | 0.64273 | 0.64273 | 0.64273 | 0.64273
2020-11-14 22:00 | Summer | 1.1293 | 1.6162 | 2.3323 | 2.3323 | 2.3323 | 2.3323 | 0.33151 | 0.54247 | 0.74339 | 0.89407 | 0.89407 | 0.89407 | 1.8481 | 2.3849 | 2.7366 | 2.9218 | 3.292 | 3.6622 | 0.80402 | 1.5869 | 1.9042 | 1.9042 | 1.9042 | 1.9042 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-11-14 23:00 | Summer | 1.1091 | 1.5873 | 2.2906 | 2.2906 | 2.2906 | 2.2906 | 0.38581 | 0.63133 | 0.86515 | 1.0405 | 1.0405 | 1.0405 | 1.7338 | 2.2374 | 2.5674 | 2.741 | 3.0884 | 3.4357 | 0.74686 | 1.4741 | 1.7689 | 1.7689 | 1.7689 | 1.7689 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-11-15 | Summer | 1.086 | 1.5542 | 2.2428 | 2.2428 | 2.2428 | 2.2428 | 0.3458 | 0.56585 | 0.77543 | 0.93261 | 0.93261 | 0.93261 | 1.6385 | 2.1145 | 2.4263 | 2.5904 | 2.9187 | 3.2469 | 0.61349 | 1.2108 | 1.453 | 1.453 | 1.453 | 1.453 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-11-15 01:00 | Summer | 1.105 | 1.5815 | 2.2822 | 2.2822 | 2.2822 | 2.2822 | 0.34866 | 0.57053 | 0.78184 | 0.94032 | 0.94032 | 0.94032 | 1.5623 | 2.0161 | 2.3135 | 2.4699 | 2.7829 | 3.0959 | 0.60968 | 1.2033 | 1.444 | 1.444 | 1.444 | 1.444 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-11-15 02:00 | Summer | 1.1241 | 1.6088 | 2.3215 | 2.3215 | 2.3215 | 2.3215 | 0.42868 | 0.70147 | 0.96128 | 1.1561 | 1.1561 | 1.1561 | 1.5433 | 1.9915 | 2.2852 | 2.4398 | 2.749 | 3.0581 | 0.5792 | 1.1431 | 1.3718 | 1.3718 | 1.3718 | 1.3718 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-11-15 03:00 | Summer | 1.105 | 1.5815 | 2.2822 | 2.2822 | 2.2822 | 2.2822 | 0.37724 | 0.6173 | 0.84593 | 1.0174 | 1.0174 | 1.0174 | 1.5052 | 1.9424 | 2.2288 | 2.3796 | 2.6811 | 2.9826 | 0.49918 | 0.98521 | 1.1823 | 1.1823 | 1.1823 | 1.1823 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-11-15 04:00 | Summer | 1.105 | 1.5815 | 2.2822 | 2.2822 | 2.2822 | 2.2822 | 0.41725 | 0.68277 | 0.93565 | 1.1253 | 1.1253 | 1.1253 | 1.5347 | 1.9805 | 2.2726 | 2.4263 | 2.7337 | 3.0412 | 0.53728 | 1.0604 | 1.2725 | 1.2725 | 1.2725 | 1.2725 | 0.45427 | 0.52844 | 0.52844 | 0.52844 | 0.52844 | 0.52844
2020-11-15 05:00 | Summer | 1.1241 | 1.6088 | 2.3215 | 2.3215 | 2.3215 | 2.3215 | 0.36295 | 0.59391 | 0.81388 | 0.97886 | 0.97886 | 0.97886 | 1.6385 | 2.1145 | 2.4263 | 2.5904 | 2.9187 | 3.2469 | 0.54109 | 1.0679 | 1.2815 | 1.2815 | 1.2815 | 1.2815 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-11-15 06:00 | Summer | 1.105 | 1.5815 | 2.2822 | 2.2822 | 2.2822 | 2.2822 | 0.34294 | 0.56118 | 0.76902 | 0.92491 | 0.92491 | 0.92491 | 1.6571 | 2.1384 | 2.4537 | 2.6197 | 2.9517 | 3.2836 | 0.54109 | 1.0679 | 1.2815 | 1.2815 | 1.2815 | 1.2815 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-11-15 07:00 | Summer | 1.0669 | 1.527 | 2.2035 | 2.2035 | 2.2035 | 2.2035 | 0.45154 | 0.73889 | 1.0125 | 1.2178 | 1.2178 | 1.2178 | 1.7743 | 2.2897 | 2.6273 | 2.8051 | 3.1605 | 3.5159 | 0.68208 | 1.3462 | 1.6155 | 1.6155 | 1.6155 | 1.6155 | 0.47615 | 0.55388 | 0.55388 | 0.55388 | 0.55388 | 0.55388
2020-11-15 08:00 | Summer | 1.1813 | 1.6906 | 2.4396 | 2.4396 | 2.4396 | 2.4396 | 0.36295 | 0.59391 | 0.81388 | 0.97886 | 0.97886 | 0.97886 | 1.9434 | 2.5079 | 2.8777 | 3.0724 | 3.4617 | 3.851 | 0.70494 | 1.3913 | 1.6696 | 1.6696 | 1.6696 | 1.6696 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-11-15 09:00 | Summer | 1.2003 | 1.7178 | 2.4789 | 2.4789 | 2.4789 | 2.4789 | 0.43725 | 0.7155 | 0.98051 | 1.1793 | 1.1793 | 1.1793 | 2.114 | 2.7281 | 3.1305 | 3.3422 | 3.7657 | 4.1892 | 0.75067 | 1.4816 | 1.7779 | 1.7779 | 1.7779 | 1.7779 | 0.53347 | 0.62057 | 0.62057 | 0.62057 | 0.62057 | 0.62057
2020-11-15 10:00 | Summer | 1.2956 | 1.8542 | 2.6756 | 2.6756 | 2.6756 | 2.6756 | 0.35152 | 0.57521 | 0.78825 | 0.94803 | 0.94803 | 0.94803 | 2.2291 | 2.8765 | 3.3008 | 3.524 | 3.9706 | 4.4171 | 0.82307 | 1.6245 | 1.9494 | 1.9494 | 1.9494 | 1.9494 | 0.53256 | 0.61951 | 0.61951 | 0.61951 | 0.61951 | 0.61951
2020-11-15 11:00 | Summer | 1.3527 | 1.936 | 2.7937 | 2.7937 | 2.7937 | 2.7937 | 0.34866 | 0.57053 | 0.78184 | 0.94032 | 0.94032 | 0.94032 | 2.3244 | 2.9996 | 3.442 | 3.6748 | 4.1404 | 4.6061 | 0.77734 | 1.5342 | 1.8411 | 1.8411 | 1.8411 | 1.8411 | 0.55252 | 0.64273 | 0.64273 | 0.64273 | 0.64273 | 0.64273
2020-11-15 12:00 | Summer | 1.2956 | 1.8542 | 2.6756 | 2.6756 | 2.6756 | 2.6756 | 0.37152 | 0.60794 | 0.83311 | 1.002 | 1.002 | 1.002 | 2.3625 | 3.0488 | 3.4984 | 3.735 | 4.2083 | 4.6816 | 0.81545 | 1.6094 | 1.9313 | 1.9313 | 1.9313 | 1.9313 | 0.57158 | 0.6649 | 0.6649 | 0.6649 | 0.6649 | 0.6649
2020-11-15 13:00 | Summer | 1.3146 | 1.8814 | 2.715 | 2.715 | 2.715 | 2.715 | 0.44011 | 0.72018 | 0.98691 | 1.187 | 1.187 | 1.187 | 2.3051 | 2.9747 | 3.4134 | 3.6442 | 4.106 | 4.5678 | 0.70113 | 1.3838 | 1.6606 | 1.6606 | 1.6606 | 1.6606 | 0.56549 | 0.65781 | 0.65781 | 0.65781 | 0.65781 | 0.65781
2020-11-15 14:00 | Summer | 1.3527 | 1.936 | 2.7937 | 2.7937 | 2.7937 | 2.7937 | 0.42582 | 0.6968 | 0.95487 | 1.1484 | 1.1484 | 1.1484 | 2.3054 | 2.975 | 3.4138 | 3.6447 | 4.1065 | 4.5683 | 0.69351 | 1.3688 | 1.6425 | 1.6425 | 1.6425 | 1.6425 | 0.57158 | 0.6649 | 0.6649 | 0.6649 | 0.6649 | 0.6649
2020-11-15 15:00 | Summer | 1.3337 | 1.9087 | 2.7543 | 2.7543 | 2.7543 | 2.7543 | 0.46297 | 0.75759 | 1.0382 | 1.2486 | 1.2486 | 1.2486 | 2.3625 | 3.0488 | 3.4984 | 3.735 | 4.2083 | 4.6816 | 0.71637 | 1.4139 | 1.6967 | 1.6967 | 1.6967 | 1.6967 | 0.55252 | 0.64273 | 0.64273 | 0.64273 | 0.64273 | 0.64273
2020-11-15 16:00 | Summer | 1.3718 | 1.9632 | 2.833 | 2.833 | 2.833 | 2.833 | 0.53156 | 0.86983 | 1.192 | 1.4336 | 1.4336 | 1.4336 | 2.4387 | 3.1471 | 3.6112 | 3.8555 | 4.3441 | 4.8326 | 0.75067 | 1.4816 | 1.7779 | 1.7779 | 1.7779 | 1.7779 | 0.55252 | 0.64273 | 0.64273 | 0.64273 | 0.64273 | 0.64273
2020-11-15 17:00 | Summer | 1.3718 | 1.9632 | 2.833 | 2.833 | 2.833 | 2.833 | 0.56014 | 0.9166 | 1.2561 | 1.5107 | 1.5107 | 1.5107 | 2.3678 | 3.0556 | 3.5063 | 3.7434 | 4.2178 | 4.6921 | 0.76591 | 1.5117 | 1.814 | 1.814 | 1.814 | 1.814 | 0.57158 | 0.6649 | 0.6649 | 0.6649 | 0.6649 | 0.6649
2020-11-15 18:00 | Summer | 1.4289 | 2.045 | 2.9511 | 2.9511 | 2.9511 | 2.9511 | 0.51727 | 0.84645 | 1.1599 | 1.3951 | 1.3951 | 1.3951 | 2.172 | 2.8029 | 3.2163 | 3.4338 | 3.8689 | 4.3041 | 0.8345 | 1.647 | 1.9764 | 1.9764 | 1.9764 | 1.9764 | 0.54607 | 0.63522 | 0.63522 | 0.63522 | 0.63522 | 0.63522
2020-11-15 19:00 | Summer | 1.4289 | 2.045 | 2.9511 | 2.9511 | 2.9511 | 2.9511 | 0.42011 | 0.68744 | 0.94205 | 1.133 | 1.133 | 1.133 | 2.191 | 2.8275 | 3.2445 | 3.4639 | 3.9029 | 4.3418 | 0.79258 | 1.5643 | 1.8772 | 1.8772 | 1.8772 | 1.8772 | 0.57158 | 0.6649 | 0.6649 | 0.6649 | 0.6649 | 0.6649
2020-11-15 20:00 | Summer | 1.3718 | 1.9632 | 2.833 | 2.833 | 2.833 | 2.833 | 0.45726 | 0.74824 | 1.0254 | 1.2332 | 1.2332 | 1.2332 | 2.191 | 2.8275 | 3.2445 | 3.4639 | 3.9029 | 4.3418 | 0.81545 | 1.6094 | 1.9313 | 1.9313 | 1.9313 | 1.9313 | 0.57158 | 0.6649 | 0.6649 | 0.6649 | 0.6649 | 0.6649
2020-11-15 21:00 | Summer | 1.3527 | 1.936 | 2.7937 | 2.7937 | 2.7937 | 2.7937 | 0.39153 | 0.64068 | 0.87797 | 1.0559 | 1.0559 | 1.0559 | 2.1148 | 2.7291 | 3.1316 | 3.3435 | 3.7671 | 4.1908 | 0.80021 | 1.5794 | 1.8952 | 1.8952 | 1.8952 | 1.8952 | 0.55252 | 0.64273 | 0.64273 | 0.64273 | 0.64273 | 0.64273
2020-11-15 22:00 | Summer | 1.3527 | 1.936 | 2.7937 | 2.7937 | 2.7937 | 2.7937 | 0.33723 | 0.55183 | 0.75621 | 0.90949 | 0.90949 | 0.90949 | 1.9243 | 2.4833 | 2.8495 | 3.0422 | 3.4277 | 3.8132 | 0.76591 | 1.5117 | 1.814 | 1.814 | 1.814 | 1.814 | 0.53347 | 0.62057 | 0.62057 | 0.62057 | 0.62057 | 0.62057
2020-11-15 23:00 | Summer | 1.3527 | 1.936 | 2.7937 | 2.7937 | 2.7937 | 2.7937 | 0.33151 | 0.54247 | 0.74339 | 0.89407 | 0.89407 | 0.89407 | 1.8862 | 2.4341 | 2.7931 | 2.982 | 3.3599 | 3.7377 | 0.60587 | 1.1958 | 1.435 | 1.435 | 1.435 | 1.435 | 0.49545 | 0.57634 | 0.57634 | 0.57634 | 0.57634 | 0.57634
2020-11-16 | Summer | 1.2575 | 1.7996 | 2.5969 | 2.5969 | 2.5969 | 2.5969 | 0.37438 | 0.61262 | 0.83952 | 1.0097 | 1.0097 | 1.0097 | 1.6766 | 2.1636 | 2.4827 | 2.6507 | 2.9865 | 3.3224 | 0.59063 | 1.1657 | 1.3989 | 1.3989 | 1.3989 | 1.3989 | 0.49931 | 0.58083 | 0.58083 | 0.58083 | 0.58083 | 0.58083
2020-11-16 01:00 | Summer | 1.2765 | 1.8269 | 2.6363 | 2.6363 | 2.6363 | 2.6363 | 0.37438 | 0.61262 | 0.83952 | 1.0097 | 1.0097 | 1.0097 | 1.6197 | 2.0902 | 2.3984 | 2.5607 | 2.8851 | 3.2096 | 0.58682 | 1.1582 | 1.3898 | 1.3898 | 1.3898 | 1.3898 | 0.52239 | 0.60768 | 0.60768 | 0.60768 | 0.60768 | 0.60768
2020-11-16 02:00 | Summer | 1.2194 | 1.7451 | 2.5183 | 2.5183 | 2.5183 | 2.5183 | 0.4001 | 0.65471 | 0.89719 | 1.0791 | 1.0791 | 1.0791 | 1.6385 | 2.1145 | 2.4263 | 2.5904 | 2.9187 | 3.2469 | 0.58301 | 1.1507 | 1.3808 | 1.3808 | 1.3808 | 1.3808 | 0.57158 | 0.6649 | 0.6649 | 0.6649 | 0.6649 | 0.6649
2020-11-16 03:00 | Summer | 1.1813 | 1.6906 | 2.4396 | 2.4396 | 2.4396 | 2.4396 | 0.32883 | 0.53808 | 0.73737 | 0.88684 | 0.88684 | 0.88684 | 1.5814 | 2.0407 | 2.3417 | 2.5001 | 2.8169 | 3.1337 | 0.5792 | 1.1431 | 1.3718 | 1.3718 | 1.3718 | 1.3718 | 0.56162 | 0.65331 | 0.65331 | 0.65331 | 0.65331 | 0.65331
2020-11-16 04:00 | Summer | 1.3146 | 1.8814 | 2.715 | 2.715 | 2.715 | 2.715 | 0.38295 | 0.62665 | 0.85874 | 1.0328 | 1.0328 | 1.0328 | 1.6195 | 2.0899 | 2.3981 | 2.5603 | 2.8847 | 3.2092 | 0.60206 | 1.1883 | 1.4259 | 1.4259 | 1.4259 | 1.4259 | 0.55252 | 0.64273 | 0.64273 | 0.64273 | 0.64273 | 0.64273
2020-11-16 05:00 | Summer | 1.258 | 1.8005 | 2.5981 | 2.5981 | 2.5981 | 2.5981 | 0.46583 | 0.76227 | 1.0446 | 1.2563 | 1.2563 | 1.2563 | 1.7546 | 2.2642 | 2.5981 | 2.7739 | 3.1254 | 3.4769 | 0.56776 | 1.1206 | 1.3447 | 1.3447 | 1.3447 | 1.3447 | 0.64779 | 0.75355 | 0.75355 | 0.75355 | 0.75355 | 0.75355
2020-11-16 06:00 | Summer | 1.5623 | 2.2359 | 3.2265 | 3.2265 | 3.2265 | 3.2265 | 0.64302 | 1.0522 | 1.4419 | 1.7342 | 1.7342 | 1.7342 | 1.9297 | 2.4903 | 2.8575 | 3.0508 | 3.4374 | 3.824 | 0.75829 | 1.4966 | 1.796 | 1.796 | 1.796 | 1.796 | 0.84412 | 0.98194 | 0.98194 | 0.98194 | 0.98194 | 0.98194
2020-11-16 07:00 | Summer | 2.0196 | 2.8903 | 4.1709 | 4.1709 | 4.1709 | 4.1709 | 0.82021 | 1.3422 | 1.8393 | 2.2121 | 2.2121 | 2.2121 | 2.4959 | 3.221 | 3.696 | 3.946 | 4.446 | 4.946 | 1.1698 | 2.3089 | 2.7706 | 2.7706 | 2.7706 | 2.7706 | 1.1813 | 1.3741 | 1.3741 | 1.3741 | 1.3741 | 1.3741
2020-11-16 08:00 | Summer | 2.4481 | 3.5036 | 5.0559 | 5.0559 | 5.0559 | 5.0559 | 0.87451 | 1.431 | 1.961 | 2.3585 | 2.3585 | 2.3585 | 2.9722 | 3.8356 | 4.4012 | 4.6989 | 5.2943 | 5.8898 | 1.166 | 2.3013 | 2.7616 | 2.7616 | 2.7616 | 2.7616 | 1.4099 | 1.6401 | 1.6401 | 1.6401 | 1.6401 | 1.6401
2020-11-16 09:00 | Summer | 2.5149 | 3.5993 | 5.1939 | 5.1939 | 5.1939 | 5.1939 | 1.2346 | 2.0203 | 2.7685 | 3.3297 | 3.3297 | 3.3297 | 3.0675 | 3.9585 | 4.5423 | 4.8495 | 5.464 | 6.0785 | 1.1546 | 2.2788 | 2.7345 | 2.7345 | 2.7345 | 2.7345 | 1.5433 | 1.7952 | 1.7952 | 1.7952 | 1.7952 | 1.7952
2020-11-16 10:00 | Summer | 2.8198 | 4.0356 | 5.8235 | 5.8235 | 5.8235 | 5.8235 | 1.2175 | 1.9922 | 2.7301 | 3.2834 | 3.2834 | 3.2834 | 3.2389 | 4.1798 | 4.7962 | 5.1206 | 5.7695 | 6.4183 | 1.1317 | 2.2337 | 2.6804 | 2.6804 | 2.6804 | 2.6804 | 1.6195 | 1.8839 | 1.8839 | 1.8839 | 1.8839 | 1.8839
2020-11-16 11:00 | Summer | 2.5149 | 3.5993 | 5.1939 | 5.1939 | 5.1939 | 5.1939 | 1.1003 | 1.8005 | 2.4673 | 2.9674 | 2.9674 | 2.9674 | 3.1818 | 4.106 | 4.7115 | 5.0303 | 5.6677 | 6.3051 | 1.1012 | 2.1735 | 2.6082 | 2.6082 | 2.6082 | 2.6082 | 1.6004 | 1.8617 | 1.8617 | 1.8617 | 1.8617 | 1.8617
2020-11-16 12:00 | Summer | 2.5721 | 3.6811 | 5.3119 | 5.3119 | 5.3119 | 5.3119 | 1.0831 | 1.7724 | 2.4288 | 2.9212 | 2.9212 | 2.9212 | 3.2008 | 4.1306 | 4.7398 | 5.0604 | 5.7016 | 6.3428 | 1.1546 | 2.2788 | 2.7345 | 2.7345 | 2.7345 | 2.7345 | 1.6004 | 1.8617 | 1.8617 | 1.8617 | 1.8617 | 1.8617
2020-11-16 13:00 | Summer | 2.5911 | 3.7083 | 5.3513 | 5.3513 | 5.3513 | 5.3513 | 1.1403 | 1.8659 | 2.557 | 3.0753 | 3.0753 | 3.0753 | 3.1246 | 4.0323 | 4.6269 | 4.9399 | 5.5658 | 6.1918 | 1.1127 | 2.1961 | 2.6353 | 2.6353 | 2.6353 | 2.6353 | 1.5814 | 1.8395 | 1.8395 | 1.8395 | 1.8395 | 1.8395
2020-11-16 14:00 | Summer | 2.3816 | 3.4084 | 4.9185 | 4.9185 | 4.9185 | 4.9185 | 1.0888 | 1.7818 | 2.4417 | 2.9366 | 2.9366 | 2.9366 | 2.8007 | 3.6143 | 4.1473 | 4.4278 | 4.9889 | 5.55 | 0.86498 | 1.7072 | 2.0486 | 2.0486 | 2.0486 | 2.0486 | 1.3908 | 1.6179 | 1.6179 | 1.6179 | 1.6179 | 1.6179
2020-11-16 15:00 | Summer | 2.3244 | 3.3266 | 4.8004 | 4.8004 | 4.8004 | 4.8004 | 0.97453 | 1.5947 | 2.1853 | 2.6283 | 2.6283 | 2.6283 | 2.8198 | 3.6389 | 4.1755 | 4.4579 | 5.0228 | 5.5877 | 0.81926 | 1.617 | 1.9403 | 1.9403 | 1.9403 | 1.9403 | 1.3451 | 1.5647 | 1.5647 | 1.5647 | 1.5647 | 1.5647
2020-11-16 16:00 | Summer | 2.2863 | 3.2721 | 4.7217 | 4.7217 | 4.7217 | 4.7217 | 1.0031 | 1.6415 | 2.2494 | 2.7054 | 2.7054 | 2.7054 | 2.6483 | 3.4176 | 3.9216 | 4.1869 | 4.7174 | 5.2479 | 0.85736 | 1.6922 | 2.0306 | 2.0306 | 2.0306 | 2.0306 | 1.3337 | 1.5514 | 1.5514 | 1.5514 | 1.5514 | 1.5514
2020-11-16 17:00 | Summer | 2.0266 | 2.9005 | 4.1855 | 4.1855 | 4.1855 | 4.1855 | 0.85165 | 1.3936 | 1.9098 | 2.2969 | 2.2969 | 2.2969 | 2.5534 | 3.295 | 3.781 | 4.0367 | 4.5482 | 5.0598 | 0.84212 | 1.6621 | 1.9945 | 1.9945 | 1.9945 | 1.9945 | 1.2003 | 1.3963 | 1.3963 | 1.3963 | 1.3963 | 1.3963
2020-11-16 18:00 | Summer | 1.8036 | 2.5813 | 3.7249 | 3.7249 | 3.7249 | 3.7249 | 0.62473 | 1.0223 | 1.4009 | 1.6849 | 1.6849 | 1.6849 | 2.3625 | 3.0488 | 3.4984 | 3.735 | 4.2083 | 4.6816 | 0.76972 | 1.5192 | 1.823 | 1.823 | 1.823 | 1.823 | 0.86352 | 1.0045 | 1.0045 | 1.0045 | 1.0045 | 1.0045
2020-11-16 19:00 | Summer | 1.4099 | 2.0178 | 2.9117 | 2.9117 | 2.9117 | 2.9117 | 0.40867 | 0.66874 | 0.91642 | 1.1022 | 1.1022 | 1.1022 | 2.0958 | 2.7046 | 3.1034 | 3.3133 | 3.7332 | 4.153 | 0.75067 | 1.4816 | 1.7779 | 1.7779 | 1.7779 | 1.7779 | 0.67292 | 0.78278 | 0.78278 | 0.78278 | 0.78278 | 0.78278
2020-11-16 20:00 | Summer | 1.2384 | 1.7724 | 2.5576 | 2.5576 | 2.5576 | 2.5576 | 0.45726 | 0.74824 | 1.0254 | 1.2332 | 1.2332 | 1.2332 | 2.0577 | 2.6554 | 3.047 | 3.2531 | 3.6653 | 4.0775 | 0.8345 | 1.647 | 1.9764 | 1.9764 | 1.9764 | 1.9764 | 0.59063 | 0.68706 | 0.68706 | 0.68706 | 0.68706 | 0.68706
2020-11-16 21:00 | Summer | 1.1432 | 1.636 | 2.3609 | 2.3609 | 2.3609 | 2.3609 | 0.37438 | 0.61262 | 0.83952 | 1.0097 | 1.0097 | 1.0097 | 2.0005 | 2.5816 | 2.9624 | 3.1627 | 3.5635 | 3.9643 | 0.72018 | 1.4214 | 1.7057 | 1.7057 | 1.7057 | 1.7057 | 0.55252 | 0.64273 | 0.64273 | 0.64273 | 0.64273 | 0.64273
2020-11-16 22:00 | Summer | 1.1241 | 1.6088 | 2.3215 | 2.3215 | 2.3215 | 2.3215 | 0.36581 | 0.59859 | 0.82029 | 0.98657 | 0.98657 | 0.98657 | 1.8672 | 2.4095 | 2.7649 | 2.9519 | 3.3259 | 3.7 | 0.73924 | 1.459 | 1.7508 | 1.7508 | 1.7508 | 1.7508 | 0.49558 | 0.57649 | 0.57649 | 0.57649 | 0.57649 | 0.57649
2020-11-16 23:00 | Summer | 1.0479 | 1.4997 | 2.1641 | 2.1641 | 2.1641 | 2.1641 | 0.41725 | 0.68277 | 0.93565 | 1.1253 | 1.1253 | 1.1253 | 1.7244 | 2.2254 | 2.5535 | 2.7263 | 3.0717 | 3.4172 | 0.82307 | 1.6245 | 1.9494 | 1.9494 | 1.9494 | 1.9494 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-11-17 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.38009 | 0.62197 | 0.85233 | 1.0251 | 1.0251 | 1.0251 | 1.6008 | 2.0657 | 2.3704 | 2.5307 | 2.8514 | 3.1721 | 0.62111 | 1.2259 | 1.4711 | 1.4711 | 1.4711 | 1.4711 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-11-17 01:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.37438 | 0.61262 | 0.83952 | 1.0097 | 1.0097 | 1.0097 | 1.5052 | 1.9424 | 2.2288 | 2.3796 | 2.6811 | 2.9826 | 0.5792 | 1.1431 | 1.3718 | 1.3718 | 1.3718 | 1.3718 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-11-17 02:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.39153 | 0.64068 | 0.87797 | 1.0559 | 1.0559 | 1.0559 | 1.4861 | 1.9178 | 2.2006 | 2.3495 | 2.6472 | 2.9449 | 0.49155 | 0.97017 | 1.1642 | 1.1642 | 1.1642 | 1.1642 | 0.43231 | 0.50289 | 0.50289 | 0.50289 | 0.50289 | 0.50289
2020-11-17 03:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.47155 | 0.77162 | 1.0574 | 1.2717 | 1.2717 | 1.2717 | 1.5052 | 1.9424 | 2.2288 | 2.3796 | 2.6811 | 2.9826 | 0.55252 | 1.0905 | 1.3086 | 1.3086 | 1.3086 | 1.3086 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-11-17 04:00 | Summer | 1.0288 | 1.4724 | 2.1248 | 2.1248 | 2.1248 | 2.1248 | 0.43154 | 0.70615 | 0.96769 | 1.1638 | 1.1638 | 1.1638 | 1.5814 | 2.0407 | 2.3417 | 2.5001 | 2.8169 | 3.1337 | 0.48012 | 0.94761 | 1.1371 | 1.1371 | 1.1371 | 1.1371 | 0.52245 | 0.60775 | 0.60775 | 0.60775 | 0.60775 | 0.60775
2020-11-17 05:00 | Summer | 1.0329 | 1.4782 | 2.1331 | 2.1331 | 2.1331 | 2.1331 | 0.43154 | 0.70615 | 0.96769 | 1.1638 | 1.1638 | 1.1638 | 1.6385 | 2.1145 | 2.4263 | 2.5904 | 2.9187 | 3.2469 | 0.59063 | 1.1657 | 1.3989 | 1.3989 | 1.3989 | 1.3989 | 0.57158 | 0.6649 | 0.6649 | 0.6649 | 0.6649 | 0.6649
2020-11-17 06:00 | Summer | 1.2194 | 1.7451 | 2.5183 | 2.5183 | 2.5183 | 2.5183 | 0.53728 | 0.87918 | 1.2048 | 1.449 | 1.449 | 1.449 | 1.6348 | 2.1096 | 2.4208 | 2.5845 | 2.912 | 3.2395 | 0.67065 | 1.3236 | 1.5884 | 1.5884 | 1.5884 | 1.5884 | 0.72202 | 0.8399 | 0.8399 | 0.8399 | 0.8399 | 0.8399
2020-11-17 07:00 | Summer | 1.8122 | 2.5935 | 3.7426 | 3.7426 | 3.7426 | 3.7426 | 0.70747 | 1.1577 | 1.5864 | 1.908 | 1.908 | 1.908 | 1.9778 | 2.5523 | 2.9286 | 3.1268 | 3.523 | 3.9192 | 0.83831 | 1.6546 | 1.9855 | 1.9855 | 1.9855 | 1.9855 | 0.99073 | 1.1525 | 1.1525 | 1.1525 | 1.1525 | 1.1525
2020-11-17 08:00 | Summer | 2.2968 | 3.2871 | 4.7434 | 4.7434 | 4.7434 | 4.7434 | 0.81735 | 1.3375 | 1.8328 | 2.2044 | 2.2044 | 2.2044 | 2.4959 | 3.2209 | 3.6959 | 3.9459 | 4.4459 | 4.9459 | 0.95263 | 1.8802 | 2.2562 | 2.2562 | 2.2562 | 2.2562 | 1.2003 | 1.3963 | 1.3963 | 1.3963 | 1.3963 | 1.3963
2020-11-17 09:00 | Summer | 2.4387 | 3.4902 | 5.0365 | 5.0365 | 5.0365 | 5.0365 | 0.81449 | 1.3328 | 1.8264 | 2.1967 | 2.1967 | 2.1967 | 2.5802 | 3.3296 | 3.8207 | 4.0791 | 4.596 | 5.1129 | 0.93357 | 1.8426 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 1.3908 | 1.6179 | 1.6179 | 1.6179 | 1.6179 | 1.6179
2020-11-17 10:00 | Summer | 2.7817 | 3.981 | 5.7448 | 5.7448 | 5.7448 | 5.7448 | 0.82592 | 1.3515 | 1.8521 | 2.2275 | 2.2275 | 2.2275 | 2.6864 | 3.4668 | 3.978 | 4.2471 | 4.7853 | 5.3234 | 0.93738 | 1.8501 | 2.2201 | 2.2201 | 2.2201 | 2.2201 | 1.3337 | 1.5514 | 1.5514 | 1.5514 | 1.5514 | 1.5514
2020-11-17 11:00 | Summer | 2.6483 | 3.7901 | 5.4693 | 5.4693 | 5.4693 | 5.4693 | 0.86879 | 1.4217 | 1.9482 | 2.3431 | 2.3431 | 2.3431 | 2.7568 | 3.5575 | 4.0822 | 4.3583 | 4.9106 | 5.4628 | 1.0784 | 2.1284 | 2.554 | 2.554 | 2.554 | 2.554 | 1.3908 | 1.6179 | 1.6179 | 1.6179 | 1.6179 | 1.6179
2020-11-17 12:00 | Summer | 2.6293 | 3.7629 | 5.43 | 5.43 | 5.43 | 5.43 | 0.93167 | 1.5245 | 2.0892 | 2.5127 | 2.5127 | 2.5127 | 2.8198 | 3.6389 | 4.1755 | 4.4579 | 5.0228 | 5.5877 | 1.0517 | 2.0757 | 2.4909 | 2.4909 | 2.4909 | 2.4909 | 1.4099 | 1.6401 | 1.6401 | 1.6401 | 1.6401 | 1.6401
2020-11-17 13:00 | Summer | 2.6674 | 3.8174 | 5.5087 | 5.5087 | 5.5087 | 5.5087 | 0.95453 | 1.562 | 2.1405 | 2.5743 | 2.5743 | 2.5743 | 2.8579 | 3.688 | 4.2319 | 4.5182 | 5.0907 | 5.6632 | 1.0631 | 2.0983 | 2.5179 | 2.5179 | 2.5179 | 2.5179 | 1.4099 | 1.6401 | 1.6401 | 1.6401 | 1.6401 | 1.6401
2020-11-17 14:00 | Summer | 2.6293 | 3.7629 | 5.43 | 5.43 | 5.43 | 5.43 | 0.95739 | 1.5666 | 2.1469 | 2.582 | 2.582 | 2.582 | 2.8198 | 3.6389 | 4.1755 | 4.4579 | 5.0228 | 5.5877 | 1.0822 | 2.1359 | 2.5631 | 2.5631 | 2.5631 | 2.5631 | 1.4099 | 1.6401 | 1.6401 | 1.6401 | 1.6401 | 1.6401
2020-11-17 15:00 | Summer | 2.7055 | 3.8719 | 5.5874 | 5.5874 | 5.5874 | 5.5874 | 0.98025 | 1.604 | 2.1981 | 2.6437 | 2.6437 | 2.6437 | 2.8007 | 3.6143 | 4.1473 | 4.4278 | 4.9889 | 5.55 | 1.0631 | 2.0983 | 2.5179 | 2.5179 | 2.5179 | 2.5179 | 1.3718 | 1.5957 | 1.5957 | 1.5957 | 1.5957 | 1.5957
2020-11-17 16:00 | Summer | 2.6864 | 3.8447 | 5.548 | 5.548 | 5.548 | 5.548 | 1.046 | 1.7116 | 2.3455 | 2.821 | 2.821 | 2.821 | 2.8007 | 3.6143 | 4.1473 | 4.4278 | 4.9889 | 5.55 | 1.1889 | 2.3465 | 2.8158 | 2.8158 | 2.8158 | 2.8158 | 1.3337 | 1.5514 | 1.5514 | 1.5514 | 1.5514 | 1.5514
2020-11-17 17:00 | Summer | 2.4768 | 3.5447 | 5.1152 | 5.1152 | 5.1152 | 5.1152 | 1.0152 | 1.6613 | 2.2766 | 2.738 | 2.738 | 2.738 | 2.7436 | 3.5405 | 4.0627 | 4.3375 | 4.8871 | 5.4367 | 1.105 | 2.181 | 2.6172 | 2.6172 | 2.6172 | 2.6172 | 1.3149 | 1.5296 | 1.5296 | 1.5296 | 1.5296 | 1.5296
2020-11-17 18:00 | Summer | 2.0299 | 2.9051 | 4.1922 | 4.1922 | 4.1922 | 4.1922 | 0.71733 | 1.1738 | 1.6085 | 1.9346 | 1.9346 | 1.9346 | 2.5721 | 3.3192 | 3.8087 | 4.0664 | 4.5816 | 5.0969 | 0.92214 | 1.82 | 2.184 | 2.184 | 2.184 | 2.184 | 0.88885 | 1.034 | 1.034 | 1.034 | 1.034 | 1.034
2020-11-17 19:00 | Summer | 1.3527 | 1.936 | 2.7937 | 2.7937 | 2.7937 | 2.7937 | 0.52585 | 0.86048 | 1.1792 | 1.4182 | 1.4182 | 1.4182 | 2.3435 | 3.0242 | 3.4702 | 3.7049 | 4.1744 | 4.6438 | 0.89547 | 1.7674 | 2.1208 | 2.1208 | 2.1208 | 2.1208 | 0.62965 | 0.73245 | 0.73245 | 0.73245 | 0.73245 | 0.73245
2020-11-17 20:00 | Summer | 1.2003 | 1.7178 | 2.4789 | 2.4789 | 2.4789 | 2.4789 | 0.44297 | 0.72486 | 0.99332 | 1.1947 | 1.1947 | 1.1947 | 2.0577 | 2.6554 | 3.047 | 3.2531 | 3.6653 | 4.0775 | 0.87642 | 1.7298 | 2.0757 | 2.0757 | 2.0757 | 2.0757 | 0.59063 | 0.68706 | 0.68706 | 0.68706 | 0.68706 | 0.68706
2020-11-17 21:00 | Summer | 1.2194 | 1.7451 | 2.5183 | 2.5183 | 2.5183 | 2.5183 | 0.39724 | 0.65003 | 0.89079 | 1.0713 | 1.0713 | 1.0713 | 1.9819 | 2.5576 | 2.9348 | 3.1333 | 3.5303 | 3.9274 | 0.82636 | 1.631 | 1.9572 | 1.9572 | 1.9572 | 1.9572 | 0.53347 | 0.62057 | 0.62057 | 0.62057 | 0.62057 | 0.62057
2020-11-17 22:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.39724 | 0.65003 | 0.89079 | 1.0713 | 1.0713 | 1.0713 | 1.8862 | 2.4341 | 2.7931 | 2.982 | 3.3599 | 3.7377 | 0.73924 | 1.459 | 1.7508 | 1.7508 | 1.7508 | 1.7508 | 0.47645 | 0.55424 | 0.55424 | 0.55424 | 0.55424 | 0.55424
2020-11-17 23:00 | Summer | 0.99102 | 1.4183 | 2.0467 | 2.0467 | 2.0467 | 2.0467 | 0.36866 | 0.60327 | 0.8267 | 0.99427 | 0.99427 | 0.99427 | 1.6766 | 2.1636 | 2.4827 | 2.6507 | 2.9865 | 3.3224 | 0.64016 | 1.2635 | 1.5162 | 1.5162 | 1.5162 | 1.5162 | 0.45729 | 0.53195 | 0.53195 | 0.53195 | 0.53195 | 0.53195
2020-11-18 | Summer | 0.96314 | 1.3784 | 1.9891 | 1.9891 | 1.9891 | 1.9891 | 0.3458 | 0.56585 | 0.77543 | 0.93261 | 0.93261 | 0.93261 | 1.6195 | 2.0899 | 2.3981 | 2.5603 | 2.8847 | 3.2092 | 0.63635 | 1.256 | 1.5072 | 1.5072 | 1.5072 | 1.5072 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-11-18 01:00 | Summer | 1.105 | 1.5815 | 2.2822 | 2.2822 | 2.2822 | 2.2822 | 0.40867 | 0.66874 | 0.91642 | 1.1022 | 1.1022 | 1.1022 | 1.5433 | 1.9915 | 2.2852 | 2.4398 | 2.749 | 3.0581 | 0.55252 | 1.0905 | 1.3086 | 1.3086 | 1.3086 | 1.3086 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-11-18 02:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.37724 | 0.6173 | 0.84593 | 1.0174 | 1.0174 | 1.0174 | 1.5433 | 1.9915 | 2.2852 | 2.4398 | 2.749 | 3.0581 | 0.63635 | 1.256 | 1.5072 | 1.5072 | 1.5072 | 1.5072 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-11-18 03:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.37152 | 0.60794 | 0.83311 | 1.002 | 1.002 | 1.002 | 1.5433 | 1.9915 | 2.2852 | 2.4398 | 2.749 | 3.0581 | 0.5449 | 1.0755 | 1.2906 | 1.2906 | 1.2906 | 1.2906 | 0.42767 | 0.49749 | 0.49749 | 0.49749 | 0.49749 | 0.49749
2020-11-18 04:00 | Summer | 1.0479 | 1.4997 | 2.1641 | 2.1641 | 2.1641 | 2.1641 | 0.40296 | 0.65939 | 0.9036 | 1.0868 | 1.0868 | 1.0868 | 1.5623 | 2.0161 | 2.3135 | 2.4699 | 2.7829 | 3.0959 | 0.64397 | 1.271 | 1.5252 | 1.5252 | 1.5252 | 1.5252 | 0.53347 | 0.62057 | 0.62057 | 0.62057 | 0.62057 | 0.62057
2020-11-18 05:00 | Summer | 1.1432 | 1.636 | 2.3609 | 2.3609 | 2.3609 | 2.3609 | 0.42011 | 0.68744 | 0.94205 | 1.133 | 1.133 | 1.133 | 1.6576 | 2.1391 | 2.4545 | 2.6205 | 2.9526 | 3.2847 | 0.62873 | 1.2409 | 1.4891 | 1.4891 | 1.4891 | 1.4891 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-11-18 06:00 | Summer | 1.1813 | 1.6906 | 2.4396 | 2.4396 | 2.4396 | 2.4396 | 0.56586 | 0.92595 | 1.2689 | 1.5261 | 1.5261 | 1.5261 | 1.7909 | 2.3112 | 2.652 | 2.8314 | 3.1902 | 3.549 | 0.70875 | 1.3989 | 1.6786 | 1.6786 | 1.6786 | 1.6786 | 0.723 | 0.84104 | 0.84104 | 0.84104 | 0.84104 | 0.84104
2020-11-18 07:00 | Summer | 1.7909 | 2.5631 | 3.6987 | 3.6987 | 3.6987 | 3.6987 | 0.75448 | 1.2346 | 1.6919 | 2.0348 | 2.0348 | 2.0348 | 2.1776 | 2.8102 | 3.2246 | 3.4428 | 3.879 | 4.3153 | 1.0708 | 2.1133 | 2.536 | 2.536 | 2.536 | 2.536 | 0.97168 | 1.1303 | 1.1303 | 1.1303 | 1.1303 | 1.1303
2020-11-18 08:00 | Summer | 2.4578 | 3.5175 | 5.0759 | 5.0759 | 5.0759 | 5.0759 | 0.73733 | 1.2065 | 1.6534 | 1.9886 | 1.9886 | 1.9886 | 2.553 | 3.2946 | 3.7805 | 4.0362 | 4.5477 | 5.0591 | 1.0517 | 2.0757 | 2.4909 | 2.4909 | 2.4909 | 2.4909 | 1.2765 | 1.4849 | 1.4849 | 1.4849 | 1.4849 | 1.4849
2020-11-18 09:00 | Summer | 2.4959 | 3.572 | 5.1545 | 5.1545 | 5.1545 | 5.1545 | 0.87451 | 1.431 | 1.961 | 2.3585 | 2.3585 | 2.3585 | 2.5721 | 3.3192 | 3.8087 | 4.0664 | 4.5816 | 5.0969 | 1.0098 | 1.993 | 2.3916 | 2.3916 | 2.3916 | 2.3916 | 1.3703 | 1.594 | 1.594 | 1.594 | 1.594 | 1.594
2020-11-18 10:00 | Summer | 2.5899 | 3.7066 | 5.3488 | 5.3488 | 5.3488 | 5.3488 | 0.87451 | 1.431 | 1.961 | 2.3585 | 2.3585 | 2.3585 | 2.6864 | 3.4668 | 3.978 | 4.2471 | 4.7853 | 5.3234 | 0.96025 | 1.8952 | 2.2743 | 2.2743 | 2.2743 | 2.2743 | 1.4099 | 1.6401 | 1.6401 | 1.6401 | 1.6401 | 1.6401
2020-11-18 11:00 | Summer | 2.6293 | 3.7629 | 5.43 | 5.43 | 5.43 | 5.43 | 0.8888 | 1.4544 | 1.9931 | 2.3971 | 2.3971 | 2.3971 | 2.6864 | 3.4668 | 3.978 | 4.2471 | 4.7853 | 5.3234 | 1.0174 | 2.008 | 2.4096 | 2.4096 | 2.4096 | 2.4096 | 1.3908 | 1.6179 | 1.6179 | 1.6179 | 1.6179 | 1.6179
2020-11-18 12:00 | Summer | 2.6293 | 3.7629 | 5.43 | 5.43 | 5.43 | 5.43 | 0.92595 | 1.5152 | 2.0764 | 2.4973 | 2.4973 | 2.4973 | 2.8388 | 3.6634 | 4.2037 | 4.4881 | 5.0568 | 5.6255 | 1.0517 | 2.0757 | 2.4909 | 2.4909 | 2.4909 | 2.4909 | 1.4099 | 1.6401 | 1.6401 | 1.6401 | 1.6401 | 1.6401
2020-11-18 13:00 | Summer | 2.7055 | 3.8719 | 5.5874 | 5.5874 | 5.5874 | 5.5874 | 1.086 | 1.7771 | 2.4353 | 2.9289 | 2.9289 | 2.9289 | 3.0675 | 3.9585 | 4.5423 | 4.8495 | 5.464 | 6.0785 | 1.1393 | 2.2487 | 2.6984 | 2.6984 | 2.6984 | 2.6984 | 1.448 | 1.6844 | 1.6844 | 1.6844 | 1.6844 | 1.6844
2020-11-18 14:00 | Summer | 2.6864 | 3.8447 | 5.548 | 5.548 | 5.548 | 5.548 | 1.2346 | 2.0203 | 2.7685 | 3.3297 | 3.3297 | 3.3297 | 3.1056 | 4.0077 | 4.5987 | 4.9098 | 5.5319 | 6.154 | 1.0708 | 2.1133 | 2.536 | 2.536 | 2.536 | 2.536 | 1.4099 | 1.6401 | 1.6401 | 1.6401 | 1.6401 | 1.6401
2020-11-18 15:00 | Summer | 2.6864 | 3.8447 | 5.548 | 5.548 | 5.548 | 5.548 | 1.0317 | 1.6882 | 2.3135 | 2.7824 | 2.7824 | 2.7824 | 3.1056 | 4.0077 | 4.5987 | 4.9098 | 5.5319 | 6.154 | 1.1736 | 2.3164 | 2.7797 | 2.7797 | 2.7797 | 2.7797 | 1.3908 | 1.6179 | 1.6179 | 1.6179 | 1.6179 | 1.6179
2020-11-18 16:00 | Summer | 2.7245 | 3.8992 | 5.6267 | 5.6267 | 5.6267 | 5.6267 | 1.0403 | 1.7023 | 2.3327 | 2.8056 | 2.8056 | 2.8056 | 3.0675 | 3.9585 | 4.5423 | 4.8495 | 5.464 | 6.0785 | 1.166 | 2.3013 | 2.7616 | 2.7616 | 2.7616 | 2.7616 | 1.3718 | 1.5957 | 1.5957 | 1.5957 | 1.5957 | 1.5957
2020-11-18 17:00 | Summer | 2.553 | 3.6538 | 5.2726 | 5.2726 | 5.2726 | 5.2726 | 0.93452 | 1.5292 | 2.0956 | 2.5204 | 2.5204 | 2.5204 | 2.9786 | 3.8438 | 4.4106 | 4.709 | 5.3057 | 5.9024 | 1.1089 | 2.1885 | 2.6262 | 2.6262 | 2.6262 | 2.6262 | 1.3337 | 1.5514 | 1.5514 | 1.5514 | 1.5514 | 1.5514
2020-11-18 18:00 | Summer | 1.9098 | 2.7332 | 3.9441 | 3.9441 | 3.9441 | 3.9441 | 0.68702 | 1.1242 | 1.5406 | 1.8529 | 1.8529 | 1.8529 | 2.8208 | 3.6402 | 4.1771 | 4.4596 | 5.0247 | 5.5898 | 0.95263 | 1.8802 | 2.2562 | 2.2562 | 2.2562 | 2.2562 | 0.92504 | 1.0761 | 1.0761 | 1.0761 | 1.0761 | 1.0761
2020-11-18 19:00 | Summer | 1.2626 | 1.8069 | 2.6075 | 2.6075 | 2.6075 | 2.6075 | 0.5151 | 0.8429 | 1.1551 | 1.3892 | 1.3892 | 1.3892 | 2.4379 | 3.1461 | 3.61 | 3.8542 | 4.3426 | 4.831 | 0.91452 | 1.805 | 2.166 | 2.166 | 2.166 | 2.166 | 0.68617 | 0.7982 | 0.7982 | 0.7982 | 0.7982 | 0.7982
2020-11-18 20:00 | Summer | 1.2575 | 1.7996 | 2.5969 | 2.5969 | 2.5969 | 2.5969 | 0.44011 | 0.72018 | 0.98691 | 1.187 | 1.187 | 1.187 | 2.2673 | 2.9258 | 3.3573 | 3.5844 | 4.0386 | 4.4928 | 0.92595 | 1.8275 | 2.193 | 2.193 | 2.193 | 2.193 | 0.68589 | 0.79787 | 0.79787 | 0.79787 | 0.79787 | 0.79787
2020-11-18 21:00 | Summer | 1.2384 | 1.7724 | 2.5576 | 2.5576 | 2.5576 | 2.5576 | 0.40867 | 0.66874 | 0.91642 | 1.1022 | 1.1022 | 1.1022 | 2.1674 | 2.797 | 3.2095 | 3.4266 | 3.8608 | 4.295 | 0.84974 | 1.6771 | 2.0125 | 2.0125 | 2.0125 | 2.0125 | 0.55252 | 0.64273 | 0.64273 | 0.64273 | 0.64273 | 0.64273
2020-11-18 22:00 | Summer | 1.105 | 1.5815 | 2.2822 | 2.2822 | 2.2822 | 2.2822 | 0.4001 | 0.65471 | 0.89719 | 1.0791 | 1.0791 | 1.0791 | 2.0386 | 2.6308 | 3.0188 | 3.223 | 3.6314 | 4.0398 | 0.80783 | 1.5944 | 1.9133 | 1.9133 | 1.9133 | 1.9133 | 0.55252 | 0.64273 | 0.64273 | 0.64273 | 0.64273 | 0.64273
2020-11-18 23:00 | Summer | 1.105 | 1.5815 | 2.2822 | 2.2822 | 2.2822 | 2.2822 | 0.39438 | 0.64536 | 0.88438 | 1.0636 | 1.0636 | 1.0636 | 1.8481 | 2.3849 | 2.7366 | 2.9218 | 3.292 | 3.6622 | 0.74305 | 1.4665 | 1.7599 | 1.7599 | 1.7599 | 1.7599 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-11-19 | Summer | 1.0479 | 1.4997 | 2.1641 | 2.1641 | 2.1641 | 2.1641 | 0.3458 | 0.56585 | 0.77543 | 0.93261 | 0.93261 | 0.93261 | 1.7147 | 2.2128 | 2.5392 | 2.7109 | 3.0544 | 3.3979 | 0.70365 | 1.3888 | 1.6665 | 1.6665 | 1.6665 | 1.6665 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-11-19 01:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.38581 | 0.63133 | 0.86515 | 1.0405 | 1.0405 | 1.0405 | 1.6576 | 2.1391 | 2.4545 | 2.6205 | 2.9526 | 3.2847 | 0.70494 | 1.3913 | 1.6696 | 1.6696 | 1.6696 | 1.6696 | 0.47648 | 0.55427 | 0.55427 | 0.55427 | 0.55427 | 0.55427
2020-11-19 02:00 | Summer | 0.99058 | 1.4177 | 2.0458 | 2.0458 | 2.0458 | 2.0458 | 0.39724 | 0.65003 | 0.89079 | 1.0713 | 1.0713 | 1.0713 | 1.6004 | 2.0653 | 2.3699 | 2.5302 | 2.8508 | 3.1714 | 0.64397 | 1.271 | 1.5252 | 1.5252 | 1.5252 | 1.5252 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-11-19 03:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.37192 | 0.6086 | 0.83401 | 1.0031 | 1.0031 | 1.0031 | 1.6004 | 2.0653 | 2.3699 | 2.5302 | 2.8508 | 3.1714 | 0.64016 | 1.2635 | 1.5162 | 1.5162 | 1.5162 | 1.5162 | 0.47136 | 0.54832 | 0.54832 | 0.54832 | 0.54832 | 0.54832
2020-11-19 04:00 | Summer | 1.1619 | 1.6629 | 2.3996 | 2.3996 | 2.3996 | 2.3996 | 0.38867 | 0.636 | 0.87156 | 1.0482 | 1.0482 | 1.0482 | 1.6219 | 2.093 | 2.4017 | 2.5641 | 2.889 | 3.2139 | 0.63635 | 1.256 | 1.5072 | 1.5072 | 1.5072 | 1.5072 | 0.49453 | 0.57527 | 0.57527 | 0.57527 | 0.57527 | 0.57527
2020-11-19 05:00 | Summer | 1.1813 | 1.6906 | 2.4396 | 2.4396 | 2.4396 | 2.4396 | 0.39438 | 0.64536 | 0.88438 | 1.0636 | 1.0636 | 1.0636 | 1.6957 | 2.1882 | 2.5109 | 2.6808 | 3.0205 | 3.3602 | 0.77353 | 1.5267 | 1.832 | 1.832 | 1.832 | 1.832 | 0.57158 | 0.6649 | 0.6649 | 0.6649 | 0.6649 | 0.6649
2020-11-19 06:00 | Summer | 1.2956 | 1.8542 | 2.6756 | 2.6756 | 2.6756 | 2.6756 | 0.50584 | 0.82774 | 1.1343 | 1.3642 | 1.3642 | 1.3642 | 1.8672 | 2.4095 | 2.7649 | 2.9519 | 3.3259 | 3.7 | 0.72018 | 1.4214 | 1.7057 | 1.7057 | 1.7057 | 1.7057 | 0.69756 | 0.81145 | 0.81145 | 0.81145 | 0.81145 | 0.81145
2020-11-19 07:00 | Summer | 1.8089 | 2.5888 | 3.7357 | 3.7357 | 3.7357 | 3.7357 | 0.74305 | 1.2159 | 1.6662 | 2.004 | 2.004 | 2.004 | 2.3054 | 2.975 | 3.4138 | 3.6447 | 4.1065 | 4.5683 | 1.0517 | 2.0757 | 2.4909 | 2.4909 | 2.4909 | 2.4909 | 1.086 | 1.2633 | 1.2633 | 1.2633 | 1.2633 | 1.2633
2020-11-19 08:00 | Summer | 2.6119 | 3.738 | 5.394 | 5.394 | 5.394 | 5.394 | 0.84879 | 1.3889 | 1.9033 | 2.2892 | 2.2892 | 2.2892 | 2.5991 | 3.3541 | 3.8488 | 4.1091 | 4.6298 | 5.1505 | 1.1279 | 2.2261 | 2.6714 | 2.6714 | 2.6714 | 2.6714 | 1.3527 | 1.5736 | 1.5736 | 1.5736 | 1.5736 | 1.5736
2020-11-19 09:00 | Summer | 2.8769 | 4.1174 | 5.9415 | 5.9415 | 5.9415 | 5.9415 | 0.87165 | 1.4263 | 1.9546 | 2.3508 | 2.3508 | 2.3508 | 2.7817 | 3.5897 | 4.1191 | 4.3977 | 4.955 | 5.5122 | 1.1241 | 2.2186 | 2.6623 | 2.6623 | 2.6623 | 2.6623 | 1.4099 | 1.6401 | 1.6401 | 1.6401 | 1.6401 | 1.6401
2020-11-19 10:00 | Summer | 2.9531 | 4.2264 | 6.0989 | 6.0989 | 6.0989 | 6.0989 | 0.93452 | 1.5292 | 2.0956 | 2.5204 | 2.5204 | 2.5204 | 3.1627 | 4.0814 | 4.6833 | 5.0001 | 5.6337 | 6.2673 | 0.89547 | 1.7674 | 2.1208 | 2.1208 | 2.1208 | 2.1208 | 1.5433 | 1.7952 | 1.7952 | 1.7952 | 1.7952 | 1.7952
2020-11-19 11:00 | Summer | 2.8769 | 4.1174 | 5.9415 | 5.9415 | 5.9415 | 5.9415 | 1.0003 | 1.6368 | 2.243 | 2.6977 | 2.6977 | 2.6977 | 3.277 | 4.2289 | 4.8526 | 5.1809 | 5.8373 | 6.4938 | 0.87642 | 1.7298 | 2.0757 | 2.0757 | 2.0757 | 2.0757 | 1.5814 | 1.8395 | 1.8395 | 1.8395 | 1.8395 | 1.8395
2020-11-19 12:00 | Summer | 3.0675 | 4.39 | 6.335 | 6.335 | 6.335 | 6.335 | 1.0374 | 1.6976 | 2.3263 | 2.7979 | 2.7979 | 2.7979 | 3.3533 | 4.3273 | 4.9655 | 5.3013 | 5.9731 | 6.6449 | 0.89928 | 1.7749 | 2.1299 | 2.1299 | 2.1299 | 2.1299 | 1.6004 | 1.8617 | 1.8617 | 1.8617 | 1.8617 | 1.8617
2020-11-19 13:00 | Summer | 3.0675 | 4.39 | 6.335 | 6.335 | 6.335 | 6.335 | 1.0117 | 1.6555 | 2.2686 | 2.7285 | 2.7285 | 2.7285 | 3.277 | 4.2289 | 4.8526 | 5.1809 | 5.8373 | 6.4938 | 0.89547 | 1.7674 | 2.1208 | 2.1208 | 2.1208 | 2.1208 | 1.6004 | 1.8617 | 1.8617 | 1.8617 | 1.8617 | 1.8617
2020-11-19 14:00 | Summer | 3.0294 | 4.3355 | 6.2563 | 6.2563 | 6.2563 | 6.2563 | 1.046 | 1.7116 | 2.3455 | 2.821 | 2.821 | 2.821 | 3.3151 | 4.2781 | 4.909 | 5.2411 | 5.9052 | 6.5693 | 0.87642 | 1.7298 | 2.0757 | 2.0757 | 2.0757 | 2.0757 | 1.6385 | 1.906 | 1.906 | 1.906 | 1.906 | 1.906
2020-11-19 15:00 | Summer | 3.0865 | 4.4173 | 6.3743 | 6.3743 | 6.3743 | 6.3743 | 1.1174 | 1.8285 | 2.5057 | 3.0137 | 3.0137 | 3.0137 | 3.3533 | 4.3273 | 4.9655 | 5.3013 | 5.9731 | 6.6449 | 0.89928 | 1.7749 | 2.1299 | 2.1299 | 2.1299 | 2.1299 | 1.5433 | 1.7952 | 1.7952 | 1.7952 | 1.7952 | 1.7952
2020-11-19 16:00 | Summer | 3.0675 | 4.39 | 6.335 | 6.335 | 6.335 | 6.335 | 1.1746 | 1.9221 | 2.6339 | 3.1678 | 3.1678 | 3.1678 | 3.201 | 4.1309 | 4.7401 | 5.0607 | 5.702 | 6.3432 | 0.88023 | 1.7373 | 2.0847 | 2.0847 | 2.0847 | 2.0847 | 1.4861 | 1.7287 | 1.7287 | 1.7287 | 1.7287 | 1.7287
2020-11-19 17:00 | Summer | 2.6674 | 3.8174 | 5.5087 | 5.5087 | 5.5087 | 5.5087 | 0.98965 | 1.6194 | 2.2192 | 2.6691 | 2.6691 | 2.6691 | 3.1249 | 4.0326 | 4.6274 | 4.9404 | 5.5664 | 6.1924 | 0.89928 | 1.7749 | 2.1299 | 2.1299 | 2.1299 | 2.1299 | 1.4176 | 1.649 | 1.649 | 1.649 | 1.649 | 1.649
2020-11-19 18:00 | Summer | 1.9493 | 2.7897 | 4.0256 | 4.0256 | 4.0256 | 4.0256 | 0.81449 | 1.3328 | 1.8264 | 2.1967 | 2.1967 | 2.1967 | 2.7817 | 3.5897 | 4.1191 | 4.3977 | 4.955 | 5.5122 | 0.89166 | 1.7599 | 2.1118 | 2.1118 | 2.1118 | 2.1118 | 0.96676 | 1.1246 | 1.1246 | 1.1246 | 1.1246 | 1.1246
2020-11-19 19:00 | Summer | 1.3527 | 1.936 | 2.7937 | 2.7937 | 2.7937 | 2.7937 | 0.59158 | 0.96804 | 1.3266 | 1.5955 | 1.5955 | 1.5955 | 2.553 | 3.2946 | 3.7805 | 4.0362 | 4.5477 | 5.0591 | 0.86498 | 1.7072 | 2.0486 | 2.0486 | 2.0486 | 2.0486 | 0.70494 | 0.82004 | 0.82004 | 0.82004 | 0.82004 | 0.82004
2020-11-19 20:00 | Summer | 1.2765 | 1.8269 | 2.6363 | 2.6363 | 2.6363 | 2.6363 | 0.50298 | 0.82306 | 1.1279 | 1.3565 | 1.3565 | 1.3565 | 2.4578 | 3.1717 | 3.6395 | 3.8856 | 4.378 | 4.8704 | 0.94119 | 1.8576 | 2.2291 | 2.2291 | 2.2291 | 2.2291 | 0.66684 | 0.77571 | 0.77571 | 0.77571 | 0.77571 | 0.77571
2020-11-19 21:00 | Summer | 1.2194 | 1.7451 | 2.5183 | 2.5183 | 2.5183 | 2.5183 | 0.47726 | 0.78098 | 1.0702 | 1.2872 | 1.2872 | 1.2872 | 2.3435 | 3.0242 | 3.4702 | 3.7049 | 4.1744 | 4.6438 | 0.86879 | 1.7147 | 2.0577 | 2.0577 | 2.0577 | 2.0577 | 0.55252 | 0.64273 | 0.64273 | 0.64273 | 0.64273 | 0.64273
2020-11-19 22:00 | Summer | 1.2003 | 1.7178 | 2.4789 | 2.4789 | 2.4789 | 2.4789 | 0.43725 | 0.7155 | 0.98051 | 1.1793 | 1.1793 | 1.1793 | 2.172 | 2.8029 | 3.2163 | 3.4338 | 3.8689 | 4.3041 | 0.81926 | 1.617 | 1.9403 | 1.9403 | 1.9403 | 1.9403 | 0.53347 | 0.62057 | 0.62057 | 0.62057 | 0.62057 | 0.62057
2020-11-19 23:00 | Summer | 1.1432 | 1.636 | 2.3609 | 2.3609 | 2.3609 | 2.3609 | 0.41725 | 0.68277 | 0.93565 | 1.1253 | 1.1253 | 1.1253 | 1.9434 | 2.5079 | 2.8777 | 3.0724 | 3.4617 | 3.851 | 0.78877 | 1.5568 | 1.8681 | 1.8681 | 1.8681 | 1.8681 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-11-20 | Summer | 1.0288 | 1.4724 | 2.1248 | 2.1248 | 2.1248 | 2.1248 | 0.38867 | 0.636 | 0.87156 | 1.0482 | 1.0482 | 1.0482 | 1.7713 | 2.2858 | 2.6229 | 2.8003 | 3.1552 | 3.51 | 0.65541 | 1.2936 | 1.5523 | 1.5523 | 1.5523 | 1.5523 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-11-20 01:00 | Summer | 1.0288 | 1.4724 | 2.1248 | 2.1248 | 2.1248 | 2.1248 | 0.41439 | 0.67809 | 0.92924 | 1.1176 | 1.1176 | 1.1176 | 1.6959 | 2.1885 | 2.5112 | 2.6811 | 3.0208 | 3.3605 | 0.64016 | 1.2635 | 1.5162 | 1.5162 | 1.5162 | 1.5162 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-11-20 02:00 | Summer | 1.0669 | 1.527 | 2.2035 | 2.2035 | 2.2035 | 2.2035 | 0.45726 | 0.74824 | 1.0254 | 1.2332 | 1.2332 | 1.2332 | 1.7147 | 2.2128 | 2.5392 | 2.7109 | 3.0544 | 3.3979 | 0.63254 | 1.2484 | 1.4981 | 1.4981 | 1.4981 | 1.4981 | 0.45699 | 0.5316 | 0.5316 | 0.5316 | 0.5316 | 0.5316
2020-11-20 03:00 | Summer | 1.031 | 1.4756 | 2.1293 | 2.1293 | 2.1293 | 2.1293 | 0.38295 | 0.62665 | 0.85874 | 1.0328 | 1.0328 | 1.0328 | 1.6195 | 2.0899 | 2.3981 | 2.5603 | 2.8847 | 3.2092 | 0.60206 | 1.1883 | 1.4259 | 1.4259 | 1.4259 | 1.4259 | 0.4862 | 0.56558 | 0.56558 | 0.56558 | 0.56558 | 0.56558
2020-11-20 04:00 | Summer | 1.1971 | 1.7132 | 2.4723 | 2.4723 | 2.4723 | 2.4723 | 0.45154 | 0.73889 | 1.0125 | 1.2178 | 1.2178 | 1.2178 | 1.6004 | 2.0653 | 2.3699 | 2.5302 | 2.8508 | 3.1714 | 0.59444 | 1.1732 | 1.4079 | 1.4079 | 1.4079 | 1.4079 | 0.53347 | 0.62057 | 0.62057 | 0.62057 | 0.62057 | 0.62057
2020-11-20 05:00 | Summer | 1.2194 | 1.7451 | 2.5183 | 2.5183 | 2.5183 | 2.5183 | 0.45726 | 0.74824 | 1.0254 | 1.2332 | 1.2332 | 1.2332 | 1.7147 | 2.2128 | 2.5392 | 2.7109 | 3.0544 | 3.3979 | 0.68208 | 1.3462 | 1.6155 | 1.6155 | 1.6155 | 1.6155 | 0.55252 | 0.64273 | 0.64273 | 0.64273 | 0.64273 | 0.64273
2020-11-20 06:00 | Summer | 1.3579 | 1.9433 | 2.8043 | 2.8043 | 2.8043 | 2.8043 | 0.59158 | 0.96804 | 1.3266 | 1.5955 | 1.5955 | 1.5955 | 1.8672 | 2.4095 | 2.7649 | 2.9519 | 3.3259 | 3.7 | 0.6897 | 1.3613 | 1.6335 | 1.6335 | 1.6335 | 1.6335 | 0.71584 | 0.83271 | 0.83271 | 0.83271 | 0.83271 | 0.83271
2020-11-20 07:00 | Summer | 2.0998 | 3.0052 | 4.3365 | 4.3365 | 4.3365 | 4.3365 | 0.72304 | 1.1832 | 1.6214 | 1.95 | 1.95 | 1.95 | 2.3054 | 2.975 | 3.4138 | 3.6447 | 4.1065 | 4.5683 | 1.0174 | 2.008 | 2.4096 | 2.4096 | 2.4096 | 2.4096 | 1.1241 | 1.3076 | 1.3076 | 1.3076 | 1.3076 | 1.3076
2020-11-20 08:00 | Summer | 2.9531 | 4.2264 | 6.0989 | 6.0989 | 6.0989 | 6.0989 | 0.83164 | 1.3609 | 1.8649 | 2.2429 | 2.2429 | 2.2429 | 2.7958 | 3.6079 | 4.1399 | 4.42 | 4.9801 | 5.5401 | 0.9793 | 1.9328 | 2.3194 | 2.3194 | 2.3194 | 2.3194 | 1.3511 | 1.5717 | 1.5717 | 1.5717 | 1.5717 | 1.5717
2020-11-20 09:00 | Summer | 3.0865 | 4.4173 | 6.3743 | 6.3743 | 6.3743 | 6.3743 | 0.97739 | 1.5994 | 2.1917 | 2.636 | 2.636 | 2.636 | 3.3676 | 4.3458 | 4.9867 | 5.324 | 5.9986 | 6.6732 | 0.97549 | 1.9253 | 2.3104 | 2.3104 | 2.3104 | 2.3104 | 1.5433 | 1.7952 | 1.7952 | 1.7952 | 1.7952 | 1.7952
2020-11-20 10:00 | Summer | 3.2961 | 4.7172 | 6.8071 | 6.8071 | 6.8071 | 6.8071 | 1.0603 | 1.735 | 2.3776 | 2.8595 | 2.8595 | 2.8595 | 3.4104 | 4.4011 | 5.0501 | 5.3917 | 6.0749 | 6.7581 | 0.93357 | 1.8426 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 1.6576 | 1.9282 | 1.9282 | 1.9282 | 1.9282 | 1.9282
2020-11-20 11:00 | Summer | 3.2199 | 4.6082 | 6.6498 | 6.6498 | 6.6498 | 6.6498 | 1.0974 | 1.7958 | 2.4609 | 2.9597 | 2.9597 | 2.9597 | 3.62 | 4.6715 | 5.3604 | 5.723 | 6.4482 | 7.1734 | 0.92214 | 1.82 | 2.184 | 2.184 | 2.184 | 2.184 | 1.7528 | 2.039 | 2.039 | 2.039 | 2.039 | 2.039
2020-11-20 12:00 | Summer | 3.277 | 4.69 | 6.7678 | 6.7678 | 6.7678 | 6.7678 | 1.266 | 2.0717 | 2.839 | 3.4145 | 3.4145 | 3.4145 | 3.8867 | 5.0157 | 5.7554 | 6.1447 | 6.9234 | 7.702 | 1.3337 | 2.6323 | 3.1587 | 3.1587 | 3.1587 | 3.1587 | 1.7719 | 2.0612 | 2.0612 | 2.0612 | 2.0612 | 2.0612
2020-11-20 13:00 | Summer | 3.258 | 4.6627 | 6.7285 | 6.7285 | 6.7285 | 6.7285 | 1.2289 | 2.0109 | 2.7557 | 3.3143 | 3.3143 | 3.3143 | 3.7724 | 4.8682 | 5.5861 | 5.964 | 6.7197 | 7.4755 | 1.3176 | 2.6006 | 3.1207 | 3.1207 | 3.1207 | 3.1207 | 1.7147 | 1.9947 | 1.9947 | 1.9947 | 1.9947 | 1.9947
2020-11-20 14:00 | Summer | 3.3723 | 4.8263 | 6.9645 | 6.9645 | 6.9645 | 6.9645 | 1.2517 | 2.0483 | 2.807 | 3.3759 | 3.3759 | 3.3759 | 4.001 | 5.1633 | 5.9247 | 6.3255 | 7.127 | 7.9285 | 1.2994 | 2.5646 | 3.0775 | 3.0775 | 3.0775 | 3.0775 | 1.7147 | 1.9947 | 1.9947 | 1.9947 | 1.9947 | 1.9947
2020-11-20 15:00 | Summer | 3.2963 | 4.7176 | 6.8076 | 6.8076 | 6.8076 | 6.8076 | 1.2346 | 2.0203 | 2.7685 | 3.3297 | 3.3297 | 3.3297 | 3.982 | 5.1387 | 5.8965 | 6.2953 | 7.0931 | 7.8908 | 1.2918 | 2.5495 | 3.0594 | 3.0594 | 3.0594 | 3.0594 | 1.6766 | 1.9504 | 1.9504 | 1.9504 | 1.9504 | 1.9504
2020-11-20 16:00 | Summer | 3.277 | 4.69 | 6.7678 | 6.7678 | 6.7678 | 6.7678 | 1.2032 | 1.9688 | 2.698 | 3.2449 | 3.2449 | 3.2449 | 3.9248 | 5.0649 | 5.8119 | 6.205 | 6.9912 | 7.7775 | 1.2803 | 2.527 | 3.0324 | 3.0324 | 3.0324 | 3.0324 | 1.5433 | 1.7952 | 1.7952 | 1.7952 | 1.7952 | 1.7952
2020-11-20 17:00 | Summer | 3.0892 | 4.4211 | 6.3799 | 6.3799 | 6.3799 | 6.3799 | 1.2032 | 1.9688 | 2.698 | 3.2449 | 3.2449 | 3.2449 | 3.6807 | 4.7498 | 5.4503 | 5.819 | 6.5563 | 7.2937 | 1.2803 | 2.527 | 3.0324 | 3.0324 | 3.0324 | 3.0324 | 1.4292 | 1.6625 | 1.6625 | 1.6625 | 1.6625 | 1.6625
2020-11-20 18:00 | Summer | 2.1364 | 3.0575 | 4.4121 | 4.4121 | 4.4121 | 4.4121 | 0.9214 | 1.5077 | 2.0662 | 2.485 | 2.485 | 2.485 | 3.6328 | 4.6881 | 5.3795 | 5.7434 | 6.4711 | 7.1989 | 1.1393 | 2.2487 | 2.6984 | 2.6984 | 2.6984 | 2.6984 | 1.1173 | 1.2997 | 1.2997 | 1.2997 | 1.2997 | 1.2997
2020-11-20 19:00 | Summer | 1.4232 | 2.0369 | 2.9393 | 2.9393 | 2.9393 | 2.9393 | 0.69446 | 1.1364 | 1.5573 | 1.8729 | 1.8729 | 1.8729 | 2.9922 | 3.8614 | 4.4309 | 4.7306 | 5.33 | 5.9295 | 1.1698 | 2.3089 | 2.7706 | 2.7706 | 2.7706 | 2.7706 | 0.72491 | 0.84326 | 0.84326 | 0.84326 | 0.84326 | 0.84326
2020-11-20 20:00 | Summer | 1.3527 | 1.936 | 2.7937 | 2.7937 | 2.7937 | 2.7937 | 0.49727 | 0.81371 | 1.1151 | 1.3411 | 1.3411 | 1.3411 | 2.6293 | 3.393 | 3.8934 | 4.1567 | 4.6835 | 5.2102 | 1.1241 | 2.2186 | 2.6623 | 2.6623 | 2.6623 | 2.6623 | 0.64779 | 0.75355 | 0.75355 | 0.75355 | 0.75355 | 0.75355
2020-11-20 21:00 | Summer | 1.2384 | 1.7724 | 2.5576 | 2.5576 | 2.5576 | 2.5576 | 0.51156 | 0.83709 | 1.1471 | 1.3797 | 1.3797 | 1.3797 | 2.4197 | 3.1225 | 3.583 | 3.8254 | 4.3101 | 4.7949 | 0.98692 | 1.9479 | 2.3374 | 2.3374 | 2.3374 | 2.3374 | 0.60968 | 0.70922 | 0.70922 | 0.70922 | 0.70922 | 0.70922
2020-11-20 22:00 | Summer | 1.1622 | 1.6633 | 2.4002 | 2.4002 | 2.4002 | 2.4002 | 0.43725 | 0.7155 | 0.98051 | 1.1793 | 1.1793 | 1.1793 | 2.3054 | 2.975 | 3.4138 | 3.6447 | 4.1065 | 4.5683 | 0.98692 | 1.9479 | 2.3374 | 2.3374 | 2.3374 | 2.3374 | 0.59063 | 0.68706 | 0.68706 | 0.68706 | 0.68706 | 0.68706
2020-11-20 23:00 | Summer | 1.0788 | 1.5439 | 2.228 | 2.228 | 2.228 | 2.228 | 0.5087 | 0.83242 | 1.1407 | 1.3719 | 1.3719 | 1.3719 | 2.0196 | 2.6062 | 2.9906 | 3.1929 | 3.5974 | 4.002 | 0.89547 | 1.7674 | 2.1208 | 2.1208 | 2.1208 | 2.1208 | 0.53345 | 0.62054 | 0.62054 | 0.62054 | 0.62054 | 0.62054
2020-11-21 | Summer | 1.1241 | 1.6088 | 2.3215 | 2.3215 | 2.3215 | 2.3215 | 0.41439 | 0.67809 | 0.92924 | 1.1176 | 1.1176 | 1.1176 | 1.8672 | 2.4095 | 2.7649 | 2.9519 | 3.3259 | 3.7 | 0.77387 | 1.5274 | 1.8328 | 1.8328 | 1.8328 | 1.8328 | 0.53347 | 0.62057 | 0.62057 | 0.62057 | 0.62057 | 0.62057
2020-11-21 01:00 | Summer | 1.0479 | 1.4997 | 2.1641 | 2.1641 | 2.1641 | 2.1641 | 0.42011 | 0.68744 | 0.94205 | 1.133 | 1.133 | 1.133 | 1.7909 | 2.3112 | 2.652 | 2.8314 | 3.1902 | 3.549 | 0.71256 | 1.4064 | 1.6877 | 1.6877 | 1.6877 | 1.6877 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-11-21 02:00 | Summer | 1.0669 | 1.527 | 2.2035 | 2.2035 | 2.2035 | 2.2035 | 0.42011 | 0.68744 | 0.94205 | 1.133 | 1.133 | 1.133 | 1.7147 | 2.2128 | 2.5392 | 2.7109 | 3.0544 | 3.3979 | 0.6897 | 1.3613 | 1.6335 | 1.6335 | 1.6335 | 1.6335 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-11-21 03:00 | Summer | 0.99471 | 1.4236 | 2.0543 | 2.0543 | 2.0543 | 2.0543 | 0.40582 | 0.66406 | 0.91001 | 1.0945 | 1.0945 | 1.0945 | 1.7147 | 2.2128 | 2.5392 | 2.7109 | 3.0544 | 3.3979 | 0.69351 | 1.3688 | 1.6425 | 1.6425 | 1.6425 | 1.6425 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-11-21 04:00 | Summer | 1.0479 | 1.4997 | 2.1641 | 2.1641 | 2.1641 | 2.1641 | 0.4001 | 0.65471 | 0.89719 | 1.0791 | 1.0791 | 1.0791 | 1.7466 | 2.2539 | 2.5863 | 2.7612 | 3.1111 | 3.461 | 0.63635 | 1.256 | 1.5072 | 1.5072 | 1.5072 | 1.5072 | 0.47624 | 0.55399 | 0.55399 | 0.55399 | 0.55399 | 0.55399
2020-11-21 05:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.37288 | 0.61016 | 0.83615 | 1.0056 | 1.0056 | 1.0056 | 1.7909 | 2.3112 | 2.652 | 2.8314 | 3.1902 | 3.549 | 0.67446 | 1.3312 | 1.5974 | 1.5974 | 1.5974 | 1.5974 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-11-21 06:00 | Summer | 1.0669 | 1.527 | 2.2035 | 2.2035 | 2.2035 | 2.2035 | 0.39438 | 0.64536 | 0.88438 | 1.0636 | 1.0636 | 1.0636 | 1.829 | 2.3603 | 2.7084 | 2.8916 | 3.2581 | 3.6245 | 0.86498 | 1.7072 | 2.0486 | 2.0486 | 2.0486 | 2.0486 | 0.5245 | 0.61013 | 0.61013 | 0.61013 | 0.61013 | 0.61013
2020-11-21 07:00 | Summer | 1.105 | 1.5815 | 2.2822 | 2.2822 | 2.2822 | 2.2822 | 0.47726 | 0.78098 | 1.0702 | 1.2872 | 1.2872 | 1.2872 | 2.102 | 2.7125 | 3.1126 | 3.3231 | 3.7442 | 4.1653 | 0.87261 | 1.7222 | 2.0667 | 2.0667 | 2.0667 | 2.0667 | 0.59063 | 0.68706 | 0.68706 | 0.68706 | 0.68706 | 0.68706
2020-11-21 08:00 | Summer | 1.1241 | 1.6088 | 2.3215 | 2.3215 | 2.3215 | 2.3215 | 0.49441 | 0.80903 | 1.1087 | 1.3334 | 1.3334 | 1.3334 | 2.2101 | 2.8521 | 3.2727 | 3.4941 | 3.9368 | 4.3796 | 1.006 | 1.9855 | 2.3826 | 2.3826 | 2.3826 | 2.3826 | 0.60968 | 0.70922 | 0.70922 | 0.70922 | 0.70922 | 0.70922
2020-11-21 09:00 | Summer | 1.1622 | 1.6633 | 2.4002 | 2.4002 | 2.4002 | 2.4002 | 0.54299 | 0.88854 | 1.2176 | 1.4644 | 1.4644 | 1.4644 | 2.4768 | 3.1963 | 3.6677 | 3.9158 | 4.4119 | 4.9081 | 0.94882 | 1.8727 | 2.2472 | 2.2472 | 2.2472 | 2.2472 | 0.60953 | 0.70905 | 0.70905 | 0.70905 | 0.70905 | 0.70905
2020-11-21 10:00 | Summer | 1.2194 | 1.7451 | 2.5183 | 2.5183 | 2.5183 | 2.5183 | 0.6173 | 1.0101 | 1.3842 | 1.6648 | 1.6648 | 1.6648 | 2.534 | 3.2701 | 3.7523 | 4.0061 | 4.5138 | 5.0214 | 0.97549 | 1.9253 | 2.3104 | 2.3104 | 2.3104 | 2.3104 | 0.62873 | 0.73138 | 0.73138 | 0.73138 | 0.73138 | 0.73138
2020-11-21 11:00 | Summer | 1.1813 | 1.6906 | 2.4396 | 2.4396 | 2.4396 | 2.4396 | 0.62873 | 1.0288 | 1.4099 | 1.6957 | 1.6957 | 1.6957 | 2.5149 | 3.2455 | 3.7241 | 3.976 | 4.4798 | 4.9836 | 0.91833 | 1.8125 | 2.175 | 2.175 | 2.175 | 2.175 | 0.64779 | 0.75355 | 0.75355 | 0.75355 | 0.75355 | 0.75355
2020-11-21 12:00 | Summer | 1.2003 | 1.7178 | 2.4789 | 2.4789 | 2.4789 | 2.4789 | 0.60873 | 0.9961 | 1.365 | 1.6417 | 1.6417 | 1.6417 | 2.6864 | 3.4668 | 3.978 | 4.2471 | 4.7853 | 5.3234 | 0.96025 | 1.8952 | 2.2743 | 2.2743 | 2.2743 | 2.2743 | 0.64779 | 0.75355 | 0.75355 | 0.75355 | 0.75355 | 0.75355
2020-11-21 13:00 | Summer | 1.1813 | 1.6906 | 2.4396 | 2.4396 | 2.4396 | 2.4396 | 0.63159 | 1.0335 | 1.4163 | 1.7034 | 1.7034 | 1.7034 | 2.7245 | 3.5159 | 4.0344 | 4.3073 | 4.8531 | 5.3989 | 0.94882 | 1.8727 | 2.2472 | 2.2472 | 2.2472 | 2.2472 | 0.64779 | 0.75355 | 0.75355 | 0.75355 | 0.75355 | 0.75355
2020-11-21 14:00 | Summer | 1.1622 | 1.6633 | 2.4002 | 2.4002 | 2.4002 | 2.4002 | 0.78591 | 1.286 | 1.7624 | 2.1196 | 2.1196 | 2.1196 | 2.8388 | 3.6634 | 4.2037 | 4.4881 | 5.0568 | 5.6255 | 1.0212 | 2.0156 | 2.4187 | 2.4187 | 2.4187 | 2.4187 | 0.60968 | 0.70922 | 0.70922 | 0.70922 | 0.70922 | 0.70922
2020-11-21 15:00 | Summer | 1.2194 | 1.7451 | 2.5183 | 2.5183 | 2.5183 | 2.5183 | 0.82878 | 1.3562 | 1.8585 | 2.2352 | 2.2352 | 2.2352 | 2.8388 | 3.6634 | 4.2037 | 4.4881 | 5.0568 | 5.6255 | 1.0403 | 2.0532 | 2.4638 | 2.4638 | 2.4638 | 2.4638 | 0.60968 | 0.70922 | 0.70922 | 0.70922 | 0.70922 | 0.70922
2020-11-21 16:00 | Summer | 1.2003 | 1.7178 | 2.4789 | 2.4789 | 2.4789 | 2.4789 | 0.85165 | 1.3936 | 1.9098 | 2.2969 | 2.2969 | 2.2969 | 3.0675 | 3.9585 | 4.5423 | 4.8495 | 5.464 | 6.0785 | 1.0669 | 2.1058 | 2.527 | 2.527 | 2.527 | 2.527 | 0.60968 | 0.70922 | 0.70922 | 0.70922 | 0.70922 | 0.70922
2020-11-21 17:00 | Summer | 1.2384 | 1.7724 | 2.5576 | 2.5576 | 2.5576 | 2.5576 | 0.82021 | 1.3422 | 1.8393 | 2.2121 | 2.2121 | 2.2121 | 2.9913 | 3.8601 | 4.4294 | 4.729 | 5.3283 | 5.9275 | 1.1965 | 2.3615 | 2.8338 | 2.8338 | 2.8338 | 2.8338 | 0.60968 | 0.70922 | 0.70922 | 0.70922 | 0.70922 | 0.70922
2020-11-21 18:00 | Summer | 1.1455 | 1.6394 | 2.3657 | 2.3657 | 2.3657 | 2.3657 | 0.80592 | 1.3188 | 1.8072 | 2.1735 | 2.1735 | 2.1735 | 2.8592 | 3.6898 | 4.2339 | 4.5203 | 5.0931 | 5.6659 | 1.2156 | 2.3991 | 2.8789 | 2.8789 | 2.8789 | 2.8789 | 0.59063 | 0.68706 | 0.68706 | 0.68706 | 0.68706 | 0.68706
2020-11-21 19:00 | Summer | 1.1432 | 1.636 | 2.3609 | 2.3609 | 2.3609 | 2.3609 | 0.7459 | 1.2206 | 1.6726 | 2.0117 | 2.0117 | 2.0117 | 2.8198 | 3.6389 | 4.1755 | 4.4579 | 5.0228 | 5.5877 | 1.1774 | 2.3239 | 2.7887 | 2.7887 | 2.7887 | 2.7887 | 0.59063 | 0.68706 | 0.68706 | 0.68706 | 0.68706 | 0.68706
2020-11-21 20:00 | Summer | 1.1432 | 1.636 | 2.3609 | 2.3609 | 2.3609 | 2.3609 | 0.72304 | 1.1832 | 1.6214 | 1.95 | 1.95 | 1.95 | 2.5723 | 3.3195 | 3.809 | 4.0667 | 4.582 | 5.0973 | 1.1127 | 2.1961 | 2.6353 | 2.6353 | 2.6353 | 2.6353 | 0.55252 | 0.64273 | 0.64273 | 0.64273 | 0.64273 | 0.64273
2020-11-21 21:00 | Summer | 1.105 | 1.5815 | 2.2822 | 2.2822 | 2.2822 | 2.2822 | 0.60873 | 0.9961 | 1.365 | 1.6417 | 1.6417 | 1.6417 | 2.3244 | 2.9996 | 3.442 | 3.6748 | 4.1404 | 4.6061 | 1.0593 | 2.0908 | 2.5089 | 2.5089 | 2.5089 | 2.5089 | 0.57128 | 0.66455 | 0.66455 | 0.66455 | 0.66455 | 0.66455
2020-11-21 22:00 | Summer | 1.0479 | 1.4997 | 2.1641 | 2.1641 | 2.1641 | 2.1641 | 0.47726 | 0.78098 | 1.0702 | 1.2872 | 1.2872 | 1.2872 | 2.2291 | 2.8767 | 3.3009 | 3.5242 | 3.9708 | 4.4173 | 1.0174 | 2.008 | 2.4096 | 2.4096 | 2.4096 | 2.4096 | 0.57158 | 0.6649 | 0.6649 | 0.6649 | 0.6649 | 0.6649
2020-11-21 23:00 | Summer | 1.0479 | 1.4997 | 2.1641 | 2.1641 | 2.1641 | 2.1641 | 0.44868 | 0.73421 | 1.0061 | 1.2101 | 1.2101 | 1.2101 | 1.9815 | 2.557 | 2.9341 | 3.1326 | 3.5296 | 3.9265 | 0.94501 | 1.8651 | 2.2382 | 2.2382 | 2.2382 | 2.2382 | 0.55252 | 0.64273 | 0.64273 | 0.64273 | 0.64273 | 0.64273
2020-11-22 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.41725 | 0.68277 | 0.93565 | 1.1253 | 1.1253 | 1.1253 | 1.8677 | 2.4103 | 2.7657 | 2.9528 | 3.327 | 3.7011 | 0.86498 | 1.7072 | 2.0486 | 2.0486 | 2.0486 | 2.0486 | 0.47726 | 0.55518 | 0.55518 | 0.55518 | 0.55518 | 0.55518
2020-11-22 01:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.46583 | 0.76227 | 1.0446 | 1.2563 | 1.2563 | 1.2563 | 1.7338 | 2.2374 | 2.5674 | 2.741 | 3.0884 | 3.4357 | 0.7621 | 1.5041 | 1.805 | 1.805 | 1.805 | 1.805 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-11-22 02:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.42582 | 0.6968 | 0.95487 | 1.1484 | 1.1484 | 1.1484 | 1.6977 | 2.1908 | 2.5139 | 2.6839 | 3.024 | 3.3641 | 0.70875 | 1.3989 | 1.6786 | 1.6786 | 1.6786 | 1.6786 | 0.53347 | 0.62057 | 0.62057 | 0.62057 | 0.62057 | 0.62057
2020-11-22 03:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.42296 | 0.69212 | 0.94846 | 1.1407 | 1.1407 | 1.1407 | 1.6576 | 2.1391 | 2.4545 | 2.6205 | 2.9526 | 3.2847 | 0.73924 | 1.459 | 1.7508 | 1.7508 | 1.7508 | 1.7508 | 0.49508 | 0.57591 | 0.57591 | 0.57591 | 0.57591 | 0.57591
2020-11-22 04:00 | Summer | 0.98773 | 1.4136 | 2.0399 | 2.0399 | 2.0399 | 2.0399 | 0.45154 | 0.73889 | 1.0125 | 1.2178 | 1.2178 | 1.2178 | 1.6195 | 2.0899 | 2.3981 | 2.5603 | 2.8847 | 3.2092 | 0.70494 | 1.3913 | 1.6696 | 1.6696 | 1.6696 | 1.6696 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-11-22 05:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.41439 | 0.67809 | 0.92924 | 1.1176 | 1.1176 | 1.1176 | 1.6957 | 2.1882 | 2.5109 | 2.6808 | 3.0205 | 3.3602 | 0.78496 | 1.5493 | 1.8591 | 1.8591 | 1.8591 | 1.8591 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-11-22 06:00 | Summer | 1.0288 | 1.4724 | 2.1248 | 2.1248 | 2.1248 | 2.1248 | 0.51442 | 0.84177 | 1.1535 | 1.3874 | 1.3874 | 1.3874 | 1.7714 | 2.286 | 2.6231 | 2.8006 | 3.1554 | 3.5103 | 0.8345 | 1.647 | 1.9764 | 1.9764 | 1.9764 | 1.9764 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-11-22 07:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.6173 | 1.0101 | 1.3842 | 1.6648 | 1.6648 | 1.6648 | 2.0005 | 2.5816 | 2.9624 | 3.1627 | 3.5635 | 3.9643 | 0.81545 | 1.6094 | 1.9313 | 1.9313 | 1.9313 | 1.9313 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-11-22 08:00 | Summer | 1.105 | 1.5815 | 2.2822 | 2.2822 | 2.2822 | 2.2822 | 0.44011 | 0.72018 | 0.98691 | 1.187 | 1.187 | 1.187 | 2.2673 | 2.9258 | 3.3573 | 3.5844 | 4.0386 | 4.4928 | 0.92976 | 1.8351 | 2.2021 | 2.2021 | 2.2021 | 2.2021 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-11-22 09:00 | Summer | 1.105 | 1.5815 | 2.2822 | 2.2822 | 2.2822 | 2.2822 | 0.48869 | 0.79968 | 1.0959 | 1.318 | 1.318 | 1.318 | 2.3054 | 2.975 | 3.4138 | 3.6447 | 4.1065 | 4.5683 | 0.92976 | 1.8351 | 2.2021 | 2.2021 | 2.2021 | 2.2021 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-11-22 10:00 | Summer | 1.1432 | 1.636 | 2.3609 | 2.3609 | 2.3609 | 2.3609 | 0.5087 | 0.83242 | 1.1407 | 1.3719 | 1.3719 | 1.3719 | 2.3435 | 3.0242 | 3.4702 | 3.7049 | 4.1744 | 4.6438 | 0.94119 | 1.8576 | 2.2291 | 2.2291 | 2.2291 | 2.2291 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-11-22 11:00 | Summer | 1.1622 | 1.6633 | 2.4002 | 2.4002 | 2.4002 | 2.4002 | 0.51442 | 0.84177 | 1.1535 | 1.3874 | 1.3874 | 1.3874 | 2.4768 | 3.1963 | 3.6677 | 3.9158 | 4.4119 | 4.9081 | 1.0326 | 2.0381 | 2.4457 | 2.4457 | 2.4457 | 2.4457 | 0.62873 | 0.73138 | 0.73138 | 0.73138 | 0.73138 | 0.73138
2020-11-22 12:00 | Summer | 1.105 | 1.5815 | 2.2822 | 2.2822 | 2.2822 | 2.2822 | 0.48298 | 0.79033 | 1.083 | 1.3026 | 1.3026 | 1.3026 | 2.4387 | 3.1471 | 3.6112 | 3.8555 | 4.3441 | 4.8326 | 0.96025 | 1.8952 | 2.2743 | 2.2743 | 2.2743 | 2.2743 | 0.60977 | 0.70933 | 0.70933 | 0.70933 | 0.70933 | 0.70933
2020-11-22 13:00 | Summer | 1.2003 | 1.7178 | 2.4789 | 2.4789 | 2.4789 | 2.4789 | 0.47155 | 0.77162 | 1.0574 | 1.2717 | 1.2717 | 1.2717 | 2.5149 | 3.2455 | 3.7241 | 3.976 | 4.4798 | 4.9836 | 0.96787 | 1.9103 | 2.2923 | 2.2923 | 2.2923 | 2.2923 | 0.58383 | 0.67915 | 0.67915 | 0.67915 | 0.67915 | 0.67915
2020-11-22 14:00 | Summer | 1.0669 | 1.527 | 2.2035 | 2.2035 | 2.2035 | 2.2035 | 0.46297 | 0.75759 | 1.0382 | 1.2486 | 1.2486 | 1.2486 | 2.553 | 3.2946 | 3.7805 | 4.0362 | 4.5477 | 5.0591 | 0.94501 | 1.8651 | 2.2382 | 2.2382 | 2.2382 | 2.2382 | 0.55252 | 0.64273 | 0.64273 | 0.64273 | 0.64273 | 0.64273
2020-11-22 15:00 | Summer | 1.1241 | 1.6088 | 2.3215 | 2.3215 | 2.3215 | 2.3215 | 0.53156 | 0.86983 | 1.192 | 1.4336 | 1.4336 | 1.4336 | 2.5721 | 3.3192 | 3.8087 | 4.0664 | 4.5816 | 5.0969 | 0.93357 | 1.8426 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 0.55252 | 0.64273 | 0.64273 | 0.64273 | 0.64273 | 0.64273
2020-11-22 16:00 | Summer | 1.1432 | 1.636 | 2.3609 | 2.3609 | 2.3609 | 2.3609 | 0.52585 | 0.86048 | 1.1792 | 1.4182 | 1.4182 | 1.4182 | 2.8198 | 3.6389 | 4.1755 | 4.4579 | 5.0228 | 5.5877 | 0.94501 | 1.8651 | 2.2382 | 2.2382 | 2.2382 | 2.2382 | 0.59063 | 0.68706 | 0.68706 | 0.68706 | 0.68706 | 0.68706
2020-11-22 17:00 | Summer | 1.1813 | 1.6906 | 2.4396 | 2.4396 | 2.4396 | 2.4396 | 0.55157 | 0.90257 | 1.2368 | 1.4876 | 1.4876 | 1.4876 | 2.6768 | 3.4543 | 3.9638 | 4.2319 | 4.7681 | 5.3044 | 0.96406 | 1.9027 | 2.2833 | 2.2833 | 2.2833 | 2.2833 | 0.59063 | 0.68706 | 0.68706 | 0.68706 | 0.68706 | 0.68706
2020-11-22 18:00 | Summer | 1.1813 | 1.6906 | 2.4396 | 2.4396 | 2.4396 | 2.4396 | 0.53428 | 0.87428 | 1.1981 | 1.4409 | 1.4409 | 1.4409 | 2.5782 | 3.3272 | 3.8178 | 4.0761 | 4.5926 | 5.1091 | 0.95263 | 1.8802 | 2.2562 | 2.2562 | 2.2562 | 2.2562 | 0.57356 | 0.6672 | 0.6672 | 0.6672 | 0.6672 | 0.6672
2020-11-22 19:00 | Summer | 1.2384 | 1.7724 | 2.5576 | 2.5576 | 2.5576 | 2.5576 | 0.54585 | 0.89321 | 1.224 | 1.4721 | 1.4721 | 1.4721 | 2.4006 | 3.098 | 3.5548 | 3.7953 | 4.2762 | 4.7571 | 0.96406 | 1.9027 | 2.2833 | 2.2833 | 2.2833 | 2.2833 | 0.59063 | 0.68706 | 0.68706 | 0.68706 | 0.68706 | 0.68706
2020-11-22 20:00 | Summer | 1.2384 | 1.7724 | 2.5576 | 2.5576 | 2.5576 | 2.5576 | 0.50584 | 0.82774 | 1.1343 | 1.3642 | 1.3642 | 1.3642 | 2.4006 | 3.098 | 3.5548 | 3.7953 | 4.2762 | 4.7571 | 1.0098 | 1.993 | 2.3916 | 2.3916 | 2.3916 | 2.3916 | 0.57158 | 0.6649 | 0.6649 | 0.6649 | 0.6649 | 0.6649
2020-11-22 21:00 | Summer | 1.1813 | 1.6906 | 2.4396 | 2.4396 | 2.4396 | 2.4396 | 0.48012 | 0.78565 | 1.0766 | 1.2949 | 1.2949 | 1.2949 | 2.3244 | 2.9996 | 3.442 | 3.6748 | 4.1404 | 4.6061 | 0.9793 | 1.9328 | 2.3194 | 2.3194 | 2.3194 | 2.3194 | 0.57158 | 0.6649 | 0.6649 | 0.6649 | 0.6649 | 0.6649
2020-11-22 22:00 | Summer | 1.1622 | 1.6633 | 2.4002 | 2.4002 | 2.4002 | 2.4002 | 0.43439 | 0.71083 | 0.9741 | 1.1715 | 1.1715 | 1.1715 | 2.0709 | 2.6725 | 3.0666 | 3.274 | 3.6889 | 4.1037 | 0.89908 | 1.7745 | 2.1294 | 2.1294 | 2.1294 | 2.1294 | 0.49542 | 0.57631 | 0.57631 | 0.57631 | 0.57631 | 0.57631
2020-11-22 23:00 | Summer | 1.1241 | 1.6088 | 2.3215 | 2.3215 | 2.3215 | 2.3215 | 0.43154 | 0.70615 | 0.96769 | 1.1638 | 1.1638 | 1.1638 | 1.9243 | 2.4833 | 2.8495 | 3.0422 | 3.4277 | 3.8132 | 0.84593 | 1.6696 | 2.0035 | 2.0035 | 2.0035 | 2.0035 | 0.48091 | 0.55942 | 0.55942 | 0.55942 | 0.55942 | 0.55942
2020-11-23 | Summer | 1.0288 | 1.4724 | 2.1248 | 2.1248 | 2.1248 | 2.1248 | 0.46583 | 0.76227 | 1.0446 | 1.2563 | 1.2563 | 1.2563 | 1.7719 | 2.2866 | 2.6238 | 2.8013 | 3.1562 | 3.5112 | 0.78877 | 1.5568 | 1.8681 | 1.8681 | 1.8681 | 1.8681 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-11-23 01:00 | Summer | 1.0479 | 1.4997 | 2.1641 | 2.1641 | 2.1641 | 2.1641 | 0.50013 | 0.81839 | 1.1215 | 1.3488 | 1.3488 | 1.3488 | 1.7528 | 2.262 | 2.5956 | 2.7712 | 3.1223 | 3.4734 | 0.79258 | 1.5643 | 1.8772 | 1.8772 | 1.8772 | 1.8772 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-11-23 02:00 | Summer | 1.0288 | 1.4724 | 2.1248 | 2.1248 | 2.1248 | 2.1248 | 0.55728 | 0.91192 | 1.2497 | 1.503 | 1.503 | 1.503 | 1.6576 | 2.1391 | 2.4545 | 2.6205 | 2.9526 | 3.2847 | 0.73924 | 1.459 | 1.7508 | 1.7508 | 1.7508 | 1.7508 | 0.57158 | 0.6649 | 0.6649 | 0.6649 | 0.6649 | 0.6649
2020-11-23 03:00 | Summer | 1.0288 | 1.4724 | 2.1248 | 2.1248 | 2.1248 | 2.1248 | 0.47441 | 0.7763 | 1.0638 | 1.2795 | 1.2795 | 1.2795 | 1.6576 | 2.1391 | 2.4545 | 2.6205 | 2.9526 | 3.2847 | 0.74686 | 1.4741 | 1.7689 | 1.7689 | 1.7689 | 1.7689 | 0.57158 | 0.6649 | 0.6649 | 0.6649 | 0.6649 | 0.6649
2020-11-23 04:00 | Summer | 1.2956 | 1.8542 | 2.6756 | 2.6756 | 2.6756 | 2.6756 | 0.50298 | 0.82306 | 1.1279 | 1.3565 | 1.3565 | 1.3565 | 1.6689 | 2.1537 | 2.4713 | 2.6384 | 2.9728 | 3.3071 | 0.75829 | 1.4966 | 1.796 | 1.796 | 1.796 | 1.796 | 0.55252 | 0.64273 | 0.64273 | 0.64273 | 0.64273 | 0.64273
2020-11-23 05:00 | Summer | 1.448 | 2.0723 | 2.9904 | 2.9904 | 2.9904 | 2.9904 | 0.54014 | 0.88386 | 1.2112 | 1.4567 | 1.4567 | 1.4567 | 1.8235 | 2.3532 | 2.7003 | 2.8829 | 3.2482 | 3.6135 | 0.75829 | 1.4966 | 1.796 | 1.796 | 1.796 | 1.796 | 0.57146 | 0.66476 | 0.66476 | 0.66476 | 0.66476 | 0.66476
2020-11-23 06:00 | Summer | 1.5623 | 2.2359 | 3.2265 | 3.2265 | 3.2265 | 3.2265 | 0.71733 | 1.1738 | 1.6085 | 1.9346 | 1.9346 | 1.9346 | 1.9815 | 2.557 | 2.9341 | 3.1326 | 3.5296 | 3.9265 | 0.89547 | 1.7674 | 2.1208 | 2.1208 | 2.1208 | 2.1208 | 0.75888 | 0.88278 | 0.88278 | 0.88278 | 0.88278 | 0.88278
2020-11-23 07:00 | Summer | 2.4578 | 3.5175 | 5.0759 | 5.0759 | 5.0759 | 5.0759 | 0.84593 | 1.3842 | 1.8969 | 2.2814 | 2.2814 | 2.2814 | 2.3962 | 3.0922 | 3.5483 | 3.7883 | 4.2683 | 4.7483 | 0.95644 | 1.8877 | 2.2652 | 2.2652 | 2.2652 | 2.2652 | 1.2003 | 1.3963 | 1.3963 | 1.3963 | 1.3963 | 1.3963
2020-11-23 08:00 | Summer | 2.7817 | 3.981 | 5.7448 | 5.7448 | 5.7448 | 5.7448 | 1.0117 | 1.6555 | 2.2686 | 2.7285 | 2.7285 | 2.7285 | 2.6293 | 3.393 | 3.8934 | 4.1567 | 4.6835 | 5.2102 | 0.99454 | 1.9629 | 2.3555 | 2.3555 | 2.3555 | 2.3555 | 1.3337 | 1.5514 | 1.5514 | 1.5514 | 1.5514 | 1.5514
2020-11-23 09:00 | Summer | 2.8651 | 4.1004 | 5.9171 | 5.9171 | 5.9171 | 5.9171 | 1.1089 | 1.8145 | 2.4865 | 2.9905 | 2.9905 | 2.9905 | 2.7817 | 3.5897 | 4.1191 | 4.3977 | 4.955 | 5.5122 | 1.0136 | 2.0005 | 2.4006 | 2.4006 | 2.4006 | 2.4006 | 1.448 | 1.6844 | 1.6844 | 1.6844 | 1.6844 | 1.6844
2020-11-23 10:00 | Summer | 2.8769 | 4.1174 | 5.9415 | 5.9415 | 5.9415 | 5.9415 | 1.0746 | 1.7584 | 2.4096 | 2.8981 | 2.8981 | 2.8981 | 2.8579 | 3.688 | 4.2319 | 4.5182 | 5.0907 | 5.6632 | 0.99454 | 1.9629 | 2.3555 | 2.3555 | 2.3555 | 2.3555 | 1.5052 | 1.7509 | 1.7509 | 1.7509 | 1.7509 | 1.7509
2020-11-23 11:00 | Summer | 2.896 | 4.1446 | 5.9808 | 5.9808 | 5.9808 | 5.9808 | 0.97453 | 1.5947 | 2.1853 | 2.6283 | 2.6283 | 2.6283 | 2.9722 | 3.8356 | 4.4012 | 4.6989 | 5.2943 | 5.8898 | 0.96025 | 1.8952 | 2.2743 | 2.2743 | 2.2743 | 2.2743 | 1.5623 | 1.8174 | 1.8174 | 1.8174 | 1.8174 | 1.8174
2020-11-23 12:00 | Summer | 3.0103 | 4.3082 | 6.2169 | 6.2169 | 6.2169 | 6.2169 | 1.0288 | 1.6835 | 2.3071 | 2.7747 | 2.7747 | 2.7747 | 3.1246 | 4.0323 | 4.6269 | 4.9399 | 5.5658 | 6.1918 | 1.0212 | 2.0156 | 2.4187 | 2.4187 | 2.4187 | 2.4187 | 1.5623 | 1.8174 | 1.8174 | 1.8174 | 1.8174 | 1.8174
2020-11-23 13:00 | Summer | 2.8579 | 4.0901 | 5.9022 | 5.9022 | 5.9022 | 5.9022 | 0.96882 | 1.5853 | 2.1725 | 2.6129 | 2.6129 | 2.6129 | 3.1246 | 4.0323 | 4.6269 | 4.9399 | 5.5658 | 6.1918 | 1.2994 | 2.5646 | 3.0775 | 3.0775 | 3.0775 | 3.0775 | 1.5052 | 1.7509 | 1.7509 | 1.7509 | 1.7509 | 1.7509
2020-11-23 14:00 | Summer | 2.6102 | 3.7356 | 5.3906 | 5.3906 | 5.3906 | 5.3906 | 0.86022 | 1.4076 | 1.929 | 2.32 | 2.32 | 2.32 | 2.7626 | 3.5651 | 4.0909 | 4.3676 | 4.921 | 5.4745 | 1.0708 | 2.1133 | 2.536 | 2.536 | 2.536 | 2.536 | 1.3146 | 1.5293 | 1.5293 | 1.5293 | 1.5293 | 1.5293
2020-11-23 15:00 | Summer | 2.4768 | 3.5447 | 5.1152 | 5.1152 | 5.1152 | 5.1152 | 0.81164 | 1.3281 | 1.82 | 2.189 | 2.189 | 2.189 | 2.8769 | 3.7126 | 4.2601 | 4.5483 | 5.1246 | 5.701 | 1.0669 | 2.1058 | 2.527 | 2.527 | 2.527 | 2.527 | 1.3337 | 1.5514 | 1.5514 | 1.5514 | 1.5514 | 1.5514
2020-11-23 16:00 | Summer | 2.6293 | 3.7629 | 5.43 | 5.43 | 5.43 | 5.43 | 0.87451 | 1.431 | 1.961 | 2.3585 | 2.3585 | 2.3585 | 2.9341 | 3.7864 | 4.3448 | 4.6387 | 5.2265 | 5.8142 | 1.0784 | 2.1284 | 2.554 | 2.554 | 2.554 | 2.554 | 1.3718 | 1.5957 | 1.5957 | 1.5957 | 1.5957 | 1.5957
2020-11-23 17:00 | Summer | 2.5143 | 3.5984 | 5.1926 | 5.1926 | 5.1926 | 5.1926 | 0.84593 | 1.3842 | 1.8969 | 2.2814 | 2.2814 | 2.2814 | 2.8198 | 3.6389 | 4.1755 | 4.4579 | 5.0228 | 5.5877 | 1.086 | 2.1434 | 2.5721 | 2.5721 | 2.5721 | 2.5721 | 1.2765 | 1.4849 | 1.4849 | 1.4849 | 1.4849 | 1.4849
2020-11-23 18:00 | Summer | 1.8352 | 2.6265 | 3.7901 | 3.7901 | 3.7901 | 3.7901 | 0.68303 | 1.1177 | 1.5316 | 1.8421 | 1.8421 | 1.8421 | 2.6674 | 3.4422 | 3.9498 | 4.217 | 4.7513 | 5.2857 | 0.92214 | 1.82 | 2.184 | 2.184 | 2.184 | 2.184 | 0.9224 | 1.073 | 1.073 | 1.073 | 1.073 | 1.073
2020-11-23 19:00 | Summer | 1.3337 | 1.9087 | 2.7543 | 2.7543 | 2.7543 | 2.7543 | 0.57157 | 0.9353 | 1.2817 | 1.5415 | 1.5415 | 1.5415 | 2.3816 | 3.0734 | 3.5266 | 3.7652 | 4.2423 | 4.7194 | 0.86879 | 1.7147 | 2.0577 | 2.0577 | 2.0577 | 2.0577 | 0.78115 | 0.90869 | 0.90869 | 0.90869 | 0.90869 | 0.90869
2020-11-23 20:00 | Summer | 1.2956 | 1.8542 | 2.6756 | 2.6756 | 2.6756 | 2.6756 | 0.54871 | 0.89789 | 1.2304 | 1.4799 | 1.4799 | 1.4799 | 2.191 | 2.8275 | 3.2445 | 3.4639 | 3.9029 | 4.3418 | 0.87642 | 1.7298 | 2.0757 | 2.0757 | 2.0757 | 2.0757 | 0.60968 | 0.70922 | 0.70922 | 0.70922 | 0.70922 | 0.70922
2020-11-23 21:00 | Summer | 1.1813 | 1.6906 | 2.4396 | 2.4396 | 2.4396 | 2.4396 | 0.47155 | 0.77162 | 1.0574 | 1.2717 | 1.2717 | 1.2717 | 2.0386 | 2.6308 | 3.0188 | 3.223 | 3.6314 | 4.0398 | 0.88023 | 1.7373 | 2.0847 | 2.0847 | 2.0847 | 2.0847 | 0.55265 | 0.64288 | 0.64288 | 0.64288 | 0.64288 | 0.64288
2020-11-23 22:00 | Summer | 1.105 | 1.5815 | 2.2822 | 2.2822 | 2.2822 | 2.2822 | 0.46268 | 0.75712 | 1.0375 | 1.2478 | 1.2478 | 1.2478 | 1.9624 | 2.5325 | 2.9059 | 3.1025 | 3.4956 | 3.8887 | 0.78115 | 1.5417 | 1.8501 | 1.8501 | 1.8501 | 1.8501 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-11-23 23:00 | Summer | 1.0721 | 1.5344 | 2.2142 | 2.2142 | 2.2142 | 2.2142 | 0.50298 | 0.82306 | 1.1279 | 1.3565 | 1.3565 | 1.3565 | 1.8481 | 2.3849 | 2.7366 | 2.9218 | 3.292 | 3.6622 | 0.72018 | 1.4214 | 1.7057 | 1.7057 | 1.7057 | 1.7057 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-11-24 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.41153 | 0.67342 | 0.92283 | 1.1099 | 1.1099 | 1.1099 | 1.7338 | 2.2374 | 2.5674 | 2.741 | 3.0884 | 3.4357 | 0.70494 | 1.3913 | 1.6696 | 1.6696 | 1.6696 | 1.6696 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-11-24 01:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.42868 | 0.70147 | 0.96128 | 1.1561 | 1.1561 | 1.1561 | 1.6576 | 2.1391 | 2.4545 | 2.6205 | 2.9526 | 3.2847 | 0.67827 | 1.3387 | 1.6064 | 1.6064 | 1.6064 | 1.6064 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-11-24 02:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.43154 | 0.70615 | 0.96769 | 1.1638 | 1.1638 | 1.1638 | 1.6385 | 2.1145 | 2.4263 | 2.5904 | 2.9187 | 3.2469 | 0.66051 | 1.3036 | 1.5644 | 1.5644 | 1.5644 | 1.5644 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-11-24 03:00 | Summer | 0.99165 | 1.4192 | 2.048 | 2.048 | 2.048 | 2.048 | 0.44583 | 0.72953 | 0.99973 | 1.2024 | 1.2024 | 1.2024 | 1.6576 | 2.1391 | 2.4545 | 2.6205 | 2.9526 | 3.2847 | 0.67065 | 1.3236 | 1.5884 | 1.5884 | 1.5884 | 1.5884 | 0.43821 | 0.50975 | 0.50975 | 0.50975 | 0.50975 | 0.50975
2020-11-24 04:00 | Summer | 1.1846 | 1.6954 | 2.4465 | 2.4465 | 2.4465 | 2.4465 | 0.42868 | 0.70147 | 0.96128 | 1.1561 | 1.1561 | 1.1561 | 1.6444 | 2.122 | 2.435 | 2.5997 | 2.9291 | 3.2585 | 0.73924 | 1.459 | 1.7508 | 1.7508 | 1.7508 | 1.7508 | 0.51206 | 0.59567 | 0.59567 | 0.59567 | 0.59567 | 0.59567
2020-11-24 05:00 | Summer | 1.2956 | 1.8542 | 2.6756 | 2.6756 | 2.6756 | 2.6756 | 0.47155 | 0.77162 | 1.0574 | 1.2717 | 1.2717 | 1.2717 | 1.7716 | 2.2862 | 2.6234 | 2.8008 | 3.1557 | 3.5106 | 0.70113 | 1.3838 | 1.6606 | 1.6606 | 1.6606 | 1.6606 | 0.57191 | 0.66529 | 0.66529 | 0.66529 | 0.66529 | 0.66529
2020-11-24 06:00 | Summer | 1.448 | 2.0723 | 2.9904 | 2.9904 | 2.9904 | 2.9904 | 0.58872 | 0.96336 | 1.3202 | 1.5878 | 1.5878 | 1.5878 | 1.8481 | 2.3849 | 2.7366 | 2.9218 | 3.292 | 3.6622 | 0.83069 | 1.6395 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.69917 | 0.81333 | 0.81333 | 0.81333 | 0.81333 | 0.81333
2020-11-24 07:00 | Summer | 1.9243 | 2.754 | 3.9741 | 3.9741 | 3.9741 | 3.9741 | 0.73733 | 1.2065 | 1.6534 | 1.9886 | 1.9886 | 1.9886 | 2.2482 | 2.9013 | 3.3291 | 3.5543 | 4.0047 | 4.4551 | 1.1012 | 2.1735 | 2.6082 | 2.6082 | 2.6082 | 2.6082 | 1.0211 | 1.1878 | 1.1878 | 1.1878 | 1.1878 | 1.1878
2020-11-24 08:00 | Summer | 2.2482 | 3.2175 | 4.643 | 4.643 | 4.643 | 4.643 | 0.72304 | 1.1832 | 1.6214 | 1.95 | 1.95 | 1.95 | 2.533 | 3.2688 | 3.7508 | 4.0046 | 4.512 | 5.0194 | 1.0898 | 2.1509 | 2.5811 | 2.5811 | 2.5811 | 2.5811 | 1.2956 | 1.5071 | 1.5071 | 1.5071 | 1.5071 | 1.5071
2020-11-24 09:00 | Summer | 2.5422 | 3.6383 | 5.2503 | 5.2503 | 5.2503 | 5.2503 | 0.85165 | 1.3936 | 1.9098 | 2.2969 | 2.2969 | 2.2969 | 2.5911 | 3.3438 | 3.8369 | 4.0965 | 4.6156 | 5.1347 | 1.0479 | 2.0682 | 2.4818 | 2.4818 | 2.4818 | 2.4818 | 1.3718 | 1.5957 | 1.5957 | 1.5957 | 1.5957 | 1.5957
2020-11-24 10:00 | Summer | 2.6293 | 3.7629 | 5.43 | 5.43 | 5.43 | 5.43 | 0.86308 | 1.4123 | 1.9354 | 2.3277 | 2.3277 | 2.3277 | 2.7436 | 3.5405 | 4.0627 | 4.3375 | 4.8871 | 5.4367 | 1.0708 | 2.1133 | 2.536 | 2.536 | 2.536 | 2.536 | 1.448 | 1.6844 | 1.6844 | 1.6844 | 1.6844 | 1.6844
2020-11-24 11:00 | Summer | 2.7436 | 3.9265 | 5.6661 | 5.6661 | 5.6661 | 5.6661 | 0.86308 | 1.4123 | 1.9354 | 2.3277 | 2.3277 | 2.3277 | 2.8388 | 3.6634 | 4.2037 | 4.4881 | 5.0568 | 5.6255 | 1.1127 | 2.1961 | 2.6353 | 2.6353 | 2.6353 | 2.6353 | 1.467 | 1.7066 | 1.7066 | 1.7066 | 1.7066 | 1.7066
2020-11-24 12:00 | Summer | 2.7436 | 3.9265 | 5.6661 | 5.6661 | 5.6661 | 5.6661 | 0.92881 | 1.5199 | 2.0828 | 2.505 | 2.505 | 2.505 | 2.8769 | 3.7126 | 4.2601 | 4.5483 | 5.1246 | 5.701 | 1.1355 | 2.2412 | 2.6894 | 2.6894 | 2.6894 | 2.6894 | 1.467 | 1.7066 | 1.7066 | 1.7066 | 1.7066 | 1.7066
2020-11-24 13:00 | Summer | 2.7817 | 3.981 | 5.7448 | 5.7448 | 5.7448 | 5.7448 | 0.92309 | 1.5105 | 2.07 | 2.4896 | 2.4896 | 2.4896 | 2.915 | 3.7618 | 4.3166 | 4.6086 | 5.1925 | 5.7765 | 1.1241 | 2.2186 | 2.6623 | 2.6623 | 2.6623 | 2.6623 | 1.5052 | 1.7509 | 1.7509 | 1.7509 | 1.7509 | 1.7509
2020-11-24 14:00 | Summer | 2.8388 | 4.0628 | 5.8628 | 5.8628 | 5.8628 | 5.8628 | 0.95167 | 1.5573 | 2.1341 | 2.5666 | 2.5666 | 2.5666 | 3.0103 | 3.8847 | 4.4576 | 4.7592 | 5.3622 | 5.9653 | 0.9793 | 1.9328 | 2.3194 | 2.3194 | 2.3194 | 2.3194 | 1.4811 | 1.7229 | 1.7229 | 1.7229 | 1.7229 | 1.7229
2020-11-24 15:00 | Summer | 2.8007 | 4.0083 | 5.7841 | 5.7841 | 5.7841 | 5.7841 | 0.85736 | 1.403 | 1.9226 | 2.3123 | 2.3123 | 2.3123 | 2.8579 | 3.688 | 4.2319 | 4.5182 | 5.0907 | 5.6632 | 1.0403 | 2.0532 | 2.4638 | 2.4638 | 2.4638 | 2.4638 | 1.4289 | 1.6622 | 1.6622 | 1.6622 | 1.6622 | 1.6622
2020-11-24 16:00 | Summer | 2.6102 | 3.7356 | 5.3906 | 5.3906 | 5.3906 | 5.3906 | 0.91452 | 1.4965 | 2.0507 | 2.4664 | 2.4664 | 2.4664 | 2.8007 | 3.6143 | 4.1473 | 4.4278 | 4.9889 | 5.55 | 1.0326 | 2.0381 | 2.4457 | 2.4457 | 2.4457 | 2.4457 | 1.2956 | 1.5071 | 1.5071 | 1.5071 | 1.5071 | 1.5071
2020-11-24 17:00 | Summer | 2.3054 | 3.2993 | 4.7611 | 4.7611 | 4.7611 | 4.7611 | 0.86022 | 1.4076 | 1.929 | 2.32 | 2.32 | 2.32 | 2.7608 | 3.5628 | 4.0882 | 4.3648 | 4.9178 | 5.4709 | 0.95263 | 1.8802 | 2.2562 | 2.2562 | 2.2562 | 2.2562 | 1.2226 | 1.4222 | 1.4222 | 1.4222 | 1.4222 | 1.4222
2020-11-24 18:00 | Summer | 1.7921 | 2.5648 | 3.7011 | 3.7011 | 3.7011 | 3.7011 | 0.62855 | 1.0285 | 1.4095 | 1.6952 | 1.6952 | 1.6952 | 2.4731 | 3.1914 | 3.6621 | 3.9098 | 4.4052 | 4.9007 | 0.89928 | 1.7749 | 2.1299 | 2.1299 | 2.1299 | 2.1299 | 0.85955 | 0.99989 | 0.99989 | 0.99989 | 0.99989 | 0.99989
2020-11-24 19:00 | Summer | 1.2765 | 1.8269 | 2.6363 | 2.6363 | 2.6363 | 2.6363 | 0.51442 | 0.84177 | 1.1535 | 1.3874 | 1.3874 | 1.3874 | 2.2673 | 2.9258 | 3.3573 | 3.5844 | 4.0386 | 4.4928 | 0.89547 | 1.7674 | 2.1208 | 2.1208 | 2.1208 | 2.1208 | 0.62309 | 0.72482 | 0.72482 | 0.72482 | 0.72482 | 0.72482
2020-11-24 20:00 | Summer | 1.2384 | 1.7724 | 2.5576 | 2.5576 | 2.5576 | 2.5576 | 0.50298 | 0.82306 | 1.1279 | 1.3565 | 1.3565 | 1.3565 | 2.191 | 2.8275 | 3.2445 | 3.4639 | 3.9029 | 4.3418 | 0.95263 | 1.8802 | 2.2562 | 2.2562 | 2.2562 | 2.2562 | 0.60968 | 0.70922 | 0.70922 | 0.70922 | 0.70922 | 0.70922
2020-11-24 21:00 | Summer | 1.086 | 1.5542 | 2.2428 | 2.2428 | 2.2428 | 2.2428 | 0.48298 | 0.79033 | 1.083 | 1.3026 | 1.3026 | 1.3026 | 2.172 | 2.8029 | 3.2163 | 3.4338 | 3.8689 | 4.3041 | 0.85355 | 1.6846 | 2.0216 | 2.0216 | 2.0216 | 2.0216 | 0.50523 | 0.58771 | 0.58771 | 0.58771 | 0.58771 | 0.58771
2020-11-24 22:00 | Summer | 1.0135 | 1.4505 | 2.0931 | 2.0931 | 2.0931 | 2.0931 | 0.43154 | 0.70615 | 0.96769 | 1.1638 | 1.1638 | 1.1638 | 1.9624 | 2.5325 | 2.9059 | 3.1025 | 3.4956 | 3.8887 | 0.89928 | 1.7749 | 2.1299 | 2.1299 | 2.1299 | 2.1299 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-11-24 23:00 | Summer | 0.97142 | 1.3903 | 2.0062 | 2.0062 | 2.0062 | 2.0062 | 0.4001 | 0.65471 | 0.89719 | 1.0791 | 1.0791 | 1.0791 | 1.8369 | 2.3705 | 2.7201 | 2.9041 | 3.2721 | 3.6401 | 0.74686 | 1.4741 | 1.7689 | 1.7689 | 1.7689 | 1.7689 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-11-25 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.42582 | 0.6968 | 0.95487 | 1.1484 | 1.1484 | 1.1484 | 1.81 | 2.3358 | 2.6802 | 2.8615 | 3.2241 | 3.5867 | 0.72781 | 1.4365 | 1.7238 | 1.7238 | 1.7238 | 1.7238 | 0.43821 | 0.50975 | 0.50975 | 0.50975 | 0.50975 | 0.50975
2020-11-25 01:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.37438 | 0.61262 | 0.83952 | 1.0097 | 1.0097 | 1.0097 | 1.6385 | 2.1145 | 2.4263 | 2.5904 | 2.9187 | 3.2469 | 0.63635 | 1.256 | 1.5072 | 1.5072 | 1.5072 | 1.5072 | 0.42903 | 0.49908 | 0.49908 | 0.49908 | 0.49908 | 0.49908
2020-11-25 02:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.45154 | 0.73889 | 1.0125 | 1.2178 | 1.2178 | 1.2178 | 1.5623 | 2.0161 | 2.3135 | 2.4699 | 2.7829 | 3.0959 | 0.63254 | 1.2484 | 1.4981 | 1.4981 | 1.4981 | 1.4981 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-11-25 03:00 | Summer | 0.95046 | 1.3603 | 1.9629 | 1.9629 | 1.9629 | 1.9629 | 0.43725 | 0.7155 | 0.98051 | 1.1793 | 1.1793 | 1.1793 | 1.6004 | 2.0653 | 2.3699 | 2.5302 | 2.8508 | 3.1714 | 0.62873 | 1.2409 | 1.4891 | 1.4891 | 1.4891 | 1.4891 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-11-25 04:00 | Summer | 1.0288 | 1.4724 | 2.1248 | 2.1248 | 2.1248 | 2.1248 | 0.39724 | 0.65003 | 0.89079 | 1.0713 | 1.0713 | 1.0713 | 1.601 | 2.0661 | 2.3708 | 2.5312 | 2.8519 | 3.1726 | 0.59063 | 1.1657 | 1.3989 | 1.3989 | 1.3989 | 1.3989 | 0.53347 | 0.62057 | 0.62057 | 0.62057 | 0.62057 | 0.62057
2020-11-25 05:00 | Summer | 1.1622 | 1.6633 | 2.4002 | 2.4002 | 2.4002 | 2.4002 | 0.45154 | 0.73889 | 1.0125 | 1.2178 | 1.2178 | 1.2178 | 1.6957 | 2.1882 | 2.5109 | 2.6808 | 3.0205 | 3.3602 | 0.71256 | 1.4064 | 1.6877 | 1.6877 | 1.6877 | 1.6877 | 0.6096 | 0.70913 | 0.70913 | 0.70913 | 0.70913 | 0.70913
2020-11-25 06:00 | Summer | 1.3704 | 1.9612 | 2.8301 | 2.8301 | 2.8301 | 2.8301 | 0.57729 | 0.94465 | 1.2945 | 1.5569 | 1.5569 | 1.5569 | 1.829 | 2.3603 | 2.7084 | 2.8916 | 3.2581 | 3.6245 | 0.79258 | 1.5643 | 1.8772 | 1.8772 | 1.8772 | 1.8772 | 0.77643 | 0.9032 | 0.9032 | 0.9032 | 0.9032 | 0.9032
2020-11-25 07:00 | Summer | 1.8415 | 2.6355 | 3.8031 | 3.8031 | 3.8031 | 3.8031 | 0.65159 | 1.0662 | 1.4611 | 1.7573 | 1.7573 | 1.7573 | 2.2291 | 2.8767 | 3.3009 | 3.5242 | 3.9708 | 4.4173 | 1.086 | 2.1434 | 2.5721 | 2.5721 | 2.5721 | 2.5721 | 0.99697 | 1.1597 | 1.1597 | 1.1597 | 1.1597 | 1.1597
2020-11-25 08:00 | Summer | 2.2101 | 3.163 | 4.5643 | 4.5643 | 4.5643 | 4.5643 | 0.81449 | 1.3328 | 1.8264 | 2.1967 | 2.1967 | 2.1967 | 2.5149 | 3.2455 | 3.7241 | 3.976 | 4.4798 | 4.9836 | 1.1012 | 2.1735 | 2.6082 | 2.6082 | 2.6082 | 2.6082 | 1.2575 | 1.4628 | 1.4628 | 1.4628 | 1.4628 | 1.4628
2020-11-25 09:00 | Summer | 2.4578 | 3.5175 | 5.0759 | 5.0759 | 5.0759 | 5.0759 | 0.89166 | 1.4591 | 1.9995 | 2.4048 | 2.4048 | 2.4048 | 2.6864 | 3.4668 | 3.978 | 4.2471 | 4.7853 | 5.3234 | 1.0517 | 2.0757 | 2.4909 | 2.4909 | 2.4909 | 2.4909 | 1.3146 | 1.5293 | 1.5293 | 1.5293 | 1.5293 | 1.5293
2020-11-25 10:00 | Summer | 2.5149 | 3.5993 | 5.1939 | 5.1939 | 5.1939 | 5.1939 | 0.77448 | 1.2673 | 1.7367 | 2.0888 | 2.0888 | 2.0888 | 2.7436 | 3.5405 | 4.0627 | 4.3375 | 4.8871 | 5.4367 | 1.0631 | 2.0983 | 2.5179 | 2.5179 | 2.5179 | 2.5179 | 1.4289 | 1.6622 | 1.6622 | 1.6622 | 1.6622 | 1.6622
2020-11-25 11:00 | Summer | 2.5721 | 3.6811 | 5.3119 | 5.3119 | 5.3119 | 5.3119 | 0.78591 | 1.286 | 1.7624 | 2.1196 | 2.1196 | 2.1196 | 2.8198 | 3.6389 | 4.1755 | 4.4579 | 5.0228 | 5.5877 | 1.0936 | 2.1585 | 2.5901 | 2.5901 | 2.5901 | 2.5901 | 1.467 | 1.7066 | 1.7066 | 1.7066 | 1.7066 | 1.7066
2020-11-25 12:00 | Summer | 2.7055 | 3.8719 | 5.5874 | 5.5874 | 5.5874 | 5.5874 | 0.89166 | 1.4591 | 1.9995 | 2.4048 | 2.4048 | 2.4048 | 2.8579 | 3.688 | 4.2319 | 4.5182 | 5.0907 | 5.6632 | 1.1584 | 2.2863 | 2.7436 | 2.7436 | 2.7436 | 2.7436 | 1.5814 | 1.8395 | 1.8395 | 1.8395 | 1.8395 | 1.8395
2020-11-25 13:00 | Summer | 2.8007 | 4.0083 | 5.7841 | 5.7841 | 5.7841 | 5.7841 | 0.95167 | 1.5573 | 2.1341 | 2.5666 | 2.5666 | 2.5666 | 3.1056 | 4.0077 | 4.5987 | 4.9098 | 5.5319 | 6.154 | 1.1546 | 2.2788 | 2.7345 | 2.7345 | 2.7345 | 2.7345 | 1.4861 | 1.7287 | 1.7287 | 1.7287 | 1.7287 | 1.7287
2020-11-25 14:00 | Summer | 2.7817 | 3.981 | 5.7448 | 5.7448 | 5.7448 | 5.7448 | 0.96596 | 1.5807 | 2.1661 | 2.6052 | 2.6052 | 2.6052 | 3.0294 | 3.9093 | 4.4858 | 4.7893 | 5.3962 | 6.003 | 1.1224 | 2.2152 | 2.6583 | 2.6583 | 2.6583 | 2.6583 | 1.4861 | 1.7287 | 1.7287 | 1.7287 | 1.7287 | 1.7287
2020-11-25 15:00 | Summer | 2.8198 | 4.0356 | 5.8235 | 5.8235 | 5.8235 | 5.8235 | 1.0174 | 1.6648 | 2.2814 | 2.7439 | 2.7439 | 2.7439 | 2.9341 | 3.7864 | 4.3448 | 4.6387 | 5.2265 | 5.8142 | 1.0136 | 2.0005 | 2.4006 | 2.4006 | 2.4006 | 2.4006 | 1.4289 | 1.6622 | 1.6622 | 1.6622 | 1.6622 | 1.6622
2020-11-25 16:00 | Summer | 2.7597 | 3.9495 | 5.6993 | 5.6993 | 5.6993 | 5.6993 | 1.0031 | 1.6415 | 2.2494 | 2.7054 | 2.7054 | 2.7054 | 3.1437 | 4.0568 | 4.6551 | 4.97 | 5.5998 | 6.2296 | 0.99454 | 1.9629 | 2.3555 | 2.3555 | 2.3555 | 2.3555 | 1.3908 | 1.6179 | 1.6179 | 1.6179 | 1.6179 | 1.6179
2020-11-25 17:00 | Summer | 2.6878 | 3.8466 | 5.5508 | 5.5508 | 5.5508 | 5.5508 | 1.1031 | 1.8051 | 2.4737 | 2.9751 | 2.9751 | 2.9751 | 3.0663 | 3.9569 | 4.5405 | 4.8476 | 5.4619 | 6.0761 | 1.006 | 1.9855 | 2.3826 | 2.3826 | 2.3826 | 2.3826 | 1.3845 | 1.6106 | 1.6106 | 1.6106 | 1.6106 | 1.6106
2020-11-25 18:00 | Summer | 1.9586 | 2.8031 | 4.0449 | 4.0449 | 4.0449 | 4.0449 | 0.7356 | 1.2037 | 1.6495 | 1.9839 | 1.9839 | 1.9839 | 2.8579 | 3.688 | 4.2319 | 4.5182 | 5.0907 | 5.6632 | 1.0593 | 2.0908 | 2.5089 | 2.5089 | 2.5089 | 2.5089 | 1.0215 | 1.1882 | 1.1882 | 1.1882 | 1.1882 | 1.1882
2020-11-25 19:00 | Summer | 1.467 | 2.0996 | 3.0298 | 3.0298 | 3.0298 | 3.0298 | 0.57269 | 0.93712 | 1.2842 | 1.5445 | 1.5445 | 1.5445 | 2.6311 | 3.3954 | 3.8961 | 4.1597 | 4.6867 | 5.2138 | 0.94882 | 1.8727 | 2.2472 | 2.2472 | 2.2472 | 2.2472 | 0.72404 | 0.84225 | 0.84225 | 0.84225 | 0.84225 | 0.84225
2020-11-25 20:00 | Summer | 1.2384 | 1.7724 | 2.5576 | 2.5576 | 2.5576 | 2.5576 | 0.51156 | 0.83709 | 1.1471 | 1.3797 | 1.3797 | 1.3797 | 2.4634 | 3.179 | 3.6478 | 3.8946 | 4.3881 | 4.8815 | 0.99073 | 1.9554 | 2.3465 | 2.3465 | 2.3465 | 2.3465 | 0.60968 | 0.70922 | 0.70922 | 0.70922 | 0.70922 | 0.70922
2020-11-25 21:00 | Summer | 1.2194 | 1.7451 | 2.5183 | 2.5183 | 2.5183 | 2.5183 | 0.44011 | 0.72018 | 0.98691 | 1.187 | 1.187 | 1.187 | 2.2482 | 2.9013 | 3.3291 | 3.5543 | 4.0047 | 4.4551 | 0.93357 | 1.8426 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 0.59063 | 0.68706 | 0.68706 | 0.68706 | 0.68706 | 0.68706
2020-11-25 22:00 | Summer | 1.1432 | 1.636 | 2.3609 | 2.3609 | 2.3609 | 2.3609 | 0.4544 | 0.74356 | 1.019 | 1.2255 | 1.2255 | 1.2255 | 2.0958 | 2.7046 | 3.1034 | 3.3133 | 3.7332 | 4.153 | 0.88023 | 1.7373 | 2.0847 | 2.0847 | 2.0847 | 2.0847 | 0.55252 | 0.64273 | 0.64273 | 0.64273 | 0.64273 | 0.64273
2020-11-25 23:00 | Summer | 1.0669 | 1.527 | 2.2035 | 2.2035 | 2.2035 | 2.2035 | 0.48869 | 0.79968 | 1.0959 | 1.318 | 1.318 | 1.318 | 1.8862 | 2.4341 | 2.7931 | 2.982 | 3.3599 | 3.7377 | 0.86879 | 1.7147 | 2.0577 | 2.0577 | 2.0577 | 2.0577 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-11-26 | Summer | 1.0288 | 1.4724 | 2.1248 | 2.1248 | 2.1248 | 2.1248 | 0.40582 | 0.66406 | 0.91001 | 1.0945 | 1.0945 | 1.0945 | 1.7528 | 2.262 | 2.5956 | 2.7712 | 3.1223 | 3.4734 | 0.80783 | 1.5944 | 1.9133 | 1.9133 | 1.9133 | 1.9133 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-11-26 01:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.42868 | 0.70147 | 0.96128 | 1.1561 | 1.1561 | 1.1561 | 1.6766 | 2.1636 | 2.4827 | 2.6507 | 2.9865 | 3.3224 | 0.74305 | 1.4665 | 1.7599 | 1.7599 | 1.7599 | 1.7599 | 0.46774 | 0.54411 | 0.54411 | 0.54411 | 0.54411 | 0.54411
2020-11-26 02:00 | Summer | 1.0288 | 1.4724 | 2.1248 | 2.1248 | 2.1248 | 2.1248 | 0.39724 | 0.65003 | 0.89079 | 1.0713 | 1.0713 | 1.0713 | 1.6766 | 2.1636 | 2.4827 | 2.6507 | 2.9865 | 3.3224 | 0.64779 | 1.2785 | 1.5342 | 1.5342 | 1.5342 | 1.5342 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-11-26 03:00 | Summer | 1.0288 | 1.4724 | 2.1248 | 2.1248 | 2.1248 | 2.1248 | 0.35711 | 0.58436 | 0.80079 | 0.96311 | 0.96311 | 0.96311 | 1.6385 | 2.1145 | 2.4263 | 2.5904 | 2.9187 | 3.2469 | 0.69732 | 1.3763 | 1.6516 | 1.6516 | 1.6516 | 1.6516 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-11-26 04:00 | Summer | 1.1609 | 1.6614 | 2.3975 | 2.3975 | 2.3975 | 2.3975 | 0.39153 | 0.64068 | 0.87797 | 1.0559 | 1.0559 | 1.0559 | 1.6195 | 2.0899 | 2.3981 | 2.5603 | 2.8847 | 3.2092 | 0.67827 | 1.3387 | 1.6064 | 1.6064 | 1.6064 | 1.6064 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-11-26 05:00 | Summer | 1.2575 | 1.7996 | 2.5969 | 2.5969 | 2.5969 | 2.5969 | 0.44868 | 0.73421 | 1.0061 | 1.2101 | 1.2101 | 1.2101 | 1.7528 | 2.262 | 2.5956 | 2.7712 | 3.1223 | 3.4734 | 0.93738 | 1.8501 | 2.2201 | 2.2201 | 2.2201 | 2.2201 | 0.64349 | 0.74855 | 0.74855 | 0.74855 | 0.74855 | 0.74855
2020-11-26 06:00 | Summer | 1.4465 | 2.0701 | 2.9873 | 2.9873 | 2.9873 | 2.9873 | 1.026 | 1.6789 | 2.3007 | 2.767 | 2.767 | 2.767 | 1.9434 | 2.5079 | 2.8777 | 3.0724 | 3.4617 | 3.851 | 0.78877 | 1.5568 | 1.8681 | 1.8681 | 1.8681 | 1.8681 | 0.81808 | 0.95165 | 0.95165 | 0.95165 | 0.95165 | 0.95165
2020-11-26 07:00 | Summer | 1.9614 | 2.807 | 4.0507 | 4.0507 | 4.0507 | 4.0507 | 0.69446 | 1.1364 | 1.5573 | 1.8729 | 1.8729 | 1.8729 | 2.4287 | 3.1341 | 3.5963 | 3.8396 | 4.3261 | 4.8127 | 1.0974 | 2.166 | 2.5992 | 2.5992 | 2.5992 | 2.5992 | 1.1432 | 1.3298 | 1.3298 | 1.3298 | 1.3298 | 1.3298
2020-11-26 08:00 | Summer | 3.0865 | 4.4173 | 6.3743 | 6.3743 | 6.3743 | 6.3743 | 0.84593 | 1.3842 | 1.8969 | 2.2814 | 2.2814 | 2.2814 | 2.7659 | 3.5693 | 4.0957 | 4.3727 | 4.9268 | 5.4809 | 1.0631 | 2.0983 | 2.5179 | 2.5179 | 2.5179 | 2.5179 | 1.4069 | 1.6366 | 1.6366 | 1.6366 | 1.6366 | 1.6366
2020-11-26 09:00 | Summer | 3.1437 | 4.4991 | 6.4924 | 6.4924 | 6.4924 | 6.4924 | 0.9431 | 1.5433 | 2.1148 | 2.5435 | 2.5435 | 2.5435 | 2.9913 | 3.8601 | 4.4294 | 4.729 | 5.3283 | 5.9275 | 1.0631 | 2.0983 | 2.5179 | 2.5179 | 2.5179 | 2.5179 | 1.4859 | 1.7285 | 1.7285 | 1.7285 | 1.7285 | 1.7285
2020-11-26 10:00 | Summer | 3.1437 | 4.4991 | 6.4924 | 6.4924 | 6.4924 | 6.4924 | 1.0231 | 1.6742 | 2.2943 | 2.7593 | 2.7593 | 2.7593 | 3.3932 | 4.3789 | 5.0247 | 5.3645 | 6.0443 | 6.7241 | 1.0441 | 2.0607 | 2.4728 | 2.4728 | 2.4728 | 2.4728 | 1.6195 | 1.8839 | 1.8839 | 1.8839 | 1.8839 | 1.8839
2020-11-26 11:00 | Summer | 3.1627 | 4.5264 | 6.5317 | 6.5317 | 6.5317 | 6.5317 | 1.0688 | 1.749 | 2.3968 | 2.8826 | 2.8826 | 2.8826 | 3.6771 | 4.7453 | 5.4451 | 5.8134 | 6.55 | 7.2867 | 1.0326 | 2.0381 | 2.4457 | 2.4457 | 2.4457 | 2.4457 | 1.6576 | 1.9282 | 1.9282 | 1.9282 | 1.9282 | 1.9282
2020-11-26 12:00 | Summer | 3.2199 | 4.6082 | 6.6498 | 6.6498 | 6.6498 | 6.6498 | 1.0717 | 1.7537 | 2.4032 | 2.8903 | 2.8903 | 2.8903 | 3.5057 | 4.524 | 5.1912 | 5.5423 | 6.2446 | 6.9469 | 1.0555 | 2.0832 | 2.4999 | 2.4999 | 2.4999 | 2.4999 | 1.6957 | 1.9725 | 1.9725 | 1.9725 | 1.9725 | 1.9725
2020-11-26 13:00 | Summer | 3.2389 | 4.6354 | 6.6891 | 6.6891 | 6.6891 | 6.6891 | 1.2889 | 2.1091 | 2.8903 | 3.4761 | 3.4761 | 3.4761 | 3.6009 | 4.6469 | 5.3322 | 5.6929 | 6.4143 | 7.1357 | 1.0669 | 2.1058 | 2.527 | 2.527 | 2.527 | 2.527 | 1.7147 | 1.9947 | 1.9947 | 1.9947 | 1.9947 | 1.9947
2020-11-26 14:00 | Summer | 3.2961 | 4.7172 | 6.8071 | 6.8071 | 6.8071 | 6.8071 | 1.2575 | 2.0577 | 2.8198 | 3.3913 | 3.3913 | 3.3913 | 3.6962 | 4.7699 | 5.4733 | 5.8435 | 6.584 | 7.3244 | 1.1432 | 2.2562 | 2.7075 | 2.7075 | 2.7075 | 2.7075 | 1.6766 | 1.9504 | 1.9504 | 1.9504 | 1.9504 | 1.9504
2020-11-26 15:00 | Summer | 3.3342 | 4.7718 | 6.8858 | 6.8858 | 6.8858 | 6.8858 | 1.3146 | 2.1512 | 2.9479 | 3.5455 | 3.5455 | 3.5455 | 3.8105 | 4.9174 | 5.6426 | 6.0243 | 6.7876 | 7.551 | 1.1889 | 2.3465 | 2.8158 | 2.8158 | 2.8158 | 2.8158 | 1.6766 | 1.9504 | 1.9504 | 1.9504 | 1.9504 | 1.9504
2020-11-26 16:00 | Summer | 3.3533 | 4.799 | 6.9252 | 6.9252 | 6.9252 | 6.9252 | 1.2746 | 2.0857 | 2.8582 | 3.4376 | 3.4376 | 3.4376 | 3.8296 | 4.942 | 5.6708 | 6.0544 | 6.8215 | 7.5887 | 1.1127 | 2.1961 | 2.6353 | 2.6353 | 2.6353 | 2.6353 | 1.6195 | 1.8839 | 1.8839 | 1.8839 | 1.8839 | 1.8839
2020-11-26 17:00 | Summer | 3.1627 | 4.5264 | 6.5317 | 6.5317 | 6.5317 | 6.5317 | 1.2546 | 2.053 | 2.8134 | 3.3836 | 3.3836 | 3.3836 | 3.7915 | 4.8928 | 5.6144 | 5.9941 | 6.7537 | 7.5132 | 1.0974 | 2.166 | 2.5992 | 2.5992 | 2.5992 | 2.5992 | 1.5433 | 1.7952 | 1.7952 | 1.7952 | 1.7952 | 1.7952
2020-11-26 18:00 | Summer | 2.2299 | 3.1914 | 4.6053 | 4.6053 | 4.6053 | 4.6053 | 1.0013 | 1.6385 | 2.2453 | 2.7005 | 2.7005 | 2.7005 | 3.6663 | 4.7313 | 5.4291 | 5.7963 | 6.5308 | 7.2652 | 1.166 | 2.3013 | 2.7616 | 2.7616 | 2.7616 | 2.7616 | 1.0779 | 1.2539 | 1.2539 | 1.2539 | 1.2539 | 1.2539
2020-11-26 19:00 | Summer | 1.3718 | 1.9632 | 2.833 | 2.833 | 2.833 | 2.833 | 0.64588 | 1.0569 | 1.4483 | 1.7419 | 1.7419 | 1.7419 | 3.3347 | 4.3034 | 4.9381 | 5.2721 | 5.9401 | 6.6082 | 1.1317 | 2.2337 | 2.6804 | 2.6804 | 2.6804 | 2.6804 | 0.7621 | 0.88653 | 0.88653 | 0.88653 | 0.88653 | 0.88653
2020-11-26 20:00 | Summer | 1.2956 | 1.8542 | 2.6756 | 2.6756 | 2.6756 | 2.6756 | 0.53728 | 0.87918 | 1.2048 | 1.449 | 1.449 | 1.449 | 2.7817 | 3.5897 | 4.1191 | 4.3977 | 4.955 | 5.5122 | 1.0784 | 2.1284 | 2.554 | 2.554 | 2.554 | 2.554 | 0.62889 | 0.73156 | 0.73156 | 0.73156 | 0.73156 | 0.73156
2020-11-26 21:00 | Summer | 1.2384 | 1.7724 | 2.5576 | 2.5576 | 2.5576 | 2.5576 | 0.49441 | 0.80903 | 1.1087 | 1.3334 | 1.3334 | 1.3334 | 2.412 | 3.1127 | 3.5717 | 3.8133 | 4.2965 | 4.7797 | 1.0403 | 2.0532 | 2.4638 | 2.4638 | 2.4638 | 2.4638 | 0.59063 | 0.68706 | 0.68706 | 0.68706 | 0.68706 | 0.68706
2020-11-26 22:00 | Summer | 1.2003 | 1.7178 | 2.4789 | 2.4789 | 2.4789 | 2.4789 | 0.42011 | 0.68744 | 0.94205 | 1.133 | 1.133 | 1.133 | 2.2291 | 2.8767 | 3.3009 | 3.5242 | 3.9708 | 4.4173 | 1.0022 | 1.978 | 2.3735 | 2.3735 | 2.3735 | 2.3735 | 0.53366 | 0.62079 | 0.62079 | 0.62079 | 0.62079 | 0.62079
2020-11-26 23:00 | Summer | 1.0669 | 1.527 | 2.2035 | 2.2035 | 2.2035 | 2.2035 | 0.44297 | 0.72486 | 0.99332 | 1.1947 | 1.1947 | 1.1947 | 2.0005 | 2.5816 | 2.9624 | 3.1627 | 3.5635 | 3.9643 | 0.95644 | 1.8877 | 2.2652 | 2.2652 | 2.2652 | 2.2652 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-11-27 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.42296 | 0.69212 | 0.94846 | 1.1407 | 1.1407 | 1.1407 | 1.8348 | 2.3678 | 2.717 | 2.9008 | 3.2684 | 3.636 | 0.82307 | 1.6245 | 1.9494 | 1.9494 | 1.9494 | 1.9494 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-11-27 01:00 | Summer | 1.0288 | 1.4724 | 2.1248 | 2.1248 | 2.1248 | 2.1248 | 0.45726 | 0.74824 | 1.0254 | 1.2332 | 1.2332 | 1.2332 | 1.7147 | 2.2128 | 2.5392 | 2.7109 | 3.0544 | 3.3979 | 0.724 | 1.4289 | 1.7147 | 1.7147 | 1.7147 | 1.7147 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-11-27 02:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.40296 | 0.65939 | 0.9036 | 1.0868 | 1.0868 | 1.0868 | 1.6576 | 2.1391 | 2.4545 | 2.6205 | 2.9526 | 3.2847 | 0.64888 | 1.2807 | 1.5368 | 1.5368 | 1.5368 | 1.5368 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-11-27 03:00 | Summer | 1.0288 | 1.4724 | 2.1248 | 2.1248 | 2.1248 | 2.1248 | 0.40296 | 0.65939 | 0.9036 | 1.0868 | 1.0868 | 1.0868 | 1.6696 | 2.1545 | 2.4723 | 2.6395 | 2.974 | 3.3085 | 0.65541 | 1.2936 | 1.5523 | 1.5523 | 1.5523 | 1.5523 | 0.46451 | 0.54035 | 0.54035 | 0.54035 | 0.54035 | 0.54035
2020-11-27 04:00 | Summer | 1.2126 | 1.7354 | 2.5043 | 2.5043 | 2.5043 | 2.5043 | 0.46012 | 0.75292 | 1.0318 | 1.2409 | 1.2409 | 1.2409 | 1.7147 | 2.2128 | 2.5392 | 2.7109 | 3.0544 | 3.3979 | 0.64397 | 1.271 | 1.5252 | 1.5252 | 1.5252 | 1.5252 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-11-27 05:00 | Summer | 1.2956 | 1.8542 | 2.6756 | 2.6756 | 2.6756 | 2.6756 | 0.44297 | 0.72486 | 0.99332 | 1.1947 | 1.1947 | 1.1947 | 1.7528 | 2.262 | 2.5956 | 2.7712 | 3.1223 | 3.4734 | 0.78877 | 1.5568 | 1.8681 | 1.8681 | 1.8681 | 1.8681 | 0.62826 | 0.73083 | 0.73083 | 0.73083 | 0.73083 | 0.73083
2020-11-27 06:00 | Summer | 1.5394 | 2.2032 | 3.1793 | 3.1793 | 3.1793 | 3.1793 | 0.563 | 0.92127 | 1.2625 | 1.5184 | 1.5184 | 1.5184 | 1.9362 | 2.4987 | 2.8672 | 3.0611 | 3.449 | 3.8369 | 0.84974 | 1.6771 | 2.0125 | 2.0125 | 2.0125 | 2.0125 | 0.74131 | 0.86234 | 0.86234 | 0.86234 | 0.86234 | 0.86234
2020-11-27 07:00 | Summer | 1.9226 | 2.7516 | 3.9707 | 3.9707 | 3.9707 | 3.9707 | 0.7909 | 1.2942 | 1.7735 | 2.133 | 2.133 | 2.133 | 2.4197 | 3.1225 | 3.583 | 3.8254 | 4.3101 | 4.7949 | 1.1279 | 2.2261 | 2.6714 | 2.6714 | 2.6714 | 2.6714 | 1.0678 | 1.2421 | 1.2421 | 1.2421 | 1.2421 | 1.2421
2020-11-27 08:00 | Summer | 2.6102 | 3.7356 | 5.3906 | 5.3906 | 5.3906 | 5.3906 | 0.84593 | 1.3842 | 1.8969 | 2.2814 | 2.2814 | 2.2814 | 2.6293 | 3.393 | 3.8934 | 4.1567 | 4.6835 | 5.2102 | 1.1245 | 2.2195 | 2.6634 | 2.6634 | 2.6634 | 2.6634 | 1.2575 | 1.4628 | 1.4628 | 1.4628 | 1.4628 | 1.4628
2020-11-27 09:00 | Summer | 2.6674 | 3.8174 | 5.5087 | 5.5087 | 5.5087 | 5.5087 | 0.9431 | 1.5433 | 2.1148 | 2.5435 | 2.5435 | 2.5435 | 2.9531 | 3.811 | 4.373 | 4.6688 | 5.2604 | 5.852 | 1.1203 | 2.2111 | 2.6533 | 2.6533 | 2.6533 | 2.6533 | 1.3527 | 1.5736 | 1.5736 | 1.5736 | 1.5736 | 1.5736
2020-11-27 10:00 | Summer | 2.7626 | 3.9538 | 5.7054 | 5.7054 | 5.7054 | 5.7054 | 0.399 | 0.65291 | 0.89473 | 1.0761 | 1.0761 | 1.0761 | 2.9913 | 3.8601 | 4.4294 | 4.729 | 5.3283 | 5.9275 | 1.1279 | 2.2261 | 2.6714 | 2.6714 | 2.6714 | 2.6714 | 1.448 | 1.6844 | 1.6844 | 1.6844 | 1.6844 | 1.6844
2020-11-27 11:00 | Summer | 2.8769 | 4.1174 | 5.9415 | 5.9415 | 5.9415 | 5.9415 | 1.1174 | 1.8285 | 2.5057 | 3.0137 | 3.0137 | 3.0137 | 3.3533 | 4.3273 | 4.9655 | 5.3013 | 5.9731 | 6.6449 | 1.1012 | 2.1735 | 2.6082 | 2.6082 | 2.6082 | 2.6082 | 1.6004 | 1.8617 | 1.8617 | 1.8617 | 1.8617 | 1.8617
2020-11-27 12:00 | Summer | 2.915 | 4.1719 | 6.0202 | 6.0202 | 6.0202 | 6.0202 | 1.1146 | 1.8238 | 2.4993 | 3.006 | 3.006 | 3.006 | 3.3342 | 4.3027 | 4.9373 | 5.2712 | 5.9392 | 6.6071 | 1.0249 | 2.0227 | 2.4273 | 2.4273 | 2.4273 | 2.4273 | 1.5808 | 1.8389 | 1.8389 | 1.8389 | 1.8389 | 1.8389
2020-11-27 13:00 | Summer | 2.915 | 4.1719 | 6.0202 | 6.0202 | 6.0202 | 6.0202 | 1.2032 | 1.9688 | 2.698 | 3.2449 | 3.2449 | 3.2449 | 3.6962 | 4.7699 | 5.4733 | 5.8435 | 6.584 | 7.3244 | 1.0669 | 2.1058 | 2.527 | 2.527 | 2.527 | 2.527 | 1.5814 | 1.8395 | 1.8395 | 1.8395 | 1.8395 | 1.8395
2020-11-27 14:00 | Summer | 3.1437 | 4.4991 | 6.4924 | 6.4924 | 6.4924 | 6.4924 | 1.2232 | 2.0016 | 2.7429 | 3.2989 | 3.2989 | 3.2989 | 3.7915 | 4.8928 | 5.6144 | 5.9941 | 6.7537 | 7.5132 | 1.1241 | 2.2186 | 2.6623 | 2.6623 | 2.6623 | 2.6623 | 1.6385 | 1.906 | 1.906 | 1.906 | 1.906 | 1.906
2020-11-27 15:00 | Summer | 3.0484 | 4.3628 | 6.2956 | 6.2956 | 6.2956 | 6.2956 | 1.1974 | 1.9595 | 2.6852 | 3.2295 | 3.2295 | 3.2295 | 3.7915 | 4.8928 | 5.6144 | 5.9941 | 6.7537 | 7.5132 | 1.1203 | 2.2111 | 2.6533 | 2.6533 | 2.6533 | 2.6533 | 1.637 | 1.9042 | 1.9042 | 1.9042 | 1.9042 | 1.9042
2020-11-27 16:00 | Summer | 3.0294 | 4.3355 | 6.2563 | 6.2563 | 6.2563 | 6.2563 | 1.1917 | 1.9501 | 2.6724 | 3.2141 | 3.2141 | 3.2141 | 3.8105 | 4.9174 | 5.6426 | 6.0243 | 6.7876 | 7.551 | 1.1317 | 2.2337 | 2.6804 | 2.6804 | 2.6804 | 2.6804 | 1.6385 | 1.906 | 1.906 | 1.906 | 1.906 | 1.906
2020-11-27 17:00 | Summer | 2.896 | 4.1446 | 5.9808 | 5.9808 | 5.9808 | 5.9808 | 1.186 | 1.9408 | 2.6596 | 3.1987 | 3.1987 | 3.1987 | 3.8105 | 4.9174 | 5.6426 | 6.0243 | 6.7876 | 7.551 | 1.1889 | 2.3465 | 2.8158 | 2.8158 | 2.8158 | 2.8158 | 1.5052 | 1.7509 | 1.7509 | 1.7509 | 1.7509 | 1.7509
2020-11-27 18:00 | Summer | 2.0205 | 2.8917 | 4.1728 | 4.1728 | 4.1728 | 4.1728 | 1.0145 | 1.6602 | 2.275 | 2.7362 | 2.7362 | 2.7362 | 3.62 | 4.6715 | 5.3604 | 5.723 | 6.4482 | 7.1734 | 1.2156 | 2.3991 | 2.8789 | 2.8789 | 2.8789 | 2.8789 | 1.0565 | 1.229 | 1.229 | 1.229 | 1.229 | 1.229
2020-11-27 19:00 | Summer | 1.3718 | 1.9632 | 2.833 | 2.833 | 2.833 | 2.833 | 0.79281 | 1.2973 | 1.7778 | 2.1382 | 2.1382 | 2.1382 | 3.1034 | 4.0049 | 4.5955 | 4.9063 | 5.5281 | 6.1498 | 1.2308 | 2.4292 | 2.915 | 2.915 | 2.915 | 2.915 | 0.78115 | 0.90869 | 0.90869 | 0.90869 | 0.90869 | 0.90869
2020-11-27 20:00 | Summer | 1.2765 | 1.8269 | 2.6363 | 2.6363 | 2.6363 | 2.6363 | 0.69446 | 1.1364 | 1.5573 | 1.8729 | 1.8729 | 1.8729 | 2.7436 | 3.5405 | 4.0627 | 4.3375 | 4.8871 | 5.4367 | 1.1889 | 2.3465 | 2.8158 | 2.8158 | 2.8158 | 2.8158 | 0.68589 | 0.79787 | 0.79787 | 0.79787 | 0.79787 | 0.79787
2020-11-27 21:00 | Summer | 1.2194 | 1.7451 | 2.5183 | 2.5183 | 2.5183 | 2.5183 | 0.66588 | 1.0896 | 1.4932 | 1.7959 | 1.7959 | 1.7959 | 2.6637 | 3.4374 | 3.9443 | 4.2111 | 4.7447 | 5.2783 | 1.2003 | 2.369 | 2.8428 | 2.8428 | 2.8428 | 2.8428 | 0.64779 | 0.75355 | 0.75355 | 0.75355 | 0.75355 | 0.75355
2020-11-27 22:00 | Summer | 1.1622 | 1.6633 | 2.4002 | 2.4002 | 2.4002 | 2.4002 | 0.6173 | 1.0101 | 1.3842 | 1.6648 | 1.6648 | 1.6648 | 2.5149 | 3.2455 | 3.7241 | 3.976 | 4.4798 | 4.9836 | 1.1813 | 2.3314 | 2.7977 | 2.7977 | 2.7977 | 2.7977 | 0.62873 | 0.73138 | 0.73138 | 0.73138 | 0.73138 | 0.73138
2020-11-27 23:00 | Summer | 1.105 | 1.5815 | 2.2822 | 2.2822 | 2.2822 | 2.2822 | 0.48012 | 0.78565 | 1.0766 | 1.2949 | 1.2949 | 1.2949 | 2.2818 | 2.9446 | 3.3789 | 3.6074 | 4.0645 | 4.5217 | 1.0212 | 2.0156 | 2.4187 | 2.4187 | 2.4187 | 2.4187 | 0.57158 | 0.6649 | 0.6649 | 0.6649 | 0.6649 | 0.6649
2020-11-28 | Summer | 1.105 | 1.5815 | 2.2822 | 2.2822 | 2.2822 | 2.2822 | 0.43154 | 0.70615 | 0.96769 | 1.1638 | 1.1638 | 1.1638 | 2.2101 | 2.8521 | 3.2727 | 3.4941 | 3.9368 | 4.3796 | 0.91833 | 1.8125 | 2.175 | 2.175 | 2.175 | 2.175 | 0.55252 | 0.64273 | 0.64273 | 0.64273 | 0.64273 | 0.64273
2020-11-28 01:00 | Summer | 1.1241 | 1.6088 | 2.3215 | 2.3215 | 2.3215 | 2.3215 | 0.42868 | 0.70147 | 0.96128 | 1.1561 | 1.1561 | 1.1561 | 1.9434 | 2.5079 | 2.8777 | 3.0724 | 3.4617 | 3.851 | 0.84593 | 1.6696 | 2.0035 | 2.0035 | 2.0035 | 2.0035 | 0.57158 | 0.6649 | 0.6649 | 0.6649 | 0.6649 | 0.6649
2020-11-28 02:00 | Summer | 1.1241 | 1.6088 | 2.3215 | 2.3215 | 2.3215 | 2.3215 | 0.46583 | 0.76227 | 1.0446 | 1.2563 | 1.2563 | 1.2563 | 1.9624 | 2.5325 | 2.9059 | 3.1025 | 3.4956 | 3.8887 | 0.80783 | 1.5944 | 1.9133 | 1.9133 | 1.9133 | 1.9133 | 0.51441 | 0.59839 | 0.59839 | 0.59839 | 0.59839 | 0.59839
2020-11-28 03:00 | Summer | 1.0288 | 1.4724 | 2.1248 | 2.1248 | 2.1248 | 2.1248 | 0.40279 | 0.65912 | 0.90323 | 1.0863 | 1.0863 | 1.0863 | 1.8481 | 2.3849 | 2.7366 | 2.9218 | 3.292 | 3.6622 | 0.77734 | 1.5342 | 1.8411 | 1.8411 | 1.8411 | 1.8411 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-11-28 04:00 | Summer | 1.1813 | 1.6906 | 2.4396 | 2.4396 | 2.4396 | 2.4396 | 0.47441 | 0.7763 | 1.0638 | 1.2795 | 1.2795 | 1.2795 | 1.8481 | 2.3849 | 2.7366 | 2.9218 | 3.292 | 3.6622 | 0.75829 | 1.4966 | 1.796 | 1.796 | 1.796 | 1.796 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-11-28 05:00 | Summer | 1.1241 | 1.6088 | 2.3215 | 2.3215 | 2.3215 | 2.3215 | 0.40867 | 0.66874 | 0.91642 | 1.1022 | 1.1022 | 1.1022 | 1.8672 | 2.4095 | 2.7649 | 2.9519 | 3.3259 | 3.7 | 0.74686 | 1.4741 | 1.7689 | 1.7689 | 1.7689 | 1.7689 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-11-28 06:00 | Summer | 1.086 | 1.5542 | 2.2428 | 2.2428 | 2.2428 | 2.2428 | 0.44297 | 0.72486 | 0.99332 | 1.1947 | 1.1947 | 1.1947 | 1.9434 | 2.5079 | 2.8777 | 3.0724 | 3.4617 | 3.851 | 0.87261 | 1.7222 | 2.0667 | 2.0667 | 2.0667 | 2.0667 | 0.51429 | 0.59826 | 0.59826 | 0.59826 | 0.59826 | 0.59826
2020-11-28 07:00 | Summer | 1.2003 | 1.7178 | 2.4789 | 2.4789 | 2.4789 | 2.4789 | 0.53156 | 0.86983 | 1.192 | 1.4336 | 1.4336 | 1.4336 | 2.1609 | 2.7886 | 3.1998 | 3.4163 | 3.8492 | 4.2821 | 0.94501 | 1.8651 | 2.2382 | 2.2382 | 2.2382 | 2.2382 | 0.60968 | 0.70922 | 0.70922 | 0.70922 | 0.70922 | 0.70922
2020-11-28 08:00 | Summer | 1.3146 | 1.8814 | 2.715 | 2.715 | 2.715 | 2.715 | 0.54585 | 0.89321 | 1.224 | 1.4721 | 1.4721 | 1.4721 | 2.4768 | 3.1963 | 3.6677 | 3.9158 | 4.4119 | 4.9081 | 0.9793 | 1.9328 | 2.3194 | 2.3194 | 2.3194 | 2.3194 | 0.62873 | 0.73138 | 0.73138 | 0.73138 | 0.73138 | 0.73138
2020-11-28 09:00 | Summer | 1.3337 | 1.9087 | 2.7543 | 2.7543 | 2.7543 | 2.7543 | 0.71161 | 1.1645 | 1.5957 | 1.9192 | 1.9192 | 1.9192 | 2.6293 | 3.393 | 3.8934 | 4.1567 | 4.6835 | 5.2102 | 1.1089 | 2.1885 | 2.6262 | 2.6262 | 2.6262 | 2.6262 | 0.74274 | 0.86401 | 0.86401 | 0.86401 | 0.86401 | 0.86401
2020-11-28 10:00 | Summer | 1.448 | 2.0723 | 2.9904 | 2.9904 | 2.9904 | 2.9904 | 0.73161 | 1.1972 | 1.6406 | 1.9731 | 1.9731 | 1.9731 | 2.7892 | 3.5993 | 4.1302 | 4.4095 | 4.9683 | 5.527 | 0.97549 | 1.9253 | 2.3104 | 2.3104 | 2.3104 | 2.3104 | 0.80021 | 0.93085 | 0.93085 | 0.93085 | 0.93085 | 0.93085
2020-11-28 11:00 | Summer | 1.467 | 2.0996 | 3.0298 | 3.0298 | 3.0298 | 3.0298 | 0.9088 | 1.4871 | 2.0379 | 2.451 | 2.451 | 2.451 | 2.9913 | 3.8601 | 4.4294 | 4.729 | 5.3283 | 5.9275 | 0.98692 | 1.9479 | 2.3374 | 2.3374 | 2.3374 | 2.3374 | 0.77567 | 0.90231 | 0.90231 | 0.90231 | 0.90231 | 0.90231
2020-11-28 12:00 | Summer | 1.5242 | 2.1814 | 3.1478 | 3.1478 | 3.1478 | 3.1478 | 0.93452 | 1.5292 | 2.0956 | 2.5204 | 2.5204 | 2.5204 | 3.041 | 3.9243 | 4.503 | 4.8076 | 5.4168 | 6.026 | 1.0288 | 2.0306 | 2.4367 | 2.4367 | 2.4367 | 2.4367 | 0.78115 | 0.90869 | 0.90869 | 0.90869 | 0.90869 | 0.90869
2020-11-28 13:00 | Summer | 1.5242 | 2.1814 | 3.1478 | 3.1478 | 3.1478 | 3.1478 | 0.96882 | 1.5853 | 2.1725 | 2.6129 | 2.6129 | 2.6129 | 3.1437 | 4.0568 | 4.6551 | 4.97 | 5.5998 | 6.2296 | 1.1089 | 2.1885 | 2.6262 | 2.6262 | 2.6262 | 2.6262 | 0.83831 | 0.97518 | 0.97518 | 0.97518 | 0.97518 | 0.97518
2020-11-28 14:00 | Summer | 1.3718 | 1.9632 | 2.833 | 2.833 | 2.833 | 2.833 | 1.1003 | 1.8005 | 2.4673 | 2.9674 | 2.9674 | 2.9674 | 3.2389 | 4.1798 | 4.7962 | 5.1206 | 5.7695 | 6.4183 | 1.0822 | 2.1359 | 2.5631 | 2.5631 | 2.5631 | 2.5631 | 0.80021 | 0.93085 | 0.93085 | 0.93085 | 0.93085 | 0.93085
2020-11-28 15:00 | Summer | 1.2956 | 1.8542 | 2.6756 | 2.6756 | 2.6756 | 2.6756 | 1.0051 | 1.6446 | 2.2538 | 2.7106 | 2.7106 | 2.7106 | 3.2008 | 4.1306 | 4.7398 | 5.0604 | 5.7016 | 6.3428 | 1.1432 | 2.2562 | 2.7075 | 2.7075 | 2.7075 | 2.7075 | 0.74305 | 0.86436 | 0.86436 | 0.86436 | 0.86436 | 0.86436
2020-11-28 16:00 | Summer | 1.1813 | 1.6906 | 2.4396 | 2.4396 | 2.4396 | 2.4396 | 0.95453 | 1.562 | 2.1405 | 2.5743 | 2.5743 | 2.5743 | 3.0865 | 3.9831 | 4.5705 | 4.8796 | 5.498 | 6.1163 | 1.1622 | 2.2938 | 2.7526 | 2.7526 | 2.7526 | 2.7526 | 0.74305 | 0.86436 | 0.86436 | 0.86436 | 0.86436 | 0.86436
2020-11-28 17:00 | Summer | 1.2384 | 1.7724 | 2.5576 | 2.5576 | 2.5576 | 2.5576 | 0.87737 | 1.4357 | 1.9674 | 2.3662 | 2.3662 | 2.3662 | 3.0188 | 3.8956 | 4.4701 | 4.7725 | 5.3773 | 5.982 | 1.1432 | 2.2562 | 2.7075 | 2.7075 | 2.7075 | 2.7075 | 0.724 | 0.8422 | 0.8422 | 0.8422 | 0.8422 | 0.8422
2020-11-28 18:00 | Summer | 1.1622 | 1.6633 | 2.4002 | 2.4002 | 2.4002 | 2.4002 | 0.76305 | 1.2486 | 1.7111 | 2.0579 | 2.0579 | 2.0579 | 2.8007 | 3.6143 | 4.1473 | 4.4278 | 4.9889 | 5.55 | 1.2117 | 2.3916 | 2.8699 | 2.8699 | 2.8699 | 2.8699 | 0.70494 | 0.82004 | 0.82004 | 0.82004 | 0.82004 | 0.82004
2020-11-28 19:00 | Summer | 1.1241 | 1.6088 | 2.3215 | 2.3215 | 2.3215 | 2.3215 | 0.63159 | 1.0335 | 1.4163 | 1.7034 | 1.7034 | 1.7034 | 2.8007 | 3.6143 | 4.1473 | 4.4278 | 4.9889 | 5.55 | 1.1927 | 2.354 | 2.8248 | 2.8248 | 2.8248 | 2.8248 | 0.68589 | 0.79787 | 0.79787 | 0.79787 | 0.79787 | 0.79787
2020-11-28 20:00 | Summer | 1.0869 | 1.5556 | 2.2448 | 2.2448 | 2.2448 | 2.2448 | 0.6173 | 1.0101 | 1.3842 | 1.6648 | 1.6648 | 1.6648 | 2.7626 | 3.5651 | 4.0909 | 4.3676 | 4.921 | 5.4745 | 1.227 | 2.4217 | 2.906 | 2.906 | 2.906 | 2.906 | 0.70494 | 0.82004 | 0.82004 | 0.82004 | 0.82004 | 0.82004
2020-11-28 21:00 | Summer | 1.086 | 1.5542 | 2.2428 | 2.2428 | 2.2428 | 2.2428 | 0.58872 | 0.96336 | 1.3202 | 1.5878 | 1.5878 | 1.5878 | 2.6483 | 3.4176 | 3.9216 | 4.1869 | 4.7174 | 5.2479 | 1.1736 | 2.3164 | 2.7797 | 2.7797 | 2.7797 | 2.7797 | 0.68589 | 0.79787 | 0.79787 | 0.79787 | 0.79787 | 0.79787
2020-11-28 22:00 | Summer | 1.0669 | 1.527 | 2.2035 | 2.2035 | 2.2035 | 2.2035 | 0.57443 | 0.93998 | 1.2881 | 1.5492 | 1.5492 | 1.5492 | 2.4621 | 3.1773 | 3.6459 | 3.8925 | 4.3857 | 4.879 | 1.1241 | 2.2186 | 2.6623 | 2.6623 | 2.6623 | 2.6623 | 0.64779 | 0.75355 | 0.75355 | 0.75355 | 0.75355 | 0.75355
2020-11-28 23:00 | Summer | 1.0669 | 1.527 | 2.2035 | 2.2035 | 2.2035 | 2.2035 | 0.53442 | 0.87451 | 1.1984 | 1.4413 | 1.4413 | 1.4413 | 2.3625 | 3.0488 | 3.4984 | 3.735 | 4.2083 | 4.6816 | 1.0593 | 2.0908 | 2.5089 | 2.5089 | 2.5089 | 2.5089 | 0.60968 | 0.70922 | 0.70922 | 0.70922 | 0.70922 | 0.70922
2020-11-29 | Summer | 1.0479 | 1.4997 | 2.1641 | 2.1641 | 2.1641 | 2.1641 | 0.50298 | 0.82306 | 1.1279 | 1.3565 | 1.3565 | 1.3565 | 2.1898 | 2.8259 | 3.2427 | 3.462 | 3.9007 | 4.3394 | 0.95644 | 1.8877 | 2.2652 | 2.2652 | 2.2652 | 2.2652 | 0.55252 | 0.64273 | 0.64273 | 0.64273 | 0.64273 | 0.64273
2020-11-29 01:00 | Summer | 1.086 | 1.5542 | 2.2428 | 2.2428 | 2.2428 | 2.2428 | 0.53442 | 0.87451 | 1.1984 | 1.4413 | 1.4413 | 1.4413 | 2.0005 | 2.5816 | 2.9624 | 3.1627 | 3.5635 | 3.9643 | 0.84212 | 1.6621 | 1.9945 | 1.9945 | 1.9945 | 1.9945 | 0.57158 | 0.6649 | 0.6649 | 0.6649 | 0.6649 | 0.6649
2020-11-29 02:00 | Summer | 1.0669 | 1.527 | 2.2035 | 2.2035 | 2.2035 | 2.2035 | 0.51426 | 0.84151 | 1.1532 | 1.3869 | 1.3869 | 1.3869 | 1.9175 | 2.4745 | 2.8394 | 3.0315 | 3.4156 | 3.7998 | 0.83831 | 1.6546 | 1.9855 | 1.9855 | 1.9855 | 1.9855 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-11-29 03:00 | Summer | 1.0669 | 1.527 | 2.2035 | 2.2035 | 2.2035 | 2.2035 | 0.51442 | 0.84177 | 1.1535 | 1.3874 | 1.3874 | 1.3874 | 1.9053 | 2.4587 | 2.8213 | 3.0121 | 3.3938 | 3.7755 | 0.82688 | 1.632 | 1.9584 | 1.9584 | 1.9584 | 1.9584 | 0.49548 | 0.57638 | 0.57638 | 0.57638 | 0.57638 | 0.57638
2020-11-29 04:00 | Summer | 1.0479 | 1.4997 | 2.1641 | 2.1641 | 2.1641 | 2.1641 | 0.52585 | 0.86048 | 1.1792 | 1.4182 | 1.4182 | 1.4182 | 1.9243 | 2.4833 | 2.8495 | 3.0422 | 3.4277 | 3.8132 | 0.82688 | 1.632 | 1.9584 | 1.9584 | 1.9584 | 1.9584 | 0.51439 | 0.59837 | 0.59837 | 0.59837 | 0.59837 | 0.59837
2020-11-29 05:00 | Summer | 1.0479 | 1.4997 | 2.1641 | 2.1641 | 2.1641 | 2.1641 | 0.5287 | 0.86515 | 1.1856 | 1.4259 | 1.4259 | 1.4259 | 1.9624 | 2.5325 | 2.9059 | 3.1025 | 3.4956 | 3.8887 | 0.83831 | 1.6546 | 1.9855 | 1.9855 | 1.9855 | 1.9855 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-11-29 06:00 | Summer | 1.086 | 1.5542 | 2.2428 | 2.2428 | 2.2428 | 2.2428 | 0.59158 | 0.96804 | 1.3266 | 1.5955 | 1.5955 | 1.5955 | 2.0386 | 2.6308 | 3.0188 | 3.223 | 3.6314 | 4.0398 | 0.88023 | 1.7373 | 2.0847 | 2.0847 | 2.0847 | 2.0847 | 0.49621 | 0.57723 | 0.57723 | 0.57723 | 0.57723 | 0.57723
2020-11-29 07:00 | Summer | 1.105 | 1.5815 | 2.2822 | 2.2822 | 2.2822 | 2.2822 | 0.65159 | 1.0662 | 1.4611 | 1.7573 | 1.7573 | 1.7573 | 2.2673 | 2.9258 | 3.3573 | 3.5844 | 4.0386 | 4.4928 | 0.89928 | 1.7749 | 2.1299 | 2.1299 | 2.1299 | 2.1299 | 0.51204 | 0.59564 | 0.59564 | 0.59564 | 0.59564 | 0.59564
2020-11-29 08:00 | Summer | 1.105 | 1.5815 | 2.2822 | 2.2822 | 2.2822 | 2.2822 | 0.6716 | 1.099 | 1.506 | 1.8113 | 1.8113 | 1.8113 | 2.5819 | 3.3319 | 3.8233 | 4.0819 | 4.5992 | 5.1164 | 1.0746 | 2.1208 | 2.545 | 2.545 | 2.545 | 2.545 | 0.55252 | 0.64273 | 0.64273 | 0.64273 | 0.64273 | 0.64273
2020-11-29 09:00 | Summer | 1.0479 | 1.4997 | 2.1641 | 2.1641 | 2.1641 | 2.1641 | 0.71447 | 1.1691 | 1.6021 | 1.9269 | 1.9269 | 1.9269 | 2.8388 | 3.6634 | 4.2037 | 4.4881 | 5.0568 | 5.6255 | 1.1012 | 2.1735 | 2.6082 | 2.6082 | 2.6082 | 2.6082 | 0.55252 | 0.64273 | 0.64273 | 0.64273 | 0.64273 | 0.64273
2020-11-29 10:00 | Summer | 1.1622 | 1.6633 | 2.4002 | 2.4002 | 2.4002 | 2.4002 | 0.77734 | 1.272 | 1.7431 | 2.0965 | 2.0965 | 2.0965 | 2.8388 | 3.6634 | 4.2037 | 4.4881 | 5.0568 | 5.6255 | 0.99454 | 1.9629 | 2.3555 | 2.3555 | 2.3555 | 2.3555 | 0.54952 | 0.63923 | 0.63923 | 0.63923 | 0.63923 | 0.63923
2020-11-29 11:00 | Summer | 1.1432 | 1.636 | 2.3609 | 2.3609 | 2.3609 | 2.3609 | 0.69732 | 1.1411 | 1.5637 | 1.8807 | 1.8807 | 1.8807 | 2.8007 | 3.6143 | 4.1473 | 4.4278 | 4.9889 | 5.55 | 1.0441 | 2.0607 | 2.4728 | 2.4728 | 2.4728 | 2.4728 | 0.54252 | 0.63109 | 0.63109 | 0.63109 | 0.63109 | 0.63109
2020-11-29 12:00 | Summer | 1.105 | 1.5815 | 2.2822 | 2.2822 | 2.2822 | 2.2822 | 0.68589 | 1.1224 | 1.5381 | 1.8498 | 1.8498 | 1.8498 | 2.8769 | 3.7126 | 4.2601 | 4.5483 | 5.1246 | 5.701 | 0.95263 | 1.8802 | 2.2562 | 2.2562 | 2.2562 | 2.2562 | 0.57158 | 0.6649 | 0.6649 | 0.6649 | 0.6649 | 0.6649
2020-11-29 13:00 | Summer | 1.1241 | 1.6088 | 2.3215 | 2.3215 | 2.3215 | 2.3215 | 0.67446 | 1.1037 | 1.5124 | 1.819 | 1.819 | 1.819 | 2.8579 | 3.688 | 4.2319 | 4.5182 | 5.0907 | 5.6632 | 0.99835 | 1.9704 | 2.3645 | 2.3645 | 2.3645 | 2.3645 | 0.57158 | 0.6649 | 0.6649 | 0.6649 | 0.6649 | 0.6649
2020-11-29 14:00 | Summer | 1.1241 | 1.6088 | 2.3215 | 2.3215 | 2.3215 | 2.3215 | 0.74019 | 1.2112 | 1.6598 | 1.9963 | 1.9963 | 1.9963 | 2.8395 | 3.6643 | 4.2047 | 4.4892 | 5.058 | 5.6268 | 0.99835 | 1.9704 | 2.3645 | 2.3645 | 2.3645 | 2.3645 | 0.56046 | 0.65196 | 0.65196 | 0.65196 | 0.65196 | 0.65196
2020-11-29 15:00 | Summer | 1.086 | 1.5542 | 2.2428 | 2.2428 | 2.2428 | 2.2428 | 0.77448 | 1.2673 | 1.7367 | 2.0888 | 2.0888 | 2.0888 | 2.7436 | 3.5405 | 4.0627 | 4.3375 | 4.8871 | 5.4367 | 0.98692 | 1.9479 | 2.3374 | 2.3374 | 2.3374 | 2.3374 | 0.57158 | 0.6649 | 0.6649 | 0.6649 | 0.6649 | 0.6649
2020-11-29 16:00 | Summer | 1.1241 | 1.6088 | 2.3215 | 2.3215 | 2.3215 | 2.3215 | 0.69732 | 1.1411 | 1.5637 | 1.8807 | 1.8807 | 1.8807 | 2.896 | 3.7372 | 4.2884 | 4.5784 | 5.1586 | 5.7387 | 0.94119 | 1.8576 | 2.2291 | 2.2291 | 2.2291 | 2.2291 | 0.70494 | 0.82004 | 0.82004 | 0.82004 | 0.82004 | 0.82004
2020-11-29 17:00 | Summer | 1.105 | 1.5815 | 2.2822 | 2.2822 | 2.2822 | 2.2822 | 0.73447 | 1.2019 | 1.647 | 1.9808 | 1.9808 | 1.9808 | 2.7817 | 3.5897 | 4.1191 | 4.3977 | 4.955 | 5.5122 | 0.94501 | 1.8651 | 2.2382 | 2.2382 | 2.2382 | 2.2382 | 0.66684 | 0.77571 | 0.77571 | 0.77571 | 0.77571 | 0.77571
2020-11-29 18:00 | Summer | 1.086 | 1.5542 | 2.2428 | 2.2428 | 2.2428 | 2.2428 | 0.55443 | 0.90724 | 1.2433 | 1.4953 | 1.4953 | 1.4953 | 2.4768 | 3.1963 | 3.6677 | 3.9158 | 4.4119 | 4.9081 | 0.93357 | 1.8426 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 0.66684 | 0.77571 | 0.77571 | 0.77571 | 0.77571 | 0.77571
2020-11-29 19:00 | Summer | 1.1241 | 1.6088 | 2.3215 | 2.3215 | 2.3215 | 2.3215 | 0.53442 | 0.87451 | 1.1984 | 1.4413 | 1.4413 | 1.4413 | 2.4006 | 3.098 | 3.5548 | 3.7953 | 4.2762 | 4.7571 | 0.92976 | 1.8351 | 2.2021 | 2.2021 | 2.2021 | 2.2021 | 0.57158 | 0.6649 | 0.6649 | 0.6649 | 0.6649 | 0.6649
2020-11-29 20:00 | Summer | 1.1241 | 1.6088 | 2.3215 | 2.3215 | 2.3215 | 2.3215 | 0.54585 | 0.89321 | 1.224 | 1.4721 | 1.4721 | 1.4721 | 2.3625 | 3.0488 | 3.4984 | 3.735 | 4.2083 | 4.6816 | 0.96406 | 1.9027 | 2.2833 | 2.2833 | 2.2833 | 2.2833 | 0.56914 | 0.66207 | 0.66207 | 0.66207 | 0.66207 | 0.66207
2020-11-29 21:00 | Summer | 1.105 | 1.5815 | 2.2822 | 2.2822 | 2.2822 | 2.2822 | 0.45154 | 0.73889 | 1.0125 | 1.2178 | 1.2178 | 1.2178 | 2.2291 | 2.8767 | 3.3009 | 3.5242 | 3.9708 | 4.4173 | 0.89547 | 1.7674 | 2.1208 | 2.1208 | 2.1208 | 2.1208 | 0.55252 | 0.64273 | 0.64273 | 0.64273 | 0.64273 | 0.64273
2020-11-29 22:00 | Summer | 1.105 | 1.5815 | 2.2822 | 2.2822 | 2.2822 | 2.2822 | 0.41439 | 0.67809 | 0.92924 | 1.1176 | 1.1176 | 1.1176 | 2.1529 | 2.7783 | 3.1881 | 3.4037 | 3.835 | 4.2663 | 0.86117 | 1.6997 | 2.0396 | 2.0396 | 2.0396 | 2.0396 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-11-29 23:00 | Summer | 1.0479 | 1.4997 | 2.1641 | 2.1641 | 2.1641 | 2.1641 | 0.42868 | 0.70147 | 0.96128 | 1.1561 | 1.1561 | 1.1561 | 1.8998 | 2.4516 | 2.8131 | 3.0034 | 3.384 | 3.7646 | 0.82307 | 1.6245 | 1.9494 | 1.9494 | 1.9494 | 1.9494 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-11-30 | Summer | 1.0669 | 1.527 | 2.2035 | 2.2035 | 2.2035 | 2.2035 | 0.50584 | 0.82774 | 1.1343 | 1.3642 | 1.3642 | 1.3642 | 1.829 | 2.3603 | 2.7084 | 2.8916 | 3.2581 | 3.6245 | 0.76591 | 1.5117 | 1.814 | 1.814 | 1.814 | 1.814 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-11-30 01:00 | Summer | 1.0288 | 1.4724 | 2.1248 | 2.1248 | 2.1248 | 2.1248 | 0.40867 | 0.66874 | 0.91642 | 1.1022 | 1.1022 | 1.1022 | 1.7528 | 2.262 | 2.5956 | 2.7712 | 3.1223 | 3.4734 | 0.71256 | 1.4064 | 1.6877 | 1.6877 | 1.6877 | 1.6877 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-11-30 02:00 | Summer | 1.0669 | 1.527 | 2.2035 | 2.2035 | 2.2035 | 2.2035 | 0.43725 | 0.7155 | 0.98051 | 1.1793 | 1.1793 | 1.1793 | 1.7147 | 2.2128 | 2.5392 | 2.7109 | 3.0544 | 3.3979 | 0.6897 | 1.3613 | 1.6335 | 1.6335 | 1.6335 | 1.6335 | 0.55252 | 0.64273 | 0.64273 | 0.64273 | 0.64273 | 0.64273
2020-11-30 03:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.40582 | 0.66406 | 0.91001 | 1.0945 | 1.0945 | 1.0945 | 1.7528 | 2.262 | 2.5956 | 2.7712 | 3.1223 | 3.4734 | 0.71256 | 1.4064 | 1.6877 | 1.6877 | 1.6877 | 1.6877 | 0.57158 | 0.6649 | 0.6649 | 0.6649 | 0.6649 | 0.6649
2020-11-30 04:00 | Summer | 1.3527 | 1.936 | 2.7937 | 2.7937 | 2.7937 | 2.7937 | 0.42011 | 0.68744 | 0.94205 | 1.133 | 1.133 | 1.133 | 1.7338 | 2.2374 | 2.5674 | 2.741 | 3.0884 | 3.4357 | 0.70113 | 1.3838 | 1.6606 | 1.6606 | 1.6606 | 1.6606 | 0.57158 | 0.6649 | 0.6649 | 0.6649 | 0.6649 | 0.6649
2020-11-30 05:00 | Summer | 1.448 | 2.0723 | 2.9904 | 2.9904 | 2.9904 | 2.9904 | 0.53442 | 0.87451 | 1.1984 | 1.4413 | 1.4413 | 1.4413 | 1.8719 | 2.4156 | 2.7719 | 2.9594 | 3.3343 | 3.7093 | 0.73162 | 1.444 | 1.7328 | 1.7328 | 1.7328 | 1.7328 | 0.59003 | 0.68636 | 0.68636 | 0.68636 | 0.68636 | 0.68636
2020-11-30 06:00 | Summer | 1.6979 | 2.4299 | 3.5064 | 3.5064 | 3.5064 | 3.5064 | 0.64588 | 1.0569 | 1.4483 | 1.7419 | 1.7419 | 1.7419 | 1.9434 | 2.5079 | 2.8777 | 3.0724 | 3.4617 | 3.851 | 0.84974 | 1.6771 | 2.0125 | 2.0125 | 2.0125 | 2.0125 | 0.77151 | 0.89747 | 0.89747 | 0.89747 | 0.89747 | 0.89747
2020-11-30 07:00 | Summer | 2.172 | 3.1085 | 4.4856 | 4.4856 | 4.4856 | 4.4856 | 0.77734 | 1.272 | 1.7431 | 2.0965 | 2.0965 | 2.0965 | 2.2673 | 2.9258 | 3.3573 | 3.5844 | 4.0386 | 4.4928 | 1.0441 | 2.0607 | 2.4728 | 2.4728 | 2.4728 | 2.4728 | 1.1624 | 1.3522 | 1.3522 | 1.3522 | 1.3522 | 1.3522
2020-11-30 08:00 | Summer | 2.4959 | 3.572 | 5.1545 | 5.1545 | 5.1545 | 5.1545 | 0.95739 | 1.5666 | 2.1469 | 2.582 | 2.582 | 2.582 | 2.6293 | 3.393 | 3.8934 | 4.1567 | 4.6835 | 5.2102 | 1.0403 | 2.0532 | 2.4638 | 2.4638 | 2.4638 | 2.4638 | 1.3718 | 1.5957 | 1.5957 | 1.5957 | 1.5957 | 1.5957
2020-11-30 09:00 | Summer | 2.4607 | 3.5216 | 5.0818 | 5.0818 | 5.0818 | 5.0818 | 1.026 | 1.6789 | 2.3007 | 2.767 | 2.767 | 2.767 | 2.7245 | 3.5159 | 4.0344 | 4.3073 | 4.8531 | 5.3989 | 1.1241 | 2.2186 | 2.6623 | 2.6623 | 2.6623 | 2.6623 | 1.3718 | 1.5957 | 1.5957 | 1.5957 | 1.5957 | 1.5957
2020-11-30 10:00 | Summer | 2.6293 | 3.7629 | 5.43 | 5.43 | 5.43 | 5.43 | 0.95453 | 1.562 | 2.1405 | 2.5743 | 2.5743 | 2.5743 | 2.6674 | 3.4422 | 3.9498 | 4.217 | 4.7513 | 5.2857 | 1.105 | 2.181 | 2.6172 | 2.6172 | 2.6172 | 2.6172 | 1.448 | 1.6844 | 1.6844 | 1.6844 | 1.6844 | 1.6844
2020-11-30 11:00 | Summer | 2.7245 | 3.8992 | 5.6267 | 5.6267 | 5.6267 | 5.6267 | 0.93452 | 1.5292 | 2.0956 | 2.5204 | 2.5204 | 2.5204 | 2.8198 | 3.6389 | 4.1755 | 4.4579 | 5.0228 | 5.5877 | 1.1393 | 2.2487 | 2.6984 | 2.6984 | 2.6984 | 2.6984 | 1.5242 | 1.7731 | 1.7731 | 1.7731 | 1.7731 | 1.7731
2020-11-30 12:00 | Summer | 2.8198 | 4.0356 | 5.8235 | 5.8235 | 5.8235 | 5.8235 | 1.0374 | 1.6976 | 2.3263 | 2.7979 | 2.7979 | 2.7979 | 2.9531 | 3.811 | 4.373 | 4.6688 | 5.2604 | 5.852 | 1.1203 | 2.2111 | 2.6533 | 2.6533 | 2.6533 | 2.6533 | 1.6004 | 1.8617 | 1.8617 | 1.8617 | 1.8617 | 1.8617
2020-11-30 13:00 | Summer | 2.896 | 4.1446 | 5.9808 | 5.9808 | 5.9808 | 5.9808 | 1.046 | 1.7116 | 2.3455 | 2.821 | 2.821 | 2.821 | 3.0484 | 3.9339 | 4.5141 | 4.8194 | 5.4301 | 6.0408 | 1.1089 | 2.1885 | 2.6262 | 2.6262 | 2.6262 | 2.6262 | 1.6004 | 1.8617 | 1.8617 | 1.8617 | 1.8617 | 1.8617
2020-11-30 14:00 | Summer | 2.896 | 4.1446 | 5.9808 | 5.9808 | 5.9808 | 5.9808 | 1.0917 | 1.7864 | 2.4481 | 2.9443 | 2.9443 | 2.9443 | 3.1437 | 4.0568 | 4.6551 | 4.97 | 5.5998 | 6.2296 | 1.0022 | 1.978 | 2.3735 | 2.3735 | 2.3735 | 2.3735 | 1.5617 | 1.8167 | 1.8167 | 1.8167 | 1.8167 | 1.8167
2020-11-30 15:00 | Summer | 2.9341 | 4.1992 | 6.0595 | 6.0595 | 6.0595 | 6.0595 | 1.1231 | 1.8379 | 2.5186 | 3.0291 | 3.0291 | 3.0291 | 3.2389 | 4.1798 | 4.7962 | 5.1206 | 5.7695 | 6.4183 | 0.99073 | 1.9554 | 2.3465 | 2.3465 | 2.3465 | 2.3465 | 1.5052 | 1.7509 | 1.7509 | 1.7509 | 1.7509 | 1.7509
2020-11-30 16:00 | Summer | 2.8769 | 4.1174 | 5.9415 | 5.9415 | 5.9415 | 5.9415 | 1.1203 | 1.8332 | 2.5122 | 3.0214 | 3.0214 | 3.0214 | 3.2008 | 4.1306 | 4.7398 | 5.0604 | 5.7016 | 6.3428 | 1.0174 | 2.008 | 2.4096 | 2.4096 | 2.4096 | 2.4096 | 1.467 | 1.7066 | 1.7066 | 1.7066 | 1.7066 | 1.7066
2020-11-30 17:00 | Summer | 2.763 | 3.9543 | 5.7062 | 5.7062 | 5.7062 | 5.7062 | 1.0546 | 1.7256 | 2.3648 | 2.8441 | 2.8441 | 2.8441 | 3.1437 | 4.0568 | 4.6551 | 4.97 | 5.5998 | 6.2296 | 1.025 | 2.0231 | 2.4277 | 2.4277 | 2.4277 | 2.4277 | 1.3339 | 1.5517 | 1.5517 | 1.5517 | 1.5517 | 1.5517
2020-11-30 18:00 | Summer | 1.9206 | 2.7487 | 3.9665 | 3.9665 | 3.9665 | 3.9665 | 0.82617 | 1.3519 | 1.8526 | 2.2282 | 2.2282 | 2.2282 | 2.915 | 3.7618 | 4.3166 | 4.6086 | 5.1925 | 5.7765 | 1.0212 | 2.0156 | 2.4187 | 2.4187 | 2.4187 | 2.4187 | 0.95467 | 1.1105 | 1.1105 | 1.1105 | 1.1105 | 1.1105
2020-11-30 19:00 | Summer | 1.2956 | 1.8542 | 2.6756 | 2.6756 | 2.6756 | 2.6756 | 0.55951 | 0.91556 | 1.2547 | 1.509 | 1.509 | 1.509 | 2.5724 | 3.3196 | 3.8092 | 4.0669 | 4.5822 | 5.0975 | 0.97168 | 1.9178 | 2.3013 | 2.3013 | 2.3013 | 2.3013 | 0.724 | 0.8422 | 0.8422 | 0.8422 | 0.8422 | 0.8422
2020-11-30 20:00 | Summer | 1.2575 | 1.7996 | 2.5969 | 2.5969 | 2.5969 | 2.5969 | 0.52299 | 0.8558 | 1.1728 | 1.4105 | 1.4105 | 1.4105 | 2.3059 | 2.9758 | 3.4146 | 3.6456 | 4.1075 | 4.5695 | 0.9793 | 1.9328 | 2.3194 | 2.3194 | 2.3194 | 2.3194 | 0.60968 | 0.70922 | 0.70922 | 0.70922 | 0.70922 | 0.70922
2020-11-30 21:00 | Summer | 1.1813 | 1.6906 | 2.4396 | 2.4396 | 2.4396 | 2.4396 | 0.50298 | 0.82306 | 1.1279 | 1.3565 | 1.3565 | 1.3565 | 2.172 | 2.8029 | 3.2163 | 3.4338 | 3.8689 | 4.3041 | 0.93738 | 1.8501 | 2.2201 | 2.2201 | 2.2201 | 2.2201 | 0.55252 | 0.64273 | 0.64273 | 0.64273 | 0.64273 | 0.64273
2020-11-30 22:00 | Summer | 1.1241 | 1.6088 | 2.3215 | 2.3215 | 2.3215 | 2.3215 | 0.57443 | 0.93998 | 1.2881 | 1.5492 | 1.5492 | 1.5492 | 2.0588 | 2.6568 | 3.0486 | 3.2548 | 3.6673 | 4.0797 | 0.88785 | 1.7523 | 2.1028 | 2.1028 | 2.1028 | 2.1028 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-11-30 23:00 | Summer | 1.0479 | 1.4997 | 2.1641 | 2.1641 | 2.1641 | 2.1641 | 0.48012 | 0.78565 | 1.0766 | 1.2949 | 1.2949 | 1.2949 | 1.8481 | 2.3849 | 2.7366 | 2.9218 | 3.292 | 3.6622 | 0.79582 | 1.5707 | 1.8848 | 1.8848 | 1.8848 | 1.8848 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-12-01 | Summer | 1.0288 | 1.4724 | 2.1248 | 2.1248 | 2.1248 | 2.1248 | 0.43725 | 0.7155 | 0.98051 | 1.1793 | 1.1793 | 1.1793 | 1.7528 | 2.262 | 2.5956 | 2.7712 | 3.1223 | 3.4734 | 0.7964 | 1.5718 | 1.8862 | 1.8862 | 1.8862 | 1.8862 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-12-01 01:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.38295 | 0.62665 | 0.85874 | 1.0328 | 1.0328 | 1.0328 | 1.829 | 2.3603 | 2.7084 | 2.8916 | 3.2581 | 3.6245 | 0.68589 | 1.3537 | 1.6245 | 1.6245 | 1.6245 | 1.6245 | 0.46883 | 0.54537 | 0.54537 | 0.54537 | 0.54537 | 0.54537
2020-12-01 02:00 | Summer | 1.0479 | 1.4997 | 2.1641 | 2.1641 | 2.1641 | 2.1641 | 0.41153 | 0.67342 | 0.92283 | 1.1099 | 1.1099 | 1.1099 | 1.6957 | 2.1882 | 2.5109 | 2.6808 | 3.0205 | 3.3602 | 0.66303 | 1.3086 | 1.5703 | 1.5703 | 1.5703 | 1.5703 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-12-01 03:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.41725 | 0.68277 | 0.93565 | 1.1253 | 1.1253 | 1.1253 | 1.7147 | 2.2128 | 2.5392 | 2.7109 | 3.0544 | 3.3979 | 0.66684 | 1.3161 | 1.5794 | 1.5794 | 1.5794 | 1.5794 | 0.48623 | 0.56562 | 0.56562 | 0.56562 | 0.56562 | 0.56562
2020-12-01 04:00 | Summer | 1.2765 | 1.8269 | 2.6363 | 2.6363 | 2.6363 | 2.6363 | 0.43725 | 0.7155 | 0.98051 | 1.1793 | 1.1793 | 1.1793 | 1.7532 | 2.2624 | 2.5961 | 2.7717 | 3.1229 | 3.4741 | 0.6897 | 1.3613 | 1.6335 | 1.6335 | 1.6335 | 1.6335 | 0.55252 | 0.64273 | 0.64273 | 0.64273 | 0.64273 | 0.64273
2020-12-01 05:00 | Summer | 1.3718 | 1.9632 | 2.833 | 2.833 | 2.833 | 2.833 | 0.41725 | 0.68277 | 0.93565 | 1.1253 | 1.1253 | 1.1253 | 1.829 | 2.3603 | 2.7084 | 2.8916 | 3.2581 | 3.6245 | 0.76175 | 1.5035 | 1.8042 | 1.8042 | 1.8042 | 1.8042 | 0.59093 | 0.6874 | 0.6874 | 0.6874 | 0.6874 | 0.6874
2020-12-01 06:00 | Summer | 1.5234 | 2.1803 | 3.1463 | 3.1463 | 3.1463 | 3.1463 | 0.58872 | 0.96336 | 1.3202 | 1.5878 | 1.5878 | 1.5878 | 1.9624 | 2.5325 | 2.9059 | 3.1025 | 3.4956 | 3.8887 | 0.88023 | 1.7373 | 2.0847 | 2.0847 | 2.0847 | 2.0847 | 0.81145 | 0.94393 | 0.94393 | 0.94393 | 0.94393 | 0.94393
2020-12-01 07:00 | Summer | 2.1546 | 3.0835 | 4.4497 | 4.4497 | 4.4497 | 4.4497 | 0.64874 | 1.0616 | 1.4547 | 1.7496 | 1.7496 | 1.7496 | 2.4578 | 3.1717 | 3.6395 | 3.8856 | 4.378 | 4.8704 | 1.1584 | 2.2863 | 2.7436 | 2.7436 | 2.7436 | 2.7436 | 1.1424 | 1.3289 | 1.3289 | 1.3289 | 1.3289 | 1.3289
2020-12-01 08:00 | Summer | 2.7575 | 3.9464 | 5.6948 | 5.6948 | 5.6948 | 5.6948 | 0.85165 | 1.3936 | 1.9098 | 2.2969 | 2.2969 | 2.2969 | 2.7436 | 3.5405 | 4.0627 | 4.3375 | 4.8871 | 5.4367 | 1.1508 | 2.2713 | 2.7255 | 2.7255 | 2.7255 | 2.7255 | 1.3669 | 1.59 | 1.59 | 1.59 | 1.59 | 1.59
2020-12-01 09:00 | Summer | 2.8198 | 4.0356 | 5.8235 | 5.8235 | 5.8235 | 5.8235 | 0.99454 | 1.6274 | 2.2302 | 2.6822 | 2.6822 | 2.6822 | 2.9913 | 3.8601 | 4.4294 | 4.729 | 5.3283 | 5.9275 | 1.1432 | 2.2562 | 2.7075 | 2.7075 | 2.7075 | 2.7075 | 1.4669 | 1.7064 | 1.7064 | 1.7064 | 1.7064 | 1.7064
2020-12-01 10:00 | Summer | 2.9722 | 4.2537 | 6.1382 | 6.1382 | 6.1382 | 6.1382 | 1.1832 | 1.9361 | 2.6531 | 3.1909 | 3.1909 | 3.1909 | 3.1056 | 4.0077 | 4.5987 | 4.9098 | 5.5319 | 6.154 | 1.0403 | 2.0532 | 2.4638 | 2.4638 | 2.4638 | 2.4638 | 1.5716 | 1.8282 | 1.8282 | 1.8282 | 1.8282 | 1.8282
2020-12-01 11:00 | Summer | 3.0865 | 4.4173 | 6.3743 | 6.3743 | 6.3743 | 6.3743 | 1.1746 | 1.9221 | 2.6339 | 3.1678 | 3.1678 | 3.1678 | 3.3914 | 4.3765 | 5.0219 | 5.3616 | 6.041 | 6.7204 | 1.0479 | 2.0682 | 2.4818 | 2.4818 | 2.4818 | 2.4818 | 1.6957 | 1.9725 | 1.9725 | 1.9725 | 1.9725 | 1.9725
2020-12-01 12:00 | Summer | 3.3151 | 4.7445 | 6.8465 | 6.8465 | 6.8465 | 6.8465 | 1.3832 | 2.2634 | 3.1017 | 3.7305 | 3.7305 | 3.7305 | 3.5628 | 4.5978 | 5.2758 | 5.6327 | 6.3464 | 7.0602 | 0.95263 | 1.8802 | 2.2562 | 2.2562 | 2.2562 | 2.2562 | 1.6957 | 1.9725 | 1.9725 | 1.9725 | 1.9725 | 1.9725
2020-12-01 13:00 | Summer | 3.3533 | 4.799 | 6.9252 | 6.9252 | 6.9252 | 6.9252 | 1.3889 | 2.2728 | 3.1146 | 3.7459 | 3.7459 | 3.7459 | 3.8677 | 4.9911 | 5.7272 | 6.1146 | 6.8894 | 7.6642 | 0.9793 | 1.9328 | 2.3194 | 2.3194 | 2.3194 | 2.3194 | 1.6774 | 1.9513 | 1.9513 | 1.9513 | 1.9513 | 1.9513
2020-12-01 14:00 | Summer | 3.4295 | 4.9081 | 7.0826 | 7.0826 | 7.0826 | 7.0826 | 1.4775 | 2.4178 | 3.3132 | 3.9848 | 3.9848 | 3.9848 | 3.9439 | 5.0895 | 5.8401 | 6.2351 | 7.0252 | 7.8153 | 0.95263 | 1.8802 | 2.2562 | 2.2562 | 2.2562 | 2.2562 | 1.6766 | 1.9504 | 1.9504 | 1.9504 | 1.9504 | 1.9504
2020-12-01 15:00 | Summer | 3.6771 | 5.2626 | 7.5941 | 7.5941 | 7.5941 | 7.5941 | 1.649 | 2.6984 | 3.6977 | 4.4473 | 4.4473 | 4.4473 | 4.0201 | 5.1878 | 5.9529 | 6.3556 | 7.1609 | 7.9663 | 1.2557 | 2.4784 | 2.9741 | 2.9741 | 2.9741 | 2.9741 | 1.7338 | 2.0168 | 2.0168 | 2.0168 | 2.0168 | 2.0168
2020-12-01 16:00 | Summer | 3.5984 | 5.1499 | 7.4315 | 7.4315 | 7.4315 | 7.4315 | 1.509 | 2.4692 | 3.3837 | 4.0696 | 4.0696 | 4.0696 | 4.001 | 5.1633 | 5.9247 | 6.3255 | 7.127 | 7.9285 | 1.3032 | 2.5721 | 3.0865 | 3.0865 | 3.0865 | 3.0865 | 1.6576 | 1.9282 | 1.9282 | 1.9282 | 1.9282 | 1.9282
2020-12-01 17:00 | Summer | 2.6591 | 3.8056 | 5.4917 | 5.4917 | 5.4917 | 5.4917 | 1.0746 | 1.7584 | 2.4096 | 2.8981 | 2.8981 | 2.8981 | 3.6581 | 4.7207 | 5.4169 | 5.7833 | 6.5161 | 7.2489 | 1.3489 | 2.6623 | 3.1948 | 3.1948 | 3.1948 | 3.1948 | 1.4994 | 1.7442 | 1.7442 | 1.7442 | 1.7442 | 1.7442
2020-12-01 18:00 | Summer | 2.1743 | 3.1118 | 4.4905 | 4.4905 | 4.4905 | 4.4905 | 0.92604 | 1.5153 | 2.0766 | 2.4975 | 2.4975 | 2.4975 | 3.5628 | 4.5978 | 5.2758 | 5.6327 | 6.3464 | 7.0602 | 1.2956 | 2.5571 | 3.0685 | 3.0685 | 3.0685 | 3.0685 | 1.039 | 1.2087 | 1.2087 | 1.2087 | 1.2087 | 1.2087
2020-12-01 19:00 | Summer | 1.5277 | 2.1865 | 3.1551 | 3.1551 | 3.1551 | 3.1551 | 0.72917 | 1.1932 | 1.6351 | 1.9665 | 1.9665 | 1.9665 | 3.0145 | 3.8902 | 4.4639 | 4.7658 | 5.3697 | 5.9736 | 1.086 | 2.1434 | 2.5721 | 2.5721 | 2.5721 | 2.5721 | 0.70446 | 0.81948 | 0.81948 | 0.81948 | 0.81948 | 0.81948
2020-12-01 20:00 | Summer | 1.3337 | 1.9087 | 2.7543 | 2.7543 | 2.7543 | 2.7543 | 0.73161 | 1.1972 | 1.6406 | 1.9731 | 1.9731 | 1.9731 | 2.7817 | 3.5897 | 4.1191 | 4.3977 | 4.955 | 5.5122 | 0.95644 | 1.8877 | 2.2652 | 2.2652 | 2.2652 | 2.2652 | 0.64779 | 0.75355 | 0.75355 | 0.75355 | 0.75355 | 0.75355
2020-12-01 21:00 | Summer | 1.2213 | 1.7479 | 2.5222 | 2.5222 | 2.5222 | 2.5222 | 0.6173 | 1.0101 | 1.3842 | 1.6648 | 1.6648 | 1.6648 | 2.4959 | 3.2209 | 3.6959 | 3.9459 | 4.4459 | 4.9459 | 0.9793 | 1.9328 | 2.3194 | 2.3194 | 2.3194 | 2.3194 | 0.55277 | 0.64302 | 0.64302 | 0.64302 | 0.64302 | 0.64302
2020-12-01 22:00 | Summer | 1.2008 | 1.7185 | 2.4798 | 2.4798 | 2.4798 | 2.4798 | 0.59158 | 0.96804 | 1.3266 | 1.5955 | 1.5955 | 1.5955 | 2.3054 | 2.975 | 3.4138 | 3.6447 | 4.1065 | 4.5683 | 0.89166 | 1.7599 | 2.1118 | 2.1118 | 2.1118 | 2.1118 | 0.55252 | 0.64273 | 0.64273 | 0.64273 | 0.64273 | 0.64273
2020-12-01 23:00 | Summer | 1.1432 | 1.636 | 2.3609 | 2.3609 | 2.3609 | 2.3609 | 0.48584 | 0.79501 | 1.0895 | 1.3103 | 1.3103 | 1.3103 | 2.0803 | 2.6846 | 3.0805 | 3.2889 | 3.7057 | 4.1224 | 0.75448 | 1.4891 | 1.7869 | 1.7869 | 1.7869 | 1.7869 | 0.49543 | 0.57632 | 0.57632 | 0.57632 | 0.57632 | 0.57632
2020-12-02 | Summer | 1.086 | 1.5542 | 2.2428 | 2.2428 | 2.2428 | 2.2428 | 0.34014 | 0.55659 | 0.76273 | 0.91734 | 0.91734 | 0.91734 | 1.9246 | 2.4836 | 2.8499 | 3.0426 | 3.4282 | 3.8137 | 0.72781 | 1.4365 | 1.7238 | 1.7238 | 1.7238 | 1.7238 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-12-02 01:00 | Summer | 1.105 | 1.5815 | 2.2822 | 2.2822 | 2.2822 | 2.2822 | 0.33962 | 0.55575 | 0.76158 | 0.91596 | 0.91596 | 0.91596 | 1.8481 | 2.3849 | 2.7366 | 2.9218 | 3.292 | 3.6622 | 0.65541 | 1.2936 | 1.5523 | 1.5523 | 1.5523 | 1.5523 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-12-02 02:00 | Summer | 1.086 | 1.5542 | 2.2428 | 2.2428 | 2.2428 | 2.2428 | 0.3458 | 0.56585 | 0.77543 | 0.93261 | 0.93261 | 0.93261 | 1.8414 | 2.3763 | 2.7267 | 2.9112 | 3.28 | 3.6489 | 0.67446 | 1.3312 | 1.5974 | 1.5974 | 1.5974 | 1.5974 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-12-02 03:00 | Summer | 1.086 | 1.5542 | 2.2428 | 2.2428 | 2.2428 | 2.2428 | 0.32294 | 0.52844 | 0.72416 | 0.87095 | 0.87095 | 0.87095 | 1.829 | 2.3603 | 2.7084 | 2.8916 | 3.2581 | 3.6245 | 0.62873 | 1.2409 | 1.4891 | 1.4891 | 1.4891 | 1.4891 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-12-02 04:00 | Summer | 1.1813 | 1.6906 | 2.4396 | 2.4396 | 2.4396 | 2.4396 | 0.37058 | 0.6064 | 0.83099 | 0.99943 | 0.99943 | 0.99943 | 1.81 | 2.3358 | 2.6802 | 2.8615 | 3.2241 | 3.5867 | 0.67446 | 1.3312 | 1.5974 | 1.5974 | 1.5974 | 1.5974 | 0.57158 | 0.6649 | 0.6649 | 0.6649 | 0.6649 | 0.6649
2020-12-02 05:00 | Summer | 1.3718 | 1.9632 | 2.833 | 2.833 | 2.833 | 2.833 | 0.39153 | 0.64068 | 0.87797 | 1.0559 | 1.0559 | 1.0559 | 1.8862 | 2.4341 | 2.7931 | 2.982 | 3.3599 | 3.7377 | 0.68208 | 1.3462 | 1.6155 | 1.6155 | 1.6155 | 1.6155 | 0.55249 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427
2020-12-02 06:00 | Summer | 1.4652 | 2.0969 | 3.0259 | 3.0259 | 3.0259 | 3.0259 | 0.49155 | 0.80436 | 1.1023 | 1.3257 | 1.3257 | 1.3257 | 1.9815 | 2.557 | 2.9341 | 3.1326 | 3.5296 | 3.9265 | 0.77575 | 1.5311 | 1.8373 | 1.8373 | 1.8373 | 1.8373 | 0.75834 | 0.88215 | 0.88215 | 0.88215 | 0.88215 | 0.88215
2020-12-02 07:00 | Summer | 1.9719 | 2.8221 | 4.0724 | 4.0724 | 4.0724 | 4.0724 | 0.79735 | 1.3047 | 1.788 | 2.1504 | 2.1504 | 2.1504 | 2.2101 | 2.8521 | 3.2727 | 3.4941 | 3.9368 | 4.3796 | 1.0631 | 2.0983 | 2.5179 | 2.5179 | 2.5179 | 2.5179 | 1.0098 | 1.1746 | 1.1746 | 1.1746 | 1.1746 | 1.1746
2020-12-02 08:00 | Summer | 2.4682 | 3.5324 | 5.0974 | 5.0974 | 5.0974 | 5.0974 | 0.78877 | 1.2907 | 1.7688 | 2.1273 | 2.1273 | 2.1273 | 2.6483 | 3.4176 | 3.9216 | 4.1869 | 4.7174 | 5.2479 | 1.025 | 2.0231 | 2.4277 | 2.4277 | 2.4277 | 2.4277 | 1.2765 | 1.4849 | 1.4849 | 1.4849 | 1.4849 | 1.4849
2020-12-02 09:00 | Summer | 3.1246 | 4.4718 | 6.453 | 6.453 | 6.453 | 6.453 | 0.88308 | 1.445 | 1.9802 | 2.3816 | 2.3816 | 2.3816 | 2.8959 | 3.7371 | 4.2882 | 4.5782 | 5.1584 | 5.7385 | 1.0403 | 2.0532 | 2.4638 | 2.4638 | 2.4638 | 2.4638 | 1.3718 | 1.5957 | 1.5957 | 1.5957 | 1.5957 | 1.5957
2020-12-02 10:00 | Summer | 3.0833 | 4.4127 | 6.3678 | 6.3678 | 6.3678 | 6.3678 | 0.91166 | 1.4918 | 2.0443 | 2.4587 | 2.4587 | 2.4587 | 3.0103 | 3.8847 | 4.4576 | 4.7592 | 5.3622 | 5.9653 | 1.006 | 1.9855 | 2.3826 | 2.3826 | 2.3826 | 2.3826 | 1.5242 | 1.7731 | 1.7731 | 1.7731 | 1.7731 | 1.7731
2020-12-02 11:00 | Summer | 3.1627 | 4.5264 | 6.5317 | 6.5317 | 6.5317 | 6.5317 | 0.90023 | 1.4731 | 2.0187 | 2.4279 | 2.4279 | 2.4279 | 3.0865 | 3.9831 | 4.5705 | 4.8796 | 5.498 | 6.1163 | 0.89928 | 1.7749 | 2.1299 | 2.1299 | 2.1299 | 2.1299 | 1.5623 | 1.8174 | 1.8174 | 1.8174 | 1.8174 | 1.8174
2020-12-02 12:00 | Summer | 2.9531 | 4.2264 | 6.0989 | 6.0989 | 6.0989 | 6.0989 | 0.93738 | 1.5339 | 2.102 | 2.5281 | 2.5281 | 2.5281 | 3.1246 | 4.0323 | 4.6269 | 4.9399 | 5.5658 | 6.1918 | 0.92214 | 1.82 | 2.184 | 2.184 | 2.184 | 2.184 | 1.5623 | 1.8174 | 1.8174 | 1.8174 | 1.8174 | 1.8174
2020-12-02 13:00 | Summer | 2.915 | 4.1719 | 6.0202 | 6.0202 | 6.0202 | 6.0202 | 1.006 | 1.6461 | 2.2558 | 2.7131 | 2.7131 | 2.7131 | 3.2389 | 4.1798 | 4.7962 | 5.1206 | 5.7695 | 6.4183 | 0.94119 | 1.8576 | 2.2291 | 2.2291 | 2.2291 | 2.2291 | 1.5623 | 1.8174 | 1.8174 | 1.8174 | 1.8174 | 1.8174
2020-12-02 14:00 | Summer | 2.9531 | 4.2264 | 6.0989 | 6.0989 | 6.0989 | 6.0989 | 1.3089 | 2.1418 | 2.9351 | 3.5301 | 3.5301 | 3.5301 | 3.2378 | 4.1783 | 4.7944 | 5.1188 | 5.7674 | 6.416 | 0.94882 | 1.8727 | 2.2472 | 2.2472 | 2.2472 | 2.2472 | 1.5433 | 1.7952 | 1.7952 | 1.7952 | 1.7952 | 1.7952
2020-12-02 15:00 | Summer | 2.9531 | 4.2264 | 6.0989 | 6.0989 | 6.0989 | 6.0989 | 1.1803 | 1.9314 | 2.6467 | 3.1832 | 3.1832 | 3.1832 | 3.2389 | 4.1798 | 4.7962 | 5.1206 | 5.7695 | 6.4183 | 0.96787 | 1.9103 | 2.2923 | 2.2923 | 2.2923 | 2.2923 | 1.4861 | 1.7287 | 1.7287 | 1.7287 | 1.7287 | 1.7287
2020-12-02 16:00 | Summer | 2.8388 | 4.0628 | 5.8628 | 5.8628 | 5.8628 | 5.8628 | 1.1717 | 1.9174 | 2.6275 | 3.1601 | 3.1601 | 3.1601 | 3.1818 | 4.106 | 4.7115 | 5.0303 | 5.6677 | 6.3051 | 0.97549 | 1.9253 | 2.3104 | 2.3104 | 2.3104 | 2.3104 | 1.4099 | 1.6401 | 1.6401 | 1.6401 | 1.6401 | 1.6401
2020-12-02 17:00 | Summer | 2.6945 | 3.8562 | 5.5646 | 5.5646 | 5.5646 | 5.5646 | 1.1832 | 1.9361 | 2.6531 | 3.1909 | 3.1909 | 3.1909 | 3.106 | 4.0082 | 4.5993 | 4.9104 | 5.5327 | 6.1549 | 0.96025 | 1.8952 | 2.2743 | 2.2743 | 2.2743 | 2.2743 | 1.3337 | 1.5514 | 1.5514 | 1.5514 | 1.5514 | 1.5514
2020-12-02 18:00 | Summer | 1.7395 | 2.4894 | 3.5924 | 3.5924 | 3.5924 | 3.5924 | 0.93167 | 1.5245 | 2.0892 | 2.5127 | 2.5127 | 2.5127 | 2.9241 | 3.7735 | 4.3299 | 4.6228 | 5.2086 | 5.7944 | 0.99835 | 1.9704 | 2.3645 | 2.3645 | 2.3645 | 2.3645 | 0.92533 | 1.0764 | 1.0764 | 1.0764 | 1.0764 | 1.0764
2020-12-02 19:00 | Summer | 1.2647 | 1.81 | 2.6119 | 2.6119 | 2.6119 | 2.6119 | 0.62301 | 1.0195 | 1.3971 | 1.6803 | 1.6803 | 1.6803 | 2.5939 | 3.3473 | 3.841 | 4.1008 | 4.6204 | 5.1401 | 0.91071 | 1.7975 | 2.1569 | 2.1569 | 2.1569 | 2.1569 | 0.68415 | 0.79585 | 0.79585 | 0.79585 | 0.79585 | 0.79585
2020-12-02 20:00 | Summer | 1.1241 | 1.6088 | 2.3215 | 2.3215 | 2.3215 | 2.3215 | 0.56872 | 0.93062 | 1.2753 | 1.5338 | 1.5338 | 1.5338 | 2.2764 | 2.9377 | 3.3709 | 3.5989 | 4.055 | 4.511 | 0.96787 | 1.9103 | 2.2923 | 2.2923 | 2.2923 | 2.2923 | 0.66684 | 0.77571 | 0.77571 | 0.77571 | 0.77571 | 0.77571
2020-12-02 21:00 | Summer | 1.105 | 1.5815 | 2.2822 | 2.2822 | 2.2822 | 2.2822 | 0.49441 | 0.80903 | 1.1087 | 1.3334 | 1.3334 | 1.3334 | 2.1529 | 2.7783 | 3.1881 | 3.4037 | 3.835 | 4.2663 | 0.85736 | 1.6922 | 2.0306 | 2.0306 | 2.0306 | 2.0306 | 0.53364 | 0.62077 | 0.62077 | 0.62077 | 0.62077 | 0.62077
2020-12-02 22:00 | Summer | 1.0669 | 1.527 | 2.2035 | 2.2035 | 2.2035 | 2.2035 | 0.43154 | 0.70615 | 0.96769 | 1.1638 | 1.1638 | 1.1638 | 2.1148 | 2.7291 | 3.1316 | 3.3435 | 3.7671 | 4.1908 | 0.80021 | 1.5794 | 1.8952 | 1.8952 | 1.8952 | 1.8952 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-12-02 23:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.41725 | 0.68277 | 0.93565 | 1.1253 | 1.1253 | 1.1253 | 1.9243 | 2.4833 | 2.8495 | 3.0422 | 3.4277 | 3.8132 | 0.75448 | 1.4891 | 1.7869 | 1.7869 | 1.7869 | 1.7869 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-12-03 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.40296 | 0.65939 | 0.9036 | 1.0868 | 1.0868 | 1.0868 | 1.81 | 2.3358 | 2.6802 | 2.8615 | 3.2241 | 3.5867 | 0.68589 | 1.3537 | 1.6245 | 1.6245 | 1.6245 | 1.6245 | 0.45664 | 0.53119 | 0.53119 | 0.53119 | 0.53119 | 0.53119
2020-12-03 01:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.36581 | 0.59859 | 0.82029 | 0.98657 | 0.98657 | 0.98657 | 1.7139 | 2.2117 | 2.5379 | 2.7095 | 3.0529 | 3.3962 | 0.63254 | 1.2484 | 1.4981 | 1.4981 | 1.4981 | 1.4981 | 0.45723 | 0.53187 | 0.53187 | 0.53187 | 0.53187 | 0.53187
2020-12-03 02:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.36866 | 0.60327 | 0.8267 | 0.99427 | 0.99427 | 0.99427 | 1.7338 | 2.2374 | 2.5674 | 2.741 | 3.0884 | 3.4357 | 0.68589 | 1.3537 | 1.6245 | 1.6245 | 1.6245 | 1.6245 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-12-03 03:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.35437 | 0.57988 | 0.79466 | 0.95574 | 0.95574 | 0.95574 | 1.6766 | 2.1636 | 2.4827 | 2.6507 | 2.9865 | 3.3224 | 0.64016 | 1.2635 | 1.5162 | 1.5162 | 1.5162 | 1.5162 | 0.44787 | 0.52099 | 0.52099 | 0.52099 | 0.52099 | 0.52099
2020-12-03 04:00 | Summer | 1.1307 | 1.6182 | 2.3351 | 2.3351 | 2.3351 | 2.3351 | 0.39438 | 0.64536 | 0.88438 | 1.0636 | 1.0636 | 1.0636 | 1.7338 | 2.2374 | 2.5674 | 2.741 | 3.0884 | 3.4357 | 0.65541 | 1.2936 | 1.5523 | 1.5523 | 1.5523 | 1.5523 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-12-03 05:00 | Summer | 1.2575 | 1.7996 | 2.5969 | 2.5969 | 2.5969 | 2.5969 | 0.43621 | 0.71379 | 0.97816 | 1.1764 | 1.1764 | 1.1764 | 1.843 | 2.3784 | 2.7292 | 2.9138 | 3.283 | 3.6522 | 0.70494 | 1.3913 | 1.6696 | 1.6696 | 1.6696 | 1.6696 | 0.55252 | 0.64273 | 0.64273 | 0.64273 | 0.64273 | 0.64273
2020-12-03 06:00 | Summer | 1.459 | 2.0881 | 3.0132 | 3.0132 | 3.0132 | 3.0132 | 0.46012 | 0.75292 | 1.0318 | 1.2409 | 1.2409 | 1.2409 | 1.9434 | 2.5079 | 2.8777 | 3.0724 | 3.4617 | 3.851 | 0.74686 | 1.4741 | 1.7689 | 1.7689 | 1.7689 | 1.7689 | 0.73274 | 0.85237 | 0.85237 | 0.85237 | 0.85237 | 0.85237
2020-12-03 07:00 | Summer | 1.8916 | 2.7071 | 3.9065 | 3.9065 | 3.9065 | 3.9065 | 0.73447 | 1.2019 | 1.647 | 1.9808 | 1.9808 | 1.9808 | 2.3054 | 2.975 | 3.4138 | 3.6447 | 4.1065 | 4.5683 | 1.0974 | 2.166 | 2.5992 | 2.5992 | 2.5992 | 2.5992 | 0.96018 | 1.1169 | 1.1169 | 1.1169 | 1.1169 | 1.1169
2020-12-03 08:00 | Summer | 2.3489 | 3.3616 | 4.851 | 4.851 | 4.851 | 4.851 | 0.77162 | 1.2627 | 1.7303 | 2.081 | 2.081 | 2.081 | 2.4787 | 3.1988 | 3.6705 | 3.9188 | 4.4153 | 4.9119 | 1.0288 | 2.0306 | 2.4367 | 2.4367 | 2.4367 | 2.4367 | 1.2194 | 1.4184 | 1.4184 | 1.4184 | 1.4184 | 1.4184
2020-12-03 09:00 | Summer | 2.3816 | 3.4084 | 4.9185 | 4.9185 | 4.9185 | 4.9185 | 1.1203 | 1.8332 | 2.5122 | 3.0214 | 3.0214 | 3.0214 | 2.7436 | 3.5405 | 4.0627 | 4.3375 | 4.8871 | 5.4367 | 0.97549 | 1.9253 | 2.3104 | 2.3104 | 2.3104 | 2.3104 | 1.3468 | 1.5667 | 1.5667 | 1.5667 | 1.5667 | 1.5667
2020-12-03 10:00 | Summer | 2.534 | 3.6265 | 5.2332 | 5.2332 | 5.2332 | 5.2332 | 1.1832 | 1.9361 | 2.6531 | 3.1909 | 3.1909 | 3.1909 | 2.9341 | 3.7864 | 4.3448 | 4.6387 | 5.2265 | 5.8142 | 0.99073 | 1.9554 | 2.3465 | 2.3465 | 2.3465 | 2.3465 | 1.448 | 1.6844 | 1.6844 | 1.6844 | 1.6844 | 1.6844
2020-12-03 11:00 | Summer | 2.5911 | 3.7083 | 5.3513 | 5.3513 | 5.3513 | 5.3513 | 1.0946 | 1.7911 | 2.4545 | 2.952 | 2.952 | 2.952 | 2.9341 | 3.7864 | 4.3448 | 4.6387 | 5.2265 | 5.8142 | 1.0365 | 2.0456 | 2.4548 | 2.4548 | 2.4548 | 2.4548 | 1.467 | 1.7066 | 1.7066 | 1.7066 | 1.7066 | 1.7066
2020-12-03 12:00 | Summer | 2.7436 | 3.9265 | 5.6661 | 5.6661 | 5.6661 | 5.6661 | 1.1174 | 1.8285 | 2.5057 | 3.0137 | 3.0137 | 3.0137 | 2.9531 | 3.811 | 4.373 | 4.6688 | 5.2604 | 5.852 | 1.1012 | 2.1735 | 2.6082 | 2.6082 | 2.6082 | 2.6082 | 1.5052 | 1.7509 | 1.7509 | 1.7509 | 1.7509 | 1.7509
2020-12-03 13:00 | Summer | 2.7415 | 3.9236 | 5.6619 | 5.6619 | 5.6619 | 5.6619 | 1.2375 | 2.0249 | 2.7749 | 3.3374 | 3.3374 | 3.3374 | 3.2008 | 4.1306 | 4.7398 | 5.0604 | 5.7016 | 6.3428 | 1.2803 | 2.527 | 3.0324 | 3.0324 | 3.0324 | 3.0324 | 1.6004 | 1.8617 | 1.8617 | 1.8617 | 1.8617 | 1.8617
2020-12-03 14:00 | Summer | 2.8198 | 4.0356 | 5.8235 | 5.8235 | 5.8235 | 5.8235 | 1.2775 | 2.0904 | 2.8646 | 3.4453 | 3.4453 | 3.4453 | 3.1254 | 4.0333 | 4.6281 | 4.9412 | 5.5673 | 6.1934 | 1.1813 | 2.3314 | 2.7977 | 2.7977 | 2.7977 | 2.7977 | 1.4861 | 1.7287 | 1.7287 | 1.7287 | 1.7287 | 1.7287
2020-12-03 15:00 | Summer | 2.8198 | 4.0356 | 5.8235 | 5.8235 | 5.8235 | 5.8235 | 1.3289 | 2.1746 | 2.98 | 3.584 | 3.584 | 3.584 | 3.277 | 4.2289 | 4.8526 | 5.1809 | 5.8373 | 6.4938 | 1.1927 | 2.354 | 2.8248 | 2.8248 | 2.8248 | 2.8248 | 1.467 | 1.7066 | 1.7066 | 1.7066 | 1.7066 | 1.7066
2020-12-03 16:00 | Summer | 2.8198 | 4.0356 | 5.8235 | 5.8235 | 5.8235 | 5.8235 | 1.3232 | 2.1652 | 2.9672 | 3.5686 | 3.5686 | 3.5686 | 3.1437 | 4.0568 | 4.6551 | 4.97 | 5.5998 | 6.2296 | 1.2308 | 2.4292 | 2.915 | 2.915 | 2.915 | 2.915 | 1.4099 | 1.6401 | 1.6401 | 1.6401 | 1.6401 | 1.6401
2020-12-03 17:00 | Summer | 2.534 | 3.6265 | 5.2332 | 5.2332 | 5.2332 | 5.2332 | 1.2146 | 1.9875 | 2.7236 | 3.2757 | 3.2757 | 3.2757 | 3.0484 | 3.9339 | 4.5141 | 4.8194 | 5.4301 | 6.0408 | 1.147 | 2.2637 | 2.7165 | 2.7165 | 2.7165 | 2.7165 | 1.3337 | 1.5514 | 1.5514 | 1.5514 | 1.5514 | 1.5514
2020-12-03 18:00 | Summer | 1.8063 | 2.5851 | 3.7304 | 3.7304 | 3.7304 | 3.7304 | 0.97273 | 1.5917 | 2.1813 | 2.6234 | 2.6234 | 2.6234 | 2.7927 | 3.6039 | 4.1354 | 4.4151 | 4.9746 | 5.5341 | 0.96787 | 1.9103 | 2.2923 | 2.2923 | 2.2923 | 2.2923 | 0.97501 | 1.1342 | 1.1342 | 1.1342 | 1.1342 | 1.1342
2020-12-03 19:00 | Summer | 1.3146 | 1.8814 | 2.715 | 2.715 | 2.715 | 2.715 | 0.84593 | 1.3842 | 1.8969 | 2.2814 | 2.2814 | 2.2814 | 2.6831 | 3.4625 | 3.9731 | 4.2419 | 4.7794 | 5.3169 | 0.98692 | 1.9479 | 2.3374 | 2.3374 | 2.3374 | 2.3374 | 0.71834 | 0.83562 | 0.83562 | 0.83562 | 0.83562 | 0.83562
2020-12-03 20:00 | Summer | 1.2765 | 1.8269 | 2.6363 | 2.6363 | 2.6363 | 2.6363 | 0.71733 | 1.1738 | 1.6085 | 1.9346 | 1.9346 | 1.9346 | 2.3244 | 2.9996 | 3.442 | 3.6748 | 4.1404 | 4.6061 | 0.91452 | 1.805 | 2.166 | 2.166 | 2.166 | 2.166 | 0.6074 | 0.70656 | 0.70656 | 0.70656 | 0.70656 | 0.70656
2020-12-03 21:00 | Summer | 1.2384 | 1.7724 | 2.5576 | 2.5576 | 2.5576 | 2.5576 | 0.72018 | 1.1785 | 1.615 | 1.9423 | 1.9423 | 1.9423 | 2.2101 | 2.8521 | 3.2727 | 3.4941 | 3.9368 | 4.3796 | 0.91071 | 1.7975 | 2.1569 | 2.1569 | 2.1569 | 2.1569 | 0.60968 | 0.70922 | 0.70922 | 0.70922 | 0.70922 | 0.70922
2020-12-03 22:00 | Summer | 1.1432 | 1.636 | 2.3609 | 2.3609 | 2.3609 | 2.3609 | 0.64016 | 1.0475 | 1.4355 | 1.7265 | 1.7265 | 1.7265 | 2.0005 | 2.5816 | 2.9624 | 3.1627 | 3.5635 | 3.9643 | 0.87261 | 1.7222 | 2.0667 | 2.0667 | 2.0667 | 2.0667 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-12-03 23:00 | Summer | 1.0669 | 1.527 | 2.2035 | 2.2035 | 2.2035 | 2.2035 | 0.46583 | 0.76227 | 1.0446 | 1.2563 | 1.2563 | 1.2563 | 1.9043 | 2.4574 | 2.8198 | 3.0106 | 3.3921 | 3.7736 | 0.80402 | 1.5869 | 1.9042 | 1.9042 | 1.9042 | 1.9042 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-12-04 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.40867 | 0.66874 | 0.91642 | 1.1022 | 1.1022 | 1.1022 | 1.7528 | 2.262 | 2.5956 | 2.7712 | 3.1223 | 3.4734 | 0.68208 | 1.3462 | 1.6155 | 1.6155 | 1.6155 | 1.6155 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-12-04 01:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.40867 | 0.66874 | 0.91642 | 1.1022 | 1.1022 | 1.1022 | 1.6576 | 2.1391 | 2.4545 | 2.6205 | 2.9526 | 3.2847 | 0.67446 | 1.3312 | 1.5974 | 1.5974 | 1.5974 | 1.5974 | 0.45099 | 0.52462 | 0.52462 | 0.52462 | 0.52462 | 0.52462
2020-12-04 02:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.42296 | 0.69212 | 0.94846 | 1.1407 | 1.1407 | 1.1407 | 1.6385 | 2.1145 | 2.4263 | 2.5904 | 2.9187 | 3.2469 | 0.64779 | 1.2785 | 1.5342 | 1.5342 | 1.5342 | 1.5342 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-12-04 03:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.38581 | 0.63133 | 0.86515 | 1.0405 | 1.0405 | 1.0405 | 1.6316 | 2.1055 | 2.416 | 2.5795 | 2.9063 | 3.2332 | 0.64016 | 1.2635 | 1.5162 | 1.5162 | 1.5162 | 1.5162 | 0.46027 | 0.53541 | 0.53541 | 0.53541 | 0.53541 | 0.53541
2020-12-04 04:00 | Summer | 1.0973 | 1.5704 | 2.2661 | 2.2661 | 2.2661 | 2.2661 | 0.38295 | 0.62665 | 0.85874 | 1.0328 | 1.0328 | 1.0328 | 1.6683 | 2.1529 | 2.4704 | 2.6375 | 2.9717 | 3.3059 | 0.59825 | 1.1808 | 1.4169 | 1.4169 | 1.4169 | 1.4169 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-12-04 05:00 | Summer | 1.2384 | 1.7724 | 2.5576 | 2.5576 | 2.5576 | 2.5576 | 0.45154 | 0.73889 | 1.0125 | 1.2178 | 1.2178 | 1.2178 | 1.7731 | 2.2881 | 2.6256 | 2.8032 | 3.1584 | 3.5136 | 0.62492 | 1.2334 | 1.4801 | 1.4801 | 1.4801 | 1.4801 | 0.54325 | 0.63195 | 0.63195 | 0.63195 | 0.63195 | 0.63195
2020-12-04 06:00 | Summer | 1.2969 | 1.8561 | 2.6784 | 2.6784 | 2.6784 | 2.6784 | 0.60301 | 0.98674 | 1.3522 | 1.6263 | 1.6263 | 1.6263 | 1.9053 | 2.4587 | 2.8213 | 3.0121 | 3.3938 | 3.7755 | 0.75067 | 1.4816 | 1.7779 | 1.7779 | 1.7779 | 1.7779 | 0.69628 | 0.80996 | 0.80996 | 0.80996 | 0.80996 | 0.80996
2020-12-04 07:00 | Summer | 1.8998 | 2.7189 | 3.9234 | 3.9234 | 3.9234 | 3.9234 | 0.67446 | 1.1037 | 1.5124 | 1.819 | 1.819 | 1.819 | 2.3244 | 2.9996 | 3.442 | 3.6748 | 4.1404 | 4.6061 | 0.96025 | 1.8952 | 2.2743 | 2.2743 | 2.2743 | 2.2743 | 0.91406 | 1.0633 | 1.0633 | 1.0633 | 1.0633 | 1.0633
2020-12-04 08:00 | Summer | 2.4402 | 3.4923 | 5.0395 | 5.0395 | 5.0395 | 5.0395 | 0.83736 | 1.3702 | 1.8777 | 2.2583 | 2.2583 | 2.2583 | 2.6572 | 3.429 | 3.9347 | 4.2009 | 4.7332 | 5.2655 | 1.0517 | 2.0757 | 2.4909 | 2.4909 | 2.4909 | 2.4909 | 1.2365 | 1.4383 | 1.4383 | 1.4383 | 1.4383 | 1.4383
2020-12-04 09:00 | Summer | 2.7626 | 3.9538 | 5.7054 | 5.7054 | 5.7054 | 5.7054 | 0.86879 | 1.4217 | 1.9482 | 2.3431 | 2.3431 | 2.3431 | 2.8769 | 3.7126 | 4.2601 | 4.5483 | 5.1246 | 5.701 | 1.1012 | 2.1735 | 2.6082 | 2.6082 | 2.6082 | 2.6082 | 1.4099 | 1.6401 | 1.6401 | 1.6401 | 1.6401 | 1.6401
2020-12-04 10:00 | Summer | 2.7436 | 3.9265 | 5.6661 | 5.6661 | 5.6661 | 5.6661 | 0.91738 | 1.5012 | 2.0571 | 2.4741 | 2.4741 | 2.4741 | 3.0484 | 3.9339 | 4.5141 | 4.8194 | 5.4301 | 6.0408 | 1.2575 | 2.4818 | 2.9782 | 2.9782 | 2.9782 | 2.9782 | 1.4289 | 1.6622 | 1.6622 | 1.6622 | 1.6622 | 1.6622
2020-12-04 11:00 | Summer | 2.7436 | 3.9265 | 5.6661 | 5.6661 | 5.6661 | 5.6661 | 0.98597 | 1.6134 | 2.211 | 2.6591 | 2.6591 | 2.6591 | 3.1056 | 4.0077 | 4.5987 | 4.9098 | 5.5319 | 6.154 | 1.1241 | 2.2186 | 2.6623 | 2.6623 | 2.6623 | 2.6623 | 1.467 | 1.7066 | 1.7066 | 1.7066 | 1.7066 | 1.7066
2020-12-04 12:00 | Summer | 2.7626 | 3.9538 | 5.7054 | 5.7054 | 5.7054 | 5.7054 | 0.99168 | 1.6228 | 2.2238 | 2.6745 | 2.6745 | 2.6745 | 3.1056 | 4.0077 | 4.5987 | 4.9098 | 5.5319 | 6.154 | 1.1165 | 2.2036 | 2.6443 | 2.6443 | 2.6443 | 2.6443 | 1.4861 | 1.7287 | 1.7287 | 1.7287 | 1.7287 | 1.7287
2020-12-04 13:00 | Summer | 2.6293 | 3.7629 | 5.43 | 5.43 | 5.43 | 5.43 | 1.2289 | 2.0109 | 2.7557 | 3.3143 | 3.3143 | 3.3143 | 3.2008 | 4.1306 | 4.7398 | 5.0604 | 5.7016 | 6.3428 | 1.1279 | 2.2261 | 2.6714 | 2.6714 | 2.6714 | 2.6714 | 1.5052 | 1.7509 | 1.7509 | 1.7509 | 1.7509 | 1.7509
2020-12-04 14:00 | Summer | 2.6864 | 3.8447 | 5.548 | 5.548 | 5.548 | 5.548 | 1.2375 | 2.0249 | 2.7749 | 3.3374 | 3.3374 | 3.3374 | 3.1627 | 4.0814 | 4.6833 | 5.0001 | 5.6337 | 6.2673 | 1.1774 | 2.3239 | 2.7887 | 2.7887 | 2.7887 | 2.7887 | 1.4861 | 1.7287 | 1.7287 | 1.7287 | 1.7287 | 1.7287
2020-12-04 15:00 | Summer | 2.7626 | 3.9538 | 5.7054 | 5.7054 | 5.7054 | 5.7054 | 1.3375 | 2.1886 | 2.9992 | 3.6072 | 3.6072 | 3.6072 | 3.2008 | 4.1306 | 4.7398 | 5.0604 | 5.7016 | 6.3428 | 1.2384 | 2.4442 | 2.9331 | 2.9331 | 2.9331 | 2.9331 | 1.5052 | 1.7509 | 1.7509 | 1.7509 | 1.7509 | 1.7509
2020-12-04 16:00 | Summer | 2.7436 | 3.9265 | 5.6661 | 5.6661 | 5.6661 | 5.6661 | 1.266 | 2.0717 | 2.839 | 3.4145 | 3.4145 | 3.4145 | 3.2008 | 4.1306 | 4.7398 | 5.0604 | 5.7016 | 6.3428 | 1.2232 | 2.4142 | 2.897 | 2.897 | 2.897 | 2.897 | 1.4289 | 1.6622 | 1.6622 | 1.6622 | 1.6622 | 1.6622
2020-12-04 17:00 | Summer | 2.6027 | 3.7249 | 5.3752 | 5.3752 | 5.3752 | 5.3752 | 1.1546 | 1.8893 | 2.5891 | 3.1139 | 3.1139 | 3.1139 | 3.1818 | 4.106 | 4.7115 | 5.0303 | 5.6677 | 6.3051 | 1.2194 | 2.4066 | 2.888 | 2.888 | 2.888 | 2.888 | 1.3908 | 1.6179 | 1.6179 | 1.6179 | 1.6179 | 1.6179
2020-12-04 18:00 | Summer | 1.9328 | 2.7661 | 3.9916 | 3.9916 | 3.9916 | 3.9916 | 0.95157 | 1.5571 | 2.1338 | 2.5664 | 2.5664 | 2.5664 | 2.8388 | 3.6634 | 4.2037 | 4.4881 | 5.0568 | 5.6255 | 1.0365 | 2.0456 | 2.4548 | 2.4548 | 2.4548 | 2.4548 | 0.94956 | 1.1046 | 1.1046 | 1.1046 | 1.1046 | 1.1046
2020-12-04 19:00 | Summer | 1.2956 | 1.8542 | 2.6756 | 2.6756 | 2.6756 | 2.6756 | 0.71733 | 1.1738 | 1.6085 | 1.9346 | 1.9346 | 1.9346 | 2.6715 | 3.4475 | 3.9559 | 4.2235 | 4.7587 | 5.2938 | 1.0631 | 2.0983 | 2.5179 | 2.5179 | 2.5179 | 2.5179 | 0.72698 | 0.84567 | 0.84567 | 0.84567 | 0.84567 | 0.84567
2020-12-04 20:00 | Summer | 1.2575 | 1.7996 | 2.5969 | 2.5969 | 2.5969 | 2.5969 | 0.69732 | 1.1411 | 1.5637 | 1.8807 | 1.8807 | 1.8807 | 2.3435 | 3.0242 | 3.4702 | 3.7049 | 4.1744 | 4.6438 | 1.0212 | 2.0156 | 2.4187 | 2.4187 | 2.4187 | 2.4187 | 0.70494 | 0.82004 | 0.82004 | 0.82004 | 0.82004 | 0.82004
2020-12-04 21:00 | Summer | 1.1622 | 1.6633 | 2.4002 | 2.4002 | 2.4002 | 2.4002 | 0.61444 | 1.0054 | 1.3778 | 1.6571 | 1.6571 | 1.6571 | 2.2101 | 2.8521 | 3.2727 | 3.4941 | 3.9368 | 4.3796 | 0.91452 | 1.805 | 2.166 | 2.166 | 2.166 | 2.166 | 0.59063 | 0.68706 | 0.68706 | 0.68706 | 0.68706 | 0.68706
2020-12-04 22:00 | Summer | 1.105 | 1.5815 | 2.2822 | 2.2822 | 2.2822 | 2.2822 | 0.58872 | 0.96336 | 1.3202 | 1.5878 | 1.5878 | 1.5878 | 2.0577 | 2.6554 | 3.047 | 3.2531 | 3.6653 | 4.0775 | 0.89928 | 1.7749 | 2.1299 | 2.1299 | 2.1299 | 2.1299 | 0.54161 | 0.63004 | 0.63004 | 0.63004 | 0.63004 | 0.63004
2020-12-04 23:00 | Summer | 1.0288 | 1.4724 | 2.1248 | 2.1248 | 2.1248 | 2.1248 | 0.66588 | 1.0896 | 1.4932 | 1.7959 | 1.7959 | 1.7959 | 1.9243 | 2.4833 | 2.8495 | 3.0422 | 3.4277 | 3.8132 | 0.87261 | 1.7222 | 2.0667 | 2.0667 | 2.0667 | 2.0667 | 0.49267 | 0.5731 | 0.5731 | 0.5731 | 0.5731 | 0.5731
2020-12-05 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.43439 | 0.71083 | 0.9741 | 1.1715 | 1.1715 | 1.1715 | 1.7711 | 2.2855 | 2.6226 | 2.8 | 3.1548 | 3.5096 | 0.73924 | 1.459 | 1.7508 | 1.7508 | 1.7508 | 1.7508 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-12-05 01:00 | Summer | 0.99193 | 1.4196 | 2.0485 | 2.0485 | 2.0485 | 2.0485 | 0.35437 | 0.57988 | 0.79466 | 0.95574 | 0.95574 | 0.95574 | 1.7338 | 2.2374 | 2.5674 | 2.741 | 3.0884 | 3.4357 | 0.6516 | 1.286 | 1.5433 | 1.5433 | 1.5433 | 1.5433 | 0.47173 | 0.54875 | 0.54875 | 0.54875 | 0.54875 | 0.54875
2020-12-05 02:00 | Summer | 1.0288 | 1.4724 | 2.1248 | 2.1248 | 2.1248 | 2.1248 | 0.37438 | 0.61262 | 0.83952 | 1.0097 | 1.0097 | 1.0097 | 1.6766 | 2.1636 | 2.4827 | 2.6507 | 2.9865 | 3.3224 | 0.6516 | 1.286 | 1.5433 | 1.5433 | 1.5433 | 1.5433 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-12-05 03:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.37724 | 0.6173 | 0.84593 | 1.0174 | 1.0174 | 1.0174 | 1.6004 | 2.0653 | 2.3699 | 2.5302 | 2.8508 | 3.1714 | 0.62873 | 1.2409 | 1.4891 | 1.4891 | 1.4891 | 1.4891 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-12-05 04:00 | Summer | 1.0097 | 1.4451 | 2.0853 | 2.0853 | 2.0853 | 2.0853 | 0.40296 | 0.65939 | 0.9036 | 1.0868 | 1.0868 | 1.0868 | 1.6675 | 2.1518 | 2.4692 | 2.6362 | 2.9702 | 3.3043 | 0.58301 | 1.1507 | 1.3808 | 1.3808 | 1.3808 | 1.3808 | 0.42598 | 0.49553 | 0.49553 | 0.49553 | 0.49553 | 0.49553
2020-12-05 05:00 | Summer | 1.0479 | 1.4997 | 2.1641 | 2.1641 | 2.1641 | 2.1641 | 0.37724 | 0.6173 | 0.84593 | 1.0174 | 1.0174 | 1.0174 | 1.7481 | 2.2559 | 2.5886 | 2.7637 | 3.1139 | 3.4641 | 0.60587 | 1.1958 | 1.435 | 1.435 | 1.435 | 1.435 | 0.43821 | 0.50975 | 0.50975 | 0.50975 | 0.50975 | 0.50975
2020-12-05 06:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.44583 | 0.72953 | 0.99973 | 1.2024 | 1.2024 | 1.2024 | 1.9015 | 2.4538 | 2.8157 | 3.0062 | 3.3871 | 3.768 | 0.71637 | 1.4139 | 1.6967 | 1.6967 | 1.6967 | 1.6967 | 0.4816 | 0.56023 | 0.56023 | 0.56023 | 0.56023 | 0.56023
2020-12-05 07:00 | Summer | 1.1432 | 1.636 | 2.3609 | 2.3609 | 2.3609 | 2.3609 | 0.49441 | 0.80903 | 1.1087 | 1.3334 | 1.3334 | 1.3334 | 2.0386 | 2.6308 | 3.0188 | 3.223 | 3.6314 | 4.0398 | 0.73924 | 1.459 | 1.7508 | 1.7508 | 1.7508 | 1.7508 | 0.55252 | 0.64273 | 0.64273 | 0.64273 | 0.64273 | 0.64273
2020-12-05 08:00 | Summer | 1.1622 | 1.6633 | 2.4002 | 2.4002 | 2.4002 | 2.4002 | 0.52299 | 0.8558 | 1.1728 | 1.4105 | 1.4105 | 1.4105 | 2.2169 | 2.8608 | 3.2827 | 3.5048 | 3.9489 | 4.393 | 0.7964 | 1.5718 | 1.8862 | 1.8862 | 1.8862 | 1.8862 | 0.55252 | 0.64273 | 0.64273 | 0.64273 | 0.64273 | 0.64273
2020-12-05 09:00 | Summer | 1.1622 | 1.6633 | 2.4002 | 2.4002 | 2.4002 | 2.4002 | 0.53728 | 0.87918 | 1.2048 | 1.449 | 1.449 | 1.449 | 2.3625 | 3.0488 | 3.4984 | 3.735 | 4.2083 | 4.6816 | 0.88404 | 1.7448 | 2.0938 | 2.0938 | 2.0938 | 2.0938 | 0.59063 | 0.68706 | 0.68706 | 0.68706 | 0.68706 | 0.68706
2020-12-05 10:00 | Summer | 1.2194 | 1.7451 | 2.5183 | 2.5183 | 2.5183 | 2.5183 | 0.66303 | 1.085 | 1.4868 | 1.7882 | 1.7882 | 1.7882 | 2.4959 | 3.2209 | 3.6959 | 3.9459 | 4.4459 | 4.9459 | 0.84593 | 1.6696 | 2.0035 | 2.0035 | 2.0035 | 2.0035 | 0.62873 | 0.73138 | 0.73138 | 0.73138 | 0.73138 | 0.73138
2020-12-05 11:00 | Summer | 1.2956 | 1.8542 | 2.6756 | 2.6756 | 2.6756 | 2.6756 | 0.77448 | 1.2673 | 1.7367 | 2.0888 | 2.0888 | 2.0888 | 2.4959 | 3.2209 | 3.6959 | 3.9459 | 4.4459 | 4.9459 | 0.81926 | 1.617 | 1.9403 | 1.9403 | 1.9403 | 1.9403 | 0.62873 | 0.73138 | 0.73138 | 0.73138 | 0.73138 | 0.73138
2020-12-05 12:00 | Summer | 1.2575 | 1.7996 | 2.5969 | 2.5969 | 2.5969 | 2.5969 | 0.83736 | 1.3702 | 1.8777 | 2.2583 | 2.2583 | 2.2583 | 2.534 | 3.2701 | 3.7523 | 4.0061 | 4.5138 | 5.0214 | 0.81545 | 1.6094 | 1.9313 | 1.9313 | 1.9313 | 1.9313 | 0.62873 | 0.73138 | 0.73138 | 0.73138 | 0.73138 | 0.73138
2020-12-05 13:00 | Summer | 1.2765 | 1.8269 | 2.6363 | 2.6363 | 2.6363 | 2.6363 | 1.0231 | 1.6742 | 2.2943 | 2.7593 | 2.7593 | 2.7593 | 2.6293 | 3.393 | 3.8934 | 4.1567 | 4.6835 | 5.2102 | 0.84593 | 1.6696 | 2.0035 | 2.0035 | 2.0035 | 2.0035 | 0.62873 | 0.73138 | 0.73138 | 0.73138 | 0.73138 | 0.73138
2020-12-05 14:00 | Summer | 1.2194 | 1.7451 | 2.5183 | 2.5183 | 2.5183 | 2.5183 | 0.98882 | 1.6181 | 2.2174 | 2.6668 | 2.6668 | 2.6668 | 2.6483 | 3.4176 | 3.9216 | 4.1869 | 4.7174 | 5.2479 | 0.86879 | 1.7147 | 2.0577 | 2.0577 | 2.0577 | 2.0577 | 0.57208 | 0.66548 | 0.66548 | 0.66548 | 0.66548 | 0.66548
2020-12-05 15:00 | Summer | 1.2384 | 1.7724 | 2.5576 | 2.5576 | 2.5576 | 2.5576 | 0.88308 | 1.445 | 1.9802 | 2.3816 | 2.3816 | 2.3816 | 2.5988 | 3.3537 | 3.8483 | 4.1087 | 4.6293 | 5.1499 | 0.87261 | 1.7222 | 2.0667 | 2.0667 | 2.0667 | 2.0667 | 0.59063 | 0.68706 | 0.68706 | 0.68706 | 0.68706 | 0.68706
2020-12-05 16:00 | Summer | 1.2765 | 1.8269 | 2.6363 | 2.6363 | 2.6363 | 2.6363 | 0.8888 | 1.4544 | 1.9931 | 2.3971 | 2.3971 | 2.3971 | 2.7055 | 3.4913 | 4.0062 | 4.2772 | 4.8192 | 5.3612 | 0.92976 | 1.8351 | 2.2021 | 2.2021 | 2.2021 | 2.2021 | 0.60968 | 0.70922 | 0.70922 | 0.70922 | 0.70922 | 0.70922
2020-12-05 17:00 | Summer | 1.2003 | 1.7178 | 2.4789 | 2.4789 | 2.4789 | 2.4789 | 0.86594 | 1.417 | 1.9418 | 2.3354 | 2.3354 | 2.3354 | 2.6102 | 3.3684 | 3.8652 | 4.1266 | 4.6495 | 5.1724 | 1.0098 | 1.993 | 2.3916 | 2.3916 | 2.3916 | 2.3916 | 0.59063 | 0.68706 | 0.68706 | 0.68706 | 0.68706 | 0.68706
2020-12-05 18:00 | Summer | 1.1432 | 1.636 | 2.3609 | 2.3609 | 2.3609 | 2.3609 | 0.85736 | 1.403 | 1.9226 | 2.3123 | 2.3123 | 2.3123 | 2.3821 | 3.074 | 3.5274 | 3.766 | 4.2432 | 4.7204 | 1.0441 | 2.0607 | 2.4728 | 2.4728 | 2.4728 | 2.4728 | 0.57158 | 0.6649 | 0.6649 | 0.6649 | 0.6649 | 0.6649
2020-12-05 19:00 | Summer | 1.105 | 1.5815 | 2.2822 | 2.2822 | 2.2822 | 2.2822 | 0.87165 | 1.4263 | 1.9546 | 2.3508 | 2.3508 | 2.3508 | 2.3816 | 3.0734 | 3.5266 | 3.7652 | 4.2423 | 4.7194 | 1.0136 | 2.0005 | 2.4006 | 2.4006 | 2.4006 | 2.4006 | 0.59063 | 0.68706 | 0.68706 | 0.68706 | 0.68706 | 0.68706
2020-12-05 20:00 | Summer | 1.086 | 1.5542 | 2.2428 | 2.2428 | 2.2428 | 2.2428 | 0.77734 | 1.272 | 1.7431 | 2.0965 | 2.0965 | 2.0965 | 2.3816 | 3.0734 | 3.5266 | 3.7652 | 4.2423 | 4.7194 | 0.97549 | 1.9253 | 2.3104 | 2.3104 | 2.3104 | 2.3104 | 0.57158 | 0.6649 | 0.6649 | 0.6649 | 0.6649 | 0.6649
2020-12-05 21:00 | Summer | 1.0669 | 1.527 | 2.2035 | 2.2035 | 2.2035 | 2.2035 | 0.74019 | 1.2112 | 1.6598 | 1.9963 | 1.9963 | 1.9963 | 2.2482 | 2.9013 | 3.3291 | 3.5543 | 4.0047 | 4.4551 | 0.89547 | 1.7674 | 2.1208 | 2.1208 | 2.1208 | 2.1208 | 0.55252 | 0.64273 | 0.64273 | 0.64273 | 0.64273 | 0.64273
2020-12-05 22:00 | Summer | 1.0288 | 1.4724 | 2.1248 | 2.1248 | 2.1248 | 2.1248 | 0.67446 | 1.1037 | 1.5124 | 1.819 | 1.819 | 1.819 | 2.0196 | 2.6062 | 2.9906 | 3.1929 | 3.5974 | 4.002 | 0.92976 | 1.8351 | 2.2021 | 2.2021 | 2.2021 | 2.2021 | 0.53347 | 0.62057 | 0.62057 | 0.62057 | 0.62057 | 0.62057
2020-12-05 23:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.54299 | 0.88854 | 1.2176 | 1.4644 | 1.4644 | 1.4644 | 1.9434 | 2.5079 | 2.8777 | 3.0724 | 3.4617 | 3.851 | 0.8345 | 1.647 | 1.9764 | 1.9764 | 1.9764 | 1.9764 | 0.50328 | 0.58545 | 0.58545 | 0.58545 | 0.58545 | 0.58545
2020-12-06 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.44297 | 0.72486 | 0.99332 | 1.1947 | 1.1947 | 1.1947 | 1.81 | 2.3358 | 2.6802 | 2.8615 | 3.2241 | 3.5867 | 0.77353 | 1.5267 | 1.832 | 1.832 | 1.832 | 1.832 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-12-06 01:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.44011 | 0.72018 | 0.98691 | 1.187 | 1.187 | 1.187 | 1.689 | 2.1796 | 2.501 | 2.6702 | 3.0086 | 3.3469 | 0.64779 | 1.2785 | 1.5342 | 1.5342 | 1.5342 | 1.5342 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-12-06 02:00 | Summer | 1.0288 | 1.4724 | 2.1248 | 2.1248 | 2.1248 | 2.1248 | 0.39824 | 0.65167 | 0.89303 | 1.074 | 1.074 | 1.074 | 1.7147 | 2.2128 | 2.5392 | 2.7109 | 3.0544 | 3.3979 | 0.62111 | 1.2259 | 1.4711 | 1.4711 | 1.4711 | 1.4711 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-12-06 03:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.40296 | 0.65939 | 0.9036 | 1.0868 | 1.0868 | 1.0868 | 1.5814 | 2.0407 | 2.3417 | 2.5001 | 2.8169 | 3.1337 | 0.63635 | 1.256 | 1.5072 | 1.5072 | 1.5072 | 1.5072 | 0.43821 | 0.50975 | 0.50975 | 0.50975 | 0.50975 | 0.50975
2020-12-06 04:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.40867 | 0.66874 | 0.91642 | 1.1022 | 1.1022 | 1.1022 | 1.5814 | 2.0407 | 2.3417 | 2.5001 | 2.8169 | 3.1337 | 0.59444 | 1.1732 | 1.4079 | 1.4079 | 1.4079 | 1.4079 | 0.41933 | 0.48779 | 0.48779 | 0.48779 | 0.48779 | 0.48779
2020-12-06 05:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.38581 | 0.63133 | 0.86515 | 1.0405 | 1.0405 | 1.0405 | 1.6195 | 2.0899 | 2.3981 | 2.5603 | 2.8847 | 3.2092 | 0.57157 | 1.1281 | 1.3537 | 1.3537 | 1.3537 | 1.3537 | 0.41916 | 0.48759 | 0.48759 | 0.48759 | 0.48759 | 0.48759
2020-12-06 06:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.43439 | 0.71083 | 0.9741 | 1.1715 | 1.1715 | 1.1715 | 1.6195 | 2.0899 | 2.3981 | 2.5603 | 2.8847 | 3.2092 | 0.6173 | 1.2184 | 1.462 | 1.462 | 1.462 | 1.462 | 0.43188 | 0.50239 | 0.50239 | 0.50239 | 0.50239 | 0.50239
2020-12-06 07:00 | Summer | 1.0288 | 1.4724 | 2.1248 | 2.1248 | 2.1248 | 2.1248 | 0.45154 | 0.73889 | 1.0125 | 1.2178 | 1.2178 | 1.2178 | 1.7606 | 2.272 | 2.6071 | 2.7834 | 3.1361 | 3.4888 | 0.70113 | 1.3838 | 1.6606 | 1.6606 | 1.6606 | 1.6606 | 0.43821 | 0.50975 | 0.50975 | 0.50975 | 0.50975 | 0.50975
2020-12-06 08:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.43725 | 0.7155 | 0.98051 | 1.1793 | 1.1793 | 1.1793 | 1.9624 | 2.5325 | 2.9059 | 3.1025 | 3.4956 | 3.8887 | 0.73924 | 1.459 | 1.7508 | 1.7508 | 1.7508 | 1.7508 | 0.45653 | 0.53106 | 0.53106 | 0.53106 | 0.53106 | 0.53106
2020-12-06 09:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.46297 | 0.75759 | 1.0382 | 1.2486 | 1.2486 | 1.2486 | 2.0386 | 2.6308 | 3.0188 | 3.223 | 3.6314 | 4.0398 | 0.76591 | 1.5117 | 1.814 | 1.814 | 1.814 | 1.814 | 0.50251 | 0.58455 | 0.58455 | 0.58455 | 0.58455 | 0.58455
2020-12-06 10:00 | Summer | 0.9563 | 1.3686 | 1.975 | 1.975 | 1.975 | 1.975 | 0.49727 | 0.81371 | 1.1151 | 1.3411 | 1.3411 | 1.3411 | 2.1529 | 2.7783 | 3.1881 | 3.4037 | 3.835 | 4.2663 | 0.72018 | 1.4214 | 1.7057 | 1.7057 | 1.7057 | 1.7057 | 0.55252 | 0.64273 | 0.64273 | 0.64273 | 0.64273 | 0.64273
2020-12-06 11:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.41725 | 0.68277 | 0.93565 | 1.1253 | 1.1253 | 1.1253 | 2.1339 | 2.7537 | 3.1598 | 3.3736 | 3.8011 | 4.2285 | 0.75067 | 1.4816 | 1.7779 | 1.7779 | 1.7779 | 1.7779 | 0.55252 | 0.64273 | 0.64273 | 0.64273 | 0.64273 | 0.64273
2020-12-06 12:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.39724 | 0.65003 | 0.89079 | 1.0713 | 1.0713 | 1.0713 | 2.172 | 2.8029 | 3.2163 | 3.4338 | 3.8689 | 4.3041 | 0.73543 | 1.4515 | 1.7418 | 1.7418 | 1.7418 | 1.7418 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-12-06 13:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.37724 | 0.6173 | 0.84593 | 1.0174 | 1.0174 | 1.0174 | 2.0958 | 2.7046 | 3.1034 | 3.3133 | 3.7332 | 4.153 | 0.76591 | 1.5117 | 1.814 | 1.814 | 1.814 | 1.814 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-12-06 14:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.42011 | 0.68744 | 0.94205 | 1.133 | 1.133 | 1.133 | 2.1141 | 2.7282 | 3.1305 | 3.3423 | 3.7658 | 4.1893 | 0.75829 | 1.4966 | 1.796 | 1.796 | 1.796 | 1.796 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-12-06 15:00 | Summer | 1.0479 | 1.4997 | 2.1641 | 2.1641 | 2.1641 | 2.1641 | 0.40867 | 0.66874 | 0.91642 | 1.1022 | 1.1022 | 1.1022 | 2.1148 | 2.7291 | 3.1316 | 3.3435 | 3.7671 | 4.1908 | 0.78496 | 1.5493 | 1.8591 | 1.8591 | 1.8591 | 1.8591 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-12-06 16:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.42011 | 0.68744 | 0.94205 | 1.133 | 1.133 | 1.133 | 2.1339 | 2.7537 | 3.1598 | 3.3736 | 3.8011 | 4.2285 | 0.76972 | 1.5192 | 1.823 | 1.823 | 1.823 | 1.823 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-12-06 17:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.40582 | 0.66406 | 0.91001 | 1.0945 | 1.0945 | 1.0945 | 2.0971 | 2.7063 | 3.1054 | 3.3155 | 3.7356 | 4.1557 | 0.724 | 1.4289 | 1.7147 | 1.7147 | 1.7147 | 1.7147 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-12-06 18:00 | Summer | 0.97505 | 1.3954 | 2.0137 | 2.0137 | 2.0137 | 2.0137 | 0.43439 | 0.71083 | 0.9741 | 1.1715 | 1.1715 | 1.1715 | 1.9666 | 2.5379 | 2.9122 | 3.1092 | 3.5032 | 3.8971 | 0.75067 | 1.4816 | 1.7779 | 1.7779 | 1.7779 | 1.7779 | 0.49523 | 0.57609 | 0.57609 | 0.57609 | 0.57609 | 0.57609
2020-12-06 19:00 | Summer | 1.0479 | 1.4997 | 2.1641 | 2.1641 | 2.1641 | 2.1641 | 0.42582 | 0.6968 | 0.95487 | 1.1484 | 1.1484 | 1.1484 | 1.9243 | 2.4833 | 2.8495 | 3.0422 | 3.4277 | 3.8132 | 0.76972 | 1.5192 | 1.823 | 1.823 | 1.823 | 1.823 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-12-06 20:00 | Summer | 1.0479 | 1.4997 | 2.1641 | 2.1641 | 2.1641 | 2.1641 | 0.46278 | 0.75728 | 1.0378 | 1.2481 | 1.2481 | 1.2481 | 1.9053 | 2.4587 | 2.8213 | 3.0121 | 3.3938 | 3.7755 | 0.76591 | 1.5117 | 1.814 | 1.814 | 1.814 | 1.814 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-12-06 21:00 | Summer | 1.0479 | 1.4997 | 2.1641 | 2.1641 | 2.1641 | 2.1641 | 0.46583 | 0.76227 | 1.0446 | 1.2563 | 1.2563 | 1.2563 | 1.8672 | 2.4095 | 2.7649 | 2.9519 | 3.3259 | 3.7 | 0.78496 | 1.5493 | 1.8591 | 1.8591 | 1.8591 | 1.8591 | 0.45249 | 0.52636 | 0.52636 | 0.52636 | 0.52636 | 0.52636
2020-12-06 22:00 | Summer | 1.0288 | 1.4724 | 2.1248 | 2.1248 | 2.1248 | 2.1248 | 0.43154 | 0.70615 | 0.96769 | 1.1638 | 1.1638 | 1.1638 | 1.7909 | 2.3112 | 2.652 | 2.8314 | 3.1902 | 3.549 | 0.70113 | 1.3838 | 1.6606 | 1.6606 | 1.6606 | 1.6606 | 0.43825 | 0.5098 | 0.5098 | 0.5098 | 0.5098 | 0.5098
2020-12-06 23:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.39153 | 0.64068 | 0.87797 | 1.0559 | 1.0559 | 1.0559 | 1.7052 | 2.2005 | 2.5251 | 2.6959 | 3.0375 | 3.3791 | 0.6897 | 1.3613 | 1.6335 | 1.6335 | 1.6335 | 1.6335 | 0.43821 | 0.50975 | 0.50975 | 0.50975 | 0.50975 | 0.50975
2020-12-07 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.38295 | 0.62665 | 0.85874 | 1.0328 | 1.0328 | 1.0328 | 1.6004 | 2.0653 | 2.3699 | 2.5302 | 2.8508 | 3.1714 | 0.68589 | 1.3537 | 1.6245 | 1.6245 | 1.6245 | 1.6245 | 0.41916 | 0.48759 | 0.48759 | 0.48759 | 0.48759 | 0.48759
2020-12-07 01:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.34866 | 0.57053 | 0.78184 | 0.94032 | 0.94032 | 0.94032 | 1.5623 | 2.0161 | 2.3135 | 2.4699 | 2.7829 | 3.0959 | 0.60537 | 1.1948 | 1.4338 | 1.4338 | 1.4338 | 1.4338 | 0.43821 | 0.50975 | 0.50975 | 0.50975 | 0.50975 | 0.50975
2020-12-07 02:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.46297 | 0.75759 | 1.0382 | 1.2486 | 1.2486 | 1.2486 | 1.5052 | 1.9424 | 2.2288 | 2.3796 | 2.6811 | 2.9826 | 0.60587 | 1.1958 | 1.435 | 1.435 | 1.435 | 1.435 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-12-07 03:00 | Summer | 0.99066 | 1.4178 | 2.0459 | 2.0459 | 2.0459 | 2.0459 | 0.41153 | 0.67342 | 0.92283 | 1.1099 | 1.1099 | 1.1099 | 1.5052 | 1.9424 | 2.2288 | 2.3796 | 2.6811 | 2.9826 | 0.59444 | 1.1732 | 1.4079 | 1.4079 | 1.4079 | 1.4079 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-12-07 04:00 | Summer | 1.2575 | 1.7996 | 2.5969 | 2.5969 | 2.5969 | 2.5969 | 0.43725 | 0.7155 | 0.98051 | 1.1793 | 1.1793 | 1.1793 | 1.5572 | 2.0095 | 2.3059 | 2.4619 | 2.7738 | 3.0858 | 0.59063 | 1.1657 | 1.3989 | 1.3989 | 1.3989 | 1.3989 | 0.45572 | 0.53013 | 0.53013 | 0.53013 | 0.53013 | 0.53013
2020-12-07 05:00 | Summer | 1.2993 | 1.8595 | 2.6834 | 2.6834 | 2.6834 | 2.6834 | 0.53442 | 0.87451 | 1.1984 | 1.4413 | 1.4413 | 1.4413 | 1.6378 | 2.1135 | 2.4252 | 2.5892 | 2.9173 | 3.2454 | 0.6516 | 1.286 | 1.5433 | 1.5433 | 1.5433 | 1.5433 | 0.54865 | 0.63823 | 0.63823 | 0.63823 | 0.63823 | 0.63823
2020-12-07 06:00 | Summer | 1.4861 | 2.1268 | 3.0691 | 3.0691 | 3.0691 | 3.0691 | 0.74305 | 1.2159 | 1.6662 | 2.004 | 2.004 | 2.004 | 1.8672 | 2.4095 | 2.7649 | 2.9519 | 3.3259 | 3.7 | 0.76972 | 1.5192 | 1.823 | 1.823 | 1.823 | 1.823 | 0.73655 | 0.85681 | 0.85681 | 0.85681 | 0.85681 | 0.85681
2020-12-07 07:00 | Summer | 2.0577 | 2.9449 | 4.2495 | 4.2495 | 4.2495 | 4.2495 | 0.79449 | 1.3001 | 1.7816 | 2.1427 | 2.1427 | 2.1427 | 2.1339 | 2.7537 | 3.1598 | 3.3736 | 3.8011 | 4.2285 | 1.1127 | 2.1961 | 2.6353 | 2.6353 | 2.6353 | 2.6353 | 0.93358 | 1.086 | 1.086 | 1.086 | 1.086 | 1.086
2020-12-07 08:00 | Summer | 2.3816 | 3.4084 | 4.9185 | 4.9185 | 4.9185 | 4.9185 | 0.84593 | 1.3842 | 1.8969 | 2.2814 | 2.2814 | 2.2814 | 2.3435 | 3.0242 | 3.4702 | 3.7049 | 4.1744 | 4.6438 | 1.1127 | 2.1961 | 2.6353 | 2.6353 | 2.6353 | 2.6353 | 1.1428 | 1.3294 | 1.3294 | 1.3294 | 1.3294 | 1.3294
2020-12-07 09:00 | Summer | 2.534 | 3.6265 | 5.2332 | 5.2332 | 5.2332 | 5.2332 | 0.87451 | 1.431 | 1.961 | 2.3585 | 2.3585 | 2.3585 | 2.4578 | 3.1717 | 3.6395 | 3.8856 | 4.378 | 4.8704 | 0.97549 | 1.9253 | 2.3104 | 2.3104 | 2.3104 | 2.3104 | 1.2956 | 1.5071 | 1.5071 | 1.5071 | 1.5071 | 1.5071
2020-12-07 10:00 | Summer | 2.5149 | 3.5993 | 5.1939 | 5.1939 | 5.1939 | 5.1939 | 0.90023 | 1.4731 | 2.0187 | 2.4279 | 2.4279 | 2.4279 | 2.4988 | 3.2246 | 3.7001 | 3.9504 | 4.451 | 4.9516 | 0.95644 | 1.8877 | 2.2652 | 2.2652 | 2.2652 | 2.2652 | 1.3146 | 1.5293 | 1.5293 | 1.5293 | 1.5293 | 1.5293
2020-12-07 11:00 | Summer | 2.5721 | 3.6811 | 5.3119 | 5.3119 | 5.3119 | 5.3119 | 0.81735 | 1.3375 | 1.8328 | 2.2044 | 2.2044 | 2.2044 | 2.6293 | 3.393 | 3.8934 | 4.1567 | 4.6835 | 5.2102 | 0.99835 | 1.9704 | 2.3645 | 2.3645 | 2.3645 | 2.3645 | 1.3337 | 1.5514 | 1.5514 | 1.5514 | 1.5514 | 1.5514
2020-12-07 12:00 | Summer | 2.5149 | 3.5993 | 5.1939 | 5.1939 | 5.1939 | 5.1939 | 0.99168 | 1.6228 | 2.2238 | 2.6745 | 2.6745 | 2.6745 | 2.6483 | 3.4176 | 3.9216 | 4.1869 | 4.7174 | 5.2479 | 0.97168 | 1.9178 | 2.3013 | 2.3013 | 2.3013 | 2.3013 | 1.2956 | 1.5071 | 1.5071 | 1.5071 | 1.5071 | 1.5071
2020-12-07 13:00 | Summer | 2.4578 | 3.5175 | 5.0759 | 5.0759 | 5.0759 | 5.0759 | 0.95739 | 1.5666 | 2.1469 | 2.582 | 2.582 | 2.582 | 2.6864 | 3.4668 | 3.978 | 4.2471 | 4.7853 | 5.3234 | 0.93738 | 1.8501 | 2.2201 | 2.2201 | 2.2201 | 2.2201 | 1.3146 | 1.5293 | 1.5293 | 1.5293 | 1.5293 | 1.5293
2020-12-07 14:00 | Summer | 2.4768 | 3.5447 | 5.1152 | 5.1152 | 5.1152 | 5.1152 | 1.006 | 1.6461 | 2.2558 | 2.7131 | 2.7131 | 2.7131 | 2.6102 | 3.3684 | 3.8652 | 4.1266 | 4.6495 | 5.1724 | 0.97549 | 1.9253 | 2.3104 | 2.3104 | 2.3104 | 2.3104 | 1.2765 | 1.4849 | 1.4849 | 1.4849 | 1.4849 | 1.4849
2020-12-07 15:00 | Summer | 2.4578 | 3.5175 | 5.0759 | 5.0759 | 5.0759 | 5.0759 | 1.0145 | 1.6602 | 2.275 | 2.7362 | 2.7362 | 2.7362 | 2.6293 | 3.393 | 3.8934 | 4.1567 | 4.6835 | 5.2102 | 0.99073 | 1.9554 | 2.3465 | 2.3465 | 2.3465 | 2.3465 | 1.2384 | 1.4406 | 1.4406 | 1.4406 | 1.4406 | 1.4406
2020-12-07 16:00 | Summer | 2.4768 | 3.5447 | 5.1152 | 5.1152 | 5.1152 | 5.1152 | 1.0203 | 1.6695 | 2.2879 | 2.7516 | 2.7516 | 2.7516 | 2.5911 | 3.3438 | 3.8369 | 4.0965 | 4.6156 | 5.1347 | 1.0022 | 1.978 | 2.3735 | 2.3735 | 2.3735 | 2.3735 | 1.2194 | 1.4184 | 1.4184 | 1.4184 | 1.4184 | 1.4184
2020-12-07 17:00 | Summer | 2.2698 | 3.2484 | 4.6876 | 4.6876 | 4.6876 | 4.6876 | 0.9431 | 1.5433 | 2.1148 | 2.5435 | 2.5435 | 2.5435 | 2.4587 | 3.173 | 3.6409 | 3.8872 | 4.3797 | 4.8723 | 0.89166 | 1.7599 | 2.1118 | 2.1118 | 2.1118 | 2.1118 | 1.1241 | 1.3076 | 1.3076 | 1.3076 | 1.3076 | 1.3076
2020-12-07 18:00 | Summer | 1.6192 | 2.3173 | 3.344 | 3.344 | 3.344 | 3.344 | 0.7802 | 1.2767 | 1.7495 | 2.1042 | 2.1042 | 2.1042 | 2.2482 | 2.9013 | 3.3291 | 3.5543 | 4.0047 | 4.4551 | 0.8345 | 1.647 | 1.9764 | 1.9764 | 1.9764 | 1.9764 | 0.76872 | 0.89423 | 0.89423 | 0.89423 | 0.89423 | 0.89423
2020-12-07 19:00 | Summer | 1.1813 | 1.6906 | 2.4396 | 2.4396 | 2.4396 | 2.4396 | 0.66303 | 1.085 | 1.4868 | 1.7882 | 1.7882 | 1.7882 | 2.1725 | 2.8036 | 3.2171 | 3.4347 | 3.8699 | 4.3051 | 0.82307 | 1.6245 | 1.9494 | 1.9494 | 1.9494 | 1.9494 | 0.60143 | 0.69963 | 0.69963 | 0.69963 | 0.69963 | 0.69963
2020-12-07 20:00 | Summer | 1.1622 | 1.6633 | 2.4002 | 2.4002 | 2.4002 | 2.4002 | 0.66588 | 1.0896 | 1.4932 | 1.7959 | 1.7959 | 1.7959 | 2.0005 | 2.5816 | 2.9624 | 3.1627 | 3.5635 | 3.9643 | 0.88023 | 1.7373 | 2.0847 | 2.0847 | 2.0847 | 2.0847 | 0.57158 | 0.6649 | 0.6649 | 0.6649 | 0.6649 | 0.6649
2020-12-07 21:00 | Summer | 1.0669 | 1.527 | 2.2035 | 2.2035 | 2.2035 | 2.2035 | 0.64588 | 1.0569 | 1.4483 | 1.7419 | 1.7419 | 1.7419 | 1.9434 | 2.5079 | 2.8777 | 3.0724 | 3.4617 | 3.851 | 0.75067 | 1.4816 | 1.7779 | 1.7779 | 1.7779 | 1.7779 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-12-07 22:00 | Summer | 1.0291 | 1.4728 | 2.1254 | 2.1254 | 2.1254 | 2.1254 | 0.51156 | 0.83709 | 1.1471 | 1.3797 | 1.3797 | 1.3797 | 1.8862 | 2.4341 | 2.7931 | 2.982 | 3.3599 | 3.7377 | 0.75067 | 1.4816 | 1.7779 | 1.7779 | 1.7779 | 1.7779 | 0.43729 | 0.50869 | 0.50869 | 0.50869 | 0.50869 | 0.50869
2020-12-07 23:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.45726 | 0.74824 | 1.0254 | 1.2332 | 1.2332 | 1.2332 | 1.6967 | 2.1896 | 2.5125 | 2.6825 | 3.0224 | 3.3623 | 0.70875 | 1.3989 | 1.6786 | 1.6786 | 1.6786 | 1.6786 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-12-08 | Summer | 1.0288 | 1.4724 | 2.1248 | 2.1248 | 2.1248 | 2.1248 | 0.42868 | 0.70147 | 0.96128 | 1.1561 | 1.1561 | 1.1561 | 1.5623 | 2.0161 | 2.3135 | 2.4699 | 2.7829 | 3.0959 | 0.61349 | 1.2108 | 1.453 | 1.453 | 1.453 | 1.453 | 0.43821 | 0.50975 | 0.50975 | 0.50975 | 0.50975 | 0.50975
2020-12-08 01:00 | Summer | 1.0288 | 1.4724 | 2.1248 | 2.1248 | 2.1248 | 2.1248 | 0.4001 | 0.65471 | 0.89719 | 1.0791 | 1.0791 | 1.0791 | 1.5623 | 2.0161 | 2.3135 | 2.4699 | 2.7829 | 3.0959 | 0.56395 | 1.1131 | 1.3357 | 1.3357 | 1.3357 | 1.3357 | 0.41916 | 0.48759 | 0.48759 | 0.48759 | 0.48759 | 0.48759
2020-12-08 02:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.36581 | 0.59859 | 0.82029 | 0.98657 | 0.98657 | 0.98657 | 1.5242 | 1.967 | 2.257 | 2.4097 | 2.715 | 3.0204 | 0.56776 | 1.1206 | 1.3447 | 1.3447 | 1.3447 | 1.3447 | 0.41916 | 0.48759 | 0.48759 | 0.48759 | 0.48759 | 0.48759
2020-12-08 03:00 | Summer | 1.022 | 1.4627 | 2.1107 | 2.1107 | 2.1107 | 2.1107 | 0.41153 | 0.67342 | 0.92283 | 1.1099 | 1.1099 | 1.1099 | 1.5242 | 1.967 | 2.257 | 2.4097 | 2.715 | 3.0204 | 0.58301 | 1.1507 | 1.3808 | 1.3808 | 1.3808 | 1.3808 | 0.46202 | 0.53745 | 0.53745 | 0.53745 | 0.53745 | 0.53745
2020-12-08 04:00 | Summer | 1.1024 | 1.5778 | 2.2768 | 2.2768 | 2.2768 | 2.2768 | 0.47155 | 0.77162 | 1.0574 | 1.2717 | 1.2717 | 1.2717 | 1.6385 | 2.1145 | 2.4263 | 2.5904 | 2.9187 | 3.2469 | 0.62111 | 1.2259 | 1.4711 | 1.4711 | 1.4711 | 1.4711 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-12-08 05:00 | Summer | 1.2765 | 1.8269 | 2.6363 | 2.6363 | 2.6363 | 2.6363 | 0.52299 | 0.8558 | 1.1728 | 1.4105 | 1.4105 | 1.4105 | 1.6385 | 2.1145 | 2.4263 | 2.5904 | 2.9187 | 3.2469 | 0.75829 | 1.4966 | 1.796 | 1.796 | 1.796 | 1.796 | 0.52938 | 0.6158 | 0.6158 | 0.6158 | 0.6158 | 0.6158
2020-12-08 06:00 | Summer | 1.3256 | 1.8971 | 2.7376 | 2.7376 | 2.7376 | 2.7376 | 0.56872 | 0.93062 | 1.2753 | 1.5338 | 1.5338 | 1.5338 | 1.8339 | 2.3666 | 2.7156 | 2.8993 | 3.2667 | 3.6341 | 0.70875 | 1.3989 | 1.6786 | 1.6786 | 1.6786 | 1.6786 | 0.76183 | 0.88621 | 0.88621 | 0.88621 | 0.88621 | 0.88621
2020-12-08 07:00 | Summer | 2.1746 | 3.1122 | 4.491 | 4.491 | 4.491 | 4.491 | 0.8002 | 1.3094 | 1.7944 | 2.1581 | 2.1581 | 2.1581 | 2.1386 | 2.7598 | 3.1668 | 3.381 | 3.8095 | 4.2379 | 0.96787 | 1.9103 | 2.2923 | 2.2923 | 2.2923 | 2.2923 | 0.95867 | 1.1152 | 1.1152 | 1.1152 | 1.1152 | 1.1152
2020-12-08 08:00 | Summer | 2.2482 | 3.2175 | 4.643 | 4.643 | 4.643 | 4.643 | 0.85165 | 1.3936 | 1.9098 | 2.2969 | 2.2969 | 2.2969 | 2.3435 | 3.0242 | 3.4702 | 3.7049 | 4.1744 | 4.6438 | 0.96787 | 1.9103 | 2.2923 | 2.2923 | 2.2923 | 2.2923 | 1.1432 | 1.3298 | 1.3298 | 1.3298 | 1.3298 | 1.3298
2020-12-08 09:00 | Summer | 2.3625 | 3.3811 | 4.8791 | 4.8791 | 4.8791 | 4.8791 | 0.8345 | 1.3655 | 1.8713 | 2.2506 | 2.2506 | 2.2506 | 2.4578 | 3.1717 | 3.6395 | 3.8856 | 4.378 | 4.8704 | 0.96787 | 1.9103 | 2.2923 | 2.2923 | 2.2923 | 2.2923 | 1.2384 | 1.4406 | 1.4406 | 1.4406 | 1.4406 | 1.4406
2020-12-08 10:00 | Summer | 2.4768 | 3.5447 | 5.1152 | 5.1152 | 5.1152 | 5.1152 | 0.84307 | 1.3796 | 1.8905 | 2.2737 | 2.2737 | 2.2737 | 2.5149 | 3.2455 | 3.7241 | 3.976 | 4.4798 | 4.9836 | 1.1012 | 2.1735 | 2.6082 | 2.6082 | 2.6082 | 2.6082 | 1.2765 | 1.4849 | 1.4849 | 1.4849 | 1.4849 | 1.4849
2020-12-08 11:00 | Summer | 2.4387 | 3.4902 | 5.0365 | 5.0365 | 5.0365 | 5.0365 | 0.84879 | 1.3889 | 1.9033 | 2.2892 | 2.2892 | 2.2892 | 2.553 | 3.2946 | 3.7805 | 4.0362 | 4.5477 | 5.0591 | 1.0098 | 1.993 | 2.3916 | 2.3916 | 2.3916 | 2.3916 | 1.3146 | 1.5293 | 1.5293 | 1.5293 | 1.5293 | 1.5293
2020-12-08 12:00 | Summer | 2.4387 | 3.4902 | 5.0365 | 5.0365 | 5.0365 | 5.0365 | 0.8345 | 1.3655 | 1.8713 | 2.2506 | 2.2506 | 2.2506 | 2.6674 | 3.4422 | 3.9498 | 4.217 | 4.7513 | 5.2857 | 0.98311 | 1.9403 | 2.3284 | 2.3284 | 2.3284 | 2.3284 | 1.3146 | 1.5293 | 1.5293 | 1.5293 | 1.5293 | 1.5293
2020-12-08 13:00 | Summer | 2.3625 | 3.3811 | 4.8791 | 4.8791 | 4.8791 | 4.8791 | 0.9088 | 1.4871 | 2.0379 | 2.451 | 2.451 | 2.451 | 2.6293 | 3.393 | 3.8934 | 4.1567 | 4.6835 | 5.2102 | 0.99454 | 1.9629 | 2.3555 | 2.3555 | 2.3555 | 2.3555 | 1.2765 | 1.4849 | 1.4849 | 1.4849 | 1.4849 | 1.4849
2020-12-08 14:00 | Summer | 2.3625 | 3.3811 | 4.8791 | 4.8791 | 4.8791 | 4.8791 | 0.95453 | 1.562 | 2.1405 | 2.5743 | 2.5743 | 2.5743 | 2.6102 | 3.3684 | 3.8652 | 4.1266 | 4.6495 | 5.1724 | 1.0326 | 2.0381 | 2.4457 | 2.4457 | 2.4457 | 2.4457 | 1.2765 | 1.4849 | 1.4849 | 1.4849 | 1.4849 | 1.4849
2020-12-08 15:00 | Summer | 2.3764 | 3.4009 | 4.9077 | 4.9077 | 4.9077 | 4.9077 | 0.95453 | 1.562 | 2.1405 | 2.5743 | 2.5743 | 2.5743 | 2.6293 | 3.393 | 3.8934 | 4.1567 | 4.6835 | 5.2102 | 1.0174 | 2.008 | 2.4096 | 2.4096 | 2.4096 | 2.4096 | 1.2956 | 1.5071 | 1.5071 | 1.5071 | 1.5071 | 1.5071
2020-12-08 16:00 | Summer | 2.3816 | 3.4084 | 4.9185 | 4.9185 | 4.9185 | 4.9185 | 0.91738 | 1.5012 | 2.0571 | 2.4741 | 2.4741 | 2.4741 | 2.6293 | 3.393 | 3.8934 | 4.1567 | 4.6835 | 5.2102 | 1.0403 | 2.0532 | 2.4638 | 2.4638 | 2.4638 | 2.4638 | 1.2575 | 1.4628 | 1.4628 | 1.4628 | 1.4628 | 1.4628
2020-12-08 17:00 | Summer | 2.2781 | 3.2604 | 4.7048 | 4.7048 | 4.7048 | 4.7048 | 0.93167 | 1.5245 | 2.0892 | 2.5127 | 2.5127 | 2.5127 | 2.4959 | 3.2209 | 3.6959 | 3.9459 | 4.4459 | 4.9459 | 1.0403 | 2.0532 | 2.4638 | 2.4638 | 2.4638 | 2.4638 | 1.1622 | 1.352 | 1.352 | 1.352 | 1.352 | 1.352
2020-12-08 18:00 | Summer | 1.6865 | 2.4136 | 3.4829 | 3.4829 | 3.4829 | 3.4829 | 0.76877 | 1.258 | 1.7239 | 2.0733 | 2.0733 | 2.0733 | 2.4387 | 3.1471 | 3.6112 | 3.8555 | 4.3441 | 4.8326 | 1.0174 | 2.008 | 2.4096 | 2.4096 | 2.4096 | 2.4096 | 0.8811 | 1.0249 | 1.0249 | 1.0249 | 1.0249 | 1.0249
2020-12-08 19:00 | Summer | 1.2485 | 1.7869 | 2.5785 | 2.5785 | 2.5785 | 2.5785 | 0.64473 | 1.055 | 1.4458 | 1.7388 | 1.7388 | 1.7388 | 2.1718 | 2.8027 | 3.216 | 3.4335 | 3.8686 | 4.3037 | 0.99454 | 1.9629 | 2.3555 | 2.3555 | 2.3555 | 2.3555 | 0.68589 | 0.79787 | 0.79787 | 0.79787 | 0.79787 | 0.79787
2020-12-08 20:00 | Summer | 1.1241 | 1.6088 | 2.3215 | 2.3215 | 2.3215 | 2.3215 | 0.59158 | 0.96804 | 1.3266 | 1.5955 | 1.5955 | 1.5955 | 2.0386 | 2.6308 | 3.0188 | 3.223 | 3.6314 | 4.0398 | 1.0631 | 2.0983 | 2.5179 | 2.5179 | 2.5179 | 2.5179 | 0.57158 | 0.6649 | 0.6649 | 0.6649 | 0.6649 | 0.6649
2020-12-08 21:00 | Summer | 1.0669 | 1.527 | 2.2035 | 2.2035 | 2.2035 | 2.2035 | 0.54299 | 0.88854 | 1.2176 | 1.4644 | 1.4644 | 1.4644 | 1.9624 | 2.5325 | 2.9059 | 3.1025 | 3.4956 | 3.8887 | 0.91833 | 1.8125 | 2.175 | 2.175 | 2.175 | 2.175 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-12-08 22:00 | Summer | 1.0288 | 1.4724 | 2.1248 | 2.1248 | 2.1248 | 2.1248 | 0.46313 | 0.75784 | 1.0385 | 1.249 | 1.249 | 1.249 | 1.8481 | 2.3849 | 2.7366 | 2.9218 | 3.292 | 3.6622 | 0.81164 | 1.6019 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-12-08 23:00 | Summer | 0.97533 | 1.3959 | 2.0143 | 2.0143 | 2.0143 | 2.0143 | 0.44297 | 0.72486 | 0.99332 | 1.1947 | 1.1947 | 1.1947 | 1.6957 | 2.1882 | 2.5109 | 2.6808 | 3.0205 | 3.3602 | 0.76591 | 1.5117 | 1.814 | 1.814 | 1.814 | 1.814 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-12-09 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.36295 | 0.59391 | 0.81388 | 0.97886 | 0.97886 | 0.97886 | 1.5623 | 2.0161 | 2.3135 | 2.4699 | 2.7829 | 3.0959 | 0.71637 | 1.4139 | 1.6967 | 1.6967 | 1.6967 | 1.6967 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-12-09 01:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.38295 | 0.62665 | 0.85874 | 1.0328 | 1.0328 | 1.0328 | 1.5433 | 1.9915 | 2.2852 | 2.4398 | 2.749 | 3.0581 | 0.64779 | 1.2785 | 1.5342 | 1.5342 | 1.5342 | 1.5342 | 0.43821 | 0.50975 | 0.50975 | 0.50975 | 0.50975 | 0.50975
2020-12-09 02:00 | Summer | 0.96814 | 1.3856 | 1.9994 | 1.9994 | 1.9994 | 1.9994 | 0.38295 | 0.62665 | 0.85874 | 1.0328 | 1.0328 | 1.0328 | 1.5433 | 1.9915 | 2.2852 | 2.4398 | 2.749 | 3.0581 | 0.59297 | 1.1703 | 1.4044 | 1.4044 | 1.4044 | 1.4044 | 0.43821 | 0.50975 | 0.50975 | 0.50975 | 0.50975 | 0.50975
2020-12-09 03:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.40867 | 0.66874 | 0.91642 | 1.1022 | 1.1022 | 1.1022 | 1.5623 | 2.0161 | 2.3135 | 2.4699 | 2.7829 | 3.0959 | 0.64397 | 1.271 | 1.5252 | 1.5252 | 1.5252 | 1.5252 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-12-09 04:00 | Summer | 1.0509 | 1.5041 | 2.1704 | 2.1704 | 2.1704 | 2.1704 | 0.35369 | 0.57877 | 0.79313 | 0.9539 | 0.9539 | 0.9539 | 1.5814 | 2.0407 | 2.3417 | 2.5001 | 2.8169 | 3.1337 | 0.65922 | 1.3011 | 1.5613 | 1.5613 | 1.5613 | 1.5613 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-12-09 05:00 | Summer | 1.1622 | 1.6633 | 2.4002 | 2.4002 | 2.4002 | 2.4002 | 0.54585 | 0.89321 | 1.224 | 1.4721 | 1.4721 | 1.4721 | 1.6766 | 2.1636 | 2.4827 | 2.6507 | 2.9865 | 3.3224 | 0.90309 | 1.7824 | 2.1389 | 2.1389 | 2.1389 | 2.1389 | 0.54364 | 0.63239 | 0.63239 | 0.63239 | 0.63239 | 0.63239
2020-12-09 06:00 | Summer | 1.2956 | 1.8542 | 2.6756 | 2.6756 | 2.6756 | 2.6756 | 0.54299 | 0.88854 | 1.2176 | 1.4644 | 1.4644 | 1.4644 | 1.7909 | 2.3112 | 2.652 | 2.8314 | 3.1902 | 3.549 | 0.81545 | 1.6094 | 1.9313 | 1.9313 | 1.9313 | 1.9313 | 0.68525 | 0.79713 | 0.79713 | 0.79713 | 0.79713 | 0.79713
2020-12-09 07:00 | Summer | 1.7338 | 2.4813 | 3.5806 | 3.5806 | 3.5806 | 3.5806 | 0.68875 | 1.127 | 1.5445 | 1.8575 | 1.8575 | 1.8575 | 2.1394 | 2.7608 | 3.168 | 3.3823 | 3.8109 | 4.2394 | 0.94882 | 1.8727 | 2.2472 | 2.2472 | 2.2472 | 2.2472 | 0.97546 | 1.1347 | 1.1347 | 1.1347 | 1.1347 | 1.1347
2020-12-09 08:00 | Summer | 2.2673 | 3.2448 | 4.6824 | 4.6824 | 4.6824 | 4.6824 | 0.81735 | 1.3375 | 1.8328 | 2.2044 | 2.2044 | 2.2044 | 2.3816 | 3.0734 | 3.5266 | 3.7652 | 4.2423 | 4.7194 | 1.025 | 2.0231 | 2.4277 | 2.4277 | 2.4277 | 2.4277 | 1.2194 | 1.4184 | 1.4184 | 1.4184 | 1.4184 | 1.4184
2020-12-09 09:00 | Summer | 2.3981 | 3.4321 | 4.9526 | 4.9526 | 4.9526 | 4.9526 | 0.79449 | 1.3001 | 1.7816 | 2.1427 | 2.1427 | 2.1427 | 2.5149 | 3.2455 | 3.7241 | 3.976 | 4.4798 | 4.9836 | 1.0022 | 1.978 | 2.3735 | 2.3735 | 2.3735 | 2.3735 | 1.2765 | 1.4849 | 1.4849 | 1.4849 | 1.4849 | 1.4849
2020-12-09 10:00 | Summer | 2.4959 | 3.572 | 5.1545 | 5.1545 | 5.1545 | 5.1545 | 0.87737 | 1.4357 | 1.9674 | 2.3662 | 2.3662 | 2.3662 | 2.6674 | 3.4422 | 3.9498 | 4.217 | 4.7513 | 5.2857 | 0.9793 | 1.9328 | 2.3194 | 2.3194 | 2.3194 | 2.3194 | 1.3527 | 1.5736 | 1.5736 | 1.5736 | 1.5736 | 1.5736
2020-12-09 11:00 | Summer | 2.4387 | 3.4902 | 5.0365 | 5.0365 | 5.0365 | 5.0365 | 0.84021 | 1.3749 | 1.8841 | 2.266 | 2.266 | 2.266 | 2.7626 | 3.5651 | 4.0909 | 4.3676 | 4.921 | 5.4745 | 0.96787 | 1.9103 | 2.2923 | 2.2923 | 2.2923 | 2.2923 | 1.3718 | 1.5957 | 1.5957 | 1.5957 | 1.5957 | 1.5957
2020-12-09 12:00 | Summer | 2.4959 | 3.572 | 5.1545 | 5.1545 | 5.1545 | 5.1545 | 0.96882 | 1.5853 | 2.1725 | 2.6129 | 2.6129 | 2.6129 | 2.7626 | 3.5651 | 4.0909 | 4.3676 | 4.921 | 5.4745 | 1.0212 | 2.0156 | 2.4187 | 2.4187 | 2.4187 | 2.4187 | 1.3527 | 1.5736 | 1.5736 | 1.5736 | 1.5736 | 1.5736
2020-12-09 13:00 | Summer | 2.4959 | 3.572 | 5.1545 | 5.1545 | 5.1545 | 5.1545 | 1.1431 | 1.8706 | 2.5634 | 3.083 | 3.083 | 3.083 | 2.7817 | 3.5897 | 4.1191 | 4.3977 | 4.955 | 5.5122 | 1.1393 | 2.2487 | 2.6984 | 2.6984 | 2.6984 | 2.6984 | 1.3256 | 1.5421 | 1.5421 | 1.5421 | 1.5421 | 1.5421
2020-12-09 14:00 | Summer | 2.5911 | 3.7083 | 5.3513 | 5.3513 | 5.3513 | 5.3513 | 1.2232 | 2.0016 | 2.7429 | 3.2989 | 3.2989 | 3.2989 | 2.915 | 3.7618 | 4.3166 | 4.6086 | 5.1925 | 5.7765 | 1.0593 | 2.0908 | 2.5089 | 2.5089 | 2.5089 | 2.5089 | 1.3146 | 1.5293 | 1.5293 | 1.5293 | 1.5293 | 1.5293
2020-12-09 15:00 | Summer | 2.534 | 3.6265 | 5.2332 | 5.2332 | 5.2332 | 5.2332 | 1.1117 | 1.8192 | 2.4929 | 2.9983 | 2.9983 | 2.9983 | 2.8198 | 3.6389 | 4.1755 | 4.4579 | 5.0228 | 5.5877 | 1.2117 | 2.3916 | 2.8699 | 2.8699 | 2.8699 | 2.8699 | 1.2956 | 1.5071 | 1.5071 | 1.5071 | 1.5071 | 1.5071
2020-12-09 16:00 | Summer | 2.6483 | 3.7901 | 5.4693 | 5.4693 | 5.4693 | 5.4693 | 1.2203 | 1.9969 | 2.7365 | 3.2911 | 3.2911 | 3.2911 | 2.8769 | 3.7126 | 4.2601 | 4.5483 | 5.1246 | 5.701 | 1.2232 | 2.4142 | 2.897 | 2.897 | 2.897 | 2.897 | 1.2765 | 1.4849 | 1.4849 | 1.4849 | 1.4849 | 1.4849
2020-12-09 17:00 | Summer | 2.5201 | 3.6067 | 5.2046 | 5.2046 | 5.2046 | 5.2046 | 1.0774 | 1.763 | 2.416 | 2.9058 | 2.9058 | 2.9058 | 2.8057 | 3.6206 | 4.1546 | 4.4356 | 4.9977 | 5.5597 | 1.1432 | 2.2562 | 2.7075 | 2.7075 | 2.7075 | 2.7075 | 1.2194 | 1.4184 | 1.4184 | 1.4184 | 1.4184 | 1.4184
2020-12-09 18:00 | Summer | 1.8195 | 2.604 | 3.7577 | 3.7577 | 3.7577 | 3.7577 | 0.97168 | 1.59 | 2.1789 | 2.6206 | 2.6206 | 2.6206 | 2.5721 | 3.3192 | 3.8087 | 4.0664 | 4.5816 | 5.0969 | 1.0555 | 2.0832 | 2.4999 | 2.4999 | 2.4999 | 2.4999 | 0.85278 | 0.99201 | 0.99201 | 0.99201 | 0.99201 | 0.99201
2020-12-09 19:00 | Summer | 1.3146 | 1.8814 | 2.715 | 2.715 | 2.715 | 2.715 | 0.84593 | 1.3842 | 1.8969 | 2.2814 | 2.2814 | 2.2814 | 2.483 | 3.2042 | 3.6768 | 3.9255 | 4.4229 | 4.9203 | 1.0403 | 2.0532 | 2.4638 | 2.4638 | 2.4638 | 2.4638 | 0.70517 | 0.8203 | 0.8203 | 0.8203 | 0.8203 | 0.8203
2020-12-09 20:00 | Summer | 1.2575 | 1.7996 | 2.5969 | 2.5969 | 2.5969 | 2.5969 | 0.70589 | 1.1551 | 1.5829 | 1.9038 | 1.9038 | 1.9038 | 2.1529 | 2.7783 | 3.1881 | 3.4037 | 3.835 | 4.2663 | 0.96406 | 1.9027 | 2.2833 | 2.2833 | 2.2833 | 2.2833 | 0.59063 | 0.68706 | 0.68706 | 0.68706 | 0.68706 | 0.68706
2020-12-09 21:00 | Summer | 1.0669 | 1.527 | 2.2035 | 2.2035 | 2.2035 | 2.2035 | 0.82021 | 1.3422 | 1.8393 | 2.2121 | 2.2121 | 2.2121 | 2.0767 | 2.68 | 3.0752 | 3.2832 | 3.6992 | 4.1153 | 0.88785 | 1.7523 | 2.1028 | 2.1028 | 2.1028 | 2.1028 | 0.53347 | 0.62057 | 0.62057 | 0.62057 | 0.62057 | 0.62057
2020-12-09 22:00 | Summer | 1.0102 | 1.4457 | 2.0862 | 2.0862 | 2.0862 | 2.0862 | 0.54871 | 0.89789 | 1.2304 | 1.4799 | 1.4799 | 1.4799 | 1.9053 | 2.4587 | 2.8213 | 3.0121 | 3.3938 | 3.7755 | 0.82688 | 1.632 | 1.9584 | 1.9584 | 1.9584 | 1.9584 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-12-09 23:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.48012 | 0.78565 | 1.0766 | 1.2949 | 1.2949 | 1.2949 | 1.7338 | 2.2374 | 2.5674 | 2.741 | 3.0884 | 3.4357 | 0.80021 | 1.5794 | 1.8952 | 1.8952 | 1.8952 | 1.8952 | 0.47626 | 0.55401 | 0.55401 | 0.55401 | 0.55401 | 0.55401
2020-12-10 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.39153 | 0.64068 | 0.87797 | 1.0559 | 1.0559 | 1.0559 | 1.6385 | 2.1145 | 2.4263 | 2.5904 | 2.9187 | 3.2469 | 0.73162 | 1.444 | 1.7328 | 1.7328 | 1.7328 | 1.7328 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-12-10 01:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.35152 | 0.57521 | 0.78825 | 0.94803 | 0.94803 | 0.94803 | 1.5623 | 2.0161 | 2.3135 | 2.4699 | 2.7829 | 3.0959 | 0.65922 | 1.3011 | 1.5613 | 1.5613 | 1.5613 | 1.5613 | 0.43883 | 0.51047 | 0.51047 | 0.51047 | 0.51047 | 0.51047
2020-12-10 02:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.36581 | 0.59859 | 0.82029 | 0.98657 | 0.98657 | 0.98657 | 1.5052 | 1.9424 | 2.2288 | 2.3796 | 2.6811 | 2.9826 | 0.67446 | 1.3312 | 1.5974 | 1.5974 | 1.5974 | 1.5974 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-12-10 03:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.31436 | 0.51441 | 0.70494 | 0.84783 | 0.84783 | 0.84783 | 1.5239 | 1.9666 | 2.2566 | 2.4092 | 2.7145 | 3.0198 | 0.64707 | 1.2771 | 1.5325 | 1.5325 | 1.5325 | 1.5325 | 0.41345 | 0.48095 | 0.48095 | 0.48095 | 0.48095 | 0.48095
2020-12-10 04:00 | Summer | 1.0608 | 1.5182 | 2.1908 | 2.1908 | 2.1908 | 2.1908 | 0.41725 | 0.68277 | 0.93565 | 1.1253 | 1.1253 | 1.1253 | 1.5377 | 1.9844 | 2.277 | 2.431 | 2.7391 | 3.0471 | 0.64779 | 1.2785 | 1.5342 | 1.5342 | 1.5342 | 1.5342 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-12-10 05:00 | Summer | 1.105 | 1.5815 | 2.2822 | 2.2822 | 2.2822 | 2.2822 | 0.5287 | 0.86515 | 1.1856 | 1.4259 | 1.4259 | 1.4259 | 1.6195 | 2.0899 | 2.3981 | 2.5603 | 2.8847 | 3.2092 | 0.76591 | 1.5117 | 1.814 | 1.814 | 1.814 | 1.814 | 0.57264 | 0.66614 | 0.66614 | 0.66614 | 0.66614 | 0.66614
2020-12-10 06:00 | Summer | 1.2956 | 1.8542 | 2.6756 | 2.6756 | 2.6756 | 2.6756 | 0.63159 | 1.0335 | 1.4163 | 1.7034 | 1.7034 | 1.7034 | 1.7966 | 2.3185 | 2.6604 | 2.8404 | 3.2003 | 3.5602 | 0.81164 | 1.6019 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 0.74305 | 0.86436 | 0.86436 | 0.86436 | 0.86436 | 0.86436
2020-12-10 07:00 | Summer | 2.0134 | 2.8815 | 4.1581 | 4.1581 | 4.1581 | 4.1581 | 0.66874 | 1.0943 | 1.4996 | 1.8036 | 1.8036 | 1.8036 | 2.2482 | 2.9013 | 3.3291 | 3.5543 | 4.0047 | 4.4551 | 1.0941 | 2.1594 | 2.5913 | 2.5913 | 2.5913 | 2.5913 | 1.0288 | 1.1968 | 1.1968 | 1.1968 | 1.1968 | 1.1968
2020-12-10 08:00 | Summer | 2.6312 | 3.7657 | 5.4341 | 5.4341 | 5.4341 | 5.4341 | 0.85736 | 1.403 | 1.9226 | 2.3123 | 2.3123 | 2.3123 | 2.5926 | 3.3457 | 3.8391 | 4.0988 | 4.6181 | 5.1375 | 1.0593 | 2.0908 | 2.5089 | 2.5089 | 2.5089 | 2.5089 | 1.2765 | 1.4849 | 1.4849 | 1.4849 | 1.4849 | 1.4849
2020-12-10 09:00 | Summer | 2.6483 | 3.7901 | 5.4693 | 5.4693 | 5.4693 | 5.4693 | 0.94024 | 1.5386 | 2.1084 | 2.5358 | 2.5358 | 2.5358 | 2.7055 | 3.4913 | 4.0062 | 4.2772 | 4.8192 | 5.3612 | 0.99835 | 1.9704 | 2.3645 | 2.3645 | 2.3645 | 2.3645 | 1.3527 | 1.5736 | 1.5736 | 1.5736 | 1.5736 | 1.5736
2020-12-10 10:00 | Summer | 2.7817 | 3.981 | 5.7448 | 5.7448 | 5.7448 | 5.7448 | 1.0145 | 1.6602 | 2.275 | 2.7362 | 2.7362 | 2.7362 | 2.9013 | 3.7441 | 4.2963 | 4.5869 | 5.1681 | 5.7494 | 1.0746 | 2.1208 | 2.545 | 2.545 | 2.545 | 2.545 | 1.4289 | 1.6622 | 1.6622 | 1.6622 | 1.6622 | 1.6622
2020-12-10 11:00 | Summer | 2.8007 | 4.0083 | 5.7841 | 5.7841 | 5.7841 | 5.7841 | 1.1574 | 1.894 | 2.5955 | 3.1216 | 3.1216 | 3.1216 | 3.1437 | 4.0568 | 4.6551 | 4.97 | 5.5998 | 6.2296 | 1.0517 | 2.0757 | 2.4909 | 2.4909 | 2.4909 | 2.4909 | 1.5052 | 1.7509 | 1.7509 | 1.7509 | 1.7509 | 1.7509
2020-12-10 12:00 | Summer | 2.8198 | 4.0356 | 5.8235 | 5.8235 | 5.8235 | 5.8235 | 1.1317 | 1.8519 | 2.5378 | 3.0522 | 3.0522 | 3.0522 | 3.1437 | 4.0568 | 4.6551 | 4.97 | 5.5998 | 6.2296 | 0.42108 | 0.83109 | 0.99731 | 0.99731 | 0.99731 | 0.99731 | 1.5623 | 1.8174 | 1.8174 | 1.8174 | 1.8174 | 1.8174
2020-12-10 13:00 | Summer | 2.7817 | 3.981 | 5.7448 | 5.7448 | 5.7448 | 5.7448 | 1.2289 | 2.0109 | 2.7557 | 3.3143 | 3.3143 | 3.3143 | 3.1246 | 4.0323 | 4.6269 | 4.9399 | 5.5658 | 6.1918 | 0.66782 | 1.3181 | 1.5817 | 1.5817 | 1.5817 | 1.5817 | 1.6195 | 1.8839 | 1.8839 | 1.8839 | 1.8839 | 1.8839
2020-12-10 14:00 | Summer | 2.7626 | 3.9538 | 5.7054 | 5.7054 | 5.7054 | 5.7054 | 1.066 | 1.7443 | 2.3904 | 2.8749 | 2.8749 | 2.8749 | 3.0573 | 3.9453 | 4.5272 | 4.8334 | 5.4459 | 6.0583 | 0.99073 | 1.9554 | 2.3465 | 2.3465 | 2.3465 | 2.3465 | 1.5052 | 1.7509 | 1.7509 | 1.7509 | 1.7509 | 1.7509
2020-12-10 15:00 | Summer | 2.6293 | 3.7629 | 5.43 | 5.43 | 5.43 | 5.43 | 1.206 | 1.9735 | 2.7044 | 3.2526 | 3.2526 | 3.2526 | 3.0484 | 3.9339 | 4.5141 | 4.8194 | 5.4301 | 6.0408 | 1.147 | 2.2637 | 2.7165 | 2.7165 | 2.7165 | 2.7165 | 1.4099 | 1.6401 | 1.6401 | 1.6401 | 1.6401 | 1.6401
2020-12-10 16:00 | Summer | 2.6483 | 3.7901 | 5.4693 | 5.4693 | 5.4693 | 5.4693 | 1.1603 | 1.8987 | 2.6019 | 3.1293 | 3.1293 | 3.1293 | 3.0304 | 3.9106 | 4.4873 | 4.7909 | 5.3979 | 6.005 | 1.1165 | 2.2036 | 2.6443 | 2.6443 | 2.6443 | 2.6443 | 1.4099 | 1.6401 | 1.6401 | 1.6401 | 1.6401 | 1.6401
2020-12-10 17:00 | Summer | 2.3048 | 3.2985 | 4.7599 | 4.7599 | 4.7599 | 4.7599 | 0.99168 | 1.6228 | 2.2238 | 2.6745 | 2.6745 | 2.6745 | 2.6138 | 3.373 | 3.8705 | 4.1323 | 4.6559 | 5.1795 | 1.1851 | 2.3389 | 2.8067 | 2.8067 | 2.8067 | 2.8067 | 1.2194 | 1.4184 | 1.4184 | 1.4184 | 1.4184 | 1.4184
2020-12-10 18:00 | Summer | 1.8675 | 2.6727 | 3.8569 | 3.8569 | 3.8569 | 3.8569 | 0.79449 | 1.3001 | 1.7816 | 2.1427 | 2.1427 | 2.1427 | 2.3625 | 3.0488 | 3.4984 | 3.735 | 4.2083 | 4.6816 | 0.96025 | 1.8952 | 2.2743 | 2.2743 | 2.2743 | 2.2743 | 0.86146 | 1.0021 | 1.0021 | 1.0021 | 1.0021 | 1.0021
2020-12-10 19:00 | Summer | 1.2194 | 1.7451 | 2.5183 | 2.5183 | 2.5183 | 2.5183 | 0.68017 | 1.113 | 1.5252 | 1.8344 | 1.8344 | 1.8344 | 2.1724 | 2.8035 | 3.2169 | 3.4345 | 3.8697 | 4.3049 | 0.92214 | 1.82 | 2.184 | 2.184 | 2.184 | 2.184 | 0.63348 | 0.7369 | 0.7369 | 0.7369 | 0.7369 | 0.7369
2020-12-10 20:00 | Summer | 1.1055 | 1.5821 | 2.283 | 2.283 | 2.283 | 2.283 | 0.68017 | 1.113 | 1.5252 | 1.8344 | 1.8344 | 1.8344 | 2.0196 | 2.6062 | 2.9906 | 3.1929 | 3.5974 | 4.002 | 0.94119 | 1.8576 | 2.2291 | 2.2291 | 2.2291 | 2.2291 | 0.59063 | 0.68706 | 0.68706 | 0.68706 | 0.68706 | 0.68706
2020-12-10 21:00 | Summer | 1.0669 | 1.527 | 2.2035 | 2.2035 | 2.2035 | 2.2035 | 0.63445 | 1.0382 | 1.4227 | 1.7111 | 1.7111 | 1.7111 | 1.938 | 2.501 | 2.8698 | 3.0639 | 3.4522 | 3.8404 | 0.95263 | 1.8802 | 2.2562 | 2.2562 | 2.2562 | 2.2562 | 0.55252 | 0.64273 | 0.64273 | 0.64273 | 0.64273 | 0.64273
2020-12-10 22:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.60015 | 0.98207 | 1.3458 | 1.6186 | 1.6186 | 1.6186 | 1.829 | 2.3603 | 2.7084 | 2.8916 | 3.2581 | 3.6245 | 0.88785 | 1.7523 | 2.1028 | 2.1028 | 2.1028 | 2.1028 | 0.49557 | 0.57648 | 0.57648 | 0.57648 | 0.57648 | 0.57648
2020-12-10 23:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.50298 | 0.82306 | 1.1279 | 1.3565 | 1.3565 | 1.3565 | 1.6957 | 2.1882 | 2.5109 | 2.6808 | 3.0205 | 3.3602 | 0.82688 | 1.632 | 1.9584 | 1.9584 | 1.9584 | 1.9584 | 0.46372 | 0.53943 | 0.53943 | 0.53943 | 0.53943 | 0.53943
2020-12-11 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.36866 | 0.60327 | 0.8267 | 0.99427 | 0.99427 | 0.99427 | 1.5814 | 2.0407 | 2.3417 | 2.5001 | 2.8169 | 3.1337 | 0.89928 | 1.7749 | 2.1299 | 2.1299 | 2.1299 | 2.1299 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-12-11 01:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.42582 | 0.6968 | 0.95487 | 1.1484 | 1.1484 | 1.1484 | 1.5623 | 2.0161 | 2.3135 | 2.4699 | 2.7829 | 3.0959 | 0.64779 | 1.2785 | 1.5342 | 1.5342 | 1.5342 | 1.5342 | 0.4194 | 0.48787 | 0.48787 | 0.48787 | 0.48787 | 0.48787
2020-12-11 02:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.41439 | 0.67809 | 0.92924 | 1.1176 | 1.1176 | 1.1176 | 1.5052 | 1.9424 | 2.2288 | 2.3796 | 2.6811 | 2.9826 | 0.66684 | 1.3161 | 1.5794 | 1.5794 | 1.5794 | 1.5794 | 0.43821 | 0.50975 | 0.50975 | 0.50975 | 0.50975 | 0.50975
2020-12-11 03:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.35152 | 0.57521 | 0.78825 | 0.94803 | 0.94803 | 0.94803 | 1.4861 | 1.9178 | 2.2006 | 2.3495 | 2.6472 | 2.9449 | 0.6516 | 1.286 | 1.5433 | 1.5433 | 1.5433 | 1.5433 | 0.43821 | 0.50975 | 0.50975 | 0.50975 | 0.50975 | 0.50975
2020-12-11 04:00 | Summer | 1.0799 | 1.5456 | 2.2303 | 2.2303 | 2.2303 | 2.2303 | 0.43725 | 0.7155 | 0.98051 | 1.1793 | 1.1793 | 1.1793 | 1.5487 | 1.9986 | 2.2933 | 2.4485 | 2.7587 | 3.069 | 0.64397 | 1.271 | 1.5252 | 1.5252 | 1.5252 | 1.5252 | 0.55252 | 0.64273 | 0.64273 | 0.64273 | 0.64273 | 0.64273
2020-12-11 05:00 | Summer | 1.2003 | 1.7178 | 2.4789 | 2.4789 | 2.4789 | 2.4789 | 0.46869 | 0.76695 | 1.051 | 1.264 | 1.264 | 1.264 | 1.627 | 2.0997 | 2.4093 | 2.5723 | 2.8982 | 3.2242 | 0.65922 | 1.3011 | 1.5613 | 1.5613 | 1.5613 | 1.5613 | 0.53347 | 0.62057 | 0.62057 | 0.62057 | 0.62057 | 0.62057
2020-12-11 06:00 | Summer | 1.2519 | 1.7917 | 2.5854 | 2.5854 | 2.5854 | 2.5854 | 0.57729 | 0.94465 | 1.2945 | 1.5569 | 1.5569 | 1.5569 | 1.8002 | 2.3231 | 2.6657 | 2.846 | 3.2066 | 3.5673 | 0.82027 | 1.619 | 1.9428 | 1.9428 | 1.9428 | 1.9428 | 0.70734 | 0.82282 | 0.82282 | 0.82282 | 0.82282 | 0.82282
2020-12-11 07:00 | Summer | 1.7719 | 2.5359 | 3.6593 | 3.6593 | 3.6593 | 3.6593 | 0.74967 | 1.2267 | 1.6811 | 2.0218 | 2.0218 | 2.0218 | 2.1339 | 2.7537 | 3.1598 | 3.3736 | 3.8011 | 4.2285 | 0.98692 | 1.9479 | 2.3374 | 2.3374 | 2.3374 | 2.3374 | 0.87642 | 1.0195 | 1.0195 | 1.0195 | 1.0195 | 1.0195
2020-12-11 08:00 | Summer | 2.0958 | 2.9994 | 4.3282 | 4.3282 | 4.3282 | 4.3282 | 0.78741 | 1.2885 | 1.7657 | 2.1236 | 2.1236 | 2.1236 | 2.3054 | 2.975 | 3.4138 | 3.6447 | 4.1065 | 4.5683 | 1.0593 | 2.0908 | 2.5089 | 2.5089 | 2.5089 | 2.5089 | 1.1432 | 1.3298 | 1.3298 | 1.3298 | 1.3298 | 1.3298
2020-12-11 09:00 | Summer | 2.1529 | 3.0812 | 4.4463 | 4.4463 | 4.4463 | 4.4463 | 0.8345 | 1.3655 | 1.8713 | 2.2506 | 2.2506 | 2.2506 | 2.4387 | 3.1471 | 3.6112 | 3.8555 | 4.3441 | 4.8326 | 0.99835 | 1.9704 | 2.3645 | 2.3645 | 2.3645 | 2.3645 | 1.1622 | 1.352 | 1.352 | 1.352 | 1.352 | 1.352
2020-12-11 10:00 | Summer | 2.0767 | 2.9721 | 4.2889 | 4.2889 | 4.2889 | 4.2889 | 0.80878 | 1.3235 | 1.8136 | 2.1812 | 2.1812 | 2.1812 | 2.4768 | 3.1963 | 3.6677 | 3.9158 | 4.4119 | 4.9081 | 1.0746 | 2.1208 | 2.545 | 2.545 | 2.545 | 2.545 | 1.2956 | 1.5071 | 1.5071 | 1.5071 | 1.5071 | 1.5071
2020-12-11 11:00 | Summer | 2.0767 | 2.9721 | 4.2889 | 4.2889 | 4.2889 | 4.2889 | 0.85736 | 1.403 | 1.9226 | 2.3123 | 2.3123 | 2.3123 | 2.6293 | 3.393 | 3.8934 | 4.1567 | 4.6835 | 5.2102 | 1.0517 | 2.0757 | 2.4909 | 2.4909 | 2.4909 | 2.4909 | 1.2765 | 1.4849 | 1.4849 | 1.4849 | 1.4849 | 1.4849
2020-12-11 12:00 | Summer | 2.2482 | 3.2175 | 4.643 | 4.643 | 4.643 | 4.643 | 0.89166 | 1.4591 | 1.9995 | 2.4048 | 2.4048 | 2.4048 | 2.6155 | 3.3753 | 3.8731 | 4.1351 | 4.659 | 5.183 | 1.0784 | 2.1284 | 2.554 | 2.554 | 2.554 | 2.554 | 1.2765 | 1.4849 | 1.4849 | 1.4849 | 1.4849 | 1.4849
2020-12-11 13:00 | Summer | 2.2482 | 3.2175 | 4.643 | 4.643 | 4.643 | 4.643 | 0.99168 | 1.6228 | 2.2238 | 2.6745 | 2.6745 | 2.6745 | 2.534 | 3.2701 | 3.7523 | 4.0061 | 4.5138 | 5.0214 | 1.0098 | 1.993 | 2.3916 | 2.3916 | 2.3916 | 2.3916 | 1.2575 | 1.4628 | 1.4628 | 1.4628 | 1.4628 | 1.4628
2020-12-11 14:00 | Summer | 2.2291 | 3.1903 | 4.6037 | 4.6037 | 4.6037 | 4.6037 | 0.96882 | 1.5853 | 2.1725 | 2.6129 | 2.6129 | 2.6129 | 2.5746 | 3.3225 | 3.8125 | 4.0704 | 4.5862 | 5.1019 | 0.98692 | 1.9479 | 2.3374 | 2.3374 | 2.3374 | 2.3374 | 1.2194 | 1.4184 | 1.4184 | 1.4184 | 1.4184 | 1.4184
2020-12-11 15:00 | Summer | 2.4006 | 3.4357 | 4.9578 | 4.9578 | 4.9578 | 4.9578 | 0.9974 | 1.6321 | 2.2366 | 2.69 | 2.69 | 2.69 | 2.7055 | 3.4913 | 4.0062 | 4.2772 | 4.8192 | 5.3612 | 1.0174 | 2.008 | 2.4096 | 2.4096 | 2.4096 | 2.4096 | 1.2765 | 1.4849 | 1.4849 | 1.4849 | 1.4849 | 1.4849
2020-12-11 16:00 | Summer | 2.3054 | 3.2993 | 4.7611 | 4.7611 | 4.7611 | 4.7611 | 0.92023 | 1.5058 | 2.0636 | 2.4818 | 2.4818 | 2.4818 | 2.5911 | 3.3438 | 3.8369 | 4.0965 | 4.6156 | 5.1347 | 1.0212 | 2.0156 | 2.4187 | 2.4187 | 2.4187 | 2.4187 | 1.2384 | 1.4406 | 1.4406 | 1.4406 | 1.4406 | 1.4406
2020-12-11 17:00 | Summer | 2.153 | 3.0813 | 4.4464 | 4.4464 | 4.4464 | 4.4464 | 0.95167 | 1.5573 | 2.1341 | 2.5666 | 2.5666 | 2.5666 | 2.5721 | 3.3192 | 3.8087 | 4.0664 | 4.5816 | 5.0969 | 1.1241 | 2.2186 | 2.6623 | 2.6623 | 2.6623 | 2.6623 | 1.2194 | 1.4184 | 1.4184 | 1.4184 | 1.4184 | 1.4184
2020-12-11 18:00 | Summer | 1.5689 | 2.2453 | 3.2401 | 3.2401 | 3.2401 | 3.2401 | 0.83736 | 1.3702 | 1.8777 | 2.2583 | 2.2583 | 2.2583 | 2.3435 | 3.0242 | 3.4702 | 3.7049 | 4.1744 | 4.6438 | 1.006 | 1.9855 | 2.3826 | 2.3826 | 2.3826 | 2.3826 | 0.87674 | 1.0199 | 1.0199 | 1.0199 | 1.0199 | 1.0199
2020-12-11 19:00 | Summer | 1.1242 | 1.6089 | 2.3217 | 2.3217 | 2.3217 | 2.3217 | 0.76877 | 1.258 | 1.7239 | 2.0733 | 2.0733 | 2.0733 | 2.1129 | 2.7266 | 3.1287 | 3.3403 | 3.7636 | 4.1869 | 0.92976 | 1.8351 | 2.2021 | 2.2021 | 2.2021 | 2.2021 | 0.70494 | 0.82004 | 0.82004 | 0.82004 | 0.82004 | 0.82004
2020-12-11 20:00 | Summer | 1.0479 | 1.4997 | 2.1641 | 2.1641 | 2.1641 | 2.1641 | 0.67731 | 1.1083 | 1.5188 | 1.8267 | 1.8267 | 1.8267 | 2.0005 | 2.5816 | 2.9624 | 3.1627 | 3.5635 | 3.9643 | 0.88023 | 1.7373 | 2.0847 | 2.0847 | 2.0847 | 2.0847 | 0.66684 | 0.77571 | 0.77571 | 0.77571 | 0.77571 | 0.77571
2020-12-11 21:00 | Summer | 1.0288 | 1.4724 | 2.1248 | 2.1248 | 2.1248 | 2.1248 | 0.66588 | 1.0896 | 1.4932 | 1.7959 | 1.7959 | 1.7959 | 1.9815 | 2.557 | 2.9341 | 3.1326 | 3.5296 | 3.9265 | 0.88023 | 1.7373 | 2.0847 | 2.0847 | 2.0847 | 2.0847 | 0.59081 | 0.68727 | 0.68727 | 0.68727 | 0.68727 | 0.68727
2020-12-11 22:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.56014 | 0.9166 | 1.2561 | 1.5107 | 1.5107 | 1.5107 | 1.9243 | 2.4833 | 2.8495 | 3.0422 | 3.4277 | 3.8132 | 0.89928 | 1.7749 | 2.1299 | 2.1299 | 2.1299 | 2.1299 | 0.55252 | 0.64273 | 0.64273 | 0.64273 | 0.64273 | 0.64273
2020-12-11 23:00 | Summer | 0.93397 | 1.3367 | 1.9289 | 1.9289 | 1.9289 | 1.9289 | 0.52013 | 0.85112 | 1.1664 | 1.4028 | 1.4028 | 1.4028 | 1.7719 | 2.2866 | 2.6238 | 2.8013 | 3.1562 | 3.5112 | 0.81164 | 1.6019 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-12-12 | Summer | 0.91452 | 1.3088 | 1.8887 | 1.8887 | 1.8887 | 1.8887 | 0.45154 | 0.73889 | 1.0125 | 1.2178 | 1.2178 | 1.2178 | 1.6385 | 2.1145 | 2.4263 | 2.5904 | 2.9187 | 3.2469 | 0.96406 | 1.9027 | 2.2833 | 2.2833 | 2.2833 | 2.2833 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-12-12 01:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.41439 | 0.67809 | 0.92924 | 1.1176 | 1.1176 | 1.1176 | 1.5623 | 2.0161 | 2.3135 | 2.4699 | 2.7829 | 3.0959 | 0.64016 | 1.2635 | 1.5162 | 1.5162 | 1.5162 | 1.5162 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-12-12 02:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.43154 | 0.70615 | 0.96769 | 1.1638 | 1.1638 | 1.1638 | 1.6004 | 2.0653 | 2.3699 | 2.5302 | 2.8508 | 3.1714 | 0.68589 | 1.3537 | 1.6245 | 1.6245 | 1.6245 | 1.6245 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-12-12 03:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.37058 | 0.6064 | 0.83099 | 0.99943 | 0.99943 | 0.99943 | 1.5433 | 1.9915 | 2.2852 | 2.4398 | 2.749 | 3.0581 | 0.67065 | 1.3236 | 1.5884 | 1.5884 | 1.5884 | 1.5884 | 0.43821 | 0.50975 | 0.50975 | 0.50975 | 0.50975 | 0.50975
2020-12-12 04:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.37438 | 0.61262 | 0.83952 | 1.0097 | 1.0097 | 1.0097 | 1.5814 | 2.0407 | 2.3417 | 2.5001 | 2.8169 | 3.1337 | 0.64016 | 1.2635 | 1.5162 | 1.5162 | 1.5162 | 1.5162 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-12-12 05:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.44297 | 0.72486 | 0.99332 | 1.1947 | 1.1947 | 1.1947 | 1.6576 | 2.1391 | 2.4545 | 2.6205 | 2.9526 | 3.2847 | 0.66303 | 1.3086 | 1.5703 | 1.5703 | 1.5703 | 1.5703 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-12-12 06:00 | Summer | 1.0288 | 1.4724 | 2.1248 | 2.1248 | 2.1248 | 2.1248 | 0.43439 | 0.71083 | 0.9741 | 1.1715 | 1.1715 | 1.1715 | 1.7147 | 2.2128 | 2.5392 | 2.7109 | 3.0544 | 3.3979 | 0.70494 | 1.3913 | 1.6696 | 1.6696 | 1.6696 | 1.6696 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-12-12 07:00 | Summer | 1.0209 | 1.461 | 2.1083 | 2.1083 | 2.1083 | 2.1083 | 0.47155 | 0.77162 | 1.0574 | 1.2717 | 1.2717 | 1.2717 | 1.821 | 2.3499 | 2.6964 | 2.8788 | 3.2436 | 3.6084 | 0.74686 | 1.4741 | 1.7689 | 1.7689 | 1.7689 | 1.7689 | 0.55252 | 0.64273 | 0.64273 | 0.64273 | 0.64273 | 0.64273
2020-12-12 08:00 | Summer | 1.1241 | 1.6088 | 2.3215 | 2.3215 | 2.3215 | 2.3215 | 0.44868 | 0.73421 | 1.0061 | 1.2101 | 1.2101 | 1.2101 | 2.0386 | 2.6308 | 3.0188 | 3.223 | 3.6314 | 4.0398 | 0.85355 | 1.6846 | 2.0216 | 2.0216 | 2.0216 | 2.0216 | 0.53335 | 0.62042 | 0.62042 | 0.62042 | 0.62042 | 0.62042
2020-12-12 09:00 | Summer | 1.086 | 1.5542 | 2.2428 | 2.2428 | 2.2428 | 2.2428 | 0.51442 | 0.84177 | 1.1535 | 1.3874 | 1.3874 | 1.3874 | 2.0196 | 2.6062 | 2.9906 | 3.1929 | 3.5974 | 4.002 | 0.80783 | 1.5944 | 1.9133 | 1.9133 | 1.9133 | 1.9133 | 0.60968 | 0.70922 | 0.70922 | 0.70922 | 0.70922 | 0.70922
2020-12-12 10:00 | Summer | 1.0479 | 1.4997 | 2.1641 | 2.1641 | 2.1641 | 2.1641 | 0.52585 | 0.86048 | 1.1792 | 1.4182 | 1.4182 | 1.4182 | 2.0577 | 2.6554 | 3.047 | 3.2531 | 3.6653 | 4.0775 | 0.81545 | 1.6094 | 1.9313 | 1.9313 | 1.9313 | 1.9313 | 0.62873 | 0.73138 | 0.73138 | 0.73138 | 0.73138 | 0.73138
2020-12-12 11:00 | Summer | 1.0479 | 1.4997 | 2.1641 | 2.1641 | 2.1641 | 2.1641 | 0.51727 | 0.84645 | 1.1599 | 1.3951 | 1.3951 | 1.3951 | 2.0767 | 2.68 | 3.0752 | 3.2832 | 3.6992 | 4.1153 | 0.8345 | 1.647 | 1.9764 | 1.9764 | 1.9764 | 1.9764 | 0.60968 | 0.70922 | 0.70922 | 0.70922 | 0.70922 | 0.70922
2020-12-12 12:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.65445 | 1.0709 | 1.4676 | 1.765 | 1.765 | 1.765 | 2.191 | 2.8275 | 3.2445 | 3.4639 | 3.9029 | 4.3418 | 0.82688 | 1.632 | 1.9584 | 1.9584 | 1.9584 | 1.9584 | 0.59063 | 0.68706 | 0.68706 | 0.68706 | 0.68706 | 0.68706
2020-12-12 13:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.71161 | 1.1645 | 1.5957 | 1.9192 | 1.9192 | 1.9192 | 2.1339 | 2.7537 | 3.1598 | 3.3736 | 3.8011 | 4.2285 | 0.8345 | 1.647 | 1.9764 | 1.9764 | 1.9764 | 1.9764 | 0.59063 | 0.68706 | 0.68706 | 0.68706 | 0.68706 | 0.68706
2020-12-12 14:00 | Summer | 1.0078 | 1.4424 | 2.0814 | 2.0814 | 2.0814 | 2.0814 | 0.73101 | 1.1962 | 1.6392 | 1.9715 | 1.9715 | 1.9715 | 2.1339 | 2.7537 | 3.1598 | 3.3736 | 3.8011 | 4.2285 | 0.79258 | 1.5643 | 1.8772 | 1.8772 | 1.8772 | 1.8772 | 0.57283 | 0.66635 | 0.66635 | 0.66635 | 0.66635 | 0.66635
2020-12-12 15:00 | Summer | 1.0479 | 1.4997 | 2.1641 | 2.1641 | 2.1641 | 2.1641 | 0.77448 | 1.2673 | 1.7367 | 2.0888 | 2.0888 | 2.0888 | 2.1339 | 2.7537 | 3.1598 | 3.3736 | 3.8011 | 4.2285 | 0.81926 | 1.617 | 1.9403 | 1.9403 | 1.9403 | 1.9403 | 0.55252 | 0.64273 | 0.64273 | 0.64273 | 0.64273 | 0.64273
2020-12-12 16:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.68017 | 1.113 | 1.5252 | 1.8344 | 1.8344 | 1.8344 | 2.0767 | 2.68 | 3.0752 | 3.2832 | 3.6992 | 4.1153 | 0.83069 | 1.6395 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.59063 | 0.68706 | 0.68706 | 0.68706 | 0.68706 | 0.68706
2020-12-12 17:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.69446 | 1.1364 | 1.5573 | 1.8729 | 1.8729 | 1.8729 | 2.0577 | 2.6554 | 3.047 | 3.2531 | 3.6653 | 4.0775 | 0.85736 | 1.6922 | 2.0306 | 2.0306 | 2.0306 | 2.0306 | 0.57158 | 0.6649 | 0.6649 | 0.6649 | 0.6649 | 0.6649
2020-12-12 18:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.71733 | 1.1738 | 1.6085 | 1.9346 | 1.9346 | 1.9346 | 1.9434 | 2.5079 | 2.8777 | 3.0724 | 3.4617 | 3.851 | 0.93738 | 1.8501 | 2.2201 | 2.2201 | 2.2201 | 2.2201 | 0.57158 | 0.6649 | 0.6649 | 0.6649 | 0.6649 | 0.6649
2020-12-12 19:00 | Summer | 0.95269 | 1.3634 | 1.9675 | 1.9675 | 1.9675 | 1.9675 | 0.6173 | 1.0101 | 1.3842 | 1.6648 | 1.6648 | 1.6648 | 1.9434 | 2.5079 | 2.8777 | 3.0724 | 3.4617 | 3.851 | 0.89547 | 1.7674 | 2.1208 | 2.1208 | 2.1208 | 2.1208 | 0.55252 | 0.64273 | 0.64273 | 0.64273 | 0.64273 | 0.64273
2020-12-12 20:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.61444 | 1.0054 | 1.3778 | 1.6571 | 1.6571 | 1.6571 | 1.9815 | 2.557 | 2.9341 | 3.1326 | 3.5296 | 3.9265 | 0.94119 | 1.8576 | 2.2291 | 2.2291 | 2.2291 | 2.2291 | 0.59063 | 0.68706 | 0.68706 | 0.68706 | 0.68706 | 0.68706
2020-12-12 21:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.52299 | 0.8558 | 1.1728 | 1.4105 | 1.4105 | 1.4105 | 1.977 | 2.5513 | 2.9275 | 3.1255 | 3.5216 | 3.9176 | 0.93738 | 1.8501 | 2.2201 | 2.2201 | 2.2201 | 2.2201 | 0.59063 | 0.68706 | 0.68706 | 0.68706 | 0.68706 | 0.68706
2020-12-12 22:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.43725 | 0.7155 | 0.98051 | 1.1793 | 1.1793 | 1.1793 | 1.9121 | 2.4675 | 2.8314 | 3.0229 | 3.406 | 3.789 | 0.85355 | 1.6846 | 2.0216 | 2.0216 | 2.0216 | 2.0216 | 0.51328 | 0.59708 | 0.59708 | 0.59708 | 0.59708 | 0.59708
2020-12-12 23:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.38009 | 0.62197 | 0.85233 | 1.0251 | 1.0251 | 1.0251 | 1.81 | 2.3358 | 2.6802 | 2.8615 | 3.2241 | 3.5867 | 0.79258 | 1.5643 | 1.8772 | 1.8772 | 1.8772 | 1.8772 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-12-13 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.32008 | 0.52377 | 0.71775 | 0.86324 | 0.86324 | 0.86324 | 1.6576 | 2.1391 | 2.4545 | 2.6205 | 2.9526 | 3.2847 | 0.72018 | 1.4214 | 1.7057 | 1.7057 | 1.7057 | 1.7057 | 0.47782 | 0.55583 | 0.55583 | 0.55583 | 0.55583 | 0.55583
2020-12-13 01:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.40296 | 0.65939 | 0.9036 | 1.0868 | 1.0868 | 1.0868 | 1.5814 | 2.0407 | 2.3417 | 2.5001 | 2.8169 | 3.1337 | 0.67446 | 1.3312 | 1.5974 | 1.5974 | 1.5974 | 1.5974 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-12-13 02:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.37724 | 0.6173 | 0.84593 | 1.0174 | 1.0174 | 1.0174 | 1.5623 | 2.0161 | 2.3135 | 2.4699 | 2.7829 | 3.0959 | 0.64016 | 1.2635 | 1.5162 | 1.5162 | 1.5162 | 1.5162 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-12-13 03:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.33723 | 0.55183 | 0.75621 | 0.90949 | 0.90949 | 0.90949 | 1.5242 | 1.967 | 2.257 | 2.4097 | 2.715 | 3.0204 | 0.6516 | 1.286 | 1.5433 | 1.5433 | 1.5433 | 1.5433 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-12-13 04:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.39724 | 0.65003 | 0.89079 | 1.0713 | 1.0713 | 1.0713 | 1.5665 | 2.0216 | 2.3197 | 2.4766 | 2.7904 | 3.1043 | 0.62111 | 1.2259 | 1.4711 | 1.4711 | 1.4711 | 1.4711 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-12-13 05:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.39153 | 0.64068 | 0.87797 | 1.0559 | 1.0559 | 1.0559 | 1.6004 | 2.0653 | 2.3699 | 2.5302 | 2.8508 | 3.1714 | 0.62111 | 1.2259 | 1.4711 | 1.4711 | 1.4711 | 1.4711 | 0.45754 | 0.53224 | 0.53224 | 0.53224 | 0.53224 | 0.53224
2020-12-13 06:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.44011 | 0.72018 | 0.98691 | 1.187 | 1.187 | 1.187 | 1.6195 | 2.0899 | 2.3981 | 2.5603 | 2.8847 | 3.2092 | 0.70494 | 1.3913 | 1.6696 | 1.6696 | 1.6696 | 1.6696 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-12-13 07:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.49727 | 0.81371 | 1.1151 | 1.3411 | 1.3411 | 1.3411 | 1.7998 | 2.3226 | 2.6652 | 2.8455 | 3.206 | 3.5666 | 0.77353 | 1.5267 | 1.832 | 1.832 | 1.832 | 1.832 | 0.444 | 0.51649 | 0.51649 | 0.51649 | 0.51649 | 0.51649
2020-12-13 08:00 | Summer | 1.0479 | 1.4997 | 2.1641 | 2.1641 | 2.1641 | 2.1641 | 0.52299 | 0.8558 | 1.1728 | 1.4105 | 1.4105 | 1.4105 | 1.9434 | 2.5079 | 2.8777 | 3.0724 | 3.4617 | 3.851 | 0.76972 | 1.5192 | 1.823 | 1.823 | 1.823 | 1.823 | 0.48631 | 0.5657 | 0.5657 | 0.5657 | 0.5657 | 0.5657
2020-12-13 09:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.53442 | 0.87451 | 1.1984 | 1.4413 | 1.4413 | 1.4413 | 2.0767 | 2.68 | 3.0752 | 3.2832 | 3.6992 | 4.1153 | 0.83069 | 1.6395 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.49761 | 0.57885 | 0.57885 | 0.57885 | 0.57885 | 0.57885
2020-12-13 10:00 | Summer | 1.0479 | 1.4997 | 2.1641 | 2.1641 | 2.1641 | 2.1641 | 0.48012 | 0.78565 | 1.0766 | 1.2949 | 1.2949 | 1.2949 | 2.0668 | 2.6672 | 3.0605 | 3.2676 | 3.6816 | 4.0957 | 0.99454 | 1.9629 | 2.3555 | 2.3555 | 2.3555 | 2.3555 | 0.53347 | 0.62057 | 0.62057 | 0.62057 | 0.62057 | 0.62057
2020-12-13 11:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.47726 | 0.78098 | 1.0702 | 1.2872 | 1.2872 | 1.2872 | 2.191 | 2.8275 | 3.2445 | 3.4639 | 3.9029 | 4.3418 | 0.80021 | 1.5794 | 1.8952 | 1.8952 | 1.8952 | 1.8952 | 0.54767 | 0.63709 | 0.63709 | 0.63709 | 0.63709 | 0.63709
2020-12-13 12:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.53728 | 0.87918 | 1.2048 | 1.449 | 1.449 | 1.449 | 2.1529 | 2.7783 | 3.1881 | 3.4037 | 3.835 | 4.2663 | 0.81545 | 1.6094 | 1.9313 | 1.9313 | 1.9313 | 1.9313 | 0.55252 | 0.64273 | 0.64273 | 0.64273 | 0.64273 | 0.64273
2020-12-13 13:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.50013 | 0.81839 | 1.1215 | 1.3488 | 1.3488 | 1.3488 | 2.172 | 2.8029 | 3.2163 | 3.4338 | 3.8689 | 4.3041 | 0.80021 | 1.5794 | 1.8952 | 1.8952 | 1.8952 | 1.8952 | 0.49049 | 0.57057 | 0.57057 | 0.57057 | 0.57057 | 0.57057
2020-12-13 14:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.55157 | 0.90257 | 1.2368 | 1.4876 | 1.4876 | 1.4876 | 2.191 | 2.8275 | 3.2445 | 3.4639 | 3.9029 | 4.3418 | 0.86117 | 1.6997 | 2.0396 | 2.0396 | 2.0396 | 2.0396 | 0.53347 | 0.62057 | 0.62057 | 0.62057 | 0.62057 | 0.62057
2020-12-13 15:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.58015 | 0.94933 | 1.3009 | 1.5646 | 1.5646 | 1.5646 | 2.2291 | 2.8767 | 3.3009 | 3.5242 | 3.9708 | 4.4173 | 0.75448 | 1.4891 | 1.7869 | 1.7869 | 1.7869 | 1.7869 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-12-13 16:00 | Summer | 1.0479 | 1.4997 | 2.1641 | 2.1641 | 2.1641 | 2.1641 | 0.58872 | 0.96336 | 1.3202 | 1.5878 | 1.5878 | 1.5878 | 2.191 | 2.8275 | 3.2445 | 3.4639 | 3.9029 | 4.3418 | 0.84593 | 1.6696 | 2.0035 | 2.0035 | 2.0035 | 2.0035 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-12-13 17:00 | Summer | 1.0479 | 1.4997 | 2.1641 | 2.1641 | 2.1641 | 2.1641 | 0.59729 | 0.97739 | 1.3394 | 1.6109 | 1.6109 | 1.6109 | 2.191 | 2.8275 | 3.2445 | 3.4639 | 3.9029 | 4.3418 | 0.84974 | 1.6771 | 2.0125 | 2.0125 | 2.0125 | 2.0125 | 0.53347 | 0.62057 | 0.62057 | 0.62057 | 0.62057 | 0.62057
2020-12-13 18:00 | Summer | 1.0288 | 1.4724 | 2.1248 | 2.1248 | 2.1248 | 2.1248 | 0.52585 | 0.86048 | 1.1792 | 1.4182 | 1.4182 | 1.4182 | 2.1148 | 2.7291 | 3.1316 | 3.3435 | 3.7671 | 4.1908 | 0.84212 | 1.6621 | 1.9945 | 1.9945 | 1.9945 | 1.9945 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-12-13 19:00 | Summer | 1.0288 | 1.4724 | 2.1248 | 2.1248 | 2.1248 | 2.1248 | 0.48298 | 0.79033 | 1.083 | 1.3026 | 1.3026 | 1.3026 | 2.0767 | 2.68 | 3.0752 | 3.2832 | 3.6992 | 4.1153 | 0.88404 | 1.7448 | 2.0938 | 2.0938 | 2.0938 | 2.0938 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-12-13 20:00 | Summer | 1.0288 | 1.4724 | 2.1248 | 2.1248 | 2.1248 | 2.1248 | 0.40867 | 0.66874 | 0.91642 | 1.1022 | 1.1022 | 1.1022 | 1.9243 | 2.4833 | 2.8495 | 3.0422 | 3.4277 | 3.8132 | 0.89547 | 1.7674 | 2.1208 | 2.1208 | 2.1208 | 2.1208 | 0.53347 | 0.62057 | 0.62057 | 0.62057 | 0.62057 | 0.62057
2020-12-13 21:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.40296 | 0.65939 | 0.9036 | 1.0868 | 1.0868 | 1.0868 | 1.9053 | 2.4587 | 2.8213 | 3.0121 | 3.3938 | 3.7755 | 0.81164 | 1.6019 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-12-13 22:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.36295 | 0.59391 | 0.81388 | 0.97886 | 0.97886 | 0.97886 | 1.8862 | 2.4341 | 2.7931 | 2.982 | 3.3599 | 3.7377 | 0.80021 | 1.5794 | 1.8952 | 1.8952 | 1.8952 | 1.8952 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-12-13 23:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.36866 | 0.60327 | 0.8267 | 0.99427 | 0.99427 | 0.99427 | 1.7338 | 2.2374 | 2.5674 | 2.741 | 3.0884 | 3.4357 | 0.68589 | 1.3537 | 1.6245 | 1.6245 | 1.6245 | 1.6245 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-12-14 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.42296 | 0.69212 | 0.94846 | 1.1407 | 1.1407 | 1.1407 | 1.6195 | 2.0899 | 2.3981 | 2.5603 | 2.8847 | 3.2092 | 0.65541 | 1.2936 | 1.5523 | 1.5523 | 1.5523 | 1.5523 | 0.43142 | 0.50186 | 0.50186 | 0.50186 | 0.50186 | 0.50186
2020-12-14 01:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.34866 | 0.57053 | 0.78184 | 0.94032 | 0.94032 | 0.94032 | 1.5814 | 2.0407 | 2.3417 | 2.5001 | 2.8169 | 3.1337 | 0.6516 | 1.286 | 1.5433 | 1.5433 | 1.5433 | 1.5433 | 0.43821 | 0.50975 | 0.50975 | 0.50975 | 0.50975 | 0.50975
2020-12-14 02:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.45726 | 0.74824 | 1.0254 | 1.2332 | 1.2332 | 1.2332 | 1.5242 | 1.967 | 2.257 | 2.4097 | 2.715 | 3.0204 | 0.60206 | 1.1883 | 1.4259 | 1.4259 | 1.4259 | 1.4259 | 0.49448 | 0.57522 | 0.57522 | 0.57522 | 0.57522 | 0.57522
2020-12-14 03:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.3549 | 0.58074 | 0.79583 | 0.95715 | 0.95715 | 0.95715 | 1.5433 | 1.9915 | 2.2852 | 2.4398 | 2.749 | 3.0581 | 0.5449 | 1.0755 | 1.2906 | 1.2906 | 1.2906 | 1.2906 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-12-14 04:00 | Summer | 1.1813 | 1.6906 | 2.4396 | 2.4396 | 2.4396 | 2.4396 | 0.49155 | 0.80436 | 1.1023 | 1.3257 | 1.3257 | 1.3257 | 1.5327 | 1.978 | 2.2697 | 2.4232 | 2.7303 | 3.0373 | 0.62111 | 1.2259 | 1.4711 | 1.4711 | 1.4711 | 1.4711 | 0.52873 | 0.61505 | 0.61505 | 0.61505 | 0.61505 | 0.61505
2020-12-14 05:00 | Summer | 1.2765 | 1.8269 | 2.6363 | 2.6363 | 2.6363 | 2.6363 | 0.40867 | 0.66874 | 0.91642 | 1.1022 | 1.1022 | 1.1022 | 1.6766 | 2.1636 | 2.4827 | 2.6507 | 2.9865 | 3.3224 | 0.74686 | 1.4741 | 1.7689 | 1.7689 | 1.7689 | 1.7689 | 0.59063 | 0.68706 | 0.68706 | 0.68706 | 0.68706 | 0.68706
2020-12-14 06:00 | Summer | 1.3515 | 1.9342 | 2.7911 | 2.7911 | 2.7911 | 2.7911 | 0.60301 | 0.98674 | 1.3522 | 1.6263 | 1.6263 | 1.6263 | 1.8273 | 2.3581 | 2.7058 | 2.8889 | 3.2549 | 3.621 | 0.75829 | 1.4966 | 1.796 | 1.796 | 1.796 | 1.796 | 0.76847 | 0.89393 | 0.89393 | 0.89393 | 0.89393 | 0.89393
2020-12-14 07:00 | Summer | 2.0076 | 2.8732 | 4.1461 | 4.1461 | 4.1461 | 4.1461 | 0.74305 | 1.2159 | 1.6662 | 2.004 | 2.004 | 2.004 | 2.1689 | 2.799 | 3.2117 | 3.429 | 3.8635 | 4.298 | 0.98311 | 1.9403 | 2.3284 | 2.3284 | 2.3284 | 2.3284 | 0.95263 | 1.1082 | 1.1082 | 1.1082 | 1.1082 | 1.1082
2020-12-14 08:00 | Summer | 2.3244 | 3.3266 | 4.8004 | 4.8004 | 4.8004 | 4.8004 | 0.72018 | 1.1785 | 1.615 | 1.9423 | 1.9423 | 1.9423 | 2.3816 | 3.0734 | 3.5266 | 3.7652 | 4.2423 | 4.7194 | 1.0174 | 2.008 | 2.4096 | 2.4096 | 2.4096 | 2.4096 | 1.2119 | 1.4097 | 1.4097 | 1.4097 | 1.4097 | 1.4097
2020-12-14 09:00 | Summer | 2.3435 | 3.3539 | 4.8398 | 4.8398 | 4.8398 | 4.8398 | 0.81164 | 1.3281 | 1.82 | 2.189 | 2.189 | 2.189 | 2.534 | 3.2701 | 3.7523 | 4.0061 | 4.5138 | 5.0214 | 0.98692 | 1.9479 | 2.3374 | 2.3374 | 2.3374 | 2.3374 | 1.2575 | 1.4628 | 1.4628 | 1.4628 | 1.4628 | 1.4628
2020-12-14 10:00 | Summer | 2.5911 | 3.7083 | 5.3513 | 5.3513 | 5.3513 | 5.3513 | 0.86879 | 1.4217 | 1.9482 | 2.3431 | 2.3431 | 2.3431 | 2.6483 | 3.4176 | 3.9216 | 4.1869 | 4.7174 | 5.2479 | 1.0708 | 2.1133 | 2.536 | 2.536 | 2.536 | 2.536 | 1.3337 | 1.5514 | 1.5514 | 1.5514 | 1.5514 | 1.5514
2020-12-14 11:00 | Summer | 2.6102 | 3.7356 | 5.3906 | 5.3906 | 5.3906 | 5.3906 | 0.86022 | 1.4076 | 1.929 | 2.32 | 2.32 | 2.32 | 2.81 | 3.6263 | 4.161 | 4.4425 | 5.0054 | 5.5684 | 1.0822 | 2.1359 | 2.5631 | 2.5631 | 2.5631 | 2.5631 | 1.448 | 1.6844 | 1.6844 | 1.6844 | 1.6844 | 1.6844
2020-12-14 12:00 | Summer | 2.7626 | 3.9538 | 5.7054 | 5.7054 | 5.7054 | 5.7054 | 0.94024 | 1.5386 | 2.1084 | 2.5358 | 2.5358 | 2.5358 | 2.8579 | 3.688 | 4.2319 | 4.5182 | 5.0907 | 5.6632 | 1.166 | 2.3013 | 2.7616 | 2.7616 | 2.7616 | 2.7616 | 1.467 | 1.7066 | 1.7066 | 1.7066 | 1.7066 | 1.7066
2020-12-14 13:00 | Summer | 2.7055 | 3.8719 | 5.5874 | 5.5874 | 5.5874 | 5.5874 | 1.0231 | 1.6742 | 2.2943 | 2.7593 | 2.7593 | 2.7593 | 2.8198 | 3.6389 | 4.1755 | 4.4579 | 5.0228 | 5.5877 | 1.166 | 2.3013 | 2.7616 | 2.7616 | 2.7616 | 2.7616 | 1.448 | 1.6844 | 1.6844 | 1.6844 | 1.6844 | 1.6844
2020-12-14 14:00 | Summer | 2.7245 | 3.8992 | 5.6267 | 5.6267 | 5.6267 | 5.6267 | 1.1974 | 1.9595 | 2.6852 | 3.2295 | 3.2295 | 3.2295 | 2.915 | 3.7618 | 4.3166 | 4.6086 | 5.1925 | 5.7765 | 1.0631 | 2.0983 | 2.5179 | 2.5179 | 2.5179 | 2.5179 | 1.448 | 1.6844 | 1.6844 | 1.6844 | 1.6844 | 1.6844
2020-12-14 15:00 | Summer | 2.6674 | 3.8174 | 5.5087 | 5.5087 | 5.5087 | 5.5087 | 1.1917 | 1.9501 | 2.6724 | 3.2141 | 3.2141 | 3.2141 | 2.8939 | 3.7346 | 4.2853 | 4.5752 | 5.1549 | 5.7347 | 1.0411 | 2.0548 | 2.4657 | 2.4657 | 2.4657 | 2.4657 | 1.4099 | 1.6401 | 1.6401 | 1.6401 | 1.6401 | 1.6401
2020-12-14 16:00 | Summer | 2.5911 | 3.7083 | 5.3513 | 5.3513 | 5.3513 | 5.3513 | 1.1489 | 1.88 | 2.5762 | 3.0985 | 3.0985 | 3.0985 | 2.915 | 3.7618 | 4.3166 | 4.6086 | 5.1925 | 5.7765 | 0.9793 | 1.9328 | 2.3194 | 2.3194 | 2.3194 | 2.3194 | 1.3527 | 1.5736 | 1.5736 | 1.5736 | 1.5736 | 1.5736
2020-12-14 17:00 | Summer | 2.4768 | 3.5447 | 5.1152 | 5.1152 | 5.1152 | 5.1152 | 1.1889 | 1.9454 | 2.666 | 3.2064 | 3.2064 | 3.2064 | 2.896 | 3.7372 | 4.2884 | 4.5784 | 5.1586 | 5.7387 | 0.94501 | 1.8651 | 2.2382 | 2.2382 | 2.2382 | 2.2382 | 1.2975 | 1.5093 | 1.5093 | 1.5093 | 1.5093 | 1.5093
2020-12-14 18:00 | Summer | 1.7983 | 2.5737 | 3.714 | 3.714 | 3.714 | 3.714 | 0.87737 | 1.4357 | 1.9674 | 2.3662 | 2.3662 | 2.3662 | 2.6752 | 3.4522 | 3.9614 | 4.2293 | 4.7652 | 5.3012 | 0.92214 | 1.82 | 2.184 | 2.184 | 2.184 | 2.184 | 0.89214 | 1.0378 | 1.0378 | 1.0378 | 1.0378 | 1.0378
2020-12-14 19:00 | Summer | 1.2575 | 1.7996 | 2.5969 | 2.5969 | 2.5969 | 2.5969 | 0.65159 | 1.0662 | 1.4611 | 1.7573 | 1.7573 | 1.7573 | 2.4768 | 3.1963 | 3.6677 | 3.9158 | 4.4119 | 4.9081 | 0.9793 | 1.9328 | 2.3194 | 2.3194 | 2.3194 | 2.3194 | 0.68612 | 0.79814 | 0.79814 | 0.79814 | 0.79814 | 0.79814
2020-12-14 20:00 | Summer | 1.2003 | 1.7178 | 2.4789 | 2.4789 | 2.4789 | 2.4789 | 0.62587 | 1.0242 | 1.4035 | 1.688 | 1.688 | 1.688 | 2.1529 | 2.7783 | 3.1881 | 3.4037 | 3.835 | 4.2663 | 0.93738 | 1.8501 | 2.2201 | 2.2201 | 2.2201 | 2.2201 | 0.60968 | 0.70922 | 0.70922 | 0.70922 | 0.70922 | 0.70922
2020-12-14 21:00 | Summer | 1.1432 | 1.636 | 2.3609 | 2.3609 | 2.3609 | 2.3609 | 0.58872 | 0.96336 | 1.3202 | 1.5878 | 1.5878 | 1.5878 | 2.0958 | 2.7046 | 3.1034 | 3.3133 | 3.7332 | 4.153 | 0.94501 | 1.8651 | 2.2382 | 2.2382 | 2.2382 | 2.2382 | 0.56074 | 0.65229 | 0.65229 | 0.65229 | 0.65229 | 0.65229
2020-12-14 22:00 | Summer | 1.086 | 1.5542 | 2.2428 | 2.2428 | 2.2428 | 2.2428 | 0.57443 | 0.93998 | 1.2881 | 1.5492 | 1.5492 | 1.5492 | 1.9815 | 2.557 | 2.9341 | 3.1326 | 3.5296 | 3.9265 | 0.85736 | 1.6922 | 2.0306 | 2.0306 | 2.0306 | 2.0306 | 0.57158 | 0.6649 | 0.6649 | 0.6649 | 0.6649 | 0.6649
2020-12-14 23:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.42296 | 0.69212 | 0.94846 | 1.1407 | 1.1407 | 1.1407 | 1.81 | 2.3358 | 2.6802 | 2.8615 | 3.2241 | 3.5867 | 0.73543 | 1.4515 | 1.7418 | 1.7418 | 1.7418 | 1.7418 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-12-15 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.45154 | 0.73889 | 1.0125 | 1.2178 | 1.2178 | 1.2178 | 1.7719 | 2.2866 | 2.6238 | 2.8013 | 3.1562 | 3.5112 | 0.73162 | 1.444 | 1.7328 | 1.7328 | 1.7328 | 1.7328 | 0.47651 | 0.5543 | 0.5543 | 0.5543 | 0.5543 | 0.5543
2020-12-15 01:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.41439 | 0.67809 | 0.92924 | 1.1176 | 1.1176 | 1.1176 | 1.6576 | 2.1391 | 2.4545 | 2.6205 | 2.9526 | 3.2847 | 0.6516 | 1.286 | 1.5433 | 1.5433 | 1.5433 | 1.5433 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-12-15 02:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.43154 | 0.70615 | 0.96769 | 1.1638 | 1.1638 | 1.1638 | 1.6576 | 2.1391 | 2.4545 | 2.6205 | 2.9526 | 3.2847 | 0.82307 | 1.6245 | 1.9494 | 1.9494 | 1.9494 | 1.9494 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-12-15 03:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.48298 | 0.79033 | 1.083 | 1.3026 | 1.3026 | 1.3026 | 1.6004 | 2.0653 | 2.3699 | 2.5302 | 2.8508 | 3.1714 | 0.62111 | 1.2259 | 1.4711 | 1.4711 | 1.4711 | 1.4711 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-12-15 04:00 | Summer | 1.1045 | 1.5807 | 2.281 | 2.281 | 2.281 | 2.281 | 0.49727 | 0.81371 | 1.1151 | 1.3411 | 1.3411 | 1.3411 | 1.6004 | 2.0653 | 2.3699 | 2.5302 | 2.8508 | 3.1714 | 0.65922 | 1.3011 | 1.5613 | 1.5613 | 1.5613 | 1.5613 | 0.55188 | 0.64199 | 0.64199 | 0.64199 | 0.64199 | 0.64199
2020-12-15 05:00 | Summer | 1.161 | 1.6616 | 2.3978 | 2.3978 | 2.3978 | 2.3978 | 0.48012 | 0.78565 | 1.0766 | 1.2949 | 1.2949 | 1.2949 | 1.6576 | 2.1391 | 2.4545 | 2.6205 | 2.9526 | 3.2847 | 0.75009 | 1.4804 | 1.7765 | 1.7765 | 1.7765 | 1.7765 | 0.57299 | 0.66654 | 0.66654 | 0.66654 | 0.66654 | 0.66654
2020-12-15 06:00 | Summer | 1.3457 | 1.926 | 2.7792 | 2.7792 | 2.7792 | 2.7792 | 0.59158 | 0.96804 | 1.3266 | 1.5955 | 1.5955 | 1.5955 | 1.8026 | 2.3262 | 2.6693 | 2.8498 | 3.211 | 3.5721 | 0.81926 | 1.617 | 1.9403 | 1.9403 | 1.9403 | 1.9403 | 0.78562 | 0.91389 | 0.91389 | 0.91389 | 0.91389 | 0.91389
2020-12-15 07:00 | Summer | 2.0806 | 2.9777 | 4.297 | 4.297 | 4.297 | 4.297 | 0.64588 | 1.0569 | 1.4483 | 1.7419 | 1.7419 | 1.7419 | 2.1946 | 2.832 | 3.2497 | 3.4695 | 3.9091 | 4.3488 | 1.086 | 2.1434 | 2.5721 | 2.5721 | 2.5721 | 2.5721 | 1.0278 | 1.1956 | 1.1956 | 1.1956 | 1.1956 | 1.1956
2020-12-15 08:00 | Summer | 2.3789 | 3.4046 | 4.913 | 4.913 | 4.913 | 4.913 | 0.81735 | 1.3375 | 1.8328 | 2.2044 | 2.2044 | 2.2044 | 2.4578 | 3.1717 | 3.6395 | 3.8856 | 4.378 | 4.8704 | 1.1508 | 2.2713 | 2.7255 | 2.7255 | 2.7255 | 2.7255 | 1.2956 | 1.5071 | 1.5071 | 1.5071 | 1.5071 | 1.5071
2020-12-15 09:00 | Summer | 2.4578 | 3.5175 | 5.0759 | 5.0759 | 5.0759 | 5.0759 | 0.90595 | 1.4825 | 2.0315 | 2.4433 | 2.4433 | 2.4433 | 2.6864 | 3.4668 | 3.978 | 4.2471 | 4.7853 | 5.3234 | 1.1355 | 2.2412 | 2.6894 | 2.6894 | 2.6894 | 2.6894 | 1.3718 | 1.5957 | 1.5957 | 1.5957 | 1.5957 | 1.5957
2020-12-15 10:00 | Summer | 2.534 | 3.6265 | 5.2332 | 5.2332 | 5.2332 | 5.2332 | 0.9431 | 1.5433 | 2.1148 | 2.5435 | 2.5435 | 2.5435 | 2.7436 | 3.5405 | 4.0627 | 4.3375 | 4.8871 | 5.4367 | 1.0593 | 2.0908 | 2.5089 | 2.5089 | 2.5089 | 2.5089 | 1.4285 | 1.6617 | 1.6617 | 1.6617 | 1.6617 | 1.6617
2020-12-15 11:00 | Summer | 2.6864 | 3.8447 | 5.548 | 5.548 | 5.548 | 5.548 | 0.93167 | 1.5245 | 2.0892 | 2.5127 | 2.5127 | 2.5127 | 3.0484 | 3.9339 | 4.5141 | 4.8194 | 5.4301 | 6.0408 | 1.2194 | 2.4066 | 2.888 | 2.888 | 2.888 | 2.888 | 1.6004 | 1.8617 | 1.8617 | 1.8617 | 1.8617 | 1.8617
2020-12-15 12:00 | Summer | 2.8388 | 4.0628 | 5.8628 | 5.8628 | 5.8628 | 5.8628 | 1.1803 | 1.9314 | 2.6467 | 3.1832 | 3.1832 | 3.1832 | 3.1056 | 4.0077 | 4.5987 | 4.9098 | 5.5319 | 6.154 | 1.2079 | 2.3841 | 2.8609 | 2.8609 | 2.8609 | 2.8609 | 1.5623 | 1.8174 | 1.8174 | 1.8174 | 1.8174 | 1.8174
2020-12-15 13:00 | Summer | 2.8579 | 4.0901 | 5.9022 | 5.9022 | 5.9022 | 5.9022 | 1.1603 | 1.8987 | 2.6019 | 3.1293 | 3.1293 | 3.1293 | 3.3914 | 4.3765 | 5.0219 | 5.3616 | 6.041 | 6.7204 | 1.1965 | 2.3615 | 2.8338 | 2.8338 | 2.8338 | 2.8338 | 1.5623 | 1.8174 | 1.8174 | 1.8174 | 1.8174 | 1.8174
2020-12-15 14:00 | Summer | 2.9341 | 4.1992 | 6.0595 | 6.0595 | 6.0595 | 6.0595 | 1.2432 | 2.0343 | 2.7877 | 3.3528 | 3.3528 | 3.3528 | 3.3723 | 4.3519 | 4.9937 | 5.3315 | 6.007 | 6.6826 | 1.246 | 2.4593 | 2.9511 | 2.9511 | 2.9511 | 2.9511 | 1.5814 | 1.8395 | 1.8395 | 1.8395 | 1.8395 | 1.8395
2020-12-15 15:00 | Summer | 2.9531 | 4.2264 | 6.0989 | 6.0989 | 6.0989 | 6.0989 | 1.2918 | 2.1138 | 2.8967 | 3.4838 | 3.4838 | 3.4838 | 3.1626 | 4.0813 | 4.6832 | 5 | 5.6336 | 6.2671 | 1.2651 | 2.4969 | 2.9963 | 2.9963 | 2.9963 | 2.9963 | 1.5242 | 1.7731 | 1.7731 | 1.7731 | 1.7731 | 1.7731
2020-12-15 16:00 | Summer | 2.9341 | 4.1992 | 6.0595 | 6.0595 | 6.0595 | 6.0595 | 1.1746 | 1.9221 | 2.6339 | 3.1678 | 3.1678 | 3.1678 | 3.4295 | 4.4256 | 5.0783 | 5.4218 | 6.1088 | 6.7959 | 1.2498 | 2.4668 | 2.9602 | 2.9602 | 2.9602 | 2.9602 | 1.467 | 1.7066 | 1.7066 | 1.7066 | 1.7066 | 1.7066
2020-12-15 17:00 | Summer | 2.6508 | 3.7937 | 5.4744 | 5.4744 | 5.4744 | 5.4744 | 1.1974 | 1.9595 | 2.6852 | 3.2295 | 3.2295 | 3.2295 | 3.2303 | 4.1687 | 4.7834 | 5.107 | 5.7541 | 6.4012 | 1.1889 | 2.3465 | 2.8158 | 2.8158 | 2.8158 | 2.8158 | 1.3079 | 1.5215 | 1.5215 | 1.5215 | 1.5215 | 1.5215
2020-12-15 18:00 | Summer | 2.0958 | 2.9994 | 4.3282 | 4.3282 | 4.3282 | 4.3282 | 0.9631 | 1.576 | 2.1597 | 2.5975 | 2.5975 | 2.5975 | 2.9531 | 3.811 | 4.373 | 4.6688 | 5.2604 | 5.852 | 1.0669 | 2.1058 | 2.527 | 2.527 | 2.527 | 2.527 | 1.0065 | 1.1708 | 1.1708 | 1.1708 | 1.1708 | 1.1708
2020-12-15 19:00 | Summer | 1.3121 | 1.8778 | 2.7097 | 2.7097 | 2.7097 | 2.7097 | 0.78877 | 1.2907 | 1.7688 | 2.1273 | 2.1273 | 2.1273 | 2.6611 | 3.434 | 3.9405 | 4.207 | 4.7401 | 5.2732 | 1.0936 | 2.1585 | 2.5901 | 2.5901 | 2.5901 | 2.5901 | 0.68969 | 0.8023 | 0.8023 | 0.8023 | 0.8023 | 0.8023
2020-12-15 20:00 | Summer | 1.2575 | 1.7996 | 2.5969 | 2.5969 | 2.5969 | 2.5969 | 0.72304 | 1.1832 | 1.6214 | 1.95 | 1.95 | 1.95 | 2.5459 | 3.2854 | 3.7699 | 4.0249 | 4.5349 | 5.0449 | 1.0326 | 2.0381 | 2.4457 | 2.4457 | 2.4457 | 2.4457 | 0.60968 | 0.70922 | 0.70922 | 0.70922 | 0.70922 | 0.70922
2020-12-15 21:00 | Summer | 1.1863 | 1.6977 | 2.4499 | 2.4499 | 2.4499 | 2.4499 | 0.6916 | 1.1317 | 1.5509 | 1.8652 | 1.8652 | 1.8652 | 2.3054 | 2.975 | 3.4138 | 3.6447 | 4.1065 | 4.5683 | 1.0098 | 1.993 | 2.3916 | 2.3916 | 2.3916 | 2.3916 | 0.59063 | 0.68706 | 0.68706 | 0.68706 | 0.68706 | 0.68706
2020-12-15 22:00 | Summer | 1.1241 | 1.6088 | 2.3215 | 2.3215 | 2.3215 | 2.3215 | 0.63445 | 1.0382 | 1.4227 | 1.7111 | 1.7111 | 1.7111 | 2.2304 | 2.8783 | 3.3028 | 3.5262 | 3.973 | 4.4198 | 0.94882 | 1.8727 | 2.2472 | 2.2472 | 2.2472 | 2.2472 | 0.53347 | 0.62057 | 0.62057 | 0.62057 | 0.62057 | 0.62057
2020-12-15 23:00 | Summer | 1.0479 | 1.4997 | 2.1641 | 2.1641 | 2.1641 | 2.1641 | 0.56586 | 0.92595 | 1.2689 | 1.5261 | 1.5261 | 1.5261 | 1.9624 | 2.5325 | 2.9059 | 3.1025 | 3.4956 | 3.8887 | 0.81926 | 1.617 | 1.9403 | 1.9403 | 1.9403 | 1.9403 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-12-16 | Summer | 1.0479 | 1.4997 | 2.1641 | 2.1641 | 2.1641 | 2.1641 | 0.50584 | 0.82774 | 1.1343 | 1.3642 | 1.3642 | 1.3642 | 1.8672 | 2.4095 | 2.7649 | 2.9519 | 3.3259 | 3.7 | 0.80783 | 1.5944 | 1.9133 | 1.9133 | 1.9133 | 1.9133 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-12-16 01:00 | Summer | 1.0288 | 1.4724 | 2.1248 | 2.1248 | 2.1248 | 2.1248 | 0.44297 | 0.72486 | 0.99332 | 1.1947 | 1.1947 | 1.1947 | 1.7719 | 2.2866 | 2.6238 | 2.8013 | 3.1562 | 3.5112 | 0.77353 | 1.5267 | 1.832 | 1.832 | 1.832 | 1.832 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-12-16 02:00 | Summer | 1.0479 | 1.4997 | 2.1641 | 2.1641 | 2.1641 | 2.1641 | 0.50013 | 0.81839 | 1.1215 | 1.3488 | 1.3488 | 1.3488 | 1.7909 | 2.3112 | 2.652 | 2.8314 | 3.1902 | 3.549 | 0.74305 | 1.4665 | 1.7599 | 1.7599 | 1.7599 | 1.7599 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-12-16 03:00 | Summer | 1.0288 | 1.4724 | 2.1248 | 2.1248 | 2.1248 | 2.1248 | 0.47726 | 0.78098 | 1.0702 | 1.2872 | 1.2872 | 1.2872 | 1.7719 | 2.2866 | 2.6238 | 2.8013 | 3.1562 | 3.5112 | 0.724 | 1.4289 | 1.7147 | 1.7147 | 1.7147 | 1.7147 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-12-16 04:00 | Summer | 1.105 | 1.5815 | 2.2822 | 2.2822 | 2.2822 | 2.2822 | 0.47726 | 0.78098 | 1.0702 | 1.2872 | 1.2872 | 1.2872 | 1.7719 | 2.2866 | 2.6238 | 2.8013 | 3.1562 | 3.5112 | 0.73543 | 1.4515 | 1.7418 | 1.7418 | 1.7418 | 1.7418 | 0.57158 | 0.6649 | 0.6649 | 0.6649 | 0.6649 | 0.6649
2020-12-16 05:00 | Summer | 1.2194 | 1.7451 | 2.5183 | 2.5183 | 2.5183 | 2.5183 | 0.49441 | 0.80903 | 1.1087 | 1.3334 | 1.3334 | 1.3334 | 1.829 | 2.3603 | 2.7084 | 2.8916 | 3.2581 | 3.6245 | 0.77734 | 1.5342 | 1.8411 | 1.8411 | 1.8411 | 1.8411 | 0.61164 | 0.71149 | 0.71149 | 0.71149 | 0.71149 | 0.71149
2020-12-16 06:00 | Summer | 1.3001 | 1.8607 | 2.685 | 2.685 | 2.685 | 2.685 | 0.73447 | 1.2019 | 1.647 | 1.9808 | 1.9808 | 1.9808 | 2.0011 | 2.5824 | 2.9632 | 3.1636 | 3.5645 | 3.9654 | 0.98311 | 1.9403 | 2.3284 | 2.3284 | 2.3284 | 2.3284 | 0.74285 | 0.86413 | 0.86413 | 0.86413 | 0.86413 | 0.86413
2020-12-16 07:00 | Summer | 2.0554 | 2.9416 | 4.2449 | 4.2449 | 4.2449 | 4.2449 | 0.86022 | 1.4076 | 1.929 | 2.32 | 2.32 | 2.32 | 2.5911 | 3.3438 | 3.8369 | 4.0965 | 4.6156 | 5.1347 | 1.3489 | 2.6623 | 3.1948 | 3.1948 | 3.1948 | 3.1948 | 1.086 | 1.2633 | 1.2633 | 1.2633 | 1.2633 | 1.2633
2020-12-16 08:00 | Summer | 2.8388 | 4.0628 | 5.8628 | 5.8628 | 5.8628 | 5.8628 | 1.1117 | 1.8192 | 2.4929 | 2.9983 | 2.9983 | 2.9983 | 2.8007 | 3.6143 | 4.1473 | 4.4278 | 4.9889 | 5.55 | 1.3375 | 2.6398 | 3.1677 | 3.1677 | 3.1677 | 3.1677 | 1.467 | 1.7066 | 1.7066 | 1.7066 | 1.7066 | 1.7066
2020-12-16 09:00 | Summer | 2.8769 | 4.1174 | 5.9415 | 5.9415 | 5.9415 | 5.9415 | 1.2375 | 2.0249 | 2.7749 | 3.3374 | 3.3374 | 3.3374 | 3.0294 | 3.9093 | 4.4858 | 4.7893 | 5.3962 | 6.003 | 1.2918 | 2.5495 | 3.0594 | 3.0594 | 3.0594 | 3.0594 | 1.467 | 1.7066 | 1.7066 | 1.7066 | 1.7066 | 1.7066
2020-12-16 10:00 | Summer | 2.9722 | 4.2537 | 6.1382 | 6.1382 | 6.1382 | 6.1382 | 1.2032 | 1.9688 | 2.698 | 3.2449 | 3.2449 | 3.2449 | 3.2008 | 4.1306 | 4.7398 | 5.0604 | 5.7016 | 6.3428 | 1.3184 | 2.6022 | 3.1226 | 3.1226 | 3.1226 | 3.1226 | 1.6957 | 1.9725 | 1.9725 | 1.9725 | 1.9725 | 1.9725
2020-12-16 11:00 | Summer | 3.0484 | 4.3628 | 6.2956 | 6.2956 | 6.2956 | 6.2956 | 1.2918 | 2.1138 | 2.8967 | 3.4838 | 3.4838 | 3.4838 | 3.2173 | 4.1519 | 4.7642 | 5.0865 | 5.731 | 6.3755 | 1.3032 | 2.5721 | 3.0865 | 3.0865 | 3.0865 | 3.0865 | 1.7338 | 2.0168 | 2.0168 | 2.0168 | 2.0168 | 2.0168
2020-12-16 12:00 | Summer | 2.9722 | 4.2537 | 6.1382 | 6.1382 | 6.1382 | 6.1382 | 1.3518 | 2.212 | 3.0313 | 3.6457 | 3.6457 | 3.6457 | 3.3723 | 4.3519 | 4.9937 | 5.3315 | 6.007 | 6.6826 | 1.3832 | 2.73 | 3.276 | 3.276 | 3.276 | 3.276 | 1.6766 | 1.9504 | 1.9504 | 1.9504 | 1.9504 | 1.9504
2020-12-16 13:00 | Summer | 3.1246 | 4.4718 | 6.453 | 6.453 | 6.453 | 6.453 | 1.3603 | 2.226 | 3.0505 | 3.6688 | 3.6688 | 3.6688 | 3.4866 | 4.4994 | 5.163 | 5.5122 | 6.2107 | 6.9091 | 1.3565 | 2.6774 | 3.2129 | 3.2129 | 3.2129 | 3.2129 | 1.829 | 2.1277 | 2.1277 | 2.1277 | 2.1277 | 2.1277
2020-12-16 14:00 | Summer | 3.1056 | 4.4446 | 6.4137 | 6.4137 | 6.4137 | 6.4137 | 1.3946 | 2.2821 | 3.1274 | 3.7613 | 3.7613 | 3.7613 | 3.4676 | 4.4748 | 5.1347 | 5.4821 | 6.1767 | 6.8714 | 1.3565 | 2.6774 | 3.2129 | 3.2129 | 3.2129 | 3.2129 | 1.6957 | 1.9725 | 1.9725 | 1.9725 | 1.9725 | 1.9725
2020-12-16 15:00 | Summer | 3.1056 | 4.4446 | 6.4137 | 6.4137 | 6.4137 | 6.4137 | 1.4661 | 2.3991 | 3.2876 | 3.954 | 3.954 | 3.954 | 3.5628 | 4.5978 | 5.2758 | 5.6327 | 6.3464 | 7.0602 | 1.387 | 2.7375 | 3.2851 | 3.2851 | 3.2851 | 3.2851 | 1.6576 | 1.9282 | 1.9282 | 1.9282 | 1.9282 | 1.9282
2020-12-16 16:00 | Summer | 3.0106 | 4.3086 | 6.2175 | 6.2175 | 6.2175 | 6.2175 | 1.3089 | 2.1418 | 2.9351 | 3.5301 | 3.5301 | 3.5301 | 3.5628 | 4.5978 | 5.2758 | 5.6327 | 6.3464 | 7.0602 | 1.3527 | 2.6699 | 3.2038 | 3.2038 | 3.2038 | 3.2038 | 1.5814 | 1.8395 | 1.8395 | 1.8395 | 1.8395 | 1.8395
2020-12-16 17:00 | Summer | 2.9004 | 4.1509 | 5.9899 | 5.9899 | 5.9899 | 5.9899 | 1.3003 | 2.1278 | 2.9159 | 3.507 | 3.507 | 3.507 | 3.5208 | 4.5435 | 5.2135 | 5.5662 | 6.2715 | 6.9768 | 1.3642 | 2.6924 | 3.2309 | 3.2309 | 3.2309 | 3.2309 | 1.5623 | 1.8174 | 1.8174 | 1.8174 | 1.8174 | 1.8174
2020-12-16 18:00 | Summer | 1.9124 | 2.737 | 3.9495 | 3.9495 | 3.9495 | 3.9495 | 1.0949 | 1.7916 | 2.4552 | 2.9529 | 2.9529 | 2.9529 | 3.1627 | 4.0814 | 4.6833 | 5.0001 | 5.6337 | 6.2673 | 1.1355 | 2.2412 | 2.6894 | 2.6894 | 2.6894 | 2.6894 | 1.0334 | 1.2021 | 1.2021 | 1.2021 | 1.2021 | 1.2021
2020-12-16 19:00 | Summer | 1.3146 | 1.8814 | 2.715 | 2.715 | 2.715 | 2.715 | 0.82021 | 1.3422 | 1.8393 | 2.2121 | 2.2121 | 2.2121 | 2.7631 | 3.5657 | 4.0916 | 4.3684 | 4.9219 | 5.4754 | 1.1279 | 2.2261 | 2.6714 | 2.6714 | 2.6714 | 2.6714 | 0.7621 | 0.88653 | 0.88653 | 0.88653 | 0.88653 | 0.88653
2020-12-16 20:00 | Summer | 1.3908 | 1.9905 | 2.8724 | 2.8724 | 2.8724 | 2.8724 | 0.76591 | 1.2533 | 1.7175 | 2.0656 | 2.0656 | 2.0656 | 2.5149 | 3.2455 | 3.7241 | 3.976 | 4.4798 | 4.9836 | 1.0708 | 2.1133 | 2.536 | 2.536 | 2.536 | 2.536 | 0.64779 | 0.75355 | 0.75355 | 0.75355 | 0.75355 | 0.75355
2020-12-16 21:00 | Summer | 1.1813 | 1.6906 | 2.4396 | 2.4396 | 2.4396 | 2.4396 | 0.67731 | 1.1083 | 1.5188 | 1.8267 | 1.8267 | 1.8267 | 2.2897 | 2.9549 | 3.3906 | 3.62 | 4.0787 | 4.5374 | 1.0669 | 2.1058 | 2.527 | 2.527 | 2.527 | 2.527 | 0.64779 | 0.75355 | 0.75355 | 0.75355 | 0.75355 | 0.75355
2020-12-16 22:00 | Summer | 1.1432 | 1.636 | 2.3609 | 2.3609 | 2.3609 | 2.3609 | 0.64588 | 1.0569 | 1.4483 | 1.7419 | 1.7419 | 1.7419 | 2.2101 | 2.8521 | 3.2727 | 3.4941 | 3.9368 | 4.3796 | 0.98311 | 1.9403 | 2.3284 | 2.3284 | 2.3284 | 2.3284 | 0.57158 | 0.6649 | 0.6649 | 0.6649 | 0.6649 | 0.6649
2020-12-16 23:00 | Summer | 1.086 | 1.5542 | 2.2428 | 2.2428 | 2.2428 | 2.2428 | 0.54585 | 0.89321 | 1.224 | 1.4721 | 1.4721 | 1.4721 | 2.0005 | 2.5816 | 2.9624 | 3.1627 | 3.5635 | 3.9643 | 0.92595 | 1.8275 | 2.193 | 2.193 | 2.193 | 2.193 | 0.49565 | 0.57657 | 0.57657 | 0.57657 | 0.57657 | 0.57657
2020-12-17 | Summer | 1.0479 | 1.4997 | 2.1641 | 2.1641 | 2.1641 | 2.1641 | 0.49155 | 0.80436 | 1.1023 | 1.3257 | 1.3257 | 1.3257 | 1.9243 | 2.4833 | 2.8495 | 3.0422 | 3.4277 | 3.8132 | 0.8345 | 1.647 | 1.9764 | 1.9764 | 1.9764 | 1.9764 | 0.47635 | 0.55412 | 0.55412 | 0.55412 | 0.55412 | 0.55412
2020-12-17 01:00 | Summer | 1.0669 | 1.527 | 2.2035 | 2.2035 | 2.2035 | 2.2035 | 0.41725 | 0.68277 | 0.93565 | 1.1253 | 1.1253 | 1.1253 | 1.8672 | 2.4095 | 2.7649 | 2.9519 | 3.3259 | 3.7 | 0.82307 | 1.6245 | 1.9494 | 1.9494 | 1.9494 | 1.9494 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-12-17 02:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.48012 | 0.78565 | 1.0766 | 1.2949 | 1.2949 | 1.2949 | 1.8672 | 2.4095 | 2.7649 | 2.9519 | 3.3259 | 3.7 | 0.77353 | 1.5267 | 1.832 | 1.832 | 1.832 | 1.832 | 0.45313 | 0.5271 | 0.5271 | 0.5271 | 0.5271 | 0.5271
2020-12-17 03:00 | Summer | 1.0288 | 1.4724 | 2.1248 | 2.1248 | 2.1248 | 2.1248 | 0.57729 | 0.94465 | 1.2945 | 1.5569 | 1.5569 | 1.5569 | 1.7909 | 2.3112 | 2.652 | 2.8314 | 3.1902 | 3.549 | 0.73543 | 1.4515 | 1.7418 | 1.7418 | 1.7418 | 1.7418 | 0.44568 | 0.51845 | 0.51845 | 0.51845 | 0.51845 | 0.51845
2020-12-17 04:00 | Summer | 1.105 | 1.5815 | 2.2822 | 2.2822 | 2.2822 | 2.2822 | 0.54871 | 0.89789 | 1.2304 | 1.4799 | 1.4799 | 1.4799 | 1.8221 | 2.3514 | 2.6981 | 2.8806 | 3.2457 | 3.6107 | 0.76591 | 1.5117 | 1.814 | 1.814 | 1.814 | 1.814 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-12-17 05:00 | Summer | 1.1432 | 1.636 | 2.3609 | 2.3609 | 2.3609 | 2.3609 | 0.60873 | 0.9961 | 1.365 | 1.6417 | 1.6417 | 1.6417 | 1.9815 | 2.557 | 2.9341 | 3.1326 | 3.5296 | 3.9265 | 0.86498 | 1.7072 | 2.0486 | 2.0486 | 2.0486 | 2.0486 | 0.60968 | 0.70922 | 0.70922 | 0.70922 | 0.70922 | 0.70922
2020-12-17 06:00 | Summer | 1.3034 | 1.8653 | 2.6917 | 2.6917 | 2.6917 | 2.6917 | 0.77448 | 1.2673 | 1.7367 | 2.0888 | 2.0888 | 2.0888 | 2.0689 | 2.6698 | 3.0636 | 3.2708 | 3.6853 | 4.0997 | 0.89547 | 1.7674 | 2.1208 | 2.1208 | 2.1208 | 2.1208 | 0.77965 | 0.90694 | 0.90694 | 0.90694 | 0.90694 | 0.90694
2020-12-17 07:00 | Summer | 2.0577 | 2.9449 | 4.2495 | 4.2495 | 4.2495 | 4.2495 | 0.97453 | 1.5947 | 2.1853 | 2.6283 | 2.6283 | 2.6283 | 2.6674 | 3.4422 | 3.9498 | 4.217 | 4.7513 | 5.2857 | 1.1089 | 2.1885 | 2.6262 | 2.6262 | 2.6262 | 2.6262 | 1.2575 | 1.4628 | 1.4628 | 1.4628 | 1.4628 | 1.4628
2020-12-17 08:00 | Summer | 2.7245 | 3.8992 | 5.6267 | 5.6267 | 5.6267 | 5.6267 | 1.066 | 1.7443 | 2.3904 | 2.8749 | 2.8749 | 2.8749 | 2.915 | 3.7618 | 4.3166 | 4.6086 | 5.1925 | 5.7765 | 1.4213 | 2.8052 | 3.3663 | 3.3663 | 3.3663 | 3.3663 | 1.467 | 1.7066 | 1.7066 | 1.7066 | 1.7066 | 1.7066
2020-12-17 09:00 | Summer | 2.896 | 4.1446 | 5.9808 | 5.9808 | 5.9808 | 5.9808 | 1.1774 | 1.9267 | 2.6403 | 3.1755 | 3.1755 | 3.1755 | 3.2359 | 4.1758 | 4.7916 | 5.1157 | 5.764 | 6.4122 | 1.4099 | 2.7827 | 3.3392 | 3.3392 | 3.3392 | 3.3392 | 1.5433 | 1.7952 | 1.7952 | 1.7952 | 1.7952 | 1.7952
2020-12-17 10:00 | Summer | 3.0865 | 4.4173 | 6.3743 | 6.3743 | 6.3743 | 6.3743 | 1.2657 | 2.0711 | 2.8382 | 3.4135 | 3.4135 | 3.4135 | 3.4676 | 4.4748 | 5.1347 | 5.4821 | 6.1767 | 6.8714 | 1.3832 | 2.73 | 3.276 | 3.276 | 3.276 | 3.276 | 1.6195 | 1.8839 | 1.8839 | 1.8839 | 1.8839 | 1.8839
2020-12-17 11:00 | Summer | 3.0484 | 4.3628 | 6.2956 | 6.2956 | 6.2956 | 6.2956 | 1.3003 | 2.1278 | 2.9159 | 3.507 | 3.507 | 3.507 | 3.6377 | 4.6944 | 5.3867 | 5.751 | 6.4798 | 7.2085 | 1.4404 | 2.8428 | 3.4114 | 3.4114 | 3.4114 | 3.4114 | 1.7147 | 1.9947 | 1.9947 | 1.9947 | 1.9947 | 1.9947
2020-12-17 12:00 | Summer | 3.3533 | 4.799 | 6.9252 | 6.9252 | 6.9252 | 6.9252 | 1.4004 | 2.2915 | 3.1402 | 3.7767 | 3.7767 | 3.7767 | 3.7152 | 4.7944 | 5.5015 | 5.8736 | 6.6179 | 7.3622 | 1.467 | 2.8955 | 3.4746 | 3.4746 | 3.4746 | 3.4746 | 1.7147 | 1.9947 | 1.9947 | 1.9947 | 1.9947 | 1.9947
2020-12-17 13:00 | Summer | 3.0675 | 4.39 | 6.335 | 6.335 | 6.335 | 6.335 | 1.4232 | 2.3289 | 3.1915 | 3.8384 | 3.8384 | 3.8384 | 3.5628 | 4.5978 | 5.2758 | 5.6327 | 6.3464 | 7.0602 | 1.4213 | 2.8052 | 3.3663 | 3.3663 | 3.3663 | 3.3663 | 1.6957 | 1.9725 | 1.9725 | 1.9725 | 1.9725 | 1.9725
2020-12-17 14:00 | Summer | 3.0263 | 4.3312 | 6.2501 | 6.2501 | 6.2501 | 6.2501 | 1.4146 | 2.3149 | 3.1722 | 3.8153 | 3.8153 | 3.8153 | 3.6326 | 4.6878 | 5.3792 | 5.743 | 6.4707 | 7.1985 | 1.4518 | 2.8654 | 3.4385 | 3.4385 | 3.4385 | 3.4385 | 1.7147 | 1.9947 | 1.9947 | 1.9947 | 1.9947 | 1.9947
2020-12-17 15:00 | Summer | 3.0675 | 4.39 | 6.335 | 6.335 | 6.335 | 6.335 | 1.3391 | 2.1913 | 3.0029 | 3.6116 | 3.6116 | 3.6116 | 3.7343 | 4.819 | 5.5297 | 5.9038 | 6.6519 | 7.4 | 1.246 | 2.4593 | 2.9511 | 2.9511 | 2.9511 | 2.9511 | 1.6576 | 1.9282 | 1.9282 | 1.9282 | 1.9282 | 1.9282
2020-12-17 16:00 | Summer | 3.0294 | 4.3355 | 6.2563 | 6.2563 | 6.2563 | 6.2563 | 1.4661 | 2.3991 | 3.2876 | 3.954 | 3.954 | 3.954 | 3.6771 | 4.7453 | 5.4451 | 5.8134 | 6.55 | 7.2867 | 1.2117 | 2.3916 | 2.8699 | 2.8699 | 2.8699 | 2.8699 | 1.5623 | 1.8174 | 1.8174 | 1.8174 | 1.8174 | 1.8174
2020-12-17 17:00 | Summer | 2.9177 | 4.1757 | 6.0257 | 6.0257 | 6.0257 | 6.0257 | 1.5318 | 2.5066 | 3.435 | 4.1313 | 4.1313 | 4.1313 | 3.5457 | 4.5756 | 5.2504 | 5.6056 | 6.3159 | 7.0262 | 1.227 | 2.4217 | 2.906 | 2.906 | 2.906 | 2.906 | 1.5055 | 1.7514 | 1.7514 | 1.7514 | 1.7514 | 1.7514
2020-12-17 18:00 | Summer | 1.8832 | 2.6951 | 3.8892 | 3.8892 | 3.8892 | 3.8892 | 1.1403 | 1.8659 | 2.557 | 3.0753 | 3.0753 | 3.0753 | 3.3076 | 4.2684 | 4.8979 | 5.2292 | 5.8918 | 6.5545 | 1.2194 | 2.4066 | 2.888 | 2.888 | 2.888 | 2.888 | 1.1064 | 1.2871 | 1.2871 | 1.2871 | 1.2871 | 1.2871
2020-12-17 19:00 | Summer | 1.2003 | 1.7178 | 2.4789 | 2.4789 | 2.4789 | 2.4789 | 1.0288 | 1.6835 | 2.3071 | 2.7747 | 2.7747 | 2.7747 | 3.0233 | 3.9015 | 4.4768 | 4.7797 | 5.3853 | 5.991 | 1.1736 | 2.3164 | 2.7797 | 2.7797 | 2.7797 | 2.7797 | 0.7621 | 0.88653 | 0.88653 | 0.88653 | 0.88653 | 0.88653
2020-12-17 20:00 | Summer | 1.2003 | 1.7178 | 2.4789 | 2.4789 | 2.4789 | 2.4789 | 0.89166 | 1.4591 | 1.9995 | 2.4048 | 2.4048 | 2.4048 | 2.6674 | 3.4422 | 3.9498 | 4.217 | 4.7513 | 5.2857 | 1.2041 | 2.3766 | 2.8519 | 2.8519 | 2.8519 | 2.8519 | 0.70494 | 0.82004 | 0.82004 | 0.82004 | 0.82004 | 0.82004
2020-12-17 21:00 | Summer | 1.1622 | 1.6633 | 2.4002 | 2.4002 | 2.4002 | 2.4002 | 0.81449 | 1.3328 | 1.8264 | 2.1967 | 2.1967 | 2.1967 | 2.7245 | 3.5159 | 4.0344 | 4.3073 | 4.8531 | 5.3989 | 1.1508 | 2.2713 | 2.7255 | 2.7255 | 2.7255 | 2.7255 | 0.64779 | 0.75355 | 0.75355 | 0.75355 | 0.75355 | 0.75355
2020-12-17 22:00 | Summer | 1.0669 | 1.527 | 2.2035 | 2.2035 | 2.2035 | 2.2035 | 0.70875 | 1.1598 | 1.5893 | 1.9115 | 1.9115 | 1.9115 | 2.4006 | 3.098 | 3.5548 | 3.7953 | 4.2762 | 4.7571 | 1.0974 | 2.166 | 2.5992 | 2.5992 | 2.5992 | 2.5992 | 0.62873 | 0.73138 | 0.73138 | 0.73138 | 0.73138 | 0.73138
2020-12-17 23:00 | Summer | 1.0479 | 1.4997 | 2.1641 | 2.1641 | 2.1641 | 2.1641 | 0.58586 | 0.95868 | 1.3138 | 1.5801 | 1.5801 | 1.5801 | 2.2673 | 2.9258 | 3.3573 | 3.5844 | 4.0386 | 4.4928 | 1.006 | 1.9855 | 2.3826 | 2.3826 | 2.3826 | 2.3826 | 0.57158 | 0.6649 | 0.6649 | 0.6649 | 0.6649 | 0.6649
2020-12-18 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.54871 | 0.89789 | 1.2304 | 1.4799 | 1.4799 | 1.4799 | 2.0577 | 2.6554 | 3.047 | 3.2531 | 3.6653 | 4.0775 | 0.92214 | 1.82 | 2.184 | 2.184 | 2.184 | 2.184 | 0.52815 | 0.61437 | 0.61437 | 0.61437 | 0.61437 | 0.61437
2020-12-18 01:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.41439 | 0.67809 | 0.92924 | 1.1176 | 1.1176 | 1.1176 | 1.9434 | 2.5079 | 2.8777 | 3.0724 | 3.4617 | 3.851 | 0.82307 | 1.6245 | 1.9494 | 1.9494 | 1.9494 | 1.9494 | 0.53347 | 0.62057 | 0.62057 | 0.62057 | 0.62057 | 0.62057
2020-12-18 02:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.45154 | 0.73889 | 1.0125 | 1.2178 | 1.2178 | 1.2178 | 1.8481 | 2.3849 | 2.7366 | 2.9218 | 3.292 | 3.6622 | 0.77353 | 1.5267 | 1.832 | 1.832 | 1.832 | 1.832 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-12-18 03:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.48298 | 0.79033 | 1.083 | 1.3026 | 1.3026 | 1.3026 | 1.7668 | 2.2801 | 2.6163 | 2.7933 | 3.1473 | 3.5012 | 0.76591 | 1.5117 | 1.814 | 1.814 | 1.814 | 1.814 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-12-18 04:00 | Summer | 1.0914 | 1.5619 | 2.2539 | 2.2539 | 2.2539 | 2.2539 | 0.57634 | 0.9431 | 1.2924 | 1.5544 | 1.5544 | 1.5544 | 1.81 | 2.3358 | 2.6802 | 2.8615 | 3.2241 | 3.5867 | 0.7621 | 1.5041 | 1.805 | 1.805 | 1.805 | 1.805 | 0.55252 | 0.64273 | 0.64273 | 0.64273 | 0.64273 | 0.64273
2020-12-18 05:00 | Summer | 1.1622 | 1.6633 | 2.4002 | 2.4002 | 2.4002 | 2.4002 | 0.57729 | 0.94465 | 1.2945 | 1.5569 | 1.5569 | 1.5569 | 1.9815 | 2.557 | 2.9341 | 3.1326 | 3.5296 | 3.9265 | 0.80402 | 1.5869 | 1.9042 | 1.9042 | 1.9042 | 1.9042 | 0.62873 | 0.73138 | 0.73138 | 0.73138 | 0.73138 | 0.73138
2020-12-18 06:00 | Summer | 1.2384 | 1.7724 | 2.5576 | 2.5576 | 2.5576 | 2.5576 | 0.71733 | 1.1738 | 1.6085 | 1.9346 | 1.9346 | 1.9346 | 2.0196 | 2.6062 | 2.9906 | 3.1929 | 3.5974 | 4.002 | 0.93738 | 1.8501 | 2.2201 | 2.2201 | 2.2201 | 2.2201 | 0.82748 | 0.96258 | 0.96258 | 0.96258 | 0.96258 | 0.96258
2020-12-18 07:00 | Summer | 2.2315 | 3.1936 | 4.6085 | 4.6085 | 4.6085 | 4.6085 | 0.87165 | 1.4263 | 1.9546 | 2.3508 | 2.3508 | 2.3508 | 2.6864 | 3.4668 | 3.978 | 4.2471 | 4.7853 | 5.3234 | 1.1622 | 2.2938 | 2.7526 | 2.7526 | 2.7526 | 2.7526 | 1.2194 | 1.4184 | 1.4184 | 1.4184 | 1.4184 | 1.4184
2020-12-18 08:00 | Summer | 3.0103 | 4.3082 | 6.2169 | 6.2169 | 6.2169 | 6.2169 | 1.1006 | 1.801 | 2.468 | 2.9683 | 2.9683 | 2.9683 | 3.1627 | 4.0814 | 4.6833 | 5.0001 | 5.6337 | 6.2673 | 1.1203 | 2.2111 | 2.6533 | 2.6533 | 2.6533 | 2.6533 | 1.4285 | 1.6617 | 1.6617 | 1.6617 | 1.6617 | 1.6617
2020-12-18 09:00 | Summer | 3.0484 | 4.3628 | 6.2956 | 6.2956 | 6.2956 | 6.2956 | 1.1603 | 1.8987 | 2.6019 | 3.1293 | 3.1293 | 3.1293 | 3.2199 | 4.1552 | 4.768 | 5.0905 | 5.7355 | 6.3806 | 1.0403 | 2.0532 | 2.4638 | 2.4638 | 2.4638 | 2.4638 | 1.5052 | 1.7509 | 1.7509 | 1.7509 | 1.7509 | 1.7509
2020-12-18 10:00 | Summer | 2.8388 | 4.0628 | 5.8628 | 5.8628 | 5.8628 | 5.8628 | 1.2032 | 1.9688 | 2.698 | 3.2449 | 3.2449 | 3.2449 | 3.2199 | 4.1552 | 4.768 | 5.0905 | 5.7355 | 6.3806 | 1.0974 | 2.166 | 2.5992 | 2.5992 | 2.5992 | 2.5992 | 1.5814 | 1.8395 | 1.8395 | 1.8395 | 1.8395 | 1.8395
2020-12-18 11:00 | Summer | 2.9722 | 4.2537 | 6.1382 | 6.1382 | 6.1382 | 6.1382 | 1.3146 | 2.1512 | 2.9479 | 3.5455 | 3.5455 | 3.5455 | 3.5057 | 4.524 | 5.1912 | 5.5423 | 6.2446 | 6.9469 | 1.0784 | 2.1284 | 2.554 | 2.554 | 2.554 | 2.554 | 1.6385 | 1.906 | 1.906 | 1.906 | 1.906 | 1.906
2020-12-18 12:00 | Summer | 2.9341 | 4.1992 | 6.0595 | 6.0595 | 6.0595 | 6.0595 | 1.206 | 1.9735 | 2.7044 | 3.2526 | 3.2526 | 3.2526 | 3.5057 | 4.524 | 5.1912 | 5.5423 | 6.2446 | 6.9469 | 1.0593 | 2.0908 | 2.5089 | 2.5089 | 2.5089 | 2.5089 | 1.6346 | 1.9015 | 1.9015 | 1.9015 | 1.9015 | 1.9015
2020-12-18 13:00 | Summer | 2.8579 | 4.0901 | 5.9022 | 5.9022 | 5.9022 | 5.9022 | 1.2117 | 1.9828 | 2.7172 | 3.268 | 3.268 | 3.268 | 3.3533 | 4.3273 | 4.9655 | 5.3013 | 5.9731 | 6.6449 | 1.0136 | 2.0005 | 2.4006 | 2.4006 | 2.4006 | 2.4006 | 1.6004 | 1.8617 | 1.8617 | 1.8617 | 1.8617 | 1.8617
2020-12-18 14:00 | Summer | 2.7055 | 3.8719 | 5.5874 | 5.5874 | 5.5874 | 5.5874 | 1.2117 | 1.9828 | 2.7172 | 3.268 | 3.268 | 3.268 | 3.3723 | 4.3519 | 4.9937 | 5.3315 | 6.007 | 6.6826 | 1.0403 | 2.0532 | 2.4638 | 2.4638 | 2.4638 | 2.4638 | 1.6004 | 1.8617 | 1.8617 | 1.8617 | 1.8617 | 1.8617
2020-12-18 15:00 | Summer | 2.6293 | 3.7629 | 5.43 | 5.43 | 5.43 | 5.43 | 1.1717 | 1.9174 | 2.6275 | 3.1601 | 3.1601 | 3.1601 | 3.3533 | 4.3273 | 4.9655 | 5.3013 | 5.9731 | 6.6449 | 1.0746 | 2.1208 | 2.545 | 2.545 | 2.545 | 2.545 | 1.4861 | 1.7287 | 1.7287 | 1.7287 | 1.7287 | 1.7287
2020-12-18 16:00 | Summer | 2.6483 | 3.7901 | 5.4693 | 5.4693 | 5.4693 | 5.4693 | 1.1489 | 1.88 | 2.5762 | 3.0985 | 3.0985 | 3.0985 | 3.258 | 4.2044 | 4.8244 | 5.1507 | 5.8034 | 6.4561 | 1.0517 | 2.0757 | 2.4909 | 2.4909 | 2.4909 | 2.4909 | 1.4099 | 1.6401 | 1.6401 | 1.6401 | 1.6401 | 1.6401
2020-12-18 17:00 | Summer | 2.6264 | 3.7589 | 5.4242 | 5.4242 | 5.4242 | 5.4242 | 1.0774 | 1.763 | 2.416 | 2.9058 | 2.9058 | 2.9058 | 3.2008 | 4.1306 | 4.7398 | 5.0604 | 5.7016 | 6.3428 | 1.0746 | 2.1208 | 2.545 | 2.545 | 2.545 | 2.545 | 1.3718 | 1.5957 | 1.5957 | 1.5957 | 1.5957 | 1.5957
2020-12-18 18:00 | Summer | 1.8583 | 2.6596 | 3.8379 | 3.8379 | 3.8379 | 3.8379 | 0.94881 | 1.5526 | 2.1276 | 2.5589 | 2.5589 | 2.5589 | 2.8417 | 3.6672 | 4.208 | 4.4926 | 5.0619 | 5.6312 | 1.0822 | 2.1359 | 2.5631 | 2.5631 | 2.5631 | 2.5631 | 1.0295 | 1.1975 | 1.1975 | 1.1975 | 1.1975 | 1.1975
2020-12-18 19:00 | Summer | 1.2956 | 1.8542 | 2.6756 | 2.6756 | 2.6756 | 2.6756 | 0.74876 | 1.2252 | 1.679 | 2.0194 | 2.0194 | 2.0194 | 2.7506 | 3.5496 | 4.0731 | 4.3486 | 4.8996 | 5.4506 | 1.0936 | 2.1585 | 2.5901 | 2.5901 | 2.5901 | 2.5901 | 0.724 | 0.8422 | 0.8422 | 0.8422 | 0.8422 | 0.8422
2020-12-18 20:00 | Summer | 1.2575 | 1.7996 | 2.5969 | 2.5969 | 2.5969 | 2.5969 | 0.68017 | 1.113 | 1.5252 | 1.8344 | 1.8344 | 1.8344 | 2.2291 | 2.8767 | 3.3009 | 3.5242 | 3.9708 | 4.4173 | 1.0212 | 2.0156 | 2.4187 | 2.4187 | 2.4187 | 2.4187 | 0.64779 | 0.75355 | 0.75355 | 0.75355 | 0.75355 | 0.75355
2020-12-18 21:00 | Summer | 1.2194 | 1.7451 | 2.5183 | 2.5183 | 2.5183 | 2.5183 | 0.69732 | 1.1411 | 1.5637 | 1.8807 | 1.8807 | 1.8807 | 2.172 | 2.8029 | 3.2163 | 3.4338 | 3.8689 | 4.3041 | 1.006 | 1.9855 | 2.3826 | 2.3826 | 2.3826 | 2.3826 | 0.62873 | 0.73138 | 0.73138 | 0.73138 | 0.73138 | 0.73138
2020-12-18 22:00 | Summer | 1.0669 | 1.527 | 2.2035 | 2.2035 | 2.2035 | 2.2035 | 0.64016 | 1.0475 | 1.4355 | 1.7265 | 1.7265 | 1.7265 | 2.0005 | 2.5816 | 2.9624 | 3.1627 | 3.5635 | 3.9643 | 0.98311 | 1.9403 | 2.3284 | 2.3284 | 2.3284 | 2.3284 | 0.54164 | 0.63007 | 0.63007 | 0.63007 | 0.63007 | 0.63007
2020-12-18 23:00 | Summer | 0.98022 | 1.4029 | 2.0244 | 2.0244 | 2.0244 | 2.0244 | 0.57729 | 0.94465 | 1.2945 | 1.5569 | 1.5569 | 1.5569 | 1.8862 | 2.4341 | 2.7931 | 2.982 | 3.3599 | 3.7377 | 0.92595 | 1.8275 | 2.193 | 2.193 | 2.193 | 2.193 | 0.55252 | 0.64273 | 0.64273 | 0.64273 | 0.64273 | 0.64273
2020-12-19 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.54299 | 0.88854 | 1.2176 | 1.4644 | 1.4644 | 1.4644 | 1.81 | 2.3358 | 2.6803 | 2.8616 | 3.2242 | 3.5868 | 0.81164 | 1.6019 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 0.50573 | 0.58829 | 0.58829 | 0.58829 | 0.58829 | 0.58829
2020-12-19 01:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.40582 | 0.66406 | 0.91001 | 1.0945 | 1.0945 | 1.0945 | 1.7147 | 2.2128 | 2.5392 | 2.7109 | 3.0544 | 3.3979 | 0.77734 | 1.5342 | 1.8411 | 1.8411 | 1.8411 | 1.8411 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-12-19 02:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.48012 | 0.78565 | 1.0766 | 1.2949 | 1.2949 | 1.2949 | 1.6766 | 2.1636 | 2.4827 | 2.6507 | 2.9865 | 3.3224 | 0.69732 | 1.3763 | 1.6516 | 1.6516 | 1.6516 | 1.6516 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-12-19 03:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.47441 | 0.7763 | 1.0638 | 1.2795 | 1.2795 | 1.2795 | 1.6195 | 2.0899 | 2.3981 | 2.5603 | 2.8847 | 3.2092 | 0.70494 | 1.3913 | 1.6696 | 1.6696 | 1.6696 | 1.6696 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-12-19 04:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.47726 | 0.78098 | 1.0702 | 1.2872 | 1.2872 | 1.2872 | 1.6766 | 2.1636 | 2.4827 | 2.6507 | 2.9865 | 3.3224 | 0.70113 | 1.3838 | 1.6606 | 1.6606 | 1.6606 | 1.6606 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-12-19 05:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.40867 | 0.66874 | 0.91642 | 1.1022 | 1.1022 | 1.1022 | 1.6957 | 2.1882 | 2.5109 | 2.6808 | 3.0205 | 3.3602 | 0.69732 | 1.3763 | 1.6516 | 1.6516 | 1.6516 | 1.6516 | 0.47347 | 0.55077 | 0.55077 | 0.55077 | 0.55077 | 0.55077
2020-12-19 06:00 | Summer | 0.99685 | 1.4266 | 2.0587 | 2.0587 | 2.0587 | 2.0587 | 0.43439 | 0.71083 | 0.9741 | 1.1715 | 1.1715 | 1.1715 | 1.7719 | 2.2866 | 2.6238 | 2.8013 | 3.1562 | 3.5112 | 0.78496 | 1.5493 | 1.8591 | 1.8591 | 1.8591 | 1.8591 | 0.52935 | 0.61578 | 0.61578 | 0.61578 | 0.61578 | 0.61578
2020-12-19 07:00 | Summer | 1.105 | 1.5815 | 2.2822 | 2.2822 | 2.2822 | 2.2822 | 0.51442 | 0.84177 | 1.1535 | 1.3874 | 1.3874 | 1.3874 | 1.8481 | 2.3849 | 2.7366 | 2.9218 | 3.292 | 3.6622 | 0.87642 | 1.7298 | 2.0757 | 2.0757 | 2.0757 | 2.0757 | 0.60968 | 0.70922 | 0.70922 | 0.70922 | 0.70922 | 0.70922
2020-12-19 08:00 | Summer | 1.105 | 1.5815 | 2.2822 | 2.2822 | 2.2822 | 2.2822 | 0.50573 | 0.82755 | 1.1341 | 1.3639 | 1.3639 | 1.3639 | 2.0767 | 2.68 | 3.0752 | 3.2832 | 3.6992 | 4.1153 | 0.86498 | 1.7072 | 2.0486 | 2.0486 | 2.0486 | 2.0486 | 0.55252 | 0.64273 | 0.64273 | 0.64273 | 0.64273 | 0.64273
2020-12-19 09:00 | Summer | 1.1813 | 1.6906 | 2.4396 | 2.4396 | 2.4396 | 2.4396 | 0.57729 | 0.94465 | 1.2945 | 1.5569 | 1.5569 | 1.5569 | 2.1148 | 2.7291 | 3.1316 | 3.3435 | 3.7671 | 4.1908 | 0.8345 | 1.647 | 1.9764 | 1.9764 | 1.9764 | 1.9764 | 0.59063 | 0.68706 | 0.68706 | 0.68706 | 0.68706 | 0.68706
2020-12-19 10:00 | Summer | 1.1432 | 1.636 | 2.3609 | 2.3609 | 2.3609 | 2.3609 | 0.63159 | 1.0335 | 1.4163 | 1.7034 | 1.7034 | 1.7034 | 2.172 | 2.8029 | 3.2163 | 3.4338 | 3.8689 | 4.3041 | 0.94119 | 1.8576 | 2.2291 | 2.2291 | 2.2291 | 2.2291 | 0.64779 | 0.75355 | 0.75355 | 0.75355 | 0.75355 | 0.75355
2020-12-19 11:00 | Summer | 1.086 | 1.5542 | 2.2428 | 2.2428 | 2.2428 | 2.2428 | 0.66874 | 1.0943 | 1.4996 | 1.8036 | 1.8036 | 1.8036 | 2.245 | 2.8971 | 3.3243 | 3.5492 | 3.9989 | 4.4487 | 0.91071 | 1.7975 | 2.1569 | 2.1569 | 2.1569 | 2.1569 | 0.62873 | 0.73138 | 0.73138 | 0.73138 | 0.73138 | 0.73138
2020-12-19 12:00 | Summer | 1.1813 | 1.6906 | 2.4396 | 2.4396 | 2.4396 | 2.4396 | 0.76877 | 1.258 | 1.7239 | 2.0733 | 2.0733 | 2.0733 | 2.2673 | 2.9258 | 3.3573 | 3.5844 | 4.0386 | 4.4928 | 0.80783 | 1.5944 | 1.9133 | 1.9133 | 1.9133 | 1.9133 | 0.62873 | 0.73138 | 0.73138 | 0.73138 | 0.73138 | 0.73138
2020-12-19 13:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.75162 | 1.2299 | 1.6855 | 2.0271 | 2.0271 | 2.0271 | 2.3625 | 3.0488 | 3.4984 | 3.735 | 4.2083 | 4.6816 | 0.84974 | 1.6771 | 2.0125 | 2.0125 | 2.0125 | 2.0125 | 0.60968 | 0.70922 | 0.70922 | 0.70922 | 0.70922 | 0.70922
2020-12-19 14:00 | Summer | 0.83831 | 1.1998 | 1.7313 | 1.7313 | 1.7313 | 1.7313 | 0.80592 | 1.3188 | 1.8072 | 2.1735 | 2.1735 | 2.1735 | 2.2863 | 2.9504 | 3.3855 | 3.6146 | 4.0726 | 4.5306 | 0.9069 | 1.7899 | 2.1479 | 2.1479 | 2.1479 | 2.1479 | 0.55252 | 0.64273 | 0.64273 | 0.64273 | 0.64273 | 0.64273
2020-12-19 15:00 | Summer | 0.91452 | 1.3088 | 1.8887 | 1.8887 | 1.8887 | 1.8887 | 0.81164 | 1.3281 | 1.82 | 2.189 | 2.189 | 2.189 | 2.2863 | 2.9504 | 3.3855 | 3.6146 | 4.0726 | 4.5306 | 0.8345 | 1.647 | 1.9764 | 1.9764 | 1.9764 | 1.9764 | 0.57158 | 0.6649 | 0.6649 | 0.6649 | 0.6649 | 0.6649
2020-12-19 16:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.78591 | 1.286 | 1.7624 | 2.1196 | 2.1196 | 2.1196 | 2.3816 | 3.0734 | 3.5266 | 3.7652 | 4.2423 | 4.7194 | 0.84974 | 1.6771 | 2.0125 | 2.0125 | 2.0125 | 2.0125 | 0.55252 | 0.64273 | 0.64273 | 0.64273 | 0.64273 | 0.64273
2020-12-19 17:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.66874 | 1.0943 | 1.4996 | 1.8036 | 1.8036 | 1.8036 | 2.1339 | 2.7537 | 3.1598 | 3.3736 | 3.8011 | 4.2285 | 0.88785 | 1.7523 | 2.1028 | 2.1028 | 2.1028 | 2.1028 | 0.53347 | 0.62057 | 0.62057 | 0.62057 | 0.62057 | 0.62057
2020-12-19 18:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.62301 | 1.0195 | 1.3971 | 1.6803 | 1.6803 | 1.6803 | 2.0098 | 2.5935 | 2.976 | 3.1773 | 3.5799 | 3.9826 | 0.93357 | 1.8426 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 0.55252 | 0.64273 | 0.64273 | 0.64273 | 0.64273 | 0.64273
2020-12-19 19:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.67731 | 1.1083 | 1.5188 | 1.8267 | 1.8267 | 1.8267 | 1.9624 | 2.5325 | 2.9059 | 3.1025 | 3.4956 | 3.8887 | 0.92976 | 1.8351 | 2.2021 | 2.2021 | 2.2021 | 2.2021 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-12-19 20:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.66303 | 1.085 | 1.4868 | 1.7882 | 1.7882 | 1.7882 | 2.017 | 2.6029 | 2.9867 | 3.1887 | 3.5928 | 3.9969 | 0.96025 | 1.8952 | 2.2743 | 2.2743 | 2.2743 | 2.2743 | 0.53347 | 0.62057 | 0.62057 | 0.62057 | 0.62057 | 0.62057
2020-12-19 21:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.56586 | 0.92595 | 1.2689 | 1.5261 | 1.5261 | 1.5261 | 2.0196 | 2.6062 | 2.9906 | 3.1929 | 3.5974 | 4.002 | 0.91833 | 1.8125 | 2.175 | 2.175 | 2.175 | 2.175 | 0.55252 | 0.64273 | 0.64273 | 0.64273 | 0.64273 | 0.64273
2020-12-19 22:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.57729 | 0.94465 | 1.2945 | 1.5569 | 1.5569 | 1.5569 | 1.8481 | 2.3849 | 2.7366 | 2.9218 | 3.292 | 3.6622 | 0.89166 | 1.7599 | 2.1118 | 2.1118 | 2.1118 | 2.1118 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-12-19 23:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.54014 | 0.88386 | 1.2112 | 1.4567 | 1.4567 | 1.4567 | 1.829 | 2.3603 | 2.7084 | 2.8916 | 3.2581 | 3.6245 | 0.81545 | 1.6094 | 1.9313 | 1.9313 | 1.9313 | 1.9313 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-12-20 | Summer | 0.92954 | 1.3303 | 1.9197 | 1.9197 | 1.9197 | 1.9197 | 0.46869 | 0.76695 | 1.051 | 1.264 | 1.264 | 1.264 | 1.6766 | 2.1636 | 2.4827 | 2.6507 | 2.9865 | 3.3224 | 0.76591 | 1.5117 | 1.814 | 1.814 | 1.814 | 1.814 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-12-20 01:00 | Summer | 0.91452 | 1.3088 | 1.8887 | 1.8887 | 1.8887 | 1.8887 | 0.49155 | 0.80436 | 1.1023 | 1.3257 | 1.3257 | 1.3257 | 1.6004 | 2.0653 | 2.3699 | 2.5302 | 2.8508 | 3.1714 | 0.67827 | 1.3387 | 1.6064 | 1.6064 | 1.6064 | 1.6064 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-12-20 02:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.44297 | 0.72486 | 0.99332 | 1.1947 | 1.1947 | 1.1947 | 1.6385 | 2.1145 | 2.4263 | 2.5904 | 2.9187 | 3.2469 | 0.64016 | 1.2635 | 1.5162 | 1.5162 | 1.5162 | 1.5162 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-12-20 03:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.43725 | 0.7155 | 0.98051 | 1.1793 | 1.1793 | 1.1793 | 1.5433 | 1.9915 | 2.2852 | 2.4398 | 2.749 | 3.0581 | 0.67446 | 1.3312 | 1.5974 | 1.5974 | 1.5974 | 1.5974 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-12-20 04:00 | Summer | 0.91452 | 1.3088 | 1.8887 | 1.8887 | 1.8887 | 1.8887 | 0.43725 | 0.7155 | 0.98051 | 1.1793 | 1.1793 | 1.1793 | 1.5623 | 2.0161 | 2.3135 | 2.4699 | 2.7829 | 3.0959 | 0.64779 | 1.2785 | 1.5342 | 1.5342 | 1.5342 | 1.5342 | 0.41354 | 0.48106 | 0.48106 | 0.48106 | 0.48106 | 0.48106
2020-12-20 05:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.43725 | 0.7155 | 0.98051 | 1.1793 | 1.1793 | 1.1793 | 1.6004 | 2.0653 | 2.3699 | 2.5302 | 2.8508 | 3.1714 | 0.67065 | 1.3236 | 1.5884 | 1.5884 | 1.5884 | 1.5884 | 0.41916 | 0.48759 | 0.48759 | 0.48759 | 0.48759 | 0.48759
2020-12-20 06:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.46869 | 0.76695 | 1.051 | 1.264 | 1.264 | 1.264 | 1.6385 | 2.1145 | 2.4263 | 2.5904 | 2.9187 | 3.2469 | 0.75829 | 1.4966 | 1.796 | 1.796 | 1.796 | 1.796 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-12-20 07:00 | Summer | 0.91452 | 1.3088 | 1.8887 | 1.8887 | 1.8887 | 1.8887 | 0.52585 | 0.86048 | 1.1792 | 1.4182 | 1.4182 | 1.4182 | 1.8481 | 2.3849 | 2.7366 | 2.9218 | 3.292 | 3.6622 | 0.74686 | 1.4741 | 1.7689 | 1.7689 | 1.7689 | 1.7689 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-12-20 08:00 | Summer | 0.91452 | 1.3088 | 1.8887 | 1.8887 | 1.8887 | 1.8887 | 0.42296 | 0.69212 | 0.94846 | 1.1407 | 1.1407 | 1.1407 | 1.9434 | 2.5079 | 2.8777 | 3.0724 | 3.4617 | 3.851 | 0.8345 | 1.647 | 1.9764 | 1.9764 | 1.9764 | 1.9764 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-12-20 09:00 | Summer | 0.87642 | 1.2543 | 1.81 | 1.81 | 1.81 | 1.81 | 0.48584 | 0.79501 | 1.0895 | 1.3103 | 1.3103 | 1.3103 | 2.1148 | 2.7291 | 3.1316 | 3.3435 | 3.7671 | 4.1908 | 0.89166 | 1.7599 | 2.1118 | 2.1118 | 2.1118 | 2.1118 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-12-20 10:00 | Summer | 0.87642 | 1.2543 | 1.81 | 1.81 | 1.81 | 1.81 | 0.50298 | 0.82306 | 1.1279 | 1.3565 | 1.3565 | 1.3565 | 2.1529 | 2.7783 | 3.1881 | 3.4037 | 3.835 | 4.2663 | 0.85736 | 1.6922 | 2.0306 | 2.0306 | 2.0306 | 2.0306 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-12-20 11:00 | Summer | 0.89547 | 1.2816 | 1.8493 | 1.8493 | 1.8493 | 1.8493 | 0.46012 | 0.75292 | 1.0318 | 1.2409 | 1.2409 | 1.2409 | 2.191 | 2.8275 | 3.2445 | 3.4639 | 3.9029 | 4.3418 | 0.84974 | 1.6771 | 2.0125 | 2.0125 | 2.0125 | 2.0125 | 0.64779 | 0.75355 | 0.75355 | 0.75355 | 0.75355 | 0.75355
2020-12-20 12:00 | Summer | 0.85737 | 1.227 | 1.7706 | 1.7706 | 1.7706 | 1.7706 | 0.54585 | 0.89321 | 1.224 | 1.4721 | 1.4721 | 1.4721 | 2.2863 | 2.9504 | 3.3855 | 3.6146 | 4.0726 | 4.5306 | 0.78115 | 1.5417 | 1.8501 | 1.8501 | 1.8501 | 1.8501 | 0.59063 | 0.68706 | 0.68706 | 0.68706 | 0.68706 | 0.68706
2020-12-20 13:00 | Summer | 0.81926 | 1.1725 | 1.692 | 1.692 | 1.692 | 1.692 | 0.57157 | 0.9353 | 1.2817 | 1.5415 | 1.5415 | 1.5415 | 2.2291 | 2.8767 | 3.3009 | 3.5242 | 3.9708 | 4.4173 | 0.78496 | 1.5493 | 1.8591 | 1.8591 | 1.8591 | 1.8591 | 0.56934 | 0.66229 | 0.66229 | 0.66229 | 0.66229 | 0.66229
2020-12-20 14:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.64016 | 1.0475 | 1.4355 | 1.7265 | 1.7265 | 1.7265 | 2.2291 | 2.8767 | 3.3009 | 3.5242 | 3.9708 | 4.4173 | 0.77353 | 1.5267 | 1.832 | 1.832 | 1.832 | 1.832 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-12-20 15:00 | Summer | 0.91452 | 1.3088 | 1.8887 | 1.8887 | 1.8887 | 1.8887 | 0.61158 | 1.0008 | 1.3714 | 1.6494 | 1.6494 | 1.6494 | 2.3244 | 2.9996 | 3.442 | 3.6748 | 4.1404 | 4.6061 | 0.85355 | 1.6846 | 2.0216 | 2.0216 | 2.0216 | 2.0216 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-12-20 16:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.60873 | 0.9961 | 1.365 | 1.6417 | 1.6417 | 1.6417 | 2.4006 | 3.098 | 3.5548 | 3.7953 | 4.2762 | 4.7571 | 0.88023 | 1.7373 | 2.0847 | 2.0847 | 2.0847 | 2.0847 | 0.52346 | 0.60892 | 0.60892 | 0.60892 | 0.60892 | 0.60892
2020-12-20 17:00 | Summer | 1.105 | 1.5815 | 2.2822 | 2.2822 | 2.2822 | 2.2822 | 0.62587 | 1.0242 | 1.4035 | 1.688 | 1.688 | 1.688 | 2.4006 | 3.098 | 3.5548 | 3.7953 | 4.2762 | 4.7571 | 0.87642 | 1.7298 | 2.0757 | 2.0757 | 2.0757 | 2.0757 | 0.53347 | 0.62057 | 0.62057 | 0.62057 | 0.62057 | 0.62057
2020-12-20 18:00 | Summer | 1.1813 | 1.6906 | 2.4396 | 2.4396 | 2.4396 | 2.4396 | 0.5287 | 0.86515 | 1.1856 | 1.4259 | 1.4259 | 1.4259 | 2.2101 | 2.8521 | 3.2727 | 3.4941 | 3.9368 | 4.3796 | 0.9069 | 1.7899 | 2.1479 | 2.1479 | 2.1479 | 2.1479 | 0.53347 | 0.62057 | 0.62057 | 0.62057 | 0.62057 | 0.62057
2020-12-20 19:00 | Summer | 1.1187 | 1.6011 | 2.3104 | 2.3104 | 2.3104 | 2.3104 | 0.54585 | 0.89321 | 1.224 | 1.4721 | 1.4721 | 1.4721 | 2.1111 | 2.7243 | 3.1261 | 3.3376 | 3.7605 | 4.1834 | 0.83831 | 1.6546 | 1.9855 | 1.9855 | 1.9855 | 1.9855 | 0.55252 | 0.64273 | 0.64273 | 0.64273 | 0.64273 | 0.64273
2020-12-20 20:00 | Summer | 1.086 | 1.5542 | 2.2428 | 2.2428 | 2.2428 | 2.2428 | 0.51442 | 0.84177 | 1.1535 | 1.3874 | 1.3874 | 1.3874 | 2.058 | 2.6558 | 3.0474 | 3.2536 | 3.6659 | 4.0781 | 0.86117 | 1.6997 | 2.0396 | 2.0396 | 2.0396 | 2.0396 | 0.53347 | 0.62057 | 0.62057 | 0.62057 | 0.62057 | 0.62057
2020-12-20 21:00 | Summer | 1.086 | 1.5542 | 2.2428 | 2.2428 | 2.2428 | 2.2428 | 0.51727 | 0.84645 | 1.1599 | 1.3951 | 1.3951 | 1.3951 | 2.0005 | 2.5816 | 2.9624 | 3.1627 | 3.5635 | 3.9643 | 0.91833 | 1.8125 | 2.175 | 2.175 | 2.175 | 2.175 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-12-20 22:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.40296 | 0.65939 | 0.9036 | 1.0868 | 1.0868 | 1.0868 | 1.9624 | 2.5325 | 2.9059 | 3.1025 | 3.4956 | 3.8887 | 0.86117 | 1.6997 | 2.0396 | 2.0396 | 2.0396 | 2.0396 | 0.49624 | 0.57725 | 0.57725 | 0.57725 | 0.57725 | 0.57725
2020-12-20 23:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.44297 | 0.72486 | 0.99332 | 1.1947 | 1.1947 | 1.1947 | 1.7909 | 2.3112 | 2.652 | 2.8314 | 3.1902 | 3.549 | 0.75448 | 1.4891 | 1.7869 | 1.7869 | 1.7869 | 1.7869 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-12-21 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.42868 | 0.70147 | 0.96128 | 1.1561 | 1.1561 | 1.1561 | 1.6576 | 2.1391 | 2.4545 | 2.6205 | 2.9526 | 3.2847 | 0.73543 | 1.4515 | 1.7418 | 1.7418 | 1.7418 | 1.7418 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-12-21 01:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.41439 | 0.67809 | 0.92924 | 1.1176 | 1.1176 | 1.1176 | 1.6576 | 2.1391 | 2.4545 | 2.6205 | 2.9526 | 3.2847 | 0.70494 | 1.3913 | 1.6696 | 1.6696 | 1.6696 | 1.6696 | 0.45722 | 0.53187 | 0.53187 | 0.53187 | 0.53187 | 0.53187
2020-12-21 02:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.44868 | 0.73421 | 1.0061 | 1.2101 | 1.2101 | 1.2101 | 1.6195 | 2.0899 | 2.3981 | 2.5603 | 2.8847 | 3.2092 | 0.6998 | 1.3812 | 1.6574 | 1.6574 | 1.6574 | 1.6574 | 0.47536 | 0.55297 | 0.55297 | 0.55297 | 0.55297 | 0.55297
2020-12-21 03:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.53156 | 0.86983 | 1.192 | 1.4336 | 1.4336 | 1.4336 | 1.6195 | 2.0899 | 2.3981 | 2.5603 | 2.8847 | 3.2092 | 0.70113 | 1.3838 | 1.6606 | 1.6606 | 1.6606 | 1.6606 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-12-21 04:00 | Summer | 1.2374 | 1.7709 | 2.5555 | 2.5555 | 2.5555 | 2.5555 | 0.53728 | 0.87918 | 1.2048 | 1.449 | 1.449 | 1.449 | 1.6043 | 2.0703 | 2.3756 | 2.5363 | 2.8577 | 3.179 | 0.67065 | 1.3236 | 1.5884 | 1.5884 | 1.5884 | 1.5884 | 0.55252 | 0.64273 | 0.64273 | 0.64273 | 0.64273 | 0.64273
2020-12-21 05:00 | Summer | 1.4099 | 2.0178 | 2.9117 | 2.9117 | 2.9117 | 2.9117 | 0.53728 | 0.87918 | 1.2048 | 1.449 | 1.449 | 1.449 | 1.6957 | 2.1882 | 2.5109 | 2.6808 | 3.0205 | 3.3602 | 0.78877 | 1.5568 | 1.8681 | 1.8681 | 1.8681 | 1.8681 | 0.58928 | 0.68549 | 0.68549 | 0.68549 | 0.68549 | 0.68549
2020-12-21 06:00 | Summer | 1.4418 | 2.0635 | 2.9777 | 2.9777 | 2.9777 | 2.9777 | 0.6716 | 1.099 | 1.506 | 1.8113 | 1.8113 | 1.8113 | 1.9053 | 2.4587 | 2.8213 | 3.0121 | 3.3938 | 3.7755 | 0.83069 | 1.6395 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.77173 | 0.89773 | 0.89773 | 0.89773 | 0.89773 | 0.89773
2020-12-21 07:00 | Summer | 2.0767 | 2.9721 | 4.2889 | 4.2889 | 4.2889 | 4.2889 | 0.68303 | 1.1177 | 1.5316 | 1.8421 | 1.8421 | 1.8421 | 2.172 | 2.8029 | 3.2163 | 3.4338 | 3.8689 | 4.3041 | 0.95383 | 1.8826 | 2.2591 | 2.2591 | 2.2591 | 2.2591 | 1.086 | 1.2633 | 1.2633 | 1.2633 | 1.2633 | 1.2633
2020-12-21 08:00 | Summer | 2.3188 | 3.3186 | 4.7888 | 4.7888 | 4.7888 | 4.7888 | 0.84593 | 1.3842 | 1.8969 | 2.2814 | 2.2814 | 2.2814 | 2.4578 | 3.1717 | 3.6395 | 3.8856 | 4.378 | 4.8704 | 0.95644 | 1.8877 | 2.2652 | 2.2652 | 2.2652 | 2.2652 | 1.2003 | 1.3963 | 1.3963 | 1.3963 | 1.3963 | 1.3963
2020-12-21 09:00 | Summer | 2.4768 | 3.5447 | 5.1152 | 5.1152 | 5.1152 | 5.1152 | 0.79163 | 1.2954 | 1.7752 | 2.135 | 2.135 | 2.135 | 2.534 | 3.2701 | 3.7523 | 4.0061 | 4.5138 | 5.0214 | 1.0746 | 2.1208 | 2.545 | 2.545 | 2.545 | 2.545 | 1.2956 | 1.5071 | 1.5071 | 1.5071 | 1.5071 | 1.5071
2020-12-21 10:00 | Summer | 2.4959 | 3.572 | 5.1545 | 5.1545 | 5.1545 | 5.1545 | 0.82021 | 1.3422 | 1.8393 | 2.2121 | 2.2121 | 2.2121 | 2.7046 | 3.4902 | 4.0049 | 4.2759 | 4.8177 | 5.3595 | 0.9793 | 1.9328 | 2.3194 | 2.3194 | 2.3194 | 2.3194 | 1.3908 | 1.6179 | 1.6179 | 1.6179 | 1.6179 | 1.6179
2020-12-21 11:00 | Summer | 2.5911 | 3.7083 | 5.3513 | 5.3513 | 5.3513 | 5.3513 | 0.89166 | 1.4591 | 1.9995 | 2.4048 | 2.4048 | 2.4048 | 2.7436 | 3.5405 | 4.0627 | 4.3375 | 4.8871 | 5.4367 | 0.9793 | 1.9328 | 2.3194 | 2.3194 | 2.3194 | 2.3194 | 1.4289 | 1.6622 | 1.6622 | 1.6622 | 1.6622 | 1.6622
2020-12-21 12:00 | Summer | 2.6473 | 3.7887 | 5.4673 | 5.4673 | 5.4673 | 5.4673 | 0.9088 | 1.4871 | 2.0379 | 2.451 | 2.451 | 2.451 | 2.8769 | 3.7126 | 4.2601 | 4.5483 | 5.1246 | 5.701 | 0.96025 | 1.8952 | 2.2743 | 2.2743 | 2.2743 | 2.2743 | 1.3337 | 1.5514 | 1.5514 | 1.5514 | 1.5514 | 1.5514
2020-12-21 13:00 | Summer | 2.6483 | 3.7901 | 5.4693 | 5.4693 | 5.4693 | 5.4693 | 0.92595 | 1.5152 | 2.0764 | 2.4973 | 2.4973 | 2.4973 | 2.8388 | 3.6634 | 4.2037 | 4.4881 | 5.0568 | 5.6255 | 0.96025 | 1.8952 | 2.2743 | 2.2743 | 2.2743 | 2.2743 | 1.3908 | 1.6179 | 1.6179 | 1.6179 | 1.6179 | 1.6179
2020-12-21 14:00 | Summer | 2.6674 | 3.8174 | 5.5087 | 5.5087 | 5.5087 | 5.5087 | 0.93167 | 1.5245 | 2.0892 | 2.5127 | 2.5127 | 2.5127 | 2.8198 | 3.6389 | 4.1755 | 4.4579 | 5.0228 | 5.5877 | 0.97168 | 1.9178 | 2.3013 | 2.3013 | 2.3013 | 2.3013 | 1.3128 | 1.5271 | 1.5271 | 1.5271 | 1.5271 | 1.5271
2020-12-21 15:00 | Summer | 2.6293 | 3.7629 | 5.43 | 5.43 | 5.43 | 5.43 | 0.90309 | 1.4778 | 2.0251 | 2.4356 | 2.4356 | 2.4356 | 2.7055 | 3.4913 | 4.0062 | 4.2772 | 4.8192 | 5.3612 | 0.93738 | 1.8501 | 2.2201 | 2.2201 | 2.2201 | 2.2201 | 1.2575 | 1.4628 | 1.4628 | 1.4628 | 1.4628 | 1.4628
2020-12-21 16:00 | Summer | 2.5011 | 3.5794 | 5.1653 | 5.1653 | 5.1653 | 5.1653 | 0.82592 | 1.3515 | 1.8521 | 2.2275 | 2.2275 | 2.2275 | 2.7055 | 3.4913 | 4.0062 | 4.2772 | 4.8192 | 5.3612 | 0.95263 | 1.8802 | 2.2562 | 2.2562 | 2.2562 | 2.2562 | 1.2003 | 1.3963 | 1.3963 | 1.3963 | 1.3963 | 1.3963
2020-12-21 17:00 | Summer | 2.1916 | 3.1366 | 4.5262 | 4.5262 | 4.5262 | 4.5262 | 0.76877 | 1.258 | 1.7239 | 2.0733 | 2.0733 | 2.0733 | 2.4387 | 3.1471 | 3.6112 | 3.8555 | 4.3441 | 4.8326 | 0.92595 | 1.8275 | 2.193 | 2.193 | 2.193 | 2.193 | 1.1241 | 1.3076 | 1.3076 | 1.3076 | 1.3076 | 1.3076
2020-12-21 18:00 | Summer | 1.5688 | 2.2451 | 3.2398 | 3.2398 | 3.2398 | 3.2398 | 0.57202 | 0.93604 | 1.2827 | 1.5427 | 1.5427 | 1.5427 | 2.2291 | 2.8767 | 3.3009 | 3.5242 | 3.9708 | 4.4173 | 0.90309 | 1.7824 | 2.1389 | 2.1389 | 2.1389 | 2.1389 | 0.83928 | 0.9763 | 0.9763 | 0.9763 | 0.9763 | 0.9763
2020-12-21 19:00 | Summer | 1.1422 | 1.6347 | 2.3589 | 2.3589 | 2.3589 | 2.3589 | 0.54585 | 0.89321 | 1.224 | 1.4721 | 1.4721 | 1.4721 | 2.0115 | 2.5959 | 2.9787 | 3.1802 | 3.5831 | 3.9861 | 0.85736 | 1.6922 | 2.0306 | 2.0306 | 2.0306 | 2.0306 | 0.57707 | 0.67129 | 0.67129 | 0.67129 | 0.67129 | 0.67129
2020-12-21 20:00 | Summer | 1.0673 | 1.5275 | 2.2043 | 2.2043 | 2.2043 | 2.2043 | 0.53442 | 0.87451 | 1.1984 | 1.4413 | 1.4413 | 1.4413 | 1.9053 | 2.4587 | 2.8213 | 3.0121 | 3.3938 | 3.7755 | 0.90731 | 1.7908 | 2.1489 | 2.1489 | 2.1489 | 2.1489 | 0.57158 | 0.6649 | 0.6649 | 0.6649 | 0.6649 | 0.6649
2020-12-21 21:00 | Summer | 1.0669 | 1.527 | 2.2035 | 2.2035 | 2.2035 | 2.2035 | 0.57443 | 0.93998 | 1.2881 | 1.5492 | 1.5492 | 1.5492 | 1.9243 | 2.4833 | 2.8495 | 3.0422 | 3.4277 | 3.8132 | 0.92214 | 1.82 | 2.184 | 2.184 | 2.184 | 2.184 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-12-21 22:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.46583 | 0.76227 | 1.0446 | 1.2563 | 1.2563 | 1.2563 | 1.81 | 2.3358 | 2.6802 | 2.8615 | 3.2241 | 3.5867 | 0.80783 | 1.5944 | 1.9133 | 1.9133 | 1.9133 | 1.9133 | 0.46224 | 0.53771 | 0.53771 | 0.53771 | 0.53771 | 0.53771
2020-12-21 23:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.4001 | 0.65471 | 0.89719 | 1.0791 | 1.0791 | 1.0791 | 1.7338 | 2.2374 | 2.5674 | 2.741 | 3.0884 | 3.4357 | 0.88404 | 1.7448 | 2.0938 | 2.0938 | 2.0938 | 2.0938 | 0.43821 | 0.50975 | 0.50975 | 0.50975 | 0.50975 | 0.50975
2020-12-22 | Summer | 0.92908 | 1.3297 | 1.9187 | 1.9187 | 1.9187 | 1.9187 | 0.42582 | 0.6968 | 0.95487 | 1.1484 | 1.1484 | 1.1484 | 1.6004 | 2.0653 | 2.3699 | 2.5302 | 2.8508 | 3.1714 | 0.72018 | 1.4214 | 1.7057 | 1.7057 | 1.7057 | 1.7057 | 0.43821 | 0.50975 | 0.50975 | 0.50975 | 0.50975 | 0.50975
2020-12-22 01:00 | Summer | 0.91452 | 1.3088 | 1.8887 | 1.8887 | 1.8887 | 1.8887 | 0.4001 | 0.65471 | 0.89719 | 1.0791 | 1.0791 | 1.0791 | 1.5242 | 1.967 | 2.257 | 2.4097 | 2.715 | 3.0204 | 0.66303 | 1.3086 | 1.5703 | 1.5703 | 1.5703 | 1.5703 | 0.41935 | 0.48782 | 0.48782 | 0.48782 | 0.48782 | 0.48782
2020-12-22 02:00 | Summer | 0.93232 | 1.3343 | 1.9254 | 1.9254 | 1.9254 | 1.9254 | 0.41439 | 0.67809 | 0.92924 | 1.1176 | 1.1176 | 1.1176 | 1.5242 | 1.967 | 2.257 | 2.4097 | 2.715 | 3.0204 | 0.61313 | 1.2101 | 1.4521 | 1.4521 | 1.4521 | 1.4521 | 0.41282 | 0.48022 | 0.48022 | 0.48022 | 0.48022 | 0.48022
2020-12-22 03:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.39438 | 0.64536 | 0.88438 | 1.0636 | 1.0636 | 1.0636 | 1.5258 | 1.969 | 2.2594 | 2.4123 | 2.7179 | 3.0236 | 0.68589 | 1.3537 | 1.6245 | 1.6245 | 1.6245 | 1.6245 | 0.40648 | 0.47284 | 0.47284 | 0.47284 | 0.47284 | 0.47284
2020-12-22 04:00 | Summer | 1.0454 | 1.4961 | 2.159 | 2.159 | 2.159 | 2.159 | 0.40582 | 0.66406 | 0.91001 | 1.0945 | 1.0945 | 1.0945 | 1.5623 | 2.0161 | 2.3135 | 2.4699 | 2.7829 | 3.0959 | 0.72018 | 1.4214 | 1.7057 | 1.7057 | 1.7057 | 1.7057 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-12-22 05:00 | Summer | 1.2003 | 1.7178 | 2.4789 | 2.4789 | 2.4789 | 2.4789 | 0.47155 | 0.77162 | 1.0574 | 1.2717 | 1.2717 | 1.2717 | 1.6385 | 2.1145 | 2.4263 | 2.5904 | 2.9187 | 3.2469 | 0.77353 | 1.5267 | 1.832 | 1.832 | 1.832 | 1.832 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-12-22 06:00 | Summer | 1.2765 | 1.8269 | 2.6363 | 2.6363 | 2.6363 | 2.6363 | 0.60015 | 0.98207 | 1.3458 | 1.6186 | 1.6186 | 1.6186 | 1.7909 | 2.3112 | 2.652 | 2.8314 | 3.1902 | 3.549 | 0.81164 | 1.6019 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 0.69959 | 0.81381 | 0.81381 | 0.81381 | 0.81381 | 0.81381
2020-12-22 07:00 | Summer | 1.9243 | 2.754 | 3.9741 | 3.9741 | 3.9741 | 3.9741 | 0.74019 | 1.2112 | 1.6598 | 1.9963 | 1.9963 | 1.9963 | 2.0386 | 2.6308 | 3.0188 | 3.223 | 3.6314 | 4.0398 | 1.0784 | 2.1284 | 2.554 | 2.554 | 2.554 | 2.554 | 0.85737 | 0.99734 | 0.99734 | 0.99734 | 0.99734 | 0.99734
2020-12-22 08:00 | Summer | 2.0005 | 2.8631 | 4.1315 | 4.1315 | 4.1315 | 4.1315 | 0.74305 | 1.2159 | 1.6662 | 2.004 | 2.004 | 2.004 | 2.3625 | 3.0488 | 3.4984 | 3.735 | 4.2083 | 4.6816 | 1.0555 | 2.0832 | 2.4999 | 2.4999 | 2.4999 | 2.4999 | 1.086 | 1.2633 | 1.2633 | 1.2633 | 1.2633 | 1.2633
2020-12-22 09:00 | Summer | 2.2503 | 3.2206 | 4.6475 | 4.6475 | 4.6475 | 4.6475 | 0.86879 | 1.4217 | 1.9482 | 2.3431 | 2.3431 | 2.3431 | 2.4197 | 3.1225 | 3.583 | 3.8254 | 4.3101 | 4.7949 | 1.0288 | 2.0306 | 2.4367 | 2.4367 | 2.4367 | 2.4367 | 1.086 | 1.2633 | 1.2633 | 1.2633 | 1.2633 | 1.2633
2020-12-22 10:00 | Summer | 2.3435 | 3.3539 | 4.8398 | 4.8398 | 4.8398 | 4.8398 | 0.90595 | 1.4825 | 2.0315 | 2.4433 | 2.4433 | 2.4433 | 2.4959 | 3.2209 | 3.6959 | 3.9459 | 4.4459 | 4.9459 | 0.89166 | 1.7599 | 2.1118 | 2.1118 | 2.1118 | 2.1118 | 1.2384 | 1.4406 | 1.4406 | 1.4406 | 1.4406 | 1.4406
2020-12-22 11:00 | Summer | 2.3054 | 3.2993 | 4.7611 | 4.7611 | 4.7611 | 4.7611 | 0.93738 | 1.5339 | 2.102 | 2.5281 | 2.5281 | 2.5281 | 2.4578 | 3.1717 | 3.6395 | 3.8856 | 4.378 | 4.8704 | 0.9793 | 1.9328 | 2.3194 | 2.3194 | 2.3194 | 2.3194 | 1.2384 | 1.4406 | 1.4406 | 1.4406 | 1.4406 | 1.4406
2020-12-22 12:00 | Summer | 2.2101 | 3.163 | 4.5643 | 4.5643 | 4.5643 | 4.5643 | 0.87737 | 1.4357 | 1.9674 | 2.3662 | 2.3662 | 2.3662 | 2.4768 | 3.1963 | 3.6677 | 3.9158 | 4.4119 | 4.9081 | 0.96406 | 1.9027 | 2.2833 | 2.2833 | 2.2833 | 2.2833 | 1.2954 | 1.5069 | 1.5069 | 1.5069 | 1.5069 | 1.5069
2020-12-22 13:00 | Summer | 2.2863 | 3.2721 | 4.7217 | 4.7217 | 4.7217 | 4.7217 | 0.93167 | 1.5245 | 2.0892 | 2.5127 | 2.5127 | 2.5127 | 2.6674 | 3.4422 | 3.9498 | 4.217 | 4.7513 | 5.2857 | 0.9793 | 1.9328 | 2.3194 | 2.3194 | 2.3194 | 2.3194 | 1.2956 | 1.5071 | 1.5071 | 1.5071 | 1.5071 | 1.5071
2020-12-22 14:00 | Summer | 2.3054 | 3.2993 | 4.7611 | 4.7611 | 4.7611 | 4.7611 | 0.86879 | 1.4217 | 1.9482 | 2.3431 | 2.3431 | 2.3431 | 2.5721 | 3.3192 | 3.8087 | 4.0664 | 4.5816 | 5.0969 | 0.93357 | 1.8426 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 1.1622 | 1.352 | 1.352 | 1.352 | 1.352 | 1.352
2020-12-22 15:00 | Summer | 2.2673 | 3.2448 | 4.6824 | 4.6824 | 4.6824 | 4.6824 | 0.79449 | 1.3001 | 1.7816 | 2.1427 | 2.1427 | 2.1427 | 2.6102 | 3.3684 | 3.8652 | 4.1266 | 4.6495 | 5.1724 | 1.0326 | 2.0381 | 2.4457 | 2.4457 | 2.4457 | 2.4457 | 1.1622 | 1.352 | 1.352 | 1.352 | 1.352 | 1.352
2020-12-22 16:00 | Summer | 2.2673 | 3.2448 | 4.6824 | 4.6824 | 4.6824 | 4.6824 | 0.84879 | 1.3889 | 1.9033 | 2.2892 | 2.2892 | 2.2892 | 2.6293 | 3.393 | 3.8934 | 4.1567 | 4.6835 | 5.2102 | 0.94119 | 1.8576 | 2.2291 | 2.2291 | 2.2291 | 2.2291 | 1.1241 | 1.3076 | 1.3076 | 1.3076 | 1.3076 | 1.3076
2020-12-22 17:00 | Summer | 2.1834 | 3.1248 | 4.5092 | 4.5092 | 4.5092 | 4.5092 | 0.79735 | 1.3047 | 1.788 | 2.1504 | 2.1504 | 2.1504 | 2.4902 | 3.2136 | 3.6875 | 3.937 | 4.4358 | 4.9347 | 0.92214 | 1.82 | 2.184 | 2.184 | 2.184 | 2.184 | 1.105 | 1.2855 | 1.2855 | 1.2855 | 1.2855 | 1.2855
2020-12-22 18:00 | Summer | 1.5161 | 2.1698 | 3.1312 | 3.1312 | 3.1312 | 3.1312 | 0.64016 | 1.0475 | 1.4355 | 1.7265 | 1.7265 | 1.7265 | 2.2519 | 2.906 | 3.3345 | 3.5601 | 4.0112 | 4.4623 | 0.87642 | 1.7298 | 2.0757 | 2.0757 | 2.0757 | 2.0757 | 0.81984 | 0.95369 | 0.95369 | 0.95369 | 0.95369 | 0.95369
2020-12-22 19:00 | Summer | 1.0671 | 1.5272 | 2.2037 | 2.2037 | 2.2037 | 2.2037 | 0.55728 | 0.91192 | 1.2497 | 1.503 | 1.503 | 1.503 | 2.0951 | 2.7037 | 3.1024 | 3.3122 | 3.7319 | 4.1516 | 0.80021 | 1.5794 | 1.8952 | 1.8952 | 1.8952 | 1.8952 | 0.60975 | 0.7093 | 0.7093 | 0.7093 | 0.7093 | 0.7093
2020-12-22 20:00 | Summer | 1.0479 | 1.4997 | 2.1641 | 2.1641 | 2.1641 | 2.1641 | 0.48298 | 0.79033 | 1.083 | 1.3026 | 1.3026 | 1.3026 | 1.8481 | 2.3849 | 2.7366 | 2.9218 | 3.292 | 3.6622 | 0.73543 | 1.4515 | 1.7418 | 1.7418 | 1.7418 | 1.7418 | 0.55252 | 0.64273 | 0.64273 | 0.64273 | 0.64273 | 0.64273
2020-12-22 21:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.46869 | 0.76695 | 1.051 | 1.264 | 1.264 | 1.264 | 1.8481 | 2.3849 | 2.7366 | 2.9218 | 3.292 | 3.6622 | 0.88023 | 1.7373 | 2.0847 | 2.0847 | 2.0847 | 2.0847 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-12-22 22:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.41153 | 0.67342 | 0.92283 | 1.1099 | 1.1099 | 1.1099 | 1.7338 | 2.2374 | 2.5674 | 2.741 | 3.0884 | 3.4357 | 0.72018 | 1.4214 | 1.7057 | 1.7057 | 1.7057 | 1.7057 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-12-22 23:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.34294 | 0.56118 | 0.76902 | 0.92491 | 0.92491 | 0.92491 | 1.6195 | 2.0899 | 2.3981 | 2.5603 | 2.8847 | 3.2092 | 0.59825 | 1.1808 | 1.4169 | 1.4169 | 1.4169 | 1.4169 | 0.43835 | 0.50992 | 0.50992 | 0.50992 | 0.50992 | 0.50992
2020-12-23 | Summer | 0.93024 | 1.3313 | 1.9211 | 1.9211 | 1.9211 | 1.9211 | 0.41725 | 0.68277 | 0.93565 | 1.1253 | 1.1253 | 1.1253 | 1.5242 | 1.967 | 2.257 | 2.4097 | 2.715 | 3.0204 | 0.58682 | 1.1582 | 1.3898 | 1.3898 | 1.3898 | 1.3898 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-12-23 01:00 | Summer | 0.89547 | 1.2816 | 1.8493 | 1.8493 | 1.8493 | 1.8493 | 0.44583 | 0.72953 | 0.99973 | 1.2024 | 1.2024 | 1.2024 | 1.4861 | 1.9178 | 2.2006 | 2.3495 | 2.6472 | 2.9449 | 0.5792 | 1.1431 | 1.3718 | 1.3718 | 1.3718 | 1.3718 | 0.41513 | 0.48291 | 0.48291 | 0.48291 | 0.48291 | 0.48291
2020-12-23 02:00 | Summer | 0.89547 | 1.2816 | 1.8493 | 1.8493 | 1.8493 | 1.8493 | 0.37724 | 0.6173 | 0.84593 | 1.0174 | 1.0174 | 1.0174 | 1.467 | 1.8932 | 2.1724 | 2.3193 | 2.6132 | 2.9071 | 0.49918 | 0.98521 | 1.1823 | 1.1823 | 1.1823 | 1.1823 | 0.41916 | 0.48759 | 0.48759 | 0.48759 | 0.48759 | 0.48759
2020-12-23 03:00 | Summer | 0.89547 | 1.2816 | 1.8493 | 1.8493 | 1.8493 | 1.8493 | 0.44583 | 0.72953 | 0.99973 | 1.2024 | 1.2024 | 1.2024 | 1.4544 | 1.8768 | 2.1536 | 2.2993 | 2.5907 | 2.882 | 0.59444 | 1.1732 | 1.4079 | 1.4079 | 1.4079 | 1.4079 | 0.45715 | 0.53179 | 0.53179 | 0.53179 | 0.53179 | 0.53179
2020-12-23 04:00 | Summer | 0.99491 | 1.4239 | 2.0547 | 2.0547 | 2.0547 | 2.0547 | 0.50013 | 0.81839 | 1.1215 | 1.3488 | 1.3488 | 1.3488 | 1.5336 | 1.979 | 2.2709 | 2.4245 | 2.7317 | 3.0389 | 0.77353 | 1.5267 | 1.832 | 1.832 | 1.832 | 1.832 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-12-23 05:00 | Summer | 1.086 | 1.5542 | 2.2428 | 2.2428 | 2.2428 | 2.2428 | 0.48012 | 0.78565 | 1.0766 | 1.2949 | 1.2949 | 1.2949 | 1.6195 | 2.0899 | 2.3981 | 2.5603 | 2.8847 | 3.2092 | 0.59444 | 1.1732 | 1.4079 | 1.4079 | 1.4079 | 1.4079 | 0.53234 | 0.61925 | 0.61925 | 0.61925 | 0.61925 | 0.61925
2020-12-23 06:00 | Summer | 1.1925 | 1.7067 | 2.4628 | 2.4628 | 2.4628 | 2.4628 | 0.55728 | 0.91192 | 1.2497 | 1.503 | 1.503 | 1.503 | 1.7528 | 2.262 | 2.5956 | 2.7712 | 3.1223 | 3.4734 | 0.67827 | 1.3387 | 1.6064 | 1.6064 | 1.6064 | 1.6064 | 0.7027 | 0.81743 | 0.81743 | 0.81743 | 0.81743 | 0.81743
2020-12-23 07:00 | Summer | 1.6719 | 2.3927 | 3.4528 | 3.4528 | 3.4528 | 3.4528 | 0.66588 | 1.0896 | 1.4932 | 1.7959 | 1.7959 | 1.7959 | 2.0386 | 2.6308 | 3.0188 | 3.223 | 3.6314 | 4.0398 | 1.0326 | 2.0381 | 2.4457 | 2.4457 | 2.4457 | 2.4457 | 0.89326 | 1.0391 | 1.0391 | 1.0391 | 1.0391 | 1.0391
2020-12-23 08:00 | Summer | 2.1149 | 3.0267 | 4.3677 | 4.3677 | 4.3677 | 4.3677 | 0.75162 | 1.2299 | 1.6855 | 2.0271 | 2.0271 | 2.0271 | 2.3625 | 3.0488 | 3.4984 | 3.735 | 4.2083 | 4.6816 | 0.95263 | 1.8802 | 2.2562 | 2.2562 | 2.2562 | 2.2562 | 1.0479 | 1.219 | 1.219 | 1.219 | 1.219 | 1.219
2020-12-23 09:00 | Summer | 2.1339 | 3.0539 | 4.4069 | 4.4069 | 4.4069 | 4.4069 | 0.7459 | 1.2206 | 1.6726 | 2.0117 | 2.0117 | 2.0117 | 2.4768 | 3.1963 | 3.6677 | 3.9158 | 4.4119 | 4.9081 | 0.91071 | 1.7975 | 2.1569 | 2.1569 | 2.1569 | 2.1569 | 1.093 | 1.2715 | 1.2715 | 1.2715 | 1.2715 | 1.2715
2020-12-23 10:00 | Summer | 2.172 | 3.1085 | 4.4856 | 4.4856 | 4.4856 | 4.4856 | 0.79449 | 1.3001 | 1.7816 | 2.1427 | 2.1427 | 2.1427 | 2.4959 | 3.2209 | 3.6959 | 3.9459 | 4.4459 | 4.9459 | 0.89547 | 1.7674 | 2.1208 | 2.1208 | 2.1208 | 2.1208 | 1.1432 | 1.3298 | 1.3298 | 1.3298 | 1.3298 | 1.3298
2020-12-23 11:00 | Summer | 2.2101 | 3.163 | 4.5643 | 4.5643 | 4.5643 | 4.5643 | 0.73733 | 1.2065 | 1.6534 | 1.9886 | 1.9886 | 1.9886 | 2.4768 | 3.1963 | 3.6677 | 3.9158 | 4.4119 | 4.9081 | 0.99073 | 1.9554 | 2.3465 | 2.3465 | 2.3465 | 2.3465 | 1.2194 | 1.4184 | 1.4184 | 1.4184 | 1.4184 | 1.4184
2020-12-23 12:00 | Summer | 2.2673 | 3.2448 | 4.6824 | 4.6824 | 4.6824 | 4.6824 | 0.89737 | 1.4684 | 2.0123 | 2.4202 | 2.4202 | 2.4202 | 2.554 | 3.2958 | 3.7819 | 4.0377 | 4.5493 | 5.0609 | 0.95063 | 1.8762 | 2.2515 | 2.2515 | 2.2515 | 2.2515 | 1.2575 | 1.4628 | 1.4628 | 1.4628 | 1.4628 | 1.4628
2020-12-23 13:00 | Summer | 2.2673 | 3.2448 | 4.6824 | 4.6824 | 4.6824 | 4.6824 | 0.86308 | 1.4123 | 1.9354 | 2.3277 | 2.3277 | 2.3277 | 2.5721 | 3.3192 | 3.8087 | 4.0664 | 4.5816 | 5.0969 | 0.99835 | 1.9704 | 2.3645 | 2.3645 | 2.3645 | 2.3645 | 1.2384 | 1.4406 | 1.4406 | 1.4406 | 1.4406 | 1.4406
2020-12-23 14:00 | Summer | 2.2673 | 3.2448 | 4.6824 | 4.6824 | 4.6824 | 4.6824 | 0.84021 | 1.3749 | 1.8841 | 2.266 | 2.266 | 2.266 | 2.7233 | 3.5144 | 4.0326 | 4.3054 | 4.851 | 5.3965 | 0.97549 | 1.9253 | 2.3104 | 2.3104 | 2.3104 | 2.3104 | 1.2384 | 1.4406 | 1.4406 | 1.4406 | 1.4406 | 1.4406
2020-12-23 15:00 | Summer | 2.3435 | 3.3539 | 4.8398 | 4.8398 | 4.8398 | 4.8398 | 0.89166 | 1.4591 | 1.9995 | 2.4048 | 2.4048 | 2.4048 | 2.8198 | 3.6389 | 4.1755 | 4.4579 | 5.0228 | 5.5877 | 1.0288 | 2.0306 | 2.4367 | 2.4367 | 2.4367 | 2.4367 | 1.1432 | 1.3298 | 1.3298 | 1.3298 | 1.3298 | 1.3298
2020-12-23 16:00 | Summer | 2.2673 | 3.2448 | 4.6824 | 4.6824 | 4.6824 | 4.6824 | 0.89451 | 1.4638 | 2.0059 | 2.4125 | 2.4125 | 2.4125 | 2.7055 | 3.4913 | 4.0062 | 4.2772 | 4.8192 | 5.3612 | 0.89547 | 1.7674 | 2.1208 | 2.1208 | 2.1208 | 2.1208 | 1.1241 | 1.3076 | 1.3076 | 1.3076 | 1.3076 | 1.3076
2020-12-23 17:00 | Summer | 2.1398 | 3.0623 | 4.4191 | 4.4191 | 4.4191 | 4.4191 | 0.84307 | 1.3796 | 1.8905 | 2.2737 | 2.2737 | 2.2737 | 2.5346 | 3.2709 | 3.7532 | 4.0071 | 4.5149 | 5.0226 | 0.80783 | 1.5944 | 1.9133 | 1.9133 | 1.9133 | 1.9133 | 1.086 | 1.2633 | 1.2633 | 1.2633 | 1.2633 | 1.2633
2020-12-23 18:00 | Summer | 1.4541 | 2.0811 | 3.0031 | 3.0031 | 3.0031 | 3.0031 | 0.64739 | 1.0594 | 1.4517 | 1.746 | 1.746 | 1.746 | 2.4387 | 3.1471 | 3.6112 | 3.8555 | 4.3441 | 4.8326 | 0.78877 | 1.5568 | 1.8681 | 1.8681 | 1.8681 | 1.8681 | 0.93402 | 1.0865 | 1.0865 | 1.0865 | 1.0865 | 1.0865
2020-12-23 19:00 | Summer | 1.0875 | 1.5564 | 2.2459 | 2.2459 | 2.2459 | 2.2459 | 0.52299 | 0.8558 | 1.1728 | 1.4105 | 1.4105 | 1.4105 | 2.1725 | 2.8035 | 3.217 | 3.4346 | 3.8698 | 4.305 | 0.79258 | 1.5643 | 1.8772 | 1.8772 | 1.8772 | 1.8772 | 0.66684 | 0.77571 | 0.77571 | 0.77571 | 0.77571 | 0.77571
2020-12-23 20:00 | Summer | 1.0479 | 1.4997 | 2.1641 | 2.1641 | 2.1641 | 2.1641 | 0.47726 | 0.78098 | 1.0702 | 1.2872 | 1.2872 | 1.2872 | 2.0196 | 2.6062 | 2.9906 | 3.1929 | 3.5974 | 4.002 | 0.80783 | 1.5944 | 1.9133 | 1.9133 | 1.9133 | 1.9133 | 0.57158 | 0.6649 | 0.6649 | 0.6649 | 0.6649 | 0.6649
2020-12-23 21:00 | Summer | 1.0373 | 1.4846 | 2.1423 | 2.1423 | 2.1423 | 2.1423 | 0.46012 | 0.75292 | 1.0318 | 1.2409 | 1.2409 | 1.2409 | 1.9624 | 2.5325 | 2.9059 | 3.1025 | 3.4956 | 3.8887 | 0.84593 | 1.6696 | 2.0035 | 2.0035 | 2.0035 | 2.0035 | 0.59063 | 0.68706 | 0.68706 | 0.68706 | 0.68706 | 0.68706
2020-12-23 22:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.42582 | 0.6968 | 0.95487 | 1.1484 | 1.1484 | 1.1484 | 1.8672 | 2.4095 | 2.7649 | 2.9519 | 3.3259 | 3.7 | 0.71637 | 1.4139 | 1.6967 | 1.6967 | 1.6967 | 1.6967 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-12-23 23:00 | Summer | 0.95592 | 1.3681 | 1.9742 | 1.9742 | 1.9742 | 1.9742 | 0.42582 | 0.6968 | 0.95487 | 1.1484 | 1.1484 | 1.1484 | 1.7338 | 2.2374 | 2.5674 | 2.741 | 3.0884 | 3.4357 | 0.66303 | 1.3086 | 1.5703 | 1.5703 | 1.5703 | 1.5703 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-12-24 | Summer | 0.91452 | 1.3088 | 1.8887 | 1.8887 | 1.8887 | 1.8887 | 0.47155 | 0.77162 | 1.0574 | 1.2717 | 1.2717 | 1.2717 | 1.5818 | 2.0413 | 2.3423 | 2.5007 | 2.8176 | 3.1345 | 0.73543 | 1.4515 | 1.7418 | 1.7418 | 1.7418 | 1.7418 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-12-24 01:00 | Summer | 0.91152 | 1.3045 | 1.8825 | 1.8825 | 1.8825 | 1.8825 | 0.44297 | 0.72486 | 0.99332 | 1.1947 | 1.1947 | 1.1947 | 1.5486 | 1.9984 | 2.2932 | 2.4483 | 2.7585 | 3.0687 | 0.60587 | 1.1958 | 1.435 | 1.435 | 1.435 | 1.435 | 0.43821 | 0.50975 | 0.50975 | 0.50975 | 0.50975 | 0.50975
2020-12-24 02:00 | Summer | 0.91452 | 1.3088 | 1.8887 | 1.8887 | 1.8887 | 1.8887 | 0.42582 | 0.6968 | 0.95487 | 1.1484 | 1.1484 | 1.1484 | 1.5623 | 2.0161 | 2.3135 | 2.4699 | 2.7829 | 3.0959 | 0.57157 | 1.1281 | 1.3537 | 1.3537 | 1.3537 | 1.3537 | 0.41916 | 0.48759 | 0.48759 | 0.48759 | 0.48759 | 0.48759
2020-12-24 03:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.46297 | 0.75759 | 1.0382 | 1.2486 | 1.2486 | 1.2486 | 1.5052 | 1.9424 | 2.2288 | 2.3796 | 2.6811 | 2.9826 | 0.59063 | 1.1657 | 1.3989 | 1.3989 | 1.3989 | 1.3989 | 0.41916 | 0.48759 | 0.48759 | 0.48759 | 0.48759 | 0.48759
2020-12-24 04:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.40296 | 0.65939 | 0.9036 | 1.0868 | 1.0868 | 1.0868 | 1.5052 | 1.9424 | 2.2288 | 2.3796 | 2.6811 | 2.9826 | 0.54378 | 1.0733 | 1.2879 | 1.2879 | 1.2879 | 1.2879 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-12-24 05:00 | Summer | 1.105 | 1.5815 | 2.2822 | 2.2822 | 2.2822 | 2.2822 | 0.43725 | 0.7155 | 0.98051 | 1.1793 | 1.1793 | 1.1793 | 1.6004 | 2.0653 | 2.3699 | 2.5302 | 2.8508 | 3.1714 | 0.63635 | 1.256 | 1.5072 | 1.5072 | 1.5072 | 1.5072 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-12-24 06:00 | Summer | 1.2034 | 1.7223 | 2.4853 | 2.4853 | 2.4853 | 2.4853 | 0.64588 | 1.0569 | 1.4483 | 1.7419 | 1.7419 | 1.7419 | 1.7147 | 2.2128 | 2.5392 | 2.7109 | 3.0544 | 3.3979 | 0.6516 | 1.286 | 1.5433 | 1.5433 | 1.5433 | 1.5433 | 0.67843 | 0.7892 | 0.7892 | 0.7892 | 0.7892 | 0.7892
2020-12-24 07:00 | Summer | 1.7355 | 2.4838 | 3.5842 | 3.5842 | 3.5842 | 3.5842 | 0.6373 | 1.0429 | 1.4291 | 1.7188 | 1.7188 | 1.7188 | 2.0425 | 2.6358 | 3.0245 | 3.2291 | 3.6382 | 4.0474 | 0.86498 | 1.7072 | 2.0486 | 2.0486 | 2.0486 | 2.0486 | 0.84126 | 0.9786 | 0.9786 | 0.9786 | 0.9786 | 0.9786
2020-12-24 08:00 | Summer | 2.172 | 3.1085 | 4.4856 | 4.4856 | 4.4856 | 4.4856 | 0.70018 | 1.1457 | 1.5701 | 1.8884 | 1.8884 | 1.8884 | 2.3816 | 3.0734 | 3.5266 | 3.7652 | 4.2423 | 4.7194 | 0.89166 | 1.7599 | 2.1118 | 2.1118 | 2.1118 | 2.1118 | 1.0669 | 1.2411 | 1.2411 | 1.2411 | 1.2411 | 1.2411
2020-12-24 09:00 | Summer | 2.3054 | 3.2993 | 4.7611 | 4.7611 | 4.7611 | 4.7611 | 0.73447 | 1.2019 | 1.647 | 1.9808 | 1.9808 | 1.9808 | 2.4387 | 3.1471 | 3.6112 | 3.8555 | 4.3441 | 4.8326 | 0.91833 | 1.8125 | 2.175 | 2.175 | 2.175 | 2.175 | 1.0742 | 1.2496 | 1.2496 | 1.2496 | 1.2496 | 1.2496
2020-12-24 10:00 | Summer | 2.2113 | 3.1647 | 4.5668 | 4.5668 | 4.5668 | 4.5668 | 0.71733 | 1.1738 | 1.6085 | 1.9346 | 1.9346 | 1.9346 | 2.4197 | 3.1225 | 3.583 | 3.8254 | 4.3101 | 4.7949 | 1.0174 | 2.008 | 2.4096 | 2.4096 | 2.4096 | 2.4096 | 1.1241 | 1.3076 | 1.3076 | 1.3076 | 1.3076 | 1.3076
2020-12-24 11:00 | Summer | 2.3054 | 3.2993 | 4.7611 | 4.7611 | 4.7611 | 4.7611 | 0.81735 | 1.3375 | 1.8328 | 2.2044 | 2.2044 | 2.2044 | 2.6293 | 3.393 | 3.8934 | 4.1567 | 4.6835 | 5.2102 | 0.94119 | 1.8576 | 2.2291 | 2.2291 | 2.2291 | 2.2291 | 1.1241 | 1.3076 | 1.3076 | 1.3076 | 1.3076 | 1.3076
2020-12-24 12:00 | Summer | 2.2101 | 3.163 | 4.5643 | 4.5643 | 4.5643 | 4.5643 | 0.84307 | 1.3796 | 1.8905 | 2.2737 | 2.2737 | 2.2737 | 2.7055 | 3.4913 | 4.0062 | 4.2772 | 4.8192 | 5.3612 | 0.93738 | 1.8501 | 2.2201 | 2.2201 | 2.2201 | 2.2201 | 1.105 | 1.2855 | 1.2855 | 1.2855 | 1.2855 | 1.2855
2020-12-24 13:00 | Summer | 2.172 | 3.1085 | 4.4856 | 4.4856 | 4.4856 | 4.4856 | 0.83164 | 1.3609 | 1.8649 | 2.2429 | 2.2429 | 2.2429 | 2.6674 | 3.4422 | 3.9498 | 4.217 | 4.7513 | 5.2857 | 0.96406 | 1.9027 | 2.2833 | 2.2833 | 2.2833 | 2.2833 | 1.0669 | 1.2411 | 1.2411 | 1.2411 | 1.2411 | 1.2411
2020-12-24 14:00 | Summer | 1.9624 | 2.8085 | 4.0528 | 4.0528 | 4.0528 | 4.0528 | 0.81164 | 1.3281 | 1.82 | 2.189 | 2.189 | 2.189 | 2.7245 | 3.5159 | 4.0344 | 4.3073 | 4.8531 | 5.3989 | 0.91452 | 1.805 | 2.166 | 2.166 | 2.166 | 2.166 | 1.0669 | 1.2411 | 1.2411 | 1.2411 | 1.2411 | 1.2411
2020-12-24 15:00 | Summer | 1.9624 | 2.8085 | 4.0528 | 4.0528 | 4.0528 | 4.0528 | 0.82307 | 1.3468 | 1.8457 | 2.2198 | 2.2198 | 2.2198 | 2.7436 | 3.5405 | 4.0627 | 4.3375 | 4.8871 | 5.4367 | 0.88785 | 1.7523 | 2.1028 | 2.1028 | 2.1028 | 2.1028 | 1.0669 | 1.2411 | 1.2411 | 1.2411 | 1.2411 | 1.2411
2020-12-24 16:00 | Summer | 1.9815 | 2.8358 | 4.0922 | 4.0922 | 4.0922 | 4.0922 | 0.88594 | 1.4497 | 1.9867 | 2.3894 | 2.3894 | 2.3894 | 2.6483 | 3.4176 | 3.9216 | 4.1869 | 4.7174 | 5.2479 | 0.92595 | 1.8275 | 2.193 | 2.193 | 2.193 | 2.193 | 1.0288 | 1.1968 | 1.1968 | 1.1968 | 1.1968 | 1.1968
2020-12-24 17:00 | Summer | 1.9624 | 2.8085 | 4.0528 | 4.0528 | 4.0528 | 4.0528 | 0.74384 | 1.2172 | 1.668 | 2.0061 | 2.0061 | 2.0061 | 2.6674 | 3.4422 | 3.9498 | 4.217 | 4.7513 | 5.2857 | 0.83069 | 1.6395 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 1.0288 | 1.1968 | 1.1968 | 1.1968 | 1.1968 | 1.1968
2020-12-24 18:00 | Summer | 1.4928 | 2.1364 | 3.0829 | 3.0829 | 3.0829 | 3.0829 | 0.72683 | 1.1894 | 1.6299 | 1.9602 | 1.9602 | 1.9602 | 2.4959 | 3.2209 | 3.6959 | 3.9459 | 4.4459 | 4.9459 | 0.84974 | 1.6771 | 2.0125 | 2.0125 | 2.0125 | 2.0125 | 0.76508 | 0.88999 | 0.88999 | 0.88999 | 0.88999 | 0.88999
2020-12-24 19:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.50298 | 0.82306 | 1.1279 | 1.3565 | 1.3565 | 1.3565 | 2.2495 | 2.903 | 3.3311 | 3.5564 | 4.0071 | 4.4577 | 0.81926 | 1.617 | 1.9403 | 1.9403 | 1.9403 | 1.9403 | 0.58463 | 0.68008 | 0.68008 | 0.68008 | 0.68008 | 0.68008
2020-12-24 20:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.53728 | 0.87918 | 1.2048 | 1.449 | 1.449 | 1.449 | 1.9434 | 2.5079 | 2.8777 | 3.0724 | 3.4617 | 3.851 | 0.81164 | 1.6019 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 0.55252 | 0.64273 | 0.64273 | 0.64273 | 0.64273 | 0.64273
2020-12-24 21:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.42951 | 0.70283 | 0.96314 | 1.1584 | 1.1584 | 1.1584 | 1.8672 | 2.4095 | 2.7649 | 2.9519 | 3.3259 | 3.7 | 0.79258 | 1.5643 | 1.8772 | 1.8772 | 1.8772 | 1.8772 | 0.49539 | 0.57627 | 0.57627 | 0.57627 | 0.57627 | 0.57627
2020-12-24 22:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.46583 | 0.76227 | 1.0446 | 1.2563 | 1.2563 | 1.2563 | 1.7799 | 2.297 | 2.6357 | 2.814 | 3.1706 | 3.5271 | 0.78115 | 1.5417 | 1.8501 | 1.8501 | 1.8501 | 1.8501 | 0.49389 | 0.57452 | 0.57452 | 0.57452 | 0.57452 | 0.57452
2020-12-24 23:00 | Summer | 0.94581 | 1.3536 | 1.9533 | 1.9533 | 1.9533 | 1.9533 | 0.43439 | 0.71083 | 0.9741 | 1.1715 | 1.1715 | 1.1715 | 1.7147 | 2.2128 | 2.5392 | 2.7109 | 3.0544 | 3.3979 | 0.73543 | 1.4515 | 1.7418 | 1.7418 | 1.7418 | 1.7418 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-12-25 | Summer | 0.89547 | 1.2816 | 1.8493 | 1.8493 | 1.8493 | 1.8493 | 0.42011 | 0.68744 | 0.94205 | 1.133 | 1.133 | 1.133 | 1.6385 | 2.1145 | 2.4263 | 2.5904 | 2.9187 | 3.2469 | 0.62111 | 1.2259 | 1.4711 | 1.4711 | 1.4711 | 1.4711 | 0.43821 | 0.50975 | 0.50975 | 0.50975 | 0.50975 | 0.50975
2020-12-25 01:00 | Summer | 0.91452 | 1.3088 | 1.8887 | 1.8887 | 1.8887 | 1.8887 | 0.41175 | 0.67377 | 0.92332 | 1.1105 | 1.1105 | 1.1105 | 1.5433 | 1.9915 | 2.2852 | 2.4398 | 2.749 | 3.0581 | 0.60587 | 1.1958 | 1.435 | 1.435 | 1.435 | 1.435 | 0.41916 | 0.48759 | 0.48759 | 0.48759 | 0.48759 | 0.48759
2020-12-25 02:00 | Summer | 0.89547 | 1.2816 | 1.8493 | 1.8493 | 1.8493 | 1.8493 | 0.44011 | 0.72018 | 0.98691 | 1.187 | 1.187 | 1.187 | 1.5433 | 1.9915 | 2.2852 | 2.4398 | 2.749 | 3.0581 | 0.49918 | 0.98521 | 1.1823 | 1.1823 | 1.1823 | 1.1823 | 0.4169 | 0.48496 | 0.48496 | 0.48496 | 0.48496 | 0.48496
2020-12-25 03:00 | Summer | 0.87642 | 1.2543 | 1.81 | 1.81 | 1.81 | 1.81 | 0.48869 | 0.79968 | 1.0959 | 1.318 | 1.318 | 1.318 | 1.5242 | 1.967 | 2.257 | 2.4097 | 2.715 | 3.0204 | 0.59063 | 1.1657 | 1.3989 | 1.3989 | 1.3989 | 1.3989 | 0.41916 | 0.48759 | 0.48759 | 0.48759 | 0.48759 | 0.48759
2020-12-25 04:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.46012 | 0.75292 | 1.0318 | 1.2409 | 1.2409 | 1.2409 | 1.543 | 1.9912 | 2.2849 | 2.4395 | 2.7486 | 3.0577 | 0.59063 | 1.1657 | 1.3989 | 1.3989 | 1.3989 | 1.3989 | 0.40984 | 0.47676 | 0.47676 | 0.47676 | 0.47676 | 0.47676
2020-12-25 05:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.42969 | 0.70312 | 0.96354 | 1.1589 | 1.1589 | 1.1589 | 1.5814 | 2.0407 | 2.3417 | 2.5001 | 2.8169 | 3.1337 | 0.56014 | 1.1055 | 1.3267 | 1.3267 | 1.3267 | 1.3267 | 0.41916 | 0.48759 | 0.48759 | 0.48759 | 0.48759 | 0.48759
2020-12-25 06:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.53442 | 0.87451 | 1.1984 | 1.4413 | 1.4413 | 1.4413 | 1.5623 | 2.0161 | 2.3135 | 2.4699 | 2.7829 | 3.0959 | 0.62873 | 1.2409 | 1.4891 | 1.4891 | 1.4891 | 1.4891 | 0.4563 | 0.5308 | 0.5308 | 0.5308 | 0.5308 | 0.5308
2020-12-25 07:00 | Summer | 1.0288 | 1.4724 | 2.1248 | 2.1248 | 2.1248 | 2.1248 | 0.52013 | 0.85112 | 1.1664 | 1.4028 | 1.4028 | 1.4028 | 1.7534 | 2.2627 | 2.5964 | 2.7721 | 3.1233 | 3.4746 | 0.84974 | 1.6771 | 2.0125 | 2.0125 | 2.0125 | 2.0125 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-12-25 08:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.54585 | 0.89321 | 1.224 | 1.4721 | 1.4721 | 1.4721 | 1.81 | 2.3358 | 2.6802 | 2.8615 | 3.2241 | 3.5867 | 0.82307 | 1.6245 | 1.9494 | 1.9494 | 1.9494 | 1.9494 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-12-25 09:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.48298 | 0.79033 | 1.083 | 1.3026 | 1.3026 | 1.3026 | 1.9625 | 2.5326 | 2.9061 | 3.1027 | 3.4958 | 3.889 | 0.87261 | 1.7222 | 2.0667 | 2.0667 | 2.0667 | 2.0667 | 0.49899 | 0.58046 | 0.58046 | 0.58046 | 0.58046 | 0.58046
2020-12-25 10:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.52585 | 0.86048 | 1.1792 | 1.4182 | 1.4182 | 1.4182 | 2.0386 | 2.6308 | 3.0188 | 3.223 | 3.6314 | 4.0398 | 0.88404 | 1.7448 | 2.0938 | 2.0938 | 2.0938 | 2.0938 | 0.53347 | 0.62057 | 0.62057 | 0.62057 | 0.62057 | 0.62057
2020-12-25 11:00 | Summer | 0.91481 | 1.3092 | 1.8893 | 1.8893 | 1.8893 | 1.8893 | 0.51442 | 0.84177 | 1.1535 | 1.3874 | 1.3874 | 1.3874 | 2.0577 | 2.6554 | 3.047 | 3.2531 | 3.6653 | 4.0775 | 0.88404 | 1.7448 | 2.0938 | 2.0938 | 2.0938 | 2.0938 | 0.53347 | 0.62057 | 0.62057 | 0.62057 | 0.62057 | 0.62057
2020-12-25 12:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.52585 | 0.86048 | 1.1792 | 1.4182 | 1.4182 | 1.4182 | 2.0767 | 2.68 | 3.0752 | 3.2832 | 3.6992 | 4.1153 | 0.83069 | 1.6395 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.55228 | 0.64245 | 0.64245 | 0.64245 | 0.64245 | 0.64245
2020-12-25 13:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.48298 | 0.79033 | 1.083 | 1.3026 | 1.3026 | 1.3026 | 2.0577 | 2.6554 | 3.047 | 3.2531 | 3.6653 | 4.0775 | 0.91071 | 1.7975 | 2.1569 | 2.1569 | 2.1569 | 2.1569 | 0.59063 | 0.68706 | 0.68706 | 0.68706 | 0.68706 | 0.68706
2020-12-25 14:00 | Summer | 1.0479 | 1.4997 | 2.1641 | 2.1641 | 2.1641 | 2.1641 | 0.52013 | 0.85112 | 1.1664 | 1.4028 | 1.4028 | 1.4028 | 2.0767 | 2.68 | 3.0752 | 3.2832 | 3.6992 | 4.1153 | 0.89547 | 1.7674 | 2.1208 | 2.1208 | 2.1208 | 2.1208 | 0.57158 | 0.6649 | 0.6649 | 0.6649 | 0.6649 | 0.6649
2020-12-25 15:00 | Summer | 1.0229 | 1.4639 | 2.1125 | 2.1125 | 2.1125 | 2.1125 | 0.48466 | 0.79308 | 1.0868 | 1.3071 | 1.3071 | 1.3071 | 2.0386 | 2.6308 | 3.0188 | 3.223 | 3.6314 | 4.0398 | 0.85355 | 1.6846 | 2.0216 | 2.0216 | 2.0216 | 2.0216 | 0.55252 | 0.64273 | 0.64273 | 0.64273 | 0.64273 | 0.64273
2020-12-25 16:00 | Summer | 1.0479 | 1.4997 | 2.1641 | 2.1641 | 2.1641 | 2.1641 | 0.49155 | 0.80436 | 1.1023 | 1.3257 | 1.3257 | 1.3257 | 2.0577 | 2.6554 | 3.047 | 3.2531 | 3.6653 | 4.0775 | 0.93738 | 1.8501 | 2.2201 | 2.2201 | 2.2201 | 2.2201 | 0.57158 | 0.6649 | 0.6649 | 0.6649 | 0.6649 | 0.6649
2020-12-25 17:00 | Summer | 1.086 | 1.5542 | 2.2428 | 2.2428 | 2.2428 | 2.2428 | 0.46869 | 0.76695 | 1.051 | 1.264 | 1.264 | 1.264 | 2.0423 | 2.6356 | 3.0243 | 3.2288 | 3.638 | 4.0471 | 0.88023 | 1.7373 | 2.0847 | 2.0847 | 2.0847 | 2.0847 | 0.57158 | 0.6649 | 0.6649 | 0.6649 | 0.6649 | 0.6649
2020-12-25 18:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.47726 | 0.78098 | 1.0702 | 1.2872 | 1.2872 | 1.2872 | 1.9624 | 2.5325 | 2.9059 | 3.1025 | 3.4956 | 3.8887 | 0.74686 | 1.4741 | 1.7689 | 1.7689 | 1.7689 | 1.7689 | 0.44293 | 0.51525 | 0.51525 | 0.51525 | 0.51525 | 0.51525
2020-12-25 19:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.42582 | 0.6968 | 0.95487 | 1.1484 | 1.1484 | 1.1484 | 1.81 | 2.3358 | 2.6802 | 2.8615 | 3.2241 | 3.5867 | 0.69351 | 1.3688 | 1.6425 | 1.6425 | 1.6425 | 1.6425 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-12-25 20:00 | Summer | 0.93352 | 1.336 | 1.9279 | 1.9279 | 1.9279 | 1.9279 | 0.42296 | 0.69212 | 0.94846 | 1.1407 | 1.1407 | 1.1407 | 1.7528 | 2.262 | 2.5956 | 2.7712 | 3.1223 | 3.4734 | 0.78115 | 1.5417 | 1.8501 | 1.8501 | 1.8501 | 1.8501 | 0.41916 | 0.48759 | 0.48759 | 0.48759 | 0.48759 | 0.48759
2020-12-25 21:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.47726 | 0.78098 | 1.0702 | 1.2872 | 1.2872 | 1.2872 | 1.7528 | 2.262 | 2.5956 | 2.7712 | 3.1223 | 3.4734 | 0.67827 | 1.3387 | 1.6064 | 1.6064 | 1.6064 | 1.6064 | 0.41911 | 0.48754 | 0.48754 | 0.48754 | 0.48754 | 0.48754
2020-12-25 22:00 | Summer | 0.89547 | 1.2816 | 1.8493 | 1.8493 | 1.8493 | 1.8493 | 0.47726 | 0.78098 | 1.0702 | 1.2872 | 1.2872 | 1.2872 | 1.7719 | 2.2866 | 2.6238 | 2.8013 | 3.1562 | 3.5112 | 0.69351 | 1.3688 | 1.6425 | 1.6425 | 1.6425 | 1.6425 | 0.43821 | 0.50975 | 0.50975 | 0.50975 | 0.50975 | 0.50975
2020-12-25 23:00 | Summer | 0.89386 | 1.2793 | 1.846 | 1.846 | 1.846 | 1.846 | 0.50584 | 0.82774 | 1.1343 | 1.3642 | 1.3642 | 1.3642 | 1.6195 | 2.0899 | 2.3981 | 2.5603 | 2.8847 | 3.2092 | 0.65922 | 1.3011 | 1.5613 | 1.5613 | 1.5613 | 1.5613 | 0.41916 | 0.48759 | 0.48759 | 0.48759 | 0.48759 | 0.48759
2020-12-26 | Summer | 0.89547 | 1.2816 | 1.8493 | 1.8493 | 1.8493 | 1.8493 | 0.5087 | 0.83242 | 1.1407 | 1.3719 | 1.3719 | 1.3719 | 1.6385 | 2.1145 | 2.4263 | 2.5904 | 2.9187 | 3.2469 | 0.59825 | 1.1808 | 1.4169 | 1.4169 | 1.4169 | 1.4169 | 0.43821 | 0.50975 | 0.50975 | 0.50975 | 0.50975 | 0.50975
2020-12-26 01:00 | Summer | 0.89547 | 1.2816 | 1.8493 | 1.8493 | 1.8493 | 1.8493 | 0.41439 | 0.67809 | 0.92924 | 1.1176 | 1.1176 | 1.1176 | 1.5814 | 2.0407 | 2.3417 | 2.5001 | 2.8169 | 3.1337 | 0.59825 | 1.1808 | 1.4169 | 1.4169 | 1.4169 | 1.4169 | 0.4001 | 0.46543 | 0.46543 | 0.46543 | 0.46543 | 0.46543
2020-12-26 02:00 | Summer | 0.89547 | 1.2816 | 1.8493 | 1.8493 | 1.8493 | 1.8493 | 0.42269 | 0.69168 | 0.94786 | 1.14 | 1.14 | 1.14 | 1.5433 | 1.9915 | 2.2852 | 2.4398 | 2.749 | 3.0581 | 0.49536 | 0.97769 | 1.1732 | 1.1732 | 1.1732 | 1.1732 | 0.4001 | 0.46543 | 0.46543 | 0.46543 | 0.46543 | 0.46543
2020-12-26 03:00 | Summer | 0.87642 | 1.2543 | 1.81 | 1.81 | 1.81 | 1.81 | 0.42296 | 0.69212 | 0.94846 | 1.1407 | 1.1407 | 1.1407 | 1.5242 | 1.967 | 2.257 | 2.4097 | 2.715 | 3.0204 | 0.5792 | 1.1431 | 1.3718 | 1.3718 | 1.3718 | 1.3718 | 0.39981 | 0.46508 | 0.46508 | 0.46508 | 0.46508 | 0.46508
2020-12-26 04:00 | Summer | 0.89547 | 1.2816 | 1.8493 | 1.8493 | 1.8493 | 1.8493 | 0.39438 | 0.64536 | 0.88438 | 1.0636 | 1.0636 | 1.0636 | 1.5433 | 1.9915 | 2.2852 | 2.4398 | 2.749 | 3.0581 | 0.57157 | 1.1281 | 1.3537 | 1.3537 | 1.3537 | 1.3537 | 0.41916 | 0.48759 | 0.48759 | 0.48759 | 0.48759 | 0.48759
2020-12-26 05:00 | Summer | 0.89547 | 1.2816 | 1.8493 | 1.8493 | 1.8493 | 1.8493 | 0.44868 | 0.73421 | 1.0061 | 1.2101 | 1.2101 | 1.2101 | 1.6385 | 2.1145 | 2.4263 | 2.5904 | 2.9187 | 3.2469 | 0.5792 | 1.1431 | 1.3718 | 1.3718 | 1.3718 | 1.3718 | 0.40039 | 0.46576 | 0.46576 | 0.46576 | 0.46576 | 0.46576
2020-12-26 06:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.39724 | 0.65003 | 0.89079 | 1.0713 | 1.0713 | 1.0713 | 1.5242 | 1.967 | 2.257 | 2.4097 | 2.715 | 3.0204 | 0.67065 | 1.3236 | 1.5884 | 1.5884 | 1.5884 | 1.5884 | 0.41916 | 0.48759 | 0.48759 | 0.48759 | 0.48759 | 0.48759
2020-12-26 07:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.45154 | 0.73889 | 1.0125 | 1.2178 | 1.2178 | 1.2178 | 1.6766 | 2.1636 | 2.4827 | 2.6507 | 2.9865 | 3.3224 | 0.66303 | 1.3086 | 1.5703 | 1.5703 | 1.5703 | 1.5703 | 0.43821 | 0.50975 | 0.50975 | 0.50975 | 0.50975 | 0.50975
2020-12-26 08:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.4544 | 0.74356 | 1.019 | 1.2255 | 1.2255 | 1.2255 | 1.7528 | 2.262 | 2.5956 | 2.7712 | 3.1223 | 3.4734 | 0.6897 | 1.3613 | 1.6335 | 1.6335 | 1.6335 | 1.6335 | 0.43821 | 0.50975 | 0.50975 | 0.50975 | 0.50975 | 0.50975
2020-12-26 09:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.41725 | 0.68277 | 0.93565 | 1.1253 | 1.1253 | 1.1253 | 1.8672 | 2.4095 | 2.7649 | 2.9519 | 3.3259 | 3.7 | 0.77734 | 1.5342 | 1.8411 | 1.8411 | 1.8411 | 1.8411 | 0.41916 | 0.48759 | 0.48759 | 0.48759 | 0.48759 | 0.48759
2020-12-26 10:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.43439 | 0.71083 | 0.9741 | 1.1715 | 1.1715 | 1.1715 | 1.8862 | 2.4341 | 2.7931 | 2.982 | 3.3599 | 3.7377 | 0.75829 | 1.4966 | 1.796 | 1.796 | 1.796 | 1.796 | 0.43821 | 0.50975 | 0.50975 | 0.50975 | 0.50975 | 0.50975
2020-12-26 11:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.42011 | 0.68744 | 0.94205 | 1.133 | 1.133 | 1.133 | 1.9053 | 2.4587 | 2.8213 | 3.0121 | 3.3938 | 3.7755 | 0.66684 | 1.3161 | 1.5794 | 1.5794 | 1.5794 | 1.5794 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-12-26 12:00 | Summer | 0.89547 | 1.2816 | 1.8493 | 1.8493 | 1.8493 | 1.8493 | 0.46012 | 0.75292 | 1.0318 | 1.2409 | 1.2409 | 1.2409 | 2.0196 | 2.6062 | 2.9906 | 3.1929 | 3.5974 | 4.002 | 0.75067 | 1.4816 | 1.7779 | 1.7779 | 1.7779 | 1.7779 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-12-26 13:00 | Summer | 0.89547 | 1.2816 | 1.8493 | 1.8493 | 1.8493 | 1.8493 | 0.49155 | 0.80436 | 1.1023 | 1.3257 | 1.3257 | 1.3257 | 2.1339 | 2.7537 | 3.1598 | 3.3736 | 3.8011 | 4.2285 | 0.73543 | 1.4515 | 1.7418 | 1.7418 | 1.7418 | 1.7418 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-12-26 14:00 | Summer | 0.87642 | 1.2543 | 1.81 | 1.81 | 1.81 | 1.81 | 0.4544 | 0.74356 | 1.019 | 1.2255 | 1.2255 | 1.2255 | 2.2291 | 2.8767 | 3.3009 | 3.5242 | 3.9708 | 4.4173 | 0.77353 | 1.5267 | 1.832 | 1.832 | 1.832 | 1.832 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-12-26 15:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.53728 | 0.87918 | 1.2048 | 1.449 | 1.449 | 1.449 | 2.2291 | 2.8767 | 3.3009 | 3.5242 | 3.9708 | 4.4173 | 0.74686 | 1.4741 | 1.7689 | 1.7689 | 1.7689 | 1.7689 | 0.45959 | 0.53462 | 0.53462 | 0.53462 | 0.53462 | 0.53462
2020-12-26 16:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.51442 | 0.84177 | 1.1535 | 1.3874 | 1.3874 | 1.3874 | 2.2101 | 2.8521 | 3.2727 | 3.4941 | 3.9368 | 4.3796 | 0.72781 | 1.4365 | 1.7238 | 1.7238 | 1.7238 | 1.7238 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-12-26 17:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.5087 | 0.83242 | 1.1407 | 1.3719 | 1.3719 | 1.3719 | 2.1126 | 2.7263 | 3.1284 | 3.34 | 3.7632 | 4.1864 | 0.75067 | 1.4816 | 1.7779 | 1.7779 | 1.7779 | 1.7779 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-12-26 18:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.62873 | 1.0288 | 1.4099 | 1.6957 | 1.6957 | 1.6957 | 2.1529 | 2.7783 | 3.1881 | 3.4037 | 3.835 | 4.2663 | 0.77353 | 1.5267 | 1.832 | 1.832 | 1.832 | 1.832 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-12-26 19:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.59952 | 0.98103 | 1.3444 | 1.6169 | 1.6169 | 1.6169 | 2.0196 | 2.6062 | 2.9906 | 3.1929 | 3.5974 | 4.002 | 0.75067 | 1.4816 | 1.7779 | 1.7779 | 1.7779 | 1.7779 | 0.45754 | 0.53223 | 0.53223 | 0.53223 | 0.53223 | 0.53223
2020-12-26 20:00 | Summer | 0.95764 | 1.3705 | 1.9777 | 1.9777 | 1.9777 | 1.9777 | 0.58015 | 0.94933 | 1.3009 | 1.5646 | 1.5646 | 1.5646 | 1.9053 | 2.4587 | 2.8213 | 3.0121 | 3.3938 | 3.7755 | 0.73162 | 1.444 | 1.7328 | 1.7328 | 1.7328 | 1.7328 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-12-26 21:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.52299 | 0.8558 | 1.1728 | 1.4105 | 1.4105 | 1.4105 | 1.8762 | 2.4211 | 2.7782 | 2.9661 | 3.342 | 3.7178 | 0.7964 | 1.5718 | 1.8862 | 1.8862 | 1.8862 | 1.8862 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-12-26 22:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.51156 | 0.83709 | 1.1471 | 1.3797 | 1.3797 | 1.3797 | 1.7909 | 2.3112 | 2.652 | 2.8314 | 3.1902 | 3.549 | 0.77734 | 1.5342 | 1.8411 | 1.8411 | 1.8411 | 1.8411 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-12-26 23:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.51442 | 0.84177 | 1.1535 | 1.3874 | 1.3874 | 1.3874 | 1.6766 | 2.1636 | 2.4827 | 2.6507 | 2.9865 | 3.3224 | 0.70113 | 1.3838 | 1.6606 | 1.6606 | 1.6606 | 1.6606 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-12-27 | Summer | 0.91452 | 1.3088 | 1.8887 | 1.8887 | 1.8887 | 1.8887 | 0.51442 | 0.84177 | 1.1535 | 1.3874 | 1.3874 | 1.3874 | 1.6195 | 2.0899 | 2.3981 | 2.5603 | 2.8847 | 3.2092 | 0.65541 | 1.2936 | 1.5523 | 1.5523 | 1.5523 | 1.5523 | 0.4387 | 0.51032 | 0.51032 | 0.51032 | 0.51032 | 0.51032
2020-12-27 01:00 | Summer | 0.89736 | 1.2843 | 1.8532 | 1.8532 | 1.8532 | 1.8532 | 0.5087 | 0.83242 | 1.1407 | 1.3719 | 1.3719 | 1.3719 | 1.6111 | 2.079 | 2.3857 | 2.547 | 2.8698 | 3.1925 | 0.5792 | 1.1431 | 1.3718 | 1.3718 | 1.3718 | 1.3718 | 0.41916 | 0.48759 | 0.48759 | 0.48759 | 0.48759 | 0.48759
2020-12-27 02:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.50013 | 0.81839 | 1.1215 | 1.3488 | 1.3488 | 1.3488 | 1.5814 | 2.0407 | 2.3417 | 2.5001 | 2.8169 | 3.1337 | 0.51868 | 1.0237 | 1.2284 | 1.2284 | 1.2284 | 1.2284 | 0.41916 | 0.48759 | 0.48759 | 0.48759 | 0.48759 | 0.48759
2020-12-27 03:00 | Summer | 0.91452 | 1.3088 | 1.8887 | 1.8887 | 1.8887 | 1.8887 | 0.49727 | 0.81371 | 1.1151 | 1.3411 | 1.3411 | 1.3411 | 1.5623 | 2.0161 | 2.3135 | 2.4699 | 2.7829 | 3.0959 | 0.5792 | 1.1431 | 1.3718 | 1.3718 | 1.3718 | 1.3718 | 0.41505 | 0.48282 | 0.48282 | 0.48282 | 0.48282 | 0.48282
2020-12-27 04:00 | Summer | 0.89529 | 1.2813 | 1.849 | 1.849 | 1.849 | 1.849 | 0.46869 | 0.76695 | 1.051 | 1.264 | 1.264 | 1.264 | 1.5272 | 1.9708 | 2.2615 | 2.4144 | 2.7204 | 3.0263 | 0.55252 | 1.0905 | 1.3086 | 1.3086 | 1.3086 | 1.3086 | 0.41916 | 0.48759 | 0.48759 | 0.48759 | 0.48759 | 0.48759
2020-12-27 05:00 | Summer | 0.89547 | 1.2816 | 1.8493 | 1.8493 | 1.8493 | 1.8493 | 0.42868 | 0.70147 | 0.96128 | 1.1561 | 1.1561 | 1.1561 | 1.6195 | 2.0899 | 2.3981 | 2.5603 | 2.8847 | 3.2092 | 0.49918 | 0.98521 | 1.1823 | 1.1823 | 1.1823 | 1.1823 | 0.4001 | 0.46543 | 0.46543 | 0.46543 | 0.46543 | 0.46543
2020-12-27 06:00 | Summer | 0.89547 | 1.2816 | 1.8493 | 1.8493 | 1.8493 | 1.8493 | 0.4544 | 0.74356 | 1.019 | 1.2255 | 1.2255 | 1.2255 | 1.6576 | 2.1391 | 2.4545 | 2.6205 | 2.9526 | 3.2847 | 0.64397 | 1.271 | 1.5252 | 1.5252 | 1.5252 | 1.5252 | 0.41916 | 0.48759 | 0.48759 | 0.48759 | 0.48759 | 0.48759
2020-12-27 07:00 | Summer | 0.89547 | 1.2816 | 1.8493 | 1.8493 | 1.8493 | 1.8493 | 0.47155 | 0.77162 | 1.0574 | 1.2717 | 1.2717 | 1.2717 | 1.7719 | 2.2866 | 2.6238 | 2.8013 | 3.1562 | 3.5112 | 0.82307 | 1.6245 | 1.9494 | 1.9494 | 1.9494 | 1.9494 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-12-27 08:00 | Summer | 0.83831 | 1.1998 | 1.7313 | 1.7313 | 1.7313 | 1.7313 | 0.43154 | 0.70615 | 0.96769 | 1.1638 | 1.1638 | 1.1638 | 1.9614 | 2.5312 | 2.9044 | 3.1009 | 3.4938 | 3.8868 | 0.74305 | 1.4665 | 1.7599 | 1.7599 | 1.7599 | 1.7599 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-12-27 09:00 | Summer | 0.81926 | 1.1725 | 1.692 | 1.692 | 1.692 | 1.692 | 0.48298 | 0.79033 | 1.083 | 1.3026 | 1.3026 | 1.3026 | 2.0606 | 2.6592 | 3.0513 | 3.2577 | 3.6705 | 4.0833 | 0.74686 | 1.4741 | 1.7689 | 1.7689 | 1.7689 | 1.7689 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-12-27 10:00 | Summer | 0.83831 | 1.1998 | 1.7313 | 1.7313 | 1.7313 | 1.7313 | 0.5087 | 0.83242 | 1.1407 | 1.3719 | 1.3719 | 1.3719 | 2.3054 | 2.975 | 3.4138 | 3.6447 | 4.1065 | 4.5683 | 0.74686 | 1.4741 | 1.7689 | 1.7689 | 1.7689 | 1.7689 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-12-27 11:00 | Summer | 0.83831 | 1.1998 | 1.7313 | 1.7313 | 1.7313 | 1.7313 | 0.49727 | 0.81371 | 1.1151 | 1.3411 | 1.3411 | 1.3411 | 2.2444 | 2.8964 | 3.3235 | 3.5483 | 3.9979 | 4.4475 | 0.75829 | 1.4966 | 1.796 | 1.796 | 1.796 | 1.796 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-12-27 12:00 | Summer | 0.81926 | 1.1725 | 1.692 | 1.692 | 1.692 | 1.692 | 0.58015 | 0.94933 | 1.3009 | 1.5646 | 1.5646 | 1.5646 | 2.3244 | 2.9996 | 3.442 | 3.6748 | 4.1404 | 4.6061 | 0.75067 | 1.4816 | 1.7779 | 1.7779 | 1.7779 | 1.7779 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-12-27 13:00 | Summer | 0.83831 | 1.1998 | 1.7313 | 1.7313 | 1.7313 | 1.7313 | 0.56014 | 0.9166 | 1.2561 | 1.5107 | 1.5107 | 1.5107 | 2.3844 | 3.0771 | 3.5309 | 3.7697 | 4.2474 | 4.7251 | 0.75448 | 1.4891 | 1.7869 | 1.7869 | 1.7869 | 1.7869 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-12-27 14:00 | Summer | 0.85737 | 1.227 | 1.7706 | 1.7706 | 1.7706 | 1.7706 | 0.56872 | 0.93062 | 1.2753 | 1.5338 | 1.5338 | 1.5338 | 2.4387 | 3.1471 | 3.6112 | 3.8555 | 4.3441 | 4.8326 | 0.7326 | 1.4459 | 1.7351 | 1.7351 | 1.7351 | 1.7351 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-12-27 15:00 | Summer | 0.83831 | 1.1998 | 1.7313 | 1.7313 | 1.7313 | 1.7313 | 0.58872 | 0.96336 | 1.3202 | 1.5878 | 1.5878 | 1.5878 | 2.4959 | 3.2209 | 3.6959 | 3.9459 | 4.4459 | 4.9459 | 0.7964 | 1.5718 | 1.8862 | 1.8862 | 1.8862 | 1.8862 | 0.53347 | 0.62057 | 0.62057 | 0.62057 | 0.62057 | 0.62057
2020-12-27 16:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.59444 | 0.97271 | 1.333 | 1.6032 | 1.6032 | 1.6032 | 2.4768 | 3.1963 | 3.6677 | 3.9158 | 4.4119 | 4.9081 | 0.80783 | 1.5944 | 1.9133 | 1.9133 | 1.9133 | 1.9133 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-12-27 17:00 | Summer | 1.0288 | 1.4724 | 2.1248 | 2.1248 | 2.1248 | 2.1248 | 0.62587 | 1.0242 | 1.4035 | 1.688 | 1.688 | 1.688 | 2.3538 | 3.0376 | 3.4855 | 3.7213 | 4.1929 | 4.6644 | 0.85736 | 1.6922 | 2.0306 | 2.0306 | 2.0306 | 2.0306 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-12-27 18:00 | Summer | 1.0089 | 1.4438 | 2.0835 | 2.0835 | 2.0835 | 2.0835 | 0.66588 | 1.0896 | 1.4932 | 1.7959 | 1.7959 | 1.7959 | 2.3054 | 2.975 | 3.4138 | 3.6447 | 4.1065 | 4.5683 | 0.86498 | 1.7072 | 2.0486 | 2.0486 | 2.0486 | 2.0486 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-12-27 19:00 | Summer | 1.0479 | 1.4997 | 2.1641 | 2.1641 | 2.1641 | 2.1641 | 0.6173 | 1.0101 | 1.3842 | 1.6648 | 1.6648 | 1.6648 | 2.2863 | 2.9504 | 3.3855 | 3.6146 | 4.0726 | 4.5306 | 0.81926 | 1.617 | 1.9403 | 1.9403 | 1.9403 | 1.9403 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-12-27 20:00 | Summer | 1.0669 | 1.527 | 2.2035 | 2.2035 | 2.2035 | 2.2035 | 0.60587 | 0.99142 | 1.3586 | 1.634 | 1.634 | 1.634 | 2.0767 | 2.68 | 3.0752 | 3.2832 | 3.6992 | 4.1153 | 0.8345 | 1.647 | 1.9764 | 1.9764 | 1.9764 | 1.9764 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-12-27 21:00 | Summer | 1.0288 | 1.4724 | 2.1248 | 2.1248 | 2.1248 | 2.1248 | 0.54014 | 0.88386 | 1.2112 | 1.4567 | 1.4567 | 1.4567 | 2.1148 | 2.7291 | 3.1316 | 3.3435 | 3.7671 | 4.1908 | 0.81545 | 1.6094 | 1.9313 | 1.9313 | 1.9313 | 1.9313 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-12-27 22:00 | Summer | 1.0479 | 1.4997 | 2.1641 | 2.1641 | 2.1641 | 2.1641 | 0.48012 | 0.78565 | 1.0766 | 1.2949 | 1.2949 | 1.2949 | 2.0767 | 2.68 | 3.0752 | 3.2832 | 3.6992 | 4.1153 | 0.78877 | 1.5568 | 1.8681 | 1.8681 | 1.8681 | 1.8681 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-12-27 23:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.44868 | 0.73421 | 1.0061 | 1.2101 | 1.2101 | 1.2101 | 1.8481 | 2.3849 | 2.7366 | 2.9218 | 3.292 | 3.6622 | 0.71215 | 1.4056 | 1.6867 | 1.6867 | 1.6867 | 1.6867 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-12-28 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.42296 | 0.69212 | 0.94846 | 1.1407 | 1.1407 | 1.1407 | 1.7719 | 2.2866 | 2.6238 | 2.8013 | 3.1562 | 3.5112 | 0.89547 | 1.7674 | 2.1208 | 2.1208 | 2.1208 | 2.1208 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-12-28 01:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.40582 | 0.66406 | 0.91001 | 1.0945 | 1.0945 | 1.0945 | 1.6857 | 2.1754 | 2.4962 | 2.665 | 3.0027 | 3.3404 | 0.8675 | 1.7122 | 2.0546 | 2.0546 | 2.0546 | 2.0546 | 0.43821 | 0.50975 | 0.50975 | 0.50975 | 0.50975 | 0.50975
2020-12-28 02:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.46297 | 0.75759 | 1.0382 | 1.2486 | 1.2486 | 1.2486 | 1.6957 | 2.1882 | 2.5109 | 2.6808 | 3.0205 | 3.3602 | 0.61349 | 1.2108 | 1.453 | 1.453 | 1.453 | 1.453 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-12-28 03:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.43725 | 0.7155 | 0.98051 | 1.1793 | 1.1793 | 1.1793 | 1.6385 | 2.1145 | 2.4263 | 2.5904 | 2.9187 | 3.2469 | 0.60968 | 1.2033 | 1.444 | 1.444 | 1.444 | 1.444 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-12-28 04:00 | Summer | 1.0669 | 1.527 | 2.2035 | 2.2035 | 2.2035 | 2.2035 | 0.46583 | 0.76227 | 1.0446 | 1.2563 | 1.2563 | 1.2563 | 1.6916 | 2.1829 | 2.5049 | 2.6743 | 3.0132 | 3.352 | 0.65541 | 1.2936 | 1.5523 | 1.5523 | 1.5523 | 1.5523 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-12-28 05:00 | Summer | 1.1241 | 1.6088 | 2.3215 | 2.3215 | 2.3215 | 2.3215 | 0.43439 | 0.71083 | 0.9741 | 1.1715 | 1.1715 | 1.1715 | 1.829 | 2.3603 | 2.7084 | 2.8916 | 3.2581 | 3.6245 | 0.74686 | 1.4741 | 1.7689 | 1.7689 | 1.7689 | 1.7689 | 0.49052 | 0.5706 | 0.5706 | 0.5706 | 0.5706 | 0.5706
2020-12-28 06:00 | Summer | 1.1622 | 1.6633 | 2.4002 | 2.4002 | 2.4002 | 2.4002 | 0.47441 | 0.7763 | 1.0638 | 1.2795 | 1.2795 | 1.2795 | 1.829 | 2.3603 | 2.7084 | 2.8916 | 3.2581 | 3.6245 | 0.73924 | 1.459 | 1.7508 | 1.7508 | 1.7508 | 1.7508 | 0.57146 | 0.66476 | 0.66476 | 0.66476 | 0.66476 | 0.66476
2020-12-28 07:00 | Summer | 1.5433 | 2.2086 | 3.1872 | 3.1872 | 3.1872 | 3.1872 | 0.62301 | 1.0195 | 1.3971 | 1.6803 | 1.6803 | 1.6803 | 2.0005 | 2.5816 | 2.9624 | 3.1627 | 3.5635 | 3.9643 | 0.74305 | 1.4665 | 1.7599 | 1.7599 | 1.7599 | 1.7599 | 0.78115 | 0.90869 | 0.90869 | 0.90869 | 0.90869 | 0.90869
2020-12-28 08:00 | Summer | 1.7528 | 2.5086 | 3.62 | 3.62 | 3.62 | 3.62 | 0.74305 | 1.2159 | 1.6662 | 2.004 | 2.004 | 2.004 | 2.2482 | 2.9013 | 3.3291 | 3.5543 | 4.0047 | 4.4551 | 0.78496 | 1.5493 | 1.8591 | 1.8591 | 1.8591 | 1.8591 | 0.74305 | 0.86436 | 0.86436 | 0.86436 | 0.86436 | 0.86436
2020-12-28 09:00 | Summer | 1.6385 | 2.345 | 3.3839 | 3.3839 | 3.3839 | 3.3839 | 0.71131 | 1.164 | 1.5951 | 1.9184 | 1.9184 | 1.9184 | 2.3816 | 3.0734 | 3.5266 | 3.7652 | 4.2423 | 4.7194 | 0.83069 | 1.6395 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.7621 | 0.88653 | 0.88653 | 0.88653 | 0.88653 | 0.88653
2020-12-28 10:00 | Summer | 1.6576 | 2.3723 | 3.4232 | 3.4232 | 3.4232 | 3.4232 | 0.73327 | 1.1999 | 1.6443 | 1.9776 | 1.9776 | 1.9776 | 2.543 | 3.2817 | 3.7657 | 4.0204 | 4.5298 | 5.0393 | 0.84593 | 1.6696 | 2.0035 | 2.0035 | 2.0035 | 2.0035 | 0.80021 | 0.93085 | 0.93085 | 0.93085 | 0.93085 | 0.93085
2020-12-28 11:00 | Summer | 1.6576 | 2.3723 | 3.4232 | 3.4232 | 3.4232 | 3.4232 | 0.77448 | 1.2673 | 1.7367 | 2.0888 | 2.0888 | 2.0888 | 2.6483 | 3.4176 | 3.9216 | 4.1869 | 4.7174 | 5.2479 | 0.86117 | 1.6997 | 2.0396 | 2.0396 | 2.0396 | 2.0396 | 0.78115 | 0.90869 | 0.90869 | 0.90869 | 0.90869 | 0.90869
2020-12-28 12:00 | Summer | 1.7318 | 2.4784 | 3.5764 | 3.5764 | 3.5764 | 3.5764 | 0.77448 | 1.2673 | 1.7367 | 2.0888 | 2.0888 | 2.0888 | 2.5785 | 3.3275 | 3.8182 | 4.0765 | 4.593 | 5.1096 | 0.86879 | 1.7147 | 2.0577 | 2.0577 | 2.0577 | 2.0577 | 0.78811 | 0.91678 | 0.91678 | 0.91678 | 0.91678 | 0.91678
2020-12-28 13:00 | Summer | 1.8481 | 2.6449 | 3.8167 | 3.8167 | 3.8167 | 3.8167 | 0.82592 | 1.3515 | 1.8521 | 2.2275 | 2.2275 | 2.2275 | 2.7817 | 3.5897 | 4.1191 | 4.3977 | 4.955 | 5.5122 | 0.84212 | 1.6621 | 1.9945 | 1.9945 | 1.9945 | 1.9945 | 0.80021 | 0.93085 | 0.93085 | 0.93085 | 0.93085 | 0.93085
2020-12-28 14:00 | Summer | 1.7909 | 2.5631 | 3.6987 | 3.6987 | 3.6987 | 3.6987 | 0.81164 | 1.3281 | 1.82 | 2.189 | 2.189 | 2.189 | 2.6102 | 3.3684 | 3.8652 | 4.1266 | 4.6495 | 5.1724 | 0.87642 | 1.7298 | 2.0757 | 2.0757 | 2.0757 | 2.0757 | 0.78115 | 0.90869 | 0.90869 | 0.90869 | 0.90869 | 0.90869
2020-12-28 15:00 | Summer | 1.6576 | 2.3723 | 3.4232 | 3.4232 | 3.4232 | 3.4232 | 0.78877 | 1.2907 | 1.7688 | 2.1273 | 2.1273 | 2.1273 | 2.4959 | 3.2209 | 3.6959 | 3.9459 | 4.4459 | 4.9459 | 0.82688 | 1.632 | 1.9584 | 1.9584 | 1.9584 | 1.9584 | 0.74305 | 0.86436 | 0.86436 | 0.86436 | 0.86436 | 0.86436
2020-12-28 16:00 | Summer | 1.5052 | 2.1541 | 3.1085 | 3.1085 | 3.1085 | 3.1085 | 0.69446 | 1.1364 | 1.5573 | 1.8729 | 1.8729 | 1.8729 | 2.3244 | 2.9996 | 3.442 | 3.6748 | 4.1404 | 4.6061 | 0.86498 | 1.7072 | 2.0486 | 2.0486 | 2.0486 | 2.0486 | 0.70494 | 0.82004 | 0.82004 | 0.82004 | 0.82004 | 0.82004
2020-12-28 17:00 | Summer | 1.2662 | 1.8121 | 2.6149 | 2.6149 | 2.6149 | 2.6149 | 0.60015 | 0.98207 | 1.3458 | 1.6186 | 1.6186 | 1.6186 | 2.2863 | 2.9504 | 3.3855 | 3.6146 | 4.0726 | 4.5306 | 0.92214 | 1.82 | 2.184 | 2.184 | 2.184 | 2.184 | 0.64779 | 0.75355 | 0.75355 | 0.75355 | 0.75355 | 0.75355
2020-12-28 18:00 | Summer | 1.105 | 1.5815 | 2.2822 | 2.2822 | 2.2822 | 2.2822 | 0.57157 | 0.9353 | 1.2817 | 1.5415 | 1.5415 | 1.5415 | 2.0005 | 2.5816 | 2.9624 | 3.1627 | 3.5635 | 3.9643 | 0.81164 | 1.6019 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 0.51154 | 0.59505 | 0.59505 | 0.59505 | 0.59505 | 0.59505
2020-12-28 19:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.42868 | 0.70147 | 0.96128 | 1.1561 | 1.1561 | 1.1561 | 1.8672 | 2.4095 | 2.7649 | 2.9519 | 3.3259 | 3.7 | 0.80783 | 1.5944 | 1.9133 | 1.9133 | 1.9133 | 1.9133 | 0.45265 | 0.52655 | 0.52655 | 0.52655 | 0.52655 | 0.52655
2020-12-28 20:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.46869 | 0.76695 | 1.051 | 1.264 | 1.264 | 1.264 | 1.8481 | 2.3849 | 2.7366 | 2.9218 | 3.292 | 3.6622 | 0.74305 | 1.4665 | 1.7599 | 1.7599 | 1.7599 | 1.7599 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-12-28 21:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.37438 | 0.61262 | 0.83952 | 1.0097 | 1.0097 | 1.0097 | 1.8103 | 2.3362 | 2.6807 | 2.8621 | 3.2247 | 3.5874 | 0.78877 | 1.5568 | 1.8681 | 1.8681 | 1.8681 | 1.8681 | 0.41916 | 0.48759 | 0.48759 | 0.48759 | 0.48759 | 0.48759
2020-12-28 22:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.39724 | 0.65003 | 0.89079 | 1.0713 | 1.0713 | 1.0713 | 1.7528 | 2.262 | 2.5956 | 2.7712 | 3.1223 | 3.4734 | 0.70875 | 1.3989 | 1.6786 | 1.6786 | 1.6786 | 1.6786 | 0.43821 | 0.50975 | 0.50975 | 0.50975 | 0.50975 | 0.50975
2020-12-28 23:00 | Summer | 0.89547 | 1.2816 | 1.8493 | 1.8493 | 1.8493 | 1.8493 | 0.41576 | 0.68034 | 0.93231 | 1.1213 | 1.1213 | 1.1213 | 1.6766 | 2.1636 | 2.4827 | 2.6507 | 2.9865 | 3.3224 | 0.63254 | 1.2484 | 1.4981 | 1.4981 | 1.4981 | 1.4981 | 0.39945 | 0.46467 | 0.46467 | 0.46467 | 0.46467 | 0.46467
2020-12-29 | Summer | 0.87642 | 1.2543 | 1.81 | 1.81 | 1.81 | 1.81 | 0.42011 | 0.68744 | 0.94205 | 1.133 | 1.133 | 1.133 | 1.5623 | 2.0161 | 2.3135 | 2.4699 | 2.7829 | 3.0959 | 0.6173 | 1.2184 | 1.462 | 1.462 | 1.462 | 1.462 | 0.41916 | 0.48759 | 0.48759 | 0.48759 | 0.48759 | 0.48759
2020-12-29 01:00 | Summer | 0.87629 | 1.2541 | 1.8097 | 1.8097 | 1.8097 | 1.8097 | 0.4001 | 0.65471 | 0.89719 | 1.0791 | 1.0791 | 1.0791 | 1.5052 | 1.9424 | 2.2288 | 2.3796 | 2.6811 | 2.9826 | 0.59063 | 1.1657 | 1.3989 | 1.3989 | 1.3989 | 1.3989 | 0.41916 | 0.48759 | 0.48759 | 0.48759 | 0.48759 | 0.48759
2020-12-29 02:00 | Summer | 0.89547 | 1.2816 | 1.8493 | 1.8493 | 1.8493 | 1.8493 | 0.40867 | 0.66874 | 0.91642 | 1.1022 | 1.1022 | 1.1022 | 1.4861 | 1.9178 | 2.2006 | 2.3495 | 2.6472 | 2.9449 | 0.58301 | 1.1507 | 1.3808 | 1.3808 | 1.3808 | 1.3808 | 0.43821 | 0.50975 | 0.50975 | 0.50975 | 0.50975 | 0.50975
2020-12-29 03:00 | Summer | 0.89547 | 1.2816 | 1.8493 | 1.8493 | 1.8493 | 1.8493 | 0.41153 | 0.67342 | 0.92283 | 1.1099 | 1.1099 | 1.1099 | 1.4861 | 1.9178 | 2.2006 | 2.3495 | 2.6472 | 2.9449 | 0.56776 | 1.1206 | 1.3447 | 1.3447 | 1.3447 | 1.3447 | 0.4001 | 0.46543 | 0.46543 | 0.46543 | 0.46543 | 0.46543
2020-12-29 04:00 | Summer | 1.0094 | 1.4446 | 2.0846 | 2.0846 | 2.0846 | 2.0846 | 0.42296 | 0.69212 | 0.94846 | 1.1407 | 1.1407 | 1.1407 | 1.5052 | 1.9424 | 2.2288 | 2.3796 | 2.6811 | 2.9826 | 0.57157 | 1.1281 | 1.3537 | 1.3537 | 1.3537 | 1.3537 | 0.53347 | 0.62057 | 0.62057 | 0.62057 | 0.62057 | 0.62057
2020-12-29 05:00 | Summer | 1.2765 | 1.8269 | 2.6363 | 2.6363 | 2.6363 | 2.6363 | 0.42011 | 0.68744 | 0.94205 | 1.133 | 1.133 | 1.133 | 1.6195 | 2.0899 | 2.3981 | 2.5603 | 2.8847 | 3.2092 | 0.69732 | 1.3763 | 1.6516 | 1.6516 | 1.6516 | 1.6516 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2020-12-29 06:00 | Summer | 1.2954 | 1.854 | 2.6753 | 2.6753 | 2.6753 | 2.6753 | 0.58015 | 0.94933 | 1.3009 | 1.5646 | 1.5646 | 1.5646 | 1.6004 | 2.0653 | 2.3699 | 2.5302 | 2.8508 | 3.1714 | 0.69732 | 1.3763 | 1.6516 | 1.6516 | 1.6516 | 1.6516 | 0.64779 | 0.75355 | 0.75355 | 0.75355 | 0.75355 | 0.75355
2020-12-29 07:00 | Summer | 1.448 | 2.0723 | 2.9904 | 2.9904 | 2.9904 | 2.9904 | 0.56586 | 0.92595 | 1.2689 | 1.5261 | 1.5261 | 1.5261 | 1.81 | 2.3358 | 2.6802 | 2.8615 | 3.2241 | 3.5867 | 0.89547 | 1.7674 | 2.1208 | 2.1208 | 2.1208 | 2.1208 | 0.85737 | 0.99734 | 0.99734 | 0.99734 | 0.99734 | 0.99734
2020-12-29 08:00 | Summer | 1.6004 | 2.2904 | 3.3052 | 3.3052 | 3.3052 | 3.3052 | 0.7259 | 1.1878 | 1.6278 | 1.9577 | 1.9577 | 1.9577 | 1.9624 | 2.5325 | 2.9059 | 3.1025 | 3.4956 | 3.8887 | 0.81164 | 1.6019 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 0.83831 | 0.97518 | 0.97518 | 0.97518 | 0.97518 | 0.97518
2020-12-29 09:00 | Summer | 1.5814 | 2.2632 | 3.2659 | 3.2659 | 3.2659 | 3.2659 | 0.79163 | 1.2954 | 1.7752 | 2.135 | 2.135 | 2.135 | 2.2673 | 2.9258 | 3.3573 | 3.5844 | 4.0386 | 4.4928 | 0.88785 | 1.7523 | 2.1028 | 2.1028 | 2.1028 | 2.1028 | 0.91452 | 1.0638 | 1.0638 | 1.0638 | 1.0638 | 1.0638
2020-12-29 10:00 | Summer | 1.6766 | 2.3995 | 3.4626 | 3.4626 | 3.4626 | 3.4626 | 0.73161 | 1.1972 | 1.6406 | 1.9731 | 1.9731 | 1.9731 | 2.1529 | 2.7783 | 3.1881 | 3.4037 | 3.835 | 4.2663 | 0.87261 | 1.7222 | 2.0667 | 2.0667 | 2.0667 | 2.0667 | 0.91452 | 1.0638 | 1.0638 | 1.0638 | 1.0638 | 1.0638
2020-12-29 11:00 | Summer | 1.81 | 2.5904 | 3.738 | 3.738 | 3.738 | 3.738 | 0.70589 | 1.1551 | 1.5829 | 1.9038 | 1.9038 | 1.9038 | 2.172 | 2.8029 | 3.2163 | 3.4338 | 3.8689 | 4.3041 | 1.025 | 2.0231 | 2.4277 | 2.4277 | 2.4277 | 2.4277 | 0.99073 | 1.1525 | 1.1525 | 1.1525 | 1.1525 | 1.1525
2020-12-29 12:00 | Summer | 1.829 | 2.6177 | 3.7774 | 3.7774 | 3.7774 | 3.7774 | 0.7259 | 1.1878 | 1.6278 | 1.9577 | 1.9577 | 1.9577 | 2.2101 | 2.8521 | 3.2727 | 3.4941 | 3.9368 | 4.3796 | 0.92595 | 1.8275 | 2.193 | 2.193 | 2.193 | 2.193 | 0.97168 | 1.1303 | 1.1303 | 1.1303 | 1.1303 | 1.1303
2020-12-29 13:00 | Summer | 1.829 | 2.6177 | 3.7774 | 3.7774 | 3.7774 | 3.7774 | 0.7802 | 1.2767 | 1.7495 | 2.1042 | 2.1042 | 2.1042 | 2.2101 | 2.8521 | 3.2727 | 3.4941 | 3.9368 | 4.3796 | 0.93738 | 1.8501 | 2.2201 | 2.2201 | 2.2201 | 2.2201 | 1.0479 | 1.219 | 1.219 | 1.219 | 1.219 | 1.219
2020-12-29 14:00 | Summer | 1.8672 | 2.6722 | 3.8561 | 3.8561 | 3.8561 | 3.8561 | 0.83164 | 1.3609 | 1.8649 | 2.2429 | 2.2429 | 2.2429 | 2.2673 | 2.9258 | 3.3573 | 3.5844 | 4.0386 | 4.4928 | 0.96406 | 1.9027 | 2.2833 | 2.2833 | 2.2833 | 2.2833 | 1.0288 | 1.1968 | 1.1968 | 1.1968 | 1.1968 | 1.1968
2020-12-29 15:00 | Summer | 2.0386 | 2.9176 | 4.2102 | 4.2102 | 4.2102 | 4.2102 | 0.86879 | 1.4217 | 1.9482 | 2.3431 | 2.3431 | 2.3431 | 2.3244 | 2.9996 | 3.442 | 3.6748 | 4.1404 | 4.6061 | 0.96504 | 1.9047 | 2.2856 | 2.2856 | 2.2856 | 2.2856 | 1.086 | 1.2633 | 1.2633 | 1.2633 | 1.2633 | 1.2633
2020-12-29 16:00 | Summer | 1.928 | 2.7592 | 3.9817 | 3.9817 | 3.9817 | 3.9817 | 0.86594 | 1.417 | 1.9418 | 2.3354 | 2.3354 | 2.3354 | 2.3167 | 2.9896 | 3.4305 | 3.6625 | 4.1266 | 4.5907 | 0.97549 | 1.9253 | 2.3104 | 2.3104 | 2.3104 | 2.3104 | 0.99073 | 1.1525 | 1.1525 | 1.1525 | 1.1525 | 1.1525
2020-12-29 17:00 | Summer | 1.7719 | 2.5359 | 3.6593 | 3.6593 | 3.6593 | 3.6593 | 0.78591 | 1.286 | 1.7624 | 2.1196 | 2.1196 | 2.1196 | 2.2101 | 2.8521 | 3.2727 | 3.4941 | 3.9368 | 4.3796 | 0.88404 | 1.7448 | 2.0938 | 2.0938 | 2.0938 | 2.0938 | 0.91452 | 1.0638 | 1.0638 | 1.0638 | 1.0638 | 1.0638
2020-12-29 18:00 | Summer | 1.3006 | 1.8614 | 2.686 | 2.686 | 2.686 | 2.686 | 0.63851 | 1.0448 | 1.4318 | 1.722 | 1.722 | 1.722 | 2.0386 | 2.6308 | 3.0188 | 3.223 | 3.6314 | 4.0398 | 0.82688 | 1.632 | 1.9584 | 1.9584 | 1.9584 | 1.9584 | 0.66495 | 0.77351 | 0.77351 | 0.77351 | 0.77351 | 0.77351
2020-12-29 19:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.45726 | 0.74824 | 1.0254 | 1.2332 | 1.2332 | 1.2332 | 1.9357 | 2.498 | 2.8664 | 3.0603 | 3.4481 | 3.8359 | 0.78877 | 1.5568 | 1.8681 | 1.8681 | 1.8681 | 1.8681 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-12-29 20:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.42296 | 0.69212 | 0.94846 | 1.1407 | 1.1407 | 1.1407 | 1.8672 | 2.4095 | 2.7649 | 2.9519 | 3.3259 | 3.7 | 0.80021 | 1.5794 | 1.8952 | 1.8952 | 1.8952 | 1.8952 | 0.43821 | 0.50975 | 0.50975 | 0.50975 | 0.50975 | 0.50975
2020-12-29 21:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.53442 | 0.87451 | 1.1984 | 1.4413 | 1.4413 | 1.4413 | 1.8481 | 2.3849 | 2.7366 | 2.9218 | 3.292 | 3.6622 | 0.81545 | 1.6094 | 1.9313 | 1.9313 | 1.9313 | 1.9313 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-12-29 22:00 | Summer | 0.91547 | 1.3102 | 1.8906 | 1.8906 | 1.8906 | 1.8906 | 0.50013 | 0.81839 | 1.1215 | 1.3488 | 1.3488 | 1.3488 | 1.7528 | 2.262 | 2.5956 | 2.7712 | 3.1223 | 3.4734 | 0.78877 | 1.5568 | 1.8681 | 1.8681 | 1.8681 | 1.8681 | 0.43821 | 0.50975 | 0.50975 | 0.50975 | 0.50975 | 0.50975
2020-12-29 23:00 | Summer | 0.89547 | 1.2816 | 1.8493 | 1.8493 | 1.8493 | 1.8493 | 0.44297 | 0.72486 | 0.99332 | 1.1947 | 1.1947 | 1.1947 | 1.6576 | 2.1391 | 2.4545 | 2.6205 | 2.9526 | 3.2847 | 0.74686 | 1.4741 | 1.7689 | 1.7689 | 1.7689 | 1.7689 | 0.40018 | 0.46552 | 0.46552 | 0.46552 | 0.46552 | 0.46552
2020-12-30 | Summer | 0.89547 | 1.2816 | 1.8493 | 1.8493 | 1.8493 | 1.8493 | 0.48298 | 0.79033 | 1.083 | 1.3026 | 1.3026 | 1.3026 | 1.6385 | 2.1145 | 2.4263 | 2.5904 | 2.9187 | 3.2469 | 0.6516 | 1.286 | 1.5433 | 1.5433 | 1.5433 | 1.5433 | 0.41916 | 0.48759 | 0.48759 | 0.48759 | 0.48759 | 0.48759
2020-12-30 01:00 | Summer | 0.85737 | 1.227 | 1.7706 | 1.7706 | 1.7706 | 1.7706 | 0.39724 | 0.65003 | 0.89079 | 1.0713 | 1.0713 | 1.0713 | 1.5433 | 1.9915 | 2.2852 | 2.4398 | 2.749 | 3.0581 | 0.61455 | 1.2129 | 1.4555 | 1.4555 | 1.4555 | 1.4555 | 0.40057 | 0.46596 | 0.46596 | 0.46596 | 0.46596 | 0.46596
2020-12-30 02:00 | Summer | 0.87642 | 1.2543 | 1.81 | 1.81 | 1.81 | 1.81 | 0.44011 | 0.72018 | 0.98691 | 1.187 | 1.187 | 1.187 | 1.5623 | 2.0161 | 2.3135 | 2.4699 | 2.7829 | 3.0959 | 0.62111 | 1.2259 | 1.4711 | 1.4711 | 1.4711 | 1.4711 | 0.41916 | 0.48759 | 0.48759 | 0.48759 | 0.48759 | 0.48759
2020-12-30 03:00 | Summer | 0.87642 | 1.2543 | 1.81 | 1.81 | 1.81 | 1.81 | 0.48584 | 0.79501 | 1.0895 | 1.3103 | 1.3103 | 1.3103 | 1.5433 | 1.9915 | 2.2852 | 2.4398 | 2.749 | 3.0581 | 0.6516 | 1.286 | 1.5433 | 1.5433 | 1.5433 | 1.5433 | 0.41916 | 0.48759 | 0.48759 | 0.48759 | 0.48759 | 0.48759
2020-12-30 04:00 | Summer | 1.0357 | 1.4822 | 2.1389 | 2.1389 | 2.1389 | 2.1389 | 0.42011 | 0.68744 | 0.94205 | 1.133 | 1.133 | 1.133 | 1.543 | 1.9912 | 2.2849 | 2.4395 | 2.7486 | 3.0577 | 0.61349 | 1.2108 | 1.453 | 1.453 | 1.453 | 1.453 | 0.41913 | 0.48756 | 0.48756 | 0.48756 | 0.48756 | 0.48756
2020-12-30 05:00 | Summer | 1.2765 | 1.8269 | 2.6363 | 2.6363 | 2.6363 | 2.6363 | 0.46297 | 0.75759 | 1.0382 | 1.2486 | 1.2486 | 1.2486 | 1.6004 | 2.0653 | 2.3699 | 2.5302 | 2.8508 | 3.1714 | 0.72018 | 1.4214 | 1.7057 | 1.7057 | 1.7057 | 1.7057 | 0.55252 | 0.64273 | 0.64273 | 0.64273 | 0.64273 | 0.64273
2020-12-30 06:00 | Summer | 1.2956 | 1.8542 | 2.6756 | 2.6756 | 2.6756 | 2.6756 | 0.59729 | 0.97739 | 1.3394 | 1.6109 | 1.6109 | 1.6109 | 1.6576 | 2.1391 | 2.4545 | 2.6205 | 2.9526 | 3.2847 | 0.6897 | 1.3613 | 1.6335 | 1.6335 | 1.6335 | 1.6335 | 0.6521 | 0.75856 | 0.75856 | 0.75856 | 0.75856 | 0.75856
2020-12-30 07:00 | Summer | 1.3908 | 1.9905 | 2.8724 | 2.8724 | 2.8724 | 2.8724 | 0.58586 | 0.95868 | 1.3138 | 1.5801 | 1.5801 | 1.5801 | 1.7719 | 2.2866 | 2.6238 | 2.8013 | 3.1562 | 3.5112 | 0.87261 | 1.7222 | 2.0667 | 2.0667 | 2.0667 | 2.0667 | 0.85737 | 0.99734 | 0.99734 | 0.99734 | 0.99734 | 0.99734
2020-12-30 08:00 | Summer | 1.5623 | 2.2359 | 3.2265 | 3.2265 | 3.2265 | 3.2265 | 0.66017 | 1.0803 | 1.4804 | 1.7805 | 1.7805 | 1.7805 | 1.9434 | 2.5079 | 2.8777 | 3.0724 | 3.4617 | 3.851 | 0.86117 | 1.6997 | 2.0396 | 2.0396 | 2.0396 | 2.0396 | 0.87642 | 1.0195 | 1.0195 | 1.0195 | 1.0195 | 1.0195
2020-12-30 09:00 | Summer | 1.5026 | 2.1505 | 3.1033 | 3.1033 | 3.1033 | 3.1033 | 0.74876 | 1.2252 | 1.679 | 2.0194 | 2.0194 | 2.0194 | 2.0958 | 2.7046 | 3.1034 | 3.3133 | 3.7332 | 4.153 | 0.88785 | 1.7523 | 2.1028 | 2.1028 | 2.1028 | 2.1028 | 0.93358 | 1.086 | 1.086 | 1.086 | 1.086 | 1.086
2020-12-30 10:00 | Summer | 1.7147 | 2.4541 | 3.5413 | 3.5413 | 3.5413 | 3.5413 | 0.64016 | 1.0475 | 1.4355 | 1.7265 | 1.7265 | 1.7265 | 2.1529 | 2.7783 | 3.1881 | 3.4037 | 3.835 | 4.2663 | 0.91452 | 1.805 | 2.166 | 2.166 | 2.166 | 2.166 | 0.9429 | 1.0968 | 1.0968 | 1.0968 | 1.0968 | 1.0968
2020-12-30 11:00 | Summer | 1.7147 | 2.4541 | 3.5413 | 3.5413 | 3.5413 | 3.5413 | 0.66874 | 1.0943 | 1.4996 | 1.8036 | 1.8036 | 1.8036 | 2.191 | 2.8275 | 3.2445 | 3.4639 | 3.9029 | 4.3418 | 0.88404 | 1.7448 | 2.0938 | 2.0938 | 2.0938 | 2.0938 | 1.0098 | 1.1746 | 1.1746 | 1.1746 | 1.1746 | 1.1746
2020-12-30 12:00 | Summer | 1.81 | 2.5904 | 3.738 | 3.738 | 3.738 | 3.738 | 0.75734 | 1.2393 | 1.6983 | 2.0425 | 2.0425 | 2.0425 | 2.2863 | 2.9504 | 3.3855 | 3.6146 | 4.0726 | 4.5306 | 0.91071 | 1.7975 | 2.1569 | 2.1569 | 2.1569 | 2.1569 | 1.0098 | 1.1746 | 1.1746 | 1.1746 | 1.1746 | 1.1746
2020-12-30 13:00 | Summer | 1.9624 | 2.8085 | 4.0528 | 4.0528 | 4.0528 | 4.0528 | 0.72018 | 1.1785 | 1.615 | 1.9423 | 1.9423 | 1.9423 | 2.3625 | 3.0488 | 3.4984 | 3.735 | 4.2083 | 4.6816 | 1.0022 | 1.978 | 2.3735 | 2.3735 | 2.3735 | 2.3735 | 1.0288 | 1.1968 | 1.1968 | 1.1968 | 1.1968 | 1.1968
2020-12-30 14:00 | Summer | 1.9442 | 2.7825 | 4.0153 | 4.0153 | 4.0153 | 4.0153 | 0.83736 | 1.3702 | 1.8777 | 2.2583 | 2.2583 | 2.2583 | 2.3435 | 3.0242 | 3.4702 | 3.7049 | 4.1744 | 4.6438 | 1.0212 | 2.0156 | 2.4187 | 2.4187 | 2.4187 | 2.4187 | 1.0479 | 1.219 | 1.219 | 1.219 | 1.219 | 1.219
2020-12-30 15:00 | Summer | 1.9624 | 2.8085 | 4.0528 | 4.0528 | 4.0528 | 4.0528 | 0.82878 | 1.3562 | 1.8585 | 2.2352 | 2.2352 | 2.2352 | 2.4959 | 3.2209 | 3.6959 | 3.9459 | 4.4459 | 4.9459 | 1.0022 | 1.978 | 2.3735 | 2.3735 | 2.3735 | 2.3735 | 1.0187 | 1.1851 | 1.1851 | 1.1851 | 1.1851 | 1.1851
2020-12-30 16:00 | Summer | 1.9815 | 2.8358 | 4.0922 | 4.0922 | 4.0922 | 4.0922 | 0.80878 | 1.3235 | 1.8136 | 2.1812 | 2.1812 | 2.1812 | 2.4776 | 3.1973 | 3.6688 | 3.917 | 4.4133 | 4.9096 | 1.0517 | 2.0757 | 2.4909 | 2.4909 | 2.4909 | 2.4909 | 0.99073 | 1.1525 | 1.1525 | 1.1525 | 1.1525 | 1.1525
2020-12-30 17:00 | Summer | 1.7909 | 2.5631 | 3.6987 | 3.6987 | 3.6987 | 3.6987 | 0.85736 | 1.403 | 1.9226 | 2.3123 | 2.3123 | 2.3123 | 2.4205 | 3.1236 | 3.5843 | 3.8268 | 4.3117 | 4.7966 | 0.9069 | 1.7899 | 2.1479 | 2.1479 | 2.1479 | 2.1479 | 0.95263 | 1.1082 | 1.1082 | 1.1082 | 1.1082 | 1.1082
2020-12-30 18:00 | Summer | 1.2848 | 1.8387 | 2.6533 | 2.6533 | 2.6533 | 2.6533 | 0.64662 | 1.0581 | 1.45 | 1.7439 | 1.7439 | 1.7439 | 2.2482 | 2.9013 | 3.3291 | 3.5543 | 4.0047 | 4.4551 | 0.89928 | 1.7749 | 2.1299 | 2.1299 | 2.1299 | 2.1299 | 0.68724 | 0.79944 | 0.79944 | 0.79944 | 0.79944 | 0.79944
2020-12-30 19:00 | Summer | 1.0669 | 1.527 | 2.2035 | 2.2035 | 2.2035 | 2.2035 | 0.49727 | 0.81371 | 1.1151 | 1.3411 | 1.3411 | 1.3411 | 2.1274 | 2.7454 | 3.1503 | 3.3634 | 3.7896 | 4.2158 | 0.86117 | 1.6997 | 2.0396 | 2.0396 | 2.0396 | 2.0396 | 0.5335 | 0.6206 | 0.6206 | 0.6206 | 0.6206 | 0.6206
2020-12-30 20:00 | Summer | 1.0091 | 1.4442 | 2.0841 | 2.0841 | 2.0841 | 2.0841 | 0.46583 | 0.76227 | 1.0446 | 1.2563 | 1.2563 | 1.2563 | 1.9434 | 2.5079 | 2.8777 | 3.0724 | 3.4617 | 3.851 | 0.89166 | 1.7599 | 2.1118 | 2.1118 | 2.1118 | 2.1118 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-12-30 21:00 | Summer | 1.0288 | 1.4724 | 2.1248 | 2.1248 | 2.1248 | 2.1248 | 0.44868 | 0.73421 | 1.0061 | 1.2101 | 1.2101 | 1.2101 | 1.9243 | 2.4833 | 2.8495 | 3.0422 | 3.4277 | 3.8132 | 0.9069 | 1.7899 | 2.1479 | 2.1479 | 2.1479 | 2.1479 | 0.47625 | 0.554 | 0.554 | 0.554 | 0.554 | 0.554
2020-12-30 22:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.45154 | 0.73889 | 1.0125 | 1.2178 | 1.2178 | 1.2178 | 1.81 | 2.3358 | 2.6802 | 2.8615 | 3.2241 | 3.5867 | 0.81545 | 1.6094 | 1.9313 | 1.9313 | 1.9313 | 1.9313 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2020-12-30 23:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.43154 | 0.70615 | 0.96769 | 1.1638 | 1.1638 | 1.1638 | 1.7338 | 2.2374 | 2.5674 | 2.741 | 3.0884 | 3.4357 | 0.75829 | 1.4966 | 1.796 | 1.796 | 1.796 | 1.796 | 0.43814 | 0.50967 | 0.50967 | 0.50967 | 0.50967 | 0.50967
2020-12-31 | Summer | 0.89547 | 1.2816 | 1.8493 | 1.8493 | 1.8493 | 1.8493 | 0.43439 | 0.71083 | 0.9741 | 1.1715 | 1.1715 | 1.1715 | 1.6766 | 2.1636 | 2.4827 | 2.6507 | 2.9865 | 3.3224 | 0.73543 | 1.4515 | 1.7418 | 1.7418 | 1.7418 | 1.7418 | 0.43821 | 0.50975 | 0.50975 | 0.50975 | 0.50975 | 0.50975
2020-12-31 01:00 | Summer | 0.91452 | 1.3088 | 1.8887 | 1.8887 | 1.8887 | 1.8887 | 0.43154 | 0.70615 | 0.96769 | 1.1638 | 1.1638 | 1.1638 | 1.6206 | 2.0913 | 2.3997 | 2.5621 | 2.8867 | 3.2114 | 0.66684 | 1.3161 | 1.5794 | 1.5794 | 1.5794 | 1.5794 | 0.43821 | 0.50975 | 0.50975 | 0.50975 | 0.50975 | 0.50975
2020-12-31 02:00 | Summer | 0.91452 | 1.3088 | 1.8887 | 1.8887 | 1.8887 | 1.8887 | 0.42011 | 0.68744 | 0.94205 | 1.133 | 1.133 | 1.133 | 1.5623 | 2.0161 | 2.3135 | 2.4699 | 2.7829 | 3.0959 | 0.66684 | 1.3161 | 1.5794 | 1.5794 | 1.5794 | 1.5794 | 0.41916 | 0.48759 | 0.48759 | 0.48759 | 0.48759 | 0.48759
2020-12-31 03:00 | Summer | 0.91452 | 1.3088 | 1.8887 | 1.8887 | 1.8887 | 1.8887 | 0.4544 | 0.74356 | 1.019 | 1.2255 | 1.2255 | 1.2255 | 1.5242 | 1.967 | 2.257 | 2.4097 | 2.715 | 3.0204 | 0.65922 | 1.3011 | 1.5613 | 1.5613 | 1.5613 | 1.5613 | 0.41916 | 0.48759 | 0.48759 | 0.48759 | 0.48759 | 0.48759
2020-12-31 04:00 | Summer | 1.0707 | 1.5323 | 2.2112 | 2.2112 | 2.2112 | 2.2112 | 0.52299 | 0.8558 | 1.1728 | 1.4105 | 1.4105 | 1.4105 | 1.5433 | 1.9915 | 2.2852 | 2.4398 | 2.749 | 3.0581 | 0.66684 | 1.3161 | 1.5794 | 1.5794 | 1.5794 | 1.5794 | 0.41916 | 0.48759 | 0.48759 | 0.48759 | 0.48759 | 0.48759
2020-12-31 05:00 | Summer | 1.2575 | 1.7996 | 2.5969 | 2.5969 | 2.5969 | 2.5969 | 0.49441 | 0.80903 | 1.1087 | 1.3334 | 1.3334 | 1.3334 | 1.6385 | 2.1145 | 2.4263 | 2.5904 | 2.9187 | 3.2469 | 0.75829 | 1.4966 | 1.796 | 1.796 | 1.796 | 1.796 | 0.53291 | 0.61991 | 0.61991 | 0.61991 | 0.61991 | 0.61991
2020-12-31 06:00 | Summer | 1.3527 | 1.936 | 2.7937 | 2.7937 | 2.7937 | 2.7937 | 0.58586 | 0.95868 | 1.3138 | 1.5801 | 1.5801 | 1.5801 | 1.6617 | 2.1443 | 2.4606 | 2.627 | 2.9599 | 3.2928 | 0.70494 | 1.3913 | 1.6696 | 1.6696 | 1.6696 | 1.6696 | 0.62708 | 0.72946 | 0.72946 | 0.72946 | 0.72946 | 0.72946
2020-12-31 07:00 | Summer | 1.4099 | 2.0178 | 2.9117 | 2.9117 | 2.9117 | 2.9117 | 0.56586 | 0.92595 | 1.2689 | 1.5261 | 1.5261 | 1.5261 | 1.8672 | 2.4095 | 2.7649 | 2.9519 | 3.3259 | 3.7 | 0.91071 | 1.7975 | 2.1569 | 2.1569 | 2.1569 | 2.1569 | 0.87642 | 1.0195 | 1.0195 | 1.0195 | 1.0195 | 1.0195
2020-12-31 08:00 | Summer | 1.5814 | 2.2632 | 3.2659 | 3.2659 | 3.2659 | 3.2659 | 0.70875 | 1.1598 | 1.5893 | 1.9115 | 1.9115 | 1.9115 | 1.9815 | 2.557 | 2.9341 | 3.1326 | 3.5296 | 3.9265 | 0.89928 | 1.7749 | 2.1299 | 2.1299 | 2.1299 | 2.1299 | 0.87642 | 1.0195 | 1.0195 | 1.0195 | 1.0195 | 1.0195
2020-12-31 09:00 | Summer | 1.5242 | 2.1814 | 3.1478 | 3.1478 | 3.1478 | 3.1478 | 0.78306 | 1.2814 | 1.7559 | 2.1119 | 2.1119 | 2.1119 | 2.0577 | 2.6554 | 3.047 | 3.2531 | 3.6653 | 4.0775 | 0.99454 | 1.9629 | 2.3555 | 2.3555 | 2.3555 | 2.3555 | 0.95263 | 1.1082 | 1.1082 | 1.1082 | 1.1082 | 1.1082
2020-12-31 10:00 | Summer | 1.5814 | 2.2632 | 3.2659 | 3.2659 | 3.2659 | 3.2659 | 0.65445 | 1.0709 | 1.4676 | 1.765 | 1.765 | 1.765 | 2.1339 | 2.7537 | 3.1598 | 3.3736 | 3.8011 | 4.2285 | 0.96787 | 1.9103 | 2.2923 | 2.2923 | 2.2923 | 2.2923 | 0.89547 | 1.0417 | 1.0417 | 1.0417 | 1.0417 | 1.0417
2020-12-31 11:00 | Summer | 1.6957 | 2.4268 | 3.5019 | 3.5019 | 3.5019 | 3.5019 | 0.64016 | 1.0475 | 1.4355 | 1.7265 | 1.7265 | 1.7265 | 2.172 | 2.8029 | 3.2163 | 3.4338 | 3.8689 | 4.3041 | 0.98311 | 1.9403 | 2.3284 | 2.3284 | 2.3284 | 2.3284 | 0.87642 | 1.0195 | 1.0195 | 1.0195 | 1.0195 | 1.0195
2020-12-31 12:00 | Summer | 1.7338 | 2.4813 | 3.5806 | 3.5806 | 3.5806 | 3.5806 | 0.76591 | 1.2533 | 1.7175 | 2.0656 | 2.0656 | 2.0656 | 2.2101 | 2.8521 | 3.2727 | 3.4941 | 3.9368 | 4.3796 | 0.99454 | 1.9629 | 2.3555 | 2.3555 | 2.3555 | 2.3555 | 0.93688 | 1.0898 | 1.0898 | 1.0898 | 1.0898 | 1.0898
2020-12-31 13:00 | Summer | 1.7528 | 2.5086 | 3.62 | 3.62 | 3.62 | 3.62 | 0.73733 | 1.2065 | 1.6534 | 1.9886 | 1.9886 | 1.9886 | 2.2482 | 2.9013 | 3.3291 | 3.5543 | 4.0047 | 4.4551 | 0.96787 | 1.9103 | 2.2923 | 2.2923 | 2.2923 | 2.2923 | 1.0098 | 1.1746 | 1.1746 | 1.1746 | 1.1746 | 1.1746
2020-12-31 14:00 | Summer | 1.7719 | 2.5359 | 3.6593 | 3.6593 | 3.6593 | 3.6593 | 0.7459 | 1.2206 | 1.6726 | 2.0117 | 2.0117 | 2.0117 | 2.3435 | 3.0242 | 3.4702 | 3.7049 | 4.1744 | 4.6438 | 1.025 | 2.0231 | 2.4277 | 2.4277 | 2.4277 | 2.4277 | 0.97168 | 1.1303 | 1.1303 | 1.1303 | 1.1303 | 1.1303
2020-12-31 15:00 | Summer | 1.7909 | 2.5631 | 3.6987 | 3.6987 | 3.6987 | 3.6987 | 0.80878 | 1.3235 | 1.8136 | 2.1812 | 2.1812 | 2.1812 | 2.3333 | 3.011 | 3.4551 | 3.6888 | 4.1562 | 4.6236 | 0.88404 | 1.7448 | 2.0938 | 2.0938 | 2.0938 | 2.0938 | 1.0098 | 1.1746 | 1.1746 | 1.1746 | 1.1746 | 1.1746
2020-12-31 16:00 | Summer | 1.8862 | 2.6995 | 3.8954 | 3.8954 | 3.8954 | 3.8954 | 0.79735 | 1.3047 | 1.788 | 2.1504 | 2.1504 | 2.1504 | 2.534 | 3.2701 | 3.7523 | 4.0061 | 4.5138 | 5.0214 | 0.92976 | 1.8351 | 2.2021 | 2.2021 | 2.2021 | 2.2021 | 0.99073 | 1.1525 | 1.1525 | 1.1525 | 1.1525 | 1.1525
2020-12-31 17:00 | Summer | 1.7338 | 2.4813 | 3.5806 | 3.5806 | 3.5806 | 3.5806 | 0.7802 | 1.2767 | 1.7495 | 2.1042 | 2.1042 | 2.1042 | 2.3753 | 3.0653 | 3.5174 | 3.7553 | 4.2312 | 4.707 | 0.94501 | 1.8651 | 2.2382 | 2.2382 | 2.2382 | 2.2382 | 0.97168 | 1.1303 | 1.1303 | 1.1303 | 1.1303 | 1.1303
2020-12-31 18:00 | Summer | 1.5437 | 2.2093 | 3.1881 | 3.1881 | 3.1881 | 3.1881 | 0.70192 | 1.1486 | 1.574 | 1.8931 | 1.8931 | 1.8931 | 2.1606 | 2.7882 | 3.1994 | 3.4158 | 3.8486 | 4.2814 | 0.89166 | 1.7599 | 2.1118 | 2.1118 | 2.1118 | 2.1118 | 0.74305 | 0.86436 | 0.86436 | 0.86436 | 0.86436 | 0.86436
2020-12-31 19:00 | Summer | 0.93394 | 1.3366 | 1.9288 | 1.9288 | 1.9288 | 1.9288 | 0.49727 | 0.81371 | 1.1151 | 1.3411 | 1.3411 | 1.3411 | 2.0577 | 2.6554 | 3.047 | 3.2531 | 3.6653 | 4.0775 | 0.88785 | 1.7523 | 2.1028 | 2.1028 | 2.1028 | 2.1028 | 0.4992 | 0.5807 | 0.5807 | 0.5807 | 0.5807 | 0.5807
2020-12-31 20:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.49155 | 0.80436 | 1.1023 | 1.3257 | 1.3257 | 1.3257 | 1.9243 | 2.4833 | 2.8495 | 3.0422 | 3.4277 | 3.8132 | 0.92214 | 1.82 | 2.184 | 2.184 | 2.184 | 2.184 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2020-12-31 21:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.48298 | 0.79033 | 1.083 | 1.3026 | 1.3026 | 1.3026 | 1.9624 | 2.5325 | 2.9059 | 3.1025 | 3.4956 | 3.8887 | 0.88404 | 1.7448 | 2.0938 | 2.0938 | 2.0938 | 2.0938 | 0.45098 | 0.52461 | 0.52461 | 0.52461 | 0.52461 | 0.52461
2020-12-31 22:00 | Summer | 0.95312 | 1.3641 | 1.9684 | 1.9684 | 1.9684 | 1.9684 | 0.6173 | 1.0101 | 1.3842 | 1.6648 | 1.6648 | 1.6648 | 1.8862 | 2.4341 | 2.7931 | 2.982 | 3.3599 | 3.7377 | 0.85736 | 1.6922 | 2.0306 | 2.0306 | 2.0306 | 2.0306 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2020-12-31 23:00 | Summer | 0.91452 | 1.3088 | 1.8887 | 1.8887 | 1.8887 | 1.8887 | 0.50584 | 0.82774 | 1.1343 | 1.3642 | 1.3642 | 1.3642 | 1.829 | 2.3603 | 2.7084 | 2.8916 | 3.2581 | 3.6245 | 0.84212 | 1.6621 | 1.9945 | 1.9945 | 1.9945 | 1.9945 | 0.41181 | 0.47905 | 0.47905 | 0.47905 | 0.47905 | 0.47905
2021-01-01 | Summer | 0.89547 | 1.2816 | 1.8493 | 1.8493 | 1.8493 | 1.8493 | 0.46583 | 0.76227 | 1.0446 | 1.2563 | 1.2563 | 1.2563 | 1.7147 | 2.2128 | 2.5392 | 2.7109 | 3.0544 | 3.3979 | 0.98311 | 1.9403 | 2.3284 | 2.3284 | 2.3284 | 2.3284 | 0.4001 | 0.46543 | 0.46543 | 0.46543 | 0.46543 | 0.46543
2021-01-01 01:00 | Summer | 0.89547 | 1.2816 | 1.8493 | 1.8493 | 1.8493 | 1.8493 | 0.5087 | 0.83242 | 1.1407 | 1.3719 | 1.3719 | 1.3719 | 1.6004 | 2.0653 | 2.3699 | 2.5302 | 2.8508 | 3.1714 | 0.7621 | 1.5041 | 1.805 | 1.805 | 1.805 | 1.805 | 0.43821 | 0.50975 | 0.50975 | 0.50975 | 0.50975 | 0.50975
2021-01-01 02:00 | Summer | 0.91452 | 1.3088 | 1.8887 | 1.8887 | 1.8887 | 1.8887 | 0.54585 | 0.89321 | 1.224 | 1.4721 | 1.4721 | 1.4721 | 1.5814 | 2.0407 | 2.3417 | 2.5001 | 2.8169 | 3.1337 | 0.69732 | 1.3763 | 1.6516 | 1.6516 | 1.6516 | 1.6516 | 0.41916 | 0.48759 | 0.48759 | 0.48759 | 0.48759 | 0.48759
2021-01-01 03:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.5151 | 0.84288 | 1.1551 | 1.3892 | 1.3892 | 1.3892 | 1.6004 | 2.0653 | 2.3699 | 2.5302 | 2.8508 | 3.1714 | 0.67446 | 1.3312 | 1.5974 | 1.5974 | 1.5974 | 1.5974 | 0.41916 | 0.48759 | 0.48759 | 0.48759 | 0.48759 | 0.48759
2021-01-01 04:00 | Summer | 0.93592 | 1.3395 | 1.9329 | 1.9329 | 1.9329 | 1.9329 | 0.60015 | 0.98207 | 1.3458 | 1.6186 | 1.6186 | 1.6186 | 1.6385 | 2.1145 | 2.4263 | 2.5904 | 2.9187 | 3.2469 | 0.64779 | 1.2785 | 1.5342 | 1.5342 | 1.5342 | 1.5342 | 0.41916 | 0.48759 | 0.48759 | 0.48759 | 0.48759 | 0.48759
2021-01-01 05:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.4544 | 0.74356 | 1.019 | 1.2255 | 1.2255 | 1.2255 | 1.6766 | 2.1636 | 2.4827 | 2.6507 | 2.9865 | 3.3224 | 0.70494 | 1.3913 | 1.6696 | 1.6696 | 1.6696 | 1.6696 | 0.43821 | 0.50975 | 0.50975 | 0.50975 | 0.50975 | 0.50975
2021-01-01 06:00 | Summer | 0.98984 | 1.4166 | 2.0442 | 2.0442 | 2.0442 | 2.0442 | 0.48869 | 0.79968 | 1.0959 | 1.318 | 1.318 | 1.318 | 1.6766 | 2.1636 | 2.4827 | 2.6507 | 2.9865 | 3.3224 | 0.70494 | 1.3913 | 1.6696 | 1.6696 | 1.6696 | 1.6696 | 0.45071 | 0.5243 | 0.5243 | 0.5243 | 0.5243 | 0.5243
2021-01-01 07:00 | Summer | 1.0288 | 1.4724 | 2.1248 | 2.1248 | 2.1248 | 2.1248 | 0.46869 | 0.76695 | 1.051 | 1.264 | 1.264 | 1.264 | 1.6957 | 2.1882 | 2.5109 | 2.6808 | 3.0205 | 3.3602 | 0.86117 | 1.6997 | 2.0396 | 2.0396 | 2.0396 | 2.0396 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2021-01-01 08:00 | Summer | 1.0479 | 1.4997 | 2.1641 | 2.1641 | 2.1641 | 2.1641 | 0.54871 | 0.89789 | 1.2304 | 1.4799 | 1.4799 | 1.4799 | 1.9053 | 2.4587 | 2.8213 | 3.0121 | 3.3938 | 3.7755 | 0.86879 | 1.7147 | 2.0577 | 2.0577 | 2.0577 | 2.0577 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2021-01-01 09:00 | Summer | 1.0288 | 1.4724 | 2.1248 | 2.1248 | 2.1248 | 2.1248 | 0.49155 | 0.80436 | 1.1023 | 1.3257 | 1.3257 | 1.3257 | 2.0289 | 2.6182 | 3.0043 | 3.2076 | 3.614 | 4.0205 | 0.84585 | 1.6694 | 2.0033 | 2.0033 | 2.0033 | 2.0033 | 0.53347 | 0.62057 | 0.62057 | 0.62057 | 0.62057 | 0.62057
2021-01-01 10:00 | Summer | 1.0479 | 1.4997 | 2.1641 | 2.1641 | 2.1641 | 2.1641 | 0.53728 | 0.87918 | 1.2048 | 1.449 | 1.449 | 1.449 | 2.0386 | 2.6308 | 3.0188 | 3.223 | 3.6314 | 4.0398 | 0.87261 | 1.7222 | 2.0667 | 2.0667 | 2.0667 | 2.0667 | 0.55252 | 0.64273 | 0.64273 | 0.64273 | 0.64273 | 0.64273
2021-01-01 11:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.52924 | 0.86602 | 1.1868 | 1.4273 | 1.4273 | 1.4273 | 2.191 | 2.8275 | 3.2445 | 3.4639 | 3.9029 | 4.3418 | 0.86879 | 1.7147 | 2.0577 | 2.0577 | 2.0577 | 2.0577 | 0.59063 | 0.68706 | 0.68706 | 0.68706 | 0.68706 | 0.68706
2021-01-01 12:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.49155 | 0.80436 | 1.1023 | 1.3257 | 1.3257 | 1.3257 | 2.1722 | 2.8032 | 3.2166 | 3.4342 | 3.8693 | 4.3045 | 0.86498 | 1.7072 | 2.0486 | 2.0486 | 2.0486 | 2.0486 | 0.57158 | 0.6649 | 0.6649 | 0.6649 | 0.6649 | 0.6649
2021-01-01 13:00 | Summer | 1.0288 | 1.4724 | 2.1248 | 2.1248 | 2.1248 | 2.1248 | 0.51727 | 0.84645 | 1.1599 | 1.3951 | 1.3951 | 1.3951 | 2.1148 | 2.7291 | 3.1316 | 3.3435 | 3.7671 | 4.1908 | 0.87261 | 1.7222 | 2.0667 | 2.0667 | 2.0667 | 2.0667 | 0.59063 | 0.68706 | 0.68706 | 0.68706 | 0.68706 | 0.68706
2021-01-01 14:00 | Summer | 1.0288 | 1.4724 | 2.1248 | 2.1248 | 2.1248 | 2.1248 | 0.5087 | 0.83242 | 1.1407 | 1.3719 | 1.3719 | 1.3719 | 2.0577 | 2.6554 | 3.047 | 3.2531 | 3.6653 | 4.0775 | 0.84974 | 1.6771 | 2.0125 | 2.0125 | 2.0125 | 2.0125 | 0.57158 | 0.6649 | 0.6649 | 0.6649 | 0.6649 | 0.6649
2021-01-01 15:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.61999 | 1.0145 | 1.3903 | 1.6721 | 1.6721 | 1.6721 | 2.0577 | 2.6554 | 3.047 | 3.2531 | 3.6653 | 4.0775 | 0.85736 | 1.6922 | 2.0306 | 2.0306 | 2.0306 | 2.0306 | 0.57158 | 0.6649 | 0.6649 | 0.6649 | 0.6649 | 0.6649
2021-01-01 16:00 | Summer | 1.0288 | 1.4724 | 2.1248 | 2.1248 | 2.1248 | 2.1248 | 0.62873 | 1.0288 | 1.4099 | 1.6957 | 1.6957 | 1.6957 | 2.0386 | 2.6308 | 3.0188 | 3.223 | 3.6314 | 4.0398 | 0.86879 | 1.7147 | 2.0577 | 2.0577 | 2.0577 | 2.0577 | 0.60968 | 0.70922 | 0.70922 | 0.70922 | 0.70922 | 0.70922
2021-01-01 17:00 | Summer | 1.0669 | 1.527 | 2.2035 | 2.2035 | 2.2035 | 2.2035 | 0.55443 | 0.90724 | 1.2433 | 1.4953 | 1.4953 | 1.4953 | 1.9634 | 2.5337 | 2.9073 | 3.104 | 3.4973 | 3.8906 | 0.8345 | 1.647 | 1.9764 | 1.9764 | 1.9764 | 1.9764 | 0.55252 | 0.64273 | 0.64273 | 0.64273 | 0.64273 | 0.64273
2021-01-01 18:00 | Summer | 0.99185 | 1.4195 | 2.0484 | 2.0484 | 2.0484 | 2.0484 | 0.48869 | 0.79968 | 1.0959 | 1.318 | 1.318 | 1.318 | 1.9243 | 2.4833 | 2.8495 | 3.0422 | 3.4277 | 3.8132 | 0.78115 | 1.5417 | 1.8501 | 1.8501 | 1.8501 | 1.8501 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2021-01-01 19:00 | Summer | 0.91504 | 1.3096 | 1.8898 | 1.8898 | 1.8898 | 1.8898 | 0.57157 | 0.9353 | 1.2817 | 1.5415 | 1.5415 | 1.5415 | 1.8593 | 2.3993 | 2.7532 | 2.9394 | 3.3119 | 3.6843 | 0.77353 | 1.5267 | 1.832 | 1.832 | 1.832 | 1.832 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2021-01-01 20:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.48869 | 0.79968 | 1.0959 | 1.318 | 1.318 | 1.318 | 1.8481 | 2.3849 | 2.7366 | 2.9218 | 3.292 | 3.6622 | 0.80783 | 1.5944 | 1.9133 | 1.9133 | 1.9133 | 1.9133 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2021-01-01 21:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.46583 | 0.76227 | 1.0446 | 1.2563 | 1.2563 | 1.2563 | 1.7909 | 2.3112 | 2.652 | 2.8314 | 3.1902 | 3.549 | 0.82307 | 1.6245 | 1.9494 | 1.9494 | 1.9494 | 1.9494 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2021-01-01 22:00 | Summer | 0.91452 | 1.3088 | 1.8887 | 1.8887 | 1.8887 | 1.8887 | 0.44868 | 0.73421 | 1.0061 | 1.2101 | 1.2101 | 1.2101 | 1.7719 | 2.2866 | 2.6238 | 2.8013 | 3.1562 | 3.5112 | 0.74305 | 1.4665 | 1.7599 | 1.7599 | 1.7599 | 1.7599 | 0.43821 | 0.50975 | 0.50975 | 0.50975 | 0.50975 | 0.50975
2021-01-01 23:00 | Summer | 0.91452 | 1.3088 | 1.8887 | 1.8887 | 1.8887 | 1.8887 | 0.47155 | 0.77162 | 1.0574 | 1.2717 | 1.2717 | 1.2717 | 1.7147 | 2.2128 | 2.5392 | 2.7109 | 3.0544 | 3.3979 | 0.73924 | 1.459 | 1.7508 | 1.7508 | 1.7508 | 1.7508 | 0.41916 | 0.48759 | 0.48759 | 0.48759 | 0.48759 | 0.48759
2021-01-02 | Summer | 0.91452 | 1.3088 | 1.8887 | 1.8887 | 1.8887 | 1.8887 | 0.47726 | 0.78098 | 1.0702 | 1.2872 | 1.2872 | 1.2872 | 1.6385 | 2.1145 | 2.4263 | 2.5904 | 2.9187 | 3.2469 | 0.73924 | 1.459 | 1.7508 | 1.7508 | 1.7508 | 1.7508 | 0.4001 | 0.46543 | 0.46543 | 0.46543 | 0.46543 | 0.46543
2021-01-02 01:00 | Summer | 0.89547 | 1.2816 | 1.8493 | 1.8493 | 1.8493 | 1.8493 | 0.45154 | 0.73889 | 1.0125 | 1.2178 | 1.2178 | 1.2178 | 1.5814 | 2.0407 | 2.3417 | 2.5001 | 2.8169 | 3.1337 | 0.64397 | 1.271 | 1.5252 | 1.5252 | 1.5252 | 1.5252 | 0.41916 | 0.48759 | 0.48759 | 0.48759 | 0.48759 | 0.48759
2021-01-02 02:00 | Summer | 0.89547 | 1.2816 | 1.8493 | 1.8493 | 1.8493 | 1.8493 | 0.44583 | 0.72953 | 0.99973 | 1.2024 | 1.2024 | 1.2024 | 1.5242 | 1.967 | 2.257 | 2.4097 | 2.715 | 3.0204 | 0.65541 | 1.2936 | 1.5523 | 1.5523 | 1.5523 | 1.5523 | 0.4001 | 0.46543 | 0.46543 | 0.46543 | 0.46543 | 0.46543
2021-01-02 03:00 | Summer | 0.89547 | 1.2816 | 1.8493 | 1.8493 | 1.8493 | 1.8493 | 0.45726 | 0.74824 | 1.0254 | 1.2332 | 1.2332 | 1.2332 | 1.5162 | 1.9567 | 2.2452 | 2.3971 | 2.7008 | 3.0046 | 0.81545 | 1.6094 | 1.9313 | 1.9313 | 1.9313 | 1.9313 | 0.38116 | 0.44339 | 0.44339 | 0.44339 | 0.44339 | 0.44339
2021-01-02 04:00 | Summer | 0.91452 | 1.3088 | 1.8887 | 1.8887 | 1.8887 | 1.8887 | 0.47441 | 0.7763 | 1.0638 | 1.2795 | 1.2795 | 1.2795 | 1.5623 | 2.0161 | 2.3135 | 2.4699 | 2.7829 | 3.0959 | 0.54805 | 1.0817 | 1.298 | 1.298 | 1.298 | 1.298 | 0.4001 | 0.46543 | 0.46543 | 0.46543 | 0.46543 | 0.46543
2021-01-02 05:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.42868 | 0.70147 | 0.96128 | 1.1561 | 1.1561 | 1.1561 | 1.6576 | 2.1391 | 2.4545 | 2.6205 | 2.9526 | 3.2847 | 0.86879 | 1.7147 | 2.0577 | 2.0577 | 2.0577 | 2.0577 | 0.4001 | 0.46543 | 0.46543 | 0.46543 | 0.46543 | 0.46543
2021-01-02 06:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.48869 | 0.79968 | 1.0959 | 1.318 | 1.318 | 1.318 | 1.6385 | 2.1145 | 2.4263 | 2.5904 | 2.9187 | 3.2469 | 0.74305 | 1.4665 | 1.7599 | 1.7599 | 1.7599 | 1.7599 | 0.44647 | 0.51937 | 0.51937 | 0.51937 | 0.51937 | 0.51937
2021-01-02 07:00 | Summer | 1.0288 | 1.4724 | 2.1248 | 2.1248 | 2.1248 | 2.1248 | 0.44868 | 0.73421 | 1.0061 | 1.2101 | 1.2101 | 1.2101 | 1.7147 | 2.2128 | 2.5392 | 2.7109 | 3.0544 | 3.3979 | 0.67827 | 1.3387 | 1.6064 | 1.6064 | 1.6064 | 1.6064 | 0.47711 | 0.55501 | 0.55501 | 0.55501 | 0.55501 | 0.55501
2021-01-02 08:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.42582 | 0.6968 | 0.95487 | 1.1484 | 1.1484 | 1.1484 | 1.9053 | 2.4587 | 2.8213 | 3.0121 | 3.3938 | 3.7755 | 0.66303 | 1.3086 | 1.5703 | 1.5703 | 1.5703 | 1.5703 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2021-01-02 09:00 | Summer | 0.93445 | 1.3373 | 1.9298 | 1.9298 | 1.9298 | 1.9298 | 0.48298 | 0.79033 | 1.083 | 1.3026 | 1.3026 | 1.3026 | 1.9243 | 2.4833 | 2.8495 | 3.0422 | 3.4277 | 3.8132 | 0.81545 | 1.6094 | 1.9313 | 1.9313 | 1.9313 | 1.9313 | 0.53347 | 0.62057 | 0.62057 | 0.62057 | 0.62057 | 0.62057
2021-01-02 10:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.52585 | 0.86048 | 1.1792 | 1.4182 | 1.4182 | 1.4182 | 2.0196 | 2.6062 | 2.9906 | 3.1929 | 3.5974 | 4.002 | 0.74686 | 1.4741 | 1.7689 | 1.7689 | 1.7689 | 1.7689 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2021-01-02 11:00 | Summer | 0.91452 | 1.3088 | 1.8887 | 1.8887 | 1.8887 | 1.8887 | 0.46869 | 0.76695 | 1.051 | 1.264 | 1.264 | 1.264 | 2.0767 | 2.68 | 3.0752 | 3.2832 | 3.6992 | 4.1153 | 0.72018 | 1.4214 | 1.7057 | 1.7057 | 1.7057 | 1.7057 | 0.53347 | 0.62057 | 0.62057 | 0.62057 | 0.62057 | 0.62057
2021-01-02 12:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.50298 | 0.82306 | 1.1279 | 1.3565 | 1.3565 | 1.3565 | 2.0767 | 2.68 | 3.0752 | 3.2832 | 3.6992 | 4.1153 | 0.75067 | 1.4816 | 1.7779 | 1.7779 | 1.7779 | 1.7779 | 0.53347 | 0.62057 | 0.62057 | 0.62057 | 0.62057 | 0.62057
2021-01-02 13:00 | Summer | 0.91452 | 1.3088 | 1.8887 | 1.8887 | 1.8887 | 1.8887 | 0.46869 | 0.76695 | 1.051 | 1.264 | 1.264 | 1.264 | 2.0767 | 2.68 | 3.0752 | 3.2832 | 3.6992 | 4.1153 | 0.76972 | 1.5192 | 1.823 | 1.823 | 1.823 | 1.823 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2021-01-02 14:00 | Summer | 0.91452 | 1.3088 | 1.8887 | 1.8887 | 1.8887 | 1.8887 | 0.54585 | 0.89321 | 1.224 | 1.4721 | 1.4721 | 1.4721 | 2.172 | 2.8029 | 3.2163 | 3.4338 | 3.8689 | 4.3041 | 0.77734 | 1.5342 | 1.8411 | 1.8411 | 1.8411 | 1.8411 | 0.47403 | 0.55142 | 0.55142 | 0.55142 | 0.55142 | 0.55142
2021-01-02 15:00 | Summer | 0.89715 | 1.284 | 1.8528 | 1.8528 | 1.8528 | 1.8528 | 0.52299 | 0.8558 | 1.1728 | 1.4105 | 1.4105 | 1.4105 | 2.0767 | 2.68 | 3.0752 | 3.2832 | 3.6992 | 4.1153 | 0.76591 | 1.5117 | 1.814 | 1.814 | 1.814 | 1.814 | 0.45865 | 0.53354 | 0.53354 | 0.53354 | 0.53354 | 0.53354
2021-01-02 16:00 | Summer | 0.89547 | 1.2816 | 1.8493 | 1.8493 | 1.8493 | 1.8493 | 0.5287 | 0.86515 | 1.1856 | 1.4259 | 1.4259 | 1.4259 | 2.0958 | 2.7046 | 3.1034 | 3.3133 | 3.7332 | 4.153 | 0.84212 | 1.6621 | 1.9945 | 1.9945 | 1.9945 | 1.9945 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2021-01-02 17:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.54585 | 0.89321 | 1.224 | 1.4721 | 1.4721 | 1.4721 | 1.9893 | 2.5671 | 2.9457 | 3.1449 | 3.5435 | 3.942 | 0.80021 | 1.5794 | 1.8952 | 1.8952 | 1.8952 | 1.8952 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2021-01-02 18:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.46869 | 0.76695 | 1.051 | 1.264 | 1.264 | 1.264 | 1.9434 | 2.5079 | 2.8777 | 3.0724 | 3.4617 | 3.851 | 0.84974 | 1.6771 | 2.0125 | 2.0125 | 2.0125 | 2.0125 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2021-01-02 19:00 | Summer | 0.91452 | 1.3088 | 1.8887 | 1.8887 | 1.8887 | 1.8887 | 0.48584 | 0.79501 | 1.0895 | 1.3103 | 1.3103 | 1.3103 | 1.8862 | 2.4341 | 2.7931 | 2.982 | 3.3599 | 3.7377 | 0.84974 | 1.6771 | 2.0125 | 2.0125 | 2.0125 | 2.0125 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2021-01-02 20:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.48298 | 0.79033 | 1.083 | 1.3026 | 1.3026 | 1.3026 | 1.9243 | 2.4833 | 2.8495 | 3.0422 | 3.4277 | 3.8132 | 0.91452 | 1.805 | 2.166 | 2.166 | 2.166 | 2.166 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2021-01-02 21:00 | Summer | 0.91452 | 1.3088 | 1.8887 | 1.8887 | 1.8887 | 1.8887 | 0.48298 | 0.79033 | 1.083 | 1.3026 | 1.3026 | 1.3026 | 1.8481 | 2.3849 | 2.7366 | 2.9218 | 3.292 | 3.6622 | 0.85355 | 1.6846 | 2.0216 | 2.0216 | 2.0216 | 2.0216 | 0.43821 | 0.50975 | 0.50975 | 0.50975 | 0.50975 | 0.50975
2021-01-02 22:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.42582 | 0.6968 | 0.95487 | 1.1484 | 1.1484 | 1.1484 | 1.8481 | 2.3849 | 2.7366 | 2.9218 | 3.292 | 3.6622 | 0.81545 | 1.6094 | 1.9313 | 1.9313 | 1.9313 | 1.9313 | 0.43821 | 0.50975 | 0.50975 | 0.50975 | 0.50975 | 0.50975
2021-01-02 23:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.47441 | 0.7763 | 1.0638 | 1.2795 | 1.2795 | 1.2795 | 1.7338 | 2.2374 | 2.5674 | 2.741 | 3.0884 | 3.4357 | 0.75067 | 1.4816 | 1.7779 | 1.7779 | 1.7779 | 1.7779 | 0.41916 | 0.48759 | 0.48759 | 0.48759 | 0.48759 | 0.48759
2021-01-03 | Summer | 0.89547 | 1.2816 | 1.8493 | 1.8493 | 1.8493 | 1.8493 | 0.40296 | 0.65939 | 0.9036 | 1.0868 | 1.0868 | 1.0868 | 1.6385 | 2.1145 | 2.4263 | 2.5904 | 2.9187 | 3.2469 | 0.78877 | 1.5568 | 1.8681 | 1.8681 | 1.8681 | 1.8681 | 0.40048 | 0.46587 | 0.46587 | 0.46587 | 0.46587 | 0.46587
2021-01-03 01:00 | Summer | 0.89547 | 1.2816 | 1.8493 | 1.8493 | 1.8493 | 1.8493 | 0.45154 | 0.73889 | 1.0125 | 1.2178 | 1.2178 | 1.2178 | 1.6195 | 2.0899 | 2.3981 | 2.5603 | 2.8847 | 3.2092 | 0.69732 | 1.3763 | 1.6516 | 1.6516 | 1.6516 | 1.6516 | 0.41916 | 0.48759 | 0.48759 | 0.48759 | 0.48759 | 0.48759
2021-01-03 02:00 | Summer | 0.89547 | 1.2816 | 1.8493 | 1.8493 | 1.8493 | 1.8493 | 0.45726 | 0.74824 | 1.0254 | 1.2332 | 1.2332 | 1.2332 | 1.6195 | 2.0899 | 2.3981 | 2.5603 | 2.8847 | 3.2092 | 0.68589 | 1.3537 | 1.6245 | 1.6245 | 1.6245 | 1.6245 | 0.41916 | 0.48759 | 0.48759 | 0.48759 | 0.48759 | 0.48759
2021-01-03 03:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.44583 | 0.72953 | 0.99973 | 1.2024 | 1.2024 | 1.2024 | 1.5441 | 1.9926 | 2.2864 | 2.4411 | 2.7504 | 3.0597 | 0.69351 | 1.3688 | 1.6425 | 1.6425 | 1.6425 | 1.6425 | 0.4001 | 0.46543 | 0.46543 | 0.46543 | 0.46543 | 0.46543
2021-01-03 04:00 | Summer | 0.91452 | 1.3088 | 1.8887 | 1.8887 | 1.8887 | 1.8887 | 0.43154 | 0.70615 | 0.96769 | 1.1638 | 1.1638 | 1.1638 | 1.6004 | 2.0653 | 2.3699 | 2.5302 | 2.8508 | 3.1714 | 0.69351 | 1.3688 | 1.6425 | 1.6425 | 1.6425 | 1.6425 | 0.41916 | 0.48759 | 0.48759 | 0.48759 | 0.48759 | 0.48759
2021-01-03 05:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.44011 | 0.72018 | 0.98691 | 1.187 | 1.187 | 1.187 | 1.6576 | 2.1391 | 2.4545 | 2.6205 | 2.9526 | 3.2847 | 0.70746 | 1.3963 | 1.6756 | 1.6756 | 1.6756 | 1.6756 | 0.4001 | 0.46543 | 0.46543 | 0.46543 | 0.46543 | 0.46543
2021-01-03 06:00 | Summer | 0.89533 | 1.2814 | 1.849 | 1.849 | 1.849 | 1.849 | 0.45726 | 0.74824 | 1.0254 | 1.2332 | 1.2332 | 1.2332 | 1.6576 | 2.1391 | 2.4545 | 2.6205 | 2.9526 | 3.2847 | 0.74686 | 1.4741 | 1.7689 | 1.7689 | 1.7689 | 1.7689 | 0.43821 | 0.50975 | 0.50975 | 0.50975 | 0.50975 | 0.50975
2021-01-03 07:00 | Summer | 0.89547 | 1.2816 | 1.8493 | 1.8493 | 1.8493 | 1.8493 | 0.52299 | 0.8558 | 1.1728 | 1.4105 | 1.4105 | 1.4105 | 1.7447 | 2.2515 | 2.5836 | 2.7583 | 3.1078 | 3.4574 | 0.75829 | 1.4966 | 1.796 | 1.796 | 1.796 | 1.796 | 0.41916 | 0.48759 | 0.48759 | 0.48759 | 0.48759 | 0.48759
2021-01-03 08:00 | Summer | 0.91452 | 1.3088 | 1.8887 | 1.8887 | 1.8887 | 1.8887 | 0.43154 | 0.70615 | 0.96769 | 1.1638 | 1.1638 | 1.1638 | 1.9815 | 2.557 | 2.9341 | 3.1326 | 3.5296 | 3.9265 | 0.79258 | 1.5643 | 1.8772 | 1.8772 | 1.8772 | 1.8772 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2021-01-03 09:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.49727 | 0.81371 | 1.1151 | 1.3411 | 1.3411 | 1.3411 | 1.9815 | 2.557 | 2.9341 | 3.1326 | 3.5296 | 3.9265 | 0.81545 | 1.6094 | 1.9313 | 1.9313 | 1.9313 | 1.9313 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2021-01-03 10:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.49155 | 0.80436 | 1.1023 | 1.3257 | 1.3257 | 1.3257 | 2.0577 | 2.6554 | 3.047 | 3.2531 | 3.6653 | 4.0775 | 0.82688 | 1.632 | 1.9584 | 1.9584 | 1.9584 | 1.9584 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2021-01-03 11:00 | Summer | 0.92627 | 1.3256 | 1.913 | 1.913 | 1.913 | 1.913 | 0.46869 | 0.76695 | 1.051 | 1.264 | 1.264 | 1.264 | 2.1148 | 2.7291 | 3.1316 | 3.3435 | 3.7671 | 4.1908 | 0.82307 | 1.6245 | 1.9494 | 1.9494 | 1.9494 | 1.9494 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2021-01-03 12:00 | Summer | 0.85737 | 1.227 | 1.7706 | 1.7706 | 1.7706 | 1.7706 | 0.44011 | 0.72018 | 0.98691 | 1.187 | 1.187 | 1.187 | 2.1529 | 2.7783 | 3.1881 | 3.4037 | 3.835 | 4.2663 | 0.86879 | 1.7147 | 2.0577 | 2.0577 | 2.0577 | 2.0577 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2021-01-03 13:00 | Summer | 0.81926 | 1.1725 | 1.692 | 1.692 | 1.692 | 1.692 | 0.61158 | 1.0008 | 1.3714 | 1.6494 | 1.6494 | 1.6494 | 2.2863 | 2.9504 | 3.3855 | 3.6146 | 4.0726 | 4.5306 | 0.88023 | 1.7373 | 2.0847 | 2.0847 | 2.0847 | 2.0847 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2021-01-03 14:00 | Summer | 0.89547 | 1.2816 | 1.8493 | 1.8493 | 1.8493 | 1.8493 | 0.52585 | 0.86048 | 1.1792 | 1.4182 | 1.4182 | 1.4182 | 2.3476 | 3.0295 | 3.4763 | 3.7114 | 4.1817 | 4.652 | 0.84974 | 1.6771 | 2.0125 | 2.0125 | 2.0125 | 2.0125 | 0.47624 | 0.55399 | 0.55399 | 0.55399 | 0.55399 | 0.55399
2021-01-03 15:00 | Summer | 0.89547 | 1.2816 | 1.8493 | 1.8493 | 1.8493 | 1.8493 | 0.60873 | 0.9961 | 1.365 | 1.6417 | 1.6417 | 1.6417 | 2.3816 | 3.0734 | 3.5266 | 3.7652 | 4.2423 | 4.7194 | 0.87261 | 1.7222 | 2.0667 | 2.0667 | 2.0667 | 2.0667 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2021-01-03 16:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.61158 | 1.0008 | 1.3714 | 1.6494 | 1.6494 | 1.6494 | 2.3435 | 3.0242 | 3.4702 | 3.7049 | 4.1744 | 4.6438 | 0.86879 | 1.7147 | 2.0577 | 2.0577 | 2.0577 | 2.0577 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2021-01-03 17:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.60587 | 0.99142 | 1.3586 | 1.634 | 1.634 | 1.634 | 2.172 | 2.8029 | 3.2163 | 3.4338 | 3.8689 | 4.3041 | 0.83831 | 1.6546 | 1.9855 | 1.9855 | 1.9855 | 1.9855 | 0.49537 | 0.57624 | 0.57624 | 0.57624 | 0.57624 | 0.57624
2021-01-03 18:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.65445 | 1.0709 | 1.4676 | 1.765 | 1.765 | 1.765 | 2.1566 | 2.783 | 3.1935 | 3.4095 | 3.8415 | 4.2736 | 0.88785 | 1.7523 | 2.1028 | 2.1028 | 2.1028 | 2.1028 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2021-01-03 19:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.54871 | 0.89789 | 1.2304 | 1.4799 | 1.4799 | 1.4799 | 2.0577 | 2.6554 | 3.047 | 3.2531 | 3.6653 | 4.0775 | 0.86879 | 1.7147 | 2.0577 | 2.0577 | 2.0577 | 2.0577 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2021-01-03 20:00 | Summer | 1.0288 | 1.4724 | 2.1248 | 2.1248 | 2.1248 | 2.1248 | 0.54585 | 0.89321 | 1.224 | 1.4721 | 1.4721 | 1.4721 | 2.0196 | 2.6062 | 2.9906 | 3.1929 | 3.5974 | 4.002 | 0.92976 | 1.8351 | 2.2021 | 2.2021 | 2.2021 | 2.2021 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2021-01-03 21:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.42868 | 0.70147 | 0.96128 | 1.1561 | 1.1561 | 1.1561 | 1.9434 | 2.5079 | 2.8777 | 3.0724 | 3.4617 | 3.851 | 0.89547 | 1.7674 | 2.1208 | 2.1208 | 2.1208 | 2.1208 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2021-01-03 22:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.46869 | 0.76695 | 1.051 | 1.264 | 1.264 | 1.264 | 1.8862 | 2.4341 | 2.7931 | 2.982 | 3.3599 | 3.7377 | 0.88023 | 1.7373 | 2.0847 | 2.0847 | 2.0847 | 2.0847 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2021-01-03 23:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.50298 | 0.82306 | 1.1279 | 1.3565 | 1.3565 | 1.3565 | 1.7528 | 2.262 | 2.5956 | 2.7712 | 3.1223 | 3.4734 | 0.78877 | 1.5568 | 1.8681 | 1.8681 | 1.8681 | 1.8681 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2021-01-04 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.4544 | 0.74356 | 1.019 | 1.2255 | 1.2255 | 1.2255 | 1.6908 | 2.182 | 2.5038 | 2.6732 | 3.0119 | 3.3506 | 0.78496 | 1.5493 | 1.8591 | 1.8591 | 1.8591 | 1.8591 | 0.41352 | 0.48103 | 0.48103 | 0.48103 | 0.48103 | 0.48103
2021-01-04 01:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.42582 | 0.6968 | 0.95487 | 1.1484 | 1.1484 | 1.1484 | 1.6004 | 2.0653 | 2.3699 | 2.5302 | 2.8508 | 3.1714 | 0.82688 | 1.632 | 1.9584 | 1.9584 | 1.9584 | 1.9584 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2021-01-04 02:00 | Summer | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.54014 | 0.88386 | 1.2112 | 1.4567 | 1.4567 | 1.4567 | 1.5814 | 2.0407 | 2.3417 | 2.5001 | 2.8169 | 3.1337 | 0.67446 | 1.3312 | 1.5974 | 1.5974 | 1.5974 | 1.5974 | 0.43821 | 0.50975 | 0.50975 | 0.50975 | 0.50975 | 0.50975
2021-01-04 03:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.38867 | 0.636 | 0.87156 | 1.0482 | 1.0482 | 1.0482 | 1.6004 | 2.0653 | 2.3699 | 2.5302 | 2.8508 | 3.1714 | 0.72018 | 1.4214 | 1.7057 | 1.7057 | 1.7057 | 1.7057 | 0.43821 | 0.50975 | 0.50975 | 0.50975 | 0.50975 | 0.50975
2021-01-04 04:00 | Summer | 1.3146 | 1.8814 | 2.715 | 2.715 | 2.715 | 2.715 | 0.45694 | 0.74772 | 1.0247 | 1.2324 | 1.2324 | 1.2324 | 1.6195 | 2.0899 | 2.3981 | 2.5603 | 2.8847 | 3.2092 | 0.724 | 1.4289 | 1.7147 | 1.7147 | 1.7147 | 1.7147 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2021-01-04 05:00 | Summer | 1.4289 | 2.045 | 2.9511 | 2.9511 | 2.9511 | 2.9511 | 0.45726 | 0.74824 | 1.0254 | 1.2332 | 1.2332 | 1.2332 | 1.7147 | 2.2128 | 2.5392 | 2.7109 | 3.0544 | 3.3979 | 0.77353 | 1.5267 | 1.832 | 1.832 | 1.832 | 1.832 | 0.51703 | 0.60145 | 0.60145 | 0.60145 | 0.60145 | 0.60145
2021-01-04 06:00 | Summer | 1.3984 | 2.0013 | 2.8879 | 2.8879 | 2.8879 | 2.8879 | 0.563 | 0.92127 | 1.2625 | 1.5184 | 1.5184 | 1.5184 | 1.7719 | 2.2866 | 2.6238 | 2.8013 | 3.1562 | 3.5112 | 0.95644 | 1.8877 | 2.2652 | 2.2652 | 2.2652 | 2.2652 | 0.66653 | 0.77535 | 0.77535 | 0.77535 | 0.77535 | 0.77535
2021-01-04 07:00 | Summer | 2.1233 | 3.0388 | 4.3851 | 4.3851 | 4.3851 | 4.3851 | 0.63445 | 1.0382 | 1.4227 | 1.7111 | 1.7111 | 1.7111 | 2.1148 | 2.7291 | 3.1316 | 3.3435 | 3.7671 | 4.1908 | 1.2194 | 2.4066 | 2.888 | 2.888 | 2.888 | 2.888 | 1.0064 | 1.1707 | 1.1707 | 1.1707 | 1.1707 | 1.1707
2021-01-04 08:00 | Summer | 3.0294 | 4.3355 | 6.2563 | 6.2563 | 6.2563 | 6.2563 | 0.84307 | 1.3796 | 1.8905 | 2.2737 | 2.2737 | 2.2737 | 2.4006 | 3.098 | 3.5548 | 3.7953 | 4.2762 | 4.7571 | 1.2117 | 2.3916 | 2.8699 | 2.8699 | 2.8699 | 2.8699 | 1.086 | 1.2633 | 1.2633 | 1.2633 | 1.2633 | 1.2633
2021-01-04 09:00 | Summer | 2.8388 | 4.0628 | 5.8628 | 5.8628 | 5.8628 | 5.8628 | 0.9631 | 1.576 | 2.1597 | 2.5975 | 2.5975 | 2.5975 | 2.5149 | 3.2455 | 3.7241 | 3.976 | 4.4798 | 4.9836 | 1.2346 | 2.4367 | 2.9241 | 2.9241 | 2.9241 | 2.9241 | 1.1777 | 1.3699 | 1.3699 | 1.3699 | 1.3699 | 1.3699
2021-01-04 10:00 | Summer | 2.7436 | 3.9265 | 5.6661 | 5.6661 | 5.6661 | 5.6661 | 1.0317 | 1.6882 | 2.3135 | 2.7824 | 2.7824 | 2.7824 | 2.7817 | 3.5897 | 4.1191 | 4.3977 | 4.955 | 5.5122 | 1.2308 | 2.4292 | 2.915 | 2.915 | 2.915 | 2.915 | 1.2194 | 1.4184 | 1.4184 | 1.4184 | 1.4184 | 1.4184
2021-01-04 11:00 | Summer | 2.7055 | 3.8719 | 5.5874 | 5.5874 | 5.5874 | 5.5874 | 1.0803 | 1.7677 | 2.4224 | 2.9135 | 2.9135 | 2.9135 | 2.9722 | 3.8356 | 4.4012 | 4.6989 | 5.2943 | 5.8898 | 1.2651 | 2.4969 | 2.9963 | 2.9963 | 2.9963 | 2.9963 | 1.2575 | 1.4628 | 1.4628 | 1.4628 | 1.4628 | 1.4628
2021-01-04 12:00 | Summer | 2.7055 | 3.8719 | 5.5874 | 5.5874 | 5.5874 | 5.5874 | 1.086 | 1.7771 | 2.4353 | 2.9289 | 2.9289 | 2.9289 | 2.9913 | 3.8601 | 4.4294 | 4.729 | 5.3283 | 5.9275 | 1.2727 | 2.5119 | 3.0143 | 3.0143 | 3.0143 | 3.0143 | 1.3337 | 1.5514 | 1.5514 | 1.5514 | 1.5514 | 1.5514
2021-01-04 13:00 | Summer | 2.6483 | 3.7901 | 5.4693 | 5.4693 | 5.4693 | 5.4693 | 1.0117 | 1.6555 | 2.2686 | 2.7285 | 2.7285 | 2.7285 | 2.915 | 3.7618 | 4.3166 | 4.6086 | 5.1925 | 5.7765 | 1.2803 | 2.527 | 3.0324 | 3.0324 | 3.0324 | 3.0324 | 1.2401 | 1.4425 | 1.4425 | 1.4425 | 1.4425 | 1.4425
2021-01-04 14:00 | Summer | 2.5149 | 3.5993 | 5.1939 | 5.1939 | 5.1939 | 5.1939 | 0.9974 | 1.6321 | 2.2366 | 2.69 | 2.69 | 2.69 | 2.8007 | 3.6143 | 4.1473 | 4.4278 | 4.9889 | 5.55 | 1.246 | 2.4593 | 2.9511 | 2.9511 | 2.9511 | 2.9511 | 1.1774 | 1.3696 | 1.3696 | 1.3696 | 1.3696 | 1.3696
2021-01-04 15:00 | Summer | 2.2101 | 3.163 | 4.5643 | 4.5643 | 4.5643 | 4.5643 | 0.77448 | 1.2673 | 1.7367 | 2.0888 | 2.0888 | 2.0888 | 2.553 | 3.2946 | 3.7805 | 4.0362 | 4.5477 | 5.0591 | 1.1508 | 2.2713 | 2.7255 | 2.7255 | 2.7255 | 2.7255 | 1.1432 | 1.3298 | 1.3298 | 1.3298 | 1.3298 | 1.3298
2021-01-04 16:00 | Summer | 2.0386 | 2.9176 | 4.2102 | 4.2102 | 4.2102 | 4.2102 | 0.78306 | 1.2814 | 1.7559 | 2.1119 | 2.1119 | 2.1119 | 2.4768 | 3.1963 | 3.6677 | 3.9158 | 4.4119 | 4.9081 | 1.1089 | 2.1885 | 2.6262 | 2.6262 | 2.6262 | 2.6262 | 1.0669 | 1.2411 | 1.2411 | 1.2411 | 1.2411 | 1.2411
2021-01-04 17:00 | Summer | 1.9829 | 2.8379 | 4.0952 | 4.0952 | 4.0952 | 4.0952 | 0.7802 | 1.2767 | 1.7495 | 2.1042 | 2.1042 | 2.1042 | 2.4578 | 3.1717 | 3.6395 | 3.8856 | 4.378 | 4.8704 | 1.0212 | 2.0156 | 2.4187 | 2.4187 | 2.4187 | 2.4187 | 1.0098 | 1.1746 | 1.1746 | 1.1746 | 1.1746 | 1.1746
2021-01-04 18:00 | Summer | 1.3671 | 1.9565 | 2.8234 | 2.8234 | 2.8234 | 2.8234 | 0.53442 | 0.87451 | 1.1984 | 1.4413 | 1.4413 | 1.4413 | 2.4578 | 3.1717 | 3.6395 | 3.8856 | 4.378 | 4.8704 | 0.88023 | 1.7373 | 2.0847 | 2.0847 | 2.0847 | 2.0847 | 0.76506 | 0.88997 | 0.88997 | 0.88997 | 0.88997 | 0.88997
2021-01-04 19:00 | Summer | 1.105 | 1.5815 | 2.2822 | 2.2822 | 2.2822 | 2.2822 | 0.43154 | 0.70615 | 0.96769 | 1.1638 | 1.1638 | 1.1638 | 2.2182 | 2.8626 | 3.2847 | 3.5069 | 3.9513 | 4.3956 | 0.87261 | 1.7222 | 2.0667 | 2.0667 | 2.0667 | 2.0667 | 0.59316 | 0.69 | 0.69 | 0.69 | 0.69 | 0.69
2021-01-04 20:00 | Summer | 1.1241 | 1.6088 | 2.3215 | 2.3215 | 2.3215 | 2.3215 | 0.45154 | 0.73889 | 1.0125 | 1.2178 | 1.2178 | 1.2178 | 1.9624 | 2.5325 | 2.9059 | 3.1025 | 3.4956 | 3.8887 | 0.91071 | 1.7975 | 2.1569 | 2.1569 | 2.1569 | 2.1569 | 0.57158 | 0.6649 | 0.6649 | 0.6649 | 0.6649 | 0.6649
2021-01-04 21:00 | Summer | 1.086 | 1.5542 | 2.2428 | 2.2428 | 2.2428 | 2.2428 | 0.45726 | 0.74824 | 1.0254 | 1.2332 | 1.2332 | 1.2332 | 1.9243 | 2.4833 | 2.8495 | 3.0422 | 3.4277 | 3.8132 | 0.88785 | 1.7523 | 2.1028 | 2.1028 | 2.1028 | 2.1028 | 0.53347 | 0.62057 | 0.62057 | 0.62057 | 0.62057 | 0.62057
2021-01-04 22:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.40867 | 0.66874 | 0.91642 | 1.1022 | 1.1022 | 1.1022 | 1.9053 | 2.4587 | 2.8213 | 3.0121 | 3.3938 | 3.7755 | 0.87642 | 1.7298 | 2.0757 | 2.0757 | 2.0757 | 2.0757 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2021-01-04 23:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.40867 | 0.66874 | 0.91642 | 1.1022 | 1.1022 | 1.1022 | 1.81 | 2.3358 | 2.6802 | 2.8615 | 3.2241 | 3.5867 | 0.70113 | 1.3838 | 1.6606 | 1.6606 | 1.6606 | 1.6606 | 0.43821 | 0.50975 | 0.50975 | 0.50975 | 0.50975 | 0.50975
2021-01-05 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.39153 | 0.64068 | 0.87797 | 1.0559 | 1.0559 | 1.0559 | 1.6957 | 2.1882 | 2.5109 | 2.6808 | 3.0205 | 3.3602 | 0.70113 | 1.3838 | 1.6606 | 1.6606 | 1.6606 | 1.6606 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2021-01-05 01:00 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.36009 | 0.58924 | 0.80747 | 0.97115 | 0.97115 | 0.97115 | 1.6004 | 2.0653 | 2.3699 | 2.5302 | 2.8508 | 3.1714 | 0.6843 | 1.3506 | 1.6207 | 1.6207 | 1.6207 | 1.6207 | 0.43821 | 0.50975 | 0.50975 | 0.50975 | 0.50975 | 0.50975
2021-01-05 02:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.35437 | 0.57988 | 0.79466 | 0.95574 | 0.95574 | 0.95574 | 1.6195 | 2.0899 | 2.3981 | 2.5603 | 2.8847 | 3.2092 | 0.73162 | 1.444 | 1.7328 | 1.7328 | 1.7328 | 1.7328 | 0.43821 | 0.50975 | 0.50975 | 0.50975 | 0.50975 | 0.50975
2021-01-05 03:00 | Summer | 0.91452 | 1.3088 | 1.8887 | 1.8887 | 1.8887 | 1.8887 | 0.40061 | 0.65554 | 0.89834 | 1.0804 | 1.0804 | 1.0804 | 1.6004 | 2.0653 | 2.3699 | 2.5302 | 2.8508 | 3.1714 | 0.70875 | 1.3989 | 1.6786 | 1.6786 | 1.6786 | 1.6786 | 0.41912 | 0.48755 | 0.48755 | 0.48755 | 0.48755 | 0.48755
2021-01-05 04:00 | Summer | 1.0541 | 1.5086 | 2.177 | 2.177 | 2.177 | 2.177 | 0.48298 | 0.79033 | 1.083 | 1.3026 | 1.3026 | 1.3026 | 1.6576 | 2.1391 | 2.4545 | 2.6205 | 2.9526 | 3.2847 | 0.62873 | 1.2409 | 1.4891 | 1.4891 | 1.4891 | 1.4891 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2021-01-05 05:00 | Summer | 1.2575 | 1.7996 | 2.5969 | 2.5969 | 2.5969 | 2.5969 | 0.43154 | 0.70615 | 0.96769 | 1.1638 | 1.1638 | 1.1638 | 1.7338 | 2.2374 | 2.5674 | 2.741 | 3.0884 | 3.4357 | 0.78496 | 1.5493 | 1.8591 | 1.8591 | 1.8591 | 1.8591 | 0.51419 | 0.59814 | 0.59814 | 0.59814 | 0.59814 | 0.59814
2021-01-05 06:00 | Summer | 1.2956 | 1.8542 | 2.6756 | 2.6756 | 2.6756 | 2.6756 | 0.51156 | 0.83709 | 1.1471 | 1.3797 | 1.3797 | 1.3797 | 1.81 | 2.3358 | 2.6802 | 2.8615 | 3.2241 | 3.5867 | 0.71637 | 1.4139 | 1.6967 | 1.6967 | 1.6967 | 1.6967 | 0.62783 | 0.73033 | 0.73033 | 0.73033 | 0.73033 | 0.73033
2021-01-05 07:00 | Summer | 1.9325 | 2.7657 | 3.991 | 3.991 | 3.991 | 3.991 | 0.62873 | 1.0288 | 1.4099 | 1.6957 | 1.6957 | 1.6957 | 2.25 | 2.9036 | 3.3318 | 3.5571 | 4.0079 | 4.4586 | 1.1965 | 2.3615 | 2.8338 | 2.8338 | 2.8338 | 2.8338 | 0.89547 | 1.0417 | 1.0417 | 1.0417 | 1.0417 | 1.0417
2021-01-05 08:00 | Summer | 2.2603 | 3.2348 | 4.6679 | 4.6679 | 4.6679 | 4.6679 | 0.72876 | 1.1925 | 1.6342 | 1.9654 | 1.9654 | 1.9654 | 2.4197 | 3.1225 | 3.583 | 3.8254 | 4.3101 | 4.7949 | 1.1851 | 2.3389 | 2.8067 | 2.8067 | 2.8067 | 2.8067 | 1.0479 | 1.219 | 1.219 | 1.219 | 1.219 | 1.219
2021-01-05 09:00 | Summer | 2.4578 | 3.5175 | 5.0759 | 5.0759 | 5.0759 | 5.0759 | 0.81735 | 1.3375 | 1.8328 | 2.2044 | 2.2044 | 2.2044 | 2.6896 | 3.4709 | 3.9828 | 4.2522 | 4.791 | 5.3298 | 1.1927 | 2.354 | 2.8248 | 2.8248 | 2.8248 | 2.8248 | 1.1241 | 1.3076 | 1.3076 | 1.3076 | 1.3076 | 1.3076
2021-01-05 10:00 | Summer | 2.4768 | 3.5447 | 5.1152 | 5.1152 | 5.1152 | 5.1152 | 0.82592 | 1.3515 | 1.8521 | 2.2275 | 2.2275 | 2.2275 | 2.8198 | 3.6389 | 4.1755 | 4.4579 | 5.0228 | 5.5877 | 1.1851 | 2.3389 | 2.8067 | 2.8067 | 2.8067 | 2.8067 | 1.1852 | 1.3787 | 1.3787 | 1.3787 | 1.3787 | 1.3787
2021-01-05 11:00 | Summer | 2.6293 | 3.7629 | 5.43 | 5.43 | 5.43 | 5.43 | 0.87165 | 1.4263 | 1.9546 | 2.3508 | 2.3508 | 2.3508 | 2.9341 | 3.7864 | 4.3448 | 4.6387 | 5.2265 | 5.8142 | 1.2422 | 2.4518 | 2.9421 | 2.9421 | 2.9421 | 2.9421 | 1.2384 | 1.4406 | 1.4406 | 1.4406 | 1.4406 | 1.4406
2021-01-05 12:00 | Summer | 2.6102 | 3.7356 | 5.3906 | 5.3906 | 5.3906 | 5.3906 | 0.97739 | 1.5994 | 2.1917 | 2.636 | 2.636 | 2.636 | 2.915 | 3.7618 | 4.3166 | 4.6086 | 5.1925 | 5.7765 | 1.1508 | 2.2713 | 2.7255 | 2.7255 | 2.7255 | 2.7255 | 1.2575 | 1.4628 | 1.4628 | 1.4628 | 1.4628 | 1.4628
2021-01-05 13:00 | Summer | 2.553 | 3.6538 | 5.2726 | 5.2726 | 5.2726 | 5.2726 | 0.90023 | 1.4731 | 2.0187 | 2.4279 | 2.4279 | 2.4279 | 2.9341 | 3.7864 | 4.3448 | 4.6387 | 5.2265 | 5.8142 | 1.1089 | 2.1885 | 2.6262 | 2.6262 | 2.6262 | 2.6262 | 1.2384 | 1.4406 | 1.4406 | 1.4406 | 1.4406 | 1.4406
2021-01-05 14:00 | Summer | 2.5911 | 3.7083 | 5.3513 | 5.3513 | 5.3513 | 5.3513 | 0.9088 | 1.4871 | 2.0379 | 2.451 | 2.451 | 2.451 | 3.1056 | 4.0077 | 4.5987 | 4.9098 | 5.5319 | 6.154 | 1.1317 | 2.2337 | 2.6804 | 2.6804 | 2.6804 | 2.6804 | 1.2384 | 1.4406 | 1.4406 | 1.4406 | 1.4406 | 1.4406
2021-01-05 15:00 | Summer | 2.6293 | 3.7629 | 5.43 | 5.43 | 5.43 | 5.43 | 0.96882 | 1.5853 | 2.1725 | 2.6129 | 2.6129 | 2.6129 | 2.9722 | 3.8356 | 4.4012 | 4.6989 | 5.2943 | 5.8898 | 1.166 | 2.3013 | 2.7616 | 2.7616 | 2.7616 | 2.7616 | 1.2194 | 1.4184 | 1.4184 | 1.4184 | 1.4184 | 1.4184
2021-01-05 16:00 | Summer | 2.6293 | 3.7629 | 5.43 | 5.43 | 5.43 | 5.43 | 0.94535 | 1.5469 | 2.1199 | 2.5496 | 2.5496 | 2.5496 | 2.9531 | 3.811 | 4.373 | 4.6688 | 5.2604 | 5.852 | 1.0784 | 2.1284 | 2.554 | 2.554 | 2.554 | 2.554 | 1.2384 | 1.4406 | 1.4406 | 1.4406 | 1.4406 | 1.4406
2021-01-05 17:00 | Summer | 2.3816 | 3.4084 | 4.9185 | 4.9185 | 4.9185 | 4.9185 | 0.99168 | 1.6228 | 2.2238 | 2.6745 | 2.6745 | 2.6745 | 2.915 | 3.7618 | 4.3166 | 4.6086 | 5.1925 | 5.7765 | 1.0479 | 2.0682 | 2.4818 | 2.4818 | 2.4818 | 2.4818 | 1.2238 | 1.4236 | 1.4236 | 1.4236 | 1.4236 | 1.4236
2021-01-05 18:00 | Summer | 1.7025 | 2.4365 | 3.516 | 3.516 | 3.516 | 3.516 | 0.68903 | 1.1275 | 1.5451 | 1.8583 | 1.8583 | 1.8583 | 2.6864 | 3.4668 | 3.978 | 4.2471 | 4.7853 | 5.3234 | 0.92976 | 1.8351 | 2.2021 | 2.2021 | 2.2021 | 2.2021 | 0.82234 | 0.9566 | 0.9566 | 0.9566 | 0.9566 | 0.9566
2021-01-05 19:00 | Summer | 1.2384 | 1.7724 | 2.5576 | 2.5576 | 2.5576 | 2.5576 | 0.49863 | 0.81594 | 1.1181 | 1.3448 | 1.3448 | 1.3448 | 2.4969 | 3.2222 | 3.6974 | 3.9475 | 4.4477 | 4.9479 | 0.95263 | 1.8802 | 2.2562 | 2.2562 | 2.2562 | 2.2562 | 0.61958 | 0.72073 | 0.72073 | 0.72073 | 0.72073 | 0.72073
2021-01-05 20:00 | Summer | 1.2194 | 1.7451 | 2.5183 | 2.5183 | 2.5183 | 2.5183 | 0.47441 | 0.7763 | 1.0638 | 1.2795 | 1.2795 | 1.2795 | 2.172 | 2.8029 | 3.2163 | 3.4338 | 3.8689 | 4.3041 | 0.89166 | 1.7599 | 2.1118 | 2.1118 | 2.1118 | 2.1118 | 0.57158 | 0.6649 | 0.6649 | 0.6649 | 0.6649 | 0.6649
2021-01-05 21:00 | Summer | 1.1307 | 1.6182 | 2.3352 | 2.3352 | 2.3352 | 2.3352 | 0.47155 | 0.77162 | 1.0574 | 1.2717 | 1.2717 | 1.2717 | 1.9957 | 2.5754 | 2.9552 | 3.1551 | 3.5549 | 3.9546 | 0.83831 | 1.6546 | 1.9855 | 1.9855 | 1.9855 | 1.9855 | 0.51442 | 0.59841 | 0.59841 | 0.59841 | 0.59841 | 0.59841
2021-01-05 22:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.47441 | 0.7763 | 1.0638 | 1.2795 | 1.2795 | 1.2795 | 1.9053 | 2.4587 | 2.8213 | 3.0121 | 3.3938 | 3.7755 | 0.80021 | 1.5794 | 1.8952 | 1.8952 | 1.8952 | 1.8952 | 0.47631 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
2021-01-05 23:00 | Summer | 1.0098 | 1.4452 | 2.0854 | 2.0854 | 2.0854 | 2.0854 | 0.45726 | 0.74824 | 1.0254 | 1.2332 | 1.2332 | 1.2332 | 1.7873 | 2.3065 | 2.6466 | 2.8257 | 3.1837 | 3.5418 | 0.69732 | 1.3763 | 1.6516 | 1.6516 | 1.6516 | 1.6516 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2021-01-06 | Summer | 0.97168 | 1.3906 | 2.0067 | 2.0067 | 2.0067 | 2.0067 | 0.42582 | 0.6968 | 0.95487 | 1.1484 | 1.1484 | 1.1484 | 1.674 | 2.1603 | 2.4789 | 2.6466 | 2.982 | 3.3173 | 0.71637 | 1.4139 | 1.6967 | 1.6967 | 1.6967 | 1.6967 | 0.43823 | 0.50978 | 0.50978 | 0.50978 | 0.50978 | 0.50978
2021-01-06 01:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.44297 | 0.72486 | 0.99332 | 1.1947 | 1.1947 | 1.1947 | 1.6576 | 2.1391 | 2.4545 | 2.6205 | 2.9526 | 3.2847 | 0.67827 | 1.3387 | 1.6064 | 1.6064 | 1.6064 | 1.6064 | 0.43821 | 0.50975 | 0.50975 | 0.50975 | 0.50975 | 0.50975
2021-01-06 02:00 | Summer | 0.93358 | 1.3361 | 1.928 | 1.928 | 1.928 | 1.928 | 0.45154 | 0.73889 | 1.0125 | 1.2178 | 1.2178 | 1.2178 | 1.5623 | 2.0161 | 2.3135 | 2.4699 | 2.7829 | 3.0959 | 0.58301 | 1.1507 | 1.3808 | 1.3808 | 1.3808 | 1.3808 | 0.43821 | 0.50975 | 0.50975 | 0.50975 | 0.50975 | 0.50975
2021-01-06 03:00 | Summer | 0.95263 | 1.3634 | 1.9674 | 1.9674 | 1.9674 | 1.9674 | 0.4063 | 0.66485 | 0.91109 | 1.0958 | 1.0958 | 1.0958 | 1.5623 | 2.0161 | 2.3135 | 2.4699 | 2.7829 | 3.0959 | 0.65922 | 1.3011 | 1.5613 | 1.5613 | 1.5613 | 1.5613 | 0.43821 | 0.50975 | 0.50975 | 0.50975 | 0.50975 | 0.50975
2021-01-06 04:00 | Summer | 1.0957 | 1.5681 | 2.2628 | 2.2628 | 2.2628 | 2.2628 | 0.47726 | 0.78098 | 1.0702 | 1.2872 | 1.2872 | 1.2872 | 1.6576 | 2.1391 | 2.4545 | 2.6205 | 2.9526 | 3.2847 | 0.65922 | 1.3011 | 1.5613 | 1.5613 | 1.5613 | 1.5613 | 0.45726 | 0.53192 | 0.53192 | 0.53192 | 0.53192 | 0.53192
2021-01-06 05:00 | Summer | 1.2383 | 1.7722 | 2.5573 | 2.5573 | 2.5573 | 2.5573 | 0.46297 | 0.75759 | 1.0382 | 1.2486 | 1.2486 | 1.2486 | 1.7147 | 2.2128 | 2.5392 | 2.7109 | 3.0544 | 3.3979 | 0.70494 | 1.3913 | 1.6696 | 1.6696 | 1.6696 | 1.6696 | 0.55252 | 0.64273 | 0.64273 | 0.64273 | 0.64273 | 0.64273
2021-01-06 06:00 | Summer | 1.3361 | 1.9122 | 2.7594 | 2.7594 | 2.7594 | 2.7594 | 0.52585 | 0.86048 | 1.1792 | 1.4182 | 1.4182 | 1.4182 | 1.81 | 2.3358 | 2.6802 | 2.8615 | 3.2241 | 3.5867 | 0.78877 | 1.5568 | 1.8681 | 1.8681 | 1.8681 | 1.8681 | 0.64652 | 0.75207 | 0.75207 | 0.75207 | 0.75207 | 0.75207
2021-01-06 07:00 | Summer | 1.796 | 2.5704 | 3.7092 | 3.7092 | 3.7092 | 3.7092 | 0.67731 | 1.1083 | 1.5188 | 1.8267 | 1.8267 | 1.8267 | 2.172 | 2.8029 | 3.2163 | 3.4338 | 3.8689 | 4.3041 | 1.1317 | 2.2337 | 2.6804 | 2.6804 | 2.6804 | 2.6804 | 0.95263 | 1.1082 | 1.1082 | 1.1082 | 1.1082 | 1.1082
2021-01-06 08:00 | Summer | 2.373 | 3.3961 | 4.9008 | 4.9008 | 4.9008 | 4.9008 | 0.86594 | 1.417 | 1.9418 | 2.3354 | 2.3354 | 2.3354 | 2.4197 | 3.1225 | 3.583 | 3.8254 | 4.3101 | 4.7949 | 1.1089 | 2.1885 | 2.6262 | 2.6262 | 2.6262 | 2.6262 | 1.0669 | 1.2411 | 1.2411 | 1.2411 | 1.2411 | 1.2411
2021-01-06 09:00 | Summer | 2.4006 | 3.4357 | 4.9578 | 4.9578 | 4.9578 | 4.9578 | 0.83736 | 1.3702 | 1.8777 | 2.2583 | 2.2583 | 2.2583 | 2.4768 | 3.1963 | 3.6677 | 3.9158 | 4.4119 | 4.9081 | 1.1127 | 2.1961 | 2.6353 | 2.6353 | 2.6353 | 2.6353 | 1.105 | 1.2855 | 1.2855 | 1.2855 | 1.2855 | 1.2855
2021-01-06 10:00 | Summer | 2.2291 | 3.1903 | 4.6037 | 4.6037 | 4.6037 | 4.6037 | 0.88308 | 1.445 | 1.9802 | 2.3816 | 2.3816 | 2.3816 | 2.553 | 3.2946 | 3.7805 | 4.0362 | 4.5477 | 5.0591 | 0.98692 | 1.9479 | 2.3374 | 2.3374 | 2.3374 | 2.3374 | 1.1622 | 1.352 | 1.352 | 1.352 | 1.352 | 1.352
2021-01-06 11:00 | Summer | 2.3625 | 3.3811 | 4.8791 | 4.8791 | 4.8791 | 4.8791 | 0.86022 | 1.4076 | 1.929 | 2.32 | 2.32 | 2.32 | 2.5911 | 3.3438 | 3.8369 | 4.0965 | 4.6156 | 5.1347 | 1.0517 | 2.0757 | 2.4909 | 2.4909 | 2.4909 | 2.4909 | 1.3527 | 1.5736 | 1.5736 | 1.5736 | 1.5736 | 1.5736
2021-01-06 12:00 | Summer | 2.4387 | 3.4902 | 5.0365 | 5.0365 | 5.0365 | 5.0365 | 0.94024 | 1.5386 | 2.1084 | 2.5358 | 2.5358 | 2.5358 | 2.7436 | 3.5405 | 4.0627 | 4.3375 | 4.8871 | 5.4367 | 1.025 | 2.0231 | 2.4277 | 2.4277 | 2.4277 | 2.4277 | 1.2956 | 1.5071 | 1.5071 | 1.5071 | 1.5071 | 1.5071

## Daily Load - Winter
| Hobart Short | [11 empty] | Electricity House | [11 empty] | Edinburgh | [11 empty] | Edmund Barton | [11 empty] | Hobart Long
| Average Winter Day Load (MW/MVA) | [5 empty] | Peak Winter Day Load (MW/MVA) | [5 empty] | Average Winter Day Load (MW/MVA) | [5 empty] | Peak Winter Day Load (MW/MVA) | [5 empty] | Average Winter Day Load (MW/MVA) | [5 empty] | Peak Winter Day Load (MW/MVA) | [5 empty] | Average Winter Day Load (MW/MVA) | [5 empty] | Peak Winter Day Load (MW/MVA) | [5 empty] | Average Winter Day Load (MW/MVA) | [5 empty] | Peak Winter Day Load (MW/MVA)
Time | 2020 | 2025 | 2026 | 2027 | 2028 | 2029 | 2020 | 2025 | 2026 | 2027 | 2028 | 2029 | 2020 | 2025 | 2026 | 2027 | 2028 | 2029 | 2020 | 2025 | 2026 | 2027 | 2028 | 2029 | 2020 | 2025 | 2026 | 2027 | 2028 | 2029 | 2020 | 2025 | 2026 | 2027 | 2028 | 2029 | 2020 | 2025 | 2026 | 2027 | 2028 | 2029 | 2020 | 2025 | 2026 | 2027 | 2028 | 2029 | 2020 | 2025 | 2026 | 2027 | 2028 | 2029 | 2020 | 2025 | 2026 | 2027 | 2028 | 2029
0:00 | 0.73391 | 1.1285 | 1.7076 | 1.7076 | 1.7076 | 1.7076 | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.41886 | 0.45508 | 0.48958 | 0.51545 | 0.51545 | 0.51545 | 0.42582 | 0.42582 | 0.42582 | 0.42582 | 0.42582 | 0.42582 | 1.7096 | 2.466 | 2.9616 | 3.2225 | 3.7442 | 4.2658 | 1.6957 | 2.446 | 2.9375 | 3.1963 | 3.7137 | 4.2311 | 0.56442 | 1.5332 | 1.923 | 1.923 | 1.923 | 1.923 | 0.5792 | 1.5733 | 1.9733 | 1.9733 | 1.9733 | 1.9733 | 0.71374 | 0.90593 | 0.90593 | 0.90593 | 0.90593 | 0.90593 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
1:00 | 0.73137 | 1.1246 | 1.7017 | 1.7017 | 1.7017 | 1.7017 | 1.0098 | 1.5527 | 2.3495 | 2.3495 | 2.3495 | 2.3495 | 0.41579 | 0.45139 | 0.48529 | 0.51072 | 0.51072 | 0.51072 | 0.42296 | 0.42296 | 0.42296 | 0.42296 | 0.42296 | 0.42296 | 1.6373 | 2.3618 | 2.8364 | 3.0862 | 3.5858 | 4.0855 | 1.7338 | 2.5009 | 3.0036 | 3.2681 | 3.7972 | 4.3262 | 0.54836 | 1.4896 | 1.8683 | 1.8683 | 1.8683 | 1.8683 | 0.56776 | 1.5423 | 1.9344 | 1.9344 | 1.9344 | 1.9344 | 0.70951 | 0.90056 | 0.90056 | 0.90056 | 0.90056 | 0.90056 | 0.7621 | 0.96732 | 0.96732 | 0.96732 | 0.96732 | 0.96732
2:00 | 0.75778 | 1.1652 | 1.7631 | 1.7631 | 1.7631 | 1.7631 | 1.1796 | 1.8138 | 2.7446 | 2.7446 | 2.7446 | 2.7446 | 0.43182 | 0.46799 | 0.50245 | 0.52829 | 0.52829 | 0.52829 | 0.46869 | 0.46869 | 0.46869 | 0.46869 | 0.46869 | 0.46869 | 1.6116 | 2.3247 | 2.7919 | 3.0378 | 3.5296 | 4.0213 | 1.6806 | 2.4242 | 2.9114 | 3.1678 | 3.6806 | 4.1935 | 0.53936 | 1.4651 | 1.8376 | 1.8376 | 1.8376 | 1.8376 | 0.61349 | 1.6665 | 2.0902 | 2.0902 | 2.0902 | 2.0902 | 0.74873 | 0.95035 | 0.95035 | 0.95035 | 0.95035 | 0.95035 | 0.78115 | 0.9915 | 0.9915 | 0.9915 | 0.9915 | 0.9915
3:00 | 0.76686 | 1.1791 | 1.7843 | 1.7843 | 1.7843 | 1.7843 | 1.1813 | 1.8163 | 2.7485 | 2.7485 | 2.7485 | 2.7485 | 0.42336 | 0.45927 | 0.49347 | 0.51912 | 0.51912 | 0.51912 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 0.44583 | 1.6054 | 2.3158 | 2.7812 | 3.0262 | 3.5161 | 4.006 | 1.6385 | 2.3635 | 2.8385 | 3.0885 | 3.5885 | 4.0885 | 0.53623 | 1.4566 | 1.827 | 1.827 | 1.827 | 1.827 | 0.56014 | 1.5216 | 1.9084 | 1.9084 | 1.9084 | 1.9084 | 0.75735 | 0.96128 | 0.96128 | 0.96128 | 0.96128 | 0.96128 | 0.80021 | 1.0157 | 1.0157 | 1.0157 | 1.0157 | 1.0157
4:00 | 0.80646 | 1.24 | 1.8764 | 1.8764 | 1.8764 | 1.8764 | 1.2002 | 1.8454 | 2.7925 | 2.7925 | 2.7925 | 2.7925 | 0.44802 | 0.48474 | 0.51971 | 0.54594 | 0.54594 | 0.54594 | 0.4544 | 0.4544 | 0.4544 | 0.4544 | 0.4544 | 0.4544 | 1.6436 | 2.3709 | 2.8474 | 3.0981 | 3.5997 | 4.1013 | 1.6766 | 2.4185 | 2.9045 | 3.1603 | 3.672 | 4.1836 | 0.54366 | 1.4768 | 1.8523 | 1.8523 | 1.8523 | 1.8523 | 0.5792 | 1.5733 | 1.9733 | 1.9733 | 1.9733 | 1.9733 | 0.80489 | 1.0216 | 1.0216 | 1.0216 | 1.0216 | 1.0216 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
5:00 | 0.87019 | 1.338 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 1.3328 | 2.0494 | 3.1011 | 3.1011 | 3.1011 | 3.1011 | 0.55114 | 0.59383 | 0.63449 | 0.66498 | 0.66498 | 0.66498 | 0.62301 | 0.62301 | 0.62301 | 0.62301 | 0.62301 | 0.62301 | 1.762 | 2.5416 | 3.0524 | 3.3213 | 3.8589 | 4.3966 | 1.7719 | 2.5559 | 3.0696 | 3.3399 | 3.8806 | 4.4213 | 0.61345 | 1.6664 | 2.0901 | 2.0901 | 2.0901 | 2.0901 | 0.724 | 1.9667 | 2.4667 | 2.4667 | 2.4667 | 2.4667 | 1.0161 | 1.2898 | 1.2898 | 1.2898 | 1.2898 | 1.2898 | 1.1782 | 1.4955 | 1.4955 | 1.4955 | 1.4955 | 1.4955
6:00 | 0.97419 | 1.4979 | 2.2667 | 2.2667 | 2.2667 | 2.2667 | 1.6669 | 2.5631 | 3.8785 | 3.8785 | 3.8785 | 3.8785 | 0.64494 | 0.69719 | 0.74696 | 0.78428 | 0.78428 | 0.78428 | 0.70589 | 0.70589 | 0.70589 | 0.70589 | 0.70589 | 0.70589 | 1.9521 | 2.8158 | 3.3817 | 3.6796 | 4.2752 | 4.8709 | 1.81 | 2.6109 | 3.1356 | 3.4117 | 3.9641 | 4.5164 | 0.66194 | 1.7981 | 2.2553 | 2.2553 | 2.2553 | 2.2553 | 0.81926 | 2.2254 | 2.7912 | 2.7912 | 2.7912 | 2.7912 | 1.2369 | 1.57 | 1.57 | 1.57 | 1.57 | 1.57 | 1.5241 | 1.9345 | 1.9345 | 1.9345 | 1.9345 | 1.9345
7:00 | 1.215 | 1.8682 | 2.8269 | 2.8269 | 2.8269 | 2.8269 | 2.1631 | 3.326 | 5.0328 | 5.0328 | 5.0328 | 5.0328 | 0.77553 | 0.8406 | 0.90258 | 0.94906 | 0.94906 | 0.94906 | 0.79163 | 0.79163 | 0.79163 | 0.79163 | 0.79163 | 0.79163 | 2.1815 | 3.1468 | 3.7792 | 4.112 | 4.7777 | 5.4434 | 2.1148 | 3.0506 | 3.6637 | 3.9863 | 4.6317 | 5.277 | 0.75007 | 2.0375 | 2.5555 | 2.5555 | 2.5555 | 2.5555 | 0.94882 | 2.5774 | 3.2326 | 3.2326 | 3.2326 | 3.2326 | 1.5074 | 1.9133 | 1.9133 | 1.9133 | 1.9133 | 1.9133 | 1.9815 | 2.515 | 2.515 | 2.515 | 2.515 | 2.515
8:00 | 1.3678 | 2.1031 | 3.1825 | 3.1825 | 3.1825 | 3.1825 | 3.6604 | 5.6283 | 8.5168 | 8.5168 | 8.5168 | 8.5168 | 0.85422 | 0.92417 | 0.99078 | 1.0407 | 1.0407 | 1.0407 | 1.6861 | 1.6861 | 1.6861 | 1.6861 | 1.6861 | 1.6861 | 2.3423 | 3.3787 | 4.0577 | 4.4151 | 5.1299 | 5.8446 | 2.2863 | 3.2979 | 3.9607 | 4.3096 | 5.0072 | 5.7049 | 0.79186 | 2.151 | 2.6979 | 2.6979 | 2.6979 | 2.6979 | 0.97549 | 2.6498 | 3.3235 | 3.3235 | 3.3235 | 3.3235 | 1.6578 | 2.1043 | 2.1043 | 2.1043 | 2.1043 | 2.1043 | 2.108 | 2.6756 | 2.6756 | 2.6756 | 2.6756 | 2.6756
9:00 | 1.3741 | 2.1128 | 3.1971 | 3.1971 | 3.1971 | 3.1971 | 3.6962 | 5.6833 | 8.6 | 8.6 | 8.6 | 8.6 | 0.86749 | 0.93753 | 1.0042 | 1.0543 | 1.0543 | 1.0543 | 1.3203 | 1.3203 | 1.3203 | 1.3203 | 1.3203 | 1.3203 | 2.3766 | 3.4281 | 4.1171 | 4.4797 | 5.2049 | 5.9301 | 2.2291 | 3.2155 | 3.8617 | 4.2018 | 4.8821 | 5.5623 | 0.79073 | 2.1479 | 2.694 | 2.694 | 2.694 | 2.694 | 1.086 | 2.95 | 3.7 | 3.7 | 3.7 | 3.7 | 1.6909 | 2.1463 | 2.1463 | 2.1463 | 2.1463 | 2.1463 | 2.1529 | 2.7327 | 2.7327 | 2.7327 | 2.7327 | 2.7327
10:00 | 1.3551 | 2.0837 | 3.153 | 3.153 | 3.153 | 3.153 | 3.6009 | 5.5369 | 8.3784 | 8.3784 | 8.3784 | 8.3784 | 0.84477 | 0.91217 | 0.97635 | 1.0245 | 1.0245 | 1.0245 | 1.186 | 1.186 | 1.186 | 1.186 | 1.186 | 1.186 | 2.4119 | 3.4792 | 4.1784 | 4.5464 | 5.2824 | 6.0184 | 2.3263 | 3.3557 | 4.0301 | 4.385 | 5.0949 | 5.8048 | 0.77157 | 2.0959 | 2.6288 | 2.6288 | 2.6288 | 2.6288 | 0.92214 | 2.5049 | 3.1418 | 3.1418 | 3.1418 | 3.1418 | 1.6927 | 2.1485 | 2.1485 | 2.1485 | 2.1485 | 2.1485 | 2.0386 | 2.5876 | 2.5876 | 2.5876 | 2.5876 | 2.5876
11:00 | 1.3511 | 2.0775 | 3.1437 | 3.1437 | 3.1437 | 3.1437 | 3.6009 | 5.5369 | 8.3784 | 8.3784 | 8.3784 | 8.3784 | 0.82577 | 0.89541 | 0.96174 | 1.0115 | 1.0115 | 1.0115 | 1.1917 | 1.1917 | 1.1917 | 1.1917 | 1.1917 | 1.1917 | 2.4043 | 3.4682 | 4.1652 | 4.532 | 5.2657 | 5.9994 | 2.3625 | 3.4079 | 4.0927 | 4.4532 | 5.1741 | 5.8951 | 0.75076 | 2.0394 | 2.5578 | 2.5578 | 2.5578 | 2.5578 | 0.89547 | 2.4325 | 3.0509 | 3.0509 | 3.0509 | 3.0509 | 1.6885 | 2.1432 | 2.1432 | 2.1432 | 2.1432 | 2.1432 | 2.896 | 3.6758 | 3.6758 | 3.6758 | 3.6758 | 3.6758
12:00 | 1.3528 | 2.0801 | 3.1475 | 3.1475 | 3.1475 | 3.1475 | 3.62 | 5.5662 | 8.4227 | 8.4227 | 8.4227 | 8.4227 | 0.81489 | 0.88203 | 0.94597 | 0.99393 | 0.99393 | 0.99393 | 1.1289 | 1.1289 | 1.1289 | 1.1289 | 1.1289 | 1.1289 | 2.4105 | 3.477 | 4.1758 | 4.5436 | 5.2792 | 6.0147 | 2.4387 | 3.5178 | 4.2248 | 4.5969 | 5.3411 | 6.0852 | 0.74319 | 2.0188 | 2.5321 | 2.5321 | 2.5321 | 2.5321 | 0.81545 | 2.2151 | 2.7782 | 2.7782 | 2.7782 | 2.7782 | 1.6593 | 2.1061 | 2.1061 | 2.1061 | 2.1061 | 2.1061 | 2.915 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
13:00 | 1.3377 | 2.0568 | 3.1124 | 3.1124 | 3.1124 | 3.1124 | 2.2482 | 3.4569 | 5.2309 | 5.2309 | 5.2309 | 5.2309 | 0.80037 | 0.86611 | 0.92872 | 0.97568 | 0.97568 | 0.97568 | 1.4004 | 1.4004 | 1.4004 | 1.4004 | 1.4004 | 1.4004 | 2.4082 | 3.4738 | 4.1719 | 4.5393 | 5.2742 | 6.0091 | 3.277 | 4.727 | 5.677 | 6.177 | 7.177 | 8.177 | 0.73282 | 1.9906 | 2.4967 | 2.4967 | 2.4967 | 2.4967 | 0.82688 | 2.2461 | 2.8172 | 2.8172 | 2.8172 | 2.8172 | 1.6261 | 2.064 | 2.064 | 2.064 | 2.064 | 2.064 | 1.9624 | 2.4908 | 2.4908 | 2.4908 | 2.4908 | 2.4908
14:00 | 1.3335 | 2.0504 | 3.1026 | 3.1026 | 3.1026 | 3.1026 | 2.2291 | 3.4276 | 5.1866 | 5.1866 | 5.1866 | 5.1866 | 0.79509 | 0.85956 | 0.92096 | 0.96701 | 0.96701 | 0.96701 | 0.93738 | 0.93738 | 0.93738 | 0.93738 | 0.93738 | 0.93738 | 2.3762 | 3.4277 | 4.1165 | 4.4791 | 5.2042 | 5.9293 | 2.3244 | 3.3529 | 4.0267 | 4.3814 | 5.0907 | 5.8 | 0.73259 | 1.99 | 2.4959 | 2.4959 | 2.4959 | 2.4959 | 0.80783 | 2.1944 | 2.7523 | 2.7523 | 2.7523 | 2.7523 | 1.5727 | 1.9961 | 1.9961 | 1.9961 | 1.9961 | 1.9961 | 1.9624 | 2.4908 | 2.4908 | 2.4908 | 2.4908 | 2.4908
15:00 | 1.3223 | 2.0331 | 3.0765 | 3.0765 | 3.0765 | 3.0765 | 2.1529 | 3.3104 | 5.0093 | 5.0093 | 5.0093 | 5.0093 | 0.78622 | 0.85152 | 0.91371 | 0.96036 | 0.96036 | 0.96036 | 0.87737 | 0.87737 | 0.87737 | 0.87737 | 0.87737 | 0.87737 | 2.3475 | 3.3862 | 4.0668 | 4.425 | 5.1413 | 5.8577 | 2.4197 | 3.4903 | 4.1918 | 4.561 | 5.2993 | 6.0377 | 0.73867 | 2.0065 | 2.5167 | 2.5167 | 2.5167 | 2.5167 | 0.81926 | 2.2254 | 2.7912 | 2.7912 | 2.7912 | 2.7912 | 1.5243 | 1.9348 | 1.9348 | 1.9348 | 1.9348 | 1.9348 | 1.9815 | 2.515 | 2.515 | 2.515 | 2.515 | 2.515
16:00 | 1.3082 | 2.0115 | 3.0438 | 3.0438 | 3.0438 | 3.0438 | 2.0767 | 3.1932 | 4.832 | 4.832 | 4.832 | 4.832 | 0.78543 | 0.85156 | 0.91454 | 0.96177 | 0.96177 | 0.96177 | 0.8345 | 0.8345 | 0.8345 | 0.8345 | 0.8345 | 0.8345 | 2.3511 | 3.3914 | 4.073 | 4.4318 | 5.1492 | 5.8667 | 2.2101 | 3.188 | 3.8287 | 4.1659 | 4.8403 | 5.5147 | 0.74839 | 2.0329 | 2.5498 | 2.5498 | 2.5498 | 2.5498 | 0.83831 | 2.2772 | 2.8561 | 2.8561 | 2.8561 | 2.8561 | 1.4881 | 1.8888 | 1.8888 | 1.8888 | 1.8888 | 1.8888 | 1.9434 | 2.4667 | 2.4667 | 2.4667 | 2.4667 | 2.4667
17:00 | 1.2427 | 1.9107 | 2.8913 | 2.8913 | 2.8913 | 2.8913 | 2.0377 | 3.1333 | 4.7412 | 4.7412 | 4.7412 | 4.7412 | 0.75923 | 0.82426 | 0.88621 | 0.93266 | 0.93266 | 0.93266 | 0.75162 | 0.75162 | 0.75162 | 0.75162 | 0.75162 | 0.75162 | 2.4224 | 3.4943 | 4.1965 | 4.5661 | 5.3053 | 6.0445 | 2.2863 | 3.2979 | 3.9607 | 4.3096 | 5.0072 | 5.7049 | 0.76235 | 2.0708 | 2.5973 | 2.5973 | 2.5973 | 2.5973 | 0.86879 | 2.36 | 2.96 | 2.96 | 2.96 | 2.96 | 1.4285 | 1.8132 | 1.8132 | 1.8132 | 1.8132 | 1.8132 | 1.8139 | 2.3023 | 2.3023 | 2.3023 | 2.3023 | 2.3023
18:00 | 1.0641 | 1.6361 | 2.4758 | 2.4758 | 2.4758 | 2.4758 | 1.6891 | 2.5971 | 3.93 | 3.93 | 3.93 | 3.93 | 0.67734 | 0.73372 | 0.78741 | 0.82768 | 0.82768 | 0.82768 | 0.69446 | 0.69446 | 0.69446 | 0.69446 | 0.69446 | 0.69446 | 2.4058 | 3.4703 | 4.1677 | 4.5347 | 5.2689 | 6.003 | 2.2673 | 3.2705 | 3.9277 | 4.2736 | 4.9655 | 5.6574 | 0.75961 | 2.0634 | 2.588 | 2.588 | 2.588 | 2.588 | 0.85736 | 2.3289 | 2.9211 | 2.9211 | 2.9211 | 2.9211 | 1.1431 | 1.451 | 1.451 | 1.451 | 1.451 | 1.451 | 1.4192 | 1.8014 | 1.8014 | 1.8014 | 1.8014 | 1.8014
19:00 | 0.83098 | 1.2777 | 1.9335 | 1.9335 | 1.9335 | 1.9335 | 1.1625 | 1.7874 | 2.7047 | 2.7047 | 2.7047 | 2.7047 | 0.57091 | 0.61836 | 0.66356 | 0.69746 | 0.69746 | 0.69746 | 0.64874 | 0.64874 | 0.64874 | 0.64874 | 0.64874 | 0.64874 | 2.2971 | 3.3135 | 3.9794 | 4.3299 | 5.0308 | 5.7318 | 2.0767 | 2.9956 | 3.5977 | 3.9145 | 4.5482 | 5.182 | 0.73037 | 1.984 | 2.4884 | 2.4884 | 2.4884 | 2.4884 | 0.81164 | 2.2047 | 2.7653 | 2.7653 | 2.7653 | 2.7653 | 0.90393 | 1.1473 | 1.1473 | 1.1473 | 1.1473 | 1.1473 | 1.0337 | 1.312 | 1.312 | 1.312 | 1.312 | 1.312
20:00 | 0.79103 | 1.2163 | 1.8405 | 1.8405 | 1.8405 | 1.8405 | 1.105 | 1.6991 | 2.5711 | 2.5711 | 2.5711 | 2.5711 | 0.5041 | 0.55062 | 0.59491 | 0.62813 | 0.62813 | 0.62813 | 0.5087 | 0.5087 | 0.5087 | 0.5087 | 0.5087 | 0.5087 | 2.1971 | 3.1693 | 3.8062 | 4.1414 | 4.8119 | 5.4823 | 1.9815 | 2.8582 | 3.4326 | 3.735 | 4.3396 | 4.9443 | 0.70216 | 1.9073 | 2.3923 | 2.3923 | 2.3923 | 2.3923 | 0.76591 | 2.0805 | 2.6095 | 2.6095 | 2.6095 | 2.6095 | 0.84932 | 1.078 | 1.078 | 1.078 | 1.078 | 1.078 | 0.97168 | 1.2333 | 1.2333 | 1.2333 | 1.2333 | 1.2333
21:00 | 0.75265 | 1.1573 | 1.7512 | 1.7512 | 1.7512 | 1.7512 | 1.0288 | 1.582 | 2.3938 | 2.3938 | 2.3938 | 2.3938 | 0.47253 | 0.51569 | 0.5568 | 0.58763 | 0.58763 | 0.58763 | 0.50013 | 0.50013 | 0.50013 | 0.50013 | 0.50013 | 0.50013 | 2.1056 | 3.0372 | 3.6476 | 3.9689 | 4.6114 | 5.2539 | 1.9364 | 2.7932 | 3.3546 | 3.65 | 4.2409 | 4.8318 | 0.68842 | 1.87 | 2.3455 | 2.3455 | 2.3455 | 2.3455 | 0.70875 | 1.9253 | 2.4147 | 2.4147 | 2.4147 | 2.4147 | 0.79059 | 1.0035 | 1.0035 | 1.0035 | 1.0035 | 1.0035 | 0.89547 | 1.1366 | 1.1366 | 1.1366 | 1.1366 | 1.1366
22:00 | 0.74448 | 1.1447 | 1.7322 | 1.7322 | 1.7322 | 1.7322 | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.44676 | 0.48809 | 0.52745 | 0.55697 | 0.55697 | 0.55697 | 0.49155 | 0.49155 | 0.49155 | 0.49155 | 0.49155 | 0.49155 | 1.9726 | 2.8454 | 3.4172 | 3.7182 | 4.3201 | 4.922 | 1.8481 | 2.6658 | 3.2016 | 3.4836 | 4.0475 | 4.6115 | 0.66157 | 1.7971 | 2.254 | 2.254 | 2.254 | 2.254 | 0.69351 | 1.8839 | 2.3628 | 2.3628 | 2.3628 | 2.3628 | 0.73918 | 0.93823 | 0.93823 | 0.93823 | 0.93823 | 0.93823 | 0.83831 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 1.0641
23:00 | 0.73858 | 1.1357 | 1.7185 | 1.7185 | 1.7185 | 1.7185 | 0.97168 | 1.4941 | 2.2608 | 2.2608 | 2.2608 | 2.2608 | 0.4235 | 0.46135 | 0.49739 | 0.52443 | 0.52443 | 0.52443 | 0.42428 | 0.42428 | 0.42428 | 0.42428 | 0.42428 | 0.42428 | 1.8269 | 2.6353 | 3.1649 | 3.4437 | 4.0012 | 4.5587 | 1.7719 | 2.5559 | 3.0696 | 3.3399 | 3.8806 | 4.4213 | 0.60058 | 1.6314 | 2.0462 | 2.0462 | 2.0462 | 2.0462 | 0.62492 | 1.6975 | 2.1291 | 2.1291 | 2.1291 | 2.1291 | 0.71832 | 0.91175 | 0.91175 | 0.91175 | 0.91175 | 0.91175 | 0.81926 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 1.0399

## Daily Load - Summer
| Hobart Short | [11 empty] | Electricity House | [11 empty] | Edinburgh | [11 empty] | Edmund Barton | [11 empty] | Hobart Long
| Average Summer Day Load (MW/MVA) | [5 empty] | Peak Summer Day Load (MW/MVA) | [5 empty] | Average Summer Day Load (MW/MVA) | [5 empty] | Peak Summer Day Load (MW/MVA) | [5 empty] | Average Summer Day Load (MW/MVA) | [5 empty] | Peak Summer Day Load (MW/MVA) | [5 empty] | Average Summer Day Load (MW/MVA) | [5 empty] | Peak Summer Day Load (MW/MVA) | [5 empty] | Average Summer Day Load (MW/MVA) | [5 empty] | Peak Summer Day Load (MW/MVA)
Time | 2020 | 2025 | 2026 | 2027 | 2028 | 2029 | 2020 | 2025 | 2026 | 2027 | 2028 | 2029 | 2020 | 2025 | 2026 | 2027 | 2028 | 2029 | 2020 | 2025 | 2026 | 2027 | 2028 | 2029 | 2020 | 2025 | 2026 | 2027 | 2028 | 2029 | 2020 | 2025 | 2026 | 2027 | 2028 | 2029 | 2020 | 2025 | 2026 | 2027 | 2028 | 2029 | 2020 | 2025 | 2026 | 2027 | 2028 | 2029 | 2020 | 2025 | 2026 | 2027 | 2028 | 2029 | 2020 | 2025 | 2026 | 2027 | 2028 | 2029
0:00 | 0.79938 | 1.144 | 1.6509 | 1.6509 | 1.6509 | 1.6509 | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.44172 | 0.79983 | 0.93082 | 1.0291 | 1.0291 | 1.0291 | 0.39724 | 0.78565 | 0.78565 | 0.78565 | 0.78565 | 0.78565 | 1.8327 | 2.365 | 2.7138 | 2.8974 | 3.2645 | 3.6317 | 2.4183 | 3.1207 | 3.5809 | 3.8232 | 4.3076 | 4.7921 | 0.68415 | 1.3503 | 1.6204 | 1.6204 | 1.6204 | 1.6204 | 0.5792 | 1.1431 | 1.3718 | 1.3718 | 1.3718 | 1.3718 | 0.70913 | 0.82491 | 0.82491 | 0.82491 | 0.82491 | 0.82491 | 1.7147 | 1.9947 | 1.9947 | 1.9947 | 1.9947 | 1.9947
1:00 | 0.79659 | 1.1401 | 1.6451 | 1.6451 | 1.6451 | 1.6451 | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.43579 | 0.78891 | 0.91845 | 1.0156 | 1.0156 | 1.0156 | 0.40582 | 0.8026 | 0.8026 | 0.8026 | 0.8026 | 0.8026 | 1.7508 | 2.2594 | 2.5926 | 2.768 | 3.1187 | 3.4694 | 2.191 | 2.8275 | 3.2445 | 3.4639 | 3.9029 | 4.3418 | 0.64056 | 1.2643 | 1.5171 | 1.5171 | 1.5171 | 1.5171 | 0.5068 | 1.0003 | 1.2003 | 1.2003 | 1.2003 | 1.2003 | 0.69794 | 0.8119 | 0.8119 | 0.8119 | 0.8119 | 0.8119 | 1.6004 | 1.8617 | 1.8617 | 1.8617 | 1.8617 | 1.8617
2:00 | 0.79461 | 1.1372 | 1.641 | 1.641 | 1.641 | 1.641 | 0.57158 | 0.81802 | 1.1804 | 1.1804 | 1.1804 | 1.1804 | 0.44664 | 0.80842 | 0.94142 | 1.0412 | 1.0412 | 1.0412 | 0.45726 | 0.90434 | 0.90434 | 0.90434 | 0.90434 | 0.90434 | 1.7257 | 2.227 | 2.5554 | 2.7282 | 3.0739 | 3.4196 | 2.1529 | 2.7783 | 3.1881 | 3.4037 | 3.835 | 4.2663 | 0.61777 | 1.2193 | 1.4631 | 1.4631 | 1.4631 | 1.4631 | 0.53686 | 1.0596 | 1.2715 | 1.2715 | 1.2715 | 1.2715 | 0.69496 | 0.80842 | 0.80842 | 0.80842 | 0.80842 | 0.80842 | 1.5623 | 1.8174 | 1.8174 | 1.8174 | 1.8174 | 1.8174
3:00 | 0.79628 | 1.1396 | 1.6445 | 1.6445 | 1.6445 | 1.6445 | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.43816 | 0.79221 | 0.92421 | 1.0232 | 1.0232 | 1.0232 | 0.39153 | 0.77434 | 0.77434 | 0.77434 | 0.77434 | 0.77434 | 1.699 | 2.1925 | 2.5159 | 2.6861 | 3.0264 | 3.3668 | 2.0577 | 2.6554 | 3.047 | 3.2531 | 3.6653 | 4.0775 | 0.61629 | 1.2164 | 1.4596 | 1.4596 | 1.4596 | 1.4596 | 0.53728 | 1.0604 | 1.2725 | 1.2725 | 1.2725 | 1.2725 | 0.69645 | 0.81015 | 0.81015 | 0.81015 | 0.81015 | 0.81015 | 1.5814 | 1.8395 | 1.8395 | 1.8395 | 1.8395 | 1.8395
4:00 | 0.86255 | 1.2345 | 1.7814 | 1.7814 | 1.7814 | 1.7814 | 0.59063 | 0.84528 | 1.2198 | 1.2198 | 1.2198 | 1.2198 | 0.45725 | 0.82691 | 0.96434 | 1.0674 | 1.0674 | 1.0674 | 0.48298 | 0.95521 | 0.95521 | 0.95521 | 0.95521 | 0.95521 | 1.7253 | 2.2265 | 2.5548 | 2.7276 | 3.0733 | 3.4189 | 2.0958 | 2.7046 | 3.1034 | 3.3133 | 3.7332 | 4.153 | 0.61521 | 1.2142 | 1.4571 | 1.4571 | 1.4571 | 1.4571 | 0.51823 | 1.0228 | 1.2274 | 1.2274 | 1.2274 | 1.2274 | 0.73908 | 0.85975 | 0.85975 | 0.85975 | 0.85975 | 0.85975 | 1.6957 | 1.9725 | 1.9725 | 1.9725 | 1.9725 | 1.9725
5:00 | 0.94237 | 1.3487 | 1.9462 | 1.9462 | 1.9462 | 1.9462 | 0.60937 | 0.87211 | 1.2585 | 1.2585 | 1.2585 | 1.2585 | 0.5017 | 0.90998 | 1.056 | 1.1656 | 1.1656 | 1.1656 | 0.65159 | 1.2887 | 1.2887 | 1.2887 | 1.2887 | 1.2887 | 1.8063 | 2.331 | 2.6747 | 2.8557 | 3.2175 | 3.5794 | 2.1339 | 2.7537 | 3.1598 | 3.3736 | 3.8011 | 4.2285 | 0.73713 | 1.4549 | 1.7458 | 1.7458 | 1.7458 | 1.7458 | 0.56395 | 1.1131 | 1.3357 | 1.3357 | 1.3357 | 1.3357 | 0.83064 | 0.96625 | 0.96625 | 0.96625 | 0.96625 | 0.96625 | 2.0395 | 2.3725 | 2.3725 | 2.3725 | 2.3725 | 2.3725
6:00 | 1.0568 | 1.5125 | 2.1826 | 2.1826 | 2.1826 | 2.1826 | 0.99073 | 1.4179 | 2.0461 | 2.0461 | 2.0461 | 2.0461 | 0.63679 | 1.1575 | 1.3384 | 1.4741 | 1.4741 | 1.4741 | 0.73161 | 1.447 | 1.447 | 1.447 | 1.447 | 1.447 | 1.9379 | 2.5008 | 2.8696 | 3.0637 | 3.4519 | 3.8401 | 2.3625 | 3.0488 | 3.4984 | 3.735 | 4.2083 | 4.6816 | 0.81474 | 1.608 | 1.9296 | 1.9296 | 1.9296 | 1.9296 | 0.64397 | 1.271 | 1.5252 | 1.5252 | 1.5252 | 1.5252 | 0.99299 | 1.1551 | 1.1551 | 1.1551 | 1.1551 | 1.1551 | 2.6293 | 3.0585 | 3.0585 | 3.0585 | 3.0585 | 3.0585
7:00 | 1.4492 | 2.0741 | 2.993 | 2.993 | 2.993 | 2.993 | 1.4289 | 2.045 | 2.9511 | 2.9511 | 2.9511 | 2.9511 | 0.7498 | 1.363 | 1.5759 | 1.7356 | 1.7356 | 1.7356 | 0.86022 | 1.7013 | 1.7013 | 1.7013 | 1.7013 | 1.7013 | 2.3016 | 2.9701 | 3.4081 | 3.6387 | 4.0997 | 4.5608 | 3.4485 | 4.4502 | 5.1065 | 5.4519 | 6.1428 | 6.8336 | 0.99324 | 1.9603 | 2.3524 | 2.3524 | 2.3524 | 2.3524 | 1.6499 | 3.2565 | 3.9078 | 3.9078 | 3.9078 | 3.9078 | 1.2602 | 1.466 | 1.466 | 1.466 | 1.466 | 1.466 | 3.4198 | 3.9781 | 3.9781 | 3.9781 | 3.9781 | 3.9781
8:00 | 1.7094 | 2.4465 | 3.5304 | 3.5304 | 3.5304 | 3.5304 | 1.5814 | 2.2632 | 3.2659 | 3.2659 | 3.2659 | 3.2659 | 0.81847 | 1.4877 | 1.7203 | 1.8948 | 1.8948 | 1.8948 | 1.0003 | 1.9783 | 1.9783 | 1.9783 | 1.9783 | 1.9783 | 2.5506 | 3.2915 | 3.7769 | 4.0324 | 4.5434 | 5.0544 | 3.9248 | 5.0649 | 5.8119 | 6.205 | 6.9912 | 7.7775 | 1.0154 | 2.0042 | 2.405 | 2.405 | 2.405 | 2.405 | 1.7947 | 3.5423 | 4.2507 | 4.2507 | 4.2507 | 4.2507 | 1.4857 | 1.7282 | 1.7282 | 1.7282 | 1.7282 | 1.7282 | 3.9629 | 4.6099 | 4.6099 | 4.6099 | 4.6099 | 4.6099
9:00 | 1.7615 | 2.521 | 3.6379 | 3.6379 | 3.6379 | 3.6379 | 1.8862 | 2.6995 | 3.8954 | 3.8954 | 3.8954 | 3.8954 | 0.89384 | 1.6252 | 1.8783 | 2.0682 | 2.0682 | 2.0682 | 1.1117 | 2.1987 | 2.1987 | 2.1987 | 2.1987 | 2.1987 | 2.6764 | 3.4539 | 3.9632 | 4.2313 | 4.7675 | 5.3037 | 4.001 | 5.1633 | 5.9247 | 6.3255 | 7.127 | 7.9285 | 1.031 | 2.0348 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 1.8138 | 3.5799 | 4.2958 | 4.2958 | 4.2958 | 4.2958 | 1.5746 | 1.8317 | 1.8317 | 1.8317 | 1.8317 | 1.8317 | 4.0772 | 4.7429 | 4.7429 | 4.7429 | 4.7429 | 4.7429
10:00 | 1.7963 | 2.5708 | 3.7098 | 3.7098 | 3.7098 | 3.7098 | 2.0196 | 2.8903 | 4.1709 | 4.1709 | 4.1709 | 4.1709 | 0.91365 | 1.6642 | 1.9176 | 2.1076 | 2.1076 | 2.1076 | 1.0803 | 2.1365 | 2.1365 | 2.1365 | 2.1365 | 2.1365 | 2.7864 | 3.5958 | 4.1261 | 4.4052 | 4.9634 | 5.5217 | 4.3818 | 5.6546 | 6.4885 | 6.9274 | 7.8052 | 8.683 | 1.0297 | 2.0323 | 2.4387 | 2.4387 | 2.4387 | 2.4387 | 1.8024 | 3.5573 | 4.2688 | 4.2688 | 4.2688 | 4.2688 | 1.6466 | 1.9155 | 1.9155 | 1.9155 | 1.9155 | 1.9155 | 4.3059 | 5.0089 | 5.0089 | 5.0089 | 5.0089 | 5.0089
11:00 | 1.8219 | 2.6074 | 3.7626 | 3.7626 | 3.7626 | 3.7626 | 2.7395 | 3.9206 | 5.6576 | 5.6576 | 5.6576 | 5.6576 | 0.91884 | 1.6716 | 1.9301 | 2.124 | 2.124 | 2.124 | 1.3832 | 2.7356 | 2.7356 | 2.7356 | 2.7356 | 2.7356 | 2.8788 | 3.715 | 4.2629 | 4.5512 | 5.1279 | 5.7046 | 4.6388 | 5.9863 | 6.8691 | 7.3338 | 8.2631 | 9.1924 | 1.0263 | 2.0256 | 2.4307 | 2.4307 | 2.4307 | 2.4307 | 1.7452 | 3.4445 | 4.1334 | 4.1334 | 4.1334 | 4.1334 | 1.6961 | 1.9731 | 1.9731 | 1.9731 | 1.9731 | 1.9731 | 4.6128 | 5.3659 | 5.3659 | 5.3659 | 5.3659 | 5.3659
12:00 | 1.8626 | 2.6656 | 3.8466 | 3.8466 | 3.8466 | 3.8466 | 4.6107 | 6.5833 | 9.5 | 9.5 | 9.5 | 9.5 | 0.97716 | 1.78 | 2.0509 | 2.254 | 2.254 | 2.254 | 3.2866 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 2.9479 | 3.8042 | 4.3652 | 4.6605 | 5.251 | 5.8416 | 4.9918 | 6.4418 | 7.3918 | 7.8918 | 8.8918 | 9.8918 | 1.0239 | 2.0209 | 2.4251 | 2.4251 | 2.4251 | 2.4251 | 1.9014 | 3.75 | 4.5 | 4.5 | 4.5 | 4.5 | 1.7258 | 2.0076 | 2.0076 | 2.0076 | 2.0076 | 2.0076 | 4.8393 | 5.6294 | 5.6294 | 5.6294 | 5.6294 | 5.6294
13:00 | 1.8338 | 2.6245 | 3.7872 | 3.7872 | 3.7872 | 3.7872 | 3.9789 | 5.6945 | 8.2174 | 8.2174 | 8.2174 | 8.2174 | 1.0015 | 1.8248 | 2.1015 | 2.3091 | 2.3091 | 2.3091 | 3.2694 | 6.4661 | 6.4661 | 6.4661 | 6.4661 | 6.4661 | 2.9835 | 3.8501 | 4.4179 | 4.7168 | 5.3144 | 5.9121 | 4.9918 | 6.4418 | 7.3918 | 7.8918 | 8.8918 | 9.8918 | 1.0234 | 2.0199 | 2.4238 | 2.4238 | 2.4238 | 2.4238 | 1.7947 | 3.5423 | 4.2507 | 4.2507 | 4.2507 | 4.2507 | 1.7261 | 2.0076 | 2.0076 | 2.0076 | 2.0076 | 2.0076 | 4.9537 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7
14:00 | 1.8293 | 2.618 | 3.7779 | 3.7779 | 3.7779 | 3.7779 | 4.4774 | 6.4078 | 9.2467 | 9.2467 | 9.2467 | 9.2467 | 1.0157 | 1.8507 | 2.1313 | 2.3418 | 2.3418 | 2.3418 | 3.2065 | 6.3417 | 6.3417 | 6.3417 | 6.3417 | 6.3417 | 2.9825 | 3.8489 | 4.4165 | 4.7153 | 5.3127 | 5.9102 | 4.9918 | 6.4418 | 7.3918 | 7.8918 | 8.8918 | 9.8918 | 1.0287 | 2.0303 | 2.4364 | 2.4364 | 2.4364 | 2.4364 | 1.8748 | 3.7002 | 4.4402 | 4.4402 | 4.4402 | 4.4402 | 1.7121 | 1.9915 | 1.9915 | 1.9915 | 1.9915 | 1.9915 | 4.9156 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7
15:00 | 1.8171 | 2.6006 | 3.7527 | 3.7527 | 3.7527 | 3.7527 | 1.9243 | 2.754 | 3.9741 | 3.9741 | 3.9741 | 3.9741 | 1.0175 | 1.8523 | 2.1365 | 2.3497 | 2.3497 | 2.3497 | 1.2947 | 2.5606 | 2.5606 | 2.5606 | 2.5606 | 2.5606 | 2.9779 | 3.8429 | 4.4096 | 4.7079 | 5.3045 | 5.901 | 4.9918 | 6.4418 | 7.3918 | 7.8918 | 8.8918 | 9.8918 | 1.0314 | 2.0357 | 2.4429 | 2.4429 | 2.4429 | 2.4429 | 1.7185 | 3.3919 | 4.0702 | 4.0702 | 4.0702 | 4.0702 | 1.6872 | 1.9626 | 1.9626 | 1.9626 | 1.9626 | 1.9626 | 4.7822 | 5.563 | 5.563 | 5.563 | 5.563 | 5.563
16:00 | 1.7984 | 2.5738 | 3.7141 | 3.7141 | 3.7141 | 3.7141 | 1.81 | 2.5904 | 3.738 | 3.738 | 3.738 | 3.738 | 1.0159 | 1.8495 | 2.1332 | 2.3459 | 2.3459 | 2.3459 | 1.2775 | 2.5265 | 2.5265 | 2.5265 | 2.5265 | 2.5265 | 2.967 | 3.8288 | 4.3934 | 4.6906 | 5.285 | 5.8794 | 4.9918 | 6.4418 | 7.3918 | 7.8918 | 8.8918 | 9.8918 | 1.0227 | 2.0185 | 2.4222 | 2.4222 | 2.4222 | 2.4222 | 1.0441 | 2.0607 | 2.4728 | 2.4728 | 2.4728 | 2.4728 | 1.6518 | 1.9215 | 1.9215 | 1.9215 | 1.9215 | 1.9215 | 4.8012 | 5.5851 | 5.5851 | 5.5851 | 5.5851 | 5.5851
17:00 | 1.6905 | 2.4194 | 3.4912 | 3.4912 | 3.4912 | 3.4912 | 1.6766 | 2.3995 | 3.4626 | 3.4626 | 3.4626 | 3.4626 | 0.97278 | 1.7718 | 2.0419 | 2.2445 | 2.2445 | 2.2445 | 1.2517 | 2.4756 | 2.4756 | 2.4756 | 2.4756 | 2.4756 | 2.8869 | 3.7255 | 4.2749 | 4.5641 | 5.1424 | 5.7208 | 4.9918 | 6.4418 | 7.3918 | 7.8918 | 8.8918 | 9.8918 | 0.99974 | 1.9732 | 2.3678 | 2.3678 | 2.3678 | 2.3678 | 0.89415 | 1.7648 | 2.1177 | 2.1177 | 2.1177 | 2.1177 | 1.576 | 1.8333 | 1.8333 | 1.8333 | 1.8333 | 1.8333 | 4.362 | 5.0742 | 5.0742 | 5.0742 | 5.0742 | 5.0742
18:00 | 1.3225 | 1.8927 | 2.7312 | 2.7312 | 2.7312 | 2.7312 | 1.2244 | 1.7523 | 2.5286 | 2.5286 | 2.5286 | 2.5286 | 0.80678 | 1.4698 | 1.6932 | 1.8607 | 1.8607 | 1.8607 | 0.91246 | 1.8046 | 1.8046 | 1.8046 | 1.8046 | 1.8046 | 2.7052 | 3.491 | 4.0058 | 4.2768 | 4.8187 | 5.3607 | 4.9156 | 6.3434 | 7.2789 | 7.7713 | 8.756 | 9.7408 | 0.94547 | 1.8661 | 2.2393 | 2.2393 | 2.2393 | 2.2393 | 0.83831 | 1.6546 | 1.9855 | 1.9855 | 1.9855 | 1.9855 | 1.2334 | 1.4348 | 1.4348 | 1.4348 | 1.4348 | 1.4348 | 3.5122 | 4.0856 | 4.0856 | 4.0856 | 4.0856 | 4.0856
19:00 | 0.9826 | 1.4063 | 2.0293 | 2.0293 | 2.0293 | 2.0293 | 0.80021 | 1.1452 | 1.6526 | 1.6526 | 1.6526 | 1.6526 | 0.64686 | 1.1757 | 1.3597 | 1.4976 | 1.4976 | 1.4976 | 0.68303 | 1.3509 | 1.3509 | 1.3509 | 1.3509 | 1.3509 | 2.5015 | 3.2282 | 3.7043 | 3.9548 | 4.456 | 4.9571 | 4.4392 | 5.7288 | 6.5736 | 7.0183 | 7.9076 | 8.7969 | 0.92464 | 1.8249 | 2.1899 | 2.1899 | 2.1899 | 2.1899 | 0.78496 | 1.5493 | 1.8591 | 1.8591 | 1.8591 | 1.8591 | 0.92362 | 1.0744 | 1.0744 | 1.0744 | 1.0744 | 1.0744 | 2.3237 | 2.7031 | 2.7031 | 2.7031 | 2.7031 | 2.7031
20:00 | 0.94385 | 1.3508 | 1.9492 | 1.9492 | 1.9492 | 1.9492 | 0.74305 | 1.0634 | 1.5346 | 1.5346 | 1.5346 | 1.5346 | 0.61036 | 1.1089 | 1.2833 | 1.4141 | 1.4141 | 1.4141 | 0.66017 | 1.3056 | 1.3056 | 1.3056 | 1.3056 | 1.3056 | 2.3338 | 3.0117 | 3.4559 | 3.6896 | 4.1572 | 4.6247 | 3.8867 | 5.0157 | 5.7554 | 6.1447 | 6.9234 | 7.702 | 0.92153 | 1.8188 | 2.1826 | 2.1826 | 2.1826 | 2.1826 | 0.81926 | 1.617 | 1.9403 | 1.9403 | 1.9403 | 1.9403 | 0.87455 | 1.0173 | 1.0173 | 1.0173 | 1.0173 | 1.0173 | 2.0577 | 2.3936 | 2.3936 | 2.3936 | 2.3936 | 2.3936
21:00 | 0.8769 | 1.255 | 1.811 | 1.811 | 1.811 | 1.811 | 0.66684 | 0.95435 | 1.3772 | 1.3772 | 1.3772 | 1.3772 | 0.554 | 1.0018 | 1.1684 | 1.2934 | 1.2934 | 1.2934 | 0.54871 | 1.0852 | 1.0852 | 1.0852 | 1.0852 | 1.0852 | 2.2412 | 2.8922 | 3.3187 | 3.5432 | 3.9922 | 4.4412 | 3.639 | 4.6961 | 5.3887 | 5.7532 | 6.4822 | 7.2112 | 0.89682 | 1.77 | 2.124 | 2.124 | 2.124 | 2.124 | 0.76591 | 1.5117 | 1.814 | 1.814 | 1.814 | 1.814 | 0.81226 | 0.94487 | 0.94487 | 0.94487 | 0.94487 | 0.94487 | 1.9053 | 2.2163 | 2.2163 | 2.2163 | 2.2163 | 2.2163
22:00 | 0.84077 | 1.2033 | 1.7364 | 1.7364 | 1.7364 | 1.7364 | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.51515 | 0.93327 | 1.0852 | 1.1991 | 1.1991 | 1.1991 | 0.55443 | 1.0965 | 1.0965 | 1.0965 | 1.0965 | 1.0965 | 2.1201 | 2.7359 | 3.1394 | 3.3518 | 3.7765 | 4.2012 | 3.4297 | 4.426 | 5.0787 | 5.4223 | 6.1094 | 6.7964 | 0.85621 | 1.6899 | 2.0279 | 2.0279 | 2.0279 | 2.0279 | 0.84593 | 1.6696 | 2.0035 | 2.0035 | 2.0035 | 2.0035 | 0.75904 | 0.88296 | 0.88296 | 0.88296 | 0.88296 | 0.88296 | 1.81 | 2.1055 | 2.1055 | 2.1055 | 2.1055 | 2.1055
23:00 | 0.81983 | 1.1733 | 1.6931 | 1.6931 | 1.6931 | 1.6931 | 0.60968 | 0.87255 | 1.2591 | 1.2591 | 1.2591 | 1.2591 | 0.47682 | 0.86414 | 1.0042 | 1.1093 | 1.1093 | 1.1093 | 0.52585 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.9818 | 2.5575 | 2.9347 | 3.1332 | 3.5302 | 3.9272 | 3.2584 | 4.2049 | 4.825 | 5.1514 | 5.8041 | 6.4569 | 0.78645 | 1.5522 | 1.8626 | 1.8626 | 1.8626 | 1.8626 | 0.58357 | 1.1518 | 1.3821 | 1.3821 | 1.3821 | 1.3821 | 0.72556 | 0.84402 | 0.84402 | 0.84402 | 0.84402 | 0.84402 | 1.7338 | 2.0168 | 2.0168 | 2.0168 | 2.0168 | 2.0168

## Feeder Loadings
Feeder | Summer |  | Winter |  | 2025 |  | 2026 |  | 2027 |  | 2028 |  | 2029
| Firm | Thermal | Firm | Thermal | Summer | Winter | Summer | Winter | Summer | Winter | Summer | Winter | Summer | Winter
Electricity House | 4.7 | 6.3 | 5.3 | 7 | 6.5 | 4.9 | 6.5 | 4.9 | 6.5 | 4.9 | 6.5 | 4.9 | 6.5 | 4.9
Hobart Short | 4.8 | 6.4 | 5.4 | 7.1 | 6.5833 | 5.6833 | 9.5 | 8.6 | 9.5 | 8.6 | 9.5 | 8.6 | 9.5 | 8.6
Edinburgh | 5 | 6.8 | 5.5 | 7.4 | 6.4418 | 4.727 | 7.3918 | 5.677 | 7.8918 | 6.177 | 8.8918 | 7.177 | 9.8918 | 8.177
Edmund Barton | 3.4 | 4.5 | 3.8 | 5 | 3.75 | 2.95 | 4.5 | 3.7 | 4.5 | 3.7 | 4.5 | 3.7 | 4.5 | 3.7
Hobart Long | 4.4 | 5.8 | 4.9 | 6.5 | 5.7 | 3.7 | 5.7 | 3.7 | 5.7 | 3.7 | 5.7 | 3.7 | 5.7 | 3.7
Above Firm
Above Thermal
Unit: MVA/MW

## Methodology
Tab | Description
Annual Load | Hourly historical demand of relevant feeders and their hourly forecasts. These forecasts preserve relative percentage of seasonal peak demand in any given hour across a year, and scale the peak demand itself based on addition of point loads as described in the business case
Daily Load | Average Summer / Winter Day load: Calculated by averaging the demand at the same hour throughtout the year. Peak Summer / Winter Day load: The daily load profile on the day when the peak summer/winter demand occurs.
Feeder Loadings | Forecast peak seasonal loadings of relevant feeders in winter and summer.