## Annual Load
| Peak Demand | 5.0699 | 2021-07-22 08:00 |  | Winter |  | Peak Demand | 3.1179 | 2021-07-25 18:00 |  | Winter |  |  | Peak Demand | 3.1389 | 2020-01-31 16:00 |  | Summer
| Wolseley | [5 empty] | Quick | [6 empty] | Bowen
| Historical Load (MVA/MW) | Forecast Load (MVA/MW) |  |  |  |  | Historical Load (MVA/MW) | Forecast Load (MVA/MW) | [5 empty] | Historical Load (MVA/MW) | Forecast Load (MVA/MW)
Timestamp | 2021 | 2025 | 2026 | 2027 | 2028 | 2029 | 2021 | 2025 | 2026 | 2027 | 2028 | 2029 | Timestamp | 2019 | 2025 | 2026 | 2027 | 2028 | 2029
2021-01-01 12:00 | 1.3141 | 1.5992 | 1.5647 | 1.6829 | 1.5942 | 1.7125 | 1.3918 | 2.3867 | 2.945 | 2.945 | 3.3173 | 3.3173 | 2019-03-01 | 1.6385 | 2.6852 | 4.4078 | 4.4078 | 4.4078 | 4.4078
2021-01-01 13:00 | 1.3689 | 1.6658 | 1.6299 | 1.7531 | 1.6607 | 1.7839 | 1.4146 | 2.4259 | 2.9934 | 2.9934 | 3.3718 | 3.3718 | 2019-03-01 01:00 | 1.5928 | 2.6103 | 4.2848 | 4.2848 | 4.2848 | 4.2848
2021-01-01 14:00 | 1.3261 | 1.6137 | 1.5789 | 1.6982 | 1.6087 | 1.728 | 1.4175 | 2.4308 | 2.9995 | 2.9995 | 3.3786 | 3.3786 | 2019-03-01 02:00 | 1.5623 | 2.5603 | 4.2028 | 4.2028 | 4.2028 | 4.2028
2021-01-01 15:00 | 1.2603 | 1.5337 | 1.5006 | 1.614 | 1.529 | 1.6424 | 1.3375 | 2.2936 | 2.8301 | 2.8301 | 3.1878 | 3.1878 | 2019-03-01 03:00 | 1.509 | 2.4729 | 4.0593 | 4.0593 | 4.0593 | 4.0593
2021-01-01 16:00 | 1.3579 | 1.6524 | 1.6167 | 1.7389 | 1.6473 | 1.7695 | 1.3003 | 2.2299 | 2.7515 | 2.7515 | 3.0993 | 3.0993 | 2019-03-01 04:00 | 1.5775 | 2.5853 | 4.2438 | 4.2438 | 4.2438 | 4.2438
2021-01-01 17:00 | 1.4899 | 1.813 | 1.7739 | 1.908 | 1.8074 | 1.9415 | 1.4489 | 2.4847 | 3.066 | 3.066 | 3.4535 | 3.4535 | 2019-03-01 05:00 | 1.6842 | 2.7602 | 4.5308 | 4.5308 | 4.5308 | 4.5308
2021-01-01 18:00 | 1.5261 | 1.8571 | 1.8171 | 1.9544 | 1.8514 | 1.9887 | 1.3461 | 2.3083 | 2.8483 | 2.8483 | 3.2083 | 3.2083 | 2019-03-01 06:00 | 2.0119 | 3.2972 | 5.4124 | 5.4124 | 5.4124 | 5.4124
2021-01-01 19:00 | 1.4975 | 1.8223 | 1.783 | 1.9178 | 1.8167 | 1.9515 | 1.3489 | 2.3132 | 2.8543 | 2.8543 | 3.2151 | 3.2151 | 2019-03-01 07:00 | 1.89 | 3.0974 | 5.0844 | 5.0844 | 5.0844 | 5.0844
2021-01-01 20:00 | 1.5118 | 1.8397 | 1.8 | 1.9361 | 1.8341 | 1.9701 | 1.3089 | 2.2446 | 2.7697 | 2.7697 | 3.1197 | 3.1197 | 2019-03-01 08:00 | 2.1949 | 3.597 | 5.9044 | 5.9044 | 5.9044 | 5.9044
2021-01-01 21:00 | 1.5261 | 1.8571 | 1.8171 | 1.9544 | 1.8514 | 1.9887 | 1.2746 | 2.1858 | 2.6971 | 2.6971 | 3.038 | 3.038 | 2019-03-01 09:00 | 2.2025 | 3.6094 | 5.9249 | 5.9249 | 5.9249 | 5.9249
2021-01-01 22:00 | 1.4318 | 1.7423 | 1.7048 | 1.8336 | 1.737 | 1.8658 | 1.246 | 2.1367 | 2.6366 | 2.6366 | 2.9699 | 2.9699 | 2019-03-01 10:00 | 2.2863 | 3.7468 | 6.1505 | 6.1505 | 6.1505 | 6.1505
2021-01-01 23:00 | 1.3946 | 1.6971 | 1.6605 | 1.786 | 1.6919 | 1.8174 | 1.0203 | 1.7496 | 2.1589 | 2.1589 | 2.4317 | 2.4317 | 2019-03-01 11:00 | 2.4463 | 4.0091 | 6.581 | 6.581 | 6.581 | 6.581
2021-01-02 | 1.4089 | 1.7145 | 1.6775 | 1.8043 | 1.7092 | 1.836 | 0.93452 | 1.6026 | 1.9775 | 1.9775 | 2.2274 | 2.2274 | 2019-03-01 12:00 | 2.4082 | 3.9467 | 6.4785 | 6.4785 | 6.4785 | 6.4785
2021-01-02 01:00 | 1.1889 | 1.4467 | 1.4155 | 1.5225 | 1.4423 | 1.5493 | 0.75483 | 1.2944 | 1.5972 | 1.5972 | 1.7991 | 1.7991 | 2019-03-01 13:00 | 2.393 | 3.9217 | 6.4375 | 6.4375 | 6.4375 | 6.4375
2021-01-02 02:00 | 1.1749 | 1.4298 | 1.3989 | 1.5047 | 1.4254 | 1.5311 | 0.74019 | 1.2693 | 1.5662 | 1.5662 | 1.7642 | 1.7642 | 2019-03-01 14:00 | 2.3397 | 3.8343 | 6.294 | 6.294 | 6.294 | 6.294
2021-01-02 03:00 | 1.1546 | 1.405 | 1.3747 | 1.4786 | 1.4007 | 1.5046 | 0.73187 | 1.255 | 1.5486 | 1.5486 | 1.7444 | 1.7444 | 2019-03-01 15:00 | 2.3092 | 3.7843 | 6.212 | 6.212 | 6.212 | 6.212
2021-01-02 04:00 | 1.1231 | 1.3668 | 1.3373 | 1.4384 | 1.3625 | 1.4636 | 0.68875 | 1.1811 | 1.4574 | 1.4574 | 1.6416 | 1.6416 | 2019-03-01 16:00 | 2.3092 | 3.7843 | 6.212 | 6.212 | 6.212 | 6.212
2021-01-02 05:00 | 1.1174 | 1.3598 | 1.3305 | 1.431 | 1.3556 | 1.4562 | 0.72304 | 1.2399 | 1.53 | 1.53 | 1.7233 | 1.7233 | 2019-03-01 17:00 | 2.2711 | 3.7218 | 6.1095 | 6.1095 | 6.1095 | 6.1095
2021-01-02 06:00 | 1.1317 | 1.3772 | 1.3475 | 1.4493 | 1.3729 | 1.4748 | 0.79731 | 1.3673 | 1.6871 | 1.6871 | 1.9003 | 1.9003 | 2019-03-01 18:00 | 2.0805 | 3.4096 | 5.5969 | 5.5969 | 5.5969 | 5.5969
2021-01-02 07:00 | 1.1746 | 1.4294 | 1.3985 | 1.5042 | 1.4249 | 1.5307 | 0.82878 | 1.4212 | 1.7537 | 1.7537 | 1.9754 | 1.9754 | 2019-03-01 19:00 | 1.9357 | 3.1723 | 5.2074 | 5.2074 | 5.2074 | 5.2074
2021-01-02 08:00 | 1.206 | 1.4676 | 1.4359 | 1.5445 | 1.4631 | 1.5716 | 1.0917 | 1.8721 | 2.3101 | 2.3101 | 2.602 | 2.602 | 2019-03-01 20:00 | 1.9205 | 3.1473 | 5.1664 | 5.1664 | 5.1664 | 5.1664
2021-01-02 09:00 | 1.1832 | 1.4398 | 1.4087 | 1.5152 | 1.4353 | 1.5418 | 1.1717 | 2.0093 | 2.4794 | 2.4794 | 2.7928 | 2.7928 | 2019-03-01 21:00 | 1.7833 | 2.9225 | 4.7974 | 4.7974 | 4.7974 | 4.7974
2021-01-02 10:00 | 1.1679 | 1.4212 | 1.3906 | 1.4957 | 1.4169 | 1.522 | 1.4718 | 2.5239 | 3.1144 | 3.1144 | 3.508 | 3.508 | 2019-03-01 22:00 | 1.7681 | 2.8975 | 4.7564 | 4.7564 | 4.7564 | 4.7564
2021-01-02 11:00 | 1.2489 | 1.5198 | 1.487 | 1.5994 | 1.5151 | 1.6275 | 1.3946 | 2.3916 | 2.9511 | 2.9511 | 3.3241 | 3.3241 | 2019-03-01 23:00 | 1.6842 | 2.7602 | 4.5308 | 4.5308 | 4.5308 | 4.5308
2021-01-02 12:00 | 1.3661 | 1.6624 | 1.6265 | 1.7494 | 1.6572 | 1.7802 | 1.5118 | 2.5925 | 3.199 | 3.199 | 3.6034 | 3.6034 | 2019-03-02 | 1.5699 | 2.5728 | 4.2233 | 4.2233 | 4.2233 | 4.2233
2021-01-02 13:00 | 1.3318 | 1.6206 | 1.5857 | 1.7055 | 1.6156 | 1.7355 | 1.4632 | 2.5092 | 3.0962 | 3.0962 | 3.4876 | 3.4876 | 2019-03-02 01:00 | 1.5242 | 2.4979 | 4.1003 | 4.1003 | 4.1003 | 4.1003
2021-01-02 14:00 | 1.2918 | 1.5719 | 1.538 | 1.6543 | 1.5671 | 1.6834 | 1.4289 | 2.4504 | 3.0236 | 3.0236 | 3.4058 | 3.4058 | 2019-03-02 02:00 | 1.4861 | 2.4354 | 3.9978 | 3.9978 | 3.9978 | 3.9978
2021-01-02 15:00 | 1.3146 | 1.5998 | 1.5653 | 1.6836 | 1.5948 | 1.7131 | 1.4089 | 2.4161 | 2.9813 | 2.9813 | 3.3581 | 3.3581 | 2019-03-02 03:00 | 1.4709 | 2.4105 | 3.9568 | 3.9568 | 3.9568 | 3.9568
2021-01-02 16:00 | 1.3203 | 1.6067 | 1.5721 | 1.6909 | 1.6018 | 1.7206 | 1.3575 | 2.3279 | 2.8725 | 2.8725 | 3.2355 | 3.2355 | 2019-03-02 04:00 | 1.5775 | 2.5853 | 4.2438 | 4.2438 | 4.2438 | 4.2438
2021-01-02 17:00 | 1.5455 | 1.8808 | 1.8402 | 1.9793 | 1.875 | 2.0141 | 1.3933 | 2.3893 | 2.9482 | 2.9482 | 3.3209 | 3.3209 | 2019-03-02 05:00 | 1.608 | 2.6353 | 4.3258 | 4.3258 | 4.3258 | 4.3258
2021-01-02 18:00 | 1.5604 | 1.8988 | 1.8579 | 1.9983 | 1.893 | 2.0334 | 1.4175 | 2.4308 | 2.9995 | 2.9995 | 3.3786 | 3.3786 | 2019-03-02 06:00 | 1.73 | 2.8351 | 4.6538 | 4.6538 | 4.6538 | 4.6538
2021-01-02 19:00 | 1.5404 | 1.8745 | 1.8341 | 1.9727 | 1.8687 | 2.0074 | 1.4175 | 2.4308 | 2.9995 | 2.9995 | 3.3786 | 3.3786 | 2019-03-02 07:00 | 1.9205 | 3.1473 | 5.1664 | 5.1664 | 5.1664 | 5.1664
2021-01-02 20:00 | 1.5215 | 1.8515 | 1.8115 | 1.9485 | 1.8458 | 1.9827 | 1.4089 | 2.4161 | 2.9813 | 2.9813 | 3.3581 | 3.3581 | 2019-03-02 08:00 | 2.0577 | 3.3721 | 5.5354 | 5.5354 | 5.5354 | 5.5354
2021-01-02 21:00 | 1.5404 | 1.8745 | 1.8341 | 1.9727 | 1.8687 | 2.0074 | 1.3489 | 2.3132 | 2.8543 | 2.8543 | 3.2151 | 3.2151 | 2019-03-02 09:00 | 2.0424 | 3.3472 | 5.4944 | 5.4944 | 5.4944 | 5.4944
2021-01-02 22:00 | 1.376 | 1.6745 | 1.6384 | 1.7622 | 1.6693 | 1.7932 | 1.2718 | 2.1809 | 2.691 | 2.691 | 3.0312 | 3.0312 | 2019-03-02 10:00 | 2.2558 | 3.6969 | 6.0685 | 6.0685 | 6.0685 | 6.0685
2021-01-02 23:00 | 1.4289 | 1.7389 | 1.7014 | 1.83 | 1.7335 | 1.8621 | 1.0688 | 1.8329 | 2.2617 | 2.2617 | 2.5475 | 2.5475 | 2019-03-02 11:00 | 2.2406 | 3.6719 | 6.0275 | 6.0275 | 6.0275 | 6.0275
2021-01-03 | 1.3547 | 1.6485 | 1.6129 | 1.7348 | 1.6434 | 1.7653 | 0.93011 | 1.595 | 1.9681 | 1.9681 | 2.2169 | 2.2169 | 2019-03-02 12:00 | 2.2939 | 3.7593 | 6.171 | 6.171 | 6.171 | 6.171
2021-01-03 01:00 | 1.2689 | 1.5441 | 1.5108 | 1.625 | 1.5394 | 1.6536 | 0.83736 | 1.4359 | 1.7719 | 1.7719 | 1.9958 | 1.9958 | 2019-03-02 13:00 | 2.2253 | 3.6469 | 5.9865 | 5.9865 | 5.9865 | 5.9865
2021-01-03 02:00 | 1.1346 | 1.3807 | 1.3509 | 1.453 | 1.3764 | 1.4785 | 0.73161 | 1.2546 | 1.5481 | 1.5481 | 1.7438 | 1.7438 | 2019-03-02 14:00 | 2.2177 | 3.6344 | 5.966 | 5.966 | 5.966 | 5.966
2021-01-03 03:00 | 1.0946 | 1.332 | 1.3032 | 1.4018 | 1.3279 | 1.4264 | 0.69446 | 1.1909 | 1.4695 | 1.4695 | 1.6552 | 1.6552 | 2019-03-02 15:00 | 2.2406 | 3.6719 | 6.0275 | 6.0275 | 6.0275 | 6.0275
2021-01-03 04:00 | 1.1315 | 1.377 | 1.3472 | 1.4491 | 1.3727 | 1.4745 | 0.68017 | 1.1664 | 1.4393 | 1.4393 | 1.6212 | 1.6212 | 2019-03-02 16:00 | 2.2101 | 3.6219 | 5.9454 | 5.9454 | 5.9454 | 5.9454
2021-01-03 05:00 | 1.1317 | 1.3772 | 1.3475 | 1.4493 | 1.3729 | 1.4748 | 0.76877 | 1.3183 | 1.6267 | 1.6267 | 1.8323 | 1.8323 | 2019-03-02 17:00 | 2.1491 | 3.522 | 5.7814 | 5.7814 | 5.7814 | 5.7814
2021-01-03 06:00 | 1.1317 | 1.3772 | 1.3475 | 1.4493 | 1.3729 | 1.4748 | 0.73676 | 1.2634 | 1.559 | 1.559 | 1.756 | 1.756 | 2019-03-02 18:00 | 1.9815 | 3.2472 | 5.3304 | 5.3304 | 5.3304 | 5.3304
2021-01-03 07:00 | 1.1828 | 1.4394 | 1.4083 | 1.5148 | 1.4349 | 1.5414 | 0.84593 | 1.4506 | 1.79 | 1.79 | 2.0162 | 2.0162 | 2019-03-02 19:00 | 2.0424 | 3.3472 | 5.4944 | 5.4944 | 5.4944 | 5.4944
2021-01-03 08:00 | 1.3003 | 1.5824 | 1.5482 | 1.6653 | 1.5775 | 1.6945 | 1.0554 | 1.8098 | 2.2332 | 2.2332 | 2.5155 | 2.5155 | 2019-03-02 20:00 | 1.9662 | 3.2223 | 5.2894 | 5.2894 | 5.2894 | 5.2894
2021-01-03 09:00 | 1.3746 | 1.6728 | 1.6367 | 1.7604 | 1.6676 | 1.7914 | 1.3289 | 2.2789 | 2.812 | 2.812 | 3.1674 | 3.1674 | 2019-03-02 21:00 | 1.9357 | 3.1723 | 5.2074 | 5.2074 | 5.2074 | 5.2074
2021-01-03 10:00 | 1.5162 | 1.8451 | 1.8053 | 1.9417 | 1.8394 | 1.9758 | 1.4518 | 2.4896 | 3.072 | 3.072 | 3.4603 | 3.4603 | 2019-03-02 22:00 | 1.6919 | 2.7726 | 4.5513 | 4.5513 | 4.5513 | 4.5513
2021-01-03 11:00 | 1.5775 | 1.9197 | 1.8783 | 2.0203 | 1.9138 | 2.0558 | 1.509 | 2.5876 | 3.193 | 3.193 | 3.5965 | 3.5965 | 2019-03-02 23:00 | 1.669 | 2.7352 | 4.4898 | 4.4898 | 4.4898 | 4.4898
2021-01-03 12:00 | 1.4232 | 1.7319 | 1.6946 | 1.8226 | 1.7266 | 1.8547 | 1.509 | 2.5876 | 3.193 | 3.193 | 3.5965 | 3.5965 | 2019-03-03 | 1.5242 | 2.4979 | 4.1003 | 4.1003 | 4.1003 | 4.1003
2021-01-03 13:00 | 1.266 | 1.5406 | 1.5074 | 1.6213 | 1.5359 | 1.6498 | 1.4661 | 2.5141 | 3.1023 | 3.1023 | 3.4944 | 3.4944 | 2019-03-03 01:00 | 1.4861 | 2.4354 | 3.9978 | 3.9978 | 3.9978 | 3.9978
2021-01-03 14:00 | 1.2689 | 1.5441 | 1.5108 | 1.625 | 1.5394 | 1.6536 | 1.4175 | 2.4308 | 2.9995 | 2.9995 | 3.3786 | 3.3786 | 2019-03-03 02:00 | 1.4709 | 2.4105 | 3.9568 | 3.9568 | 3.9568 | 3.9568
2021-01-03 15:00 | 1.3518 | 1.645 | 1.6095 | 1.7311 | 1.6399 | 1.7616 | 1.4061 | 2.4112 | 2.9753 | 2.9753 | 3.3513 | 3.3513 | 2019-03-03 03:00 | 1.5166 | 2.4854 | 4.0798 | 4.0798 | 4.0798 | 4.0798
2021-01-03 16:00 | 1.4289 | 1.7389 | 1.7014 | 1.83 | 1.7335 | 1.8621 | 1.4543 | 2.4939 | 3.0773 | 3.0773 | 3.4662 | 3.4662 | 2019-03-03 04:00 | 1.5547 | 2.5478 | 4.1823 | 4.1823 | 4.1823 | 4.1823
2021-01-03 17:00 | 1.5147 | 1.8432 | 1.8034 | 1.9398 | 1.8375 | 1.9738 | 1.4575 | 2.4994 | 3.0841 | 3.0841 | 3.4739 | 3.4739 | 2019-03-03 05:00 | 1.5547 | 2.5478 | 4.1823 | 4.1823 | 4.1823 | 4.1823
2021-01-03 18:00 | 1.6404 | 1.9962 | 1.9532 | 2.1008 | 1.9901 | 2.1377 | 1.4461 | 2.4798 | 3.0599 | 3.0599 | 3.4467 | 3.4467 | 2019-03-03 06:00 | 1.7376 | 2.8476 | 4.6744 | 4.6744 | 4.6744 | 4.6744
2021-01-03 19:00 | 1.5915 | 1.9367 | 1.8949 | 2.0382 | 1.9307 | 2.074 | 1.4604 | 2.5043 | 3.0902 | 3.0902 | 3.4807 | 3.4807 | 2019-03-03 07:00 | 1.7757 | 2.91 | 4.7769 | 4.7769 | 4.7769 | 4.7769
2021-01-03 20:00 | 1.5775 | 1.9197 | 1.8783 | 2.0203 | 1.9138 | 2.0558 | 1.4318 | 2.4553 | 3.0297 | 3.0297 | 3.4126 | 3.4126 | 2019-03-03 08:00 | 1.9891 | 3.2597 | 5.3509 | 5.3509 | 5.3509 | 5.3509
2021-01-03 21:00 | 1.5167 | 1.8456 | 1.8058 | 1.9423 | 1.84 | 1.9765 | 1.4204 | 2.4357 | 3.0055 | 3.0055 | 3.3854 | 3.3854 | 2019-03-03 09:00 | 2.0577 | 3.3721 | 5.5354 | 5.5354 | 5.5354 | 5.5354
2021-01-03 22:00 | 1.4722 | 1.7915 | 1.7528 | 1.8853 | 1.7859 | 1.9184 | 1.2946 | 2.2201 | 2.7394 | 2.7394 | 3.0857 | 3.0857 | 2019-03-03 10:00 | 2.0805 | 3.4096 | 5.5969 | 5.5969 | 5.5969 | 5.5969
2021-01-03 23:00 | 1.3719 | 1.6695 | 1.6335 | 1.757 | 1.6644 | 1.7878 | 1.0661 | 1.8281 | 2.2558 | 2.2558 | 2.5409 | 2.5409 | 2019-03-03 11:00 | 2.1949 | 3.597 | 5.9044 | 5.9044 | 5.9044 | 5.9044
2021-01-04 | 1.3003 | 1.5824 | 1.5482 | 1.6653 | 1.5775 | 1.6945 | 0.95167 | 1.632 | 2.0137 | 2.0137 | 2.2683 | 2.2683 | 2019-03-03 12:00 | 2.2101 | 3.6219 | 5.9454 | 5.9454 | 5.9454 | 5.9454
2021-01-04 01:00 | 1.226 | 1.492 | 1.4598 | 1.5701 | 1.4874 | 1.5977 | 0.80592 | 1.382 | 1.7053 | 1.7053 | 1.9209 | 1.9209 | 2019-03-03 13:00 | 2.2253 | 3.6469 | 5.9865 | 5.9865 | 5.9865 | 5.9865
2021-01-04 02:00 | 1.1376 | 1.3843 | 1.3545 | 1.4569 | 1.3801 | 1.4825 | 0.7459 | 1.2791 | 1.5783 | 1.5783 | 1.7778 | 1.7778 | 2019-03-03 14:00 | 2.3015 | 3.7718 | 6.1915 | 6.1915 | 6.1915 | 6.1915
2021-01-04 03:00 | 1.1546 | 1.405 | 1.3747 | 1.4786 | 1.4007 | 1.5046 | 0.69732 | 1.1958 | 1.4755 | 1.4755 | 1.662 | 1.662 | 2019-03-03 15:00 | 2.2482 | 3.6844 | 6.048 | 6.048 | 6.048 | 6.048
2021-01-04 04:00 | 1.1183 | 1.3608 | 1.3315 | 1.4321 | 1.3566 | 1.4573 | 0.73161 | 1.2546 | 1.5481 | 1.5481 | 1.7438 | 1.7438 | 2019-03-03 16:00 | 2.2634 | 3.7094 | 6.089 | 6.089 | 6.089 | 6.089
2021-01-04 05:00 | 1.148 | 1.397 | 1.3668 | 1.4701 | 1.3927 | 1.496 | 0.72018 | 1.235 | 1.5239 | 1.5239 | 1.7165 | 1.7165 | 2019-03-03 17:00 | 2.2025 | 3.6094 | 5.9249 | 5.9249 | 5.9249 | 5.9249
2021-01-04 06:00 | 1.3346 | 1.6241 | 1.5891 | 1.7092 | 1.6191 | 1.7392 | 0.86879 | 1.4898 | 1.8384 | 1.8384 | 2.0707 | 2.0707 | 2019-03-03 18:00 | 2.1186 | 3.4721 | 5.6994 | 5.6994 | 5.6994 | 5.6994
2021-01-04 07:00 | 1.3831 | 1.6831 | 1.6468 | 1.7713 | 1.6779 | 1.8024 | 1.0374 | 1.779 | 2.1952 | 2.1952 | 2.4726 | 2.4726 | 2019-03-03 19:00 | 2.0348 | 3.3347 | 5.4739 | 5.4739 | 5.4739 | 5.4739
2021-01-04 08:00 | 1.6204 | 1.9719 | 1.9293 | 2.0752 | 1.9658 | 2.1116 | 1.1803 | 2.024 | 2.4975 | 2.4975 | 2.8132 | 2.8132 | 2019-03-03 20:00 | 2.0805 | 3.4096 | 5.5969 | 5.5969 | 5.5969 | 5.5969
2021-01-04 09:00 | 1.6861 | 2.0519 | 2.0076 | 2.1594 | 2.0455 | 2.1973 | 1.2603 | 2.1613 | 2.6669 | 2.6669 | 3.0039 | 3.0039 | 2019-03-03 21:00 | 1.8824 | 3.0849 | 5.0639 | 5.0639 | 5.0639 | 5.0639
2021-01-04 10:00 | 1.7862 | 2.1736 | 2.1267 | 2.2875 | 2.1669 | 2.3276 | 1.3325 | 2.285 | 2.8195 | 2.8195 | 3.1759 | 3.1759 | 2019-03-03 22:00 | 1.73 | 2.8351 | 4.6538 | 4.6538 | 4.6538 | 4.6538
2021-01-04 11:00 | 1.809 | 2.2014 | 2.1539 | 2.3167 | 2.1946 | 2.3574 | 1.3632 | 2.3377 | 2.8846 | 2.8846 | 3.2491 | 3.2491 | 2019-03-03 23:00 | 1.6309 | 2.6727 | 4.3873 | 4.3873 | 4.3873 | 4.3873
2021-01-04 12:00 | 1.8519 | 2.2536 | 2.205 | 2.3716 | 2.2466 | 2.4133 | 1.4518 | 2.4896 | 3.072 | 3.072 | 3.4603 | 3.4603 | 2019-03-04 | 1.509 | 2.4729 | 4.0593 | 4.0593 | 4.0593 | 4.0593
2021-01-04 13:00 | 1.8033 | 2.1945 | 2.1471 | 2.3094 | 2.1877 | 2.35 | 1.509 | 2.5876 | 3.193 | 3.193 | 3.5965 | 3.5965 | 2019-03-04 01:00 | 1.4861 | 2.4354 | 3.9978 | 3.9978 | 3.9978 | 3.9978
2021-01-04 14:00 | 1.8119 | 2.2049 | 2.1573 | 2.3204 | 2.1981 | 2.3612 | 1.4518 | 2.4896 | 3.072 | 3.072 | 3.4603 | 3.4603 | 2019-03-04 02:00 | 1.5013 | 2.4604 | 4.0388 | 4.0388 | 4.0388 | 4.0388
2021-01-04 15:00 | 1.5861 | 1.9301 | 1.8885 | 2.0313 | 1.9242 | 2.0669 | 1.3746 | 2.3573 | 2.9088 | 2.9088 | 3.2764 | 3.2764 | 2019-03-04 03:00 | 1.5013 | 2.4604 | 4.0388 | 4.0388 | 4.0388 | 4.0388
2021-01-04 16:00 | 1.6033 | 1.951 | 1.9089 | 2.0532 | 1.945 | 2.0893 | 1.3575 | 2.3279 | 2.8725 | 2.8725 | 3.2355 | 3.2355 | 2019-03-04 04:00 | 1.5166 | 2.4854 | 4.0798 | 4.0798 | 4.0798 | 4.0798
2021-01-04 17:00 | 1.6576 | 2.0171 | 1.9736 | 2.1228 | 2.0109 | 2.1601 | 1.3175 | 2.2593 | 2.7878 | 2.7878 | 3.1402 | 3.1402 | 2019-03-04 05:00 | 1.7605 | 2.8851 | 4.7359 | 4.7359 | 4.7359 | 4.7359
2021-01-04 18:00 | 1.8262 | 2.2223 | 2.1743 | 2.3387 | 2.2154 | 2.3798 | 1.3661 | 2.3426 | 2.8906 | 2.8906 | 3.256 | 3.256 | 2019-03-04 06:00 | 1.9281 | 3.1598 | 5.1869 | 5.1869 | 5.1869 | 5.1869
2021-01-04 19:00 | 1.7262 | 2.1006 | 2.0552 | 2.2106 | 2.0941 | 2.2494 | 1.3918 | 2.3867 | 2.945 | 2.945 | 3.3173 | 3.3173 | 2019-03-04 07:00 | 1.8595 | 3.0474 | 5.0024 | 5.0024 | 5.0024 | 5.0024
2021-01-04 20:00 | 1.6919 | 2.0588 | 2.0144 | 2.1667 | 2.0525 | 2.2047 | 1.3689 | 2.3475 | 2.8967 | 2.8967 | 3.2628 | 3.2628 | 2019-03-04 08:00 | 2.2711 | 3.7218 | 6.1095 | 6.1095 | 6.1095 | 6.1095
2021-01-04 21:00 | 1.649 | 2.0067 | 1.9634 | 2.1118 | 2.0005 | 2.1489 | 1.3346 | 2.2887 | 2.8241 | 2.8241 | 3.181 | 3.181 | 2019-03-04 09:00 | 2.393 | 3.9217 | 6.4375 | 6.4375 | 6.4375 | 6.4375
2021-01-04 22:00 | 1.5633 | 1.9023 | 1.8613 | 2.002 | 1.8965 | 2.0372 | 1.1862 | 2.0342 | 2.5101 | 2.5101 | 2.8273 | 2.8273 | 2019-03-04 10:00 | 2.4768 | 4.0591 | 6.663 | 6.663 | 6.663 | 6.663
2021-01-04 23:00 | 1.4089 | 1.7145 | 1.6775 | 1.8043 | 1.7092 | 1.836 | 1.0431 | 1.7888 | 2.2073 | 2.2073 | 2.4862 | 2.4862 | 2019-03-04 11:00 | 2.5226 | 4.134 | 6.786 | 6.786 | 6.786 | 6.786
2021-01-05 | 1.3691 | 1.6661 | 1.6301 | 1.7534 | 1.661 | 1.7842 | 0.88344 | 1.515 | 1.8694 | 1.8694 | 2.1056 | 2.1056 | 2019-03-04 12:00 | 2.5683 | 4.2089 | 6.909 | 6.909 | 6.909 | 6.909
2021-01-05 01:00 | 1.2346 | 1.5024 | 1.47 | 1.5811 | 1.4978 | 1.6089 | 0.77162 | 1.3232 | 1.6328 | 1.6328 | 1.8391 | 1.8391 | 2019-03-04 13:00 | 2.614 | 4.2839 | 7.032 | 7.032 | 7.032 | 7.032
2021-01-05 02:00 | 1.1866 | 1.444 | 1.4129 | 1.5197 | 1.4396 | 1.5464 | 0.74305 | 1.2742 | 1.5723 | 1.5723 | 1.771 | 1.771 | 2019-03-04 14:00 | 2.6292 | 4.3088 | 7.073 | 7.073 | 7.073 | 7.073
2021-01-05 03:00 | 1.1714 | 1.4255 | 1.3947 | 1.5001 | 1.4211 | 1.5265 | 0.67731 | 1.1615 | 1.4332 | 1.4332 | 1.6144 | 1.6144 | 2019-03-04 15:00 | 2.6902 | 4.4088 | 7.237 | 7.237 | 7.237 | 7.237
2021-01-05 04:00 | 1.1717 | 1.4259 | 1.3951 | 1.5006 | 1.4215 | 1.5269 | 0.67145 | 1.1514 | 1.4208 | 1.4208 | 1.6004 | 1.6004 | 2019-03-04 16:00 | 2.6978 | 4.4213 | 7.2576 | 7.2576 | 7.2576 | 7.2576
2021-01-05 05:00 | 1.166 | 1.4189 | 1.3883 | 1.4933 | 1.4145 | 1.5195 | 0.73447 | 1.2595 | 1.5542 | 1.5542 | 1.7506 | 1.7506 | 2019-03-04 17:00 | 2.5226 | 4.134 | 6.786 | 6.786 | 6.786 | 6.786
2021-01-05 06:00 | 1.3032 | 1.5858 | 1.5516 | 1.6689 | 1.581 | 1.6982 | 0.84593 | 1.4506 | 1.79 | 1.79 | 2.0162 | 2.0162 | 2019-03-04 18:00 | 2.2787 | 3.7343 | 6.13 | 6.13 | 6.13 | 6.13
2021-01-05 07:00 | 1.4918 | 1.8154 | 1.7762 | 1.9105 | 1.8098 | 1.944 | 1.0517 | 1.8035 | 2.2254 | 2.2254 | 2.5067 | 2.5067 | 2019-03-04 19:00 | 2.0348 | 3.3347 | 5.4739 | 5.4739 | 5.4739 | 5.4739
2021-01-05 08:00 | 1.5204 | 1.8502 | 1.8102 | 1.9471 | 1.8445 | 1.9813 | 1.186 | 2.0338 | 2.5096 | 2.5096 | 2.8268 | 2.8268 | 2019-03-04 20:00 | 1.9738 | 3.2348 | 5.3099 | 5.3099 | 5.3099 | 5.3099
2021-01-05 09:00 | 1.5947 | 1.9406 | 1.8987 | 2.0422 | 1.9346 | 2.0781 | 1.2746 | 2.1858 | 2.6971 | 2.6971 | 3.038 | 3.038 | 2019-03-04 21:00 | 1.8824 | 3.0849 | 5.0639 | 5.0639 | 5.0639 | 5.0639
2021-01-05 10:00 | 1.5947 | 1.9406 | 1.8987 | 2.0422 | 1.9346 | 2.0781 | 1.3632 | 2.3377 | 2.8846 | 2.8846 | 3.2491 | 3.2491 | 2019-03-04 22:00 | 1.9053 | 3.1224 | 5.1254 | 5.1254 | 5.1254 | 5.1254
2021-01-05 11:00 | 1.7462 | 2.1249 | 2.0791 | 2.2362 | 2.1184 | 2.2755 | 1.3489 | 2.3132 | 2.8543 | 2.8543 | 3.2151 | 3.2151 | 2019-03-04 23:00 | 1.8443 | 3.0224 | 4.9614 | 4.9614 | 4.9614 | 4.9614
2021-01-05 12:00 | 1.8176 | 2.2118 | 2.1641 | 2.3277 | 2.205 | 2.3686 | 1.3975 | 2.3965 | 2.9571 | 2.9571 | 3.3309 | 3.3309 | 2019-03-05 | 1.7071 | 2.7976 | 4.5923 | 4.5923 | 4.5923 | 4.5923
2021-01-05 13:00 | 1.7319 | 2.1075 | 2.0621 | 2.2179 | 2.101 | 2.2569 | 1.4375 | 2.4651 | 3.0418 | 3.0418 | 3.4262 | 3.4262 | 2019-03-05 01:00 | 1.6614 | 2.7227 | 4.4693 | 4.4693 | 4.4693 | 4.4693
2021-01-05 14:00 | 1.5633 | 1.9023 | 1.8613 | 2.002 | 1.8965 | 2.0372 | 1.5061 | 2.5827 | 3.1869 | 3.1869 | 3.5897 | 3.5897 | 2019-03-05 02:00 | 1.6919 | 2.7726 | 4.5513 | 4.5513 | 4.5513 | 4.5513
2021-01-05 15:00 | 1.6776 | 2.0414 | 1.9974 | 2.1484 | 2.0351 | 2.1861 | 1.3832 | 2.372 | 2.9269 | 2.9269 | 3.2968 | 3.2968 | 2019-03-05 03:00 | 1.608 | 2.6353 | 4.3258 | 4.3258 | 4.3258 | 4.3258
2021-01-05 16:00 | 1.6376 | 1.9927 | 1.9498 | 2.0971 | 1.9866 | 2.134 | 1.3718 | 2.3524 | 2.9027 | 2.9027 | 3.2696 | 3.2696 | 2019-03-05 04:00 | 1.6233 | 2.6602 | 4.3668 | 4.3668 | 4.3668 | 4.3668
2021-01-05 17:00 | 1.8433 | 2.2431 | 2.1948 | 2.3607 | 2.2362 | 2.4021 | 1.4918 | 2.5582 | 3.1567 | 3.1567 | 3.5557 | 3.5557 | 2019-03-05 05:00 | 1.7909 | 2.935 | 4.8179 | 4.8179 | 4.8179 | 4.8179
2021-01-05 18:00 | 2.0177 | 2.4553 | 2.4023 | 2.5839 | 2.4477 | 2.6293 | 1.5032 | 2.5778 | 3.1809 | 3.1809 | 3.5829 | 3.5829 | 2019-03-05 06:00 | 1.9891 | 3.2597 | 5.3509 | 5.3509 | 5.3509 | 5.3509
2021-01-05 19:00 | 1.8662 | 2.271 | 2.222 | 2.3899 | 2.264 | 2.4319 | 1.5804 | 2.7101 | 3.3442 | 3.3442 | 3.7668 | 3.7668 | 2019-03-05 07:00 | 2.0882 | 3.4221 | 5.6174 | 5.6174 | 5.6174 | 5.6174
2021-01-05 20:00 | 1.669 | 2.031 | 1.9872 | 2.1374 | 2.0247 | 2.175 | 1.5147 | 2.5974 | 3.2051 | 3.2051 | 3.6102 | 3.6102 | 2019-03-05 08:00 | 2.2253 | 3.6469 | 5.9865 | 5.9865 | 5.9865 | 5.9865
2021-01-05 21:00 | 1.669 | 2.031 | 1.9872 | 2.1374 | 2.0247 | 2.175 | 1.4718 | 2.5239 | 3.1144 | 3.1144 | 3.508 | 3.508 | 2019-03-05 09:00 | 2.4235 | 3.9716 | 6.5195 | 6.5195 | 6.5195 | 6.5195
2021-01-05 22:00 | 1.629 | 1.9823 | 1.9396 | 2.0862 | 1.9762 | 2.1228 | 1.2918 | 2.2152 | 2.7334 | 2.7334 | 3.0789 | 3.0789 | 2019-03-05 10:00 | 2.4311 | 3.9841 | 6.54 | 6.54 | 6.54 | 6.54
2021-01-05 23:00 | 1.3889 | 1.6902 | 1.6537 | 1.7787 | 1.685 | 1.81 | 1.0346 | 1.7741 | 2.1891 | 2.1891 | 2.4658 | 2.4658 | 2019-03-05 11:00 | 2.5454 | 4.1715 | 6.8475 | 6.8475 | 6.8475 | 6.8475
2021-01-06 | 1.312 | 1.5966 | 1.5622 | 1.6803 | 1.5917 | 1.7098 | 0.93187 | 1.598 | 1.9718 | 1.9718 | 2.2211 | 2.2211 | 2019-03-05 12:00 | 2.5607 | 4.1964 | 6.8885 | 6.8885 | 6.8885 | 6.8885
2021-01-06 01:00 | 1.2449 | 1.5149 | 1.4823 | 1.5943 | 1.5103 | 1.6223 | 0.80604 | 1.3822 | 1.7056 | 1.7056 | 1.9212 | 1.9212 | 2019-03-05 13:00 | 2.4463 | 4.0091 | 6.581 | 6.581 | 6.581 | 6.581
2021-01-06 02:00 | 1.1603 | 1.412 | 1.3816 | 1.486 | 1.4077 | 1.5121 | 0.76305 | 1.3085 | 1.6146 | 1.6146 | 1.8187 | 1.8187 | 2019-03-05 14:00 | 2.4311 | 3.9841 | 6.54 | 6.54 | 6.54 | 6.54
2021-01-06 03:00 | 1.1344 | 1.3804 | 1.3506 | 1.4527 | 1.3762 | 1.4783 | 0.71733 | 1.2301 | 1.5179 | 1.5179 | 1.7097 | 1.7097 | 2019-03-05 15:00 | 2.5226 | 4.134 | 6.786 | 6.786 | 6.786 | 6.786
2021-01-06 04:00 | 1.1403 | 1.3876 | 1.3577 | 1.4603 | 1.3833 | 1.486 | 0.71733 | 1.2301 | 1.5179 | 1.5179 | 1.7097 | 1.7097 | 2019-03-05 16:00 | 2.4387 | 3.9966 | 6.5605 | 6.5605 | 6.5605 | 6.5605
2021-01-06 05:00 | 1.1915 | 1.4499 | 1.4186 | 1.5258 | 1.4454 | 1.5526 | 0.75734 | 1.2987 | 1.6025 | 1.6025 | 1.8051 | 1.8051 | 2019-03-05 17:00 | 2.3701 | 3.8842 | 6.376 | 6.376 | 6.376 | 6.376
2021-01-06 06:00 | 1.2803 | 1.558 | 1.5244 | 1.6396 | 1.5532 | 1.6685 | 0.9431 | 1.6173 | 1.9956 | 1.9956 | 2.2478 | 2.2478 | 2019-03-05 18:00 | 2.2406 | 3.6719 | 6.0275 | 6.0275 | 6.0275 | 6.0275
2021-01-06 07:00 | 1.5232 | 1.8536 | 1.8137 | 1.9507 | 1.8479 | 1.985 | 1.106 | 1.8966 | 2.3403 | 2.3403 | 2.6361 | 2.6361 | 2019-03-05 19:00 | 2.1034 | 3.4471 | 5.6584 | 5.6584 | 5.6584 | 5.6584
2021-01-06 08:00 | 1.6004 | 1.9475 | 1.9055 | 2.0496 | 1.9415 | 2.0856 | 1.2375 | 2.122 | 2.6185 | 2.6185 | 2.9494 | 2.9494 | 2019-03-05 20:00 | 2.0272 | 3.3222 | 5.4534 | 5.4534 | 5.4534 | 5.4534
2021-01-06 09:00 | 1.5547 | 1.8919 | 1.8511 | 1.991 | 1.8861 | 2.026 | 1.2146 | 2.0828 | 2.5701 | 2.5701 | 2.8949 | 2.8949 | 2019-03-05 21:00 | 1.9738 | 3.2348 | 5.3099 | 5.3099 | 5.3099 | 5.3099
2021-01-06 10:00 | 1.5947 | 1.9406 | 1.8987 | 2.0422 | 1.9346 | 2.0781 | 1.3375 | 2.2936 | 2.8301 | 2.8301 | 3.1878 | 3.1878 | 2019-03-05 22:00 | 1.8976 | 3.1099 | 5.1049 | 5.1049 | 5.1049 | 5.1049
2021-01-06 11:00 | 1.5575 | 1.8954 | 1.8545 | 1.9947 | 1.8895 | 2.0297 | 1.4118 | 2.421 | 2.9874 | 2.9874 | 3.3649 | 3.3649 | 2019-03-05 23:00 | 1.8062 | 2.96 | 4.8589 | 4.8589 | 4.8589 | 4.8589
2021-01-06 12:00 | 1.7404 | 2.1179 | 2.0723 | 2.2289 | 2.1114 | 2.2681 | 1.4175 | 2.4308 | 2.9995 | 2.9995 | 3.3786 | 3.3786 | 2019-03-06 | 1.8062 | 2.96 | 4.8589 | 4.8589 | 4.8589 | 4.8589
2021-01-06 13:00 | 1.5918 | 1.9371 | 1.8953 | 2.0386 | 1.9311 | 2.0744 | 1.5461 | 2.6513 | 3.2716 | 3.2716 | 3.6851 | 3.6851 | 2019-03-06 01:00 | 1.7071 | 2.7976 | 4.5923 | 4.5923 | 4.5923 | 4.5923
2021-01-06 14:00 | 1.6861 | 2.0519 | 2.0076 | 2.1594 | 2.0455 | 2.1973 | 1.4575 | 2.4994 | 3.0841 | 3.0841 | 3.4739 | 3.4739 | 2019-03-06 02:00 | 1.6385 | 2.6852 | 4.4078 | 4.4078 | 4.4078 | 4.4078
2021-01-06 15:00 | 1.6204 | 1.9719 | 1.9293 | 2.0752 | 1.9658 | 2.1116 | 1.3889 | 2.3818 | 2.939 | 2.939 | 3.3105 | 3.3105 | 2019-03-06 03:00 | 1.6309 | 2.6727 | 4.3873 | 4.3873 | 4.3873 | 4.3873
2021-01-06 16:00 | 1.6004 | 1.9475 | 1.9055 | 2.0496 | 1.9415 | 2.0856 | 1.3603 | 2.3328 | 2.8785 | 2.8785 | 3.2423 | 3.2423 | 2019-03-06 04:00 | 1.6309 | 2.6727 | 4.3873 | 4.3873 | 4.3873 | 4.3873
2021-01-06 17:00 | 1.6347 | 1.9893 | 1.9464 | 2.0935 | 1.9831 | 2.1303 | 1.5461 | 2.6513 | 3.2716 | 3.2716 | 3.6851 | 3.6851 | 2019-03-06 05:00 | 1.7528 | 2.8726 | 4.7154 | 4.7154 | 4.7154 | 4.7154
2021-01-06 18:00 | 1.709 | 2.0797 | 2.0348 | 2.1886 | 2.0733 | 2.2271 | 1.4261 | 2.4455 | 3.0176 | 3.0176 | 3.399 | 3.399 | 2019-03-06 06:00 | 1.9815 | 3.2472 | 5.3304 | 5.3304 | 5.3304 | 5.3304
2021-01-06 19:00 | 1.609 | 1.958 | 1.9157 | 2.0605 | 1.9519 | 2.0967 | 1.4204 | 2.4357 | 3.0055 | 3.0055 | 3.3854 | 3.3854 | 2019-03-06 07:00 | 2.0805 | 3.4096 | 5.5969 | 5.5969 | 5.5969 | 5.5969
2021-01-06 20:00 | 1.6176 | 1.9684 | 1.9259 | 2.0715 | 1.9623 | 2.1079 | 1.4032 | 2.4063 | 2.9692 | 2.9692 | 3.3445 | 3.3445 | 2019-03-06 08:00 | 2.3168 | 3.7968 | 6.2325 | 6.2325 | 6.2325 | 6.2325
2021-01-06 21:00 | 1.6061 | 1.9545 | 1.9123 | 2.0569 | 1.9485 | 2.093 | 1.4061 | 2.4112 | 2.9753 | 2.9753 | 3.3513 | 3.3513 | 2019-03-06 09:00 | 2.3168 | 3.7968 | 6.2325 | 6.2325 | 6.2325 | 6.2325
2021-01-06 22:00 | 1.4432 | 1.7563 | 1.7184 | 1.8483 | 1.7508 | 1.8807 | 1.246 | 2.1367 | 2.6366 | 2.6366 | 2.9699 | 2.9699 | 2019-03-06 10:00 | 2.3473 | 3.8467 | 6.3145 | 6.3145 | 6.3145 | 6.3145
2021-01-06 23:00 | 1.4089 | 1.7145 | 1.6775 | 1.8043 | 1.7092 | 1.836 | 1.012 | 1.7354 | 2.1414 | 2.1414 | 2.412 | 2.412 | 2019-03-06 11:00 | 2.3549 | 3.8592 | 6.335 | 6.335 | 6.335 | 6.335
2021-01-07 | 1.3861 | 1.6867 | 1.6503 | 1.7751 | 1.6815 | 1.8063 | 0.8888 | 1.5241 | 1.8807 | 1.8807 | 2.1184 | 2.1184 | 2019-03-06 12:00 | 2.2939 | 3.7593 | 6.171 | 6.171 | 6.171 | 6.171
2021-01-07 01:00 | 1.2346 | 1.5024 | 1.47 | 1.5811 | 1.4978 | 1.6089 | 0.7459 | 1.2791 | 1.5783 | 1.5783 | 1.7778 | 1.7778 | 2019-03-06 13:00 | 2.3625 | 3.8717 | 6.3555 | 6.3555 | 6.3555 | 6.3555
2021-01-07 02:00 | 1.1575 | 1.4085 | 1.3782 | 1.4823 | 1.4042 | 1.5084 | 0.68589 | 1.1762 | 1.4513 | 1.4513 | 1.6348 | 1.6348 | 2019-03-06 14:00 | 2.3625 | 3.8717 | 6.3555 | 6.3555 | 6.3555 | 6.3555
2021-01-07 03:00 | 1.1317 | 1.3772 | 1.3475 | 1.4493 | 1.3729 | 1.4748 | 0.69732 | 1.1958 | 1.4755 | 1.4755 | 1.662 | 1.662 | 2019-03-06 15:00 | 2.2406 | 3.6719 | 6.0275 | 6.0275 | 6.0275 | 6.0275
2021-01-07 04:00 | 1.1746 | 1.4294 | 1.3985 | 1.5042 | 1.4249 | 1.5307 | 0.67731 | 1.1615 | 1.4332 | 1.4332 | 1.6144 | 1.6144 | 2019-03-06 16:00 | 2.2177 | 3.6344 | 5.966 | 5.966 | 5.966 | 5.966
2021-01-07 05:00 | 1.1746 | 1.4294 | 1.3985 | 1.5042 | 1.4249 | 1.5307 | 0.6916 | 1.186 | 1.4634 | 1.4634 | 1.6484 | 1.6484 | 2019-03-06 17:00 | 2.1567 | 3.5345 | 5.8019 | 5.8019 | 5.8019 | 5.8019
2021-01-07 06:00 | 1.3661 | 1.6624 | 1.6265 | 1.7494 | 1.6572 | 1.7802 | 0.88594 | 1.5192 | 1.8747 | 1.8747 | 2.1116 | 2.1116 | 2019-03-06 18:00 | 1.9738 | 3.2348 | 5.3099 | 5.3099 | 5.3099 | 5.3099
2021-01-07 07:00 | 1.4232 | 1.7319 | 1.6946 | 1.8226 | 1.7266 | 1.8547 | 1.1089 | 1.9015 | 2.3464 | 2.3464 | 2.6429 | 2.6429 | 2019-03-06 19:00 | 1.9662 | 3.2223 | 5.2894 | 5.2894 | 5.2894 | 5.2894
2021-01-07 08:00 | 1.4804 | 1.8015 | 1.7626 | 1.8958 | 1.7959 | 1.9292 | 1.2003 | 2.0583 | 2.5399 | 2.5399 | 2.8609 | 2.8609 | 2019-03-06 20:00 | 1.8062 | 2.96 | 4.8589 | 4.8589 | 4.8589 | 4.8589
2021-01-07 09:00 | 1.5147 | 1.8432 | 1.8034 | 1.9398 | 1.8375 | 1.9738 | 1.2403 | 2.1269 | 2.6245 | 2.6245 | 2.9562 | 2.9562 | 2019-03-06 21:00 | 1.6766 | 2.7477 | 4.5103 | 4.5103 | 4.5103 | 4.5103
2021-01-07 10:00 | 1.5547 | 1.8919 | 1.8511 | 1.991 | 1.8861 | 2.026 | 1.4175 | 2.4308 | 2.9995 | 2.9995 | 3.3786 | 3.3786 | 2019-03-06 22:00 | 1.6461 | 2.6977 | 4.4283 | 4.4283 | 4.4283 | 4.4283
2021-01-07 11:00 | 1.5261 | 1.8571 | 1.8171 | 1.9544 | 1.8514 | 1.9887 | 1.4689 | 2.519 | 3.1083 | 3.1083 | 3.5012 | 3.5012 | 2019-03-06 23:00 | 1.5623 | 2.5603 | 4.2028 | 4.2028 | 4.2028 | 4.2028
2021-01-07 12:00 | 1.549 | 1.8849 | 1.8443 | 1.9837 | 1.8791 | 2.0185 | 1.4347 | 2.4602 | 3.0357 | 3.0357 | 3.4194 | 3.4194 | 2019-03-07 | 1.5547 | 2.5478 | 4.1823 | 4.1823 | 4.1823 | 4.1823
2021-01-07 13:00 | 1.4918 | 1.8154 | 1.7762 | 1.9105 | 1.8098 | 1.944 | 1.4232 | 2.4406 | 3.0116 | 3.0116 | 3.3922 | 3.3922 | 2019-03-07 01:00 | 1.5318 | 2.5104 | 4.1208 | 4.1208 | 4.1208 | 4.1208
2021-01-07 14:00 | 1.5804 | 1.9232 | 1.8817 | 2.0239 | 1.9173 | 2.0595 | 1.4375 | 2.4651 | 3.0418 | 3.0418 | 3.4262 | 3.4262 | 2019-03-07 02:00 | 1.4404 | 2.3605 | 3.8748 | 3.8748 | 3.8748 | 3.8748
2021-01-07 15:00 | 1.6147 | 1.9649 | 1.9225 | 2.0679 | 1.9589 | 2.1042 | 1.3746 | 2.3573 | 2.9088 | 2.9088 | 3.2764 | 3.2764 | 2019-03-07 03:00 | 1.4251 | 2.3355 | 3.8338 | 3.8338 | 3.8338 | 3.8338
2021-01-07 16:00 | 1.5918 | 1.9371 | 1.8953 | 2.0386 | 1.9311 | 2.0744 | 1.3518 | 2.3181 | 2.8604 | 2.8604 | 3.2219 | 3.2219 | 2019-03-07 04:00 | 1.4175 | 2.323 | 3.8133 | 3.8133 | 3.8133 | 3.8133
2021-01-07 17:00 | 1.6376 | 1.9927 | 1.9498 | 2.0971 | 1.9866 | 2.134 | 1.4375 | 2.4651 | 3.0418 | 3.0418 | 3.4262 | 3.4262 | 2019-03-07 05:00 | 1.5928 | 2.6103 | 4.2848 | 4.2848 | 4.2848 | 4.2848
2021-01-07 18:00 | 1.7347 | 2.111 | 2.0655 | 2.2216 | 2.1045 | 2.2606 | 1.4547 | 2.4945 | 3.0781 | 3.0781 | 3.4671 | 3.4671 | 2019-03-07 06:00 | 1.7528 | 2.8726 | 4.7154 | 4.7154 | 4.7154 | 4.7154
2021-01-07 19:00 | 1.7218 | 2.0952 | 2.05 | 2.205 | 2.0887 | 2.2437 | 1.489 | 2.5533 | 3.1506 | 3.1506 | 3.5489 | 3.5489 | 2019-03-07 07:00 | 2.172 | 3.5595 | 5.8429 | 5.8429 | 5.8429 | 5.8429
2021-01-07 20:00 | 1.6204 | 1.9719 | 1.9293 | 2.0752 | 1.9658 | 2.1116 | 1.4575 | 2.4994 | 3.0841 | 3.0841 | 3.4739 | 3.4739 | 2019-03-07 08:00 | 2.0424 | 3.3472 | 5.4944 | 5.4944 | 5.4944 | 5.4944
2021-01-07 21:00 | 1.5839 | 1.9274 | 1.8858 | 2.0284 | 1.9215 | 2.064 | 1.4146 | 2.4259 | 2.9934 | 2.9934 | 3.3718 | 3.3718 | 2019-03-07 09:00 | 2.2482 | 3.6844 | 6.048 | 6.048 | 6.048 | 6.048
2021-01-07 22:00 | 1.5118 | 1.8397 | 1.8 | 1.9361 | 1.8341 | 1.9701 | 1.2547 | 2.1516 | 2.6549 | 2.6549 | 2.9905 | 2.9905 | 2019-03-07 10:00 | 2.2711 | 3.7218 | 6.1095 | 6.1095 | 6.1095 | 6.1095
2021-01-07 23:00 | 1.4061 | 1.711 | 1.6741 | 1.8007 | 1.7058 | 1.8323 | 1.0803 | 1.8525 | 2.2859 | 2.2859 | 2.5748 | 2.5748 | 2019-03-07 11:00 | 2.1491 | 3.522 | 5.7814 | 5.7814 | 5.7814 | 5.7814
2021-01-08 | 1.3746 | 1.6728 | 1.6367 | 1.7604 | 1.6676 | 1.7914 | 0.91452 | 1.5683 | 1.9351 | 1.9351 | 2.1797 | 2.1797 | 2019-03-07 12:00 | 2.2863 | 3.7468 | 6.1505 | 6.1505 | 6.1505 | 6.1505
2021-01-08 01:00 | 1.2346 | 1.5024 | 1.47 | 1.5811 | 1.4978 | 1.6089 | 0.80592 | 1.382 | 1.7053 | 1.7053 | 1.9209 | 1.9209 | 2019-03-07 13:00 | 2.3015 | 3.7718 | 6.1915 | 6.1915 | 6.1915 | 6.1915
2021-01-08 02:00 | 1.2205 | 1.4852 | 1.4532 | 1.563 | 1.4806 | 1.5905 | 0.71071 | 1.2188 | 1.5039 | 1.5039 | 1.694 | 1.694 | 2019-03-07 14:00 | 2.2939 | 3.7593 | 6.171 | 6.171 | 6.171 | 6.171
2021-01-08 03:00 | 1.1746 | 1.4294 | 1.3985 | 1.5042 | 1.4249 | 1.5307 | 0.73447 | 1.2595 | 1.5542 | 1.5542 | 1.7506 | 1.7506 | 2019-03-07 15:00 | 2.1415 | 3.5095 | 5.7609 | 5.7609 | 5.7609 | 5.7609
2021-01-08 04:00 | 1.1721 | 1.4264 | 1.3956 | 1.5011 | 1.422 | 1.5275 | 0.76591 | 1.3134 | 1.6207 | 1.6207 | 1.8255 | 1.8255 | 2019-03-07 16:00 | 2.1491 | 3.522 | 5.7814 | 5.7814 | 5.7814 | 5.7814
2021-01-08 05:00 | 1.3146 | 1.5998 | 1.5653 | 1.6836 | 1.5948 | 1.7131 | 0.76011 | 1.3035 | 1.6084 | 1.6084 | 1.8117 | 1.8117 | 2019-03-07 17:00 | 2.1949 | 3.597 | 5.9044 | 5.9044 | 5.9044 | 5.9044
2021-01-08 06:00 | 1.4232 | 1.7319 | 1.6946 | 1.8226 | 1.7266 | 1.8547 | 0.89451 | 1.5339 | 1.8928 | 1.8928 | 2.132 | 2.132 | 2019-03-07 18:00 | 2.0119 | 3.2972 | 5.4124 | 5.4124 | 5.4124 | 5.4124
2021-01-08 07:00 | 1.6118 | 1.9614 | 1.9191 | 2.0642 | 1.9554 | 2.1005 | 1.046 | 1.7937 | 2.2133 | 2.2133 | 2.4931 | 2.4931 | 2019-03-07 19:00 | 2.0119 | 3.2972 | 5.4124 | 5.4124 | 5.4124 | 5.4124
2021-01-08 08:00 | 1.7062 | 2.0762 | 2.0314 | 2.185 | 2.0698 | 2.2234 | 1.2232 | 2.0975 | 2.5882 | 2.5882 | 2.9154 | 2.9154 | 2019-03-07 20:00 | 1.89 | 3.0974 | 5.0844 | 5.0844 | 5.0844 | 5.0844
2021-01-08 09:00 | 1.7033 | 2.0727 | 2.028 | 2.1813 | 2.0663 | 2.2196 | 1.2175 | 2.0877 | 2.5761 | 2.5761 | 2.9018 | 2.9018 | 2019-03-07 21:00 | 1.7147 | 2.8101 | 4.6128 | 4.6128 | 4.6128 | 4.6128
2021-01-08 10:00 | 1.709 | 2.0797 | 2.0348 | 2.1886 | 2.0733 | 2.2271 | 1.4204 | 2.4357 | 3.0055 | 3.0055 | 3.3854 | 3.3854 | 2019-03-07 22:00 | 1.7223 | 2.8226 | 4.6333 | 4.6333 | 4.6333 | 4.6333
2021-01-08 11:00 | 1.769 | 2.1527 | 2.1063 | 2.2655 | 2.1461 | 2.3053 | 1.3861 | 2.3769 | 2.9329 | 2.9329 | 3.3036 | 3.3036 | 2019-03-07 23:00 | 1.5852 | 2.5978 | 4.2643 | 4.2643 | 4.2643 | 4.2643
2021-01-08 12:00 | 1.7062 | 2.0762 | 2.0314 | 2.185 | 2.0698 | 2.2234 | 1.4289 | 2.4504 | 3.0236 | 3.0236 | 3.4058 | 3.4058 | 2019-03-08 | 1.5394 | 2.5229 | 4.1413 | 4.1413 | 4.1413 | 4.1413
2021-01-08 13:00 | 1.6376 | 1.9927 | 1.9498 | 2.0971 | 1.9866 | 2.134 | 1.4375 | 2.4651 | 3.0418 | 3.0418 | 3.4262 | 3.4262 | 2019-03-08 01:00 | 1.4327 | 2.348 | 3.8543 | 3.8543 | 3.8543 | 3.8543
2021-01-08 14:00 | 1.7004 | 2.0693 | 2.0246 | 2.1777 | 2.0629 | 2.2159 | 1.3918 | 2.3867 | 2.945 | 2.945 | 3.3173 | 3.3173 | 2019-03-08 02:00 | 1.4175 | 2.323 | 3.8133 | 3.8133 | 3.8133 | 3.8133
2021-01-08 15:00 | 1.6622 | 2.0228 | 1.9791 | 2.1287 | 2.0165 | 2.1661 | 1.3032 | 2.2348 | 2.7576 | 2.7576 | 3.1061 | 3.1061 | 2019-03-08 03:00 | 1.4175 | 2.323 | 3.8133 | 3.8133 | 3.8133 | 3.8133
2021-01-08 16:00 | 1.5918 | 1.9371 | 1.8953 | 2.0386 | 1.9311 | 2.0744 | 1.3946 | 2.3916 | 2.9511 | 2.9511 | 3.3241 | 3.3241 | 2019-03-08 04:00 | 1.5013 | 2.4604 | 4.0388 | 4.0388 | 4.0388 | 4.0388
2021-01-08 17:00 | 1.7605 | 2.1423 | 2.0961 | 2.2545 | 2.1357 | 2.2941 | 1.4975 | 2.568 | 3.1688 | 3.1688 | 3.5693 | 3.5693 | 2019-03-08 05:00 | 1.6004 | 2.6228 | 4.3053 | 4.3053 | 4.3053 | 4.3053
2021-01-08 18:00 | 1.9148 | 2.3301 | 2.2798 | 2.4522 | 2.3229 | 2.4952 | 1.569 | 2.6905 | 3.32 | 3.32 | 3.7396 | 3.7396 | 2019-03-08 06:00 | 1.7071 | 2.7976 | 4.5923 | 4.5923 | 4.5923 | 4.5923
2021-01-08 19:00 | 1.7914 | 2.1799 | 2.1329 | 2.2941 | 2.1732 | 2.3344 | 1.6776 | 2.8768 | 3.5498 | 3.5498 | 3.9984 | 3.9984 | 2019-03-08 07:00 | 1.89 | 3.0974 | 5.0844 | 5.0844 | 5.0844 | 5.0844
2021-01-08 20:00 | 1.7433 | 2.1214 | 2.0757 | 2.2326 | 2.1149 | 2.2718 | 1.5661 | 2.6856 | 3.3139 | 3.3139 | 3.7328 | 3.7328 | 2019-03-08 08:00 | 2.0348 | 3.3347 | 5.4739 | 5.4739 | 5.4739 | 5.4739
2021-01-08 21:00 | 1.6604 | 2.0206 | 1.977 | 2.1264 | 2.0143 | 2.1638 | 1.569 | 2.6905 | 3.32 | 3.32 | 3.7396 | 3.7396 | 2019-03-08 09:00 | 2.0577 | 3.3721 | 5.5354 | 5.5354 | 5.5354 | 5.5354
2021-01-08 22:00 | 1.5404 | 1.8745 | 1.8341 | 1.9727 | 1.8687 | 2.0074 | 1.3546 | 2.323 | 2.8664 | 2.8664 | 3.2287 | 3.2287 | 2019-03-08 10:00 | 2.2025 | 3.6094 | 5.9249 | 5.9249 | 5.9249 | 5.9249
2021-01-08 23:00 | 1.4632 | 1.7806 | 1.7422 | 1.8739 | 1.7751 | 1.9068 | 1.1603 | 1.9897 | 2.4552 | 2.4552 | 2.7655 | 2.7655 | 2019-03-08 11:00 | 2.2253 | 3.6469 | 5.9865 | 5.9865 | 5.9865 | 5.9865
2021-01-09 | 1.4004 | 1.7041 | 1.6673 | 1.7934 | 1.6988 | 1.8249 | 1.0088 | 1.73 | 2.1347 | 2.1347 | 2.4045 | 2.4045 | 2019-03-08 12:00 | 2.2787 | 3.7343 | 6.13 | 6.13 | 6.13 | 6.13
2021-01-09 01:00 | 1.2803 | 1.558 | 1.5244 | 1.6396 | 1.5532 | 1.6685 | 0.81735 | 1.4016 | 1.7295 | 1.7295 | 1.9481 | 1.9481 | 2019-03-08 13:00 | 2.4921 | 4.084 | 6.704 | 6.704 | 6.704 | 6.704
2021-01-09 02:00 | 1.1774 | 1.4328 | 1.4019 | 1.5079 | 1.4284 | 1.5344 | 0.76308 | 1.3086 | 1.6147 | 1.6147 | 1.8188 | 1.8188 | 2019-03-08 14:00 | 2.4463 | 4.0091 | 6.581 | 6.581 | 6.581 | 6.581
2021-01-09 03:00 | 1.1718 | 1.4259 | 1.3952 | 1.5006 | 1.4216 | 1.527 | 0.73161 | 1.2546 | 1.5481 | 1.5481 | 1.7438 | 1.7438 | 2019-03-08 15:00 | 2.3473 | 3.8467 | 6.3145 | 6.3145 | 6.3145 | 6.3145
2021-01-09 04:00 | 1.1946 | 1.4537 | 1.4223 | 1.5298 | 1.4492 | 1.5567 | 0.72876 | 1.2497 | 1.5421 | 1.5421 | 1.737 | 1.737 | 2019-03-08 16:00 | 2.3015 | 3.7718 | 6.1915 | 6.1915 | 6.1915 | 6.1915
2021-01-09 05:00 | 1.1832 | 1.4398 | 1.4087 | 1.5152 | 1.4353 | 1.5418 | 0.7459 | 1.2791 | 1.5783 | 1.5783 | 1.7778 | 1.7778 | 2019-03-08 17:00 | 2.1949 | 3.597 | 5.9044 | 5.9044 | 5.9044 | 5.9044
2021-01-09 06:00 | 1.2603 | 1.5337 | 1.5006 | 1.614 | 1.529 | 1.6424 | 0.78278 | 1.3423 | 1.6564 | 1.6564 | 1.8657 | 1.8657 | 2019-03-08 18:00 | 2.0882 | 3.4221 | 5.6174 | 5.6174 | 5.6174 | 5.6174
2021-01-09 07:00 | 1.3118 | 1.5963 | 1.5618 | 1.6799 | 1.5914 | 1.7094 | 0.96882 | 1.6614 | 2.05 | 2.05 | 2.3091 | 2.3091 | 2019-03-08 19:00 | 1.89 | 3.0974 | 5.0844 | 5.0844 | 5.0844 | 5.0844
2021-01-09 08:00 | 1.3346 | 1.6241 | 1.5891 | 1.7092 | 1.6191 | 1.7392 | 1.1003 | 1.8868 | 2.3282 | 2.3282 | 2.6225 | 2.6225 | 2019-03-08 20:00 | 1.9281 | 3.1598 | 5.1869 | 5.1869 | 5.1869 | 5.1869
2021-01-09 09:00 | 1.3518 | 1.645 | 1.6095 | 1.7311 | 1.6399 | 1.7616 | 1.2289 | 2.1073 | 2.6003 | 2.6003 | 2.929 | 2.929 | 2019-03-08 21:00 | 1.7909 | 2.935 | 4.8179 | 4.8179 | 4.8179 | 4.8179
2021-01-09 10:00 | 1.3489 | 1.6415 | 1.6061 | 1.7275 | 1.6364 | 1.7578 | 1.4432 | 2.4749 | 3.0539 | 3.0539 | 3.4399 | 3.4399 | 2019-03-08 22:00 | 1.7605 | 2.8851 | 4.7359 | 4.7359 | 4.7359 | 4.7359
2021-01-09 11:00 | 1.3403 | 1.6311 | 1.5959 | 1.7165 | 1.626 | 1.7467 | 1.3918 | 2.3867 | 2.945 | 2.945 | 3.3173 | 3.3173 | 2019-03-08 23:00 | 1.6995 | 2.7851 | 4.5718 | 4.5718 | 4.5718 | 4.5718
2021-01-09 12:00 | 1.2889 | 1.5685 | 1.5346 | 1.6506 | 1.5636 | 1.6796 | 1.4947 | 2.5631 | 3.1627 | 3.1627 | 3.5625 | 3.5625 | 2019-03-09 | 1.5699 | 2.5728 | 4.2233 | 4.2233 | 4.2233 | 4.2233
2021-01-09 13:00 | 1.2603 | 1.5337 | 1.5006 | 1.614 | 1.529 | 1.6424 | 1.43 | 2.4523 | 3.026 | 3.026 | 3.4084 | 3.4084 | 2019-03-09 01:00 | 1.5623 | 2.5603 | 4.2028 | 4.2028 | 4.2028 | 4.2028
2021-01-09 14:00 | 1.266 | 1.5406 | 1.5074 | 1.6213 | 1.5359 | 1.6498 | 1.4575 | 2.4994 | 3.0841 | 3.0841 | 3.4739 | 3.4739 | 2019-03-09 02:00 | 1.5166 | 2.4854 | 4.0798 | 4.0798 | 4.0798 | 4.0798
2021-01-09 15:00 | 1.1974 | 1.4572 | 1.4257 | 1.5335 | 1.4527 | 1.5605 | 1.4347 | 2.4602 | 3.0357 | 3.0357 | 3.4194 | 3.4194 | 2019-03-09 03:00 | 1.5013 | 2.4604 | 4.0388 | 4.0388 | 4.0388 | 4.0388
2021-01-09 16:00 | 1.4206 | 1.7287 | 1.6914 | 1.8193 | 1.7234 | 1.8512 | 1.474 | 2.5276 | 3.1189 | 3.1189 | 3.5131 | 3.5131 | 2019-03-09 04:00 | 1.5775 | 2.5853 | 4.2438 | 4.2438 | 4.2438 | 4.2438
2021-01-09 17:00 | 1.4547 | 1.7702 | 1.732 | 1.8629 | 1.7647 | 1.8956 | 1.5804 | 2.7101 | 3.3442 | 3.3442 | 3.7668 | 3.7668 | 2019-03-09 05:00 | 1.608 | 2.6353 | 4.3258 | 4.3258 | 4.3258 | 4.3258
2021-01-09 18:00 | 1.629 | 1.9823 | 1.9396 | 2.0862 | 1.9762 | 2.1228 | 1.5775 | 2.7052 | 3.3381 | 3.3381 | 3.76 | 3.76 | 2019-03-09 06:00 | 1.7909 | 2.935 | 4.8179 | 4.8179 | 4.8179 | 4.8179
2021-01-09 19:00 | 1.6206 | 1.9721 | 1.9296 | 2.0754 | 1.966 | 2.1119 | 1.5947 | 2.7346 | 3.3744 | 3.3744 | 3.8009 | 3.8009 | 2019-03-09 07:00 | 1.8595 | 3.0474 | 5.0024 | 5.0024 | 5.0024 | 5.0024
2021-01-09 20:00 | 1.6347 | 1.9893 | 1.9464 | 2.0935 | 1.9831 | 2.1303 | 1.4747 | 2.5288 | 3.1204 | 3.1204 | 3.5148 | 3.5148 | 2019-03-09 08:00 | 2.0729 | 3.3971 | 5.5764 | 5.5764 | 5.5764 | 5.5764
2021-01-09 21:00 | 1.6033 | 1.951 | 1.9089 | 2.0532 | 1.945 | 2.0893 | 1.4261 | 2.4455 | 3.0176 | 3.0176 | 3.399 | 3.399 | 2019-03-09 09:00 | 2.1949 | 3.597 | 5.9044 | 5.9044 | 5.9044 | 5.9044
2021-01-09 22:00 | 1.5318 | 1.8641 | 1.8239 | 1.9617 | 1.8583 | 1.9962 | 1.3403 | 2.2985 | 2.8362 | 2.8362 | 3.1947 | 3.1947 | 2019-03-09 10:00 | 2.2787 | 3.7343 | 6.13 | 6.13 | 6.13 | 6.13
2021-01-09 23:00 | 1.4289 | 1.7389 | 1.7014 | 1.83 | 1.7335 | 1.8621 | 1.1546 | 1.9799 | 2.4431 | 2.4431 | 2.7519 | 2.7519 | 2019-03-09 11:00 | 2.332 | 3.8218 | 6.2735 | 6.2735 | 6.2735 | 6.2735
2021-01-10 | 1.3552 | 1.6491 | 1.6135 | 1.7355 | 1.644 | 1.766 | 1.0203 | 1.7496 | 2.1589 | 2.1589 | 2.4317 | 2.4317 | 2019-03-09 12:00 | 2.1949 | 3.597 | 5.9044 | 5.9044 | 5.9044 | 5.9044
2021-01-10 01:00 | 1.2375 | 1.5059 | 1.4734 | 1.5847 | 1.5012 | 1.6126 | 0.88022 | 1.5094 | 1.8626 | 1.8626 | 2.098 | 2.098 | 2019-03-09 13:00 | 2.233 | 3.6594 | 6.007 | 6.007 | 6.007 | 6.007
2021-01-10 02:00 | 1.2232 | 1.4885 | 1.4564 | 1.5664 | 1.4839 | 1.594 | 0.74019 | 1.2693 | 1.5662 | 1.5662 | 1.7642 | 1.7642 | 2019-03-09 14:00 | 2.2787 | 3.7343 | 6.13 | 6.13 | 6.13 | 6.13
2021-01-10 03:00 | 1.1917 | 1.4502 | 1.4189 | 1.5262 | 1.4457 | 1.553 | 0.75734 | 1.2987 | 1.6025 | 1.6025 | 1.8051 | 1.8051 | 2019-03-09 15:00 | 2.2711 | 3.7218 | 6.1095 | 6.1095 | 6.1095 | 6.1095
2021-01-10 04:00 | 1.1632 | 1.4154 | 1.3849 | 1.4896 | 1.4111 | 1.5158 | 0.70062 | 1.2015 | 1.4825 | 1.4825 | 1.6699 | 1.6699 | 2019-03-09 16:00 | 2.2939 | 3.7593 | 6.171 | 6.171 | 6.171 | 6.171
2021-01-10 05:00 | 1.1959 | 1.4553 | 1.4239 | 1.5315 | 1.4508 | 1.5584 | 0.7459 | 1.2791 | 1.5783 | 1.5783 | 1.7778 | 1.7778 | 2019-03-09 17:00 | 2.2787 | 3.7343 | 6.13 | 6.13 | 6.13 | 6.13
2021-01-10 06:00 | 1.2142 | 1.4775 | 1.4457 | 1.5549 | 1.473 | 1.5823 | 0.7773 | 1.333 | 1.6448 | 1.6448 | 1.8527 | 1.8527 | 2019-03-09 18:00 | 2.0958 | 3.4346 | 5.6379 | 5.6379 | 5.6379 | 5.6379
2021-01-10 07:00 | 1.2689 | 1.5441 | 1.5108 | 1.625 | 1.5394 | 1.6536 | 0.90309 | 1.5487 | 1.9109 | 1.9109 | 2.1525 | 2.1525 | 2019-03-09 19:00 | 2.0043 | 3.2847 | 5.3919 | 5.3919 | 5.3919 | 5.3919
2021-01-10 08:00 | 1.3096 | 1.5936 | 1.5592 | 1.6771 | 1.5887 | 1.7066 | 1.1832 | 2.0289 | 2.5036 | 2.5036 | 2.82 | 2.82 | 2019-03-09 20:00 | 1.9357 | 3.1723 | 5.2074 | 5.2074 | 5.2074 | 5.2074
2021-01-10 09:00 | 1.3461 | 1.638 | 1.6027 | 1.7238 | 1.633 | 1.7541 | 1.3375 | 2.2936 | 2.8301 | 2.8301 | 3.1878 | 3.1878 | 2019-03-09 21:00 | 1.8367 | 3.0099 | 4.9409 | 4.9409 | 4.9409 | 4.9409
2021-01-10 10:00 | 1.3775 | 1.6763 | 1.6401 | 1.7641 | 1.6711 | 1.7951 | 1.4375 | 2.4651 | 3.0418 | 3.0418 | 3.4262 | 3.4262 | 2019-03-09 22:00 | 1.7452 | 2.8601 | 4.6949 | 4.6949 | 4.6949 | 4.6949
2021-01-10 11:00 | 1.3549 | 1.6487 | 1.6132 | 1.7351 | 1.6437 | 1.7656 | 1.4832 | 2.5435 | 3.1385 | 3.1385 | 3.5352 | 3.5352 | 2019-03-09 23:00 | 1.6233 | 2.6602 | 4.3668 | 4.3668 | 4.3668 | 4.3668
2021-01-10 12:00 | 1.3861 | 1.6867 | 1.6503 | 1.7751 | 1.6815 | 1.8063 | 1.5061 | 2.5827 | 3.1869 | 3.1869 | 3.5897 | 3.5897 | 2019-03-10 | 1.5928 | 2.6103 | 4.2848 | 4.2848 | 4.2848 | 4.2848
2021-01-10 13:00 | 1.3661 | 1.6624 | 1.6265 | 1.7494 | 1.6572 | 1.7802 | 1.549 | 2.6562 | 3.2776 | 3.2776 | 3.6919 | 3.6919 | 2019-03-10 01:00 | 1.5394 | 2.5229 | 4.1413 | 4.1413 | 4.1413 | 4.1413
2021-01-10 14:00 | 1.4661 | 1.7841 | 1.7456 | 1.8775 | 1.7786 | 1.9105 | 1.5833 | 2.715 | 3.3502 | 3.3502 | 3.7736 | 3.7736 | 2019-03-10 02:00 | 1.5318 | 2.5104 | 4.1208 | 4.1208 | 4.1208 | 4.1208
2021-01-10 15:00 | 1.5833 | 1.9267 | 1.8851 | 2.0276 | 1.9207 | 2.0632 | 1.549 | 2.6562 | 3.2776 | 3.2776 | 3.6919 | 3.6919 | 2019-03-10 03:00 | 1.5242 | 2.4979 | 4.1003 | 4.1003 | 4.1003 | 4.1003
2021-01-10 16:00 | 1.6747 | 2.038 | 1.994 | 2.1447 | 2.0317 | 2.1824 | 1.6031 | 2.7491 | 3.3922 | 3.3922 | 3.8209 | 3.8209 | 2019-03-10 04:00 | 1.5699 | 2.5728 | 4.2233 | 4.2233 | 4.2233 | 4.2233
2021-01-10 17:00 | 1.8319 | 2.2292 | 2.1811 | 2.346 | 2.2224 | 2.3872 | 1.6719 | 2.867 | 3.5377 | 3.5377 | 3.9848 | 3.9848 | 2019-03-10 05:00 | 1.5852 | 2.5978 | 4.2643 | 4.2643 | 4.2643 | 4.2643
2021-01-10 18:00 | 1.9319 | 2.351 | 2.3002 | 2.4741 | 2.3437 | 2.5176 | 1.7033 | 2.9209 | 3.6042 | 3.6042 | 4.0597 | 4.0597 | 2019-03-10 06:00 | 1.6842 | 2.7602 | 4.5308 | 4.5308 | 4.5308 | 4.5308
2021-01-10 19:00 | 1.9176 | 2.3336 | 2.2832 | 2.4558 | 2.3264 | 2.499 | 1.6519 | 2.8327 | 3.4953 | 3.4953 | 3.9371 | 3.9371 | 2019-03-10 07:00 | 1.7681 | 2.8975 | 4.7564 | 4.7564 | 4.7564 | 4.7564
2021-01-10 20:00 | 1.8433 | 2.2431 | 2.1948 | 2.3607 | 2.2362 | 2.4021 | 1.5718 | 2.6954 | 3.326 | 3.326 | 3.7464 | 3.7464 | 2019-03-10 08:00 | 2.0196 | 3.3097 | 5.4329 | 5.4329 | 5.4329 | 5.4329
2021-01-10 21:00 | 1.7523 | 2.1323 | 2.0863 | 2.244 | 2.1257 | 2.2834 | 1.5747 | 2.7003 | 3.3321 | 3.3321 | 3.7532 | 3.7532 | 2019-03-10 09:00 | 2.1186 | 3.4721 | 5.6994 | 5.6994 | 5.6994 | 5.6994
2021-01-10 22:00 | 1.6389 | 1.9944 | 1.9513 | 2.0988 | 1.9882 | 2.1357 | 1.4089 | 2.4161 | 2.9813 | 2.9813 | 3.3581 | 3.3581 | 2019-03-10 10:00 | 2.1491 | 3.522 | 5.7814 | 5.7814 | 5.7814 | 5.7814
2021-01-10 23:00 | 1.469 | 1.7877 | 1.7491 | 1.8813 | 1.7822 | 1.9144 | 1.1209 | 1.9222 | 2.3718 | 2.3718 | 2.6716 | 2.6716 | 2019-03-10 11:00 | 2.332 | 3.8218 | 6.2735 | 6.2735 | 6.2735 | 6.2735
2021-01-11 | 1.4319 | 1.7424 | 1.7048 | 1.8337 | 1.737 | 1.8659 | 0.97739 | 1.6761 | 2.0682 | 2.0682 | 2.3296 | 2.3296 | 2019-03-10 12:00 | 2.3244 | 3.8093 | 6.253 | 6.253 | 6.253 | 6.253
2021-01-11 01:00 | 1.2746 | 1.5511 | 1.5176 | 1.6323 | 1.5463 | 1.661 | 0.84879 | 1.4555 | 1.796 | 1.796 | 2.0231 | 2.0231 | 2019-03-10 13:00 | 2.2482 | 3.6844 | 6.048 | 6.048 | 6.048 | 6.048
2021-01-11 02:00 | 1.1775 | 1.4329 | 1.402 | 1.508 | 1.4285 | 1.5345 | 0.77466 | 1.3284 | 1.6392 | 1.6392 | 1.8464 | 1.8464 | 2019-03-10 14:00 | 2.2406 | 3.6719 | 6.0275 | 6.0275 | 6.0275 | 6.0275
2021-01-11 03:00 | 1.1974 | 1.4571 | 1.4257 | 1.5335 | 1.4526 | 1.5604 | 0.74305 | 1.2742 | 1.5723 | 1.5723 | 1.771 | 1.771 | 2019-03-10 15:00 | 2.233 | 3.6594 | 6.007 | 6.007 | 6.007 | 6.007
2021-01-11 04:00 | 1.1974 | 1.4572 | 1.4257 | 1.5335 | 1.4527 | 1.5605 | 0.74305 | 1.2742 | 1.5723 | 1.5723 | 1.771 | 1.771 | 2019-03-10 16:00 | 2.2253 | 3.6469 | 5.9865 | 5.9865 | 5.9865 | 5.9865
2021-01-11 05:00 | 1.2375 | 1.5059 | 1.4734 | 1.5847 | 1.5012 | 1.6126 | 0.80592 | 1.382 | 1.7053 | 1.7053 | 1.9209 | 1.9209 | 2019-03-10 17:00 | 2.1034 | 3.4471 | 5.6584 | 5.6584 | 5.6584 | 5.6584
2021-01-11 06:00 | 1.5461 | 1.8815 | 1.8409 | 1.98 | 1.8757 | 2.0148 | 0.9088 | 1.5585 | 1.923 | 1.923 | 2.1661 | 2.1661 | 2019-03-10 18:00 | 1.829 | 2.9975 | 4.9204 | 4.9204 | 4.9204 | 4.9204
2021-01-11 07:00 | 1.809 | 2.2014 | 2.1539 | 2.3167 | 2.1946 | 2.3574 | 1.2346 | 2.1171 | 2.6124 | 2.6124 | 2.9426 | 2.9426 | 2019-03-10 19:00 | 1.9129 | 3.1348 | 5.1459 | 5.1459 | 5.1459 | 5.1459
2021-01-11 08:00 | 2.0805 | 2.5318 | 2.4772 | 2.6644 | 2.524 | 2.7112 | 1.3318 | 2.2838 | 2.818 | 2.818 | 3.1742 | 3.1742 | 2019-03-10 20:00 | 1.8595 | 3.0474 | 5.0024 | 5.0024 | 5.0024 | 5.0024
2021-01-11 09:00 | 2.152 | 2.6187 | 2.5623 | 2.7559 | 2.6107 | 2.8043 | 1.3175 | 2.2593 | 2.7878 | 2.7878 | 3.1402 | 3.1402 | 2019-03-10 21:00 | 1.7833 | 2.9225 | 4.7974 | 4.7974 | 4.7974 | 4.7974
2021-01-11 10:00 | 2.2091 | 2.6883 | 2.6303 | 2.8291 | 2.68 | 2.8788 | 1.3946 | 2.3916 | 2.9511 | 2.9511 | 3.3241 | 3.3241 | 2019-03-10 22:00 | 1.6842 | 2.7602 | 4.5308 | 4.5308 | 4.5308 | 4.5308
2021-01-11 11:00 | 2.1891 | 2.664 | 2.6065 | 2.8035 | 2.6557 | 2.8528 | 1.4575 | 2.4994 | 3.0841 | 3.0841 | 3.4739 | 3.4739 | 2019-03-10 23:00 | 1.6461 | 2.6977 | 4.4283 | 4.4283 | 4.4283 | 4.4283
2021-01-11 12:00 | 2.2692 | 2.7613 | 2.7018 | 2.906 | 2.7528 | 2.957 | 1.4432 | 2.4749 | 3.0539 | 3.0539 | 3.4399 | 3.4399 | 2019-03-11 | 1.5471 | 2.5353 | 4.1618 | 4.1618 | 4.1618 | 4.1618
2021-01-11 13:00 | 2.2206 | 2.7022 | 2.6439 | 2.8438 | 2.6939 | 2.8937 | 1.5204 | 2.6072 | 3.2172 | 3.2172 | 3.6238 | 3.6238 | 2019-03-11 01:00 | 1.5166 | 2.4854 | 4.0798 | 4.0798 | 4.0798 | 4.0798
2021-01-11 14:00 | 2.3549 | 2.8657 | 2.8038 | 3.0158 | 2.8568 | 3.0688 | 1.4832 | 2.5435 | 3.1385 | 3.1385 | 3.5352 | 3.5352 | 2019-03-11 02:00 | 1.4556 | 2.3855 | 3.9158 | 3.9158 | 3.9158 | 3.9158
2021-01-11 15:00 | 2.4635 | 2.9978 | 2.9331 | 3.1549 | 2.9886 | 3.2103 | 1.4947 | 2.5631 | 3.1627 | 3.1627 | 3.5625 | 3.5625 | 2019-03-11 03:00 | 1.4861 | 2.4354 | 3.9978 | 3.9978 | 3.9978 | 3.9978
2021-01-11 16:00 | 2.5378 | 3.0882 | 3.0216 | 3.25 | 3.0787 | 3.3071 | 1.5872 | 2.7219 | 3.3586 | 3.3586 | 3.7831 | 3.7831 | 2019-03-11 04:00 | 1.6385 | 2.6852 | 4.4078 | 4.4078 | 4.4078 | 4.4078
2021-01-11 17:00 | 2.7979 | 3.4047 | 3.3313 | 3.5831 | 3.3942 | 3.646 | 1.729 | 2.965 | 3.6586 | 3.6586 | 4.121 | 4.121 | 2019-03-11 05:00 | 1.6461 | 2.6977 | 4.4283 | 4.4283 | 4.4283 | 4.4283
2021-01-11 18:00 | 2.8693 | 3.4917 | 3.4163 | 3.6746 | 3.4809 | 3.7391 | 1.8062 | 3.0973 | 3.8219 | 3.8219 | 4.305 | 4.305 | 2019-03-11 06:00 | 1.8138 | 2.9725 | 4.8794 | 4.8794 | 4.8794 | 4.8794
2021-01-11 19:00 | 2.7564 | 3.3542 | 3.2819 | 3.5299 | 3.3439 | 3.592 | 1.7347 | 2.9748 | 3.6707 | 3.6707 | 4.1347 | 4.1347 | 2019-03-11 07:00 | 1.6309 | 2.6727 | 4.3873 | 4.3873 | 4.3873 | 4.3873
2021-01-11 20:00 | 2.2806 | 2.7752 | 2.7154 | 2.9206 | 2.7667 | 2.9719 | 1.6461 | 2.8229 | 3.4832 | 3.4832 | 3.9235 | 3.9235 | 2019-03-11 08:00 | 1.8595 | 3.0474 | 5.0024 | 5.0024 | 5.0024 | 5.0024
2021-01-11 21:00 | 2.1842 | 2.6579 | 2.6006 | 2.7972 | 2.6497 | 2.8463 | 1.6461 | 2.8229 | 3.4832 | 3.4832 | 3.9235 | 3.9235 | 2019-03-11 09:00 | 1.9129 | 3.1348 | 5.1459 | 5.1459 | 5.1459 | 5.1459
2021-01-11 22:00 | 1.8633 | 2.2675 | 2.2186 | 2.3863 | 2.2605 | 2.4282 | 1.489 | 2.5533 | 3.1506 | 3.1506 | 3.5489 | 3.5489 | 2019-03-11 10:00 | 2.0958 | 3.4346 | 5.6379 | 5.6379 | 5.6379 | 5.6379
2021-01-11 23:00 | 1.6033 | 1.951 | 1.9089 | 2.0532 | 1.945 | 2.0893 | 1.1974 | 2.0534 | 2.5338 | 2.5338 | 2.8541 | 2.8541 | 2019-03-11 11:00 | 2.1186 | 3.4721 | 5.6994 | 5.6994 | 5.6994 | 5.6994
2021-01-12 | 1.4804 | 1.8015 | 1.7626 | 1.8958 | 1.7959 | 1.9292 | 1.006 | 1.7251 | 2.1286 | 2.1286 | 2.3977 | 2.3977 | 2019-03-11 12:00 | 2.172 | 3.5595 | 5.8429 | 5.8429 | 5.8429 | 5.8429
2021-01-12 01:00 | 1.2691 | 1.5443 | 1.511 | 1.6252 | 1.5396 | 1.6538 | 0.86879 | 1.4898 | 1.8384 | 1.8384 | 2.0707 | 2.0707 | 2019-03-11 13:00 | 2.2025 | 3.6094 | 5.9249 | 5.9249 | 5.9249 | 5.9249
2021-01-12 02:00 | 1.2575 | 1.5302 | 1.4972 | 1.6104 | 1.5255 | 1.6387 | 0.80592 | 1.382 | 1.7053 | 1.7053 | 1.9209 | 1.9209 | 2019-03-11 14:00 | 2.1949 | 3.597 | 5.9044 | 5.9044 | 5.9044 | 5.9044
2021-01-12 03:00 | 1.2403 | 1.5093 | 1.4768 | 1.5884 | 1.5047 | 1.6163 | 0.75162 | 1.2889 | 1.5904 | 1.5904 | 1.7915 | 1.7915 | 2019-03-11 15:00 | 2.172 | 3.5595 | 5.8429 | 5.8429 | 5.8429 | 5.8429
2021-01-12 04:00 | 1.2175 | 1.4815 | 1.4496 | 1.5591 | 1.477 | 1.5865 | 0.77446 | 1.3281 | 1.6388 | 1.6388 | 1.8459 | 1.8459 | 2019-03-11 16:00 | 2.1872 | 3.5845 | 5.8839 | 5.8839 | 5.8839 | 5.8839
2021-01-12 05:00 | 1.303 | 1.5857 | 1.5514 | 1.6687 | 1.5808 | 1.698 | 0.7802 | 1.3379 | 1.6509 | 1.6509 | 1.8596 | 1.8596 | 2019-03-11 17:00 | 2.1186 | 3.4721 | 5.6994 | 5.6994 | 5.6994 | 5.6994
2021-01-12 06:00 | 1.5032 | 1.8293 | 1.7898 | 1.9251 | 1.8237 | 1.9589 | 1.0507 | 1.8018 | 2.2233 | 2.2233 | 2.5043 | 2.5043 | 2019-03-11 18:00 | 1.9053 | 3.1224 | 5.1254 | 5.1254 | 5.1254 | 5.1254
2021-01-12 07:00 | 1.8262 | 2.2223 | 2.1743 | 2.3387 | 2.2154 | 2.3798 | 1.2175 | 2.0877 | 2.5761 | 2.5761 | 2.9018 | 2.9018 | 2019-03-11 19:00 | 1.8062 | 2.96 | 4.8589 | 4.8589 | 4.8589 | 4.8589
2021-01-12 08:00 | 2.1691 | 2.6396 | 2.5827 | 2.7779 | 2.6315 | 2.8267 | 1.3403 | 2.2985 | 2.8362 | 2.8362 | 3.1947 | 3.1947 | 2019-03-11 20:00 | 1.6919 | 2.7726 | 4.5513 | 4.5513 | 4.5513 | 4.5513
2021-01-12 09:00 | 2.2149 | 2.6953 | 2.6371 | 2.8364 | 2.6869 | 2.8863 | 1.2946 | 2.2201 | 2.7394 | 2.7394 | 3.0857 | 3.0857 | 2019-03-11 21:00 | 1.608 | 2.6353 | 4.3258 | 4.3258 | 4.3258 | 4.3258
2021-01-12 10:00 | 2.2692 | 2.7613 | 2.7018 | 2.906 | 2.7528 | 2.957 | 1.529 | 2.6219 | 3.2353 | 3.2353 | 3.6442 | 3.6442 | 2019-03-11 22:00 | 1.6233 | 2.6602 | 4.3668 | 4.3668 | 4.3668 | 4.3668
2021-01-12 11:00 | 2.3663 | 2.8796 | 2.8175 | 3.0304 | 2.8707 | 3.0837 | 1.5032 | 2.5778 | 3.1809 | 3.1809 | 3.5829 | 3.5829 | 2019-03-11 23:00 | 1.5013 | 2.4604 | 4.0388 | 4.0388 | 4.0388 | 4.0388
2021-01-12 12:00 | 2.6235 | 3.1926 | 3.1237 | 3.3598 | 3.1827 | 3.4188 | 1.5718 | 2.6954 | 3.326 | 3.326 | 3.7464 | 3.7464 | 2019-03-12 | 1.4556 | 2.3855 | 3.9158 | 3.9158 | 3.9158 | 3.9158
2021-01-12 13:00 | 2.7236 | 3.3143 | 3.2428 | 3.4879 | 3.3041 | 3.5492 | 1.6347 | 2.8033 | 3.4591 | 3.4591 | 3.8963 | 3.8963 | 2019-03-12 01:00 | 1.4861 | 2.4354 | 3.9978 | 3.9978 | 3.9978 | 3.9978
2021-01-12 14:00 | 2.8179 | 3.4291 | 3.3551 | 3.6087 | 3.4185 | 3.6721 | 1.6833 | 2.8866 | 3.5619 | 3.5619 | 4.0121 | 4.0121 | 2019-03-12 02:00 | 1.4404 | 2.3605 | 3.8748 | 3.8748 | 3.8748 | 3.8748
2021-01-12 15:00 | 2.9722 | 3.6169 | 3.5388 | 3.8063 | 3.6057 | 3.8732 | 1.6347 | 2.8033 | 3.4591 | 3.4591 | 3.8963 | 3.8963 | 2019-03-12 03:00 | 1.3946 | 2.2856 | 3.7518 | 3.7518 | 3.7518 | 3.7518
2021-01-12 16:00 | 2.8522 | 3.4708 | 3.3959 | 3.6526 | 3.4601 | 3.7168 | 1.6261 | 2.7886 | 3.4409 | 3.4409 | 3.8758 | 3.8758 | 2019-03-12 04:00 | 1.4099 | 2.3105 | 3.7928 | 3.7928 | 3.7928 | 3.7928
2021-01-12 17:00 | 2.7036 | 3.2899 | 3.219 | 3.4623 | 3.2798 | 3.5231 | 1.7547 | 3.0091 | 3.713 | 3.713 | 4.1823 | 4.1823 | 2019-03-12 05:00 | 1.5699 | 2.5728 | 4.2233 | 4.2233 | 4.2233 | 4.2233
2021-01-12 18:00 | 2.8207 | 3.4325 | 3.3585 | 3.6124 | 3.422 | 3.6758 | 1.6261 | 2.7886 | 3.4409 | 3.4409 | 3.8758 | 3.8758 | 2019-03-12 06:00 | 1.8824 | 3.0849 | 5.0639 | 5.0639 | 5.0639 | 5.0639
2021-01-12 19:00 | 2.7571 | 3.3551 | 3.2827 | 3.5309 | 3.3448 | 3.5929 | 1.6661 | 2.8572 | 3.5256 | 3.5256 | 3.9712 | 3.9712 | 2019-03-12 07:00 | 1.8519 | 3.0349 | 4.9819 | 4.9819 | 4.9819 | 4.9819
2021-01-12 20:00 | 2.292 | 2.7892 | 2.729 | 2.9353 | 2.7806 | 2.9868 | 1.6576 | 2.8425 | 3.5074 | 3.5074 | 3.9507 | 3.9507 | 2019-03-12 08:00 | 2.111 | 3.4596 | 5.6789 | 5.6789 | 5.6789 | 5.6789
2021-01-12 21:00 | 2.2034 | 2.6813 | 2.6235 | 2.8218 | 2.6731 | 2.8714 | 1.6061 | 2.7543 | 3.3986 | 3.3986 | 3.8281 | 3.8281 | 2019-03-12 09:00 | 2.233 | 3.6594 | 6.007 | 6.007 | 6.007 | 6.007
2021-01-12 22:00 | 1.9548 | 2.3788 | 2.3275 | 2.5034 | 2.3714 | 2.5474 | 1.3918 | 2.3867 | 2.945 | 2.945 | 3.3173 | 3.3173 | 2019-03-12 10:00 | 2.1949 | 3.597 | 5.9044 | 5.9044 | 5.9044 | 5.9044
2021-01-12 23:00 | 1.5833 | 1.9267 | 1.8851 | 2.0276 | 1.9207 | 2.0632 | 1.206 | 2.0681 | 2.552 | 2.552 | 2.8745 | 2.8745 | 2019-03-12 11:00 | 2.2253 | 3.6469 | 5.9865 | 5.9865 | 5.9865 | 5.9865
2021-01-13 | 1.5147 | 1.8432 | 1.8034 | 1.9398 | 1.8375 | 1.9738 | 1.0603 | 1.8182 | 2.2435 | 2.2435 | 2.5271 | 2.5271 | 2019-03-12 12:00 | 2.2787 | 3.7343 | 6.13 | 6.13 | 6.13 | 6.13
2021-01-13 01:00 | 1.3575 | 1.6519 | 1.6163 | 1.7385 | 1.6468 | 1.769 | 0.89166 | 1.529 | 1.8868 | 1.8868 | 2.1252 | 2.1252 | 2019-03-12 13:00 | 2.2863 | 3.7468 | 6.1505 | 6.1505 | 6.1505 | 6.1505
2021-01-13 02:00 | 1.2375 | 1.5059 | 1.4734 | 1.5847 | 1.5012 | 1.6126 | 0.80592 | 1.382 | 1.7053 | 1.7053 | 1.9209 | 1.9209 | 2019-03-12 14:00 | 2.2482 | 3.6844 | 6.048 | 6.048 | 6.048 | 6.048
2021-01-13 03:00 | 1.2575 | 1.5302 | 1.4972 | 1.6104 | 1.5255 | 1.6387 | 0.8345 | 1.431 | 1.7658 | 1.7658 | 1.989 | 1.989 | 2019-03-12 15:00 | 2.2177 | 3.6344 | 5.966 | 5.966 | 5.966 | 5.966
2021-01-13 04:00 | 1.226 | 1.4919 | 1.4597 | 1.5701 | 1.4873 | 1.5977 | 0.82602 | 1.4165 | 1.7479 | 1.7479 | 1.9688 | 1.9688 | 2019-03-12 16:00 | 2.2025 | 3.6094 | 5.9249 | 5.9249 | 5.9249 | 5.9249
2021-01-13 05:00 | 1.3859 | 1.6865 | 1.6501 | 1.7748 | 1.6813 | 1.806 | 0.82307 | 1.4114 | 1.7416 | 1.7416 | 1.9617 | 1.9617 | 2019-03-12 17:00 | 2.2177 | 3.6344 | 5.966 | 5.966 | 5.966 | 5.966
2021-01-13 06:00 | 1.5804 | 1.9232 | 1.8817 | 2.0239 | 1.9173 | 2.0595 | 1.1317 | 1.9407 | 2.3947 | 2.3947 | 2.6974 | 2.6974 | 2019-03-12 18:00 | 2.0805 | 3.4096 | 5.5969 | 5.5969 | 5.5969 | 5.5969
2021-01-13 07:00 | 2.0148 | 2.4518 | 2.3989 | 2.5803 | 2.4443 | 2.6256 | 1.2489 | 2.1416 | 2.6427 | 2.6427 | 2.9767 | 2.9767 | 2019-03-12 19:00 | 2.0958 | 3.4346 | 5.6379 | 5.6379 | 5.6379 | 5.6379
2021-01-13 08:00 | 2.292 | 2.7892 | 2.729 | 2.9353 | 2.7806 | 2.9868 | 1.3118 | 2.2495 | 2.7757 | 2.7757 | 3.1265 | 3.1265 | 2019-03-12 20:00 | 1.9586 | 3.2098 | 5.2689 | 5.2689 | 5.2689 | 5.2689
2021-01-13 09:00 | 2.3578 | 2.8691 | 2.8072 | 3.0194 | 2.8603 | 3.0725 | 1.3546 | 2.323 | 2.8664 | 2.8664 | 3.2287 | 3.2287 | 2019-03-12 21:00 | 1.7605 | 2.8851 | 4.7359 | 4.7359 | 4.7359 | 4.7359
2021-01-13 10:00 | 2.5206 | 3.0674 | 3.0012 | 3.2281 | 3.0579 | 3.2848 | 1.5433 | 2.6464 | 3.2655 | 3.2655 | 3.6783 | 3.6783 | 2019-03-12 22:00 | 1.6766 | 2.7477 | 4.5103 | 4.5103 | 4.5103 | 4.5103
2021-01-13 11:00 | 2.5235 | 3.0708 | 3.0046 | 3.2317 | 3.0614 | 3.2885 | 1.6061 | 2.7543 | 3.3986 | 3.3986 | 3.8281 | 3.8281 | 2019-03-12 23:00 | 1.6157 | 2.6478 | 4.3463 | 4.3463 | 4.3463 | 4.3463
2021-01-13 12:00 | 2.6693 | 3.2482 | 3.1781 | 3.4184 | 3.2382 | 3.4784 | 1.6176 | 2.7739 | 3.4228 | 3.4228 | 3.8554 | 3.8554 | 2019-03-13 | 1.509 | 2.4729 | 4.0593 | 4.0593 | 4.0593 | 4.0593
2021-01-13 13:00 | 2.7207 | 3.3108 | 3.2394 | 3.4843 | 3.3006 | 3.5455 | 1.6118 | 2.7641 | 3.4107 | 3.4107 | 3.8418 | 3.8418 | 2019-03-13 01:00 | 1.4709 | 2.4105 | 3.9568 | 3.9568 | 3.9568 | 3.9568
2021-01-13 14:00 | 2.9751 | 3.6203 | 3.5422 | 3.81 | 3.6092 | 3.8769 | 1.6404 | 2.8131 | 3.4712 | 3.4712 | 3.9099 | 3.9099 | 2019-03-13 02:00 | 1.4251 | 2.3355 | 3.8338 | 3.8338 | 3.8338 | 3.8338
2021-01-13 15:00 | 3.1179 | 3.7942 | 3.7124 | 3.993 | 3.7825 | 4.0631 | 1.6233 | 2.7837 | 3.4349 | 3.4349 | 3.869 | 3.869 | 2019-03-13 03:00 | 1.4251 | 2.3355 | 3.8338 | 3.8338 | 3.8338 | 3.8338
2021-01-13 16:00 | 3.198 | 3.8916 | 3.8077 | 4.0955 | 3.8796 | 4.1674 | 1.6575 | 2.8423 | 3.5073 | 3.5073 | 3.9506 | 3.9506 | 2019-03-13 04:00 | 1.4709 | 2.4105 | 3.9568 | 3.9568 | 3.9568 | 3.9568
2021-01-13 17:00 | 3.1408 | 3.822 | 3.7396 | 4.0223 | 3.8103 | 4.0929 | 1.8262 | 3.1316 | 3.8642 | 3.8642 | 4.3526 | 4.3526 | 2019-03-13 05:00 | 1.6385 | 2.6852 | 4.4078 | 4.4078 | 4.4078 | 4.4078
2021-01-13 18:00 | 3.2237 | 3.9229 | 3.8383 | 4.1284 | 3.9108 | 4.2009 | 1.9919 | 3.4159 | 4.215 | 4.215 | 4.7477 | 4.7477 | 2019-03-13 06:00 | 1.7071 | 2.7976 | 4.5923 | 4.5923 | 4.5923 | 4.5923
2021-01-13 19:00 | 2.9065 | 3.5369 | 3.4606 | 3.7222 | 3.526 | 3.7875 | 1.9005 | 3.259 | 4.0215 | 4.0215 | 4.5297 | 4.5297 | 2019-03-13 07:00 | 1.8214 | 2.985 | 4.8999 | 4.8999 | 4.8999 | 4.8999
2021-01-13 20:00 | 2.4121 | 2.9352 | 2.8719 | 3.089 | 2.9262 | 3.1433 | 1.7662 | 3.0287 | 3.7372 | 3.7372 | 4.2096 | 4.2096 | 2019-03-13 08:00 | 2.0272 | 3.3222 | 5.4534 | 5.4534 | 5.4534 | 5.4534
2021-01-13 21:00 | 2.192 | 2.6674 | 2.6099 | 2.8072 | 2.6592 | 2.8565 | 1.6833 | 2.8866 | 3.5619 | 3.5619 | 4.0121 | 4.0121 | 2019-03-13 09:00 | 2.1034 | 3.4471 | 5.6584 | 5.6584 | 5.6584 | 5.6584
2021-01-13 22:00 | 1.9979 | 2.4313 | 2.3788 | 2.5586 | 2.4238 | 2.6036 | 1.5718 | 2.6954 | 3.326 | 3.326 | 3.7464 | 3.7464 | 2019-03-13 10:00 | 2.0501 | 3.3597 | 5.5149 | 5.5149 | 5.5149 | 5.5149
2021-01-13 23:00 | 1.7033 | 2.0727 | 2.028 | 2.1813 | 2.0663 | 2.2196 | 1.2609 | 2.1622 | 2.668 | 2.668 | 3.0052 | 3.0052 | 2019-03-13 11:00 | 2.1491 | 3.522 | 5.7814 | 5.7814 | 5.7814 | 5.7814
2021-01-14 | 1.589 | 1.9336 | 1.8919 | 2.0349 | 1.9277 | 2.0707 | 1.0577 | 1.8138 | 2.2381 | 2.2381 | 2.521 | 2.521 | 2019-03-13 12:00 | 2.2177 | 3.6344 | 5.966 | 5.966 | 5.966 | 5.966
2021-01-14 01:00 | 1.4347 | 1.7458 | 1.7082 | 1.8373 | 1.7404 | 1.8696 | 0.9974 | 1.7104 | 2.1105 | 2.1105 | 2.3773 | 2.3773 | 2019-03-13 13:00 | 2.2482 | 3.6844 | 6.048 | 6.048 | 6.048 | 6.048
2021-01-14 02:00 | 1.3032 | 1.5858 | 1.5516 | 1.6689 | 1.581 | 1.6982 | 0.91738 | 1.5732 | 1.9412 | 1.9412 | 2.1865 | 2.1865 | 2019-03-13 14:00 | 2.2558 | 3.6969 | 6.0685 | 6.0685 | 6.0685 | 6.0685
2021-01-14 03:00 | 1.2746 | 1.5511 | 1.5176 | 1.6323 | 1.5463 | 1.661 | 0.80878 | 1.3869 | 1.7114 | 1.7114 | 1.9277 | 1.9277 | 2019-03-13 15:00 | 2.2177 | 3.6344 | 5.966 | 5.966 | 5.966 | 5.966
2021-01-14 04:00 | 1.2925 | 1.5729 | 1.5389 | 1.6553 | 1.568 | 1.6843 | 0.81735 | 1.4016 | 1.7295 | 1.7295 | 1.9481 | 1.9481 | 2019-03-13 16:00 | 2.1872 | 3.5845 | 5.8839 | 5.8839 | 5.8839 | 5.8839
2021-01-14 05:00 | 1.4409 | 1.7534 | 1.7156 | 1.8453 | 1.748 | 1.8777 | 0.85736 | 1.4702 | 1.8142 | 1.8142 | 2.0435 | 2.0435 | 2019-03-13 17:00 | 2.0805 | 3.4096 | 5.5969 | 5.5969 | 5.5969 | 5.5969
2021-01-14 06:00 | 1.7347 | 2.111 | 2.0655 | 2.2216 | 2.1045 | 2.2606 | 1.0403 | 1.7839 | 2.2012 | 2.2012 | 2.4794 | 2.4794 | 2019-03-13 18:00 | 1.9662 | 3.2223 | 5.2894 | 5.2894 | 5.2894 | 5.2894
2021-01-14 07:00 | 2.2034 | 2.6813 | 2.6235 | 2.8218 | 2.6731 | 2.8714 | 1.2432 | 2.1318 | 2.6306 | 2.6306 | 2.9631 | 2.9631 | 2019-03-13 19:00 | 1.9891 | 3.2597 | 5.3509 | 5.3509 | 5.3509 | 5.3509
2021-01-14 08:00 | 2.4978 | 3.0395 | 2.974 | 3.1988 | 3.0302 | 3.255 | 1.4804 | 2.5386 | 3.1325 | 3.1325 | 3.5284 | 3.5284 | 2019-03-13 20:00 | 1.9891 | 3.2597 | 5.3509 | 5.3509 | 5.3509 | 5.3509
2021-01-14 09:00 | 2.5693 | 3.1266 | 3.0591 | 3.2904 | 3.117 | 3.3482 | 1.5833 | 2.715 | 3.3502 | 3.3502 | 3.7736 | 3.7736 | 2019-03-13 21:00 | 1.8367 | 3.0099 | 4.9409 | 4.9409 | 4.9409 | 4.9409
2021-01-14 10:00 | 2.7264 | 3.3178 | 3.2462 | 3.4916 | 3.3075 | 3.5529 | 1.6261 | 2.7886 | 3.4409 | 3.4409 | 3.8758 | 3.8758 | 2019-03-13 22:00 | 1.73 | 2.8351 | 4.6538 | 4.6538 | 4.6538 | 4.6538
2021-01-14 11:00 | 2.7579 | 3.356 | 3.2836 | 3.5318 | 3.3457 | 3.5939 | 1.629 | 2.7935 | 3.447 | 3.447 | 3.8826 | 3.8826 | 2019-03-13 23:00 | 1.6538 | 2.7102 | 4.4488 | 4.4488 | 4.4488 | 4.4488
2021-01-14 12:00 | 2.7893 | 3.3943 | 3.3211 | 3.5721 | 3.3838 | 3.6349 | 1.6719 | 2.867 | 3.5377 | 3.5377 | 3.9848 | 3.9848 | 2019-03-14 | 1.5394 | 2.5229 | 4.1413 | 4.1413 | 4.1413 | 4.1413
2021-01-14 13:00 | 2.7521 | 3.3491 | 3.2768 | 3.5245 | 3.3387 | 3.5864 | 1.649 | 2.8278 | 3.4893 | 3.4893 | 3.9303 | 3.9303 | 2019-03-14 01:00 | 1.509 | 2.4729 | 4.0593 | 4.0593 | 4.0593 | 4.0593
2021-01-14 14:00 | 2.8807 | 3.5056 | 3.4299 | 3.6892 | 3.4948 | 3.754 | 1.6604 | 2.8474 | 3.5135 | 3.5135 | 3.9576 | 3.9576 | 2019-03-14 02:00 | 1.5852 | 2.5978 | 4.2643 | 4.2643 | 4.2643 | 4.2643
2021-01-14 15:00 | 2.8493 | 3.4673 | 3.3925 | 3.649 | 3.4566 | 3.7131 | 1.629 | 2.7935 | 3.447 | 3.447 | 3.8826 | 3.8826 | 2019-03-14 03:00 | 1.5013 | 2.4604 | 4.0388 | 4.0388 | 4.0388 | 4.0388
2021-01-14 16:00 | 2.7264 | 3.3178 | 3.2462 | 3.4916 | 3.3075 | 3.5529 | 1.6318 | 2.7984 | 3.453 | 3.453 | 3.8894 | 3.8894 | 2019-03-14 04:00 | 1.6004 | 2.6228 | 4.3053 | 4.3053 | 4.3053 | 4.3053
2021-01-14 17:00 | 2.8607 | 3.4812 | 3.4061 | 3.6636 | 3.4705 | 3.728 | 1.7262 | 2.9601 | 3.6526 | 3.6526 | 4.1142 | 4.1142 | 2019-03-14 05:00 | 1.7681 | 2.8975 | 4.7564 | 4.7564 | 4.7564 | 4.7564
2021-01-14 18:00 | 2.9379 | 3.5751 | 3.498 | 3.7624 | 3.5641 | 3.8285 | 1.8033 | 3.0924 | 3.8158 | 3.8158 | 4.2981 | 4.2981 | 2019-03-14 06:00 | 2.0119 | 3.2972 | 5.4124 | 5.4124 | 5.4124 | 5.4124
2021-01-14 19:00 | 2.8264 | 3.4395 | 3.3653 | 3.6197 | 3.4289 | 3.6833 | 1.809 | 3.1022 | 3.8279 | 3.8279 | 4.3118 | 4.3118 | 2019-03-14 07:00 | 2.0501 | 3.3597 | 5.5149 | 5.5149 | 5.5149 | 5.5149
2021-01-14 20:00 | 2.4149 | 2.9387 | 2.8753 | 3.0926 | 2.9296 | 3.147 | 1.7204 | 2.9503 | 3.6405 | 3.6405 | 4.1006 | 4.1006 | 2019-03-14 08:00 | 2.2711 | 3.7218 | 6.1095 | 6.1095 | 6.1095 | 6.1095
2021-01-14 21:00 | 2.2481 | 2.7357 | 2.6767 | 2.879 | 2.7273 | 2.9296 | 1.6461 | 2.8229 | 3.4832 | 3.4832 | 3.9235 | 3.9235 | 2019-03-14 09:00 | 2.2863 | 3.7468 | 6.1505 | 6.1505 | 6.1505 | 6.1505
2021-01-14 22:00 | 1.8033 | 2.1945 | 2.1471 | 2.3094 | 2.1877 | 2.35 | 1.4547 | 2.4945 | 3.0781 | 3.0781 | 3.4671 | 3.4671 | 2019-03-14 10:00 | 2.3854 | 3.9092 | 6.417 | 6.417 | 6.417 | 6.417
2021-01-14 23:00 | 1.6118 | 1.9614 | 1.9191 | 2.0642 | 1.9554 | 2.1005 | 1.2289 | 2.1073 | 2.6003 | 2.6003 | 2.929 | 2.929 | 2019-03-14 11:00 | 2.4387 | 3.9966 | 6.5605 | 6.5605 | 6.5605 | 6.5605
2021-01-15 | 1.4577 | 1.7738 | 1.7356 | 1.8668 | 1.7684 | 1.8996 | 1.0635 | 1.8236 | 2.2503 | 2.2503 | 2.5347 | 2.5347 | 2019-03-14 12:00 | 2.3778 | 3.8967 | 6.3965 | 6.3965 | 6.3965 | 6.3965
2021-01-15 01:00 | 1.3261 | 1.6138 | 1.5789 | 1.6983 | 1.6088 | 1.7281 | 0.88022 | 1.5094 | 1.8626 | 1.8626 | 2.098 | 2.098 | 2019-03-14 13:00 | 2.4463 | 4.0091 | 6.581 | 6.581 | 6.581 | 6.581
2021-01-15 02:00 | 1.2975 | 1.5789 | 1.5448 | 1.6616 | 1.574 | 1.6908 | 0.8345 | 1.431 | 1.7658 | 1.7658 | 1.989 | 1.989 | 2019-03-14 14:00 | 2.4311 | 3.9841 | 6.54 | 6.54 | 6.54 | 6.54
2021-01-15 03:00 | 1.2431 | 1.5127 | 1.4801 | 1.5919 | 1.508 | 1.6199 | 0.79103 | 1.3565 | 1.6738 | 1.6738 | 1.8854 | 1.8854 | 2019-03-14 15:00 | 2.4082 | 3.9467 | 6.4785 | 6.4785 | 6.4785 | 6.4785
2021-01-15 04:00 | 1.2432 | 1.5128 | 1.4802 | 1.5921 | 1.5082 | 1.62 | 0.81684 | 1.4007 | 1.7284 | 1.7284 | 1.9469 | 1.9469 | 2019-03-14 16:00 | 2.3168 | 3.7968 | 6.2325 | 6.2325 | 6.2325 | 6.2325
2021-01-15 05:00 | 1.4154 | 1.7224 | 1.6852 | 1.8126 | 1.7171 | 1.8445 | 0.83736 | 1.4359 | 1.7719 | 1.7719 | 1.9958 | 1.9958 | 2019-03-14 17:00 | 2.2177 | 3.6344 | 5.966 | 5.966 | 5.966 | 5.966
2021-01-15 06:00 | 1.5831 | 1.9265 | 1.885 | 2.0274 | 1.9206 | 2.0631 | 1.0203 | 1.7496 | 2.1589 | 2.1589 | 2.4317 | 2.4317 | 2019-03-14 18:00 | 2.0653 | 3.3846 | 5.5559 | 5.5559 | 5.5559 | 5.5559
2021-01-15 07:00 | 1.8805 | 2.2884 | 2.239 | 2.4082 | 2.2813 | 2.4505 | 1.3032 | 2.2348 | 2.7576 | 2.7576 | 3.1061 | 3.1061 | 2019-03-14 19:00 | 2.0424 | 3.3472 | 5.4944 | 5.4944 | 5.4944 | 5.4944
2021-01-15 08:00 | 2.1577 | 2.6257 | 2.5691 | 2.7632 | 2.6176 | 2.8118 | 1.3718 | 2.3524 | 2.9027 | 2.9027 | 3.2696 | 3.2696 | 2019-03-14 20:00 | 1.9205 | 3.1473 | 5.1664 | 5.1664 | 5.1664 | 5.1664
2021-01-15 09:00 | 2.2291 | 2.7126 | 2.6541 | 2.8547 | 2.7043 | 2.9049 | 1.3289 | 2.2789 | 2.812 | 2.812 | 3.1674 | 3.1674 | 2019-03-14 21:00 | 1.7681 | 2.8975 | 4.7564 | 4.7564 | 4.7564 | 4.7564
2021-01-15 10:00 | 2.3492 | 2.8587 | 2.797 | 3.0085 | 2.8499 | 3.0613 | 1.5461 | 2.6513 | 3.2716 | 3.2716 | 3.6851 | 3.6851 | 2019-03-14 22:00 | 1.6919 | 2.7726 | 4.5513 | 4.5513 | 4.5513 | 4.5513
2021-01-15 11:00 | 2.2606 | 2.7509 | 2.6916 | 2.895 | 2.7424 | 2.9459 | 1.609 | 2.7592 | 3.4046 | 3.4046 | 3.8349 | 3.8349 | 2019-03-14 23:00 | 1.6461 | 2.6977 | 4.4283 | 4.4283 | 4.4283 | 4.4283
2021-01-15 12:00 | 2.2263 | 2.7092 | 2.6507 | 2.8511 | 2.7008 | 2.9012 | 1.4718 | 2.5239 | 3.1144 | 3.1144 | 3.508 | 3.508 | 2019-03-15 | 1.5852 | 2.5978 | 4.2643 | 4.2643 | 4.2643 | 4.2643
2021-01-15 13:00 | 2.212 | 2.6918 | 2.6337 | 2.8328 | 2.6835 | 2.8826 | 1.5175 | 2.6023 | 3.2111 | 3.2111 | 3.617 | 3.617 | 2019-03-15 01:00 | 1.5699 | 2.5728 | 4.2233 | 4.2233 | 4.2233 | 4.2233
2021-01-15 14:00 | 2.2263 | 2.7092 | 2.6507 | 2.8511 | 2.7008 | 2.9012 | 1.529 | 2.6219 | 3.2353 | 3.2353 | 3.6442 | 3.6442 | 2019-03-15 02:00 | 1.5471 | 2.5353 | 4.1618 | 4.1618 | 4.1618 | 4.1618
2021-01-15 15:00 | 2.2206 | 2.7022 | 2.6439 | 2.8438 | 2.6939 | 2.8937 | 1.4518 | 2.4896 | 3.072 | 3.072 | 3.4603 | 3.4603 | 2019-03-15 03:00 | 1.4632 | 2.398 | 3.9363 | 3.9363 | 3.9363 | 3.9363
2021-01-15 16:00 | 2.2663 | 2.7579 | 2.6984 | 2.9023 | 2.7494 | 2.9533 | 1.4804 | 2.5386 | 3.1325 | 3.1325 | 3.5284 | 3.5284 | 2019-03-15 04:00 | 1.5775 | 2.5853 | 4.2438 | 4.2438 | 4.2438 | 4.2438
2021-01-15 17:00 | 2.3063 | 2.8065 | 2.746 | 2.9536 | 2.7979 | 3.0055 | 1.5976 | 2.7395 | 3.3804 | 3.3804 | 3.8077 | 3.8077 | 2019-03-15 05:00 | 1.6995 | 2.7851 | 4.5718 | 4.5718 | 4.5718 | 4.5718
2021-01-15 18:00 | 2.3263 | 2.8309 | 2.7698 | 2.9792 | 2.8222 | 3.0315 | 1.7062 | 2.9258 | 3.6102 | 3.6102 | 4.0665 | 4.0665 | 2019-03-15 06:00 | 1.8062 | 2.96 | 4.8589 | 4.8589 | 4.8589 | 4.8589
2021-01-15 19:00 | 2.3006 | 2.7996 | 2.7392 | 2.9462 | 2.791 | 2.998 | 1.6776 | 2.8768 | 3.5498 | 3.5498 | 3.9984 | 3.9984 | 2019-03-15 07:00 | 1.8214 | 2.985 | 4.8999 | 4.8999 | 4.8999 | 4.8999
2021-01-15 20:00 | 1.8292 | 2.226 | 2.178 | 2.3426 | 2.2191 | 2.3837 | 1.649 | 2.8278 | 3.4893 | 3.4893 | 3.9303 | 3.9303 | 2019-03-15 08:00 | 2.0882 | 3.4221 | 5.6174 | 5.6174 | 5.6174 | 5.6174
2021-01-15 21:00 | 1.7348 | 2.111 | 2.0655 | 2.2216 | 2.1045 | 2.2607 | 1.6176 | 2.7739 | 3.4228 | 3.4228 | 3.8554 | 3.8554 | 2019-03-15 09:00 | 2.1415 | 3.5095 | 5.7609 | 5.7609 | 5.7609 | 5.7609
2021-01-15 22:00 | 1.5861 | 1.9301 | 1.8885 | 2.0313 | 1.9242 | 2.0669 | 1.3946 | 2.3916 | 2.9511 | 2.9511 | 3.3241 | 3.3241 | 2019-03-15 10:00 | 2.0882 | 3.4221 | 5.6174 | 5.6174 | 5.6174 | 5.6174
2021-01-15 23:00 | 1.4226 | 1.7311 | 1.6938 | 1.8218 | 1.7258 | 1.8538 | 1.1089 | 1.9015 | 2.3464 | 2.3464 | 2.6429 | 2.6429 | 2019-03-15 11:00 | 2.1415 | 3.5095 | 5.7609 | 5.7609 | 5.7609 | 5.7609
2021-01-16 | 1.3833 | 1.6833 | 1.647 | 1.7715 | 1.6781 | 1.8026 | 0.96314 | 1.6516 | 2.038 | 2.038 | 2.2956 | 2.2956 | 2019-03-15 12:00 | 2.1872 | 3.5845 | 5.8839 | 5.8839 | 5.8839 | 5.8839
2021-01-16 01:00 | 1.2575 | 1.5302 | 1.4972 | 1.6104 | 1.5255 | 1.6387 | 0.85736 | 1.4702 | 1.8142 | 1.8142 | 2.0435 | 2.0435 | 2019-03-15 13:00 | 2.1872 | 3.5845 | 5.8839 | 5.8839 | 5.8839 | 5.8839
2021-01-16 02:00 | 1.1774 | 1.4328 | 1.4019 | 1.5079 | 1.4284 | 1.5344 | 0.79449 | 1.3624 | 1.6811 | 1.6811 | 1.8936 | 1.8936 | 2019-03-15 14:00 | 2.2177 | 3.6344 | 5.966 | 5.966 | 5.966 | 5.966
2021-01-16 03:00 | 1.1574 | 1.4084 | 1.3781 | 1.4822 | 1.4041 | 1.5083 | 0.79449 | 1.3624 | 1.6811 | 1.6811 | 1.8936 | 1.8936 | 2019-03-15 15:00 | 2.233 | 3.6594 | 6.007 | 6.007 | 6.007 | 6.007
2021-01-16 04:00 | 1.1574 | 1.4085 | 1.3781 | 1.4823 | 1.4041 | 1.5083 | 0.75445 | 1.2938 | 1.5964 | 1.5964 | 1.7982 | 1.7982 | 2019-03-15 16:00 | 2.2558 | 3.6969 | 6.0685 | 6.0685 | 6.0685 | 6.0685
2021-01-16 05:00 | 1.2403 | 1.5093 | 1.4768 | 1.5884 | 1.5047 | 1.6163 | 0.75448 | 1.2938 | 1.5965 | 1.5965 | 1.7983 | 1.7983 | 2019-03-15 17:00 | 2.1339 | 3.497 | 5.7404 | 5.7404 | 5.7404 | 5.7404
2021-01-16 06:00 | 1.2803 | 1.558 | 1.5244 | 1.6396 | 1.5532 | 1.6685 | 0.9974 | 1.7104 | 2.1105 | 2.1105 | 2.3773 | 2.3773 | 2019-03-15 18:00 | 1.9053 | 3.1224 | 5.1254 | 5.1254 | 5.1254 | 5.1254
2021-01-16 07:00 | 1.3518 | 1.645 | 1.6095 | 1.7311 | 1.6399 | 1.7616 | 1.0574 | 1.8133 | 2.2375 | 2.2375 | 2.5203 | 2.5203 | 2019-03-15 19:00 | 1.6538 | 2.7102 | 4.4488 | 4.4488 | 4.4488 | 4.4488
2021-01-16 08:00 | 1.4375 | 1.7493 | 1.7116 | 1.8409 | 1.7439 | 1.8733 | 1.2375 | 2.122 | 2.6185 | 2.6185 | 2.9494 | 2.9494 | 2019-03-15 20:00 | 1.5699 | 2.5728 | 4.2233 | 4.2233 | 4.2233 | 4.2233
2021-01-16 09:00 | 1.4547 | 1.7702 | 1.732 | 1.8629 | 1.7647 | 1.8956 | 1.3089 | 2.2446 | 2.7697 | 2.7697 | 3.1197 | 3.1197 | 2019-03-15 21:00 | 1.5699 | 2.5728 | 4.2233 | 4.2233 | 4.2233 | 4.2233
2021-01-16 10:00 | 1.4432 | 1.7563 | 1.7184 | 1.8483 | 1.7508 | 1.8807 | 1.5204 | 2.6072 | 3.2172 | 3.2172 | 3.6238 | 3.6238 | 2019-03-15 22:00 | 1.5852 | 2.5978 | 4.2643 | 4.2643 | 4.2643 | 4.2643
2021-01-16 11:00 | 1.3546 | 1.6484 | 1.6129 | 1.7348 | 1.6434 | 1.7653 | 1.509 | 2.5876 | 3.193 | 3.193 | 3.5965 | 3.5965 | 2019-03-15 23:00 | 1.4937 | 2.4479 | 4.0183 | 4.0183 | 4.0183 | 4.0183
2021-01-16 12:00 | 1.3261 | 1.6137 | 1.5789 | 1.6982 | 1.6087 | 1.728 | 1.5175 | 2.6023 | 3.2111 | 3.2111 | 3.617 | 3.617 | 2019-03-16 | 1.4632 | 2.398 | 3.9363 | 3.9363 | 3.9363 | 3.9363
2021-01-16 13:00 | 1.2975 | 1.5789 | 1.5448 | 1.6616 | 1.574 | 1.6908 | 1.529 | 2.6219 | 3.2353 | 3.2353 | 3.6442 | 3.6442 | 2019-03-16 01:00 | 1.4632 | 2.398 | 3.9363 | 3.9363 | 3.9363 | 3.9363
2021-01-16 14:00 | 1.2575 | 1.5302 | 1.4972 | 1.6104 | 1.5255 | 1.6387 | 1.4832 | 2.5435 | 3.1385 | 3.1385 | 3.5352 | 3.5352 | 2019-03-16 02:00 | 1.4251 | 2.3355 | 3.8338 | 3.8338 | 3.8338 | 3.8338
2021-01-16 15:00 | 1.2517 | 1.5232 | 1.4904 | 1.603 | 1.5186 | 1.6312 | 1.3403 | 2.2985 | 2.8362 | 2.8362 | 3.1947 | 3.1947 | 2019-03-16 03:00 | 1.387 | 2.2731 | 3.7313 | 3.7313 | 3.7313 | 3.7313
2021-01-16 16:00 | 1.2689 | 1.5441 | 1.5108 | 1.625 | 1.5394 | 1.6536 | 1.4375 | 2.4651 | 3.0418 | 3.0418 | 3.4262 | 3.4262 | 2019-03-16 04:00 | 1.4937 | 2.4479 | 4.0183 | 4.0183 | 4.0183 | 4.0183
2021-01-16 17:00 | 1.3661 | 1.6624 | 1.6265 | 1.7494 | 1.6572 | 1.7802 | 1.4461 | 2.4798 | 3.0599 | 3.0599 | 3.4467 | 3.4467 | 2019-03-16 05:00 | 1.5775 | 2.5853 | 4.2438 | 4.2438 | 4.2438 | 4.2438
2021-01-16 18:00 | 1.5147 | 1.8432 | 1.8034 | 1.9398 | 1.8375 | 1.9738 | 1.4289 | 2.4504 | 3.0236 | 3.0236 | 3.4058 | 3.4058 | 2019-03-16 06:00 | 1.6233 | 2.6602 | 4.3668 | 4.3668 | 4.3668 | 4.3668
2021-01-16 19:00 | 1.5775 | 1.9197 | 1.8783 | 2.0203 | 1.9138 | 2.0558 | 1.4461 | 2.4798 | 3.0599 | 3.0599 | 3.4467 | 3.4467 | 2019-03-16 07:00 | 1.8519 | 3.0349 | 4.9819 | 4.9819 | 4.9819 | 4.9819
2021-01-16 20:00 | 1.6004 | 1.9475 | 1.9055 | 2.0496 | 1.9415 | 2.0856 | 1.4375 | 2.4651 | 3.0418 | 3.0418 | 3.4262 | 3.4262 | 2019-03-16 08:00 | 2.0272 | 3.3222 | 5.4534 | 5.4534 | 5.4534 | 5.4534
2021-01-16 21:00 | 1.5547 | 1.8919 | 1.8511 | 1.991 | 1.8861 | 2.026 | 1.4089 | 2.4161 | 2.9813 | 2.9813 | 3.3581 | 3.3581 | 2019-03-16 09:00 | 2.0882 | 3.4221 | 5.6174 | 5.6174 | 5.6174 | 5.6174
2021-01-16 22:00 | 1.4689 | 1.7876 | 1.749 | 1.8812 | 1.7821 | 1.9143 | 1.2489 | 2.1416 | 2.6427 | 2.6427 | 2.9767 | 2.9767 | 2019-03-16 10:00 | 2.1339 | 3.497 | 5.7404 | 5.7404 | 5.7404 | 5.7404
2021-01-16 23:00 | 1.4375 | 1.7493 | 1.7116 | 1.8409 | 1.7439 | 1.8733 | 1.0574 | 1.8133 | 2.2375 | 2.2375 | 2.5203 | 2.5203 | 2019-03-16 11:00 | 2.2177 | 3.6344 | 5.966 | 5.966 | 5.966 | 5.966
2021-01-17 | 1.4204 | 1.7284 | 1.6912 | 1.819 | 1.7231 | 1.8509 | 0.94777 | 1.6253 | 2.0055 | 2.0055 | 2.259 | 2.259 | 2019-03-16 12:00 | 2.1644 | 3.547 | 5.8224 | 5.8224 | 5.8224 | 5.8224
2021-01-17 01:00 | 1.2946 | 1.5754 | 1.5414 | 1.6579 | 1.5706 | 1.6871 | 0.81485 | 1.3973 | 1.7242 | 1.7242 | 1.9422 | 1.9422 | 2019-03-16 13:00 | 2.111 | 3.4596 | 5.6789 | 5.6789 | 5.6789 | 5.6789
2021-01-17 02:00 | 1.1568 | 1.4077 | 1.3773 | 1.4815 | 1.4034 | 1.5075 | 0.78591 | 1.3477 | 1.663 | 1.663 | 1.8732 | 1.8732 | 2019-03-16 14:00 | 2.1186 | 3.4721 | 5.6994 | 5.6994 | 5.6994 | 5.6994
2021-01-17 03:00 | 1.1774 | 1.4328 | 1.4019 | 1.5079 | 1.4284 | 1.5344 | 0.7259 | 1.2448 | 1.536 | 1.536 | 1.7301 | 1.7301 | 2019-03-16 15:00 | 2.1491 | 3.522 | 5.7814 | 5.7814 | 5.7814 | 5.7814
2021-01-17 04:00 | 1.1317 | 1.3772 | 1.3475 | 1.4493 | 1.3729 | 1.4748 | 0.72098 | 1.2364 | 1.5256 | 1.5256 | 1.7184 | 1.7184 | 2019-03-16 16:00 | 2.1339 | 3.497 | 5.7404 | 5.7404 | 5.7404 | 5.7404
2021-01-17 05:00 | 1.1546 | 1.405 | 1.3747 | 1.4786 | 1.4007 | 1.5046 | 0.72018 | 1.235 | 1.5239 | 1.5239 | 1.7165 | 1.7165 | 2019-03-16 17:00 | 2.0272 | 3.3222 | 5.4534 | 5.4534 | 5.4534 | 5.4534
2021-01-17 06:00 | 1.1857 | 1.4429 | 1.4118 | 1.5185 | 1.4385 | 1.5452 | 0.76877 | 1.3183 | 1.6267 | 1.6267 | 1.8323 | 1.8323 | 2019-03-16 18:00 | 1.8138 | 2.9725 | 4.8794 | 4.8794 | 4.8794 | 4.8794
2021-01-17 07:00 | 1.3175 | 1.6032 | 1.5687 | 1.6872 | 1.5983 | 1.7169 | 0.93452 | 1.6026 | 1.9775 | 1.9775 | 2.2274 | 2.2274 | 2019-03-16 19:00 | 1.8519 | 3.0349 | 4.9819 | 4.9819 | 4.9819 | 4.9819
2021-01-17 08:00 | 1.306 | 1.5893 | 1.555 | 1.6726 | 1.5844 | 1.702 | 1.1374 | 1.9505 | 2.4068 | 2.4068 | 2.711 | 2.711 | 2019-03-16 20:00 | 1.7452 | 2.8601 | 4.6949 | 4.6949 | 4.6949 | 4.6949
2021-01-17 09:00 | 1.3346 | 1.6241 | 1.5891 | 1.7092 | 1.6191 | 1.7392 | 1.226 | 2.1024 | 2.5943 | 2.5943 | 2.9222 | 2.9222 | 2019-03-16 21:00 | 1.6842 | 2.7602 | 4.5308 | 4.5308 | 4.5308 | 4.5308
2021-01-17 10:00 | 1.2918 | 1.5719 | 1.538 | 1.6543 | 1.5671 | 1.6834 | 1.4661 | 2.5141 | 3.1023 | 3.1023 | 3.4944 | 3.4944 | 2019-03-16 22:00 | 1.6842 | 2.7602 | 4.5308 | 4.5308 | 4.5308 | 4.5308
2021-01-17 11:00 | 1.3232 | 1.6102 | 1.5755 | 1.6945 | 1.6052 | 1.7243 | 1.4404 | 2.47 | 3.0478 | 3.0478 | 3.4331 | 3.4331 | 2019-03-16 23:00 | 1.6614 | 2.7227 | 4.4693 | 4.4693 | 4.4693 | 4.4693
2021-01-17 12:00 | 1.2432 | 1.5128 | 1.4802 | 1.5921 | 1.5082 | 1.62 | 1.4975 | 2.568 | 3.1688 | 3.1688 | 3.5693 | 3.5693 | 2019-03-17 | 1.5775 | 2.5853 | 4.2438 | 4.2438 | 4.2438 | 4.2438
2021-01-17 13:00 | 1.1403 | 1.3876 | 1.3577 | 1.4603 | 1.3833 | 1.486 | 1.4375 | 2.4651 | 3.0418 | 3.0418 | 3.4262 | 3.4262 | 2019-03-17 01:00 | 1.5852 | 2.5978 | 4.2643 | 4.2643 | 4.2643 | 4.2643
2021-01-17 14:00 | 1.1803 | 1.4363 | 1.4053 | 1.5115 | 1.4319 | 1.5381 | 1.4375 | 2.4651 | 3.0418 | 3.0418 | 3.4262 | 3.4262 | 2019-03-17 02:00 | 1.4861 | 2.4354 | 3.9978 | 3.9978 | 3.9978 | 3.9978
2021-01-17 15:00 | 1.1803 | 1.4363 | 1.4053 | 1.5115 | 1.4319 | 1.5381 | 1.4375 | 2.4651 | 3.0418 | 3.0418 | 3.4262 | 3.4262 | 2019-03-17 03:00 | 1.5166 | 2.4854 | 4.0798 | 4.0798 | 4.0798 | 4.0798
2021-01-17 16:00 | 1.3375 | 1.6276 | 1.5925 | 1.7128 | 1.6226 | 1.7429 | 1.4347 | 2.4602 | 3.0357 | 3.0357 | 3.4194 | 3.4194 | 2019-03-17 04:00 | 1.5166 | 2.4854 | 4.0798 | 4.0798 | 4.0798 | 4.0798
2021-01-17 17:00 | 1.589 | 1.9336 | 1.8919 | 2.0349 | 1.9277 | 2.0707 | 1.5347 | 2.6317 | 3.2474 | 3.2474 | 3.6578 | 3.6578 | 2019-03-17 05:00 | 1.6233 | 2.6602 | 4.3668 | 4.3668 | 4.3668 | 4.3668
2021-01-17 18:00 | 1.7404 | 2.1179 | 2.0723 | 2.2289 | 2.1114 | 2.2681 | 1.5747 | 2.7003 | 3.3321 | 3.3321 | 3.7532 | 3.7532 | 2019-03-17 06:00 | 1.6919 | 2.7726 | 4.5513 | 4.5513 | 4.5513 | 4.5513
2021-01-17 19:00 | 1.7233 | 2.0971 | 2.0518 | 2.2069 | 2.0906 | 2.2457 | 1.6033 | 2.7494 | 3.3925 | 3.3925 | 3.8213 | 3.8213 | 2019-03-17 07:00 | 1.7605 | 2.8851 | 4.7359 | 4.7359 | 4.7359 | 4.7359
2021-01-17 20:00 | 1.7404 | 2.1179 | 2.0723 | 2.2289 | 2.1114 | 2.2681 | 1.5315 | 2.6263 | 3.2407 | 3.2407 | 3.6503 | 3.6503 | 2019-03-17 08:00 | 2.0424 | 3.3472 | 5.4944 | 5.4944 | 5.4944 | 5.4944
2021-01-17 21:00 | 1.669 | 2.031 | 1.9872 | 2.1374 | 2.0247 | 2.175 | 1.5318 | 2.6268 | 3.2414 | 3.2414 | 3.651 | 3.651 | 2019-03-17 09:00 | 2.0501 | 3.3597 | 5.5149 | 5.5149 | 5.5149 | 5.5149
2021-01-17 22:00 | 1.5633 | 1.9024 | 1.8613 | 2.002 | 1.8965 | 2.0372 | 1.2576 | 2.1566 | 2.6611 | 2.6611 | 2.9974 | 2.9974 | 2019-03-17 10:00 | 2.1415 | 3.5095 | 5.7609 | 5.7609 | 5.7609 | 5.7609
2021-01-17 23:00 | 1.4432 | 1.7563 | 1.7184 | 1.8483 | 1.7508 | 1.8807 | 1.1574 | 1.9848 | 2.4492 | 2.4492 | 2.7587 | 2.7587 | 2019-03-17 11:00 | 2.111 | 3.4596 | 5.6789 | 5.6789 | 5.6789 | 5.6789
2021-01-18 | 1.4061 | 1.711 | 1.6741 | 1.8007 | 1.7058 | 1.8323 | 0.96888 | 1.6615 | 2.0502 | 2.0502 | 2.3093 | 2.3093 | 2019-03-17 12:00 | 2.0882 | 3.4221 | 5.6174 | 5.6174 | 5.6174 | 5.6174
2021-01-18 01:00 | 1.2489 | 1.5198 | 1.487 | 1.5994 | 1.5151 | 1.6275 | 0.80887 | 1.3871 | 1.7116 | 1.7116 | 1.9279 | 1.9279 | 2019-03-17 13:00 | 2.1186 | 3.4721 | 5.6994 | 5.6994 | 5.6994 | 5.6994
2021-01-18 02:00 | 1.2289 | 1.4954 | 1.4632 | 1.5738 | 1.4908 | 1.6014 | 0.77162 | 1.3232 | 1.6328 | 1.6328 | 1.8391 | 1.8391 | 2019-03-17 14:00 | 2.1186 | 3.4721 | 5.6994 | 5.6994 | 5.6994 | 5.6994
2021-01-18 03:00 | 1.2089 | 1.4711 | 1.4394 | 1.5481 | 1.4666 | 1.5753 | 0.72876 | 1.2497 | 1.5421 | 1.5421 | 1.737 | 1.737 | 2019-03-17 15:00 | 2.0805 | 3.4096 | 5.5969 | 5.5969 | 5.5969 | 5.5969
2021-01-18 04:00 | 1.1946 | 1.4537 | 1.4223 | 1.5298 | 1.4492 | 1.5567 | 0.75162 | 1.2889 | 1.5904 | 1.5904 | 1.7915 | 1.7915 | 2019-03-17 16:00 | 2.0805 | 3.4096 | 5.5969 | 5.5969 | 5.5969 | 5.5969
2021-01-18 05:00 | 1.263 | 1.537 | 1.5038 | 1.6175 | 1.5322 | 1.6459 | 0.76305 | 1.3085 | 1.6146 | 1.6146 | 1.8187 | 1.8187 | 2019-03-17 17:00 | 2.1034 | 3.4471 | 5.6584 | 5.6584 | 5.6584 | 5.6584
2021-01-18 06:00 | 1.5947 | 1.9406 | 1.8987 | 2.0422 | 1.9346 | 2.0781 | 0.92023 | 1.5781 | 1.9472 | 1.9472 | 2.1933 | 2.1933 | 2019-03-17 18:00 | 1.8214 | 2.985 | 4.8999 | 4.8999 | 4.8999 | 4.8999
2021-01-18 07:00 | 1.7176 | 2.0901 | 2.045 | 2.1996 | 2.0837 | 2.2383 | 1.2089 | 2.073 | 2.558 | 2.558 | 2.8813 | 2.8813 | 2019-03-17 19:00 | 1.7376 | 2.8476 | 4.6744 | 4.6744 | 4.6744 | 4.6744
2021-01-18 08:00 | 2.0148 | 2.4518 | 2.3989 | 2.5803 | 2.4443 | 2.6256 | 1.2517 | 2.1466 | 2.6487 | 2.6487 | 2.9835 | 2.9835 | 2019-03-17 20:00 | 1.7376 | 2.8476 | 4.6744 | 4.6744 | 4.6744 | 4.6744
2021-01-18 09:00 | 2.0205 | 2.4588 | 2.4057 | 2.5876 | 2.4512 | 2.633 | 1.3032 | 2.2348 | 2.7576 | 2.7576 | 3.1061 | 3.1061 | 2019-03-17 21:00 | 1.6766 | 2.7477 | 4.5103 | 4.5103 | 4.5103 | 4.5103
2021-01-18 10:00 | 2.1348 | 2.5979 | 2.5418 | 2.734 | 2.5899 | 2.782 | 1.3918 | 2.3867 | 2.945 | 2.945 | 3.3173 | 3.3173 | 2019-03-17 22:00 | 1.5699 | 2.5728 | 4.2233 | 4.2233 | 4.2233 | 4.2233
2021-01-18 11:00 | 2.1034 | 2.5596 | 2.5044 | 2.6937 | 2.5517 | 2.741 | 1.3804 | 2.3671 | 2.9208 | 2.9208 | 3.29 | 3.29 | 2019-03-17 23:00 | 1.5394 | 2.5229 | 4.1413 | 4.1413 | 4.1413 | 4.1413
2021-01-18 12:00 | 2.0977 | 2.5527 | 2.4976 | 2.6864 | 2.5448 | 2.7336 | 1.3775 | 2.3622 | 2.9148 | 2.9148 | 3.2832 | 3.2832 | 2019-03-18 | 1.4632 | 2.398 | 3.9363 | 3.9363 | 3.9363 | 3.9363
2021-01-18 13:00 | 2.0748 | 2.5248 | 2.4704 | 2.6571 | 2.5171 | 2.7038 | 1.4918 | 2.5582 | 3.1567 | 3.1567 | 3.5557 | 3.5557 | 2019-03-18 01:00 | 1.3794 | 2.2606 | 3.7108 | 3.7108 | 3.7108 | 3.7108
2021-01-18 14:00 | 2.172 | 2.6431 | 2.5861 | 2.7815 | 2.6349 | 2.8304 | 1.3832 | 2.372 | 2.9269 | 2.9269 | 3.2968 | 3.2968 | 2019-03-18 02:00 | 1.3642 | 2.2356 | 3.6698 | 3.6698 | 3.6698 | 3.6698
2021-01-18 15:00 | 2.2634 | 2.7544 | 2.695 | 2.8987 | 2.7459 | 2.9496 | 1.3518 | 2.3181 | 2.8604 | 2.8604 | 3.2219 | 3.2219 | 2019-03-18 03:00 | 1.4251 | 2.3355 | 3.8338 | 3.8338 | 3.8338 | 3.8338
2021-01-18 16:00 | 2.3063 | 2.8065 | 2.746 | 2.9536 | 2.7979 | 3.0055 | 1.4299 | 2.452 | 3.0257 | 3.0257 | 3.4081 | 3.4081 | 2019-03-18 04:00 | 1.4175 | 2.323 | 3.8133 | 3.8133 | 3.8133 | 3.8133
2021-01-18 17:00 | 2.4921 | 3.0326 | 2.9672 | 3.1915 | 3.0232 | 3.2475 | 1.5518 | 2.6611 | 3.2837 | 3.2837 | 3.6987 | 3.6987 | 2019-03-18 05:00 | 1.6919 | 2.7726 | 4.5513 | 4.5513 | 4.5513 | 4.5513
2021-01-18 18:00 | 2.5006 | 3.043 | 2.9774 | 3.2024 | 3.0336 | 3.2587 | 1.6661 | 2.8572 | 3.5256 | 3.5256 | 3.9712 | 3.9712 | 2019-03-18 06:00 | 1.8214 | 2.985 | 4.8999 | 4.8999 | 4.8999 | 4.8999
2021-01-18 19:00 | 2.1977 | 2.6744 | 2.6167 | 2.8145 | 2.6661 | 2.8639 | 1.709 | 2.9307 | 3.6163 | 3.6163 | 4.0734 | 4.0734 | 2019-03-18 07:00 | 1.8824 | 3.0849 | 5.0639 | 5.0639 | 5.0639 | 5.0639
2021-01-18 20:00 | 2.052 | 2.497 | 2.4432 | 2.6278 | 2.4893 | 2.674 | 1.5433 | 2.6464 | 3.2655 | 3.2655 | 3.6783 | 3.6783 | 2019-03-18 08:00 | 2.0424 | 3.3472 | 5.4944 | 5.4944 | 5.4944 | 5.4944
2021-01-18 21:00 | 1.8833 | 2.2918 | 2.2424 | 2.4119 | 2.2848 | 2.4543 | 1.5175 | 2.6023 | 3.2111 | 3.2111 | 3.617 | 3.617 | 2019-03-18 09:00 | 2.1034 | 3.4471 | 5.6584 | 5.6584 | 5.6584 | 5.6584
2021-01-18 22:00 | 1.729 | 2.104 | 2.0586 | 2.2143 | 2.0976 | 2.2532 | 1.349 | 2.3133 | 2.8545 | 2.8545 | 3.2153 | 3.2153 | 2019-03-18 10:00 | 2.4845 | 4.0716 | 6.6835 | 6.6835 | 6.6835 | 6.6835
2021-01-18 23:00 | 1.5148 | 1.8433 | 1.8035 | 1.9399 | 1.8376 | 1.9739 | 1.2317 | 2.1122 | 2.6064 | 2.6064 | 2.9358 | 2.9358 | 2019-03-18 11:00 | 2.6064 | 4.2714 | 7.0115 | 7.0115 | 7.0115 | 7.0115
2021-01-19 | 1.4089 | 1.7145 | 1.6775 | 1.8043 | 1.7092 | 1.836 | 0.97739 | 1.6761 | 2.0682 | 2.0682 | 2.3296 | 2.3296 | 2019-03-18 12:00 | 2.6826 | 4.3963 | 7.2165 | 7.2165 | 7.2165 | 7.2165
2021-01-19 01:00 | 1.306 | 1.5893 | 1.555 | 1.6726 | 1.5844 | 1.702 | 0.86308 | 1.48 | 1.8263 | 1.8263 | 2.0571 | 2.0571 | 2019-03-18 13:00 | 2.614 | 4.2839 | 7.032 | 7.032 | 7.032 | 7.032
2021-01-19 02:00 | 1.1946 | 1.4537 | 1.4223 | 1.5298 | 1.4492 | 1.5567 | 0.77734 | 1.333 | 1.6449 | 1.6449 | 1.8528 | 1.8528 | 2019-03-18 14:00 | 2.6064 | 4.2714 | 7.0115 | 7.0115 | 7.0115 | 7.0115
2021-01-19 03:00 | 1.2317 | 1.4989 | 1.4666 | 1.5774 | 1.4943 | 1.6051 | 0.77162 | 1.3232 | 1.6328 | 1.6328 | 1.8391 | 1.8391 | 2019-03-18 15:00 | 2.553 | 4.184 | 6.868 | 6.868 | 6.868 | 6.868
2021-01-19 04:00 | 1.2117 | 1.4746 | 1.4428 | 1.5518 | 1.47 | 1.5791 | 0.75734 | 1.2987 | 1.6025 | 1.6025 | 1.8051 | 1.8051 | 2019-03-18 16:00 | 2.5454 | 4.1715 | 6.8475 | 6.8475 | 6.8475 | 6.8475
2021-01-19 05:00 | 1.3368 | 1.6267 | 1.5916 | 1.7119 | 1.6217 | 1.742 | 0.7802 | 1.3379 | 1.6509 | 1.6509 | 1.8596 | 1.8596 | 2019-03-18 17:00 | 2.3854 | 3.9092 | 6.417 | 6.417 | 6.417 | 6.417
2021-01-19 06:00 | 1.5518 | 1.8884 | 1.8477 | 1.9873 | 1.8826 | 2.0223 | 0.94596 | 1.6222 | 2.0017 | 2.0017 | 2.2546 | 2.2546 | 2019-03-18 18:00 | 2.1415 | 3.5095 | 5.7609 | 5.7609 | 5.7609 | 5.7609
2021-01-19 07:00 | 1.8633 | 2.2675 | 2.2186 | 2.3863 | 2.2605 | 2.4282 | 1.1889 | 2.0387 | 2.5157 | 2.5157 | 2.8336 | 2.8336 | 2019-03-18 19:00 | 1.7605 | 2.8851 | 4.7359 | 4.7359 | 4.7359 | 4.7359
2021-01-19 08:00 | 2.0577 | 2.504 | 2.45 | 2.6352 | 2.4963 | 2.6814 | 1.3918 | 2.3867 | 2.945 | 2.945 | 3.3173 | 3.3173 | 2019-03-18 20:00 | 1.7757 | 2.91 | 4.7769 | 4.7769 | 4.7769 | 4.7769
2021-01-19 09:00 | 2.0777 | 2.5283 | 2.4738 | 2.6608 | 2.5205 | 2.7075 | 1.2232 | 2.0975 | 2.5882 | 2.5882 | 2.9154 | 2.9154 | 2019-03-18 21:00 | 1.608 | 2.6353 | 4.3258 | 4.3258 | 4.3258 | 4.3258
2021-01-19 10:00 | 2.1748 | 2.6466 | 2.5895 | 2.7852 | 2.6384 | 2.8341 | 1.3946 | 2.3916 | 2.9511 | 2.9511 | 3.3241 | 3.3241 | 2019-03-18 22:00 | 1.669 | 2.7352 | 4.4898 | 4.4898 | 4.4898 | 4.4898
2021-01-19 11:00 | 2.0977 | 2.5527 | 2.4976 | 2.6864 | 2.5448 | 2.7336 | 1.3746 | 2.3573 | 2.9088 | 2.9088 | 3.2764 | 3.2764 | 2019-03-18 23:00 | 1.5318 | 2.5104 | 4.1208 | 4.1208 | 4.1208 | 4.1208
2021-01-19 12:00 | 2.1748 | 2.6466 | 2.5895 | 2.7852 | 2.6384 | 2.8341 | 1.3775 | 2.3622 | 2.9148 | 2.9148 | 3.2832 | 3.2832 | 2019-03-19 | 1.5242 | 2.4979 | 4.1003 | 4.1003 | 4.1003 | 4.1003
2021-01-19 13:00 | 2.1348 | 2.5979 | 2.5418 | 2.734 | 2.5899 | 2.782 | 1.4604 | 2.5043 | 3.0902 | 3.0902 | 3.4807 | 3.4807 | 2019-03-19 01:00 | 1.5013 | 2.4604 | 4.0388 | 4.0388 | 4.0388 | 4.0388
2021-01-19 14:00 | 2.1548 | 2.6222 | 2.5657 | 2.7596 | 2.6141 | 2.8081 | 1.3661 | 2.3426 | 2.8906 | 2.8906 | 3.256 | 3.256 | 2019-03-19 02:00 | 1.4632 | 2.398 | 3.9363 | 3.9363 | 3.9363 | 3.9363
2021-01-19 15:00 | 2.3778 | 2.8935 | 2.8311 | 3.0451 | 2.8846 | 3.0986 | 1.3661 | 2.3426 | 2.8906 | 2.8906 | 3.256 | 3.256 | 2019-03-19 03:00 | 1.4556 | 2.3855 | 3.9158 | 3.9158 | 3.9158 | 3.9158
2021-01-19 16:00 | 2.4092 | 2.9317 | 2.8685 | 3.0853 | 2.9227 | 3.1395 | 1.4032 | 2.4063 | 2.9692 | 2.9692 | 3.3445 | 3.3445 | 2019-03-19 04:00 | 1.448 | 2.373 | 3.8953 | 3.8953 | 3.8953 | 3.8953
2021-01-19 17:00 | 2.2063 | 2.6848 | 2.6269 | 2.8255 | 2.6765 | 2.8751 | 1.529 | 2.6219 | 3.2353 | 3.2353 | 3.6442 | 3.6442 | 2019-03-19 05:00 | 1.6538 | 2.7102 | 4.4488 | 4.4488 | 4.4488 | 4.4488
2021-01-19 18:00 | 2.252 | 2.7405 | 2.6813 | 2.884 | 2.732 | 2.9347 | 1.6233 | 2.7837 | 3.4349 | 3.4349 | 3.869 | 3.869 | 2019-03-19 06:00 | 1.7986 | 2.9475 | 4.8384 | 4.8384 | 4.8384 | 4.8384
2021-01-19 19:00 | 2.0922 | 2.546 | 2.491 | 2.6793 | 2.5381 | 2.7264 | 1.5347 | 2.6317 | 3.2474 | 3.2474 | 3.6578 | 3.6578 | 2019-03-19 07:00 | 2.172 | 3.5595 | 5.8429 | 5.8429 | 5.8429 | 5.8429
2021-01-19 20:00 | 1.829 | 2.2258 | 2.1777 | 2.3424 | 2.2189 | 2.3835 | 1.489 | 2.5533 | 3.1506 | 3.1506 | 3.5489 | 3.5489 | 2019-03-19 08:00 | 2.1034 | 3.4471 | 5.6584 | 5.6584 | 5.6584 | 5.6584
2021-01-19 21:00 | 1.7976 | 2.1875 | 2.1403 | 2.3021 | 2.1808 | 2.3425 | 1.4432 | 2.4749 | 3.0539 | 3.0539 | 3.4399 | 3.4399 | 2019-03-19 09:00 | 2.1872 | 3.5845 | 5.8839 | 5.8839 | 5.8839 | 5.8839
2021-01-19 22:00 | 1.5721 | 1.913 | 1.8718 | 2.0133 | 1.9071 | 2.0486 | 1.3318 | 2.2838 | 2.818 | 2.818 | 3.1742 | 3.1742 | 2019-03-19 10:00 | 2.3473 | 3.8467 | 6.3145 | 6.3145 | 6.3145 | 6.3145
2021-01-19 23:00 | 1.4461 | 1.7597 | 1.7218 | 1.8519 | 1.7543 | 1.8845 | 1.0978 | 1.8826 | 2.3231 | 2.3231 | 2.6167 | 2.6167 | 2019-03-19 11:00 | 2.6826 | 4.3963 | 7.2165 | 7.2165 | 7.2165 | 7.2165
2021-01-20 | 1.3661 | 1.6624 | 1.6265 | 1.7494 | 1.6572 | 1.7802 | 0.84307 | 1.4457 | 1.7839 | 1.7839 | 2.0094 | 2.0094 | 2019-03-19 12:00 | 2.6521 | 4.3463 | 7.1345 | 7.1345 | 7.1345 | 7.1345
2021-01-20 01:00 | 1.2494 | 1.5204 | 1.4876 | 1.6 | 1.5157 | 1.6281 | 0.8002 | 1.3722 | 1.6932 | 1.6932 | 1.9073 | 1.9073 | 2019-03-19 13:00 | 2.6292 | 4.3088 | 7.073 | 7.073 | 7.073 | 7.073
2021-01-20 02:00 | 1.1832 | 1.4398 | 1.4087 | 1.5152 | 1.4353 | 1.5418 | 0.72304 | 1.2399 | 1.53 | 1.53 | 1.7233 | 1.7233 | 2019-03-19 14:00 | 2.6064 | 4.2714 | 7.0115 | 7.0115 | 7.0115 | 7.0115
2021-01-20 03:00 | 1.2146 | 1.478 | 1.4462 | 1.5555 | 1.4735 | 1.5828 | 0.70304 | 1.2056 | 1.4876 | 1.4876 | 1.6757 | 1.6757 | 2019-03-19 15:00 | 2.6064 | 4.2714 | 7.0115 | 7.0115 | 7.0115 | 7.0115
2021-01-20 04:00 | 1.1689 | 1.4224 | 1.3918 | 1.497 | 1.4181 | 1.5233 | 0.68589 | 1.1762 | 1.4513 | 1.4513 | 1.6348 | 1.6348 | 2019-03-19 16:00 | 2.5454 | 4.1715 | 6.8475 | 6.8475 | 6.8475 | 6.8475
2021-01-20 05:00 | 1.2746 | 1.5511 | 1.5176 | 1.6323 | 1.5463 | 1.661 | 0.7459 | 1.2791 | 1.5783 | 1.5783 | 1.7778 | 1.7778 | 2019-03-19 17:00 | 2.332 | 3.8218 | 6.2735 | 6.2735 | 6.2735 | 6.2735
2021-01-20 06:00 | 1.5848 | 1.9286 | 1.887 | 2.0296 | 1.9226 | 2.0653 | 0.97168 | 1.6663 | 2.0561 | 2.0561 | 2.316 | 2.316 | 2019-03-19 18:00 | 1.9891 | 3.2597 | 5.3509 | 5.3509 | 5.3509 | 5.3509
2021-01-20 07:00 | 1.7976 | 2.1875 | 2.1403 | 2.3021 | 2.1808 | 2.3425 | 1.1289 | 1.9358 | 2.3887 | 2.3887 | 2.6906 | 2.6906 | 2019-03-19 19:00 | 1.9586 | 3.2098 | 5.2689 | 5.2689 | 5.2689 | 5.2689
2021-01-20 08:00 | 1.8862 | 2.2953 | 2.2458 | 2.4156 | 2.2882 | 2.458 | 1.266 | 2.1711 | 2.679 | 2.679 | 3.0176 | 3.0176 | 2019-03-19 20:00 | 1.8519 | 3.0349 | 4.9819 | 4.9819 | 4.9819 | 4.9819
2021-01-20 09:00 | 1.9091 | 2.3231 | 2.273 | 2.4448 | 2.316 | 2.4878 | 1.2403 | 2.1269 | 2.6245 | 2.6245 | 2.9562 | 2.9562 | 2019-03-19 21:00 | 1.8519 | 3.0349 | 4.9819 | 4.9819 | 4.9819 | 4.9819
2021-01-20 10:00 | 1.8919 | 2.3023 | 2.2526 | 2.4229 | 2.2952 | 2.4654 | 1.4061 | 2.4112 | 2.9753 | 2.9753 | 3.3513 | 3.3513 | 2019-03-19 22:00 | 1.7452 | 2.8601 | 4.6949 | 4.6949 | 4.6949 | 4.6949
2021-01-20 11:00 | 1.8976 | 2.3092 | 2.2594 | 2.4302 | 2.3021 | 2.4729 | 1.4032 | 2.4063 | 2.9692 | 2.9692 | 3.3445 | 3.3445 | 2019-03-19 23:00 | 1.6538 | 2.7102 | 4.4488 | 4.4488 | 4.4488 | 4.4488
2021-01-20 12:00 | 1.8748 | 2.2814 | 2.2322 | 2.4009 | 2.2744 | 2.4431 | 1.3689 | 2.3475 | 2.8967 | 2.8967 | 3.2628 | 3.2628 | 2019-03-20 | 1.5013 | 2.4604 | 4.0388 | 4.0388 | 4.0388 | 4.0388
2021-01-20 13:00 | 2.0148 | 2.4518 | 2.3989 | 2.5803 | 2.4443 | 2.6256 | 1.3861 | 2.3769 | 2.9329 | 2.9329 | 3.3036 | 3.3036 | 2019-03-20 01:00 | 1.448 | 2.373 | 3.8953 | 3.8953 | 3.8953 | 3.8953
2021-01-20 14:00 | 2.0777 | 2.5283 | 2.4738 | 2.6608 | 2.5205 | 2.7075 | 1.4689 | 2.519 | 3.1083 | 3.1083 | 3.5012 | 3.5012 | 2019-03-20 02:00 | 1.448 | 2.373 | 3.8953 | 3.8953 | 3.8953 | 3.8953
2021-01-20 15:00 | 1.9891 | 2.4205 | 2.3683 | 2.5473 | 2.4131 | 2.5921 | 1.3661 | 2.3426 | 2.8906 | 2.8906 | 3.256 | 3.256 | 2019-03-20 03:00 | 1.4327 | 2.348 | 3.8543 | 3.8543 | 3.8543 | 3.8543
2021-01-20 16:00 | 2.0377 | 2.4796 | 2.4261 | 2.6095 | 2.472 | 2.6554 | 1.4632 | 2.5092 | 3.0962 | 3.0962 | 3.4876 | 3.4876 | 2019-03-20 04:00 | 1.509 | 2.4729 | 4.0593 | 4.0593 | 4.0593 | 4.0593
2021-01-20 17:00 | 2.1348 | 2.5979 | 2.5418 | 2.734 | 2.5899 | 2.782 | 1.5147 | 2.5974 | 3.2051 | 3.2051 | 3.6102 | 3.6102 | 2019-03-20 05:00 | 1.6614 | 2.7227 | 4.4693 | 4.4693 | 4.4693 | 4.4693
2021-01-20 18:00 | 2.2749 | 2.7683 | 2.7086 | 2.9133 | 2.7598 | 2.9645 | 1.5861 | 2.7199 | 3.3563 | 3.3563 | 3.7805 | 3.7805 | 2019-03-20 06:00 | 1.7757 | 2.91 | 4.7769 | 4.7769 | 4.7769 | 4.7769
2021-01-20 19:00 | 2.212 | 2.6918 | 2.6337 | 2.8328 | 2.6835 | 2.8826 | 1.5318 | 2.6268 | 3.2414 | 3.2414 | 3.651 | 3.651 | 2019-03-20 07:00 | 1.8519 | 3.0349 | 4.9819 | 4.9819 | 4.9819 | 4.9819
2021-01-20 20:00 | 1.8833 | 2.2918 | 2.2424 | 2.4119 | 2.2848 | 2.4543 | 1.4575 | 2.4994 | 3.0841 | 3.0841 | 3.4739 | 3.4739 | 2019-03-20 08:00 | 2.0653 | 3.3846 | 5.5559 | 5.5559 | 5.5559 | 5.5559
2021-01-20 21:00 | 1.8262 | 2.2223 | 2.1743 | 2.3387 | 2.2154 | 2.3798 | 1.4347 | 2.4602 | 3.0357 | 3.0357 | 3.4194 | 3.4194 | 2019-03-20 09:00 | 2.233 | 3.6594 | 6.007 | 6.007 | 6.007 | 6.007
2021-01-20 22:00 | 1.6576 | 2.0171 | 1.9736 | 2.1228 | 2.0109 | 2.1601 | 1.3157 | 2.2562 | 2.7841 | 2.7841 | 3.1359 | 3.1359 | 2019-03-20 10:00 | 2.4692 | 4.0466 | 6.6425 | 6.6425 | 6.6425 | 6.6425
2021-01-20 23:00 | 1.4318 | 1.7423 | 1.7048 | 1.8336 | 1.737 | 1.8658 | 1.1204 | 1.9213 | 2.3708 | 2.3708 | 2.6705 | 2.6705 | 2019-03-20 11:00 | 2.5683 | 4.2089 | 6.909 | 6.909 | 6.909 | 6.909
2021-01-21 | 1.3775 | 1.6763 | 1.6401 | 1.7641 | 1.6711 | 1.7951 | 0.91458 | 1.5684 | 1.9353 | 1.9353 | 2.1799 | 2.1799 | 2019-03-20 12:00 | 2.675 | 4.3838 | 7.196 | 7.196 | 7.196 | 7.196
2021-01-21 01:00 | 1.2261 | 1.492 | 1.4598 | 1.5701 | 1.4874 | 1.5977 | 0.75734 | 1.2987 | 1.6025 | 1.6025 | 1.8051 | 1.8051 | 2019-03-20 13:00 | 2.7283 | 4.4712 | 7.3396 | 7.3396 | 7.3396 | 7.3396
2021-01-21 02:00 | 1.206 | 1.4676 | 1.4359 | 1.5445 | 1.4631 | 1.5716 | 0.75162 | 1.2889 | 1.5904 | 1.5904 | 1.7915 | 1.7915 | 2019-03-20 14:00 | 2.6216 | 4.2964 | 7.0525 | 7.0525 | 7.0525 | 7.0525
2021-01-21 03:00 | 1.1403 | 1.3876 | 1.3577 | 1.4603 | 1.3833 | 1.486 | 0.7259 | 1.2448 | 1.536 | 1.536 | 1.7301 | 1.7301 | 2019-03-20 15:00 | 2.6597 | 4.3588 | 7.155 | 7.155 | 7.155 | 7.155
2021-01-21 04:00 | 1.1717 | 1.4259 | 1.3951 | 1.5006 | 1.4215 | 1.5269 | 0.71161 | 1.2203 | 1.5058 | 1.5058 | 1.6961 | 1.6961 | 2019-03-20 16:00 | 2.614 | 4.2839 | 7.032 | 7.032 | 7.032 | 7.032
2021-01-21 05:00 | 1.28 | 1.5576 | 1.524 | 1.6392 | 1.5528 | 1.668 | 0.77448 | 1.3281 | 1.6388 | 1.6388 | 1.8459 | 1.8459 | 2019-03-20 17:00 | 2.5149 | 4.1215 | 6.7655 | 6.7655 | 6.7655 | 6.7655
2021-01-21 06:00 | 1.6089 | 1.9578 | 1.9156 | 2.0604 | 1.9518 | 2.0966 | 1.006 | 1.7251 | 2.1286 | 2.1286 | 2.3977 | 2.3977 | 2019-03-20 18:00 | 2.3092 | 3.7843 | 6.212 | 6.212 | 6.212 | 6.212
2021-01-21 07:00 | 1.8862 | 2.2953 | 2.2458 | 2.4156 | 2.2882 | 2.458 | 1.1774 | 2.0191 | 2.4915 | 2.4915 | 2.8064 | 2.8064 | 2019-03-20 19:00 | 1.9662 | 3.2223 | 5.2894 | 5.2894 | 5.2894 | 5.2894
2021-01-21 08:00 | 1.8691 | 2.2744 | 2.2254 | 2.3936 | 2.2674 | 2.4356 | 1.2832 | 2.2005 | 2.7152 | 2.7152 | 3.0584 | 3.0584 | 2019-03-20 20:00 | 1.9129 | 3.1348 | 5.1459 | 5.1459 | 5.1459 | 5.1459
2021-01-21 09:00 | 1.9291 | 2.3475 | 2.2968 | 2.4705 | 2.3402 | 2.5139 | 1.2718 | 2.1809 | 2.691 | 2.691 | 3.0312 | 3.0312 | 2019-03-20 21:00 | 1.8138 | 2.9725 | 4.8794 | 4.8794 | 4.8794 | 4.8794
2021-01-21 10:00 | 1.9091 | 2.3231 | 2.273 | 2.4448 | 2.316 | 2.4878 | 1.3546 | 2.323 | 2.8664 | 2.8664 | 3.2287 | 3.2287 | 2019-03-20 22:00 | 1.6385 | 2.6852 | 4.4078 | 4.4078 | 4.4078 | 4.4078
2021-01-21 11:00 | 2.0148 | 2.4518 | 2.3989 | 2.5803 | 2.4443 | 2.6256 | 1.4575 | 2.4994 | 3.0841 | 3.0841 | 3.4739 | 3.4739 | 2019-03-20 23:00 | 1.5699 | 2.5728 | 4.2233 | 4.2233 | 4.2233 | 4.2233
2021-01-21 12:00 | 2.0462 | 2.4901 | 2.4364 | 2.6205 | 2.4824 | 2.6666 | 1.4461 | 2.4798 | 3.0599 | 3.0599 | 3.4467 | 3.4467 | 2019-03-21 | 1.4937 | 2.4479 | 4.0183 | 4.0183 | 4.0183 | 4.0183
2021-01-21 13:00 | 2.0291 | 2.4692 | 2.4159 | 2.5986 | 2.4616 | 2.6442 | 1.4461 | 2.4798 | 3.0599 | 3.0599 | 3.4467 | 3.4467 | 2019-03-21 01:00 | 1.4861 | 2.4354 | 3.9978 | 3.9978 | 3.9978 | 3.9978
2021-01-21 14:00 | 2.2349 | 2.7196 | 2.6609 | 2.8621 | 2.7112 | 2.9124 | 1.3832 | 2.372 | 2.9269 | 2.9269 | 3.2968 | 3.2968 | 2019-03-21 02:00 | 1.4861 | 2.4354 | 3.9978 | 3.9978 | 3.9978 | 3.9978
2021-01-21 15:00 | 2.1977 | 2.6744 | 2.6167 | 2.8145 | 2.6661 | 2.8639 | 1.3832 | 2.372 | 2.9269 | 2.9269 | 3.2968 | 3.2968 | 2019-03-21 03:00 | 1.4861 | 2.4354 | 3.9978 | 3.9978 | 3.9978 | 3.9978
2021-01-21 16:00 | 2.3892 | 2.9074 | 2.8447 | 3.0597 | 2.8984 | 3.1135 | 1.4261 | 2.4455 | 3.0176 | 3.0176 | 3.399 | 3.399 | 2019-03-21 04:00 | 1.4632 | 2.398 | 3.9363 | 3.9363 | 3.9363 | 3.9363
2021-01-21 17:00 | 2.4463 | 2.9769 | 2.9127 | 3.1329 | 2.9678 | 3.1879 | 1.5918 | 2.7297 | 3.3683 | 3.3683 | 3.7941 | 3.7941 | 2019-03-21 05:00 | 1.6919 | 2.7726 | 4.5513 | 4.5513 | 4.5513 | 4.5513
2021-01-21 18:00 | 2.5235 | 3.0708 | 3.0046 | 3.2317 | 3.0614 | 3.2885 | 1.7033 | 2.9209 | 3.6042 | 3.6042 | 4.0597 | 4.0597 | 2019-03-21 06:00 | 1.8443 | 3.0224 | 4.9614 | 4.9614 | 4.9614 | 4.9614
2021-01-21 19:00 | 2.2777 | 2.7718 | 2.712 | 2.917 | 2.7632 | 2.9682 | 1.6633 | 2.8523 | 3.5195 | 3.5195 | 3.9644 | 3.9644 | 2019-03-21 07:00 | 2.1491 | 3.522 | 5.7814 | 5.7814 | 5.7814 | 5.7814
2021-01-21 20:00 | 2.1205 | 2.5805 | 2.5248 | 2.7157 | 2.5725 | 2.7634 | 1.6204 | 2.7788 | 3.4288 | 3.4288 | 3.8622 | 3.8622 | 2019-03-21 08:00 | 2.1567 | 3.5345 | 5.8019 | 5.8019 | 5.8019 | 5.8019
2021-01-21 21:00 | 2.0662 | 2.5144 | 2.4602 | 2.6461 | 2.5067 | 2.6926 | 1.6118 | 2.7641 | 3.4107 | 3.4107 | 3.8418 | 3.8418 | 2019-03-21 09:00 | 2.4616 | 4.0341 | 6.622 | 6.622 | 6.622 | 6.622
2021-01-21 22:00 | 1.7121 | 2.0834 | 2.0385 | 2.1926 | 2.077 | 2.2311 | 1.3689 | 2.3475 | 2.8967 | 2.8967 | 3.2628 | 3.2628 | 2019-03-21 10:00 | 2.553 | 4.184 | 6.868 | 6.868 | 6.868 | 6.868
2021-01-21 23:00 | 1.4634 | 1.7809 | 1.7425 | 1.8742 | 1.7754 | 1.9071 | 1.2008 | 2.0592 | 2.541 | 2.541 | 2.8621 | 2.8621 | 2019-03-21 11:00 | 2.5988 | 4.2589 | 6.991 | 6.991 | 6.991 | 6.991
2021-01-22 | 1.4061 | 1.711 | 1.6741 | 1.8007 | 1.7058 | 1.8323 | 1.0093 | 1.7308 | 2.1357 | 2.1357 | 2.4057 | 2.4057 | 2019-03-21 12:00 | 2.6902 | 4.4088 | 7.237 | 7.237 | 7.237 | 7.237
2021-01-22 01:00 | 1.266 | 1.5406 | 1.5074 | 1.6213 | 1.5359 | 1.6498 | 0.82592 | 1.4163 | 1.7477 | 1.7477 | 1.9686 | 1.9686 | 2019-03-21 13:00 | 2.7131 | 4.4462 | 7.2986 | 7.2986 | 7.2986 | 7.2986
2021-01-22 02:00 | 1.206 | 1.4676 | 1.4359 | 1.5445 | 1.4631 | 1.5716 | 0.76019 | 1.3036 | 1.6086 | 1.6086 | 1.8119 | 1.8119 | 2019-03-21 14:00 | 2.7512 | 4.5087 | 7.4011 | 7.4011 | 7.4011 | 7.4011
2021-01-22 03:00 | 1.1689 | 1.4224 | 1.3917 | 1.4969 | 1.418 | 1.5232 | 0.7459 | 1.2791 | 1.5783 | 1.5783 | 1.7778 | 1.7778 | 2019-03-21 15:00 | 2.7131 | 4.4462 | 7.2986 | 7.2986 | 7.2986 | 7.2986
2021-01-22 04:00 | 1.1832 | 1.4398 | 1.4087 | 1.5152 | 1.4353 | 1.5418 | 0.74876 | 1.284 | 1.5844 | 1.5844 | 1.7846 | 1.7846 | 2019-03-21 16:00 | 2.675 | 4.3838 | 7.196 | 7.196 | 7.196 | 7.196
2021-01-22 05:00 | 1.4289 | 1.7389 | 1.7014 | 1.83 | 1.7335 | 1.8621 | 0.79149 | 1.3573 | 1.6748 | 1.6748 | 1.8865 | 1.8865 | 2019-03-21 17:00 | 2.3701 | 3.8842 | 6.376 | 6.376 | 6.376 | 6.376
2021-01-22 06:00 | 1.5204 | 1.8502 | 1.8102 | 1.9471 | 1.8445 | 1.9813 | 1.0117 | 1.7349 | 2.1407 | 2.1407 | 2.4113 | 2.4113 | 2019-03-21 18:00 | 2.3244 | 3.8093 | 6.253 | 6.253 | 6.253 | 6.253
2021-01-22 07:00 | 2.0091 | 2.4449 | 2.3921 | 2.5729 | 2.4373 | 2.6181 | 1.186 | 2.0338 | 2.5096 | 2.5096 | 2.8268 | 2.8268 | 2019-03-21 19:00 | 2.0043 | 3.2847 | 5.3919 | 5.3919 | 5.3919 | 5.3919
2021-01-22 08:00 | 2.2234 | 2.7057 | 2.6473 | 2.8474 | 2.6973 | 2.8975 | 1.3146 | 2.2544 | 2.7818 | 2.7818 | 3.1333 | 3.1333 | 2019-03-21 20:00 | 1.9434 | 3.1848 | 5.2279 | 5.2279 | 5.2279 | 5.2279
2021-01-22 09:00 | 2.2492 | 2.737 | 2.6779 | 2.8804 | 2.7286 | 2.931 | 1.3775 | 2.3622 | 2.9148 | 2.9148 | 3.2832 | 3.2832 | 2019-03-21 21:00 | 1.7528 | 2.8726 | 4.7154 | 4.7154 | 4.7154 | 4.7154
2021-01-22 10:00 | 2.4549 | 2.9874 | 2.9229 | 3.1439 | 2.9782 | 3.1991 | 1.4832 | 2.5435 | 3.1385 | 3.1385 | 3.5352 | 3.5352 | 2019-03-21 22:00 | 1.6385 | 2.6852 | 4.4078 | 4.4078 | 4.4078 | 4.4078
2021-01-22 11:00 | 2.3892 | 2.9074 | 2.8447 | 3.0597 | 2.8984 | 3.1135 | 1.5061 | 2.5827 | 3.1869 | 3.1869 | 3.5897 | 3.5897 | 2019-03-21 23:00 | 1.5547 | 2.5478 | 4.1823 | 4.1823 | 4.1823 | 4.1823
2021-01-22 12:00 | 2.4092 | 2.9317 | 2.8685 | 3.0853 | 2.9227 | 3.1395 | 1.5547 | 2.666 | 3.2897 | 3.2897 | 3.7055 | 3.7055 | 2019-03-22 | 1.509 | 2.4729 | 4.0593 | 4.0593 | 4.0593 | 4.0593
2021-01-22 13:00 | 2.6778 | 3.2586 | 3.1884 | 3.4294 | 3.2486 | 3.4896 | 1.6004 | 2.7445 | 3.3865 | 3.3865 | 3.8145 | 3.8145 | 2019-03-22 01:00 | 1.4937 | 2.4479 | 4.0183 | 4.0183 | 4.0183 | 4.0183
2021-01-22 14:00 | 2.9493 | 3.589 | 3.5116 | 3.7771 | 3.578 | 3.8434 | 1.6576 | 2.8425 | 3.5074 | 3.5074 | 3.9507 | 3.9507 | 2019-03-22 02:00 | 1.4709 | 2.4105 | 3.9568 | 3.9568 | 3.9568 | 3.9568
2021-01-22 15:00 | 2.9322 | 3.5682 | 3.4912 | 3.7551 | 3.5572 | 3.8211 | 1.569 | 2.6905 | 3.32 | 3.32 | 3.7396 | 3.7396 | 2019-03-22 03:00 | 1.5013 | 2.4604 | 4.0388 | 4.0388 | 4.0388 | 4.0388
2021-01-22 16:00 | 2.9208 | 3.5543 | 3.4776 | 3.7405 | 3.5433 | 3.8062 | 1.6776 | 2.8768 | 3.5498 | 3.5498 | 3.9984 | 3.9984 | 2019-03-22 04:00 | 1.4632 | 2.398 | 3.9363 | 3.9363 | 3.9363 | 3.9363
2021-01-22 17:00 | 2.8094 | 3.4187 | 3.345 | 3.5978 | 3.4082 | 3.661 | 1.7605 | 3.0189 | 3.7251 | 3.7251 | 4.196 | 4.196 | 2019-03-22 05:00 | 1.5852 | 2.5978 | 4.2643 | 4.2643 | 4.2643 | 4.2643
2021-01-22 18:00 | 2.8579 | 3.4777 | 3.4027 | 3.6599 | 3.467 | 3.7242 | 1.8748 | 3.2149 | 3.967 | 3.967 | 4.4684 | 4.4684 | 2019-03-22 06:00 | 1.8062 | 2.96 | 4.8589 | 4.8589 | 4.8589 | 4.8589
2021-01-22 19:00 | 2.795 | 3.4012 | 3.3279 | 3.5794 | 3.3908 | 3.6423 | 1.8891 | 3.2394 | 3.9973 | 3.9973 | 4.5025 | 4.5025 | 2019-03-22 07:00 | 2.0043 | 3.2847 | 5.3919 | 5.3919 | 5.3919 | 5.3919
2021-01-22 20:00 | 2.232 | 2.7161 | 2.6575 | 2.8584 | 2.7077 | 2.9086 | 1.8262 | 3.1316 | 3.8642 | 3.8642 | 4.3526 | 4.3526 | 2019-03-22 08:00 | 2.3168 | 3.7968 | 6.2325 | 6.2325 | 6.2325 | 6.2325
2021-01-22 21:00 | 2.1092 | 2.5666 | 2.5113 | 2.7011 | 2.5587 | 2.7485 | 1.7119 | 2.9356 | 3.6223 | 3.6223 | 4.0802 | 4.0802 | 2019-03-22 09:00 | 2.4768 | 4.0591 | 6.663 | 6.663 | 6.663 | 6.663
2021-01-22 22:00 | 1.8869 | 2.2962 | 2.2467 | 2.4165 | 2.2891 | 2.4589 | 1.5032 | 2.5778 | 3.1809 | 3.1809 | 3.5829 | 3.5829 | 2019-03-22 10:00 | 2.5607 | 4.1964 | 6.8885 | 6.8885 | 6.8885 | 6.8885
2021-01-22 23:00 | 1.5918 | 1.9371 | 1.8953 | 2.0386 | 1.9311 | 2.0744 | 1.1744 | 2.0139 | 2.485 | 2.485 | 2.7991 | 2.7991 | 2019-03-22 11:00 | 2.553 | 4.184 | 6.868 | 6.868 | 6.868 | 6.868
2021-01-23 | 1.5118 | 1.8397 | 1.8 | 1.9361 | 1.8341 | 1.9701 | 1.0546 | 1.8084 | 2.2315 | 2.2315 | 2.5135 | 2.5135 | 2019-03-22 12:00 | 2.5759 | 4.2214 | 6.9295 | 6.9295 | 6.9295 | 6.9295
2021-01-23 01:00 | 1.338 | 1.6282 | 1.5931 | 1.7135 | 1.6232 | 1.7436 | 0.91738 | 1.5732 | 1.9412 | 1.9412 | 2.1865 | 2.1865 | 2019-03-22 13:00 | 2.5683 | 4.2089 | 6.909 | 6.909 | 6.909 | 6.909
2021-01-23 02:00 | 1.2432 | 1.5128 | 1.4802 | 1.5921 | 1.5082 | 1.62 | 0.86022 | 1.4751 | 1.8202 | 1.8202 | 2.0503 | 2.0503 | 2019-03-22 14:00 | 2.4921 | 4.084 | 6.704 | 6.704 | 6.704 | 6.704
2021-01-23 03:00 | 1.2632 | 1.5372 | 1.504 | 1.6177 | 1.5324 | 1.6461 | 0.81164 | 1.3918 | 1.7174 | 1.7174 | 1.9345 | 1.9345 | 2019-03-22 15:00 | 2.4768 | 4.0591 | 6.663 | 6.663 | 6.663 | 6.663
2021-01-23 04:00 | 1.2135 | 1.4768 | 1.4449 | 1.5541 | 1.4722 | 1.5814 | 0.79163 | 1.3575 | 1.6751 | 1.6751 | 1.8868 | 1.8868 | 2019-03-22 16:00 | 2.4463 | 4.0091 | 6.581 | 6.581 | 6.581 | 6.581
2021-01-23 05:00 | 1.2375 | 1.5059 | 1.4734 | 1.5847 | 1.5012 | 1.6126 | 0.86879 | 1.4898 | 1.8384 | 1.8384 | 2.0707 | 2.0707 | 2019-03-22 17:00 | 2.2558 | 3.6969 | 6.0685 | 6.0685 | 6.0685 | 6.0685
2021-01-23 06:00 | 1.2775 | 1.5545 | 1.521 | 1.636 | 1.5498 | 1.6647 | 0.89451 | 1.5339 | 1.8928 | 1.8928 | 2.132 | 2.132 | 2019-03-22 18:00 | 1.951 | 3.1973 | 5.2484 | 5.2484 | 5.2484 | 5.2484
2021-01-23 07:00 | 1.4089 | 1.7145 | 1.6775 | 1.8043 | 1.7092 | 1.836 | 1.0403 | 1.7839 | 2.2012 | 2.2012 | 2.4794 | 2.4794 | 2019-03-22 19:00 | 1.7909 | 2.935 | 4.8179 | 4.8179 | 4.8179 | 4.8179
2021-01-23 08:00 | 1.5347 | 1.8675 | 1.8273 | 1.9654 | 1.8618 | 1.9999 | 1.2575 | 2.1564 | 2.6608 | 2.6608 | 2.9971 | 2.9971 | 2019-03-22 20:00 | 1.7376 | 2.8476 | 4.6744 | 4.6744 | 4.6744 | 4.6744
2021-01-23 09:00 | 1.5918 | 1.9371 | 1.8953 | 2.0386 | 1.9311 | 2.0744 | 1.3689 | 2.3475 | 2.8966 | 2.8966 | 3.2627 | 3.2627 | 2019-03-22 21:00 | 1.6614 | 2.7227 | 4.4693 | 4.4693 | 4.4693 | 4.4693
2021-01-23 10:00 | 1.6033 | 1.951 | 1.9089 | 2.0532 | 1.945 | 2.0893 | 1.6604 | 2.8474 | 3.5135 | 3.5135 | 3.9576 | 3.9576 | 2019-03-22 22:00 | 1.6538 | 2.7102 | 4.4488 | 4.4488 | 4.4488 | 4.4488
2021-01-23 11:00 | 1.6404 | 1.9962 | 1.9532 | 2.1008 | 1.9901 | 2.1377 | 1.6004 | 2.7445 | 3.3865 | 3.3865 | 3.8145 | 3.8145 | 2019-03-22 23:00 | 1.5775 | 2.5853 | 4.2438 | 4.2438 | 4.2438 | 4.2438
2021-01-23 12:00 | 1.7147 | 2.0866 | 2.0416 | 2.196 | 2.0802 | 2.2345 | 1.6347 | 2.8033 | 3.4591 | 3.4591 | 3.8963 | 3.8963 | 2019-03-23 | 1.509 | 2.4729 | 4.0593 | 4.0593 | 4.0593 | 4.0593
2021-01-23 13:00 | 1.7147 | 2.0866 | 2.0416 | 2.196 | 2.0802 | 2.2345 | 1.6861 | 2.8915 | 3.5679 | 3.5679 | 4.0189 | 4.0189 | 2019-03-23 01:00 | 1.509 | 2.4729 | 4.0593 | 4.0593 | 4.0593 | 4.0593
2021-01-23 14:00 | 1.849 | 2.2501 | 2.2016 | 2.368 | 2.2432 | 2.4096 | 1.7204 | 2.9503 | 3.6405 | 3.6405 | 4.1006 | 4.1006 | 2019-03-23 02:00 | 1.4327 | 2.348 | 3.8543 | 3.8543 | 3.8543 | 3.8543
2021-01-23 15:00 | 1.9777 | 2.4066 | 2.3547 | 2.5327 | 2.3992 | 2.5772 | 1.7576 | 3.014 | 3.7191 | 3.7191 | 4.1892 | 4.1892 | 2019-03-23 03:00 | 1.4251 | 2.3355 | 3.8338 | 3.8338 | 3.8338 | 3.8338
2021-01-23 16:00 | 2.0262 | 2.4657 | 2.4125 | 2.5949 | 2.4581 | 2.6405 | 1.8033 | 3.0924 | 3.8158 | 3.8158 | 4.2981 | 4.2981 | 2019-03-23 04:00 | 1.4632 | 2.398 | 3.9363 | 3.9363 | 3.9363 | 3.9363
2021-01-23 17:00 | 2.1348 | 2.5979 | 2.5418 | 2.734 | 2.5899 | 2.782 | 1.8805 | 3.2247 | 3.9791 | 3.9791 | 4.4821 | 4.4821 | 2019-03-23 05:00 | 1.5166 | 2.4854 | 4.0798 | 4.0798 | 4.0798 | 4.0798
2021-01-23 18:00 | 2.2749 | 2.7683 | 2.7086 | 2.9133 | 2.7598 | 2.9645 | 1.8862 | 3.2345 | 3.9912 | 3.9912 | 4.4957 | 4.4957 | 2019-03-23 06:00 | 1.6538 | 2.7102 | 4.4488 | 4.4488 | 4.4488 | 4.4488
2021-01-23 19:00 | 2.2834 | 2.7787 | 2.7188 | 2.9243 | 2.7702 | 2.9757 | 1.9234 | 3.2982 | 4.0698 | 4.0698 | 4.5842 | 4.5842 | 2019-03-23 07:00 | 1.6995 | 2.7851 | 4.5718 | 4.5718 | 4.5718 | 4.5718
2021-01-23 20:00 | 2.0806 | 2.5319 | 2.4773 | 2.6645 | 2.5241 | 2.7113 | 1.7776 | 3.0483 | 3.7614 | 3.7614 | 4.2368 | 4.2368 | 2019-03-23 08:00 | 1.9357 | 3.1723 | 5.2074 | 5.2074 | 5.2074 | 5.2074
2021-01-23 21:00 | 1.9176 | 2.3336 | 2.2832 | 2.4558 | 2.3264 | 2.499 | 1.6604 | 2.8474 | 3.5135 | 3.5135 | 3.9576 | 3.9576 | 2019-03-23 09:00 | 1.951 | 3.1973 | 5.2484 | 5.2484 | 5.2484 | 5.2484
2021-01-23 22:00 | 1.8462 | 2.2466 | 2.1982 | 2.3643 | 2.2397 | 2.4059 | 1.6261 | 2.7886 | 3.4409 | 3.4409 | 3.8758 | 3.8758 | 2019-03-23 10:00 | 2.0272 | 3.3222 | 5.4534 | 5.4534 | 5.4534 | 5.4534
2021-01-23 23:00 | 1.6776 | 2.0414 | 1.9974 | 2.1484 | 2.0351 | 2.1861 | 1.2804 | 2.1958 | 2.7094 | 2.7094 | 3.0519 | 3.0519 | 2019-03-23 11:00 | 2.0577 | 3.3721 | 5.5354 | 5.5354 | 5.5354 | 5.5354
2021-01-24 | 1.5747 | 1.9162 | 1.8749 | 2.0166 | 1.9103 | 2.0521 | 1.086 | 1.8623 | 2.298 | 2.298 | 2.5884 | 2.5884 | 2019-03-23 12:00 | 2.0805 | 3.4096 | 5.5969 | 5.5969 | 5.5969 | 5.5969
2021-01-24 01:00 | 1.3659 | 1.6622 | 1.6264 | 1.7493 | 1.6571 | 1.78 | 0.95739 | 1.6418 | 2.0258 | 2.0258 | 2.2819 | 2.2819 | 2019-03-23 13:00 | 2.1034 | 3.4471 | 5.6584 | 5.6584 | 5.6584 | 5.6584
2021-01-24 02:00 | 1.3661 | 1.6624 | 1.6265 | 1.7494 | 1.6572 | 1.7802 | 0.85965 | 1.4742 | 1.819 | 1.819 | 2.0489 | 2.0489 | 2019-03-23 14:00 | 2.0729 | 3.3971 | 5.5764 | 5.5764 | 5.5764 | 5.5764
2021-01-24 03:00 | 1.2946 | 1.5754 | 1.5414 | 1.6579 | 1.5706 | 1.6871 | 0.86879 | 1.4898 | 1.8384 | 1.8384 | 2.0707 | 2.0707 | 2019-03-23 15:00 | 2.1263 | 3.4845 | 5.7199 | 5.7199 | 5.7199 | 5.7199
2021-01-24 04:00 | 1.2232 | 1.4885 | 1.4564 | 1.5665 | 1.4839 | 1.594 | 0.81735 | 1.4016 | 1.7295 | 1.7295 | 1.9481 | 1.9481 | 2019-03-23 16:00 | 2.0729 | 3.3971 | 5.5764 | 5.5764 | 5.5764 | 5.5764
2021-01-24 05:00 | 1.2715 | 1.5473 | 1.5139 | 1.6284 | 1.5425 | 1.657 | 0.82021 | 1.4065 | 1.7356 | 1.7356 | 1.9549 | 1.9549 | 2019-03-23 17:00 | 2.0501 | 3.3597 | 5.5149 | 5.5149 | 5.5149 | 5.5149
2021-01-24 06:00 | 1.2718 | 1.5476 | 1.5142 | 1.6287 | 1.5428 | 1.6573 | 0.87491 | 1.5003 | 1.8513 | 1.8513 | 2.0853 | 2.0853 | 2019-03-23 18:00 | 1.8748 | 3.0724 | 5.0434 | 5.0434 | 5.0434 | 5.0434
2021-01-24 07:00 | 1.2918 | 1.5719 | 1.538 | 1.6543 | 1.5671 | 1.6834 | 1.0631 | 1.8231 | 2.2496 | 2.2496 | 2.5339 | 2.5339 | 2019-03-23 19:00 | 1.8595 | 3.0474 | 5.0024 | 5.0024 | 5.0024 | 5.0024
2021-01-24 08:00 | 1.4689 | 1.7876 | 1.749 | 1.8812 | 1.7821 | 1.9143 | 1.2232 | 2.0975 | 2.5882 | 2.5882 | 2.9154 | 2.9154 | 2019-03-23 20:00 | 1.8824 | 3.0849 | 5.0639 | 5.0639 | 5.0639 | 5.0639
2021-01-24 09:00 | 1.5718 | 1.9128 | 1.8715 | 2.013 | 1.9069 | 2.0483 | 1.489 | 2.5533 | 3.1506 | 3.1506 | 3.5489 | 3.5489 | 2019-03-23 21:00 | 1.6995 | 2.7851 | 4.5718 | 4.5718 | 4.5718 | 4.5718
2021-01-24 10:00 | 1.6233 | 1.9754 | 1.9327 | 2.0788 | 1.9693 | 2.1154 | 1.7433 | 2.9895 | 3.6889 | 3.6889 | 4.1551 | 4.1551 | 2019-03-23 22:00 | 1.6157 | 2.6478 | 4.3463 | 4.3463 | 4.3463 | 4.3463
2021-01-24 11:00 | 1.8433 | 2.2431 | 2.1948 | 2.3607 | 2.2362 | 2.4021 | 1.8805 | 3.2247 | 3.9791 | 3.9791 | 4.4821 | 4.4821 | 2019-03-23 23:00 | 1.5318 | 2.5104 | 4.1208 | 4.1208 | 4.1208 | 4.1208
2021-01-24 12:00 | 1.829 | 2.2258 | 2.1777 | 2.3424 | 2.2189 | 2.3835 | 1.9091 | 3.2737 | 4.0396 | 4.0396 | 4.5502 | 4.5502 | 2019-03-24 | 1.5166 | 2.4854 | 4.0798 | 4.0798 | 4.0798 | 4.0798
2021-01-24 13:00 | 1.9576 | 2.3823 | 2.3309 | 2.5071 | 2.3749 | 2.5511 | 1.8519 | 3.1757 | 3.9187 | 3.9187 | 4.4139 | 4.4139 | 2019-03-24 01:00 | 1.4632 | 2.398 | 3.9363 | 3.9363 | 3.9363 | 3.9363
2021-01-24 14:00 | 2.1034 | 2.5596 | 2.5044 | 2.6937 | 2.5517 | 2.741 | 1.9576 | 3.3571 | 4.1424 | 4.1424 | 4.666 | 4.666 | 2019-03-24 02:00 | 1.4251 | 2.3355 | 3.8338 | 3.8338 | 3.8338 | 3.8338
2021-01-24 15:00 | 2.192 | 2.6674 | 2.6099 | 2.8072 | 2.6592 | 2.8565 | 1.9405 | 3.3276 | 4.1061 | 4.1061 | 4.6251 | 4.6251 | 2019-03-24 03:00 | 1.4175 | 2.323 | 3.8133 | 3.8133 | 3.8133 | 3.8133
2021-01-24 16:00 | 2.1634 | 2.6327 | 2.5759 | 2.7706 | 2.6245 | 2.8192 | 1.9548 | 3.3522 | 4.1364 | 4.1364 | 4.6592 | 4.6592 | 2019-03-24 04:00 | 1.4251 | 2.3355 | 3.8338 | 3.8338 | 3.8338 | 3.8338
2021-01-24 17:00 | 2.312 | 2.8135 | 2.7528 | 2.9609 | 2.8048 | 3.0129 | 2.0834 | 3.5727 | 4.4085 | 4.4085 | 4.9657 | 4.9657 | 2019-03-24 05:00 | 1.4937 | 2.4479 | 4.0183 | 4.0183 | 4.0183 | 4.0183
2021-01-24 18:00 | 2.3892 | 2.9074 | 2.8447 | 3.0597 | 2.8984 | 3.1135 | 1.9319 | 3.3129 | 4.088 | 4.088 | 4.6047 | 4.6047 | 2019-03-24 06:00 | 1.608 | 2.6353 | 4.3258 | 4.3258 | 4.3258 | 4.3258
2021-01-24 19:00 | 2.332 | 2.8378 | 2.7766 | 2.9865 | 2.8291 | 3.039 | 1.8433 | 3.161 | 3.9005 | 3.9005 | 4.3935 | 4.3935 | 2019-03-24 07:00 | 1.6995 | 2.7851 | 4.5718 | 4.5718 | 4.5718 | 4.5718
2021-01-24 20:00 | 2.2234 | 2.7057 | 2.6473 | 2.8474 | 2.6973 | 2.8975 | 1.8233 | 3.1267 | 3.8582 | 3.8582 | 4.3458 | 4.3458 | 2019-03-24 08:00 | 1.9357 | 3.1723 | 5.2074 | 5.2074 | 5.2074 | 5.2074
2021-01-24 21:00 | 2.1863 | 2.6605 | 2.6031 | 2.7998 | 2.6523 | 2.849 | 1.7262 | 2.9601 | 3.6526 | 3.6526 | 4.1142 | 4.1142 | 2019-03-24 09:00 | 2.0348 | 3.3347 | 5.4739 | 5.4739 | 5.4739 | 5.4739
2021-01-24 22:00 | 1.952 | 2.3754 | 2.3241 | 2.4998 | 2.3681 | 2.5437 | 1.5147 | 2.5974 | 3.2051 | 3.2051 | 3.6102 | 3.6102 | 2019-03-24 10:00 | 2.0348 | 3.3347 | 5.4739 | 5.4739 | 5.4739 | 5.4739
2021-01-24 23:00 | 1.6977 | 2.0659 | 2.0214 | 2.1741 | 2.0596 | 2.2123 | 1.3294 | 2.2796 | 2.8129 | 2.8129 | 3.1685 | 3.1685 | 2019-03-24 11:00 | 2.1339 | 3.497 | 5.7404 | 5.7404 | 5.7404 | 5.7404
2021-01-25 | 1.6061 | 1.9545 | 1.9123 | 2.0569 | 1.9485 | 2.093 | 1.1804 | 2.0243 | 2.4978 | 2.4978 | 2.8135 | 2.8135 | 2019-03-24 12:00 | 2.2025 | 3.6094 | 5.9249 | 5.9249 | 5.9249 | 5.9249
2021-01-25 01:00 | 1.4604 | 1.7771 | 1.7388 | 1.8702 | 1.7716 | 1.9031 | 1.0147 | 1.74 | 2.1471 | 2.1471 | 2.4185 | 2.4185 | 2019-03-24 13:00 | 2.1949 | 3.597 | 5.9044 | 5.9044 | 5.9044 | 5.9044
2021-01-25 02:00 | 1.3804 | 1.6797 | 1.6435 | 1.7677 | 1.6746 | 1.7988 | 0.9632 | 1.6517 | 2.0381 | 2.0381 | 2.2958 | 2.2958 | 2019-03-24 14:00 | 2.2025 | 3.6094 | 5.9249 | 5.9249 | 5.9249 | 5.9249
2021-01-25 03:00 | 1.3832 | 1.6832 | 1.6469 | 1.7714 | 1.678 | 1.8025 | 0.91166 | 1.5634 | 1.9291 | 1.9291 | 2.1729 | 2.1729 | 2019-03-24 15:00 | 2.1872 | 3.5845 | 5.8839 | 5.8839 | 5.8839 | 5.8839
2021-01-25 04:00 | 1.3257 | 1.6132 | 1.5784 | 1.6978 | 1.6083 | 1.7276 | 0.88308 | 1.5143 | 1.8686 | 1.8686 | 2.1048 | 2.1048 | 2019-03-24 16:00 | 2.1415 | 3.5095 | 5.7609 | 5.7609 | 5.7609 | 5.7609
2021-01-25 05:00 | 1.7822 | 2.1688 | 2.122 | 2.2824 | 2.1621 | 2.3225 | 0.92023 | 1.5781 | 1.9472 | 1.9472 | 2.1933 | 2.1933 | 2019-03-24 17:00 | 1.9815 | 3.2472 | 5.3304 | 5.3304 | 5.3304 | 5.3304
2021-01-25 06:00 | 1.9095 | 2.3237 | 2.2736 | 2.4454 | 2.3165 | 2.4884 | 0.98311 | 1.6859 | 2.0803 | 2.0803 | 2.3432 | 2.3432 | 2019-03-24 18:00 | 1.7452 | 2.8601 | 4.6949 | 4.6949 | 4.6949 | 4.6949
2021-01-25 07:00 | 2.2624 | 2.7531 | 2.6937 | 2.8973 | 2.7446 | 2.9482 | 1.2489 | 2.1416 | 2.6427 | 2.6427 | 2.9767 | 2.9767 | 2019-03-24 19:00 | 1.8671 | 3.0599 | 5.0229 | 5.0229 | 5.0229 | 5.0229
2021-01-25 08:00 | 2.5492 | 3.1021 | 3.0352 | 3.2647 | 3.0926 | 3.322 | 1.3375 | 2.2936 | 2.8301 | 2.8301 | 3.1878 | 3.1878 | 2019-03-24 20:00 | 1.7605 | 2.8851 | 4.7359 | 4.7359 | 4.7359 | 4.7359
2021-01-25 09:00 | 2.9036 | 3.5334 | 3.4572 | 3.7185 | 3.5225 | 3.7838 | 1.5118 | 2.5925 | 3.199 | 3.199 | 3.6034 | 3.6034 | 2019-03-24 21:00 | 1.7147 | 2.8101 | 4.6128 | 4.6128 | 4.6128 | 4.6128
2021-01-25 10:00 | 2.9979 | 3.6482 | 3.5695 | 3.8393 | 3.6369 | 3.9067 | 1.6947 | 2.9062 | 3.586 | 3.586 | 4.0393 | 4.0393 | 2019-03-24 22:00 | 1.5928 | 2.6103 | 4.2848 | 4.2848 | 4.2848 | 4.2848
2021-01-25 11:00 | 3.1151 | 3.7907 | 3.709 | 3.9893 | 3.7791 | 4.0594 | 1.7662 | 3.0287 | 3.7372 | 3.7372 | 4.2096 | 4.2096 | 2019-03-24 23:00 | 1.5394 | 2.5229 | 4.1413 | 4.1413 | 4.1413 | 4.1413
2021-01-25 12:00 | 3.2837 | 3.9959 | 3.9097 | 4.2053 | 3.9836 | 4.2791 | 1.769 | 3.0336 | 3.7433 | 3.7433 | 4.2164 | 4.2164 | 2019-03-25 | 1.4632 | 2.398 | 3.9363 | 3.9363 | 3.9363 | 3.9363
2021-01-25 13:00 | 3.6009 | 4.382 | 4.2874 | 4.6115 | 4.3685 | 4.6925 | 1.9119 | 3.2786 | 4.0456 | 4.0456 | 4.557 | 4.557 | 2019-03-25 01:00 | 1.4632 | 2.398 | 3.9363 | 3.9363 | 3.9363 | 3.9363
2021-01-25 14:00 | 3.6895 | 4.4898 | 4.3929 | 4.725 | 4.4759 | 4.808 | 1.9262 | 3.3031 | 4.0759 | 4.0759 | 4.591 | 4.591 | 2019-03-25 02:00 | 1.4251 | 2.3355 | 3.8338 | 3.8338 | 3.8338 | 3.8338
2021-01-25 15:00 | 3.8096 | 4.6358 | 4.5358 | 4.8787 | 4.6216 | 4.9644 | 1.8862 | 3.2345 | 3.9912 | 3.9912 | 4.4957 | 4.4957 | 2019-03-25 03:00 | 1.4556 | 2.3855 | 3.9158 | 3.9158 | 3.9158 | 3.9158
2021-01-25 16:00 | 3.8038 | 4.6289 | 4.529 | 4.8714 | 4.6146 | 4.957 | 1.9434 | 3.3325 | 4.1122 | 4.1122 | 4.6319 | 4.6319 | 2019-03-25 04:00 | 1.509 | 2.4729 | 4.0593 | 4.0593 | 4.0593 | 4.0593
2021-01-25 17:00 | 3.7981 | 4.6219 | 4.5222 | 4.8641 | 4.6077 | 4.9495 | 2.1834 | 3.7442 | 4.6201 | 4.6201 | 5.2041 | 5.2041 | 2019-03-25 05:00 | 1.669 | 2.7352 | 4.4898 | 4.4898 | 4.4898 | 4.4898
2021-01-25 18:00 | 3.7553 | 4.5698 | 4.4712 | 4.8092 | 4.5557 | 4.8936 | 2.2177 | 3.803 | 4.6927 | 4.6927 | 5.2858 | 5.2858 | 2019-03-25 06:00 | 1.8671 | 3.0599 | 5.0229 | 5.0229 | 5.0229 | 5.0229
2021-01-25 19:00 | 3.5612 | 4.3336 | 4.2401 | 4.5606 | 4.3202 | 4.6407 | 2.2434 | 3.8471 | 4.7471 | 4.7471 | 5.3471 | 5.3471 | 2019-03-25 07:00 | 1.9357 | 3.1723 | 5.2074 | 5.2074 | 5.2074 | 5.2074
2021-01-25 20:00 | 2.9865 | 3.6342 | 3.5558 | 3.8246 | 3.623 | 3.8918 | 2.0691 | 3.5482 | 4.3782 | 4.3782 | 4.9316 | 4.9316 | 2019-03-25 08:00 | 2.3092 | 3.7843 | 6.212 | 6.212 | 6.212 | 6.212
2021-01-25 21:00 | 2.7693 | 3.3699 | 3.2972 | 3.5465 | 3.3596 | 3.6088 | 1.9033 | 3.2639 | 4.0275 | 4.0275 | 4.5365 | 4.5365 | 2019-03-25 09:00 | 2.3397 | 3.8343 | 6.294 | 6.294 | 6.294 | 6.294
2021-01-25 22:00 | 2.2263 | 2.7092 | 2.6507 | 2.8511 | 2.7008 | 2.9012 | 1.8719 | 3.21 | 3.961 | 3.961 | 4.4616 | 4.4616 | 2019-03-25 10:00 | 2.3397 | 3.8343 | 6.294 | 6.294 | 6.294 | 6.294
2021-01-25 23:00 | 1.9491 | 2.3718 | 2.3207 | 2.4961 | 2.3645 | 2.5399 | 1.5105 | 2.5902 | 3.1961 | 3.1961 | 3.6001 | 3.6001 | 2019-03-25 11:00 | 2.3549 | 3.8592 | 6.335 | 6.335 | 6.335 | 6.335
2021-01-26 | 1.7665 | 2.1496 | 2.1033 | 2.2622 | 2.143 | 2.302 | 1.3318 | 2.2838 | 2.818 | 2.818 | 3.1742 | 3.1742 | 2019-03-25 12:00 | 2.3854 | 3.9092 | 6.417 | 6.417 | 6.417 | 6.417
2021-01-26 01:00 | 1.6033 | 1.951 | 1.9089 | 2.0532 | 1.945 | 2.0893 | 1.0946 | 1.877 | 2.3161 | 2.3161 | 2.6089 | 2.6089 | 2019-03-25 13:00 | 2.3625 | 3.8717 | 6.3555 | 6.3555 | 6.3555 | 6.3555
2021-01-26 02:00 | 1.4804 | 1.8015 | 1.7626 | 1.8958 | 1.7959 | 1.9292 | 1.0546 | 1.8084 | 2.2315 | 2.2315 | 2.5135 | 2.5135 | 2019-03-25 14:00 | 2.3397 | 3.8343 | 6.294 | 6.294 | 6.294 | 6.294
2021-01-26 03:00 | 1.4604 | 1.7771 | 1.7388 | 1.8702 | 1.7716 | 1.9031 | 0.97453 | 1.6712 | 2.0621 | 2.0621 | 2.3228 | 2.3228 | 2019-03-25 15:00 | 2.1796 | 3.572 | 5.8634 | 5.8634 | 5.8634 | 5.8634
2021-01-26 04:00 | 1.3461 | 1.638 | 1.6027 | 1.7238 | 1.633 | 1.7541 | 0.99454 | 1.7055 | 2.1045 | 2.1045 | 2.3704 | 2.3704 | 2019-03-25 16:00 | 2.2253 | 3.6469 | 5.9865 | 5.9865 | 5.9865 | 5.9865
2021-01-26 05:00 | 1.3746 | 1.6728 | 1.6367 | 1.7604 | 1.6676 | 1.7914 | 0.94881 | 1.6271 | 2.0077 | 2.0077 | 2.2615 | 2.2615 | 2019-03-25 17:00 | 2.0729 | 3.3971 | 5.5764 | 5.5764 | 5.5764 | 5.5764
2021-01-26 06:00 | 1.3634 | 1.6591 | 1.6233 | 1.746 | 1.654 | 1.7767 | 1.0088 | 1.73 | 2.1347 | 2.1347 | 2.4045 | 2.4045 | 2019-03-25 18:00 | 1.951 | 3.1973 | 5.2484 | 5.2484 | 5.2484 | 5.2484
2021-01-26 07:00 | 1.5006 | 1.8261 | 1.7867 | 1.9218 | 1.8205 | 1.9555 | 1.1517 | 1.975 | 2.4371 | 2.4371 | 2.7451 | 2.7451 | 2019-03-25 19:00 | 1.73 | 2.8351 | 4.6538 | 4.6538 | 4.6538 | 4.6538
2021-01-26 08:00 | 1.6791 | 2.0432 | 1.9992 | 2.1503 | 2.0369 | 2.1881 | 1.4575 | 2.4994 | 3.0841 | 3.0841 | 3.4739 | 3.4739 | 2019-03-25 20:00 | 1.7528 | 2.8726 | 4.7154 | 4.7154 | 4.7154 | 4.7154
2021-01-26 09:00 | 1.7347 | 2.111 | 2.0655 | 2.2216 | 2.1045 | 2.2606 | 1.5175 | 2.6023 | 3.2111 | 3.2111 | 3.617 | 3.617 | 2019-03-25 21:00 | 1.608 | 2.6353 | 4.3258 | 4.3258 | 4.3258 | 4.3258
2021-01-26 10:00 | 1.8519 | 2.2536 | 2.205 | 2.3716 | 2.2466 | 2.4133 | 1.7805 | 3.0532 | 3.7675 | 3.7675 | 4.2436 | 4.2436 | 2019-03-25 22:00 | 1.5318 | 2.5104 | 4.1208 | 4.1208 | 4.1208 | 4.1208
2021-01-26 11:00 | 1.9319 | 2.351 | 2.3002 | 2.4741 | 2.3437 | 2.5176 | 1.7805 | 3.0532 | 3.7675 | 3.7675 | 4.2436 | 4.2436 | 2019-03-25 23:00 | 1.5166 | 2.4854 | 4.0798 | 4.0798 | 4.0798 | 4.0798
2021-01-26 12:00 | 2.1691 | 2.6396 | 2.5827 | 2.7779 | 2.6315 | 2.8267 | 1.8748 | 3.2149 | 3.967 | 3.967 | 4.4684 | 4.4684 | 2019-03-26 | 1.4785 | 2.4229 | 3.9773 | 3.9773 | 3.9773 | 3.9773
2021-01-26 13:00 | 2.1234 | 2.584 | 2.5282 | 2.7193 | 2.576 | 2.7671 | 1.8948 | 3.2492 | 4.0094 | 4.0094 | 4.5161 | 4.5161 | 2019-03-26 01:00 | 1.4556 | 2.3855 | 3.9158 | 3.9158 | 3.9158 | 3.9158
2021-01-26 14:00 | 2.0981 | 2.5531 | 2.498 | 2.6869 | 2.5453 | 2.7341 | 1.8119 | 3.1071 | 3.834 | 3.834 | 4.3186 | 4.3186 | 2019-03-26 02:00 | 1.4023 | 2.2981 | 3.7723 | 3.7723 | 3.7723 | 3.7723
2021-01-26 15:00 | 2.001 | 2.435 | 2.3825 | 2.5625 | 2.4275 | 2.6076 | 1.7262 | 2.9601 | 3.6526 | 3.6526 | 4.1142 | 4.1142 | 2019-03-26 03:00 | 1.4251 | 2.3355 | 3.8338 | 3.8338 | 3.8338 | 3.8338
2021-01-26 16:00 | 1.9634 | 2.3892 | 2.3377 | 2.5144 | 2.3818 | 2.5585 | 1.5949 | 2.735 | 3.3748 | 3.3748 | 3.8014 | 3.8014 | 2019-03-26 04:00 | 1.448 | 2.373 | 3.8953 | 3.8953 | 3.8953 | 3.8953
2021-01-26 17:00 | 2.0005 | 2.4344 | 2.3819 | 2.562 | 2.4269 | 2.607 | 1.6118 | 2.7641 | 3.4107 | 3.4107 | 3.8418 | 3.8418 | 2019-03-26 05:00 | 1.5318 | 2.5104 | 4.1208 | 4.1208 | 4.1208 | 4.1208
2021-01-26 18:00 | 2.0691 | 2.5179 | 2.4636 | 2.6498 | 2.5101 | 2.6963 | 1.6947 | 2.9062 | 3.586 | 3.586 | 4.0393 | 4.0393 | 2019-03-26 06:00 | 1.73 | 2.8351 | 4.6538 | 4.6538 | 4.6538 | 4.6538
2021-01-26 19:00 | 2.0491 | 2.4935 | 2.4398 | 2.6242 | 2.4859 | 2.6703 | 1.7119 | 2.9356 | 3.6223 | 3.6223 | 4.0802 | 4.0802 | 2019-03-26 07:00 | 1.829 | 2.9975 | 4.9204 | 4.9204 | 4.9204 | 4.9204
2021-01-26 20:00 | 2.0167 | 2.4541 | 2.4011 | 2.5826 | 2.4465 | 2.628 | 1.7176 | 2.9454 | 3.6344 | 3.6344 | 4.0938 | 4.0938 | 2019-03-26 08:00 | 2.0501 | 3.3597 | 5.5149 | 5.5149 | 5.5149 | 5.5149
2021-01-26 21:00 | 1.8691 | 2.2746 | 2.2255 | 2.3937 | 2.2675 | 2.4358 | 1.6465 | 2.8234 | 3.4839 | 3.4839 | 3.9242 | 3.9242 | 2019-03-26 09:00 | 2.0958 | 3.4346 | 5.6379 | 5.6379 | 5.6379 | 5.6379
2021-01-26 22:00 | 1.7892 | 2.1773 | 2.1303 | 2.2914 | 2.1706 | 2.3316 | 1.4694 | 2.5199 | 3.1094 | 3.1094 | 3.5024 | 3.5024 | 2019-03-26 10:00 | 2.0348 | 3.3347 | 5.4739 | 5.4739 | 5.4739 | 5.4739
2021-01-26 23:00 | 1.6348 | 1.9894 | 1.9465 | 2.0936 | 1.9833 | 2.1304 | 1.2953 | 2.2212 | 2.7408 | 2.7408 | 3.0872 | 3.0872 | 2019-03-26 11:00 | 2.1491 | 3.522 | 5.7814 | 5.7814 | 5.7814 | 5.7814
2021-01-27 | 1.489 | 1.8119 | 1.7728 | 1.9068 | 1.8063 | 1.9403 | 1.106 | 1.8966 | 2.3403 | 2.3403 | 2.6361 | 2.6361 | 2019-03-26 12:00 | 2.2025 | 3.6094 | 5.9249 | 5.9249 | 5.9249 | 5.9249
2021-01-27 01:00 | 1.3714 | 1.6689 | 1.6329 | 1.7563 | 1.6637 | 1.7871 | 0.92023 | 1.5781 | 1.9472 | 1.9472 | 2.1933 | 2.1933 | 2019-03-26 13:00 | 2.233 | 3.6594 | 6.007 | 6.007 | 6.007 | 6.007
2021-01-27 02:00 | 1.3203 | 1.6067 | 1.5721 | 1.6909 | 1.6018 | 1.7206 | 0.86594 | 1.4849 | 1.8323 | 1.8323 | 2.0639 | 2.0639 | 2019-03-26 14:00 | 2.1644 | 3.547 | 5.8224 | 5.8224 | 5.8224 | 5.8224
2021-01-27 03:00 | 1.2489 | 1.5198 | 1.487 | 1.5994 | 1.5151 | 1.6275 | 0.8345 | 1.431 | 1.7658 | 1.7658 | 1.989 | 1.989 | 2019-03-26 15:00 | 2.1644 | 3.547 | 5.8224 | 5.8224 | 5.8224 | 5.8224
2021-01-27 04:00 | 1.2432 | 1.5128 | 1.4802 | 1.5921 | 1.5082 | 1.62 | 0.85165 | 1.4604 | 1.8021 | 1.8021 | 2.0299 | 2.0299 | 2019-03-26 16:00 | 2.2101 | 3.6219 | 5.9454 | 5.9454 | 5.9454 | 5.9454
2021-01-27 05:00 | 1.485 | 1.8071 | 1.7681 | 1.9018 | 1.8016 | 1.9352 | 0.89411 | 1.5333 | 1.892 | 1.892 | 2.1311 | 2.1311 | 2019-03-26 17:00 | 2.0958 | 3.4346 | 5.6379 | 5.6379 | 5.6379 | 5.6379
2021-01-27 06:00 | 2.132 | 2.5944 | 2.5384 | 2.7303 | 2.5864 | 2.7783 | 1.2175 | 2.0877 | 2.5761 | 2.5761 | 2.9018 | 2.9018 | 2019-03-26 18:00 | 1.9281 | 3.1598 | 5.1869 | 5.1869 | 5.1869 | 5.1869
2021-01-27 07:00 | 2.2291 | 2.7126 | 2.6541 | 2.8547 | 2.7043 | 2.9049 | 1.3775 | 2.3622 | 2.9148 | 2.9148 | 3.2832 | 3.2832 | 2019-03-26 19:00 | 1.9205 | 3.1473 | 5.1664 | 5.1664 | 5.1664 | 5.1664
2021-01-27 08:00 | 2.4892 | 3.0291 | 2.9638 | 3.1878 | 3.0198 | 3.2438 | 1.3661 | 2.3426 | 2.8906 | 2.8906 | 3.256 | 3.256 | 2019-03-26 20:00 | 1.7452 | 2.8601 | 4.6949 | 4.6949 | 4.6949 | 4.6949
2021-01-27 09:00 | 2.4035 | 2.9248 | 2.8617 | 3.078 | 2.9158 | 3.1321 | 1.4804 | 2.5386 | 3.1325 | 3.1325 | 3.5284 | 3.5284 | 2019-03-26 21:00 | 1.6614 | 2.7227 | 4.4693 | 4.4693 | 4.4693 | 4.4693
2021-01-27 10:00 | 2.352 | 2.8622 | 2.8004 | 3.0121 | 2.8534 | 3.065 | 1.4518 | 2.4896 | 3.072 | 3.072 | 3.4603 | 3.4603 | 2019-03-26 22:00 | 1.6538 | 2.7102 | 4.4488 | 4.4488 | 4.4488 | 4.4488
2021-01-27 11:00 | 2.3778 | 2.8935 | 2.8311 | 3.0451 | 2.8846 | 3.0986 | 1.5861 | 2.7199 | 3.3563 | 3.3563 | 3.7805 | 3.7805 | 2019-03-26 23:00 | 1.5471 | 2.5353 | 4.1618 | 4.1618 | 4.1618 | 4.1618
2021-01-27 12:00 | 2.4292 | 2.9561 | 2.8923 | 3.1109 | 2.947 | 3.1656 | 1.489 | 2.5533 | 3.1506 | 3.1506 | 3.5489 | 3.5489 | 2019-03-27 | 1.4556 | 2.3855 | 3.9158 | 3.9158 | 3.9158 | 3.9158
2021-01-27 13:00 | 2.4092 | 2.9317 | 2.8685 | 3.0853 | 2.9227 | 3.1395 | 1.4804 | 2.5386 | 3.1325 | 3.1325 | 3.5284 | 3.5284 | 2019-03-27 01:00 | 1.4251 | 2.3355 | 3.8338 | 3.8338 | 3.8338 | 3.8338
2021-01-27 14:00 | 2.2577 | 2.7474 | 2.6882 | 2.8913 | 2.739 | 2.9421 | 1.4461 | 2.4798 | 3.0599 | 3.0599 | 3.4467 | 3.4467 | 2019-03-27 02:00 | 1.387 | 2.2731 | 3.7313 | 3.7313 | 3.7313 | 3.7313
2021-01-27 15:00 | 2.2234 | 2.7057 | 2.6473 | 2.8474 | 2.6973 | 2.8975 | 1.4146 | 2.4259 | 2.9934 | 2.9934 | 3.3718 | 3.3718 | 2019-03-27 03:00 | 1.3718 | 2.2481 | 3.6903 | 3.6903 | 3.6903 | 3.6903
2021-01-27 16:00 | 2.1291 | 2.5909 | 2.535 | 2.7266 | 2.5829 | 2.7746 | 1.4232 | 2.4406 | 3.0116 | 3.0116 | 3.3922 | 3.3922 | 2019-03-27 04:00 | 1.3718 | 2.2481 | 3.6903 | 3.6903 | 3.6903 | 3.6903
2021-01-27 17:00 | 2.1005 | 2.5561 | 2.501 | 2.69 | 2.5483 | 2.7373 | 1.4547 | 2.4945 | 3.0781 | 3.0781 | 3.4671 | 3.4671 | 2019-03-27 05:00 | 1.5394 | 2.5229 | 4.1413 | 4.1413 | 4.1413 | 4.1413
2021-01-27 18:00 | 2.1291 | 2.5909 | 2.535 | 2.7266 | 2.5829 | 2.7746 | 1.5375 | 2.6366 | 3.2534 | 3.2534 | 3.6647 | 3.6647 | 2019-03-27 06:00 | 1.7071 | 2.7976 | 4.5923 | 4.5923 | 4.5923 | 4.5923
2021-01-27 19:00 | 2.0273 | 2.467 | 2.4138 | 2.5963 | 2.4594 | 2.6419 | 1.5032 | 2.5778 | 3.1809 | 3.1809 | 3.5829 | 3.5829 | 2019-03-27 07:00 | 1.8519 | 3.0349 | 4.9819 | 4.9819 | 4.9819 | 4.9819
2021-01-27 20:00 | 1.8805 | 2.2884 | 2.239 | 2.4082 | 2.2813 | 2.4505 | 1.4775 | 2.5337 | 3.1265 | 3.1265 | 3.5216 | 3.5216 | 2019-03-27 08:00 | 1.9129 | 3.1348 | 5.1459 | 5.1459 | 5.1459 | 5.1459
2021-01-27 21:00 | 1.789 | 2.1771 | 2.1301 | 2.2911 | 2.1704 | 2.3314 | 1.3832 | 2.372 | 2.9269 | 2.9269 | 3.2968 | 3.2968 | 2019-03-27 09:00 | 2.0882 | 3.4221 | 5.6174 | 5.6174 | 5.6174 | 5.6174
2021-01-27 22:00 | 1.5649 | 1.9043 | 1.8632 | 2.0041 | 1.8985 | 2.0393 | 1.2918 | 2.2152 | 2.7334 | 2.7334 | 3.0789 | 3.0789 | 2019-03-27 10:00 | 2.1644 | 3.547 | 5.8224 | 5.8224 | 5.8224 | 5.8224
2021-01-27 23:00 | 1.4238 | 1.7327 | 1.6953 | 1.8234 | 1.7273 | 1.8555 | 1.1174 | 1.9162 | 2.3645 | 2.3645 | 2.6633 | 2.6633 | 2019-03-27 11:00 | 2.1644 | 3.547 | 5.8224 | 5.8224 | 5.8224 | 5.8224
2021-01-28 | 1.3405 | 1.6312 | 1.596 | 1.7167 | 1.6262 | 1.7468 | 0.9431 | 1.6173 | 1.9956 | 1.9956 | 2.2478 | 2.2478 | 2019-03-27 12:00 | 2.2177 | 3.6344 | 5.966 | 5.966 | 5.966 | 5.966
2021-01-28 01:00 | 1.2546 | 1.5267 | 1.4938 | 1.6067 | 1.522 | 1.6349 | 0.80306 | 1.3771 | 1.6993 | 1.6993 | 1.9141 | 1.9141 | 2019-03-27 13:00 | 2.1186 | 3.4721 | 5.6994 | 5.6994 | 5.6994 | 5.6994
2021-01-28 02:00 | 1.2059 | 1.4675 | 1.4358 | 1.5444 | 1.463 | 1.5715 | 0.79163 | 1.3575 | 1.6751 | 1.6751 | 1.8868 | 1.8868 | 2019-03-27 14:00 | 2.2101 | 3.6219 | 5.9454 | 5.9454 | 5.9454 | 5.9454
2021-01-28 03:00 | 1.206 | 1.4676 | 1.4359 | 1.5445 | 1.4631 | 1.5716 | 0.75165 | 1.289 | 1.5905 | 1.5905 | 1.7915 | 1.7915 | 2019-03-27 15:00 | 2.1644 | 3.547 | 5.8224 | 5.8224 | 5.8224 | 5.8224
2021-01-28 04:00 | 1.2403 | 1.5093 | 1.4768 | 1.5884 | 1.5047 | 1.6163 | 0.76787 | 1.3168 | 1.6248 | 1.6248 | 1.8302 | 1.8302 | 2019-03-27 16:00 | 2.1872 | 3.5845 | 5.8839 | 5.8839 | 5.8839 | 5.8839
2021-01-28 05:00 | 1.3653 | 1.6614 | 1.6256 | 1.7484 | 1.6563 | 1.7792 | 0.80878 | 1.3869 | 1.7114 | 1.7114 | 1.9277 | 1.9277 | 2019-03-27 17:00 | 2.1415 | 3.5095 | 5.7609 | 5.7609 | 5.7609 | 5.7609
2021-01-28 06:00 | 1.5886 | 1.9331 | 1.8914 | 2.0344 | 1.9272 | 2.0701 | 1.0831 | 1.8574 | 2.2919 | 2.2919 | 2.5816 | 2.5816 | 2019-03-27 18:00 | 2.0043 | 3.2847 | 5.3919 | 5.3919 | 5.3919 | 5.3919
2021-01-28 07:00 | 1.9519 | 2.3753 | 2.3241 | 2.4997 | 2.368 | 2.5437 | 1.2232 | 2.0975 | 2.5882 | 2.5882 | 2.9154 | 2.9154 | 2019-03-27 19:00 | 2.0119 | 3.2972 | 5.4124 | 5.4124 | 5.4124 | 5.4124
2021-01-28 08:00 | 2.1891 | 2.664 | 2.6065 | 2.8035 | 2.6557 | 2.8528 | 1.286 | 2.2054 | 2.7213 | 2.7213 | 3.0652 | 3.0652 | 2019-03-27 20:00 | 1.7986 | 2.9475 | 4.8384 | 4.8384 | 4.8384 | 4.8384
2021-01-28 09:00 | 2.1148 | 2.5735 | 2.518 | 2.7083 | 2.5656 | 2.7559 | 1.3232 | 2.2691 | 2.7999 | 2.7999 | 3.1538 | 3.1538 | 2019-03-27 21:00 | 1.7376 | 2.8476 | 4.6744 | 4.6744 | 4.6744 | 4.6744
2021-01-28 10:00 | 2.1434 | 2.6083 | 2.552 | 2.7449 | 2.6003 | 2.7932 | 1.4461 | 2.4798 | 3.0599 | 3.0599 | 3.4467 | 3.4467 | 2019-03-27 22:00 | 1.6309 | 2.6727 | 4.3873 | 4.3873 | 4.3873 | 4.3873
2021-01-28 11:00 | 2.1949 | 2.6709 | 2.6133 | 2.8108 | 2.6627 | 2.8602 | 1.4547 | 2.4945 | 3.0781 | 3.0781 | 3.4671 | 3.4671 | 2019-03-27 23:00 | 1.5547 | 2.5478 | 4.1823 | 4.1823 | 4.1823 | 4.1823
2021-01-28 12:00 | 2.1863 | 2.6605 | 2.6031 | 2.7998 | 2.6523 | 2.849 | 1.4689 | 2.519 | 3.1083 | 3.1083 | 3.5012 | 3.5012 | 2019-03-28 | 1.5013 | 2.4604 | 4.0388 | 4.0388 | 4.0388 | 4.0388
2021-01-28 13:00 | 2.1234 | 2.584 | 2.5282 | 2.7193 | 2.576 | 2.7671 | 1.4689 | 2.519 | 3.1083 | 3.1083 | 3.5012 | 3.5012 | 2019-03-28 01:00 | 1.4709 | 2.4105 | 3.9568 | 3.9568 | 3.9568 | 3.9568
2021-01-28 14:00 | 2.0018 | 2.4359 | 2.3834 | 2.5635 | 2.4284 | 2.6086 | 1.489 | 2.5533 | 3.1506 | 3.1506 | 3.5489 | 3.5489 | 2019-03-28 02:00 | 1.4404 | 2.3605 | 3.8748 | 3.8748 | 3.8748 | 3.8748
2021-01-28 15:00 | 1.9176 | 2.3336 | 2.2832 | 2.4558 | 2.3264 | 2.499 | 1.3203 | 2.2642 | 2.7939 | 2.7939 | 3.147 | 3.147 | 2019-03-28 03:00 | 1.4785 | 2.4229 | 3.9773 | 3.9773 | 3.9773 | 3.9773
2021-01-28 16:00 | 1.9119 | 2.3266 | 2.2764 | 2.4485 | 2.3194 | 2.4915 | 1.3575 | 2.3279 | 2.8725 | 2.8725 | 3.2355 | 3.2355 | 2019-03-28 04:00 | 1.5394 | 2.5229 | 4.1413 | 4.1413 | 4.1413 | 4.1413
2021-01-28 17:00 | 2.0462 | 2.4901 | 2.4364 | 2.6205 | 2.4824 | 2.6666 | 1.4118 | 2.421 | 2.9874 | 2.9874 | 3.3649 | 3.3649 | 2019-03-28 05:00 | 1.7376 | 2.8476 | 4.6744 | 4.6744 | 4.6744 | 4.6744
2021-01-28 18:00 | 2.0691 | 2.5179 | 2.4636 | 2.6498 | 2.5101 | 2.6963 | 1.4175 | 2.4308 | 2.9995 | 2.9995 | 3.3786 | 3.3786 | 2019-03-28 06:00 | 1.8748 | 3.0724 | 5.0434 | 5.0434 | 5.0434 | 5.0434
2021-01-28 19:00 | 1.9572 | 2.3817 | 2.3303 | 2.5065 | 2.3744 | 2.5505 | 1.5347 | 2.6317 | 3.2474 | 3.2474 | 3.6578 | 3.6578 | 2019-03-28 07:00 | 2.0043 | 3.2847 | 5.3919 | 5.3919 | 5.3919 | 5.3919
2021-01-28 20:00 | 1.8748 | 2.2814 | 2.2322 | 2.4009 | 2.2744 | 2.4431 | 1.5204 | 2.6072 | 3.2172 | 3.2172 | 3.6238 | 3.6238 | 2019-03-28 08:00 | 2.1872 | 3.5845 | 5.8839 | 5.8839 | 5.8839 | 5.8839
2021-01-28 21:00 | 1.7613 | 2.1433 | 2.0971 | 2.2556 | 2.1367 | 2.2952 | 1.4547 | 2.4945 | 3.0781 | 3.0781 | 3.4671 | 3.4671 | 2019-03-28 09:00 | 2.1644 | 3.547 | 5.8224 | 5.8224 | 5.8224 | 5.8224
2021-01-28 22:00 | 1.6604 | 2.0206 | 1.977 | 2.1264 | 2.0143 | 2.1638 | 1.1961 | 2.0512 | 2.531 | 2.531 | 2.8509 | 2.8509 | 2019-03-28 10:00 | 2.2634 | 3.7094 | 6.089 | 6.089 | 6.089 | 6.089
2021-01-28 23:00 | 1.5118 | 1.8397 | 1.8 | 1.9361 | 1.8341 | 1.9701 | 1.0346 | 1.7741 | 2.1891 | 2.1891 | 2.4658 | 2.4658 | 2019-03-28 11:00 | 2.1796 | 3.572 | 5.8634 | 5.8634 | 5.8634 | 5.8634
2021-01-29 | 1.4004 | 1.7041 | 1.6673 | 1.7934 | 1.6988 | 1.8249 | 0.88423 | 1.5163 | 1.871 | 1.871 | 2.1075 | 2.1075 | 2019-03-28 12:00 | 2.2939 | 3.7593 | 6.171 | 6.171 | 6.171 | 6.171
2021-01-29 01:00 | 1.2346 | 1.5024 | 1.47 | 1.5811 | 1.4978 | 1.6089 | 0.76877 | 1.3183 | 1.6267 | 1.6267 | 1.8323 | 1.8323 | 2019-03-28 13:00 | 2.2406 | 3.6719 | 6.0275 | 6.0275 | 6.0275 | 6.0275
2021-01-29 02:00 | 1.226 | 1.492 | 1.4598 | 1.5701 | 1.4874 | 1.5977 | 0.74019 | 1.2693 | 1.5662 | 1.5662 | 1.7642 | 1.7642 | 2019-03-28 14:00 | 2.3015 | 3.7718 | 6.1915 | 6.1915 | 6.1915 | 6.1915
2021-01-29 03:00 | 1.1946 | 1.4537 | 1.4223 | 1.5298 | 1.4492 | 1.5567 | 0.73126 | 1.254 | 1.5474 | 1.5474 | 1.7429 | 1.7429 | 2019-03-28 15:00 | 2.2482 | 3.6844 | 6.048 | 6.048 | 6.048 | 6.048
2021-01-29 04:00 | 1.1746 | 1.4294 | 1.3985 | 1.5042 | 1.4249 | 1.5307 | 0.74019 | 1.2693 | 1.5662 | 1.5662 | 1.7642 | 1.7642 | 2019-03-28 16:00 | 2.2634 | 3.7094 | 6.089 | 6.089 | 6.089 | 6.089
2021-01-29 05:00 | 1.4423 | 1.7551 | 1.7172 | 1.847 | 1.7497 | 1.8795 | 0.77439 | 1.328 | 1.6386 | 1.6386 | 1.8457 | 1.8457 | 2019-03-28 17:00 | 2.1415 | 3.5095 | 5.7609 | 5.7609 | 5.7609 | 5.7609
2021-01-29 06:00 | 1.6275 | 1.9805 | 1.9378 | 2.0842 | 1.9744 | 2.1208 | 0.96596 | 1.6565 | 2.044 | 2.044 | 2.3023 | 2.3023 | 2019-03-28 18:00 | 2.0119 | 3.2972 | 5.4124 | 5.4124 | 5.4124 | 5.4124
2021-01-29 07:00 | 1.9592 | 2.3841 | 2.3327 | 2.509 | 2.3768 | 2.5531 | 1.226 | 2.1024 | 2.5943 | 2.5943 | 2.9222 | 2.9222 | 2019-03-28 19:00 | 2.0272 | 3.3222 | 5.4534 | 5.4534 | 5.4534 | 5.4534
2021-01-29 08:00 | 1.9977 | 2.4309 | 2.3785 | 2.5583 | 2.4235 | 2.6032 | 1.365 | 2.3408 | 2.8884 | 2.8884 | 3.2535 | 3.2535 | 2019-03-28 20:00 | 1.9357 | 3.1723 | 5.2074 | 5.2074 | 5.2074 | 5.2074
2021-01-29 09:00 | 2.0205 | 2.4588 | 2.4057 | 2.5876 | 2.4512 | 2.633 | 1.3975 | 2.3965 | 2.9571 | 2.9571 | 3.3309 | 3.3309 | 2019-03-28 21:00 | 1.7605 | 2.8851 | 4.7359 | 4.7359 | 4.7359 | 4.7359
2021-01-29 10:00 | 2.0491 | 2.4935 | 2.4398 | 2.6242 | 2.4859 | 2.6703 | 1.4575 | 2.4994 | 3.0841 | 3.0841 | 3.4739 | 3.4739 | 2019-03-28 22:00 | 1.7376 | 2.8476 | 4.6744 | 4.6744 | 4.6744 | 4.6744
2021-01-29 11:00 | 2.1348 | 2.5979 | 2.5418 | 2.734 | 2.5899 | 2.782 | 1.4261 | 2.4455 | 3.0176 | 3.0176 | 3.399 | 3.399 | 2019-03-28 23:00 | 1.6614 | 2.7227 | 4.4693 | 4.4693 | 4.4693 | 4.4693
2021-01-29 12:00 | 2.092 | 2.5457 | 2.4908 | 2.6791 | 2.5379 | 2.7261 | 1.4289 | 2.4504 | 3.0236 | 3.0236 | 3.4058 | 3.4058 | 2019-03-29 | 1.5013 | 2.4604 | 4.0388 | 4.0388 | 4.0388 | 4.0388
2021-01-29 13:00 | 2.0662 | 2.5144 | 2.4602 | 2.6461 | 2.5067 | 2.6926 | 1.5661 | 2.6856 | 3.3139 | 3.3139 | 3.7328 | 3.7328 | 2019-03-29 01:00 | 1.4861 | 2.4354 | 3.9978 | 3.9978 | 3.9978 | 3.9978
2021-01-29 14:00 | 2.112 | 2.5701 | 2.5146 | 2.7047 | 2.5621 | 2.7522 | 1.3861 | 2.3769 | 2.9329 | 2.9329 | 3.3036 | 3.3036 | 2019-03-29 02:00 | 1.4099 | 2.3105 | 3.7928 | 3.7928 | 3.7928 | 3.7928
2021-01-29 15:00 | 2.1063 | 2.5631 | 2.5078 | 2.6974 | 2.5552 | 2.7448 | 1.3375 | 2.2936 | 2.8301 | 2.8301 | 3.1878 | 3.1878 | 2019-03-29 03:00 | 1.4404 | 2.3605 | 3.8748 | 3.8748 | 3.8748 | 3.8748
2021-01-29 16:00 | 1.9291 | 2.3475 | 2.2968 | 2.4705 | 2.3402 | 2.5139 | 1.4146 | 2.4259 | 2.9934 | 2.9934 | 3.3718 | 3.3718 | 2019-03-29 04:00 | 1.4937 | 2.4479 | 4.0183 | 4.0183 | 4.0183 | 4.0183
2021-01-29 17:00 | 1.9662 | 2.3927 | 2.3411 | 2.518 | 2.3853 | 2.5623 | 1.4947 | 2.5631 | 3.1627 | 3.1627 | 3.5625 | 3.5625 | 2019-03-29 05:00 | 1.6004 | 2.6228 | 4.3053 | 4.3053 | 4.3053 | 4.3053
2021-01-29 18:00 | 2.0291 | 2.4692 | 2.4159 | 2.5986 | 2.4616 | 2.6442 | 1.6204 | 2.7788 | 3.4288 | 3.4288 | 3.8622 | 3.8622 | 2019-03-29 06:00 | 1.8367 | 3.0099 | 4.9409 | 4.9409 | 4.9409 | 4.9409
2021-01-29 19:00 | 1.8776 | 2.2849 | 2.2356 | 2.4046 | 2.2778 | 2.4468 | 1.5918 | 2.7297 | 3.3683 | 3.3683 | 3.7941 | 3.7941 | 2019-03-29 07:00 | 1.8824 | 3.0849 | 5.0639 | 5.0639 | 5.0639 | 5.0639
2021-01-29 20:00 | 1.8433 | 2.2431 | 2.1948 | 2.3607 | 2.2362 | 2.4021 | 1.5718 | 2.6954 | 3.326 | 3.326 | 3.7464 | 3.7464 | 2019-03-29 08:00 | 2.1263 | 3.4845 | 5.7199 | 5.7199 | 5.7199 | 5.7199
2021-01-29 21:00 | 1.7805 | 2.1666 | 2.1199 | 2.2801 | 2.16 | 2.3202 | 1.4947 | 2.5631 | 3.1627 | 3.1627 | 3.5625 | 3.5625 | 2019-03-29 09:00 | 2.2406 | 3.6719 | 6.0275 | 6.0275 | 6.0275 | 6.0275
2021-01-29 22:00 | 1.5867 | 1.9309 | 1.8892 | 2.032 | 1.9249 | 2.0677 | 1.3032 | 2.2348 | 2.7576 | 2.7576 | 3.1061 | 3.1061 | 2019-03-29 10:00 | 2.1949 | 3.597 | 5.9044 | 5.9044 | 5.9044 | 5.9044
2021-01-29 23:00 | 1.5032 | 1.8293 | 1.7898 | 1.9251 | 1.8237 | 1.9589 | 1.0888 | 1.8672 | 2.304 | 2.304 | 2.5952 | 2.5952 | 2019-03-29 11:00 | 2.3092 | 3.7843 | 6.212 | 6.212 | 6.212 | 6.212
2021-01-30 | 1.3614 | 1.6567 | 1.621 | 1.7435 | 1.6516 | 1.7742 | 0.98621 | 1.6912 | 2.0868 | 2.0868 | 2.3506 | 2.3506 | 2019-03-29 12:00 | 2.3244 | 3.8093 | 6.253 | 6.253 | 6.253 | 6.253
2021-01-30 01:00 | 1.2546 | 1.5267 | 1.4938 | 1.6067 | 1.522 | 1.6349 | 0.81121 | 1.3911 | 1.7165 | 1.7165 | 1.9335 | 1.9335 | 2019-03-29 13:00 | 2.4235 | 3.9716 | 6.5195 | 6.5195 | 6.5195 | 6.5195
2021-01-30 02:00 | 1.2146 | 1.478 | 1.4462 | 1.5555 | 1.4735 | 1.5828 | 0.81164 | 1.3918 | 1.7174 | 1.7174 | 1.9345 | 1.9345 | 2019-03-29 14:00 | 2.4006 | 3.9342 | 6.458 | 6.458 | 6.458 | 6.458
2021-01-30 03:00 | 1.2146 | 1.478 | 1.4462 | 1.5555 | 1.4735 | 1.5828 | 0.72304 | 1.2399 | 1.53 | 1.53 | 1.7233 | 1.7233 | 2019-03-29 15:00 | 2.332 | 3.8218 | 6.2735 | 6.2735 | 6.2735 | 6.2735
2021-01-30 04:00 | 1.1832 | 1.4398 | 1.4087 | 1.5152 | 1.4353 | 1.5418 | 0.76591 | 1.3134 | 1.6207 | 1.6207 | 1.8255 | 1.8255 | 2019-03-29 16:00 | 2.3549 | 3.8592 | 6.335 | 6.335 | 6.335 | 6.335
2021-01-30 05:00 | 1.2831 | 1.5614 | 1.5277 | 1.6432 | 1.5566 | 1.6721 | 0.73733 | 1.2644 | 1.5602 | 1.5602 | 1.7574 | 1.7574 | 2019-03-29 17:00 | 2.1263 | 3.4845 | 5.7199 | 5.7199 | 5.7199 | 5.7199
2021-01-30 06:00 | 1.2841 | 1.5626 | 1.5289 | 1.6444 | 1.5577 | 1.6733 | 0.84021 | 1.4408 | 1.7779 | 1.7779 | 2.0026 | 2.0026 | 2019-03-29 18:00 | 2.0043 | 3.2847 | 5.3919 | 5.3919 | 5.3919 | 5.3919
2021-01-30 07:00 | 1.4461 | 1.7597 | 1.7218 | 1.8519 | 1.7543 | 1.8845 | 1.0288 | 1.7643 | 2.177 | 2.177 | 2.4522 | 2.4522 | 2019-03-29 19:00 | 1.8595 | 3.0474 | 5.0024 | 5.0024 | 5.0024 | 5.0024
2021-01-30 08:00 | 1.4861 | 1.8084 | 1.7694 | 1.9032 | 1.8029 | 1.9366 | 1.2603 | 2.1613 | 2.6669 | 2.6669 | 3.0039 | 3.0039 | 2019-03-29 20:00 | 1.8214 | 2.985 | 4.8999 | 4.8999 | 4.8999 | 4.8999
2021-01-30 09:00 | 1.649 | 2.0067 | 1.9634 | 2.1118 | 2.0005 | 2.1489 | 1.3489 | 2.3132 | 2.8543 | 2.8543 | 3.2151 | 3.2151 | 2019-03-29 21:00 | 1.8214 | 2.985 | 4.8999 | 4.8999 | 4.8999 | 4.8999
2021-01-30 10:00 | 1.529 | 1.8606 | 1.8205 | 1.9581 | 1.8549 | 1.9925 | 1.4975 | 2.568 | 3.1688 | 3.1688 | 3.5693 | 3.5693 | 2019-03-29 22:00 | 1.8367 | 3.0099 | 4.9409 | 4.9409 | 4.9409 | 4.9409
2021-01-30 11:00 | 1.629 | 1.9823 | 1.9396 | 2.0862 | 1.9762 | 2.1228 | 1.5604 | 2.6758 | 3.3018 | 3.3018 | 3.7192 | 3.7192 | 2019-03-29 23:00 | 1.7223 | 2.8226 | 4.6333 | 4.6333 | 4.6333 | 4.6333
2021-01-30 12:00 | 1.7004 | 2.0693 | 2.0246 | 2.1777 | 2.0629 | 2.2159 | 1.5661 | 2.6856 | 3.3139 | 3.3139 | 3.7328 | 3.7328 | 2019-03-30 | 1.669 | 2.7352 | 4.4898 | 4.4898 | 4.4898 | 4.4898
2021-01-30 13:00 | 1.6804 | 2.0449 | 2.0008 | 2.152 | 2.0386 | 2.1898 | 1.6147 | 2.769 | 3.4167 | 3.4167 | 3.8486 | 3.8486 | 2019-03-30 01:00 | 1.6385 | 2.6852 | 4.4078 | 4.4078 | 4.4078 | 4.4078
2021-01-30 14:00 | 1.729 | 2.104 | 2.0586 | 2.2143 | 2.0976 | 2.2532 | 1.5375 | 2.6366 | 3.2534 | 3.2534 | 3.6647 | 3.6647 | 2019-03-30 02:00 | 1.5852 | 2.5978 | 4.2643 | 4.2643 | 4.2643 | 4.2643
2021-01-30 15:00 | 1.5061 | 1.8328 | 1.7932 | 1.9288 | 1.8271 | 1.9627 | 1.4518 | 2.4896 | 3.072 | 3.072 | 3.4603 | 3.4603 | 2019-03-30 03:00 | 1.5852 | 2.5978 | 4.2643 | 4.2643 | 4.2643 | 4.2643
2021-01-30 16:00 | 1.609 | 1.958 | 1.9157 | 2.0605 | 1.9519 | 2.0967 | 1.5718 | 2.6954 | 3.326 | 3.326 | 3.7464 | 3.7464 | 2019-03-30 04:00 | 1.5928 | 2.6103 | 4.2848 | 4.2848 | 4.2848 | 4.2848
2021-01-30 17:00 | 1.6318 | 1.9858 | 1.943 | 2.0898 | 1.9797 | 2.1265 | 1.6719 | 2.867 | 3.5377 | 3.5377 | 3.9848 | 3.9848 | 2019-03-30 05:00 | 1.6538 | 2.7102 | 4.4488 | 4.4488 | 4.4488 | 4.4488
2021-01-30 18:00 | 1.8062 | 2.1979 | 2.1505 | 2.3131 | 2.1912 | 2.3537 | 1.7004 | 2.916 | 3.5981 | 3.5981 | 4.0529 | 4.0529 | 2019-03-30 06:00 | 1.8519 | 3.0349 | 4.9819 | 4.9819 | 4.9819 | 4.9819
2021-01-30 19:00 | 1.8348 | 2.2327 | 2.1845 | 2.3497 | 2.2258 | 2.391 | 1.689 | 2.8964 | 3.574 | 3.574 | 4.0257 | 4.0257 | 2019-03-30 07:00 | 1.8595 | 3.0474 | 5.0024 | 5.0024 | 5.0024 | 5.0024
2021-01-30 20:00 | 1.7719 | 2.1562 | 2.1097 | 2.2692 | 2.1496 | 2.309 | 1.5775 | 2.7052 | 3.3381 | 3.3381 | 3.76 | 3.76 | 2019-03-30 08:00 | 2.1186 | 3.4721 | 5.6994 | 5.6994 | 5.6994 | 5.6994
2021-01-30 21:00 | 1.7633 | 2.1458 | 2.0995 | 2.2582 | 2.1392 | 2.2979 | 1.5604 | 2.6758 | 3.3018 | 3.3018 | 3.7192 | 3.7192 | 2019-03-30 09:00 | 2.1872 | 3.5845 | 5.8839 | 5.8839 | 5.8839 | 5.8839
2021-01-30 22:00 | 1.6038 | 1.9516 | 1.9095 | 2.0539 | 1.9456 | 2.09 | 1.5118 | 2.5925 | 3.199 | 3.199 | 3.6034 | 3.6034 | 2019-03-30 10:00 | 2.1034 | 3.4471 | 5.6584 | 5.6584 | 5.6584 | 5.6584
2021-01-30 23:00 | 1.5347 | 1.8675 | 1.8273 | 1.9654 | 1.8618 | 1.9999 | 1.1896 | 2.0399 | 2.5172 | 2.5172 | 2.8353 | 2.8353 | 2019-03-30 11:00 | 2.0882 | 3.4221 | 5.6174 | 5.6174 | 5.6174 | 5.6174
2021-01-31 | 1.4604 | 1.7771 | 1.7388 | 1.8702 | 1.7716 | 1.9031 | 1.0914 | 1.8716 | 2.3095 | 2.3095 | 2.6014 | 2.6014 | 2019-03-30 12:00 | 1.9967 | 3.2722 | 5.3714 | 5.3714 | 5.3714 | 5.3714
2021-01-31 01:00 | 1.3346 | 1.6241 | 1.5891 | 1.7092 | 1.6191 | 1.7392 | 0.85719 | 1.4699 | 1.8138 | 1.8138 | 2.0431 | 2.0431 | 2019-03-30 13:00 | 1.9738 | 3.2348 | 5.3099 | 5.3099 | 5.3099 | 5.3099
2021-01-31 02:00 | 1.2517 | 1.5232 | 1.4904 | 1.603 | 1.5186 | 1.6312 | 0.82878 | 1.4212 | 1.7537 | 1.7537 | 1.9754 | 1.9754 | 2019-03-30 14:00 | 2.0119 | 3.2972 | 5.4124 | 5.4124 | 5.4124 | 5.4124
2021-01-31 03:00 | 1.1746 | 1.4294 | 1.3985 | 1.5042 | 1.4249 | 1.5307 | 0.75734 | 1.2987 | 1.6025 | 1.6025 | 1.8051 | 1.8051 | 2019-03-30 15:00 | 1.9129 | 3.1348 | 5.1459 | 5.1459 | 5.1459 | 5.1459
2021-01-31 04:00 | 1.1508 | 1.4005 | 1.3703 | 1.4738 | 1.3961 | 1.4997 | 0.79399 | 1.3616 | 1.6801 | 1.6801 | 1.8924 | 1.8924 | 2019-03-30 16:00 | 1.9281 | 3.1598 | 5.1869 | 5.1869 | 5.1869 | 5.1869
2021-01-31 05:00 | 1.2055 | 1.467 | 1.4354 | 1.5439 | 1.4625 | 1.571 | 0.79449 | 1.3624 | 1.6811 | 1.6811 | 1.8936 | 1.8936 | 2019-03-30 17:00 | 1.8214 | 2.985 | 4.8999 | 4.8999 | 4.8999 | 4.8999
2021-01-31 06:00 | 1.2203 | 1.485 | 1.453 | 1.5628 | 1.4804 | 1.5902 | 0.85736 | 1.4702 | 1.8142 | 1.8142 | 2.0435 | 2.0435 | 2019-03-30 18:00 | 1.73 | 2.8351 | 4.6538 | 4.6538 | 4.6538 | 4.6538
2021-01-31 07:00 | 1.3518 | 1.645 | 1.6095 | 1.7311 | 1.6399 | 1.7616 | 0.9431 | 1.6173 | 1.9956 | 1.9956 | 2.2478 | 2.2478 | 2019-03-30 19:00 | 1.6995 | 2.7851 | 4.5718 | 4.5718 | 4.5718 | 4.5718
2021-01-31 08:00 | 1.4375 | 1.7493 | 1.7116 | 1.8409 | 1.7439 | 1.8733 | 1.1289 | 1.9358 | 2.3887 | 2.3887 | 2.6906 | 2.6906 | 2019-03-30 20:00 | 1.6995 | 2.7851 | 4.5718 | 4.5718 | 4.5718 | 4.5718
2021-01-31 09:00 | 1.5661 | 1.9058 | 1.8647 | 2.0056 | 1.8999 | 2.0409 | 1.2662 | 2.1713 | 2.6793 | 2.6793 | 3.0179 | 3.0179 | 2019-03-30 21:00 | 1.6233 | 2.6602 | 4.3668 | 4.3668 | 4.3668 | 4.3668
2021-01-31 10:00 | 1.6404 | 1.9962 | 1.9532 | 2.1008 | 1.9901 | 2.1377 | 1.5518 | 2.6611 | 3.2837 | 3.2837 | 3.6987 | 3.6987 | 2019-03-30 22:00 | 1.5318 | 2.5104 | 4.1208 | 4.1208 | 4.1208 | 4.1208
2021-01-31 11:00 | 1.7062 | 2.0762 | 2.0314 | 2.185 | 2.0698 | 2.2234 | 1.5518 | 2.6611 | 3.2837 | 3.2837 | 3.6987 | 3.6987 | 2019-03-30 23:00 | 1.448 | 2.373 | 3.8953 | 3.8953 | 3.8953 | 3.8953
2021-01-31 12:00 | 1.5747 | 1.9162 | 1.8749 | 2.0166 | 1.9103 | 2.0521 | 1.609 | 2.7592 | 3.4046 | 3.4046 | 3.8349 | 3.8349 | 2019-03-31 | 1.4023 | 2.2981 | 3.7723 | 3.7723 | 3.7723 | 3.7723
2021-01-31 13:00 | 1.4804 | 1.8015 | 1.7626 | 1.8958 | 1.7959 | 1.9292 | 1.5718 | 2.6954 | 3.326 | 3.326 | 3.7464 | 3.7464 | 2019-03-31 01:00 | 1.4175 | 2.323 | 3.8133 | 3.8133 | 3.8133 | 3.8133
2021-01-31 14:00 | 1.3723 | 1.67 | 1.634 | 1.7575 | 1.6648 | 1.7884 | 1.4947 | 2.5631 | 3.1627 | 3.1627 | 3.5625 | 3.5625 | 2019-03-31 02:00 | 1.3565 | 2.2231 | 3.6493 | 3.6493 | 3.6493 | 3.6493
2021-01-31 15:00 | 1.4689 | 1.7876 | 1.749 | 1.8812 | 1.7821 | 1.9143 | 1.5628 | 2.6799 | 3.3068 | 3.3068 | 3.7248 | 3.7248 | 2019-03-31 03:00 | 1.3794 | 2.2606 | 3.7108 | 3.7108 | 3.7108 | 3.7108
2021-01-31 16:00 | 1.4861 | 1.8084 | 1.7694 | 1.9032 | 1.8029 | 1.9366 | 1.6204 | 2.7786 | 3.4287 | 3.4287 | 3.862 | 3.862 | 2019-03-31 04:00 | 1.3794 | 2.2606 | 3.7108 | 3.7108 | 3.7108 | 3.7108
2021-01-31 17:00 | 1.5833 | 1.9267 | 1.8851 | 2.0276 | 1.9207 | 2.0632 | 1.6204 | 2.7788 | 3.4288 | 3.4288 | 3.8622 | 3.8622 | 2019-03-31 05:00 | 1.4632 | 2.398 | 3.9363 | 3.9363 | 3.9363 | 3.9363
2021-01-31 18:00 | 1.8805 | 2.2884 | 2.239 | 2.4082 | 2.2813 | 2.4505 | 1.629 | 2.7935 | 3.447 | 3.447 | 3.8826 | 3.8826 | 2019-03-31 06:00 | 1.5775 | 2.5853 | 4.2438 | 4.2438 | 4.2438 | 4.2438
2021-01-31 19:00 | 1.829 | 2.2258 | 2.1777 | 2.3424 | 2.2189 | 2.3835 | 1.6604 | 2.8474 | 3.5135 | 3.5135 | 3.9576 | 3.9576 | 2019-03-31 07:00 | 1.6766 | 2.7477 | 4.5103 | 4.5103 | 4.5103 | 4.5103
2021-01-31 20:00 | 1.789 | 2.1771 | 2.1301 | 2.2911 | 2.1704 | 2.3314 | 1.5547 | 2.666 | 3.2897 | 3.2897 | 3.7055 | 3.7055 | 2019-03-31 08:00 | 1.7986 | 2.9475 | 4.8384 | 4.8384 | 4.8384 | 4.8384
2021-01-31 21:00 | 1.7552 | 2.1359 | 2.0898 | 2.2478 | 2.1293 | 2.2873 | 1.5433 | 2.6464 | 3.2655 | 3.2655 | 3.6783 | 3.6783 | 2019-03-31 09:00 | 1.9053 | 3.1224 | 5.1254 | 5.1254 | 5.1254 | 5.1254
2021-01-31 22:00 | 1.669 | 2.031 | 1.9872 | 2.1374 | 2.0247 | 2.175 | 1.3261 | 2.274 | 2.8059 | 2.8059 | 3.1606 | 3.1606 | 2019-03-31 10:00 | 1.9815 | 3.2472 | 5.3304 | 5.3304 | 5.3304 | 5.3304
2021-01-31 23:00 | 1.5061 | 1.8328 | 1.7932 | 1.9288 | 1.8271 | 1.9627 | 1.0974 | 1.8819 | 2.3222 | 2.3222 | 2.6157 | 2.6157 | 2019-03-31 11:00 | 1.951 | 3.1973 | 5.2484 | 5.2484 | 5.2484 | 5.2484
2021-02-01 | 1.479 | 1.7998 | 1.7609 | 1.894 | 1.7942 | 1.9273 | 0.96596 | 1.6565 | 2.044 | 2.044 | 2.3023 | 2.3023 | 2019-03-31 12:00 | 1.9434 | 3.1848 | 5.2279 | 5.2279 | 5.2279 | 5.2279
2021-02-01 01:00 | 1.3118 | 1.5963 | 1.5619 | 1.6799 | 1.5914 | 1.7095 | 0.77734 | 1.333 | 1.6449 | 1.6449 | 1.8528 | 1.8528 | 2019-03-31 13:00 | 1.9205 | 3.1473 | 5.1664 | 5.1664 | 5.1664 | 5.1664
2021-02-01 02:00 | 1.2175 | 1.4815 | 1.4496 | 1.5591 | 1.477 | 1.5865 | 0.75986 | 1.303 | 1.6079 | 1.6079 | 1.8111 | 1.8111 | 2019-03-31 14:00 | 1.9815 | 3.2472 | 5.3304 | 5.3304 | 5.3304 | 5.3304
2021-02-01 03:00 | 1.206 | 1.4676 | 1.4359 | 1.5445 | 1.4631 | 1.5716 | 0.76019 | 1.3036 | 1.6086 | 1.6086 | 1.8119 | 1.8119 | 2019-03-31 15:00 | 1.9281 | 3.1598 | 5.1869 | 5.1869 | 5.1869 | 5.1869
2021-02-01 04:00 | 1.2146 | 1.478 | 1.4462 | 1.5555 | 1.4735 | 1.5828 | 0.7557 | 1.2959 | 1.5991 | 1.5991 | 1.8012 | 1.8012 | 2019-03-31 16:00 | 1.9662 | 3.2223 | 5.2894 | 5.2894 | 5.2894 | 5.2894
2021-02-01 05:00 | 1.3432 | 1.6345 | 1.5993 | 1.7202 | 1.6295 | 1.7504 | 0.81449 | 1.3967 | 1.7235 | 1.7235 | 1.9413 | 1.9413 | 2019-03-31 17:00 | 1.9129 | 3.1348 | 5.1459 | 5.1459 | 5.1459 | 5.1459
2021-02-01 06:00 | 1.7576 | 2.1388 | 2.0927 | 2.2509 | 2.1322 | 2.2904 | 1.0346 | 1.7741 | 2.1891 | 2.1891 | 2.4658 | 2.4658 | 2019-03-31 18:00 | 1.7909 | 2.935 | 4.8179 | 4.8179 | 4.8179 | 4.8179
2021-02-01 07:00 | 2.0948 | 2.5492 | 2.4942 | 2.6827 | 2.5413 | 2.7299 | 1.2403 | 2.1269 | 2.6245 | 2.6245 | 2.9562 | 2.9562 | 2019-03-31 19:00 | 1.8062 | 2.96 | 4.8589 | 4.8589 | 4.8589 | 4.8589
2021-02-01 08:00 | 2.2091 | 2.6883 | 2.6303 | 2.8291 | 2.68 | 2.8788 | 1.246 | 2.1367 | 2.6366 | 2.6366 | 2.9699 | 2.9699 | 2019-03-31 20:00 | 1.7757 | 2.91 | 4.7769 | 4.7769 | 4.7769 | 4.7769
2021-02-01 09:00 | 2.2063 | 2.6848 | 2.6269 | 2.8255 | 2.6765 | 2.8751 | 1.2289 | 2.1073 | 2.6003 | 2.6003 | 2.929 | 2.929 | 2019-03-31 21:00 | 1.7605 | 2.8851 | 4.7359 | 4.7359 | 4.7359 | 4.7359
2021-02-01 10:00 | 2.3492 | 2.8587 | 2.797 | 3.0085 | 2.8499 | 3.0613 | 1.3289 | 2.2789 | 2.812 | 2.812 | 3.1674 | 3.1674 | 2019-03-31 22:00 | 1.669 | 2.7352 | 4.4898 | 4.4898 | 4.4898 | 4.4898
2021-02-01 11:00 | 2.3435 | 2.8518 | 2.7902 | 3.0011 | 2.843 | 3.0539 | 1.3175 | 2.2593 | 2.7878 | 2.7878 | 3.1402 | 3.1402 | 2019-03-31 23:00 | 1.4937 | 2.4479 | 4.0183 | 4.0183 | 4.0183 | 4.0183
2021-02-01 12:00 | 2.4463 | 2.9769 | 2.9127 | 3.1329 | 2.9678 | 3.1879 | 1.3918 | 2.3867 | 2.945 | 2.945 | 3.3173 | 3.3173 | 2019-04-01 | 1.4556 | 2.4978 | 4.2218 | 4.2218 | 4.2218 | 4.2218
2021-02-01 13:00 | 2.5178 | 3.0639 | 2.9978 | 3.2244 | 3.0545 | 3.2811 | 1.5004 | 2.5729 | 3.1748 | 3.1748 | 3.5761 | 3.5761 | 2019-04-01 01:00 | 1.4251 | 2.4455 | 4.1333 | 4.1333 | 4.1333 | 4.1333
2021-02-01 14:00 | 2.6321 | 3.203 | 3.1339 | 3.3708 | 3.1931 | 3.43 | 1.4146 | 2.4259 | 2.9934 | 2.9934 | 3.3718 | 3.3718 | 2019-04-01 02:00 | 1.3946 | 2.3932 | 4.0449 | 4.0449 | 4.0449 | 4.0449
2021-02-01 15:00 | 2.5578 | 3.1126 | 3.0454 | 3.2756 | 3.103 | 3.3332 | 1.4089 | 2.4161 | 2.9813 | 2.9813 | 3.3581 | 3.3581 | 2019-04-01 03:00 | 1.3718 | 2.354 | 3.9786 | 3.9786 | 3.9786 | 3.9786
2021-02-01 16:00 | 2.5607 | 3.1161 | 3.0488 | 3.2793 | 3.1065 | 3.3369 | 1.3946 | 2.3916 | 2.9511 | 2.9511 | 3.3241 | 3.3241 | 2019-04-01 04:00 | 1.4175 | 2.4324 | 4.1112 | 4.1112 | 4.1112 | 4.1112
2021-02-01 17:00 | 2.6407 | 3.2134 | 3.1441 | 3.3818 | 3.2035 | 3.4412 | 1.6976 | 2.9111 | 3.5921 | 3.5921 | 4.0461 | 4.0461 | 2019-04-01 05:00 | 1.6309 | 2.7986 | 4.7301 | 4.7301 | 4.7301 | 4.7301
2021-02-01 18:00 | 2.7779 | 3.3804 | 3.3075 | 3.5575 | 3.37 | 3.62 | 1.7004 | 2.916 | 3.5981 | 3.5981 | 4.0529 | 4.0529 | 2019-04-01 06:00 | 1.9281 | 3.3087 | 5.5922 | 5.5922 | 5.5922 | 5.5922
2021-02-01 19:00 | 2.4806 | 3.0187 | 2.9536 | 3.1768 | 3.0094 | 3.2326 | 1.569 | 2.6905 | 3.32 | 3.32 | 3.7396 | 3.7396 | 2019-04-01 07:00 | 1.9434 | 3.3348 | 5.6364 | 5.6364 | 5.6364 | 5.6364
2021-02-01 20:00 | 2.112 | 2.5701 | 2.5146 | 2.7047 | 2.5621 | 2.7522 | 1.489 | 2.5533 | 3.1506 | 3.1506 | 3.5489 | 3.5489 | 2019-04-01 08:00 | 1.9205 | 3.2956 | 5.5701 | 5.5701 | 5.5701 | 5.5701
2021-02-01 21:00 | 1.9919 | 2.424 | 2.3717 | 2.551 | 2.4165 | 2.5958 | 1.4061 | 2.4112 | 2.9753 | 2.9753 | 3.3513 | 3.3513 | 2019-04-01 09:00 | 1.9281 | 3.3087 | 5.5922 | 5.5922 | 5.5922 | 5.5922
2021-02-01 22:00 | 1.776 | 2.1612 | 2.1146 | 2.2744 | 2.1545 | 2.3144 | 1.3461 | 2.3083 | 2.8483 | 2.8483 | 3.2083 | 3.2083 | 2019-04-01 10:00 | 1.9815 | 3.4002 | 5.7469 | 5.7469 | 5.7469 | 5.7469
2021-02-01 23:00 | 1.4556 | 1.7713 | 1.7331 | 1.8641 | 1.7658 | 1.8968 | 1.1077 | 1.8996 | 2.3439 | 2.3439 | 2.6402 | 2.6402 | 2019-04-01 11:00 | 2.0501 | 3.5179 | 5.9458 | 5.9458 | 5.9458 | 5.9458
2021-02-02 | 1.3661 | 1.6624 | 1.6265 | 1.7494 | 1.6572 | 1.7802 | 0.88902 | 1.5245 | 1.8812 | 1.8812 | 2.1189 | 2.1189 | 2019-04-01 12:00 | 2.0424 | 3.5048 | 5.9237 | 5.9237 | 5.9237 | 5.9237
2021-02-02 01:00 | 1.3003 | 1.5824 | 1.5482 | 1.6653 | 1.5775 | 1.6945 | 0.79449 | 1.3624 | 1.6811 | 1.6811 | 1.8936 | 1.8936 | 2019-04-01 13:00 | 2.0805 | 3.5702 | 6.0343 | 6.0343 | 6.0343 | 6.0343
2021-02-02 02:00 | 1.2232 | 1.4885 | 1.4564 | 1.5664 | 1.4839 | 1.594 | 0.75836 | 1.3005 | 1.6047 | 1.6047 | 1.8075 | 1.8075 | 2019-04-01 14:00 | 2.1263 | 3.6487 | 6.1669 | 6.1669 | 6.1669 | 6.1669
2021-02-02 03:00 | 1.2603 | 1.5337 | 1.5006 | 1.614 | 1.529 | 1.6424 | 0.71733 | 1.2301 | 1.5179 | 1.5179 | 1.7097 | 1.7097 | 2019-04-01 15:00 | 1.9815 | 3.4002 | 5.7469 | 5.7469 | 5.7469 | 5.7469
2021-02-02 04:00 | 1.2117 | 1.4746 | 1.4428 | 1.5518 | 1.47 | 1.5791 | 0.73161 | 1.2546 | 1.5481 | 1.5481 | 1.7438 | 1.7438 | 2019-04-01 16:00 | 1.9662 | 3.374 | 5.7027 | 5.7027 | 5.7027 | 5.7027
2021-02-02 05:00 | 1.3546 | 1.6484 | 1.6129 | 1.7348 | 1.6434 | 1.7653 | 0.7802 | 1.3379 | 1.6509 | 1.6509 | 1.8596 | 1.8596 | 2019-04-01 17:00 | 1.9281 | 3.3087 | 5.5922 | 5.5922 | 5.5922 | 5.5922
2021-02-02 06:00 | 1.6519 | 2.0101 | 1.9668 | 2.1154 | 2.0039 | 2.1526 | 1.046 | 1.7937 | 2.2133 | 2.2133 | 2.4931 | 2.4931 | 2019-04-01 18:00 | 1.7223 | 2.9556 | 4.9954 | 4.9954 | 4.9954 | 4.9954
2021-02-02 07:00 | 1.8633 | 2.2675 | 2.2186 | 2.3863 | 2.2605 | 2.4282 | 1.226 | 2.1024 | 2.5943 | 2.5943 | 2.9222 | 2.9222 | 2019-04-01 19:00 | 1.7376 | 2.9817 | 5.0396 | 5.0396 | 5.0396 | 5.0396
2021-02-02 08:00 | 1.9834 | 2.4136 | 2.3615 | 2.54 | 2.4061 | 2.5846 | 1.4289 | 2.4504 | 3.0236 | 3.0236 | 3.4058 | 3.4058 | 2019-04-01 20:00 | 1.6385 | 2.8117 | 4.7522 | 4.7522 | 4.7522 | 4.7522
2021-02-02 09:00 | 2.0062 | 2.4414 | 2.3887 | 2.5693 | 2.4339 | 2.6144 | 1.2546 | 2.1515 | 2.6548 | 2.6548 | 2.9903 | 2.9903 | 2019-04-01 21:00 | 1.5852 | 2.7202 | 4.5975 | 4.5975 | 4.5975 | 4.5975
2021-02-02 10:00 | 2.1148 | 2.5735 | 2.518 | 2.7083 | 2.5656 | 2.7559 | 1.4032 | 2.4063 | 2.9692 | 2.9692 | 3.3445 | 3.3445 | 2019-04-01 22:00 | 1.6157 | 2.7725 | 4.6859 | 4.6859 | 4.6859 | 4.6859
2021-02-02 11:00 | 2.1377 | 2.6014 | 2.5452 | 2.7376 | 2.5933 | 2.7857 | 1.4347 | 2.4602 | 3.0357 | 3.0357 | 3.4194 | 3.4194 | 2019-04-01 23:00 | 1.4709 | 2.524 | 4.266 | 4.266 | 4.266 | 4.266
2021-02-02 12:00 | 2.092 | 2.5457 | 2.4908 | 2.6791 | 2.5379 | 2.7261 | 1.4004 | 2.4014 | 2.9632 | 2.9632 | 3.3377 | 3.3377 | 2019-04-02 | 1.509 | 2.5894 | 4.3765 | 4.3765 | 4.3765 | 4.3765
2021-02-02 13:00 | 2.152 | 2.6187 | 2.5623 | 2.7559 | 2.6107 | 2.8043 | 1.4089 | 2.4161 | 2.9813 | 2.9813 | 3.3581 | 3.3581 | 2019-04-02 01:00 | 1.4327 | 2.4586 | 4.1555 | 4.1555 | 4.1555 | 4.1555
2021-02-02 14:00 | 2.1091 | 2.5666 | 2.5112 | 2.701 | 2.5587 | 2.7485 | 1.3489 | 2.3132 | 2.8543 | 2.8543 | 3.2151 | 3.2151 | 2019-04-02 02:00 | 1.3946 | 2.3932 | 4.0449 | 4.0449 | 4.0449 | 4.0449
2021-02-02 15:00 | 2.2692 | 2.7613 | 2.7018 | 2.906 | 2.7528 | 2.957 | 1.3575 | 2.3279 | 2.8725 | 2.8725 | 3.2355 | 3.2355 | 2019-04-02 03:00 | 1.3946 | 2.3932 | 4.0449 | 4.0449 | 4.0449 | 4.0449
2021-02-02 16:00 | 2.2557 | 2.745 | 2.6858 | 2.8888 | 2.7365 | 2.9395 | 1.4489 | 2.4847 | 3.066 | 3.066 | 3.4535 | 3.4535 | 2019-04-02 04:00 | 1.4251 | 2.4455 | 4.1333 | 4.1333 | 4.1333 | 4.1333
2021-02-02 17:00 | 2.2834 | 2.7787 | 2.7188 | 2.9243 | 2.7702 | 2.9757 | 1.5347 | 2.6317 | 3.2474 | 3.2474 | 3.6578 | 3.6578 | 2019-04-02 05:00 | 1.6461 | 2.8248 | 4.7743 | 4.7743 | 4.7743 | 4.7743
2021-02-02 18:00 | 2.4549 | 2.9874 | 2.9229 | 3.1439 | 2.9782 | 3.1991 | 1.5918 | 2.7297 | 3.3683 | 3.3683 | 3.7941 | 3.7941 | 2019-04-02 06:00 | 1.829 | 3.1386 | 5.3048 | 5.3048 | 5.3048 | 5.3048
2021-02-02 19:00 | 2.3295 | 2.8347 | 2.7736 | 2.9832 | 2.826 | 3.0356 | 1.6204 | 2.7788 | 3.4288 | 3.4288 | 3.8622 | 3.8622 | 2019-04-02 07:00 | 1.9434 | 3.3348 | 5.6364 | 5.6364 | 5.6364 | 5.6364
2021-02-02 20:00 | 2.092 | 2.5457 | 2.4908 | 2.6791 | 2.5379 | 2.7261 | 1.5461 | 2.6513 | 3.2716 | 3.2716 | 3.6851 | 3.6851 | 2019-04-02 08:00 | 2.0119 | 3.4525 | 5.8353 | 5.8353 | 5.8353 | 5.8353
2021-02-02 21:00 | 1.9862 | 2.417 | 2.3649 | 2.5437 | 2.4096 | 2.5883 | 1.4918 | 2.5582 | 3.1567 | 3.1567 | 3.5557 | 3.5557 | 2019-04-02 09:00 | 2.0501 | 3.5179 | 5.9458 | 5.9458 | 5.9458 | 5.9458
2021-02-02 22:00 | 1.7526 | 2.1327 | 2.0867 | 2.2444 | 2.1261 | 2.2838 | 1.3489 | 2.3132 | 2.8543 | 2.8543 | 3.2151 | 3.2151 | 2019-04-02 10:00 | 2.0119 | 3.4525 | 5.8353 | 5.8353 | 5.8353 | 5.8353
2021-02-02 23:00 | 1.5175 | 1.8467 | 1.8068 | 1.9434 | 1.841 | 1.9776 | 1.0399 | 1.7832 | 2.2003 | 2.2003 | 2.4784 | 2.4784 | 2019-04-02 11:00 | 2.0577 | 3.531 | 5.9679 | 5.9679 | 5.9679 | 5.9679
2021-02-03 | 1.4289 | 1.7389 | 1.7014 | 1.83 | 1.7335 | 1.8621 | 0.92881 | 1.5928 | 1.9654 | 1.9654 | 2.2138 | 2.2138 | 2019-04-02 12:00 | 2.1415 | 3.6748 | 6.2111 | 6.2111 | 6.2111 | 6.2111
2021-02-03 01:00 | 1.2775 | 1.5545 | 1.521 | 1.636 | 1.5498 | 1.6647 | 0.79506 | 1.3634 | 1.6824 | 1.6824 | 1.895 | 1.895 | 2019-04-02 13:00 | 2.0424 | 3.5048 | 5.9237 | 5.9237 | 5.9237 | 5.9237
2021-02-03 02:00 | 1.2603 | 1.5337 | 1.5006 | 1.614 | 1.529 | 1.6424 | 0.70308 | 1.2057 | 1.4877 | 1.4877 | 1.6758 | 1.6758 | 2019-04-02 14:00 | 2.0577 | 3.531 | 5.9679 | 5.9679 | 5.9679 | 5.9679
2021-02-03 03:00 | 1.2261 | 1.492 | 1.4599 | 1.5702 | 1.4874 | 1.5978 | 0.70239 | 1.2045 | 1.4863 | 1.4863 | 1.6741 | 1.6741 | 2019-04-02 15:00 | 2.0043 | 3.4394 | 5.8132 | 5.8132 | 5.8132 | 5.8132
2021-02-03 04:00 | 1.2375 | 1.5059 | 1.4734 | 1.5847 | 1.5012 | 1.6126 | 0.70304 | 1.2056 | 1.4876 | 1.4876 | 1.6757 | 1.6757 | 2019-04-02 16:00 | 2.2253 | 3.8187 | 6.4542 | 6.4542 | 6.4542 | 6.4542
2021-02-03 05:00 | 1.5115 | 1.8393 | 1.7996 | 1.9357 | 1.8336 | 1.9697 | 0.8002 | 1.3722 | 1.6932 | 1.6932 | 1.9073 | 1.9073 | 2019-04-02 17:00 | 2.0653 | 3.5441 | 5.99 | 5.99 | 5.99 | 5.99
2021-02-03 06:00 | 1.6661 | 2.0275 | 1.9838 | 2.1337 | 2.0213 | 2.1712 | 1.0203 | 1.7496 | 2.1589 | 2.1589 | 2.4317 | 2.4317 | 2019-04-02 18:00 | 1.9967 | 3.4264 | 5.7911 | 5.7911 | 5.7911 | 5.7911
2021-02-03 07:00 | 1.9376 | 2.3579 | 2.307 | 2.4814 | 2.3506 | 2.525 | 1.3289 | 2.2789 | 2.812 | 2.812 | 3.1674 | 3.1674 | 2019-04-02 19:00 | 1.8519 | 3.1779 | 5.3711 | 5.3711 | 5.3711 | 5.3711
2021-02-03 08:00 | 2.0291 | 2.4692 | 2.4159 | 2.5986 | 2.4616 | 2.6442 | 1.2832 | 2.2005 | 2.7152 | 2.7152 | 3.0584 | 3.0584 | 2019-04-02 20:00 | 1.8138 | 3.1125 | 5.2606 | 5.2606 | 5.2606 | 5.2606
2021-02-03 09:00 | 1.9576 | 2.3823 | 2.3309 | 2.5071 | 2.3749 | 2.5511 | 1.3403 | 2.2985 | 2.8362 | 2.8362 | 3.1947 | 3.1947 | 2019-04-02 21:00 | 1.7071 | 2.9294 | 4.9512 | 4.9512 | 4.9512 | 4.9512
2021-02-03 10:00 | 1.8862 | 2.2953 | 2.2458 | 2.4156 | 2.2882 | 2.458 | 1.2689 | 2.176 | 2.685 | 2.685 | 3.0244 | 3.0244 | 2019-04-02 22:00 | 1.6233 | 2.7855 | 4.708 | 4.708 | 4.708 | 4.708
2021-02-03 11:00 | 1.9719 | 2.3996 | 2.3479 | 2.5254 | 2.3922 | 2.5697 | 1.2946 | 2.2201 | 2.7394 | 2.7394 | 3.0857 | 3.0857 | 2019-04-02 23:00 | 1.5242 | 2.6155 | 4.4207 | 4.4207 | 4.4207 | 4.4207
2021-02-03 12:00 | 1.9862 | 2.417 | 2.3649 | 2.5437 | 2.4096 | 2.5883 | 1.3403 | 2.2985 | 2.8362 | 2.8362 | 3.1947 | 3.1947 | 2019-04-03 | 1.5013 | 2.5763 | 4.3544 | 4.3544 | 4.3544 | 4.3544
2021-02-03 13:00 | 1.9948 | 2.4275 | 2.3751 | 2.5546 | 2.42 | 2.5995 | 1.3575 | 2.3279 | 2.8725 | 2.8725 | 3.2355 | 3.2355 | 2019-04-03 01:00 | 1.4709 | 2.524 | 4.266 | 4.266 | 4.266 | 4.266
2021-02-03 14:00 | 2.192 | 2.6674 | 2.6099 | 2.8072 | 2.6592 | 2.8565 | 1.4347 | 2.4602 | 3.0357 | 3.0357 | 3.4194 | 3.4194 | 2019-04-03 02:00 | 1.3337 | 2.2886 | 3.8681 | 3.8681 | 3.8681 | 3.8681
2021-02-03 15:00 | 2.0605 | 2.5075 | 2.4534 | 2.6388 | 2.4997 | 2.6852 | 1.2803 | 2.1956 | 2.7092 | 2.7092 | 3.0516 | 3.0516 | 2019-04-03 03:00 | 1.3718 | 2.354 | 3.9786 | 3.9786 | 3.9786 | 3.9786
2021-02-03 16:00 | 2.2749 | 2.7683 | 2.7086 | 2.9133 | 2.7598 | 2.9645 | 1.3089 | 2.2446 | 2.7697 | 2.7697 | 3.1197 | 3.1197 | 2019-04-03 04:00 | 1.4404 | 2.4717 | 4.1776 | 4.1776 | 4.1776 | 4.1776
2021-02-03 17:00 | 2.3377 | 2.8448 | 2.7834 | 2.9938 | 2.836 | 3.0464 | 1.4604 | 2.5043 | 3.0902 | 3.0902 | 3.4807 | 3.4807 | 2019-04-03 05:00 | 1.5394 | 2.6417 | 4.4649 | 4.4649 | 4.4649 | 4.4649
2021-02-03 18:00 | 2.3006 | 2.7996 | 2.7392 | 2.9462 | 2.791 | 2.998 | 1.5147 | 2.5974 | 3.2051 | 3.2051 | 3.6102 | 3.6102 | 2019-04-03 06:00 | 1.8443 | 3.1648 | 5.349 | 5.349 | 5.349 | 5.349
2021-02-03 19:00 | 2.2149 | 2.6953 | 2.6371 | 2.8364 | 2.6869 | 2.8863 | 1.5404 | 2.6415 | 3.2595 | 3.2595 | 3.6715 | 3.6715 | 2019-04-03 07:00 | 1.8443 | 3.1648 | 5.349 | 5.349 | 5.349 | 5.349
2021-02-03 20:00 | 2.0748 | 2.5248 | 2.4704 | 2.6571 | 2.5171 | 2.7038 | 1.4775 | 2.5337 | 3.1265 | 3.1265 | 3.5216 | 3.5216 | 2019-04-03 08:00 | 1.9434 | 3.3348 | 5.6364 | 5.6364 | 5.6364 | 5.6364
2021-02-03 21:00 | 1.9519 | 2.3753 | 2.3241 | 2.4997 | 2.368 | 2.5437 | 1.4861 | 2.5484 | 3.1446 | 3.1446 | 3.542 | 3.542 | 2019-04-03 09:00 | 0.87641 | 1.5039 | 2.5419 | 2.5419 | 2.5419 | 2.5419
2021-02-03 22:00 | 1.7296 | 2.1047 | 2.0593 | 2.215 | 2.0983 | 2.2539 | 1.3042 | 2.2364 | 2.7596 | 2.7596 | 3.1084 | 3.1084 | 2019-04-03 10:00 | 0.85355 | 1.4647 | 2.4756 | 2.4756 | 2.4756 | 2.4756
2021-02-03 23:00 | 1.4518 | 1.7667 | 1.7286 | 1.8592 | 1.7612 | 1.8919 | 1.1031 | 1.8917 | 2.3343 | 2.3343 | 2.6293 | 2.6293 | 2019-04-03 11:00 | 1.7986 | 3.0863 | 5.2164 | 5.2164 | 5.2164 | 5.2164
2021-02-04 | 1.4161 | 1.7232 | 1.686 | 1.8135 | 1.7179 | 1.8453 | 0.93452 | 1.6026 | 1.9775 | 1.9775 | 2.2274 | 2.2274 | 2019-04-03 12:00 | 2.1186 | 3.6356 | 6.1448 | 6.1448 | 6.1448 | 6.1448
2021-02-04 01:00 | 1.2632 | 1.5372 | 1.504 | 1.6177 | 1.5324 | 1.6461 | 0.81735 | 1.4016 | 1.7295 | 1.7295 | 1.9481 | 1.9481 | 2019-04-03 13:00 | 2.1644 | 3.7141 | 6.2774 | 6.2774 | 6.2774 | 6.2774
2021-02-04 02:00 | 1.1919 | 1.4505 | 1.4192 | 1.5264 | 1.446 | 1.5533 | 0.7802 | 1.3379 | 1.6509 | 1.6509 | 1.8596 | 1.8596 | 2019-04-03 14:00 | 2.1567 | 3.701 | 6.2553 | 6.2553 | 6.2553 | 6.2553
2021-02-04 03:00 | 1.2232 | 1.4885 | 1.4564 | 1.5664 | 1.4839 | 1.594 | 0.74384 | 1.2756 | 1.574 | 1.574 | 1.7729 | 1.7729 | 2019-04-03 15:00 | 2.2177 | 3.8056 | 6.4321 | 6.4321 | 6.4321 | 6.4321
2021-02-04 04:00 | 1.1859 | 1.4431 | 1.412 | 1.5187 | 1.4386 | 1.5454 | 0.80592 | 1.382 | 1.7053 | 1.7053 | 1.9209 | 1.9209 | 2019-04-03 16:00 | 2.2711 | 3.8972 | 6.5868 | 6.5868 | 6.5868 | 6.5868
2021-02-04 05:00 | 1.4004 | 1.7041 | 1.6673 | 1.7934 | 1.6988 | 1.8249 | 0.79683 | 1.3664 | 1.6861 | 1.6861 | 1.8992 | 1.8992 | 2019-04-03 17:00 | 2.1339 | 3.6618 | 6.189 | 6.189 | 6.189 | 6.189
2021-02-04 06:00 | 1.6033 | 1.951 | 1.9089 | 2.0532 | 1.945 | 2.0893 | 1.0372 | 1.7786 | 2.1946 | 2.1946 | 2.472 | 2.472 | 2019-04-03 18:00 | 2.0653 | 3.5441 | 5.99 | 5.99 | 5.99 | 5.99
2021-02-04 07:00 | 1.9462 | 2.3683 | 2.3173 | 2.4924 | 2.361 | 2.5362 | 1.2175 | 2.0877 | 2.5761 | 2.5761 | 2.9018 | 2.9018 | 2019-04-03 19:00 | 1.9738 | 3.3871 | 5.7248 | 5.7248 | 5.7248 | 5.7248
2021-02-04 08:00 | 2.172 | 2.6431 | 2.5861 | 2.7815 | 2.6349 | 2.8304 | 1.3203 | 2.2642 | 2.7939 | 2.7939 | 3.147 | 3.147 | 2019-04-03 20:00 | 1.8519 | 3.1779 | 5.3711 | 5.3711 | 5.3711 | 5.3711
2021-02-04 09:00 | 2.1806 | 2.6535 | 2.5963 | 2.7925 | 2.6453 | 2.8416 | 1.2803 | 2.1956 | 2.7092 | 2.7092 | 3.0516 | 3.0516 | 2019-04-03 21:00 | 1.7071 | 2.9294 | 4.9512 | 4.9512 | 4.9512 | 4.9512
2021-02-04 10:00 | 2.3092 | 2.81 | 2.7494 | 2.9572 | 2.8014 | 3.0092 | 1.4146 | 2.4259 | 2.9934 | 2.9934 | 3.3718 | 3.3718 | 2019-04-03 22:00 | 1.6919 | 2.9032 | 4.907 | 4.907 | 4.907 | 4.907
2021-02-04 11:00 | 2.2892 | 2.7857 | 2.7256 | 2.9316 | 2.7771 | 2.9831 | 1.3746 | 2.3573 | 2.9088 | 2.9088 | 3.2764 | 3.2764 | 2019-04-03 23:00 | 1.5394 | 2.6417 | 4.4649 | 4.4649 | 4.4649 | 4.4649
2021-02-04 12:00 | 2.4006 | 2.9213 | 2.8583 | 3.0743 | 2.9123 | 3.1284 | 1.3746 | 2.3573 | 2.9088 | 2.9088 | 3.2764 | 3.2764 | 2019-04-04 | 1.4632 | 2.5109 | 4.2439 | 4.2439 | 4.2439 | 4.2439
2021-02-04 13:00 | 2.6092 | 3.1752 | 3.1067 | 3.3415 | 3.1654 | 3.4002 | 1.4604 | 2.5043 | 3.0902 | 3.0902 | 3.4807 | 3.4807 | 2019-04-04 01:00 | 1.4023 | 2.4063 | 4.067 | 4.067 | 4.067 | 4.067
2021-02-04 14:00 | 2.5607 | 3.1161 | 3.0488 | 3.2793 | 3.1065 | 3.3369 | 1.4547 | 2.4945 | 3.0781 | 3.0781 | 3.4671 | 3.4671 | 2019-04-04 02:00 | 1.4023 | 2.4063 | 4.067 | 4.067 | 4.067 | 4.067
2021-02-04 15:00 | 2.5778 | 3.1369 | 3.0693 | 3.3013 | 3.1273 | 3.3593 | 1.4289 | 2.4504 | 3.0236 | 3.0236 | 3.4058 | 3.4058 | 2019-04-04 03:00 | 1.3642 | 2.3409 | 3.9565 | 3.9565 | 3.9565 | 3.9565
2021-02-04 16:00 | 2.615 | 3.1821 | 3.1135 | 3.3488 | 3.1723 | 3.4077 | 1.4432 | 2.4749 | 3.0539 | 3.0539 | 3.4399 | 3.4399 | 2019-04-04 04:00 | 1.387 | 2.3801 | 4.0228 | 4.0228 | 4.0228 | 4.0228
2021-02-04 17:00 | 2.655 | 3.2308 | 3.1611 | 3.4001 | 3.2209 | 3.4598 | 1.5204 | 2.6072 | 3.2172 | 3.2172 | 3.6238 | 3.6238 | 2019-04-04 05:00 | 1.6385 | 2.8117 | 4.7522 | 4.7522 | 4.7522 | 4.7522
2021-02-04 18:00 | 2.5235 | 3.0708 | 3.0046 | 3.2317 | 3.0614 | 3.2885 | 1.549 | 2.6562 | 3.2776 | 3.2776 | 3.6919 | 3.6919 | 2019-04-04 06:00 | 1.8748 | 3.2171 | 5.4375 | 5.4375 | 5.4375 | 5.4375
2021-02-04 19:00 | 2.3806 | 2.8969 | 2.8344 | 3.0487 | 2.888 | 3.1022 | 1.5604 | 2.6758 | 3.3018 | 3.3018 | 3.7192 | 3.7192 | 2019-04-04 07:00 | 1.829 | 3.1386 | 5.3048 | 5.3048 | 5.3048 | 5.3048
2021-02-04 20:00 | 2.2749 | 2.7683 | 2.7086 | 2.9133 | 2.7598 | 2.9645 | 1.5404 | 2.6415 | 3.2595 | 3.2595 | 3.6715 | 3.6715 | 2019-04-04 08:00 | 2.0043 | 3.4394 | 5.8132 | 5.8132 | 5.8132 | 5.8132
2021-02-04 21:00 | 2.0691 | 2.5179 | 2.4636 | 2.6498 | 2.5101 | 2.6963 | 1.5061 | 2.5827 | 3.1869 | 3.1869 | 3.5897 | 3.5897 | 2019-04-04 09:00 | 1.951 | 3.3479 | 5.6585 | 5.6585 | 5.6585 | 5.6585
2021-02-04 22:00 | 1.7987 | 2.1889 | 2.1417 | 2.3035 | 2.1821 | 2.344 | 1.3403 | 2.2985 | 2.8362 | 2.8362 | 3.1947 | 3.1947 | 2019-04-04 10:00 | 2.172 | 3.7271 | 6.2995 | 6.2995 | 6.2995 | 6.2995
2021-02-04 23:00 | 1.5718 | 1.9128 | 1.8715 | 2.013 | 1.9069 | 2.0483 | 1.126 | 1.9309 | 2.3826 | 2.3826 | 2.6838 | 2.6838 | 2019-04-04 11:00 | 2.1186 | 3.6356 | 6.1448 | 6.1448 | 6.1448 | 6.1448
2021-02-05 | 1.4604 | 1.7771 | 1.7388 | 1.8702 | 1.7716 | 1.9031 | 0.91321 | 1.566 | 1.9324 | 1.9324 | 2.1766 | 2.1766 | 2019-04-04 12:00 | 2.2787 | 3.9102 | 6.6089 | 6.6089 | 6.6089 | 6.6089
2021-02-05 01:00 | 1.3262 | 1.6138 | 1.579 | 1.6984 | 1.6088 | 1.7282 | 0.81164 | 1.3918 | 1.7174 | 1.7174 | 1.9345 | 1.9345 | 2019-04-04 13:00 | 2.0653 | 3.5441 | 5.99 | 5.99 | 5.99 | 5.99
2021-02-05 02:00 | 1.2718 | 1.5476 | 1.5142 | 1.6287 | 1.5428 | 1.6573 | 0.76591 | 1.3134 | 1.6207 | 1.6207 | 1.8255 | 1.8255 | 2019-04-04 14:00 | 2.0805 | 3.5702 | 6.0343 | 6.0343 | 6.0343 | 6.0343
2021-02-05 03:00 | 1.2175 | 1.4815 | 1.4496 | 1.5591 | 1.477 | 1.5865 | 0.75162 | 1.2889 | 1.5904 | 1.5904 | 1.7915 | 1.7915 | 2019-04-04 15:00 | 2.0805 | 3.5702 | 6.0343 | 6.0343 | 6.0343 | 6.0343
2021-02-05 04:00 | 1.2603 | 1.5337 | 1.5006 | 1.614 | 1.529 | 1.6424 | 0.7459 | 1.2791 | 1.5783 | 1.5783 | 1.7778 | 1.7778 | 2019-04-04 16:00 | 2.0424 | 3.5048 | 5.9237 | 5.9237 | 5.9237 | 5.9237
2021-02-05 05:00 | 1.4918 | 1.8154 | 1.7762 | 1.9105 | 1.8098 | 1.944 | 0.80306 | 1.3771 | 1.6993 | 1.6993 | 1.9141 | 1.9141 | 2019-04-04 17:00 | 2.0882 | 3.5833 | 6.0564 | 6.0564 | 6.0564 | 6.0564
2021-02-05 06:00 | 1.729 | 2.104 | 2.0586 | 2.2143 | 2.0976 | 2.2532 | 1.0288 | 1.7643 | 2.177 | 2.177 | 2.4522 | 2.4522 | 2019-04-04 18:00 | 1.9357 | 3.3217 | 5.6143 | 5.6143 | 5.6143 | 5.6143
2021-02-05 07:00 | 2.1634 | 2.6327 | 2.5759 | 2.7706 | 2.6245 | 2.8192 | 1.2946 | 2.2201 | 2.7394 | 2.7394 | 3.0857 | 3.0857 | 2019-04-04 19:00 | 1.9053 | 3.2694 | 5.5259 | 5.5259 | 5.5259 | 5.5259
2021-02-05 08:00 | 2.3578 | 2.8691 | 2.8072 | 3.0194 | 2.8603 | 3.0725 | 1.306 | 2.2397 | 2.7636 | 2.7636 | 3.1129 | 3.1129 | 2019-04-04 20:00 | 1.8824 | 3.2302 | 5.4596 | 5.4596 | 5.4596 | 5.4596
2021-02-05 09:00 | 2.2577 | 2.7474 | 2.6882 | 2.8913 | 2.739 | 2.9421 | 1.266 | 2.1711 | 2.679 | 2.679 | 3.0176 | 3.0176 | 2019-04-04 21:00 | 1.7223 | 2.9556 | 4.9954 | 4.9954 | 4.9954 | 4.9954
2021-02-05 10:00 | 2.4549 | 2.9874 | 2.9229 | 3.1439 | 2.9782 | 3.1991 | 1.4518 | 2.4896 | 3.072 | 3.072 | 3.4603 | 3.4603 | 2019-04-04 22:00 | 1.6461 | 2.8248 | 4.7743 | 4.7743 | 4.7743 | 4.7743
2021-02-05 11:00 | 2.4864 | 3.0256 | 2.9604 | 3.1841 | 3.0163 | 3.2401 | 1.4689 | 2.519 | 3.1083 | 3.1083 | 3.5012 | 3.5012 | 2019-04-04 23:00 | 1.5775 | 2.7071 | 4.5754 | 4.5754 | 4.5754 | 4.5754
2021-02-05 12:00 | 2.6121 | 3.1787 | 3.1101 | 3.3452 | 3.1689 | 3.404 | 1.549 | 2.6562 | 3.2776 | 3.2776 | 3.6919 | 3.6919 | 2019-04-05 | 1.4404 | 2.4717 | 4.1776 | 4.1776 | 4.1776 | 4.1776
2021-02-05 13:00 | 2.6635 | 3.2413 | 3.1713 | 3.4111 | 3.2313 | 3.471 | 1.5804 | 2.7101 | 3.3442 | 3.3442 | 3.7668 | 3.7668 | 2019-04-05 01:00 | 1.3946 | 2.3932 | 4.0449 | 4.0449 | 4.0449 | 4.0449
2021-02-05 14:00 | 2.5892 | 3.1508 | 3.0829 | 3.3159 | 3.1411 | 3.3742 | 1.4661 | 2.5141 | 3.1023 | 3.1023 | 3.4944 | 3.4944 | 2019-04-05 02:00 | 1.387 | 2.3801 | 4.0228 | 4.0228 | 4.0228 | 4.0228
2021-02-05 15:00 | 2.5692 | 3.1265 | 3.0591 | 3.2903 | 3.1169 | 3.3481 | 1.5032 | 2.5778 | 3.1809 | 3.1809 | 3.5829 | 3.5829 | 2019-04-05 03:00 | 1.387 | 2.3801 | 4.0228 | 4.0228 | 4.0228 | 4.0228
2021-02-05 16:00 | 2.4263 | 2.9526 | 2.8889 | 3.1073 | 2.9435 | 3.1619 | 1.4604 | 2.5043 | 3.0902 | 3.0902 | 3.4807 | 3.4807 | 2019-04-05 04:00 | 1.4099 | 2.4194 | 4.0891 | 4.0891 | 4.0891 | 4.0891
2021-02-05 17:00 | 2.4492 | 2.9804 | 2.9161 | 3.1366 | 2.9712 | 3.1917 | 1.5947 | 2.7346 | 3.3744 | 3.3744 | 3.8009 | 3.8009 | 2019-04-05 05:00 | 1.5699 | 2.694 | 4.5533 | 4.5533 | 4.5533 | 4.5533
2021-02-05 18:00 | 2.5521 | 3.1056 | 3.0386 | 3.2683 | 3.0961 | 3.3257 | 1.6719 | 2.867 | 3.5377 | 3.5377 | 3.9848 | 3.9848 | 2019-04-05 06:00 | 1.8214 | 3.1256 | 5.2827 | 5.2827 | 5.2827 | 5.2827
2021-02-05 19:00 | 2.2892 | 2.7857 | 2.7256 | 2.9316 | 2.7771 | 2.9831 | 1.7062 | 2.9258 | 3.6102 | 3.6102 | 4.0665 | 4.0665 | 2019-04-05 07:00 | 1.7528 | 3.0079 | 5.0838 | 5.0838 | 5.0838 | 5.0838
2021-02-05 20:00 | 1.9376 | 2.3579 | 2.307 | 2.4814 | 2.3506 | 2.525 | 1.6804 | 2.8817 | 3.5558 | 3.5558 | 4.0052 | 4.0052 | 2019-04-05 08:00 | 2.0501 | 3.5179 | 5.9458 | 5.9458 | 5.9458 | 5.9458
2021-02-05 21:00 | 1.8919 | 2.3023 | 2.2526 | 2.4229 | 2.2952 | 2.4654 | 1.6376 | 2.8082 | 3.4651 | 3.4651 | 3.9031 | 3.9031 | 2019-04-05 09:00 | 2.0501 | 3.5179 | 5.9458 | 5.9458 | 5.9458 | 5.9458
2021-02-05 22:00 | 1.7147 | 2.0866 | 2.0416 | 2.196 | 2.0802 | 2.2345 | 1.4489 | 2.4847 | 3.066 | 3.066 | 3.4535 | 3.4535 | 2019-04-05 10:00 | 2.0272 | 3.4787 | 5.8795 | 5.8795 | 5.8795 | 5.8795
2021-02-05 23:00 | 1.6233 | 1.9754 | 1.9328 | 2.0789 | 1.9693 | 2.1154 | 1.186 | 2.0338 | 2.5096 | 2.5096 | 2.8268 | 2.8268 | 2019-04-05 11:00 | 2.172 | 3.7271 | 6.2995 | 6.2995 | 6.2995 | 6.2995
2021-02-06 | 1.4832 | 1.8049 | 1.766 | 1.8995 | 1.7994 | 1.9329 | 1.1031 | 1.8917 | 2.3343 | 2.3343 | 2.6293 | 2.6293 | 2019-04-05 12:00 | 2.0958 | 3.5964 | 6.0785 | 6.0785 | 6.0785 | 6.0785
2021-02-06 01:00 | 1.3347 | 1.6241 | 1.5891 | 1.7092 | 1.6191 | 1.7393 | 0.91738 | 1.5732 | 1.9412 | 1.9412 | 2.1865 | 2.1865 | 2019-04-05 13:00 | 2.0196 | 3.4656 | 5.8574 | 5.8574 | 5.8574 | 5.8574
2021-02-06 02:00 | 1.266 | 1.5406 | 1.5073 | 1.6213 | 1.5358 | 1.6498 | 0.8345 | 1.431 | 1.7658 | 1.7658 | 1.989 | 1.989 | 2019-04-05 14:00 | 2.111 | 3.6225 | 6.1227 | 6.1227 | 6.1227 | 6.1227
2021-02-06 03:00 | 1.266 | 1.5406 | 1.5074 | 1.6213 | 1.5359 | 1.6498 | 0.81463 | 1.397 | 1.7238 | 1.7238 | 1.9416 | 1.9416 | 2019-04-05 15:00 | 1.9967 | 3.4264 | 5.7911 | 5.7911 | 5.7911 | 5.7911
2021-02-06 04:00 | 1.2489 | 1.5197 | 1.487 | 1.5994 | 1.5151 | 1.6275 | 0.76019 | 1.3036 | 1.6086 | 1.6086 | 1.8119 | 1.8119 | 2019-04-05 16:00 | 2.0729 | 3.5571 | 6.0121 | 6.0121 | 6.0121 | 6.0121
2021-02-06 05:00 | 1.3175 | 1.6032 | 1.5687 | 1.6872 | 1.5983 | 1.7169 | 0.83951 | 1.4396 | 1.7764 | 1.7764 | 2.0009 | 2.0009 | 2019-04-05 17:00 | 1.8976 | 3.2563 | 5.5038 | 5.5038 | 5.5038 | 5.5038
2021-02-06 06:00 | 1.3775 | 1.6763 | 1.6401 | 1.7641 | 1.6711 | 1.7951 | 0.87451 | 1.4996 | 1.8505 | 1.8505 | 2.0844 | 2.0844 | 2019-04-05 18:00 | 1.6919 | 2.9032 | 4.907 | 4.907 | 4.907 | 4.907
2021-02-06 07:00 | 1.5433 | 1.878 | 1.8375 | 1.9764 | 1.8722 | 2.0111 | 1.0517 | 1.8035 | 2.2254 | 2.2254 | 2.5067 | 2.5067 | 2019-04-05 19:00 | 1.6157 | 2.7725 | 4.6859 | 4.6859 | 4.6859 | 4.6859
2021-02-06 08:00 | 1.7033 | 2.0727 | 2.028 | 2.1813 | 2.0663 | 2.2196 | 1.2775 | 2.1907 | 2.7031 | 2.7031 | 3.0448 | 3.0448 | 2019-04-05 20:00 | 1.5394 | 2.6417 | 4.4649 | 4.4649 | 4.4649 | 4.4649
2021-02-06 09:00 | 1.7947 | 2.184 | 2.1369 | 2.2984 | 2.1773 | 2.3388 | 1.3775 | 2.3622 | 2.9148 | 2.9148 | 3.2832 | 3.2832 | 2019-04-05 21:00 | 1.5013 | 2.5763 | 4.3544 | 4.3544 | 4.3544 | 4.3544
2021-02-06 10:00 | 1.7519 | 2.1319 | 2.0859 | 2.2435 | 2.1253 | 2.283 | 1.5433 | 2.6464 | 3.2655 | 3.2655 | 3.6783 | 3.6783 | 2019-04-05 22:00 | 1.5318 | 2.6286 | 4.4428 | 4.4428 | 4.4428 | 4.4428
2021-02-06 11:00 | 1.7519 | 2.1319 | 2.0859 | 2.2435 | 2.1253 | 2.283 | 1.5604 | 2.6758 | 3.3018 | 3.3018 | 3.7192 | 3.7192 | 2019-04-05 23:00 | 1.5242 | 2.6155 | 4.4207 | 4.4207 | 4.4207 | 4.4207
2021-02-06 12:00 | 1.4689 | 1.7876 | 1.749 | 1.8812 | 1.7821 | 1.9143 | 1.5375 | 2.6366 | 3.2534 | 3.2534 | 3.6647 | 3.6647 | 2019-04-06 | 1.4709 | 2.524 | 4.266 | 4.266 | 4.266 | 4.266
2021-02-06 13:00 | 1.4232 | 1.7319 | 1.6946 | 1.8226 | 1.7266 | 1.8547 | 1.5747 | 2.7003 | 3.3321 | 3.3321 | 3.7532 | 3.7532 | 2019-04-06 01:00 | 1.4709 | 2.524 | 4.266 | 4.266 | 4.266 | 4.266
2021-02-06 14:00 | 1.5804 | 1.9232 | 1.8817 | 2.0239 | 1.9173 | 2.0595 | 1.5061 | 2.5827 | 3.1869 | 3.1869 | 3.5897 | 3.5897 | 2019-04-06 02:00 | 1.4175 | 2.4324 | 4.1112 | 4.1112 | 4.1112 | 4.1112
2021-02-06 15:00 | 1.5433 | 1.878 | 1.8375 | 1.9764 | 1.8722 | 2.0111 | 1.4947 | 2.5631 | 3.1627 | 3.1627 | 3.5625 | 3.5625 | 2019-04-06 03:00 | 1.4404 | 2.4717 | 4.1776 | 4.1776 | 4.1776 | 4.1776
2021-02-06 16:00 | 1.5947 | 1.9406 | 1.8987 | 2.0422 | 1.9346 | 2.0781 | 1.5375 | 2.6366 | 3.2534 | 3.2534 | 3.6647 | 3.6647 | 2019-04-06 04:00 | 1.4556 | 2.4978 | 4.2218 | 4.2218 | 4.2218 | 4.2218
2021-02-06 17:00 | 1.5947 | 1.9406 | 1.8987 | 2.0422 | 1.9346 | 2.0781 | 1.6176 | 2.7739 | 3.4228 | 3.4228 | 3.8554 | 3.8554 | 2019-04-06 05:00 | 1.5318 | 2.6286 | 4.4428 | 4.4428 | 4.4428 | 4.4428
2021-02-06 18:00 | 1.7062 | 2.0762 | 2.0314 | 2.185 | 2.0698 | 2.2234 | 1.5661 | 2.6856 | 3.3139 | 3.3139 | 3.7328 | 3.7328 | 2019-04-06 06:00 | 1.6233 | 2.7855 | 4.708 | 4.708 | 4.708 | 4.708
2021-02-06 19:00 | 1.7576 | 2.1388 | 2.0927 | 2.2509 | 2.1322 | 2.2904 | 1.6176 | 2.7739 | 3.4228 | 3.4228 | 3.8554 | 3.8554 | 2019-04-06 07:00 | 1.73 | 2.9686 | 5.0175 | 5.0175 | 5.0175 | 5.0175
2021-02-06 20:00 | 1.7033 | 2.0727 | 2.028 | 2.1813 | 2.0663 | 2.2196 | 1.6147 | 2.769 | 3.4167 | 3.4167 | 3.8486 | 3.8486 | 2019-04-06 08:00 | 1.9129 | 3.2825 | 5.548 | 5.548 | 5.548 | 5.548
2021-02-06 21:00 | 1.6976 | 2.0658 | 2.0212 | 2.174 | 2.0594 | 2.2122 | 1.5232 | 2.6121 | 3.2232 | 3.2232 | 3.6306 | 3.6306 | 2019-04-06 09:00 | 1.951 | 3.3479 | 5.6585 | 5.6585 | 5.6585 | 5.6585
2021-02-06 22:00 | 1.6261 | 1.9788 | 1.9361 | 2.0825 | 1.9727 | 2.1191 | 1.3746 | 2.3573 | 2.9088 | 2.9088 | 3.2764 | 3.2764 | 2019-04-06 10:00 | 1.951 | 3.3479 | 5.6585 | 5.6585 | 5.6585 | 5.6585
2021-02-06 23:00 | 1.5118 | 1.8397 | 1.8 | 1.9361 | 1.8341 | 1.9701 | 1.1603 | 1.9897 | 2.4552 | 2.4552 | 2.7655 | 2.7655 | 2019-04-06 11:00 | 2.0119 | 3.4525 | 5.8353 | 5.8353 | 5.8353 | 5.8353
2021-02-07 | 1.4089 | 1.7145 | 1.6775 | 1.8043 | 1.7092 | 1.836 | 1.0831 | 1.8574 | 2.2919 | 2.2919 | 2.5816 | 2.5816 | 2019-04-06 12:00 | 1.951 | 3.3479 | 5.6585 | 5.6585 | 5.6585 | 5.6585
2021-02-07 01:00 | 1.266 | 1.5406 | 1.5074 | 1.6213 | 1.5359 | 1.6498 | 0.86879 | 1.4898 | 1.8384 | 1.8384 | 2.0707 | 2.0707 | 2019-04-06 13:00 | 2.0196 | 3.4656 | 5.8574 | 5.8574 | 5.8574 | 5.8574
2021-02-07 02:00 | 1.2032 | 1.4642 | 1.4326 | 1.5409 | 1.4597 | 1.568 | 0.82592 | 1.4163 | 1.7477 | 1.7477 | 1.9686 | 1.9686 | 2019-04-06 14:00 | 2.0958 | 3.5964 | 6.0785 | 6.0785 | 6.0785 | 6.0785
2021-02-07 03:00 | 1.1889 | 1.4467 | 1.4155 | 1.5225 | 1.4423 | 1.5493 | 0.75734 | 1.2987 | 1.6025 | 1.6025 | 1.8051 | 1.8051 | 2019-04-06 15:00 | 1.9738 | 3.3871 | 5.7248 | 5.7248 | 5.7248 | 5.7248
2021-02-07 04:00 | 1.2032 | 1.4641 | 1.4325 | 1.5408 | 1.4596 | 1.5679 | 0.76877 | 1.3183 | 1.6267 | 1.6267 | 1.8323 | 1.8323 | 2019-04-06 16:00 | 2.0424 | 3.5048 | 5.9237 | 5.9237 | 5.9237 | 5.9237
2021-02-07 05:00 | 1.2432 | 1.5128 | 1.4802 | 1.5921 | 1.5082 | 1.62 | 0.76334 | 1.309 | 1.6152 | 1.6152 | 1.8194 | 1.8194 | 2019-04-06 17:00 | 1.9434 | 3.3348 | 5.6364 | 5.6364 | 5.6364 | 5.6364
2021-02-07 06:00 | 1.2746 | 1.5511 | 1.5176 | 1.6323 | 1.5463 | 1.661 | 0.82262 | 1.4107 | 1.7407 | 1.7407 | 1.9607 | 1.9607 | 2019-04-06 18:00 | 1.7376 | 2.9817 | 5.0396 | 5.0396 | 5.0396 | 5.0396
2021-02-07 07:00 | 1.3832 | 1.6832 | 1.6469 | 1.7714 | 1.678 | 1.8025 | 0.99168 | 1.7006 | 2.0984 | 2.0984 | 2.3636 | 2.3636 | 2019-04-06 19:00 | 1.7223 | 2.9556 | 4.9954 | 4.9954 | 4.9954 | 4.9954
2021-02-07 08:00 | 1.4661 | 1.7841 | 1.7456 | 1.8775 | 1.7786 | 1.9105 | 1.2003 | 2.0583 | 2.5399 | 2.5399 | 2.8609 | 2.8609 | 2019-04-06 20:00 | 1.6842 | 2.8902 | 4.8849 | 4.8849 | 4.8849 | 4.8849
2021-02-07 09:00 | 1.4661 | 1.7841 | 1.7456 | 1.8775 | 1.7786 | 1.9105 | 1.3155 | 2.2559 | 2.7836 | 2.7836 | 3.1354 | 3.1354 | 2019-04-06 21:00 | 1.6157 | 2.7725 | 4.6859 | 4.6859 | 4.6859 | 4.6859
2021-02-07 10:00 | 1.4518 | 1.7667 | 1.7286 | 1.8592 | 1.7612 | 1.8919 | 1.4261 | 2.4455 | 3.0176 | 3.0176 | 3.399 | 3.399 | 2019-04-06 22:00 | 1.5775 | 2.7071 | 4.5754 | 4.5754 | 4.5754 | 4.5754
2021-02-07 11:00 | 1.4118 | 1.718 | 1.6809 | 1.808 | 1.7127 | 1.8398 | 1.4404 | 2.47 | 3.0478 | 3.0478 | 3.4331 | 3.4331 | 2019-04-06 23:00 | 1.5623 | 2.6809 | 4.5312 | 4.5312 | 4.5312 | 4.5312
2021-02-07 12:00 | 1.3575 | 1.6519 | 1.6163 | 1.7385 | 1.6468 | 1.769 | 1.4625 | 2.508 | 3.0947 | 3.0947 | 3.4859 | 3.4859 | 2019-04-07 | 1.4099 | 2.4194 | 4.0891 | 4.0891 | 4.0891 | 4.0891
2021-02-07 13:00 | 1.549 | 1.8849 | 1.8443 | 1.9837 | 1.8791 | 2.0185 | 1.569 | 2.6905 | 3.32 | 3.32 | 3.7396 | 3.7396 | 2019-04-07 01:00 | 1.3642 | 2.3409 | 3.9565 | 3.9565 | 3.9565 | 3.9565
2021-02-07 14:00 | 1.4175 | 1.725 | 1.6878 | 1.8153 | 1.7196 | 1.8472 | 1.5575 | 2.6709 | 3.2958 | 3.2958 | 3.7123 | 3.7123 | 2019-04-07 02:00 | 1.3184 | 2.2624 | 3.8239 | 3.8239 | 3.8239 | 3.8239
2021-02-07 15:00 | 1.5061 | 1.8328 | 1.7932 | 1.9288 | 1.8271 | 1.9627 | 1.5404 | 2.6415 | 3.2595 | 3.2595 | 3.6715 | 3.6715 | 2019-04-07 03:00 | 1.3337 | 2.2886 | 3.8681 | 3.8681 | 3.8681 | 3.8681
2021-02-07 16:00 | 1.5918 | 1.9371 | 1.8953 | 2.0386 | 1.9311 | 2.0744 | 1.569 | 2.6905 | 3.32 | 3.32 | 3.7396 | 3.7396 | 2019-04-07 04:00 | 1.3565 | 2.3278 | 3.9344 | 3.9344 | 3.9344 | 3.9344
2021-02-07 17:00 | 1.8307 | 2.2278 | 2.1797 | 2.3445 | 2.2209 | 2.3857 | 1.6604 | 2.8474 | 3.5135 | 3.5135 | 3.9576 | 3.9576 | 2019-04-07 05:00 | 1.509 | 2.5894 | 4.3765 | 4.3765 | 4.3765 | 4.3765
2021-02-07 18:00 | 1.9719 | 2.3996 | 2.3479 | 2.5254 | 2.3922 | 2.5697 | 1.7062 | 2.9258 | 3.6102 | 3.6102 | 4.0665 | 4.0665 | 2019-04-07 06:00 | 1.5699 | 2.694 | 4.5533 | 4.5533 | 4.5533 | 4.5533
2021-02-07 19:00 | 1.9005 | 2.3127 | 2.2628 | 2.4339 | 2.3056 | 2.4766 | 1.6033 | 2.7494 | 3.3925 | 3.3925 | 3.8213 | 3.8213 | 2019-04-07 07:00 | 1.7605 | 3.0209 | 5.1059 | 5.1059 | 5.1059 | 5.1059
2021-02-07 20:00 | 1.8548 | 2.2571 | 2.2084 | 2.3753 | 2.2501 | 2.417 | 1.6318 | 2.7984 | 3.453 | 3.453 | 3.8894 | 3.8894 | 2019-04-07 08:00 | 1.8595 | 3.191 | 5.3932 | 5.3932 | 5.3932 | 5.3932
2021-02-07 21:00 | 1.7519 | 2.1319 | 2.0859 | 2.2435 | 2.1253 | 2.283 | 1.5518 | 2.6611 | 3.2837 | 3.2837 | 3.6987 | 3.6987 | 2019-04-07 09:00 | 1.89 | 3.2433 | 5.4817 | 5.4817 | 5.4817 | 5.4817
2021-02-07 22:00 | 1.6128 | 1.9627 | 1.9203 | 2.0655 | 1.9566 | 2.1018 | 1.3375 | 2.2936 | 2.8301 | 2.8301 | 3.1878 | 3.1878 | 2019-04-07 10:00 | 1.9129 | 3.2825 | 5.548 | 5.548 | 5.548 | 5.548
2021-02-07 23:00 | 1.4747 | 1.7945 | 1.7558 | 1.8885 | 1.789 | 1.9217 | 1.0974 | 1.8819 | 2.3222 | 2.3222 | 2.6157 | 2.6157 | 2019-04-07 11:00 | 2.1186 | 3.6356 | 6.1448 | 6.1448 | 6.1448 | 6.1448
2021-02-08 | 1.4119 | 1.7181 | 1.681 | 1.8081 | 1.7128 | 1.8399 | 0.92683 | 1.5894 | 1.9612 | 1.9612 | 2.209 | 2.209 | 2019-04-07 12:00 | 2.0119 | 3.4525 | 5.8353 | 5.8353 | 5.8353 | 5.8353
2021-02-08 01:00 | 1.2918 | 1.5719 | 1.538 | 1.6543 | 1.5671 | 1.6834 | 0.86594 | 1.4849 | 1.8323 | 1.8323 | 2.0639 | 2.0639 | 2019-04-07 13:00 | 1.9053 | 3.2694 | 5.5259 | 5.5259 | 5.5259 | 5.5259
2021-02-08 02:00 | 1.206 | 1.4676 | 1.4359 | 1.5445 | 1.4631 | 1.5716 | 0.76026 | 1.3037 | 1.6087 | 1.6087 | 1.812 | 1.812 | 2019-04-07 14:00 | 1.9662 | 3.374 | 5.7027 | 5.7027 | 5.7027 | 5.7027
2021-02-08 03:00 | 1.2117 | 1.4746 | 1.4428 | 1.5518 | 1.47 | 1.5791 | 0.77162 | 1.3232 | 1.6328 | 1.6328 | 1.8391 | 1.8391 | 2019-04-07 15:00 | 1.9357 | 3.3217 | 5.6143 | 5.6143 | 5.6143 | 5.6143
2021-02-08 04:00 | 1.2489 | 1.5198 | 1.487 | 1.5994 | 1.5151 | 1.6275 | 0.73447 | 1.2595 | 1.5542 | 1.5542 | 1.7506 | 1.7506 | 2019-04-07 16:00 | 2.0272 | 3.4787 | 5.8795 | 5.8795 | 5.8795 | 5.8795
2021-02-08 05:00 | 1.3375 | 1.6276 | 1.5925 | 1.7128 | 1.6226 | 1.7429 | 0.79163 | 1.3575 | 1.6751 | 1.6751 | 1.8868 | 1.8868 | 2019-04-07 17:00 | 1.9205 | 3.2956 | 5.5701 | 5.5701 | 5.5701 | 5.5701
2021-02-08 06:00 | 1.7462 | 2.1249 | 2.0791 | 2.2362 | 2.1184 | 2.2755 | 0.97168 | 1.6663 | 2.0561 | 2.0561 | 2.316 | 2.316 | 2019-04-07 18:00 | 1.8214 | 3.1256 | 5.2827 | 5.2827 | 5.2827 | 5.2827
2021-02-08 07:00 | 2.0091 | 2.4449 | 2.3921 | 2.5729 | 2.4373 | 2.6181 | 1.226 | 2.1024 | 2.5943 | 2.5943 | 2.9222 | 2.9222 | 2019-04-07 19:00 | 1.6614 | 2.8509 | 4.8186 | 4.8186 | 4.8186 | 4.8186
2021-02-08 08:00 | 2.2063 | 2.6848 | 2.6269 | 2.8255 | 2.6765 | 2.8751 | 1.3232 | 2.2691 | 2.7999 | 2.7999 | 3.1538 | 3.1538 | 2019-04-07 20:00 | 1.6157 | 2.7725 | 4.6859 | 4.6859 | 4.6859 | 4.6859
2021-02-08 09:00 | 2.0863 | 2.5388 | 2.484 | 2.6718 | 2.5309 | 2.7187 | 1.2832 | 2.2005 | 2.7152 | 2.7152 | 3.0584 | 3.0584 | 2019-04-07 21:00 | 1.5852 | 2.7202 | 4.5975 | 4.5975 | 4.5975 | 4.5975
2021-02-08 10:00 | 2.0577 | 2.504 | 2.45 | 2.6352 | 2.4963 | 2.6814 | 1.3518 | 2.3181 | 2.8604 | 2.8604 | 3.2219 | 3.2219 | 2019-04-07 22:00 | 1.4023 | 2.4063 | 4.067 | 4.067 | 4.067 | 4.067
2021-02-08 11:00 | 2.1577 | 2.6257 | 2.5691 | 2.7632 | 2.6176 | 2.8118 | 1.3603 | 2.3328 | 2.8785 | 2.8785 | 3.2423 | 3.2423 | 2019-04-07 23:00 | 1.3946 | 2.3932 | 4.0449 | 4.0449 | 4.0449 | 4.0449
2021-02-08 12:00 | 2.2463 | 2.7335 | 2.6745 | 2.8767 | 2.7251 | 2.9272 | 1.3775 | 2.3622 | 2.9148 | 2.9148 | 3.2832 | 3.2832 | 2019-04-08 | 1.3489 | 2.3148 | 3.9123 | 3.9123 | 3.9123 | 3.9123
2021-02-08 13:00 | 2.172 | 2.6431 | 2.5861 | 2.7815 | 2.6349 | 2.8304 | 1.3318 | 2.2838 | 2.818 | 2.818 | 3.1742 | 3.1742 | 2019-04-08 01:00 | 1.3337 | 2.2886 | 3.8681 | 3.8681 | 3.8681 | 3.8681
2021-02-08 14:00 | 2.352 | 2.8622 | 2.8004 | 3.0121 | 2.8534 | 3.065 | 1.3746 | 2.3573 | 2.9088 | 2.9088 | 3.2764 | 3.2764 | 2019-04-08 02:00 | 1.3718 | 2.354 | 3.9786 | 3.9786 | 3.9786 | 3.9786
2021-02-08 15:00 | 2.3379 | 2.845 | 2.7836 | 2.994 | 2.8362 | 3.0466 | 1.3003 | 2.2299 | 2.7515 | 2.7515 | 3.0993 | 3.0993 | 2019-04-08 03:00 | 1.3565 | 2.3278 | 3.9344 | 3.9344 | 3.9344 | 3.9344
2021-02-08 16:00 | 2.3492 | 2.8587 | 2.797 | 3.0085 | 2.8499 | 3.0613 | 1.3318 | 2.2838 | 2.818 | 2.818 | 3.1742 | 3.1742 | 2019-04-08 04:00 | 1.4556 | 2.4978 | 4.2218 | 4.2218 | 4.2218 | 4.2218
2021-02-08 17:00 | 2.3635 | 2.8761 | 2.8141 | 3.0268 | 2.8672 | 3.0799 | 1.5461 | 2.6513 | 3.2716 | 3.2716 | 3.6851 | 3.6851 | 2019-04-08 05:00 | 1.5394 | 2.6417 | 4.4649 | 4.4649 | 4.4649 | 4.4649
2021-02-08 18:00 | 2.4206 | 2.9456 | 2.8821 | 3.1 | 2.9366 | 3.1544 | 1.4804 | 2.5386 | 3.1325 | 3.1325 | 3.5284 | 3.5284 | 2019-04-08 06:00 | 1.6538 | 2.8379 | 4.7965 | 4.7965 | 4.7965 | 4.7965
2021-02-08 19:00 | 2.2777 | 2.7718 | 2.712 | 2.917 | 2.7632 | 2.9682 | 1.5147 | 2.5974 | 3.2051 | 3.2051 | 3.6102 | 3.6102 | 2019-04-08 07:00 | 1.7223 | 2.9556 | 4.9954 | 4.9954 | 4.9954 | 4.9954
2021-02-08 20:00 | 2.1977 | 2.6744 | 2.6167 | 2.8145 | 2.6661 | 2.8639 | 1.4689 | 2.519 | 3.1083 | 3.1083 | 3.5012 | 3.5012 | 2019-04-08 08:00 | 2.1186 | 3.6356 | 6.1448 | 6.1448 | 6.1448 | 6.1448
2021-02-08 21:00 | 1.9862 | 2.417 | 2.3649 | 2.5437 | 2.4096 | 2.5883 | 1.3718 | 2.3524 | 2.9027 | 2.9027 | 3.2696 | 3.2696 | 2019-04-08 09:00 | 2.0805 | 3.5702 | 6.0343 | 6.0343 | 6.0343 | 6.0343
2021-02-08 22:00 | 1.6723 | 2.0351 | 1.9912 | 2.1417 | 2.0288 | 2.1793 | 1.2603 | 2.1613 | 2.6669 | 2.6669 | 3.0039 | 3.0039 | 2019-04-08 10:00 | 2.2101 | 3.7925 | 6.41 | 6.41 | 6.41 | 6.41
2021-02-08 23:00 | 1.4689 | 1.7876 | 1.749 | 1.8812 | 1.7821 | 1.9143 | 1.0274 | 1.7619 | 2.174 | 2.174 | 2.4488 | 2.4488 | 2019-04-08 11:00 | 2.4768 | 4.2503 | 7.1836 | 7.1836 | 7.1836 | 7.1836
2021-02-09 | 1.3746 | 1.6728 | 1.6367 | 1.7604 | 1.6676 | 1.7914 | 0.90891 | 1.5586 | 1.9233 | 1.9233 | 2.1664 | 2.1664 | 2019-04-08 12:00 | 2.5454 | 4.368 | 7.3826 | 7.3826 | 7.3826 | 7.3826
2021-02-09 01:00 | 1.2632 | 1.5372 | 1.5041 | 1.6177 | 1.5325 | 1.6462 | 0.86594 | 1.4849 | 1.8323 | 1.8323 | 2.0639 | 2.0639 | 2019-04-08 13:00 | 2.4768 | 4.2503 | 7.1836 | 7.1836 | 7.1836 | 7.1836
2021-02-09 02:00 | 1.206 | 1.4676 | 1.4359 | 1.5445 | 1.4631 | 1.5716 | 0.76591 | 1.3134 | 1.6207 | 1.6207 | 1.8255 | 1.8255 | 2019-04-08 14:00 | 2.4616 | 4.2241 | 7.1394 | 7.1394 | 7.1394 | 7.1394
2021-02-09 03:00 | 1.2289 | 1.4954 | 1.4632 | 1.5738 | 1.4908 | 1.6014 | 0.71447 | 1.2252 | 1.5118 | 1.5118 | 1.7029 | 1.7029 | 2019-04-08 15:00 | 2.4692 | 4.2372 | 7.1615 | 7.1615 | 7.1615 | 7.1615
2021-02-09 04:00 | 1.1946 | 1.4537 | 1.4223 | 1.5298 | 1.4492 | 1.5567 | 0.73161 | 1.2546 | 1.5481 | 1.5481 | 1.7438 | 1.7438 | 2019-04-08 16:00 | 2.4845 | 4.2633 | 7.2057 | 7.2057 | 7.2057 | 7.2057
2021-02-09 05:00 | 1.412 | 1.7183 | 1.6812 | 1.8083 | 1.713 | 1.84 | 0.79163 | 1.3575 | 1.6751 | 1.6751 | 1.8868 | 1.8868 | 2019-04-08 17:00 | 2.1567 | 3.701 | 6.2553 | 6.2553 | 6.2553 | 6.2553
2021-02-09 06:00 | 1.6519 | 2.0101 | 1.9668 | 2.1154 | 2.0039 | 2.1526 | 1.0145 | 1.7398 | 2.1468 | 2.1468 | 2.4181 | 2.4181 | 2019-04-08 18:00 | 2.0805 | 3.5702 | 6.0343 | 6.0343 | 6.0343 | 6.0343
2021-02-09 07:00 | 1.9205 | 2.337 | 2.2866 | 2.4595 | 2.3298 | 2.5027 | 1.2775 | 2.1907 | 2.7031 | 2.7031 | 3.0448 | 3.0448 | 2019-04-08 19:00 | 2.0805 | 3.5702 | 6.0343 | 6.0343 | 6.0343 | 6.0343
2021-02-09 08:00 | 2.0262 | 2.4657 | 2.4125 | 2.5949 | 2.4581 | 2.6405 | 1.3146 | 2.2544 | 2.7818 | 2.7818 | 3.1333 | 3.1333 | 2019-04-08 20:00 | 1.8443 | 3.1648 | 5.349 | 5.349 | 5.349 | 5.349
2021-02-09 09:00 | 2.0462 | 2.4901 | 2.4364 | 2.6205 | 2.4824 | 2.6666 | 1.3661 | 2.3426 | 2.8906 | 2.8906 | 3.256 | 3.256 | 2019-04-08 21:00 | 1.73 | 2.9686 | 5.0175 | 5.0175 | 5.0175 | 5.0175
2021-02-09 10:00 | 2.1434 | 2.6083 | 2.552 | 2.7449 | 2.6003 | 2.7932 | 1.4632 | 2.5092 | 3.0962 | 3.0962 | 3.4876 | 3.4876 | 2019-04-08 22:00 | 1.6614 | 2.8509 | 4.8186 | 4.8186 | 4.8186 | 4.8186
2021-02-09 11:00 | 2.252 | 2.7405 | 2.6813 | 2.884 | 2.732 | 2.9347 | 1.3889 | 2.3818 | 2.939 | 2.939 | 3.3105 | 3.3105 | 2019-04-08 23:00 | 1.6233 | 2.7855 | 4.708 | 4.708 | 4.708 | 4.708
2021-02-09 12:00 | 2.1777 | 2.65 | 2.5929 | 2.7889 | 2.6419 | 2.8379 | 1.3689 | 2.3475 | 2.8967 | 2.8967 | 3.2628 | 3.2628 | 2019-04-09 | 1.5242 | 2.6155 | 4.4207 | 4.4207 | 4.4207 | 4.4207
2021-02-09 13:00 | 2.2349 | 2.7196 | 2.6609 | 2.8621 | 2.7112 | 2.9124 | 1.4232 | 2.4406 | 3.0116 | 3.0116 | 3.3922 | 3.3922 | 2019-04-09 01:00 | 1.5318 | 2.6286 | 4.4428 | 4.4428 | 4.4428 | 4.4428
2021-02-09 14:00 | 2.2206 | 2.7022 | 2.6439 | 2.8438 | 2.6939 | 2.8937 | 1.3975 | 2.3965 | 2.9571 | 2.9571 | 3.3309 | 3.3309 | 2019-04-09 02:00 | 1.4937 | 2.5632 | 4.3323 | 4.3323 | 4.3323 | 4.3323
2021-02-09 15:00 | 2.212 | 2.6918 | 2.6337 | 2.8328 | 2.6835 | 2.8826 | 1.2489 | 2.1416 | 2.6427 | 2.6427 | 2.9767 | 2.9767 | 2019-04-09 03:00 | 1.4861 | 2.5501 | 4.3102 | 4.3102 | 4.3102 | 4.3102
2021-02-09 16:00 | 2.1491 | 2.6153 | 2.5588 | 2.7523 | 2.6072 | 2.8006 | 1.4118 | 2.421 | 2.9874 | 2.9874 | 3.3649 | 3.3649 | 2019-04-09 04:00 | 1.4709 | 2.524 | 4.266 | 4.266 | 4.266 | 4.266
2021-02-09 17:00 | 2.2377 | 2.7231 | 2.6643 | 2.8657 | 2.7147 | 2.9161 | 1.4146 | 2.4259 | 2.9934 | 2.9934 | 3.3718 | 3.3718 | 2019-04-09 05:00 | 1.6461 | 2.8248 | 4.7743 | 4.7743 | 4.7743 | 4.7743
2021-02-09 18:00 | 2.2549 | 2.7439 | 2.6848 | 2.8877 | 2.7355 | 2.9384 | 1.5604 | 2.6758 | 3.3018 | 3.3018 | 3.7192 | 3.7192 | 2019-04-09 06:00 | 1.7909 | 3.0733 | 5.1943 | 5.1943 | 5.1943 | 5.1943
2021-02-09 19:00 | 2.192 | 2.6674 | 2.6099 | 2.8072 | 2.6592 | 2.8565 | 1.5204 | 2.6072 | 3.2172 | 3.2172 | 3.6238 | 3.6238 | 2019-04-09 07:00 | 1.9357 | 3.3217 | 5.6143 | 5.6143 | 5.6143 | 5.6143
2021-02-09 20:00 | 2.0863 | 2.5388 | 2.484 | 2.6718 | 2.5309 | 2.7187 | 1.4718 | 2.5239 | 3.1144 | 3.1144 | 3.508 | 3.508 | 2019-04-09 08:00 | 2.111 | 3.6225 | 6.1227 | 6.1227 | 6.1227 | 6.1227
2021-02-09 21:00 | 1.9234 | 2.3405 | 2.2901 | 2.4632 | 2.3333 | 2.5064 | 1.4175 | 2.4308 | 2.9995 | 2.9995 | 3.3786 | 3.3786 | 2019-04-09 09:00 | 2.1034 | 3.6094 | 6.1006 | 6.1006 | 6.1006 | 6.1006
2021-02-09 22:00 | 1.7176 | 2.0901 | 2.045 | 2.1996 | 2.0837 | 2.2383 | 1.2575 | 2.1564 | 2.6608 | 2.6608 | 2.9971 | 2.9971 | 2019-04-09 10:00 | 2.1644 | 3.7141 | 6.2774 | 6.2774 | 6.2774 | 6.2774
2021-02-09 23:00 | 1.5204 | 1.8502 | 1.8102 | 1.9471 | 1.8445 | 1.9813 | 1.1031 | 1.8917 | 2.3343 | 2.3343 | 2.6293 | 2.6293 | 2019-04-09 11:00 | 2.3015 | 3.9495 | 6.6753 | 6.6753 | 6.6753 | 6.6753
2021-02-10 | 1.4061 | 1.711 | 1.6741 | 1.8007 | 1.7058 | 1.8323 | 0.92881 | 1.5928 | 1.9654 | 1.9654 | 2.2138 | 2.2138 | 2019-04-09 12:00 | 2.2406 | 3.8448 | 6.4984 | 6.4984 | 6.4984 | 6.4984
2021-02-10 01:00 | 1.306 | 1.5893 | 1.555 | 1.6726 | 1.5844 | 1.702 | 0.81449 | 1.3967 | 1.7235 | 1.7235 | 1.9413 | 1.9413 | 2019-04-09 13:00 | 2.2558 | 3.871 | 6.5426 | 6.5426 | 6.5426 | 6.5426
2021-02-10 02:00 | 1.2117 | 1.4746 | 1.4428 | 1.5518 | 1.47 | 1.5791 | 0.75813 | 1.3001 | 1.6042 | 1.6042 | 1.807 | 1.807 | 2019-04-09 14:00 | 2.3015 | 3.9495 | 6.6753 | 6.6753 | 6.6753 | 6.6753
2021-02-10 03:00 | 1.2146 | 1.478 | 1.4462 | 1.5555 | 1.4735 | 1.5828 | 0.76877 | 1.3183 | 1.6267 | 1.6267 | 1.8323 | 1.8323 | 2019-04-09 15:00 | 2.2939 | 3.9364 | 6.6531 | 6.6531 | 6.6531 | 6.6531
2021-02-10 04:00 | 1.2289 | 1.4954 | 1.4632 | 1.5738 | 1.4908 | 1.6014 | 0.72018 | 1.235 | 1.5239 | 1.5239 | 1.7165 | 1.7165 | 2019-04-09 16:00 | 2.233 | 3.8318 | 6.4763 | 6.4763 | 6.4763 | 6.4763
2021-02-10 05:00 | 1.4313 | 1.7417 | 1.7041 | 1.8329 | 1.7363 | 1.8651 | 0.84021 | 1.4408 | 1.7779 | 1.7779 | 2.0026 | 2.0026 | 2019-04-09 17:00 | 2.233 | 3.8318 | 6.4763 | 6.4763 | 6.4763 | 6.4763
2021-02-10 06:00 | 1.649 | 2.0067 | 1.9634 | 2.1118 | 2.0005 | 2.1489 | 1.0203 | 1.7496 | 2.1589 | 2.1589 | 2.4317 | 2.4317 | 2019-04-09 18:00 | 2.1034 | 3.6094 | 6.1006 | 6.1006 | 6.1006 | 6.1006
2021-02-10 07:00 | 1.9091 | 2.3231 | 2.273 | 2.4448 | 2.316 | 2.4878 | 1.2775 | 2.1907 | 2.7031 | 2.7031 | 3.0448 | 3.0448 | 2019-04-09 19:00 | 1.9967 | 3.4264 | 5.7911 | 5.7911 | 5.7911 | 5.7911
2021-02-10 08:00 | 2.0948 | 2.5492 | 2.4942 | 2.6827 | 2.5413 | 2.7299 | 1.3375 | 2.2936 | 2.8301 | 2.8301 | 3.1878 | 3.1878 | 2019-04-09 20:00 | 1.8214 | 3.1256 | 5.2827 | 5.2827 | 5.2827 | 5.2827
2021-02-10 09:00 | 2.0777 | 2.5283 | 2.4738 | 2.6608 | 2.5205 | 2.7075 | 1.3403 | 2.2985 | 2.8362 | 2.8362 | 3.1947 | 3.1947 | 2019-04-09 21:00 | 1.7452 | 2.9948 | 5.0617 | 5.0617 | 5.0617 | 5.0617
2021-02-10 10:00 | 2.0548 | 2.5005 | 2.4466 | 2.6315 | 2.4928 | 2.6777 | 1.4861 | 2.5484 | 3.1446 | 3.1446 | 3.542 | 3.542 | 2019-04-09 22:00 | 1.7147 | 2.9425 | 4.9733 | 4.9733 | 4.9733 | 4.9733
2021-02-10 11:00 | 2.152 | 2.6187 | 2.5623 | 2.7559 | 2.6107 | 2.8043 | 1.3461 | 2.3083 | 2.8483 | 2.8483 | 3.2083 | 3.2083 | 2019-04-09 23:00 | 1.6461 | 2.8248 | 4.7743 | 4.7743 | 4.7743 | 4.7743
2021-02-10 12:00 | 2.1663 | 2.6361 | 2.5793 | 2.7742 | 2.628 | 2.823 | 1.3746 | 2.3573 | 2.9088 | 2.9088 | 3.2764 | 3.2764 | 2019-04-10 | 1.5242 | 2.6155 | 4.4207 | 4.4207 | 4.4207 | 4.4207
2021-02-10 13:00 | 2.1463 | 2.6118 | 2.5554 | 2.7486 | 2.6037 | 2.7969 | 1.3432 | 2.3034 | 2.8422 | 2.8422 | 3.2015 | 3.2015 | 2019-04-10 01:00 | 1.4175 | 2.4324 | 4.1112 | 4.1112 | 4.1112 | 4.1112
2021-02-10 14:00 | 2.2006 | 2.6779 | 2.6201 | 2.8181 | 2.6696 | 2.8677 | 1.3118 | 2.2495 | 2.7757 | 2.7757 | 3.1265 | 3.1265 | 2019-04-10 02:00 | 1.3718 | 2.354 | 3.9786 | 3.9786 | 3.9786 | 3.9786
2021-02-10 15:00 | 2.2492 | 2.737 | 2.6779 | 2.8804 | 2.7286 | 2.931 | 1.2918 | 2.2152 | 2.7334 | 2.7334 | 3.0789 | 3.0789 | 2019-04-10 03:00 | 1.4023 | 2.4063 | 4.067 | 4.067 | 4.067 | 4.067
2021-02-10 16:00 | 2.3978 | 2.9178 | 2.8549 | 3.0707 | 2.9088 | 3.1246 | 1.4004 | 2.4014 | 2.9632 | 2.9632 | 3.3377 | 3.3377 | 2019-04-10 04:00 | 1.4404 | 2.4717 | 4.1776 | 4.1776 | 4.1776 | 4.1776
2021-02-10 17:00 | 2.3177 | 2.8205 | 2.7596 | 2.9682 | 2.8118 | 3.0204 | 1.4461 | 2.4798 | 3.0599 | 3.0599 | 3.4467 | 3.4467 | 2019-04-10 05:00 | 1.6233 | 2.7855 | 4.708 | 4.708 | 4.708 | 4.708
2021-02-10 18:00 | 2.3978 | 2.9178 | 2.8549 | 3.0707 | 2.9088 | 3.1246 | 1.5375 | 2.6366 | 3.2534 | 3.2534 | 3.6647 | 3.6647 | 2019-04-10 06:00 | 1.8214 | 3.1256 | 5.2827 | 5.2827 | 5.2827 | 5.2827
2021-02-10 19:00 | 2.2949 | 2.7926 | 2.7324 | 2.9389 | 2.784 | 2.9906 | 1.5204 | 2.6072 | 3.2172 | 3.2172 | 3.6238 | 3.6238 | 2019-04-10 07:00 | 1.89 | 3.2433 | 5.4817 | 5.4817 | 5.4817 | 5.4817
2021-02-10 20:00 | 2.1463 | 2.6118 | 2.5554 | 2.7486 | 2.6037 | 2.7969 | 1.5604 | 2.6758 | 3.3018 | 3.3018 | 3.7192 | 3.7192 | 2019-04-10 08:00 | 1.9967 | 3.4264 | 5.7911 | 5.7911 | 5.7911 | 5.7911
2021-02-10 21:00 | 1.9234 | 2.3405 | 2.29 | 2.4631 | 2.3333 | 2.5064 | 1.5375 | 2.6366 | 3.2534 | 3.2534 | 3.6647 | 3.6647 | 2019-04-10 09:00 | 2.1263 | 3.6487 | 6.1669 | 6.1669 | 6.1669 | 6.1669
2021-02-10 22:00 | 1.7147 | 2.0866 | 2.0416 | 2.196 | 2.0802 | 2.2345 | 1.3718 | 2.3524 | 2.9027 | 2.9027 | 3.2696 | 3.2696 | 2019-04-10 10:00 | 2.0729 | 3.5571 | 6.0121 | 6.0121 | 6.0121 | 6.0121
2021-02-10 23:00 | 1.4693 | 1.788 | 1.7494 | 1.8816 | 1.7825 | 1.9147 | 1.0803 | 1.8525 | 2.2859 | 2.2859 | 2.5748 | 2.5748 | 2019-04-10 11:00 | 2.1415 | 3.6748 | 6.2111 | 6.2111 | 6.2111 | 6.2111
2021-02-11 | 1.4061 | 1.7111 | 1.6741 | 1.8007 | 1.7058 | 1.8323 | 0.92023 | 1.5781 | 1.9472 | 1.9472 | 2.1933 | 2.1933 | 2019-04-10 12:00 | 2.1339 | 3.6618 | 6.189 | 6.189 | 6.189 | 6.189
2021-02-11 01:00 | 1.2775 | 1.5545 | 1.521 | 1.636 | 1.5498 | 1.6647 | 0.80878 | 1.3869 | 1.7114 | 1.7114 | 1.9277 | 1.9277 | 2019-04-10 13:00 | 2.1263 | 3.6487 | 6.1669 | 6.1669 | 6.1669 | 6.1669
2021-02-11 02:00 | 1.2317 | 1.4989 | 1.4666 | 1.5774 | 1.4943 | 1.6051 | 0.76591 | 1.3134 | 1.6207 | 1.6207 | 1.8255 | 1.8255 | 2019-04-10 14:00 | 2.2101 | 3.7925 | 6.41 | 6.41 | 6.41 | 6.41
2021-02-11 03:00 | 1.1808 | 1.437 | 1.406 | 1.5122 | 1.4325 | 1.5388 | 0.70304 | 1.2056 | 1.4876 | 1.4876 | 1.6757 | 1.6757 | 2019-04-10 15:00 | 2.2939 | 3.9364 | 6.6531 | 6.6531 | 6.6531 | 6.6531
2021-02-11 04:00 | 1.1944 | 1.4534 | 1.4221 | 1.5296 | 1.449 | 1.5565 | 0.76877 | 1.3183 | 1.6267 | 1.6267 | 1.8323 | 1.8323 | 2019-04-10 16:00 | 2.4311 | 4.1718 | 7.051 | 7.051 | 7.051 | 7.051
2021-02-11 05:00 | 1.4342 | 1.7453 | 1.7076 | 1.8367 | 1.7399 | 1.869 | 0.8002 | 1.3722 | 1.6932 | 1.6932 | 1.9073 | 1.9073 | 2019-04-10 17:00 | 2.2482 | 3.8579 | 6.5205 | 6.5205 | 6.5205 | 6.5205
2021-02-11 06:00 | 1.6719 | 2.0345 | 1.9906 | 2.1411 | 2.0282 | 2.1787 | 1.0281 | 1.7631 | 2.1755 | 2.1755 | 2.4505 | 2.4505 | 2019-04-10 18:00 | 2.1339 | 3.6618 | 6.189 | 6.189 | 6.189 | 6.189
2021-02-11 07:00 | 1.9234 | 2.3405 | 2.29 | 2.4631 | 2.3333 | 2.5064 | 1.2546 | 2.1515 | 2.6548 | 2.6548 | 2.9903 | 2.9903 | 2019-04-10 19:00 | 2.0424 | 3.5048 | 5.9237 | 5.9237 | 5.9237 | 5.9237
2021-02-11 08:00 | 2.0863 | 2.5388 | 2.484 | 2.6718 | 2.5309 | 2.7187 | 1.3918 | 2.3867 | 2.945 | 2.945 | 3.3173 | 3.3173 | 2019-04-10 20:00 | 1.829 | 3.1386 | 5.3048 | 5.3048 | 5.3048 | 5.3048
2021-02-11 09:00 | 2.1634 | 2.6327 | 2.5759 | 2.7706 | 2.6245 | 2.8192 | 1.2832 | 2.2005 | 2.7152 | 2.7152 | 3.0584 | 3.0584 | 2019-04-10 21:00 | 1.8062 | 3.0994 | 5.2385 | 5.2385 | 5.2385 | 5.2385
2021-02-11 10:00 | 2.252 | 2.7405 | 2.6813 | 2.884 | 2.732 | 2.9347 | 1.3775 | 2.3622 | 2.9148 | 2.9148 | 3.2832 | 3.2832 | 2019-04-10 22:00 | 1.6919 | 2.9032 | 4.907 | 4.907 | 4.907 | 4.907
2021-02-11 11:00 | 2.2777 | 2.7718 | 2.712 | 2.917 | 2.7632 | 2.9682 | 1.3203 | 2.2642 | 2.7939 | 2.7939 | 3.147 | 3.147 | 2019-04-10 23:00 | 1.6157 | 2.7725 | 4.6859 | 4.6859 | 4.6859 | 4.6859
2021-02-11 12:00 | 2.3177 | 2.8205 | 2.7596 | 2.9682 | 2.8118 | 3.0204 | 1.4489 | 2.4847 | 3.066 | 3.066 | 3.4535 | 3.4535 | 2019-04-11 | 1.4937 | 2.5632 | 4.3323 | 4.3323 | 4.3323 | 4.3323
2021-02-11 13:00 | 2.3949 | 2.9143 | 2.8515 | 3.067 | 2.9054 | 3.1209 | 1.4289 | 2.4504 | 3.0236 | 3.0236 | 3.4058 | 3.4058 | 2019-04-11 01:00 | 1.5471 | 2.6548 | 4.487 | 4.487 | 4.487 | 4.487
2021-02-11 14:00 | 2.4692 | 3.0048 | 2.94 | 3.1622 | 2.9955 | 3.2177 | 1.4347 | 2.4602 | 3.0357 | 3.0357 | 3.4194 | 3.4194 | 2019-04-11 02:00 | 1.4251 | 2.4455 | 4.1333 | 4.1333 | 4.1333 | 4.1333
2021-02-11 15:00 | 2.4681 | 3.0034 | 2.9386 | 3.1607 | 2.9941 | 3.2162 | 1.3746 | 2.3573 | 2.9088 | 2.9088 | 3.2764 | 3.2764 | 2019-04-11 03:00 | 1.4785 | 2.5371 | 4.2881 | 4.2881 | 4.2881 | 4.2881
2021-02-11 16:00 | 2.6064 | 3.1717 | 3.1033 | 3.3379 | 3.1619 | 3.3965 | 1.4547 | 2.4945 | 3.0781 | 3.0781 | 3.4671 | 3.4671 | 2019-04-11 04:00 | 1.5166 | 2.6025 | 4.3986 | 4.3986 | 4.3986 | 4.3986
2021-02-11 17:00 | 2.5206 | 3.0674 | 3.0012 | 3.2281 | 3.0579 | 3.2848 | 1.589 | 2.7248 | 3.3623 | 3.3623 | 3.7873 | 3.7873 | 2019-04-11 05:00 | 1.6842 | 2.8902 | 4.8849 | 4.8849 | 4.8849 | 4.8849
2021-02-11 18:00 | 2.6493 | 3.2239 | 3.1543 | 3.3928 | 3.2139 | 3.4524 | 1.6004 | 2.7445 | 3.3865 | 3.3865 | 3.8145 | 3.8145 | 2019-04-11 06:00 | 1.9129 | 3.2825 | 5.548 | 5.548 | 5.548 | 5.548
2021-02-11 19:00 | 2.6092 | 3.1752 | 3.1067 | 3.3415 | 3.1654 | 3.4002 | 1.6118 | 2.7641 | 3.4107 | 3.4107 | 3.8418 | 3.8418 | 2019-04-11 07:00 | 1.9434 | 3.3348 | 5.6364 | 5.6364 | 5.6364 | 5.6364
2021-02-11 20:00 | 2.232 | 2.7161 | 2.6575 | 2.8584 | 2.7077 | 2.9086 | 1.5347 | 2.6317 | 3.2474 | 3.2474 | 3.6578 | 3.6578 | 2019-04-11 08:00 | 2.0348 | 3.4917 | 5.9016 | 5.9016 | 5.9016 | 5.9016
2021-02-11 21:00 | 2.2091 | 2.6883 | 2.6303 | 2.8291 | 2.68 | 2.8788 | 1.5147 | 2.5974 | 3.2051 | 3.2051 | 3.6102 | 3.6102 | 2019-04-11 09:00 | 2.1186 | 3.6356 | 6.1448 | 6.1448 | 6.1448 | 6.1448
2021-02-11 22:00 | 1.8862 | 2.2953 | 2.2458 | 2.4156 | 2.2882 | 2.458 | 1.4118 | 2.421 | 2.9874 | 2.9874 | 3.3649 | 3.3649 | 2019-04-11 10:00 | 2.0882 | 3.5833 | 6.0564 | 6.0564 | 6.0564 | 6.0564
2021-02-11 23:00 | 1.5833 | 1.9267 | 1.8851 | 2.0276 | 1.9207 | 2.0632 | 1.106 | 1.8966 | 2.3403 | 2.3403 | 2.6361 | 2.6361 | 2019-04-11 11:00 | 2.2025 | 3.7795 | 6.3879 | 6.3879 | 6.3879 | 6.3879
2021-02-12 | 1.449 | 1.7633 | 1.7252 | 1.8556 | 1.7578 | 1.8882 | 0.97739 | 1.6761 | 2.0682 | 2.0682 | 2.3296 | 2.3296 | 2019-04-11 12:00 | 2.2939 | 3.9364 | 6.6531 | 6.6531 | 6.6531 | 6.6531
2021-02-12 01:00 | 1.3232 | 1.6102 | 1.5755 | 1.6945 | 1.6052 | 1.7243 | 0.81449 | 1.3967 | 1.7235 | 1.7235 | 1.9413 | 1.9413 | 2019-04-11 13:00 | 2.3854 | 4.0933 | 6.9184 | 6.9184 | 6.9184 | 6.9184
2021-02-12 02:00 | 1.2632 | 1.5372 | 1.504 | 1.6177 | 1.5324 | 1.6461 | 0.78651 | 1.3487 | 1.6643 | 1.6643 | 1.8746 | 1.8746 | 2019-04-11 14:00 | 2.2863 | 3.9233 | 6.631 | 6.631 | 6.631 | 6.631
2021-02-12 03:00 | 1.2548 | 1.5269 | 1.494 | 1.6069 | 1.5222 | 1.6352 | 0.7802 | 1.3379 | 1.6509 | 1.6509 | 1.8596 | 1.8596 | 2019-04-11 15:00 | 2.2025 | 3.7795 | 6.3879 | 6.3879 | 6.3879 | 6.3879
2021-02-12 04:00 | 1.2543 | 1.5263 | 1.4934 | 1.6063 | 1.5216 | 1.6345 | 0.80538 | 1.3811 | 1.7042 | 1.7042 | 1.9196 | 1.9196 | 2019-04-11 16:00 | 2.2406 | 3.8448 | 6.4984 | 6.4984 | 6.4984 | 6.4984
2021-02-12 05:00 | 1.4775 | 1.798 | 1.7592 | 1.8922 | 1.7925 | 1.9254 | 0.81735 | 1.4016 | 1.7295 | 1.7295 | 1.9481 | 1.9481 | 2019-04-11 17:00 | 2.0196 | 3.4656 | 5.8574 | 5.8574 | 5.8574 | 5.8574
2021-02-12 06:00 | 1.7062 | 2.0762 | 2.0314 | 2.185 | 2.0698 | 2.2234 | 1.0117 | 1.7349 | 2.1407 | 2.1407 | 2.4113 | 2.4113 | 2019-04-11 18:00 | 2.0348 | 3.4917 | 5.9016 | 5.9016 | 5.9016 | 5.9016
2021-02-12 07:00 | 2.0405 | 2.4831 | 2.4295 | 2.6132 | 2.4755 | 2.6591 | 1.2603 | 2.1613 | 2.6669 | 2.6669 | 3.0039 | 3.0039 | 2019-04-11 19:00 | 1.9891 | 3.4133 | 5.769 | 5.769 | 5.769 | 5.769
2021-02-12 08:00 | 2.352 | 2.8622 | 2.8004 | 3.0121 | 2.8534 | 3.065 | 1.3546 | 2.323 | 2.8664 | 2.8664 | 3.2287 | 3.2287 | 2019-04-11 20:00 | 1.8367 | 3.1517 | 5.3269 | 5.3269 | 5.3269 | 5.3269
2021-02-12 09:00 | 2.3406 | 2.8483 | 2.7868 | 2.9975 | 2.8395 | 3.0501 | 1.2832 | 2.2005 | 2.7152 | 2.7152 | 3.0584 | 3.0584 | 2019-04-11 21:00 | 1.7071 | 2.9294 | 4.9512 | 4.9512 | 4.9512 | 4.9512
2021-02-12 10:00 | 2.4159 | 2.9399 | 2.8765 | 3.0939 | 2.9308 | 3.1482 | 1.3603 | 2.3328 | 2.8785 | 2.8785 | 3.2423 | 3.2423 | 2019-04-11 22:00 | 1.669 | 2.864 | 4.8407 | 4.8407 | 4.8407 | 4.8407
2021-02-12 11:00 | 2.5292 | 3.0778 | 3.0114 | 3.239 | 3.0683 | 3.2959 | 1.4232 | 2.4406 | 3.0116 | 3.0116 | 3.3922 | 3.3922 | 2019-04-11 23:00 | 1.5547 | 2.6678 | 4.5091 | 4.5091 | 4.5091 | 4.5091
2021-02-12 12:00 | 2.4864 | 3.0256 | 2.9604 | 3.1841 | 3.0163 | 3.2401 | 1.4261 | 2.4455 | 3.0176 | 3.0176 | 3.399 | 3.399 | 2019-04-12 | 1.5242 | 2.6155 | 4.4207 | 4.4207 | 4.4207 | 4.4207
2021-02-12 13:00 | 2.5264 | 3.0743 | 3.008 | 3.2354 | 3.0649 | 3.2922 | 1.4689 | 2.519 | 3.1083 | 3.1083 | 3.5012 | 3.5012 | 2019-04-12 01:00 | 1.4937 | 2.5632 | 4.3323 | 4.3323 | 4.3323 | 4.3323
2021-02-12 14:00 | 2.5206 | 3.0674 | 3.0012 | 3.2281 | 3.0579 | 3.2848 | 1.4832 | 2.5435 | 3.1385 | 3.1385 | 3.5352 | 3.5352 | 2019-04-12 02:00 | 1.4251 | 2.4455 | 4.1333 | 4.1333 | 4.1333 | 4.1333
2021-02-12 15:00 | 2.4092 | 2.9317 | 2.8685 | 3.0853 | 2.9227 | 3.1395 | 1.4232 | 2.4406 | 3.0116 | 3.0116 | 3.3922 | 3.3922 | 2019-04-12 03:00 | 1.4251 | 2.4455 | 4.1333 | 4.1333 | 4.1333 | 4.1333
2021-02-12 16:00 | 2.2463 | 2.7335 | 2.6745 | 2.8767 | 2.7251 | 2.9272 | 1.3861 | 2.3769 | 2.9329 | 2.9329 | 3.3036 | 3.3036 | 2019-04-12 04:00 | 1.4099 | 2.4194 | 4.0891 | 4.0891 | 4.0891 | 4.0891
2021-02-12 17:00 | 2.2749 | 2.7683 | 2.7086 | 2.9133 | 2.7598 | 2.9645 | 1.4289 | 2.4504 | 3.0236 | 3.0236 | 3.4058 | 3.4058 | 2019-04-12 05:00 | 1.6309 | 2.7986 | 4.7301 | 4.7301 | 4.7301 | 4.7301
2021-02-12 18:00 | 2.1548 | 2.6222 | 2.5657 | 2.7596 | 2.6141 | 2.8081 | 1.5604 | 2.6758 | 3.3018 | 3.3018 | 3.7192 | 3.7192 | 2019-04-12 06:00 | 1.8519 | 3.1779 | 5.3711 | 5.3711 | 5.3711 | 5.3711
2021-02-12 19:00 | 1.9634 | 2.3892 | 2.3377 | 2.5144 | 2.3818 | 2.5585 | 1.5461 | 2.6513 | 3.2716 | 3.2716 | 3.6851 | 3.6851 | 2019-04-12 07:00 | 1.829 | 3.1386 | 5.3048 | 5.3048 | 5.3048 | 5.3048
2021-02-12 20:00 | 1.829 | 2.2258 | 2.1777 | 2.3424 | 2.2189 | 2.3835 | 1.6118 | 2.7641 | 3.4107 | 3.4107 | 3.8418 | 3.8418 | 2019-04-12 08:00 | 2.111 | 3.6225 | 6.1227 | 6.1227 | 6.1227 | 6.1227
2021-02-12 21:00 | 1.7719 | 2.1562 | 2.1097 | 2.2692 | 2.1496 | 2.309 | 1.5061 | 2.5827 | 3.1869 | 3.1869 | 3.5897 | 3.5897 | 2019-04-12 09:00 | 2.1644 | 3.7141 | 6.2774 | 6.2774 | 6.2774 | 6.2774
2021-02-12 22:00 | 1.6347 | 1.9893 | 1.9464 | 2.0935 | 1.9831 | 2.1303 | 1.3489 | 2.3132 | 2.8543 | 2.8543 | 3.2151 | 3.2151 | 2019-04-12 10:00 | 2.1491 | 3.6879 | 6.2332 | 6.2332 | 6.2332 | 6.2332
2021-02-12 23:00 | 1.5775 | 1.9197 | 1.8783 | 2.0203 | 1.9138 | 2.0558 | 1.2175 | 2.0877 | 2.5761 | 2.5761 | 2.9018 | 2.9018 | 2019-04-12 11:00 | 2.2177 | 3.8056 | 6.4321 | 6.4321 | 6.4321 | 6.4321
2021-02-13 | 1.4661 | 1.7841 | 1.7456 | 1.8775 | 1.7786 | 1.9105 | 1.0436 | 1.7896 | 2.2082 | 2.2082 | 2.4873 | 2.4873 | 2019-04-12 12:00 | 2.3015 | 3.9495 | 6.6753 | 6.6753 | 6.6753 | 6.6753
2021-02-13 01:00 | 1.3146 | 1.5998 | 1.5653 | 1.6836 | 1.5948 | 1.7131 | 0.88632 | 1.5199 | 1.8755 | 1.8755 | 2.1125 | 2.1125 | 2019-04-12 13:00 | 2.2406 | 3.8448 | 6.4984 | 6.4984 | 6.4984 | 6.4984
2021-02-13 02:00 | 1.2808 | 1.5586 | 1.525 | 1.6402 | 1.5538 | 1.669 | 0.80878 | 1.3869 | 1.7114 | 1.7114 | 1.9277 | 1.9277 | 2019-04-12 14:00 | 2.2787 | 3.9102 | 6.6089 | 6.6089 | 6.6089 | 6.6089
2021-02-13 03:00 | 1.246 | 1.5163 | 1.4836 | 1.5957 | 1.5116 | 1.6238 | 0.79735 | 1.3673 | 1.6872 | 1.6872 | 1.9004 | 1.9004 | 2019-04-12 15:00 | 2.2787 | 3.9102 | 6.6089 | 6.6089 | 6.6089 | 6.6089
2021-02-13 04:00 | 1.2603 | 1.5337 | 1.5006 | 1.614 | 1.529 | 1.6424 | 0.74064 | 1.2701 | 1.5672 | 1.5672 | 1.7653 | 1.7653 | 2019-04-12 16:00 | 2.2787 | 3.9102 | 6.6089 | 6.6089 | 6.6089 | 6.6089
2021-02-13 05:00 | 1.2718 | 1.5476 | 1.5142 | 1.6287 | 1.5428 | 1.6573 | 0.81164 | 1.3918 | 1.7174 | 1.7174 | 1.9345 | 1.9345 | 2019-04-12 17:00 | 2.1491 | 3.6879 | 6.2332 | 6.2332 | 6.2332 | 6.2332
2021-02-13 06:00 | 1.3718 | 1.6693 | 1.6333 | 1.7568 | 1.6642 | 1.7876 | 0.91738 | 1.5732 | 1.9412 | 1.9412 | 2.1865 | 2.1865 | 2019-04-12 18:00 | 1.9967 | 3.4264 | 5.7911 | 5.7911 | 5.7911 | 5.7911
2021-02-13 07:00 | 1.5175 | 1.8467 | 1.8068 | 1.9434 | 1.841 | 1.9776 | 1.1146 | 1.9113 | 2.3584 | 2.3584 | 2.6565 | 2.6565 | 2019-04-12 19:00 | 1.89 | 3.2433 | 5.4817 | 5.4817 | 5.4817 | 5.4817
2021-02-13 08:00 | 1.5947 | 1.9406 | 1.8987 | 2.0422 | 1.9346 | 2.0781 | 1.2575 | 2.1564 | 2.6608 | 2.6608 | 2.9971 | 2.9971 | 2019-04-12 20:00 | 1.6995 | 2.9163 | 4.9291 | 4.9291 | 4.9291 | 4.9291
2021-02-13 09:00 | 1.709 | 2.0797 | 2.0348 | 2.1886 | 2.0733 | 2.2271 | 1.3775 | 2.3622 | 2.9148 | 2.9148 | 3.2832 | 3.2832 | 2019-04-12 21:00 | 1.6385 | 2.8117 | 4.7522 | 4.7522 | 4.7522 | 4.7522
2021-02-13 10:00 | 1.7862 | 2.1736 | 2.1267 | 2.2875 | 2.1669 | 2.3276 | 1.5861 | 2.7199 | 3.3563 | 3.3563 | 3.7805 | 3.7805 | 2019-04-12 22:00 | 1.6538 | 2.8379 | 4.7965 | 4.7965 | 4.7965 | 4.7965
2021-02-13 11:00 | 1.8205 | 2.2153 | 2.1675 | 2.3314 | 2.2085 | 2.3723 | 1.6833 | 2.8866 | 3.5619 | 3.5619 | 4.0121 | 4.0121 | 2019-04-12 23:00 | 1.6614 | 2.8509 | 4.8186 | 4.8186 | 4.8186 | 4.8186
2021-02-13 12:00 | 1.849 | 2.2501 | 2.2016 | 2.368 | 2.2432 | 2.4096 | 1.7033 | 2.9209 | 3.6042 | 3.6042 | 4.0597 | 4.0597 | 2019-04-13 | 1.4632 | 2.5109 | 4.2439 | 4.2439 | 4.2439 | 4.2439
2021-02-13 13:00 | 1.5804 | 1.9232 | 1.8817 | 2.0239 | 1.9173 | 2.0595 | 1.5833 | 2.715 | 3.3502 | 3.3502 | 3.7736 | 3.7736 | 2019-04-13 01:00 | 1.4404 | 2.4717 | 4.1776 | 4.1776 | 4.1776 | 4.1776
2021-02-13 14:00 | 1.7119 | 2.0832 | 2.0382 | 2.1923 | 2.0767 | 2.2308 | 1.6147 | 2.769 | 3.4167 | 3.4167 | 3.8486 | 3.8486 | 2019-04-13 02:00 | 1.4175 | 2.4324 | 4.1112 | 4.1112 | 4.1112 | 4.1112
2021-02-13 15:00 | 1.6633 | 2.024 | 1.9804 | 2.1301 | 2.0178 | 2.1675 | 1.6318 | 2.7984 | 3.453 | 3.453 | 3.8894 | 3.8894 | 2019-04-13 03:00 | 1.4175 | 2.4324 | 4.1112 | 4.1112 | 4.1112 | 4.1112
2021-02-13 16:00 | 1.6147 | 1.9649 | 1.9225 | 2.0679 | 1.9589 | 2.1042 | 1.5976 | 2.7395 | 3.3804 | 3.3804 | 3.8077 | 3.8077 | 2019-04-13 04:00 | 1.3946 | 2.3932 | 4.0449 | 4.0449 | 4.0449 | 4.0449
2021-02-13 17:00 | 1.6719 | 2.0345 | 1.9906 | 2.1411 | 2.0282 | 2.1787 | 1.5461 | 2.6513 | 3.2716 | 3.2716 | 3.6851 | 3.6851 | 2019-04-13 05:00 | 1.4861 | 2.5501 | 4.3102 | 4.3102 | 4.3102 | 4.3102
2021-02-13 18:00 | 1.649 | 2.0067 | 1.9634 | 2.1118 | 2.0005 | 2.1489 | 1.5118 | 2.5925 | 3.199 | 3.199 | 3.6034 | 3.6034 | 2019-04-13 06:00 | 1.5318 | 2.6286 | 4.4428 | 4.4428 | 4.4428 | 4.4428
2021-02-13 19:00 | 1.6833 | 2.0484 | 2.0042 | 2.1557 | 2.0421 | 2.1936 | 1.5461 | 2.6513 | 3.2716 | 3.2716 | 3.6851 | 3.6851 | 2019-04-13 07:00 | 1.6766 | 2.8771 | 4.8628 | 4.8628 | 4.8628 | 4.8628
2021-02-13 20:00 | 1.709 | 2.0797 | 2.0348 | 2.1886 | 2.0733 | 2.2271 | 1.569 | 2.6905 | 3.32 | 3.32 | 3.7396 | 3.7396 | 2019-04-13 08:00 | 1.9053 | 3.2694 | 5.5259 | 5.5259 | 5.5259 | 5.5259
2021-02-13 21:00 | 1.5461 | 1.8815 | 1.8409 | 1.98 | 1.8757 | 2.0148 | 1.4518 | 2.4896 | 3.072 | 3.072 | 3.4603 | 3.4603 | 2019-04-13 09:00 | 1.9053 | 3.2694 | 5.5259 | 5.5259 | 5.5259 | 5.5259
2021-02-13 22:00 | 1.5375 | 1.871 | 1.8307 | 1.969 | 1.8653 | 2.0036 | 1.3632 | 2.3377 | 2.8846 | 2.8846 | 3.2491 | 3.2491 | 2019-04-13 10:00 | 2.0119 | 3.4525 | 5.8353 | 5.8353 | 5.8353 | 5.8353
2021-02-13 23:00 | 1.4804 | 1.8015 | 1.7626 | 1.8958 | 1.7959 | 1.9292 | 1.0897 | 1.8687 | 2.3059 | 2.3059 | 2.5973 | 2.5973 | 2019-04-13 11:00 | 2.1263 | 3.6487 | 6.1669 | 6.1669 | 6.1669 | 6.1669
2021-02-14 | 1.4004 | 1.7041 | 1.6673 | 1.7934 | 1.6988 | 1.8249 | 1.0231 | 1.7545 | 2.1649 | 2.1649 | 2.4386 | 2.4386 | 2019-04-13 12:00 | 2.233 | 3.8318 | 6.4763 | 6.4763 | 6.4763 | 6.4763
2021-02-14 01:00 | 1.247 | 1.5175 | 1.4848 | 1.597 | 1.5128 | 1.625 | 0.90309 | 1.5487 | 1.9109 | 1.9109 | 2.1525 | 2.1525 | 2019-04-13 13:00 | 2.2025 | 3.7795 | 6.3879 | 6.3879 | 6.3879 | 6.3879
2021-02-14 02:00 | 1.2403 | 1.5093 | 1.4768 | 1.5884 | 1.5047 | 1.6163 | 0.7802 | 1.3379 | 1.6509 | 1.6509 | 1.8596 | 1.8596 | 2019-04-13 14:00 | 2.1949 | 3.7664 | 6.3658 | 6.3658 | 6.3658 | 6.3658
2021-02-14 03:00 | 1.1751 | 1.43 | 1.3991 | 1.5049 | 1.4256 | 1.5313 | 0.76305 | 1.3085 | 1.6146 | 1.6146 | 1.8187 | 1.8187 | 2019-04-13 15:00 | 2.0958 | 3.5964 | 6.0785 | 6.0785 | 6.0785 | 6.0785
2021-02-14 04:00 | 1.1974 | 1.4572 | 1.4257 | 1.5335 | 1.4527 | 1.5605 | 0.73733 | 1.2644 | 1.5602 | 1.5602 | 1.7574 | 1.7574 | 2019-04-13 16:00 | 2.1567 | 3.701 | 6.2553 | 6.2553 | 6.2553 | 6.2553
2021-02-14 05:00 | 1.2258 | 1.4917 | 1.4595 | 1.5699 | 1.4871 | 1.5975 | 0.74305 | 1.2742 | 1.5723 | 1.5723 | 1.771 | 1.771 | 2019-04-13 17:00 | 2.0653 | 3.5441 | 5.99 | 5.99 | 5.99 | 5.99
2021-02-14 06:00 | 1.3432 | 1.6345 | 1.5993 | 1.7202 | 1.6295 | 1.7504 | 0.76019 | 1.3036 | 1.6086 | 1.6086 | 1.8119 | 1.8119 | 2019-04-13 18:00 | 1.9357 | 3.3217 | 5.6143 | 5.6143 | 5.6143 | 5.6143
2021-02-14 07:00 | 1.3375 | 1.6276 | 1.5925 | 1.7128 | 1.6226 | 1.7429 | 0.93167 | 1.5977 | 1.9714 | 1.9714 | 2.2206 | 2.2206 | 2019-04-13 19:00 | 1.7986 | 3.0863 | 5.2164 | 5.2164 | 5.2164 | 5.2164
2021-02-14 08:00 | 1.4089 | 1.7145 | 1.6775 | 1.8043 | 1.7092 | 1.836 | 1.1342 | 1.945 | 2.4 | 2.4 | 2.7034 | 2.7034 | 2019-04-13 20:00 | 1.6538 | 2.8379 | 4.7965 | 4.7965 | 4.7965 | 4.7965
2021-02-14 09:00 | 1.4718 | 1.791 | 1.7524 | 1.8849 | 1.7855 | 1.918 | 1.3032 | 2.2348 | 2.7576 | 2.7576 | 3.1061 | 3.1061 | 2019-04-13 21:00 | 1.6766 | 2.8771 | 4.8628 | 4.8628 | 4.8628 | 4.8628
2021-02-14 10:00 | 1.4947 | 1.8189 | 1.7796 | 1.9141 | 1.8133 | 1.9478 | 1.4261 | 2.4455 | 3.0176 | 3.0176 | 3.399 | 3.399 | 2019-04-13 22:00 | 1.5852 | 2.7202 | 4.5975 | 4.5975 | 4.5975 | 4.5975
2021-02-14 11:00 | 1.5833 | 1.9267 | 1.8851 | 2.0276 | 1.9207 | 2.0632 | 1.4947 | 2.5631 | 3.1627 | 3.1627 | 3.5625 | 3.5625 | 2019-04-13 23:00 | 1.5013 | 2.5763 | 4.3544 | 4.3544 | 4.3544 | 4.3544
2021-02-14 12:00 | 1.3175 | 1.6032 | 1.5687 | 1.6872 | 1.5983 | 1.7169 | 1.5118 | 2.5925 | 3.199 | 3.199 | 3.6034 | 3.6034 | 2019-04-14 | 1.4861 | 2.5501 | 4.3102 | 4.3102 | 4.3102 | 4.3102
2021-02-14 13:00 | 1.2975 | 1.5789 | 1.5448 | 1.6616 | 1.574 | 1.6908 | 1.5318 | 2.6268 | 3.2414 | 3.2414 | 3.651 | 3.651 | 2019-04-14 01:00 | 1.4556 | 2.4978 | 4.2218 | 4.2218 | 4.2218 | 4.2218
2021-02-14 14:00 | 1.3289 | 1.6171 | 1.5823 | 1.7019 | 1.6122 | 1.7318 | 1.5004 | 2.5729 | 3.1748 | 3.1748 | 3.5761 | 3.5761 | 2019-04-14 02:00 | 1.4023 | 2.4063 | 4.067 | 4.067 | 4.067 | 4.067
2021-02-14 15:00 | 1.3461 | 1.638 | 1.6027 | 1.7238 | 1.633 | 1.7541 | 1.4547 | 2.4945 | 3.0781 | 3.0781 | 3.4671 | 3.4671 | 2019-04-14 03:00 | 1.4251 | 2.4455 | 4.1333 | 4.1333 | 4.1333 | 4.1333
2021-02-14 16:00 | 1.4432 | 1.7563 | 1.7184 | 1.8483 | 1.7508 | 1.8807 | 1.5175 | 2.6023 | 3.2111 | 3.2111 | 3.617 | 3.617 | 2019-04-14 04:00 | 1.4556 | 2.4978 | 4.2218 | 4.2218 | 4.2218 | 4.2218
2021-02-14 17:00 | 1.6376 | 1.9927 | 1.9498 | 2.0971 | 1.9866 | 2.134 | 1.6118 | 2.7641 | 3.4107 | 3.4107 | 3.8418 | 3.8418 | 2019-04-14 05:00 | 1.509 | 2.5894 | 4.3765 | 4.3765 | 4.3765 | 4.3765
2021-02-14 18:00 | 1.7919 | 2.1805 | 2.1335 | 2.2948 | 2.1738 | 2.3351 | 1.629 | 2.7935 | 3.447 | 3.447 | 3.8826 | 3.8826 | 2019-04-14 06:00 | 1.608 | 2.7594 | 4.6638 | 4.6638 | 4.6638 | 4.6638
2021-02-14 19:00 | 1.7776 | 2.1632 | 2.1165 | 2.2765 | 2.1565 | 2.3165 | 1.6318 | 2.7984 | 3.453 | 3.453 | 3.8894 | 3.8894 | 2019-04-14 07:00 | 1.6842 | 2.8902 | 4.8849 | 4.8849 | 4.8849 | 4.8849
2021-02-14 20:00 | 1.789 | 2.1771 | 2.1301 | 2.2911 | 2.1704 | 2.3314 | 1.5718 | 2.6954 | 3.326 | 3.326 | 3.7464 | 3.7464 | 2019-04-14 08:00 | 1.8976 | 3.2563 | 5.5038 | 5.5038 | 5.5038 | 5.5038
2021-02-14 21:00 | 1.7236 | 2.0974 | 2.0522 | 2.2073 | 2.091 | 2.2461 | 1.5375 | 2.6366 | 3.2534 | 3.2534 | 3.6647 | 3.6647 | 2019-04-14 09:00 | 1.951 | 3.3479 | 5.6585 | 5.6585 | 5.6585 | 5.6585
2021-02-14 22:00 | 1.6061 | 1.9545 | 1.9123 | 2.0569 | 1.9485 | 2.093 | 1.3375 | 2.2936 | 2.8301 | 2.8301 | 3.1878 | 3.1878 | 2019-04-14 10:00 | 2.1186 | 3.6356 | 6.1448 | 6.1448 | 6.1448 | 6.1448
2021-02-14 23:00 | 1.4501 | 1.7647 | 1.7266 | 1.8571 | 1.7592 | 1.8897 | 1.1037 | 1.8927 | 2.3354 | 2.3354 | 2.6306 | 2.6306 | 2019-04-14 11:00 | 2.111 | 3.6225 | 6.1227 | 6.1227 | 6.1227 | 6.1227
2021-02-15 | 1.4006 | 1.7044 | 1.6677 | 1.7937 | 1.6992 | 1.8252 | 0.92309 | 1.583 | 1.9533 | 1.9533 | 2.2002 | 2.2002 | 2019-04-14 12:00 | 2.1339 | 3.6618 | 6.189 | 6.189 | 6.189 | 6.189
2021-02-15 01:00 | 1.2403 | 1.5093 | 1.4768 | 1.5884 | 1.5047 | 1.6163 | 0.86594 | 1.4849 | 1.8323 | 1.8323 | 2.0639 | 2.0639 | 2019-04-14 13:00 | 2.1644 | 3.7141 | 6.2774 | 6.2774 | 6.2774 | 6.2774
2021-02-15 02:00 | 1.2918 | 1.5719 | 1.538 | 1.6543 | 1.5671 | 1.6834 | 0.73198 | 1.2552 | 1.5489 | 1.5489 | 1.7447 | 1.7447 | 2019-04-14 14:00 | 2.2025 | 3.7795 | 6.3879 | 6.3879 | 6.3879 | 6.3879
2021-02-15 03:00 | 1.1946 | 1.4537 | 1.4223 | 1.5298 | 1.4492 | 1.5567 | 0.75162 | 1.2889 | 1.5904 | 1.5904 | 1.7915 | 1.7915 | 2019-04-14 15:00 | 2.172 | 3.7271 | 6.2995 | 6.2995 | 6.2995 | 6.2995
2021-02-15 04:00 | 1.2117 | 1.4746 | 1.4428 | 1.5518 | 1.47 | 1.5791 | 0.70948 | 1.2166 | 1.5013 | 1.5013 | 1.691 | 1.691 | 2019-04-14 16:00 | 2.1567 | 3.701 | 6.2553 | 6.2553 | 6.2553 | 6.2553
2021-02-15 05:00 | 1.3226 | 1.6094 | 1.5747 | 1.6937 | 1.6045 | 1.7235 | 0.82307 | 1.4114 | 1.7416 | 1.7416 | 1.9617 | 1.9617 | 2019-04-14 17:00 | 2.0653 | 3.5441 | 5.99 | 5.99 | 5.99 | 5.99
2021-02-15 06:00 | 1.7376 | 2.1145 | 2.0689 | 2.2252 | 2.108 | 2.2643 | 1.0374 | 1.779 | 2.1952 | 2.1952 | 2.4726 | 2.4726 | 2019-04-14 18:00 | 1.9357 | 3.3217 | 5.6143 | 5.6143 | 5.6143 | 5.6143
2021-02-15 07:00 | 1.8748 | 2.2814 | 2.2322 | 2.4009 | 2.2744 | 2.4431 | 1.2317 | 2.1122 | 2.6064 | 2.6064 | 2.9358 | 2.9358 | 2019-04-14 19:00 | 1.8519 | 3.1779 | 5.3711 | 5.3711 | 5.3711 | 5.3711
2021-02-15 08:00 | 1.9634 | 2.3892 | 2.3377 | 2.5144 | 2.3818 | 2.5585 | 1.3032 | 2.2348 | 2.7576 | 2.7576 | 3.1061 | 3.1061 | 2019-04-14 20:00 | 1.7528 | 3.0079 | 5.0838 | 5.0838 | 5.0838 | 5.0838
2021-02-15 09:00 | 1.9148 | 2.3301 | 2.2798 | 2.4522 | 2.3229 | 2.4952 | 1.3118 | 2.2495 | 2.7757 | 2.7757 | 3.1265 | 3.1265 | 2019-04-14 21:00 | 1.6919 | 2.9032 | 4.907 | 4.907 | 4.907 | 4.907
2021-02-15 10:00 | 1.9405 | 2.3614 | 2.3104 | 2.4851 | 2.3541 | 2.5288 | 1.2946 | 2.2201 | 2.7394 | 2.7394 | 3.0857 | 3.0857 | 2019-04-14 22:00 | 1.5775 | 2.7071 | 4.5754 | 4.5754 | 4.5754 | 4.5754
2021-02-15 11:00 | 1.9605 | 2.3857 | 2.3343 | 2.5107 | 2.3784 | 2.5548 | 1.2832 | 2.2005 | 2.7152 | 2.7152 | 3.0584 | 3.0584 | 2019-04-14 23:00 | 1.4785 | 2.5371 | 4.2881 | 4.2881 | 4.2881 | 4.2881
2021-02-15 12:00 | 1.9907 | 2.4225 | 2.3702 | 2.5494 | 2.415 | 2.5942 | 1.2946 | 2.2201 | 2.7394 | 2.7394 | 3.0857 | 3.0857 | 2019-04-15 | 1.4632 | 2.5109 | 4.2439 | 4.2439 | 4.2439 | 4.2439
2021-02-15 13:00 | 2.0262 | 2.4657 | 2.4125 | 2.5949 | 2.4581 | 2.6405 | 1.3461 | 2.3083 | 2.8483 | 2.8483 | 3.2083 | 3.2083 | 2019-04-15 01:00 | 1.5013 | 2.5763 | 4.3544 | 4.3544 | 4.3544 | 4.3544
2021-02-15 14:00 | 2.0634 | 2.5109 | 2.4568 | 2.6425 | 2.5032 | 2.6889 | 1.3118 | 2.2495 | 2.7757 | 2.7757 | 3.1265 | 3.1265 | 2019-04-15 02:00 | 1.4023 | 2.4063 | 4.067 | 4.067 | 4.067 | 4.067
2021-02-15 15:00 | 2.0234 | 2.4622 | 2.4091 | 2.5912 | 2.4547 | 2.6368 | 1.3261 | 2.274 | 2.8059 | 2.8059 | 3.1606 | 3.1606 | 2019-04-15 03:00 | 1.4709 | 2.524 | 4.266 | 4.266 | 4.266 | 4.266
2021-02-15 16:00 | 2.0434 | 2.4866 | 2.4329 | 2.6169 | 2.4789 | 2.6628 | 1.3661 | 2.3426 | 2.8906 | 2.8906 | 3.256 | 3.256 | 2019-04-15 04:00 | 1.4937 | 2.5632 | 4.3323 | 4.3323 | 4.3323 | 4.3323
2021-02-15 17:00 | 2.0634 | 2.5109 | 2.4568 | 2.6425 | 2.5032 | 2.6889 | 1.4947 | 2.5631 | 3.1627 | 3.1627 | 3.5625 | 3.5625 | 2019-04-15 05:00 | 1.5699 | 2.694 | 4.5533 | 4.5533 | 4.5533 | 4.5533
2021-02-15 18:00 | 2.2949 | 2.7926 | 2.7324 | 2.9389 | 2.784 | 2.9906 | 1.5232 | 2.6121 | 3.2232 | 3.2232 | 3.6306 | 3.6306 | 2019-04-15 06:00 | 1.6766 | 2.8771 | 4.8628 | 4.8628 | 4.8628 | 4.8628
2021-02-15 19:00 | 2.112 | 2.5701 | 2.5147 | 2.7047 | 2.5622 | 2.7523 | 1.5861 | 2.7199 | 3.3563 | 3.3563 | 3.7805 | 3.7805 | 2019-04-15 07:00 | 1.7681 | 3.034 | 5.128 | 5.128 | 5.128 | 5.128
2021-02-15 20:00 | 2.0977 | 2.5527 | 2.4976 | 2.6864 | 2.5448 | 2.7336 | 1.5032 | 2.5778 | 3.1809 | 3.1809 | 3.5829 | 3.5829 | 2019-04-15 08:00 | 1.9281 | 3.3087 | 5.5922 | 5.5922 | 5.5922 | 5.5922
2021-02-15 21:00 | 1.8946 | 2.3055 | 2.2558 | 2.4263 | 2.2984 | 2.469 | 1.4118 | 2.421 | 2.9874 | 2.9874 | 3.3649 | 3.3649 | 2019-04-15 09:00 | 2.0043 | 3.4394 | 5.8132 | 5.8132 | 5.8132 | 5.8132
2021-02-15 22:00 | 1.7276 | 2.1023 | 2.0569 | 2.2124 | 2.0958 | 2.2513 | 1.3146 | 2.2544 | 2.7818 | 2.7818 | 3.1333 | 3.1333 | 2019-04-15 10:00 | 2.0653 | 3.5441 | 5.99 | 5.99 | 5.99 | 5.99
2021-02-15 23:00 | 1.5032 | 1.8293 | 1.7898 | 1.9251 | 1.8237 | 1.9589 | 1.0917 | 1.8721 | 2.3101 | 2.3101 | 2.602 | 2.602 | 2019-04-15 11:00 | 2.1567 | 3.701 | 6.2553 | 6.2553 | 6.2553 | 6.2553
2021-02-16 | 1.3876 | 1.6885 | 1.6521 | 1.777 | 1.6833 | 1.8082 | 0.90309 | 1.5487 | 1.9109 | 1.9109 | 2.1525 | 2.1525 | 2019-04-15 12:00 | 2.1567 | 3.701 | 6.2553 | 6.2553 | 6.2553 | 6.2553
2021-02-16 01:00 | 1.2576 | 1.5303 | 1.4973 | 1.6105 | 1.5256 | 1.6388 | 0.78306 | 1.3428 | 1.657 | 1.657 | 1.8664 | 1.8664 | 2019-04-15 13:00 | 2.1186 | 3.6356 | 6.1448 | 6.1448 | 6.1448 | 6.1448
2021-02-16 02:00 | 1.2203 | 1.485 | 1.453 | 1.5628 | 1.4804 | 1.5902 | 0.74305 | 1.2742 | 1.5723 | 1.5723 | 1.771 | 1.771 | 2019-04-15 14:00 | 2.1339 | 3.6618 | 6.189 | 6.189 | 6.189 | 6.189
2021-02-16 03:00 | 1.2175 | 1.4815 | 1.4496 | 1.5591 | 1.477 | 1.5865 | 0.68307 | 1.1714 | 1.4454 | 1.4454 | 1.6281 | 1.6281 | 2019-04-15 15:00 | 2.0805 | 3.5702 | 6.0343 | 6.0343 | 6.0343 | 6.0343
2021-02-16 04:00 | 1.2118 | 1.4746 | 1.4428 | 1.5519 | 1.4701 | 1.5791 | 0.70304 | 1.2056 | 1.4876 | 1.4876 | 1.6757 | 1.6757 | 2019-04-15 16:00 | 2.1034 | 3.6094 | 6.1006 | 6.1006 | 6.1006 | 6.1006
2021-02-16 05:00 | 1.404 | 1.7085 | 1.6717 | 1.798 | 1.7033 | 1.8296 | 0.76019 | 1.3036 | 1.6086 | 1.6086 | 1.8119 | 1.8119 | 2019-04-15 17:00 | 1.9738 | 3.3871 | 5.7248 | 5.7248 | 5.7248 | 5.7248
2021-02-16 06:00 | 1.6919 | 2.0588 | 2.0144 | 2.1667 | 2.0525 | 2.2047 | 0.9631 | 1.6516 | 2.0379 | 2.0379 | 2.2955 | 2.2955 | 2019-04-15 18:00 | 1.9434 | 3.3348 | 5.6364 | 5.6364 | 5.6364 | 5.6364
2021-02-16 07:00 | 1.9777 | 2.4066 | 2.3547 | 2.5327 | 2.3992 | 2.5772 | 1.1889 | 2.0387 | 2.5157 | 2.5157 | 2.8336 | 2.8336 | 2019-04-15 19:00 | 1.8595 | 3.191 | 5.3932 | 5.3932 | 5.3932 | 5.3932
2021-02-16 08:00 | 1.9948 | 2.4275 | 2.3751 | 2.5546 | 2.42 | 2.5995 | 1.3003 | 2.2299 | 2.7515 | 2.7515 | 3.0993 | 3.0993 | 2019-04-15 20:00 | 1.7376 | 2.9817 | 5.0396 | 5.0396 | 5.0396 | 5.0396
2021-02-16 09:00 | 2.1234 | 2.584 | 2.5282 | 2.7193 | 2.576 | 2.7671 | 1.2746 | 2.1858 | 2.6971 | 2.6971 | 3.038 | 3.038 | 2019-04-15 21:00 | 1.6538 | 2.8379 | 4.7965 | 4.7965 | 4.7965 | 4.7965
2021-02-16 10:00 | 2.272 | 2.7648 | 2.7052 | 2.9096 | 2.7563 | 2.9608 | 1.4061 | 2.4112 | 2.9753 | 2.9753 | 3.3513 | 3.3513 | 2019-04-15 22:00 | 1.6461 | 2.8248 | 4.7743 | 4.7743 | 4.7743 | 4.7743
2021-02-16 11:00 | 2.3149 | 2.817 | 2.7562 | 2.9645 | 2.8083 | 3.0166 | 1.4261 | 2.4455 | 3.0176 | 3.0176 | 3.399 | 3.399 | 2019-04-15 23:00 | 1.509 | 2.5894 | 4.3765 | 4.3765 | 4.3765 | 4.3765
2021-02-16 12:00 | 2.4263 | 2.9526 | 2.8889 | 3.1073 | 2.9435 | 3.1619 | 1.4432 | 2.4749 | 3.0539 | 3.0539 | 3.4399 | 3.4399 | 2019-04-16 | 1.4251 | 2.4455 | 4.1333 | 4.1333 | 4.1333 | 4.1333
2021-02-16 13:00 | 2.392 | 2.9109 | 2.8481 | 3.0634 | 2.9019 | 3.1172 | 1.4804 | 2.5386 | 3.1325 | 3.1325 | 3.5284 | 3.5284 | 2019-04-16 01:00 | 1.3565 | 2.3278 | 3.9344 | 3.9344 | 3.9344 | 3.9344
2021-02-16 14:00 | 2.5321 | 3.0813 | 3.0148 | 3.2427 | 3.0718 | 3.2997 | 1.4261 | 2.4455 | 3.0176 | 3.0176 | 3.399 | 3.399 | 2019-04-16 02:00 | 1.3718 | 2.354 | 3.9786 | 3.9786 | 3.9786 | 3.9786
2021-02-16 15:00 | 2.2463 | 2.7335 | 2.6745 | 2.8767 | 2.7251 | 2.9272 | 1.3318 | 2.2838 | 2.818 | 2.818 | 3.1742 | 3.1742 | 2019-04-16 03:00 | 1.3794 | 2.3671 | 4.0007 | 4.0007 | 4.0007 | 4.0007
2021-02-16 16:00 | 2.4349 | 2.963 | 2.8991 | 3.1183 | 2.9539 | 3.173 | 1.4647 | 2.5117 | 3.0992 | 3.0992 | 3.491 | 3.491 | 2019-04-16 04:00 | 1.4404 | 2.4717 | 4.1776 | 4.1776 | 4.1776 | 4.1776
2021-02-16 17:00 | 2.3606 | 2.8726 | 2.8107 | 3.0231 | 2.8638 | 3.0762 | 1.589 | 2.7248 | 3.3623 | 3.3623 | 3.7873 | 3.7873 | 2019-04-16 05:00 | 1.5394 | 2.6417 | 4.4649 | 4.4649 | 4.4649 | 4.4649
2021-02-16 18:00 | 2.4646 | 2.9991 | 2.9344 | 3.1562 | 2.9899 | 3.2117 | 1.5861 | 2.7199 | 3.3563 | 3.3563 | 3.7805 | 3.7805 | 2019-04-16 06:00 | 1.6995 | 2.9163 | 4.9291 | 4.9291 | 4.9291 | 4.9291
2021-02-16 19:00 | 2.4692 | 3.0048 | 2.94 | 3.1622 | 2.9955 | 3.2177 | 1.6061 | 2.7543 | 3.3986 | 3.3986 | 3.8281 | 3.8281 | 2019-04-16 07:00 | 1.7833 | 3.0602 | 5.1722 | 5.1722 | 5.1722 | 5.1722
2021-02-16 20:00 | 2.1091 | 2.5666 | 2.5112 | 2.701 | 2.5587 | 2.7485 | 1.5604 | 2.6758 | 3.3018 | 3.3018 | 3.7192 | 3.7192 | 2019-04-16 08:00 | 1.9662 | 3.374 | 5.7027 | 5.7027 | 5.7027 | 5.7027
2021-02-16 21:00 | 2.0805 | 2.5318 | 2.4772 | 2.6644 | 2.524 | 2.7112 | 1.4689 | 2.519 | 3.1083 | 3.1083 | 3.5012 | 3.5012 | 2019-04-16 09:00 | 1.9662 | 3.374 | 5.7027 | 5.7027 | 5.7027 | 5.7027
2021-02-16 22:00 | 1.829 | 2.2258 | 2.1777 | 2.3424 | 2.2189 | 2.3835 | 1.2775 | 2.1907 | 2.7031 | 2.7031 | 3.0448 | 3.0448 | 2019-04-16 10:00 | 2.1339 | 3.6618 | 6.189 | 6.189 | 6.189 | 6.189
2021-02-16 23:00 | 1.4832 | 1.8049 | 1.766 | 1.8995 | 1.7994 | 1.9329 | 1.0946 | 1.877 | 2.3161 | 2.3161 | 2.6089 | 2.6089 | 2019-04-16 11:00 | 2.1949 | 3.7664 | 6.3658 | 6.3658 | 6.3658 | 6.3658
2021-02-17 | 1.4061 | 1.711 | 1.6741 | 1.8007 | 1.7058 | 1.8323 | 0.94407 | 1.6189 | 1.9977 | 1.9977 | 2.2501 | 2.2501 | 2019-04-16 12:00 | 2.1644 | 3.7141 | 6.2774 | 6.2774 | 6.2774 | 6.2774
2021-02-17 01:00 | 1.3032 | 1.5858 | 1.5516 | 1.6689 | 1.581 | 1.6982 | 0.83164 | 1.4261 | 1.7598 | 1.7598 | 1.9822 | 1.9822 | 2019-04-16 13:00 | 2.1872 | 3.7533 | 6.3437 | 6.3437 | 6.3437 | 6.3437
2021-02-17 02:00 | 1.226 | 1.492 | 1.4598 | 1.5701 | 1.4874 | 1.5977 | 0.76877 | 1.3183 | 1.6267 | 1.6267 | 1.8323 | 1.8323 | 2019-04-16 14:00 | 2.1339 | 3.6618 | 6.189 | 6.189 | 6.189 | 6.189
2021-02-17 03:00 | 1.2346 | 1.5024 | 1.47 | 1.5811 | 1.4978 | 1.6089 | 0.76591 | 1.3134 | 1.6207 | 1.6207 | 1.8255 | 1.8255 | 2019-04-16 15:00 | 2.2406 | 3.8448 | 6.4984 | 6.4984 | 6.4984 | 6.4984
2021-02-17 04:00 | 1.2232 | 1.4885 | 1.4564 | 1.5664 | 1.4839 | 1.594 | 0.74838 | 1.2834 | 1.5836 | 1.5836 | 1.7837 | 1.7837 | 2019-04-16 16:00 | 2.1644 | 3.7141 | 6.2774 | 6.2774 | 6.2774 | 6.2774
2021-02-17 05:00 | 1.4189 | 1.7267 | 1.6894 | 1.8171 | 1.7214 | 1.8491 | 0.82021 | 1.4065 | 1.7356 | 1.7356 | 1.9549 | 1.9549 | 2019-04-16 17:00 | 1.9967 | 3.4264 | 5.7911 | 5.7911 | 5.7911 | 5.7911
2021-02-17 06:00 | 1.6233 | 1.9754 | 1.9327 | 2.0788 | 1.9693 | 2.1154 | 1.0517 | 1.8035 | 2.2254 | 2.2254 | 2.5067 | 2.5067 | 2019-04-16 18:00 | 1.8443 | 3.1648 | 5.349 | 5.349 | 5.349 | 5.349
2021-02-17 07:00 | 1.829 | 2.2258 | 2.1777 | 2.3424 | 2.2189 | 2.3835 | 1.2632 | 2.1662 | 2.6729 | 2.6729 | 3.0107 | 3.0107 | 2019-04-16 19:00 | 1.7757 | 3.0471 | 5.1501 | 5.1501 | 5.1501 | 5.1501
2021-02-17 08:00 | 2.0805 | 2.5318 | 2.4772 | 2.6644 | 2.524 | 2.7112 | 1.3432 | 2.3034 | 2.8422 | 2.8422 | 3.2015 | 3.2015 | 2019-04-16 20:00 | 1.6461 | 2.8248 | 4.7743 | 4.7743 | 4.7743 | 4.7743
2021-02-17 09:00 | 2.0891 | 2.5422 | 2.4874 | 2.6754 | 2.5344 | 2.7224 | 1.3261 | 2.274 | 2.8059 | 2.8059 | 3.1606 | 3.1606 | 2019-04-16 21:00 | 1.5547 | 2.6678 | 4.5091 | 4.5091 | 4.5091 | 4.5091
2021-02-17 10:00 | 2.1977 | 2.6744 | 2.6167 | 2.8145 | 2.6661 | 2.8639 | 1.3718 | 2.3524 | 2.9027 | 2.9027 | 3.2696 | 3.2696 | 2019-04-16 22:00 | 1.5623 | 2.6809 | 4.5312 | 4.5312 | 4.5312 | 4.5312
2021-02-17 11:00 | 2.2577 | 2.7474 | 2.6882 | 2.8913 | 2.739 | 2.9421 | 1.4204 | 2.4357 | 3.0055 | 3.0055 | 3.3854 | 3.3854 | 2019-04-16 23:00 | 1.4785 | 2.5371 | 4.2881 | 4.2881 | 4.2881 | 4.2881
2021-02-17 12:00 | 2.1691 | 2.6396 | 2.5827 | 2.7779 | 2.6315 | 2.8267 | 1.4032 | 2.4063 | 2.9692 | 2.9692 | 3.3445 | 3.3445 | 2019-04-17 | 1.3565 | 2.3278 | 3.9344 | 3.9344 | 3.9344 | 3.9344
2021-02-17 13:00 | 2.3949 | 2.9143 | 2.8515 | 3.067 | 2.9054 | 3.1209 | 1.4347 | 2.4602 | 3.0357 | 3.0357 | 3.4194 | 3.4194 | 2019-04-17 01:00 | 1.3718 | 2.354 | 3.9786 | 3.9786 | 3.9786 | 3.9786
2021-02-17 14:00 | 2.392 | 2.9109 | 2.8481 | 3.0634 | 2.9019 | 3.1172 | 1.3718 | 2.3524 | 2.9027 | 2.9027 | 3.2696 | 3.2696 | 2019-04-17 02:00 | 1.3642 | 2.3409 | 3.9565 | 3.9565 | 3.9565 | 3.9565
2021-02-17 15:00 | 2.3578 | 2.8691 | 2.8072 | 3.0194 | 2.8603 | 3.0725 | 1.3146 | 2.2544 | 2.7818 | 2.7818 | 3.1333 | 3.1333 | 2019-04-17 03:00 | 1.3489 | 2.3148 | 3.9123 | 3.9123 | 3.9123 | 3.9123
2021-02-17 16:00 | 2.2777 | 2.7718 | 2.712 | 2.917 | 2.7632 | 2.9682 | 1.3832 | 2.372 | 2.9269 | 2.9269 | 3.2968 | 3.2968 | 2019-04-17 04:00 | 1.4251 | 2.4455 | 4.1333 | 4.1333 | 4.1333 | 4.1333
2021-02-17 17:00 | 2.292 | 2.7892 | 2.729 | 2.9353 | 2.7806 | 2.9868 | 1.4918 | 2.5582 | 3.1567 | 3.1567 | 3.5557 | 3.5557 | 2019-04-17 05:00 | 1.5318 | 2.6286 | 4.4428 | 4.4428 | 4.4428 | 4.4428
2021-02-17 18:00 | 2.3235 | 2.8274 | 2.7664 | 2.9755 | 2.8187 | 3.0278 | 1.5061 | 2.5827 | 3.1869 | 3.1869 | 3.5897 | 3.5897 | 2019-04-17 06:00 | 1.7071 | 2.9294 | 4.9512 | 4.9512 | 4.9512 | 4.9512
2021-02-17 19:00 | 2.1777 | 2.65 | 2.5929 | 2.7889 | 2.6419 | 2.8379 | 1.5175 | 2.6023 | 3.2111 | 3.2111 | 3.617 | 3.617 | 2019-04-17 07:00 | 1.7223 | 2.9556 | 4.9954 | 4.9954 | 4.9954 | 4.9954
2021-02-17 20:00 | 2.0462 | 2.4901 | 2.4364 | 2.6205 | 2.4824 | 2.6666 | 1.5232 | 2.6121 | 3.2232 | 3.2232 | 3.6306 | 3.6306 | 2019-04-17 08:00 | 1.9967 | 3.4264 | 5.7911 | 5.7911 | 5.7911 | 5.7911
2021-02-17 21:00 | 2.0091 | 2.4449 | 2.3921 | 2.5729 | 2.4373 | 2.6181 | 1.4947 | 2.5631 | 3.1627 | 3.1627 | 3.5625 | 3.5625 | 2019-04-17 09:00 | 2.0119 | 3.4525 | 5.8353 | 5.8353 | 5.8353 | 5.8353
2021-02-17 22:00 | 1.6901 | 2.0567 | 2.0123 | 2.1644 | 2.0504 | 2.2025 | 1.3032 | 2.2348 | 2.7576 | 2.7576 | 3.1061 | 3.1061 | 2019-04-17 10:00 | 2.0805 | 3.5702 | 6.0343 | 6.0343 | 6.0343 | 6.0343
2021-02-17 23:00 | 1.4648 | 1.7825 | 1.7441 | 1.8759 | 1.777 | 1.9089 | 1.1214 | 1.923 | 2.3729 | 2.3729 | 2.6728 | 2.6728 | 2019-04-17 11:00 | 2.1644 | 3.7141 | 6.2774 | 6.2774 | 6.2774 | 6.2774
2021-02-18 | 1.4004 | 1.7041 | 1.6673 | 1.7934 | 1.6988 | 1.8249 | 0.9431 | 1.6173 | 1.9956 | 1.9956 | 2.2478 | 2.2478 | 2019-04-17 12:00 | 2.2634 | 3.8841 | 6.5647 | 6.5647 | 6.5647 | 6.5647
2021-02-18 01:00 | 1.2517 | 1.5232 | 1.4904 | 1.603 | 1.5186 | 1.6312 | 0.79342 | 1.3606 | 1.6789 | 1.6789 | 1.8911 | 1.8911 | 2019-04-17 13:00 | 2.3015 | 3.9495 | 6.6753 | 6.6753 | 6.6753 | 6.6753
2021-02-18 02:00 | 1.246 | 1.5163 | 1.4836 | 1.5957 | 1.5116 | 1.6238 | 0.76305 | 1.3085 | 1.6146 | 1.6146 | 1.8187 | 1.8187 | 2019-04-17 14:00 | 2.1872 | 3.7533 | 6.3437 | 6.3437 | 6.3437 | 6.3437
2021-02-18 03:00 | 1.2289 | 1.4954 | 1.4632 | 1.5738 | 1.4908 | 1.6014 | 0.71161 | 1.2203 | 1.5058 | 1.5058 | 1.6961 | 1.6961 | 2019-04-17 15:00 | 2.233 | 3.8318 | 6.4763 | 6.4763 | 6.4763 | 6.4763
2021-02-18 04:00 | 1.2074 | 1.4693 | 1.4376 | 1.5463 | 1.4648 | 1.5735 | 0.73161 | 1.2546 | 1.5481 | 1.5481 | 1.7438 | 1.7438 | 2019-04-17 16:00 | 2.0882 | 3.5833 | 6.0564 | 6.0564 | 6.0564 | 6.0564
2021-02-18 05:00 | 1.4374 | 1.7491 | 1.7114 | 1.8407 | 1.7437 | 1.8731 | 0.80013 | 1.3721 | 1.6931 | 1.6931 | 1.9071 | 1.9071 | 2019-04-17 17:00 | 2.0043 | 3.4394 | 5.8132 | 5.8132 | 5.8132 | 5.8132
2021-02-18 06:00 | 1.7147 | 2.0866 | 2.0416 | 2.196 | 2.0802 | 2.2345 | 1.0491 | 1.7991 | 2.22 | 2.22 | 2.5005 | 2.5005 | 2019-04-17 18:00 | 2.172 | 3.7271 | 6.2995 | 6.2995 | 6.2995 | 6.2995
2021-02-18 07:00 | 1.8862 | 2.2953 | 2.2458 | 2.4156 | 2.2882 | 2.458 | 1.286 | 2.2054 | 2.7213 | 2.7213 | 3.0652 | 3.0652 | 2019-04-17 19:00 | 1.8214 | 3.1256 | 5.2827 | 5.2827 | 5.2827 | 5.2827
2021-02-18 08:00 | 2.0634 | 2.5109 | 2.4568 | 2.6425 | 2.5032 | 2.6889 | 1.3746 | 2.3573 | 2.9088 | 2.9088 | 3.2764 | 3.2764 | 2019-04-17 20:00 | 1.6538 | 2.8379 | 4.7965 | 4.7965 | 4.7965 | 4.7965
2021-02-18 09:00 | 2.1691 | 2.6396 | 2.5827 | 2.7779 | 2.6315 | 2.8267 | 1.3546 | 2.323 | 2.8664 | 2.8664 | 3.2287 | 3.2287 | 2019-04-17 21:00 | 1.6004 | 2.7463 | 4.6417 | 4.6417 | 4.6417 | 4.6417
2021-02-18 10:00 | 2.0558 | 2.5017 | 2.4478 | 2.6328 | 2.494 | 2.6791 | 1.4518 | 2.4896 | 3.072 | 3.072 | 3.4603 | 3.4603 | 2019-04-17 22:00 | 1.5394 | 2.6417 | 4.4649 | 4.4649 | 4.4649 | 4.4649
2021-02-18 11:00 | 2.2549 | 2.7439 | 2.6848 | 2.8877 | 2.7355 | 2.9384 | 1.4004 | 2.4014 | 2.9632 | 2.9632 | 3.3377 | 3.3377 | 2019-04-17 23:00 | 1.4404 | 2.4717 | 4.1776 | 4.1776 | 4.1776 | 4.1776
2021-02-18 12:00 | 2.1863 | 2.6605 | 2.6031 | 2.7998 | 2.6523 | 2.849 | 1.4461 | 2.4798 | 3.0599 | 3.0599 | 3.4467 | 3.4467 | 2019-04-18 | 1.5013 | 2.5763 | 4.3544 | 4.3544 | 4.3544 | 4.3544
2021-02-18 13:00 | 2.1891 | 2.664 | 2.6065 | 2.8035 | 2.6557 | 2.8528 | 1.4175 | 2.4308 | 2.9995 | 2.9995 | 3.3786 | 3.3786 | 2019-04-18 01:00 | 1.4023 | 2.4063 | 4.067 | 4.067 | 4.067 | 4.067
2021-02-18 14:00 | 2.2034 | 2.6813 | 2.6235 | 2.8218 | 2.6731 | 2.8714 | 1.4775 | 2.5337 | 3.1265 | 3.1265 | 3.5216 | 3.5216 | 2019-04-18 02:00 | 1.4023 | 2.4063 | 4.067 | 4.067 | 4.067 | 4.067
2021-02-18 15:00 | 2.2263 | 2.7092 | 2.6507 | 2.8511 | 2.7008 | 2.9012 | 1.3661 | 2.3426 | 2.8906 | 2.8906 | 3.256 | 3.256 | 2019-04-18 03:00 | 1.3794 | 2.3671 | 4.0007 | 4.0007 | 4.0007 | 4.0007
2021-02-18 16:00 | 2.2006 | 2.6779 | 2.6201 | 2.8181 | 2.6696 | 2.8677 | 1.2975 | 2.225 | 2.7455 | 2.7455 | 3.0925 | 3.0925 | 2019-04-18 04:00 | 1.4251 | 2.4455 | 4.1333 | 4.1333 | 4.1333 | 4.1333
2021-02-18 17:00 | 2.2749 | 2.7683 | 2.7086 | 2.9133 | 2.7598 | 2.9645 | 1.4118 | 2.421 | 2.9874 | 2.9874 | 3.3649 | 3.3649 | 2019-04-18 05:00 | 1.5394 | 2.6417 | 4.4649 | 4.4649 | 4.4649 | 4.4649
2021-02-18 18:00 | 2.2949 | 2.7926 | 2.7324 | 2.9389 | 2.784 | 2.9906 | 1.5061 | 2.5827 | 3.1869 | 3.1869 | 3.5897 | 3.5897 | 2019-04-18 06:00 | 1.6461 | 2.8248 | 4.7743 | 4.7743 | 4.7743 | 4.7743
2021-02-18 19:00 | 2.2577 | 2.7474 | 2.6882 | 2.8913 | 2.739 | 2.9421 | 1.5375 | 2.6366 | 3.2534 | 3.2534 | 3.6647 | 3.6647 | 2019-04-18 07:00 | 1.8519 | 3.1779 | 5.3711 | 5.3711 | 5.3711 | 5.3711
2021-02-18 20:00 | 2.1291 | 2.5909 | 2.535 | 2.7266 | 2.5829 | 2.7746 | 1.5461 | 2.6513 | 3.2716 | 3.2716 | 3.6851 | 3.6851 | 2019-04-18 08:00 | 2.0577 | 3.531 | 5.9679 | 5.9679 | 5.9679 | 5.9679
2021-02-18 21:00 | 1.9217 | 2.3385 | 2.2881 | 2.461 | 2.3313 | 2.5043 | 1.5061 | 2.5827 | 3.1869 | 3.1869 | 3.5897 | 3.5897 | 2019-04-18 09:00 | 1.9891 | 3.4133 | 5.769 | 5.769 | 5.769 | 5.769
2021-02-18 22:00 | 1.7805 | 2.1666 | 2.1199 | 2.2801 | 2.16 | 2.3202 | 1.3064 | 2.2403 | 2.7644 | 2.7644 | 3.1138 | 3.1138 | 2019-04-18 10:00 | 2.0501 | 3.5179 | 5.9458 | 5.9458 | 5.9458 | 5.9458
2021-02-18 23:00 | 1.4947 | 1.8189 | 1.7796 | 1.9141 | 1.8133 | 1.9478 | 1.1146 | 1.9113 | 2.3584 | 2.3584 | 2.6565 | 2.6565 | 2019-04-18 11:00 | 2.0882 | 3.5833 | 6.0564 | 6.0564 | 6.0564 | 6.0564
2021-02-19 | 1.404 | 1.7085 | 1.6717 | 1.798 | 1.7033 | 1.8296 | 0.98311 | 1.6859 | 2.0803 | 2.0803 | 2.3432 | 2.3432 | 2019-04-18 12:00 | 2.1872 | 3.7533 | 6.3437 | 6.3437 | 6.3437 | 6.3437
2021-02-19 01:00 | 1.2975 | 1.5789 | 1.5448 | 1.6616 | 1.574 | 1.6908 | 0.82591 | 1.4163 | 1.7476 | 1.7476 | 1.9685 | 1.9685 | 2019-04-18 13:00 | 2.1872 | 3.7533 | 6.3437 | 6.3437 | 6.3437 | 6.3437
2021-02-19 02:00 | 1.286 | 1.565 | 1.5312 | 1.647 | 1.5602 | 1.6759 | 0.74876 | 1.284 | 1.5844 | 1.5844 | 1.7846 | 1.7846 | 2019-04-18 14:00 | 2.1872 | 3.7533 | 6.3437 | 6.3437 | 6.3437 | 6.3437
2021-02-19 03:00 | 1.2375 | 1.5059 | 1.4734 | 1.5847 | 1.5012 | 1.6126 | 0.69568 | 1.193 | 1.4721 | 1.4721 | 1.6581 | 1.6581 | 2019-04-18 15:00 | 2.172 | 3.7271 | 6.2995 | 6.2995 | 6.2995 | 6.2995
2021-02-19 04:00 | 1.2403 | 1.5093 | 1.4768 | 1.5884 | 1.5047 | 1.6163 | 0.75157 | 1.2888 | 1.5903 | 1.5903 | 1.7913 | 1.7913 | 2019-04-18 16:00 | 2.0501 | 3.5179 | 5.9458 | 5.9458 | 5.9458 | 5.9458
2021-02-19 05:00 | 1.5037 | 1.8298 | 1.7903 | 1.9256 | 1.8242 | 1.9595 | 0.78591 | 1.3477 | 1.663 | 1.663 | 1.8732 | 1.8732 | 2019-04-18 17:00 | 1.9738 | 3.3871 | 5.7248 | 5.7248 | 5.7248 | 5.7248
2021-02-19 06:00 | 1.6804 | 2.0449 | 2.0008 | 2.152 | 2.0386 | 2.1898 | 1.1003 | 1.8868 | 2.3282 | 2.3282 | 2.6225 | 2.6225 | 2019-04-18 18:00 | 1.8824 | 3.2302 | 5.4596 | 5.4596 | 5.4596 | 5.4596
2021-02-19 07:00 | 1.8948 | 2.3057 | 2.256 | 2.4265 | 2.2986 | 2.4692 | 1.2718 | 2.1809 | 2.691 | 2.691 | 3.0312 | 3.0312 | 2019-04-18 19:00 | 1.8748 | 3.2171 | 5.4375 | 5.4375 | 5.4375 | 5.4375
2021-02-19 08:00 | 2.9093 | 3.5403 | 3.464 | 3.7258 | 3.5294 | 3.7913 | 1.2946 | 2.2201 | 2.7394 | 2.7394 | 3.0857 | 3.0857 | 2019-04-18 20:00 | 1.6309 | 2.7986 | 4.7301 | 4.7301 | 4.7301 | 4.7301
2021-02-19 09:00 | 2.9493 | 3.589 | 3.5116 | 3.7771 | 3.578 | 3.8434 | 1.3203 | 2.2642 | 2.7939 | 2.7939 | 3.147 | 3.147 | 2019-04-18 21:00 | 1.608 | 2.7594 | 4.6638 | 4.6638 | 4.6638 | 4.6638
2021-02-19 10:00 | 3.0636 | 3.7281 | 3.6477 | 3.9234 | 3.7167 | 3.9924 | 1.4461 | 2.4798 | 3.0599 | 3.0599 | 3.4467 | 3.4467 | 2019-04-18 22:00 | 1.5852 | 2.7202 | 4.5975 | 4.5975 | 4.5975 | 4.5975
2021-02-19 11:00 | 2.3292 | 2.8344 | 2.7732 | 2.9828 | 2.8256 | 3.0353 | 1.4775 | 2.5337 | 3.1265 | 3.1265 | 3.5216 | 3.5216 | 2019-04-18 23:00 | 1.5013 | 2.5763 | 4.3544 | 4.3544 | 4.3544 | 4.3544
2021-02-19 12:00 | 2.3035 | 2.8031 | 2.7426 | 2.9499 | 2.7944 | 3.0017 | 1.4775 | 2.5337 | 3.1265 | 3.1265 | 3.5216 | 3.5216 | 2019-04-19 | 1.448 | 2.4848 | 4.1997 | 4.1997 | 4.1997 | 4.1997
2021-02-19 13:00 | 2.3492 | 2.8587 | 2.797 | 3.0085 | 2.8499 | 3.0613 | 1.4804 | 2.5386 | 3.1325 | 3.1325 | 3.5284 | 3.5284 | 2019-04-19 01:00 | 1.4556 | 2.4978 | 4.2218 | 4.2218 | 4.2218 | 4.2218
2021-02-19 14:00 | 2.4092 | 2.9317 | 2.8685 | 3.0853 | 2.9227 | 3.1395 | 1.489 | 2.5533 | 3.1506 | 3.1506 | 3.5489 | 3.5489 | 2019-04-19 02:00 | 1.4785 | 2.5371 | 4.2881 | 4.2881 | 4.2881 | 4.2881
2021-02-19 15:00 | 2.2406 | 2.7266 | 2.6677 | 2.8694 | 2.7181 | 2.9198 | 1.3946 | 2.3916 | 2.9511 | 2.9511 | 3.3241 | 3.3241 | 2019-04-19 03:00 | 1.4404 | 2.4717 | 4.1776 | 4.1776 | 4.1776 | 4.1776
2021-02-19 16:00 | 2.1949 | 2.6709 | 2.6133 | 2.8108 | 2.6627 | 2.8602 | 1.4489 | 2.4847 | 3.066 | 3.066 | 3.4535 | 3.4535 | 2019-04-19 04:00 | 1.5013 | 2.5763 | 4.3544 | 4.3544 | 4.3544 | 4.3544
2021-02-19 17:00 | 2.3663 | 2.8796 | 2.8175 | 3.0304 | 2.8707 | 3.0837 | 1.6004 | 2.7445 | 3.3865 | 3.3865 | 3.8145 | 3.8145 | 2019-04-19 05:00 | 1.5013 | 2.5763 | 4.3544 | 4.3544 | 4.3544 | 4.3544
2021-02-19 18:00 | 2.3492 | 2.8587 | 2.797 | 3.0085 | 2.8499 | 3.0613 | 1.7576 | 3.014 | 3.7191 | 3.7191 | 4.1892 | 4.1892 | 2019-04-19 06:00 | 1.6766 | 2.8771 | 4.8628 | 4.8628 | 4.8628 | 4.8628
2021-02-19 19:00 | 2.2149 | 2.6953 | 2.6371 | 2.8364 | 2.6869 | 2.8863 | 1.6604 | 2.8474 | 3.5135 | 3.5135 | 3.9576 | 3.9576 | 2019-04-19 07:00 | 1.5547 | 2.6678 | 4.5091 | 4.5091 | 4.5091 | 4.5091
2021-02-19 20:00 | 1.8976 | 2.3092 | 2.2594 | 2.4302 | 2.3021 | 2.4729 | 1.6604 | 2.8474 | 3.5135 | 3.5135 | 3.9576 | 3.9576 | 2019-04-19 08:00 | 1.8671 | 3.204 | 5.4154 | 5.4154 | 5.4154 | 5.4154
2021-02-19 21:00 | 1.829 | 2.2258 | 2.1777 | 2.3424 | 2.2189 | 2.3835 | 1.5718 | 2.6954 | 3.326 | 3.326 | 3.7464 | 3.7464 | 2019-04-19 09:00 | 1.8214 | 3.1256 | 5.2827 | 5.2827 | 5.2827 | 5.2827
2021-02-19 22:00 | 1.589 | 1.9336 | 1.8919 | 2.0349 | 1.9277 | 2.0707 | 1.3861 | 2.3769 | 2.9329 | 2.9329 | 3.3036 | 3.3036 | 2019-04-19 10:00 | 1.9662 | 3.374 | 5.7027 | 5.7027 | 5.7027 | 5.7027
2021-02-19 23:00 | 1.5461 | 1.8815 | 1.8409 | 1.98 | 1.8757 | 2.0148 | 1.186 | 2.0338 | 2.5096 | 2.5096 | 2.8268 | 2.8268 | 2019-04-19 11:00 | 1.9357 | 3.3217 | 5.6143 | 5.6143 | 5.6143 | 5.6143
2021-02-20 | 1.4432 | 1.7563 | 1.7184 | 1.8483 | 1.7508 | 1.8807 | 1.013 | 1.7371 | 2.1435 | 2.1435 | 2.4144 | 2.4144 | 2019-04-19 12:00 | 1.9357 | 3.3217 | 5.6143 | 5.6143 | 5.6143 | 5.6143
2021-02-20 01:00 | 1.2832 | 1.5615 | 1.5278 | 1.6433 | 1.5567 | 1.6722 | 0.81735 | 1.4016 | 1.7295 | 1.7295 | 1.9481 | 1.9481 | 2019-04-19 13:00 | 1.9281 | 3.3087 | 5.5922 | 5.5922 | 5.5922 | 5.5922
2021-02-20 02:00 | 1.2318 | 1.4989 | 1.4666 | 1.5775 | 1.4943 | 1.6052 | 0.76305 | 1.3085 | 1.6146 | 1.6146 | 1.8187 | 1.8187 | 2019-04-19 14:00 | 2.0424 | 3.5048 | 5.9237 | 5.9237 | 5.9237 | 5.9237
2021-02-20 03:00 | 1.1976 | 1.4573 | 1.4259 | 1.5337 | 1.4528 | 1.5606 | 0.75448 | 1.2938 | 1.5965 | 1.5965 | 1.7983 | 1.7983 | 2019-04-19 15:00 | 2.0043 | 3.4394 | 5.8132 | 5.8132 | 5.8132 | 5.8132
2021-02-20 04:00 | 1.2175 | 1.4815 | 1.4496 | 1.5591 | 1.477 | 1.5865 | 0.76019 | 1.3036 | 1.6086 | 1.6086 | 1.8119 | 1.8119 | 2019-04-19 16:00 | 1.8824 | 3.2302 | 5.4596 | 5.4596 | 5.4596 | 5.4596
2021-02-20 05:00 | 1.3289 | 1.6171 | 1.5823 | 1.7019 | 1.6122 | 1.7318 | 0.76019 | 1.3036 | 1.6086 | 1.6086 | 1.8119 | 1.8119 | 2019-04-19 17:00 | 1.8214 | 3.1256 | 5.2827 | 5.2827 | 5.2827 | 5.2827
2021-02-20 06:00 | 1.3403 | 1.6311 | 1.5959 | 1.7165 | 1.626 | 1.7467 | 0.9431 | 1.6173 | 1.9956 | 1.9956 | 2.2478 | 2.2478 | 2019-04-19 18:00 | 1.7071 | 2.9294 | 4.9512 | 4.9512 | 4.9512 | 4.9512
2021-02-20 07:00 | 1.4861 | 1.8084 | 1.7694 | 1.9032 | 1.8029 | 1.9366 | 1.0174 | 1.7447 | 2.1528 | 2.1528 | 2.4249 | 2.4249 | 2019-04-19 19:00 | 1.6461 | 2.8248 | 4.7743 | 4.7743 | 4.7743 | 4.7743
2021-02-20 08:00 | 1.5947 | 1.9406 | 1.8987 | 2.0422 | 1.9346 | 2.0781 | 1.2546 | 2.1515 | 2.6548 | 2.6548 | 2.9903 | 2.9903 | 2019-04-19 20:00 | 1.5623 | 2.6809 | 4.5312 | 4.5312 | 4.5312 | 4.5312
2021-02-20 09:00 | 1.689 | 2.0553 | 2.011 | 2.163 | 2.049 | 2.201 | 1.4518 | 2.4896 | 3.072 | 3.072 | 3.4603 | 3.4603 | 2019-04-19 21:00 | 1.4861 | 2.5501 | 4.3102 | 4.3102 | 4.3102 | 4.3102
2021-02-20 10:00 | 1.6233 | 1.9754 | 1.9327 | 2.0788 | 1.9693 | 2.1154 | 1.609 | 2.7592 | 3.4046 | 3.4046 | 3.8349 | 3.8349 | 2019-04-19 22:00 | 1.4937 | 2.5632 | 4.3323 | 4.3323 | 4.3323 | 4.3323
2021-02-20 11:00 | 1.6118 | 1.9614 | 1.9191 | 2.0642 | 1.9554 | 2.1005 | 1.5661 | 2.6856 | 3.3139 | 3.3139 | 3.7328 | 3.7328 | 2019-04-19 23:00 | 1.4937 | 2.5632 | 4.3323 | 4.3323 | 4.3323 | 4.3323
2021-02-20 12:00 | 1.6318 | 1.9858 | 1.943 | 2.0898 | 1.9797 | 2.1265 | 1.6061 | 2.7543 | 3.3986 | 3.3986 | 3.8281 | 3.8281 | 2019-04-20 | 1.4632 | 2.5109 | 4.2439 | 4.2439 | 4.2439 | 4.2439
2021-02-20 13:00 | 1.8948 | 2.3057 | 2.256 | 2.4265 | 2.2986 | 2.4692 | 1.7662 | 3.0287 | 3.7372 | 3.7372 | 4.2096 | 4.2096 | 2019-04-20 01:00 | 1.4251 | 2.4455 | 4.1333 | 4.1333 | 4.1333 | 4.1333
2021-02-20 14:00 | 1.7947 | 2.184 | 2.1369 | 2.2984 | 2.1773 | 2.3388 | 1.6404 | 2.8131 | 3.4712 | 3.4712 | 3.9099 | 3.9099 | 2019-04-20 02:00 | 1.3794 | 2.3671 | 4.0007 | 4.0007 | 4.0007 | 4.0007
2021-02-20 15:00 | 1.6576 | 2.0171 | 1.9736 | 2.1228 | 2.0109 | 2.1601 | 1.6576 | 2.8425 | 3.5074 | 3.5074 | 3.9507 | 3.9507 | 2019-04-20 03:00 | 1.387 | 2.3801 | 4.0228 | 4.0228 | 4.0228 | 4.0228
2021-02-20 16:00 | 1.749 | 2.1284 | 2.0825 | 2.2399 | 2.1218 | 2.2792 | 1.8176 | 3.1169 | 3.8461 | 3.8461 | 4.3322 | 4.3322 | 2019-04-20 04:00 | 1.4251 | 2.4455 | 4.1333 | 4.1333 | 4.1333 | 4.1333
2021-02-20 17:00 | 1.9148 | 2.3301 | 2.2798 | 2.4522 | 2.3229 | 2.4952 | 1.8176 | 3.1169 | 3.8461 | 3.8461 | 4.3322 | 4.3322 | 2019-04-20 05:00 | 1.4404 | 2.4717 | 4.1776 | 4.1776 | 4.1776 | 4.1776
2021-02-20 18:00 | 1.9919 | 2.424 | 2.3717 | 2.551 | 2.4165 | 2.5958 | 1.789 | 3.0679 | 3.7856 | 3.7856 | 4.2641 | 4.2641 | 2019-04-20 06:00 | 1.6309 | 2.7986 | 4.7301 | 4.7301 | 4.7301 | 4.7301
2021-02-20 19:00 | 1.9405 | 2.3614 | 2.3104 | 2.4851 | 2.3541 | 2.5288 | 1.7291 | 2.9651 | 3.6588 | 3.6588 | 4.1213 | 4.1213 | 2019-04-20 07:00 | 1.669 | 2.864 | 4.8407 | 4.8407 | 4.8407 | 4.8407
2021-02-20 20:00 | 1.9119 | 2.3266 | 2.2764 | 2.4485 | 2.3194 | 2.4915 | 1.7376 | 2.9797 | 3.6768 | 3.6768 | 4.1415 | 4.1415 | 2019-04-20 08:00 | 1.9281 | 3.3087 | 5.5922 | 5.5922 | 5.5922 | 5.5922
2021-02-20 21:00 | 1.8576 | 2.2605 | 2.2118 | 2.379 | 2.2536 | 2.4208 | 1.7547 | 3.0091 | 3.713 | 3.713 | 4.1823 | 4.1823 | 2019-04-20 09:00 | 1.9205 | 3.2956 | 5.5701 | 5.5701 | 5.5701 | 5.5701
2021-02-20 22:00 | 1.8005 | 2.191 | 2.1437 | 2.3058 | 2.1842 | 2.3463 | 1.5747 | 2.7003 | 3.3321 | 3.3321 | 3.7532 | 3.7532 | 2019-04-20 10:00 | 2.0424 | 3.5048 | 5.9237 | 5.9237 | 5.9237 | 5.9237
2021-02-20 23:00 | 1.649 | 2.0067 | 1.9634 | 2.1118 | 2.0005 | 2.1489 | 1.2975 | 2.225 | 2.7455 | 2.7455 | 3.0925 | 3.0925 | 2019-04-20 11:00 | 2.0729 | 3.5571 | 6.0121 | 6.0121 | 6.0121 | 6.0121
2021-02-21 | 1.5147 | 1.8432 | 1.8034 | 1.9398 | 1.8375 | 1.9738 | 1.1546 | 1.9799 | 2.4431 | 2.4431 | 2.7519 | 2.7519 | 2019-04-20 12:00 | 2.0653 | 3.5441 | 5.99 | 5.99 | 5.99 | 5.99
2021-02-21 01:00 | 1.3975 | 1.7006 | 1.6639 | 1.7897 | 1.6954 | 1.8211 | 0.94881 | 1.6271 | 2.0077 | 2.0077 | 2.2615 | 2.2615 | 2019-04-20 13:00 | 2.1034 | 3.6094 | 6.1006 | 6.1006 | 6.1006 | 6.1006
2021-02-21 02:00 | 1.2918 | 1.572 | 1.5381 | 1.6543 | 1.5672 | 1.6834 | 0.82307 | 1.4114 | 1.7416 | 1.7416 | 1.9617 | 1.9617 | 2019-04-20 14:00 | 2.1339 | 3.6618 | 6.189 | 6.189 | 6.189 | 6.189
2021-02-21 03:00 | 1.2642 | 1.5384 | 1.5052 | 1.619 | 1.5337 | 1.6475 | 0.81449 | 1.3967 | 1.7235 | 1.7235 | 1.9413 | 1.9413 | 2019-04-20 15:00 | 2.1034 | 3.6094 | 6.1006 | 6.1006 | 6.1006 | 6.1006
2021-02-21 04:00 | 1.2426 | 1.5122 | 1.4795 | 1.5914 | 1.5075 | 1.6193 | 0.78877 | 1.3526 | 1.6691 | 1.6691 | 1.88 | 1.88 | 2019-04-20 16:00 | 2.0729 | 3.5571 | 6.0121 | 6.0121 | 6.0121 | 6.0121
2021-02-21 05:00 | 1.2689 | 1.5441 | 1.5108 | 1.625 | 1.5394 | 1.6536 | 0.82592 | 1.4163 | 1.7477 | 1.7477 | 1.9686 | 1.9686 | 2019-04-20 17:00 | 1.951 | 3.3479 | 5.6585 | 5.6585 | 5.6585 | 5.6585
2021-02-21 06:00 | 1.2661 | 1.5407 | 1.5075 | 1.6214 | 1.5359 | 1.6499 | 0.89166 | 1.529 | 1.8868 | 1.8868 | 2.1252 | 2.1252 | 2019-04-20 18:00 | 1.8519 | 3.1779 | 5.3711 | 5.3711 | 5.3711 | 5.3711
2021-02-21 07:00 | 1.4432 | 1.7563 | 1.7184 | 1.8483 | 1.7508 | 1.8807 | 1.0002 | 1.7152 | 2.1165 | 2.1165 | 2.384 | 2.384 | 2019-04-20 19:00 | 1.7528 | 3.0079 | 5.0838 | 5.0838 | 5.0838 | 5.0838
2021-02-21 08:00 | 1.5433 | 1.878 | 1.8375 | 1.9764 | 1.8722 | 2.0111 | 1.2632 | 2.1662 | 2.6729 | 2.6729 | 3.0107 | 3.0107 | 2019-04-20 20:00 | 1.669 | 2.864 | 4.8407 | 4.8407 | 4.8407 | 4.8407
2021-02-21 09:00 | 1.5976 | 1.9441 | 1.9021 | 2.0459 | 1.9381 | 2.0818 | 1.4347 | 2.4602 | 3.0357 | 3.0357 | 3.4194 | 3.4194 | 2019-04-20 21:00 | 1.6157 | 2.7725 | 4.6859 | 4.6859 | 4.6859 | 4.6859
2021-02-21 10:00 | 1.5947 | 1.9406 | 1.8987 | 2.0422 | 1.9346 | 2.0781 | 1.5804 | 2.7101 | 3.3442 | 3.3442 | 3.7668 | 3.7668 | 2019-04-20 22:00 | 1.5699 | 2.694 | 4.5533 | 4.5533 | 4.5533 | 4.5533
2021-02-21 11:00 | 1.5633 | 1.9023 | 1.8613 | 2.002 | 1.8965 | 2.0372 | 1.6773 | 2.8763 | 3.5492 | 3.5492 | 3.9978 | 3.9978 | 2019-04-20 23:00 | 1.4861 | 2.5501 | 4.3102 | 4.3102 | 4.3102 | 4.3102
2021-02-21 12:00 | 1.5621 | 1.901 | 1.86 | 2.0005 | 1.8951 | 2.0357 | 1.7204 | 2.9503 | 3.6405 | 3.6405 | 4.1006 | 4.1006 | 2019-04-21 | 1.4937 | 2.5632 | 4.3323 | 4.3323 | 4.3323 | 4.3323
2021-02-21 13:00 | 1.7822 | 2.1687 | 2.122 | 2.2824 | 2.1621 | 2.3225 | 1.809 | 3.1022 | 3.8279 | 3.8279 | 4.3118 | 4.3118 | 2019-04-21 01:00 | 1.4404 | 2.4717 | 4.1776 | 4.1776 | 4.1776 | 4.1776
2021-02-21 14:00 | 1.9405 | 2.3614 | 2.3104 | 2.4851 | 2.3541 | 2.5288 | 1.7633 | 3.0238 | 3.7312 | 3.7312 | 4.2028 | 4.2028 | 2019-04-21 02:00 | 1.4404 | 2.4717 | 4.1776 | 4.1776 | 4.1776 | 4.1776
2021-02-21 15:00 | 1.7833 | 2.1701 | 2.1233 | 2.2838 | 2.1634 | 2.3239 | 1.6976 | 2.9111 | 3.5921 | 3.5921 | 4.0461 | 4.0461 | 2019-04-21 03:00 | 1.4404 | 2.4717 | 4.1776 | 4.1776 | 4.1776 | 4.1776
2021-02-21 16:00 | 1.8405 | 2.2397 | 2.1914 | 2.357 | 2.2328 | 2.3984 | 1.6047 | 2.7519 | 3.3957 | 3.3957 | 3.8248 | 3.8248 | 2019-04-21 04:00 | 1.4327 | 2.4586 | 4.1555 | 4.1555 | 4.1555 | 4.1555
2021-02-21 17:00 | 1.8205 | 2.2153 | 2.1675 | 2.3314 | 2.2085 | 2.3723 | 1.609 | 2.7592 | 3.4046 | 3.4046 | 3.8349 | 3.8349 | 2019-04-21 05:00 | 1.4937 | 2.5632 | 4.3323 | 4.3323 | 4.3323 | 4.3323
2021-02-21 18:00 | 1.9262 | 2.344 | 2.2934 | 2.4668 | 2.3368 | 2.5101 | 1.5633 | 2.6807 | 3.3079 | 3.3079 | 3.726 | 3.726 | 2019-04-21 06:00 | 1.5623 | 2.6809 | 4.5312 | 4.5312 | 4.5312 | 4.5312
2021-02-21 19:00 | 1.8576 | 2.2605 | 2.2118 | 2.379 | 2.2536 | 2.4208 | 1.549 | 2.6562 | 3.2776 | 3.2776 | 3.6919 | 3.6919 | 2019-04-21 07:00 | 1.6919 | 2.9032 | 4.907 | 4.907 | 4.907 | 4.907
2021-02-21 20:00 | 1.8748 | 2.2814 | 2.2322 | 2.4009 | 2.2744 | 2.4431 | 1.5232 | 2.6121 | 3.2232 | 3.2232 | 3.6306 | 3.6306 | 2019-04-21 08:00 | 1.9129 | 3.2825 | 5.548 | 5.548 | 5.548 | 5.548
2021-02-21 21:00 | 1.849 | 2.2501 | 2.2016 | 2.368 | 2.2432 | 2.4096 | 1.509 | 2.5876 | 3.193 | 3.193 | 3.5965 | 3.5965 | 2019-04-21 09:00 | 1.9967 | 3.4264 | 5.7911 | 5.7911 | 5.7911 | 5.7911
2021-02-21 22:00 | 1.6633 | 2.024 | 1.9804 | 2.1301 | 2.0178 | 2.1675 | 1.3261 | 2.274 | 2.8059 | 2.8059 | 3.1606 | 3.1606 | 2019-04-21 10:00 | 2.0196 | 3.4656 | 5.8574 | 5.8574 | 5.8574 | 5.8574
2021-02-21 23:00 | 1.5461 | 1.8815 | 1.8409 | 1.98 | 1.8757 | 2.0148 | 1.118 | 1.9172 | 2.3657 | 2.3657 | 2.6647 | 2.6647 | 2019-04-21 11:00 | 2.0653 | 3.5441 | 5.99 | 5.99 | 5.99 | 5.99
2021-02-22 | 1.4261 | 1.7354 | 1.698 | 1.8263 | 1.73 | 1.8584 | 0.94881 | 1.6271 | 2.0077 | 2.0077 | 2.2615 | 2.2615 | 2019-04-21 12:00 | 2.1034 | 3.6094 | 6.1006 | 6.1006 | 6.1006 | 6.1006
2021-02-22 01:00 | 1.3118 | 1.5963 | 1.5618 | 1.6799 | 1.5914 | 1.7094 | 0.8545 | 1.4653 | 1.8081 | 1.8081 | 2.0367 | 2.0367 | 2019-04-21 13:00 | 2.0805 | 3.5702 | 6.0343 | 6.0343 | 6.0343 | 6.0343
2021-02-22 02:00 | 1.2517 | 1.5232 | 1.4904 | 1.603 | 1.5186 | 1.6312 | 0.82592 | 1.4163 | 1.7477 | 1.7477 | 1.9686 | 1.9686 | 2019-04-21 14:00 | 2.1415 | 3.6748 | 6.2111 | 6.2111 | 6.2111 | 6.2111
2021-02-22 03:00 | 1.2175 | 1.4815 | 1.4496 | 1.5591 | 1.477 | 1.5865 | 0.81449 | 1.3967 | 1.7235 | 1.7235 | 1.9413 | 1.9413 | 2019-04-21 15:00 | 2.1186 | 3.6356 | 6.1448 | 6.1448 | 6.1448 | 6.1448
2021-02-22 04:00 | 1.2241 | 1.4896 | 1.4575 | 1.5677 | 1.485 | 1.5952 | 0.82021 | 1.4065 | 1.7356 | 1.7356 | 1.9549 | 1.9549 | 2019-04-21 16:00 | 2.0882 | 3.5833 | 6.0564 | 6.0564 | 6.0564 | 6.0564
2021-02-22 05:00 | 1.3572 | 1.6516 | 1.616 | 1.7381 | 1.6465 | 1.7687 | 0.83164 | 1.4261 | 1.7598 | 1.7598 | 1.9822 | 1.9822 | 2019-04-21 17:00 | 1.9967 | 3.4264 | 5.7911 | 5.7911 | 5.7911 | 5.7911
2021-02-22 06:00 | 1.789 | 2.1771 | 2.1301 | 2.2911 | 2.1704 | 2.3314 | 1.0803 | 1.8525 | 2.2859 | 2.2859 | 2.5748 | 2.5748 | 2019-04-21 18:00 | 1.9281 | 3.3087 | 5.5922 | 5.5922 | 5.5922 | 5.5922
2021-02-22 07:00 | 2.1491 | 2.6153 | 2.5588 | 2.7523 | 2.6072 | 2.8006 | 1.2918 | 2.2152 | 2.7334 | 2.7334 | 3.0789 | 3.0789 | 2019-04-21 19:00 | 1.8443 | 3.1648 | 5.349 | 5.349 | 5.349 | 5.349
2021-02-22 08:00 | 2.2235 | 2.7058 | 2.6474 | 2.8475 | 2.6975 | 2.8976 | 1.3489 | 2.3132 | 2.8543 | 2.8543 | 3.2151 | 3.2151 | 2019-04-21 20:00 | 1.7833 | 3.0602 | 5.1722 | 5.1722 | 5.1722 | 5.1722
2021-02-22 09:00 | 2.2406 | 2.7266 | 2.6677 | 2.8694 | 2.7181 | 2.9198 | 1.4061 | 2.4112 | 2.9753 | 2.9753 | 3.3513 | 3.3513 | 2019-04-21 21:00 | 1.6919 | 2.9032 | 4.907 | 4.907 | 4.907 | 4.907
2021-02-22 10:00 | 2.4864 | 3.0256 | 2.9604 | 3.1841 | 3.0163 | 3.2401 | 1.4004 | 2.4014 | 2.9632 | 2.9632 | 3.3377 | 3.3377 | 2019-04-21 22:00 | 1.5852 | 2.7202 | 4.5975 | 4.5975 | 4.5975 | 4.5975
2021-02-22 11:00 | 2.6464 | 3.2204 | 3.1509 | 3.3891 | 3.2105 | 3.4486 | 1.3946 | 2.3916 | 2.9511 | 2.9511 | 3.3241 | 3.3241 | 2019-04-21 23:00 | 1.5166 | 2.6025 | 4.3986 | 4.3986 | 4.3986 | 4.3986
2021-02-22 12:00 | 2.695 | 3.2795 | 3.2088 | 3.4513 | 3.2694 | 3.512 | 1.4689 | 2.519 | 3.1083 | 3.1083 | 3.5012 | 3.5012 | 2019-04-22 | 1.4251 | 2.4455 | 4.1333 | 4.1333 | 4.1333 | 4.1333
2021-02-22 13:00 | 2.8179 | 3.4291 | 3.3551 | 3.6087 | 3.4185 | 3.6721 | 1.5061 | 2.5827 | 3.1869 | 3.1869 | 3.5897 | 3.5897 | 2019-04-22 01:00 | 1.4175 | 2.4324 | 4.1112 | 4.1112 | 4.1112 | 4.1112
2021-02-22 14:00 | 2.9522 | 3.5925 | 3.515 | 3.7807 | 3.5814 | 3.8471 | 1.5575 | 2.6709 | 3.2958 | 3.2958 | 3.7123 | 3.7123 | 2019-04-22 02:00 | 1.4327 | 2.4586 | 4.1555 | 4.1555 | 4.1555 | 4.1555
2021-02-22 15:00 | 2.8436 | 3.4604 | 3.3857 | 3.6416 | 3.4497 | 3.7056 | 1.4775 | 2.5337 | 3.1265 | 3.1265 | 3.5216 | 3.5216 | 2019-04-22 03:00 | 1.4251 | 2.4455 | 4.1333 | 4.1333 | 4.1333 | 4.1333
2021-02-22 16:00 | 2.7036 | 3.2899 | 3.219 | 3.4623 | 3.2798 | 3.5231 | 1.4604 | 2.5043 | 3.0902 | 3.0902 | 3.4807 | 3.4807 | 2019-04-22 04:00 | 1.4327 | 2.4586 | 4.1555 | 4.1555 | 4.1555 | 4.1555
2021-02-22 17:00 | 2.9093 | 3.5403 | 3.464 | 3.7258 | 3.5294 | 3.7913 | 1.6604 | 2.8474 | 3.5135 | 3.5135 | 3.9576 | 3.9576 | 2019-04-22 05:00 | 1.5394 | 2.6417 | 4.4649 | 4.4649 | 4.4649 | 4.4649
2021-02-22 18:00 | 2.8493 | 3.4673 | 3.3925 | 3.649 | 3.4566 | 3.7131 | 1.7433 | 2.9895 | 3.6889 | 3.6889 | 4.1551 | 4.1551 | 2019-04-22 06:00 | 1.6157 | 2.7725 | 4.6859 | 4.6859 | 4.6859 | 4.6859
2021-02-22 19:00 | 2.6464 | 3.2204 | 3.1509 | 3.3891 | 3.2105 | 3.4486 | 1.7147 | 2.9405 | 3.6284 | 3.6284 | 4.087 | 4.087 | 2019-04-22 07:00 | 1.6233 | 2.7855 | 4.708 | 4.708 | 4.708 | 4.708
2021-02-22 20:00 | 2.0834 | 2.5353 | 2.4806 | 2.6681 | 2.5275 | 2.715 | 1.6719 | 2.867 | 3.5377 | 3.5377 | 3.9848 | 3.9848 | 2019-04-22 08:00 | 1.8062 | 3.0994 | 5.2385 | 5.2385 | 5.2385 | 5.2385
2021-02-22 21:00 | 1.9605 | 2.3857 | 2.3343 | 2.5107 | 2.3784 | 2.5548 | 1.4975 | 2.568 | 3.1688 | 3.1688 | 3.5693 | 3.5693 | 2019-04-22 09:00 | 1.9891 | 3.4133 | 5.769 | 5.769 | 5.769 | 5.769
2021-02-22 22:00 | 1.7749 | 2.1599 | 2.1133 | 2.273 | 2.1532 | 2.3129 | 1.3944 | 2.3912 | 2.9506 | 2.9506 | 3.3235 | 3.3235 | 2019-04-22 10:00 | 2.0805 | 3.5702 | 6.0343 | 6.0343 | 6.0343 | 6.0343
2021-02-22 23:00 | 1.509 | 1.8362 | 1.7966 | 1.9324 | 1.8306 | 1.9664 | 1.1169 | 1.9154 | 2.3634 | 2.3634 | 2.6622 | 2.6622 | 2019-04-22 11:00 | 2.1644 | 3.7141 | 6.2774 | 6.2774 | 6.2774 | 6.2774
2021-02-23 | 1.4604 | 1.7771 | 1.7388 | 1.8702 | 1.7716 | 1.9031 | 0.96025 | 1.6467 | 2.0319 | 2.0319 | 2.2887 | 2.2887 | 2019-04-22 12:00 | 2.2482 | 3.8579 | 6.5205 | 6.5205 | 6.5205 | 6.5205
2021-02-23 01:00 | 1.3032 | 1.5858 | 1.5516 | 1.6689 | 1.581 | 1.6982 | 0.81164 | 1.3918 | 1.7174 | 1.7174 | 1.9345 | 1.9345 | 2019-04-22 13:00 | 2.1872 | 3.7533 | 6.3437 | 6.3437 | 6.3437 | 6.3437
2021-02-23 02:00 | 1.2346 | 1.5024 | 1.47 | 1.5811 | 1.4978 | 1.6089 | 0.78877 | 1.3526 | 1.6691 | 1.6691 | 1.88 | 1.88 | 2019-04-22 14:00 | 2.2634 | 3.8841 | 6.5647 | 6.5647 | 6.5647 | 6.5647
2021-02-23 03:00 | 1.1914 | 1.4498 | 1.4186 | 1.5258 | 1.4454 | 1.5526 | 0.75734 | 1.2987 | 1.6025 | 1.6025 | 1.8051 | 1.8051 | 2019-04-22 15:00 | 2.2101 | 3.7925 | 6.41 | 6.41 | 6.41 | 6.41
2021-02-23 04:00 | 1.227 | 1.4931 | 1.4609 | 1.5714 | 1.4885 | 1.599 | 0.79735 | 1.3673 | 1.6872 | 1.6872 | 1.9004 | 1.9004 | 2019-04-22 16:00 | 2.1339 | 3.6618 | 6.189 | 6.189 | 6.189 | 6.189
2021-02-23 05:00 | 1.3632 | 1.6589 | 1.6231 | 1.7458 | 1.6538 | 1.7765 | 0.8002 | 1.3722 | 1.6932 | 1.6932 | 1.9073 | 1.9073 | 2019-04-22 17:00 | 1.9738 | 3.3871 | 5.7248 | 5.7248 | 5.7248 | 5.7248
2021-02-23 06:00 | 1.7347 | 2.111 | 2.0655 | 2.2216 | 2.1045 | 2.2606 | 1.0145 | 1.7398 | 2.1468 | 2.1468 | 2.4181 | 2.4181 | 2019-04-22 18:00 | 1.9738 | 3.3871 | 5.7248 | 5.7248 | 5.7248 | 5.7248
2021-02-23 07:00 | 1.9691 | 2.3962 | 2.3445 | 2.5217 | 2.3888 | 2.566 | 1.1774 | 2.0191 | 2.4915 | 2.4915 | 2.8064 | 2.8064 | 2019-04-22 19:00 | 1.8671 | 3.204 | 5.4154 | 5.4154 | 5.4154 | 5.4154
2021-02-23 08:00 | 2.0348 | 2.4762 | 2.4227 | 2.6059 | 2.4685 | 2.6517 | 1.3489 | 2.3132 | 2.8543 | 2.8543 | 3.2151 | 3.2151 | 2019-04-22 20:00 | 1.7833 | 3.0602 | 5.1722 | 5.1722 | 5.1722 | 5.1722
2021-02-23 09:00 | 2.4864 | 3.0256 | 2.9604 | 3.1841 | 3.0163 | 3.2401 | 1.4061 | 2.4112 | 2.9753 | 2.9753 | 3.3513 | 3.3513 | 2019-04-22 21:00 | 1.7223 | 2.9556 | 4.9954 | 4.9954 | 4.9954 | 4.9954
2021-02-23 10:00 | 2.4749 | 3.0117 | 2.9468 | 3.1695 | 3.0024 | 3.2252 | 1.4004 | 2.4014 | 2.9632 | 2.9632 | 3.3377 | 3.3377 | 2019-04-22 22:00 | 1.6995 | 2.9163 | 4.9291 | 4.9291 | 4.9291 | 4.9291
2021-02-23 11:00 | 2.5121 | 3.0569 | 2.991 | 3.2171 | 3.0475 | 3.2736 | 1.3946 | 2.3916 | 2.9511 | 2.9511 | 3.3241 | 3.3241 | 2019-04-22 23:00 | 1.6004 | 2.7463 | 4.6417 | 4.6417 | 4.6417 | 4.6417
2021-02-23 12:00 | 2.4806 | 3.0187 | 2.9536 | 3.1768 | 3.0094 | 3.2326 | 1.4689 | 2.519 | 3.1083 | 3.1083 | 3.5012 | 3.5012 | 2019-04-23 | 1.5623 | 2.6809 | 4.5312 | 4.5312 | 4.5312 | 4.5312
2021-02-23 13:00 | 2.6064 | 3.1717 | 3.1033 | 3.3379 | 3.1619 | 3.3965 | 1.5061 | 2.5827 | 3.1869 | 3.1869 | 3.5897 | 3.5897 | 2019-04-23 01:00 | 1.509 | 2.5894 | 4.3765 | 4.3765 | 4.3765 | 4.3765
2021-02-23 14:00 | 2.1063 | 2.5631 | 2.5078 | 2.6974 | 2.5552 | 2.7448 | 1.5575 | 2.6709 | 3.2958 | 3.2958 | 3.7123 | 3.7123 | 2019-04-23 02:00 | 1.5242 | 2.6155 | 4.4207 | 4.4207 | 4.4207 | 4.4207
2021-02-23 15:00 | 2.172 | 2.6431 | 2.5861 | 2.7815 | 2.6349 | 2.8304 | 1.3118 | 2.2495 | 2.7757 | 2.7757 | 3.1265 | 3.1265 | 2019-04-23 03:00 | 1.509 | 2.5894 | 4.3765 | 4.3765 | 4.3765 | 4.3765
2021-02-23 16:00 | 2.1148 | 2.5735 | 2.518 | 2.7083 | 2.5656 | 2.7559 | 1.3946 | 2.3916 | 2.9511 | 2.9511 | 3.3241 | 3.3241 | 2019-04-23 04:00 | 1.4937 | 2.5632 | 4.3323 | 4.3323 | 4.3323 | 4.3323
2021-02-23 17:00 | 2.1434 | 2.6083 | 2.552 | 2.7449 | 2.6003 | 2.7932 | 1.5204 | 2.6072 | 3.2172 | 3.2172 | 3.6238 | 3.6238 | 2019-04-23 05:00 | 1.6461 | 2.8248 | 4.7743 | 4.7743 | 4.7743 | 4.7743
2021-02-23 18:00 | 2.192 | 2.6674 | 2.6099 | 2.8072 | 2.6592 | 2.8565 | 1.5004 | 2.5729 | 3.1748 | 3.1748 | 3.5761 | 3.5761 | 2019-04-23 06:00 | 1.7605 | 3.0209 | 5.1059 | 5.1059 | 5.1059 | 5.1059
2021-02-23 19:00 | 2.1148 | 2.5735 | 2.518 | 2.7083 | 2.5656 | 2.7559 | 1.5861 | 2.7199 | 3.3563 | 3.3563 | 3.7805 | 3.7805 | 2019-04-23 07:00 | 1.829 | 3.1386 | 5.3048 | 5.3048 | 5.3048 | 5.3048
2021-02-23 20:00 | 2.0948 | 2.5492 | 2.4942 | 2.6827 | 2.5413 | 2.7299 | 1.509 | 2.5876 | 3.193 | 3.193 | 3.5965 | 3.5965 | 2019-04-23 08:00 | 2.1567 | 3.701 | 6.2553 | 6.2553 | 6.2553 | 6.2553
2021-02-23 21:00 | 1.9462 | 2.3683 | 2.3173 | 2.4924 | 2.361 | 2.5362 | 1.5204 | 2.6072 | 3.2172 | 3.2172 | 3.6238 | 3.6238 | 2019-04-23 09:00 | 2.1034 | 3.6094 | 6.1006 | 6.1006 | 6.1006 | 6.1006
2021-02-23 22:00 | 1.6949 | 2.0625 | 2.018 | 2.1706 | 2.0562 | 2.2087 | 1.2746 | 2.1858 | 2.6971 | 2.6971 | 3.038 | 3.038 | 2019-04-23 10:00 | 2.2558 | 3.871 | 6.5426 | 6.5426 | 6.5426 | 6.5426
2021-02-23 23:00 | 1.4689 | 1.7876 | 1.749 | 1.8812 | 1.7821 | 1.9143 | 1.0431 | 1.7888 | 2.2073 | 2.2073 | 2.4862 | 2.4862 | 2019-04-23 11:00 | 2.2863 | 3.9233 | 6.631 | 6.631 | 6.631 | 6.631
2021-02-24 | 1.3832 | 1.6832 | 1.6469 | 1.7714 | 1.678 | 1.8025 | 0.90434 | 1.5508 | 1.9136 | 1.9136 | 2.1554 | 2.1554 | 2019-04-23 12:00 | 2.5302 | 4.3418 | 7.3384 | 7.3384 | 7.3384 | 7.3384
2021-02-24 01:00 | 1.2217 | 1.4866 | 1.4546 | 1.5645 | 1.4821 | 1.592 | 0.76019 | 1.3036 | 1.6086 | 1.6086 | 1.8119 | 1.8119 | 2019-04-23 13:00 | 2.5378 | 4.3549 | 7.3605 | 7.3605 | 7.3605 | 7.3605
2021-02-24 02:00 | 1.2346 | 1.5024 | 1.47 | 1.5811 | 1.4978 | 1.6089 | 0.74674 | 1.2805 | 1.5801 | 1.5801 | 1.7798 | 1.7798 | 2019-04-23 14:00 | 2.5607 | 4.3941 | 7.4268 | 7.4268 | 7.4268 | 7.4268
2021-02-24 03:00 | 1.2269 | 1.493 | 1.4608 | 1.5712 | 1.4884 | 1.5988 | 0.77734 | 1.333 | 1.6449 | 1.6449 | 1.8528 | 1.8528 | 2019-04-23 15:00 | 2.5683 | 4.4072 | 7.4489 | 7.4489 | 7.4489 | 7.4489
2021-02-24 04:00 | 1.2232 | 1.4885 | 1.4564 | 1.5664 | 1.4839 | 1.594 | 0.70018 | 1.2007 | 1.4816 | 1.4816 | 1.6688 | 1.6688 | 2019-04-23 16:00 | 2.2939 | 3.9364 | 6.6531 | 6.6531 | 6.6531 | 6.6531
2021-02-24 05:00 | 1.4032 | 1.7076 | 1.6707 | 1.797 | 1.7023 | 1.8286 | 0.76305 | 1.3085 | 1.6146 | 1.6146 | 1.8187 | 1.8187 | 2019-04-23 17:00 | 2.1263 | 3.6487 | 6.1669 | 6.1669 | 6.1669 | 6.1669
2021-02-24 06:00 | 1.6976 | 2.0658 | 2.0212 | 2.174 | 2.0594 | 2.2122 | 0.91452 | 1.5683 | 1.9351 | 1.9351 | 2.1797 | 2.1797 | 2019-04-23 18:00 | 2.0958 | 3.5964 | 6.0785 | 6.0785 | 6.0785 | 6.0785
2021-02-24 07:00 | 1.9376 | 2.3579 | 2.307 | 2.4814 | 2.3506 | 2.525 | 1.2032 | 2.0632 | 2.5459 | 2.5459 | 2.8677 | 2.8677 | 2019-04-23 19:00 | 2.0043 | 3.4394 | 5.8132 | 5.8132 | 5.8132 | 5.8132
2021-02-24 08:00 | 2.172 | 2.6431 | 2.5861 | 2.7815 | 2.6349 | 2.8304 | 1.2603 | 2.1613 | 2.6669 | 2.6669 | 3.0039 | 3.0039 | 2019-04-23 20:00 | 1.9205 | 3.2956 | 5.5701 | 5.5701 | 5.5701 | 5.5701
2021-02-24 09:00 | 1.9748 | 2.4031 | 2.3513 | 2.529 | 2.3957 | 2.5734 | 1.3232 | 2.2691 | 2.7999 | 2.7999 | 3.1538 | 3.1538 | 2019-04-23 21:00 | 1.7147 | 2.9425 | 4.9733 | 4.9733 | 4.9733 | 4.9733
2021-02-24 10:00 | 2.0405 | 2.4831 | 2.4295 | 2.6132 | 2.4755 | 2.6591 | 1.3146 | 2.2544 | 2.7818 | 2.7818 | 3.1333 | 3.1333 | 2019-04-23 22:00 | 1.669 | 2.864 | 4.8407 | 4.8407 | 4.8407 | 4.8407
2021-02-24 11:00 | 2.092 | 2.5457 | 2.4908 | 2.6791 | 2.5379 | 2.7261 | 1.3575 | 2.3279 | 2.8725 | 2.8725 | 3.2355 | 3.2355 | 2019-04-23 23:00 | 1.6538 | 2.8379 | 4.7965 | 4.7965 | 4.7965 | 4.7965
2021-02-24 12:00 | 2.1548 | 2.6222 | 2.5657 | 2.7596 | 2.6141 | 2.8081 | 1.3775 | 2.3622 | 2.9148 | 2.9148 | 3.2832 | 3.2832 | 2019-04-24 | 1.5623 | 2.6809 | 4.5312 | 4.5312 | 4.5312 | 4.5312
2021-02-24 13:00 | 2.0977 | 2.5527 | 2.4976 | 2.6864 | 2.5448 | 2.7336 | 1.3918 | 2.3867 | 2.945 | 2.945 | 3.3173 | 3.3173 | 2019-04-24 01:00 | 1.5394 | 2.6417 | 4.4649 | 4.4649 | 4.4649 | 4.4649
2021-02-24 14:00 | 2.152 | 2.6187 | 2.5623 | 2.7559 | 2.6107 | 2.8043 | 1.4318 | 2.4553 | 3.0297 | 3.0297 | 3.4126 | 3.4126 | 2019-04-24 02:00 | 1.5394 | 2.6417 | 4.4649 | 4.4649 | 4.4649 | 4.4649
2021-02-24 15:00 | 2.1148 | 2.5735 | 2.518 | 2.7083 | 2.5656 | 2.7559 | 1.3146 | 2.2544 | 2.7818 | 2.7818 | 3.1333 | 3.1333 | 2019-04-24 03:00 | 1.5166 | 2.6025 | 4.3986 | 4.3986 | 4.3986 | 4.3986
2021-02-24 16:00 | 2.0187 | 2.4566 | 2.4036 | 2.5853 | 2.449 | 2.6307 | 1.3889 | 2.3818 | 2.939 | 2.939 | 3.3105 | 3.3105 | 2019-04-24 04:00 | 1.608 | 2.7594 | 4.6638 | 4.6638 | 4.6638 | 4.6638
2021-02-24 17:00 | 2.1348 | 2.5979 | 2.5418 | 2.734 | 2.5899 | 2.782 | 1.4347 | 2.4602 | 3.0357 | 3.0357 | 3.4194 | 3.4194 | 2019-04-24 05:00 | 1.6614 | 2.8509 | 4.8186 | 4.8186 | 4.8186 | 4.8186
2021-02-24 18:00 | 2.2006 | 2.6779 | 2.6201 | 2.8181 | 2.6696 | 2.8677 | 1.4653 | 2.5128 | 3.1006 | 3.1006 | 3.4925 | 3.4925 | 2019-04-24 06:00 | 1.7986 | 3.0863 | 5.2164 | 5.2164 | 5.2164 | 5.2164
2021-02-24 19:00 | 2.2177 | 2.6987 | 2.6405 | 2.8401 | 2.6904 | 2.89 | 1.4918 | 2.5582 | 3.1567 | 3.1567 | 3.5557 | 3.5557 | 2019-04-24 07:00 | 1.8748 | 3.2171 | 5.4375 | 5.4375 | 5.4375 | 5.4375
2021-02-24 20:00 | 2.0548 | 2.5005 | 2.4466 | 2.6315 | 2.4928 | 2.6777 | 1.5232 | 2.6121 | 3.2232 | 3.2232 | 3.6306 | 3.6306 | 2019-04-24 08:00 | 2.111 | 3.6225 | 6.1227 | 6.1227 | 6.1227 | 6.1227
2021-02-24 21:00 | 1.8891 | 2.2988 | 2.2492 | 2.4192 | 2.2917 | 2.4617 | 1.4146 | 2.4259 | 2.9934 | 2.9934 | 3.3718 | 3.3718 | 2019-04-24 09:00 | 2.1796 | 3.7402 | 6.3216 | 6.3216 | 6.3216 | 6.3216
2021-02-24 22:00 | 1.6747 | 2.038 | 1.994 | 2.1447 | 2.0317 | 2.1824 | 1.2611 | 2.1626 | 2.6685 | 2.6685 | 3.0057 | 3.0057 | 2019-04-24 10:00 | 2.2253 | 3.8187 | 6.4542 | 6.4542 | 6.4542 | 6.4542
2021-02-24 23:00 | 1.4499 | 1.7643 | 1.7263 | 1.8568 | 1.7589 | 1.8894 | 1.0688 | 1.8329 | 2.2617 | 2.2617 | 2.5475 | 2.5475 | 2019-04-24 11:00 | 2.3015 | 3.9495 | 6.6753 | 6.6753 | 6.6753 | 6.6753
2021-02-25 | 1.4061 | 1.711 | 1.6741 | 1.8007 | 1.7058 | 1.8323 | 0.87451 | 1.4996 | 1.8505 | 1.8505 | 2.0844 | 2.0844 | 2019-04-24 12:00 | 2.4006 | 4.1195 | 6.9626 | 6.9626 | 6.9626 | 6.9626
2021-02-25 01:00 | 1.2803 | 1.558 | 1.5244 | 1.6396 | 1.5532 | 1.6685 | 0.82592 | 1.4163 | 1.7477 | 1.7477 | 1.9686 | 1.9686 | 2019-04-24 13:00 | 2.6597 | 4.5641 | 7.7141 | 7.7141 | 7.7141 | 7.7141
2021-02-25 02:00 | 1.2317 | 1.4989 | 1.4666 | 1.5774 | 1.4943 | 1.6051 | 0.79449 | 1.3624 | 1.6811 | 1.6811 | 1.8936 | 1.8936 | 2019-04-24 14:00 | 2.5835 | 4.4333 | 7.4931 | 7.4931 | 7.4931 | 7.4931
2021-02-25 03:00 | 1.2272 | 1.4934 | 1.4611 | 1.5716 | 1.4888 | 1.5992 | 0.77448 | 1.3281 | 1.6388 | 1.6388 | 1.8459 | 1.8459 | 2019-04-24 15:00 | 2.3397 | 4.0149 | 6.7858 | 6.7858 | 6.7858 | 6.7858
2021-02-25 04:00 | 1.1746 | 1.4294 | 1.3985 | 1.5042 | 1.4249 | 1.5307 | 0.74019 | 1.2693 | 1.5662 | 1.5662 | 1.7642 | 1.7642 | 2019-04-24 16:00 | 2.3092 | 3.9625 | 6.6974 | 6.6974 | 6.6974 | 6.6974
2021-02-25 05:00 | 1.4204 | 1.7284 | 1.6912 | 1.819 | 1.7231 | 1.8509 | 0.79449 | 1.3624 | 1.6811 | 1.6811 | 1.8936 | 1.8936 | 2019-04-24 17:00 | 2.111 | 3.6225 | 6.1227 | 6.1227 | 6.1227 | 6.1227
2021-02-25 06:00 | 1.858 | 2.261 | 2.2123 | 2.3795 | 2.2541 | 2.4213 | 1.1089 | 1.9015 | 2.3464 | 2.3464 | 2.6429 | 2.6429 | 2019-04-24 18:00 | 2.0729 | 3.5571 | 6.0121 | 6.0121 | 6.0121 | 6.0121
2021-02-25 07:00 | 2.3263 | 2.8309 | 2.7698 | 2.9792 | 2.8222 | 3.0315 | 1.2117 | 2.0779 | 2.5641 | 2.5641 | 2.8881 | 2.8881 | 2019-04-24 19:00 | 1.89 | 3.2433 | 5.4817 | 5.4817 | 5.4817 | 5.4817
2021-02-25 08:00 | 2.4092 | 2.9317 | 2.8685 | 3.0853 | 2.9227 | 3.1395 | 1.2289 | 2.1073 | 2.6003 | 2.6003 | 2.929 | 2.929 | 2019-04-24 20:00 | 1.8824 | 3.2302 | 5.4596 | 5.4596 | 5.4596 | 5.4596
2021-02-25 09:00 | 2.4092 | 2.9317 | 2.8685 | 3.0853 | 2.9227 | 3.1395 | 1.2803 | 2.1956 | 2.7092 | 2.7092 | 3.0516 | 3.0516 | 2019-04-24 21:00 | 1.7452 | 2.9948 | 5.0617 | 5.0617 | 5.0617 | 5.0617
2021-02-25 10:00 | 2.4121 | 2.9352 | 2.8719 | 3.089 | 2.9262 | 3.1433 | 1.3861 | 2.3769 | 2.9329 | 2.9329 | 3.3036 | 3.3036 | 2019-04-24 22:00 | 1.6538 | 2.8379 | 4.7965 | 4.7965 | 4.7965 | 4.7965
2021-02-25 11:00 | 2.2834 | 2.7787 | 2.7188 | 2.9243 | 2.7702 | 2.9757 | 1.3861 | 2.3769 | 2.9329 | 2.9329 | 3.3036 | 3.3036 | 2019-04-24 23:00 | 1.5699 | 2.694 | 4.5533 | 4.5533 | 4.5533 | 4.5533
2021-02-25 12:00 | 2.2006 | 2.6779 | 2.6201 | 2.8181 | 2.6696 | 2.8677 | 1.4661 | 2.5141 | 3.1023 | 3.1023 | 3.4944 | 3.4944 | 2019-04-25 | 1.4861 | 2.5501 | 4.3102 | 4.3102 | 4.3102 | 4.3102
2021-02-25 13:00 | 2.2063 | 2.6848 | 2.6269 | 2.8255 | 2.6765 | 2.8751 | 1.3975 | 2.3965 | 2.9571 | 2.9571 | 3.3309 | 3.3309 | 2019-04-25 01:00 | 1.4709 | 2.524 | 4.266 | 4.266 | 4.266 | 4.266
2021-02-25 14:00 | 2.2263 | 2.7092 | 2.6507 | 2.8511 | 2.7008 | 2.9012 | 1.3918 | 2.3867 | 2.945 | 2.945 | 3.3173 | 3.3173 | 2019-04-25 02:00 | 1.4556 | 2.4978 | 4.2218 | 4.2218 | 4.2218 | 4.2218
2021-02-25 15:00 | 2.2606 | 2.7509 | 2.6916 | 2.895 | 2.7424 | 2.9459 | 1.3689 | 2.3475 | 2.8967 | 2.8967 | 3.2628 | 3.2628 | 2019-04-25 03:00 | 1.5166 | 2.6025 | 4.3986 | 4.3986 | 4.3986 | 4.3986
2021-02-25 16:00 | 2.1806 | 2.6535 | 2.5963 | 2.7925 | 2.6453 | 2.8416 | 1.3546 | 2.323 | 2.8664 | 2.8664 | 3.2287 | 3.2287 | 2019-04-25 04:00 | 1.5242 | 2.6155 | 4.4207 | 4.4207 | 4.4207 | 4.4207
2021-02-25 17:00 | 2.2149 | 2.6953 | 2.6371 | 2.8364 | 2.6869 | 2.8863 | 1.4804 | 2.5386 | 3.1325 | 3.1325 | 3.5284 | 3.5284 | 2019-04-25 05:00 | 1.6233 | 2.7855 | 4.708 | 4.708 | 4.708 | 4.708
2021-02-25 18:00 | 2.4149 | 2.9387 | 2.8753 | 3.0926 | 2.9296 | 3.147 | 1.609 | 2.7592 | 3.4046 | 3.4046 | 3.8349 | 3.8349 | 2019-04-25 06:00 | 1.6919 | 2.9032 | 4.907 | 4.907 | 4.907 | 4.907
2021-02-25 19:00 | 2.2949 | 2.7926 | 2.7324 | 2.9389 | 2.784 | 2.9906 | 1.5518 | 2.6611 | 3.2837 | 3.2837 | 3.6987 | 3.6987 | 2019-04-25 07:00 | 1.6233 | 2.7855 | 4.708 | 4.708 | 4.708 | 4.708
2021-02-25 20:00 | 2.1434 | 2.6083 | 2.552 | 2.7449 | 2.6003 | 2.7932 | 1.5175 | 2.6023 | 3.2111 | 3.2111 | 3.617 | 3.617 | 2019-04-25 08:00 | 1.7986 | 3.0863 | 5.2164 | 5.2164 | 5.2164 | 5.2164
2021-02-25 21:00 | 1.9948 | 2.4275 | 2.3751 | 2.5547 | 2.42 | 2.5995 | 1.4489 | 2.4847 | 3.066 | 3.066 | 3.4535 | 3.4535 | 2019-04-25 09:00 | 1.8595 | 3.191 | 5.3932 | 5.3932 | 5.3932 | 5.3932
2021-02-25 22:00 | 1.7605 | 2.1423 | 2.0961 | 2.2545 | 2.1357 | 2.2941 | 1.3264 | 2.2745 | 2.8066 | 2.8066 | 3.1614 | 3.1614 | 2019-04-25 10:00 | 2.0729 | 3.5571 | 6.0121 | 6.0121 | 6.0121 | 6.0121
2021-02-25 23:00 | 1.489 | 1.8119 | 1.7728 | 1.9068 | 1.8063 | 1.9403 | 1.1317 | 1.9407 | 2.3947 | 2.3947 | 2.6974 | 2.6974 | 2019-04-25 11:00 | 2.0958 | 3.5964 | 6.0785 | 6.0785 | 6.0785 | 6.0785
2021-02-26 | 1.4266 | 1.736 | 1.6986 | 1.827 | 1.7307 | 1.8591 | 0.91501 | 1.5691 | 1.9362 | 1.9362 | 2.1809 | 2.1809 | 2019-04-25 12:00 | 2.1567 | 3.701 | 6.2553 | 6.2553 | 6.2553 | 6.2553
2021-02-26 01:00 | 1.2746 | 1.5511 | 1.5176 | 1.6323 | 1.5463 | 1.661 | 0.84593 | 1.4506 | 1.79 | 1.79 | 2.0162 | 2.0162 | 2019-04-25 13:00 | 2.1644 | 3.7141 | 6.2774 | 6.2774 | 6.2774 | 6.2774
2021-02-26 02:00 | 1.1935 | 1.4524 | 1.4211 | 1.5285 | 1.4479 | 1.5554 | 0.77448 | 1.3281 | 1.6388 | 1.6388 | 1.8459 | 1.8459 | 2019-04-25 14:00 | 2.0958 | 3.5964 | 6.0785 | 6.0785 | 6.0785 | 6.0785
2021-02-26 03:00 | 1.2203 | 1.485 | 1.453 | 1.5628 | 1.4804 | 1.5902 | 0.74305 | 1.2742 | 1.5723 | 1.5723 | 1.771 | 1.771 | 2019-04-25 15:00 | 2.1186 | 3.6356 | 6.1448 | 6.1448 | 6.1448 | 6.1448
2021-02-26 04:00 | 1.2258 | 1.4917 | 1.4595 | 1.5698 | 1.4871 | 1.5974 | 0.75162 | 1.2889 | 1.5904 | 1.5904 | 1.7915 | 1.7915 | 2019-04-25 16:00 | 2.0805 | 3.5702 | 6.0343 | 6.0343 | 6.0343 | 6.0343
2021-02-26 05:00 | 1.4837 | 1.8055 | 1.7665 | 1.9001 | 1.7999 | 1.9335 | 0.80878 | 1.3869 | 1.7114 | 1.7114 | 1.9277 | 1.9277 | 2019-04-25 17:00 | 1.9738 | 3.3871 | 5.7248 | 5.7248 | 5.7248 | 5.7248
2021-02-26 06:00 | 1.6261 | 1.9788 | 1.9361 | 2.0825 | 1.9727 | 2.1191 | 1.086 | 1.8623 | 2.298 | 2.298 | 2.5884 | 2.5884 | 2019-04-25 18:00 | 1.8519 | 3.1779 | 5.3711 | 5.3711 | 5.3711 | 5.3711
2021-02-26 07:00 | 1.8576 | 2.2605 | 2.2118 | 2.379 | 2.2536 | 2.4208 | 1.2117 | 2.0779 | 2.5641 | 2.5641 | 2.8881 | 2.8881 | 2019-04-25 19:00 | 1.6995 | 2.9163 | 4.9291 | 4.9291 | 4.9291 | 4.9291
2021-02-26 08:00 | 2.092 | 2.5457 | 2.4908 | 2.6791 | 2.5379 | 2.7261 | 1.2289 | 2.1073 | 2.6003 | 2.6003 | 2.929 | 2.929 | 2019-04-25 20:00 | 1.6842 | 2.8902 | 4.8849 | 4.8849 | 4.8849 | 4.8849
2021-02-26 09:00 | 2.0548 | 2.5005 | 2.4466 | 2.6315 | 2.4928 | 2.6777 | 1.2803 | 2.1956 | 2.7092 | 2.7092 | 3.0516 | 3.0516 | 2019-04-25 21:00 | 1.5928 | 2.7332 | 4.6196 | 4.6196 | 4.6196 | 4.6196
2021-02-26 10:00 | 2.0948 | 2.5492 | 2.4942 | 2.6827 | 2.5413 | 2.7299 | 1.3861 | 2.3769 | 2.9329 | 2.9329 | 3.3036 | 3.3036 | 2019-04-25 22:00 | 1.6004 | 2.7463 | 4.6417 | 4.6417 | 4.6417 | 4.6417
2021-02-26 11:00 | 2.1005 | 2.5561 | 2.501 | 2.69 | 2.5483 | 2.7373 | 1.3861 | 2.3769 | 2.9329 | 2.9329 | 3.3036 | 3.3036 | 2019-04-25 23:00 | 1.4861 | 2.5501 | 4.3102 | 4.3102 | 4.3102 | 4.3102
2021-02-26 12:00 | 2.0964 | 2.5511 | 2.4961 | 2.6847 | 2.5432 | 2.7319 | 1.3346 | 2.2887 | 2.8241 | 2.8241 | 3.181 | 3.181 | 2019-04-26 | 1.4785 | 2.5371 | 4.2881 | 4.2881 | 4.2881 | 4.2881
2021-02-26 13:00 | 2.1348 | 2.5979 | 2.5418 | 2.734 | 2.5899 | 2.782 | 1.3632 | 2.3377 | 2.8846 | 2.8846 | 3.2491 | 3.2491 | 2019-04-26 01:00 | 1.4556 | 2.4978 | 4.2218 | 4.2218 | 4.2218 | 4.2218
2021-02-26 14:00 | 2.0005 | 2.4344 | 2.3819 | 2.562 | 2.4269 | 2.607 | 1.3318 | 2.2838 | 2.818 | 2.818 | 3.1742 | 3.1742 | 2019-04-26 02:00 | 1.3946 | 2.3932 | 4.0449 | 4.0449 | 4.0449 | 4.0449
2021-02-26 15:00 | 2.0691 | 2.5179 | 2.4636 | 2.6498 | 2.5101 | 2.6963 | 1.2687 | 2.1756 | 2.6845 | 2.6845 | 3.0238 | 3.0238 | 2019-04-26 03:00 | 1.4327 | 2.4586 | 4.1555 | 4.1555 | 4.1555 | 4.1555
2021-02-26 16:00 | 1.9805 | 2.4101 | 2.3581 | 2.5363 | 2.4026 | 2.5809 | 1.4175 | 2.4308 | 2.9995 | 2.9995 | 3.3786 | 3.3786 | 2019-04-26 04:00 | 1.4099 | 2.4194 | 4.0891 | 4.0891 | 4.0891 | 4.0891
2021-02-26 17:00 | 2.0777 | 2.5283 | 2.4738 | 2.6608 | 2.5205 | 2.7075 | 1.5318 | 2.6268 | 3.2414 | 3.2414 | 3.651 | 3.651 | 2019-04-26 05:00 | 1.5852 | 2.7202 | 4.5975 | 4.5975 | 4.5975 | 4.5975
2021-02-26 18:00 | 2.2777 | 2.7718 | 2.712 | 2.917 | 2.7632 | 2.9682 | 1.6661 | 2.8572 | 3.5256 | 3.5256 | 3.9712 | 3.9712 | 2019-04-26 06:00 | 1.7071 | 2.9294 | 4.9512 | 4.9512 | 4.9512 | 4.9512
2021-02-26 19:00 | 2.1909 | 2.6661 | 2.6086 | 2.8058 | 2.6579 | 2.8551 | 1.6376 | 2.8082 | 3.4651 | 3.4651 | 3.9031 | 3.9031 | 2019-04-26 07:00 | 1.7223 | 2.9556 | 4.9954 | 4.9954 | 4.9954 | 4.9954
2021-02-26 20:00 | 1.8919 | 2.3023 | 2.2526 | 2.4229 | 2.2952 | 2.4654 | 1.6376 | 2.8082 | 3.4651 | 3.4651 | 3.9031 | 3.9031 | 2019-04-26 08:00 | 1.9281 | 3.3087 | 5.5922 | 5.5922 | 5.5922 | 5.5922
2021-02-26 21:00 | 1.8635 | 2.2677 | 2.2187 | 2.3864 | 2.2607 | 2.4284 | 1.5732 | 2.6979 | 3.329 | 3.329 | 3.7498 | 3.7498 | 2019-04-26 09:00 | 1.9662 | 3.374 | 5.7027 | 5.7027 | 5.7027 | 5.7027
2021-02-26 22:00 | 1.5404 | 1.8745 | 1.8341 | 1.9727 | 1.8687 | 2.0074 | 1.3289 | 2.2789 | 2.812 | 2.812 | 3.1674 | 3.1674 | 2019-04-26 10:00 | 2.0119 | 3.4525 | 5.8353 | 5.8353 | 5.8353 | 5.8353
2021-02-26 23:00 | 1.5147 | 1.8432 | 1.8034 | 1.9398 | 1.8375 | 1.9738 | 1.2289 | 2.1073 | 2.6003 | 2.6003 | 2.929 | 2.929 | 2019-04-26 11:00 | 2.1491 | 3.6879 | 6.2332 | 6.2332 | 6.2332 | 6.2332
2021-02-27 | 1.4004 | 1.7041 | 1.6673 | 1.7934 | 1.6988 | 1.8249 | 1.006 | 1.7251 | 2.1286 | 2.1286 | 2.3977 | 2.3977 | 2019-04-26 12:00 | 2.1186 | 3.6356 | 6.1448 | 6.1448 | 6.1448 | 6.1448
2021-02-27 01:00 | 1.286 | 1.565 | 1.5312 | 1.647 | 1.5602 | 1.6759 | 0.87456 | 1.4997 | 1.8506 | 1.8506 | 2.0845 | 2.0845 | 2019-04-26 13:00 | 2.0119 | 3.4525 | 5.8353 | 5.8353 | 5.8353 | 5.8353
2021-02-27 02:00 | 1.2375 | 1.5059 | 1.4734 | 1.5847 | 1.5012 | 1.6126 | 0.7917 | 1.3576 | 1.6752 | 1.6752 | 1.887 | 1.887 | 2019-04-26 14:00 | 2.0348 | 3.4917 | 5.9016 | 5.9016 | 5.9016 | 5.9016
2021-02-27 03:00 | 1.2031 | 1.4641 | 1.4325 | 1.5408 | 1.4596 | 1.5679 | 0.74876 | 1.284 | 1.5844 | 1.5844 | 1.7846 | 1.7846 | 2019-04-26 15:00 | 2.0424 | 3.5048 | 5.9237 | 5.9237 | 5.9237 | 5.9237
2021-02-27 04:00 | 1.2032 | 1.4641 | 1.4325 | 1.5408 | 1.4596 | 1.5679 | 0.75448 | 1.2938 | 1.5965 | 1.5965 | 1.7983 | 1.7983 | 2019-04-26 16:00 | 2.1644 | 3.7141 | 6.2774 | 6.2774 | 6.2774 | 6.2774
2021-02-27 05:00 | 1.2603 | 1.5337 | 1.5006 | 1.614 | 1.529 | 1.6424 | 0.7802 | 1.3379 | 1.6509 | 1.6509 | 1.8596 | 1.8596 | 2019-04-26 17:00 | 2.0043 | 3.4394 | 5.8132 | 5.8132 | 5.8132 | 5.8132
2021-02-27 06:00 | 1.3975 | 1.7006 | 1.6639 | 1.7897 | 1.6954 | 1.8211 | 0.84307 | 1.4457 | 1.7839 | 1.7839 | 2.0094 | 2.0094 | 2019-04-26 18:00 | 1.8443 | 3.1648 | 5.349 | 5.349 | 5.349 | 5.349
2021-02-27 07:00 | 1.4432 | 1.7563 | 1.7184 | 1.8483 | 1.7508 | 1.8807 | 1.0288 | 1.7643 | 2.177 | 2.177 | 2.4522 | 2.4522 | 2019-04-26 19:00 | 1.8062 | 3.0994 | 5.2385 | 5.2385 | 5.2385 | 5.2385
2021-02-27 08:00 | 1.5575 | 1.8954 | 1.8545 | 1.9947 | 1.8895 | 2.0297 | 1.2203 | 2.0926 | 2.5822 | 2.5822 | 2.9086 | 2.9086 | 2019-04-26 20:00 | 1.6995 | 2.9163 | 4.9291 | 4.9291 | 4.9291 | 4.9291
2021-02-27 09:00 | 1.6204 | 1.9719 | 1.9293 | 2.0752 | 1.9658 | 2.1116 | 1.4289 | 2.4504 | 3.0236 | 3.0236 | 3.4058 | 3.4058 | 2019-04-26 21:00 | 1.6233 | 2.7855 | 4.708 | 4.708 | 4.708 | 4.708
2021-02-27 10:00 | 1.6519 | 2.0101 | 1.9668 | 2.1154 | 2.0039 | 2.1526 | 1.5118 | 2.5925 | 3.199 | 3.199 | 3.6034 | 3.6034 | 2019-04-26 22:00 | 1.5699 | 2.694 | 4.5533 | 4.5533 | 4.5533 | 4.5533
2021-02-27 11:00 | 1.6118 | 1.9614 | 1.9191 | 2.0642 | 1.9554 | 2.1005 | 1.5147 | 2.5974 | 3.2051 | 3.2051 | 3.6102 | 3.6102 | 2019-04-26 23:00 | 1.4632 | 2.5109 | 4.2439 | 4.2439 | 4.2439 | 4.2439
2021-02-27 12:00 | 1.5261 | 1.8571 | 1.8171 | 1.9544 | 1.8514 | 1.9887 | 1.4689 | 2.519 | 3.1083 | 3.1083 | 3.5012 | 3.5012 | 2019-04-27 | 1.4251 | 2.4455 | 4.1333 | 4.1333 | 4.1333 | 4.1333
2021-02-27 13:00 | 1.3784 | 1.6773 | 1.6412 | 1.7652 | 1.6722 | 1.7962 | 1.549 | 2.6562 | 3.2776 | 3.2776 | 3.6919 | 3.6919 | 2019-04-27 01:00 | 1.4023 | 2.4063 | 4.067 | 4.067 | 4.067 | 4.067
2021-02-27 14:00 | 1.6347 | 1.9893 | 1.9464 | 2.0935 | 1.9831 | 2.1303 | 1.5775 | 2.7052 | 3.3381 | 3.3381 | 3.76 | 3.76 | 2019-04-27 02:00 | 1.4175 | 2.4324 | 4.1112 | 4.1112 | 4.1112 | 4.1112
2021-02-27 15:00 | 1.4004 | 1.7041 | 1.6673 | 1.7934 | 1.6988 | 1.8249 | 1.5232 | 2.6121 | 3.2232 | 3.2232 | 3.6306 | 3.6306 | 2019-04-27 03:00 | 1.4175 | 2.4324 | 4.1112 | 4.1112 | 4.1112 | 4.1112
2021-02-27 16:00 | 1.4146 | 1.7215 | 1.6843 | 1.8117 | 1.7162 | 1.8435 | 1.5833 | 2.715 | 3.3502 | 3.3502 | 3.7736 | 3.7736 | 2019-04-27 04:00 | 1.4175 | 2.4324 | 4.1112 | 4.1112 | 4.1112 | 4.1112
2021-02-27 17:00 | 1.6061 | 1.9545 | 1.9123 | 2.0569 | 1.9485 | 2.093 | 1.6461 | 2.8229 | 3.4832 | 3.4832 | 3.9235 | 3.9235 | 2019-04-27 05:00 | 1.3718 | 2.354 | 3.9786 | 3.9786 | 3.9786 | 3.9786
2021-02-27 18:00 | 1.6433 | 1.9997 | 1.9566 | 2.1045 | 1.9935 | 2.1414 | 1.6318 | 2.7984 | 3.453 | 3.453 | 3.8894 | 3.8894 | 2019-04-27 06:00 | 1.4861 | 2.5501 | 4.3102 | 4.3102 | 4.3102 | 4.3102
2021-02-27 19:00 | 1.6318 | 1.9858 | 1.943 | 2.0898 | 1.9797 | 2.1265 | 1.5661 | 2.6856 | 3.3139 | 3.3139 | 3.7328 | 3.7328 | 2019-04-27 07:00 | 1.6766 | 2.8771 | 4.8628 | 4.8628 | 4.8628 | 4.8628
2021-02-27 20:00 | 1.6519 | 2.0101 | 1.9668 | 2.1154 | 2.0039 | 2.1526 | 1.4604 | 2.5043 | 3.0902 | 3.0902 | 3.4807 | 3.4807 | 2019-04-27 08:00 | 1.7605 | 3.0209 | 5.1059 | 5.1059 | 5.1059 | 5.1059
2021-02-27 21:00 | 1.5718 | 1.9128 | 1.8715 | 2.013 | 1.9069 | 2.0483 | 1.4461 | 2.4798 | 3.0599 | 3.0599 | 3.4467 | 3.4467 | 2019-04-27 09:00 | 1.8519 | 3.1779 | 5.3711 | 5.3711 | 5.3711 | 5.3711
2021-02-27 22:00 | 1.5461 | 1.8815 | 1.8409 | 1.98 | 1.8757 | 2.0148 | 1.3489 | 2.3132 | 2.8543 | 2.8543 | 3.2151 | 3.2151 | 2019-04-27 10:00 | 1.8214 | 3.1256 | 5.2827 | 5.2827 | 5.2827 | 5.2827
2021-02-27 23:00 | 1.4661 | 1.7841 | 1.7456 | 1.8775 | 1.7786 | 1.9105 | 1.206 | 2.0681 | 2.552 | 2.552 | 2.8745 | 2.8745 | 2019-04-27 11:00 | 1.951 | 3.3479 | 5.6585 | 5.6585 | 5.6585 | 5.6585
2021-02-28 | 1.3946 | 1.6971 | 1.6605 | 1.786 | 1.6919 | 1.8174 | 0.98903 | 1.696 | 2.0928 | 2.0928 | 2.3573 | 2.3573 | 2019-04-27 12:00 | 1.9053 | 3.2694 | 5.5259 | 5.5259 | 5.5259 | 5.5259
2021-02-28 01:00 | 1.2718 | 1.5476 | 1.5142 | 1.6287 | 1.5428 | 1.6573 | 0.89451 | 1.5339 | 1.8928 | 1.8928 | 2.132 | 2.132 | 2019-04-27 13:00 | 1.8748 | 3.2171 | 5.4375 | 5.4375 | 5.4375 | 5.4375
2021-02-28 02:00 | 1.2146 | 1.478 | 1.4462 | 1.5555 | 1.4735 | 1.5828 | 0.78895 | 1.3529 | 1.6694 | 1.6694 | 1.8804 | 1.8804 | 2019-04-27 14:00 | 1.9357 | 3.3217 | 5.6143 | 5.6143 | 5.6143 | 5.6143
2021-02-28 03:00 | 1.2146 | 1.478 | 1.4462 | 1.5555 | 1.4735 | 1.5828 | 0.75448 | 1.2938 | 1.5965 | 1.5965 | 1.7983 | 1.7983 | 2019-04-27 15:00 | 1.9205 | 3.2956 | 5.5701 | 5.5701 | 5.5701 | 5.5701
2021-02-28 04:00 | 1.206 | 1.4676 | 1.4359 | 1.5445 | 1.4631 | 1.5716 | 0.72876 | 1.2497 | 1.5421 | 1.5421 | 1.737 | 1.737 | 2019-04-27 16:00 | 1.951 | 3.3479 | 5.6585 | 5.6585 | 5.6585 | 5.6585
2021-02-28 05:00 | 1.2317 | 1.4989 | 1.4666 | 1.5774 | 1.4943 | 1.6051 | 0.73438 | 1.2593 | 1.5539 | 1.5539 | 1.7504 | 1.7504 | 2019-04-27 17:00 | 1.951 | 3.3479 | 5.6585 | 5.6585 | 5.6585 | 5.6585
2021-02-28 06:00 | 1.2803 | 1.558 | 1.5244 | 1.6396 | 1.5532 | 1.6685 | 0.76591 | 1.3134 | 1.6207 | 1.6207 | 1.8255 | 1.8255 | 2019-04-27 18:00 | 1.8062 | 3.0994 | 5.2385 | 5.2385 | 5.2385 | 5.2385
2021-02-28 07:00 | 1.3918 | 1.6937 | 1.6571 | 1.7824 | 1.6884 | 1.8137 | 0.92881 | 1.5928 | 1.9654 | 1.9654 | 2.2138 | 2.2138 | 2019-04-27 19:00 | 1.6842 | 2.8902 | 4.8849 | 4.8849 | 4.8849 | 4.8849
2021-02-28 08:00 | 1.4032 | 1.7076 | 1.6707 | 1.797 | 1.7023 | 1.8286 | 1.1603 | 1.9897 | 2.4552 | 2.4552 | 2.7655 | 2.7655 | 2019-04-27 20:00 | 1.6842 | 2.8902 | 4.8849 | 4.8849 | 4.8849 | 4.8849
2021-02-28 09:00 | 1.4861 | 1.8084 | 1.7694 | 1.9032 | 1.8029 | 1.9366 | 1.2403 | 2.1269 | 2.6245 | 2.6245 | 2.9562 | 2.9562 | 2019-04-27 21:00 | 1.5775 | 2.7071 | 4.5754 | 4.5754 | 4.5754 | 4.5754
2021-02-28 10:00 | 1.3632 | 1.6589 | 1.6231 | 1.7458 | 1.6538 | 1.7765 | 1.4347 | 2.4602 | 3.0357 | 3.0357 | 3.4194 | 3.4194 | 2019-04-27 22:00 | 1.4327 | 2.4586 | 4.1555 | 4.1555 | 4.1555 | 4.1555
2021-02-28 11:00 | 1.3261 | 1.6137 | 1.5789 | 1.6982 | 1.6087 | 1.728 | 1.4747 | 2.5288 | 3.1204 | 3.1204 | 3.5148 | 3.5148 | 2019-04-27 23:00 | 1.4023 | 2.4063 | 4.067 | 4.067 | 4.067 | 4.067
2021-02-28 12:00 | 1.3603 | 1.6554 | 1.6197 | 1.7421 | 1.6503 | 1.7727 | 1.5118 | 2.5925 | 3.199 | 3.199 | 3.6034 | 3.6034 | 2019-04-28 | 1.3413 | 2.3017 | 3.8902 | 3.8902 | 3.8902 | 3.8902
2021-02-28 13:00 | 1.3546 | 1.6484 | 1.6129 | 1.7348 | 1.6434 | 1.7653 | 1.5232 | 2.6121 | 3.2232 | 3.2232 | 3.6306 | 3.6306 | 2019-04-28 01:00 | 1.3108 | 2.2494 | 3.8018 | 3.8018 | 3.8018 | 3.8018
2021-02-28 14:00 | 1.3289 | 1.6171 | 1.5823 | 1.7019 | 1.6122 | 1.7318 | 1.529 | 2.6219 | 3.2353 | 3.2353 | 3.6442 | 3.6442 | 2019-04-28 02:00 | 1.2879 | 2.2101 | 3.7355 | 3.7355 | 3.7355 | 3.7355
2021-02-28 15:00 | 1.363 | 1.6586 | 1.6229 | 1.7455 | 1.6535 | 1.7762 | 1.5604 | 2.6758 | 3.3018 | 3.3018 | 3.7192 | 3.7192 | 2019-04-28 03:00 | 1.2879 | 2.2101 | 3.7355 | 3.7355 | 3.7355 | 3.7355
2021-02-28 16:00 | 1.4347 | 1.7458 | 1.7082 | 1.8373 | 1.7404 | 1.8696 | 1.5461 | 2.6513 | 3.2716 | 3.2716 | 3.6851 | 3.6851 | 2019-04-28 04:00 | 1.3946 | 2.3932 | 4.0449 | 4.0449 | 4.0449 | 4.0449
2021-02-28 17:00 | 1.7119 | 2.0832 | 2.0382 | 2.1923 | 2.0767 | 2.2308 | 1.5433 | 2.6464 | 3.2655 | 3.2655 | 3.6783 | 3.6783 | 2019-04-28 05:00 | 1.4404 | 2.4717 | 4.1776 | 4.1776 | 4.1776 | 4.1776
2021-02-28 18:00 | 1.8319 | 2.2292 | 2.1811 | 2.346 | 2.2224 | 2.3872 | 1.649 | 2.8278 | 3.4893 | 3.4893 | 3.9303 | 3.9303 | 2019-04-28 06:00 | 1.4632 | 2.5109 | 4.2439 | 4.2439 | 4.2439 | 4.2439
2021-02-28 19:00 | 1.8233 | 2.2188 | 2.1709 | 2.335 | 2.212 | 2.3761 | 1.6376 | 2.8082 | 3.4651 | 3.4651 | 3.9031 | 3.9031 | 2019-04-28 07:00 | 1.6614 | 2.8509 | 4.8186 | 4.8186 | 4.8186 | 4.8186
2021-02-28 20:00 | 1.7833 | 2.1701 | 2.1233 | 2.2838 | 2.1634 | 2.3239 | 1.6004 | 2.7445 | 3.3865 | 3.3865 | 3.8145 | 3.8145 | 2019-04-28 08:00 | 1.7833 | 3.0602 | 5.1722 | 5.1722 | 5.1722 | 5.1722
2021-02-28 21:00 | 1.7262 | 2.1006 | 2.0552 | 2.2106 | 2.0941 | 2.2494 | 1.4918 | 2.5582 | 3.1567 | 3.1567 | 3.5557 | 3.5557 | 2019-04-28 09:00 | 1.8443 | 3.1648 | 5.349 | 5.349 | 5.349 | 5.349
2021-02-28 22:00 | 1.5835 | 1.9269 | 1.8853 | 2.0279 | 1.921 | 2.0635 | 1.2889 | 2.2103 | 2.7273 | 2.7273 | 3.072 | 3.072 | 2019-04-28 10:00 | 1.8367 | 3.1517 | 5.3269 | 5.3269 | 5.3269 | 5.3269
2021-02-28 23:00 | 1.4947 | 1.8189 | 1.7796 | 1.9141 | 1.8133 | 1.9478 | 1.0948 | 1.8775 | 2.3167 | 2.3167 | 2.6095 | 2.6095 | 2019-04-28 11:00 | 1.9053 | 3.2694 | 5.5259 | 5.5259 | 5.5259 | 5.5259
2021-03-01 | 1.4432 | 1.7563 | 1.7184 | 1.8483 | 1.7508 | 1.8807 | 0.99168 | 1.7006 | 2.0984 | 2.0984 | 2.3636 | 2.3636 | 2019-04-28 12:00 | 1.9662 | 3.374 | 5.7027 | 5.7027 | 5.7027 | 5.7027
2021-03-01 01:00 | 1.2718 | 1.5476 | 1.5142 | 1.6287 | 1.5428 | 1.6573 | 0.83736 | 1.4359 | 1.7719 | 1.7719 | 1.9958 | 1.9958 | 2019-04-28 13:00 | 1.8671 | 3.204 | 5.4154 | 5.4154 | 5.4154 | 5.4154
2021-03-01 02:00 | 1.2403 | 1.5093 | 1.4768 | 1.5884 | 1.5047 | 1.6163 | 0.78306 | 1.3428 | 1.657 | 1.657 | 1.8664 | 1.8664 | 2019-04-28 14:00 | 1.8824 | 3.2302 | 5.4596 | 5.4596 | 5.4596 | 5.4596
2021-03-01 03:00 | 1.2068 | 1.4686 | 1.4369 | 1.5455 | 1.4641 | 1.5727 | 0.74688 | 1.2808 | 1.5804 | 1.5804 | 1.7802 | 1.7802 | 2019-04-28 15:00 | 1.9434 | 3.3348 | 5.6364 | 5.6364 | 5.6364 | 5.6364
2021-03-01 04:00 | 1.2656 | 1.5401 | 1.5068 | 1.6207 | 1.5353 | 1.6492 | 0.73733 | 1.2644 | 1.5602 | 1.5602 | 1.7574 | 1.7574 | 2019-04-28 16:00 | 1.9205 | 3.2956 | 5.5701 | 5.5701 | 5.5701 | 5.5701
2021-03-01 05:00 | 1.3489 | 1.6415 | 1.6061 | 1.7275 | 1.6364 | 1.7578 | 0.77427 | 1.3277 | 1.6384 | 1.6384 | 1.8454 | 1.8454 | 2019-04-28 17:00 | 1.9205 | 3.2956 | 5.5701 | 5.5701 | 5.5701 | 5.5701
2021-03-01 06:00 | 1.629 | 1.9823 | 1.9396 | 2.0862 | 1.9762 | 2.1228 | 0.91426 | 1.5678 | 1.9346 | 1.9346 | 2.1791 | 2.1791 | 2019-04-28 18:00 | 1.89 | 3.2433 | 5.4817 | 5.4817 | 5.4817 | 5.4817
2021-03-01 07:00 | 1.8805 | 2.2884 | 2.239 | 2.4082 | 2.2813 | 2.4505 | 1.1974 | 2.0534 | 2.5338 | 2.5338 | 2.8541 | 2.8541 | 2019-04-28 19:00 | 1.8595 | 3.191 | 5.3932 | 5.3932 | 5.3932 | 5.3932
2021-03-01 08:00 | 2.0405 | 2.4831 | 2.4295 | 2.6132 | 2.4755 | 2.6591 | 1.306 | 2.2397 | 2.7636 | 2.7636 | 3.1129 | 3.1129 | 2019-04-28 20:00 | 1.8138 | 3.1125 | 5.2606 | 5.2606 | 5.2606 | 5.2606
2021-03-01 09:00 | 2.0462 | 2.4901 | 2.4364 | 2.6205 | 2.4824 | 2.6666 | 1.3032 | 2.2348 | 2.7576 | 2.7576 | 3.1061 | 3.1061 | 2019-04-28 21:00 | 1.7147 | 2.9425 | 4.9733 | 4.9733 | 4.9733 | 4.9733
2021-03-01 10:00 | 2.3492 | 2.8587 | 2.797 | 3.0085 | 2.8499 | 3.0613 | 1.3851 | 2.3752 | 2.9309 | 2.9309 | 3.3013 | 3.3013 | 2019-04-28 22:00 | 1.4785 | 2.5371 | 4.2881 | 4.2881 | 4.2881 | 4.2881
2021-03-01 11:00 | 2.3549 | 2.8657 | 2.8038 | 3.0158 | 2.8568 | 3.0688 | 1.3889 | 2.3818 | 2.939 | 2.939 | 3.3105 | 3.3105 | 2019-04-28 23:00 | 1.3946 | 2.3932 | 4.0449 | 4.0449 | 4.0449 | 4.0449
2021-03-01 12:00 | 2.2977 | 2.7961 | 2.7358 | 2.9426 | 2.7875 | 2.9943 | 1.3432 | 2.3034 | 2.8422 | 2.8422 | 3.2015 | 3.2015 | 2019-04-29 | 1.3489 | 2.3148 | 3.9123 | 3.9123 | 3.9123 | 3.9123
2021-03-01 13:00 | 2.3492 | 2.8587 | 2.797 | 3.0085 | 2.8499 | 3.0613 | 1.3632 | 2.3377 | 2.8846 | 2.8846 | 3.2491 | 3.2491 | 2019-04-29 01:00 | 1.3337 | 2.2886 | 3.8681 | 3.8681 | 3.8681 | 3.8681
2021-03-01 14:00 | 2.2692 | 2.7613 | 2.7018 | 2.906 | 2.7528 | 2.957 | 1.3804 | 2.3671 | 2.9208 | 2.9208 | 3.29 | 3.29 | 2019-04-29 02:00 | 1.2879 | 2.2101 | 3.7355 | 3.7355 | 3.7355 | 3.7355
2021-03-01 15:00 | 2.4463 | 2.9769 | 2.9127 | 3.1329 | 2.9678 | 3.1879 | 1.3832 | 2.372 | 2.9269 | 2.9269 | 3.2968 | 3.2968 | 2019-04-29 03:00 | 1.3413 | 2.3017 | 3.8902 | 3.8902 | 3.8902 | 3.8902
2021-03-01 16:00 | 2.4178 | 2.9422 | 2.8787 | 3.0963 | 2.9331 | 3.1507 | 1.4061 | 2.4112 | 2.9753 | 2.9753 | 3.3513 | 3.3513 | 2019-04-29 04:00 | 1.3794 | 2.3671 | 4.0007 | 4.0007 | 4.0007 | 4.0007
2021-03-01 17:00 | 2.4949 | 3.0361 | 2.9706 | 3.1951 | 3.0267 | 3.2513 | 1.5747 | 2.7003 | 3.3321 | 3.3321 | 3.7532 | 3.7532 | 2019-04-29 05:00 | 1.5166 | 2.6025 | 4.3986 | 4.3986 | 4.3986 | 4.3986
2021-03-01 18:00 | 2.5864 | 3.1474 | 3.0795 | 3.3122 | 3.1377 | 3.3704 | 1.6547 | 2.8376 | 3.5014 | 3.5014 | 3.9439 | 3.9439 | 2019-04-29 06:00 | 1.7147 | 2.9425 | 4.9733 | 4.9733 | 4.9733 | 4.9733
2021-03-01 19:00 | 2.5006 | 3.043 | 2.9774 | 3.2024 | 3.0336 | 3.2587 | 1.5947 | 2.7346 | 3.3744 | 3.3744 | 3.8009 | 3.8009 | 2019-04-29 07:00 | 1.8519 | 3.1779 | 5.3711 | 5.3711 | 5.3711 | 5.3711
2021-03-01 20:00 | 2.2634 | 2.7544 | 2.695 | 2.8987 | 2.7459 | 2.9496 | 1.5175 | 2.6023 | 3.2111 | 3.2111 | 3.617 | 3.617 | 2019-04-29 08:00 | 1.8976 | 3.2563 | 5.5038 | 5.5038 | 5.5038 | 5.5038
2021-03-01 21:00 | 2.092 | 2.5457 | 2.4908 | 2.6791 | 2.5379 | 2.7261 | 1.4404 | 2.47 | 3.0478 | 3.0478 | 3.4331 | 3.4331 | 2019-04-29 09:00 | 2.0119 | 3.4525 | 5.8353 | 5.8353 | 5.8353 | 5.8353
2021-03-01 22:00 | 1.7264 | 2.1008 | 2.0555 | 2.2109 | 2.0944 | 2.2497 | 1.3003 | 2.2299 | 2.7515 | 2.7515 | 3.0993 | 3.0993 | 2019-04-29 10:00 | 1.9357 | 3.3217 | 5.6143 | 5.6143 | 5.6143 | 5.6143
2021-03-01 23:00 | 1.5147 | 1.8432 | 1.8034 | 1.9398 | 1.8375 | 1.9738 | 1.1374 | 1.9505 | 2.4068 | 2.4068 | 2.711 | 2.711 | 2019-04-29 11:00 | 2.0119 | 3.4525 | 5.8353 | 5.8353 | 5.8353 | 5.8353
2021-03-02 | 1.4375 | 1.7493 | 1.7116 | 1.8409 | 1.7439 | 1.8733 | 0.96675 | 1.6578 | 2.0456 | 2.0456 | 2.3042 | 2.3042 | 2019-04-29 12:00 | 2.0196 | 3.4656 | 5.8574 | 5.8574 | 5.8574 | 5.8574
2021-03-02 01:00 | 1.2803 | 1.558 | 1.5244 | 1.6396 | 1.5532 | 1.6685 | 0.80865 | 1.3867 | 1.7111 | 1.7111 | 1.9274 | 1.9274 | 2019-04-29 13:00 | 1.9891 | 3.4133 | 5.769 | 5.769 | 5.769 | 5.769
2021-03-02 02:00 | 1.2175 | 1.4815 | 1.4496 | 1.5591 | 1.477 | 1.5865 | 0.80878 | 1.3869 | 1.7114 | 1.7114 | 1.9277 | 1.9277 | 2019-04-29 14:00 | 2.1644 | 3.7141 | 6.2774 | 6.2774 | 6.2774 | 6.2774
2021-03-02 03:00 | 1.2089 | 1.4711 | 1.4394 | 1.5481 | 1.4666 | 1.5753 | 0.73161 | 1.2546 | 1.5481 | 1.5481 | 1.7438 | 1.7438 | 2019-04-29 15:00 | 1.9967 | 3.4264 | 5.7911 | 5.7911 | 5.7911 | 5.7911
2021-03-02 04:00 | 1.261 | 1.5345 | 1.5014 | 1.6148 | 1.5297 | 1.6432 | 0.7649 | 1.3117 | 1.6185 | 1.6185 | 1.8231 | 1.8231 | 2019-04-29 16:00 | 2.0043 | 3.4394 | 5.8132 | 5.8132 | 5.8132 | 5.8132
2021-03-02 05:00 | 1.4133 | 1.7199 | 1.6828 | 1.81 | 1.7146 | 1.8418 | 0.76591 | 1.3134 | 1.6207 | 1.6207 | 1.8255 | 1.8255 | 2019-04-29 17:00 | 1.9205 | 3.2956 | 5.5701 | 5.5701 | 5.5701 | 5.5701
2021-03-02 06:00 | 1.669 | 2.031 | 1.9872 | 2.1374 | 2.0247 | 2.175 | 1.0117 | 1.7349 | 2.1407 | 2.1407 | 2.4113 | 2.4113 | 2019-04-29 18:00 | 1.8367 | 3.1517 | 5.3269 | 5.3269 | 5.3269 | 5.3269
2021-03-02 07:00 | 1.9291 | 2.3475 | 2.2968 | 2.4705 | 2.3402 | 2.5139 | 1.2375 | 2.122 | 2.6185 | 2.6185 | 2.9494 | 2.9494 | 2019-04-29 19:00 | 1.8138 | 3.1125 | 5.2606 | 5.2606 | 5.2606 | 5.2606
2021-03-02 08:00 | 2.0205 | 2.4588 | 2.4057 | 2.5876 | 2.4512 | 2.633 | 1.3746 | 2.3573 | 2.9088 | 2.9088 | 3.2764 | 3.2764 | 2019-04-29 20:00 | 1.6919 | 2.9032 | 4.907 | 4.907 | 4.907 | 4.907
2021-03-02 09:00 | 2.0662 | 2.5144 | 2.4602 | 2.6461 | 2.5067 | 2.6926 | 1.2832 | 2.2005 | 2.7152 | 2.7152 | 3.0584 | 3.0584 | 2019-04-29 21:00 | 1.6157 | 2.7725 | 4.6859 | 4.6859 | 4.6859 | 4.6859
2021-03-02 10:00 | 2.1577 | 2.6257 | 2.5691 | 2.7632 | 2.6176 | 2.8118 | 1.3832 | 2.372 | 2.9269 | 2.9269 | 3.2968 | 3.2968 | 2019-04-29 22:00 | 1.6004 | 2.7463 | 4.6417 | 4.6417 | 4.6417 | 4.6417
2021-03-02 11:00 | 2.0977 | 2.5527 | 2.4976 | 2.6864 | 2.5448 | 2.7336 | 1.4747 | 2.5288 | 3.1204 | 3.1204 | 3.5148 | 3.5148 | 2019-04-29 23:00 | 1.3946 | 2.3932 | 4.0449 | 4.0449 | 4.0449 | 4.0449
2021-03-02 12:00 | 2.0405 | 2.4831 | 2.4295 | 2.6132 | 2.4755 | 2.6591 | 1.4861 | 2.5484 | 3.1446 | 3.1446 | 3.542 | 3.542 | 2019-04-30 | 1.387 | 2.3801 | 4.0228 | 4.0228 | 4.0228 | 4.0228
2021-03-02 13:00 | 2.1034 | 2.5596 | 2.5044 | 2.6937 | 2.5517 | 2.741 | 1.4547 | 2.4945 | 3.0781 | 3.0781 | 3.4671 | 3.4671 | 2019-04-30 01:00 | 1.387 | 2.3801 | 4.0228 | 4.0228 | 4.0228 | 4.0228
2021-03-02 14:00 | 2.232 | 2.7161 | 2.6575 | 2.8584 | 2.7077 | 2.9086 | 1.3861 | 2.3769 | 2.9329 | 2.9329 | 3.3036 | 3.3036 | 2019-04-30 02:00 | 1.3718 | 2.354 | 3.9786 | 3.9786 | 3.9786 | 3.9786
2021-03-02 15:00 | 2.2149 | 2.6953 | 2.6371 | 2.8364 | 2.6869 | 2.8863 | 1.3346 | 2.2887 | 2.8241 | 2.8241 | 3.181 | 3.181 | 2019-04-30 03:00 | 1.4251 | 2.4455 | 4.1333 | 4.1333 | 4.1333 | 4.1333
2021-03-02 16:00 | 2.1663 | 2.6361 | 2.5793 | 2.7742 | 2.628 | 2.823 | 1.3861 | 2.3769 | 2.9329 | 2.9329 | 3.3036 | 3.3036 | 2019-04-30 04:00 | 1.4251 | 2.4455 | 4.1333 | 4.1333 | 4.1333 | 4.1333
2021-03-02 17:00 | 2.3092 | 2.81 | 2.7494 | 2.9572 | 2.8014 | 3.0092 | 1.5461 | 2.6513 | 3.2716 | 3.2716 | 3.6851 | 3.6851 | 2019-04-30 05:00 | 1.5928 | 2.7332 | 4.6196 | 4.6196 | 4.6196 | 4.6196
2021-03-02 18:00 | 2.4378 | 2.9665 | 2.9025 | 3.1219 | 2.9574 | 3.1768 | 1.6061 | 2.7543 | 3.3986 | 3.3986 | 3.8281 | 3.8281 | 2019-04-30 06:00 | 1.7833 | 3.0602 | 5.1722 | 5.1722 | 5.1722 | 5.1722
2021-03-02 19:00 | 2.3949 | 2.9143 | 2.8515 | 3.067 | 2.9054 | 3.1209 | 1.5377 | 2.6369 | 3.2538 | 3.2538 | 3.665 | 3.665 | 2019-04-30 07:00 | 1.8748 | 3.2171 | 5.4375 | 5.4375 | 5.4375 | 5.4375
2021-03-02 20:00 | 2.1663 | 2.6361 | 2.5793 | 2.7742 | 2.628 | 2.823 | 1.4861 | 2.5484 | 3.1446 | 3.1446 | 3.542 | 3.542 | 2019-04-30 08:00 | 2.0119 | 3.4525 | 5.8353 | 5.8353 | 5.8353 | 5.8353
2021-03-02 21:00 | 1.9605 | 2.3857 | 2.3343 | 2.5107 | 2.3784 | 2.5548 | 1.4232 | 2.4406 | 3.0116 | 3.0116 | 3.3922 | 3.3922 | 2019-04-30 09:00 | 1.9738 | 3.3871 | 5.7248 | 5.7248 | 5.7248 | 5.7248
2021-03-02 22:00 | 1.7662 | 2.1492 | 2.1029 | 2.2618 | 2.1426 | 2.3016 | 1.2718 | 2.1809 | 2.691 | 2.691 | 3.0312 | 3.0312 | 2019-04-30 10:00 | 2.0043 | 3.4394 | 5.8132 | 5.8132 | 5.8132 | 5.8132
2021-03-02 23:00 | 1.5318 | 1.8641 | 1.8239 | 1.9617 | 1.8583 | 1.9962 | 1.0174 | 1.7447 | 2.1528 | 2.1528 | 2.4249 | 2.4249 | 2019-04-30 11:00 | 2.1339 | 3.6618 | 6.189 | 6.189 | 6.189 | 6.189
2021-03-03 | 1.4689 | 1.7876 | 1.749 | 1.8812 | 1.7821 | 1.9143 | 0.85764 | 1.4707 | 1.8148 | 1.8148 | 2.0441 | 2.0441 | 2019-04-30 12:00 | 2.0577 | 3.531 | 5.9679 | 5.9679 | 5.9679 | 5.9679
2021-03-03 01:00 | 1.3477 | 1.64 | 1.6046 | 1.7259 | 1.6349 | 1.7562 | 0.76305 | 1.3085 | 1.6146 | 1.6146 | 1.8187 | 1.8187 | 2019-04-30 13:00 | 1.9891 | 3.4133 | 5.769 | 5.769 | 5.769 | 5.769
2021-03-03 02:00 | 1.2718 | 1.5476 | 1.5142 | 1.6287 | 1.5428 | 1.6573 | 0.75734 | 1.2987 | 1.6025 | 1.6025 | 1.8051 | 1.8051 | 2019-04-30 14:00 | 2.0653 | 3.5441 | 5.99 | 5.99 | 5.99 | 5.99
2021-03-03 03:00 | 1.2775 | 1.5545 | 1.521 | 1.636 | 1.5498 | 1.6647 | 0.69732 | 1.1958 | 1.4755 | 1.4755 | 1.662 | 1.662 | 2019-04-30 15:00 | 2.0272 | 3.4787 | 5.8795 | 5.8795 | 5.8795 | 5.8795
2021-03-03 04:00 | 1.2718 | 1.5476 | 1.5142 | 1.6287 | 1.5428 | 1.6573 | 0.69446 | 1.1909 | 1.4695 | 1.4695 | 1.6552 | 1.6552 | 2019-04-30 16:00 | 2.0043 | 3.4394 | 5.8132 | 5.8132 | 5.8132 | 5.8132
2021-03-03 05:00 | 1.4116 | 1.7178 | 1.6807 | 1.8078 | 1.7125 | 1.8395 | 0.75734 | 1.2987 | 1.6025 | 1.6025 | 1.8051 | 1.8051 | 2019-04-30 17:00 | 1.9967 | 3.4264 | 5.7911 | 5.7911 | 5.7911 | 5.7911
2021-03-03 06:00 | 1.7319 | 2.1075 | 2.0621 | 2.2179 | 2.101 | 2.2569 | 1.0746 | 1.8427 | 2.2738 | 2.2738 | 2.5612 | 2.5612 | 2019-04-30 18:00 | 1.9891 | 3.4133 | 5.769 | 5.769 | 5.769 | 5.769
2021-03-03 07:00 | 1.9948 | 2.4275 | 2.3751 | 2.5546 | 2.42 | 2.5995 | 1.2023 | 2.0618 | 2.5441 | 2.5441 | 2.8657 | 2.8657 | 2019-04-30 19:00 | 1.7833 | 3.0602 | 5.1722 | 5.1722 | 5.1722 | 5.1722
2021-03-03 08:00 | 2.0548 | 2.5005 | 2.4466 | 2.6315 | 2.4928 | 2.6777 | 1.3489 | 2.3132 | 2.8543 | 2.8543 | 3.2151 | 3.2151 | 2019-04-30 20:00 | 1.6995 | 2.9163 | 4.9291 | 4.9291 | 4.9291 | 4.9291
2021-03-03 09:00 | 2.0205 | 2.4588 | 2.4057 | 2.5876 | 2.4512 | 2.633 | 1.246 | 2.1367 | 2.6366 | 2.6366 | 2.9699 | 2.9699 | 2019-04-30 21:00 | 1.6004 | 2.7463 | 4.6417 | 4.6417 | 4.6417 | 4.6417
2021-03-03 10:00 | 1.9891 | 2.4205 | 2.3683 | 2.5473 | 2.4131 | 2.5921 | 1.3232 | 2.2691 | 2.7999 | 2.7999 | 3.1538 | 3.1538 | 2019-04-30 22:00 | 1.6004 | 2.7463 | 4.6417 | 4.6417 | 4.6417 | 4.6417
2021-03-03 11:00 | 1.8576 | 2.2605 | 2.2118 | 2.379 | 2.2536 | 2.4208 | 1.3346 | 2.2887 | 2.8241 | 2.8241 | 3.181 | 3.181 | 2019-04-30 23:00 | 1.4556 | 2.4978 | 4.2218 | 4.2218 | 4.2218 | 4.2218
2021-03-03 12:00 | 1.8976 | 2.3092 | 2.2594 | 2.4302 | 2.3021 | 2.4729 | 1.3661 | 2.3426 | 2.8906 | 2.8906 | 3.256 | 3.256 | 2019-05-01 | 1.387 | 2.3801 | 4.0228 | 4.0228 | 4.0228 | 4.0228
2021-03-03 13:00 | 1.9376 | 2.3579 | 2.307 | 2.4814 | 2.3506 | 2.525 | 1.3489 | 2.3132 | 2.8543 | 2.8543 | 3.2151 | 3.2151 | 2019-05-01 01:00 | 1.3946 | 2.3932 | 4.0449 | 4.0449 | 4.0449 | 4.0449
2021-03-03 14:00 | 1.9748 | 2.4031 | 2.3513 | 2.529 | 2.3957 | 2.5734 | 1.3232 | 2.2691 | 2.7999 | 2.7999 | 3.1538 | 3.1538 | 2019-05-01 02:00 | 1.4023 | 2.4063 | 4.067 | 4.067 | 4.067 | 4.067
2021-03-03 15:00 | 2.1063 | 2.5631 | 2.5078 | 2.6974 | 2.5552 | 2.7448 | 1.266 | 2.1711 | 2.679 | 2.679 | 3.0176 | 3.0176 | 2019-05-01 03:00 | 1.3718 | 2.354 | 3.9786 | 3.9786 | 3.9786 | 3.9786
2021-03-03 16:00 | 2.2349 | 2.7196 | 2.6609 | 2.8621 | 2.7112 | 2.9124 | 1.3232 | 2.2691 | 2.7999 | 2.7999 | 3.1538 | 3.1538 | 2019-05-01 04:00 | 1.4709 | 2.524 | 4.266 | 4.266 | 4.266 | 4.266
2021-03-03 17:00 | 2.1834 | 2.657 | 2.5997 | 2.7962 | 2.6488 | 2.8453 | 1.4461 | 2.4798 | 3.0599 | 3.0599 | 3.4467 | 3.4467 | 2019-05-01 05:00 | 1.5623 | 2.6809 | 4.5312 | 4.5312 | 4.5312 | 4.5312
2021-03-03 18:00 | 2.3035 | 2.8031 | 2.7426 | 2.9499 | 2.7944 | 3.0017 | 1.4004 | 2.4014 | 2.9632 | 2.9632 | 3.3377 | 3.3377 | 2019-05-01 06:00 | 1.7071 | 2.9294 | 4.9512 | 4.9512 | 4.9512 | 4.9512
2021-03-03 19:00 | 2.1949 | 2.6709 | 2.6133 | 2.8108 | 2.6627 | 2.8602 | 1.4975 | 2.568 | 3.1688 | 3.1688 | 3.5693 | 3.5693 | 2019-05-01 07:00 | 1.7071 | 2.9294 | 4.9512 | 4.9512 | 4.9512 | 4.9512
2021-03-03 20:00 | 2.1263 | 2.5874 | 2.5316 | 2.723 | 2.5795 | 2.7708 | 1.5032 | 2.5778 | 3.1809 | 3.1809 | 3.5829 | 3.5829 | 2019-05-01 08:00 | 1.9738 | 3.3871 | 5.7248 | 5.7248 | 5.7248 | 5.7248
2021-03-03 21:00 | 1.9348 | 2.3544 | 2.3036 | 2.4778 | 2.3472 | 2.5213 | 1.5004 | 2.5729 | 3.1748 | 3.1748 | 3.5761 | 3.5761 | 2019-05-01 09:00 | 1.9891 | 3.4133 | 5.769 | 5.769 | 5.769 | 5.769
2021-03-03 22:00 | 1.7462 | 2.1249 | 2.0791 | 2.2362 | 2.1184 | 2.2755 | 1.235 | 2.1179 | 2.6133 | 2.6133 | 2.9436 | 2.9436 | 2019-05-01 10:00 | 2.0958 | 3.5964 | 6.0785 | 6.0785 | 6.0785 | 6.0785
2021-03-03 23:00 | 1.4375 | 1.7493 | 1.7116 | 1.8409 | 1.7439 | 1.8733 | 1.046 | 1.7937 | 2.2133 | 2.2133 | 2.4931 | 2.4931 | 2019-05-01 11:00 | 2.0729 | 3.5571 | 6.0121 | 6.0121 | 6.0121 | 6.0121
2021-03-04 | 1.3718 | 1.6693 | 1.6333 | 1.7568 | 1.6642 | 1.7876 | 0.90615 | 1.5539 | 1.9174 | 1.9174 | 2.1598 | 2.1598 | 2019-05-01 12:00 | 2.1339 | 3.6618 | 6.189 | 6.189 | 6.189 | 6.189
2021-03-04 01:00 | 1.2232 | 1.4885 | 1.4564 | 1.5664 | 1.4839 | 1.594 | 0.76313 | 1.3086 | 1.6148 | 1.6148 | 1.8189 | 1.8189 | 2019-05-01 13:00 | 2.1186 | 3.6356 | 6.1448 | 6.1448 | 6.1448 | 6.1448
2021-03-04 02:00 | 1.2089 | 1.4712 | 1.4394 | 1.5482 | 1.4666 | 1.5754 | 0.77364 | 1.3267 | 1.637 | 1.637 | 1.8439 | 1.8439 | 2019-05-01 14:00 | 2.1567 | 3.701 | 6.2553 | 6.2553 | 6.2553 | 6.2553
2021-03-04 03:00 | 1.2143 | 1.4777 | 1.4459 | 1.5552 | 1.4732 | 1.5825 | 0.77448 | 1.3281 | 1.6388 | 1.6388 | 1.8459 | 1.8459 | 2019-05-01 15:00 | 2.0653 | 3.5441 | 5.99 | 5.99 | 5.99 | 5.99
2021-03-04 04:00 | 1.2302 | 1.4971 | 1.4648 | 1.5755 | 1.4925 | 1.6032 | 0.7459 | 1.2791 | 1.5783 | 1.5783 | 1.7778 | 1.7778 | 2019-05-01 16:00 | 2.0653 | 3.5441 | 5.99 | 5.99 | 5.99 | 5.99
2021-03-04 05:00 | 1.4217 | 1.7301 | 1.6928 | 1.8207 | 1.7248 | 1.8527 | 0.79163 | 1.3575 | 1.6751 | 1.6751 | 1.8868 | 1.8868 | 2019-05-01 17:00 | 2.0577 | 3.531 | 5.9679 | 5.9679 | 5.9679 | 5.9679
2021-03-04 06:00 | 1.6801 | 2.0445 | 2.0004 | 2.1516 | 2.0382 | 2.1894 | 0.99168 | 1.7006 | 2.0984 | 2.0984 | 2.3636 | 2.3636 | 2019-05-01 18:00 | 2.0577 | 3.531 | 5.9679 | 5.9679 | 5.9679 | 5.9679
2021-03-04 07:00 | 1.9519 | 2.3753 | 2.3241 | 2.4997 | 2.368 | 2.5437 | 1.2317 | 2.1122 | 2.6064 | 2.6064 | 2.9358 | 2.9358 | 2019-05-01 19:00 | 1.9281 | 3.3087 | 5.5922 | 5.5922 | 5.5922 | 5.5922
2021-03-04 08:00 | 2.0548 | 2.5005 | 2.4466 | 2.6315 | 2.4928 | 2.6777 | 1.3089 | 2.2446 | 2.7697 | 2.7697 | 3.1197 | 3.1197 | 2019-05-01 20:00 | 1.7681 | 3.034 | 5.128 | 5.128 | 5.128 | 5.128
2021-03-04 09:00 | 2.0205 | 2.4588 | 2.4057 | 2.5876 | 2.4512 | 2.633 | 1.2232 | 2.0975 | 2.5882 | 2.5882 | 2.9154 | 2.9154 | 2019-05-01 21:00 | 1.73 | 2.9686 | 5.0175 | 5.0175 | 5.0175 | 5.0175
2021-03-04 10:00 | 1.9891 | 2.4205 | 2.3683 | 2.5473 | 2.4131 | 2.5921 | 1.3975 | 2.3965 | 2.9571 | 2.9571 | 3.3309 | 3.3309 | 2019-05-01 22:00 | 1.6538 | 2.8379 | 4.7965 | 4.7965 | 4.7965 | 4.7965
2021-03-04 11:00 | 1.8576 | 2.2605 | 2.2118 | 2.379 | 2.2536 | 2.4208 | 1.3746 | 2.3573 | 2.9088 | 2.9088 | 3.2764 | 3.2764 | 2019-05-01 23:00 | 1.5547 | 2.6678 | 4.5091 | 4.5091 | 4.5091 | 4.5091
2021-03-04 12:00 | 1.8976 | 2.3092 | 2.2594 | 2.4302 | 2.3021 | 2.4729 | 1.3861 | 2.3769 | 2.9329 | 2.9329 | 3.3036 | 3.3036 | 2019-05-02 | 1.5166 | 2.6025 | 4.3986 | 4.3986 | 4.3986 | 4.3986
2021-03-04 13:00 | 2.092 | 2.5457 | 2.4908 | 2.6791 | 2.5379 | 2.7261 | 1.3918 | 2.3867 | 2.945 | 2.945 | 3.3173 | 3.3173 | 2019-05-02 01:00 | 1.5013 | 2.5763 | 4.3544 | 4.3544 | 4.3544 | 4.3544
2021-03-04 14:00 | 2.1377 | 2.6014 | 2.5452 | 2.7376 | 2.5933 | 2.7857 | 1.3403 | 2.2985 | 2.8362 | 2.8362 | 3.1947 | 3.1947 | 2019-05-02 02:00 | 1.4404 | 2.4717 | 4.1776 | 4.1776 | 4.1776 | 4.1776
2021-03-04 15:00 | 2.0805 | 2.5318 | 2.4772 | 2.6644 | 2.524 | 2.7112 | 1.3261 | 2.274 | 2.8059 | 2.8059 | 3.1606 | 3.1606 | 2019-05-02 03:00 | 1.4251 | 2.4455 | 4.1333 | 4.1333 | 4.1333 | 4.1333
2021-03-04 16:00 | 2.1834 | 2.657 | 2.5997 | 2.7962 | 2.6488 | 2.8453 | 1.4261 | 2.4455 | 3.0176 | 3.0176 | 3.399 | 3.399 | 2019-05-02 04:00 | 1.4556 | 2.4978 | 4.2218 | 4.2218 | 4.2218 | 4.2218
2021-03-04 17:00 | 2.2834 | 2.7787 | 2.7188 | 2.9243 | 2.7702 | 2.9757 | 1.4632 | 2.5092 | 3.0962 | 3.0962 | 3.4876 | 3.4876 | 2019-05-02 05:00 | 1.6385 | 2.8117 | 4.7522 | 4.7522 | 4.7522 | 4.7522
2021-03-04 18:00 | 2.4121 | 2.9352 | 2.8719 | 3.089 | 2.9262 | 3.1433 | 1.5261 | 2.617 | 3.2293 | 3.2293 | 3.6374 | 3.6374 | 2019-05-02 06:00 | 1.7833 | 3.0602 | 5.1722 | 5.1722 | 5.1722 | 5.1722
2021-03-04 19:00 | 2.3713 | 2.8856 | 2.8233 | 3.0367 | 2.8767 | 3.0901 | 1.489 | 2.5533 | 3.1506 | 3.1506 | 3.5489 | 3.5489 | 2019-05-02 07:00 | 1.9738 | 3.3871 | 5.7248 | 5.7248 | 5.7248 | 5.7248
2021-03-04 20:00 | 2.1634 | 2.6327 | 2.5759 | 2.7706 | 2.6245 | 2.8192 | 1.4918 | 2.5582 | 3.1567 | 3.1567 | 3.5557 | 3.5557 | 2019-05-02 08:00 | 2.1415 | 3.6748 | 6.2111 | 6.2111 | 6.2111 | 6.2111
2021-03-04 21:00 | 1.8778 | 2.2851 | 2.2358 | 2.4048 | 2.278 | 2.4471 | 1.4375 | 2.4651 | 3.0418 | 3.0418 | 3.4262 | 3.4262 | 2019-05-02 09:00 | 2.1949 | 3.7664 | 6.3658 | 6.3658 | 6.3658 | 6.3658
2021-03-04 22:00 | 1.7004 | 2.0693 | 2.0246 | 2.1777 | 2.0629 | 2.2159 | 1.2832 | 2.2005 | 2.7152 | 2.7152 | 3.0584 | 3.0584 | 2019-05-02 10:00 | 2.1034 | 3.6094 | 6.1006 | 6.1006 | 6.1006 | 6.1006
2021-03-04 23:00 | 1.4604 | 1.7771 | 1.7388 | 1.8702 | 1.7716 | 1.9031 | 1.0888 | 1.8672 | 2.304 | 2.304 | 2.5952 | 2.5952 | 2019-05-02 11:00 | 2.2787 | 3.9102 | 6.6089 | 6.6089 | 6.6089 | 6.6089
2021-03-05 | 1.341 | 1.6319 | 1.5967 | 1.7174 | 1.6268 | 1.7475 | 0.9088 | 1.5585 | 1.923 | 1.923 | 2.1661 | 2.1661 | 2019-05-02 12:00 | 2.1644 | 3.7141 | 6.2774 | 6.2774 | 6.2774 | 6.2774
2021-03-05 01:00 | 1.246 | 1.5163 | 1.4835 | 1.5957 | 1.5116 | 1.6237 | 0.81473 | 1.3971 | 1.724 | 1.724 | 1.9419 | 1.9419 | 2019-05-02 13:00 | 2.2863 | 3.9233 | 6.631 | 6.631 | 6.631 | 6.631
2021-03-05 02:00 | 1.246 | 1.5163 | 1.4836 | 1.5957 | 1.5116 | 1.6238 | 0.7802 | 1.3379 | 1.6509 | 1.6509 | 1.8596 | 1.8596 | 2019-05-02 14:00 | 2.2482 | 3.8579 | 6.5205 | 6.5205 | 6.5205 | 6.5205
2021-03-05 03:00 | 1.1803 | 1.4363 | 1.4053 | 1.5115 | 1.4319 | 1.5381 | 0.74305 | 1.2742 | 1.5723 | 1.5723 | 1.771 | 1.771 | 2019-05-02 15:00 | 2.2177 | 3.8056 | 6.4321 | 6.4321 | 6.4321 | 6.4321
2021-03-05 04:00 | 1.2346 | 1.5024 | 1.47 | 1.5811 | 1.4978 | 1.6089 | 0.71161 | 1.2203 | 1.5058 | 1.5058 | 1.6961 | 1.6961 | 2019-05-02 16:00 | 2.172 | 3.7271 | 6.2995 | 6.2995 | 6.2995 | 6.2995
2021-03-05 05:00 | 1.4368 | 1.7484 | 1.7107 | 1.84 | 1.743 | 1.8723 | 0.7802 | 1.3379 | 1.6509 | 1.6509 | 1.8596 | 1.8596 | 2019-05-02 17:00 | 2.1339 | 3.6618 | 6.189 | 6.189 | 6.189 | 6.189
2021-03-05 06:00 | 1.6604 | 2.0206 | 1.977 | 2.1264 | 2.0143 | 2.1638 | 0.96226 | 1.6501 | 2.0361 | 2.0361 | 2.2935 | 2.2935 | 2019-05-02 18:00 | 2.1567 | 3.701 | 6.2553 | 6.2553 | 6.2553 | 6.2553
2021-03-05 07:00 | 1.9205 | 2.337 | 2.2866 | 2.4595 | 2.3298 | 2.5027 | 1.2317 | 2.1122 | 2.6064 | 2.6064 | 2.9358 | 2.9358 | 2019-05-02 19:00 | 2.0272 | 3.4787 | 5.8795 | 5.8795 | 5.8795 | 5.8795
2021-03-05 08:00 | 2.072 | 2.5214 | 2.467 | 2.6535 | 2.5136 | 2.7001 | 1.3089 | 2.2446 | 2.7697 | 2.7697 | 3.1197 | 3.1197 | 2019-05-02 20:00 | 1.9205 | 3.2956 | 5.5701 | 5.5701 | 5.5701 | 5.5701
2021-03-05 09:00 | 2.0177 | 2.4553 | 2.4023 | 2.5839 | 2.4477 | 2.6293 | 1.2232 | 2.0975 | 2.5882 | 2.5882 | 2.9154 | 2.9154 | 2019-05-02 21:00 | 1.829 | 3.1386 | 5.3048 | 5.3048 | 5.3048 | 5.3048
2021-03-05 10:00 | 1.9891 | 2.4205 | 2.3683 | 2.5473 | 2.4131 | 2.5921 | 1.3975 | 2.3965 | 2.9571 | 2.9571 | 3.3309 | 3.3309 | 2019-05-02 22:00 | 1.7605 | 3.0209 | 5.1059 | 5.1059 | 5.1059 | 5.1059
2021-03-05 11:00 | 2.032 | 2.4727 | 2.4193 | 2.6022 | 2.4651 | 2.6479 | 1.3746 | 2.3573 | 2.9088 | 2.9088 | 3.2764 | 3.2764 | 2019-05-02 23:00 | 1.669 | 2.864 | 4.8407 | 4.8407 | 4.8407 | 4.8407
2021-03-05 12:00 | 2.1091 | 2.5666 | 2.5112 | 2.701 | 2.5587 | 2.7485 | 1.3861 | 2.3769 | 2.9329 | 2.9329 | 3.3036 | 3.3036 | 2019-05-03 | 1.5471 | 2.6548 | 4.487 | 4.487 | 4.487 | 4.487
2021-03-05 13:00 | 2.152 | 2.6187 | 2.5623 | 2.7559 | 2.6107 | 2.8043 | 1.3918 | 2.3867 | 2.945 | 2.945 | 3.3173 | 3.3173 | 2019-05-03 01:00 | 1.5471 | 2.6548 | 4.487 | 4.487 | 4.487 | 4.487
2021-03-05 14:00 | 2.0834 | 2.5353 | 2.4806 | 2.6681 | 2.5275 | 2.715 | 1.3718 | 2.3524 | 2.9027 | 2.9027 | 3.2696 | 3.2696 | 2019-05-03 02:00 | 1.4861 | 2.5501 | 4.3102 | 4.3102 | 4.3102 | 4.3102
2021-03-05 15:00 | 2.0863 | 2.5388 | 2.484 | 2.6718 | 2.5309 | 2.7187 | 1.3232 | 2.2691 | 2.7999 | 2.7999 | 3.1538 | 3.1538 | 2019-05-03 03:00 | 1.4556 | 2.4978 | 4.2218 | 4.2218 | 4.2218 | 4.2218
2021-03-05 16:00 | 2.1234 | 2.584 | 2.5282 | 2.7193 | 2.576 | 2.7671 | 1.4232 | 2.4406 | 3.0116 | 3.0116 | 3.3922 | 3.3922 | 2019-05-03 04:00 | 1.5699 | 2.694 | 4.5533 | 4.5533 | 4.5533 | 4.5533
2021-03-05 17:00 | 2.1205 | 2.5805 | 2.5248 | 2.7157 | 2.5725 | 2.7634 | 1.5204 | 2.6072 | 3.2172 | 3.2172 | 3.6238 | 3.6238 | 2019-05-03 05:00 | 1.73 | 2.9686 | 5.0175 | 5.0175 | 5.0175 | 5.0175
2021-03-05 18:00 | 2.1463 | 2.6118 | 2.5554 | 2.7486 | 2.6037 | 2.7969 | 1.7605 | 3.0189 | 3.7251 | 3.7251 | 4.196 | 4.196 | 2019-05-03 06:00 | 1.8595 | 3.191 | 5.3932 | 5.3932 | 5.3932 | 5.3932
2021-03-05 19:00 | 1.9438 | 2.3654 | 2.3144 | 2.4894 | 2.3581 | 2.5331 | 1.7262 | 2.9601 | 3.6526 | 3.6526 | 4.1142 | 4.1142 | 2019-05-03 07:00 | 1.9281 | 3.3087 | 5.5922 | 5.5922 | 5.5922 | 5.5922
2021-03-05 20:00 | 1.729 | 2.104 | 2.0586 | 2.2143 | 2.0976 | 2.2532 | 1.6833 | 2.8866 | 3.5619 | 3.5619 | 4.0121 | 4.0121 | 2019-05-03 08:00 | 2.2177 | 3.8056 | 6.4321 | 6.4321 | 6.4321 | 6.4321
2021-03-05 21:00 | 1.6547 | 2.0136 | 1.9702 | 2.1191 | 2.0074 | 2.1563 | 1.5347 | 2.6317 | 3.2474 | 3.2474 | 3.6578 | 3.6578 | 2019-05-03 09:00 | 2.1796 | 3.7402 | 6.3216 | 6.3216 | 6.3216 | 6.3216
2021-03-05 22:00 | 1.5118 | 1.8397 | 1.8 | 1.9361 | 1.8341 | 1.9701 | 1.3918 | 2.3867 | 2.945 | 2.945 | 3.3173 | 3.3173 | 2019-05-03 10:00 | 2.172 | 3.7271 | 6.2995 | 6.2995 | 6.2995 | 6.2995
2021-03-05 23:00 | 1.4289 | 1.7389 | 1.7014 | 1.83 | 1.7335 | 1.8621 | 1.146 | 1.9652 | 2.425 | 2.425 | 2.7315 | 2.7315 | 2019-05-03 11:00 | 2.1567 | 3.701 | 6.2553 | 6.2553 | 6.2553 | 6.2553
2021-03-06 | 1.3062 | 1.5895 | 1.5552 | 1.6728 | 1.5846 | 1.7022 | 0.98025 | 1.681 | 2.0742 | 2.0742 | 2.3364 | 2.3364 | 2019-05-03 12:00 | 2.2634 | 3.8841 | 6.5647 | 6.5647 | 6.5647 | 6.5647
2021-03-06 01:00 | 1.2203 | 1.485 | 1.453 | 1.5628 | 1.4804 | 1.5902 | 0.88594 | 1.5192 | 1.8747 | 1.8747 | 2.1116 | 2.1116 | 2019-05-03 13:00 | 2.2482 | 3.8579 | 6.5205 | 6.5205 | 6.5205 | 6.5205
2021-03-06 02:00 | 1.2146 | 1.478 | 1.4462 | 1.5555 | 1.4735 | 1.5828 | 0.78591 | 1.3477 | 1.663 | 1.663 | 1.8732 | 1.8732 | 2019-05-03 14:00 | 2.1644 | 3.7141 | 6.2774 | 6.2774 | 6.2774 | 6.2774
2021-03-06 03:00 | 1.2118 | 1.4747 | 1.4428 | 1.5519 | 1.4701 | 1.5792 | 0.75448 | 1.2938 | 1.5965 | 1.5965 | 1.7983 | 1.7983 | 2019-05-03 15:00 | 2.2025 | 3.7795 | 6.3879 | 6.3879 | 6.3879 | 6.3879
2021-03-06 04:00 | 1.1911 | 1.4494 | 1.4181 | 1.5253 | 1.4449 | 1.5521 | 0.72876 | 1.2497 | 1.5421 | 1.5421 | 1.737 | 1.737 | 2019-05-03 16:00 | 2.1034 | 3.6094 | 6.1006 | 6.1006 | 6.1006 | 6.1006
2021-03-06 05:00 | 1.2401 | 1.5091 | 1.4766 | 1.5882 | 1.5045 | 1.6161 | 0.73447 | 1.2595 | 1.5542 | 1.5542 | 1.7506 | 1.7506 | 2019-05-03 17:00 | 2.0043 | 3.4394 | 5.8132 | 5.8132 | 5.8132 | 5.8132
2021-03-06 06:00 | 1.3746 | 1.6728 | 1.6367 | 1.7604 | 1.6676 | 1.7914 | 0.83164 | 1.4261 | 1.7598 | 1.7598 | 1.9822 | 1.9822 | 2019-05-03 18:00 | 1.9357 | 3.3217 | 5.6143 | 5.6143 | 5.6143 | 5.6143
2021-03-06 07:00 | 1.4118 | 1.718 | 1.6809 | 1.808 | 1.7127 | 1.8398 | 0.93738 | 1.6075 | 1.9835 | 1.9835 | 2.2342 | 2.2342 | 2019-05-03 19:00 | 1.7681 | 3.034 | 5.128 | 5.128 | 5.128 | 5.128
2021-03-06 08:00 | 1.4832 | 1.8049 | 1.766 | 1.8995 | 1.7994 | 1.9329 | 1.146 | 1.9652 | 2.425 | 2.425 | 2.7315 | 2.7315 | 2019-05-03 20:00 | 1.7376 | 2.9817 | 5.0396 | 5.0396 | 5.0396 | 5.0396
2021-03-06 09:00 | 1.5318 | 1.8641 | 1.8239 | 1.9617 | 1.8583 | 1.9962 | 1.206 | 2.0681 | 2.552 | 2.552 | 2.8745 | 2.8745 | 2019-05-03 21:00 | 1.6157 | 2.7725 | 4.6859 | 4.6859 | 4.6859 | 4.6859
2021-03-06 10:00 | 1.3946 | 1.6971 | 1.6605 | 1.786 | 1.6919 | 1.8174 | 1.4146 | 2.4259 | 2.9934 | 2.9934 | 3.3718 | 3.3718 | 2019-05-03 22:00 | 1.6309 | 2.7986 | 4.7301 | 4.7301 | 4.7301 | 4.7301
2021-03-06 11:00 | 1.2803 | 1.558 | 1.5244 | 1.6396 | 1.5532 | 1.6685 | 1.3918 | 2.3867 | 2.945 | 2.945 | 3.3173 | 3.3173 | 2019-05-03 23:00 | 1.608 | 2.7594 | 4.6638 | 4.6638 | 4.6638 | 4.6638
2021-03-06 12:00 | 1.2632 | 1.5372 | 1.504 | 1.6177 | 1.5324 | 1.6461 | 1.3975 | 2.3965 | 2.9571 | 2.9571 | 3.3309 | 3.3309 | 2019-05-04 | 1.5394 | 2.6417 | 4.4649 | 4.4649 | 4.4649 | 4.4649
2021-03-06 13:00 | 1.1774 | 1.4328 | 1.4019 | 1.5079 | 1.4284 | 1.5344 | 1.4432 | 2.4749 | 3.0539 | 3.0539 | 3.4399 | 3.4399 | 2019-05-04 01:00 | 1.4937 | 2.5632 | 4.3323 | 4.3323 | 4.3323 | 4.3323
2021-03-06 14:00 | 1.166 | 1.4189 | 1.3883 | 1.4933 | 1.4145 | 1.5195 | 1.509 | 2.5876 | 3.193 | 3.193 | 3.5965 | 3.5965 | 2019-05-04 02:00 | 1.3642 | 2.3409 | 3.9565 | 3.9565 | 3.9565 | 3.9565
2021-03-06 15:00 | 1.1489 | 1.3981 | 1.3679 | 1.4713 | 1.3937 | 1.4971 | 1.4261 | 2.4455 | 3.0176 | 3.0176 | 3.399 | 3.399 | 2019-05-04 03:00 | 1.4937 | 2.5632 | 4.3323 | 4.3323 | 4.3323 | 4.3323
2021-03-06 16:00 | 1.3003 | 1.5824 | 1.5482 | 1.6653 | 1.5775 | 1.6945 | 1.4325 | 2.4564 | 3.0311 | 3.0311 | 3.4142 | 3.4142 | 2019-05-04 04:00 | 1.4709 | 2.524 | 4.266 | 4.266 | 4.266 | 4.266
2021-03-06 17:00 | 1.3661 | 1.6624 | 1.6265 | 1.7494 | 1.6572 | 1.7802 | 1.5175 | 2.6023 | 3.2111 | 3.2111 | 3.617 | 3.617 | 2019-05-04 05:00 | 1.4709 | 2.524 | 4.266 | 4.266 | 4.266 | 4.266
2021-03-06 18:00 | 1.4975 | 1.8223 | 1.783 | 1.9178 | 1.8167 | 1.9515 | 1.5261 | 2.617 | 3.2293 | 3.2293 | 3.6374 | 3.6374 | 2019-05-04 06:00 | 1.5394 | 2.6417 | 4.4649 | 4.4649 | 4.4649 | 4.4649
2021-03-06 19:00 | 1.6198 | 1.9711 | 1.9286 | 2.0744 | 1.965 | 2.1108 | 1.5318 | 2.6268 | 3.2414 | 3.2414 | 3.651 | 3.651 | 2019-05-04 07:00 | 1.7986 | 3.0863 | 5.2164 | 5.2164 | 5.2164 | 5.2164
2021-03-06 20:00 | 1.6204 | 1.9719 | 1.9293 | 2.0752 | 1.9658 | 2.1116 | 1.4461 | 2.4798 | 3.0599 | 3.0599 | 3.4467 | 3.4467 | 2019-05-04 08:00 | 1.8824 | 3.2302 | 5.4596 | 5.4596 | 5.4596 | 5.4596
2021-03-06 21:00 | 1.5433 | 1.878 | 1.8375 | 1.9764 | 1.8722 | 2.0111 | 1.4404 | 2.47 | 3.0478 | 3.0478 | 3.4331 | 3.4331 | 2019-05-04 09:00 | 1.8443 | 3.1648 | 5.349 | 5.349 | 5.349 | 5.349
2021-03-06 22:00 | 1.4489 | 1.7632 | 1.7252 | 1.8556 | 1.7578 | 1.8882 | 1.2975 | 2.225 | 2.7455 | 2.7455 | 3.0925 | 3.0925 | 2019-05-04 10:00 | 1.9053 | 3.2694 | 5.5259 | 5.5259 | 5.5259 | 5.5259
2021-03-06 23:00 | 1.3689 | 1.6658 | 1.6299 | 1.7531 | 1.6607 | 1.7839 | 1.0688 | 1.8329 | 2.2617 | 2.2617 | 2.5475 | 2.5475 | 2019-05-04 11:00 | 1.9738 | 3.3871 | 5.7248 | 5.7248 | 5.7248 | 5.7248
2021-03-07 | 1.3232 | 1.6102 | 1.5755 | 1.6945 | 1.6052 | 1.7243 | 0.9431 | 1.6173 | 1.9956 | 1.9956 | 2.2478 | 2.2478 | 2019-05-04 12:00 | 2.0577 | 3.531 | 5.9679 | 5.9679 | 5.9679 | 5.9679
2021-03-07 01:00 | 1.226 | 1.492 | 1.4598 | 1.5701 | 1.4874 | 1.5977 | 0.82446 | 1.4138 | 1.7446 | 1.7446 | 1.9651 | 1.9651 | 2019-05-04 13:00 | 1.8976 | 3.2563 | 5.5038 | 5.5038 | 5.5038 | 5.5038
2021-03-07 02:00 | 1.1975 | 1.4573 | 1.4258 | 1.5336 | 1.4528 | 1.5605 | 0.76019 | 1.3036 | 1.6086 | 1.6086 | 1.8119 | 1.8119 | 2019-05-04 14:00 | 1.9281 | 3.3087 | 5.5922 | 5.5922 | 5.5922 | 5.5922
2021-03-07 03:00 | 1.1803 | 1.4363 | 1.4053 | 1.5115 | 1.4319 | 1.5381 | 0.73161 | 1.2546 | 1.5481 | 1.5481 | 1.7438 | 1.7438 | 2019-05-04 15:00 | 1.9281 | 3.3087 | 5.5922 | 5.5922 | 5.5922 | 5.5922
2021-03-07 04:00 | 1.1803 | 1.4363 | 1.4053 | 1.5115 | 1.4319 | 1.5381 | 0.74305 | 1.2742 | 1.5723 | 1.5723 | 1.771 | 1.771 | 2019-05-04 16:00 | 1.8595 | 3.191 | 5.3932 | 5.3932 | 5.3932 | 5.3932
2021-03-07 05:00 | 1.2167 | 1.4806 | 1.4486 | 1.5581 | 1.476 | 1.5855 | 0.73447 | 1.2595 | 1.5542 | 1.5542 | 1.7506 | 1.7506 | 2019-05-04 17:00 | 1.8214 | 3.1256 | 5.2827 | 5.2827 | 5.2827 | 5.2827
2021-03-07 06:00 | 1.2718 | 1.5476 | 1.5142 | 1.6287 | 1.5428 | 1.6573 | 0.80592 | 1.382 | 1.7053 | 1.7053 | 1.9209 | 1.9209 | 2019-05-04 18:00 | 1.8138 | 3.1125 | 5.2606 | 5.2606 | 5.2606 | 5.2606
2021-03-07 07:00 | 1.3603 | 1.6554 | 1.6197 | 1.7421 | 1.6503 | 1.7727 | 0.81164 | 1.3918 | 1.7174 | 1.7174 | 1.9345 | 1.9345 | 2019-05-04 19:00 | 1.7071 | 2.9294 | 4.9512 | 4.9512 | 4.9512 | 4.9512
2021-03-07 08:00 | 1.4004 | 1.7041 | 1.6673 | 1.7934 | 1.6988 | 1.8249 | 1.106 | 1.8966 | 2.3403 | 2.3403 | 2.6361 | 2.6361 | 2019-05-04 20:00 | 1.6385 | 2.8117 | 4.7522 | 4.7522 | 4.7522 | 4.7522
2021-03-07 09:00 | 1.3804 | 1.6797 | 1.6435 | 1.7677 | 1.6746 | 1.7988 | 1.1546 | 1.9799 | 2.4431 | 2.4431 | 2.7519 | 2.7519 | 2019-05-04 21:00 | 1.6385 | 2.8117 | 4.7522 | 4.7522 | 4.7522 | 4.7522
2021-03-07 10:00 | 1.3889 | 1.6902 | 1.6537 | 1.7787 | 1.685 | 1.81 | 1.4175 | 2.4308 | 2.9995 | 2.9995 | 3.3786 | 3.3786 | 2019-05-04 22:00 | 1.4709 | 2.524 | 4.266 | 4.266 | 4.266 | 4.266
2021-03-07 11:00 | 1.306 | 1.5893 | 1.555 | 1.6726 | 1.5844 | 1.702 | 1.4261 | 2.4455 | 3.0176 | 3.0176 | 3.399 | 3.399 | 2019-05-04 23:00 | 1.4785 | 2.5371 | 4.2881 | 4.2881 | 4.2881 | 4.2881
2021-03-07 12:00 | 1.1774 | 1.4328 | 1.4019 | 1.5079 | 1.4284 | 1.5344 | 1.3918 | 2.3867 | 2.945 | 2.945 | 3.3173 | 3.3173 | 2019-05-05 | 1.387 | 2.3801 | 4.0228 | 4.0228 | 4.0228 | 4.0228
2021-03-07 13:00 | 1.1889 | 1.4467 | 1.4155 | 1.5225 | 1.4423 | 1.5493 | 1.4804 | 2.5386 | 3.1325 | 3.1325 | 3.5284 | 3.5284 | 2019-05-05 01:00 | 1.3489 | 2.3148 | 3.9123 | 3.9123 | 3.9123 | 3.9123
2021-03-07 14:00 | 1.166 | 1.4189 | 1.3883 | 1.4933 | 1.4145 | 1.5195 | 1.3632 | 2.3377 | 2.8846 | 2.8846 | 3.2491 | 3.2491 | 2019-05-05 02:00 | 1.3565 | 2.3278 | 3.9344 | 3.9344 | 3.9344 | 3.9344
2021-03-07 15:00 | 1.1603 | 1.412 | 1.3815 | 1.4859 | 1.4076 | 1.512 | 1.3203 | 2.2642 | 2.7939 | 2.7939 | 3.147 | 3.147 | 2019-05-05 03:00 | 1.3565 | 2.3278 | 3.9344 | 3.9344 | 3.9344 | 3.9344
2021-03-07 16:00 | 1.2803 | 1.558 | 1.5244 | 1.6396 | 1.5532 | 1.6685 | 1.4175 | 2.4308 | 2.9995 | 2.9995 | 3.3786 | 3.3786 | 2019-05-05 04:00 | 1.387 | 2.3801 | 4.0228 | 4.0228 | 4.0228 | 4.0228
2021-03-07 17:00 | 1.5032 | 1.8293 | 1.7898 | 1.9251 | 1.8237 | 1.9589 | 1.5107 | 2.5907 | 3.1967 | 3.1967 | 3.6007 | 3.6007 | 2019-05-05 05:00 | 1.4099 | 2.4194 | 4.0891 | 4.0891 | 4.0891 | 4.0891
2021-03-07 18:00 | 1.5318 | 1.8641 | 1.8239 | 1.9617 | 1.8583 | 1.9962 | 1.5118 | 2.5925 | 3.199 | 3.199 | 3.6034 | 3.6034 | 2019-05-05 06:00 | 1.5471 | 2.6548 | 4.487 | 4.487 | 4.487 | 4.487
2021-03-07 19:00 | 1.5976 | 1.9441 | 1.9021 | 2.0459 | 1.9381 | 2.0818 | 1.4347 | 2.4602 | 3.0357 | 3.0357 | 3.4194 | 3.4194 | 2019-05-05 07:00 | 1.5471 | 2.6548 | 4.487 | 4.487 | 4.487 | 4.487
2021-03-07 20:00 | 1.5518 | 1.8884 | 1.8477 | 1.9873 | 1.8826 | 2.0223 | 1.4661 | 2.5141 | 3.1023 | 3.1023 | 3.4944 | 3.4944 | 2019-05-05 08:00 | 1.829 | 3.1386 | 5.3048 | 5.3048 | 5.3048 | 5.3048
2021-03-07 21:00 | 1.4575 | 1.7736 | 1.7354 | 1.8666 | 1.7682 | 1.8994 | 1.3603 | 2.3328 | 2.8785 | 2.8785 | 3.2423 | 3.2423 | 2019-05-05 09:00 | 1.8748 | 3.2171 | 5.4375 | 5.4375 | 5.4375 | 5.4375
2021-03-07 22:00 | 1.4118 | 1.718 | 1.6809 | 1.808 | 1.7127 | 1.8398 | 1.2918 | 2.2152 | 2.7334 | 2.7334 | 3.0789 | 3.0789 | 2019-05-05 10:00 | 1.8671 | 3.204 | 5.4154 | 5.4154 | 5.4154 | 5.4154
2021-03-07 23:00 | 1.4004 | 1.7041 | 1.6673 | 1.7934 | 1.6988 | 1.8249 | 1.1003 | 1.8868 | 2.3282 | 2.3282 | 2.6225 | 2.6225 | 2019-05-05 11:00 | 1.8595 | 3.191 | 5.3932 | 5.3932 | 5.3932 | 5.3932
2021-03-08 | 1.3375 | 1.6276 | 1.5925 | 1.7128 | 1.6226 | 1.7429 | 0.90335 | 1.5491 | 1.9115 | 1.9115 | 2.1531 | 2.1531 | 2019-05-05 12:00 | 1.9281 | 3.3087 | 5.5922 | 5.5922 | 5.5922 | 5.5922
2021-03-08 01:00 | 1.2073 | 1.4691 | 1.4375 | 1.5461 | 1.4646 | 1.5733 | 0.81449 | 1.3967 | 1.7235 | 1.7235 | 1.9413 | 1.9413 | 2019-05-05 13:00 | 1.9357 | 3.3217 | 5.6143 | 5.6143 | 5.6143 | 5.6143
2021-03-08 02:00 | 1.246 | 1.5163 | 1.4836 | 1.5957 | 1.5116 | 1.6238 | 0.75509 | 1.2949 | 1.5978 | 1.5978 | 1.7997 | 1.7997 | 2019-05-05 14:00 | 1.8671 | 3.204 | 5.4154 | 5.4154 | 5.4154 | 5.4154
2021-03-08 03:00 | 1.1917 | 1.4502 | 1.4189 | 1.5262 | 1.4457 | 1.553 | 0.74305 | 1.2742 | 1.5723 | 1.5723 | 1.771 | 1.771 | 2019-05-05 15:00 | 1.9434 | 3.3348 | 5.6364 | 5.6364 | 5.6364 | 5.6364
2021-03-08 04:00 | 1.1946 | 1.4537 | 1.4223 | 1.5298 | 1.4492 | 1.5567 | 0.76259 | 1.3077 | 1.6137 | 1.6137 | 1.8176 | 1.8176 | 2019-05-05 16:00 | 1.9281 | 3.3087 | 5.5922 | 5.5922 | 5.5922 | 5.5922
2021-03-08 05:00 | 1.1689 | 1.4224 | 1.3917 | 1.4969 | 1.418 | 1.5232 | 0.76305 | 1.3085 | 1.6146 | 1.6146 | 1.8187 | 1.8187 | 2019-05-05 17:00 | 1.8976 | 3.2563 | 5.5038 | 5.5038 | 5.5038 | 5.5038
2021-03-08 06:00 | 1.266 | 1.5406 | 1.5074 | 1.6213 | 1.5359 | 1.6498 | 0.81164 | 1.3918 | 1.7174 | 1.7174 | 1.9345 | 1.9345 | 2019-05-05 18:00 | 1.8976 | 3.2563 | 5.5038 | 5.5038 | 5.5038 | 5.5038
2021-03-08 07:00 | 1.3118 | 1.5963 | 1.5618 | 1.6799 | 1.5914 | 1.7094 | 0.86022 | 1.4751 | 1.8202 | 1.8202 | 2.0503 | 2.0503 | 2019-05-05 19:00 | 1.6919 | 2.9032 | 4.907 | 4.907 | 4.907 | 4.907
2021-03-08 08:00 | 1.4193 | 1.7271 | 1.6899 | 1.8176 | 1.7218 | 1.8495 | 1.0374 | 1.779 | 2.1952 | 2.1952 | 2.4726 | 2.4726 | 2019-05-05 20:00 | 1.7147 | 2.9425 | 4.9733 | 4.9733 | 4.9733 | 4.9733
2021-03-08 09:00 | 1.4518 | 1.7667 | 1.7286 | 1.8592 | 1.7612 | 1.8919 | 1.1917 | 2.0436 | 2.5217 | 2.5217 | 2.8404 | 2.8404 | 2019-05-05 21:00 | 1.7528 | 3.0079 | 5.0838 | 5.0838 | 5.0838 | 5.0838
2021-03-08 10:00 | 1.4089 | 1.7145 | 1.6775 | 1.8043 | 1.7092 | 1.836 | 1.4518 | 2.4896 | 3.072 | 3.072 | 3.4603 | 3.4603 | 2019-05-05 22:00 | 1.5547 | 2.6678 | 4.5091 | 4.5091 | 4.5091 | 4.5091
2021-03-08 11:00 | 1.4175 | 1.725 | 1.6878 | 1.8153 | 1.7196 | 1.8472 | 1.489 | 2.5533 | 3.1506 | 3.1506 | 3.5489 | 3.5489 | 2019-05-05 23:00 | 1.4327 | 2.4586 | 4.1555 | 4.1555 | 4.1555 | 4.1555
2021-03-08 12:00 | 1.4489 | 1.7632 | 1.7252 | 1.8556 | 1.7578 | 1.8882 | 1.5123 | 2.5934 | 3.2001 | 3.2001 | 3.6046 | 3.6046 | 2019-05-06 | 1.3642 | 2.3409 | 3.9565 | 3.9565 | 3.9565 | 3.9565
2021-03-08 13:00 | 1.4604 | 1.7771 | 1.7388 | 1.8702 | 1.7716 | 1.9031 | 1.5147 | 2.5974 | 3.2051 | 3.2051 | 3.6102 | 3.6102 | 2019-05-06 01:00 | 1.2879 | 2.2101 | 3.7355 | 3.7355 | 3.7355 | 3.7355
2021-03-08 14:00 | 1.4375 | 1.7493 | 1.7116 | 1.8409 | 1.7439 | 1.8733 | 1.5118 | 2.5925 | 3.199 | 3.199 | 3.6034 | 3.6034 | 2019-05-06 02:00 | 1.3718 | 2.354 | 3.9786 | 3.9786 | 3.9786 | 3.9786
2021-03-08 15:00 | 1.589 | 1.9336 | 1.8919 | 2.0349 | 1.9277 | 2.0707 | 1.5204 | 2.6072 | 3.2172 | 3.2172 | 3.6238 | 3.6238 | 2019-05-06 03:00 | 1.3108 | 2.2494 | 3.8018 | 3.8018 | 3.8018 | 3.8018
2021-03-08 16:00 | 1.489 | 1.8119 | 1.7728 | 1.9068 | 1.8063 | 1.9403 | 1.3289 | 2.2789 | 2.812 | 2.812 | 3.1674 | 3.1674 | 2019-05-06 04:00 | 1.3489 | 2.3148 | 3.9123 | 3.9123 | 3.9123 | 3.9123
2021-03-08 17:00 | 1.5961 | 1.9423 | 1.9004 | 2.0441 | 1.9363 | 2.08 | 1.4204 | 2.4357 | 3.0055 | 3.0055 | 3.3854 | 3.3854 | 2019-05-06 05:00 | 1.4937 | 2.5632 | 4.3323 | 4.3323 | 4.3323 | 4.3323
2021-03-08 18:00 | 1.8233 | 2.2188 | 2.1709 | 2.335 | 2.212 | 2.3761 | 1.5347 | 2.6317 | 3.2474 | 3.2474 | 3.6578 | 3.6578 | 2019-05-06 06:00 | 1.7376 | 2.9817 | 5.0396 | 5.0396 | 5.0396 | 5.0396
2021-03-08 19:00 | 1.8633 | 2.2675 | 2.2186 | 2.3863 | 2.2605 | 2.4282 | 1.5804 | 2.7101 | 3.3442 | 3.3442 | 3.7668 | 3.7668 | 2019-05-06 07:00 | 1.8138 | 3.1125 | 5.2606 | 5.2606 | 5.2606 | 5.2606
2021-03-08 20:00 | 1.8348 | 2.2327 | 2.1845 | 2.3497 | 2.2258 | 2.391 | 1.5518 | 2.6611 | 3.2837 | 3.2837 | 3.6987 | 3.6987 | 2019-05-06 08:00 | 1.9738 | 3.3871 | 5.7248 | 5.7248 | 5.7248 | 5.7248
2021-03-08 21:00 | 1.7319 | 2.1075 | 2.0621 | 2.2179 | 2.101 | 2.2569 | 1.4118 | 2.421 | 2.9874 | 2.9874 | 3.3649 | 3.3649 | 2019-05-06 09:00 | 2.0272 | 3.4787 | 5.8795 | 5.8795 | 5.8795 | 5.8795
2021-03-08 22:00 | 1.6154 | 1.9658 | 1.9234 | 2.0688 | 1.9597 | 2.1051 | 1.2117 | 2.0779 | 2.5641 | 2.5641 | 2.8881 | 2.8881 | 2019-05-06 10:00 | 2.0348 | 3.4917 | 5.9016 | 5.9016 | 5.9016 | 5.9016
2021-03-08 23:00 | 1.4518 | 1.7667 | 1.7286 | 1.8592 | 1.7612 | 1.8919 | 1.0498 | 1.8002 | 2.2213 | 2.2213 | 2.5021 | 2.5021 | 2019-05-06 11:00 | 2.0805 | 3.5702 | 6.0343 | 6.0343 | 6.0343 | 6.0343
2021-03-09 | 1.3613 | 1.6565 | 1.6208 | 1.7433 | 1.6514 | 1.7739 | 0.91744 | 1.5733 | 1.9413 | 1.9413 | 2.1867 | 2.1867 | 2019-05-06 12:00 | 2.1034 | 3.6094 | 6.1006 | 6.1006 | 6.1006 | 6.1006
2021-03-09 01:00 | 1.2291 | 1.4957 | 1.4634 | 1.5741 | 1.4911 | 1.6017 | 0.83164 | 1.4261 | 1.7598 | 1.7598 | 1.9822 | 1.9822 | 2019-05-06 13:00 | 2.1491 | 3.6879 | 6.2332 | 6.2332 | 6.2332 | 6.2332
2021-03-09 02:00 | 1.1889 | 1.4467 | 1.4155 | 1.5225 | 1.4423 | 1.5493 | 0.77448 | 1.3281 | 1.6388 | 1.6388 | 1.8459 | 1.8459 | 2019-05-06 14:00 | 2.2025 | 3.7795 | 6.3879 | 6.3879 | 6.3879 | 6.3879
2021-03-09 03:00 | 1.1603 | 1.412 | 1.3815 | 1.4859 | 1.4076 | 1.512 | 0.74876 | 1.284 | 1.5844 | 1.5844 | 1.7846 | 1.7846 | 2019-05-06 15:00 | 1.9967 | 3.4264 | 5.7911 | 5.7911 | 5.7911 | 5.7911
2021-03-09 04:00 | 1.2003 | 1.4607 | 1.4291 | 1.5372 | 1.4561 | 1.5642 | 0.71974 | 1.2342 | 1.523 | 1.523 | 1.7155 | 1.7155 | 2019-05-06 16:00 | 2.0043 | 3.4394 | 5.8132 | 5.8132 | 5.8132 | 5.8132
2021-03-09 05:00 | 1.3946 | 1.6971 | 1.6605 | 1.786 | 1.6919 | 1.8174 | 0.76019 | 1.3036 | 1.6086 | 1.6086 | 1.8119 | 1.8119 | 2019-05-06 17:00 | 2.0424 | 3.5048 | 5.9237 | 5.9237 | 5.9237 | 5.9237
2021-03-09 06:00 | 1.6136 | 1.9635 | 1.9212 | 2.0664 | 1.9575 | 2.1027 | 0.95453 | 1.6369 | 2.0198 | 2.0198 | 2.2751 | 2.2751 | 2019-05-06 18:00 | 2.0119 | 3.4525 | 5.8353 | 5.8353 | 5.8353 | 5.8353
2021-03-09 07:00 | 1.9434 | 2.3649 | 2.3139 | 2.4888 | 2.3576 | 2.5325 | 1.1946 | 2.0485 | 2.5278 | 2.5278 | 2.8473 | 2.8473 | 2019-05-06 19:00 | 1.9053 | 3.2694 | 5.5259 | 5.5259 | 5.5259 | 5.5259
2021-03-09 08:00 | 2.1291 | 2.5909 | 2.535 | 2.7266 | 2.5829 | 2.7746 | 1.2032 | 2.0632 | 2.5459 | 2.5459 | 2.8677 | 2.8677 | 2019-05-06 20:00 | 1.7452 | 2.9948 | 5.0617 | 5.0617 | 5.0617 | 5.0617
2021-03-09 09:00 | 2.1148 | 2.5735 | 2.518 | 2.7083 | 2.5656 | 2.7559 | 1.2117 | 2.0779 | 2.5641 | 2.5641 | 2.8881 | 2.8881 | 2019-05-06 21:00 | 1.6385 | 2.8117 | 4.7522 | 4.7522 | 4.7522 | 4.7522
2021-03-09 10:00 | 2.1491 | 2.6153 | 2.5588 | 2.7523 | 2.6072 | 2.8006 | 1.2889 | 2.2103 | 2.7273 | 2.7273 | 3.072 | 3.072 | 2019-05-06 22:00 | 1.6157 | 2.7725 | 4.6859 | 4.6859 | 4.6859 | 4.6859
2021-03-09 11:00 | 2.2006 | 2.6779 | 2.6201 | 2.8181 | 2.6696 | 2.8677 | 1.226 | 2.1024 | 2.5943 | 2.5943 | 2.9222 | 2.9222 | 2019-05-06 23:00 | 1.4404 | 2.4717 | 4.1776 | 4.1776 | 4.1776 | 4.1776
2021-03-09 12:00 | 2.172 | 2.6431 | 2.5861 | 2.7815 | 2.6349 | 2.8304 | 1.2603 | 2.1613 | 2.6669 | 2.6669 | 3.0039 | 3.0039 | 2019-05-07 | 1.4099 | 2.4194 | 4.0891 | 4.0891 | 4.0891 | 4.0891
2021-03-09 13:00 | 2.1977 | 2.6744 | 2.6167 | 2.8145 | 2.6661 | 2.8639 | 1.2803 | 2.1956 | 2.7092 | 2.7092 | 3.0516 | 3.0516 | 2019-05-07 01:00 | 1.3718 | 2.354 | 3.9786 | 3.9786 | 3.9786 | 3.9786
2021-03-09 14:00 | 2.2206 | 2.7022 | 2.6439 | 2.8438 | 2.6939 | 2.8937 | 1.2546 | 2.1515 | 2.6548 | 2.6548 | 2.9903 | 2.9903 | 2019-05-07 02:00 | 1.3413 | 2.3017 | 3.8902 | 3.8902 | 3.8902 | 3.8902
2021-03-09 15:00 | 2.2177 | 2.6987 | 2.6405 | 2.8401 | 2.6904 | 2.89 | 1.2517 | 2.1466 | 2.6487 | 2.6487 | 2.9835 | 2.9835 | 2019-05-07 03:00 | 1.3413 | 2.3017 | 3.8902 | 3.8902 | 3.8902 | 3.8902
2021-03-09 16:00 | 2.2663 | 2.7579 | 2.6984 | 2.9023 | 2.7494 | 2.9533 | 1.4146 | 2.4259 | 2.9934 | 2.9934 | 3.3718 | 3.3718 | 2019-05-07 04:00 | 1.4632 | 2.5109 | 4.2439 | 4.2439 | 4.2439 | 4.2439
2021-03-09 17:00 | 2.4435 | 2.9735 | 2.9093 | 3.1292 | 2.9643 | 3.1842 | 1.4918 | 2.5582 | 3.1567 | 3.1567 | 3.5557 | 3.5557 | 2019-05-07 05:00 | 1.5471 | 2.6548 | 4.487 | 4.487 | 4.487 | 4.487
2021-03-09 18:00 | 2.5664 | 3.123 | 3.0556 | 3.2866 | 3.1134 | 3.3444 | 1.609 | 2.7592 | 3.4046 | 3.4046 | 3.8349 | 3.8349 | 2019-05-07 06:00 | 1.7757 | 3.0471 | 5.1501 | 5.1501 | 5.1501 | 5.1501
2021-03-09 19:00 | 2.4521 | 2.9839 | 2.9195 | 3.1402 | 2.9747 | 3.1954 | 1.6204 | 2.7788 | 3.4288 | 3.4288 | 3.8622 | 3.8622 | 2019-05-07 07:00 | 1.8824 | 3.2302 | 5.4596 | 5.4596 | 5.4596 | 5.4596
2021-03-09 20:00 | 2.2206 | 2.7022 | 2.6439 | 2.8438 | 2.6939 | 2.8937 | 1.6661 | 2.8572 | 3.5256 | 3.5256 | 3.9712 | 3.9712 | 2019-05-07 08:00 | 2.111 | 3.6225 | 6.1227 | 6.1227 | 6.1227 | 6.1227
2021-03-09 21:00 | 2.0177 | 2.4553 | 2.4023 | 2.5839 | 2.4477 | 2.6293 | 1.4777 | 2.534 | 3.1268 | 3.1268 | 3.522 | 3.522 | 2019-05-07 09:00 | 2.1034 | 3.6094 | 6.1006 | 6.1006 | 6.1006 | 6.1006
2021-03-09 22:00 | 1.7475 | 2.1265 | 2.0807 | 2.2379 | 2.12 | 2.2773 | 1.3042 | 2.2366 | 2.7598 | 2.7598 | 3.1086 | 3.1086 | 2019-05-07 10:00 | 2.0882 | 3.5833 | 6.0564 | 6.0564 | 6.0564 | 6.0564
2021-03-09 23:00 | 1.5147 | 1.8432 | 1.8034 | 1.9398 | 1.8375 | 1.9738 | 1.1033 | 1.892 | 2.3346 | 2.3346 | 2.6297 | 2.6297 | 2019-05-07 11:00 | 2.111 | 3.6225 | 6.1227 | 6.1227 | 6.1227 | 6.1227
2021-03-10 | 1.3575 | 1.6519 | 1.6163 | 1.7385 | 1.6468 | 1.769 | 0.96313 | 1.6516 | 2.038 | 2.038 | 2.2956 | 2.2956 | 2019-05-07 12:00 | 2.1491 | 3.6879 | 6.2332 | 6.2332 | 6.2332 | 6.2332
2021-03-10 01:00 | 1.2546 | 1.5267 | 1.4938 | 1.6067 | 1.522 | 1.6349 | 0.87451 | 1.4996 | 1.8505 | 1.8505 | 2.0844 | 2.0844 | 2019-05-07 13:00 | 2.0577 | 3.531 | 5.9679 | 5.9679 | 5.9679 | 5.9679
2021-03-10 02:00 | 1.1832 | 1.4398 | 1.4087 | 1.5152 | 1.4353 | 1.5418 | 0.76594 | 1.3135 | 1.6207 | 1.6207 | 1.8256 | 1.8256 | 2019-05-07 14:00 | 1.9967 | 3.4264 | 5.7911 | 5.7911 | 5.7911 | 5.7911
2021-03-10 03:00 | 1.1632 | 1.4154 | 1.3849 | 1.4896 | 1.4111 | 1.5158 | 0.71733 | 1.2301 | 1.5179 | 1.5179 | 1.7097 | 1.7097 | 2019-05-07 15:00 | 2.1263 | 3.6487 | 6.1669 | 6.1669 | 6.1669 | 6.1669
2021-03-10 04:00 | 1.183 | 1.4396 | 1.4086 | 1.5151 | 1.4352 | 1.5417 | 0.70018 | 1.2007 | 1.4816 | 1.4816 | 1.6688 | 1.6688 | 2019-05-07 16:00 | 2.111 | 3.6225 | 6.1227 | 6.1227 | 6.1227 | 6.1227
2021-03-10 05:00 | 1.3946 | 1.6971 | 1.6605 | 1.786 | 1.6919 | 1.8174 | 0.79449 | 1.3624 | 1.6811 | 1.6811 | 1.8936 | 1.8936 | 2019-05-07 17:00 | 2.1644 | 3.7141 | 6.2774 | 6.2774 | 6.2774 | 6.2774
2021-03-10 06:00 | 1.6747 | 2.038 | 1.994 | 2.1447 | 2.0317 | 2.1824 | 0.92549 | 1.5871 | 1.9584 | 1.9584 | 2.2059 | 2.2059 | 2019-05-07 18:00 | 2.1415 | 3.6748 | 6.2111 | 6.2111 | 6.2111 | 6.2111
2021-03-10 07:00 | 1.9719 | 2.3996 | 2.3479 | 2.5254 | 2.3922 | 2.5697 | 1.2718 | 2.1809 | 2.691 | 2.691 | 3.0312 | 3.0312 | 2019-05-07 19:00 | 2.0196 | 3.4656 | 5.8574 | 5.8574 | 5.8574 | 5.8574
2021-03-10 08:00 | 2.112 | 2.5701 | 2.5146 | 2.7047 | 2.5621 | 2.7522 | 1.3432 | 2.3034 | 2.8422 | 2.8422 | 3.2015 | 3.2015 | 2019-05-07 20:00 | 1.8748 | 3.2171 | 5.4375 | 5.4375 | 5.4375 | 5.4375
2021-03-10 09:00 | 2.1177 | 2.577 | 2.5214 | 2.712 | 2.5691 | 2.7597 | 1.3546 | 2.323 | 2.8664 | 2.8664 | 3.2287 | 3.2287 | 2019-05-07 21:00 | 1.7223 | 2.9556 | 4.9954 | 4.9954 | 4.9954 | 4.9954
2021-03-10 10:00 | 2.2463 | 2.7335 | 2.6745 | 2.8767 | 2.7251 | 2.9272 | 1.3832 | 2.372 | 2.9269 | 2.9269 | 3.2968 | 3.2968 | 2019-05-07 22:00 | 1.7071 | 2.9294 | 4.9512 | 4.9512 | 4.9512 | 4.9512
2021-03-10 11:00 | 2.3177 | 2.8205 | 2.7596 | 2.9682 | 2.8118 | 3.0204 | 1.3375 | 2.2936 | 2.8301 | 2.8301 | 3.1878 | 3.1878 | 2019-05-07 23:00 | 1.5242 | 2.6155 | 4.4207 | 4.4207 | 4.4207 | 4.4207
2021-03-10 12:00 | 2.3635 | 2.8761 | 2.8141 | 3.0268 | 2.8672 | 3.0799 | 1.2689 | 2.176 | 2.685 | 2.685 | 3.0244 | 3.0244 | 2019-05-08 | 1.3718 | 2.354 | 3.9786 | 3.9786 | 3.9786 | 3.9786
2021-03-10 13:00 | 2.2777 | 2.7718 | 2.712 | 2.917 | 2.7632 | 2.9682 | 1.3661 | 2.3426 | 2.8906 | 2.8906 | 3.256 | 3.256 | 2019-05-08 01:00 | 1.4251 | 2.4455 | 4.1333 | 4.1333 | 4.1333 | 4.1333
2021-03-10 14:00 | 2.3663 | 2.8796 | 2.8175 | 3.0304 | 2.8707 | 3.0837 | 1.3232 | 2.2691 | 2.7999 | 2.7999 | 3.1538 | 3.1538 | 2019-05-08 02:00 | 1.3642 | 2.3409 | 3.9565 | 3.9565 | 3.9565 | 3.9565
2021-03-10 15:00 | 2.3149 | 2.817 | 2.7562 | 2.9645 | 2.8083 | 3.0166 | 1.3889 | 2.3818 | 2.939 | 2.939 | 3.3105 | 3.3105 | 2019-05-08 03:00 | 1.3642 | 2.3409 | 3.9565 | 3.9565 | 3.9565 | 3.9565
2021-03-10 16:00 | 2.5178 | 3.0639 | 2.9978 | 3.2244 | 3.0545 | 3.2811 | 1.4232 | 2.4406 | 3.0116 | 3.0116 | 3.3922 | 3.3922 | 2019-05-08 04:00 | 1.5013 | 2.5763 | 4.3544 | 4.3544 | 4.3544 | 4.3544
2021-03-10 17:00 | 2.5778 | 3.1369 | 3.0693 | 3.3013 | 3.1273 | 3.3593 | 1.5661 | 2.6856 | 3.3139 | 3.3139 | 3.7328 | 3.7328 | 2019-05-08 05:00 | 1.5699 | 2.694 | 4.5533 | 4.5533 | 4.5533 | 4.5533
2021-03-10 18:00 | 2.4492 | 2.9804 | 2.9161 | 3.1366 | 2.9712 | 3.1917 | 1.5804 | 2.7101 | 3.3442 | 3.3442 | 3.7668 | 3.7668 | 2019-05-08 06:00 | 1.8671 | 3.204 | 5.4154 | 5.4154 | 5.4154 | 5.4154
2021-03-10 19:00 | 2.293 | 2.7904 | 2.7302 | 2.9365 | 2.7818 | 2.9881 | 1.5861 | 2.7199 | 3.3563 | 3.3563 | 3.7805 | 3.7805 | 2019-05-08 07:00 | 1.9662 | 3.374 | 5.7027 | 5.7027 | 5.7027 | 5.7027
2021-03-10 20:00 | 2.2463 | 2.7335 | 2.6745 | 2.8767 | 2.7251 | 2.9272 | 1.549 | 2.6562 | 3.2776 | 3.2776 | 3.6919 | 3.6919 | 2019-05-08 08:00 | 2.1644 | 3.7141 | 6.2774 | 6.2774 | 6.2774 | 6.2774
2021-03-10 21:00 | 2.0891 | 2.5422 | 2.4874 | 2.6754 | 2.5344 | 2.7224 | 1.4632 | 2.5092 | 3.0962 | 3.0962 | 3.4876 | 3.4876 | 2019-05-08 09:00 | 2.1339 | 3.6618 | 6.189 | 6.189 | 6.189 | 6.189
2021-03-10 22:00 | 1.8605 | 2.264 | 2.2152 | 2.3826 | 2.257 | 2.4245 | 1.2832 | 2.2005 | 2.7152 | 2.7152 | 3.0584 | 3.0584 | 2019-05-08 10:00 | 2.0958 | 3.5964 | 6.0785 | 6.0785 | 6.0785 | 6.0785
2021-03-10 23:00 | 1.6176 | 1.9684 | 1.9259 | 2.0715 | 1.9623 | 2.1079 | 1.0974 | 1.8819 | 2.3222 | 2.3222 | 2.6157 | 2.6157 | 2019-05-08 11:00 | 2.1491 | 3.6879 | 6.2332 | 6.2332 | 6.2332 | 6.2332
2021-03-11 | 1.3861 | 1.6867 | 1.6503 | 1.7751 | 1.6815 | 1.8063 | 0.96322 | 1.6518 | 2.0382 | 2.0382 | 2.2958 | 2.2958 | 2019-05-08 12:00 | 2.1339 | 3.6618 | 6.189 | 6.189 | 6.189 | 6.189
2021-03-11 01:00 | 1.2575 | 1.5302 | 1.4972 | 1.6104 | 1.5255 | 1.6387 | 0.84307 | 1.4457 | 1.7839 | 1.7839 | 2.0094 | 2.0094 | 2019-05-08 13:00 | 2.0882 | 3.5833 | 6.0564 | 6.0564 | 6.0564 | 6.0564
2021-03-11 02:00 | 1.2517 | 1.5232 | 1.4904 | 1.603 | 1.5186 | 1.6312 | 0.79449 | 1.3624 | 1.6811 | 1.6811 | 1.8936 | 1.8936 | 2019-05-08 14:00 | 2.1034 | 3.6094 | 6.1006 | 6.1006 | 6.1006 | 6.1006
2021-03-11 03:00 | 1.2317 | 1.4989 | 1.4666 | 1.5774 | 1.4943 | 1.6051 | 0.69731 | 1.1958 | 1.4755 | 1.4755 | 1.662 | 1.662 | 2019-05-08 15:00 | 2.0805 | 3.5702 | 6.0343 | 6.0343 | 6.0343 | 6.0343
2021-03-11 04:00 | 1.2757 | 1.5524 | 1.5189 | 1.6338 | 1.5476 | 1.6625 | 0.76019 | 1.3036 | 1.6086 | 1.6086 | 1.8119 | 1.8119 | 2019-05-08 16:00 | 2.1949 | 3.7664 | 6.3658 | 6.3658 | 6.3658 | 6.3658
2021-03-11 05:00 | 1.4347 | 1.7458 | 1.7082 | 1.8373 | 1.7404 | 1.8696 | 0.79987 | 1.3717 | 1.6925 | 1.6925 | 1.9065 | 1.9065 | 2019-05-08 17:00 | 2.2177 | 3.8056 | 6.4321 | 6.4321 | 6.4321 | 6.4321
2021-03-11 06:00 | 1.669 | 2.031 | 1.9872 | 2.1374 | 2.0247 | 2.175 | 1.0003 | 1.7153 | 2.1166 | 2.1166 | 2.3841 | 2.3841 | 2019-05-08 18:00 | 2.111 | 3.6225 | 6.1227 | 6.1227 | 6.1227 | 6.1227
2021-03-11 07:00 | 1.9748 | 2.4031 | 2.3513 | 2.529 | 2.3957 | 2.5734 | 1.266 | 2.1711 | 2.679 | 2.679 | 3.0176 | 3.0176 | 2019-05-08 19:00 | 2.0119 | 3.4525 | 5.8353 | 5.8353 | 5.8353 | 5.8353
2021-03-11 08:00 | 2.2892 | 2.7857 | 2.7256 | 2.9316 | 2.7771 | 2.9831 | 1.2689 | 2.176 | 2.685 | 2.685 | 3.0244 | 3.0244 | 2019-05-08 20:00 | 1.8824 | 3.2302 | 5.4596 | 5.4596 | 5.4596 | 5.4596
2021-03-11 09:00 | 2.2949 | 2.7926 | 2.7324 | 2.9389 | 2.784 | 2.9906 | 1.3032 | 2.2348 | 2.7576 | 2.7576 | 3.1061 | 3.1061 | 2019-05-08 21:00 | 1.7986 | 3.0863 | 5.2164 | 5.2164 | 5.2164 | 5.2164
2021-03-11 10:00 | 2.3835 | 2.9004 | 2.8379 | 3.0524 | 2.8915 | 3.106 | 1.3889 | 2.3818 | 2.939 | 2.939 | 3.3105 | 3.3105 | 2019-05-08 22:00 | 1.669 | 2.864 | 4.8407 | 4.8407 | 4.8407 | 4.8407
2021-03-11 11:00 | 2.4063 | 2.9283 | 2.8651 | 3.0817 | 2.9192 | 3.1358 | 1.4461 | 2.4798 | 3.0599 | 3.0599 | 3.4467 | 3.4467 | 2019-05-08 23:00 | 1.5013 | 2.5763 | 4.3544 | 4.3544 | 4.3544 | 4.3544
2021-03-11 12:00 | 2.4749 | 3.0117 | 2.9468 | 3.1695 | 3.0024 | 3.2252 | 1.4004 | 2.4014 | 2.9632 | 2.9632 | 3.3377 | 3.3377 | 2019-05-09 | 1.448 | 2.4848 | 4.1997 | 4.1997 | 4.1997 | 4.1997
2021-03-11 13:00 | 2.4435 | 2.9735 | 2.9093 | 3.1292 | 2.9643 | 3.1842 | 1.3461 | 2.3083 | 2.8483 | 2.8483 | 3.2083 | 3.2083 | 2019-05-09 01:00 | 1.4327 | 2.4586 | 4.1555 | 4.1555 | 4.1555 | 4.1555
2021-03-11 14:00 | 2.635 | 3.2065 | 3.1373 | 3.3745 | 3.1966 | 3.4337 | 1.4489 | 2.4847 | 3.066 | 3.066 | 3.4535 | 3.4535 | 2019-05-09 02:00 | 1.3413 | 2.3017 | 3.8902 | 3.8902 | 3.8902 | 3.8902
2021-03-11 15:00 | 2.4835 | 3.0222 | 2.957 | 3.1805 | 3.0128 | 3.2364 | 1.3461 | 2.3083 | 2.8483 | 2.8483 | 3.2083 | 3.2083 | 2019-05-09 03:00 | 1.3413 | 2.3017 | 3.8902 | 3.8902 | 3.8902 | 3.8902
2021-03-11 16:00 | 2.2892 | 2.7857 | 2.7256 | 2.9316 | 2.7771 | 2.9831 | 1.3088 | 2.2445 | 2.7695 | 2.7695 | 3.1196 | 3.1196 | 2019-05-09 04:00 | 1.3946 | 2.3932 | 4.0449 | 4.0449 | 4.0449 | 4.0449
2021-03-11 17:00 | 2.2206 | 2.7022 | 2.6439 | 2.8438 | 2.6939 | 2.8937 | 1.4632 | 2.5092 | 3.0962 | 3.0962 | 3.4876 | 3.4876 | 2019-05-09 05:00 | 1.5852 | 2.7202 | 4.5975 | 4.5975 | 4.5975 | 4.5975
2021-03-11 18:00 | 2.2406 | 2.7266 | 2.6677 | 2.8694 | 2.7181 | 2.9198 | 1.5518 | 2.6611 | 3.2837 | 3.2837 | 3.6987 | 3.6987 | 2019-05-09 06:00 | 1.89 | 3.2433 | 5.4817 | 5.4817 | 5.4817 | 5.4817
2021-03-11 19:00 | 2.2149 | 2.6953 | 2.6371 | 2.8364 | 2.6869 | 2.8863 | 1.5861 | 2.7199 | 3.3563 | 3.3563 | 3.7805 | 3.7805 | 2019-05-09 07:00 | 1.9891 | 3.4133 | 5.769 | 5.769 | 5.769 | 5.769
2021-03-11 20:00 | 2.0634 | 2.5109 | 2.4568 | 2.6425 | 2.5032 | 2.6889 | 1.5433 | 2.6464 | 3.2655 | 3.2655 | 3.6783 | 3.6783 | 2019-05-09 08:00 | 2.1796 | 3.7402 | 6.3216 | 6.3216 | 6.3216 | 6.3216
2021-03-11 21:00 | 1.8862 | 2.2953 | 2.2458 | 2.4156 | 2.2882 | 2.458 | 1.4689 | 2.519 | 3.1083 | 3.1083 | 3.5012 | 3.5012 | 2019-05-09 09:00 | 2.1034 | 3.6094 | 6.1006 | 6.1006 | 6.1006 | 6.1006
2021-03-11 22:00 | 1.6976 | 2.0658 | 2.0212 | 2.174 | 2.0594 | 2.2122 | 1.2718 | 2.181 | 2.6912 | 2.6912 | 3.0313 | 3.0313 | 2019-05-09 10:00 | 2.1644 | 3.7141 | 6.2774 | 6.2774 | 6.2774 | 6.2774
2021-03-11 23:00 | 1.4404 | 1.7528 | 1.715 | 1.8446 | 1.7474 | 1.877 | 1.0613 | 1.8199 | 2.2457 | 2.2457 | 2.5295 | 2.5295 | 2019-05-09 11:00 | 2.172 | 3.7271 | 6.2995 | 6.2995 | 6.2995 | 6.2995
2021-03-12 | 1.3149 | 1.6001 | 1.5656 | 1.6839 | 1.5952 | 1.7135 | 0.88887 | 1.5243 | 1.8809 | 1.8809 | 2.1186 | 2.1186 | 2019-05-09 12:00 | 2.1186 | 3.6356 | 6.1448 | 6.1448 | 6.1448 | 6.1448
2021-03-12 01:00 | 1.2632 | 1.5372 | 1.504 | 1.6177 | 1.5324 | 1.6461 | 0.80306 | 1.3771 | 1.6993 | 1.6993 | 1.9141 | 1.9141 | 2019-05-09 13:00 | 2.0501 | 3.5179 | 5.9458 | 5.9458 | 5.9458 | 5.9458
2021-03-12 02:00 | 1.1918 | 1.4503 | 1.419 | 1.5262 | 1.4458 | 1.5531 | 0.72876 | 1.2497 | 1.5421 | 1.5421 | 1.737 | 1.737 | 2019-05-09 14:00 | 2.0958 | 3.5964 | 6.0785 | 6.0785 | 6.0785 | 6.0785
2021-03-12 03:00 | 1.2346 | 1.5024 | 1.47 | 1.5811 | 1.4978 | 1.6089 | 0.70589 | 1.2105 | 1.4937 | 1.4937 | 1.6825 | 1.6825 | 2019-05-09 15:00 | 2.0653 | 3.5441 | 5.99 | 5.99 | 5.99 | 5.99
2021-03-12 04:00 | 1.206 | 1.4675 | 1.4359 | 1.5444 | 1.463 | 1.5716 | 0.69517 | 1.1921 | 1.471 | 1.471 | 1.6569 | 1.6569 | 2019-05-09 16:00 | 2.0424 | 3.5048 | 5.9237 | 5.9237 | 5.9237 | 5.9237
2021-03-12 05:00 | 1.3717 | 1.6692 | 1.6332 | 1.7567 | 1.6641 | 1.7875 | 0.75734 | 1.2987 | 1.6025 | 1.6025 | 1.8051 | 1.8051 | 2019-05-09 17:00 | 2.2253 | 3.8187 | 6.4542 | 6.4542 | 6.4542 | 6.4542
2021-03-12 06:00 | 1.7365 | 2.1131 | 2.0675 | 2.2238 | 2.1066 | 2.2629 | 0.99434 | 1.7051 | 2.104 | 2.104 | 2.37 | 2.37 | 2019-05-09 18:00 | 2.111 | 3.6225 | 6.1227 | 6.1227 | 6.1227 | 6.1227
2021-03-12 07:00 | 1.9234 | 2.3405 | 2.29 | 2.4631 | 2.3333 | 2.5064 | 1.2232 | 2.0975 | 2.5882 | 2.5882 | 2.9154 | 2.9154 | 2019-05-09 19:00 | 2.0882 | 3.5833 | 6.0564 | 6.0564 | 6.0564 | 6.0564
2021-03-12 08:00 | 2.2434 | 2.73 | 2.6711 | 2.873 | 2.7216 | 2.9235 | 1.2975 | 2.225 | 2.7455 | 2.7455 | 3.0925 | 3.0925 | 2019-05-09 20:00 | 1.9586 | 3.361 | 5.6806 | 5.6806 | 5.6806 | 5.6806
2021-03-12 09:00 | 2.2634 | 2.7544 | 2.695 | 2.8987 | 2.7459 | 2.9496 | 1.2975 | 2.225 | 2.7455 | 2.7455 | 3.0925 | 3.0925 | 2019-05-09 21:00 | 1.89 | 3.2433 | 5.4817 | 5.4817 | 5.4817 | 5.4817
2021-03-12 10:00 | 2.3235 | 2.8274 | 2.7664 | 2.9755 | 2.8187 | 3.0278 | 1.3746 | 2.3573 | 2.9088 | 2.9088 | 3.2764 | 3.2764 | 2019-05-09 22:00 | 1.8062 | 3.0994 | 5.2385 | 5.2385 | 5.2385 | 5.2385
2021-03-12 11:00 | 2.4349 | 2.963 | 2.8991 | 3.1183 | 2.9539 | 3.173 | 1.4261 | 2.4455 | 3.0176 | 3.0176 | 3.399 | 3.399 | 2019-05-09 23:00 | 1.5775 | 2.7071 | 4.5754 | 4.5754 | 4.5754 | 4.5754
2021-03-12 12:00 | 2.3692 | 2.8831 | 2.8209 | 3.0341 | 2.8742 | 3.0874 | 1.3632 | 2.3377 | 2.8846 | 2.8846 | 3.2491 | 3.2491 | 2019-05-10 | 1.4175 | 2.4324 | 4.1112 | 4.1112 | 4.1112 | 4.1112
2021-03-12 13:00 | 2.4549 | 2.9874 | 2.9229 | 3.1439 | 2.9782 | 3.1991 | 1.4232 | 2.4406 | 3.0116 | 3.0116 | 3.3922 | 3.3922 | 2019-05-10 01:00 | 1.4175 | 2.4324 | 4.1112 | 4.1112 | 4.1112 | 4.1112
2021-03-12 14:00 | 2.4206 | 2.9456 | 2.8821 | 3.1 | 2.9366 | 3.1544 | 1.4318 | 2.4553 | 3.0297 | 3.0297 | 3.4126 | 3.4126 | 2019-05-10 02:00 | 1.3794 | 2.3671 | 4.0007 | 4.0007 | 4.0007 | 4.0007
2021-03-12 15:00 | 2.3778 | 2.8935 | 2.8311 | 3.0451 | 2.8846 | 3.0986 | 1.4375 | 2.4651 | 3.0418 | 3.0418 | 3.4262 | 3.4262 | 2019-05-10 03:00 | 1.3642 | 2.3409 | 3.9565 | 3.9565 | 3.9565 | 3.9565
2021-03-12 16:00 | 2.3292 | 2.8344 | 2.7732 | 2.9828 | 2.8256 | 3.0353 | 1.4175 | 2.4308 | 2.9995 | 2.9995 | 3.3786 | 3.3786 | 2019-05-10 04:00 | 1.4175 | 2.4324 | 4.1112 | 4.1112 | 4.1112 | 4.1112
2021-03-12 17:00 | 2.2263 | 2.7092 | 2.6507 | 2.8511 | 2.7008 | 2.9012 | 1.5204 | 2.6072 | 3.2172 | 3.2172 | 3.6238 | 3.6238 | 2019-05-10 05:00 | 1.5623 | 2.6809 | 4.5312 | 4.5312 | 4.5312 | 4.5312
2021-03-12 18:00 | 2.292 | 2.7892 | 2.729 | 2.9353 | 2.7806 | 2.9868 | 1.6061 | 2.7543 | 3.3986 | 3.3986 | 3.8281 | 3.8281 | 2019-05-10 06:00 | 1.8138 | 3.1125 | 5.2606 | 5.2606 | 5.2606 | 5.2606
2021-03-12 19:00 | 2.1005 | 2.5561 | 2.501 | 2.69 | 2.5483 | 2.7373 | 1.6804 | 2.8817 | 3.5558 | 3.5558 | 4.0052 | 4.0052 | 2019-05-10 07:00 | 1.9662 | 3.374 | 5.7027 | 5.7027 | 5.7027 | 5.7027
2021-03-12 20:00 | 1.9662 | 2.3927 | 2.3411 | 2.5181 | 2.3853 | 2.5623 | 1.6719 | 2.867 | 3.5377 | 3.5377 | 3.9848 | 3.9848 | 2019-05-10 08:00 | 2.2253 | 3.8187 | 6.4542 | 6.4542 | 6.4542 | 6.4542
2021-03-12 21:00 | 1.8062 | 2.1979 | 2.1505 | 2.3131 | 2.1912 | 2.3537 | 1.5433 | 2.6464 | 3.2655 | 3.2655 | 3.6783 | 3.6783 | 2019-05-10 09:00 | 2.0653 | 3.5441 | 5.99 | 5.99 | 5.99 | 5.99
2021-03-12 22:00 | 1.6261 | 1.9788 | 1.9361 | 2.0825 | 1.9727 | 2.1191 | 1.4461 | 2.4798 | 3.0599 | 3.0599 | 3.4467 | 3.4467 | 2019-05-10 10:00 | 2.0119 | 3.4525 | 5.8353 | 5.8353 | 5.8353 | 5.8353
2021-03-12 23:00 | 1.5518 | 1.8884 | 1.8477 | 1.9873 | 1.8826 | 2.0223 | 1.1889 | 2.0387 | 2.5157 | 2.5157 | 2.8336 | 2.8336 | 2019-05-10 11:00 | 2.1339 | 3.6618 | 6.189 | 6.189 | 6.189 | 6.189
2021-03-13 | 1.4176 | 1.725 | 1.6878 | 1.8154 | 1.7197 | 1.8473 | 1.0431 | 1.7888 | 2.2073 | 2.2073 | 2.4863 | 2.4863 | 2019-05-10 12:00 | 2.1796 | 3.7402 | 6.3216 | 6.3216 | 6.3216 | 6.3216
2021-03-13 01:00 | 1.2803 | 1.558 | 1.5244 | 1.6396 | 1.5532 | 1.6685 | 0.87737 | 1.5045 | 1.8565 | 1.8565 | 2.0912 | 2.0912 | 2019-05-10 13:00 | 2.1263 | 3.6487 | 6.1669 | 6.1669 | 6.1669 | 6.1669
2021-03-13 02:00 | 1.2318 | 1.4989 | 1.4666 | 1.5775 | 1.4943 | 1.6052 | 0.84036 | 1.4411 | 1.7782 | 1.7782 | 2.003 | 2.003 | 2019-05-10 14:00 | 2.2101 | 3.7925 | 6.41 | 6.41 | 6.41 | 6.41
2021-03-13 03:00 | 1.2117 | 1.4745 | 1.4427 | 1.5518 | 1.47 | 1.579 | 0.7632 | 1.3088 | 1.6149 | 1.6149 | 1.8191 | 1.8191 | 2019-05-10 15:00 | 2.1567 | 3.701 | 6.2553 | 6.2553 | 6.2553 | 6.2553
2021-03-13 04:00 | 1.2623 | 1.5361 | 1.5029 | 1.6165 | 1.5313 | 1.6449 | 0.75448 | 1.2938 | 1.5965 | 1.5965 | 1.7983 | 1.7983 | 2019-05-10 16:00 | 2.1949 | 3.7664 | 6.3658 | 6.3658 | 6.3658 | 6.3658
2021-03-13 05:00 | 1.3146 | 1.5998 | 1.5653 | 1.6836 | 1.5948 | 1.7131 | 0.72874 | 1.2497 | 1.542 | 1.542 | 1.7369 | 1.7369 | 2019-05-10 17:00 | 2.1034 | 3.6094 | 6.1006 | 6.1006 | 6.1006 | 6.1006
2021-03-13 06:00 | 1.3718 | 1.6693 | 1.6333 | 1.7568 | 1.6642 | 1.7876 | 0.80306 | 1.3771 | 1.6993 | 1.6993 | 1.9141 | 1.9141 | 2019-05-10 18:00 | 2.0196 | 3.4656 | 5.8574 | 5.8574 | 5.8574 | 5.8574
2021-03-13 07:00 | 1.5947 | 1.9406 | 1.8987 | 2.0422 | 1.9346 | 2.0781 | 1.0346 | 1.7741 | 2.1891 | 2.1891 | 2.4658 | 2.4658 | 2019-05-10 19:00 | 2.0196 | 3.4656 | 5.8574 | 5.8574 | 5.8574 | 5.8574
2021-03-13 08:00 | 1.6661 | 2.0275 | 1.9838 | 2.1337 | 2.0213 | 2.1712 | 1.2517 | 2.1466 | 2.6487 | 2.6487 | 2.9835 | 2.9835 | 2019-05-10 20:00 | 1.7681 | 3.034 | 5.128 | 5.128 | 5.128 | 5.128
2021-03-13 09:00 | 1.7233 | 2.0971 | 2.0518 | 2.2069 | 2.0906 | 2.2457 | 1.3175 | 2.2593 | 2.7878 | 2.7878 | 3.1402 | 3.1402 | 2019-05-10 21:00 | 1.6842 | 2.8902 | 4.8849 | 4.8849 | 4.8849 | 4.8849
2021-03-13 10:00 | 1.8222 | 2.2175 | 2.1696 | 2.3336 | 2.2106 | 2.3746 | 1.5833 | 2.715 | 3.3502 | 3.3502 | 3.7736 | 3.7736 | 2019-05-10 22:00 | 1.7681 | 3.034 | 5.128 | 5.128 | 5.128 | 5.128
2021-03-13 11:00 | 1.8348 | 2.2327 | 2.1845 | 2.3497 | 2.2258 | 2.391 | 1.5604 | 2.6758 | 3.3018 | 3.3018 | 3.7192 | 3.7192 | 2019-05-10 23:00 | 1.6385 | 2.8117 | 4.7522 | 4.7522 | 4.7522 | 4.7522
2021-03-13 12:00 | 1.8433 | 2.2431 | 2.1948 | 2.3607 | 2.2362 | 2.4021 | 1.5518 | 2.6611 | 3.2837 | 3.2837 | 3.6987 | 3.6987 | 2019-05-11 | 1.5013 | 2.5763 | 4.3544 | 4.3544 | 4.3544 | 4.3544
2021-03-13 13:00 | 1.9576 | 2.3823 | 2.3309 | 2.5071 | 2.3749 | 2.5511 | 1.6519 | 2.8327 | 3.4953 | 3.4953 | 3.9371 | 3.9371 | 2019-05-11 01:00 | 1.4556 | 2.4978 | 4.2218 | 4.2218 | 4.2218 | 4.2218
2021-03-13 14:00 | 1.9176 | 2.3336 | 2.2832 | 2.4558 | 2.3264 | 2.499 | 1.6547 | 2.8376 | 3.5014 | 3.5014 | 3.9439 | 3.9439 | 2019-05-11 02:00 | 1.4251 | 2.4455 | 4.1333 | 4.1333 | 4.1333 | 4.1333
2021-03-13 15:00 | 1.9348 | 2.3544 | 2.3036 | 2.4778 | 2.3472 | 2.5213 | 1.6804 | 2.8817 | 3.5558 | 3.5558 | 4.0052 | 4.0052 | 2019-05-11 03:00 | 1.4404 | 2.4717 | 4.1776 | 4.1776 | 4.1776 | 4.1776
2021-03-13 16:00 | 1.9777 | 2.4066 | 2.3547 | 2.5327 | 2.3992 | 2.5772 | 1.6433 | 2.818 | 3.4772 | 3.4772 | 3.9167 | 3.9167 | 2019-05-11 04:00 | 1.4023 | 2.4063 | 4.067 | 4.067 | 4.067 | 4.067
2021-03-13 17:00 | 2.0177 | 2.4553 | 2.4023 | 2.5839 | 2.4477 | 2.6293 | 1.6433 | 2.818 | 3.4772 | 3.4772 | 3.9167 | 3.9167 | 2019-05-11 05:00 | 1.5242 | 2.6155 | 4.4207 | 4.4207 | 4.4207 | 4.4207
2021-03-13 18:00 | 2.072 | 2.5214 | 2.467 | 2.6535 | 2.5136 | 2.7001 | 1.8262 | 3.1316 | 3.8642 | 3.8642 | 4.3526 | 4.3526 | 2019-05-11 06:00 | 1.5775 | 2.7071 | 4.5754 | 4.5754 | 4.5754 | 4.5754
2021-03-13 19:00 | 1.9605 | 2.3857 | 2.3343 | 2.5107 | 2.3784 | 2.5548 | 1.6797 | 2.8805 | 3.5544 | 3.5544 | 4.0036 | 4.0036 | 2019-05-11 07:00 | 1.7757 | 3.0471 | 5.1501 | 5.1501 | 5.1501 | 5.1501
2021-03-13 20:00 | 1.9805 | 2.4101 | 2.3581 | 2.5363 | 2.4026 | 2.5809 | 1.5861 | 2.7199 | 3.3563 | 3.3563 | 3.7805 | 3.7805 | 2019-05-11 08:00 | 1.9357 | 3.3217 | 5.6143 | 5.6143 | 5.6143 | 5.6143
2021-03-13 21:00 | 1.8748 | 2.2814 | 2.2322 | 2.4009 | 2.2744 | 2.4431 | 1.4947 | 2.5631 | 3.1627 | 3.1627 | 3.5625 | 3.5625 | 2019-05-11 09:00 | 1.9662 | 3.374 | 5.7027 | 5.7027 | 5.7027 | 5.7027
2021-03-13 22:00 | 1.7805 | 2.1666 | 2.1199 | 2.2801 | 2.16 | 2.3202 | 1.3832 | 2.372 | 2.9269 | 2.9269 | 3.2968 | 3.2968 | 2019-05-11 10:00 | 1.9662 | 3.374 | 5.7027 | 5.7027 | 5.7027 | 5.7027
2021-03-13 23:00 | 1.7347 | 2.111 | 2.0655 | 2.2216 | 2.1045 | 2.2606 | 1.2432 | 2.1318 | 2.6306 | 2.6306 | 2.9631 | 2.9631 | 2019-05-11 11:00 | 2.0043 | 3.4394 | 5.8132 | 5.8132 | 5.8132 | 5.8132
2021-03-14 | 1.5804 | 1.9232 | 1.8817 | 2.0239 | 1.9173 | 2.0595 | 1.1574 | 1.9848 | 2.4492 | 2.4492 | 2.7587 | 2.7587 | 2019-05-11 12:00 | 1.9815 | 3.4002 | 5.7469 | 5.7469 | 5.7469 | 5.7469
2021-03-14 01:00 | 1.3634 | 1.6591 | 1.6233 | 1.746 | 1.654 | 1.7767 | 0.84307 | 1.4457 | 1.7839 | 1.7839 | 2.0094 | 2.0094 | 2019-05-11 13:00 | 1.9662 | 3.374 | 5.7027 | 5.7027 | 5.7027 | 5.7027
2021-03-14 02:00 | 1.2966 | 1.5778 | 1.5438 | 1.6605 | 1.573 | 1.6897 | 0.83164 | 1.4261 | 1.7598 | 1.7598 | 1.9822 | 1.9822 | 2019-05-11 14:00 | 1.9967 | 3.4264 | 5.7911 | 5.7911 | 5.7911 | 5.7911
2021-03-14 03:00 | 1.2434 | 1.513 | 1.4804 | 1.5923 | 1.5084 | 1.6203 | 0.78306 | 1.3428 | 1.657 | 1.657 | 1.8664 | 1.8664 | 2019-05-11 15:00 | 2.0501 | 3.5179 | 5.9458 | 5.9458 | 5.9458 | 5.9458
2021-03-14 04:00 | 1.286 | 1.565 | 1.5312 | 1.647 | 1.5602 | 1.6759 | 0.76305 | 1.3085 | 1.6146 | 1.6146 | 1.8187 | 1.8187 | 2019-05-11 16:00 | 2.0577 | 3.531 | 5.9679 | 5.9679 | 5.9679 | 5.9679
2021-03-14 05:00 | 1.2752 | 1.5518 | 1.5183 | 1.6331 | 1.547 | 1.6618 | 0.78877 | 1.3526 | 1.6691 | 1.6691 | 1.88 | 1.88 | 2019-05-11 17:00 | 2.1034 | 3.6094 | 6.1006 | 6.1006 | 6.1006 | 6.1006
2021-03-14 06:00 | 1.3546 | 1.6484 | 1.6129 | 1.7348 | 1.6434 | 1.7653 | 0.85935 | 1.4736 | 1.8184 | 1.8184 | 2.0482 | 2.0482 | 2019-05-11 18:00 | 1.9891 | 3.4133 | 5.769 | 5.769 | 5.769 | 5.769
2021-03-14 07:00 | 1.5861 | 1.9301 | 1.8885 | 2.0313 | 1.9242 | 2.0669 | 0.8888 | 1.5241 | 1.8807 | 1.8807 | 2.1184 | 2.1184 | 2019-05-11 19:00 | 1.9129 | 3.2825 | 5.548 | 5.548 | 5.548 | 5.548
2021-03-14 08:00 | 1.6433 | 1.9997 | 1.9566 | 2.1045 | 1.9935 | 2.1414 | 1.2001 | 2.058 | 2.5394 | 2.5394 | 2.8604 | 2.8604 | 2019-05-11 20:00 | 1.829 | 3.1386 | 5.3048 | 5.3048 | 5.3048 | 5.3048
2021-03-14 09:00 | 1.7119 | 2.0832 | 2.0382 | 2.1923 | 2.0767 | 2.2308 | 1.3495 | 2.3142 | 2.8556 | 2.8556 | 3.2166 | 3.2166 | 2019-05-11 21:00 | 1.7528 | 3.0079 | 5.0838 | 5.0838 | 5.0838 | 5.0838
2021-03-14 10:00 | 1.819 | 2.2136 | 2.1658 | 2.3295 | 2.2067 | 2.3704 | 1.5461 | 2.6513 | 3.2716 | 3.2716 | 3.6851 | 3.6851 | 2019-05-11 22:00 | 1.6995 | 2.9163 | 4.9291 | 4.9291 | 4.9291 | 4.9291
2021-03-14 11:00 | 1.9262 | 2.344 | 2.2934 | 2.4668 | 2.3368 | 2.5101 | 1.589 | 2.7248 | 3.3623 | 3.3623 | 3.7873 | 3.7873 | 2019-05-11 23:00 | 1.5699 | 2.694 | 4.5533 | 4.5533 | 4.5533 | 4.5533
2021-03-14 12:00 | 1.7763 | 2.1615 | 2.1149 | 2.2748 | 2.1549 | 2.3147 | 1.6661 | 2.8572 | 3.5256 | 3.5256 | 3.9712 | 3.9712 | 2019-05-12 | 1.4632 | 2.5109 | 4.2439 | 4.2439 | 4.2439 | 4.2439
2021-03-14 13:00 | 1.769 | 2.1527 | 2.1063 | 2.2655 | 2.1461 | 2.3053 | 1.5918 | 2.7297 | 3.3683 | 3.3683 | 3.7941 | 3.7941 | 2019-05-12 01:00 | 1.5166 | 2.6025 | 4.3986 | 4.3986 | 4.3986 | 4.3986
2021-03-14 14:00 | 1.6433 | 1.9997 | 1.9566 | 2.1045 | 1.9935 | 2.1414 | 1.4661 | 2.5141 | 3.1023 | 3.1023 | 3.4944 | 3.4944 | 2019-05-12 02:00 | 1.4099 | 2.4194 | 4.0891 | 4.0891 | 4.0891 | 4.0891
2021-03-14 15:00 | 1.5661 | 1.9058 | 1.8647 | 2.0056 | 1.8999 | 2.0409 | 1.4318 | 2.4553 | 3.0297 | 3.0297 | 3.4126 | 3.4126 | 2019-05-12 03:00 | 1.3413 | 2.3017 | 3.8902 | 3.8902 | 3.8902 | 3.8902
2021-03-14 16:00 | 1.6235 | 1.9757 | 1.933 | 2.0792 | 1.9696 | 2.1157 | 1.3889 | 2.3818 | 2.939 | 2.939 | 3.3105 | 3.3105 | 2019-05-12 04:00 | 1.4099 | 2.4194 | 4.0891 | 4.0891 | 4.0891 | 4.0891
2021-03-14 17:00 | 1.8405 | 2.2397 | 2.1914 | 2.357 | 2.2328 | 2.3984 | 1.4947 | 2.5631 | 3.1627 | 3.1627 | 3.5625 | 3.5625 | 2019-05-12 05:00 | 1.4404 | 2.4717 | 4.1776 | 4.1776 | 4.1776 | 4.1776
2021-03-14 18:00 | 1.9719 | 2.3996 | 2.3479 | 2.5254 | 2.3922 | 2.5697 | 1.569 | 2.6905 | 3.32 | 3.32 | 3.7396 | 3.7396 | 2019-05-12 06:00 | 1.6461 | 2.8248 | 4.7743 | 4.7743 | 4.7743 | 4.7743
2021-03-14 19:00 | 1.9462 | 2.3683 | 2.3173 | 2.4924 | 2.361 | 2.5362 | 1.6376 | 2.8082 | 3.4651 | 3.4651 | 3.9031 | 3.9031 | 2019-05-12 07:00 | 1.8443 | 3.1648 | 5.349 | 5.349 | 5.349 | 5.349
2021-03-14 20:00 | 1.9148 | 2.3301 | 2.2798 | 2.4522 | 2.3229 | 2.4952 | 1.5545 | 2.6658 | 3.2894 | 3.2894 | 3.7052 | 3.7052 | 2019-05-12 08:00 | 1.9891 | 3.4133 | 5.769 | 5.769 | 5.769 | 5.769
2021-03-14 21:00 | 1.789 | 2.1771 | 2.1301 | 2.2911 | 2.1704 | 2.3314 | 1.3746 | 2.3573 | 2.9088 | 2.9088 | 3.2764 | 3.2764 | 2019-05-12 09:00 | 2.0805 | 3.5702 | 6.0343 | 6.0343 | 6.0343 | 6.0343
2021-03-14 22:00 | 1.6376 | 1.9927 | 1.9498 | 2.0971 | 1.9866 | 2.134 | 1.2091 | 2.0735 | 2.5585 | 2.5585 | 2.8819 | 2.8819 | 2019-05-12 10:00 | 2.3015 | 3.9495 | 6.6753 | 6.6753 | 6.6753 | 6.6753
2021-03-14 23:00 | 1.5118 | 1.8397 | 1.8 | 1.9361 | 1.8341 | 1.9701 | 1.0631 | 1.8231 | 2.2496 | 2.2496 | 2.5339 | 2.5339 | 2019-05-12 11:00 | 2.1872 | 3.7533 | 6.3437 | 6.3437 | 6.3437 | 6.3437
2021-03-15 | 1.4375 | 1.7493 | 1.7116 | 1.8409 | 1.7439 | 1.8733 | 0.8441 | 1.4475 | 1.7861 | 1.7861 | 2.0119 | 2.0119 | 2019-05-12 12:00 | 2.1415 | 3.6748 | 6.2111 | 6.2111 | 6.2111 | 6.2111
2021-03-15 01:00 | 1.3146 | 1.5998 | 1.5653 | 1.6836 | 1.5948 | 1.7131 | 0.73447 | 1.2595 | 1.5542 | 1.5542 | 1.7506 | 1.7506 | 2019-05-12 13:00 | 2.1415 | 3.6748 | 6.2111 | 6.2111 | 6.2111 | 6.2111
2021-03-15 02:00 | 1.2605 | 1.5339 | 1.5009 | 1.6143 | 1.5292 | 1.6427 | 0.72018 | 1.235 | 1.5239 | 1.5239 | 1.7165 | 1.7165 | 2019-05-12 14:00 | 2.0196 | 3.4656 | 5.8574 | 5.8574 | 5.8574 | 5.8574
2021-03-15 03:00 | 1.2569 | 1.5295 | 1.4965 | 1.6096 | 1.5248 | 1.6379 | 0.72018 | 1.235 | 1.5239 | 1.5239 | 1.7165 | 1.7165 | 2019-05-12 15:00 | 2.0805 | 3.5702 | 6.0343 | 6.0343 | 6.0343 | 6.0343
2021-03-15 04:00 | 1.3016 | 1.5839 | 1.5497 | 1.6669 | 1.579 | 1.6962 | 0.70018 | 1.2007 | 1.4816 | 1.4816 | 1.6688 | 1.6688 | 2019-05-12 16:00 | 2.1263 | 3.6487 | 6.1669 | 6.1669 | 6.1669 | 6.1669
2021-03-15 05:00 | 1.4261 | 1.7354 | 1.698 | 1.8263 | 1.73 | 1.8584 | 0.80878 | 1.3869 | 1.7114 | 1.7114 | 1.9277 | 1.9277 | 2019-05-12 17:00 | 2.0577 | 3.531 | 5.9679 | 5.9679 | 5.9679 | 5.9679
2021-03-15 06:00 | 1.8233 | 2.2188 | 2.1709 | 2.335 | 2.212 | 2.3761 | 1.026 | 1.7594 | 2.171 | 2.171 | 2.4454 | 2.4454 | 2019-05-12 18:00 | 1.9967 | 3.4264 | 5.7911 | 5.7911 | 5.7911 | 5.7911
2021-03-15 07:00 | 2.0834 | 2.5353 | 2.4806 | 2.6681 | 2.5275 | 2.715 | 1.2289 | 2.1073 | 2.6003 | 2.6003 | 2.929 | 2.929 | 2019-05-12 19:00 | 1.9815 | 3.4002 | 5.7469 | 5.7469 | 5.7469 | 5.7469
2021-03-15 08:00 | 2.1949 | 2.6709 | 2.6133 | 2.8108 | 2.6627 | 2.8602 | 1.3575 | 2.3279 | 2.8725 | 2.8725 | 3.2355 | 3.2355 | 2019-05-12 20:00 | 1.8519 | 3.1779 | 5.3711 | 5.3711 | 5.3711 | 5.3711
2021-03-15 09:00 | 2.0691 | 2.5179 | 2.4636 | 2.6498 | 2.5101 | 2.6963 | 1.3832 | 2.372 | 2.9269 | 2.9269 | 3.2968 | 3.2968 | 2019-05-12 21:00 | 1.7909 | 3.0733 | 5.1943 | 5.1943 | 5.1943 | 5.1943
2021-03-15 10:00 | 1.8948 | 2.3057 | 2.256 | 2.4265 | 2.2986 | 2.4692 | 1.4004 | 2.4014 | 2.9632 | 2.9632 | 3.3377 | 3.3377 | 2019-05-12 22:00 | 1.5775 | 2.7071 | 4.5754 | 4.5754 | 4.5754 | 4.5754
2021-03-15 11:00 | 1.8062 | 2.1979 | 2.1505 | 2.3131 | 2.1912 | 2.3537 | 1.3489 | 2.3132 | 2.8543 | 2.8543 | 3.2151 | 3.2151 | 2019-05-12 23:00 | 1.4556 | 2.4978 | 4.2218 | 4.2218 | 4.2218 | 4.2218
2021-03-15 12:00 | 1.6976 | 2.0658 | 2.0212 | 2.174 | 2.0594 | 2.2122 | 1.4004 | 2.4014 | 2.9632 | 2.9632 | 3.3377 | 3.3377 | 2019-05-13 | 1.4175 | 2.4324 | 4.1112 | 4.1112 | 4.1112 | 4.1112
2021-03-15 13:00 | 1.7233 | 2.0971 | 2.0518 | 2.2069 | 2.0906 | 2.2457 | 1.3289 | 2.2789 | 2.812 | 2.812 | 3.1674 | 3.1674 | 2019-05-13 01:00 | 1.387 | 2.3801 | 4.0228 | 4.0228 | 4.0228 | 4.0228
2021-03-15 14:00 | 1.6661 | 2.0275 | 1.9838 | 2.1337 | 2.0213 | 2.1712 | 1.3032 | 2.2348 | 2.7576 | 2.7576 | 3.1061 | 3.1061 | 2019-05-13 02:00 | 1.3489 | 2.3148 | 3.9123 | 3.9123 | 3.9123 | 3.9123
2021-03-15 15:00 | 1.709 | 2.0797 | 2.0348 | 2.1886 | 2.0733 | 2.2271 | 1.2889 | 2.2103 | 2.7273 | 2.7273 | 3.072 | 3.072 | 2019-05-13 03:00 | 1.3642 | 2.3409 | 3.9565 | 3.9565 | 3.9565 | 3.9565
2021-03-15 16:00 | 1.8405 | 2.2397 | 2.1914 | 2.357 | 2.2328 | 2.3984 | 1.3146 | 2.2544 | 2.7818 | 2.7818 | 3.1333 | 3.1333 | 2019-05-13 04:00 | 1.448 | 2.4848 | 4.1997 | 4.1997 | 4.1997 | 4.1997
2021-03-15 17:00 | 1.9948 | 2.4275 | 2.3751 | 2.5546 | 2.42 | 2.5995 | 1.4146 | 2.4259 | 2.9934 | 2.9934 | 3.3718 | 3.3718 | 2019-05-13 05:00 | 1.5547 | 2.6678 | 4.5091 | 4.5091 | 4.5091 | 4.5091
2021-03-15 18:00 | 2.172 | 2.6431 | 2.5861 | 2.7815 | 2.6349 | 2.8304 | 1.549 | 2.6562 | 3.2776 | 3.2776 | 3.6919 | 3.6919 | 2019-05-13 06:00 | 1.8214 | 3.1256 | 5.2827 | 5.2827 | 5.2827 | 5.2827
2021-03-15 19:00 | 2.1891 | 2.664 | 2.6065 | 2.8035 | 2.6557 | 2.8528 | 1.6433 | 2.818 | 3.4772 | 3.4772 | 3.9167 | 3.9167 | 2019-05-13 07:00 | 1.9357 | 3.3217 | 5.6143 | 5.6143 | 5.6143 | 5.6143
2021-03-15 20:00 | 2.0377 | 2.4796 | 2.4261 | 2.6095 | 2.472 | 2.6554 | 1.5518 | 2.6611 | 3.2837 | 3.2837 | 3.6987 | 3.6987 | 2019-05-13 08:00 | 2.1263 | 3.6487 | 6.1669 | 6.1669 | 6.1669 | 6.1669
2021-03-15 21:00 | 1.8491 | 2.2501 | 2.2016 | 2.368 | 2.2432 | 2.4096 | 1.4118 | 2.421 | 2.9874 | 2.9874 | 3.3649 | 3.3649 | 2019-05-13 09:00 | 2.0805 | 3.5702 | 6.0343 | 6.0343 | 6.0343 | 6.0343
2021-03-15 22:00 | 1.649 | 2.0067 | 1.9634 | 2.1118 | 2.0005 | 2.1489 | 1.3089 | 2.2446 | 2.7697 | 2.7697 | 3.1197 | 3.1197 | 2019-05-13 10:00 | 2.0272 | 3.4787 | 5.8795 | 5.8795 | 5.8795 | 5.8795
2021-03-15 23:00 | 1.4775 | 1.798 | 1.7592 | 1.8922 | 1.7925 | 1.9254 | 1.1089 | 1.9015 | 2.3464 | 2.3464 | 2.6429 | 2.6429 | 2019-05-13 11:00 | 2.0348 | 3.4917 | 5.9016 | 5.9016 | 5.9016 | 5.9016
2021-03-16 | 1.3403 | 1.6311 | 1.5959 | 1.7165 | 1.626 | 1.7467 | 0.88897 | 1.5244 | 1.8811 | 1.8811 | 2.1188 | 2.1188 | 2019-05-13 12:00 | 1.9662 | 3.374 | 5.7027 | 5.7027 | 5.7027 | 5.7027
2021-03-16 01:00 | 1.2437 | 1.5135 | 1.4809 | 1.5928 | 1.5088 | 1.6208 | 0.84401 | 1.4473 | 1.7859 | 1.7859 | 2.0117 | 2.0117 | 2019-05-13 13:00 | 2.0577 | 3.531 | 5.9679 | 5.9679 | 5.9679 | 5.9679
2021-03-16 02:00 | 1.2203 | 1.485 | 1.453 | 1.5628 | 1.4804 | 1.5902 | 0.75162 | 1.2889 | 1.5904 | 1.5904 | 1.7915 | 1.7915 | 2019-05-13 14:00 | 1.9967 | 3.4264 | 5.7911 | 5.7911 | 5.7911 | 5.7911
2021-03-16 03:00 | 1.2144 | 1.4777 | 1.4459 | 1.5552 | 1.4732 | 1.5825 | 0.71733 | 1.2301 | 1.5179 | 1.5179 | 1.7097 | 1.7097 | 2019-05-13 15:00 | 1.9662 | 3.374 | 5.7027 | 5.7027 | 5.7027 | 5.7027
2021-03-16 04:00 | 1.2232 | 1.4885 | 1.4564 | 1.5664 | 1.4839 | 1.594 | 0.72516 | 1.2435 | 1.5344 | 1.5344 | 1.7284 | 1.7284 | 2019-05-13 16:00 | 1.9967 | 3.4264 | 5.7911 | 5.7911 | 5.7911 | 5.7911
2021-03-16 05:00 | 1.4198 | 1.7278 | 1.6905 | 1.8183 | 1.7225 | 1.8503 | 0.74265 | 1.2735 | 1.5715 | 1.5715 | 1.7701 | 1.7701 | 2019-05-13 17:00 | 2.0501 | 3.5179 | 5.9458 | 5.9458 | 5.9458 | 5.9458
2021-03-16 06:00 | 1.7576 | 2.1388 | 2.0927 | 2.2509 | 2.1322 | 2.2904 | 0.96596 | 1.6565 | 2.044 | 2.044 | 2.3023 | 2.3023 | 2019-05-13 18:00 | 2.0272 | 3.4787 | 5.8795 | 5.8795 | 5.8795 | 5.8795
2021-03-16 07:00 | 2.0777 | 2.5283 | 2.4738 | 2.6608 | 2.5205 | 2.7075 | 1.206 | 2.0681 | 2.552 | 2.552 | 2.8745 | 2.8745 | 2019-05-13 19:00 | 1.9053 | 3.2694 | 5.5259 | 5.5259 | 5.5259 | 5.5259
2021-03-16 08:00 | 2.1863 | 2.6605 | 2.6031 | 2.7998 | 2.6523 | 2.849 | 1.2718 | 2.1809 | 2.691 | 2.691 | 3.0312 | 3.0312 | 2019-05-13 20:00 | 1.8519 | 3.1779 | 5.3711 | 5.3711 | 5.3711 | 5.3711
2021-03-16 09:00 | 2.2349 | 2.7196 | 2.6609 | 2.8621 | 2.7112 | 2.9124 | 1.3403 | 2.2985 | 2.8362 | 2.8362 | 3.1947 | 3.1947 | 2019-05-13 21:00 | 1.7071 | 2.9294 | 4.9512 | 4.9512 | 4.9512 | 4.9512
2021-03-16 10:00 | 2.2463 | 2.7335 | 2.6745 | 2.8767 | 2.7251 | 2.9272 | 1.3861 | 2.3769 | 2.9329 | 2.9329 | 3.3036 | 3.3036 | 2019-05-13 22:00 | 1.6385 | 2.8117 | 4.7522 | 4.7522 | 4.7522 | 4.7522
2021-03-16 11:00 | 2.2234 | 2.7057 | 2.6473 | 2.8474 | 2.6973 | 2.8975 | 1.4004 | 2.4014 | 2.9632 | 2.9632 | 3.3377 | 3.3377 | 2019-05-13 23:00 | 1.4861 | 2.5501 | 4.3102 | 4.3102 | 4.3102 | 4.3102
2021-03-16 12:00 | 2.0491 | 2.4935 | 2.4398 | 2.6242 | 2.4859 | 2.6703 | 1.2746 | 2.1858 | 2.6971 | 2.6971 | 3.038 | 3.038 | 2019-05-14 | 1.4709 | 2.524 | 4.266 | 4.266 | 4.266 | 4.266
2021-03-16 13:00 | 2.0777 | 2.5283 | 2.4738 | 2.6608 | 2.5205 | 2.7075 | 1.3689 | 2.3475 | 2.8967 | 2.8967 | 3.2628 | 3.2628 | 2019-05-14 01:00 | 1.3413 | 2.3017 | 3.8902 | 3.8902 | 3.8902 | 3.8902
2021-03-16 14:00 | 2.1406 | 2.6048 | 2.5486 | 2.7413 | 2.5968 | 2.7895 | 1.3661 | 2.3426 | 2.8906 | 2.8906 | 3.256 | 3.256 | 2019-05-14 02:00 | 1.4023 | 2.4063 | 4.067 | 4.067 | 4.067 | 4.067
2021-03-16 15:00 | 2.1091 | 2.5666 | 2.5112 | 2.701 | 2.5587 | 2.7485 | 1.3032 | 2.2348 | 2.7576 | 2.7576 | 3.1061 | 3.1061 | 2019-05-14 03:00 | 1.3413 | 2.3017 | 3.8902 | 3.8902 | 3.8902 | 3.8902
2021-03-16 16:00 | 2.0222 | 2.4609 | 2.4078 | 2.5898 | 2.4533 | 2.6353 | 1.3118 | 2.2495 | 2.7757 | 2.7757 | 3.1265 | 3.1265 | 2019-05-14 04:00 | 1.4404 | 2.4717 | 4.1776 | 4.1776 | 4.1776 | 4.1776
2021-03-16 17:00 | 2.0262 | 2.4657 | 2.4125 | 2.5949 | 2.4581 | 2.6405 | 1.4318 | 2.4553 | 3.0297 | 3.0297 | 3.4126 | 3.4126 | 2019-05-14 05:00 | 1.5623 | 2.6809 | 4.5312 | 4.5312 | 4.5312 | 4.5312
2021-03-16 18:00 | 2.2091 | 2.6883 | 2.6303 | 2.8291 | 2.68 | 2.8788 | 1.5204 | 2.6072 | 3.2172 | 3.2172 | 3.6238 | 3.6238 | 2019-05-14 06:00 | 1.8138 | 3.1125 | 5.2606 | 5.2606 | 5.2606 | 5.2606
2021-03-16 19:00 | 2.2777 | 2.7718 | 2.712 | 2.917 | 2.7632 | 2.9682 | 1.6233 | 2.7837 | 3.4349 | 3.4349 | 3.869 | 3.869 | 2019-05-14 07:00 | 1.8519 | 3.1779 | 5.3711 | 5.3711 | 5.3711 | 5.3711
2021-03-16 20:00 | 2.1577 | 2.6257 | 2.5691 | 2.7632 | 2.6176 | 2.8118 | 1.589 | 2.7248 | 3.3623 | 3.3623 | 3.7873 | 3.7873 | 2019-05-14 08:00 | 1.9205 | 3.2956 | 5.5701 | 5.5701 | 5.5701 | 5.5701
2021-03-16 21:00 | 1.9235 | 2.3407 | 2.2902 | 2.4633 | 2.3335 | 2.5066 | 1.4261 | 2.4455 | 3.0176 | 3.0176 | 3.399 | 3.399 | 2019-05-14 09:00 | 1.9586 | 3.361 | 5.6806 | 5.6806 | 5.6806 | 5.6806
2021-03-16 22:00 | 1.7462 | 2.1249 | 2.0791 | 2.2362 | 2.1184 | 2.2755 | 1.2489 | 2.1416 | 2.6427 | 2.6427 | 2.9767 | 2.9767 | 2019-05-14 10:00 | 1.9815 | 3.4002 | 5.7469 | 5.7469 | 5.7469 | 5.7469
2021-03-16 23:00 | 1.5547 | 1.8919 | 1.8511 | 1.991 | 1.8861 | 2.026 | 1.035 | 1.7748 | 2.19 | 2.19 | 2.4668 | 2.4668 | 2019-05-14 11:00 | 2.0196 | 3.4656 | 5.8574 | 5.8574 | 5.8574 | 5.8574
2021-03-17 | 1.3861 | 1.6867 | 1.6503 | 1.7751 | 1.6815 | 1.8063 | 0.93452 | 1.6026 | 1.9775 | 1.9775 | 2.2274 | 2.2274 | 2019-05-14 12:00 | 1.9891 | 3.4133 | 5.769 | 5.769 | 5.769 | 5.769
2021-03-17 01:00 | 1.2832 | 1.5615 | 1.5278 | 1.6433 | 1.5567 | 1.6722 | 0.78905 | 1.3531 | 1.6696 | 1.6696 | 1.8807 | 1.8807 | 2019-05-14 13:00 | 1.9815 | 3.4002 | 5.7469 | 5.7469 | 5.7469 | 5.7469
2021-03-17 02:00 | 1.2803 | 1.558 | 1.5244 | 1.6396 | 1.5532 | 1.6685 | 0.74305 | 1.2742 | 1.5723 | 1.5723 | 1.771 | 1.771 | 2019-05-14 14:00 | 2.0272 | 3.4787 | 5.8795 | 5.8795 | 5.8795 | 5.8795
2021-03-17 03:00 | 1.2346 | 1.5024 | 1.47 | 1.5811 | 1.4978 | 1.6089 | 0.70886 | 1.2156 | 1.4999 | 1.4999 | 1.6895 | 1.6895 | 2019-05-14 15:00 | 1.9357 | 3.3217 | 5.6143 | 5.6143 | 5.6143 | 5.6143
2021-03-17 04:00 | 1.2517 | 1.5232 | 1.4904 | 1.603 | 1.5186 | 1.6312 | 0.67744 | 1.1617 | 1.4335 | 1.4335 | 1.6147 | 1.6147 | 2019-05-14 16:00 | 2.0043 | 3.4394 | 5.8132 | 5.8132 | 5.8132 | 5.8132
2021-03-17 05:00 | 1.4088 | 1.7144 | 1.6774 | 1.8042 | 1.7091 | 1.8359 | 0.75162 | 1.2889 | 1.5904 | 1.5904 | 1.7915 | 1.7915 | 2019-05-14 17:00 | 2.0348 | 3.4917 | 5.9016 | 5.9016 | 5.9016 | 5.9016
2021-03-17 06:00 | 1.814 | 2.2075 | 2.1599 | 2.3231 | 2.2007 | 2.3639 | 0.9431 | 1.6173 | 1.9956 | 1.9956 | 2.2478 | 2.2478 | 2019-05-14 18:00 | 2.0272 | 3.4787 | 5.8795 | 5.8795 | 5.8795 | 5.8795
2021-03-17 07:00 | 2.0691 | 2.5179 | 2.4636 | 2.6498 | 2.5101 | 2.6963 | 1.2289 | 2.1073 | 2.6003 | 2.6003 | 2.929 | 2.929 | 2019-05-14 19:00 | 1.951 | 3.3479 | 5.6585 | 5.6585 | 5.6585 | 5.6585
2021-03-17 08:00 | 2.1663 | 2.6361 | 2.5793 | 2.7742 | 2.628 | 2.823 | 1.3146 | 2.2544 | 2.7818 | 2.7818 | 3.1333 | 3.1333 | 2019-05-14 20:00 | 1.8367 | 3.1517 | 5.3269 | 5.3269 | 5.3269 | 5.3269
2021-03-17 09:00 | 2.1606 | 2.6292 | 2.5725 | 2.7669 | 2.6211 | 2.8155 | 1.3032 | 2.2348 | 2.7576 | 2.7576 | 3.1061 | 3.1061 | 2019-05-14 21:00 | 1.7605 | 3.0209 | 5.1059 | 5.1059 | 5.1059 | 5.1059
2021-03-17 10:00 | 2.2349 | 2.7196 | 2.6609 | 2.8621 | 2.7112 | 2.9124 | 1.3432 | 2.3034 | 2.8422 | 2.8422 | 3.2015 | 3.2015 | 2019-05-14 22:00 | 1.7452 | 2.9948 | 5.0617 | 5.0617 | 5.0617 | 5.0617
2021-03-17 11:00 | 2.2777 | 2.7718 | 2.712 | 2.917 | 2.7632 | 2.9682 | 1.4289 | 2.4504 | 3.0236 | 3.0236 | 3.4058 | 3.4058 | 2019-05-14 23:00 | 1.4937 | 2.5632 | 4.3323 | 4.3323 | 4.3323 | 4.3323
2021-03-17 12:00 | 2.192 | 2.6674 | 2.6099 | 2.8072 | 2.6592 | 2.8565 | 1.4004 | 2.4014 | 2.9632 | 2.9632 | 3.3377 | 3.3377 | 2019-05-15 | 1.4937 | 2.5632 | 4.3323 | 4.3323 | 4.3323 | 4.3323
2021-03-17 13:00 | 2.1806 | 2.6535 | 2.5963 | 2.7925 | 2.6453 | 2.8416 | 1.4261 | 2.4455 | 3.0176 | 3.0176 | 3.399 | 3.399 | 2019-05-15 01:00 | 1.4099 | 2.4194 | 4.0891 | 4.0891 | 4.0891 | 4.0891
2021-03-17 14:00 | 2.1863 | 2.6605 | 2.6031 | 2.7998 | 2.6523 | 2.849 | 1.4347 | 2.4602 | 3.0357 | 3.0357 | 3.4194 | 3.4194 | 2019-05-15 02:00 | 1.3946 | 2.3932 | 4.0449 | 4.0449 | 4.0449 | 4.0449
2021-03-17 15:00 | 2.112 | 2.5701 | 2.5146 | 2.7047 | 2.5621 | 2.7522 | 1.3661 | 2.3426 | 2.8906 | 2.8906 | 3.256 | 3.256 | 2019-05-15 03:00 | 1.3946 | 2.3932 | 4.0449 | 4.0449 | 4.0449 | 4.0449
2021-03-17 16:00 | 2.0748 | 2.5248 | 2.4704 | 2.6571 | 2.5171 | 2.7038 | 1.3489 | 2.3132 | 2.8543 | 2.8543 | 3.2151 | 3.2151 | 2019-05-15 04:00 | 1.4632 | 2.5109 | 4.2439 | 4.2439 | 4.2439 | 4.2439
2021-03-17 17:00 | 2.1234 | 2.584 | 2.5282 | 2.7193 | 2.576 | 2.7671 | 1.4489 | 2.4847 | 3.066 | 3.066 | 3.4535 | 3.4535 | 2019-05-15 05:00 | 1.6461 | 2.8248 | 4.7743 | 4.7743 | 4.7743 | 4.7743
2021-03-17 18:00 | 2.3035 | 2.8031 | 2.7426 | 2.9499 | 2.7944 | 3.0017 | 1.549 | 2.6562 | 3.2776 | 3.2776 | 3.6919 | 3.6919 | 2019-05-15 06:00 | 1.8214 | 3.1256 | 5.2827 | 5.2827 | 5.2827 | 5.2827
2021-03-17 19:00 | 2.3206 | 2.8239 | 2.763 | 2.9719 | 2.8152 | 3.0241 | 1.5976 | 2.7395 | 3.3804 | 3.3804 | 3.8077 | 3.8077 | 2019-05-15 07:00 | 1.9053 | 3.2694 | 5.5259 | 5.5259 | 5.5259 | 5.5259
2021-03-17 20:00 | 2.1205 | 2.5805 | 2.5248 | 2.7157 | 2.5725 | 2.7634 | 1.4918 | 2.5582 | 3.1567 | 3.1567 | 3.5557 | 3.5557 | 2019-05-15 08:00 | 2.0729 | 3.5571 | 6.0121 | 6.0121 | 6.0121 | 6.0121
2021-03-17 21:00 | 1.9862 | 2.417 | 2.3649 | 2.5437 | 2.4096 | 2.5883 | 1.4547 | 2.4945 | 3.0781 | 3.0781 | 3.4671 | 3.4671 | 2019-05-15 09:00 | 2.0196 | 3.4656 | 5.8574 | 5.8574 | 5.8574 | 5.8574
2021-03-17 22:00 | 1.7204 | 2.0936 | 2.0484 | 2.2033 | 2.0871 | 2.242 | 1.2603 | 2.1613 | 2.6669 | 2.6669 | 3.0039 | 3.0039 | 2019-05-15 10:00 | 2.0272 | 3.4787 | 5.8795 | 5.8795 | 5.8795 | 5.8795
2021-03-17 23:00 | 1.529 | 1.8606 | 1.8205 | 1.9581 | 1.8549 | 1.9925 | 1.1117 | 1.9064 | 2.3524 | 2.3524 | 2.6497 | 2.6497 | 2019-05-15 11:00 | 2.0958 | 3.5964 | 6.0785 | 6.0785 | 6.0785 | 6.0785
2021-03-18 | 1.4747 | 1.7945 | 1.7558 | 1.8885 | 1.789 | 1.9217 | 0.95167 | 1.632 | 2.0137 | 2.0137 | 2.2683 | 2.2683 | 2019-05-15 12:00 | 2.0805 | 3.5702 | 6.0343 | 6.0343 | 6.0343 | 6.0343
2021-03-18 01:00 | 1.3403 | 1.6311 | 1.5959 | 1.7165 | 1.626 | 1.7467 | 0.79449 | 1.3624 | 1.6811 | 1.6811 | 1.8936 | 1.8936 | 2019-05-15 13:00 | 2.0653 | 3.5441 | 5.99 | 5.99 | 5.99 | 5.99
2021-03-18 02:00 | 1.2718 | 1.5476 | 1.5142 | 1.6287 | 1.5428 | 1.6573 | 0.77162 | 1.3232 | 1.6328 | 1.6328 | 1.8391 | 1.8391 | 2019-05-15 14:00 | 2.0043 | 3.4394 | 5.8132 | 5.8132 | 5.8132 | 5.8132
2021-03-18 03:00 | 1.2632 | 1.5372 | 1.504 | 1.6177 | 1.5324 | 1.6461 | 0.70875 | 1.2154 | 1.4997 | 1.4997 | 1.6893 | 1.6893 | 2019-05-15 15:00 | 2.0119 | 3.4525 | 5.8353 | 5.8353 | 5.8353 | 5.8353
2021-03-18 04:00 | 1.2859 | 1.5648 | 1.5311 | 1.6468 | 1.56 | 1.6757 | 0.72876 | 1.2497 | 1.5421 | 1.5421 | 1.737 | 1.737 | 2019-05-15 16:00 | 2.0653 | 3.5441 | 5.99 | 5.99 | 5.99 | 5.99
2021-03-18 05:00 | 1.4277 | 1.7373 | 1.6999 | 1.8284 | 1.732 | 1.8605 | 0.84307 | 1.4457 | 1.7839 | 1.7839 | 2.0094 | 2.0094 | 2019-05-15 17:00 | 2.2025 | 3.7795 | 6.3879 | 6.3879 | 6.3879 | 6.3879
2021-03-18 06:00 | 1.8376 | 2.2362 | 2.188 | 2.3533 | 2.2293 | 2.3947 | 1.0346 | 1.7741 | 2.1891 | 2.1891 | 2.4658 | 2.4658 | 2019-05-15 18:00 | 2.1949 | 3.7664 | 6.3658 | 6.3658 | 6.3658 | 6.3658
2021-03-18 07:00 | 2.1606 | 2.6292 | 2.5725 | 2.7669 | 2.6211 | 2.8155 | 1.266 | 2.1711 | 2.679 | 2.679 | 3.0176 | 3.0176 | 2019-05-15 19:00 | 2.1415 | 3.6748 | 6.2111 | 6.2111 | 6.2111 | 6.2111
2021-03-18 08:00 | 2.1291 | 2.5909 | 2.535 | 2.7266 | 2.5829 | 2.7746 | 1.3804 | 2.3671 | 2.9208 | 2.9208 | 3.29 | 3.29 | 2019-05-15 20:00 | 2.0272 | 3.4787 | 5.8795 | 5.8795 | 5.8795 | 5.8795
2021-03-18 09:00 | 2.252 | 2.7405 | 2.6813 | 2.884 | 2.732 | 2.9347 | 1.3489 | 2.3132 | 2.8543 | 2.8543 | 3.2151 | 3.2151 | 2019-05-15 21:00 | 1.7909 | 3.0733 | 5.1943 | 5.1943 | 5.1943 | 5.1943
2021-03-18 10:00 | 2.172 | 2.6431 | 2.5861 | 2.7815 | 2.6349 | 2.8304 | 1.3661 | 2.3426 | 2.8906 | 2.8906 | 3.256 | 3.256 | 2019-05-15 22:00 | 1.7605 | 3.0209 | 5.1059 | 5.1059 | 5.1059 | 5.1059
2021-03-18 11:00 | 2.2406 | 2.7266 | 2.6677 | 2.8694 | 2.7181 | 2.9198 | 1.3804 | 2.3671 | 2.9208 | 2.9208 | 3.29 | 3.29 | 2019-05-15 23:00 | 1.5394 | 2.6417 | 4.4649 | 4.4649 | 4.4649 | 4.4649
2021-03-18 12:00 | 2.2977 | 2.7961 | 2.7358 | 2.9426 | 2.7875 | 2.9943 | 1.3546 | 2.323 | 2.8664 | 2.8664 | 3.2287 | 3.2287 | 2019-05-16 | 1.4709 | 2.524 | 4.266 | 4.266 | 4.266 | 4.266
2021-03-18 13:00 | 2.1148 | 2.5735 | 2.518 | 2.7083 | 2.5656 | 2.7559 | 1.3546 | 2.323 | 2.8664 | 2.8664 | 3.2287 | 3.2287 | 2019-05-16 01:00 | 1.4327 | 2.4586 | 4.1555 | 4.1555 | 4.1555 | 4.1555
2021-03-18 14:00 | 2.1034 | 2.5596 | 2.5044 | 2.6937 | 2.5517 | 2.741 | 1.3461 | 2.3083 | 2.8483 | 2.8483 | 3.2083 | 3.2083 | 2019-05-16 02:00 | 1.4099 | 2.4194 | 4.0891 | 4.0891 | 4.0891 | 4.0891
2021-03-18 15:00 | 2.1434 | 2.6083 | 2.552 | 2.7449 | 2.6003 | 2.7932 | 1.226 | 2.1024 | 2.5943 | 2.5943 | 2.9222 | 2.9222 | 2019-05-16 03:00 | 1.3946 | 2.3932 | 4.0449 | 4.0449 | 4.0449 | 4.0449
2021-03-18 16:00 | 2.0034 | 2.4379 | 2.3853 | 2.5656 | 2.4304 | 2.6107 | 1.3746 | 2.3573 | 2.9088 | 2.9088 | 3.2764 | 3.2764 | 2019-05-16 04:00 | 1.4023 | 2.4063 | 4.067 | 4.067 | 4.067 | 4.067
2021-03-18 17:00 | 2.1034 | 2.5596 | 2.5044 | 2.6937 | 2.5517 | 2.741 | 1.4547 | 2.4945 | 3.0781 | 3.0781 | 3.4671 | 3.4671 | 2019-05-16 05:00 | 1.5852 | 2.7202 | 4.5975 | 4.5975 | 4.5975 | 4.5975
2021-03-18 18:00 | 2.3406 | 2.8483 | 2.7868 | 2.9975 | 2.8395 | 3.0501 | 1.4689 | 2.519 | 3.1083 | 3.1083 | 3.5012 | 3.5012 | 2019-05-16 06:00 | 1.7681 | 3.034 | 5.128 | 5.128 | 5.128 | 5.128
2021-03-18 19:00 | 2.2777 | 2.7718 | 2.712 | 2.917 | 2.7632 | 2.9682 | 1.6176 | 2.7739 | 3.4228 | 3.4228 | 3.8554 | 3.8554 | 2019-05-16 07:00 | 1.9205 | 3.2956 | 5.5701 | 5.5701 | 5.5701 | 5.5701
2021-03-18 20:00 | 2.152 | 2.6187 | 2.5623 | 2.7559 | 2.6107 | 2.8043 | 1.5861 | 2.7199 | 3.3563 | 3.3563 | 3.7805 | 3.7805 | 2019-05-16 08:00 | 2.0272 | 3.4787 | 5.8795 | 5.8795 | 5.8795 | 5.8795
2021-03-18 21:00 | 1.9148 | 2.3301 | 2.2798 | 2.4522 | 2.3229 | 2.4952 | 1.4632 | 2.5092 | 3.0962 | 3.0962 | 3.4876 | 3.4876 | 2019-05-16 09:00 | 2.0501 | 3.5179 | 5.9458 | 5.9458 | 5.9458 | 5.9458
2021-03-18 22:00 | 1.7605 | 2.1423 | 2.0961 | 2.2545 | 2.1357 | 2.2941 | 1.2677 | 2.1739 | 2.6825 | 2.6825 | 3.0216 | 3.0216 | 2019-05-16 10:00 | 1.9738 | 3.3871 | 5.7248 | 5.7248 | 5.7248 | 5.7248
2021-03-18 23:00 | 1.5747 | 1.9162 | 1.8749 | 2.0166 | 1.9103 | 2.0521 | 1.0433 | 1.7891 | 2.2076 | 2.2076 | 2.4866 | 2.4866 | 2019-05-16 11:00 | 1.9738 | 3.3871 | 5.7248 | 5.7248 | 5.7248 | 5.7248
2021-03-19 | 1.4347 | 1.7458 | 1.7082 | 1.8373 | 1.7404 | 1.8696 | 0.87451 | 1.4996 | 1.8505 | 1.8505 | 2.0844 | 2.0844 | 2019-05-16 12:00 | 2.0043 | 3.4394 | 5.8132 | 5.8132 | 5.8132 | 5.8132
2021-03-19 01:00 | 1.3318 | 1.6206 | 1.5857 | 1.7055 | 1.6156 | 1.7355 | 0.77734 | 1.333 | 1.6449 | 1.6449 | 1.8528 | 1.8528 | 2019-05-16 13:00 | 1.9967 | 3.4264 | 5.7911 | 5.7911 | 5.7911 | 5.7911
2021-03-19 02:00 | 1.2718 | 1.5476 | 1.5142 | 1.6287 | 1.5428 | 1.6573 | 0.81735 | 1.4016 | 1.7295 | 1.7295 | 1.9481 | 1.9481 | 2019-05-16 14:00 | 1.9662 | 3.374 | 5.7027 | 5.7027 | 5.7027 | 5.7027
2021-03-19 03:00 | 1.2746 | 1.5511 | 1.5176 | 1.6323 | 1.5463 | 1.661 | 0.74019 | 1.2693 | 1.5662 | 1.5662 | 1.7642 | 1.7642 | 2019-05-16 15:00 | 1.9815 | 3.4002 | 5.7469 | 5.7469 | 5.7469 | 5.7469
2021-03-19 04:00 | 1.3146 | 1.5998 | 1.5653 | 1.6836 | 1.5948 | 1.7131 | 0.70304 | 1.2056 | 1.4876 | 1.4876 | 1.6757 | 1.6757 | 2019-05-16 16:00 | 2.0729 | 3.5571 | 6.0121 | 6.0121 | 6.0121 | 6.0121
2021-03-19 05:00 | 1.5227 | 1.853 | 1.813 | 1.95 | 1.8472 | 1.9843 | 0.74876 | 1.284 | 1.5844 | 1.5844 | 1.7846 | 1.7846 | 2019-05-16 17:00 | 2.0196 | 3.4656 | 5.8574 | 5.8574 | 5.8574 | 5.8574
2021-03-19 06:00 | 1.7283 | 2.1032 | 2.0578 | 2.2133 | 2.0967 | 2.2522 | 0.91166 | 1.5634 | 1.9291 | 1.9291 | 2.1729 | 2.1729 | 2019-05-16 18:00 | 2.0043 | 3.4394 | 5.8132 | 5.8132 | 5.8132 | 5.8132
2021-03-19 07:00 | 2.0948 | 2.5492 | 2.4942 | 2.6827 | 2.5413 | 2.7299 | 1.3175 | 2.2593 | 2.7878 | 2.7878 | 3.1402 | 3.1402 | 2019-05-16 19:00 | 1.9815 | 3.4002 | 5.7469 | 5.7469 | 5.7469 | 5.7469
2021-03-19 08:00 | 2.252 | 2.7405 | 2.6813 | 2.884 | 2.732 | 2.9347 | 1.3632 | 2.3377 | 2.8846 | 2.8846 | 3.2491 | 3.2491 | 2019-05-16 20:00 | 1.8519 | 3.1779 | 5.3711 | 5.3711 | 5.3711 | 5.3711
2021-03-19 09:00 | 2.2577 | 2.7474 | 2.6882 | 2.8913 | 2.739 | 2.9421 | 1.3375 | 2.2936 | 2.8301 | 2.8301 | 3.1878 | 3.1878 | 2019-05-16 21:00 | 1.7376 | 2.9817 | 5.0396 | 5.0396 | 5.0396 | 5.0396
2021-03-19 10:00 | 2.1491 | 2.6153 | 2.5588 | 2.7523 | 2.6072 | 2.8006 | 1.4661 | 2.5141 | 3.1023 | 3.1023 | 3.4944 | 3.4944 | 2019-05-16 22:00 | 1.7071 | 2.9294 | 4.9512 | 4.9512 | 4.9512 | 4.9512
2021-03-19 11:00 | 2.2063 | 2.6848 | 2.6269 | 2.8255 | 2.6765 | 2.8751 | 1.4261 | 2.4455 | 3.0176 | 3.0176 | 3.399 | 3.399 | 2019-05-16 23:00 | 1.5013 | 2.5763 | 4.3544 | 4.3544 | 4.3544 | 4.3544
2021-03-19 12:00 | 2.2749 | 2.7683 | 2.7086 | 2.9133 | 2.7598 | 2.9645 | 1.3461 | 2.3083 | 2.8483 | 2.8483 | 3.2083 | 3.2083 | 2019-05-17 | 1.4327 | 2.4586 | 4.1555 | 4.1555 | 4.1555 | 4.1555
2021-03-19 13:00 | 2.2349 | 2.7196 | 2.6609 | 2.8621 | 2.7112 | 2.9124 | 1.3946 | 2.3916 | 2.9511 | 2.9511 | 3.3241 | 3.3241 | 2019-05-17 01:00 | 1.4327 | 2.4586 | 4.1555 | 4.1555 | 4.1555 | 4.1555
2021-03-19 14:00 | 2.1091 | 2.5666 | 2.5112 | 2.701 | 2.5587 | 2.7485 | 1.3261 | 2.274 | 2.8059 | 2.8059 | 3.1606 | 3.1606 | 2019-05-17 02:00 | 1.4099 | 2.4194 | 4.0891 | 4.0891 | 4.0891 | 4.0891
2021-03-19 15:00 | 2.0662 | 2.5144 | 2.4602 | 2.6461 | 2.5067 | 2.6926 | 1.286 | 2.2054 | 2.7213 | 2.7213 | 3.0652 | 3.0652 | 2019-05-17 03:00 | 1.4175 | 2.4324 | 4.1112 | 4.1112 | 4.1112 | 4.1112
2021-03-19 16:00 | 1.9548 | 2.3788 | 2.3275 | 2.5034 | 2.3714 | 2.5474 | 1.3403 | 2.2985 | 2.8362 | 2.8362 | 3.1947 | 3.1947 | 2019-05-17 04:00 | 1.4861 | 2.5501 | 4.3102 | 4.3102 | 4.3102 | 4.3102
2021-03-19 17:00 | 1.9634 | 2.3892 | 2.3377 | 2.5144 | 2.3818 | 2.5585 | 1.4604 | 2.5043 | 3.0902 | 3.0902 | 3.4807 | 3.4807 | 2019-05-17 05:00 | 1.6385 | 2.8117 | 4.7522 | 4.7522 | 4.7522 | 4.7522
2021-03-19 18:00 | 2.0434 | 2.4866 | 2.4329 | 2.6169 | 2.4789 | 2.6628 | 1.529 | 2.6219 | 3.2353 | 3.2353 | 3.6442 | 3.6442 | 2019-05-17 06:00 | 1.7528 | 3.0079 | 5.0838 | 5.0838 | 5.0838 | 5.0838
2021-03-19 19:00 | 1.9062 | 2.3197 | 2.2696 | 2.4412 | 2.3125 | 2.4841 | 1.6176 | 2.7739 | 3.4228 | 3.4228 | 3.8554 | 3.8554 | 2019-05-17 07:00 | 1.8595 | 3.191 | 5.3932 | 5.3932 | 5.3932 | 5.3932
2021-03-19 20:00 | 1.8433 | 2.2431 | 2.1948 | 2.3607 | 2.2362 | 2.4021 | 1.6233 | 2.7837 | 3.4349 | 3.4349 | 3.869 | 3.869 | 2019-05-17 08:00 | 2.0043 | 3.4394 | 5.8132 | 5.8132 | 5.8132 | 5.8132
2021-03-19 21:00 | 1.8062 | 2.1979 | 2.1505 | 2.3131 | 2.1912 | 2.3537 | 1.6118 | 2.7641 | 3.4107 | 3.4107 | 3.8418 | 3.8418 | 2019-05-17 09:00 | 2.0043 | 3.4394 | 5.8132 | 5.8132 | 5.8132 | 5.8132
2021-03-19 22:00 | 1.6461 | 2.0032 | 1.96 | 2.1081 | 1.997 | 2.1452 | 1.3403 | 2.2985 | 2.8362 | 2.8362 | 3.1947 | 3.1947 | 2019-05-17 10:00 | 1.9357 | 3.3217 | 5.6143 | 5.6143 | 5.6143 | 5.6143
2021-03-19 23:00 | 1.5833 | 1.9267 | 1.8851 | 2.0276 | 1.9207 | 2.0632 | 1.166 | 1.9995 | 2.4673 | 2.4673 | 2.7791 | 2.7791 | 2019-05-17 11:00 | 1.9891 | 3.4133 | 5.769 | 5.769 | 5.769 | 5.769
2021-03-20 | 1.4778 | 1.7984 | 1.7596 | 1.8926 | 1.7928 | 1.9258 | 1.0117 | 1.7349 | 2.1407 | 2.1407 | 2.4113 | 2.4113 | 2019-05-17 12:00 | 1.9586 | 3.361 | 5.6806 | 5.6806 | 5.6806 | 5.6806
2021-03-20 01:00 | 1.3232 | 1.6102 | 1.5755 | 1.6945 | 1.6052 | 1.7243 | 0.84879 | 1.4555 | 1.796 | 1.796 | 2.0231 | 2.0231 | 2019-05-17 13:00 | 1.9738 | 3.3871 | 5.7248 | 5.7248 | 5.7248 | 5.7248
2021-03-20 02:00 | 1.2432 | 1.5128 | 1.4802 | 1.5921 | 1.5082 | 1.62 | 0.77166 | 1.3233 | 1.6328 | 1.6328 | 1.8392 | 1.8392 | 2019-05-17 14:00 | 1.9662 | 3.374 | 5.7027 | 5.7027 | 5.7027 | 5.7027
2021-03-20 03:00 | 1.2403 | 1.5093 | 1.4768 | 1.5884 | 1.5047 | 1.6163 | 0.74305 | 1.2742 | 1.5723 | 1.5723 | 1.771 | 1.771 | 2019-05-17 15:00 | 1.9967 | 3.4264 | 5.7911 | 5.7911 | 5.7911 | 5.7911
2021-03-20 04:00 | 1.2603 | 1.5337 | 1.5006 | 1.614 | 1.529 | 1.6424 | 0.74577 | 1.2789 | 1.5781 | 1.5781 | 1.7775 | 1.7775 | 2019-05-17 16:00 | 1.9205 | 3.2956 | 5.5701 | 5.5701 | 5.5701 | 5.5701
2021-03-20 05:00 | 1.3994 | 1.703 | 1.6662 | 1.7922 | 1.6977 | 1.8237 | 0.79735 | 1.3673 | 1.6872 | 1.6872 | 1.9004 | 1.9004 | 2019-05-17 17:00 | 2.0043 | 3.4394 | 5.8132 | 5.8132 | 5.8132 | 5.8132
2021-03-20 06:00 | 1.4547 | 1.7702 | 1.732 | 1.8629 | 1.7647 | 1.8956 | 0.82015 | 1.4064 | 1.7354 | 1.7354 | 1.9548 | 1.9548 | 2019-05-17 18:00 | 1.8671 | 3.204 | 5.4154 | 5.4154 | 5.4154 | 5.4154
2021-03-20 07:00 | 1.5433 | 1.878 | 1.8375 | 1.9764 | 1.8722 | 2.0111 | 1.0488 | 1.7986 | 2.2194 | 2.2194 | 2.4999 | 2.4999 | 2019-05-17 19:00 | 1.89 | 3.2433 | 5.4817 | 5.4817 | 5.4817 | 5.4817
2021-03-20 08:00 | 1.729 | 2.104 | 2.0586 | 2.2143 | 2.0976 | 2.2532 | 1.2403 | 2.1269 | 2.6245 | 2.6245 | 2.9562 | 2.9562 | 2019-05-17 20:00 | 1.669 | 2.864 | 4.8407 | 4.8407 | 4.8407 | 4.8407
2021-03-20 09:00 | 1.8376 | 2.2362 | 2.188 | 2.3533 | 2.2293 | 2.3947 | 1.4664 | 2.5146 | 3.1028 | 3.1028 | 3.495 | 3.495 | 2019-05-17 21:00 | 1.6614 | 2.8509 | 4.8186 | 4.8186 | 4.8186 | 4.8186
2021-03-20 10:00 | 1.9291 | 2.3475 | 2.2968 | 2.4705 | 2.3402 | 2.5139 | 1.6376 | 2.8082 | 3.4651 | 3.4651 | 3.9031 | 3.9031 | 2019-05-17 22:00 | 1.6995 | 2.9163 | 4.9291 | 4.9291 | 4.9291 | 4.9291
2021-03-20 11:00 | 1.9576 | 2.3823 | 2.3309 | 2.5071 | 2.3749 | 2.5511 | 1.609 | 2.7592 | 3.4046 | 3.4046 | 3.8349 | 3.8349 | 2019-05-17 23:00 | 1.5928 | 2.7332 | 4.6196 | 4.6196 | 4.6196 | 4.6196
2021-03-20 12:00 | 1.8805 | 2.2884 | 2.239 | 2.4082 | 2.2813 | 2.4505 | 1.5775 | 2.7052 | 3.3381 | 3.3381 | 3.76 | 3.76 | 2019-05-18 | 1.5471 | 2.6548 | 4.487 | 4.487 | 4.487 | 4.487
2021-03-20 13:00 | 1.8205 | 2.2153 | 2.1675 | 2.3314 | 2.2085 | 2.3723 | 1.5375 | 2.6366 | 3.2534 | 3.2534 | 3.6647 | 3.6647 | 2019-05-18 01:00 | 1.509 | 2.5894 | 4.3765 | 4.3765 | 4.3765 | 4.3765
2021-03-20 14:00 | 1.729 | 2.104 | 2.0586 | 2.2143 | 2.0976 | 2.2532 | 1.5718 | 2.6954 | 3.326 | 3.326 | 3.7464 | 3.7464 | 2019-05-18 02:00 | 1.4023 | 2.4063 | 4.067 | 4.067 | 4.067 | 4.067
2021-03-20 15:00 | 1.7176 | 2.0901 | 2.045 | 2.1996 | 2.0837 | 2.2383 | 1.4975 | 2.568 | 3.1688 | 3.1688 | 3.5693 | 3.5693 | 2019-05-18 03:00 | 1.4023 | 2.4063 | 4.067 | 4.067 | 4.067 | 4.067
2021-03-20 16:00 | 1.689 | 2.0553 | 2.011 | 2.163 | 2.049 | 2.201 | 1.5232 | 2.6121 | 3.2232 | 3.2232 | 3.6306 | 3.6306 | 2019-05-18 04:00 | 1.4556 | 2.4978 | 4.2218 | 4.2218 | 4.2218 | 4.2218
2021-03-20 17:00 | 1.7519 | 2.1319 | 2.0859 | 2.2435 | 2.1253 | 2.283 | 1.5461 | 2.6513 | 3.2716 | 3.2716 | 3.6851 | 3.6851 | 2019-05-18 05:00 | 1.6309 | 2.7986 | 4.7301 | 4.7301 | 4.7301 | 4.7301
2021-03-20 18:00 | 1.8348 | 2.2327 | 2.1845 | 2.3497 | 2.2258 | 2.391 | 1.5661 | 2.6856 | 3.3139 | 3.3139 | 3.7328 | 3.7328 | 2019-05-18 06:00 | 1.6309 | 2.7986 | 4.7301 | 4.7301 | 4.7301 | 4.7301
2021-03-20 19:00 | 1.8605 | 2.264 | 2.2152 | 2.3826 | 2.257 | 2.4245 | 1.5775 | 2.7052 | 3.3381 | 3.3381 | 3.76 | 3.76 | 2019-05-18 07:00 | 1.7757 | 3.0471 | 5.1501 | 5.1501 | 5.1501 | 5.1501
2021-03-20 20:00 | 1.7176 | 2.0901 | 2.045 | 2.1996 | 2.0837 | 2.2383 | 1.5375 | 2.6366 | 3.2534 | 3.2534 | 3.6647 | 3.6647 | 2019-05-18 08:00 | 1.9281 | 3.3087 | 5.5922 | 5.5922 | 5.5922 | 5.5922
2021-03-20 21:00 | 1.629 | 1.9823 | 1.9396 | 2.0862 | 1.9762 | 2.1228 | 1.4775 | 2.5337 | 3.1265 | 3.1265 | 3.5216 | 3.5216 | 2019-05-18 09:00 | 1.9129 | 3.2825 | 5.548 | 5.548 | 5.548 | 5.548
2021-03-20 22:00 | 1.5804 | 1.9232 | 1.8817 | 2.0239 | 1.9173 | 2.0595 | 1.3575 | 2.3279 | 2.8725 | 2.8725 | 3.2355 | 3.2355 | 2019-05-18 10:00 | 1.9281 | 3.3087 | 5.5922 | 5.5922 | 5.5922 | 5.5922
2021-03-20 23:00 | 1.5175 | 1.8467 | 1.8068 | 1.9434 | 1.841 | 1.9776 | 1.1263 | 1.9314 | 2.3833 | 2.3833 | 2.6845 | 2.6845 | 2019-05-18 11:00 | 1.9357 | 3.3217 | 5.6143 | 5.6143 | 5.6143 | 5.6143
2021-03-21 | 1.489 | 1.8119 | 1.7728 | 1.9068 | 1.8063 | 1.9403 | 0.97202 | 1.6669 | 2.0568 | 2.0568 | 2.3168 | 2.3168 | 2019-05-18 12:00 | 1.89 | 3.2433 | 5.4817 | 5.4817 | 5.4817 | 5.4817
2021-03-21 01:00 | 1.4061 | 1.711 | 1.6741 | 1.8007 | 1.7058 | 1.8323 | 0.82878 | 1.4212 | 1.7537 | 1.7537 | 1.9754 | 1.9754 | 2019-05-18 13:00 | 1.951 | 3.3479 | 5.6585 | 5.6585 | 5.6585 | 5.6585
2021-03-21 02:00 | 1.2718 | 1.5476 | 1.5142 | 1.6287 | 1.5428 | 1.6573 | 0.76305 | 1.3085 | 1.6146 | 1.6146 | 1.8187 | 1.8187 | 2019-05-18 14:00 | 1.951 | 3.3479 | 5.6585 | 5.6585 | 5.6585 | 5.6585
2021-03-21 03:00 | 1.2346 | 1.5024 | 1.47 | 1.5811 | 1.4978 | 1.6089 | 0.74305 | 1.2742 | 1.5723 | 1.5723 | 1.771 | 1.771 | 2019-05-18 15:00 | 1.8976 | 3.2563 | 5.5038 | 5.5038 | 5.5038 | 5.5038
2021-03-21 04:00 | 1.2718 | 1.5476 | 1.5142 | 1.6287 | 1.5428 | 1.6573 | 0.7259 | 1.2448 | 1.536 | 1.536 | 1.7301 | 1.7301 | 2019-05-18 16:00 | 2.0805 | 3.5702 | 6.0343 | 6.0343 | 6.0343 | 6.0343
2021-03-21 05:00 | 1.286 | 1.565 | 1.5312 | 1.647 | 1.5602 | 1.6759 | 0.78306 | 1.3428 | 1.657 | 1.657 | 1.8664 | 1.8664 | 2019-05-18 17:00 | 2.1034 | 3.6094 | 6.1006 | 6.1006 | 6.1006 | 6.1006
2021-03-21 06:00 | 1.3934 | 1.6956 | 1.659 | 1.7844 | 1.6904 | 1.8158 | 0.7573 | 1.2986 | 1.6024 | 1.6024 | 1.805 | 1.805 | 2019-05-18 18:00 | 1.9891 | 3.4133 | 5.769 | 5.769 | 5.769 | 5.769
2021-03-21 07:00 | 1.4661 | 1.7841 | 1.7456 | 1.8775 | 1.7786 | 1.9105 | 0.93131 | 1.597 | 1.9707 | 1.9707 | 2.2197 | 2.2197 | 2019-05-18 19:00 | 1.8214 | 3.1256 | 5.2827 | 5.2827 | 5.2827 | 5.2827
2021-03-21 08:00 | 1.6576 | 2.0171 | 1.9736 | 2.1228 | 2.0109 | 2.1601 | 1.1546 | 1.9799 | 2.4431 | 2.4431 | 2.7519 | 2.7519 | 2019-05-18 20:00 | 1.7681 | 3.034 | 5.128 | 5.128 | 5.128 | 5.128
2021-03-21 09:00 | 1.7062 | 2.0762 | 2.0314 | 2.185 | 2.0698 | 2.2234 | 1.2432 | 2.1318 | 2.6306 | 2.6306 | 2.9631 | 2.9631 | 2019-05-18 21:00 | 1.7452 | 2.9948 | 5.0617 | 5.0617 | 5.0617 | 5.0617
2021-03-21 10:00 | 1.8284 | 2.225 | 2.177 | 2.3415 | 2.2181 | 2.3827 | 1.629 | 2.7935 | 3.447 | 3.447 | 3.8826 | 3.8826 | 2019-05-18 22:00 | 1.7071 | 2.9294 | 4.9512 | 4.9512 | 4.9512 | 4.9512
2021-03-21 11:00 | 1.8605 | 2.264 | 2.2152 | 2.3826 | 2.257 | 2.4245 | 1.5804 | 2.7101 | 3.3442 | 3.3442 | 3.7668 | 3.7668 | 2019-05-18 23:00 | 1.5699 | 2.694 | 4.5533 | 4.5533 | 4.5533 | 4.5533
2021-03-21 12:00 | 1.8376 | 2.2362 | 2.188 | 2.3533 | 2.2293 | 2.3947 | 1.6318 | 2.7984 | 3.453 | 3.453 | 3.8894 | 3.8894 | 2019-05-19 | 1.5318 | 2.6286 | 4.4428 | 4.4428 | 4.4428 | 4.4428
2021-03-21 13:00 | 1.9119 | 2.3266 | 2.2764 | 2.4485 | 2.3194 | 2.4915 | 1.6376 | 2.8082 | 3.4651 | 3.4651 | 3.9031 | 3.9031 | 2019-05-19 01:00 | 1.4556 | 2.4978 | 4.2218 | 4.2218 | 4.2218 | 4.2218
2021-03-21 14:00 | 1.809 | 2.2014 | 2.1539 | 2.3167 | 2.1946 | 2.3574 | 1.5861 | 2.7199 | 3.3563 | 3.3563 | 3.7805 | 3.7805 | 2019-05-19 02:00 | 1.4785 | 2.5371 | 4.2881 | 4.2881 | 4.2881 | 4.2881
2021-03-21 15:00 | 1.7833 | 2.1701 | 2.1233 | 2.2838 | 2.1634 | 2.3239 | 1.5433 | 2.6464 | 3.2655 | 3.2655 | 3.6783 | 3.6783 | 2019-05-19 03:00 | 1.4785 | 2.5371 | 4.2881 | 4.2881 | 4.2881 | 4.2881
2021-03-21 16:00 | 1.8405 | 2.2397 | 2.1914 | 2.357 | 2.2328 | 2.3984 | 1.5261 | 2.617 | 3.2293 | 3.2293 | 3.6374 | 3.6374 | 2019-05-19 04:00 | 1.4937 | 2.5632 | 4.3323 | 4.3323 | 4.3323 | 4.3323
2021-03-21 17:00 | 1.9777 | 2.4066 | 2.3547 | 2.5327 | 2.3992 | 2.5772 | 1.5747 | 2.7003 | 3.3321 | 3.3321 | 3.7532 | 3.7532 | 2019-05-19 05:00 | 1.5242 | 2.6155 | 4.4207 | 4.4207 | 4.4207 | 4.4207
2021-03-21 18:00 | 2.072 | 2.5214 | 2.467 | 2.6535 | 2.5136 | 2.7001 | 1.6004 | 2.7445 | 3.3865 | 3.3865 | 3.8145 | 3.8145 | 2019-05-19 06:00 | 1.5547 | 2.6678 | 4.5091 | 4.5091 | 4.5091 | 4.5091
2021-03-21 19:00 | 2.192 | 2.6674 | 2.6099 | 2.8072 | 2.6592 | 2.8565 | 1.7233 | 2.9552 | 3.6465 | 3.6465 | 4.1074 | 4.1074 | 2019-05-19 07:00 | 1.7528 | 3.0079 | 5.0838 | 5.0838 | 5.0838 | 5.0838
2021-03-21 20:00 | 1.9348 | 2.3544 | 2.3036 | 2.4778 | 2.3472 | 2.5213 | 1.5785 | 2.7069 | 3.3402 | 3.3402 | 3.7624 | 3.7624 | 2019-05-19 08:00 | 1.8824 | 3.2302 | 5.4596 | 5.4596 | 5.4596 | 5.4596
2021-03-21 21:00 | 1.8776 | 2.2849 | 2.2356 | 2.4046 | 2.2778 | 2.4468 | 1.5261 | 2.617 | 3.2293 | 3.2293 | 3.6374 | 3.6374 | 2019-05-19 09:00 | 1.9662 | 3.374 | 5.7027 | 5.7027 | 5.7027 | 5.7027
2021-03-21 22:00 | 1.5997 | 1.9466 | 1.9046 | 2.0486 | 1.9406 | 2.0846 | 1.2575 | 2.1564 | 2.6608 | 2.6608 | 2.9971 | 2.9971 | 2019-05-19 10:00 | 1.9357 | 3.3217 | 5.6143 | 5.6143 | 5.6143 | 5.6143
2021-03-21 23:00 | 1.5262 | 1.8573 | 1.8172 | 1.9545 | 1.8515 | 1.9889 | 1.0946 | 1.877 | 2.3161 | 2.3161 | 2.6089 | 2.6089 | 2019-05-19 11:00 | 1.9815 | 3.4002 | 5.7469 | 5.7469 | 5.7469 | 5.7469
2021-03-22 | 1.4404 | 1.7528 | 1.715 | 1.8446 | 1.7474 | 1.877 | 0.88594 | 1.5192 | 1.8747 | 1.8747 | 2.1116 | 2.1116 | 2019-05-19 12:00 | 1.9891 | 3.4133 | 5.769 | 5.769 | 5.769 | 5.769
2021-03-22 01:00 | 1.3346 | 1.6241 | 1.5891 | 1.7092 | 1.6191 | 1.7392 | 0.79163 | 1.3575 | 1.6751 | 1.6751 | 1.8868 | 1.8868 | 2019-05-19 13:00 | 1.9738 | 3.3871 | 5.7248 | 5.7248 | 5.7248 | 5.7248
2021-03-22 02:00 | 1.3346 | 1.6241 | 1.5891 | 1.7092 | 1.6191 | 1.7392 | 0.76877 | 1.3183 | 1.6267 | 1.6267 | 1.8323 | 1.8323 | 2019-05-19 14:00 | 1.9891 | 3.4133 | 5.769 | 5.769 | 5.769 | 5.769
2021-03-22 03:00 | 1.2632 | 1.5372 | 1.504 | 1.6177 | 1.5324 | 1.6461 | 0.76591 | 1.3134 | 1.6207 | 1.6207 | 1.8255 | 1.8255 | 2019-05-19 15:00 | 1.951 | 3.3479 | 5.6585 | 5.6585 | 5.6585 | 5.6585
2021-03-22 04:00 | 1.2946 | 1.5754 | 1.5414 | 1.6579 | 1.5706 | 1.6871 | 0.78306 | 1.3428 | 1.657 | 1.657 | 1.8664 | 1.8664 | 2019-05-19 16:00 | 1.9357 | 3.3217 | 5.6143 | 5.6143 | 5.6143 | 5.6143
2021-03-22 05:00 | 1.3689 | 1.6658 | 1.6299 | 1.7531 | 1.6607 | 1.7839 | 0.76305 | 1.3085 | 1.6146 | 1.6146 | 1.8187 | 1.8187 | 2019-05-19 17:00 | 1.9815 | 3.4002 | 5.7469 | 5.7469 | 5.7469 | 5.7469
2021-03-22 06:00 | 1.8519 | 2.2536 | 2.205 | 2.3716 | 2.2466 | 2.4133 | 0.94277 | 1.6167 | 1.9949 | 1.9949 | 2.247 | 2.247 | 2019-05-19 18:00 | 1.8976 | 3.2563 | 5.5038 | 5.5038 | 5.5038 | 5.5038
2021-03-22 07:00 | 2.1063 | 2.5631 | 2.5078 | 2.6974 | 2.5552 | 2.7448 | 1.2975 | 2.225 | 2.7455 | 2.7455 | 3.0925 | 3.0925 | 2019-05-19 19:00 | 1.8214 | 3.1256 | 5.2827 | 5.2827 | 5.2827 | 5.2827
2021-03-22 08:00 | 2.2034 | 2.6813 | 2.6235 | 2.8218 | 2.6731 | 2.8714 | 1.2889 | 2.2103 | 2.7273 | 2.7273 | 3.072 | 3.072 | 2019-05-19 20:00 | 1.8214 | 3.1256 | 5.2827 | 5.2827 | 5.2827 | 5.2827
2021-03-22 09:00 | 2.2892 | 2.7857 | 2.7256 | 2.9316 | 2.7771 | 2.9831 | 1.4118 | 2.421 | 2.9874 | 2.9874 | 3.3649 | 3.3649 | 2019-05-19 21:00 | 1.669 | 2.864 | 4.8407 | 4.8407 | 4.8407 | 4.8407
2021-03-22 10:00 | 2.292 | 2.7892 | 2.729 | 2.9353 | 2.7806 | 2.9868 | 1.3832 | 2.372 | 2.9269 | 2.9269 | 3.2968 | 3.2968 | 2019-05-19 22:00 | 1.6233 | 2.7855 | 4.708 | 4.708 | 4.708 | 4.708
2021-03-22 11:00 | 2.2377 | 2.7231 | 2.6643 | 2.8657 | 2.7147 | 2.9161 | 1.4175 | 2.4308 | 2.9995 | 2.9995 | 3.3786 | 3.3786 | 2019-05-19 23:00 | 1.4785 | 2.5371 | 4.2881 | 4.2881 | 4.2881 | 4.2881
2021-03-22 12:00 | 2.2234 | 2.7057 | 2.6473 | 2.8474 | 2.6973 | 2.8975 | 1.3918 | 2.3867 | 2.945 | 2.945 | 3.3173 | 3.3173 | 2019-05-20 | 1.4099 | 2.4194 | 4.0891 | 4.0891 | 4.0891 | 4.0891
2021-03-22 13:00 | 2.2091 | 2.6883 | 2.6303 | 2.8291 | 2.68 | 2.8788 | 1.4032 | 2.4063 | 2.9692 | 2.9692 | 3.3445 | 3.3445 | 2019-05-20 01:00 | 1.4099 | 2.4194 | 4.0891 | 4.0891 | 4.0891 | 4.0891
2021-03-22 14:00 | 2.1291 | 2.5909 | 2.535 | 2.7266 | 2.5829 | 2.7746 | 1.4461 | 2.4798 | 3.0599 | 3.0599 | 3.4467 | 3.4467 | 2019-05-20 02:00 | 1.3718 | 2.354 | 3.9786 | 3.9786 | 3.9786 | 3.9786
2021-03-22 15:00 | 2.2377 | 2.7231 | 2.6643 | 2.8657 | 2.7147 | 2.9161 | 1.3975 | 2.3965 | 2.9571 | 2.9571 | 3.3309 | 3.3309 | 2019-05-20 03:00 | 1.3718 | 2.354 | 3.9786 | 3.9786 | 3.9786 | 3.9786
2021-03-22 16:00 | 2.132 | 2.5944 | 2.5384 | 2.7303 | 2.5864 | 2.7783 | 1.4132 | 2.4235 | 2.9904 | 2.9904 | 3.3684 | 3.3684 | 2019-05-20 04:00 | 1.4327 | 2.4586 | 4.1555 | 4.1555 | 4.1555 | 4.1555
2021-03-22 17:00 | 2.3149 | 2.817 | 2.7562 | 2.9645 | 2.8083 | 3.0166 | 1.6176 | 2.7739 | 3.4228 | 3.4228 | 3.8554 | 3.8554 | 2019-05-20 05:00 | 1.5471 | 2.6548 | 4.487 | 4.487 | 4.487 | 4.487
2021-03-22 18:00 | 2.4635 | 2.9978 | 2.9331 | 3.1549 | 2.9886 | 3.2103 | 1.5718 | 2.6954 | 3.326 | 3.326 | 3.7464 | 3.7464 | 2019-05-20 06:00 | 1.7528 | 3.0079 | 5.0838 | 5.0838 | 5.0838 | 5.0838
2021-03-22 19:00 | 2.3377 | 2.8448 | 2.7834 | 2.9938 | 2.836 | 3.0464 | 1.6033 | 2.7494 | 3.3925 | 3.3925 | 3.8213 | 3.8213 | 2019-05-20 07:00 | 1.9053 | 3.2694 | 5.5259 | 5.5259 | 5.5259 | 5.5259
2021-03-22 20:00 | 2.1949 | 2.6709 | 2.6133 | 2.8108 | 2.6627 | 2.8602 | 1.5861 | 2.7199 | 3.3563 | 3.3563 | 3.7805 | 3.7805 | 2019-05-20 08:00 | 2.1034 | 3.6094 | 6.1006 | 6.1006 | 6.1006 | 6.1006
2021-03-22 21:00 | 2.0548 | 2.5005 | 2.4466 | 2.6315 | 2.4928 | 2.6777 | 1.4804 | 2.5386 | 3.1325 | 3.1325 | 3.5284 | 3.5284 | 2019-05-20 09:00 | 2.0882 | 3.5833 | 6.0564 | 6.0564 | 6.0564 | 6.0564
2021-03-22 22:00 | 1.8348 | 2.2327 | 2.1845 | 2.3497 | 2.2258 | 2.391 | 1.2386 | 2.1239 | 2.6208 | 2.6208 | 2.952 | 2.952 | 2019-05-20 10:00 | 2.1034 | 3.6094 | 6.1006 | 6.1006 | 6.1006 | 6.1006
2021-03-22 23:00 | 1.6061 | 1.9545 | 1.9123 | 2.0569 | 1.9485 | 2.093 | 1.0488 | 1.7986 | 2.2194 | 2.2194 | 2.4999 | 2.4999 | 2019-05-20 11:00 | 2.0348 | 3.4917 | 5.9016 | 5.9016 | 5.9016 | 5.9016
2021-03-23 | 1.4633 | 1.7806 | 1.7422 | 1.8739 | 1.7751 | 1.9068 | 0.93452 | 1.6026 | 1.9775 | 1.9775 | 2.2274 | 2.2274 | 2019-05-20 12:00 | 2.1644 | 3.7141 | 6.2774 | 6.2774 | 6.2774 | 6.2774
2021-03-23 01:00 | 1.3661 | 1.6624 | 1.6265 | 1.7495 | 1.6572 | 1.7802 | 0.80592 | 1.382 | 1.7053 | 1.7053 | 1.9209 | 1.9209 | 2019-05-20 13:00 | 2.1263 | 3.6487 | 6.1669 | 6.1669 | 6.1669 | 6.1669
2021-03-23 02:00 | 1.3458 | 1.6377 | 1.6024 | 1.7235 | 1.6327 | 1.7538 | 0.76019 | 1.3036 | 1.6086 | 1.6086 | 1.8119 | 1.8119 | 2019-05-20 14:00 | 2.111 | 3.6225 | 6.1227 | 6.1227 | 6.1227 | 6.1227
2021-03-23 03:00 | 1.3032 | 1.5858 | 1.5516 | 1.6689 | 1.581 | 1.6982 | 0.78306 | 1.3428 | 1.657 | 1.657 | 1.8664 | 1.8664 | 2019-05-20 15:00 | 2.0805 | 3.5702 | 6.0343 | 6.0343 | 6.0343 | 6.0343
2021-03-23 04:00 | 1.3203 | 1.6067 | 1.5721 | 1.6909 | 1.6018 | 1.7206 | 0.70594 | 1.2106 | 1.4938 | 1.4938 | 1.6826 | 1.6826 | 2019-05-20 16:00 | 2.1491 | 3.6879 | 6.2332 | 6.2332 | 6.2332 | 6.2332
2021-03-23 05:00 | 1.5332 | 1.8658 | 1.8256 | 1.9636 | 1.8601 | 1.998 | 0.78591 | 1.3477 | 1.663 | 1.663 | 1.8732 | 1.8732 | 2019-05-20 17:00 | 2.1263 | 3.6487 | 6.1669 | 6.1669 | 6.1669 | 6.1669
2021-03-23 06:00 | 1.7747 | 2.1597 | 2.1131 | 2.2728 | 2.153 | 2.3127 | 0.97453 | 1.6712 | 2.0621 | 2.0621 | 2.3228 | 2.3228 | 2019-05-20 18:00 | 2.1339 | 3.6618 | 6.189 | 6.189 | 6.189 | 6.189
2021-03-23 07:00 | 2.172 | 2.6431 | 2.5861 | 2.7815 | 2.6349 | 2.8304 | 1.2117 | 2.0779 | 2.5641 | 2.5641 | 2.8881 | 2.8881 | 2019-05-20 19:00 | 1.9815 | 3.4002 | 5.7469 | 5.7469 | 5.7469 | 5.7469
2021-03-23 08:00 | 2.312 | 2.8135 | 2.7528 | 2.9609 | 2.8048 | 3.0129 | 1.3203 | 2.2642 | 2.7939 | 2.7939 | 3.147 | 3.147 | 2019-05-20 20:00 | 1.8748 | 3.2171 | 5.4375 | 5.4375 | 5.4375 | 5.4375
2021-03-23 09:00 | 2.4321 | 2.9596 | 2.8957 | 3.1146 | 2.9504 | 3.1693 | 1.3203 | 2.2642 | 2.7939 | 2.7939 | 3.147 | 3.147 | 2019-05-20 21:00 | 1.7605 | 3.0209 | 5.1059 | 5.1059 | 5.1059 | 5.1059
2021-03-23 10:00 | 2.4378 | 2.9665 | 2.9025 | 3.1219 | 2.9574 | 3.1768 | 1.3918 | 2.3867 | 2.945 | 2.945 | 3.3173 | 3.3173 | 2019-05-20 22:00 | 1.7605 | 3.0209 | 5.1059 | 5.1059 | 5.1059 | 5.1059
2021-03-23 11:00 | 2.635 | 3.2065 | 3.1373 | 3.3745 | 3.1966 | 3.4337 | 1.4718 | 2.5239 | 3.1144 | 3.1144 | 3.508 | 3.508 | 2019-05-20 23:00 | 1.6538 | 2.8379 | 4.7965 | 4.7965 | 4.7965 | 4.7965
2021-03-23 12:00 | 2.4806 | 3.0187 | 2.9536 | 3.1768 | 3.0094 | 3.2326 | 1.4747 | 2.5288 | 3.1204 | 3.1204 | 3.5148 | 3.5148 | 2019-05-21 | 1.5394 | 2.6417 | 4.4649 | 4.4649 | 4.4649 | 4.4649
2021-03-23 13:00 | 2.4921 | 3.0326 | 2.9672 | 3.1915 | 3.0232 | 3.2475 | 1.4689 | 2.519 | 3.1083 | 3.1083 | 3.5012 | 3.5012 | 2019-05-21 01:00 | 1.509 | 2.5894 | 4.3765 | 4.3765 | 4.3765 | 4.3765
2021-03-23 14:00 | 2.4035 | 2.9248 | 2.8617 | 3.078 | 2.9158 | 3.1321 | 1.4089 | 2.4161 | 2.9813 | 2.9813 | 3.3581 | 3.3581 | 2019-05-21 02:00 | 1.509 | 2.5894 | 4.3765 | 4.3765 | 4.3765 | 4.3765
2021-03-23 15:00 | 2.272 | 2.7648 | 2.7052 | 2.9096 | 2.7563 | 2.9608 | 1.3632 | 2.3377 | 2.8846 | 2.8846 | 3.2491 | 3.2491 | 2019-05-21 03:00 | 1.4785 | 2.5371 | 4.2881 | 4.2881 | 4.2881 | 4.2881
2021-03-23 16:00 | 2.2434 | 2.73 | 2.6711 | 2.873 | 2.7216 | 2.9235 | 1.4318 | 2.4553 | 3.0297 | 3.0297 | 3.4126 | 3.4126 | 2019-05-21 04:00 | 1.4785 | 2.5371 | 4.2881 | 4.2881 | 4.2881 | 4.2881
2021-03-23 17:00 | 2.2777 | 2.7718 | 2.712 | 2.917 | 2.7632 | 2.9682 | 1.5775 | 2.7052 | 3.3381 | 3.3381 | 3.76 | 3.76 | 2019-05-21 05:00 | 1.6919 | 2.9032 | 4.907 | 4.907 | 4.907 | 4.907
2021-03-23 18:00 | 2.5064 | 3.05 | 2.9842 | 3.2098 | 3.0406 | 3.2662 | 1.609 | 2.7592 | 3.4046 | 3.4046 | 3.8349 | 3.8349 | 2019-05-21 06:00 | 1.8519 | 3.1779 | 5.3711 | 5.3711 | 5.3711 | 5.3711
2021-03-23 19:00 | 2.4263 | 2.9526 | 2.8889 | 3.1073 | 2.9435 | 3.1619 | 1.729 | 2.965 | 3.6586 | 3.6586 | 4.121 | 4.121 | 2019-05-21 07:00 | 2.0501 | 3.5179 | 5.9458 | 5.9458 | 5.9458 | 5.9458
2021-03-23 20:00 | 2.212 | 2.6918 | 2.6337 | 2.8328 | 2.6835 | 2.8826 | 1.6433 | 2.818 | 3.4772 | 3.4772 | 3.9167 | 3.9167 | 2019-05-21 08:00 | 2.1186 | 3.6356 | 6.1448 | 6.1448 | 6.1448 | 6.1448
2021-03-23 21:00 | 2.0148 | 2.4518 | 2.3989 | 2.5803 | 2.4443 | 2.6256 | 1.5347 | 2.6317 | 3.2474 | 3.2474 | 3.6578 | 3.6578 | 2019-05-21 09:00 | 2.0729 | 3.5571 | 6.0121 | 6.0121 | 6.0121 | 6.0121
2021-03-23 22:00 | 1.8161 | 2.21 | 2.1623 | 2.3257 | 2.2031 | 2.3666 | 1.3002 | 2.2297 | 2.7513 | 2.7513 | 3.099 | 3.099 | 2019-05-21 10:00 | 2.0043 | 3.4394 | 5.8132 | 5.8132 | 5.8132 | 5.8132
2021-03-23 23:00 | 1.6061 | 1.9545 | 1.9123 | 2.0569 | 1.9485 | 2.093 | 1.0203 | 1.7497 | 2.159 | 2.159 | 2.4319 | 2.4319 | 2019-05-21 11:00 | 2.0653 | 3.5441 | 5.99 | 5.99 | 5.99 | 5.99
2021-03-24 | 1.4489 | 1.7632 | 1.7252 | 1.8556 | 1.7578 | 1.8882 | 0.92886 | 1.5928 | 1.9655 | 1.9655 | 2.2139 | 2.2139 | 2019-05-21 12:00 | 2.1339 | 3.6618 | 6.189 | 6.189 | 6.189 | 6.189
2021-03-24 01:00 | 1.3432 | 1.6345 | 1.5993 | 1.7202 | 1.6295 | 1.7504 | 0.82592 | 1.4163 | 1.7477 | 1.7477 | 1.9686 | 1.9686 | 2019-05-21 13:00 | 2.1034 | 3.6094 | 6.1006 | 6.1006 | 6.1006 | 6.1006
2021-03-24 02:00 | 1.2976 | 1.5791 | 1.545 | 1.6618 | 1.5742 | 1.691 | 0.82878 | 1.4212 | 1.7537 | 1.7537 | 1.9754 | 1.9754 | 2019-05-21 14:00 | 2.1415 | 3.6748 | 6.2111 | 6.2111 | 6.2111 | 6.2111
2021-03-24 03:00 | 1.2832 | 1.5615 | 1.5278 | 1.6433 | 1.5567 | 1.6722 | 0.73762 | 1.2649 | 1.5608 | 1.5608 | 1.7581 | 1.7581 | 2019-05-21 15:00 | 2.2787 | 3.9102 | 6.6089 | 6.6089 | 6.6089 | 6.6089
2021-03-24 04:00 | 1.3118 | 1.5963 | 1.5618 | 1.6799 | 1.5914 | 1.7094 | 0.70875 | 1.2154 | 1.4997 | 1.4997 | 1.6893 | 1.6893 | 2019-05-21 16:00 | 2.1491 | 3.6879 | 6.2332 | 6.2332 | 6.2332 | 6.2332
2021-03-24 05:00 | 1.5345 | 1.8674 | 1.8271 | 1.9652 | 1.8616 | 1.9997 | 0.82878 | 1.4212 | 1.7537 | 1.7537 | 1.9754 | 1.9754 | 2019-05-21 17:00 | 2.1796 | 3.7402 | 6.3216 | 6.3216 | 6.3216 | 6.3216
2021-03-24 06:00 | 1.8862 | 2.2953 | 2.2458 | 2.4156 | 2.2882 | 2.458 | 0.9974 | 1.7104 | 2.1105 | 2.1105 | 2.3773 | 2.3773 | 2019-05-21 18:00 | 2.0577 | 3.531 | 5.9679 | 5.9679 | 5.9679 | 5.9679
2021-03-24 07:00 | 2.152 | 2.6187 | 2.5623 | 2.7559 | 2.6107 | 2.8043 | 1.3118 | 2.2495 | 2.7757 | 2.7757 | 3.1265 | 3.1265 | 2019-05-21 19:00 | 1.9357 | 3.3217 | 5.6143 | 5.6143 | 5.6143 | 5.6143
2021-03-24 08:00 | 2.2634 | 2.7544 | 2.695 | 2.8987 | 2.7459 | 2.9496 | 1.3603 | 2.3328 | 2.8785 | 2.8785 | 3.2423 | 3.2423 | 2019-05-21 20:00 | 1.89 | 3.2433 | 5.4817 | 5.4817 | 5.4817 | 5.4817
2021-03-24 09:00 | 2.2149 | 2.6953 | 2.6371 | 2.8364 | 2.6869 | 2.8863 | 1.3632 | 2.3377 | 2.8846 | 2.8846 | 3.2491 | 3.2491 | 2019-05-21 21:00 | 1.73 | 2.9686 | 5.0175 | 5.0175 | 5.0175 | 5.0175
2021-03-24 10:00 | 2.2091 | 2.6883 | 2.6303 | 2.8291 | 2.68 | 2.8788 | 1.3861 | 2.3769 | 2.9329 | 2.9329 | 3.3036 | 3.3036 | 2019-05-21 22:00 | 1.8367 | 3.1517 | 5.3269 | 5.3269 | 5.3269 | 5.3269
2021-03-24 11:00 | 2.3606 | 2.8726 | 2.8107 | 3.0231 | 2.8638 | 3.0762 | 1.4289 | 2.4504 | 3.0236 | 3.0236 | 3.4058 | 3.4058 | 2019-05-21 23:00 | 1.669 | 2.864 | 4.8407 | 4.8407 | 4.8407 | 4.8407
2021-03-24 12:00 | 2.3749 | 2.89 | 2.8277 | 3.0414 | 2.8811 | 3.0948 | 1.4004 | 2.4014 | 2.9632 | 2.9632 | 3.3377 | 3.3377 | 2019-05-22 | 1.5547 | 2.6678 | 4.5091 | 4.5091 | 4.5091 | 4.5091
2021-03-24 13:00 | 2.2463 | 2.7335 | 2.6745 | 2.8767 | 2.7251 | 2.9272 | 1.4518 | 2.4896 | 3.072 | 3.072 | 3.4603 | 3.4603 | 2019-05-22 01:00 | 1.5775 | 2.7071 | 4.5754 | 4.5754 | 4.5754 | 4.5754
2021-03-24 14:00 | 2.1977 | 2.6744 | 2.6167 | 2.8145 | 2.6661 | 2.8639 | 1.3861 | 2.3769 | 2.9329 | 2.9329 | 3.3036 | 3.3036 | 2019-05-22 02:00 | 1.5318 | 2.6286 | 4.4428 | 4.4428 | 4.4428 | 4.4428
2021-03-24 15:00 | 2.1548 | 2.6222 | 2.5657 | 2.7596 | 2.6141 | 2.8081 | 1.4032 | 2.4063 | 2.9692 | 2.9692 | 3.3445 | 3.3445 | 2019-05-22 03:00 | 1.5471 | 2.6548 | 4.487 | 4.487 | 4.487 | 4.487
2021-03-24 16:00 | 2.1263 | 2.5874 | 2.5316 | 2.723 | 2.5795 | 2.7708 | 1.286 | 2.2054 | 2.7213 | 2.7213 | 3.0652 | 3.0652 | 2019-05-22 04:00 | 1.5928 | 2.7332 | 4.6196 | 4.6196 | 4.6196 | 4.6196
2021-03-24 17:00 | 2.2206 | 2.7022 | 2.6439 | 2.8438 | 2.6939 | 2.8937 | 1.4632 | 2.5092 | 3.0962 | 3.0962 | 3.4876 | 3.4876 | 2019-05-22 05:00 | 1.7986 | 3.0863 | 5.2164 | 5.2164 | 5.2164 | 5.2164
2021-03-24 18:00 | 2.3835 | 2.9004 | 2.8379 | 3.0524 | 2.8915 | 3.106 | 1.529 | 2.6219 | 3.2353 | 3.2353 | 3.6442 | 3.6442 | 2019-05-22 06:00 | 1.829 | 3.1386 | 5.3048 | 5.3048 | 5.3048 | 5.3048
2021-03-24 19:00 | 2.3492 | 2.8587 | 2.797 | 3.0085 | 2.8499 | 3.0613 | 1.6318 | 2.7984 | 3.453 | 3.453 | 3.8894 | 3.8894 | 2019-05-22 07:00 | 1.9357 | 3.3217 | 5.6143 | 5.6143 | 5.6143 | 5.6143
2021-03-24 20:00 | 2.2063 | 2.6848 | 2.6269 | 2.8255 | 2.6765 | 2.8751 | 1.6347 | 2.8033 | 3.4591 | 3.4591 | 3.8963 | 3.8963 | 2019-05-22 08:00 | 2.2025 | 3.7795 | 6.3879 | 6.3879 | 6.3879 | 6.3879
2021-03-24 21:00 | 2.0577 | 2.504 | 2.45 | 2.6352 | 2.4963 | 2.6814 | 1.5747 | 2.7003 | 3.3321 | 3.3321 | 3.7532 | 3.7532 | 2019-05-22 09:00 | 2.0882 | 3.5833 | 6.0564 | 6.0564 | 6.0564 | 6.0564
2021-03-24 22:00 | 1.8823 | 2.2905 | 2.2411 | 2.4105 | 2.2835 | 2.4529 | 1.3178 | 2.2598 | 2.7884 | 2.7884 | 3.1409 | 3.1409 | 2019-05-22 10:00 | 2.2177 | 3.8056 | 6.4321 | 6.4321 | 6.4321 | 6.4321
2021-03-24 23:00 | 1.6236 | 1.9758 | 1.9331 | 2.0793 | 1.9697 | 2.1158 | 1.0831 | 1.8574 | 2.2919 | 2.2919 | 2.5816 | 2.5816 | 2019-05-22 11:00 | 2.111 | 3.6225 | 6.1227 | 6.1227 | 6.1227 | 6.1227
2021-03-25 | 1.5495 | 1.8856 | 1.845 | 1.9844 | 1.8798 | 2.0193 | 0.99746 | 1.7105 | 2.1106 | 2.1106 | 2.3774 | 2.3774 | 2019-05-22 12:00 | 2.1644 | 3.7141 | 6.2774 | 6.2774 | 6.2774 | 6.2774
2021-03-25 01:00 | 1.3661 | 1.6624 | 1.6265 | 1.7494 | 1.6572 | 1.7802 | 0.80299 | 1.377 | 1.6991 | 1.6991 | 1.9139 | 1.9139 | 2019-05-22 13:00 | 2.1263 | 3.6487 | 6.1669 | 6.1669 | 6.1669 | 6.1669
2021-03-25 02:00 | 1.3089 | 1.5928 | 1.5584 | 1.6762 | 1.5879 | 1.7057 | 0.80306 | 1.3771 | 1.6993 | 1.6993 | 1.9141 | 1.9141 | 2019-05-22 14:00 | 2.172 | 3.7271 | 6.2995 | 6.2995 | 6.2995 | 6.2995
2021-03-25 03:00 | 1.3063 | 1.5897 | 1.5554 | 1.6729 | 1.5848 | 1.7023 | 0.7259 | 1.2448 | 1.536 | 1.536 | 1.7301 | 1.7301 | 2019-05-22 15:00 | 2.0958 | 3.5964 | 6.0785 | 6.0785 | 6.0785 | 6.0785
2021-03-25 04:00 | 1.2975 | 1.5789 | 1.5448 | 1.6616 | 1.574 | 1.6908 | 0.7372 | 1.2642 | 1.5599 | 1.5599 | 1.7571 | 1.7571 | 2019-05-22 16:00 | 2.2101 | 3.7925 | 6.41 | 6.41 | 6.41 | 6.41
2021-03-25 05:00 | 1.4718 | 1.791 | 1.7524 | 1.8849 | 1.7855 | 1.918 | 0.78591 | 1.3477 | 1.663 | 1.663 | 1.8732 | 1.8732 | 2019-05-22 17:00 | 2.1339 | 3.6618 | 6.189 | 6.189 | 6.189 | 6.189
2021-03-25 06:00 | 1.8983 | 2.3101 | 2.2603 | 2.4311 | 2.303 | 2.4738 | 1.066 | 1.828 | 2.2556 | 2.2556 | 2.5407 | 2.5407 | 2019-05-22 18:00 | 2.1949 | 3.7664 | 6.3658 | 6.3658 | 6.3658 | 6.3658
2021-03-25 07:00 | 2.2091 | 2.6883 | 2.6303 | 2.8291 | 2.68 | 2.8788 | 1.2517 | 2.1466 | 2.6487 | 2.6487 | 2.9835 | 2.9835 | 2019-05-22 19:00 | 2.0272 | 3.4787 | 5.8795 | 5.8795 | 5.8795 | 5.8795
2021-03-25 08:00 | 2.2577 | 2.7474 | 2.6882 | 2.8913 | 2.739 | 2.9421 | 1.3432 | 2.3034 | 2.8422 | 2.8422 | 3.2015 | 3.2015 | 2019-05-22 20:00 | 1.8214 | 3.1256 | 5.2827 | 5.2827 | 5.2827 | 5.2827
2021-03-25 09:00 | 2.2434 | 2.73 | 2.6711 | 2.873 | 2.7216 | 2.9235 | 1.3489 | 2.3132 | 2.8543 | 2.8543 | 3.2151 | 3.2151 | 2019-05-22 21:00 | 1.7452 | 2.9948 | 5.0617 | 5.0617 | 5.0617 | 5.0617
2021-03-25 10:00 | 2.2377 | 2.7231 | 2.6643 | 2.8657 | 2.7147 | 2.9161 | 1.4146 | 2.4259 | 2.9934 | 2.9934 | 3.3718 | 3.3718 | 2019-05-22 22:00 | 1.7223 | 2.9556 | 4.9954 | 4.9954 | 4.9954 | 4.9954
2021-03-25 11:00 | 2.2749 | 2.7683 | 2.7086 | 2.9133 | 2.7598 | 2.9645 | 1.3575 | 2.328 | 2.8726 | 2.8726 | 3.2356 | 3.2356 | 2019-05-22 23:00 | 1.6309 | 2.7986 | 4.7301 | 4.7301 | 4.7301 | 4.7301
2021-03-25 12:00 | 2.2063 | 2.6848 | 2.6269 | 2.8255 | 2.6765 | 2.8751 | 1.3289 | 2.2789 | 2.812 | 2.812 | 3.1674 | 3.1674 | 2019-05-23 | 1.5013 | 2.5763 | 4.3544 | 4.3544 | 4.3544 | 4.3544
2021-03-25 13:00 | 2.3663 | 2.8796 | 2.8175 | 3.0304 | 2.8707 | 3.0837 | 1.4004 | 2.4014 | 2.9632 | 2.9632 | 3.3377 | 3.3377 | 2019-05-23 01:00 | 1.5013 | 2.5763 | 4.3544 | 4.3544 | 4.3544 | 4.3544
2021-03-25 14:00 | 2.0234 | 2.4622 | 2.4091 | 2.5912 | 2.4547 | 2.6368 | 1.3289 | 2.2789 | 2.812 | 2.812 | 3.1674 | 3.1674 | 2019-05-23 02:00 | 1.5394 | 2.6417 | 4.4649 | 4.4649 | 4.4649 | 4.4649
2021-03-25 15:00 | 2.0091 | 2.4449 | 2.3921 | 2.5729 | 2.4373 | 2.6181 | 1.2632 | 2.1662 | 2.6729 | 2.6729 | 3.0107 | 3.0107 | 2019-05-23 03:00 | 1.4937 | 2.5632 | 4.3323 | 4.3323 | 4.3323 | 4.3323
2021-03-25 16:00 | 2.0662 | 2.5144 | 2.4602 | 2.6461 | 2.5067 | 2.6926 | 1.3135 | 2.2525 | 2.7794 | 2.7794 | 3.1307 | 3.1307 | 2019-05-23 04:00 | 1.5547 | 2.6678 | 4.5091 | 4.5091 | 4.5091 | 4.5091
2021-03-25 17:00 | 2.1663 | 2.6361 | 2.5793 | 2.7742 | 2.628 | 2.823 | 1.4518 | 2.4896 | 3.072 | 3.072 | 3.4603 | 3.4603 | 2019-05-23 05:00 | 1.6842 | 2.8902 | 4.8849 | 4.8849 | 4.8849 | 4.8849
2021-03-25 18:00 | 2.272 | 2.7648 | 2.7052 | 2.9096 | 2.7563 | 2.9608 | 1.4432 | 2.4749 | 3.0539 | 3.0539 | 3.4399 | 3.4399 | 2019-05-23 06:00 | 1.9357 | 3.3217 | 5.6143 | 5.6143 | 5.6143 | 5.6143
2021-03-25 19:00 | 2.2892 | 2.7857 | 2.7256 | 2.9316 | 2.7771 | 2.9831 | 1.649 | 2.8278 | 3.4893 | 3.4893 | 3.9303 | 3.9303 | 2019-05-23 07:00 | 1.9586 | 3.361 | 5.6806 | 5.6806 | 5.6806 | 5.6806
2021-03-25 20:00 | 2.2621 | 2.7527 | 2.6933 | 2.8969 | 2.7442 | 2.9478 | 1.5833 | 2.715 | 3.3502 | 3.3502 | 3.7736 | 3.7736 | 2019-05-23 08:00 | 2.2558 | 3.871 | 6.5426 | 6.5426 | 6.5426 | 6.5426
2021-03-25 21:00 | 1.9691 | 2.3962 | 2.3445 | 2.5217 | 2.3888 | 2.566 | 1.4604 | 2.5043 | 3.0902 | 3.0902 | 3.4807 | 3.4807 | 2019-05-23 09:00 | 2.172 | 3.7271 | 6.2995 | 6.2995 | 6.2995 | 6.2995
2021-03-25 22:00 | 1.7605 | 2.1423 | 2.0961 | 2.2545 | 2.1357 | 2.2941 | 1.2089 | 2.073 | 2.558 | 2.558 | 2.8813 | 2.8813 | 2019-05-23 10:00 | 2.1415 | 3.6748 | 6.2111 | 6.2111 | 6.2111 | 6.2111
2021-03-25 23:00 | 1.5633 | 1.9023 | 1.8613 | 2.002 | 1.8965 | 2.0372 | 1.1346 | 1.9456 | 2.4008 | 2.4008 | 2.7042 | 2.7042 | 2019-05-23 11:00 | 2.2253 | 3.8187 | 6.4542 | 6.4542 | 6.4542 | 6.4542
2021-03-26 | 1.4207 | 1.7289 | 1.6916 | 1.8194 | 1.7235 | 1.8514 | 0.89469 | 1.5343 | 1.8932 | 1.8932 | 2.1325 | 2.1325 | 2019-05-23 12:00 | 2.172 | 3.7271 | 6.2995 | 6.2995 | 6.2995 | 6.2995
2021-03-26 01:00 | 1.3463 | 1.6383 | 1.603 | 1.7241 | 1.6333 | 1.7544 | 0.79461 | 1.3626 | 1.6814 | 1.6814 | 1.8939 | 1.8939 | 2019-05-23 13:00 | 2.1949 | 3.7664 | 6.3658 | 6.3658 | 6.3658 | 6.3658
2021-03-26 02:00 | 1.286 | 1.565 | 1.5312 | 1.647 | 1.5602 | 1.6759 | 0.78877 | 1.3526 | 1.6691 | 1.6691 | 1.88 | 1.88 | 2019-05-23 14:00 | 2.172 | 3.7271 | 6.2995 | 6.2995 | 6.2995 | 6.2995
2021-03-26 03:00 | 1.3032 | 1.5858 | 1.5516 | 1.6689 | 1.581 | 1.6982 | 0.71447 | 1.2252 | 1.5118 | 1.5118 | 1.7029 | 1.7029 | 2019-05-23 15:00 | 2.172 | 3.7271 | 6.2995 | 6.2995 | 6.2995 | 6.2995
2021-03-26 04:00 | 1.3083 | 1.5921 | 1.5577 | 1.6755 | 1.5872 | 1.7049 | 0.7109 | 1.2191 | 1.5043 | 1.5043 | 1.6944 | 1.6944 | 2019-05-23 16:00 | 2.1644 | 3.7141 | 6.2774 | 6.2774 | 6.2774 | 6.2774
2021-03-26 05:00 | 1.5232 | 1.8536 | 1.8137 | 1.9507 | 1.8479 | 1.985 | 0.78583 | 1.3476 | 1.6628 | 1.6628 | 1.873 | 1.873 | 2019-05-23 17:00 | 2.1186 | 3.6356 | 6.1448 | 6.1448 | 6.1448 | 6.1448
2021-03-26 06:00 | 1.9429 | 2.3643 | 2.3133 | 2.4882 | 2.357 | 2.5319 | 1.1012 | 1.8883 | 2.33 | 2.33 | 2.6245 | 2.6245 | 2019-05-23 18:00 | 2.1186 | 3.6356 | 6.1448 | 6.1448 | 6.1448 | 6.1448
2021-03-26 07:00 | 2.292 | 2.7892 | 2.729 | 2.9353 | 2.7806 | 2.9868 | 1.3832 | 2.372 | 2.9269 | 2.9269 | 3.2968 | 3.2968 | 2019-05-23 19:00 | 1.9357 | 3.3217 | 5.6143 | 5.6143 | 5.6143 | 5.6143
2021-03-26 08:00 | 2.4035 | 2.9248 | 2.8617 | 3.078 | 2.9158 | 3.1321 | 1.3746 | 2.3573 | 2.9088 | 2.9088 | 3.2764 | 3.2764 | 2019-05-23 20:00 | 1.829 | 3.1386 | 5.3048 | 5.3048 | 5.3048 | 5.3048
2021-03-26 09:00 | 2.372 | 2.8865 | 2.8243 | 3.0377 | 2.8776 | 3.0911 | 1.2975 | 2.225 | 2.7455 | 2.7455 | 3.0925 | 3.0925 | 2019-05-23 21:00 | 1.7376 | 2.9817 | 5.0396 | 5.0396 | 5.0396 | 5.0396
2021-03-26 10:00 | 2.132 | 2.5944 | 2.5384 | 2.7303 | 2.5864 | 2.7783 | 1.2918 | 2.2152 | 2.7334 | 2.7334 | 3.0789 | 3.0789 | 2019-05-23 22:00 | 1.7223 | 2.9556 | 4.9954 | 4.9954 | 4.9954 | 4.9954
2021-03-26 11:00 | 2.1063 | 2.5631 | 2.5078 | 2.6974 | 2.5552 | 2.7448 | 1.3175 | 2.2593 | 2.7878 | 2.7878 | 3.1402 | 3.1402 | 2019-05-23 23:00 | 1.5471 | 2.6548 | 4.487 | 4.487 | 4.487 | 4.487
2021-03-26 12:00 | 2.032 | 2.4727 | 2.4193 | 2.6022 | 2.4651 | 2.6479 | 1.266 | 2.1711 | 2.679 | 2.679 | 3.0176 | 3.0176 | 2019-05-24 | 1.5471 | 2.6548 | 4.487 | 4.487 | 4.487 | 4.487
2021-03-26 13:00 | 2.1234 | 2.584 | 2.5282 | 2.7193 | 2.576 | 2.7671 | 1.3346 | 2.2887 | 2.8241 | 2.8241 | 3.181 | 3.181 | 2019-05-24 01:00 | 1.5166 | 2.6025 | 4.3986 | 4.3986 | 4.3986 | 4.3986
2021-03-26 14:00 | 2.0005 | 2.4344 | 2.3819 | 2.562 | 2.4269 | 2.607 | 1.2546 | 2.1515 | 2.6548 | 2.6548 | 2.9903 | 2.9903 | 2019-05-24 02:00 | 1.4785 | 2.5371 | 4.2881 | 4.2881 | 4.2881 | 4.2881
2021-03-26 15:00 | 1.9091 | 2.3231 | 2.273 | 2.4448 | 2.316 | 2.4878 | 1.2575 | 2.1564 | 2.6608 | 2.6608 | 2.9971 | 2.9971 | 2019-05-24 03:00 | 1.4327 | 2.4586 | 4.1555 | 4.1555 | 4.1555 | 4.1555
2021-03-26 16:00 | 1.8919 | 2.3023 | 2.2526 | 2.4229 | 2.2952 | 2.4654 | 1.3232 | 2.2691 | 2.7999 | 2.7999 | 3.1538 | 3.1538 | 2019-05-24 04:00 | 1.5013 | 2.5763 | 4.3544 | 4.3544 | 4.3544 | 4.3544
2021-03-26 17:00 | 1.9376 | 2.3579 | 2.307 | 2.4814 | 2.3506 | 2.525 | 1.5004 | 2.5729 | 3.1748 | 3.1748 | 3.5761 | 3.5761 | 2019-05-24 05:00 | 1.6461 | 2.8248 | 4.7743 | 4.7743 | 4.7743 | 4.7743
2021-03-26 18:00 | 2.0091 | 2.4449 | 2.3921 | 2.5729 | 2.4373 | 2.6181 | 1.6661 | 2.8572 | 3.5256 | 3.5256 | 3.9712 | 3.9712 | 2019-05-24 06:00 | 1.8443 | 3.1648 | 5.349 | 5.349 | 5.349 | 5.349
2021-03-26 19:00 | 2.0377 | 2.4796 | 2.4261 | 2.6095 | 2.472 | 2.6554 | 1.749 | 2.9993 | 3.7009 | 3.7009 | 4.1687 | 4.1687 | 2019-05-24 07:00 | 1.9129 | 3.2825 | 5.548 | 5.548 | 5.548 | 5.548
2021-03-26 20:00 | 1.8633 | 2.2675 | 2.2186 | 2.3863 | 2.2605 | 2.4282 | 1.669 | 2.8621 | 3.5316 | 3.5316 | 3.978 | 3.978 | 2019-05-24 08:00 | 1.9967 | 3.4264 | 5.7911 | 5.7911 | 5.7911 | 5.7911
2021-03-26 21:00 | 1.8119 | 2.2049 | 2.1573 | 2.3204 | 2.1981 | 2.3612 | 1.6547 | 2.8376 | 3.5014 | 3.5014 | 3.9439 | 3.9439 | 2019-05-24 09:00 | 2.111 | 3.6225 | 6.1227 | 6.1227 | 6.1227 | 6.1227
2021-03-26 22:00 | 1.6347 | 1.9893 | 1.9464 | 2.0935 | 1.9831 | 2.1303 | 1.4404 | 2.47 | 3.0478 | 3.0478 | 3.4331 | 3.4331 | 2019-05-24 10:00 | 2.0729 | 3.5571 | 6.0121 | 6.0121 | 6.0121 | 6.0121
2021-03-26 23:00 | 1.6033 | 1.951 | 1.9089 | 2.0532 | 1.945 | 2.0893 | 1.2089 | 2.073 | 2.558 | 2.558 | 2.8813 | 2.8813 | 2019-05-24 11:00 | 2.1034 | 3.6094 | 6.1006 | 6.1006 | 6.1006 | 6.1006
2021-03-27 | 1.4577 | 1.7739 | 1.7356 | 1.8668 | 1.7684 | 1.8996 | 1.0085 | 1.7294 | 2.134 | 2.134 | 2.4037 | 2.4037 | 2019-05-24 12:00 | 2.1186 | 3.6356 | 6.1448 | 6.1448 | 6.1448 | 6.1448
2021-03-27 01:00 | 1.3775 | 1.6763 | 1.6401 | 1.7641 | 1.6711 | 1.7951 | 0.85736 | 1.4702 | 1.8142 | 1.8142 | 2.0435 | 2.0435 | 2019-05-24 13:00 | 2.0653 | 3.5441 | 5.99 | 5.99 | 5.99 | 5.99
2021-03-27 02:00 | 1.2803 | 1.558 | 1.5244 | 1.6396 | 1.5532 | 1.6685 | 0.81823 | 1.4031 | 1.7314 | 1.7314 | 1.9502 | 1.9502 | 2019-05-24 14:00 | 2.0043 | 3.4394 | 5.8132 | 5.8132 | 5.8132 | 5.8132
2021-03-27 03:00 | 1.2632 | 1.5372 | 1.504 | 1.6177 | 1.5324 | 1.6461 | 0.772 | 1.3239 | 1.6336 | 1.6336 | 1.84 | 1.84 | 2019-05-24 15:00 | 2.0805 | 3.5702 | 6.0343 | 6.0343 | 6.0343 | 6.0343
2021-03-27 04:00 | 1.3001 | 1.5821 | 1.548 | 1.665 | 1.5772 | 1.6943 | 0.75448 | 1.2938 | 1.5965 | 1.5965 | 1.7983 | 1.7983 | 2019-05-24 16:00 | 2.1796 | 3.7402 | 6.3216 | 6.3216 | 6.3216 | 6.3216
2021-03-27 05:00 | 1.3689 | 1.6658 | 1.6299 | 1.7531 | 1.6607 | 1.7839 | 0.77162 | 1.3232 | 1.6328 | 1.6328 | 1.8391 | 1.8391 | 2019-05-24 17:00 | 2.0958 | 3.5964 | 6.0785 | 6.0785 | 6.0785 | 6.0785
2021-03-27 06:00 | 1.4832 | 1.8049 | 1.766 | 1.8995 | 1.7994 | 1.9329 | 0.9088 | 1.5585 | 1.923 | 1.923 | 2.1661 | 2.1661 | 2019-05-24 18:00 | 1.9205 | 3.2956 | 5.5701 | 5.5701 | 5.5701 | 5.5701
2021-03-27 07:00 | 1.6176 | 1.9684 | 1.9259 | 2.0715 | 1.9623 | 2.1079 | 1.0546 | 1.8084 | 2.2315 | 2.2315 | 2.5135 | 2.5135 | 2019-05-24 19:00 | 1.8595 | 3.191 | 5.3932 | 5.3932 | 5.3932 | 5.3932
2021-03-27 08:00 | 1.6318 | 1.9858 | 1.943 | 2.0898 | 1.9797 | 2.1265 | 1.2775 | 2.1907 | 2.7031 | 2.7031 | 3.0448 | 3.0448 | 2019-05-24 20:00 | 1.7605 | 3.0209 | 5.1059 | 5.1059 | 5.1059 | 5.1059
2021-03-27 09:00 | 1.6576 | 2.0171 | 1.9736 | 2.1228 | 2.0109 | 2.1601 | 1.3746 | 2.3573 | 2.9088 | 2.9088 | 3.2764 | 3.2764 | 2019-05-24 21:00 | 1.669 | 2.864 | 4.8407 | 4.8407 | 4.8407 | 4.8407
2021-03-27 10:00 | 1.7576 | 2.1388 | 2.0927 | 2.2509 | 2.1322 | 2.2904 | 1.5347 | 2.6317 | 3.2474 | 3.2474 | 3.6578 | 3.6578 | 2019-05-24 22:00 | 1.6919 | 2.9032 | 4.907 | 4.907 | 4.907 | 4.907
2021-03-27 11:00 | 1.6233 | 1.9754 | 1.9327 | 2.0788 | 1.9693 | 2.1154 | 1.4461 | 2.4798 | 3.0599 | 3.0599 | 3.4467 | 3.4467 | 2019-05-24 23:00 | 1.6157 | 2.7725 | 4.6859 | 4.6859 | 4.6859 | 4.6859
2021-03-27 12:00 | 1.5947 | 1.9406 | 1.8987 | 2.0422 | 1.9346 | 2.0781 | 1.6147 | 2.769 | 3.4167 | 3.4167 | 3.8486 | 3.8486 | 2019-05-25 | 1.5852 | 2.7202 | 4.5975 | 4.5975 | 4.5975 | 4.5975
2021-03-27 13:00 | 1.5718 | 1.9128 | 1.8715 | 2.013 | 1.9069 | 2.0483 | 1.5947 | 2.7346 | 3.3744 | 3.3744 | 3.8009 | 3.8009 | 2019-05-25 01:00 | 1.4099 | 2.4194 | 4.0891 | 4.0891 | 4.0891 | 4.0891
2021-03-27 14:00 | 1.5898 | 1.9346 | 1.8929 | 2.0359 | 1.9286 | 2.0717 | 1.4775 | 2.5337 | 3.1265 | 3.1265 | 3.5216 | 3.5216 | 2019-05-25 02:00 | 1.4023 | 2.4063 | 4.067 | 4.067 | 4.067 | 4.067
2021-03-27 15:00 | 1.6033 | 1.951 | 1.9089 | 2.0532 | 1.945 | 2.0893 | 1.4575 | 2.4994 | 3.0841 | 3.0841 | 3.4739 | 3.4739 | 2019-05-25 03:00 | 1.4023 | 2.4063 | 4.067 | 4.067 | 4.067 | 4.067
2021-03-27 16:00 | 1.5662 | 1.9059 | 1.8648 | 2.0058 | 1.9001 | 2.041 | 1.4804 | 2.5386 | 3.1325 | 3.1325 | 3.5284 | 3.5284 | 2019-05-25 04:00 | 1.4861 | 2.5501 | 4.3102 | 4.3102 | 4.3102 | 4.3102
2021-03-27 17:00 | 1.7033 | 2.0727 | 2.028 | 2.1813 | 2.0663 | 2.2196 | 1.4832 | 2.5435 | 3.1385 | 3.1385 | 3.5352 | 3.5352 | 2019-05-25 05:00 | 1.608 | 2.7594 | 4.6638 | 4.6638 | 4.6638 | 4.6638
2021-03-27 18:00 | 1.749 | 2.1284 | 2.0825 | 2.2399 | 2.1218 | 2.2792 | 1.5204 | 2.6072 | 3.2172 | 3.2172 | 3.6238 | 3.6238 | 2019-05-25 06:00 | 1.5928 | 2.7332 | 4.6196 | 4.6196 | 4.6196 | 4.6196
2021-03-27 19:00 | 1.7976 | 2.1875 | 2.1403 | 2.3021 | 2.1808 | 2.3425 | 1.5833 | 2.715 | 3.3502 | 3.3502 | 3.7736 | 3.7736 | 2019-05-25 07:00 | 1.7909 | 3.0733 | 5.1943 | 5.1943 | 5.1943 | 5.1943
2021-03-27 20:00 | 1.7204 | 2.0936 | 2.0484 | 2.2033 | 2.0871 | 2.242 | 1.5718 | 2.6954 | 3.326 | 3.326 | 3.7464 | 3.7464 | 2019-05-25 08:00 | 1.9662 | 3.374 | 5.7027 | 5.7027 | 5.7027 | 5.7027
2021-03-27 21:00 | 1.5762 | 1.9181 | 1.8767 | 2.0186 | 1.9122 | 2.0541 | 1.5547 | 2.666 | 3.2897 | 3.2897 | 3.7055 | 3.7055 | 2019-05-25 09:00 | 1.9662 | 3.374 | 5.7027 | 5.7027 | 5.7027 | 5.7027
2021-03-27 22:00 | 1.5259 | 1.8569 | 1.8169 | 1.9542 | 1.8512 | 1.9885 | 1.4032 | 2.4063 | 2.9692 | 2.9692 | 3.3445 | 3.3445 | 2019-05-25 10:00 | 2.0043 | 3.4394 | 5.8132 | 5.8132 | 5.8132 | 5.8132
2021-03-27 23:00 | 1.489 | 1.8119 | 1.7728 | 1.9068 | 1.8063 | 1.9403 | 1.186 | 2.0338 | 2.5096 | 2.5096 | 2.8268 | 2.8268 | 2019-05-25 11:00 | 2.0501 | 3.5179 | 5.9458 | 5.9458 | 5.9458 | 5.9458
2021-03-28 | 1.4175 | 1.725 | 1.6878 | 1.8153 | 1.7196 | 1.8472 | 1.0174 | 1.7447 | 2.1528 | 2.1528 | 2.4249 | 2.4249 | 2019-05-25 12:00 | 1.9738 | 3.3871 | 5.7248 | 5.7248 | 5.7248 | 5.7248
2021-03-28 01:00 | 1.3147 | 1.5998 | 1.5653 | 1.6836 | 1.5949 | 1.7132 | 0.82307 | 1.4114 | 1.7416 | 1.7416 | 1.9617 | 1.9617 | 2019-05-25 13:00 | 2.0348 | 3.4917 | 5.9016 | 5.9016 | 5.9016 | 5.9016
2021-03-28 02:00 | 1.2975 | 1.5789 | 1.5448 | 1.6616 | 1.574 | 1.6908 | 0.81164 | 1.3918 | 1.7174 | 1.7174 | 1.9345 | 1.9345 | 2019-05-25 14:00 | 1.9967 | 3.4264 | 5.7911 | 5.7911 | 5.7911 | 5.7911
2021-03-28 03:00 | 1.2832 | 1.5615 | 1.5278 | 1.6433 | 1.5567 | 1.6722 | 0.75162 | 1.2889 | 1.5904 | 1.5904 | 1.7915 | 1.7915 | 2019-05-25 15:00 | 1.9662 | 3.374 | 5.7027 | 5.7027 | 5.7027 | 5.7027
2021-03-28 04:00 | 1.2575 | 1.5302 | 1.4972 | 1.6104 | 1.5255 | 1.6387 | 0.73115 | 1.2538 | 1.5471 | 1.5471 | 1.7427 | 1.7427 | 2019-05-25 16:00 | 2.0043 | 3.4394 | 5.8132 | 5.8132 | 5.8132 | 5.8132
2021-03-28 05:00 | 1.2489 | 1.5198 | 1.487 | 1.5994 | 1.5151 | 1.6275 | 0.76591 | 1.3134 | 1.6207 | 1.6207 | 1.8255 | 1.8255 | 2019-05-25 17:00 | 1.9662 | 3.374 | 5.7027 | 5.7027 | 5.7027 | 5.7027
2021-03-28 06:00 | 1.4204 | 1.7284 | 1.6912 | 1.819 | 1.7231 | 1.8509 | 0.8545 | 1.4653 | 1.8081 | 1.8081 | 2.0367 | 2.0367 | 2019-05-25 18:00 | 1.8443 | 3.1648 | 5.349 | 5.349 | 5.349 | 5.349
2021-03-28 07:00 | 1.5054 | 1.8319 | 1.7924 | 1.9279 | 1.8263 | 1.9617 | 0.87451 | 1.4996 | 1.8505 | 1.8505 | 2.0844 | 2.0844 | 2019-05-25 19:00 | 1.7071 | 2.9294 | 4.9512 | 4.9512 | 4.9512 | 4.9512
2021-03-28 08:00 | 1.6625 | 2.0231 | 1.9795 | 2.1291 | 2.0169 | 2.1665 | 1.206 | 2.0681 | 2.552 | 2.552 | 2.8745 | 2.8745 | 2019-05-25 20:00 | 1.669 | 2.864 | 4.8407 | 4.8407 | 4.8407 | 4.8407
2021-03-28 09:00 | 1.6633 | 2.024 | 1.9804 | 2.1301 | 2.0178 | 2.1675 | 1.3232 | 2.2691 | 2.7999 | 2.7999 | 3.1538 | 3.1538 | 2019-05-25 21:00 | 1.6919 | 2.9032 | 4.907 | 4.907 | 4.907 | 4.907
2021-03-28 10:00 | 1.5404 | 1.8745 | 1.8341 | 1.9727 | 1.8687 | 2.0074 | 1.549 | 2.6562 | 3.2776 | 3.2776 | 3.6919 | 3.6919 | 2019-05-25 22:00 | 1.6461 | 2.8248 | 4.7743 | 4.7743 | 4.7743 | 4.7743
2021-03-28 11:00 | 1.5718 | 1.9128 | 1.8715 | 2.013 | 1.9069 | 2.0483 | 1.509 | 2.5876 | 3.193 | 3.193 | 3.5965 | 3.5965 | 2019-05-25 23:00 | 1.5394 | 2.6417 | 4.4649 | 4.4649 | 4.4649 | 4.4649
2021-03-28 12:00 | 1.5575 | 1.8954 | 1.8545 | 1.9947 | 1.8895 | 2.0297 | 1.4347 | 2.4602 | 3.0357 | 3.0357 | 3.4194 | 3.4194 | 2019-05-26 | 1.5242 | 2.6155 | 4.4207 | 4.4207 | 4.4207 | 4.4207
2021-03-28 13:00 | 1.4004 | 1.7041 | 1.6673 | 1.7934 | 1.6988 | 1.8249 | 1.4817 | 2.5409 | 3.1353 | 3.1353 | 3.5315 | 3.5315 | 2019-05-26 01:00 | 1.4632 | 2.5109 | 4.2439 | 4.2439 | 4.2439 | 4.2439
2021-03-28 14:00 | 1.4489 | 1.7632 | 1.7252 | 1.8556 | 1.7578 | 1.8882 | 1.4947 | 2.5631 | 3.1627 | 3.1627 | 3.5625 | 3.5625 | 2019-05-26 02:00 | 1.448 | 2.4848 | 4.1997 | 4.1997 | 4.1997 | 4.1997
2021-03-28 15:00 | 1.3175 | 1.6032 | 1.5687 | 1.6872 | 1.5983 | 1.7169 | 1.3946 | 2.3916 | 2.9511 | 2.9511 | 3.3241 | 3.3241 | 2019-05-26 03:00 | 1.4709 | 2.524 | 4.266 | 4.266 | 4.266 | 4.266
2021-03-28 16:00 | 1.4715 | 1.7907 | 1.7521 | 1.8845 | 1.7852 | 1.9176 | 1.4489 | 2.4846 | 3.0659 | 3.0659 | 3.4534 | 3.4534 | 2019-05-26 04:00 | 1.4861 | 2.5501 | 4.3102 | 4.3102 | 4.3102 | 4.3102
2021-03-28 17:00 | 1.6919 | 2.0588 | 2.0144 | 2.1667 | 2.0525 | 2.2047 | 1.549 | 2.6562 | 3.2776 | 3.2776 | 3.6919 | 3.6919 | 2019-05-26 05:00 | 1.5623 | 2.6809 | 4.5312 | 4.5312 | 4.5312 | 4.5312
2021-03-28 18:00 | 1.9319 | 2.351 | 2.3002 | 2.4741 | 2.3437 | 2.5176 | 1.6433 | 2.818 | 3.4772 | 3.4772 | 3.9167 | 3.9167 | 2019-05-26 06:00 | 1.6461 | 2.8248 | 4.7743 | 4.7743 | 4.7743 | 4.7743
2021-03-28 19:00 | 1.9834 | 2.4136 | 2.3615 | 2.54 | 2.4061 | 2.5846 | 1.7004 | 2.916 | 3.5981 | 3.5981 | 4.0529 | 4.0529 | 2019-05-26 07:00 | 1.7681 | 3.034 | 5.128 | 5.128 | 5.128 | 5.128
2021-03-28 20:00 | 1.9033 | 2.3162 | 2.2662 | 2.4375 | 2.309 | 2.4803 | 1.569 | 2.6905 | 3.32 | 3.32 | 3.7396 | 3.7396 | 2019-05-26 08:00 | 1.9053 | 3.2694 | 5.5259 | 5.5259 | 5.5259 | 5.5259
2021-03-28 21:00 | 1.7833 | 2.1701 | 2.1233 | 2.2838 | 2.1634 | 2.3239 | 1.5004 | 2.5729 | 3.1748 | 3.1748 | 3.5761 | 3.5761 | 2019-05-26 09:00 | 1.9891 | 3.4133 | 5.769 | 5.769 | 5.769 | 5.769
2021-03-28 22:00 | 1.7262 | 2.1006 | 2.0552 | 2.2106 | 2.0941 | 2.2494 | 1.2946 | 2.2201 | 2.7394 | 2.7394 | 3.0857 | 3.0857 | 2019-05-26 10:00 | 1.9129 | 3.2825 | 5.548 | 5.548 | 5.548 | 5.548
2021-03-28 23:00 | 1.5633 | 1.9023 | 1.8613 | 2.002 | 1.8965 | 2.0372 | 1.0776 | 1.8478 | 2.2801 | 2.2801 | 2.5683 | 2.5683 | 2019-05-26 11:00 | 2.0119 | 3.4525 | 5.8353 | 5.8353 | 5.8353 | 5.8353
2021-03-29 | 1.4781 | 1.7987 | 1.7599 | 1.8929 | 1.7931 | 1.9261 | 0.94669 | 1.6234 | 2.0032 | 2.0032 | 2.2564 | 2.2564 | 2019-05-26 12:00 | 2.0272 | 3.4787 | 5.8795 | 5.8795 | 5.8795 | 5.8795
2021-03-29 01:00 | 1.3805 | 1.6799 | 1.6437 | 1.7679 | 1.6747 | 1.799 | 0.85736 | 1.4702 | 1.8142 | 1.8142 | 2.0435 | 2.0435 | 2019-05-26 13:00 | 1.9815 | 3.4002 | 5.7469 | 5.7469 | 5.7469 | 5.7469
2021-03-29 02:00 | 1.2975 | 1.5789 | 1.5448 | 1.6616 | 1.574 | 1.6908 | 0.79735 | 1.3673 | 1.6872 | 1.6872 | 1.9004 | 1.9004 | 2019-05-26 14:00 | 1.9891 | 3.4133 | 5.769 | 5.769 | 5.769 | 5.769
2021-03-29 03:00 | 1.2887 | 1.5682 | 1.5344 | 1.6504 | 1.5634 | 1.6793 | 0.7286 | 1.2494 | 1.5417 | 1.5417 | 1.7366 | 1.7366 | 2019-05-26 15:00 | 2.0119 | 3.4525 | 5.8353 | 5.8353 | 5.8353 | 5.8353
2021-03-29 04:00 | 1.3115 | 1.5959 | 1.5615 | 1.6795 | 1.591 | 1.709 | 0.7802 | 1.3379 | 1.6509 | 1.6509 | 1.8596 | 1.8596 | 2019-05-26 16:00 | 2.0653 | 3.5441 | 5.99 | 5.99 | 5.99 | 5.99
2021-03-29 05:00 | 1.5061 | 1.8328 | 1.7932 | 1.9288 | 1.8271 | 1.9627 | 0.85136 | 1.4599 | 1.8015 | 1.8015 | 2.0292 | 2.0292 | 2019-05-26 17:00 | 1.9738 | 3.3871 | 5.7248 | 5.7248 | 5.7248 | 5.7248
2021-03-29 06:00 | 1.9805 | 2.4101 | 2.3581 | 2.5363 | 2.4026 | 2.5809 | 1.0374 | 1.779 | 2.1952 | 2.1952 | 2.4726 | 2.4726 | 2019-05-26 18:00 | 1.8748 | 3.2171 | 5.4375 | 5.4375 | 5.4375 | 5.4375
2021-03-29 07:00 | 2.3769 | 2.8924 | 2.83 | 3.044 | 2.8835 | 3.0974 | 1.3289 | 2.2789 | 2.812 | 2.812 | 3.1674 | 3.1674 | 2019-05-26 19:00 | 1.829 | 3.1386 | 5.3048 | 5.3048 | 5.3048 | 5.3048
2021-03-29 08:00 | 2.3806 | 2.897 | 2.8345 | 3.0487 | 2.888 | 3.1023 | 1.4204 | 2.4357 | 3.0055 | 3.0055 | 3.3854 | 3.3854 | 2019-05-26 20:00 | 1.7376 | 2.9817 | 5.0396 | 5.0396 | 5.0396 | 5.0396
2021-03-29 09:00 | 2.312 | 2.8135 | 2.7528 | 2.9609 | 2.8048 | 3.0129 | 1.3689 | 2.3475 | 2.8967 | 2.8967 | 3.2628 | 3.2628 | 2019-05-26 21:00 | 1.7147 | 2.9425 | 4.9733 | 4.9733 | 4.9733 | 4.9733
2021-03-29 10:00 | 2.0948 | 2.5492 | 2.4942 | 2.6827 | 2.5413 | 2.7299 | 1.4118 | 2.421 | 2.9874 | 2.9874 | 3.3649 | 3.3649 | 2019-05-26 22:00 | 1.6233 | 2.7855 | 4.708 | 4.708 | 4.708 | 4.708
2021-03-29 11:00 | 2.0691 | 2.5179 | 2.4636 | 2.6498 | 2.5101 | 2.6963 | 1.3232 | 2.2691 | 2.7999 | 2.7999 | 3.1538 | 3.1538 | 2019-05-26 23:00 | 1.5166 | 2.6025 | 4.3986 | 4.3986 | 4.3986 | 4.3986
2021-03-29 12:00 | 1.9291 | 2.3475 | 2.2968 | 2.4705 | 2.3402 | 2.5139 | 1.2775 | 2.1907 | 2.7031 | 2.7031 | 3.0448 | 3.0448 | 2019-05-27 | 1.4785 | 2.5371 | 4.2881 | 4.2881 | 4.2881 | 4.2881
2021-03-29 13:00 | 1.9462 | 2.3683 | 2.3173 | 2.4924 | 2.361 | 2.5362 | 1.2546 | 2.1515 | 2.6548 | 2.6548 | 2.9903 | 2.9903 | 2019-05-27 01:00 | 1.3794 | 2.3671 | 4.0007 | 4.0007 | 4.0007 | 4.0007
2021-03-29 14:00 | 1.8776 | 2.2849 | 2.2356 | 2.4046 | 2.2778 | 2.4468 | 1.3318 | 2.2838 | 2.818 | 2.818 | 3.1742 | 3.1742 | 2019-05-27 02:00 | 1.3184 | 2.2624 | 3.8239 | 3.8239 | 3.8239 | 3.8239
2021-03-29 15:00 | 1.9548 | 2.3788 | 2.3275 | 2.5034 | 2.3714 | 2.5474 | 1.286 | 2.2054 | 2.7213 | 2.7213 | 3.0652 | 3.0652 | 2019-05-27 03:00 | 1.3413 | 2.3017 | 3.8902 | 3.8902 | 3.8902 | 3.8902
2021-03-29 16:00 | 2.0034 | 2.4379 | 2.3853 | 2.5656 | 2.4304 | 2.6107 | 1.3118 | 2.2495 | 2.7757 | 2.7757 | 3.1265 | 3.1265 | 2019-05-27 04:00 | 1.3946 | 2.3932 | 4.0449 | 4.0449 | 4.0449 | 4.0449
2021-03-29 17:00 | 2.0977 | 2.5527 | 2.4976 | 2.6864 | 2.5448 | 2.7336 | 1.4261 | 2.4455 | 3.0176 | 3.0176 | 3.399 | 3.399 | 2019-05-27 05:00 | 1.5699 | 2.694 | 4.5533 | 4.5533 | 4.5533 | 4.5533
2021-03-29 18:00 | 2.2692 | 2.7613 | 2.7018 | 2.906 | 2.7528 | 2.957 | 1.5633 | 2.6807 | 3.3079 | 3.3079 | 3.726 | 3.726 | 2019-05-27 06:00 | 1.6309 | 2.7986 | 4.7301 | 4.7301 | 4.7301 | 4.7301
2021-03-29 19:00 | 2.2777 | 2.7718 | 2.712 | 2.917 | 2.7632 | 2.9682 | 1.6004 | 2.7445 | 3.3865 | 3.3865 | 3.8145 | 3.8145 | 2019-05-27 07:00 | 1.6766 | 2.8771 | 4.8628 | 4.8628 | 4.8628 | 4.8628
2021-03-29 20:00 | 2.1377 | 2.6014 | 2.5452 | 2.7376 | 2.5933 | 2.7857 | 1.5261 | 2.617 | 3.2293 | 3.2293 | 3.6374 | 3.6374 | 2019-05-27 08:00 | 1.829 | 3.1386 | 5.3048 | 5.3048 | 5.3048 | 5.3048
2021-03-29 21:00 | 1.9605 | 2.3857 | 2.3343 | 2.5107 | 2.3784 | 2.5548 | 1.4473 | 2.482 | 3.0626 | 3.0626 | 3.4497 | 3.4497 | 2019-05-27 09:00 | 1.89 | 3.2433 | 5.4817 | 5.4817 | 5.4817 | 5.4817
2021-03-29 22:00 | 1.7323 | 2.1081 | 2.0626 | 2.2185 | 2.1016 | 2.2575 | 1.2585 | 2.1581 | 2.663 | 2.663 | 2.9996 | 2.9996 | 2019-05-27 10:00 | 1.8976 | 3.2563 | 5.5038 | 5.5038 | 5.5038 | 5.5038
2021-03-29 23:00 | 1.5318 | 1.8641 | 1.8239 | 1.9617 | 1.8583 | 1.9962 | 1.0966 | 1.8806 | 2.3205 | 2.3205 | 2.6138 | 2.6138 | 2019-05-27 11:00 | 1.9281 | 3.3087 | 5.5922 | 5.5922 | 5.5922 | 5.5922
2021-03-30 | 1.4432 | 1.7563 | 1.7184 | 1.8483 | 1.7508 | 1.8807 | 0.94627 | 1.6227 | 2.0023 | 2.0023 | 2.2554 | 2.2554 | 2019-05-27 12:00 | 1.89 | 3.2433 | 5.4817 | 5.4817 | 5.4817 | 5.4817
2021-03-30 01:00 | 1.3518 | 1.645 | 1.6095 | 1.7311 | 1.6399 | 1.7616 | 0.81449 | 1.3967 | 1.7235 | 1.7235 | 1.9413 | 1.9413 | 2019-05-27 13:00 | 1.8519 | 3.1779 | 5.3711 | 5.3711 | 5.3711 | 5.3711
2021-03-30 02:00 | 1.2632 | 1.5372 | 1.504 | 1.6177 | 1.5324 | 1.6461 | 0.75184 | 1.2893 | 1.5909 | 1.5909 | 1.792 | 1.792 | 2019-05-27 14:00 | 1.8824 | 3.2302 | 5.4596 | 5.4596 | 5.4596 | 5.4596
2021-03-30 03:00 | 1.2603 | 1.5337 | 1.5006 | 1.614 | 1.529 | 1.6424 | 0.6723 | 1.1529 | 1.4226 | 1.4226 | 1.6024 | 1.6024 | 2019-05-27 15:00 | 1.89 | 3.2433 | 5.4817 | 5.4817 | 5.4817 | 5.4817
2021-03-30 04:00 | 1.271 | 1.5467 | 1.5133 | 1.6277 | 1.5419 | 1.6563 | 0.71447 | 1.2252 | 1.5118 | 1.5118 | 1.7029 | 1.7029 | 2019-05-27 16:00 | 1.9357 | 3.3217 | 5.6143 | 5.6143 | 5.6143 | 5.6143
2021-03-30 05:00 | 1.5404 | 1.8745 | 1.8341 | 1.9727 | 1.8687 | 2.0074 | 0.8002 | 1.3722 | 1.6932 | 1.6932 | 1.9073 | 1.9073 | 2019-05-27 17:00 | 1.951 | 3.3479 | 5.6585 | 5.6585 | 5.6585 | 5.6585
2021-03-30 06:00 | 1.9491 | 2.3718 | 2.3207 | 2.4961 | 2.3645 | 2.5399 | 0.99454 | 1.7055 | 2.1045 | 2.1045 | 2.3704 | 2.3704 | 2019-05-27 18:00 | 1.9586 | 3.361 | 5.6806 | 5.6806 | 5.6806 | 5.6806
2021-03-30 07:00 | 2.312 | 2.8135 | 2.7528 | 2.9609 | 2.8048 | 3.0129 | 1.2546 | 2.1515 | 2.6548 | 2.6548 | 2.9903 | 2.9903 | 2019-05-27 19:00 | 1.89 | 3.2433 | 5.4817 | 5.4817 | 5.4817 | 5.4817
2021-03-30 08:00 | 2.4321 | 2.9596 | 2.8957 | 3.1146 | 2.9504 | 3.1693 | 1.3746 | 2.3573 | 2.9088 | 2.9088 | 3.2764 | 3.2764 | 2019-05-27 20:00 | 1.7452 | 2.9948 | 5.0617 | 5.0617 | 5.0617 | 5.0617
2021-03-30 09:00 | 2.3206 | 2.8239 | 2.763 | 2.9719 | 2.8152 | 3.0241 | 1.3403 | 2.2985 | 2.8362 | 2.8362 | 3.1947 | 3.1947 | 2019-05-27 21:00 | 1.6842 | 2.8902 | 4.8849 | 4.8849 | 4.8849 | 4.8849
2021-03-30 10:00 | 2.2863 | 2.7822 | 2.7222 | 2.9279 | 2.7736 | 2.9794 | 1.3089 | 2.2446 | 2.7697 | 2.7697 | 3.1197 | 3.1197 | 2019-05-27 22:00 | 1.6385 | 2.8117 | 4.7522 | 4.7522 | 4.7522 | 4.7522
2021-03-30 11:00 | 2.2091 | 2.6883 | 2.6303 | 2.8291 | 2.68 | 2.8788 | 1.3775 | 2.3622 | 2.9148 | 2.9148 | 3.2832 | 3.2832 | 2019-05-27 23:00 | 1.4632 | 2.5109 | 4.2439 | 4.2439 | 4.2439 | 4.2439
2021-03-30 12:00 | 2.0948 | 2.5492 | 2.4942 | 2.6827 | 2.5413 | 2.7299 | 1.3603 | 2.3328 | 2.8785 | 2.8785 | 3.2423 | 3.2423 | 2019-05-28 | 1.4404 | 2.4717 | 4.1776 | 4.1776 | 4.1776 | 4.1776
2021-03-30 13:00 | 2.1251 | 2.5861 | 2.5303 | 2.7216 | 2.5781 | 2.7694 | 1.3203 | 2.2642 | 2.7939 | 2.7939 | 3.147 | 3.147 | 2019-05-28 01:00 | 1.3184 | 2.2624 | 3.8239 | 3.8239 | 3.8239 | 3.8239
2021-03-30 14:00 | 2.1291 | 2.5909 | 2.535 | 2.7266 | 2.5829 | 2.7746 | 1.3603 | 2.3328 | 2.8785 | 2.8785 | 3.2423 | 3.2423 | 2019-05-28 02:00 | 1.3565 | 2.3278 | 3.9344 | 3.9344 | 3.9344 | 3.9344
2021-03-30 15:00 | 2.0691 | 2.5179 | 2.4636 | 2.6498 | 2.5101 | 2.6963 | 1.2433 | 2.1321 | 2.6309 | 2.6309 | 2.9634 | 2.9634 | 2019-05-28 03:00 | 1.3565 | 2.3278 | 3.9344 | 3.9344 | 3.9344 | 3.9344
2021-03-30 16:00 | 2.0005 | 2.4344 | 2.3819 | 2.562 | 2.4269 | 2.607 | 1.2689 | 2.176 | 2.685 | 2.685 | 3.0244 | 3.0244 | 2019-05-28 04:00 | 1.448 | 2.4848 | 4.1997 | 4.1997 | 4.1997 | 4.1997
2021-03-30 17:00 | 2.1777 | 2.65 | 2.5929 | 2.7889 | 2.6419 | 2.8379 | 1.4861 | 2.5484 | 3.1446 | 3.1446 | 3.542 | 3.542 | 2019-05-28 05:00 | 1.6461 | 2.8248 | 4.7743 | 4.7743 | 4.7743 | 4.7743
2021-03-30 18:00 | 2.2663 | 2.7579 | 2.6984 | 2.9023 | 2.7494 | 2.9533 | 1.6318 | 2.7984 | 3.453 | 3.453 | 3.8894 | 3.8894 | 2019-05-28 06:00 | 1.829 | 3.1386 | 5.3048 | 5.3048 | 5.3048 | 5.3048
2021-03-30 19:00 | 2.2606 | 2.7509 | 2.6916 | 2.895 | 2.7424 | 2.9459 | 1.649 | 2.8278 | 3.4893 | 3.4893 | 3.9303 | 3.9303 | 2019-05-28 07:00 | 1.9586 | 3.361 | 5.6806 | 5.6806 | 5.6806 | 5.6806
2021-03-30 20:00 | 2.132 | 2.5944 | 2.5384 | 2.7303 | 2.5864 | 2.7783 | 1.629 | 2.7935 | 3.447 | 3.447 | 3.8826 | 3.8826 | 2019-05-28 08:00 | 2.0424 | 3.5048 | 5.9237 | 5.9237 | 5.9237 | 5.9237
2021-03-30 21:00 | 2.0062 | 2.4414 | 2.3887 | 2.5693 | 2.4339 | 2.6144 | 1.548 | 2.6545 | 3.2755 | 3.2755 | 3.6895 | 3.6895 | 2019-05-28 09:00 | 2.0119 | 3.4525 | 5.8353 | 5.8353 | 5.8353 | 5.8353
2021-03-30 22:00 | 1.7833 | 2.1701 | 2.1233 | 2.2838 | 2.1634 | 2.3239 | 1.3003 | 2.2299 | 2.7515 | 2.7515 | 3.0993 | 3.0993 | 2019-05-28 10:00 | 2.0501 | 3.5179 | 5.9458 | 5.9458 | 5.9458 | 5.9458
2021-03-30 23:00 | 1.5718 | 1.9128 | 1.8715 | 2.013 | 1.9069 | 2.0483 | 1.1774 | 2.0191 | 2.4915 | 2.4915 | 2.8064 | 2.8064 | 2019-05-28 11:00 | 2.0272 | 3.4787 | 5.8795 | 5.8795 | 5.8795 | 5.8795
2021-03-31 | 1.5147 | 1.8432 | 1.8034 | 1.9398 | 1.8375 | 1.9738 | 0.95453 | 1.6369 | 2.0198 | 2.0198 | 2.2751 | 2.2751 | 2019-05-28 12:00 | 2.0577 | 3.531 | 5.9679 | 5.9679 | 5.9679 | 5.9679
2021-03-31 01:00 | 1.3489 | 1.6415 | 1.6061 | 1.7275 | 1.6364 | 1.7578 | 0.89288 | 1.5311 | 1.8893 | 1.8893 | 2.1281 | 2.1281 | 2019-05-28 13:00 | 2.0424 | 3.5048 | 5.9237 | 5.9237 | 5.9237 | 5.9237
2021-03-31 02:00 | 1.3203 | 1.6067 | 1.5721 | 1.6909 | 1.6018 | 1.7206 | 0.80306 | 1.3771 | 1.6993 | 1.6993 | 1.9141 | 1.9141 | 2019-05-28 14:00 | 2.0577 | 3.531 | 5.9679 | 5.9679 | 5.9679 | 5.9679
2021-03-31 03:00 | 1.3232 | 1.6102 | 1.5755 | 1.6945 | 1.6052 | 1.7243 | 0.77448 | 1.3281 | 1.6388 | 1.6388 | 1.8459 | 1.8459 | 2019-05-28 15:00 | 2.0272 | 3.4787 | 5.8795 | 5.8795 | 5.8795 | 5.8795
2021-03-31 04:00 | 1.3743 | 1.6724 | 1.6364 | 1.76 | 1.6673 | 1.791 | 0.76861 | 1.318 | 1.6264 | 1.6264 | 1.832 | 1.832 | 2019-05-28 16:00 | 2.0348 | 3.4917 | 5.9016 | 5.9016 | 5.9016 | 5.9016
2021-03-31 05:00 | 1.5677 | 1.9077 | 1.8666 | 2.0077 | 1.9018 | 2.0429 | 0.83361 | 1.4295 | 1.7639 | 1.7639 | 1.9869 | 1.9869 | 2019-05-28 17:00 | 2.0805 | 3.5702 | 6.0343 | 6.0343 | 6.0343 | 6.0343
2021-03-31 06:00 | 2.0425 | 2.4855 | 2.4319 | 2.6157 | 2.4778 | 2.6616 | 1.1403 | 1.9554 | 2.4129 | 2.4129 | 2.7178 | 2.7178 | 2019-05-28 18:00 | 2.1491 | 3.6879 | 6.2332 | 6.2332 | 6.2332 | 6.2332
2021-03-31 07:00 | 2.5921 | 3.1543 | 3.0863 | 3.3196 | 3.1446 | 3.3779 | 1.2603 | 2.1613 | 2.6669 | 2.6669 | 3.0039 | 3.0039 | 2019-05-28 19:00 | 2.1491 | 3.6879 | 6.2332 | 6.2332 | 6.2332 | 6.2332
2021-03-31 08:00 | 2.6292 | 3.1995 | 3.1305 | 3.3671 | 3.1897 | 3.4263 | 1.3461 | 2.3083 | 2.8483 | 2.8483 | 3.2083 | 3.2083 | 2019-05-28 20:00 | 1.9357 | 3.3217 | 5.6143 | 5.6143 | 5.6143 | 5.6143
2021-03-31 09:00 | 2.4406 | 2.97 | 2.9059 | 3.1256 | 2.9608 | 3.1805 | 1.3632 | 2.3377 | 2.8846 | 2.8846 | 3.2491 | 3.2491 | 2019-05-28 21:00 | 1.8595 | 3.191 | 5.3932 | 5.3932 | 5.3932 | 5.3932
2021-03-31 10:00 | 2.2349 | 2.7196 | 2.6609 | 2.8621 | 2.7112 | 2.9124 | 1.3632 | 2.3377 | 2.8846 | 2.8846 | 3.2491 | 3.2491 | 2019-05-28 22:00 | 1.8595 | 3.191 | 5.3932 | 5.3932 | 5.3932 | 5.3932
2021-03-31 11:00 | 2.0205 | 2.4588 | 2.4057 | 2.5876 | 2.4512 | 2.633 | 1.3003 | 2.2299 | 2.7515 | 2.7515 | 3.0993 | 3.0993 | 2019-05-28 23:00 | 1.6461 | 2.8248 | 4.7743 | 4.7743 | 4.7743 | 4.7743
2021-03-31 12:00 | 2.0777 | 2.5283 | 2.4738 | 2.6608 | 2.5205 | 2.7075 | 1.4061 | 2.4112 | 2.9753 | 2.9753 | 3.3513 | 3.3513 | 2019-05-29 | 1.448 | 2.4848 | 4.1997 | 4.1997 | 4.1997 | 4.1997
2021-03-31 13:00 | 2.0577 | 2.504 | 2.45 | 2.6352 | 2.4963 | 2.6814 | 1.4661 | 2.5141 | 3.1023 | 3.1023 | 3.4944 | 3.4944 | 2019-05-29 01:00 | 1.3946 | 2.3932 | 4.0449 | 4.0449 | 4.0449 | 4.0449
2021-03-31 14:00 | 2.0234 | 2.4622 | 2.4091 | 2.5912 | 2.4547 | 2.6368 | 1.4375 | 2.4651 | 3.0418 | 3.0418 | 3.4262 | 3.4262 | 2019-05-29 02:00 | 1.4556 | 2.4978 | 4.2218 | 4.2218 | 4.2218 | 4.2218
2021-03-31 15:00 | 2.0634 | 2.5109 | 2.4568 | 2.6425 | 2.5032 | 2.6889 | 1.206 | 2.0681 | 2.552 | 2.552 | 2.8745 | 2.8745 | 2019-05-29 03:00 | 1.4023 | 2.4063 | 4.067 | 4.067 | 4.067 | 4.067
2021-03-31 16:00 | 2.032 | 2.4727 | 2.4193 | 2.6022 | 2.4651 | 2.6479 | 1.3689 | 2.3475 | 2.8967 | 2.8967 | 3.2628 | 3.2628 | 2019-05-29 04:00 | 1.4709 | 2.524 | 4.266 | 4.266 | 4.266 | 4.266
2021-03-31 17:00 | 2.1177 | 2.577 | 2.5214 | 2.712 | 2.5691 | 2.7597 | 1.4489 | 2.4847 | 3.066 | 3.066 | 3.4535 | 3.4535 | 2019-05-29 05:00 | 1.6385 | 2.8117 | 4.7522 | 4.7522 | 4.7522 | 4.7522
2021-03-31 18:00 | 2.3292 | 2.8344 | 2.7732 | 2.9828 | 2.8256 | 3.0353 | 1.4775 | 2.5337 | 3.1265 | 3.1265 | 3.5216 | 3.5216 | 2019-05-29 06:00 | 1.8748 | 3.2171 | 5.4375 | 5.4375 | 5.4375 | 5.4375
2021-03-31 19:00 | 2.2749 | 2.7683 | 2.7086 | 2.9133 | 2.7598 | 2.9645 | 1.5918 | 2.7297 | 3.3683 | 3.3683 | 3.7941 | 3.7941 | 2019-05-29 07:00 | 1.9815 | 3.4002 | 5.7469 | 5.7469 | 5.7469 | 5.7469
2021-03-31 20:00 | 2.192 | 2.6674 | 2.6099 | 2.8072 | 2.6592 | 2.8565 | 1.5347 | 2.6317 | 3.2474 | 3.2474 | 3.6578 | 3.6578 | 2019-05-29 08:00 | 2.1415 | 3.6748 | 6.2111 | 6.2111 | 6.2111 | 6.2111
2021-03-31 21:00 | 2.0462 | 2.4901 | 2.4364 | 2.6205 | 2.4824 | 2.6666 | 1.4747 | 2.5288 | 3.1204 | 3.1204 | 3.5148 | 3.5148 | 2019-05-29 09:00 | 2.2177 | 3.8056 | 6.4321 | 6.4321 | 6.4321 | 6.4321
2021-03-31 22:00 | 1.7404 | 2.1179 | 2.0723 | 2.2289 | 2.1114 | 2.2681 | 1.2403 | 2.1269 | 2.6245 | 2.6245 | 2.9562 | 2.9562 | 2019-05-29 10:00 | 2.0958 | 3.5964 | 6.0785 | 6.0785 | 6.0785 | 6.0785
2021-03-31 23:00 | 1.5575 | 1.8954 | 1.8545 | 1.9947 | 1.8895 | 2.0297 | 1.1632 | 1.9946 | 2.4612 | 2.4612 | 2.7723 | 2.7723 | 2019-05-29 11:00 | 2.0729 | 3.5571 | 6.0121 | 6.0121 | 6.0121 | 6.0121
2021-04-01 | 1.5204 | 1.8828 | 1.9127 | 2.0413 | 1.9899 | 2.1184 | 0.94596 | 1.4329 | 1.706 | 1.706 | 1.888 | 1.888 | 2019-05-29 12:00 | 2.0653 | 3.5441 | 5.99 | 5.99 | 5.99 | 5.99
2021-04-01 01:00 | 1.3805 | 1.7095 | 1.7367 | 1.8534 | 1.8068 | 1.9235 | 0.84021 | 1.2728 | 1.5153 | 1.5153 | 1.677 | 1.677 | 2019-05-29 13:00 | 2.0882 | 3.5833 | 6.0564 | 6.0564 | 6.0564 | 6.0564
2021-04-01 02:00 | 1.306 | 1.6173 | 1.6431 | 1.7535 | 1.7093 | 1.8197 | 0.75734 | 1.1472 | 1.3658 | 1.3658 | 1.5116 | 1.5116 | 2019-05-29 14:00 | 2.0805 | 3.5702 | 6.0343 | 6.0343 | 6.0343 | 6.0343
2021-04-01 03:00 | 1.286 | 1.5926 | 1.6179 | 1.7266 | 1.6832 | 1.7919 | 0.79449 | 1.2035 | 1.4328 | 1.4328 | 1.5857 | 1.5857 | 2019-05-29 15:00 | 2.0805 | 3.5702 | 6.0343 | 6.0343 | 6.0343 | 6.0343
2021-04-01 04:00 | 1.3289 | 1.6456 | 1.6719 | 1.7842 | 1.7393 | 1.8516 | 0.75477 | 1.1433 | 1.3612 | 1.3612 | 1.5064 | 1.5064 | 2019-05-29 16:00 | 2.1034 | 3.6094 | 6.1006 | 6.1006 | 6.1006 | 6.1006
2021-04-01 05:00 | 1.4975 | 1.8544 | 1.884 | 2.0106 | 1.9599 | 2.0865 | 0.77724 | 1.1774 | 1.4017 | 1.4017 | 1.5513 | 1.5513 | 2019-05-29 17:00 | 2.1339 | 3.6618 | 6.189 | 6.189 | 6.189 | 6.189
2021-04-01 06:00 | 1.9291 | 2.3888 | 2.4269 | 2.59 | 2.5247 | 2.6878 | 1.0431 | 1.5801 | 1.8812 | 1.8812 | 2.082 | 2.082 | 2019-05-29 18:00 | 2.1186 | 3.6356 | 6.1448 | 6.1448 | 6.1448 | 6.1448
2021-04-01 07:00 | 2.4092 | 2.9834 | 3.0309 | 3.2346 | 3.1531 | 3.3568 | 1.2603 | 1.9091 | 2.2729 | 2.2729 | 2.5155 | 2.5155 | 2019-05-29 19:00 | 2.0882 | 3.5833 | 6.0564 | 6.0564 | 6.0564 | 6.0564
2021-04-01 08:00 | 2.4092 | 2.9834 | 3.0309 | 3.2346 | 3.1531 | 3.3568 | 1.3118 | 1.9871 | 2.3657 | 2.3657 | 2.6181 | 2.6181 | 2019-05-29 20:00 | 1.9281 | 3.3087 | 5.5922 | 5.5922 | 5.5922 | 5.5922
2021-04-01 09:00 | 2.3292 | 2.8843 | 2.9302 | 3.1271 | 3.0484 | 3.2453 | 1.3289 | 2.013 | 2.3966 | 2.3966 | 2.6524 | 2.6524 | 2019-05-29 21:00 | 1.7681 | 3.034 | 5.128 | 5.128 | 5.128 | 5.128
2021-04-01 10:00 | 2.1977 | 2.7215 | 2.7649 | 2.9506 | 2.8763 | 3.0621 | 1.3689 | 2.0737 | 2.4688 | 2.4688 | 2.7322 | 2.7322 | 2019-05-29 22:00 | 1.7986 | 3.0863 | 5.2164 | 5.2164 | 5.2164 | 5.2164
2021-04-01 11:00 | 2.1748 | 2.6932 | 2.7361 | 2.9199 | 2.8464 | 3.0303 | 1.3175 | 1.9957 | 2.376 | 2.376 | 2.6295 | 2.6295 | 2019-05-29 23:00 | 1.6233 | 2.7855 | 4.708 | 4.708 | 4.708 | 4.708
2021-04-01 12:00 | 1.9777 | 2.449 | 2.488 | 2.6552 | 2.5883 | 2.7555 | 1.3403 | 2.0304 | 2.4173 | 2.4173 | 2.6752 | 2.6752 | 2019-05-30 | 1.5775 | 2.7071 | 4.5754 | 4.5754 | 4.5754 | 4.5754
2021-04-01 13:00 | 2.0548 | 2.5446 | 2.5851 | 2.7588 | 2.6893 | 2.863 | 1.3661 | 2.0693 | 2.4636 | 2.4636 | 2.7265 | 2.7265 | 2019-05-30 01:00 | 1.4251 | 2.4455 | 4.1333 | 4.1333 | 4.1333 | 4.1333
2021-04-01 14:00 | 2.0577 | 2.5481 | 2.5887 | 2.7626 | 2.6931 | 2.867 | 1.3289 | 2.013 | 2.3966 | 2.3966 | 2.6524 | 2.6524 | 2019-05-30 02:00 | 1.4175 | 2.4324 | 4.1112 | 4.1112 | 4.1112 | 4.1112
2021-04-01 15:00 | 2.0291 | 2.5127 | 2.5527 | 2.7243 | 2.6556 | 2.8272 | 1.2832 | 1.9438 | 2.3142 | 2.3142 | 2.5611 | 2.5611 | 2019-05-30 03:00 | 1.3642 | 2.3409 | 3.9565 | 3.9565 | 3.9565 | 3.9565
2021-04-01 16:00 | 2.0863 | 2.5835 | 2.6246 | 2.801 | 2.7305 | 2.9068 | 1.3175 | 1.9957 | 2.376 | 2.376 | 2.6295 | 2.6295 | 2019-05-30 04:00 | 1.4327 | 2.4586 | 4.1555 | 4.1555 | 4.1555 | 4.1555
2021-04-01 17:00 | 2.1034 | 2.6047 | 2.6462 | 2.824 | 2.7529 | 2.9307 | 1.529 | 2.3161 | 2.7574 | 2.7574 | 3.0516 | 3.0516 | 2019-05-30 05:00 | 1.6385 | 2.8117 | 4.7522 | 4.7522 | 4.7522 | 4.7522
2021-04-01 18:00 | 2.2892 | 2.8348 | 2.8799 | 3.0734 | 2.996 | 3.1895 | 1.4804 | 2.2425 | 2.6698 | 2.6698 | 2.9547 | 2.9547 | 2019-05-30 06:00 | 1.8595 | 3.191 | 5.3932 | 5.3932 | 5.3932 | 5.3932
2021-04-01 19:00 | 2.2356 | 2.7684 | 2.8125 | 3.0015 | 2.9259 | 3.1149 | 1.5004 | 2.2728 | 2.7059 | 2.7059 | 2.9946 | 2.9946 | 2019-05-30 07:00 | 2.0958 | 3.5964 | 6.0785 | 6.0785 | 6.0785 | 6.0785
2021-04-01 20:00 | 2.032 | 2.5162 | 2.5563 | 2.7281 | 2.6594 | 2.8312 | 1.5147 | 2.2944 | 2.7317 | 2.7317 | 3.0231 | 3.0231 | 2019-05-30 08:00 | 2.1491 | 3.6879 | 6.2332 | 6.2332 | 6.2332 | 6.2332
2021-04-01 21:00 | 1.8433 | 2.2827 | 2.319 | 2.4749 | 2.4125 | 2.5683 | 1.4232 | 2.1559 | 2.5667 | 2.5667 | 2.8406 | 2.8406 | 2019-05-30 09:00 | 2.0501 | 3.5179 | 5.9458 | 5.9458 | 5.9458 | 5.9458
2021-04-01 22:00 | 1.6606 | 2.0563 | 2.0891 | 2.2295 | 2.1733 | 2.3137 | 1.3403 | 2.0304 | 2.4173 | 2.4173 | 2.6752 | 2.6752 | 2019-05-30 10:00 | 2.0196 | 3.4656 | 5.8574 | 5.8574 | 5.8574 | 5.8574
2021-04-01 23:00 | 1.5118 | 1.8721 | 1.902 | 2.0298 | 1.9786 | 2.1064 | 1.0631 | 1.6104 | 1.9173 | 1.9173 | 2.1219 | 2.1219 | 2019-05-30 11:00 | 2.0272 | 3.4787 | 5.8795 | 5.8795 | 5.8795 | 5.8795
2021-04-02 | 1.4918 | 1.8474 | 1.8768 | 2.0029 | 1.9525 | 2.0786 | 0.97453 | 1.4762 | 1.7575 | 1.7575 | 1.9451 | 1.9451 | 2019-05-30 12:00 | 2.0424 | 3.5048 | 5.9237 | 5.9237 | 5.9237 | 5.9237
2021-04-02 01:00 | 1.3661 | 1.6917 | 1.7186 | 1.8341 | 1.7879 | 1.9034 | 0.83171 | 1.2599 | 1.5 | 1.5 | 1.66 | 1.66 | 2019-05-30 13:00 | 2.0958 | 3.5964 | 6.0785 | 6.0785 | 6.0785 | 6.0785
2021-04-02 02:00 | 1.2946 | 1.6032 | 1.6287 | 1.7382 | 1.6944 | 1.8038 | 0.7802 | 1.1819 | 1.4071 | 1.4071 | 1.5572 | 1.5572 | 2019-05-30 14:00 | 2.0272 | 3.4787 | 5.8795 | 5.8795 | 5.8795 | 5.8795
2021-04-02 03:00 | 1.2403 | 1.5359 | 1.5604 | 1.6652 | 1.6233 | 1.7282 | 0.79163 | 1.1992 | 1.4277 | 1.4277 | 1.58 | 1.58 | 2019-05-30 15:00 | 2.0653 | 3.5441 | 5.99 | 5.99 | 5.99 | 5.99
2021-04-02 04:00 | 1.2603 | 1.5607 | 1.5856 | 1.6921 | 1.6495 | 1.756 | 0.72018 | 1.0909 | 1.2988 | 1.2988 | 1.4374 | 1.4374 | 2019-05-30 16:00 | 2.172 | 3.7271 | 6.2995 | 6.2995 | 6.2995 | 6.2995
2021-04-02 05:00 | 1.3118 | 1.6244 | 1.6503 | 1.7612 | 1.7168 | 1.8277 | 0.72876 | 1.1039 | 1.3143 | 1.3143 | 1.4545 | 1.4545 | 2019-05-30 17:00 | 2.1949 | 3.7664 | 6.3658 | 6.3658 | 6.3658 | 6.3658
2021-04-02 06:00 | 1.4689 | 1.8191 | 1.848 | 1.9722 | 1.9225 | 2.0467 | 0.8002 | 1.2122 | 1.4431 | 1.4431 | 1.5971 | 1.5971 | 2019-05-30 18:00 | 2.1491 | 3.6879 | 6.2332 | 6.2332 | 6.2332 | 6.2332
2021-04-02 07:00 | 1.4461 | 1.7907 | 1.8193 | 1.9415 | 1.8926 | 2.0149 | 0.8545 | 1.2944 | 1.5411 | 1.5411 | 1.7055 | 1.7055 | 2019-05-30 19:00 | 2.1263 | 3.6487 | 6.1669 | 6.1669 | 6.1669 | 6.1669
2021-04-02 08:00 | 1.5861 | 1.9642 | 1.9954 | 2.1295 | 2.0759 | 2.21 | 0.987 | 1.4951 | 1.78 | 1.78 | 1.9699 | 1.9699 | 2019-05-30 20:00 | 1.9662 | 3.374 | 5.7027 | 5.7027 | 5.7027 | 5.7027
2021-04-02 09:00 | 1.5918 | 1.9712 | 2.0026 | 2.1372 | 2.0834 | 2.2179 | 1.126 | 1.7057 | 2.0307 | 2.0307 | 2.2474 | 2.2474 | 2019-05-30 21:00 | 1.7528 | 3.0079 | 5.0838 | 5.0838 | 5.0838 | 5.0838
2021-04-02 10:00 | 1.6376 | 2.0279 | 2.0602 | 2.1986 | 2.1432 | 2.2816 | 1.2175 | 1.8442 | 2.1956 | 2.1956 | 2.4299 | 2.4299 | 2019-05-30 22:00 | 1.7605 | 3.0209 | 5.1059 | 5.1059 | 5.1059 | 5.1059
2021-04-02 11:00 | 1.5404 | 1.9075 | 1.9379 | 2.0681 | 2.016 | 2.1463 | 1.2575 | 1.9048 | 2.2678 | 2.2678 | 2.5098 | 2.5098 | 2019-05-30 23:00 | 1.5775 | 2.7071 | 4.5754 | 4.5754 | 4.5754 | 4.5754
2021-04-02 12:00 | 1.4261 | 1.766 | 1.7941 | 1.9147 | 1.8664 | 1.987 | 1.226 | 1.8572 | 2.2111 | 2.2111 | 2.447 | 2.447 | 2019-05-31 | 1.4937 | 2.5632 | 4.3323 | 4.3323 | 4.3323 | 4.3323
2021-04-02 13:00 | 1.4175 | 1.7554 | 1.7833 | 1.9031 | 1.8552 | 1.975 | 1.226 | 1.8572 | 2.2111 | 2.2111 | 2.447 | 2.447 | 2019-05-31 01:00 | 1.4556 | 2.4978 | 4.2218 | 4.2218 | 4.2218 | 4.2218
2021-04-02 14:00 | 1.3432 | 1.6633 | 1.6898 | 1.8034 | 1.758 | 1.8715 | 1.126 | 1.7057 | 2.0307 | 2.0307 | 2.2474 | 2.2474 | 2019-05-31 02:00 | 1.4251 | 2.4455 | 4.1333 | 4.1333 | 4.1333 | 4.1333
2021-04-02 15:00 | 1.3975 | 1.7306 | 1.7581 | 1.8763 | 1.829 | 1.9472 | 1.2032 | 1.8226 | 2.1699 | 2.1699 | 2.4014 | 2.4014 | 2019-05-31 03:00 | 1.3565 | 2.3278 | 3.9344 | 3.9344 | 3.9344 | 3.9344
2021-04-02 16:00 | 1.4683 | 1.8183 | 1.8472 | 1.9714 | 1.9217 | 2.0458 | 1.2032 | 1.8226 | 2.1699 | 2.1699 | 2.4014 | 2.4014 | 2019-05-31 04:00 | 1.5013 | 2.5763 | 4.3544 | 4.3544 | 4.3544 | 4.3544
2021-04-02 17:00 | 1.6404 | 2.0314 | 2.0638 | 2.2024 | 2.147 | 2.2856 | 1.3489 | 2.0433 | 2.4327 | 2.4327 | 2.6923 | 2.6923 | 2019-05-31 05:00 | 1.6842 | 2.8902 | 4.8849 | 4.8849 | 4.8849 | 4.8849
2021-04-02 18:00 | 1.8062 | 2.2367 | 2.2723 | 2.425 | 2.3639 | 2.5166 | 1.3975 | 2.1169 | 2.5203 | 2.5203 | 2.7893 | 2.7893 | 2019-05-31 06:00 | 1.829 | 3.1386 | 5.3048 | 5.3048 | 5.3048 | 5.3048
2021-04-02 19:00 | 1.8233 | 2.2579 | 2.2939 | 2.448 | 2.3863 | 2.5405 | 1.4118 | 2.1386 | 2.5461 | 2.5461 | 2.8178 | 2.8178 | 2019-05-31 07:00 | 1.9738 | 3.3871 | 5.7248 | 5.7248 | 5.7248 | 5.7248
2021-04-02 20:00 | 1.7862 | 2.2119 | 2.2471 | 2.3981 | 2.3377 | 2.4887 | 1.3546 | 2.052 | 2.443 | 2.443 | 2.7037 | 2.7037 | 2019-05-31 08:00 | 2.172 | 3.7271 | 6.2995 | 6.2995 | 6.2995 | 6.2995
2021-04-02 21:00 | 1.669 | 2.0668 | 2.0997 | 2.2408 | 2.1844 | 2.3254 | 1.3203 | 2.0001 | 2.3812 | 2.3812 | 2.6353 | 2.6353 | 2019-05-31 09:00 | 2.1263 | 3.6487 | 6.1669 | 6.1669 | 6.1669 | 6.1669
2021-04-02 22:00 | 1.4975 | 1.8544 | 1.884 | 2.0106 | 1.9599 | 2.0865 | 1.2146 | 1.8399 | 2.1905 | 2.1905 | 2.4242 | 2.4242 | 2019-05-31 10:00 | 2.1567 | 3.701 | 6.2553 | 6.2553 | 6.2553 | 6.2553
2021-04-02 23:00 | 1.4547 | 1.8014 | 1.8301 | 1.953 | 1.9038 | 2.0268 | 1.0574 | 1.6018 | 1.907 | 1.907 | 2.1105 | 2.1105 | 2019-05-31 11:00 | 2.0882 | 3.5833 | 6.0564 | 6.0564 | 6.0564 | 6.0564
2021-04-03 | 1.3871 | 1.7177 | 1.7451 | 1.8623 | 1.8154 | 1.9327 | 0.92023 | 1.394 | 1.6596 | 1.6596 | 1.8367 | 1.8367 | 2019-05-31 12:00 | 2.1644 | 3.7141 | 6.2774 | 6.2774 | 6.2774 | 6.2774
2021-04-03 01:00 | 1.2443 | 1.5409 | 1.5655 | 1.6706 | 1.6286 | 1.7338 | 0.78306 | 1.1862 | 1.4122 | 1.4122 | 1.5629 | 1.5629 | 2019-05-31 13:00 | 2.0272 | 3.4787 | 5.8795 | 5.8795 | 5.8795 | 5.8795
2021-04-03 02:00 | 1.2634 | 1.5645 | 1.5894 | 1.6962 | 1.6535 | 1.7603 | 0.72876 | 1.1039 | 1.3143 | 1.3143 | 1.4545 | 1.4545 | 2019-05-31 14:00 | 2.1186 | 3.6356 | 6.1448 | 6.1448 | 6.1448 | 6.1448
2021-04-03 03:00 | 1.2689 | 1.5713 | 1.5964 | 1.7036 | 1.6607 | 1.768 | 0.69732 | 1.0563 | 1.2576 | 1.2576 | 1.3918 | 1.3918 | 2019-05-31 15:00 | 2.0348 | 3.4917 | 5.9016 | 5.9016 | 5.9016 | 5.9016
2021-04-03 04:00 | 1.2526 | 1.5512 | 1.5759 | 1.6818 | 1.6394 | 1.7453 | 0.70352 | 1.0657 | 1.2688 | 1.2688 | 1.4042 | 1.4042 | 2019-05-31 16:00 | 2.111 | 3.6225 | 6.1227 | 6.1227 | 6.1227 | 6.1227
2021-04-03 05:00 | 1.2946 | 1.6032 | 1.6287 | 1.7382 | 1.6944 | 1.8038 | 0.72175 | 1.0933 | 1.3017 | 1.3017 | 1.4405 | 1.4405 | 2019-05-31 17:00 | 2.2025 | 3.7795 | 6.3879 | 6.3879 | 6.3879 | 6.3879
2021-04-03 06:00 | 1.4318 | 1.7731 | 1.8013 | 1.9223 | 1.8739 | 1.9949 | 0.82592 | 1.2511 | 1.4895 | 1.4895 | 1.6485 | 1.6485 | 2019-05-31 18:00 | 2.0882 | 3.5833 | 6.0564 | 6.0564 | 6.0564 | 6.0564
2021-04-03 07:00 | 1.4861 | 1.8403 | 1.8696 | 1.9952 | 1.945 | 2.0706 | 0.89737 | 1.3593 | 1.6184 | 1.6184 | 1.7911 | 1.7911 | 2019-05-31 19:00 | 1.9281 | 3.3087 | 5.5922 | 5.5922 | 5.5922 | 5.5922
2021-04-03 08:00 | 1.6233 | 2.0102 | 2.0422 | 2.1794 | 2.1245 | 2.2617 | 1.126 | 1.7057 | 2.0307 | 2.0307 | 2.2474 | 2.2474 | 2019-05-31 20:00 | 1.8976 | 3.2563 | 5.5038 | 5.5038 | 5.5038 | 5.5038
2021-04-03 09:00 | 1.5804 | 1.9571 | 1.9883 | 2.1218 | 2.0684 | 2.202 | 1.2003 | 1.8182 | 2.1647 | 2.1647 | 2.3957 | 2.3957 | 2019-05-31 21:00 | 1.7757 | 3.0471 | 5.1501 | 5.1501 | 5.1501 | 5.1501
2021-04-03 10:00 | 1.4718 | 1.8226 | 1.8516 | 1.976 | 1.9263 | 2.0507 | 1.4068 | 2.1311 | 2.5372 | 2.5372 | 2.8079 | 2.8079 | 2019-05-31 22:00 | 1.7986 | 3.0863 | 5.2164 | 5.2164 | 5.2164 | 5.2164
2021-04-03 11:00 | 1.3689 | 1.6952 | 1.7222 | 1.8379 | 1.7916 | 1.9073 | 1.4146 | 2.1429 | 2.5513 | 2.5513 | 2.8235 | 2.8235 | 2019-05-31 23:00 | 1.6157 | 2.7725 | 4.6859 | 4.6859 | 4.6859 | 4.6859
2021-04-03 12:00 | 1.3175 | 1.6315 | 1.6575 | 1.7688 | 1.7243 | 1.8357 | 1.3489 | 2.0433 | 2.4327 | 2.4327 | 2.6923 | 2.6923 | 2019-06-01 | 1.5013 | 2.5763 | 4.3544 | 4.3544 | 4.3544 | 4.3544
2021-04-03 13:00 | 1.2603 | 1.5607 | 1.5856 | 1.6921 | 1.6495 | 1.756 | 1.4832 | 2.2468 | 2.675 | 2.675 | 2.9604 | 2.9604 | 2019-06-01 01:00 | 1.4099 | 2.4194 | 4.0891 | 4.0891 | 4.0891 | 4.0891
2021-04-03 14:00 | 1.2432 | 1.5395 | 1.564 | 1.6691 | 1.627 | 1.7321 | 1.3718 | 2.078 | 2.4739 | 2.4739 | 2.7379 | 2.7379 | 2019-06-01 02:00 | 1.387 | 2.3801 | 4.0228 | 4.0228 | 4.0228 | 4.0228
2021-04-03 15:00 | 1.3175 | 1.6315 | 1.6575 | 1.7688 | 1.7243 | 1.8357 | 1.3403 | 2.0304 | 2.4173 | 2.4173 | 2.6752 | 2.6752 | 2019-06-01 03:00 | 1.3794 | 2.3671 | 4.0007 | 4.0007 | 4.0007 | 4.0007
2021-04-03 16:00 | 1.3975 | 1.7306 | 1.7581 | 1.8763 | 1.829 | 1.9472 | 1.489 | 2.2555 | 2.6853 | 2.6853 | 2.9718 | 2.9718 | 2019-06-01 04:00 | 1.3794 | 2.3671 | 4.0007 | 4.0007 | 4.0007 | 4.0007
2021-04-03 17:00 | 1.4804 | 1.8332 | 1.8624 | 1.9876 | 1.9375 | 2.0626 | 1.5076 | 2.2838 | 2.719 | 2.719 | 3.0091 | 3.0091 | 2019-06-01 05:00 | 1.5318 | 2.6286 | 4.4428 | 4.4428 | 4.4428 | 4.4428
2021-04-03 18:00 | 1.6261 | 2.0137 | 2.0458 | 2.1832 | 2.1283 | 2.2657 | 1.5147 | 2.2944 | 2.7317 | 2.7317 | 3.0231 | 3.0231 | 2019-06-01 06:00 | 1.6233 | 2.7855 | 4.708 | 4.708 | 4.708 | 4.708
2021-04-03 19:00 | 1.669 | 2.0668 | 2.0997 | 2.2408 | 2.1844 | 2.3254 | 1.4975 | 2.2685 | 2.7007 | 2.7007 | 2.9889 | 2.9889 | 2019-06-01 07:00 | 1.8367 | 3.1517 | 5.3269 | 5.3269 | 5.3269 | 5.3269
2021-04-03 20:00 | 1.6061 | 1.9889 | 2.0206 | 2.1564 | 2.1021 | 2.2378 | 1.4832 | 2.2468 | 2.675 | 2.675 | 2.9604 | 2.9604 | 2019-06-01 08:00 | 2.0501 | 3.5179 | 5.9458 | 5.9458 | 5.9458 | 5.9458
2021-04-03 21:00 | 1.5877 | 1.9661 | 1.9974 | 2.1316 | 2.0779 | 2.2122 | 1.3918 | 2.1083 | 2.51 | 2.51 | 2.7779 | 2.7779 | 2019-06-01 09:00 | 2.0272 | 3.4787 | 5.8795 | 5.8795 | 5.8795 | 5.8795
2021-04-03 22:00 | 1.5032 | 1.8615 | 1.8912 | 2.0183 | 1.9674 | 2.0945 | 1.2832 | 1.9438 | 2.3142 | 2.3142 | 2.5611 | 2.5611 | 2019-06-01 10:00 | 2.0805 | 3.5702 | 6.0343 | 6.0343 | 6.0343 | 6.0343
2021-04-03 23:00 | 1.4575 | 1.8049 | 1.8337 | 1.9569 | 1.9076 | 2.0308 | 1.1357 | 1.7204 | 2.0482 | 2.0482 | 2.2668 | 2.2668 | 2019-06-01 11:00 | 2.0882 | 3.5833 | 6.0564 | 6.0564 | 6.0564 | 6.0564
2021-04-04 | 1.3805 | 1.7095 | 1.7368 | 1.8535 | 1.8068 | 1.9235 | 0.99422 | 1.5061 | 1.793 | 1.793 | 1.9844 | 1.9844 | 2019-06-01 12:00 | 2.0196 | 3.4656 | 5.8574 | 5.8574 | 5.8574 | 5.8574
2021-04-04 01:00 | 1.2689 | 1.5713 | 1.5964 | 1.7036 | 1.6607 | 1.768 | 0.79735 | 1.2078 | 1.438 | 1.438 | 1.5914 | 1.5914 | 2019-06-01 13:00 | 2.0577 | 3.531 | 5.9679 | 5.9679 | 5.9679 | 5.9679
2021-04-04 02:00 | 1.2251 | 1.517 | 1.5412 | 1.6448 | 1.6033 | 1.7069 | 0.77918 | 1.1803 | 1.4052 | 1.4052 | 1.5552 | 1.5552 | 2019-06-01 14:00 | 2.0043 | 3.4394 | 5.8132 | 5.8132 | 5.8132 | 5.8132
2021-04-04 02:00 | 1.226 | 1.5182 | 1.5424 | 1.6461 | 1.6046 | 1.7082 | 0.74876 | 1.1342 | 1.3504 | 1.3504 | 1.4944 | 1.4944 | 2019-06-01 15:00 | 2.0653 | 3.5441 | 5.99 | 5.99 | 5.99 | 5.99
2021-04-04 03:00 | 1.2146 | 1.5041 | 1.528 | 1.6307 | 1.5896 | 1.6923 | 0.70018 | 1.0606 | 1.2627 | 1.2627 | 1.3975 | 1.3975 | 2019-06-01 16:00 | 2.1034 | 3.6094 | 6.1006 | 6.1006 | 6.1006 | 6.1006
2021-04-04 04:00 | 1.2221 | 1.5134 | 1.5375 | 1.6408 | 1.5995 | 1.7028 | 0.69446 | 1.052 | 1.2524 | 1.2524 | 1.3861 | 1.3861 | 2019-06-01 17:00 | 2.1567 | 3.701 | 6.2553 | 6.2553 | 6.2553 | 6.2553
2021-04-04 05:00 | 1.3203 | 1.635 | 1.6611 | 1.7727 | 1.728 | 1.8397 | 0.76019 | 1.1515 | 1.371 | 1.371 | 1.5173 | 1.5173 | 2019-06-01 18:00 | 2.0882 | 3.5833 | 6.0564 | 6.0564 | 6.0564 | 6.0564
2021-04-04 06:00 | 1.489 | 1.8438 | 1.8732 | 1.9991 | 1.9487 | 2.0746 | 0.81164 | 1.2295 | 1.4638 | 1.4638 | 1.6199 | 1.6199 | 2019-06-01 19:00 | 1.8976 | 3.2563 | 5.5038 | 5.5038 | 5.5038 | 5.5038
2021-04-04 07:00 | 1.489 | 1.8438 | 1.8732 | 1.9991 | 1.9487 | 2.0746 | 0.90309 | 1.368 | 1.6287 | 1.6287 | 1.8025 | 1.8025 | 2019-06-01 20:00 | 1.951 | 3.3479 | 5.6585 | 5.6585 | 5.6585 | 5.6585
2021-04-04 08:00 | 1.5947 | 1.9748 | 2.0062 | 2.141 | 2.0871 | 2.2219 | 1.1031 | 1.671 | 1.9895 | 1.9895 | 2.2017 | 2.2017 | 2019-06-01 21:00 | 1.829 | 3.1386 | 5.3048 | 5.3048 | 5.3048 | 5.3048
2021-04-04 09:00 | 1.489 | 1.8438 | 1.8732 | 1.9991 | 1.9487 | 2.0746 | 1.2467 | 1.8884 | 2.2483 | 2.2483 | 2.4882 | 2.4882 | 2019-06-01 22:00 | 1.7681 | 3.034 | 5.128 | 5.128 | 5.128 | 5.128
2021-04-04 10:00 | 1.4289 | 1.7695 | 1.7977 | 1.9185 | 1.8702 | 1.991 | 1.4032 | 2.1256 | 2.5306 | 2.5306 | 2.8007 | 2.8007 | 2019-06-01 23:00 | 1.5471 | 2.6548 | 4.487 | 4.487 | 4.487 | 4.487
2021-04-04 11:00 | 1.3318 | 1.6492 | 1.6755 | 1.788 | 1.743 | 1.8556 | 1.4518 | 2.1992 | 2.6183 | 2.6183 | 2.8976 | 2.8976 | 2019-06-02 | 1.5242 | 2.6155 | 4.4207 | 4.4207 | 4.4207 | 4.4207
2021-04-04 12:00 | 1.3289 | 1.6456 | 1.6719 | 1.7842 | 1.7393 | 1.8516 | 1.4004 | 2.1213 | 2.5255 | 2.5255 | 2.795 | 2.795 | 2019-06-02 01:00 | 1.4023 | 2.4063 | 4.067 | 4.067 | 4.067 | 4.067
2021-04-04 13:00 | 1.2089 | 1.497 | 1.5209 | 1.623 | 1.5822 | 1.6844 | 1.4204 | 2.1516 | 2.5616 | 2.5616 | 2.8349 | 2.8349 | 2019-06-02 02:00 | 1.3718 | 2.354 | 3.9786 | 3.9786 | 3.9786 | 3.9786
2021-04-04 14:00 | 1.3146 | 1.628 | 1.6539 | 1.765 | 1.7206 | 1.8317 | 1.3804 | 2.091 | 2.4894 | 2.4894 | 2.755 | 2.755 | 2019-06-02 03:00 | 1.3413 | 2.3017 | 3.8902 | 3.8902 | 3.8902 | 3.8902
2021-04-04 15:00 | 1.3489 | 1.6704 | 1.697 | 1.8111 | 1.7654 | 1.8795 | 1.4347 | 2.1732 | 2.5873 | 2.5873 | 2.8634 | 2.8634 | 2019-06-02 04:00 | 1.4251 | 2.4455 | 4.1333 | 4.1333 | 4.1333 | 4.1333
2021-04-04 16:00 | 1.5175 | 1.8792 | 1.9092 | 2.0374 | 1.9861 | 2.1144 | 1.4804 | 2.2425 | 2.6698 | 2.6698 | 2.9547 | 2.9547 | 2019-06-02 05:00 | 1.6233 | 2.7855 | 4.708 | 4.708 | 4.708 | 4.708
2021-04-04 17:00 | 1.6947 | 2.0986 | 2.1321 | 2.2753 | 2.218 | 2.3613 | 1.4975 | 2.2685 | 2.7007 | 2.7007 | 2.9889 | 2.9889 | 2019-06-02 06:00 | 1.6004 | 2.7463 | 4.6417 | 4.6417 | 4.6417 | 4.6417
2021-04-04 18:00 | 1.769 | 2.1907 | 2.2255 | 2.3751 | 2.3153 | 2.4648 | 1.5461 | 2.3421 | 2.7883 | 2.7883 | 3.0859 | 3.0859 | 2019-06-02 07:00 | 1.7986 | 3.0863 | 5.2164 | 5.2164 | 5.2164 | 5.2164
2021-04-04 19:00 | 1.7431 | 2.1586 | 2.193 | 2.3403 | 2.2814 | 2.4287 | 1.5232 | 2.3074 | 2.7471 | 2.7471 | 3.0402 | 3.0402 | 2019-06-02 08:00 | 2.0119 | 3.4525 | 5.8353 | 5.8353 | 5.8353 | 5.8353
2021-04-04 20:00 | 1.649 | 2.042 | 2.0745 | 2.2139 | 2.1582 | 2.2976 | 1.4175 | 2.1472 | 2.5564 | 2.5564 | 2.8292 | 2.8292 | 2019-06-02 09:00 | 2.0196 | 3.4656 | 5.8574 | 5.8574 | 5.8574 | 5.8574
2021-04-04 21:00 | 1.5833 | 1.9606 | 1.9918 | 2.1257 | 2.0722 | 2.206 | 1.2889 | 1.9524 | 2.3245 | 2.3245 | 2.5725 | 2.5725 | 2019-06-02 10:00 | 2.0653 | 3.5441 | 5.99 | 5.99 | 5.99 | 5.99
2021-04-04 22:00 | 1.5032 | 1.8615 | 1.8912 | 2.0183 | 1.9674 | 2.0945 | 1.1403 | 1.7273 | 2.0565 | 2.0565 | 2.2759 | 2.2759 | 2019-06-02 11:00 | 1.951 | 3.3479 | 5.6585 | 5.6585 | 5.6585 | 5.6585
2021-04-04 23:00 | 1.4361 | 1.7784 | 1.8067 | 1.9281 | 1.8795 | 2.0009 | 0.96935 | 1.4684 | 1.7482 | 1.7482 | 1.9347 | 1.9347 | 2019-06-02 12:00 | 1.9738 | 3.3871 | 5.7248 | 5.7248 | 5.7248 | 5.7248
2021-04-05 | 1.2918 | 1.5996 | 1.6251 | 1.7343 | 1.6906 | 1.7998 | 0.81735 | 1.2381 | 1.4741 | 1.4741 | 1.6313 | 1.6313 | 2019-06-02 13:00 | 2.0043 | 3.4394 | 5.8132 | 5.8132 | 5.8132 | 5.8132
2021-04-05 01:00 | 1.2517 | 1.5501 | 1.5748 | 1.6806 | 1.6383 | 1.7441 | 0.74876 | 1.1342 | 1.3504 | 1.3504 | 1.4944 | 1.4944 | 2019-06-02 14:00 | 1.951 | 3.3479 | 5.6585 | 5.6585 | 5.6585 | 5.6585
2021-04-05 02:00 | 1.2013 | 1.4876 | 1.5113 | 1.6129 | 1.5723 | 1.6738 | 0.73398 | 1.1118 | 1.3237 | 1.3237 | 1.4649 | 1.4649 | 2019-06-02 15:00 | 1.9815 | 3.4002 | 5.7469 | 5.7469 | 5.7469 | 5.7469
2021-04-05 03:00 | 1.2546 | 1.5536 | 1.5784 | 1.6844 | 1.642 | 1.7481 | 0.70589 | 1.0693 | 1.273 | 1.273 | 1.4089 | 1.4089 | 2019-06-02 16:00 | 2.1263 | 3.6487 | 6.1669 | 6.1669 | 6.1669 | 6.1669
2021-04-05 04:00 | 1.2055 | 1.4928 | 1.5166 | 1.6185 | 1.5777 | 1.6797 | 0.70304 | 1.065 | 1.2679 | 1.2679 | 1.4032 | 1.4032 | 2019-06-02 17:00 | 2.1567 | 3.701 | 6.2553 | 6.2553 | 6.2553 | 6.2553
2021-04-05 05:00 | 1.2929 | 1.601 | 1.6265 | 1.7358 | 1.6921 | 1.8014 | 0.75783 | 1.148 | 1.3667 | 1.3667 | 1.5126 | 1.5126 | 2019-06-02 18:00 | 2.0577 | 3.531 | 5.9679 | 5.9679 | 5.9679 | 5.9679
2021-04-05 06:00 | 1.4289 | 1.7695 | 1.7977 | 1.9185 | 1.8702 | 1.991 | 0.79163 | 1.1992 | 1.4277 | 1.4277 | 1.58 | 1.58 | 2019-06-02 19:00 | 2.0196 | 3.4656 | 5.8574 | 5.8574 | 5.8574 | 5.8574
2021-04-05 07:00 | 1.4146 | 1.7518 | 1.7797 | 1.8993 | 1.8515 | 1.9711 | 0.90595 | 1.3723 | 1.6338 | 1.6338 | 1.8082 | 1.8082 | 2019-06-02 20:00 | 1.9129 | 3.2825 | 5.548 | 5.548 | 5.548 | 5.548
2021-04-05 08:00 | 1.4861 | 1.8403 | 1.8696 | 1.9952 | 1.945 | 2.0706 | 1.0374 | 1.5715 | 1.8709 | 1.8709 | 2.0706 | 2.0706 | 2019-06-02 21:00 | 1.8214 | 3.1256 | 5.2827 | 5.2827 | 5.2827 | 5.2827
2021-04-05 09:00 | 1.4861 | 1.8403 | 1.8696 | 1.9952 | 1.945 | 2.0706 | 1.2832 | 1.9438 | 2.3142 | 2.3142 | 2.5611 | 2.5611 | 2019-06-02 22:00 | 1.6538 | 2.8379 | 4.7965 | 4.7965 | 4.7965 | 4.7965
2021-04-05 10:00 | 1.5118 | 1.8721 | 1.902 | 2.0298 | 1.9786 | 2.1064 | 1.3315 | 2.017 | 2.4013 | 2.4013 | 2.6576 | 2.6576 | 2019-06-02 23:00 | 1.5013 | 2.5763 | 4.3544 | 4.3544 | 4.3544 | 4.3544
2021-04-05 11:00 | 1.4404 | 1.7837 | 1.8121 | 1.9338 | 1.8851 | 2.0069 | 1.489 | 2.2555 | 2.6853 | 2.6853 | 2.9718 | 2.9718 | 2019-06-03 | 1.448 | 2.4848 | 4.1997 | 4.1997 | 4.1997 | 4.1997
2021-04-05 12:00 | 1.3489 | 1.6704 | 1.697 | 1.8111 | 1.7654 | 1.8795 | 1.5004 | 2.2728 | 2.7059 | 2.7059 | 2.9946 | 2.9946 | 2019-06-03 01:00 | 1.3642 | 2.3409 | 3.9565 | 3.9565 | 3.9565 | 3.9565
2021-04-05 13:00 | 1.3718 | 1.6987 | 1.7258 | 1.8417 | 1.7954 | 1.9113 | 1.4947 | 2.2641 | 2.6956 | 2.6956 | 2.9832 | 2.9832 | 2019-06-03 02:00 | 1.2956 | 2.2232 | 3.7576 | 3.7576 | 3.7576 | 3.7576
2021-04-05 14:00 | 1.4404 | 1.7837 | 1.8121 | 1.9338 | 1.8851 | 2.0069 | 1.4975 | 2.2685 | 2.7007 | 2.7007 | 2.9889 | 2.9889 | 2019-06-03 03:00 | 1.3642 | 2.3409 | 3.9565 | 3.9565 | 3.9565 | 3.9565
2021-04-05 15:00 | 1.5061 | 1.8651 | 1.8948 | 2.0221 | 1.9712 | 2.0985 | 1.6176 | 2.4503 | 2.9172 | 2.9172 | 3.2285 | 3.2285 | 2019-06-03 04:00 | 1.4175 | 2.4324 | 4.1112 | 4.1112 | 4.1112 | 4.1112
2021-04-05 16:00 | 1.609 | 1.9925 | 2.0242 | 2.1602 | 2.1058 | 2.2418 | 1.5633 | 2.368 | 2.8193 | 2.8193 | 3.1201 | 3.1201 | 2019-06-03 05:00 | 1.5775 | 2.7071 | 4.5754 | 4.5754 | 4.5754 | 4.5754
2021-04-05 17:00 | 1.8462 | 2.2862 | 2.3226 | 2.4787 | 2.4163 | 2.5723 | 1.629 | 2.4676 | 2.9378 | 2.9378 | 3.2513 | 3.2513 | 2019-06-03 06:00 | 1.8519 | 3.1779 | 5.3711 | 5.3711 | 5.3711 | 5.3711
2021-04-05 18:00 | 2.0348 | 2.5198 | 2.5599 | 2.7319 | 2.6631 | 2.8351 | 1.6461 | 2.4936 | 2.9687 | 2.9687 | 3.2855 | 3.2855 | 2019-06-03 07:00 | 1.8824 | 3.2302 | 5.4596 | 5.4596 | 5.4596 | 5.4596
2021-04-05 19:00 | 1.9405 | 2.403 | 2.4413 | 2.6053 | 2.5397 | 2.7037 | 1.6376 | 2.4806 | 2.9533 | 2.9533 | 3.2684 | 3.2684 | 2019-06-03 08:00 | 2.1872 | 3.7533 | 6.3437 | 6.3437 | 6.3437 | 6.3437
2021-04-05 20:00 | 1.8119 | 2.2437 | 2.2795 | 2.4326 | 2.3714 | 2.5245 | 1.4118 | 2.1386 | 2.5461 | 2.5461 | 2.8178 | 2.8178 | 2019-06-03 09:00 | 2.1796 | 3.7402 | 6.3216 | 6.3216 | 6.3216 | 6.3216
2021-04-05 21:00 | 1.7033 | 2.1093 | 2.1429 | 2.2868 | 2.2292 | 2.3732 | 1.306 | 1.9784 | 2.3554 | 2.3554 | 2.6067 | 2.6067 | 2019-06-03 10:00 | 2.1415 | 3.6748 | 6.2111 | 6.2111 | 6.2111 | 6.2111
2021-04-05 22:00 | 1.524 | 1.8873 | 1.9173 | 2.0462 | 1.9946 | 2.1235 | 1.2346 | 1.8702 | 2.2266 | 2.2266 | 2.4641 | 2.4641 | 2019-06-03 11:00 | 2.1644 | 3.7141 | 6.2774 | 6.2774 | 6.2774 | 6.2774
2021-04-05 23:00 | 1.4349 | 1.7769 | 1.8052 | 1.9264 | 1.8779 | 1.9992 | 1.0526 | 1.5945 | 1.8984 | 1.8984 | 2.1009 | 2.1009 | 2019-06-03 12:00 | 2.1644 | 3.7141 | 6.2774 | 6.2774 | 6.2774 | 6.2774
2021-04-06 | 1.3176 | 1.6317 | 1.6576 | 1.769 | 1.7245 | 1.8359 | 0.87451 | 1.3247 | 1.5771 | 1.5771 | 1.7454 | 1.7454 | 2019-06-03 13:00 | 2.1034 | 3.6094 | 6.1006 | 6.1006 | 6.1006 | 6.1006
2021-04-06 01:00 | 1.2375 | 1.5324 | 1.5568 | 1.6614 | 1.6196 | 1.7242 | 0.80306 | 1.2165 | 1.4483 | 1.4483 | 1.6028 | 1.6028 | 2019-06-03 14:00 | 2.1339 | 3.6618 | 6.189 | 6.189 | 6.189 | 6.189
2021-04-06 02:00 | 1.2489 | 1.5466 | 1.5712 | 1.6768 | 1.6345 | 1.7401 | 0.73447 | 1.1126 | 1.3246 | 1.3246 | 1.4659 | 1.4659 | 2019-06-03 15:00 | 2.0805 | 3.5702 | 6.0343 | 6.0343 | 6.0343 | 6.0343
2021-04-06 03:00 | 1.2344 | 1.5286 | 1.553 | 1.6573 | 1.6156 | 1.7199 | 0.68877 | 1.0433 | 1.2422 | 1.2422 | 1.3747 | 1.3747 | 2019-06-03 16:00 | 2.2177 | 3.8056 | 6.4321 | 6.4321 | 6.4321 | 6.4321
2021-04-06 04:00 | 1.2803 | 1.5855 | 1.6107 | 1.719 | 1.6757 | 1.7839 | 0.74876 | 1.1342 | 1.3504 | 1.3504 | 1.4944 | 1.4944 | 2019-06-03 17:00 | 2.2711 | 3.8972 | 6.5868 | 6.5868 | 6.5868 | 6.5868
2021-04-06 05:00 | 1.5116 | 1.8719 | 1.9017 | 2.0295 | 1.9784 | 2.1062 | 0.74305 | 1.1256 | 1.3401 | 1.3401 | 1.483 | 1.483 | 2019-06-03 18:00 | 2.2101 | 3.7925 | 6.41 | 6.41 | 6.41 | 6.41
2021-04-06 06:00 | 1.7124 | 2.1206 | 2.1544 | 2.2991 | 2.2412 | 2.386 | 0.91738 | 1.3896 | 1.6545 | 1.6545 | 1.831 | 1.831 | 2019-06-03 19:00 | 2.111 | 3.6225 | 6.1227 | 6.1227 | 6.1227 | 6.1227
2021-04-06 07:00 | 2.0205 | 2.5021 | 2.5419 | 2.7127 | 2.6444 | 2.8152 | 1.1003 | 1.6667 | 1.9843 | 1.9843 | 2.196 | 2.196 | 2019-06-03 20:00 | 1.9662 | 3.374 | 5.7027 | 5.7027 | 5.7027 | 5.7027
2021-04-06 08:00 | 1.9576 | 2.4242 | 2.4628 | 2.6283 | 2.5621 | 2.7276 | 1.2032 | 1.8226 | 2.1699 | 2.1699 | 2.4014 | 2.4014 | 2019-06-03 21:00 | 1.8062 | 3.0994 | 5.2385 | 5.2385 | 5.2385 | 5.2385
2021-04-06 09:00 | 2.1577 | 2.672 | 2.7145 | 2.8969 | 2.824 | 3.0064 | 1.1974 | 1.8139 | 2.1596 | 2.1596 | 2.39 | 2.39 | 2019-06-03 22:00 | 1.8062 | 3.0994 | 5.2385 | 5.2385 | 5.2385 | 5.2385
2021-04-06 10:00 | 2.1263 | 2.633 | 2.675 | 2.8547 | 2.7828 | 2.9626 | 1.3003 | 1.9698 | 2.3451 | 2.3451 | 2.5953 | 2.5953 | 2019-06-03 23:00 | 1.6461 | 2.8248 | 4.7743 | 4.7743 | 4.7743 | 4.7743
2021-04-06 11:00 | 1.9948 | 2.4702 | 2.5096 | 2.6782 | 2.6108 | 2.7794 | 1.246 | 1.8875 | 2.2472 | 2.2472 | 2.4869 | 2.4869 | 2019-06-04 | 1.4709 | 2.524 | 4.266 | 4.266 | 4.266 | 4.266
2021-04-06 12:00 | 1.9541 | 2.4199 | 2.4584 | 2.6236 | 2.5575 | 2.7227 | 1.3346 | 2.0217 | 2.4069 | 2.4069 | 2.6638 | 2.6638 | 2019-06-04 01:00 | 1.4175 | 2.4324 | 4.1112 | 4.1112 | 4.1112 | 4.1112
2021-04-06 13:00 | 2.212 | 2.7392 | 2.7828 | 2.9698 | 2.895 | 3.082 | 1.4261 | 2.1602 | 2.5719 | 2.5719 | 2.8463 | 2.8463 | 2019-06-04 02:00 | 1.4175 | 2.4324 | 4.1112 | 4.1112 | 4.1112 | 4.1112
2021-04-06 14:00 | 2.2749 | 2.8171 | 2.8619 | 3.0542 | 2.9773 | 3.1696 | 1.306 | 1.9784 | 2.3554 | 2.3554 | 2.6067 | 2.6067 | 2019-06-04 03:00 | 1.3946 | 2.3932 | 4.0449 | 4.0449 | 4.0449 | 4.0449
2021-04-06 15:00 | 2.2149 | 2.7427 | 2.7864 | 2.9737 | 2.8988 | 3.086 | 1.2889 | 1.9524 | 2.3245 | 2.3245 | 2.5725 | 2.5725 | 2019-06-04 04:00 | 1.4556 | 2.4978 | 4.2218 | 4.2218 | 4.2218 | 4.2218
2021-04-06 16:00 | 2.1834 | 2.7038 | 2.7469 | 2.9315 | 2.8576 | 3.0422 | 1.5461 | 2.3421 | 2.7883 | 2.7883 | 3.0859 | 3.0859 | 2019-06-04 05:00 | 1.6614 | 2.8509 | 4.8186 | 4.8186 | 4.8186 | 4.8186
2021-04-06 17:00 | 2.3092 | 2.8595 | 2.9051 | 3.1003 | 3.0222 | 3.2174 | 1.5661 | 2.3724 | 2.8244 | 2.8244 | 3.1258 | 3.1258 | 2019-06-04 06:00 | 1.9434 | 3.3348 | 5.6364 | 5.6364 | 5.6364 | 5.6364
2021-04-06 18:00 | 2.4521 | 3.0365 | 3.0849 | 3.2921 | 3.2092 | 3.4165 | 1.649 | 2.4979 | 2.9739 | 2.9739 | 3.2912 | 3.2912 | 2019-06-04 07:00 | 2.0196 | 3.4656 | 5.8574 | 5.8574 | 5.8574 | 5.8574
2021-04-06 19:00 | 2.2443 | 2.7792 | 2.8235 | 3.0132 | 2.9373 | 3.127 | 1.6376 | 2.4806 | 2.9533 | 2.9533 | 3.2684 | 3.2684 | 2019-06-04 08:00 | 2.2863 | 3.9233 | 6.631 | 6.631 | 6.631 | 6.631
2021-04-06 20:00 | 1.9692 | 2.4386 | 2.4774 | 2.6439 | 2.5773 | 2.7438 | 1.5232 | 2.3074 | 2.7471 | 2.7471 | 3.0402 | 3.0402 | 2019-06-04 09:00 | 2.1339 | 3.6618 | 6.189 | 6.189 | 6.189 | 6.189
2021-04-06 21:00 | 1.7833 | 2.2084 | 2.2435 | 2.3943 | 2.334 | 2.4847 | 1.4375 | 2.1776 | 2.5925 | 2.5925 | 2.8691 | 2.8691 | 2019-06-04 10:00 | 2.1949 | 3.7664 | 6.3658 | 6.3658 | 6.3658 | 6.3658
2021-04-06 22:00 | 1.6321 | 2.0211 | 2.0533 | 2.1912 | 2.136 | 2.274 | 1.2291 | 1.8618 | 2.2166 | 2.2166 | 2.4531 | 2.4531 | 2019-06-04 11:00 | 2.1567 | 3.701 | 6.2553 | 6.2553 | 6.2553 | 6.2553
2021-04-06 23:00 | 1.4832 | 1.8368 | 1.866 | 1.9914 | 1.9412 | 2.0666 | 0.99302 | 1.5042 | 1.7909 | 1.7909 | 1.982 | 1.982 | 2019-06-04 12:00 | 2.2253 | 3.8187 | 6.4542 | 6.4542 | 6.4542 | 6.4542
2021-04-07 | 1.3579 | 1.6815 | 1.7083 | 1.8231 | 1.7772 | 1.8919 | 0.81449 | 1.2338 | 1.4689 | 1.4689 | 1.6256 | 1.6256 | 2019-06-04 13:00 | 2.1491 | 3.6879 | 6.2332 | 6.2332 | 6.2332 | 6.2332
2021-04-07 01:00 | 1.2546 | 1.5536 | 1.5784 | 1.6844 | 1.642 | 1.7481 | 0.7802 | 1.1819 | 1.4071 | 1.4071 | 1.5572 | 1.5572 | 2019-06-04 14:00 | 2.1491 | 3.6879 | 6.2332 | 6.2332 | 6.2332 | 6.2332
2021-04-07 02:00 | 1.1974 | 1.4829 | 1.5065 | 1.6077 | 1.5672 | 1.6684 | 0.70875 | 1.0736 | 1.2782 | 1.2782 | 1.4146 | 1.4146 | 2019-06-04 15:00 | 2.1567 | 3.701 | 6.2553 | 6.2553 | 6.2553 | 6.2553
2021-04-07 03:00 | 1.226 | 1.5182 | 1.5424 | 1.6461 | 1.6046 | 1.7082 | 0.69732 | 1.0563 | 1.2576 | 1.2576 | 1.3918 | 1.3918 | 2019-06-04 16:00 | 2.1415 | 3.6748 | 6.2111 | 6.2111 | 6.2111 | 6.2111
2021-04-07 04:00 | 1.2965 | 1.6055 | 1.6311 | 1.7407 | 1.6969 | 1.8065 | 0.72876 | 1.1039 | 1.3143 | 1.3143 | 1.4545 | 1.4545 | 2019-06-04 17:00 | 2.1872 | 3.7533 | 6.3437 | 6.3437 | 6.3437 | 6.3437
2021-04-07 05:00 | 1.5318 | 1.8969 | 1.9271 | 2.0566 | 2.0048 | 2.1343 | 0.82592 | 1.2511 | 1.4895 | 1.4895 | 1.6485 | 1.6485 | 2019-06-04 18:00 | 2.2177 | 3.8056 | 6.4321 | 6.4321 | 6.4321 | 6.4321
2021-04-07 06:00 | 1.6747 | 2.0739 | 2.1069 | 2.2485 | 2.1918 | 2.3334 | 0.97453 | 1.4762 | 1.7575 | 1.7575 | 1.9451 | 1.9451 | 2019-06-04 19:00 | 2.1796 | 3.7402 | 6.3216 | 6.3216 | 6.3216 | 6.3216
2021-04-07 07:00 | 1.9491 | 2.4136 | 2.4521 | 2.6168 | 2.5509 | 2.7157 | 1.2832 | 1.9438 | 2.3142 | 2.3142 | 2.5611 | 2.5611 | 2019-06-04 20:00 | 2.0043 | 3.4394 | 5.8132 | 5.8132 | 5.8132 | 5.8132
2021-04-07 08:00 | 2.0262 | 2.5092 | 2.5491 | 2.7204 | 2.6519 | 2.8232 | 1.3403 | 2.0304 | 2.4173 | 2.4173 | 2.6752 | 2.6752 | 2019-06-04 21:00 | 1.9129 | 3.2825 | 5.548 | 5.548 | 5.548 | 5.548
2021-04-07 09:00 | 2.0834 | 2.58 | 2.621 | 2.7972 | 2.7267 | 2.9028 | 1.2432 | 1.8832 | 2.242 | 2.242 | 2.4812 | 2.4812 | 2019-06-04 22:00 | 1.8976 | 3.2563 | 5.5038 | 5.5038 | 5.5038 | 5.5038
2021-04-07 10:00 | 2.0977 | 2.5976 | 2.639 | 2.8163 | 2.7454 | 2.9227 | 1.3718 | 2.078 | 2.4739 | 2.4739 | 2.7379 | 2.7379 | 2019-06-04 23:00 | 1.7147 | 2.9425 | 4.9733 | 4.9733 | 4.9733 | 4.9733
2021-04-07 11:00 | 2.0948 | 2.5941 | 2.6354 | 2.8125 | 2.7417 | 2.9188 | 1.4518 | 2.1992 | 2.6183 | 2.6183 | 2.8976 | 2.8976 | 2019-06-05 | 1.5394 | 2.6417 | 4.4649 | 4.4649 | 4.4649 | 4.4649
2021-04-07 12:00 | 2.0377 | 2.5233 | 2.5635 | 2.7358 | 2.6669 | 2.8391 | 1.4318 | 2.1689 | 2.5822 | 2.5822 | 2.8577 | 2.8577 | 2019-06-05 01:00 | 1.4861 | 2.5501 | 4.3102 | 4.3102 | 4.3102 | 4.3102
2021-04-07 13:00 | 2.032 | 2.5162 | 2.5563 | 2.7281 | 2.6594 | 2.8312 | 1.4261 | 2.1602 | 2.5719 | 2.5719 | 2.8463 | 2.8463 | 2019-06-05 02:00 | 1.448 | 2.4848 | 4.1997 | 4.1997 | 4.1997 | 4.1997
2021-04-07 14:00 | 2.0238 | 2.5062 | 2.5461 | 2.7171 | 2.6487 | 2.8198 | 1.3946 | 2.1126 | 2.5152 | 2.5152 | 2.7836 | 2.7836 | 2019-06-05 03:00 | 1.448 | 2.4848 | 4.1997 | 4.1997 | 4.1997 | 4.1997
2021-04-07 15:00 | 2.2063 | 2.7321 | 2.7756 | 2.9621 | 2.8875 | 3.0741 | 1.4004 | 2.1213 | 2.5255 | 2.5255 | 2.795 | 2.795 | 2019-06-05 04:00 | 1.5547 | 2.6678 | 4.5091 | 4.5091 | 4.5091 | 4.5091
2021-04-07 16:00 | 2.0948 | 2.5941 | 2.6354 | 2.8125 | 2.7417 | 2.9188 | 1.4604 | 2.2122 | 2.6337 | 2.6337 | 2.9148 | 2.9148 | 2019-06-05 05:00 | 1.6766 | 2.8771 | 4.8628 | 4.8628 | 4.8628 | 4.8628
2021-04-07 17:00 | 2.2206 | 2.7498 | 2.7936 | 2.9813 | 2.9063 | 3.094 | 1.529 | 2.3161 | 2.7574 | 2.7574 | 3.0516 | 3.0516 | 2019-06-05 06:00 | 1.9967 | 3.4264 | 5.7911 | 5.7911 | 5.7911 | 5.7911
2021-04-07 18:00 | 2.3835 | 2.9515 | 2.9986 | 3.2 | 3.1195 | 3.3209 | 1.6147 | 2.446 | 2.912 | 2.912 | 3.2228 | 3.2228 | 2019-06-05 07:00 | 1.9891 | 3.4133 | 5.769 | 5.769 | 5.769 | 5.769
2021-04-07 19:00 | 2.2492 | 2.7852 | 2.8296 | 3.0197 | 2.9437 | 3.1338 | 1.609 | 2.4373 | 2.9017 | 2.9017 | 3.2114 | 3.2114 | 2019-06-05 08:00 | 2.2482 | 3.8579 | 6.5205 | 6.5205 | 6.5205 | 6.5205
2021-04-07 20:00 | 1.9662 | 2.4349 | 2.4736 | 2.6398 | 2.5734 | 2.7396 | 1.5318 | 2.3204 | 2.7626 | 2.7626 | 3.0574 | 3.0574 | 2019-06-05 09:00 | 2.1186 | 3.6356 | 6.1448 | 6.1448 | 6.1448 | 6.1448
2021-04-07 21:00 | 1.8349 | 2.2722 | 2.3084 | 2.4635 | 2.4014 | 2.5566 | 1.4175 | 2.1472 | 2.5564 | 2.5564 | 2.8292 | 2.8292 | 2019-06-05 10:00 | 2.0805 | 3.5702 | 6.0343 | 6.0343 | 6.0343 | 6.0343
2021-04-07 22:00 | 1.6919 | 2.0951 | 2.1285 | 2.2715 | 2.2143 | 2.3573 | 1.3146 | 1.9914 | 2.3709 | 2.3709 | 2.6238 | 2.6238 | 2019-06-05 11:00 | 2.1339 | 3.6618 | 6.189 | 6.189 | 6.189 | 6.189
2021-04-07 23:00 | 1.4876 | 1.8421 | 1.8715 | 1.9972 | 1.9469 | 2.0727 | 1.0519 | 1.5935 | 1.8971 | 1.8971 | 2.0995 | 2.0995 | 2019-06-05 12:00 | 2.1263 | 3.6487 | 6.1669 | 6.1669 | 6.1669 | 6.1669
2021-04-08 | 1.4089 | 1.7447 | 1.7725 | 1.8916 | 1.844 | 1.9631 | 0.81132 | 1.229 | 1.4632 | 1.4632 | 1.6193 | 1.6193 | 2019-06-05 13:00 | 2.0805 | 3.5702 | 6.0343 | 6.0343 | 6.0343 | 6.0343
2021-04-08 01:00 | 1.2746 | 1.5784 | 1.6035 | 1.7113 | 1.6682 | 1.7759 | 0.81164 | 1.2295 | 1.4638 | 1.4638 | 1.6199 | 1.6199 | 2019-06-05 14:00 | 2.0577 | 3.531 | 5.9679 | 5.9679 | 5.9679 | 5.9679
2021-04-08 02:00 | 1.3032 | 1.6138 | 1.6395 | 1.7497 | 1.7056 | 1.8158 | 0.76313 | 1.156 | 1.3763 | 1.3763 | 1.5231 | 1.5231 | 2019-06-05 15:00 | 2.0196 | 3.4656 | 5.8574 | 5.8574 | 5.8574 | 5.8574
2021-04-08 03:00 | 1.2603 | 1.5607 | 1.5856 | 1.6921 | 1.6495 | 1.756 | 0.77448 | 1.1732 | 1.3967 | 1.3967 | 1.5458 | 1.5458 | 2019-06-05 16:00 | 2.1872 | 3.7533 | 6.3437 | 6.3437 | 6.3437 | 6.3437
2021-04-08 04:00 | 1.3137 | 1.6268 | 1.6527 | 1.7638 | 1.7194 | 1.8304 | 0.69446 | 1.052 | 1.2524 | 1.2524 | 1.3861 | 1.3861 | 2019-06-05 17:00 | 2.2711 | 3.8972 | 6.5868 | 6.5868 | 6.5868 | 6.5868
2021-04-08 05:00 | 1.4739 | 1.8252 | 1.8543 | 1.9789 | 1.9291 | 2.0536 | 0.80878 | 1.2251 | 1.4586 | 1.4586 | 1.6142 | 1.6142 | 2019-06-05 18:00 | 2.233 | 3.8318 | 6.4763 | 6.4763 | 6.4763 | 6.4763
2021-04-08 06:00 | 1.7862 | 2.2119 | 2.2471 | 2.3981 | 2.3377 | 2.4887 | 1.0917 | 1.6537 | 1.9688 | 1.9688 | 2.1789 | 2.1789 | 2019-06-05 19:00 | 2.1339 | 3.6618 | 6.189 | 6.189 | 6.189 | 6.189
2021-04-08 07:00 | 1.8919 | 2.3428 | 2.3802 | 2.5401 | 2.4761 | 2.636 | 1.266 | 1.9178 | 2.2832 | 2.2832 | 2.5269 | 2.5269 | 2019-06-05 20:00 | 2.0729 | 3.5571 | 6.0121 | 6.0121 | 6.0121 | 6.0121
2021-04-08 08:00 | 2.0462 | 2.5339 | 2.5743 | 2.7473 | 2.6781 | 2.8511 | 1.3089 | 1.9827 | 2.3606 | 2.3606 | 2.6124 | 2.6124 | 2019-06-05 21:00 | 1.9053 | 3.2694 | 5.5259 | 5.5259 | 5.5259 | 5.5259
2021-04-08 09:00 | 2.1005 | 2.6012 | 2.6426 | 2.8202 | 2.7492 | 2.9267 | 1.2889 | 1.9524 | 2.3245 | 2.3245 | 2.5725 | 2.5725 | 2019-06-05 22:00 | 1.9205 | 3.2956 | 5.5701 | 5.5701 | 5.5701 | 5.5701
2021-04-08 10:00 | 2.0634 | 2.5552 | 2.5959 | 2.7703 | 2.7005 | 2.875 | 1.3118 | 1.9871 | 2.3657 | 2.3657 | 2.6181 | 2.6181 | 2019-06-05 23:00 | 1.7376 | 2.9817 | 5.0396 | 5.0396 | 5.0396 | 5.0396
2021-04-08 11:00 | 1.9462 | 2.4101 | 2.4485 | 2.613 | 2.5472 | 2.7117 | 1.3432 | 2.0347 | 2.4224 | 2.4224 | 2.6809 | 2.6809 | 2019-06-06 | 1.5775 | 2.7071 | 4.5754 | 4.5754 | 4.5754 | 4.5754
2021-04-08 12:00 | 2.0834 | 2.58 | 2.621 | 2.7972 | 2.7267 | 2.9028 | 1.3689 | 2.0737 | 2.4688 | 2.4688 | 2.7322 | 2.7322 | 2019-06-06 01:00 | 1.509 | 2.5894 | 4.3765 | 4.3765 | 4.3765 | 4.3765
2021-04-08 13:00 | 2.0605 | 2.5516 | 2.5923 | 2.7665 | 2.6968 | 2.871 | 1.3918 | 2.1083 | 2.51 | 2.51 | 2.7779 | 2.7779 | 2019-06-06 02:00 | 1.4709 | 2.524 | 4.266 | 4.266 | 4.266 | 4.266
2021-04-08 14:00 | 2.1548 | 2.6684 | 2.7109 | 2.8931 | 2.8202 | 3.0024 | 1.4175 | 2.1472 | 2.5564 | 2.5564 | 2.8292 | 2.8292 | 2019-06-06 03:00 | 1.4251 | 2.4455 | 4.1333 | 4.1333 | 4.1333 | 4.1333
2021-04-08 15:00 | 2.1434 | 2.6543 | 2.6965 | 2.8777 | 2.8053 | 2.9864 | 1.4347 | 2.1732 | 2.5873 | 2.5873 | 2.8634 | 2.8634 | 2019-06-06 04:00 | 1.5166 | 2.6025 | 4.3986 | 4.3986 | 4.3986 | 4.3986
2021-04-08 16:00 | 2.1234 | 2.6295 | 2.6714 | 2.8509 | 2.7791 | 2.9586 | 1.4432 | 2.1862 | 2.6028 | 2.6028 | 2.8805 | 2.8805 | 2019-06-06 05:00 | 1.7376 | 2.9817 | 5.0396 | 5.0396 | 5.0396 | 5.0396
2021-04-08 17:00 | 2.2863 | 2.8312 | 2.8763 | 3.0696 | 2.9923 | 3.1855 | 1.5404 | 2.3334 | 2.778 | 2.778 | 3.0745 | 3.0745 | 2019-06-06 06:00 | 2.0043 | 3.4394 | 5.8132 | 5.8132 | 5.8132 | 5.8132
2021-04-08 18:00 | 2.4721 | 3.0613 | 3.11 | 3.319 | 3.2354 | 3.4444 | 1.7176 | 2.6018 | 3.0976 | 3.0976 | 3.4281 | 3.4281 | 2019-06-06 07:00 | 2.1339 | 3.6618 | 6.189 | 6.189 | 6.189 | 6.189
2021-04-08 19:00 | 2.292 | 2.8383 | 2.8835 | 3.0773 | 2.9998 | 3.1935 | 1.5747 | 2.3854 | 2.8399 | 2.8399 | 3.1429 | 3.1429 | 2019-06-06 08:00 | 2.1644 | 3.7141 | 6.2774 | 6.2774 | 6.2774 | 6.2774
2021-04-08 20:00 | 2.0634 | 2.5552 | 2.5959 | 2.7703 | 2.7005 | 2.875 | 1.4689 | 2.2252 | 2.6492 | 2.6492 | 2.9319 | 2.9319 | 2019-06-06 09:00 | 2.1263 | 3.6487 | 6.1669 | 6.1669 | 6.1669 | 6.1669
2021-04-08 21:00 | 1.8262 | 2.2614 | 2.2975 | 2.4518 | 2.3901 | 2.5445 | 1.4575 | 2.2079 | 2.6286 | 2.6286 | 2.909 | 2.909 | 2019-06-06 10:00 | 2.0729 | 3.5571 | 6.0121 | 6.0121 | 6.0121 | 6.0121
2021-04-08 22:00 | 1.6004 | 1.9819 | 2.0134 | 2.1487 | 2.0946 | 2.2299 | 1.3066 | 1.9793 | 2.3565 | 2.3565 | 2.6079 | 2.6079 | 2019-06-06 11:00 | 2.0272 | 3.4787 | 5.8795 | 5.8795 | 5.8795 | 5.8795
2021-04-08 23:00 | 1.5518 | 1.9217 | 1.9523 | 2.0835 | 2.031 | 2.1622 | 1.0289 | 1.5586 | 1.8556 | 1.8556 | 2.0536 | 2.0536 | 2019-06-06 12:00 | 2.1263 | 3.6487 | 6.1669 | 6.1669 | 6.1669 | 6.1669
2021-04-09 | 1.3375 | 1.6563 | 1.6827 | 1.7957 | 1.7505 | 1.8636 | 0.85165 | 1.2901 | 1.5359 | 1.5359 | 1.6998 | 1.6998 | 2019-06-06 13:00 | 2.1263 | 3.6487 | 6.1669 | 6.1669 | 6.1669 | 6.1669
2021-04-09 01:00 | 1.3118 | 1.6244 | 1.6503 | 1.7612 | 1.7168 | 1.8277 | 0.81735 | 1.2381 | 1.4741 | 1.4741 | 1.6313 | 1.6313 | 2019-06-06 14:00 | 2.1567 | 3.701 | 6.2553 | 6.2553 | 6.2553 | 6.2553
2021-04-09 02:00 | 1.2803 | 1.5855 | 1.6107 | 1.719 | 1.6757 | 1.7839 | 0.74019 | 1.1212 | 1.3349 | 1.3349 | 1.4773 | 1.4773 | 2019-06-06 15:00 | 2.1415 | 3.6748 | 6.2111 | 6.2111 | 6.2111 | 6.2111
2021-04-09 03:00 | 1.3175 | 1.6315 | 1.6575 | 1.7688 | 1.7243 | 1.8357 | 0.71447 | 1.0823 | 1.2885 | 1.2885 | 1.426 | 1.426 | 2019-06-06 16:00 | 2.1186 | 3.6356 | 6.1448 | 6.1448 | 6.1448 | 6.1448
2021-04-09 04:00 | 1.3803 | 1.7093 | 1.7365 | 1.8532 | 1.8065 | 1.9232 | 0.72304 | 1.0953 | 1.304 | 1.304 | 1.4431 | 1.4431 | 2019-06-06 17:00 | 2.1796 | 3.7402 | 6.3216 | 6.3216 | 6.3216 | 6.3216
2021-04-09 05:00 | 1.5743 | 1.9495 | 1.9805 | 2.1136 | 2.0604 | 2.1935 | 0.83736 | 1.2684 | 1.5101 | 1.5101 | 1.6713 | 1.6713 | 2019-06-06 18:00 | 2.172 | 3.7271 | 6.2995 | 6.2995 | 6.2995 | 6.2995
2021-04-09 06:00 | 1.7547 | 2.173 | 2.2076 | 2.3559 | 2.2966 | 2.4449 | 0.99168 | 1.5022 | 1.7885 | 1.7885 | 1.9793 | 1.9793 | 2019-06-06 19:00 | 2.111 | 3.6225 | 6.1227 | 6.1227 | 6.1227 | 6.1227
2021-04-09 07:00 | 2.0262 | 2.5092 | 2.5491 | 2.7204 | 2.6519 | 2.8232 | 1.2575 | 1.9048 | 2.2678 | 2.2678 | 2.5098 | 2.5098 | 2019-06-06 20:00 | 1.8976 | 3.2563 | 5.5038 | 5.5038 | 5.5038 | 5.5038
2021-04-09 08:00 | 2.0891 | 2.587 | 2.6282 | 2.8048 | 2.7342 | 2.9108 | 1.2975 | 1.9654 | 2.3399 | 2.3399 | 2.5896 | 2.5896 | 2019-06-06 21:00 | 1.8138 | 3.1125 | 5.2606 | 5.2606 | 5.2606 | 5.2606
2021-04-09 09:00 | 2.0605 | 2.5516 | 2.5923 | 2.7665 | 2.6968 | 2.871 | 1.3003 | 1.9698 | 2.3451 | 2.3451 | 2.5953 | 2.5953 | 2019-06-06 22:00 | 1.8062 | 3.0994 | 5.2385 | 5.2385 | 5.2385 | 5.2385
2021-04-09 10:00 | 2.1834 | 2.7038 | 2.7469 | 2.9315 | 2.8576 | 3.0422 | 1.4175 | 2.1472 | 2.5564 | 2.5564 | 2.8292 | 2.8292 | 2019-06-06 23:00 | 1.6385 | 2.8117 | 4.7522 | 4.7522 | 4.7522 | 4.7522
2021-04-09 11:00 | 2.0148 | 2.495 | 2.5348 | 2.7051 | 2.6369 | 2.8073 | 1.4461 | 2.1905 | 2.608 | 2.608 | 2.8862 | 2.8862 | 2019-06-07 | 1.448 | 2.4848 | 4.1997 | 4.1997 | 4.1997 | 4.1997
2021-04-09 12:00 | 2.072 | 2.5658 | 2.6067 | 2.7818 | 2.7118 | 2.8869 | 1.4518 | 2.1992 | 2.6183 | 2.6183 | 2.8976 | 2.8976 | 2019-06-07 01:00 | 1.4251 | 2.4455 | 4.1333 | 4.1333 | 4.1333 | 4.1333
2021-04-09 13:00 | 2.1434 | 2.6543 | 2.6965 | 2.8777 | 2.8053 | 2.9864 | 1.3861 | 2.0996 | 2.4997 | 2.4997 | 2.7664 | 2.7664 | 2019-06-07 02:00 | 1.4023 | 2.4063 | 4.067 | 4.067 | 4.067 | 4.067
2021-04-09 14:00 | 2.0805 | 2.5764 | 2.6174 | 2.7933 | 2.723 | 2.8988 | 1.3289 | 2.013 | 2.3966 | 2.3966 | 2.6524 | 2.6524 | 2019-06-07 03:00 | 1.3946 | 2.3932 | 4.0449 | 4.0449 | 4.0449 | 4.0449
2021-04-09 15:00 | 2.0034 | 2.4809 | 2.5204 | 2.6897 | 2.622 | 2.7913 | 1.3232 | 2.0044 | 2.3863 | 2.3863 | 2.641 | 2.641 | 2019-06-07 04:00 | 1.4327 | 2.4586 | 4.1555 | 4.1555 | 4.1555 | 4.1555
2021-04-09 16:00 | 1.9405 | 2.403 | 2.4413 | 2.6053 | 2.5397 | 2.7037 | 1.3832 | 2.0953 | 2.4946 | 2.4946 | 2.7607 | 2.7607 | 2019-06-07 05:00 | 1.6842 | 2.8902 | 4.8849 | 4.8849 | 4.8849 | 4.8849
2021-04-09 17:00 | 2.0977 | 2.5976 | 2.639 | 2.8163 | 2.7454 | 2.9227 | 1.5175 | 2.2988 | 2.7368 | 2.7368 | 3.0288 | 3.0288 | 2019-06-07 06:00 | 1.89 | 3.2433 | 5.4817 | 5.4817 | 5.4817 | 5.4817
2021-04-09 18:00 | 2.1234 | 2.6295 | 2.6714 | 2.8509 | 2.7791 | 2.9586 | 1.6604 | 2.5152 | 2.9945 | 2.9945 | 3.314 | 3.314 | 2019-06-07 07:00 | 1.951 | 3.3479 | 5.6585 | 5.6585 | 5.6585 | 5.6585
2021-04-09 19:00 | 2.0262 | 2.5092 | 2.5491 | 2.7204 | 2.6519 | 2.8232 | 1.6861 | 2.5542 | 3.0409 | 3.0409 | 3.3654 | 3.3654 | 2019-06-07 08:00 | 2.2177 | 3.8056 | 6.4321 | 6.4321 | 6.4321 | 6.4321
2021-04-09 20:00 | 1.8548 | 2.2968 | 2.3334 | 2.4902 | 2.4275 | 2.5843 | 1.5433 | 2.3377 | 2.7832 | 2.7832 | 3.0802 | 3.0802 | 2019-06-07 09:00 | 2.1263 | 3.6487 | 6.1669 | 6.1669 | 6.1669 | 6.1669
2021-04-09 21:00 | 1.7719 | 2.1942 | 2.2291 | 2.3789 | 2.319 | 2.4688 | 1.5032 | 2.2771 | 2.711 | 2.711 | 3.0003 | 3.0003 | 2019-06-07 10:00 | 1.9891 | 3.4133 | 5.769 | 5.769 | 5.769 | 5.769
2021-04-09 22:00 | 1.6118 | 1.996 | 2.0278 | 2.1641 | 2.1096 | 2.2458 | 1.3146 | 1.9914 | 2.3709 | 2.3709 | 2.6238 | 2.6238 | 2019-06-07 11:00 | 2.0501 | 3.5179 | 5.9458 | 5.9458 | 5.9458 | 5.9458
2021-04-09 23:00 | 1.529 | 1.8934 | 1.9236 | 2.0528 | 2.0011 | 2.1304 | 1.1092 | 1.6801 | 2.0003 | 2.0003 | 2.2137 | 2.2137 | 2019-06-07 12:00 | 2.0882 | 3.5833 | 6.0564 | 6.0564 | 6.0564 | 6.0564
2021-04-10 | 1.3546 | 1.6775 | 1.7042 | 1.8187 | 1.7729 | 1.8874 | 0.95453 | 1.4459 | 1.7215 | 1.7215 | 1.9051 | 1.9051 | 2019-06-07 13:00 | 2.1263 | 3.6487 | 6.1669 | 6.1669 | 6.1669 | 6.1669
2021-04-10 01:00 | 1.3032 | 1.6138 | 1.6395 | 1.7497 | 1.7056 | 1.8158 | 0.82309 | 1.2468 | 1.4844 | 1.4844 | 1.6428 | 1.6428 | 2019-06-07 14:00 | 2.1263 | 3.6487 | 6.1669 | 6.1669 | 6.1669 | 6.1669
2021-04-10 02:00 | 1.243 | 1.5392 | 1.5637 | 1.6688 | 1.6268 | 1.7319 | 0.79163 | 1.1992 | 1.4277 | 1.4277 | 1.58 | 1.58 | 2019-06-07 15:00 | 2.1491 | 3.6879 | 6.2332 | 6.2332 | 6.2332 | 6.2332
2021-04-10 03:00 | 1.2403 | 1.5359 | 1.5604 | 1.6652 | 1.6233 | 1.7282 | 0.73443 | 1.1125 | 1.3245 | 1.3245 | 1.4658 | 1.4658 | 2019-06-07 16:00 | 2.0424 | 3.5048 | 5.9237 | 5.9237 | 5.9237 | 5.9237
2021-04-10 04:00 | 1.3232 | 1.6386 | 1.6647 | 1.7765 | 1.7318 | 1.8436 | 0.73447 | 1.1126 | 1.3246 | 1.3246 | 1.4659 | 1.4659 | 2019-06-07 17:00 | 2.2101 | 3.7925 | 6.41 | 6.41 | 6.41 | 6.41
2021-04-10 05:00 | 1.3546 | 1.6775 | 1.7042 | 1.8187 | 1.7729 | 1.8874 | 0.76019 | 1.1515 | 1.371 | 1.371 | 1.5173 | 1.5173 | 2019-06-07 18:00 | 2.0805 | 3.5702 | 6.0343 | 6.0343 | 6.0343 | 6.0343
2021-04-10 06:00 | 1.529 | 1.8934 | 1.9235 | 2.0528 | 2.0011 | 2.1303 | 0.91166 | 1.381 | 1.6441 | 1.6441 | 1.8196 | 1.8196 | 2019-06-07 19:00 | 1.9053 | 3.2694 | 5.5259 | 5.5259 | 5.5259 | 5.5259
2021-04-10 07:00 | 1.5947 | 1.9748 | 2.0062 | 2.141 | 2.0871 | 2.2219 | 1.0088 | 1.5282 | 1.8194 | 1.8194 | 2.0135 | 2.0135 | 2019-06-07 20:00 | 1.8138 | 3.1125 | 5.2606 | 5.2606 | 5.2606 | 5.2606
2021-04-10 08:00 | 1.6633 | 2.0597 | 2.0925 | 2.2331 | 2.1769 | 2.3175 | 1.1917 | 1.8052 | 2.1492 | 2.1492 | 2.3786 | 2.3786 | 2019-06-07 21:00 | 1.7833 | 3.0602 | 5.1722 | 5.1722 | 5.1722 | 5.1722
2021-04-10 09:00 | 1.6804 | 2.0809 | 2.1141 | 2.2561 | 2.1993 | 2.3414 | 1.3975 | 2.1169 | 2.5203 | 2.5203 | 2.7893 | 2.7893 | 2019-06-07 22:00 | 1.8062 | 3.0994 | 5.2385 | 5.2385 | 5.2385 | 5.2385
2021-04-10 10:00 | 1.6519 | 2.0456 | 2.0781 | 2.2178 | 2.1619 | 2.3016 | 1.4861 | 2.2511 | 2.6801 | 2.6801 | 2.9661 | 2.9661 | 2019-06-07 23:00 | 1.6766 | 2.8771 | 4.8628 | 4.8628 | 4.8628 | 4.8628
2021-04-10 11:00 | 1.5461 | 1.9146 | 1.9451 | 2.0758 | 2.0235 | 2.1542 | 1.5061 | 2.2815 | 2.7162 | 2.7162 | 3.006 | 3.006 | 2019-06-08 | 1.4861 | 2.5501 | 4.3102 | 4.3102 | 4.3102 | 4.3102
2021-04-10 12:00 | 1.5804 | 1.9571 | 1.9883 | 2.1218 | 2.0684 | 2.202 | 1.5061 | 2.2815 | 2.7162 | 2.7162 | 3.006 | 3.006 | 2019-06-08 01:00 | 1.4861 | 2.5501 | 4.3102 | 4.3102 | 4.3102 | 4.3102
2021-04-10 13:00 | 1.6061 | 1.9889 | 2.0206 | 2.1564 | 2.1021 | 2.2378 | 1.5747 | 2.3854 | 2.8399 | 2.8399 | 3.1429 | 3.1429 | 2019-06-08 02:00 | 1.4023 | 2.4063 | 4.067 | 4.067 | 4.067 | 4.067
2021-04-10 14:00 | 1.6033 | 1.9854 | 2.017 | 2.1525 | 2.0983 | 2.2339 | 1.5232 | 2.3074 | 2.7471 | 2.7471 | 3.0402 | 3.0402 | 2019-06-08 03:00 | 1.387 | 2.3801 | 4.0228 | 4.0228 | 4.0228 | 4.0228
2021-04-10 15:00 | 1.4547 | 1.8014 | 1.8301 | 1.953 | 1.9038 | 2.0268 | 1.4089 | 2.1343 | 2.541 | 2.541 | 2.8121 | 2.8121 | 2019-06-08 04:00 | 1.4175 | 2.4324 | 4.1112 | 4.1112 | 4.1112 | 4.1112
2021-04-10 16:00 | 1.5789 | 1.9552 | 1.9863 | 2.1198 | 2.0664 | 2.1998 | 1.5375 | 2.3291 | 2.7729 | 2.7729 | 3.0688 | 3.0688 | 2019-06-08 05:00 | 1.5852 | 2.7202 | 4.5975 | 4.5975 | 4.5975 | 4.5975
2021-04-10 17:00 | 1.9261 | 2.3851 | 2.4231 | 2.586 | 2.5208 | 2.6836 | 1.6233 | 2.4589 | 2.9275 | 2.9275 | 3.2399 | 3.2399 | 2019-06-08 06:00 | 1.6842 | 2.8902 | 4.8849 | 4.8849 | 4.8849 | 4.8849
2021-04-10 18:00 | 2.0977 | 2.5976 | 2.639 | 2.8163 | 2.7454 | 2.9227 | 1.7833 | 2.7014 | 3.2161 | 3.2161 | 3.5593 | 3.5593 | 2019-06-08 07:00 | 1.8062 | 3.0994 | 5.2385 | 5.2385 | 5.2385 | 5.2385
2021-04-10 19:00 | 1.9977 | 2.4738 | 2.5132 | 2.682 | 2.6145 | 2.7834 | 1.6747 | 2.5369 | 3.0203 | 3.0203 | 3.3426 | 3.3426 | 2019-06-08 08:00 | 2.0805 | 3.5702 | 6.0343 | 6.0343 | 6.0343 | 6.0343
2021-04-10 20:00 | 1.8891 | 2.3393 | 2.3766 | 2.5362 | 2.4724 | 2.6321 | 1.5575 | 2.3594 | 2.809 | 2.809 | 3.1087 | 3.1087 | 2019-06-08 09:00 | 2.0729 | 3.5571 | 6.0121 | 6.0121 | 6.0121 | 6.0121
2021-04-10 21:00 | 1.8062 | 2.2368 | 2.2724 | 2.4251 | 2.364 | 2.5167 | 1.5433 | 2.3377 | 2.7832 | 2.7832 | 3.0802 | 3.0802 | 2019-06-08 10:00 | 2.1415 | 3.6748 | 6.2111 | 6.2111 | 6.2111 | 6.2111
2021-04-10 22:00 | 1.7004 | 2.1057 | 2.1393 | 2.283 | 2.2255 | 2.3692 | 1.3689 | 2.0737 | 2.4688 | 2.4688 | 2.7322 | 2.7322 | 2019-06-08 11:00 | 2.2482 | 3.8579 | 6.5205 | 6.5205 | 6.5205 | 6.5205
2021-04-10 23:00 | 1.5978 | 1.9786 | 2.0101 | 2.1451 | 2.0911 | 2.2262 | 1.2317 | 1.8659 | 2.2214 | 2.2214 | 2.4584 | 2.4584 | 2019-06-08 12:00 | 2.2177 | 3.8056 | 6.4321 | 6.4321 | 6.4321 | 6.4321
2021-04-11 | 1.4347 | 1.7766 | 1.8049 | 1.9262 | 1.8777 | 1.9989 | 1.0088 | 1.5282 | 1.8194 | 1.8194 | 2.0135 | 2.0135 | 2019-06-08 13:00 | 2.2025 | 3.7795 | 6.3879 | 6.3879 | 6.3879 | 6.3879
2021-04-11 01:00 | 1.366 | 1.6916 | 1.7185 | 1.834 | 1.7878 | 1.9033 | 0.89224 | 1.3516 | 1.6091 | 1.6091 | 1.7808 | 1.7808 | 2019-06-08 14:00 | 2.1415 | 3.6748 | 6.2111 | 6.2111 | 6.2111 | 6.2111
2021-04-11 02:00 | 1.3661 | 1.6917 | 1.7186 | 1.8341 | 1.7879 | 1.9034 | 0.82042 | 1.2428 | 1.4796 | 1.4796 | 1.6375 | 1.6375 | 2019-06-08 15:00 | 2.2025 | 3.7795 | 6.3879 | 6.3879 | 6.3879 | 6.3879
2021-04-11 03:00 | 1.3375 | 1.6563 | 1.6826 | 1.7957 | 1.7505 | 1.8635 | 0.77162 | 1.1689 | 1.3916 | 1.3916 | 1.5401 | 1.5401 | 2019-06-08 16:00 | 2.2634 | 3.8841 | 6.5647 | 6.5647 | 6.5647 | 6.5647
2021-04-11 04:00 | 1.3918 | 1.7235 | 1.751 | 1.8686 | 1.8215 | 1.9392 | 0.78877 | 1.1948 | 1.4225 | 1.4225 | 1.5743 | 1.5743 | 2019-06-08 17:00 | 2.1491 | 3.6879 | 6.2332 | 6.2332 | 6.2332 | 6.2332
2021-04-11 05:00 | 1.4323 | 1.7737 | 1.8019 | 1.923 | 1.8746 | 1.9957 | 0.84879 | 1.2857 | 1.5308 | 1.5308 | 1.6941 | 1.6941 | 2019-06-08 18:00 | 2.0729 | 3.5571 | 6.0121 | 6.0121 | 6.0121 | 6.0121
2021-04-11 06:00 | 1.4947 | 1.8509 | 1.8804 | 2.0067 | 1.9562 | 2.0825 | 0.86594 | 1.3117 | 1.5617 | 1.5617 | 1.7283 | 1.7283 | 2019-06-08 19:00 | 1.9205 | 3.2956 | 5.5701 | 5.5701 | 5.5701 | 5.5701
2021-04-11 07:00 | 1.5947 | 1.9748 | 2.0062 | 2.141 | 2.0871 | 2.2219 | 1.0488 | 1.5888 | 1.8915 | 1.8915 | 2.0934 | 2.0934 | 2019-06-08 20:00 | 1.7909 | 3.0733 | 5.1943 | 5.1943 | 5.1943 | 5.1943
2021-04-11 08:00 | 1.7747 | 2.1977 | 2.2327 | 2.3828 | 2.3228 | 2.4728 | 1.1972 | 1.8136 | 2.1591 | 2.1591 | 2.3895 | 2.3895 | 2019-06-08 21:00 | 1.7452 | 2.9948 | 5.0617 | 5.0617 | 5.0617 | 5.0617
2021-04-11 09:00 | 1.8319 | 2.2685 | 2.3046 | 2.4595 | 2.3976 | 2.5524 | 1.3661 | 2.0693 | 2.4636 | 2.4636 | 2.7265 | 2.7265 | 2019-06-08 22:00 | 1.7223 | 2.9556 | 4.9954 | 4.9954 | 4.9954 | 4.9954
2021-04-11 10:00 | 1.6976 | 2.1022 | 2.1357 | 2.2792 | 2.2218 | 2.3653 | 1.5461 | 2.3421 | 2.7883 | 2.7883 | 3.0859 | 3.0859 | 2019-06-08 23:00 | 1.6995 | 2.9163 | 4.9291 | 4.9291 | 4.9291 | 4.9291
2021-04-11 11:00 | 1.789 | 2.2154 | 2.2507 | 2.4019 | 2.3415 | 2.4927 | 1.6804 | 2.5455 | 3.0306 | 3.0306 | 3.354 | 3.354 | 2019-06-09 | 1.5394 | 2.6417 | 4.4649 | 4.4649 | 4.4649 | 4.4649
2021-04-11 12:00 | 1.8376 | 2.2756 | 2.3118 | 2.4672 | 2.405 | 2.5604 | 1.8119 | 2.7447 | 3.2677 | 3.2677 | 3.6163 | 3.6163 | 2019-06-09 01:00 | 1.3946 | 2.3932 | 4.0449 | 4.0449 | 4.0449 | 4.0449
2021-04-11 13:00 | 1.6747 | 2.0739 | 2.1069 | 2.2485 | 2.1918 | 2.3334 | 1.609 | 2.4373 | 2.9017 | 2.9017 | 3.2114 | 3.2114 | 2019-06-09 02:00 | 1.3946 | 2.3932 | 4.0449 | 4.0449 | 4.0449 | 4.0449
2021-04-11 14:00 | 1.6861 | 2.088 | 2.1213 | 2.2638 | 2.2068 | 2.3493 | 1.6747 | 2.5369 | 3.0203 | 3.0203 | 3.3426 | 3.3426 | 2019-06-09 03:00 | 1.4023 | 2.4063 | 4.067 | 4.067 | 4.067 | 4.067
2021-04-11 15:00 | 1.6604 | 2.0562 | 2.0889 | 2.2293 | 2.1731 | 2.3135 | 1.5456 | 2.3413 | 2.7874 | 2.7874 | 3.0848 | 3.0848 | 2019-06-09 04:00 | 1.4099 | 2.4194 | 4.0891 | 4.0891 | 4.0891 | 4.0891
2021-04-11 16:00 | 1.8862 | 2.3358 | 2.373 | 2.5324 | 2.4686 | 2.6281 | 1.585 | 2.4009 | 2.8585 | 2.8585 | 3.1635 | 3.1635 | 2019-06-09 05:00 | 1.7147 | 2.9425 | 4.9733 | 4.9733 | 4.9733 | 4.9733
2021-04-11 17:00 | 2.3896 | 2.9591 | 3.0062 | 3.2082 | 3.1274 | 3.3294 | 1.7772 | 2.6921 | 3.2051 | 3.2051 | 3.5471 | 3.5471 | 2019-06-09 06:00 | 1.7071 | 2.9294 | 4.9512 | 4.9512 | 4.9512 | 4.9512
2021-04-11 18:00 | 2.6035 | 3.2241 | 3.2754 | 3.4955 | 3.4075 | 3.6275 | 1.9119 | 2.8962 | 3.4481 | 3.4481 | 3.816 | 3.816 | 2019-06-09 07:00 | 1.7986 | 3.0863 | 5.2164 | 5.2164 | 5.2164 | 5.2164
2021-04-11 19:00 | 2.5407 | 3.1462 | 3.1963 | 3.4111 | 3.3252 | 3.5399 | 1.9262 | 2.9178 | 3.4738 | 3.4738 | 3.8445 | 3.8445 | 2019-06-09 08:00 | 2.172 | 3.7271 | 6.2995 | 6.2995 | 6.2995 | 6.2995
2021-04-11 20:00 | 2.232 | 2.764 | 2.808 | 2.9967 | 2.9212 | 3.1099 | 1.7747 | 2.6884 | 3.2007 | 3.2007 | 3.5422 | 3.5422 | 2019-06-09 09:00 | 2.1567 | 3.701 | 6.2553 | 6.2553 | 6.2553 | 6.2553
2021-04-11 21:00 | 2.0805 | 2.5764 | 2.6174 | 2.7933 | 2.723 | 2.8988 | 1.5833 | 2.3983 | 2.8554 | 2.8554 | 3.16 | 3.16 | 2019-06-09 10:00 | 2.1263 | 3.6487 | 6.1669 | 6.1669 | 6.1669 | 6.1669
2021-04-11 22:00 | 1.9005 | 2.3535 | 2.3909 | 2.5516 | 2.4873 | 2.648 | 1.3975 | 2.1169 | 2.5203 | 2.5203 | 2.7893 | 2.7893 | 2019-06-09 11:00 | 2.111 | 3.6225 | 6.1227 | 6.1227 | 6.1227 | 6.1227
2021-04-11 23:00 | 1.7605 | 2.18 | 2.2148 | 2.3636 | 2.3041 | 2.4529 | 1.1717 | 1.7749 | 2.1132 | 2.1132 | 2.3386 | 2.3386 | 2019-06-09 12:00 | 2.111 | 3.6225 | 6.1227 | 6.1227 | 6.1227 | 6.1227
2021-04-12 | 1.5404 | 1.9075 | 1.9379 | 2.0681 | 2.016 | 2.1463 | 0.9431 | 1.4286 | 1.7008 | 1.7008 | 1.8823 | 1.8823 | 2019-06-09 13:00 | 2.0729 | 3.5571 | 6.0121 | 6.0121 | 6.0121 | 6.0121
2021-04-12 01:00 | 1.5004 | 1.858 | 1.8876 | 2.0144 | 1.9637 | 2.0905 | 0.9431 | 1.4286 | 1.7008 | 1.7008 | 1.8823 | 1.8823 | 2019-06-09 14:00 | 2.1186 | 3.6356 | 6.1448 | 6.1448 | 6.1448 | 6.1448
2021-04-12 02:00 | 1.4547 | 1.8014 | 1.8301 | 1.953 | 1.9038 | 2.0268 | 0.82021 | 1.2425 | 1.4792 | 1.4792 | 1.637 | 1.637 | 2019-06-09 15:00 | 2.172 | 3.7271 | 6.2995 | 6.2995 | 6.2995 | 6.2995
2021-04-12 03:00 | 1.4232 | 1.7624 | 1.7905 | 1.9108 | 1.8627 | 1.983 | 0.80306 | 1.2165 | 1.4483 | 1.4483 | 1.6028 | 1.6028 | 2019-06-09 16:00 | 2.233 | 3.8318 | 6.4763 | 6.4763 | 6.4763 | 6.4763
2021-04-12 04:00 | 1.5424 | 1.91 | 1.9404 | 2.0708 | 2.0187 | 2.1491 | 0.84021 | 1.2728 | 1.5153 | 1.5153 | 1.677 | 1.677 | 2019-06-09 17:00 | 2.1949 | 3.7664 | 6.3658 | 6.3658 | 6.3658 | 6.3658
2021-04-12 05:00 | 1.8176 | 2.2508 | 2.2867 | 2.4403 | 2.3789 | 2.5325 | 0.95167 | 1.4416 | 1.7163 | 1.7163 | 1.8994 | 1.8994 | 2019-06-09 18:00 | 2.0805 | 3.5702 | 6.0343 | 6.0343 | 6.0343 | 6.0343
2021-04-12 06:00 | 2.3292 | 2.8843 | 2.9302 | 3.1271 | 3.0484 | 3.2453 | 1.1946 | 1.8096 | 2.1544 | 2.1544 | 2.3843 | 2.3843 | 2019-06-09 19:00 | 1.9434 | 3.3348 | 5.6364 | 5.6364 | 5.6364 | 5.6364
2021-04-12 07:00 | 2.7579 | 3.4152 | 3.4696 | 3.7027 | 3.6094 | 3.8426 | 1.509 | 2.2858 | 2.7213 | 2.7213 | 3.0117 | 3.0117 | 2019-06-09 20:00 | 1.9053 | 3.2694 | 5.5259 | 5.5259 | 5.5259 | 5.5259
2021-04-12 08:00 | 2.8293 | 3.5036 | 3.5594 | 3.7986 | 3.7029 | 3.9421 | 1.5518 | 2.3507 | 2.7987 | 2.7987 | 3.0973 | 3.0973 | 2019-06-09 21:00 | 1.7681 | 3.034 | 5.128 | 5.128 | 5.128 | 5.128
2021-04-12 09:00 | 2.5206 | 3.1214 | 3.1711 | 3.3842 | 3.299 | 3.5121 | 1.5261 | 2.3118 | 2.7523 | 2.7523 | 3.0459 | 3.0459 | 2019-06-09 22:00 | 1.7223 | 2.9556 | 4.9954 | 4.9954 | 4.9954 | 4.9954
2021-04-12 10:00 | 2.4778 | 3.0683 | 3.1172 | 3.3267 | 3.2429 | 3.4523 | 1.5032 | 2.2771 | 2.711 | 2.711 | 3.0003 | 3.0003 | 2019-06-09 23:00 | 1.6309 | 2.7986 | 4.7301 | 4.7301 | 4.7301 | 4.7301
2021-04-12 11:00 | 2.2177 | 2.7463 | 2.79 | 2.9775 | 2.9025 | 3.09 | 1.4689 | 2.2252 | 2.6492 | 2.6492 | 2.9319 | 2.9319 | 2019-06-10 | 1.4785 | 2.5371 | 4.2881 | 4.2881 | 4.2881 | 4.2881
2021-04-12 12:00 | 2.0377 | 2.5233 | 2.5635 | 2.7358 | 2.6669 | 2.8391 | 1.4461 | 2.1905 | 2.608 | 2.608 | 2.8862 | 2.8862 | 2019-06-10 01:00 | 1.4785 | 2.5371 | 4.2881 | 4.2881 | 4.2881 | 4.2881
2021-04-12 13:00 | 1.9834 | 2.4561 | 2.4952 | 2.6629 | 2.5958 | 2.7635 | 1.4318 | 2.1689 | 2.5822 | 2.5822 | 2.8577 | 2.8577 | 2019-06-10 02:00 | 1.448 | 2.4848 | 4.1997 | 4.1997 | 4.1997 | 4.1997
2021-04-12 14:00 | 1.9691 | 2.4384 | 2.4772 | 2.6437 | 2.5771 | 2.7436 | 1.4547 | 2.2035 | 2.6234 | 2.6234 | 2.9033 | 2.9033 | 2019-06-10 03:00 | 1.4023 | 2.4063 | 4.067 | 4.067 | 4.067 | 4.067
2021-04-12 15:00 | 1.9748 | 2.4455 | 2.4844 | 2.6514 | 2.5846 | 2.7515 | 1.4747 | 2.2338 | 2.6595 | 2.6595 | 2.9433 | 2.9433 | 2019-06-10 04:00 | 1.5013 | 2.5763 | 4.3544 | 4.3544 | 4.3544 | 4.3544
2021-04-12 16:00 | 2.1148 | 2.6189 | 2.6606 | 2.8394 | 2.7679 | 2.9466 | 1.5809 | 2.3947 | 2.851 | 2.851 | 3.1552 | 3.1552 | 2019-06-10 05:00 | 1.6995 | 2.9163 | 4.9291 | 4.9291 | 4.9291 | 4.9291
2021-04-12 17:00 | 2.6691 | 3.3053 | 3.358 | 3.5836 | 3.4933 | 3.719 | 1.8262 | 2.7663 | 3.2934 | 3.2934 | 3.6449 | 3.6449 | 2019-06-10 06:00 | 1.7833 | 3.0602 | 5.1722 | 5.1722 | 5.1722 | 5.1722
2021-04-12 18:00 | 3.0379 | 3.762 | 3.8219 | 4.0787 | 3.976 | 4.2328 | 2.0091 | 3.0434 | 3.6233 | 3.6233 | 4.0099 | 4.0099 | 2019-06-10 07:00 | 1.7909 | 3.0733 | 5.1943 | 5.1943 | 5.1943 | 5.1943
2021-04-12 19:00 | 2.9093 | 3.6027 | 3.6601 | 3.906 | 3.8077 | 4.0536 | 2.0234 | 3.065 | 3.6491 | 3.6491 | 4.0384 | 4.0384 | 2019-06-10 08:00 | 1.8976 | 3.2563 | 5.5038 | 5.5038 | 5.5038 | 5.5038
2021-04-12 20:00 | 2.6835 | 3.3231 | 3.3761 | 3.6029 | 3.5122 | 3.739 | 1.9319 | 2.9265 | 3.4841 | 3.4841 | 3.8559 | 3.8559 | 2019-06-10 09:00 | 1.9967 | 3.4264 | 5.7911 | 5.7911 | 5.7911 | 5.7911
2021-04-12 21:00 | 2.4188 | 2.9953 | 3.043 | 3.2475 | 3.1657 | 3.3701 | 1.8691 | 2.8313 | 3.3708 | 3.3708 | 3.7304 | 3.7304 | 2019-06-10 10:00 | 2.0348 | 3.4917 | 5.9016 | 5.9016 | 5.9016 | 5.9016
2021-04-12 22:00 | 2.1442 | 2.6553 | 2.6976 | 2.8788 | 2.8063 | 2.9876 | 1.5947 | 2.4157 | 2.876 | 2.876 | 3.1828 | 3.1828 | 2019-06-10 11:00 | 2.0653 | 3.5441 | 5.99 | 5.99 | 5.99 | 5.99
2021-04-12 23:00 | 1.9176 | 2.3747 | 2.4125 | 2.5746 | 2.5098 | 2.6719 | 1.2861 | 1.9482 | 2.3195 | 2.3195 | 2.567 | 2.567 | 2019-06-10 12:00 | 2.0196 | 3.4656 | 5.8574 | 5.8574 | 5.8574 | 5.8574
2021-04-13 | 1.7035 | 2.1095 | 2.1431 | 2.2871 | 2.2295 | 2.3735 | 1.0608 | 1.607 | 1.9132 | 1.9132 | 2.1173 | 2.1173 | 2019-06-10 13:00 | 1.9281 | 3.3087 | 5.5922 | 5.5922 | 5.5922 | 5.5922
2021-04-13 01:00 | 1.6433 | 2.0349 | 2.0674 | 2.2063 | 2.1507 | 2.2896 | 0.97453 | 1.4762 | 1.7575 | 1.7575 | 1.9451 | 1.9451 | 2019-06-10 14:00 | 2.0196 | 3.4656 | 5.8574 | 5.8574 | 5.8574 | 5.8574
2021-04-13 02:00 | 1.609 | 1.9925 | 2.0242 | 2.1602 | 2.1058 | 2.2418 | 0.92309 | 1.3983 | 1.6648 | 1.6648 | 1.8424 | 1.8424 | 2019-06-10 15:00 | 1.9357 | 3.3217 | 5.6143 | 5.6143 | 5.6143 | 5.6143
2021-04-13 03:00 | 1.6004 | 1.9819 | 2.0134 | 2.1487 | 2.0946 | 2.2299 | 0.90624 | 1.3728 | 1.6344 | 1.6344 | 1.8088 | 1.8088 | 2019-06-10 16:00 | 1.89 | 3.2433 | 5.4817 | 5.4817 | 5.4817 | 5.4817
2021-04-13 04:00 | 1.7062 | 2.1128 | 2.1465 | 2.2907 | 2.233 | 2.3772 | 0.92595 | 1.4026 | 1.6699 | 1.6699 | 1.8481 | 1.8481 | 2019-06-10 17:00 | 2.0043 | 3.4394 | 5.8132 | 5.8132 | 5.8132 | 5.8132
2021-04-13 05:00 | 1.9062 | 2.3605 | 2.3981 | 2.5593 | 2.4948 | 2.6559 | 0.98589 | 1.4934 | 1.778 | 1.778 | 1.9677 | 1.9677 | 2019-06-10 18:00 | 1.9434 | 3.3348 | 5.6364 | 5.6364 | 5.6364 | 5.6364
2021-04-13 06:00 | 2.5235 | 3.125 | 3.1747 | 3.3881 | 3.3027 | 3.516 | 1.3346 | 2.0217 | 2.4069 | 2.4069 | 2.6638 | 2.6638 | 2019-06-10 19:00 | 1.8748 | 3.2171 | 5.4375 | 5.4375 | 5.4375 | 5.4375
2021-04-13 07:00 | 2.9379 | 3.6381 | 3.6961 | 3.9444 | 3.8451 | 4.0934 | 1.5204 | 2.3031 | 2.742 | 2.742 | 3.0345 | 3.0345 | 2019-06-10 20:00 | 1.6995 | 2.9163 | 4.9291 | 4.9291 | 4.9291 | 4.9291
2021-04-13 08:00 | 2.9093 | 3.6027 | 3.6601 | 3.906 | 3.8077 | 4.0536 | 1.5318 | 2.3204 | 2.7626 | 2.7626 | 3.0574 | 3.0574 | 2019-06-10 21:00 | 1.5928 | 2.7332 | 4.6196 | 4.6196 | 4.6196 | 4.6196
2021-04-13 09:00 | 2.715 | 3.3621 | 3.4156 | 3.6451 | 3.5533 | 3.7828 | 1.4461 | 2.1905 | 2.608 | 2.608 | 2.8862 | 2.8862 | 2019-06-10 22:00 | 1.6233 | 2.7855 | 4.708 | 4.708 | 4.708 | 4.708
2021-04-13 10:00 | 2.4549 | 3.04 | 3.0884 | 3.296 | 3.213 | 3.4205 | 1.4975 | 2.2685 | 2.7007 | 2.7007 | 2.9889 | 2.9889 | 2019-06-10 23:00 | 1.5394 | 2.6417 | 4.4649 | 4.4649 | 4.4649 | 4.4649
2021-04-13 11:00 | 2.1748 | 2.6932 | 2.7361 | 2.9199 | 2.8464 | 3.0303 | 1.6061 | 2.433 | 2.8966 | 2.8966 | 3.2057 | 3.2057 | 2019-06-11 | 1.4785 | 2.5371 | 4.2881 | 4.2881 | 4.2881 | 4.2881
2021-04-13 12:00 | 2.1005 | 2.6012 | 2.6426 | 2.8202 | 2.7492 | 2.9267 | 1.4689 | 2.2252 | 2.6492 | 2.6492 | 2.9319 | 2.9319 | 2019-06-11 01:00 | 1.4099 | 2.4194 | 4.0891 | 4.0891 | 4.0891 | 4.0891
2021-04-13 13:00 | 2.0119 | 2.4915 | 2.5312 | 2.7012 | 2.6332 | 2.8033 | 1.4632 | 2.2165 | 2.6389 | 2.6389 | 2.9205 | 2.9205 | 2019-06-11 02:00 | 1.3489 | 2.3148 | 3.9123 | 3.9123 | 3.9123 | 3.9123
2021-04-13 14:00 | 2.0891 | 2.587 | 2.6282 | 2.8048 | 2.7342 | 2.9108 | 1.4661 | 2.2208 | 2.644 | 2.644 | 2.9262 | 2.9262 | 2019-06-11 03:00 | 1.3489 | 2.3148 | 3.9123 | 3.9123 | 3.9123 | 3.9123
2021-04-13 15:00 | 2.0605 | 2.5516 | 2.5923 | 2.7665 | 2.6968 | 2.871 | 1.4089 | 2.1343 | 2.541 | 2.541 | 2.8121 | 2.8121 | 2019-06-11 04:00 | 1.4175 | 2.4324 | 4.1112 | 4.1112 | 4.1112 | 4.1112
2021-04-13 16:00 | 2.1606 | 2.6755 | 2.7181 | 2.9008 | 2.8277 | 3.0103 | 1.5661 | 2.3724 | 2.8244 | 2.8244 | 3.1258 | 3.1258 | 2019-06-11 05:00 | 1.669 | 2.864 | 4.8407 | 4.8407 | 4.8407 | 4.8407
2021-04-13 17:00 | 2.735 | 3.3869 | 3.4408 | 3.672 | 3.5795 | 3.8107 | 1.7532 | 2.6557 | 3.1618 | 3.1618 | 3.4991 | 3.4991 | 2019-06-11 06:00 | 1.9281 | 3.3087 | 5.5922 | 5.5922 | 5.5922 | 5.5922
2021-04-13 18:00 | 2.8693 | 3.5532 | 3.6098 | 3.8523 | 3.7553 | 3.9979 | 1.8662 | 2.8269 | 3.3656 | 3.3656 | 3.7247 | 3.7247 | 2019-06-11 07:00 | 1.9738 | 3.3871 | 5.7248 | 5.7248 | 5.7248 | 5.7248
2021-04-13 19:00 | 2.6189 | 3.2431 | 3.2948 | 3.5162 | 3.4276 | 3.649 | 1.9977 | 3.0261 | 3.6027 | 3.6027 | 3.9871 | 3.9871 | 2019-06-11 08:00 | 2.0882 | 3.5833 | 6.0564 | 6.0564 | 6.0564 | 6.0564
2021-04-13 20:00 | 2.5121 | 3.1108 | 3.1604 | 3.3727 | 3.2878 | 3.5001 | 1.8519 | 2.8053 | 3.3398 | 3.3398 | 3.6962 | 3.6962 | 2019-06-11 09:00 | 2.111 | 3.6225 | 6.1227 | 6.1227 | 6.1227 | 6.1227
2021-04-13 21:00 | 2.1663 | 2.6826 | 2.7253 | 2.9084 | 2.8352 | 3.0183 | 1.729 | 2.6191 | 3.1182 | 3.1182 | 3.4509 | 3.4509 | 2019-06-11 10:00 | 2.1034 | 3.6094 | 6.1006 | 6.1006 | 6.1006 | 6.1006
2021-04-13 22:00 | 1.9176 | 2.3747 | 2.4125 | 2.5746 | 2.5098 | 2.6719 | 1.4048 | 2.128 | 2.5335 | 2.5335 | 2.8038 | 2.8038 | 2019-06-11 11:00 | 2.0653 | 3.5441 | 5.99 | 5.99 | 5.99 | 5.99
2021-04-13 23:00 | 1.7833 | 2.2084 | 2.2435 | 2.3943 | 2.334 | 2.4847 | 1.2003 | 1.8182 | 2.1647 | 2.1647 | 2.3957 | 2.3957 | 2019-06-11 12:00 | 2.0653 | 3.5441 | 5.99 | 5.99 | 5.99 | 5.99
2021-04-14 | 1.535 | 1.9008 | 1.9311 | 2.0608 | 2.0089 | 2.1387 | 0.9661 | 1.4635 | 1.7423 | 1.7423 | 1.9282 | 1.9282 | 2019-06-11 13:00 | 2.0196 | 3.4656 | 5.8574 | 5.8574 | 5.8574 | 5.8574
2021-04-14 01:00 | 1.4289 | 1.7695 | 1.7977 | 1.9185 | 1.8702 | 1.991 | 0.8888 | 1.3464 | 1.6029 | 1.6029 | 1.7739 | 1.7739 | 2019-06-11 14:00 | 1.9662 | 3.374 | 5.7027 | 5.7027 | 5.7027 | 5.7027
2021-04-14 02:00 | 1.426 | 1.7659 | 1.794 | 1.9145 | 1.8663 | 1.9869 | 0.84022 | 1.2728 | 1.5153 | 1.5153 | 1.677 | 1.677 | 2019-06-11 15:00 | 2.0119 | 3.4525 | 5.8353 | 5.8353 | 5.8353 | 5.8353
2021-04-14 03:00 | 1.4261 | 1.766 | 1.7941 | 1.9147 | 1.8664 | 1.987 | 0.82878 | 1.2554 | 1.4947 | 1.4947 | 1.6542 | 1.6542 | 2019-06-11 16:00 | 2.0577 | 3.531 | 5.9679 | 5.9679 | 5.9679 | 5.9679
2021-04-14 04:00 | 1.522 | 1.8848 | 1.9148 | 2.0435 | 1.992 | 2.1207 | 0.85009 | 1.2877 | 1.5331 | 1.5331 | 1.6967 | 1.6967 | 2019-06-11 17:00 | 2.1034 | 3.6094 | 6.1006 | 6.1006 | 6.1006 | 6.1006
2021-04-14 05:00 | 1.7724 | 2.1948 | 2.2298 | 2.3796 | 2.3197 | 2.4695 | 0.94596 | 1.4329 | 1.706 | 1.706 | 1.888 | 1.888 | 2019-06-11 18:00 | 1.9967 | 3.4264 | 5.7911 | 5.7911 | 5.7911 | 5.7911
2021-04-14 06:00 | 2.186 | 2.7071 | 2.7502 | 2.935 | 2.861 | 3.0458 | 1.1591 | 1.7558 | 2.0904 | 2.0904 | 2.3135 | 2.3135 | 2019-06-11 19:00 | 1.9662 | 3.374 | 5.7027 | 5.7027 | 5.7027 | 5.7027
2021-04-14 07:00 | 2.5321 | 3.1356 | 3.1855 | 3.3996 | 3.3139 | 3.528 | 1.4261 | 2.1602 | 2.5719 | 2.5719 | 2.8463 | 2.8463 | 2019-06-11 20:00 | 1.8748 | 3.2171 | 5.4375 | 5.4375 | 5.4375 | 5.4375
2021-04-14 08:00 | 2.4235 | 3.0011 | 3.0489 | 3.2538 | 3.1718 | 3.3767 | 1.5032 | 2.2771 | 2.711 | 2.711 | 3.0003 | 3.0003 | 2019-06-11 21:00 | 1.7681 | 3.034 | 5.128 | 5.128 | 5.128 | 5.128
2021-04-14 09:00 | 2.312 | 2.8631 | 2.9087 | 3.1041 | 3.0259 | 3.2214 | 1.4289 | 2.1646 | 2.577 | 2.577 | 2.852 | 2.852 | 2019-06-11 22:00 | 1.7223 | 2.9556 | 4.9954 | 4.9954 | 4.9954 | 4.9954
2021-04-14 10:00 | 2.192 | 2.7144 | 2.7577 | 2.943 | 2.8688 | 3.0541 | 1.4918 | 2.2598 | 2.6904 | 2.6904 | 2.9775 | 2.9775 | 2019-06-11 23:00 | 1.5623 | 2.6809 | 4.5312 | 4.5312 | 4.5312 | 4.5312
2021-04-14 11:00 | 2.1891 | 2.7109 | 2.7541 | 2.9391 | 2.8651 | 3.0502 | 1.4375 | 2.1776 | 2.5925 | 2.5925 | 2.8691 | 2.8691 | 2019-06-12 | 1.448 | 2.4848 | 4.1997 | 4.1997 | 4.1997 | 4.1997
2021-04-14 12:00 | 2.1548 | 2.6684 | 2.7109 | 2.8931 | 2.8202 | 3.0024 | 1.5147 | 2.2944 | 2.7317 | 2.7317 | 3.0231 | 3.0231 | 2019-06-12 01:00 | 1.387 | 2.3801 | 4.0228 | 4.0228 | 4.0228 | 4.0228
2021-04-14 13:00 | 2.0805 | 2.5764 | 2.6174 | 2.7933 | 2.723 | 2.8988 | 1.5433 | 2.3377 | 2.7832 | 2.7832 | 3.0802 | 3.0802 | 2019-06-12 02:00 | 1.3413 | 2.3017 | 3.8902 | 3.8902 | 3.8902 | 3.8902
2021-04-14 14:00 | 2.0777 | 2.5729 | 2.6139 | 2.7895 | 2.7192 | 2.8949 | 1.4718 | 2.2295 | 2.6543 | 2.6543 | 2.9376 | 2.9376 | 2019-06-12 03:00 | 1.3489 | 2.3148 | 3.9123 | 3.9123 | 3.9123 | 3.9123
2021-04-14 15:00 | 2.072 | 2.5658 | 2.6067 | 2.7818 | 2.7118 | 2.8869 | 1.3804 | 2.091 | 2.4894 | 2.4894 | 2.755 | 2.755 | 2019-06-12 04:00 | 1.4632 | 2.5109 | 4.2439 | 4.2439 | 4.2439 | 4.2439
2021-04-14 16:00 | 2.0739 | 2.5682 | 2.6091 | 2.7845 | 2.7143 | 2.8896 | 1.4489 | 2.1949 | 2.6131 | 2.6131 | 2.8919 | 2.8919 | 2019-06-12 05:00 | 1.7071 | 2.9294 | 4.9512 | 4.9512 | 4.9512 | 4.9512
2021-04-14 17:00 | 2.4883 | 3.0814 | 3.1305 | 3.3408 | 3.2567 | 3.467 | 1.7633 | 2.6711 | 3.1801 | 3.1801 | 3.5194 | 3.5194 | 2019-06-12 06:00 | 1.8519 | 3.1779 | 5.3711 | 5.3711 | 5.3711 | 5.3711
2021-04-14 18:00 | 2.6464 | 3.2771 | 3.3293 | 3.553 | 3.4636 | 3.6873 | 1.8233 | 2.762 | 3.2883 | 3.2883 | 3.6392 | 3.6392 | 2019-06-12 07:00 | 1.9738 | 3.3871 | 5.7248 | 5.7248 | 5.7248 | 5.7248
2021-04-14 19:00 | 2.5978 | 3.217 | 3.2682 | 3.4878 | 3.4 | 3.6196 | 1.9977 | 3.0261 | 3.6027 | 3.6027 | 3.9871 | 3.9871 | 2019-06-12 08:00 | 2.172 | 3.7271 | 6.2995 | 6.2995 | 6.2995 | 6.2995
2021-04-14 20:00 | 2.4492 | 3.0329 | 3.0813 | 3.2883 | 3.2055 | 3.4125 | 1.8519 | 2.8053 | 3.3398 | 3.3398 | 3.6962 | 3.6962 | 2019-06-12 09:00 | 2.0958 | 3.5964 | 6.0785 | 6.0785 | 6.0785 | 6.0785
2021-04-14 21:00 | 2.2063 | 2.7321 | 2.7756 | 2.9621 | 2.8875 | 3.0741 | 1.0145 | 1.5368 | 1.8297 | 1.8297 | 2.0249 | 2.0249 | 2019-06-12 10:00 | 2.0043 | 3.4394 | 5.8132 | 5.8132 | 5.8132 | 5.8132
2021-04-14 22:00 | 1.9005 | 2.3535 | 2.3909 | 2.5516 | 2.4873 | 2.648 | 1.1832 | 1.7923 | 2.1338 | 2.1338 | 2.3615 | 2.3615 | 2019-06-12 11:00 | 2.1034 | 3.6094 | 6.1006 | 6.1006 | 6.1006 | 6.1006
2021-04-14 23:00 | 1.7376 | 2.1517 | 2.186 | 2.3329 | 2.2741 | 2.421 | 1.1117 | 1.684 | 2.0049 | 2.0049 | 2.2189 | 2.2189 | 2019-06-12 12:00 | 2.0653 | 3.5441 | 5.99 | 5.99 | 5.99 | 5.99
2021-04-15 | 1.4958 | 1.8523 | 1.8818 | 2.0083 | 1.9577 | 2.0841 | 1.0317 | 1.5628 | 1.8606 | 1.8606 | 2.0591 | 2.0591 | 2019-06-12 13:00 | 1.9967 | 3.4264 | 5.7911 | 5.7911 | 5.7911 | 5.7911
2021-04-15 01:00 | 1.3889 | 1.72 | 1.7474 | 1.8648 | 1.8178 | 1.9352 | 0.83736 | 1.2684 | 1.5101 | 1.5101 | 1.6713 | 1.6713 | 2019-06-12 14:00 | 2.0348 | 3.4917 | 5.9016 | 5.9016 | 5.9016 | 5.9016
2021-04-15 02:00 | 1.3889 | 1.72 | 1.7474 | 1.8648 | 1.8178 | 1.9352 | 0.84593 | 1.2814 | 1.5256 | 1.5256 | 1.6884 | 1.6884 | 2019-06-12 15:00 | 2.0272 | 3.4787 | 5.8795 | 5.8795 | 5.8795 | 5.8795
2021-04-15 03:00 | 1.3603 | 1.6846 | 1.7114 | 1.8264 | 1.7804 | 1.8954 | 0.8002 | 1.2122 | 1.4431 | 1.4431 | 1.5971 | 1.5971 | 2019-06-12 16:00 | 2.0043 | 3.4394 | 5.8132 | 5.8132 | 5.8132 | 5.8132
2021-04-15 04:00 | 1.3803 | 1.7092 | 1.7365 | 1.8532 | 1.8065 | 1.9232 | 0.87165 | 1.3204 | 1.572 | 1.572 | 1.7397 | 1.7397 | 2019-06-12 17:00 | 2.1491 | 3.6879 | 6.2332 | 6.2332 | 6.2332 | 6.2332
2021-04-15 05:00 | 1.7676 | 2.1888 | 2.2237 | 2.3731 | 2.3133 | 2.4628 | 0.94596 | 1.4329 | 1.706 | 1.706 | 1.888 | 1.888 | 2019-06-12 18:00 | 2.0729 | 3.5571 | 6.0121 | 6.0121 | 6.0121 | 6.0121
2021-04-15 06:00 | 2.1386 | 2.6483 | 2.6905 | 2.8713 | 2.799 | 2.9798 | 1.0631 | 1.6104 | 1.9173 | 1.9173 | 2.1219 | 2.1219 | 2019-06-12 19:00 | 2.0424 | 3.5048 | 5.9237 | 5.9237 | 5.9237 | 5.9237
2021-04-15 07:00 | 2.2949 | 2.8418 | 2.8871 | 3.0811 | 3.0035 | 3.1975 | 1.3832 | 2.0953 | 2.4946 | 2.4946 | 2.7607 | 2.7607 | 2019-06-12 20:00 | 1.8367 | 3.1517 | 5.3269 | 5.3269 | 5.3269 | 5.3269
2021-04-15 08:00 | 2.3006 | 2.8489 | 2.8943 | 3.0888 | 3.011 | 3.2055 | 1.3518 | 2.0477 | 2.4379 | 2.4379 | 2.698 | 2.698 | 2019-06-12 21:00 | 1.73 | 2.9686 | 5.0175 | 5.0175 | 5.0175 | 5.0175
2021-04-15 09:00 | 2.2892 | 2.8348 | 2.8799 | 3.0734 | 2.996 | 3.1895 | 1.4232 | 2.1559 | 2.5667 | 2.5667 | 2.8406 | 2.8406 | 2019-06-12 22:00 | 1.7223 | 2.9556 | 4.9954 | 4.9954 | 4.9954 | 4.9954
2021-04-15 10:00 | 2.1977 | 2.7215 | 2.7649 | 2.9506 | 2.8763 | 3.0621 | 1.4575 | 2.2079 | 2.6286 | 2.6286 | 2.909 | 2.909 | 2019-06-12 23:00 | 1.6004 | 2.7463 | 4.6417 | 4.6417 | 4.6417 | 4.6417
2021-04-15 11:00 | 1.9348 | 2.3959 | 2.4341 | 2.5976 | 2.5322 | 2.6958 | 1.4404 | 2.1819 | 2.5976 | 2.5976 | 2.8748 | 2.8748 | 2019-06-13 | 1.4861 | 2.5501 | 4.3102 | 4.3102 | 4.3102 | 4.3102
2021-04-15 12:00 | 2.1491 | 2.6613 | 2.7037 | 2.8854 | 2.8127 | 2.9944 | 1.4375 | 2.1776 | 2.5925 | 2.5925 | 2.8691 | 2.8691 | 2019-06-13 01:00 | 1.4251 | 2.4455 | 4.1333 | 4.1333 | 4.1333 | 4.1333
2021-04-15 13:00 | 2.0491 | 2.5375 | 2.5779 | 2.7511 | 2.6818 | 2.855 | 1.5204 | 2.3031 | 2.742 | 2.742 | 3.0345 | 3.0345 | 2019-06-13 02:00 | 1.3946 | 2.3932 | 4.0449 | 4.0449 | 4.0449 | 4.0449
2021-04-15 14:00 | 1.9005 | 2.3535 | 2.3909 | 2.5516 | 2.4873 | 2.648 | 1.4832 | 2.2468 | 2.675 | 2.675 | 2.9604 | 2.9604 | 2019-06-13 03:00 | 1.3642 | 2.3409 | 3.9565 | 3.9565 | 3.9565 | 3.9565
2021-04-15 15:00 | 1.9862 | 2.4596 | 2.4988 | 2.6667 | 2.5995 | 2.7674 | 1.4347 | 2.1732 | 2.5873 | 2.5873 | 2.8634 | 2.8634 | 2019-06-13 04:00 | 1.4556 | 2.4978 | 4.2218 | 4.2218 | 4.2218 | 4.2218
2021-04-15 16:00 | 2.052 | 2.541 | 2.5815 | 2.755 | 2.6856 | 2.859 | 1.4347 | 2.1732 | 2.5873 | 2.5873 | 2.8634 | 2.8634 | 2019-06-13 05:00 | 1.608 | 2.7594 | 4.6638 | 4.6638 | 4.6638 | 4.6638
2021-04-15 17:00 | 2.4263 | 3.0046 | 3.0525 | 3.2576 | 3.1756 | 3.3807 | 1.6604 | 2.5152 | 2.9945 | 2.9945 | 3.314 | 3.314 | 2019-06-13 06:00 | 1.8976 | 3.2563 | 5.5038 | 5.5038 | 5.5038 | 5.5038
2021-04-15 18:00 | 2.615 | 3.2382 | 3.2898 | 3.5108 | 3.4224 | 3.6435 | 1.8319 | 2.775 | 3.3038 | 3.3038 | 3.6563 | 3.6563 | 2019-06-13 07:00 | 2.1263 | 3.6487 | 6.1669 | 6.1669 | 6.1669 | 6.1669
2021-04-15 19:00 | 2.5835 | 3.1993 | 3.2502 | 3.4686 | 3.3813 | 3.5997 | 1.8519 | 2.8053 | 3.3398 | 3.3398 | 3.6962 | 3.6962 | 2019-06-13 08:00 | 2.1872 | 3.7533 | 6.3437 | 6.3437 | 6.3437 | 6.3437
2021-04-15 20:00 | 2.307 | 2.8569 | 2.9024 | 3.0974 | 3.0194 | 3.2144 | 1.7062 | 2.5845 | 3.077 | 3.077 | 3.4053 | 3.4053 | 2019-06-13 09:00 | 2.0729 | 3.5571 | 6.0121 | 6.0121 | 6.0121 | 6.0121
2021-04-15 21:00 | 2.1255 | 2.6321 | 2.6741 | 2.8537 | 2.7819 | 2.9616 | 1.6318 | 2.4719 | 2.943 | 2.943 | 3.257 | 3.257 | 2019-06-13 10:00 | 2.0653 | 3.5441 | 5.99 | 5.99 | 5.99 | 5.99
2021-04-15 22:00 | 1.8976 | 2.3499 | 2.3873 | 2.5478 | 2.4836 | 2.644 | 1.5433 | 2.3377 | 2.7832 | 2.7832 | 3.0802 | 3.0802 | 2019-06-13 11:00 | 2.0958 | 3.5964 | 6.0785 | 6.0785 | 6.0785 | 6.0785
2021-04-15 23:00 | 1.729 | 2.1411 | 2.1752 | 2.3214 | 2.2629 | 2.4091 | 1.4289 | 2.1646 | 2.577 | 2.577 | 2.852 | 2.852 | 2019-06-13 12:00 | 2.0805 | 3.5702 | 6.0343 | 6.0343 | 6.0343 | 6.0343
2021-04-16 | 1.4978 | 1.8548 | 1.8843 | 2.0109 | 1.9603 | 2.0869 | 1.1803 | 1.7879 | 2.1286 | 2.1286 | 2.3558 | 2.3558 | 2019-06-13 13:00 | 2.0882 | 3.5833 | 6.0564 | 6.0564 | 6.0564 | 6.0564
2021-04-16 01:00 | 1.4204 | 1.7589 | 1.7869 | 1.907 | 1.859 | 1.979 | 0.92328 | 1.3986 | 1.6651 | 1.6651 | 1.8428 | 1.8428 | 2019-06-13 14:00 | 2.0424 | 3.5048 | 5.9237 | 5.9237 | 5.9237 | 5.9237
2021-04-16 02:00 | 1.4173 | 1.7551 | 1.783 | 1.9028 | 1.8549 | 1.9747 | 0.88308 | 1.3377 | 1.5926 | 1.5926 | 1.7625 | 1.7625 | 2019-06-13 15:00 | 2.0882 | 3.5833 | 6.0564 | 6.0564 | 6.0564 | 6.0564
2021-04-16 03:00 | 1.4175 | 1.7554 | 1.7833 | 1.9031 | 1.8552 | 1.975 | 0.78877 | 1.1948 | 1.4225 | 1.4225 | 1.5743 | 1.5743 | 2019-06-13 16:00 | 2.1034 | 3.6094 | 6.1006 | 6.1006 | 6.1006 | 6.1006
2021-04-16 04:00 | 1.5445 | 1.9126 | 1.9431 | 2.0736 | 2.0214 | 2.152 | 0.87165 | 1.3204 | 1.572 | 1.572 | 1.7397 | 1.7397 | 2019-06-13 17:00 | 2.0805 | 3.5702 | 6.0343 | 6.0343 | 6.0343 | 6.0343
2021-04-16 05:00 | 1.8205 | 2.2544 | 2.2903 | 2.4442 | 2.3826 | 2.5365 | 0.97089 | 1.4707 | 1.751 | 1.751 | 1.9378 | 1.9378 | 2019-06-13 18:00 | 2.0043 | 3.4394 | 5.8132 | 5.8132 | 5.8132 | 5.8132
2021-04-16 06:00 | 2.1891 | 2.7109 | 2.7541 | 2.9391 | 2.8651 | 3.0502 | 1.1803 | 1.7879 | 2.1286 | 2.1286 | 2.3558 | 2.3558 | 2019-06-13 19:00 | 1.9129 | 3.2825 | 5.548 | 5.548 | 5.548 | 5.548
2021-04-16 07:00 | 2.4521 | 3.0365 | 3.0849 | 3.2921 | 3.2092 | 3.4165 | 1.4661 | 2.2208 | 2.644 | 2.644 | 2.9262 | 2.9262 | 2019-06-13 20:00 | 1.8138 | 3.1125 | 5.2606 | 5.2606 | 5.2606 | 5.2606
2021-04-16 08:00 | 2.5492 | 3.1568 | 3.2071 | 3.4226 | 3.3364 | 3.5519 | 1.5175 | 2.2988 | 2.7368 | 2.7368 | 3.0288 | 3.0288 | 2019-06-13 21:00 | 1.7833 | 3.0602 | 5.1722 | 5.1722 | 5.1722 | 5.1722
2021-04-16 09:00 | 2.4235 | 3.0011 | 3.0489 | 3.2538 | 3.1718 | 3.3767 | 1.509 | 2.2858 | 2.7213 | 2.7213 | 3.0117 | 3.0117 | 2019-06-13 22:00 | 1.7909 | 3.0733 | 5.1943 | 5.1943 | 5.1943 | 5.1943
2021-04-16 10:00 | 2.2063 | 2.7321 | 2.7756 | 2.9621 | 2.8875 | 3.0741 | 1.4432 | 2.1862 | 2.6028 | 2.6028 | 2.8805 | 2.8805 | 2019-06-13 23:00 | 1.5166 | 2.6025 | 4.3986 | 4.3986 | 4.3986 | 4.3986
2021-04-16 11:00 | 2.0377 | 2.5233 | 2.5635 | 2.7358 | 2.6669 | 2.8391 | 1.5375 | 2.3291 | 2.7729 | 2.7729 | 3.0688 | 3.0688 | 2019-06-14 | 1.4404 | 2.4717 | 4.1776 | 4.1776 | 4.1776 | 4.1776
2021-04-16 12:00 | 1.8376 | 2.2756 | 2.3118 | 2.4672 | 2.405 | 2.5604 | 1.5147 | 2.2944 | 2.7317 | 2.7317 | 3.0231 | 3.0231 | 2019-06-14 01:00 | 1.3718 | 2.354 | 3.9786 | 3.9786 | 3.9786 | 3.9786
2021-04-16 13:00 | 1.9234 | 2.3818 | 2.4197 | 2.5823 | 2.5173 | 2.6798 | 1.5004 | 2.2728 | 2.7059 | 2.7059 | 2.9946 | 2.9946 | 2019-06-14 02:00 | 1.3718 | 2.354 | 3.9786 | 3.9786 | 3.9786 | 3.9786
2021-04-16 14:00 | 1.9091 | 2.3641 | 2.4017 | 2.5631 | 2.4986 | 2.6599 | 1.4718 | 2.2295 | 2.6543 | 2.6543 | 2.9376 | 2.9376 | 2019-06-14 03:00 | 1.387 | 2.3801 | 4.0228 | 4.0228 | 4.0228 | 4.0228
2021-04-16 15:00 | 1.9719 | 2.4419 | 2.4808 | 2.6475 | 2.5808 | 2.7475 | 1.3718 | 2.078 | 2.4739 | 2.4739 | 2.7379 | 2.7379 | 2019-06-14 04:00 | 1.387 | 2.3801 | 4.0228 | 4.0228 | 4.0228 | 4.0228
2021-04-16 16:00 | 2.0062 | 2.4844 | 2.524 | 2.6936 | 2.6257 | 2.7953 | 1.4775 | 2.2382 | 2.6646 | 2.6646 | 2.949 | 2.949 | 2019-06-14 05:00 | 1.6157 | 2.7725 | 4.6859 | 4.6859 | 4.6859 | 4.6859
2021-04-16 17:00 | 2.312 | 2.8631 | 2.9087 | 3.1041 | 3.0259 | 3.2214 | 1.7147 | 2.5975 | 3.0924 | 3.0924 | 3.4224 | 3.4224 | 2019-06-14 06:00 | 1.8595 | 3.191 | 5.3932 | 5.3932 | 5.3932 | 5.3932
2021-04-16 18:00 | 2.4949 | 3.0896 | 3.1388 | 3.3497 | 3.2653 | 3.4762 | 1.8847 | 2.855 | 3.3991 | 3.3991 | 3.7618 | 3.7618 | 2019-06-14 07:00 | 2.0272 | 3.4787 | 5.8795 | 5.8795 | 5.8795 | 5.8795
2021-04-16 19:00 | 2.4263 | 3.0046 | 3.0525 | 3.2576 | 3.1756 | 3.3807 | 1.9348 | 2.9308 | 3.4893 | 3.4893 | 3.8616 | 3.8616 | 2019-06-14 08:00 | 2.172 | 3.7271 | 6.2995 | 6.2995 | 6.2995 | 6.2995
2021-04-16 20:00 | 2.2463 | 2.7817 | 2.826 | 3.0159 | 2.9399 | 3.1298 | 1.8719 | 2.8356 | 3.3759 | 3.3759 | 3.7361 | 3.7361 | 2019-06-14 09:00 | 2.1567 | 3.701 | 6.2553 | 6.2553 | 6.2553 | 6.2553
2021-04-16 21:00 | 2.1748 | 2.6932 | 2.7361 | 2.9199 | 2.8464 | 3.0303 | 1.769 | 2.6797 | 3.1904 | 3.1904 | 3.5308 | 3.5308 | 2019-06-14 10:00 | 1.9967 | 3.4264 | 5.7911 | 5.7911 | 5.7911 | 5.7911
2021-04-16 22:00 | 1.8891 | 2.3393 | 2.3766 | 2.5362 | 2.4724 | 2.6321 | 1.5633 | 2.368 | 2.8193 | 2.8193 | 3.1201 | 3.1201 | 2019-06-14 11:00 | 2.0348 | 3.4917 | 5.9016 | 5.9016 | 5.9016 | 5.9016
2021-04-16 23:00 | 1.8262 | 2.2614 | 2.2975 | 2.4518 | 2.3901 | 2.5445 | 1.3032 | 1.9741 | 2.3503 | 2.3503 | 2.601 | 2.601 | 2019-06-14 12:00 | 1.9967 | 3.4264 | 5.7911 | 5.7911 | 5.7911 | 5.7911
2021-04-17 | 1.6004 | 1.9819 | 2.0134 | 2.1487 | 2.0946 | 2.2299 | 1.1832 | 1.7923 | 2.1338 | 2.1338 | 2.3615 | 2.3615 | 2019-06-14 13:00 | 2.0424 | 3.5048 | 5.9237 | 5.9237 | 5.9237 | 5.9237
2021-04-17 01:00 | 1.6004 | 1.9819 | 2.0134 | 2.1487 | 2.0946 | 2.2299 | 0.98028 | 1.4849 | 1.7679 | 1.7679 | 1.9565 | 1.9565 | 2019-06-14 14:00 | 2.0119 | 3.4525 | 5.8353 | 5.8353 | 5.8353 | 5.8353
2021-04-17 02:00 | 1.4947 | 1.8509 | 1.8804 | 2.0067 | 1.9562 | 2.0825 | 0.88035 | 1.3336 | 1.5877 | 1.5877 | 1.7571 | 1.7571 | 2019-06-14 15:00 | 2.0043 | 3.4394 | 5.8132 | 5.8132 | 5.8132 | 5.8132
2021-04-17 03:00 | 1.4632 | 1.812 | 1.8408 | 1.9645 | 1.9151 | 2.0387 | 0.86022 | 1.3031 | 1.5514 | 1.5514 | 1.7169 | 1.7169 | 2019-06-14 16:00 | 2.0348 | 3.4917 | 5.9016 | 5.9016 | 5.9016 | 5.9016
2021-04-17 04:00 | 1.5032 | 1.8615 | 1.8912 | 2.0183 | 1.9674 | 2.0945 | 0.88308 | 1.3377 | 1.5926 | 1.5926 | 1.7625 | 1.7625 | 2019-06-14 17:00 | 2.1339 | 3.6618 | 6.189 | 6.189 | 6.189 | 6.189
2021-04-17 05:00 | 1.6261 | 2.0137 | 2.0458 | 2.1832 | 2.1283 | 2.2657 | 0.91738 | 1.3896 | 1.6545 | 1.6545 | 1.831 | 1.831 | 2019-06-14 18:00 | 1.9738 | 3.3871 | 5.7248 | 5.7248 | 5.7248 | 5.7248
2021-04-17 06:00 | 1.7519 | 2.1694 | 2.204 | 2.3521 | 2.2928 | 2.4409 | 1.006 | 1.5239 | 1.8142 | 1.8142 | 2.0078 | 2.0078 | 2019-06-14 19:00 | 1.951 | 3.3479 | 5.6585 | 5.6585 | 5.6585 | 5.6585
2021-04-17 07:00 | 1.8776 | 2.3251 | 2.3622 | 2.5209 | 2.4574 | 2.6161 | 1.3289 | 2.013 | 2.3966 | 2.3966 | 2.6524 | 2.6524 | 2019-06-14 20:00 | 1.8519 | 3.1779 | 5.3711 | 5.3711 | 5.3711 | 5.3711
2021-04-17 08:00 | 1.9434 | 2.4065 | 2.4449 | 2.6091 | 2.5434 | 2.7077 | 1.4118 | 2.1386 | 2.5461 | 2.5461 | 2.8178 | 2.8178 | 2019-06-14 21:00 | 1.7376 | 2.9817 | 5.0396 | 5.0396 | 5.0396 | 5.0396
2021-04-17 09:00 | 1.8805 | 2.3287 | 2.3658 | 2.5247 | 2.4611 | 2.6201 | 1.4375 | 2.1776 | 2.5925 | 2.5925 | 2.8691 | 2.8691 | 2019-06-14 22:00 | 1.7376 | 2.9817 | 5.0396 | 5.0396 | 5.0396 | 5.0396
2021-04-17 10:00 | 1.8205 | 2.2544 | 2.2903 | 2.4442 | 2.3826 | 2.5365 | 1.6661 | 2.5239 | 3.0048 | 3.0048 | 3.3254 | 3.3254 | 2019-06-14 23:00 | 1.6004 | 2.7463 | 4.6417 | 4.6417 | 4.6417 | 4.6417
2021-04-17 11:00 | 1.7519 | 2.1694 | 2.204 | 2.3521 | 2.2928 | 2.4409 | 1.6747 | 2.5369 | 3.0203 | 3.0203 | 3.3426 | 3.3426 | 2019-06-15 | 1.4709 | 2.524 | 4.266 | 4.266 | 4.266 | 4.266
2021-04-17 12:00 | 1.6461 | 2.0385 | 2.0709 | 2.2101 | 2.1544 | 2.2936 | 1.5947 | 2.4157 | 2.876 | 2.876 | 3.1828 | 3.1828 | 2019-06-15 01:00 | 1.4327 | 2.4586 | 4.1555 | 4.1555 | 4.1555 | 4.1555
2021-04-17 13:00 | 1.6861 | 2.088 | 2.1213 | 2.2638 | 2.2068 | 2.3493 | 1.669 | 2.5282 | 3.01 | 3.01 | 3.3311 | 3.3311 | 2019-06-15 02:00 | 1.3642 | 2.3409 | 3.9565 | 3.9565 | 3.9565 | 3.9565
2021-04-17 14:00 | 1.6176 | 2.0031 | 2.035 | 2.1717 | 2.117 | 2.2538 | 1.6061 | 2.433 | 2.8966 | 2.8966 | 3.2057 | 3.2057 | 2019-06-15 03:00 | 1.3794 | 2.3671 | 4.0007 | 4.0007 | 4.0007 | 4.0007
2021-04-17 15:00 | 1.6804 | 2.0809 | 2.1141 | 2.2561 | 2.1993 | 2.3414 | 1.6004 | 2.4243 | 2.8863 | 2.8863 | 3.1942 | 3.1942 | 2019-06-15 04:00 | 1.4709 | 2.524 | 4.266 | 4.266 | 4.266 | 4.266
2021-04-17 16:00 | 1.7941 | 2.2217 | 2.2571 | 2.4088 | 2.3481 | 2.4998 | 1.609 | 2.4373 | 2.9017 | 2.9017 | 3.2114 | 3.2114 | 2019-06-15 05:00 | 1.5775 | 2.7071 | 4.5754 | 4.5754 | 4.5754 | 4.5754
2021-04-17 17:00 | 2.1548 | 2.6684 | 2.7109 | 2.8931 | 2.8202 | 3.0024 | 1.7176 | 2.6018 | 3.0976 | 3.0976 | 3.4281 | 3.4281 | 2019-06-15 06:00 | 1.73 | 2.9686 | 5.0175 | 5.0175 | 5.0175 | 5.0175
2021-04-17 18:00 | 2.1806 | 2.7003 | 2.7433 | 2.9276 | 2.8539 | 3.0382 | 1.9033 | 2.8832 | 3.4326 | 3.4326 | 3.7989 | 3.7989 | 2019-06-15 07:00 | 1.8519 | 3.1779 | 5.3711 | 5.3711 | 5.3711 | 5.3711
2021-04-17 19:00 | 2.1406 | 2.6507 | 2.693 | 2.8739 | 2.8015 | 2.9825 | 1.809 | 2.7403 | 3.2625 | 3.2625 | 3.6106 | 3.6106 | 2019-06-15 08:00 | 2.0501 | 3.5179 | 5.9458 | 5.9458 | 5.9458 | 5.9458
2021-04-17 20:00 | 2.0062 | 2.4844 | 2.524 | 2.6936 | 2.6257 | 2.7953 | 1.6861 | 2.5542 | 3.0409 | 3.0409 | 3.3654 | 3.3654 | 2019-06-15 09:00 | 2.0882 | 3.5833 | 6.0564 | 6.0564 | 6.0564 | 6.0564
2021-04-17 21:00 | 1.8462 | 2.2862 | 2.3226 | 2.4787 | 2.4163 | 2.5723 | 1.6861 | 2.5542 | 3.0409 | 3.0409 | 3.3654 | 3.3654 | 2019-06-15 10:00 | 2.1491 | 3.6879 | 6.2332 | 6.2332 | 6.2332 | 6.2332
2021-04-17 22:00 | 1.9691 | 2.4384 | 2.4772 | 2.6437 | 2.5771 | 2.7436 | 1.529 | 2.3161 | 2.7574 | 2.7574 | 3.0516 | 3.0516 | 2019-06-15 11:00 | 2.0729 | 3.5571 | 6.0121 | 6.0121 | 6.0121 | 6.0121
2021-04-17 23:00 | 1.7786 | 2.2025 | 2.2375 | 2.3879 | 2.3277 | 2.4781 | 1.2725 | 1.9276 | 2.2949 | 2.2949 | 2.5398 | 2.5398 | 2019-06-15 12:00 | 2.0653 | 3.5441 | 5.99 | 5.99 | 5.99 | 5.99
2021-04-18 | 1.5633 | 1.9358 | 1.9667 | 2.0988 | 2.046 | 2.1781 | 1.1192 | 1.6954 | 2.0185 | 2.0185 | 2.2339 | 2.2339 | 2019-06-15 13:00 | 2.0424 | 3.5048 | 5.9237 | 5.9237 | 5.9237 | 5.9237
2021-04-18 01:00 | 1.4604 | 1.8084 | 1.8372 | 1.9607 | 1.9113 | 2.0348 | 0.99454 | 1.5065 | 1.7936 | 1.7936 | 1.985 | 1.985 | 2019-06-15 14:00 | 2.0729 | 3.5571 | 6.0121 | 6.0121 | 6.0121 | 6.0121
2021-04-18 02:00 | 1.5061 | 1.8651 | 1.8948 | 2.0221 | 1.9712 | 2.0985 | 0.88308 | 1.3377 | 1.5926 | 1.5926 | 1.7625 | 1.7625 | 2019-06-15 15:00 | 2.1034 | 3.6094 | 6.1006 | 6.1006 | 6.1006 | 6.1006
2021-04-18 03:00 | 1.4747 | 1.8261 | 1.8552 | 1.9799 | 1.93 | 2.0547 | 0.82592 | 1.2511 | 1.4895 | 1.4895 | 1.6485 | 1.6485 | 2019-06-15 16:00 | 2.111 | 3.6225 | 6.1227 | 6.1227 | 6.1227 | 6.1227
2021-04-18 04:00 | 1.4547 | 1.8014 | 1.8301 | 1.953 | 1.9038 | 2.0268 | 0.86022 | 1.3031 | 1.5514 | 1.5514 | 1.7169 | 1.7169 | 2019-06-15 17:00 | 2.0805 | 3.5702 | 6.0343 | 6.0343 | 6.0343 | 6.0343
2021-04-18 05:00 | 1.5732 | 1.9481 | 1.9792 | 2.1122 | 2.059 | 2.192 | 0.88022 | 1.3334 | 1.5874 | 1.5874 | 1.7568 | 1.7568 | 2019-06-15 18:00 | 2.0196 | 3.4656 | 5.8574 | 5.8574 | 5.8574 | 5.8574
2021-04-18 06:00 | 1.6461 | 2.0385 | 2.0709 | 2.2101 | 2.1544 | 2.2936 | 0.92309 | 1.3983 | 1.6648 | 1.6648 | 1.8424 | 1.8424 | 2019-06-15 19:00 | 1.9891 | 3.4133 | 5.769 | 5.769 | 5.769 | 5.769
2021-04-18 07:00 | 1.7662 | 2.1871 | 2.222 | 2.3713 | 2.3115 | 2.4608 | 1.1317 | 1.7143 | 2.041 | 2.041 | 2.2588 | 2.2588 | 2019-06-15 20:00 | 1.8824 | 3.2302 | 5.4596 | 5.4596 | 5.4596 | 5.4596
2021-04-18 08:00 | 1.9176 | 2.3747 | 2.4125 | 2.5746 | 2.5098 | 2.6719 | 1.3661 | 2.0693 | 2.4636 | 2.4636 | 2.7265 | 2.7265 | 2019-06-15 21:00 | 1.7757 | 3.0471 | 5.1501 | 5.1501 | 5.1501 | 5.1501
2021-04-18 09:00 | 2.0363 | 2.5217 | 2.5618 | 2.734 | 2.6651 | 2.8373 | 1.585 | 2.401 | 2.8586 | 2.8586 | 3.1636 | 3.1636 | 2019-06-15 22:00 | 1.7147 | 2.9425 | 4.9733 | 4.9733 | 4.9733 | 4.9733
2021-04-18 10:00 | 2.1091 | 2.6118 | 2.6534 | 2.8317 | 2.7604 | 2.9387 | 1.6747 | 2.5369 | 3.0203 | 3.0203 | 3.3426 | 3.3426 | 2019-06-15 23:00 | 1.6766 | 2.8771 | 4.8628 | 4.8628 | 4.8628 | 4.8628
2021-04-18 11:00 | 1.7926 | 2.2199 | 2.2552 | 2.4068 | 2.3461 | 2.4977 | 1.6376 | 2.4806 | 2.9533 | 2.9533 | 3.2684 | 3.2684 | 2019-06-16 | 1.4937 | 2.5632 | 4.3323 | 4.3323 | 4.3323 | 4.3323
2021-04-18 12:00 | 1.5747 | 1.95 | 1.9811 | 2.1142 | 2.0609 | 2.194 | 1.5804 | 2.394 | 2.8502 | 2.8502 | 3.1543 | 3.1543 | 2019-06-16 01:00 | 1.448 | 2.4848 | 4.1997 | 4.1997 | 4.1997 | 4.1997
2021-04-18 13:00 | 1.4861 | 1.8403 | 1.8696 | 1.9952 | 1.945 | 2.0706 | 1.6033 | 2.4286 | 2.8914 | 2.8914 | 3.2 | 3.2 | 2019-06-16 02:00 | 1.4023 | 2.4063 | 4.067 | 4.067 | 4.067 | 4.067
2021-04-18 14:00 | 1.4975 | 1.8544 | 1.884 | 2.0106 | 1.9599 | 2.0865 | 1.5204 | 2.3031 | 2.742 | 2.742 | 3.0345 | 3.0345 | 2019-06-16 03:00 | 1.4023 | 2.4063 | 4.067 | 4.067 | 4.067 | 4.067
2021-04-18 15:00 | 1.5917 | 1.9711 | 2.0025 | 2.1371 | 2.0832 | 2.2178 | 1.5147 | 2.2944 | 2.7317 | 2.7317 | 3.0231 | 3.0231 | 2019-06-16 04:00 | 1.5166 | 2.6025 | 4.3986 | 4.3986 | 4.3986 | 4.3986
2021-04-18 16:00 | 1.8809 | 2.3292 | 2.3663 | 2.5253 | 2.4617 | 2.6206 | 1.6061 | 2.433 | 2.8966 | 2.8966 | 3.2057 | 3.2057 | 2019-06-16 05:00 | 1.5699 | 2.694 | 4.5533 | 4.5533 | 4.5533 | 4.5533
2021-04-18 17:00 | 2.4006 | 2.9728 | 3.0201 | 3.2231 | 3.1419 | 3.3448 | 1.7862 | 2.7057 | 3.2213 | 3.2213 | 3.565 | 3.565 | 2019-06-16 06:00 | 1.6995 | 2.9163 | 4.9291 | 4.9291 | 4.9291 | 4.9291
2021-04-18 18:00 | 2.4949 | 3.0896 | 3.1388 | 3.3497 | 3.2653 | 3.4762 | 1.9491 | 2.9525 | 3.5151 | 3.5151 | 3.8901 | 3.8901 | 2019-06-16 07:00 | 1.8214 | 3.1256 | 5.2827 | 5.2827 | 5.2827 | 5.2827
2021-04-18 19:00 | 2.4035 | 2.9763 | 3.0237 | 3.2269 | 3.1456 | 3.3488 | 1.9348 | 2.9308 | 3.4893 | 3.4893 | 3.8616 | 3.8616 | 2019-06-16 08:00 | 2.0577 | 3.531 | 5.9679 | 5.9679 | 5.9679 | 5.9679
2021-04-18 20:00 | 2.2463 | 2.7817 | 2.826 | 3.0159 | 2.9399 | 3.1298 | 1.8633 | 2.8226 | 3.3604 | 3.3604 | 3.719 | 3.719 | 2019-06-16 09:00 | 2.0501 | 3.5179 | 5.9458 | 5.9458 | 5.9458 | 5.9458
2021-04-18 21:00 | 2.132 | 2.6401 | 2.6822 | 2.8624 | 2.7903 | 2.9705 | 1.6727 | 2.5339 | 3.0167 | 3.0167 | 3.3386 | 3.3386 | 2019-06-16 10:00 | 2.0805 | 3.5702 | 6.0343 | 6.0343 | 6.0343 | 6.0343
2021-04-18 22:00 | 2.0377 | 2.5233 | 2.5635 | 2.7358 | 2.6669 | 2.8391 | 1.3916 | 2.108 | 2.5097 | 2.5097 | 2.7775 | 2.7775 | 2019-06-16 11:00 | 2.1491 | 3.6879 | 6.2332 | 6.2332 | 6.2332 | 6.2332
2021-04-18 23:00 | 1.8634 | 2.3075 | 2.3443 | 2.5018 | 2.4388 | 2.5963 | 1.2005 | 1.8185 | 2.165 | 2.165 | 2.3961 | 2.3961 | 2019-06-16 12:00 | 2.0882 | 3.5833 | 6.0564 | 6.0564 | 6.0564 | 6.0564
2021-04-19 | 1.6176 | 2.0031 | 2.035 | 2.1717 | 2.117 | 2.2538 | 1.0145 | 1.5368 | 1.8297 | 1.8297 | 2.0249 | 2.0249 | 2019-06-16 13:00 | 2.0653 | 3.5441 | 5.99 | 5.99 | 5.99 | 5.99
2021-04-19 01:00 | 1.5718 | 1.9465 | 1.9775 | 2.1103 | 2.0572 | 2.1901 | 0.88317 | 1.3378 | 1.5928 | 1.5928 | 1.7627 | 1.7627 | 2019-06-16 14:00 | 2.0805 | 3.5702 | 6.0343 | 6.0343 | 6.0343 | 6.0343
2021-04-19 02:00 | 1.4975 | 1.8544 | 1.884 | 2.0106 | 1.9599 | 2.0865 | 0.85736 | 1.2987 | 1.5462 | 1.5462 | 1.7112 | 1.7112 | 2019-06-16 15:00 | 2.172 | 3.7271 | 6.2995 | 6.2995 | 6.2995 | 6.2995
2021-04-19 03:00 | 1.4975 | 1.8544 | 1.884 | 2.0106 | 1.9599 | 2.0865 | 0.82319 | 1.247 | 1.4846 | 1.4846 | 1.643 | 1.643 | 2019-06-16 16:00 | 2.1186 | 3.6356 | 6.1448 | 6.1448 | 6.1448 | 6.1448
2021-04-19 04:00 | 1.5831 | 1.9604 | 1.9916 | 2.1255 | 2.0719 | 2.2058 | 0.88291 | 1.3374 | 1.5923 | 1.5923 | 1.7622 | 1.7622 | 2019-06-16 17:00 | 2.1491 | 3.6879 | 6.2332 | 6.2332 | 6.2332 | 6.2332
2021-04-19 05:00 | 1.9719 | 2.4419 | 2.4808 | 2.6475 | 2.5808 | 2.7475 | 0.9974 | 1.5109 | 1.7988 | 1.7988 | 1.9907 | 1.9907 | 2019-06-16 18:00 | 1.9357 | 3.3217 | 5.6143 | 5.6143 | 5.6143 | 5.6143
2021-04-19 06:00 | 2.7236 | 3.3727 | 3.4264 | 3.6566 | 3.5646 | 3.7948 | 1.1874 | 1.7987 | 2.1415 | 2.1415 | 2.37 | 2.37 | 2019-06-16 19:00 | 1.89 | 3.2433 | 5.4817 | 5.4817 | 5.4817 | 5.4817
2021-04-19 07:00 | 3.0351 | 3.7584 | 3.8183 | 4.0749 | 3.9723 | 4.2288 | 1.5375 | 2.3291 | 2.7729 | 2.7729 | 3.0688 | 3.0688 | 2019-06-16 20:00 | 1.829 | 3.1386 | 5.3048 | 5.3048 | 5.3048 | 5.3048
2021-04-19 08:00 | 3.0322 | 3.7549 | 3.8147 | 4.071 | 3.9685 | 4.2248 | 1.5261 | 2.3118 | 2.7523 | 2.7523 | 3.0459 | 3.0459 | 2019-06-16 21:00 | 1.73 | 2.9686 | 5.0175 | 5.0175 | 5.0175 | 5.0175
2021-04-19 09:00 | 2.7207 | 3.3692 | 3.4228 | 3.6528 | 3.5608 | 3.7908 | 1.4718 | 2.2295 | 2.6543 | 2.6543 | 2.9376 | 2.9376 | 2019-06-16 22:00 | 1.6614 | 2.8509 | 4.8186 | 4.8186 | 4.8186 | 4.8186
2021-04-19 10:00 | 2.4178 | 2.994 | 3.0417 | 3.2461 | 3.1643 | 3.3687 | 1.4604 | 2.2122 | 2.6337 | 2.6337 | 2.9148 | 2.9148 | 2019-06-16 23:00 | 1.5318 | 2.6286 | 4.4428 | 4.4428 | 4.4428 | 4.4428
2021-04-19 11:00 | 2.2434 | 2.7781 | 2.8224 | 3.012 | 2.9362 | 3.1258 | 1.4318 | 2.1689 | 2.5822 | 2.5822 | 2.8577 | 2.8577 | 2019-06-17 | 1.4404 | 2.4717 | 4.1776 | 4.1776 | 4.1776 | 4.1776
2021-04-19 12:00 | 2.1377 | 2.6472 | 2.6894 | 2.8701 | 2.7978 | 2.9785 | 1.4146 | 2.1429 | 2.5513 | 2.5513 | 2.8235 | 2.8235 | 2019-06-17 01:00 | 1.3718 | 2.354 | 3.9786 | 3.9786 | 3.9786 | 3.9786
2021-04-19 13:00 | 2.112 | 2.6153 | 2.657 | 2.8355 | 2.7641 | 2.9426 | 1.3975 | 2.1169 | 2.5203 | 2.5203 | 2.7893 | 2.7893 | 2019-06-17 02:00 | 1.3337 | 2.2886 | 3.8681 | 3.8681 | 3.8681 | 3.8681
2021-04-19 14:00 | 2.0348 | 2.5198 | 2.5599 | 2.7319 | 2.6631 | 2.8351 | 1.3289 | 2.013 | 2.3966 | 2.3966 | 2.6524 | 2.6524 | 2019-06-17 03:00 | 1.3413 | 2.3017 | 3.8902 | 3.8902 | 3.8902 | 3.8902
2021-04-19 15:00 | 2.112 | 2.6153 | 2.657 | 2.8355 | 2.7641 | 2.9426 | 1.3718 | 2.078 | 2.4739 | 2.4739 | 2.7379 | 2.7379 | 2019-06-17 04:00 | 1.4861 | 2.5501 | 4.3102 | 4.3102 | 4.3102 | 4.3102
2021-04-19 16:00 | 2.2271 | 2.7579 | 2.8018 | 2.9901 | 2.9148 | 3.1031 | 1.4861 | 2.2511 | 2.6801 | 2.6801 | 2.9661 | 2.9661 | 2019-06-17 05:00 | 1.6157 | 2.7725 | 4.6859 | 4.6859 | 4.6859 | 4.6859
2021-04-19 17:00 | 2.875 | 3.5603 | 3.617 | 3.86 | 3.7628 | 4.0058 | 1.7833 | 2.7014 | 3.2161 | 3.2161 | 3.5593 | 3.5593 | 2019-06-17 06:00 | 1.7986 | 3.0863 | 5.2164 | 5.2164 | 5.2164 | 5.2164
2021-04-19 18:00 | 3.1151 | 3.8575 | 3.919 | 4.1823 | 4.077 | 4.3403 | 1.9176 | 2.9048 | 3.4584 | 3.4584 | 3.8274 | 3.8274 | 2019-06-17 07:00 | 2.0196 | 3.4656 | 5.8574 | 5.8574 | 5.8574 | 5.8574
2021-04-19 19:00 | 2.9795 | 3.6896 | 3.7484 | 4.0003 | 3.8995 | 4.1514 | 1.9805 | 3.0001 | 3.5718 | 3.5718 | 3.9529 | 3.9529 | 2019-06-17 08:00 | 2.1567 | 3.701 | 6.2553 | 6.2553 | 6.2553 | 6.2553
2021-04-19 20:00 | 2.6893 | 3.3302 | 3.3833 | 3.6106 | 3.5197 | 3.747 | 1.9291 | 2.9222 | 3.479 | 3.479 | 3.8502 | 3.8502 | 2019-06-17 09:00 | 2.0805 | 3.5702 | 6.0343 | 6.0343 | 6.0343 | 6.0343
2021-04-19 21:00 | 2.5521 | 3.1604 | 3.2107 | 3.4264 | 3.3401 | 3.5559 | 1.6919 | 2.5628 | 3.0512 | 3.0512 | 3.3768 | 3.3768 | 2019-06-17 10:00 | 2.0196 | 3.4656 | 5.8574 | 5.8574 | 5.8574 | 5.8574
2021-04-19 22:00 | 2.0951 | 2.5945 | 2.6358 | 2.8129 | 2.7421 | 2.9192 | 1.5318 | 2.3204 | 2.7626 | 2.7626 | 3.0574 | 3.0574 | 2019-06-17 11:00 | 1.9891 | 3.4133 | 5.769 | 5.769 | 5.769 | 5.769
2021-04-19 23:00 | 1.83 | 2.2662 | 2.3023 | 2.457 | 2.3951 | 2.5498 | 1.2411 | 1.88 | 2.2383 | 2.2383 | 2.4771 | 2.4771 | 2019-06-17 12:00 | 1.9815 | 3.4002 | 5.7469 | 5.7469 | 5.7469 | 5.7469
2021-04-20 | 1.5747 | 1.95 | 1.9811 | 2.1142 | 2.0609 | 2.194 | 1.0289 | 1.5586 | 1.8556 | 1.8556 | 2.0536 | 2.0536 | 2019-06-17 13:00 | 2.0577 | 3.531 | 5.9679 | 5.9679 | 5.9679 | 5.9679
2021-04-20 01:00 | 1.5347 | 1.9005 | 1.9307 | 2.0605 | 2.0086 | 2.1383 | 0.96025 | 1.4546 | 1.7318 | 1.7318 | 1.9165 | 1.9165 | 2019-06-17 14:00 | 2.0958 | 3.5964 | 6.0785 | 6.0785 | 6.0785 | 6.0785
2021-04-20 02:00 | 1.4975 | 1.8544 | 1.884 | 2.0106 | 1.9599 | 2.0865 | 0.8345 | 1.2641 | 1.505 | 1.505 | 1.6656 | 1.6656 | 2019-06-17 15:00 | 2.0043 | 3.4394 | 5.8132 | 5.8132 | 5.8132 | 5.8132
2021-04-20 03:00 | 1.489 | 1.8438 | 1.8732 | 1.9991 | 1.9487 | 2.0746 | 0.81492 | 1.2344 | 1.4697 | 1.4697 | 1.6265 | 1.6265 | 2019-06-17 16:00 | 1.9891 | 3.4133 | 5.769 | 5.769 | 5.769 | 5.769
2021-04-20 04:00 | 1.5547 | 1.9252 | 1.9559 | 2.0873 | 2.0347 | 2.1662 | 0.86022 | 1.3031 | 1.5514 | 1.5514 | 1.7169 | 1.7169 | 2019-06-17 17:00 | 2.1491 | 3.6879 | 6.2332 | 6.2332 | 6.2332 | 6.2332
2021-04-20 05:00 | 1.8605 | 2.3039 | 2.3406 | 2.4979 | 2.435 | 2.5922 | 0.94596 | 1.4329 | 1.706 | 1.706 | 1.888 | 1.888 | 2019-06-17 18:00 | 2.0653 | 3.5441 | 5.99 | 5.99 | 5.99 | 5.99
2021-04-20 06:00 | 2.6064 | 3.2276 | 3.279 | 3.4993 | 3.4112 | 3.6315 | 1.1174 | 1.6927 | 2.0152 | 2.0152 | 2.2303 | 2.2303 | 2019-06-17 19:00 | 2.0272 | 3.4787 | 5.8795 | 5.8795 | 5.8795 | 5.8795
2021-04-20 07:00 | 2.7921 | 3.4576 | 3.5127 | 3.7487 | 3.6543 | 3.8903 | 1.5204 | 2.3031 | 2.742 | 2.742 | 3.0345 | 3.0345 | 2019-06-17 20:00 | 1.9205 | 3.2956 | 5.5701 | 5.5701 | 5.5701 | 5.5701
2021-04-20 08:00 | 2.8379 | 3.5143 | 3.5702 | 3.8101 | 3.7142 | 3.9541 | 1.4718 | 2.2295 | 2.6543 | 2.6543 | 2.9376 | 2.9376 | 2019-06-17 21:00 | 1.7681 | 3.034 | 5.128 | 5.128 | 5.128 | 5.128
2021-04-20 09:00 | 2.7064 | 3.3515 | 3.4048 | 3.6336 | 3.5421 | 3.7709 | 1.4861 | 2.2511 | 2.6801 | 2.6801 | 2.9661 | 2.9661 | 2019-06-17 22:00 | 1.7528 | 3.0079 | 5.0838 | 5.0838 | 5.0838 | 5.0838
2021-04-20 10:00 | 2.6607 | 3.2948 | 3.3473 | 3.5722 | 3.4823 | 3.7072 | 1.4375 | 2.1776 | 2.5925 | 2.5925 | 2.8691 | 2.8691 | 2019-06-17 23:00 | 1.5852 | 2.7202 | 4.5975 | 4.5975 | 4.5975 | 4.5975
2021-04-20 11:00 | 2.3235 | 2.8772 | 2.9231 | 3.1195 | 3.0409 | 3.2373 | 1.4432 | 2.1862 | 2.6028 | 2.6028 | 2.8805 | 2.8805 | 2019-06-18 | 1.5013 | 2.5763 | 4.3544 | 4.3544 | 4.3544 | 4.3544
2021-04-20 12:00 | 2.4692 | 3.0577 | 3.1064 | 3.3152 | 3.2317 | 3.4404 | 1.4804 | 2.2425 | 2.6698 | 2.6698 | 2.9547 | 2.9547 | 2019-06-18 01:00 | 1.3946 | 2.3932 | 4.0449 | 4.0449 | 4.0449 | 4.0449
2021-04-20 13:00 | 2.0891 | 2.587 | 2.6282 | 2.8048 | 2.7342 | 2.9108 | 1.4347 | 2.1732 | 2.5873 | 2.5873 | 2.8634 | 2.8634 | 2019-06-18 02:00 | 1.3718 | 2.354 | 3.9786 | 3.9786 | 3.9786 | 3.9786
2021-04-20 14:00 | 2.0834 | 2.58 | 2.621 | 2.7972 | 2.7267 | 2.9028 | 1.3375 | 2.026 | 2.4121 | 2.4121 | 2.6695 | 2.6695 | 2019-06-18 03:00 | 1.4023 | 2.4063 | 4.067 | 4.067 | 4.067 | 4.067
2021-04-20 15:00 | 2.1834 | 2.7038 | 2.7469 | 2.9315 | 2.8576 | 3.0422 | 1.4375 | 2.1776 | 2.5925 | 2.5925 | 2.8691 | 2.8691 | 2019-06-18 04:00 | 1.4632 | 2.5109 | 4.2439 | 4.2439 | 4.2439 | 4.2439
2021-04-20 16:00 | 2.2806 | 2.8241 | 2.8691 | 3.0619 | 2.9848 | 3.1776 | 1.5032 | 2.2771 | 2.711 | 2.711 | 3.0003 | 3.0003 | 2019-06-18 05:00 | 1.6995 | 2.9163 | 4.9291 | 4.9291 | 4.9291 | 4.9291
2021-04-20 17:00 | 2.8407 | 3.5178 | 3.5738 | 3.814 | 3.7179 | 3.958 | 1.7862 | 2.7057 | 3.2213 | 3.2213 | 3.565 | 3.565 | 2019-06-18 06:00 | 1.9281 | 3.3087 | 5.5922 | 5.5922 | 5.5922 | 5.5922
2021-04-20 18:00 | 3.0008 | 3.716 | 3.7752 | 4.0288 | 3.9274 | 4.181 | 1.9205 | 2.9092 | 3.4635 | 3.4635 | 3.8331 | 3.8331 | 2019-06-18 07:00 | 2.111 | 3.6225 | 6.1227 | 6.1227 | 6.1227 | 6.1227
2021-04-20 19:00 | 2.915 | 3.6098 | 3.6673 | 3.9137 | 3.8152 | 4.0616 | 1.9948 | 3.0217 | 3.5975 | 3.5975 | 3.9814 | 3.9814 | 2019-06-18 08:00 | 2.0882 | 3.5833 | 6.0564 | 6.0564 | 6.0564 | 6.0564
2021-04-20 20:00 | 2.615 | 3.2382 | 3.2898 | 3.5108 | 3.4224 | 3.6435 | 1.8033 | 2.7317 | 3.2522 | 3.2522 | 3.5992 | 3.5992 | 2019-06-18 09:00 | 2.0729 | 3.5571 | 6.0121 | 6.0121 | 6.0121 | 6.0121
2021-04-20 21:00 | 2.438 | 3.019 | 3.0671 | 3.2732 | 3.1908 | 3.3969 | 1.7719 | 2.6841 | 3.1955 | 3.1955 | 3.5365 | 3.5365 | 2019-06-18 10:00 | 2.0729 | 3.5571 | 6.0121 | 6.0121 | 6.0121 | 6.0121
2021-04-20 22:00 | 2.0348 | 2.5198 | 2.5599 | 2.7319 | 2.6631 | 2.8351 | 1.5918 | 2.4113 | 2.8708 | 2.8708 | 3.1771 | 3.1771 | 2019-06-18 11:00 | 2.1186 | 3.6356 | 6.1448 | 6.1448 | 6.1448 | 6.1448
2021-04-20 23:00 | 1.8033 | 2.2331 | 2.2687 | 2.4211 | 2.3602 | 2.5126 | 1.2689 | 1.9221 | 2.2884 | 2.2884 | 2.5326 | 2.5326 | 2019-06-18 12:00 | 2.111 | 3.6225 | 6.1227 | 6.1227 | 6.1227 | 6.1227
2021-04-21 | 1.6147 | 1.9995 | 2.0314 | 2.1679 | 2.1133 | 2.2498 | 1.0231 | 1.5498 | 1.8452 | 1.8452 | 2.042 | 2.042 | 2019-06-18 13:00 | 2.0882 | 3.5833 | 6.0564 | 6.0564 | 6.0564 | 6.0564
2021-04-21 01:00 | 1.5061 | 1.8651 | 1.8948 | 2.0221 | 1.9712 | 2.0985 | 0.94024 | 1.4243 | 1.6957 | 1.6957 | 1.8766 | 1.8766 | 2019-06-18 14:00 | 2.1339 | 3.6618 | 6.189 | 6.189 | 6.189 | 6.189
2021-04-21 02:00 | 1.4661 | 1.8155 | 1.8444 | 1.9684 | 1.9188 | 2.0427 | 0.88594 | 1.342 | 1.5978 | 1.5978 | 1.7682 | 1.7682 | 2019-06-18 15:00 | 2.0653 | 3.5441 | 5.99 | 5.99 | 5.99 | 5.99
2021-04-21 03:00 | 1.486 | 1.8402 | 1.8695 | 1.9952 | 1.9449 | 2.0705 | 0.86587 | 1.3116 | 1.5616 | 1.5616 | 1.7282 | 1.7282 | 2019-06-18 16:00 | 2.1263 | 3.6487 | 6.1669 | 6.1669 | 6.1669 | 6.1669
2021-04-21 04:00 | 1.5947 | 1.9748 | 2.0062 | 2.141 | 2.0871 | 2.2219 | 0.86594 | 1.3117 | 1.5617 | 1.5617 | 1.7283 | 1.7283 | 2019-06-18 17:00 | 2.1415 | 3.6748 | 6.2111 | 6.2111 | 6.2111 | 6.2111
2021-04-21 05:00 | 1.9473 | 2.4115 | 2.4499 | 2.6145 | 2.5487 | 2.7133 | 0.95167 | 1.4416 | 1.7163 | 1.7163 | 1.8994 | 1.8994 | 2019-06-18 18:00 | 1.9053 | 3.2694 | 5.5259 | 5.5259 | 5.5259 | 5.5259
2021-04-21 06:00 | 2.595 | 3.2134 | 3.2646 | 3.484 | 3.3962 | 3.6156 | 1.1946 | 1.8096 | 2.1544 | 2.1544 | 2.3843 | 2.3843 | 2019-06-18 19:00 | 1.8062 | 3.0994 | 5.2385 | 5.2385 | 5.2385 | 5.2385
2021-04-21 07:00 | 2.9465 | 3.6487 | 3.7069 | 3.9559 | 3.8563 | 4.1054 | 1.5232 | 2.3074 | 2.7471 | 2.7471 | 3.0402 | 3.0402 | 2019-06-18 20:00 | 1.6842 | 2.8902 | 4.8849 | 4.8849 | 4.8849 | 4.8849
2021-04-21 08:00 | 2.8893 | 3.578 | 3.6349 | 3.8792 | 3.7815 | 4.0257 | 1.6061 | 2.433 | 2.8966 | 2.8966 | 3.2057 | 3.2057 | 2019-06-18 21:00 | 1.6004 | 2.7463 | 4.6417 | 4.6417 | 4.6417 | 4.6417
2021-04-21 09:00 | 2.6255 | 3.2512 | 3.303 | 3.525 | 3.4362 | 3.6581 | 1.6004 | 2.4243 | 2.8863 | 2.8863 | 3.1942 | 3.1942 | 2019-06-18 22:00 | 1.6385 | 2.8117 | 4.7522 | 4.7522 | 4.7522 | 4.7522
2021-04-21 10:00 | 2.4921 | 3.086 | 3.1352 | 3.3458 | 3.2616 | 3.4722 | 1.509 | 2.2858 | 2.7213 | 2.7213 | 3.0117 | 3.0117 | 2019-06-18 23:00 | 1.4937 | 2.5632 | 4.3323 | 4.3323 | 4.3323 | 4.3323
2021-04-21 11:00 | 2.292 | 2.8383 | 2.8835 | 3.0773 | 2.9998 | 3.1935 | 1.5061 | 2.2815 | 2.7162 | 2.7162 | 3.006 | 3.006 | 2019-06-19 | 1.387 | 2.3801 | 4.0228 | 4.0228 | 4.0228 | 4.0228
2021-04-21 12:00 | 2.2492 | 2.7852 | 2.8296 | 3.0197 | 2.9437 | 3.1338 | 1.4775 | 2.2382 | 2.6646 | 2.6646 | 2.949 | 2.949 | 2019-06-19 01:00 | 1.3794 | 2.3671 | 4.0007 | 4.0007 | 4.0007 | 4.0007
2021-04-21 13:00 | 2.2349 | 2.7675 | 2.8116 | 3.0005 | 2.925 | 3.1139 | 1.4547 | 2.2035 | 2.6234 | 2.6234 | 2.9033 | 2.9033 | 2019-06-19 02:00 | 1.2956 | 2.2232 | 3.7576 | 3.7576 | 3.7576 | 3.7576
2021-04-21 14:00 | 2.2663 | 2.8064 | 2.8512 | 3.0427 | 2.9661 | 3.1577 | 1.5147 | 2.2944 | 2.7317 | 2.7317 | 3.0231 | 3.0231 | 2019-06-19 03:00 | 1.3489 | 2.3148 | 3.9123 | 3.9123 | 3.9123 | 3.9123
2021-04-21 15:00 | 2.2892 | 2.8348 | 2.8799 | 3.0734 | 2.996 | 3.1895 | 1.4489 | 2.1949 | 2.6131 | 2.6131 | 2.8919 | 2.8919 | 2019-06-19 04:00 | 1.4251 | 2.4455 | 4.1333 | 4.1333 | 4.1333 | 4.1333
2021-04-21 16:00 | 2.3947 | 2.9655 | 3.0127 | 3.2151 | 3.1342 | 3.3366 | 1.6433 | 2.4893 | 2.9636 | 2.9636 | 3.2798 | 3.2798 | 2019-06-19 05:00 | 1.89 | 3.2433 | 5.4817 | 5.4817 | 5.4817 | 5.4817
2021-04-21 17:00 | 2.9665 | 3.6735 | 3.732 | 3.9828 | 3.8825 | 4.1332 | 1.8919 | 2.8659 | 3.412 | 3.412 | 3.7761 | 3.7761 | 2019-06-19 06:00 | 1.9281 | 3.3087 | 5.5922 | 5.5922 | 5.5922 | 5.5922
2021-04-21 18:00 | 3.2466 | 4.0203 | 4.0844 | 4.3588 | 4.249 | 4.5235 | 2.0462 | 3.0997 | 3.6903 | 3.6903 | 4.0841 | 4.0841 | 2019-06-19 07:00 | 2.0577 | 3.531 | 5.9679 | 5.9679 | 5.9679 | 5.9679
2021-04-21 19:00 | 3.0351 | 3.7584 | 3.8183 | 4.0749 | 3.9723 | 4.2288 | 2.0034 | 3.0347 | 3.613 | 3.613 | 3.9985 | 3.9985 | 2019-06-19 08:00 | 2.1415 | 3.6748 | 6.2111 | 6.2111 | 6.2111 | 6.2111
2021-04-21 20:00 | 2.8668 | 3.5501 | 3.6066 | 3.849 | 3.752 | 3.9944 | 1.8977 | 2.8746 | 3.4224 | 3.4224 | 3.7876 | 3.7876 | 2019-06-19 09:00 | 2.1644 | 3.7141 | 6.2774 | 6.2774 | 6.2774 | 6.2774
2021-04-21 21:00 | 2.5521 | 3.1604 | 3.2107 | 3.4264 | 3.3401 | 3.5559 | 1.7719 | 2.6841 | 3.1955 | 3.1955 | 3.5365 | 3.5365 | 2019-06-19 10:00 | 2.0272 | 3.4787 | 5.8795 | 5.8795 | 5.8795 | 5.8795
2021-04-21 22:00 | 2.3035 | 2.8525 | 2.8979 | 3.0926 | 3.0147 | 3.2094 | 1.5662 | 2.3724 | 2.8245 | 2.8245 | 3.1259 | 3.1259 | 2019-06-19 11:00 | 2.1339 | 3.6618 | 6.189 | 6.189 | 6.189 | 6.189
2021-04-21 23:00 | 2.092 | 2.5906 | 2.6318 | 2.8087 | 2.7379 | 2.9148 | 1.2975 | 1.9654 | 2.3399 | 2.3399 | 2.5896 | 2.5896 | 2019-06-19 12:00 | 2.1339 | 3.6618 | 6.189 | 6.189 | 6.189 | 6.189
2021-04-22 | 1.7947 | 2.2225 | 2.2579 | 2.4096 | 2.3489 | 2.5007 | 1.0746 | 1.6278 | 1.9379 | 1.9379 | 2.1447 | 2.1447 | 2019-06-19 13:00 | 2.0653 | 3.5441 | 5.99 | 5.99 | 5.99 | 5.99
2021-04-22 01:00 | 1.7062 | 2.1128 | 2.1465 | 2.2907 | 2.233 | 2.3772 | 0.9974 | 1.5109 | 1.7988 | 1.7988 | 1.9907 | 1.9907 | 2019-06-19 14:00 | 2.0501 | 3.5179 | 5.9458 | 5.9458 | 5.9458 | 5.9458
2021-04-22 02:00 | 1.6747 | 2.0739 | 2.1069 | 2.2485 | 2.1918 | 2.3334 | 0.97453 | 1.4762 | 1.7575 | 1.7575 | 1.9451 | 1.9451 | 2019-06-19 15:00 | 1.9967 | 3.4264 | 5.7911 | 5.7911 | 5.7911 | 5.7911
2021-04-22 03:00 | 1.6775 | 2.0773 | 2.1104 | 2.2522 | 2.1955 | 2.3373 | 0.90023 | 1.3637 | 1.6235 | 1.6235 | 1.7968 | 1.7968 | 2019-06-19 16:00 | 2.0424 | 3.5048 | 5.9237 | 5.9237 | 5.9237 | 5.9237
2021-04-22 04:00 | 1.7404 | 2.1553 | 2.1896 | 2.3367 | 2.2779 | 2.425 | 0.9771 | 1.4801 | 1.7622 | 1.7622 | 1.9502 | 1.9502 | 2019-06-19 17:00 | 2.1263 | 3.6487 | 6.1669 | 6.1669 | 6.1669 | 6.1669
2021-04-22 05:00 | 2.0663 | 2.5587 | 2.5995 | 2.7742 | 2.7043 | 2.879 | 1.1289 | 1.71 | 2.0359 | 2.0359 | 2.2531 | 2.2531 | 2019-06-19 18:00 | 2.0805 | 3.5702 | 6.0343 | 6.0343 | 6.0343 | 6.0343
2021-04-22 06:00 | 2.955 | 3.6594 | 3.7176 | 3.9674 | 3.8675 | 4.1173 | 1.3918 | 2.1083 | 2.51 | 2.51 | 2.7779 | 2.7779 | 2019-06-19 19:00 | 1.9662 | 3.374 | 5.7027 | 5.7027 | 5.7027 | 5.7027
2021-04-22 07:00 | 3.1179 | 3.8611 | 3.9226 | 4.1861 | 4.0807 | 4.3443 | 1.649 | 2.4979 | 2.9739 | 2.9739 | 3.2912 | 3.2912 | 2019-06-19 20:00 | 1.89 | 3.2433 | 5.4817 | 5.4817 | 5.4817 | 5.4817
2021-04-22 08:00 | 3.2408 | 4.0133 | 4.0772 | 4.3511 | 4.2416 | 4.5155 | 1.5918 | 2.4113 | 2.8708 | 2.8708 | 3.1771 | 3.1771 | 2019-06-19 21:00 | 1.8062 | 3.0994 | 5.2385 | 5.2385 | 5.2385 | 5.2385
2021-04-22 09:00 | 2.8522 | 3.532 | 3.5882 | 3.8293 | 3.7329 | 3.974 | 1.5518 | 2.3507 | 2.7987 | 2.7987 | 3.0973 | 3.0973 | 2019-06-19 22:00 | 1.7986 | 3.0863 | 5.2164 | 5.2164 | 5.2164 | 5.2164
2021-04-22 10:00 | 2.7464 | 3.401 | 3.4552 | 3.6873 | 3.5945 | 3.8266 | 1.5604 | 2.3637 | 2.8141 | 2.8141 | 3.1144 | 3.1144 | 2019-06-19 23:00 | 1.6157 | 2.7725 | 4.6859 | 4.6859 | 4.6859 | 4.6859
2021-04-22 11:00 | 2.695 | 3.3373 | 3.3905 | 3.6183 | 3.5271 | 3.755 | 1.629 | 2.4676 | 2.9378 | 2.9378 | 3.2513 | 3.2513 | 2019-06-20 | 1.5471 | 2.6548 | 4.487 | 4.487 | 4.487 | 4.487
2021-04-22 12:00 | 2.5206 | 3.1214 | 3.1711 | 3.3842 | 3.299 | 3.5121 | 1.549 | 2.3464 | 2.7935 | 2.7935 | 3.0916 | 3.0916 | 2019-06-20 01:00 | 1.4785 | 2.5371 | 4.2881 | 4.2881 | 4.2881 | 4.2881
2021-04-22 13:00 | 2.3292 | 2.8843 | 2.9302 | 3.1271 | 3.0484 | 3.2453 | 1.5861 | 2.4027 | 2.8605 | 2.8605 | 3.1657 | 3.1657 | 2019-06-20 02:00 | 1.4175 | 2.4324 | 4.1112 | 4.1112 | 4.1112 | 4.1112
2021-04-22 14:00 | 2.4121 | 2.9869 | 3.0345 | 3.2384 | 3.1569 | 3.3608 | 1.5375 | 2.3291 | 2.7729 | 2.7729 | 3.0688 | 3.0688 | 2019-06-20 03:00 | 1.509 | 2.5894 | 4.3765 | 4.3765 | 4.3765 | 4.3765
2021-04-22 15:00 | 2.4035 | 2.9763 | 3.0237 | 3.2269 | 3.1456 | 3.3488 | 1.529 | 2.3161 | 2.7574 | 2.7574 | 3.0516 | 3.0516 | 2019-06-20 04:00 | 1.5166 | 2.6025 | 4.3986 | 4.3986 | 4.3986 | 4.3986
2021-04-22 16:00 | 2.695 | 3.3373 | 3.3905 | 3.6183 | 3.5271 | 3.755 | 1.6861 | 2.5542 | 3.0409 | 3.0409 | 3.3654 | 3.3654 | 2019-06-20 05:00 | 1.7071 | 2.9294 | 4.9512 | 4.9512 | 4.9512 | 4.9512
2021-04-22 17:00 | 3.198 | 3.9602 | 4.0233 | 4.2936 | 4.1855 | 4.4558 | 2.0059 | 3.0385 | 3.6175 | 3.6175 | 4.0036 | 4.0036 | 2019-06-20 06:00 | 1.9967 | 3.4264 | 5.7911 | 5.7911 | 5.7911 | 5.7911
2021-04-22 18:00 | 3.4409 | 4.261 | 4.3289 | 4.6197 | 4.5034 | 4.7942 | 2.0977 | 3.1776 | 3.7831 | 3.7831 | 4.1867 | 4.1867 | 2019-06-20 07:00 | 2.233 | 3.8318 | 6.4763 | 6.4763 | 6.4763 | 6.4763
2021-04-22 19:00 | 3.2966 | 4.0824 | 4.1474 | 4.4261 | 4.3146 | 4.5933 | 2.2377 | 3.3897 | 4.0356 | 4.0356 | 4.4662 | 4.4662 | 2019-06-20 08:00 | 2.3244 | 3.9887 | 6.7416 | 6.7416 | 6.7416 | 6.7416
2021-04-22 20:00 | 3.0837 | 3.8186 | 3.8794 | 4.1401 | 4.0358 | 4.2965 | 2.0805 | 3.1516 | 3.7522 | 3.7522 | 4.1525 | 4.1525 | 2019-06-20 09:00 | 2.1644 | 3.7141 | 6.2774 | 6.2774 | 6.2774 | 6.2774
2021-04-22 21:00 | 2.9236 | 3.6204 | 3.6781 | 3.9252 | 3.8264 | 4.0735 | 2.028 | 3.072 | 3.6574 | 3.6574 | 4.0477 | 4.0477 | 2019-06-20 10:00 | 2.1034 | 3.6094 | 6.1006 | 6.1006 | 6.1006 | 6.1006
2021-04-22 22:00 | 2.4121 | 2.9869 | 3.0345 | 3.2384 | 3.1569 | 3.3608 | 1.6747 | 2.5369 | 3.0203 | 3.0203 | 3.3426 | 3.3426 | 2019-06-20 11:00 | 2.111 | 3.6225 | 6.1227 | 6.1227 | 6.1227 | 6.1227
2021-04-22 23:00 | 2.2834 | 2.8277 | 2.8727 | 3.0657 | 2.9885 | 3.1816 | 1.365 | 2.0677 | 2.4617 | 2.4617 | 2.7244 | 2.7244 | 2019-06-20 12:00 | 2.172 | 3.7271 | 6.2995 | 6.2995 | 6.2995 | 6.2995
2021-04-23 | 1.9205 | 2.3782 | 2.4161 | 2.5785 | 2.5135 | 2.6759 | 1.1204 | 1.6972 | 2.0206 | 2.0206 | 2.2362 | 2.2362 | 2019-06-20 13:00 | 2.0882 | 3.5833 | 6.0564 | 6.0564 | 6.0564 | 6.0564
2021-04-23 01:00 | 1.769 | 2.1907 | 2.2255 | 2.3751 | 2.3153 | 2.4648 | 1.0032 | 1.5196 | 1.8092 | 1.8092 | 2.0023 | 2.0023 | 2019-06-20 14:00 | 2.111 | 3.6225 | 6.1227 | 6.1227 | 6.1227 | 6.1227
2021-04-23 02:00 | 1.7262 | 2.1376 | 2.1716 | 2.3175 | 2.2592 | 2.4051 | 0.9631 | 1.4589 | 1.7369 | 1.7369 | 1.9223 | 1.9223 | 2019-06-20 15:00 | 2.0653 | 3.5441 | 5.99 | 5.99 | 5.99 | 5.99
2021-04-23 03:00 | 1.7119 | 2.1199 | 2.1536 | 2.2984 | 2.2405 | 2.3852 | 0.93738 | 1.42 | 1.6905 | 1.6905 | 1.8709 | 1.8709 | 2019-06-20 16:00 | 2.1263 | 3.6487 | 6.1669 | 6.1669 | 6.1669 | 6.1669
2021-04-23 04:00 | 1.7798 | 2.204 | 2.2391 | 2.3896 | 2.3294 | 2.4799 | 1.0117 | 1.5325 | 1.8245 | 1.8245 | 2.0192 | 2.0192 | 2019-06-20 17:00 | 2.2558 | 3.871 | 6.5426 | 6.5426 | 6.5426 | 6.5426
2021-04-23 05:00 | 2.0914 | 2.5898 | 2.6311 | 2.8079 | 2.7372 | 2.9139 | 1.1174 | 1.6927 | 2.0152 | 2.0152 | 2.2303 | 2.2303 | 2019-06-20 18:00 | 2.172 | 3.7271 | 6.2995 | 6.2995 | 6.2995 | 6.2995
2021-04-23 06:00 | 2.7007 | 3.3444 | 3.3977 | 3.6259 | 3.5346 | 3.7629 | 1.3775 | 2.0866 | 2.4843 | 2.4843 | 2.7493 | 2.7493 | 2019-06-20 19:00 | 2.0501 | 3.5179 | 5.9458 | 5.9458 | 5.9458 | 5.9458
2021-04-23 07:00 | 3.0951 | 3.8328 | 3.8938 | 4.1555 | 4.0508 | 4.3124 | 1.6804 | 2.5455 | 3.0306 | 3.0306 | 3.354 | 3.354 | 2019-06-20 20:00 | 1.9815 | 3.4002 | 5.7469 | 5.7469 | 5.7469 | 5.7469
2021-04-23 08:00 | 2.9493 | 3.6523 | 3.7105 | 3.9598 | 3.86 | 4.1094 | 1.6404 | 2.4849 | 2.9584 | 2.9584 | 3.2741 | 3.2741 | 2019-06-20 21:00 | 1.8367 | 3.1517 | 5.3269 | 5.3269 | 5.3269 | 5.3269
2021-04-23 09:00 | 2.8322 | 3.5072 | 3.563 | 3.8025 | 3.7067 | 3.9461 | 1.5661 | 2.3724 | 2.8244 | 2.8244 | 3.1258 | 3.1258 | 2019-06-20 22:00 | 1.7757 | 3.0471 | 5.1501 | 5.1501 | 5.1501 | 5.1501
2021-04-23 10:00 | 2.6835 | 3.3231 | 3.3761 | 3.6029 | 3.5122 | 3.739 | 1.4804 | 2.2425 | 2.6698 | 2.6698 | 2.9547 | 2.9547 | 2019-06-20 23:00 | 1.6233 | 2.7855 | 4.708 | 4.708 | 4.708 | 4.708
2021-04-23 11:00 | 2.3406 | 2.8985 | 2.9446 | 3.1425 | 3.0633 | 3.2612 | 1.5261 | 2.3118 | 2.7523 | 2.7523 | 3.0459 | 3.0459 | 2019-06-21 | 1.4632 | 2.5109 | 4.2439 | 4.2439 | 4.2439 | 4.2439
2021-04-23 12:00 | 2.2663 | 2.8064 | 2.8512 | 3.0427 | 2.9661 | 3.1577 | 1.5061 | 2.2815 | 2.7162 | 2.7162 | 3.006 | 3.006 | 2019-06-21 01:00 | 1.4556 | 2.4978 | 4.2218 | 4.2218 | 4.2218 | 4.2218
2021-04-23 13:00 | 2.2091 | 2.7357 | 2.7792 | 2.966 | 2.8913 | 3.078 | 1.4518 | 2.1992 | 2.6183 | 2.6183 | 2.8976 | 2.8976 | 2019-06-21 02:00 | 1.387 | 2.3801 | 4.0228 | 4.0228 | 4.0228 | 4.0228
2021-04-23 14:00 | 2.0377 | 2.5233 | 2.5635 | 2.7358 | 2.6669 | 2.8391 | 1.4461 | 2.1905 | 2.608 | 2.608 | 2.8862 | 2.8862 | 2019-06-21 03:00 | 1.3946 | 2.3932 | 4.0449 | 4.0449 | 4.0449 | 4.0449
2021-04-23 15:00 | 2.1063 | 2.6083 | 2.6498 | 2.8279 | 2.7566 | 2.9347 | 1.4261 | 2.1602 | 2.5719 | 2.5719 | 2.8463 | 2.8463 | 2019-06-21 04:00 | 1.5318 | 2.6286 | 4.4428 | 4.4428 | 4.4428 | 4.4428
2021-04-23 16:00 | 2.2692 | 2.81 | 2.8548 | 3.0466 | 2.9699 | 3.1617 | 1.5604 | 2.3637 | 2.8141 | 2.8141 | 3.1144 | 3.1144 | 2019-06-21 05:00 | 1.6766 | 2.8771 | 4.8628 | 4.8628 | 4.8628 | 4.8628
2021-04-23 17:00 | 2.6292 | 3.2559 | 3.3078 | 3.53 | 3.4411 | 3.6634 | 1.9033 | 2.8832 | 3.4326 | 3.4326 | 3.7989 | 3.7989 | 2019-06-21 06:00 | 1.9129 | 3.2825 | 5.548 | 5.548 | 5.548 | 5.548
2021-04-23 18:00 | 2.7436 | 3.3975 | 3.4516 | 3.6835 | 3.5907 | 3.8227 | 2.0977 | 3.1776 | 3.7831 | 3.7831 | 4.1867 | 4.1867 | 2019-06-21 07:00 | 2.2025 | 3.7795 | 6.3879 | 6.3879 | 6.3879 | 6.3879
2021-04-23 19:00 | 2.6407 | 3.2701 | 3.3221 | 3.5454 | 3.4561 | 3.6793 | 2.0662 | 3.13 | 3.7264 | 3.7264 | 4.124 | 4.124 | 2019-06-21 08:00 | 2.3015 | 3.9495 | 6.6753 | 6.6753 | 6.6753 | 6.6753
2021-04-23 20:00 | 2.655 | 3.2878 | 3.3401 | 3.5646 | 3.4748 | 3.6992 | 1.9805 | 3.0001 | 3.5718 | 3.5718 | 3.9529 | 3.9529 | 2019-06-21 09:00 | 2.3168 | 3.9756 | 6.7195 | 6.7195 | 6.7195 | 6.7195
2021-04-23 21:00 | 2.372 | 2.9374 | 2.9842 | 3.1847 | 3.1045 | 3.305 | 1.9148 | 2.9005 | 3.4532 | 3.4532 | 3.8217 | 3.8217 | 2019-06-21 10:00 | 2.1186 | 3.6356 | 6.1448 | 6.1448 | 6.1448 | 6.1448
2021-04-23 22:00 | 2.1606 | 2.6755 | 2.7181 | 2.9008 | 2.8277 | 3.0103 | 1.6719 | 2.5325 | 3.0151 | 3.0151 | 3.3368 | 3.3368 | 2019-06-21 11:00 | 2.111 | 3.6225 | 6.1227 | 6.1227 | 6.1227 | 6.1227
2021-04-23 23:00 | 1.9637 | 2.4318 | 2.4705 | 2.6365 | 2.5701 | 2.7361 | 1.3979 | 2.1175 | 2.521 | 2.521 | 2.79 | 2.79 | 2019-06-21 12:00 | 2.1644 | 3.7141 | 6.2774 | 6.2774 | 6.2774 | 6.2774
2021-04-24 | 1.7634 | 2.1837 | 2.2184 | 2.3675 | 2.3079 | 2.457 | 1.186 | 1.7966 | 2.1389 | 2.1389 | 2.3672 | 2.3672 | 2019-06-21 13:00 | 2.0653 | 3.5441 | 5.99 | 5.99 | 5.99 | 5.99
2021-04-24 01:00 | 1.7234 | 2.1342 | 2.1682 | 2.3138 | 2.2556 | 2.4013 | 1.1031 | 1.671 | 1.9895 | 1.9895 | 2.2017 | 2.2017 | 2019-06-21 14:00 | 2.1415 | 3.6748 | 6.2111 | 6.2111 | 6.2111 | 6.2111
2021-04-24 02:00 | 1.649 | 2.042 | 2.0745 | 2.2139 | 2.1582 | 2.2976 | 1.0174 | 1.5412 | 1.8348 | 1.8348 | 2.0306 | 2.0306 | 2019-06-21 15:00 | 2.0729 | 3.5571 | 6.0121 | 6.0121 | 6.0121 | 6.0121
2021-04-24 03:00 | 1.6318 | 2.0208 | 2.053 | 2.1909 | 2.1357 | 2.2737 | 0.98597 | 1.4935 | 1.7781 | 1.7781 | 1.9679 | 1.9679 | 2019-06-21 16:00 | 2.0958 | 3.5964 | 6.0785 | 6.0785 | 6.0785 | 6.0785
2021-04-24 04:00 | 1.7347 | 2.1482 | 2.1824 | 2.329 | 2.2704 | 2.417 | 0.97739 | 1.4806 | 1.7627 | 1.7627 | 1.9508 | 1.9508 | 2019-06-21 17:00 | 2.0958 | 3.5964 | 6.0785 | 6.0785 | 6.0785 | 6.0785
2021-04-24 05:00 | 1.7995 | 2.2284 | 2.2639 | 2.416 | 2.3551 | 2.5072 | 1.0768 | 1.6311 | 1.942 | 1.942 | 2.1492 | 2.1492 | 2019-06-21 18:00 | 1.8671 | 3.204 | 5.4154 | 5.4154 | 5.4154 | 5.4154
2021-04-24 06:00 | 2.0457 | 2.5333 | 2.5737 | 2.7466 | 2.6774 | 2.8504 | 1.1803 | 1.7879 | 2.1286 | 2.1286 | 2.3558 | 2.3558 | 2019-06-21 19:00 | 1.8443 | 3.1648 | 5.349 | 5.349 | 5.349 | 5.349
2021-04-24 07:00 | 2.2349 | 2.7675 | 2.8116 | 3.0005 | 2.925 | 3.1139 | 1.3175 | 1.9957 | 2.376 | 2.376 | 2.6295 | 2.6295 | 2019-06-21 20:00 | 1.6995 | 2.9163 | 4.9291 | 4.9291 | 4.9291 | 4.9291
2021-04-24 08:00 | 2.1949 | 2.718 | 2.7613 | 2.9468 | 2.8726 | 3.0581 | 1.4832 | 2.2468 | 2.675 | 2.675 | 2.9604 | 2.9604 | 2019-06-21 21:00 | 1.6995 | 2.9163 | 4.9291 | 4.9291 | 4.9291 | 4.9291
2021-04-24 09:00 | 2.0948 | 2.5941 | 2.6354 | 2.8125 | 2.7417 | 2.9188 | 1.529 | 2.3161 | 2.7574 | 2.7574 | 3.0516 | 3.0516 | 2019-06-21 22:00 | 1.7223 | 2.9556 | 4.9954 | 4.9954 | 4.9954 | 4.9954
2021-04-24 10:00 | 2.0662 | 2.5587 | 2.5995 | 2.7741 | 2.7043 | 2.8789 | 1.6604 | 2.5152 | 2.9945 | 2.9945 | 3.314 | 3.314 | 2019-06-21 23:00 | 1.6004 | 2.7463 | 4.6417 | 4.6417 | 4.6417 | 4.6417
2021-04-24 11:00 | 1.8119 | 2.2437 | 2.2795 | 2.4326 | 2.3714 | 2.5245 | 1.669 | 2.5282 | 3.01 | 3.01 | 3.3311 | 3.3311 | 2019-06-22 | 1.4556 | 2.4978 | 4.2218 | 4.2218 | 4.2218 | 4.2218
2021-04-24 12:00 | 1.6547 | 2.0491 | 2.0817 | 2.2216 | 2.1657 | 2.3055 | 1.6519 | 2.5022 | 2.979 | 2.979 | 3.2969 | 3.2969 | 2019-06-22 01:00 | 1.4861 | 2.5501 | 4.3102 | 4.3102 | 4.3102 | 4.3102
2021-04-24 13:00 | 1.6347 | 2.0243 | 2.0566 | 2.1948 | 2.1395 | 2.2777 | 1.5575 | 2.3594 | 2.809 | 2.809 | 3.1087 | 3.1087 | 2019-06-22 02:00 | 1.4404 | 2.4717 | 4.1776 | 4.1776 | 4.1776 | 4.1776
2021-04-24 14:00 | 1.6833 | 2.0845 | 2.1177 | 2.26 | 2.2031 | 2.3454 | 1.569 | 2.3767 | 2.8296 | 2.8296 | 3.1315 | 3.1315 | 2019-06-22 03:00 | 1.4175 | 2.4324 | 4.1112 | 4.1112 | 4.1112 | 4.1112
2021-04-24 15:00 | 1.7547 | 2.173 | 2.2076 | 2.3559 | 2.2966 | 2.4449 | 1.5147 | 2.2944 | 2.7317 | 2.7317 | 3.0231 | 3.0231 | 2019-06-22 04:00 | 1.5166 | 2.6025 | 4.3986 | 4.3986 | 4.3986 | 4.3986
2021-04-24 16:00 | 1.8348 | 2.2721 | 2.3082 | 2.4633 | 2.4013 | 2.5564 | 1.6976 | 2.5715 | 3.0615 | 3.0615 | 3.3882 | 3.3882 | 2019-06-22 05:00 | 1.6004 | 2.7463 | 4.6417 | 4.6417 | 4.6417 | 4.6417
2021-04-24 17:00 | 2.4749 | 3.0648 | 3.1136 | 3.3228 | 3.2391 | 3.4484 | 1.8948 | 2.8702 | 3.4171 | 3.4171 | 3.7818 | 3.7818 | 2019-06-22 06:00 | 1.73 | 2.9686 | 5.0175 | 5.0175 | 5.0175 | 5.0175
2021-04-24 18:00 | 2.5206 | 3.1214 | 3.1711 | 3.3842 | 3.299 | 3.5121 | 1.9691 | 2.9828 | 3.5512 | 3.5512 | 3.9301 | 3.9301 | 2019-06-22 07:00 | 1.9967 | 3.4264 | 5.7911 | 5.7911 | 5.7911 | 5.7911
2021-04-24 19:00 | 2.3928 | 2.9631 | 3.0103 | 3.2125 | 3.1316 | 3.3339 | 1.8976 | 2.8745 | 3.4223 | 3.4223 | 3.7875 | 3.7875 | 2019-06-22 08:00 | 2.1186 | 3.6356 | 6.1448 | 6.1448 | 6.1448 | 6.1448
2021-04-24 20:00 | 2.3292 | 2.8843 | 2.9302 | 3.1271 | 3.0484 | 3.2453 | 1.8776 | 2.8442 | 3.3862 | 3.3862 | 3.7475 | 3.7475 | 2019-06-22 09:00 | 2.1415 | 3.6748 | 6.2111 | 6.2111 | 6.2111 | 6.2111
2021-04-24 21:00 | 2.2206 | 2.7498 | 2.7936 | 2.9813 | 2.9063 | 3.094 | 1.8148 | 2.749 | 3.2728 | 3.2728 | 3.6221 | 3.6221 | 2019-06-22 10:00 | 2.1796 | 3.7402 | 6.3216 | 6.3216 | 6.3216 | 6.3216
2021-04-24 22:00 | 2.1177 | 2.6224 | 2.6642 | 2.8432 | 2.7716 | 2.9506 | 1.6919 | 2.5628 | 3.0512 | 3.0512 | 3.3768 | 3.3768 | 2019-06-22 11:00 | 2.1644 | 3.7141 | 6.2774 | 6.2774 | 6.2774 | 6.2774
2021-04-24 23:00 | 2.012 | 2.4916 | 2.5312 | 2.7013 | 2.6333 | 2.8034 | 1.4332 | 2.1711 | 2.5848 | 2.5848 | 2.8606 | 2.8606 | 2019-06-22 12:00 | 2.1567 | 3.701 | 6.2553 | 6.2553 | 6.2553 | 6.2553
2021-04-25 | 1.7919 | 2.219 | 2.2543 | 2.4058 | 2.3452 | 2.4967 | 1.2204 | 1.8486 | 2.2009 | 2.2009 | 2.4357 | 2.4357 | 2019-06-22 13:00 | 2.0653 | 3.5441 | 5.99 | 5.99 | 5.99 | 5.99
2021-04-25 01:00 | 1.6633 | 2.0597 | 2.0925 | 2.2331 | 2.1769 | 2.3175 | 1.0717 | 1.6234 | 1.9328 | 1.9328 | 2.139 | 2.139 | 2019-06-22 14:00 | 2.1339 | 3.6618 | 6.189 | 6.189 | 6.189 | 6.189
2021-04-25 02:00 | 1.6147 | 1.9995 | 2.0314 | 2.1679 | 2.1133 | 2.2498 | 1.0231 | 1.5498 | 1.8452 | 1.8452 | 2.042 | 2.042 | 2019-06-22 15:00 | 2.111 | 3.6225 | 6.1227 | 6.1227 | 6.1227 | 6.1227
2021-04-25 03:00 | 1.7119 | 2.1199 | 2.1536 | 2.2984 | 2.2405 | 2.3852 | 0.9631 | 1.4589 | 1.7369 | 1.7369 | 1.9223 | 1.9223 | 2019-06-22 16:00 | 2.1186 | 3.6356 | 6.1448 | 6.1448 | 6.1448 | 6.1448
2021-04-25 04:00 | 1.8576 | 2.3004 | 2.337 | 2.494 | 2.4312 | 2.5883 | 1.0488 | 1.5888 | 1.8915 | 1.8915 | 2.0934 | 2.0934 | 2019-06-22 17:00 | 2.1034 | 3.6094 | 6.1006 | 6.1006 | 6.1006 | 6.1006
2021-04-25 05:00 | 1.9634 | 2.4313 | 2.47 | 2.636 | 2.5696 | 2.7356 | 1.0831 | 1.6407 | 1.9534 | 1.9534 | 2.1618 | 2.1618 | 2019-06-22 18:00 | 2.0805 | 3.5702 | 6.0343 | 6.0343 | 6.0343 | 6.0343
2021-04-25 06:00 | 2.0577 | 2.5481 | 2.5887 | 2.7626 | 2.6931 | 2.867 | 1.1374 | 1.723 | 2.0513 | 2.0513 | 2.2702 | 2.2702 | 2019-06-22 19:00 | 1.9129 | 3.2825 | 5.548 | 5.548 | 5.548 | 5.548
2021-04-25 07:00 | 2.1577 | 2.672 | 2.7145 | 2.8969 | 2.824 | 3.0064 | 1.1974 | 1.8139 | 2.1596 | 2.1596 | 2.39 | 2.39 | 2019-06-22 20:00 | 1.9129 | 3.2825 | 5.548 | 5.548 | 5.548 | 5.548
2021-04-25 08:00 | 2.1691 | 2.6861 | 2.7289 | 2.9123 | 2.8389 | 3.0223 | 1.4261 | 2.1602 | 2.5719 | 2.5719 | 2.8463 | 2.8463 | 2019-06-22 21:00 | 1.8062 | 3.0994 | 5.2385 | 5.2385 | 5.2385 | 5.2385
2021-04-25 09:00 | 2.0205 | 2.5021 | 2.5419 | 2.7127 | 2.6444 | 2.8152 | 1.4575 | 2.2079 | 2.6286 | 2.6286 | 2.909 | 2.909 | 2019-06-22 22:00 | 1.7757 | 3.0471 | 5.1501 | 5.1501 | 5.1501 | 5.1501
2021-04-25 10:00 | 1.9405 | 2.403 | 2.4413 | 2.6053 | 2.5397 | 2.7037 | 1.5861 | 2.4027 | 2.8605 | 2.8605 | 3.1657 | 3.1657 | 2019-06-22 23:00 | 1.6004 | 2.7463 | 4.6417 | 4.6417 | 4.6417 | 4.6417
2021-04-25 11:00 | 1.7576 | 2.1765 | 2.2112 | 2.3597 | 2.3003 | 2.4489 | 1.5833 | 2.3983 | 2.8554 | 2.8554 | 3.16 | 3.16 | 2019-06-23 | 1.5852 | 2.7202 | 4.5975 | 4.5975 | 4.5975 | 4.5975
2021-04-25 12:00 | 1.6833 | 2.0845 | 2.1177 | 2.26 | 2.2031 | 2.3454 | 1.629 | 2.4676 | 2.9378 | 2.9378 | 3.2513 | 3.2513 | 2019-06-23 01:00 | 1.4175 | 2.4324 | 4.1112 | 4.1112 | 4.1112 | 4.1112
2021-04-25 13:00 | 1.6661 | 2.0633 | 2.0961 | 2.237 | 2.1806 | 2.3215 | 1.5976 | 2.42 | 2.8811 | 2.8811 | 3.1885 | 3.1885 | 2019-06-23 02:00 | 1.3946 | 2.3932 | 4.0449 | 4.0449 | 4.0449 | 4.0449
2021-04-25 14:00 | 1.5547 | 1.9252 | 1.9559 | 2.0873 | 2.0347 | 2.1662 | 1.5518 | 2.3507 | 2.7987 | 2.7987 | 3.0973 | 3.0973 | 2019-06-23 03:00 | 1.4099 | 2.4194 | 4.0891 | 4.0891 | 4.0891 | 4.0891
2021-04-25 15:00 | 1.7004 | 2.1057 | 2.1393 | 2.283 | 2.2255 | 2.3692 | 1.5661 | 2.3724 | 2.8244 | 2.8244 | 3.1258 | 3.1258 | 2019-06-23 04:00 | 1.4404 | 2.4717 | 4.1776 | 4.1776 | 4.1776 | 4.1776
2021-04-25 16:00 | 1.9205 | 2.3782 | 2.4161 | 2.5785 | 2.5135 | 2.6759 | 1.7919 | 2.7144 | 3.2316 | 3.2316 | 3.5764 | 3.5764 | 2019-06-23 05:00 | 1.5394 | 2.6417 | 4.4649 | 4.4649 | 4.4649 | 4.4649
2021-04-25 17:00 | 2.3683 | 2.9328 | 2.9795 | 3.1797 | 3.0996 | 3.2998 | 1.8319 | 2.775 | 3.3038 | 3.3038 | 3.6563 | 3.6563 | 2019-06-23 06:00 | 1.7071 | 2.9294 | 4.9512 | 4.9512 | 4.9512 | 4.9512
2021-04-25 18:00 | 2.4463 | 3.0294 | 3.0777 | 3.2845 | 3.2017 | 3.4085 | 1.9062 | 2.8875 | 3.4378 | 3.4378 | 3.8046 | 3.8046 | 2019-06-23 07:00 | 1.8443 | 3.1648 | 5.349 | 5.349 | 5.349 | 5.349
2021-04-25 19:00 | 2.372 | 2.9374 | 2.9842 | 3.1847 | 3.1045 | 3.305 | 1.9691 | 2.9828 | 3.5512 | 3.5512 | 3.9301 | 3.9301 | 2019-06-23 08:00 | 2.172 | 3.7271 | 6.2995 | 6.2995 | 6.2995 | 6.2995
2021-04-25 20:00 | 2.4035 | 2.9763 | 3.0237 | 3.2269 | 3.1456 | 3.3488 | 1.8776 | 2.8442 | 3.3862 | 3.3862 | 3.7475 | 3.7475 | 2019-06-23 09:00 | 2.1491 | 3.6879 | 6.2332 | 6.2332 | 6.2332 | 6.2332
2021-04-25 21:00 | 2.1234 | 2.6295 | 2.6714 | 2.8509 | 2.7791 | 2.9586 | 1.729 | 2.6191 | 3.1182 | 3.1182 | 3.4509 | 3.4509 | 2019-06-23 10:00 | 2.1339 | 3.6618 | 6.189 | 6.189 | 6.189 | 6.189
2021-04-25 22:00 | 2.092 | 2.5906 | 2.6318 | 2.8087 | 2.7379 | 2.9148 | 1.5328 | 2.3219 | 2.7643 | 2.7643 | 3.0593 | 3.0593 | 2019-06-23 11:00 | 2.1872 | 3.7533 | 6.3437 | 6.3437 | 6.3437 | 6.3437
2021-04-25 23:00 | 1.9405 | 2.403 | 2.4413 | 2.6053 | 2.5397 | 2.7037 | 1.3775 | 2.0866 | 2.4843 | 2.4843 | 2.7493 | 2.7493 | 2019-06-23 12:00 | 2.233 | 3.8318 | 6.4763 | 6.4763 | 6.4763 | 6.4763
2021-04-26 | 1.7147 | 2.1234 | 2.1572 | 2.3022 | 2.2442 | 2.3892 | 1.1203 | 1.697 | 2.0204 | 2.0204 | 2.236 | 2.236 | 2019-06-23 13:00 | 2.1644 | 3.7141 | 6.2774 | 6.2774 | 6.2774 | 6.2774
2021-04-26 01:00 | 1.6633 | 2.0597 | 2.0925 | 2.2331 | 2.1769 | 2.3175 | 1.0631 | 1.6104 | 1.9173 | 1.9173 | 2.1219 | 2.1219 | 2019-06-23 14:00 | 2.2177 | 3.8056 | 6.4321 | 6.4321 | 6.4321 | 6.4321
2021-04-26 02:00 | 1.6919 | 2.0951 | 2.1285 | 2.2715 | 2.2143 | 2.3573 | 0.97453 | 1.4762 | 1.7575 | 1.7575 | 1.9451 | 1.9451 | 2019-06-23 15:00 | 2.2101 | 3.7925 | 6.41 | 6.41 | 6.41 | 6.41
2021-04-26 03:00 | 1.6176 | 2.0031 | 2.035 | 2.1717 | 2.117 | 2.2538 | 0.94596 | 1.4329 | 1.706 | 1.706 | 1.888 | 1.888 | 2019-06-23 16:00 | 2.1872 | 3.7533 | 6.3437 | 6.3437 | 6.3437 | 6.3437
2021-04-26 04:00 | 1.6633 | 2.0597 | 2.0925 | 2.2331 | 2.1769 | 2.3175 | 0.9431 | 1.4286 | 1.7008 | 1.7008 | 1.8823 | 1.8823 | 2019-06-23 17:00 | 2.2558 | 3.871 | 6.5426 | 6.5426 | 6.5426 | 6.5426
2021-04-26 05:00 | 1.729 | 2.1411 | 2.1752 | 2.3214 | 2.2629 | 2.4091 | 0.9773 | 1.4804 | 1.7625 | 1.7625 | 1.9506 | 1.9506 | 2019-06-23 18:00 | 2.1491 | 3.6879 | 6.2332 | 6.2332 | 6.2332 | 6.2332
2021-04-26 06:00 | 2.0205 | 2.5021 | 2.5419 | 2.7127 | 2.6444 | 2.8152 | 1.0774 | 1.6321 | 1.9431 | 1.9431 | 2.1504 | 2.1504 | 2019-06-23 19:00 | 2.1034 | 3.6094 | 6.1006 | 6.1006 | 6.1006 | 6.1006
2021-04-26 07:00 | 2.1606 | 2.6755 | 2.7181 | 2.9008 | 2.8277 | 3.0103 | 1.2346 | 1.8702 | 2.2266 | 2.2266 | 2.4641 | 2.4641 | 2019-06-23 20:00 | 1.9891 | 3.4133 | 5.769 | 5.769 | 5.769 | 5.769
2021-04-26 08:00 | 2.2434 | 2.7781 | 2.8224 | 3.012 | 2.9362 | 3.1258 | 1.4146 | 2.1429 | 2.5513 | 2.5513 | 2.8235 | 2.8235 | 2019-06-23 21:00 | 1.9815 | 3.4002 | 5.7469 | 5.7469 | 5.7469 | 5.7469
2021-04-26 09:00 | 2.1406 | 2.6507 | 2.693 | 2.8739 | 2.8015 | 2.9825 | 1.5175 | 2.2988 | 2.7368 | 2.7368 | 3.0288 | 3.0288 | 2019-06-23 22:00 | 1.7071 | 2.9294 | 4.9512 | 4.9512 | 4.9512 | 4.9512
2021-04-26 10:00 | 2.0834 | 2.58 | 2.621 | 2.7972 | 2.7267 | 2.9028 | 1.6004 | 2.4243 | 2.8863 | 2.8863 | 3.1942 | 3.1942 | 2019-06-23 23:00 | 1.5623 | 2.6809 | 4.5312 | 4.5312 | 4.5312 | 4.5312
2021-04-26 11:00 | 1.7862 | 2.2119 | 2.2471 | 2.3981 | 2.3377 | 2.4887 | 1.6776 | 2.5412 | 3.0254 | 3.0254 | 3.3483 | 3.3483 | 2019-06-24 | 1.4785 | 2.5371 | 4.2881 | 4.2881 | 4.2881 | 4.2881
2021-04-26 12:00 | 1.6674 | 2.0648 | 2.0977 | 2.2386 | 2.1823 | 2.3232 | 1.6404 | 2.4849 | 2.9584 | 2.9584 | 3.2741 | 3.2741 | 2019-06-24 01:00 | 1.4251 | 2.4455 | 4.1333 | 4.1333 | 4.1333 | 4.1333
2021-04-26 13:00 | 1.6147 | 1.9995 | 2.0314 | 2.1679 | 2.1133 | 2.2498 | 1.6147 | 2.446 | 2.912 | 2.912 | 3.2228 | 3.2228 | 2019-06-24 02:00 | 1.4175 | 2.4324 | 4.1112 | 4.1112 | 4.1112 | 4.1112
2021-04-26 14:00 | 1.6204 | 2.0066 | 2.0386 | 2.1756 | 2.1208 | 2.2578 | 1.6347 | 2.4763 | 2.9481 | 2.9481 | 3.2627 | 3.2627 | 2019-06-24 03:00 | 1.3794 | 2.3671 | 4.0007 | 4.0007 | 4.0007 | 4.0007
2021-04-26 15:00 | 1.7805 | 2.2048 | 2.2399 | 2.3904 | 2.3302 | 2.4807 | 1.649 | 2.4979 | 2.9739 | 2.9739 | 3.2912 | 3.2912 | 2019-06-24 04:00 | 1.4251 | 2.4455 | 4.1333 | 4.1333 | 4.1333 | 4.1333
2021-04-26 16:00 | 2.2463 | 2.7817 | 2.826 | 3.0159 | 2.9399 | 3.1298 | 1.7077 | 2.5868 | 3.0797 | 3.0797 | 3.4083 | 3.4083 | 2019-06-24 05:00 | 1.6538 | 2.8379 | 4.7965 | 4.7965 | 4.7965 | 4.7965
2021-04-26 17:00 | 2.6664 | 3.3019 | 3.3545 | 3.5799 | 3.4897 | 3.7151 | 1.9119 | 2.8962 | 3.4481 | 3.4481 | 3.816 | 3.816 | 2019-06-24 06:00 | 1.9357 | 3.3217 | 5.6143 | 5.6143 | 5.6143 | 5.6143
2021-04-26 18:00 | 2.7579 | 3.4152 | 3.4696 | 3.7027 | 3.6094 | 3.8426 | 2.0405 | 3.091 | 3.68 | 3.68 | 4.0727 | 4.0727 | 2019-06-24 07:00 | 2.0653 | 3.5441 | 5.99 | 5.99 | 5.99 | 5.99
2021-04-26 19:00 | 2.6374 | 3.266 | 3.318 | 3.541 | 3.4518 | 3.6748 | 2.1406 | 3.2425 | 3.8604 | 3.8604 | 4.2723 | 4.2723 | 2019-06-24 08:00 | 2.2406 | 3.8448 | 6.4984 | 6.4984 | 6.4984 | 6.4984
2021-04-26 20:00 | 2.5092 | 3.1073 | 3.1568 | 3.3689 | 3.284 | 3.4961 | 1.8748 | 2.8399 | 3.3811 | 3.3811 | 3.7418 | 3.7418 | 2019-06-24 09:00 | 2.111 | 3.6225 | 6.1227 | 6.1227 | 6.1227 | 6.1227
2021-04-26 21:00 | 2.2868 | 2.8318 | 2.8769 | 3.0702 | 2.9929 | 3.1862 | 1.8206 | 2.7579 | 3.2834 | 3.2834 | 3.6338 | 3.6338 | 2019-06-24 10:00 | 2.1034 | 3.6094 | 6.1006 | 6.1006 | 6.1006 | 6.1006
2021-04-26 22:00 | 2.112 | 2.6153 | 2.657 | 2.8355 | 2.7641 | 2.9426 | 1.5661 | 2.3724 | 2.8244 | 2.8244 | 3.1258 | 3.1258 | 2019-06-24 11:00 | 2.1339 | 3.6618 | 6.189 | 6.189 | 6.189 | 6.189
2021-04-26 23:00 | 2.0262 | 2.5092 | 2.5491 | 2.7204 | 2.6519 | 2.8232 | 1.3841 | 2.0967 | 2.4962 | 2.4962 | 2.7625 | 2.7625 | 2019-06-24 12:00 | 2.1034 | 3.6094 | 6.1006 | 6.1006 | 6.1006 | 6.1006
2021-04-27 | 1.7292 | 2.1413 | 2.1754 | 2.3216 | 2.2631 | 2.4093 | 1.1889 | 1.8009 | 2.1441 | 2.1441 | 2.3729 | 2.3729 | 2019-06-24 13:00 | 2.1034 | 3.6094 | 6.1006 | 6.1006 | 6.1006 | 6.1006
2021-04-27 01:00 | 1.6147 | 1.9995 | 2.0314 | 2.1679 | 2.1133 | 2.2498 | 1.0431 | 1.5801 | 1.8812 | 1.8812 | 2.082 | 2.082 | 2019-06-24 14:00 | 2.1263 | 3.6487 | 6.1669 | 6.1669 | 6.1669 | 6.1669
2021-04-27 02:00 | 1.6433 | 2.0349 | 2.0674 | 2.2063 | 2.1507 | 2.2896 | 0.97168 | 1.4719 | 1.7524 | 1.7524 | 1.9394 | 1.9394 | 2019-06-24 15:00 | 2.1263 | 3.6487 | 6.1669 | 6.1669 | 6.1669 | 6.1669
2021-04-27 03:00 | 1.609 | 1.9925 | 2.0242 | 2.1602 | 2.1058 | 2.2418 | 0.96563 | 1.4627 | 1.7415 | 1.7415 | 1.9273 | 1.9273 | 2019-06-24 16:00 | 2.0805 | 3.5702 | 6.0343 | 6.0343 | 6.0343 | 6.0343
2021-04-27 04:00 | 1.7833 | 2.2084 | 2.2435 | 2.3943 | 2.334 | 2.4847 | 0.96596 | 1.4632 | 1.7421 | 1.7421 | 1.928 | 1.928 | 2019-06-24 17:00 | 2.1872 | 3.7533 | 6.3437 | 6.3437 | 6.3437 | 6.3437
2021-04-27 05:00 | 2.1463 | 2.6578 | 2.7001 | 2.8816 | 2.809 | 2.9904 | 1.0717 | 1.6234 | 1.9328 | 1.9328 | 2.139 | 2.139 | 2019-06-24 18:00 | 2.2253 | 3.8187 | 6.4542 | 6.4542 | 6.4542 | 6.4542
2021-04-27 06:00 | 2.9674 | 3.6747 | 3.7332 | 3.9841 | 3.8837 | 4.1346 | 1.2889 | 1.9524 | 2.3245 | 2.3245 | 2.5725 | 2.5725 | 2019-06-24 19:00 | 2.0805 | 3.5702 | 6.0343 | 6.0343 | 6.0343 | 6.0343
2021-04-27 07:00 | 3.2037 | 3.9673 | 4.0304 | 4.3013 | 4.1929 | 4.4637 | 1.6233 | 2.4589 | 2.9275 | 2.9275 | 3.2399 | 3.2399 | 2019-06-24 20:00 | 1.9967 | 3.4264 | 5.7911 | 5.7911 | 5.7911 | 5.7911
2021-04-27 08:00 | 3.3694 | 4.1725 | 4.239 | 4.5238 | 4.4099 | 4.6947 | 1.5232 | 2.3074 | 2.7471 | 2.7471 | 3.0402 | 3.0402 | 2019-06-24 21:00 | 1.7605 | 3.0209 | 5.1059 | 5.1059 | 5.1059 | 5.1059
2021-04-27 09:00 | 2.9265 | 3.624 | 3.6817 | 3.9291 | 3.8301 | 4.0775 | 1.5347 | 2.3247 | 2.7677 | 2.7677 | 3.0631 | 3.0631 | 2019-06-24 22:00 | 1.7528 | 3.0079 | 5.0838 | 5.0838 | 5.0838 | 5.0838
2021-04-27 10:00 | 2.7036 | 3.3479 | 3.4012 | 3.6298 | 3.5384 | 3.7669 | 1.3546 | 2.052 | 2.443 | 2.443 | 2.7037 | 2.7037 | 2019-06-24 23:00 | 1.5699 | 2.694 | 4.5533 | 4.5533 | 4.5533 | 4.5533
2021-04-27 11:00 | 2.4921 | 3.086 | 3.1352 | 3.3458 | 3.2616 | 3.4722 | 1.3918 | 2.1083 | 2.51 | 2.51 | 2.7779 | 2.7779 | 2019-06-25 | 1.448 | 2.4848 | 4.1997 | 4.1997 | 4.1997 | 4.1997
2021-04-27 12:00 | 2.4606 | 3.0471 | 3.0956 | 3.3036 | 3.2204 | 3.4284 | 1.3975 | 2.1169 | 2.5203 | 2.5203 | 2.7893 | 2.7893 | 2019-06-25 01:00 | 1.4099 | 2.4194 | 4.0891 | 4.0891 | 4.0891 | 4.0891
2021-04-27 13:00 | 2.2777 | 2.8206 | 2.8655 | 3.0581 | 2.9811 | 3.1736 | 1.4575 | 2.2079 | 2.6286 | 2.6286 | 2.909 | 2.909 | 2019-06-25 02:00 | 1.3489 | 2.3148 | 3.9123 | 3.9123 | 3.9123 | 3.9123
2021-04-27 14:00 | 2.2349 | 2.7675 | 2.8116 | 3.0005 | 2.925 | 3.1139 | 1.4146 | 2.1429 | 2.5513 | 2.5513 | 2.8235 | 2.8235 | 2019-06-25 03:00 | 1.4327 | 2.4586 | 4.1555 | 4.1555 | 4.1555 | 4.1555
2021-04-27 15:00 | 2.312 | 2.8631 | 2.9087 | 3.1041 | 3.0259 | 3.2214 | 1.3689 | 2.0737 | 2.4688 | 2.4688 | 2.7322 | 2.7322 | 2019-06-25 04:00 | 1.4632 | 2.5109 | 4.2439 | 4.2439 | 4.2439 | 4.2439
2021-04-27 16:00 | 2.3892 | 2.9586 | 3.0058 | 3.2077 | 3.1269 | 3.3289 | 1.6233 | 2.4589 | 2.9275 | 2.9275 | 3.2399 | 3.2399 | 2019-06-25 05:00 | 1.5775 | 2.7071 | 4.5754 | 4.5754 | 4.5754 | 4.5754
2021-04-27 17:00 | 3.0608 | 3.7903 | 3.8507 | 4.1094 | 4.0059 | 4.2647 | 1.8119 | 2.7447 | 3.2677 | 3.2677 | 3.6163 | 3.6163 | 2019-06-25 06:00 | 1.9129 | 3.2825 | 5.548 | 5.548 | 5.548 | 5.548
2021-04-27 18:00 | 3.1865 | 3.946 | 4.0089 | 4.2782 | 4.1705 | 4.4399 | 2.1234 | 3.2165 | 3.8295 | 3.8295 | 4.2381 | 4.2381 | 2019-06-25 07:00 | 2.0729 | 3.5571 | 6.0121 | 6.0121 | 6.0121 | 6.0121
2021-04-27 19:00 | 3.0951 | 3.8328 | 3.8938 | 4.1555 | 4.0508 | 4.3124 | 2.0462 | 3.0997 | 3.6903 | 3.6903 | 4.0841 | 4.0841 | 2019-06-25 08:00 | 2.1034 | 3.6094 | 6.1006 | 6.1006 | 6.1006 | 6.1006
2021-04-27 20:00 | 2.7979 | 3.4647 | 3.5199 | 3.7564 | 3.6618 | 3.8983 | 1.9519 | 2.9568 | 3.5202 | 3.5202 | 3.8958 | 3.8958 | 2019-06-25 09:00 | 2.0805 | 3.5702 | 6.0343 | 6.0343 | 6.0343 | 6.0343
2021-04-27 21:00 | 2.5064 | 3.1037 | 3.1532 | 3.365 | 3.2803 | 3.4922 | 1.8691 | 2.8313 | 3.3708 | 3.3708 | 3.7304 | 3.7304 | 2019-06-25 10:00 | 2.111 | 3.6225 | 6.1227 | 6.1227 | 6.1227 | 6.1227
2021-04-27 22:00 | 2.1663 | 2.6826 | 2.7253 | 2.9084 | 2.8352 | 3.0183 | 1.5884 | 2.4061 | 2.8646 | 2.8646 | 3.1702 | 3.1702 | 2019-06-25 11:00 | 2.111 | 3.6225 | 6.1227 | 6.1227 | 6.1227 | 6.1227
2021-04-27 23:00 | 1.9862 | 2.4596 | 2.4988 | 2.6667 | 2.5995 | 2.7674 | 1.2975 | 1.9654 | 2.3399 | 2.3399 | 2.5896 | 2.5896 | 2019-06-25 12:00 | 2.1339 | 3.6618 | 6.189 | 6.189 | 6.189 | 6.189
2021-04-28 | 1.7233 | 2.134 | 2.168 | 2.3137 | 2.2554 | 2.4011 | 1.0403 | 1.5758 | 1.8761 | 1.8761 | 2.0763 | 2.0763 | 2019-06-25 13:00 | 2.0805 | 3.5702 | 6.0343 | 6.0343 | 6.0343 | 6.0343
2021-04-28 01:00 | 1.5833 | 1.9606 | 1.9918 | 2.1257 | 2.0722 | 2.206 | 0.96025 | 1.4546 | 1.7318 | 1.7318 | 1.9165 | 1.9165 | 2019-06-25 14:00 | 2.1034 | 3.6094 | 6.1006 | 6.1006 | 6.1006 | 6.1006
2021-04-28 02:00 | 1.5375 | 1.904 | 1.9343 | 2.0643 | 2.0123 | 2.1423 | 0.91166 | 1.381 | 1.6441 | 1.6441 | 1.8196 | 1.8196 | 2019-06-25 15:00 | 2.1263 | 3.6487 | 6.1669 | 6.1669 | 6.1669 | 6.1669
2021-04-28 03:00 | 1.5593 | 1.931 | 1.9618 | 2.0936 | 2.0408 | 2.1727 | 0.87313 | 1.3226 | 1.5747 | 1.5747 | 1.7427 | 1.7427 | 2019-06-25 16:00 | 2.1567 | 3.701 | 6.2553 | 6.2553 | 6.2553 | 6.2553
2021-04-28 04:00 | 1.6318 | 2.0208 | 2.053 | 2.1909 | 2.1357 | 2.2737 | 0.97168 | 1.4719 | 1.7524 | 1.7524 | 1.9394 | 1.9394 | 2019-06-25 17:00 | 2.1263 | 3.6487 | 6.1669 | 6.1669 | 6.1669 | 6.1669
2021-04-28 05:00 | 2.024 | 2.5064 | 2.5463 | 2.7174 | 2.649 | 2.8201 | 1.0174 | 1.5412 | 1.8348 | 1.8348 | 2.0306 | 2.0306 | 2019-06-25 18:00 | 2.1339 | 3.6618 | 6.189 | 6.189 | 6.189 | 6.189
2021-04-28 06:00 | 2.5375 | 3.1422 | 3.1923 | 3.4068 | 3.321 | 3.5355 | 1.2689 | 1.9221 | 2.2884 | 2.2884 | 2.5326 | 2.5326 | 2019-06-25 19:00 | 2.0196 | 3.4656 | 5.8574 | 5.8574 | 5.8574 | 5.8574
2021-04-28 07:00 | 2.7064 | 3.3515 | 3.4048 | 3.6336 | 3.5421 | 3.7709 | 1.6804 | 2.5455 | 3.0306 | 3.0306 | 3.354 | 3.354 | 2019-06-25 20:00 | 1.9205 | 3.2956 | 5.5701 | 5.5701 | 5.5701 | 5.5701
2021-04-28 08:00 | 2.7236 | 3.3727 | 3.4264 | 3.6566 | 3.5646 | 3.7948 | 1.5718 | 2.381 | 2.8347 | 2.8347 | 3.1372 | 3.1372 | 2019-06-25 21:00 | 1.8062 | 3.0994 | 5.2385 | 5.2385 | 5.2385 | 5.2385
2021-04-28 09:00 | 2.5835 | 3.1993 | 3.2502 | 3.4686 | 3.3813 | 3.5997 | 1.4375 | 2.1776 | 2.5925 | 2.5925 | 2.8691 | 2.8691 | 2019-06-25 22:00 | 1.7833 | 3.0602 | 5.1722 | 5.1722 | 5.1722 | 5.1722
2021-04-28 10:00 | 2.4835 | 3.0754 | 3.1244 | 3.3343 | 3.2504 | 3.4603 | 1.4004 | 2.1213 | 2.5255 | 2.5255 | 2.795 | 2.795 | 2019-06-25 23:00 | 1.6157 | 2.7725 | 4.6859 | 4.6859 | 4.6859 | 4.6859
2021-04-28 11:00 | 2.3035 | 2.8525 | 2.8979 | 3.0926 | 3.0147 | 3.2094 | 1.4347 | 2.1732 | 2.5873 | 2.5873 | 2.8634 | 2.8634 | 2019-06-26 | 1.4556 | 2.4978 | 4.2218 | 4.2218 | 4.2218 | 4.2218
2021-04-28 12:00 | 2.4378 | 3.0188 | 3.0669 | 3.2729 | 3.1905 | 3.3966 | 1.4118 | 2.1386 | 2.5461 | 2.5461 | 2.8178 | 2.8178 | 2019-06-26 01:00 | 1.4023 | 2.4063 | 4.067 | 4.067 | 4.067 | 4.067
2021-04-28 13:00 | 2.3006 | 2.8489 | 2.8943 | 3.0888 | 3.011 | 3.2055 | 1.4718 | 2.2295 | 2.6543 | 2.6543 | 2.9376 | 2.9376 | 2019-06-26 02:00 | 1.3489 | 2.3148 | 3.9123 | 3.9123 | 3.9123 | 3.9123
2021-04-28 14:00 | 2.312 | 2.8631 | 2.9087 | 3.1041 | 3.0259 | 3.2214 | 1.4689 | 2.2252 | 2.6492 | 2.6492 | 2.9319 | 2.9319 | 2019-06-26 03:00 | 1.3642 | 2.3409 | 3.9565 | 3.9565 | 3.9565 | 3.9565
2021-04-28 15:00 | 2.3035 | 2.8525 | 2.8979 | 3.0926 | 3.0147 | 3.2094 | 1.4404 | 2.1819 | 2.5976 | 2.5976 | 2.8748 | 2.8748 | 2019-06-26 04:00 | 1.4404 | 2.4717 | 4.1776 | 4.1776 | 4.1776 | 4.1776
2021-04-28 16:00 | 2.4235 | 3.0011 | 3.0489 | 3.2538 | 3.1718 | 3.3767 | 1.5147 | 2.2944 | 2.7317 | 2.7317 | 3.0231 | 3.0231 | 2019-06-26 05:00 | 1.6766 | 2.8771 | 4.8628 | 4.8628 | 4.8628 | 4.8628
2021-04-28 17:00 | 2.895 | 3.585 | 3.6421 | 3.8869 | 3.789 | 4.0337 | 1.8348 | 2.7793 | 3.3089 | 3.3089 | 3.662 | 3.662 | 2019-06-26 06:00 | 1.9434 | 3.3348 | 5.6364 | 5.6364 | 5.6364 | 5.6364
2021-04-28 18:00 | 2.9979 | 3.7124 | 3.7716 | 4.025 | 3.9236 | 4.177 | 2.0148 | 3.052 | 3.6336 | 3.6336 | 4.0213 | 4.0213 | 2019-06-26 07:00 | 2.0805 | 3.5702 | 6.0343 | 6.0343 | 6.0343 | 6.0343
2021-04-28 19:00 | 2.9179 | 3.6133 | 3.6709 | 3.9176 | 3.8189 | 4.0656 | 1.9527 | 2.9579 | 3.5216 | 3.5216 | 3.8974 | 3.8974 | 2019-06-26 08:00 | 2.3778 | 4.0802 | 6.8963 | 6.8963 | 6.8963 | 6.8963
2021-04-28 20:00 | 2.7378 | 3.3904 | 3.4444 | 3.6758 | 3.5833 | 3.8147 | 1.9091 | 2.8919 | 3.4429 | 3.4429 | 3.8103 | 3.8103 | 2019-06-26 09:00 | 2.172 | 3.7271 | 6.2995 | 6.2995 | 6.2995 | 6.2995
2021-04-28 21:00 | 2.5264 | 3.1285 | 3.1783 | 3.3919 | 3.3065 | 3.52 | 1.8348 | 2.7793 | 3.3089 | 3.3089 | 3.662 | 3.662 | 2019-06-26 10:00 | 2.0805 | 3.5702 | 6.0343 | 6.0343 | 6.0343 | 6.0343
2021-04-28 22:00 | 2.2377 | 2.7711 | 2.8152 | 3.0044 | 2.9287 | 3.1179 | 1.5976 | 2.42 | 2.8811 | 2.8811 | 3.1885 | 3.1885 | 2019-06-26 11:00 | 2.0729 | 3.5571 | 6.0121 | 6.0121 | 6.0121 | 6.0121
2021-04-28 23:00 | 2.0984 | 2.5985 | 2.6399 | 2.8173 | 2.7463 | 2.9237 | 1.3215 | 2.0018 | 2.3833 | 2.3833 | 2.6376 | 2.6376 | 2019-06-26 12:00 | 2.0805 | 3.5702 | 6.0343 | 6.0343 | 6.0343 | 6.0343
2021-04-29 | 1.789 | 2.2154 | 2.2507 | 2.4019 | 2.3415 | 2.4927 | 1.0721 | 1.624 | 1.9334 | 1.9334 | 2.1397 | 2.1397 | 2019-06-26 13:00 | 2.0805 | 3.5702 | 6.0343 | 6.0343 | 6.0343 | 6.0343
2021-04-29 01:00 | 1.7233 | 2.134 | 2.168 | 2.3137 | 2.2554 | 2.4011 | 0.98597 | 1.4935 | 1.7781 | 1.7781 | 1.9679 | 1.9679 | 2019-06-26 14:00 | 2.0805 | 3.5702 | 6.0343 | 6.0343 | 6.0343 | 6.0343
2021-04-29 02:00 | 1.6376 | 2.0279 | 2.0602 | 2.1986 | 2.1432 | 2.2816 | 0.91166 | 1.381 | 1.6441 | 1.6441 | 1.8196 | 1.8196 | 2019-06-26 15:00 | 2.0805 | 3.5702 | 6.0343 | 6.0343 | 6.0343 | 6.0343
2021-04-29 03:00 | 1.6804 | 2.0809 | 2.1141 | 2.2561 | 2.1993 | 2.3414 | 0.88308 | 1.3377 | 1.5926 | 1.5926 | 1.7625 | 1.7625 | 2019-06-26 16:00 | 2.0882 | 3.5833 | 6.0564 | 6.0564 | 6.0564 | 6.0564
2021-04-29 04:00 | 1.7633 | 2.1836 | 2.2184 | 2.3674 | 2.3078 | 2.4569 | 0.92881 | 1.407 | 1.6751 | 1.6751 | 1.8538 | 1.8538 | 2019-06-26 17:00 | 2.172 | 3.7271 | 6.2995 | 6.2995 | 6.2995 | 6.2995
2021-04-29 05:00 | 2.1491 | 2.6613 | 2.7037 | 2.8854 | 2.8127 | 2.9944 | 1.066 | 1.6148 | 1.9225 | 1.9225 | 2.1276 | 2.1276 | 2019-06-26 18:00 | 2.172 | 3.7271 | 6.2995 | 6.2995 | 6.2995 | 6.2995
2021-04-29 06:00 | 2.715 | 3.3621 | 3.4156 | 3.6451 | 3.5533 | 3.7828 | 1.288 | 1.9511 | 2.3229 | 2.3229 | 2.5708 | 2.5708 | 2019-06-26 19:00 | 2.0424 | 3.5048 | 5.9237 | 5.9237 | 5.9237 | 5.9237
2021-04-29 07:00 | 2.9493 | 3.6523 | 3.7105 | 3.9598 | 3.86 | 4.1094 | 1.6947 | 2.5672 | 3.0564 | 3.0564 | 3.3825 | 3.3825 | 2019-06-26 20:00 | 1.8824 | 3.2302 | 5.4596 | 5.4596 | 5.4596 | 5.4596
2021-04-29 08:00 | 3.0408 | 3.7655 | 3.8255 | 4.0826 | 3.9797 | 4.2368 | 1.6861 | 2.5542 | 3.0409 | 3.0409 | 3.3654 | 3.3654 | 2019-06-26 21:00 | 1.7681 | 3.034 | 5.128 | 5.128 | 5.128 | 5.128
2021-04-29 09:00 | 2.7383 | 3.3909 | 3.4449 | 3.6764 | 3.5838 | 3.8153 | 1.5004 | 2.2728 | 2.7059 | 2.7059 | 2.9946 | 2.9946 | 2019-06-26 22:00 | 1.7528 | 3.0079 | 5.0838 | 5.0838 | 5.0838 | 5.0838
2021-04-29 10:00 | 2.6835 | 3.3231 | 3.3761 | 3.6029 | 3.5122 | 3.739 | 1.4118 | 2.1386 | 2.5461 | 2.5461 | 2.8178 | 2.8178 | 2019-06-26 23:00 | 1.5928 | 2.7332 | 4.6196 | 4.6196 | 4.6196 | 4.6196
2021-04-29 11:00 | 2.3978 | 2.9692 | 3.0165 | 3.2192 | 3.1382 | 3.3408 | 1.4632 | 2.2165 | 2.6389 | 2.6389 | 2.9205 | 2.9205 | 2019-06-27 | 1.448 | 2.4848 | 4.1997 | 4.1997 | 4.1997 | 4.1997
2021-04-29 12:00 | 2.3635 | 2.9268 | 2.9734 | 3.1732 | 3.0933 | 3.2931 | 1.4232 | 2.1559 | 2.5667 | 2.5667 | 2.8406 | 2.8406 | 2019-06-27 01:00 | 1.4099 | 2.4194 | 4.0891 | 4.0891 | 4.0891 | 4.0891
2021-04-29 13:00 | 2.2453 | 2.7804 | 2.8247 | 3.0145 | 2.9386 | 3.1284 | 1.4175 | 2.1472 | 2.5564 | 2.5564 | 2.8292 | 2.8292 | 2019-06-27 02:00 | 1.3642 | 2.3409 | 3.9565 | 3.9565 | 3.9565 | 3.9565
2021-04-29 14:00 | 2.2749 | 2.8171 | 2.8619 | 3.0542 | 2.9773 | 3.1696 | 1.3861 | 2.0996 | 2.4997 | 2.4997 | 2.7664 | 2.7664 | 2019-06-27 03:00 | 1.3946 | 2.3932 | 4.0449 | 4.0449 | 4.0449 | 4.0449
2021-04-29 15:00 | 2.2377 | 2.7711 | 2.8152 | 3.0044 | 2.9287 | 3.1179 | 1.4175 | 2.1472 | 2.5564 | 2.5564 | 2.8292 | 2.8292 | 2019-06-27 04:00 | 1.4861 | 2.5501 | 4.3102 | 4.3102 | 4.3102 | 4.3102
2021-04-29 16:00 | 2.5064 | 3.1037 | 3.1532 | 3.365 | 3.2803 | 3.4922 | 1.5232 | 2.3074 | 2.7471 | 2.7471 | 3.0402 | 3.0402 | 2019-06-27 05:00 | 1.7376 | 2.9817 | 5.0396 | 5.0396 | 5.0396 | 5.0396
2021-04-29 17:00 | 2.895 | 3.585 | 3.6421 | 3.8869 | 3.789 | 4.0337 | 1.6376 | 2.4806 | 2.9533 | 2.9533 | 3.2684 | 3.2684 | 2019-06-27 06:00 | 1.9205 | 3.2956 | 5.5701 | 5.5701 | 5.5701 | 5.5701
2021-04-29 18:00 | 3.0694 | 3.8009 | 3.8615 | 4.1209 | 4.0171 | 4.2766 | 1.8662 | 2.8269 | 3.3656 | 3.3656 | 3.7247 | 3.7247 | 2019-06-27 07:00 | 2.1491 | 3.6879 | 6.2332 | 6.2332 | 6.2332 | 6.2332
2021-04-29 19:00 | 3.0233 | 3.7438 | 3.8035 | 4.059 | 3.9568 | 4.2124 | 1.8862 | 2.8572 | 3.4017 | 3.4017 | 3.7647 | 3.7647 | 2019-06-27 08:00 | 2.2101 | 3.7925 | 6.41 | 6.41 | 6.41 | 6.41
2021-04-29 20:00 | 2.7293 | 3.3798 | 3.4336 | 3.6643 | 3.572 | 3.8027 | 1.9062 | 2.8875 | 3.4378 | 3.4378 | 3.8046 | 3.8046 | 2019-06-27 09:00 | 2.0882 | 3.5833 | 6.0564 | 6.0564 | 6.0564 | 6.0564
2021-04-29 21:00 | 2.4414 | 3.0233 | 3.0714 | 3.2778 | 3.1953 | 3.4016 | 1.8462 | 2.7966 | 3.3295 | 3.3295 | 3.6848 | 3.6848 | 2019-06-27 10:00 | 2.1263 | 3.6487 | 6.1669 | 6.1669 | 6.1669 | 6.1669
2021-04-29 22:00 | 2.1949 | 2.718 | 2.7613 | 2.9468 | 2.8726 | 3.0581 | 1.5718 | 2.381 | 2.8347 | 2.8347 | 3.1372 | 3.1372 | 2019-06-27 11:00 | 2.1339 | 3.6618 | 6.189 | 6.189 | 6.189 | 6.189
2021-04-29 23:00 | 1.9526 | 2.418 | 2.4565 | 2.6216 | 2.5555 | 2.7206 | 1.3076 | 1.9808 | 2.3582 | 2.3582 | 2.6098 | 2.6098 | 2019-06-27 12:00 | 2.1415 | 3.6748 | 6.2111 | 6.2111 | 6.2111 | 6.2111
2021-04-30 | 1.769 | 2.1907 | 2.2255 | 2.3751 | 2.3153 | 2.4648 | 1.0831 | 1.6407 | 1.9534 | 1.9534 | 2.1618 | 2.1618 | 2019-06-27 13:00 | 2.0653 | 3.5441 | 5.99 | 5.99 | 5.99 | 5.99
2021-04-30 01:00 | 1.6794 | 2.0796 | 2.1127 | 2.2547 | 2.1979 | 2.3399 | 0.9631 | 1.4589 | 1.7369 | 1.7369 | 1.9223 | 1.9223 | 2019-06-27 14:00 | 2.0653 | 3.5441 | 5.99 | 5.99 | 5.99 | 5.99
2021-04-30 02:00 | 1.6461 | 2.0385 | 2.0709 | 2.2101 | 2.1544 | 2.2936 | 0.89187 | 1.351 | 1.6084 | 1.6084 | 1.7801 | 1.7801 | 2019-06-27 15:00 | 2.0882 | 3.5833 | 6.0564 | 6.0564 | 6.0564 | 6.0564
2021-04-30 03:00 | 1.6347 | 2.0243 | 2.0566 | 2.1948 | 2.1395 | 2.2777 | 0.88022 | 1.3334 | 1.5874 | 1.5874 | 1.7568 | 1.7568 | 2019-06-27 16:00 | 2.172 | 3.7271 | 6.2995 | 6.2995 | 6.2995 | 6.2995
2021-04-30 04:00 | 1.8176 | 2.2508 | 2.2867 | 2.4403 | 2.3789 | 2.5325 | 0.93738 | 1.42 | 1.6905 | 1.6905 | 1.8709 | 1.8709 | 2019-06-27 17:00 | 2.1263 | 3.6487 | 6.1669 | 6.1669 | 6.1669 | 6.1669
2021-04-30 05:00 | 2.0567 | 2.5469 | 2.5875 | 2.7613 | 2.6918 | 2.8657 | 1.0888 | 1.6494 | 1.9637 | 1.9637 | 2.1732 | 2.1732 | 2019-06-27 18:00 | 2.0805 | 3.5702 | 6.0343 | 6.0343 | 6.0343 | 6.0343
2021-04-30 06:00 | 2.755 | 3.4116 | 3.466 | 3.6989 | 3.6057 | 3.8386 | 1.2775 | 1.9351 | 2.3039 | 2.3039 | 2.5497 | 2.5497 | 2019-06-27 19:00 | 2.0805 | 3.5702 | 6.0343 | 6.0343 | 6.0343 | 6.0343
2021-04-30 07:00 | 2.9836 | 3.6947 | 3.7536 | 4.0058 | 3.9049 | 4.1571 | 1.6604 | 2.5152 | 2.9945 | 2.9945 | 3.314 | 3.314 | 2019-06-27 20:00 | 1.9205 | 3.2956 | 5.5701 | 5.5701 | 5.5701 | 5.5701
2021-04-30 08:00 | 2.9808 | 3.6912 | 3.75 | 4.002 | 3.9012 | 4.1532 | 1.5175 | 2.2988 | 2.7368 | 2.7368 | 3.0288 | 3.0288 | 2019-06-27 21:00 | 1.7833 | 3.0602 | 5.1722 | 5.1722 | 5.1722 | 5.1722
2021-04-30 09:00 | 2.6435 | 3.2736 | 3.3257 | 3.5492 | 3.4598 | 3.6833 | 1.4918 | 2.2598 | 2.6904 | 2.6904 | 2.9775 | 2.9775 | 2019-06-27 22:00 | 1.829 | 3.1386 | 5.3048 | 5.3048 | 5.3048 | 5.3048
2021-04-30 10:00 | 2.5521 | 3.1604 | 3.2107 | 3.4264 | 3.3401 | 3.5559 | 1.489 | 2.2555 | 2.6853 | 2.6853 | 2.9718 | 2.9718 | 2019-06-27 23:00 | 1.6385 | 2.8117 | 4.7522 | 4.7522 | 4.7522 | 4.7522
2021-04-30 11:00 | 2.4406 | 3.0223 | 3.0705 | 3.2768 | 3.1943 | 3.4006 | 1.5004 | 2.2728 | 2.7059 | 2.7059 | 2.9946 | 2.9946 | 2019-06-28 | 1.4709 | 2.524 | 4.266 | 4.266 | 4.266 | 4.266
2021-04-30 12:00 | 2.3463 | 2.9055 | 2.9518 | 3.1502 | 3.0708 | 3.2692 | 1.4204 | 2.1516 | 2.5616 | 2.5616 | 2.8349 | 2.8349 | 2019-06-28 01:00 | 1.4099 | 2.4194 | 4.0891 | 4.0891 | 4.0891 | 4.0891
2021-04-30 13:00 | 2.4006 | 2.9728 | 3.0201 | 3.2231 | 3.1419 | 3.3448 | 1.4947 | 2.2641 | 2.6956 | 2.6956 | 2.9832 | 2.9832 | 2019-06-28 02:00 | 1.4785 | 2.5371 | 4.2881 | 4.2881 | 4.2881 | 4.2881
2021-04-30 14:00 | 2.2406 | 2.7746 | 2.8188 | 3.0082 | 2.9324 | 3.1218 | 1.4318 | 2.1689 | 2.5822 | 2.5822 | 2.8577 | 2.8577 | 2019-06-28 03:00 | 1.3337 | 2.2886 | 3.8681 | 3.8681 | 3.8681 | 3.8681
2021-04-30 15:00 | 2.1634 | 2.679 | 2.7217 | 2.9046 | 2.8314 | 3.0143 | 1.3946 | 2.1126 | 2.5152 | 2.5152 | 2.7836 | 2.7836 | 2019-06-28 04:00 | 1.4404 | 2.4717 | 4.1776 | 4.1776 | 4.1776 | 4.1776
2021-04-30 16:00 | 2.2263 | 2.7569 | 2.8008 | 2.989 | 2.9137 | 3.1019 | 1.5775 | 2.3897 | 2.845 | 2.845 | 3.1486 | 3.1486 | 2019-06-28 05:00 | 1.6766 | 2.8771 | 4.8628 | 4.8628 | 4.8628 | 4.8628
2021-04-30 17:00 | 2.5892 | 3.2064 | 3.2574 | 3.4763 | 3.3888 | 3.6076 | 1.8762 | 2.842 | 3.3836 | 3.3836 | 3.7447 | 3.7447 | 2019-06-28 06:00 | 1.8824 | 3.2302 | 5.4596 | 5.4596 | 5.4596 | 5.4596
2021-04-30 18:00 | 2.675 | 3.3125 | 3.3653 | 3.5914 | 3.501 | 3.7271 | 1.9834 | 3.0044 | 3.5769 | 3.5769 | 3.9586 | 3.9586 | 2019-06-28 07:00 | 2.1567 | 3.701 | 6.2553 | 6.2553 | 6.2553 | 6.2553
2021-04-30 19:00 | 2.5175 | 3.1175 | 3.1671 | 3.3799 | 3.2948 | 3.5076 | 1.9834 | 3.0044 | 3.5769 | 3.5769 | 3.9586 | 3.9586 | 2019-06-28 08:00 | 2.1644 | 3.7141 | 6.2774 | 6.2774 | 6.2774 | 6.2774
2021-04-30 20:00 | 2.4524 | 3.0369 | 3.0853 | 3.2926 | 3.2097 | 3.417 | 1.9205 | 2.9092 | 3.4635 | 3.4635 | 3.8331 | 3.8331 | 2019-06-28 09:00 | 2.233 | 3.8318 | 6.4763 | 6.4763 | 6.4763 | 6.4763
2021-04-30 21:00 | 2.1949 | 2.718 | 2.7613 | 2.9468 | 2.8726 | 3.0581 | 1.8719 | 2.8356 | 3.3759 | 3.3759 | 3.7361 | 3.7361 | 2019-06-28 10:00 | 2.0424 | 3.5048 | 5.9237 | 5.9237 | 5.9237 | 5.9237
2021-04-30 22:00 | 1.9614 | 2.4289 | 2.4676 | 2.6334 | 2.5671 | 2.7329 | 1.5633 | 2.368 | 2.8193 | 2.8193 | 3.1201 | 3.1201 | 2019-06-28 11:00 | 1.9662 | 3.374 | 5.7027 | 5.7027 | 5.7027 | 5.7027
2021-04-30 23:00 | 1.9156 | 2.3721 | 2.4099 | 2.5719 | 2.5071 | 2.669 | 1.3957 | 2.1141 | 2.517 | 2.517 | 2.7856 | 2.7856 | 2019-06-28 12:00 | 2.0272 | 3.4787 | 5.8795 | 5.8795 | 5.8795 | 5.8795
2021-05-01 | 1.6531 | 2.0471 | 2.0797 | 2.2195 | 2.1636 | 2.3033 | 1.1433 | 1.7318 | 2.0618 | 2.0618 | 2.2818 | 2.2818 | 2019-06-28 13:00 | 2.0119 | 3.4525 | 5.8353 | 5.8353 | 5.8353 | 5.8353
2021-05-01 01:00 | 1.5718 | 1.9465 | 1.9775 | 2.1103 | 2.0572 | 2.1901 | 0.92309 | 1.3983 | 1.6648 | 1.6648 | 1.8424 | 1.8424 | 2019-06-28 14:00 | 2.0119 | 3.4525 | 5.8353 | 5.8353 | 5.8353 | 5.8353
2021-05-01 02:00 | 1.5433 | 1.9111 | 1.9415 | 2.072 | 2.0198 | 2.1502 | 0.88022 | 1.3334 | 1.5874 | 1.5874 | 1.7568 | 1.7568 | 2019-06-28 15:00 | 2.0272 | 3.4787 | 5.8795 | 5.8795 | 5.8795 | 5.8795
2021-05-01 03:00 | 1.5175 | 1.8792 | 1.9092 | 2.0374 | 1.9861 | 2.1144 | 0.87737 | 1.329 | 1.5823 | 1.5823 | 1.7511 | 1.7511 | 2019-06-28 16:00 | 2.0577 | 3.531 | 5.9679 | 5.9679 | 5.9679 | 5.9679
2021-05-01 04:00 | 1.5261 | 1.8898 | 1.9199 | 2.0489 | 1.9973 | 2.1264 | 0.86879 | 1.3161 | 1.5668 | 1.5668 | 1.734 | 1.734 | 2019-06-28 17:00 | 2.1339 | 3.6618 | 6.189 | 6.189 | 6.189 | 6.189
2021-05-01 05:00 | 1.6511 | 2.0446 | 2.0771 | 2.2167 | 2.1609 | 2.3004 | 0.91578 | 1.3872 | 1.6516 | 1.6516 | 1.8278 | 1.8278 | 2019-06-28 18:00 | 2.0805 | 3.5702 | 6.0343 | 6.0343 | 6.0343 | 6.0343
2021-05-01 06:00 | 1.8433 | 2.2827 | 2.319 | 2.4749 | 2.4125 | 2.5683 | 1.1127 | 1.6855 | 2.0067 | 2.0067 | 2.2208 | 2.2208 | 2019-06-28 19:00 | 1.9815 | 3.4002 | 5.7469 | 5.7469 | 5.7469 | 5.7469
2021-05-01 07:00 | 2.0748 | 2.5693 | 2.6103 | 2.7856 | 2.7155 | 2.8909 | 1.226 | 1.8572 | 2.2111 | 2.2111 | 2.447 | 2.447 | 2019-06-28 20:00 | 1.8367 | 3.1517 | 5.3269 | 5.3269 | 5.3269 | 5.3269
2021-05-01 08:00 | 2.0834 | 2.58 | 2.621 | 2.7972 | 2.7267 | 2.9028 | 1.4032 | 2.1256 | 2.5306 | 2.5306 | 2.8007 | 2.8007 | 2019-06-28 21:00 | 1.8062 | 3.0994 | 5.2385 | 5.2385 | 5.2385 | 5.2385
2021-05-01 09:00 | 2.0548 | 2.5446 | 2.5851 | 2.7588 | 2.6893 | 2.863 | 1.4832 | 2.2468 | 2.675 | 2.675 | 2.9604 | 2.9604 | 2019-06-28 22:00 | 1.829 | 3.1386 | 5.3048 | 5.3048 | 5.3048 | 5.3048
2021-05-01 10:00 | 1.9091 | 2.3641 | 2.4017 | 2.5631 | 2.4986 | 2.6599 | 1.5775 | 2.3897 | 2.845 | 2.845 | 3.1486 | 3.1486 | 2019-06-28 23:00 | 1.6538 | 2.8379 | 4.7965 | 4.7965 | 4.7965 | 4.7965
2021-05-01 11:00 | 1.7519 | 2.1694 | 2.204 | 2.3521 | 2.2928 | 2.4409 | 1.6519 | 2.5022 | 2.979 | 2.979 | 3.2969 | 3.2969 | 2019-06-29 | 1.448 | 2.4848 | 4.1997 | 4.1997 | 4.1997 | 4.1997
2021-05-01 12:00 | 1.7262 | 2.1376 | 2.1716 | 2.3175 | 2.2592 | 2.4051 | 1.6176 | 2.4503 | 2.9172 | 2.9172 | 3.2285 | 3.2285 | 2019-06-29 01:00 | 1.4251 | 2.4455 | 4.1333 | 4.1333 | 4.1333 | 4.1333
2021-05-01 13:00 | 1.6147 | 1.9995 | 2.0314 | 2.1679 | 2.1133 | 2.2498 | 1.5547 | 2.355 | 2.8038 | 2.8038 | 3.103 | 3.103 | 2019-06-29 02:00 | 1.3642 | 2.3409 | 3.9565 | 3.9565 | 3.9565 | 3.9565
2021-05-01 14:00 | 1.7062 | 2.1128 | 2.1465 | 2.2907 | 2.233 | 2.3772 | 1.6004 | 2.4243 | 2.8863 | 2.8863 | 3.1942 | 3.1942 | 2019-06-29 03:00 | 1.3642 | 2.3409 | 3.9565 | 3.9565 | 3.9565 | 3.9565
2021-05-01 15:00 | 1.6815 | 2.0823 | 2.1155 | 2.2576 | 2.2008 | 2.3429 | 1.609 | 2.4373 | 2.9017 | 2.9017 | 3.2114 | 3.2114 | 2019-06-29 04:00 | 1.448 | 2.4848 | 4.1997 | 4.1997 | 4.1997 | 4.1997
2021-05-01 16:00 | 1.8348 | 2.2721 | 2.3082 | 2.4633 | 2.4013 | 2.5564 | 1.5833 | 2.3983 | 2.8554 | 2.8554 | 3.16 | 3.16 | 2019-06-29 05:00 | 1.5699 | 2.694 | 4.5533 | 4.5533 | 4.5533 | 4.5533
2021-05-01 17:00 | 2.2977 | 2.8454 | 2.8907 | 3.0849 | 3.0072 | 3.2015 | 1.8005 | 2.7274 | 3.2471 | 3.2471 | 3.5935 | 3.5935 | 2019-06-29 06:00 | 1.73 | 2.9686 | 5.0175 | 5.0175 | 5.0175 | 5.0175
2021-05-01 18:00 | 2.312 | 2.8631 | 2.9087 | 3.1041 | 3.0259 | 3.2214 | 1.9062 | 2.8875 | 3.4378 | 3.4378 | 3.8046 | 3.8046 | 2019-06-29 07:00 | 1.7528 | 3.0079 | 5.0838 | 5.0838 | 5.0838 | 5.0838
2021-05-01 19:00 | 2.2517 | 2.7883 | 2.8327 | 3.0231 | 2.947 | 3.1373 | 1.8148 | 2.749 | 3.2728 | 3.2728 | 3.6221 | 3.6221 | 2019-06-29 08:00 | 2.0501 | 3.5179 | 5.9458 | 5.9458 | 5.9458 | 5.9458
2021-05-01 20:00 | 2.0548 | 2.5446 | 2.5851 | 2.7588 | 2.6893 | 2.863 | 1.789 | 2.71 | 3.2264 | 3.2264 | 3.5707 | 3.5707 | 2019-06-29 09:00 | 2.1263 | 3.6487 | 6.1669 | 6.1669 | 6.1669 | 6.1669
2021-05-01 21:00 | 1.9862 | 2.4596 | 2.4988 | 2.6667 | 2.5995 | 2.7674 | 1.6433 | 2.4893 | 2.9636 | 2.9636 | 3.2798 | 3.2798 | 2019-06-29 10:00 | 2.0729 | 3.5571 | 6.0121 | 6.0121 | 6.0121 | 6.0121
2021-05-01 22:00 | 1.9548 | 2.4207 | 2.4593 | 2.6245 | 2.5584 | 2.7236 | 1.529 | 2.3161 | 2.7574 | 2.7574 | 3.0516 | 3.0516 | 2019-06-29 11:00 | 2.1263 | 3.6487 | 6.1669 | 6.1669 | 6.1669 | 6.1669
2021-05-01 23:00 | 1.8734 | 2.3199 | 2.3569 | 2.5152 | 2.4519 | 2.6103 | 1.3537 | 2.0505 | 2.4413 | 2.4413 | 2.7018 | 2.7018 | 2019-06-29 12:00 | 2.1567 | 3.701 | 6.2553 | 6.2553 | 6.2553 | 6.2553
2021-05-02 | 1.5976 | 1.9783 | 2.0098 | 2.1449 | 2.0909 | 2.2259 | 1.0779 | 1.6328 | 1.9439 | 1.9439 | 2.1513 | 2.1513 | 2019-06-29 13:00 | 2.0729 | 3.5571 | 6.0121 | 6.0121 | 6.0121 | 6.0121
2021-05-02 01:00 | 1.529 | 1.8934 | 1.9235 | 2.0528 | 2.0011 | 2.1303 | 1.0145 | 1.5368 | 1.8297 | 1.8297 | 2.0249 | 2.0249 | 2019-06-29 14:00 | 2.0424 | 3.5048 | 5.9237 | 5.9237 | 5.9237 | 5.9237
2021-05-02 02:00 | 1.4861 | 1.8403 | 1.8696 | 1.9952 | 1.945 | 2.0706 | 0.91314 | 1.3832 | 1.6468 | 1.6468 | 1.8225 | 1.8225 | 2019-06-29 15:00 | 2.0958 | 3.5964 | 6.0785 | 6.0785 | 6.0785 | 6.0785
2021-05-02 03:00 | 1.4632 | 1.812 | 1.8408 | 1.9645 | 1.9151 | 2.0387 | 0.84307 | 1.2771 | 1.5204 | 1.5204 | 1.6827 | 1.6827 | 2019-06-29 16:00 | 2.111 | 3.6225 | 6.1227 | 6.1227 | 6.1227 | 6.1227
2021-05-02 04:00 | 1.4747 | 1.8261 | 1.8552 | 1.9799 | 1.93 | 2.0547 | 0.80912 | 1.2257 | 1.4592 | 1.4592 | 1.6149 | 1.6149 | 2019-06-29 17:00 | 2.172 | 3.7271 | 6.2995 | 6.2995 | 6.2995 | 6.2995
2021-05-02 05:00 | 1.579 | 1.9554 | 1.9865 | 2.12 | 2.0666 | 2.2001 | 0.8888 | 1.3464 | 1.6029 | 1.6029 | 1.7739 | 1.7739 | 2019-06-29 18:00 | 1.9434 | 3.3348 | 5.6364 | 5.6364 | 5.6364 | 5.6364
2021-05-02 06:00 | 1.7147 | 2.1234 | 2.1572 | 2.3022 | 2.2442 | 2.3892 | 1.0031 | 1.5195 | 1.8091 | 1.8091 | 2.0021 | 2.0021 | 2019-06-29 19:00 | 1.8062 | 3.0994 | 5.2385 | 5.2385 | 5.2385 | 5.2385
2021-05-02 07:00 | 1.8332 | 2.2701 | 2.3062 | 2.4612 | 2.3992 | 2.5542 | 1.0974 | 1.6624 | 1.9792 | 1.9792 | 2.1903 | 2.1903 | 2019-06-29 20:00 | 1.7605 | 3.0209 | 5.1059 | 5.1059 | 5.1059 | 5.1059
2021-05-02 08:00 | 2.0005 | 2.4773 | 2.5168 | 2.6859 | 2.6182 | 2.7874 | 1.2346 | 1.8702 | 2.2266 | 2.2266 | 2.4641 | 2.4641 | 2019-06-29 21:00 | 1.8138 | 3.1125 | 5.2606 | 5.2606 | 5.2606 | 5.2606
2021-05-02 09:00 | 1.8862 | 2.3358 | 2.373 | 2.5324 | 2.4686 | 2.6281 | 1.4061 | 2.1299 | 2.5358 | 2.5358 | 2.8064 | 2.8064 | 2019-06-29 22:00 | 1.6233 | 2.7855 | 4.708 | 4.708 | 4.708 | 4.708
2021-05-02 10:00 | 1.8776 | 2.3251 | 2.3622 | 2.5209 | 2.4574 | 2.6161 | 1.6261 | 2.4633 | 2.9327 | 2.9327 | 3.2456 | 3.2456 | 2019-06-29 23:00 | 1.5699 | 2.694 | 4.5533 | 4.5533 | 4.5533 | 4.5533
2021-05-02 11:00 | 1.709 | 2.1163 | 2.15 | 2.2945 | 2.2367 | 2.3812 | 1.6061 | 2.433 | 2.8966 | 2.8966 | 3.2057 | 3.2057 | 2019-06-30 | 1.4861 | 2.5501 | 4.3102 | 4.3102 | 4.3102 | 4.3102
2021-05-02 12:00 | 1.6261 | 2.0137 | 2.0458 | 2.1832 | 2.1283 | 2.2657 | 1.6233 | 2.4589 | 2.9275 | 2.9275 | 3.2399 | 3.2399 | 2019-06-30 01:00 | 1.4175 | 2.4324 | 4.1112 | 4.1112 | 4.1112 | 4.1112
2021-05-02 13:00 | 1.6033 | 1.9854 | 2.017 | 2.1525 | 2.0983 | 2.2339 | 1.6147 | 2.446 | 2.912 | 2.912 | 3.2228 | 3.2228 | 2019-06-30 02:00 | 1.3718 | 2.354 | 3.9786 | 3.9786 | 3.9786 | 3.9786
2021-05-02 14:00 | 1.5404 | 1.9075 | 1.9379 | 2.0681 | 2.016 | 2.1463 | 1.6147 | 2.446 | 2.912 | 2.912 | 3.2228 | 3.2228 | 2019-06-30 03:00 | 1.3794 | 2.3671 | 4.0007 | 4.0007 | 4.0007 | 4.0007
2021-05-02 15:00 | 1.5568 | 1.9279 | 1.9586 | 2.0902 | 2.0375 | 2.1692 | 1.5318 | 2.3204 | 2.7626 | 2.7626 | 3.0574 | 3.0574 | 2019-06-30 04:00 | 1.4251 | 2.4455 | 4.1333 | 4.1333 | 4.1333 | 4.1333
2021-05-02 16:00 | 1.8088 | 2.2399 | 2.2756 | 2.4285 | 2.3673 | 2.5202 | 1.6404 | 2.4849 | 2.9584 | 2.9584 | 3.2741 | 3.2741 | 2019-06-30 05:00 | 1.4785 | 2.5371 | 4.2881 | 4.2881 | 4.2881 | 4.2881
2021-05-02 17:00 | 2.293 | 2.8395 | 2.8848 | 3.0786 | 3.0011 | 3.1949 | 1.8745 | 2.8395 | 3.3806 | 3.3806 | 3.7413 | 3.7413 | 2019-06-30 06:00 | 1.6538 | 2.8379 | 4.7965 | 4.7965 | 4.7965 | 4.7965
2021-05-02 18:00 | 2.3778 | 2.9445 | 2.9914 | 3.1924 | 3.112 | 3.313 | 1.9491 | 2.9525 | 3.5151 | 3.5151 | 3.8901 | 3.8901 | 2019-06-30 07:00 | 1.7147 | 2.9425 | 4.9733 | 4.9733 | 4.9733 | 4.9733
2021-05-02 19:00 | 2.2977 | 2.8454 | 2.8907 | 3.0849 | 3.0072 | 3.2015 | 1.9005 | 2.8789 | 3.4275 | 3.4275 | 3.7932 | 3.7932 | 2019-06-30 08:00 | 1.9815 | 3.4002 | 5.7469 | 5.7469 | 5.7469 | 5.7469
2021-05-02 20:00 | 2.2034 | 2.7286 | 2.7721 | 2.9583 | 2.8838 | 3.0701 | 1.8233 | 2.762 | 3.2883 | 3.2883 | 3.6392 | 3.6392 | 2019-06-30 09:00 | 2.0196 | 3.4656 | 5.8574 | 5.8574 | 5.8574 | 5.8574
2021-05-02 21:00 | 2.052 | 2.541 | 2.5815 | 2.755 | 2.6856 | 2.859 | 1.609 | 2.4373 | 2.9017 | 2.9017 | 3.2114 | 3.2114 | 2019-06-30 10:00 | 2.0424 | 3.5048 | 5.9237 | 5.9237 | 5.9237 | 5.9237
2021-05-02 22:00 | 1.8805 | 2.3287 | 2.3658 | 2.5247 | 2.4611 | 2.6201 | 1.4004 | 2.1213 | 2.5255 | 2.5255 | 2.795 | 2.795 | 2019-06-30 11:00 | 2.0043 | 3.4394 | 5.8132 | 5.8132 | 5.8132 | 5.8132
2021-05-02 23:00 | 1.7693 | 2.191 | 2.2259 | 2.3754 | 2.3156 | 2.4652 | 1.2117 | 1.8356 | 2.1853 | 2.1853 | 2.4185 | 2.4185 | 2019-06-30 12:00 | 1.9815 | 3.4002 | 5.7469 | 5.7469 | 5.7469 | 5.7469
2021-05-03 | 1.534 | 1.8997 | 1.9299 | 2.0596 | 2.0077 | 2.1374 | 1.1068 | 1.6766 | 1.9961 | 1.9961 | 2.2091 | 2.2091 | 2019-06-30 13:00 | 2.0043 | 3.4394 | 5.8132 | 5.8132 | 5.8132 | 5.8132
2021-05-03 01:00 | 1.5347 | 1.9005 | 1.9307 | 2.0605 | 2.0086 | 2.1383 | 0.91738 | 1.3896 | 1.6545 | 1.6545 | 1.831 | 1.831 | 2019-06-30 14:00 | 1.9967 | 3.4264 | 5.7911 | 5.7911 | 5.7911 | 5.7911
2021-05-03 02:00 | 1.4461 | 1.7907 | 1.8193 | 1.9415 | 1.8926 | 2.0149 | 0.82878 | 1.2554 | 1.4947 | 1.4947 | 1.6542 | 1.6542 | 2019-06-30 15:00 | 2.0501 | 3.5179 | 5.9458 | 5.9458 | 5.9458 | 5.9458
2021-05-03 03:00 | 1.4347 | 1.7766 | 1.8049 | 1.9262 | 1.8777 | 1.9989 | 0.82759 | 1.2536 | 1.4925 | 1.4925 | 1.6518 | 1.6518 | 2019-06-30 16:00 | 2.0577 | 3.531 | 5.9679 | 5.9679 | 5.9679 | 5.9679
2021-05-03 04:00 | 1.5061 | 1.8651 | 1.8948 | 2.0221 | 1.9712 | 2.0985 | 0.89166 | 1.3507 | 1.6081 | 1.6081 | 1.7796 | 1.7796 | 2019-06-30 17:00 | 2.0729 | 3.5571 | 6.0121 | 6.0121 | 6.0121 | 6.0121
2021-05-03 05:00 | 1.829 | 2.265 | 2.3011 | 2.4557 | 2.3938 | 2.5484 | 0.95739 | 1.4503 | 1.7266 | 1.7266 | 1.9108 | 1.9108 | 2019-06-30 18:00 | 2.0577 | 3.531 | 5.9679 | 5.9679 | 5.9679 | 5.9679
2021-05-03 06:00 | 2.5492 | 3.1568 | 3.2071 | 3.4226 | 3.3364 | 3.5519 | 1.1974 | 1.8139 | 2.1596 | 2.1596 | 2.39 | 2.39 | 2019-06-30 19:00 | 1.9281 | 3.3087 | 5.5922 | 5.5922 | 5.5922 | 5.5922
2021-05-03 07:00 | 2.8051 | 3.4737 | 3.529 | 3.7662 | 3.6713 | 3.9084 | 1.5433 | 2.3377 | 2.7832 | 2.7832 | 3.0802 | 3.0802 | 2019-06-30 20:00 | 1.9129 | 3.2825 | 5.548 | 5.548 | 5.548 | 5.548
2021-05-03 08:00 | 2.8779 | 3.5638 | 3.6206 | 3.8638 | 3.7665 | 4.0098 | 1.5518 | 2.3507 | 2.7987 | 2.7987 | 3.0973 | 3.0973 | 2019-06-30 21:00 | 1.8519 | 3.1779 | 5.3711 | 5.3711 | 5.3711 | 5.3711
2021-05-03 09:00 | 2.5349 | 3.1391 | 3.1891 | 3.4034 | 3.3177 | 3.532 | 1.4832 | 2.2468 | 2.675 | 2.675 | 2.9604 | 2.9604 | 2019-06-30 22:00 | 1.6919 | 2.9032 | 4.907 | 4.907 | 4.907 | 4.907
2021-05-03 10:00 | 2.292 | 2.8383 | 2.8835 | 3.0773 | 2.9998 | 3.1935 | 1.4604 | 2.2122 | 2.6337 | 2.6337 | 2.9148 | 2.9148 | 2019-06-30 23:00 | 1.4785 | 2.5371 | 4.2881 | 4.2881 | 4.2881 | 4.2881
2021-05-03 11:00 | 2.2291 | 2.7604 | 2.8044 | 2.9928 | 2.9175 | 3.1059 | 1.4947 | 2.2641 | 2.6956 | 2.6956 | 2.9832 | 2.9832 | 2019-07-01 | 1.4556 | 2.4978 | 4.2218 | 4.2218 | 4.2218 | 4.2218
2021-05-03 12:00 | 2.112 | 2.6153 | 2.657 | 2.8355 | 2.7641 | 2.9426 | 1.4175 | 2.1472 | 2.5564 | 2.5564 | 2.8292 | 2.8292 | 2019-07-01 01:00 | 1.3642 | 2.3409 | 3.9565 | 3.9565 | 3.9565 | 3.9565
2021-05-03 13:00 | 2.1034 | 2.6047 | 2.6462 | 2.824 | 2.7529 | 2.9307 | 1.4489 | 2.1949 | 2.6131 | 2.6131 | 2.8919 | 2.8919 | 2019-07-01 02:00 | 1.3718 | 2.354 | 3.9786 | 3.9786 | 3.9786 | 3.9786
2021-05-03 14:00 | 2.1691 | 2.6861 | 2.7289 | 2.9123 | 2.8389 | 3.0223 | 1.3918 | 2.1083 | 2.51 | 2.51 | 2.7779 | 2.7779 | 2019-07-01 03:00 | 1.4099 | 2.4194 | 4.0891 | 4.0891 | 4.0891 | 4.0891
2021-05-03 15:00 | 2.1377 | 2.6472 | 2.6894 | 2.8701 | 2.7978 | 2.9785 | 1.4289 | 2.1646 | 2.577 | 2.577 | 2.852 | 2.852 | 2019-07-01 04:00 | 1.387 | 2.3801 | 4.0228 | 4.0228 | 4.0228 | 4.0228
2021-05-03 16:00 | 2.3177 | 2.8702 | 2.9159 | 3.1118 | 3.0334 | 3.2293 | 1.6747 | 2.5369 | 3.0203 | 3.0203 | 3.3426 | 3.3426 | 2019-07-01 05:00 | 1.6157 | 2.7725 | 4.6859 | 4.6859 | 4.6859 | 4.6859
2021-05-03 17:00 | 2.7178 | 3.3656 | 3.4192 | 3.649 | 3.5571 | 3.7868 | 1.8605 | 2.8183 | 3.3553 | 3.3553 | 3.7133 | 3.7133 | 2019-07-01 06:00 | 1.9205 | 3.2956 | 5.5701 | 5.5701 | 5.5701 | 5.5701
2021-05-03 18:00 | 2.9065 | 3.5992 | 3.6565 | 3.9022 | 3.8039 | 4.0496 | 1.8519 | 2.8053 | 3.3398 | 3.3398 | 3.6962 | 3.6962 | 2019-07-01 07:00 | 2.1644 | 3.7141 | 6.2774 | 6.2774 | 6.2774 | 6.2774
2021-05-03 19:00 | 2.7951 | 3.4613 | 3.5164 | 3.7527 | 3.6582 | 3.8944 | 1.9033 | 2.8832 | 3.4326 | 3.4326 | 3.7989 | 3.7989 | 2019-07-01 08:00 | 2.2634 | 3.8841 | 6.5647 | 6.5647 | 6.5647 | 6.5647
2021-05-03 20:00 | 2.6035 | 3.2241 | 3.2754 | 3.4955 | 3.4075 | 3.6275 | 1.8005 | 2.7274 | 3.2471 | 3.2471 | 3.5935 | 3.5935 | 2019-07-01 09:00 | 2.1949 | 3.7664 | 6.3658 | 6.3658 | 6.3658 | 6.3658
2021-05-03 21:00 | 2.3498 | 2.9099 | 2.9562 | 3.1548 | 3.0754 | 3.274 | 1.669 | 2.5282 | 3.01 | 3.01 | 3.3311 | 3.3311 | 2019-07-01 10:00 | 2.1567 | 3.701 | 6.2553 | 6.2553 | 6.2553 | 6.2553
2021-05-03 22:00 | 2.0777 | 2.5729 | 2.6139 | 2.7895 | 2.7192 | 2.8949 | 1.5061 | 2.2815 | 2.7162 | 2.7162 | 3.006 | 3.006 | 2019-07-01 11:00 | 2.172 | 3.7271 | 6.2995 | 6.2995 | 6.2995 | 6.2995
2021-05-03 23:00 | 1.8862 | 2.3358 | 2.373 | 2.5324 | 2.4686 | 2.6281 | 1.1948 | 1.8099 | 2.1548 | 2.1548 | 2.3847 | 2.3847 | 2019-07-01 12:00 | 2.1491 | 3.6879 | 6.2332 | 6.2332 | 6.2332 | 6.2332
2021-05-04 | 1.6947 | 2.0986 | 2.1321 | 2.2753 | 2.218 | 2.3613 | 0.99181 | 1.5024 | 1.7887 | 1.7887 | 1.9795 | 1.9795 | 2019-07-01 13:00 | 2.1644 | 3.7141 | 6.2774 | 6.2774 | 6.2774 | 6.2774
2021-05-04 01:00 | 1.5347 | 1.9005 | 1.9307 | 2.0605 | 2.0086 | 2.1383 | 0.92023 | 1.394 | 1.6596 | 1.6596 | 1.8367 | 1.8367 | 2019-07-01 14:00 | 2.111 | 3.6225 | 6.1227 | 6.1227 | 6.1227 | 6.1227
2021-05-04 02:00 | 1.5175 | 1.8792 | 1.9092 | 2.0374 | 1.9861 | 2.1144 | 0.86594 | 1.3117 | 1.5617 | 1.5617 | 1.7283 | 1.7283 | 2019-07-01 15:00 | 2.0805 | 3.5702 | 6.0343 | 6.0343 | 6.0343 | 6.0343
2021-05-04 03:00 | 1.5318 | 1.8969 | 1.9271 | 2.0566 | 2.0048 | 2.1343 | 0.80748 | 1.2232 | 1.4563 | 1.4563 | 1.6116 | 1.6116 | 2019-07-01 16:00 | 2.1034 | 3.6094 | 6.1006 | 6.1006 | 6.1006 | 6.1006
2021-05-04 04:00 | 1.5118 | 1.8721 | 1.9019 | 2.0297 | 1.9786 | 2.1064 | 0.84593 | 1.2814 | 1.5256 | 1.5256 | 1.6884 | 1.6884 | 2019-07-01 17:00 | 2.233 | 3.8318 | 6.4763 | 6.4763 | 6.4763 | 6.4763
2021-05-04 05:00 | 1.7719 | 2.1942 | 2.2291 | 2.3789 | 2.319 | 2.4688 | 0.9088 | 1.3767 | 1.639 | 1.639 | 1.8139 | 1.8139 | 2019-07-01 18:00 | 2.233 | 3.8318 | 6.4763 | 6.4763 | 6.4763 | 6.4763
2021-05-04 06:00 | 2.4006 | 2.9728 | 3.0201 | 3.2231 | 3.1419 | 3.3448 | 1.2117 | 1.8356 | 2.1853 | 2.1853 | 2.4185 | 2.4185 | 2019-07-01 19:00 | 2.1644 | 3.7141 | 6.2774 | 6.2774 | 6.2774 | 6.2774
2021-05-04 07:00 | 2.6978 | 3.3408 | 3.3941 | 3.6221 | 3.5309 | 3.7589 | 1.5633 | 2.368 | 2.8193 | 2.8193 | 3.1201 | 3.1201 | 2019-07-01 20:00 | 1.9967 | 3.4264 | 5.7911 | 5.7911 | 5.7911 | 5.7911
2021-05-04 08:00 | 2.9265 | 3.624 | 3.6817 | 3.9291 | 3.8301 | 4.0775 | 1.5318 | 2.3204 | 2.7626 | 2.7626 | 3.0574 | 3.0574 | 2019-07-01 21:00 | 1.8824 | 3.2302 | 5.4596 | 5.4596 | 5.4596 | 5.4596
2021-05-04 09:00 | 2.8979 | 3.5886 | 3.6457 | 3.8907 | 3.7927 | 4.0377 | 1.5461 | 2.3421 | 2.7883 | 2.7883 | 3.0859 | 3.0859 | 2019-07-01 22:00 | 1.7376 | 2.9817 | 5.0396 | 5.0396 | 5.0396 | 5.0396
2021-05-04 10:00 | 2.9036 | 3.5957 | 3.6529 | 3.8984 | 3.8002 | 4.0456 | 1.6204 | 2.4546 | 2.9224 | 2.9224 | 3.2342 | 3.2342 | 2019-07-01 23:00 | 1.6157 | 2.7725 | 4.6859 | 4.6859 | 4.6859 | 4.6859
2021-05-04 11:00 | 2.8436 | 3.5213 | 3.5774 | 3.8178 | 3.7216 | 3.962 | 1.669 | 2.5282 | 3.01 | 3.01 | 3.3311 | 3.3311 | 2019-07-02 | 1.4327 | 2.4586 | 4.1555 | 4.1555 | 4.1555 | 4.1555
2021-05-04 12:00 | 2.7807 | 3.4435 | 3.4983 | 3.7334 | 3.6394 | 3.8744 | 1.7319 | 2.6235 | 3.1234 | 3.1234 | 3.4566 | 3.4566 | 2019-07-02 01:00 | 1.3489 | 2.3148 | 3.9123 | 3.9123 | 3.9123 | 3.9123
2021-05-04 13:00 | 2.755 | 3.4116 | 3.466 | 3.6989 | 3.6057 | 3.8386 | 1.6147 | 2.446 | 2.912 | 2.912 | 3.2228 | 3.2228 | 2019-07-02 02:00 | 1.3032 | 2.2363 | 3.7797 | 3.7797 | 3.7797 | 3.7797
2021-05-04 14:00 | 2.6493 | 3.2807 | 3.3329 | 3.5569 | 3.4673 | 3.6913 | 1.7033 | 2.5802 | 3.0718 | 3.0718 | 3.3996 | 3.3996 | 2019-07-02 03:00 | 1.3337 | 2.2886 | 3.8681 | 3.8681 | 3.8681 | 3.8681
2021-05-04 15:00 | 2.595 | 3.2134 | 3.2646 | 3.484 | 3.3962 | 3.6156 | 1.5833 | 2.3983 | 2.8554 | 2.8554 | 3.16 | 3.16 | 2019-07-02 04:00 | 1.4175 | 2.4324 | 4.1112 | 4.1112 | 4.1112 | 4.1112
2021-05-04 16:00 | 2.8007 | 3.4682 | 3.5235 | 3.7602 | 3.6655 | 3.9023 | 1.6829 | 2.5492 | 3.035 | 3.035 | 3.3588 | 3.3588 | 2019-07-02 05:00 | 1.5852 | 2.7202 | 4.5975 | 4.5975 | 4.5975 | 4.5975
2021-05-04 17:00 | 3.218 | 3.9849 | 4.0484 | 4.3204 | 4.2116 | 4.4837 | 2.0291 | 3.0737 | 3.6594 | 3.6594 | 4.0499 | 4.0499 | 2019-07-02 06:00 | 2.0348 | 3.4917 | 5.9016 | 5.9016 | 5.9016 | 5.9016
2021-05-04 18:00 | 3.3037 | 4.0911 | 4.1563 | 4.4356 | 4.3238 | 4.6031 | 1.9891 | 3.0131 | 3.5872 | 3.5872 | 3.97 | 3.97 | 2019-07-02 07:00 | 2.1644 | 3.7141 | 6.2774 | 6.2774 | 6.2774 | 6.2774
2021-05-04 19:00 | 3.1437 | 3.8929 | 3.9549 | 4.2207 | 4.1144 | 4.3801 | 2.0548 | 3.1126 | 3.7058 | 3.7058 | 4.1012 | 4.1012 | 2019-07-02 08:00 | 2.2787 | 3.9102 | 6.6089 | 6.6089 | 6.6089 | 6.6089
2021-05-04 20:00 | 2.8464 | 3.5249 | 3.581 | 3.8216 | 3.7254 | 3.966 | 1.9376 | 2.9352 | 3.4945 | 3.4945 | 3.8673 | 3.8673 | 2019-07-02 09:00 | 2.2558 | 3.871 | 6.5426 | 6.5426 | 6.5426 | 6.5426
2021-05-04 21:00 | 2.5664 | 3.178 | 3.2287 | 3.4456 | 3.3588 | 3.5758 | 1.7776 | 2.6927 | 3.2058 | 3.2058 | 3.5479 | 3.5479 | 2019-07-02 10:00 | 2.2253 | 3.8187 | 6.4542 | 6.4542 | 6.4542 | 6.4542
2021-05-04 22:00 | 2.1863 | 2.7074 | 2.7505 | 2.9353 | 2.8614 | 3.0462 | 1.5271 | 2.3133 | 2.7541 | 2.7541 | 3.0479 | 3.0479 | 2019-07-02 11:00 | 2.1949 | 3.7664 | 6.3658 | 6.3658 | 6.3658 | 6.3658
2021-05-04 23:00 | 1.9891 | 2.4632 | 2.5024 | 2.6705 | 2.6033 | 2.7714 | 1.3689 | 2.0737 | 2.4688 | 2.4688 | 2.7322 | 2.7322 | 2019-07-02 12:00 | 2.2787 | 3.9102 | 6.6089 | 6.6089 | 6.6089 | 6.6089
2021-05-05 | 1.7662 | 2.1871 | 2.222 | 2.3713 | 2.3115 | 2.4608 | 1.0862 | 1.6453 | 1.9588 | 1.9588 | 2.1678 | 2.1678 | 2019-07-02 13:00 | 2.2025 | 3.7795 | 6.3879 | 6.3879 | 6.3879 | 6.3879
2021-05-05 01:00 | 1.609 | 1.9925 | 2.0242 | 2.1602 | 2.1058 | 2.2418 | 0.96596 | 1.4632 | 1.7421 | 1.7421 | 1.928 | 1.928 | 2019-07-02 14:00 | 2.2406 | 3.8448 | 6.4984 | 6.4984 | 6.4984 | 6.4984
2021-05-05 02:00 | 1.5718 | 1.9465 | 1.9775 | 2.1103 | 2.0572 | 2.1901 | 0.9088 | 1.3767 | 1.639 | 1.639 | 1.8139 | 1.8139 | 2019-07-02 15:00 | 2.172 | 3.7271 | 6.2995 | 6.2995 | 6.2995 | 6.2995
2021-05-05 03:00 | 1.5604 | 1.9323 | 1.9631 | 2.095 | 2.0422 | 2.1741 | 0.86879 | 1.3161 | 1.5668 | 1.5668 | 1.734 | 1.734 | 2019-07-02 16:00 | 2.2253 | 3.8187 | 6.4542 | 6.4542 | 6.4542 | 6.4542
2021-05-05 04:00 | 1.5604 | 1.9323 | 1.963 | 2.095 | 2.0422 | 2.1741 | 0.86879 | 1.3161 | 1.5668 | 1.5668 | 1.734 | 1.734 | 2019-07-02 17:00 | 2.3397 | 4.0149 | 6.7858 | 6.7858 | 6.7858 | 6.7858
2021-05-05 05:00 | 1.8805 | 2.3287 | 2.3658 | 2.5247 | 2.4611 | 2.6201 | 0.91726 | 1.3895 | 1.6542 | 1.6542 | 1.8307 | 1.8307 | 2019-07-02 18:00 | 2.3397 | 4.0149 | 6.7858 | 6.7858 | 6.7858 | 6.7858
2021-05-05 06:00 | 2.3149 | 2.8666 | 2.9123 | 3.108 | 3.0297 | 3.2254 | 1.1889 | 1.8009 | 2.1441 | 2.1441 | 2.3729 | 2.3729 | 2019-07-02 19:00 | 2.1872 | 3.7533 | 6.3437 | 6.3437 | 6.3437 | 6.3437
2021-05-05 07:00 | 2.6835 | 3.3231 | 3.3761 | 3.6029 | 3.5122 | 3.739 | 1.509 | 2.2858 | 2.7213 | 2.7213 | 3.0117 | 3.0117 | 2019-07-02 20:00 | 2.0501 | 3.5179 | 5.9458 | 5.9458 | 5.9458 | 5.9458
2021-05-05 08:00 | 2.7178 | 3.3656 | 3.4192 | 3.649 | 3.5571 | 3.7868 | 1.5861 | 2.4027 | 2.8605 | 2.8605 | 3.1657 | 3.1657 | 2019-07-02 21:00 | 1.9205 | 3.2956 | 5.5701 | 5.5701 | 5.5701 | 5.5701
2021-05-05 09:00 | 2.7664 | 3.4258 | 3.4803 | 3.7142 | 3.6207 | 3.8545 | 1.4947 | 2.2641 | 2.6956 | 2.6956 | 2.9832 | 2.9832 | 2019-07-02 22:00 | 1.9586 | 3.361 | 5.6806 | 5.6806 | 5.6806 | 5.6806
2021-05-05 10:00 | 2.8636 | 3.5461 | 3.6026 | 3.8447 | 3.7478 | 3.9899 | 1.6347 | 2.4763 | 2.9481 | 2.9481 | 3.2627 | 3.2627 | 2019-07-02 23:00 | 1.6919 | 2.9032 | 4.907 | 4.907 | 4.907 | 4.907
2021-05-05 11:00 | 2.7864 | 3.4506 | 3.5055 | 3.7411 | 3.6468 | 3.8824 | 1.7062 | 2.5845 | 3.077 | 3.077 | 3.4053 | 3.4053 | 2019-07-03 | 1.5318 | 2.6286 | 4.4428 | 4.4428 | 4.4428 | 4.4428
2021-05-05 12:00 | 2.8522 | 3.532 | 3.5882 | 3.8293 | 3.7329 | 3.974 | 1.6204 | 2.4546 | 2.9224 | 2.9224 | 3.2342 | 3.2342 | 2019-07-03 01:00 | 1.3946 | 2.3932 | 4.0449 | 4.0449 | 4.0449 | 4.0449
2021-05-05 13:00 | 2.8122 | 3.4824 | 3.5379 | 3.7756 | 3.6805 | 3.9183 | 1.7919 | 2.7144 | 3.2316 | 3.2316 | 3.5764 | 3.5764 | 2019-07-03 02:00 | 1.3489 | 2.3148 | 3.9123 | 3.9123 | 3.9123 | 3.9123
2021-05-05 14:00 | 2.695 | 3.3373 | 3.3905 | 3.6183 | 3.5271 | 3.755 | 1.5775 | 2.3897 | 2.845 | 2.845 | 3.1486 | 3.1486 | 2019-07-03 03:00 | 1.3337 | 2.2886 | 3.8681 | 3.8681 | 3.8681 | 3.8681
2021-05-05 15:00 | 2.675 | 3.3125 | 3.3653 | 3.5914 | 3.501 | 3.7271 | 1.6176 | 2.4503 | 2.9172 | 2.9172 | 3.2285 | 3.2285 | 2019-07-03 04:00 | 1.4327 | 2.4586 | 4.1555 | 4.1555 | 4.1555 | 4.1555
2021-05-05 16:00 | 2.7864 | 3.4506 | 3.5055 | 3.7411 | 3.6468 | 3.8824 | 1.709 | 2.5888 | 3.0821 | 3.0821 | 3.411 | 3.411 | 2019-07-03 05:00 | 1.6004 | 2.7463 | 4.6417 | 4.6417 | 4.6417 | 4.6417
2021-05-05 17:00 | 3.2694 | 4.0486 | 4.1131 | 4.3895 | 4.279 | 4.5553 | 1.9719 | 2.9871 | 3.5563 | 3.5563 | 3.9358 | 3.9358 | 2019-07-03 06:00 | 2.0272 | 3.4787 | 5.8795 | 5.8795 | 5.8795 | 5.8795
2021-05-05 18:00 | 3.3066 | 4.0947 | 4.1599 | 4.4394 | 4.3276 | 4.6071 | 2.092 | 3.1689 | 3.7728 | 3.7728 | 4.1753 | 4.1753 | 2019-07-03 07:00 | 2.1567 | 3.701 | 6.2553 | 6.2553 | 6.2553 | 6.2553
2021-05-05 19:00 | 3.238 | 4.0097 | 4.0736 | 4.3473 | 4.2378 | 4.5115 | 2.1606 | 3.2728 | 3.8965 | 3.8965 | 4.3122 | 4.3122 | 2019-07-03 08:00 | 2.332 | 4.0018 | 6.7637 | 6.7637 | 6.7637 | 6.7637
2021-05-05 20:00 | 2.835 | 3.5107 | 3.5666 | 3.8063 | 3.7104 | 3.9501 | 1.9802 | 2.9996 | 3.5712 | 3.5712 | 3.9522 | 3.9522 | 2019-07-03 09:00 | 2.2863 | 3.9233 | 6.631 | 6.631 | 6.631 | 6.631
2021-05-05 21:00 | 2.5921 | 3.2099 | 3.261 | 3.4801 | 3.3925 | 3.6116 | 1.7776 | 2.6927 | 3.2058 | 3.2058 | 3.5479 | 3.5479 | 2019-07-03 10:00 | 2.2863 | 3.9233 | 6.631 | 6.631 | 6.631 | 6.631
2021-05-05 22:00 | 2.2582 | 2.7964 | 2.841 | 3.0319 | 2.9555 | 3.1464 | 1.5604 | 2.3637 | 2.8141 | 2.8141 | 3.1144 | 3.1144 | 2019-07-03 11:00 | 2.3015 | 3.9495 | 6.6753 | 6.6753 | 6.6753 | 6.6753
2021-05-05 23:00 | 1.9646 | 2.4328 | 2.4715 | 2.6376 | 2.5712 | 2.7373 | 1.3203 | 2.0001 | 2.3812 | 2.3812 | 2.6353 | 2.6353 | 2019-07-03 12:00 | 2.3473 | 4.0279 | 6.8079 | 6.8079 | 6.8079 | 6.8079
2021-05-06 | 1.7233 | 2.134 | 2.168 | 2.3137 | 2.2554 | 2.4011 | 1.0295 | 1.5595 | 1.8566 | 1.8566 | 2.0548 | 2.0548 | 2019-07-03 13:00 | 2.2558 | 3.871 | 6.5426 | 6.5426 | 6.5426 | 6.5426
2021-05-06 01:00 | 1.5661 | 1.9394 | 1.9703 | 2.1027 | 2.0497 | 2.1821 | 0.98311 | 1.4892 | 1.773 | 1.773 | 1.9622 | 1.9622 | 2019-07-03 14:00 | 2.3092 | 3.9625 | 6.6974 | 6.6974 | 6.6974 | 6.6974
2021-05-06 02:00 | 1.5652 | 1.9382 | 1.9691 | 2.1014 | 2.0485 | 2.1808 | 0.86879 | 1.3161 | 1.5668 | 1.5668 | 1.734 | 1.734 | 2019-07-03 15:00 | 2.2406 | 3.8448 | 6.4984 | 6.4984 | 6.4984 | 6.4984
2021-05-06 03:00 | 1.5661 | 1.9394 | 1.9703 | 2.1027 | 2.0497 | 2.1821 | 0.85165 | 1.2901 | 1.5359 | 1.5359 | 1.6998 | 1.6998 | 2019-07-03 16:00 | 2.2177 | 3.8056 | 6.4321 | 6.4321 | 6.4321 | 6.4321
2021-05-06 04:00 | 1.5601 | 1.9319 | 1.9627 | 2.0946 | 2.0418 | 2.1737 | 0.88594 | 1.342 | 1.5978 | 1.5978 | 1.7682 | 1.7682 | 2019-07-03 17:00 | 2.3701 | 4.0672 | 6.8742 | 6.8742 | 6.8742 | 6.8742
2021-05-06 05:00 | 1.8433 | 2.2827 | 2.319 | 2.4749 | 2.4125 | 2.5683 | 0.96596 | 1.4632 | 1.7421 | 1.7421 | 1.928 | 1.928 | 2019-07-03 18:00 | 2.3244 | 3.9887 | 6.7416 | 6.7416 | 6.7416 | 6.7416
2021-05-06 06:00 | 2.4292 | 3.0082 | 3.0561 | 3.2614 | 3.1793 | 3.3846 | 1.2375 | 1.8745 | 2.2317 | 2.2317 | 2.4698 | 2.4698 | 2019-07-03 19:00 | 2.2406 | 3.8448 | 6.4984 | 6.4984 | 6.4984 | 6.4984
2021-05-06 07:00 | 2.675 | 3.3125 | 3.3653 | 3.5914 | 3.501 | 3.7271 | 1.5604 | 2.3637 | 2.8141 | 2.8141 | 3.1144 | 3.1144 | 2019-07-03 20:00 | 2.0348 | 3.4917 | 5.9016 | 5.9016 | 5.9016 | 5.9016
2021-05-06 08:00 | 2.7636 | 3.4222 | 3.4768 | 3.7104 | 3.6169 | 3.8505 | 1.5547 | 2.355 | 2.8038 | 2.8038 | 3.103 | 3.103 | 2019-07-03 21:00 | 1.9662 | 3.374 | 5.7027 | 5.7027 | 5.7027 | 5.7027
2021-05-06 09:00 | 2.5435 | 3.1497 | 3.1999 | 3.4149 | 3.3289 | 3.5439 | 1.529 | 2.3161 | 2.7574 | 2.7574 | 3.0516 | 3.0516 | 2019-07-03 22:00 | 1.8671 | 3.204 | 5.4154 | 5.4154 | 5.4154 | 5.4154
2021-05-06 10:00 | 2.5749 | 3.1887 | 3.2395 | 3.4571 | 3.3701 | 3.5877 | 1.5747 | 2.3854 | 2.8399 | 2.8399 | 3.1429 | 3.1429 | 2019-07-03 23:00 | 1.6385 | 2.8117 | 4.7522 | 4.7522 | 4.7522 | 4.7522
2021-05-06 11:00 | 2.4435 | 3.0259 | 3.0741 | 3.2806 | 3.198 | 3.4046 | 1.5547 | 2.355 | 2.8038 | 2.8038 | 3.103 | 3.103 | 2019-07-04 | 1.5318 | 2.6286 | 4.4428 | 4.4428 | 4.4428 | 4.4428
2021-05-06 12:00 | 2.6064 | 3.2276 | 3.279 | 3.4993 | 3.4112 | 3.6315 | 1.5747 | 2.3854 | 2.8399 | 2.8399 | 3.1429 | 3.1429 | 2019-07-04 01:00 | 1.448 | 2.4848 | 4.1997 | 4.1997 | 4.1997 | 4.1997
2021-05-06 13:00 | 2.4835 | 3.0754 | 3.1244 | 3.3343 | 3.2504 | 3.4603 | 1.5575 | 2.3594 | 2.809 | 2.809 | 3.1087 | 3.1087 | 2019-07-04 02:00 | 1.4099 | 2.4194 | 4.0891 | 4.0891 | 4.0891 | 4.0891
2021-05-06 14:00 | 2.5549 | 3.1639 | 3.2143 | 3.4303 | 3.3439 | 3.5598 | 1.5147 | 2.2944 | 2.7317 | 2.7317 | 3.0231 | 3.0231 | 2019-07-04 03:00 | 1.4175 | 2.4324 | 4.1112 | 4.1112 | 4.1112 | 4.1112
2021-05-06 15:00 | 2.3692 | 2.9339 | 2.9806 | 3.1809 | 3.1007 | 3.301 | 1.549 | 2.3464 | 2.7935 | 2.7935 | 3.0916 | 3.0916 | 2019-07-04 04:00 | 1.4099 | 2.4194 | 4.0891 | 4.0891 | 4.0891 | 4.0891
2021-05-06 16:00 | 2.6035 | 3.2241 | 3.2754 | 3.4955 | 3.4075 | 3.6275 | 1.6233 | 2.4589 | 2.9275 | 2.9275 | 3.2399 | 3.2399 | 2019-07-04 05:00 | 1.6766 | 2.8771 | 4.8628 | 4.8628 | 4.8628 | 4.8628
2021-05-06 17:00 | 2.9154 | 3.6102 | 3.6678 | 3.9142 | 3.8156 | 4.0621 | 1.7776 | 2.6927 | 3.2058 | 3.2058 | 3.5479 | 3.5479 | 2019-07-04 06:00 | 2.0119 | 3.4525 | 5.8353 | 5.8353 | 5.8353 | 5.8353
2021-05-06 18:00 | 2.9893 | 3.7018 | 3.7608 | 4.0135 | 3.9124 | 4.1651 | 1.9434 | 2.9438 | 3.5048 | 3.5048 | 3.8787 | 3.8787 | 2019-07-04 07:00 | 2.2558 | 3.871 | 6.5426 | 6.5426 | 6.5426 | 6.5426
2021-05-06 19:00 | 2.7921 | 3.4576 | 3.5127 | 3.7487 | 3.6543 | 3.8903 | 1.9805 | 3.0001 | 3.5718 | 3.5718 | 3.9529 | 3.9529 | 2019-07-04 08:00 | 2.3244 | 3.9887 | 6.7416 | 6.7416 | 6.7416 | 6.7416
2021-05-06 20:00 | 2.6435 | 3.2736 | 3.3257 | 3.5492 | 3.4598 | 3.6833 | 1.9005 | 2.8789 | 3.4275 | 3.4275 | 3.7932 | 3.7932 | 2019-07-04 09:00 | 2.3015 | 3.9495 | 6.6753 | 6.6753 | 6.6753 | 6.6753
2021-05-06 21:00 | 2.3749 | 2.9409 | 2.9878 | 3.1885 | 3.1082 | 3.309 | 1.7862 | 2.7057 | 3.2213 | 3.2213 | 3.565 | 3.565 | 2019-07-04 10:00 | 2.3244 | 3.9887 | 6.7416 | 6.7416 | 6.7416 | 6.7416
2021-05-06 22:00 | 2.0834 | 2.58 | 2.621 | 2.7972 | 2.7267 | 2.9028 | 1.4718 | 2.2295 | 2.6543 | 2.6543 | 2.9376 | 2.9376 | 2019-07-04 11:00 | 2.3244 | 3.9887 | 6.7416 | 6.7416 | 6.7416 | 6.7416
2021-05-06 23:00 | 1.9234 | 2.3818 | 2.4197 | 2.5823 | 2.5173 | 2.6798 | 1.2718 | 1.9265 | 2.2936 | 2.2936 | 2.5383 | 2.5383 | 2019-07-04 12:00 | 2.332 | 4.0018 | 6.7637 | 6.7637 | 6.7637 | 6.7637
2021-05-07 | 1.6376 | 2.0279 | 2.0602 | 2.1986 | 2.1432 | 2.2816 | 1.0122 | 1.5332 | 1.8254 | 1.8254 | 2.0202 | 2.0202 | 2019-07-04 13:00 | 2.2863 | 3.9233 | 6.631 | 6.631 | 6.631 | 6.631
2021-05-07 01:00 | 1.5204 | 1.8828 | 1.9127 | 2.0413 | 1.9899 | 2.1184 | 0.9088 | 1.3767 | 1.639 | 1.639 | 1.8139 | 1.8139 | 2019-07-04 14:00 | 2.3473 | 4.0279 | 6.8079 | 6.8079 | 6.8079 | 6.8079
2021-05-07 02:00 | 1.5147 | 1.8757 | 1.9056 | 2.0336 | 1.9824 | 2.1104 | 0.90309 | 1.368 | 1.6287 | 1.6287 | 1.8025 | 1.8025 | 2019-07-04 15:00 | 2.3015 | 3.9495 | 6.6753 | 6.6753 | 6.6753 | 6.6753
2021-05-07 03:00 | 1.5118 | 1.8721 | 1.902 | 2.0298 | 1.9786 | 2.1064 | 0.82878 | 1.2554 | 1.4947 | 1.4947 | 1.6542 | 1.6542 | 2019-07-04 16:00 | 2.3244 | 3.9887 | 6.7416 | 6.7416 | 6.7416 | 6.7416
2021-05-07 04:00 | 1.5947 | 1.9748 | 2.0062 | 2.141 | 2.0871 | 2.2219 | 0.82878 | 1.2554 | 1.4947 | 1.4947 | 1.6542 | 1.6542 | 2019-07-04 17:00 | 2.4006 | 4.1195 | 6.9626 | 6.9626 | 6.9626 | 6.9626
2021-05-07 05:00 | 1.7605 | 2.18 | 2.2148 | 2.3636 | 2.3041 | 2.4529 | 0.92881 | 1.407 | 1.6751 | 1.6751 | 1.8538 | 1.8538 | 2019-07-04 18:00 | 2.3397 | 4.0149 | 6.7858 | 6.7858 | 6.7858 | 6.7858
2021-05-07 06:00 | 2.172 | 2.6897 | 2.7325 | 2.9161 | 2.8427 | 3.0263 | 1.1802 | 1.7877 | 2.1284 | 2.1284 | 2.3555 | 2.3555 | 2019-07-04 19:00 | 2.2177 | 3.8056 | 6.4321 | 6.4321 | 6.4321 | 6.4321
2021-05-07 07:00 | 2.5035 | 3.1002 | 3.1496 | 3.3612 | 3.2765 | 3.4882 | 1.4089 | 2.1343 | 2.541 | 2.541 | 2.8121 | 2.8121 | 2019-07-04 20:00 | 2.1796 | 3.7402 | 6.3216 | 6.3216 | 6.3216 | 6.3216
2021-05-07 08:00 | 2.4235 | 3.0011 | 3.0489 | 3.2538 | 3.1718 | 3.3767 | 1.4604 | 2.2122 | 2.6337 | 2.6337 | 2.9148 | 2.9148 | 2019-07-04 21:00 | 2.0043 | 3.4394 | 5.8132 | 5.8132 | 5.8132 | 5.8132
2021-05-07 09:00 | 2.3463 | 2.9055 | 2.9518 | 3.1502 | 3.0708 | 3.2692 | 1.3889 | 2.104 | 2.5049 | 2.5049 | 2.7722 | 2.7722 | 2019-07-04 22:00 | 1.8824 | 3.2302 | 5.4596 | 5.4596 | 5.4596 | 5.4596
2021-05-07 10:00 | 2.2692 | 2.81 | 2.8547 | 3.0466 | 2.9698 | 3.1617 | 1.3603 | 2.0607 | 2.4533 | 2.4533 | 2.7151 | 2.7151 | 2019-07-04 23:00 | 1.7681 | 3.034 | 5.128 | 5.128 | 5.128 | 5.128
2021-05-07 11:00 | 2.332 | 2.8878 | 2.9338 | 3.131 | 3.0521 | 3.2493 | 1.4632 | 2.2165 | 2.6389 | 2.6389 | 2.9205 | 2.9205 | 2019-07-05 | 1.5394 | 2.6417 | 4.4649 | 4.4649 | 4.4649 | 4.4649
2021-05-07 12:00 | 2.392 | 2.9622 | 3.0093 | 3.2116 | 3.1307 | 3.3329 | 1.5147 | 2.2944 | 2.7317 | 2.7317 | 3.0231 | 3.0231 | 2019-07-05 01:00 | 1.4937 | 2.5632 | 4.3323 | 4.3323 | 4.3323 | 4.3323
2021-05-07 13:00 | 2.3835 | 2.9515 | 2.9986 | 3.2 | 3.1195 | 3.3209 | 1.4918 | 2.2598 | 2.6904 | 2.6904 | 2.9775 | 2.9775 | 2019-07-05 02:00 | 1.3946 | 2.3932 | 4.0449 | 4.0449 | 4.0449 | 4.0449
2021-05-07 14:00 | 2.232 | 2.764 | 2.808 | 2.9967 | 2.9212 | 3.1099 | 1.4146 | 2.1429 | 2.5513 | 2.5513 | 2.8235 | 2.8235 | 2019-07-05 03:00 | 1.3794 | 2.3671 | 4.0007 | 4.0007 | 4.0007 | 4.0007
2021-05-07 15:00 | 2.1463 | 2.6578 | 2.7001 | 2.8816 | 2.809 | 2.9904 | 1.4432 | 2.1862 | 2.6028 | 2.6028 | 2.8805 | 2.8805 | 2019-07-05 04:00 | 1.4556 | 2.4978 | 4.2218 | 4.2218 | 4.2218 | 4.2218
2021-05-07 16:00 | 2.2063 | 2.7321 | 2.7756 | 2.9621 | 2.8875 | 3.0741 | 1.4975 | 2.2685 | 2.7007 | 2.7007 | 2.9889 | 2.9889 | 2019-07-05 05:00 | 1.7452 | 2.9948 | 5.0617 | 5.0617 | 5.0617 | 5.0617
2021-05-07 17:00 | 2.5235 | 3.125 | 3.1747 | 3.3881 | 3.3027 | 3.516 | 1.849 | 2.8009 | 3.3347 | 3.3347 | 3.6905 | 3.6905 | 2019-07-05 06:00 | 1.9357 | 3.3217 | 5.6143 | 5.6143 | 5.6143 | 5.6143
2021-05-07 18:00 | 2.5092 | 3.1073 | 3.1568 | 3.3689 | 3.284 | 3.4961 | 1.9033 | 2.8832 | 3.4326 | 3.4326 | 3.7989 | 3.7989 | 2019-07-05 07:00 | 2.1796 | 3.7402 | 6.3216 | 6.3216 | 6.3216 | 6.3216
2021-05-07 19:00 | 2.3377 | 2.8949 | 2.941 | 3.1387 | 3.0596 | 3.2572 | 1.9234 | 2.9135 | 3.4687 | 3.4687 | 3.8388 | 3.8388 | 2019-07-05 08:00 | 2.4159 | 4.1456 | 7.0068 | 7.0068 | 7.0068 | 7.0068
2021-05-07 20:00 | 2.1806 | 2.7003 | 2.7433 | 2.9276 | 2.8539 | 3.0382 | 1.809 | 2.7403 | 3.2625 | 3.2625 | 3.6106 | 3.6106 | 2019-07-05 09:00 | 2.3625 | 4.0541 | 6.8521 | 6.8521 | 6.8521 | 6.8521
2021-05-07 21:00 | 2.0262 | 2.5092 | 2.5491 | 2.7204 | 2.6519 | 2.8232 | 1.7519 | 2.6538 | 3.1594 | 3.1594 | 3.4966 | 3.4966 | 2019-07-05 10:00 | 2.2634 | 3.8841 | 6.5647 | 6.5647 | 6.5647 | 6.5647
2021-05-07 22:00 | 2.0034 | 2.4809 | 2.5204 | 2.6897 | 2.622 | 2.7913 | 1.5207 | 2.3036 | 2.7426 | 2.7426 | 3.0352 | 3.0352 | 2019-07-05 11:00 | 2.3244 | 3.9887 | 6.7416 | 6.7416 | 6.7416 | 6.7416
2021-05-07 23:00 | 1.8748 | 2.3216 | 2.3586 | 2.5171 | 2.4537 | 2.6121 | 1.266 | 1.9178 | 2.2832 | 2.2832 | 2.5269 | 2.5269 | 2019-07-05 12:00 | 2.3168 | 3.9756 | 6.7195 | 6.7195 | 6.7195 | 6.7195
2021-05-08 | 1.5986 | 1.9796 | 2.0112 | 2.1463 | 2.0923 | 2.2274 | 1.0888 | 1.6494 | 1.9637 | 1.9637 | 2.1732 | 2.1732 | 2019-07-05 13:00 | 2.2787 | 3.9102 | 6.6089 | 6.6089 | 6.6089 | 6.6089
2021-05-08 01:00 | 1.5347 | 1.9005 | 1.9307 | 2.0605 | 2.0086 | 2.1383 | 0.98597 | 1.4935 | 1.7781 | 1.7781 | 1.9679 | 1.9679 | 2019-07-05 14:00 | 2.3015 | 3.9495 | 6.6753 | 6.6753 | 6.6753 | 6.6753
2021-05-08 02:00 | 1.4632 | 1.812 | 1.8408 | 1.9645 | 1.9151 | 2.0387 | 0.92023 | 1.394 | 1.6596 | 1.6596 | 1.8367 | 1.8367 | 2019-07-05 15:00 | 2.2787 | 3.9102 | 6.6089 | 6.6089 | 6.6089 | 6.6089
2021-05-08 03:00 | 1.4632 | 1.812 | 1.8408 | 1.9645 | 1.9151 | 2.0387 | 0.86115 | 1.3045 | 1.553 | 1.553 | 1.7188 | 1.7188 | 2019-07-05 16:00 | 2.2787 | 3.9102 | 6.6089 | 6.6089 | 6.6089 | 6.6089
2021-05-08 04:00 | 1.4832 | 1.8368 | 1.866 | 1.9914 | 1.9412 | 2.0666 | 0.81449 | 1.2338 | 1.4689 | 1.4689 | 1.6256 | 1.6256 | 2019-07-05 17:00 | 2.2253 | 3.8187 | 6.4542 | 6.4542 | 6.4542 | 6.4542
2021-05-08 05:00 | 1.5604 | 1.9323 | 1.9631 | 2.095 | 2.0422 | 2.1741 | 0.80592 | 1.2208 | 1.4534 | 1.4534 | 1.6085 | 1.6085 | 2019-07-05 18:00 | 2.2634 | 3.8841 | 6.5647 | 6.5647 | 6.5647 | 6.5647
2021-05-08 06:00 | 1.689 | 2.0916 | 2.1249 | 2.2677 | 2.2105 | 2.3533 | 0.94596 | 1.4329 | 1.706 | 1.706 | 1.888 | 1.888 | 2019-07-05 19:00 | 2.1339 | 3.6618 | 6.189 | 6.189 | 6.189 | 6.189
2021-05-08 07:00 | 1.8319 | 2.2685 | 2.3046 | 2.4595 | 2.3976 | 2.5524 | 1.2089 | 1.8312 | 2.1802 | 2.1802 | 2.4128 | 2.4128 | 2019-07-05 20:00 | 2.0272 | 3.4787 | 5.8795 | 5.8795 | 5.8795 | 5.8795
2021-05-08 08:00 | 2.032 | 2.5162 | 2.5563 | 2.7281 | 2.6594 | 2.8312 | 1.3403 | 2.0304 | 2.4173 | 2.4173 | 2.6752 | 2.6752 | 2019-07-05 21:00 | 1.8443 | 3.1648 | 5.349 | 5.349 | 5.349 | 5.349
2021-05-08 09:00 | 2.0977 | 2.5976 | 2.639 | 2.8163 | 2.7454 | 2.9227 | 1.5004 | 2.2728 | 2.7059 | 2.7059 | 2.9946 | 2.9946 | 2019-07-05 22:00 | 1.8824 | 3.2302 | 5.4596 | 5.4596 | 5.4596 | 5.4596
2021-05-08 10:00 | 1.9434 | 2.4065 | 2.4449 | 2.6091 | 2.5434 | 2.7077 | 1.6318 | 2.4719 | 2.943 | 2.943 | 3.257 | 3.257 | 2019-07-05 23:00 | 1.6842 | 2.8902 | 4.8849 | 4.8849 | 4.8849 | 4.8849
2021-05-08 11:00 | 1.9005 | 2.3535 | 2.3909 | 2.5516 | 2.4873 | 2.648 | 1.6404 | 2.4849 | 2.9584 | 2.9584 | 3.2741 | 3.2741 | 2019-07-06 | 1.5471 | 2.6548 | 4.487 | 4.487 | 4.487 | 4.487
2021-05-08 12:00 | 1.7547 | 2.173 | 2.2076 | 2.3559 | 2.2966 | 2.4449 | 1.6033 | 2.4286 | 2.8914 | 2.8914 | 3.2 | 3.2 | 2019-07-06 01:00 | 1.4709 | 2.524 | 4.266 | 4.266 | 4.266 | 4.266
2021-05-08 13:00 | 1.7976 | 2.226 | 2.2615 | 2.4135 | 2.3527 | 2.5046 | 1.6576 | 2.5109 | 2.9894 | 2.9894 | 3.3083 | 3.3083 | 2019-07-06 02:00 | 1.4556 | 2.4978 | 4.2218 | 4.2218 | 4.2218 | 4.2218
2021-05-08 14:00 | 1.8148 | 2.2473 | 2.2831 | 2.4365 | 2.3751 | 2.5285 | 1.6176 | 2.4503 | 2.9172 | 2.9172 | 3.2285 | 3.2285 | 2019-07-06 03:00 | 1.3794 | 2.3671 | 4.0007 | 4.0007 | 4.0007 | 4.0007
2021-05-08 15:00 | 1.8119 | 2.2437 | 2.2795 | 2.4326 | 2.3714 | 2.5245 | 1.5004 | 2.2728 | 2.7059 | 2.7059 | 2.9946 | 2.9946 | 2019-07-06 04:00 | 1.4785 | 2.5371 | 4.2881 | 4.2881 | 4.2881 | 4.2881
2021-05-08 16:00 | 1.8884 | 2.3384 | 2.3757 | 2.5353 | 2.4715 | 2.6311 | 1.7376 | 2.6321 | 3.1337 | 3.1337 | 3.468 | 3.468 | 2019-07-06 05:00 | 1.5623 | 2.6809 | 4.5312 | 4.5312 | 4.5312 | 4.5312
2021-05-08 17:00 | 2.2206 | 2.7498 | 2.7936 | 2.9813 | 2.9063 | 3.094 | 1.8176 | 2.7533 | 3.278 | 3.278 | 3.6278 | 3.6278 | 2019-07-06 06:00 | 1.73 | 2.9686 | 5.0175 | 5.0175 | 5.0175 | 5.0175
2021-05-08 18:00 | 2.2749 | 2.8171 | 2.8619 | 3.0542 | 2.9773 | 3.1696 | 1.8691 | 2.8313 | 3.3708 | 3.3708 | 3.7304 | 3.7304 | 2019-07-06 07:00 | 1.7986 | 3.0863 | 5.2164 | 5.2164 | 5.2164 | 5.2164
2021-05-08 19:00 | 2.0977 | 2.5976 | 2.639 | 2.8163 | 2.7454 | 2.9227 | 1.8262 | 2.7663 | 3.2934 | 3.2934 | 3.6449 | 3.6449 | 2019-07-06 08:00 | 2.0805 | 3.5702 | 6.0343 | 6.0343 | 6.0343 | 6.0343
2021-05-08 20:00 | 2.1348 | 2.6437 | 2.6858 | 2.8662 | 2.794 | 2.9745 | 1.7146 | 2.5973 | 3.0922 | 3.0922 | 3.4221 | 3.4221 | 2019-07-06 09:00 | 2.2558 | 3.871 | 6.5426 | 6.5426 | 6.5426 | 6.5426
2021-05-08 21:00 | 2.0148 | 2.495 | 2.5348 | 2.7051 | 2.6369 | 2.8073 | 1.6261 | 2.4633 | 2.9327 | 2.9327 | 3.2456 | 3.2456 | 2019-07-06 10:00 | 2.332 | 4.0018 | 6.7637 | 6.7637 | 6.7637 | 6.7637
2021-05-08 22:00 | 1.9033 | 2.357 | 2.3945 | 2.5554 | 2.4911 | 2.652 | 1.5004 | 2.2728 | 2.7059 | 2.7059 | 2.9946 | 2.9946 | 2019-07-06 11:00 | 2.1872 | 3.7533 | 6.3437 | 6.3437 | 6.3437 | 6.3437
2021-05-08 23:00 | 1.8605 | 2.3039 | 2.3406 | 2.4979 | 2.435 | 2.5922 | 1.344 | 2.036 | 2.4239 | 2.4239 | 2.6826 | 2.6826 | 2019-07-06 12:00 | 2.1567 | 3.701 | 6.2553 | 6.2553 | 6.2553 | 6.2553
2021-05-09 | 1.618 | 2.0036 | 2.0355 | 2.1723 | 2.1176 | 2.2544 | 1.1603 | 1.7576 | 2.0925 | 2.0925 | 2.3158 | 2.3158 | 2019-07-06 13:00 | 2.111 | 3.6225 | 6.1227 | 6.1227 | 6.1227 | 6.1227
2021-05-09 01:00 | 1.5318 | 1.8969 | 1.9271 | 2.0566 | 2.0048 | 2.1343 | 1.0203 | 1.5455 | 1.84 | 1.84 | 2.0363 | 2.0363 | 2019-07-06 14:00 | 2.1491 | 3.6879 | 6.2332 | 6.2332 | 6.2332 | 6.2332
2021-05-09 02:00 | 1.5004 | 1.858 | 1.8876 | 2.0144 | 1.9637 | 2.0905 | 0.93167 | 1.4113 | 1.6802 | 1.6802 | 1.8595 | 1.8595 | 2019-07-06 15:00 | 2.1339 | 3.6618 | 6.189 | 6.189 | 6.189 | 6.189
2021-05-09 03:00 | 1.4604 | 1.8084 | 1.8372 | 1.9607 | 1.9113 | 2.0348 | 0.86308 | 1.3074 | 1.5565 | 1.5565 | 1.7226 | 1.7226 | 2019-07-06 16:00 | 2.3015 | 3.9495 | 6.6753 | 6.6753 | 6.6753 | 6.6753
2021-05-09 04:00 | 1.4747 | 1.8261 | 1.8552 | 1.9799 | 1.93 | 2.0547 | 0.84307 | 1.2771 | 1.5204 | 1.5204 | 1.6827 | 1.6827 | 2019-07-06 17:00 | 2.2863 | 3.9233 | 6.631 | 6.631 | 6.631 | 6.631
2021-05-09 05:00 | 1.5947 | 1.9748 | 2.0062 | 2.141 | 2.0871 | 2.2219 | 0.84593 | 1.2814 | 1.5256 | 1.5256 | 1.6884 | 1.6884 | 2019-07-06 18:00 | 2.111 | 3.6225 | 6.1227 | 6.1227 | 6.1227 | 6.1227
2021-05-09 06:00 | 1.6604 | 2.0562 | 2.0889 | 2.2293 | 2.1731 | 2.3135 | 0.91166 | 1.381 | 1.6441 | 1.6441 | 1.8196 | 1.8196 | 2019-07-06 19:00 | 1.951 | 3.3479 | 5.6585 | 5.6585 | 5.6585 | 5.6585
2021-05-09 07:00 | 1.8433 | 2.2827 | 2.319 | 2.4749 | 2.4125 | 2.5683 | 1.1174 | 1.6927 | 2.0152 | 2.0152 | 2.2303 | 2.2303 | 2019-07-06 20:00 | 1.8748 | 3.2171 | 5.4375 | 5.4375 | 5.4375 | 5.4375
2021-05-09 08:00 | 1.9576 | 2.4242 | 2.4628 | 2.6283 | 2.5621 | 2.7276 | 1.2289 | 1.8615 | 2.2162 | 2.2162 | 2.4527 | 2.4527 | 2019-07-06 21:00 | 1.829 | 3.1386 | 5.3048 | 5.3048 | 5.3048 | 5.3048
2021-05-09 09:00 | 1.9548 | 2.4207 | 2.4593 | 2.6245 | 2.5584 | 2.7236 | 1.4975 | 2.2685 | 2.7007 | 2.7007 | 2.9889 | 2.9889 | 2019-07-06 22:00 | 1.7605 | 3.0209 | 5.1059 | 5.1059 | 5.1059 | 5.1059
2021-05-09 10:00 | 1.8405 | 2.2791 | 2.3154 | 2.471 | 2.4088 | 2.5644 | 1.5575 | 2.3594 | 2.809 | 2.809 | 3.1087 | 3.1087 | 2019-07-06 23:00 | 1.5699 | 2.694 | 4.5533 | 4.5533 | 4.5533 | 4.5533
2021-05-09 11:00 | 1.7347 | 2.1482 | 2.1824 | 2.329 | 2.2704 | 2.417 | 1.489 | 2.2555 | 2.6853 | 2.6853 | 2.9718 | 2.9718 | 2019-07-07 | 1.5013 | 2.5763 | 4.3544 | 4.3544 | 4.3544 | 4.3544
2021-05-09 12:00 | 1.6204 | 2.0066 | 2.0386 | 2.1756 | 2.1208 | 2.2578 | 1.5604 | 2.3637 | 2.8141 | 2.8141 | 3.1144 | 3.1144 | 2019-07-07 01:00 | 1.4632 | 2.5109 | 4.2439 | 4.2439 | 4.2439 | 4.2439
2021-05-09 13:00 | 1.5918 | 1.9712 | 2.0026 | 2.1372 | 2.0834 | 2.2179 | 1.5775 | 2.3897 | 2.845 | 2.845 | 3.1486 | 3.1486 | 2019-07-07 02:00 | 1.3718 | 2.354 | 3.9786 | 3.9786 | 3.9786 | 3.9786
2021-05-09 14:00 | 1.7547 | 2.173 | 2.2076 | 2.3559 | 2.2966 | 2.4449 | 1.6519 | 2.5022 | 2.979 | 2.979 | 3.2969 | 3.2969 | 2019-07-07 03:00 | 1.3642 | 2.3409 | 3.9565 | 3.9565 | 3.9565 | 3.9565
2021-05-09 15:00 | 1.7262 | 2.1376 | 2.1716 | 2.3175 | 2.2592 | 2.4051 | 1.6261 | 2.4633 | 2.9327 | 2.9327 | 3.2456 | 3.2456 | 2019-07-07 04:00 | 1.5013 | 2.5763 | 4.3544 | 4.3544 | 4.3544 | 4.3544
2021-05-09 16:00 | 1.9434 | 2.4065 | 2.4449 | 2.6091 | 2.5434 | 2.7077 | 1.7433 | 2.6408 | 3.144 | 3.144 | 3.4794 | 3.4794 | 2019-07-07 05:00 | 1.5242 | 2.6155 | 4.4207 | 4.4207 | 4.4207 | 4.4207
2021-05-09 17:00 | 2.3063 | 2.856 | 2.9015 | 3.0964 | 3.0185 | 3.2134 | 1.8576 | 2.8139 | 3.3501 | 3.3501 | 3.7076 | 3.7076 | 2019-07-07 06:00 | 1.6614 | 2.8509 | 4.8186 | 4.8186 | 4.8186 | 4.8186
2021-05-09 18:00 | 2.4606 | 3.0471 | 3.0956 | 3.3036 | 3.2204 | 3.4284 | 1.8974 | 2.8742 | 3.4219 | 3.4219 | 3.787 | 3.787 | 2019-07-07 07:00 | 1.7071 | 2.9294 | 4.9512 | 4.9512 | 4.9512 | 4.9512
2021-05-09 19:00 | 2.4092 | 2.9834 | 3.0309 | 3.2346 | 3.1531 | 3.3568 | 1.9434 | 2.9438 | 3.5048 | 3.5048 | 3.8787 | 3.8787 | 2019-07-07 08:00 | 2.0501 | 3.5179 | 5.9458 | 5.9458 | 5.9458 | 5.9458
2021-05-09 20:00 | 2.1748 | 2.6932 | 2.7361 | 2.9199 | 2.8464 | 3.0303 | 1.809 | 2.7403 | 3.2625 | 3.2625 | 3.6106 | 3.6106 | 2019-07-07 09:00 | 2.2025 | 3.7795 | 6.3879 | 6.3879 | 6.3879 | 6.3879
2021-05-09 21:00 | 2.1406 | 2.6507 | 2.693 | 2.8739 | 2.8015 | 2.9825 | 1.7033 | 2.5802 | 3.0718 | 3.0718 | 3.3996 | 3.3996 | 2019-07-07 10:00 | 2.1644 | 3.7141 | 6.2774 | 6.2774 | 6.2774 | 6.2774
2021-05-09 22:00 | 1.9462 | 2.4101 | 2.4485 | 2.613 | 2.5472 | 2.7117 | 1.509 | 2.2858 | 2.7213 | 2.7213 | 3.0117 | 3.0117 | 2019-07-07 11:00 | 2.233 | 3.8318 | 6.4763 | 6.4763 | 6.4763 | 6.4763
2021-05-09 23:00 | 1.8148 | 2.2473 | 2.2831 | 2.4365 | 2.3752 | 2.5286 | 1.246 | 1.8875 | 2.2472 | 2.2472 | 2.4869 | 2.4869 | 2019-07-07 12:00 | 2.0805 | 3.5702 | 6.0343 | 6.0343 | 6.0343 | 6.0343
2021-05-10 | 1.6261 | 2.0137 | 2.0458 | 2.1832 | 2.1283 | 2.2657 | 1.0003 | 1.5152 | 1.804 | 1.804 | 1.9964 | 1.9964 | 2019-07-07 13:00 | 2.1949 | 3.7664 | 6.3658 | 6.3658 | 6.3658 | 6.3658
2021-05-10 01:00 | 1.5433 | 1.9111 | 1.9415 | 2.072 | 2.0198 | 2.1502 | 0.93738 | 1.42 | 1.6905 | 1.6905 | 1.8709 | 1.8709 | 2019-07-07 14:00 | 2.0729 | 3.5571 | 6.0121 | 6.0121 | 6.0121 | 6.0121
2021-05-10 02:00 | 1.5547 | 1.9252 | 1.9559 | 2.0873 | 2.0347 | 2.1662 | 0.88308 | 1.3377 | 1.5926 | 1.5926 | 1.7625 | 1.7625 | 2019-07-07 15:00 | 2.1567 | 3.701 | 6.2553 | 6.2553 | 6.2553 | 6.2553
2021-05-10 03:00 | 1.5604 | 1.9323 | 1.9631 | 2.095 | 2.0422 | 2.1741 | 0.85736 | 1.2987 | 1.5462 | 1.5462 | 1.7112 | 1.7112 | 2019-07-07 16:00 | 2.2025 | 3.7795 | 6.3879 | 6.3879 | 6.3879 | 6.3879
2021-05-10 04:00 | 1.6118 | 1.996 | 2.0278 | 2.1641 | 2.1096 | 2.2458 | 0.91166 | 1.381 | 1.6441 | 1.6441 | 1.8196 | 1.8196 | 2019-07-07 17:00 | 2.1567 | 3.701 | 6.2553 | 6.2553 | 6.2553 | 6.2553
2021-05-10 05:00 | 1.9774 | 2.4487 | 2.4877 | 2.6548 | 2.588 | 2.7551 | 0.98597 | 1.4935 | 1.7781 | 1.7781 | 1.9679 | 1.9679 | 2019-07-07 18:00 | 2.0958 | 3.5964 | 6.0785 | 6.0785 | 6.0785 | 6.0785
2021-05-10 06:00 | 2.6407 | 3.2701 | 3.3221 | 3.5454 | 3.4561 | 3.6793 | 1.2196 | 1.8474 | 2.1995 | 2.1995 | 2.4341 | 2.4341 | 2019-07-07 19:00 | 1.9967 | 3.4264 | 5.7911 | 5.7911 | 5.7911 | 5.7911
2021-05-10 07:00 | 2.9122 | 3.6063 | 3.6637 | 3.9099 | 3.8114 | 4.0576 | 1.5147 | 2.2944 | 2.7317 | 2.7317 | 3.0231 | 3.0231 | 2019-07-07 20:00 | 1.9662 | 3.374 | 5.7027 | 5.7027 | 5.7027 | 5.7027
2021-05-10 08:00 | 2.935 | 3.6346 | 3.6925 | 3.9406 | 3.8413 | 4.0894 | 1.5204 | 2.3031 | 2.742 | 2.742 | 3.0345 | 3.0345 | 2019-07-07 21:00 | 1.8138 | 3.1125 | 5.2606 | 5.2606 | 5.2606 | 5.2606
2021-05-10 09:00 | 2.755 | 3.4116 | 3.466 | 3.6989 | 3.6057 | 3.8386 | 1.4747 | 2.2338 | 2.6595 | 2.6595 | 2.9433 | 2.9433 | 2019-07-07 22:00 | 1.6766 | 2.8771 | 4.8628 | 4.8628 | 4.8628 | 4.8628
2021-05-10 10:00 | 2.5978 | 3.217 | 3.2682 | 3.4878 | 3.4 | 3.6196 | 1.5147 | 2.2944 | 2.7317 | 2.7317 | 3.0231 | 3.0231 | 2019-07-07 23:00 | 1.5013 | 2.5763 | 4.3544 | 4.3544 | 4.3544 | 4.3544
2021-05-10 11:00 | 2.5349 | 3.1391 | 3.1891 | 3.4034 | 3.3177 | 3.532 | 1.4747 | 2.2338 | 2.6595 | 2.6595 | 2.9433 | 2.9433 | 2019-07-08 | 1.4861 | 2.5501 | 4.3102 | 4.3102 | 4.3102 | 4.3102
2021-05-10 12:00 | 2.5807 | 3.1957 | 3.2466 | 3.4648 | 3.3775 | 3.5957 | 1.5118 | 2.2901 | 2.7265 | 2.7265 | 3.0174 | 3.0174 | 2019-07-08 01:00 | 1.3794 | 2.3671 | 4.0007 | 4.0007 | 4.0007 | 4.0007
2021-05-10 13:00 | 2.4435 | 3.0259 | 3.0741 | 3.2806 | 3.198 | 3.4046 | 1.5061 | 2.2815 | 2.7162 | 2.7162 | 3.006 | 3.006 | 2019-07-08 02:00 | 1.3946 | 2.3932 | 4.0449 | 4.0449 | 4.0449 | 4.0449
2021-05-10 14:00 | 2.3349 | 2.8914 | 2.9374 | 3.1348 | 3.0559 | 3.2532 | 1.4518 | 2.1992 | 2.6183 | 2.6183 | 2.8976 | 2.8976 | 2019-07-08 03:00 | 1.3946 | 2.3932 | 4.0449 | 4.0449 | 4.0449 | 4.0449
2021-05-10 15:00 | 2.3463 | 2.9055 | 2.9518 | 3.1502 | 3.0708 | 3.2692 | 1.4261 | 2.1602 | 2.5719 | 2.5719 | 2.8463 | 2.8463 | 2019-07-08 04:00 | 1.4785 | 2.5371 | 4.2881 | 4.2881 | 4.2881 | 4.2881
2021-05-10 16:00 | 2.5835 | 3.1993 | 3.2502 | 3.4686 | 3.3813 | 3.5997 | 1.4965 | 2.267 | 2.6989 | 2.6989 | 2.9869 | 2.9869 | 2019-07-08 05:00 | 1.608 | 2.7594 | 4.6638 | 4.6638 | 4.6638 | 4.6638
2021-05-10 17:00 | 2.9952 | 3.709 | 3.7681 | 4.0213 | 3.92 | 4.1732 | 1.809 | 2.7403 | 3.2625 | 3.2625 | 3.6106 | 3.6106 | 2019-07-08 06:00 | 1.8824 | 3.2302 | 5.4596 | 5.4596 | 5.4596 | 5.4596
2021-05-10 18:00 | 3.0465 | 3.7726 | 3.8327 | 4.0902 | 3.9872 | 4.2447 | 1.9748 | 2.9914 | 3.5615 | 3.5615 | 3.9415 | 3.9415 | 2019-07-08 07:00 | 2.1186 | 3.6356 | 6.1448 | 6.1448 | 6.1448 | 6.1448
2021-05-10 19:00 | 2.9671 | 3.6743 | 3.7329 | 3.9837 | 3.8833 | 4.1342 | 1.8948 | 2.8702 | 3.4171 | 3.4171 | 3.7818 | 3.7818 | 2019-07-08 08:00 | 2.2634 | 3.8841 | 6.5647 | 6.5647 | 6.5647 | 6.5647
2021-05-10 20:00 | 2.7093 | 3.355 | 3.4084 | 3.6375 | 3.5459 | 3.7749 | 1.7576 | 2.6624 | 3.1697 | 3.1697 | 3.508 | 3.508 | 2019-07-08 09:00 | 2.2101 | 3.7925 | 6.41 | 6.41 | 6.41 | 6.41
2021-05-10 21:00 | 2.4435 | 3.0259 | 3.0741 | 3.2806 | 3.198 | 3.4046 | 1.6833 | 2.5499 | 3.0357 | 3.0357 | 3.3597 | 3.3597 | 2019-07-08 10:00 | 2.2025 | 3.7795 | 6.3879 | 6.3879 | 6.3879 | 6.3879
2021-05-10 22:00 | 2.2377 | 2.7711 | 2.8152 | 3.0044 | 2.9287 | 3.1179 | 1.5661 | 2.3724 | 2.8244 | 2.8244 | 3.1258 | 3.1258 | 2019-07-08 11:00 | 2.2634 | 3.8841 | 6.5647 | 6.5647 | 6.5647 | 6.5647
2021-05-10 23:00 | 1.9183 | 2.3755 | 2.4134 | 2.5755 | 2.5107 | 2.6728 | 1.3518 | 2.0477 | 2.4379 | 2.4379 | 2.698 | 2.698 | 2019-07-08 12:00 | 2.2711 | 3.8972 | 6.5868 | 6.5868 | 6.5868 | 6.5868
2021-05-11 | 1.6604 | 2.0562 | 2.0889 | 2.2293 | 2.1731 | 2.3135 | 1.0803 | 1.6364 | 1.9482 | 1.9482 | 2.1561 | 2.1561 | 2019-07-08 13:00 | 2.2177 | 3.8056 | 6.4321 | 6.4321 | 6.4321 | 6.4321
2021-05-11 01:00 | 1.4916 | 1.8472 | 1.8766 | 2.0027 | 1.9522 | 2.0783 | 0.92046 | 1.3943 | 1.66 | 1.66 | 1.8371 | 1.8371 | 2019-07-08 14:00 | 2.2482 | 3.8579 | 6.5205 | 6.5205 | 6.5205 | 6.5205
2021-05-11 02:00 | 1.5347 | 1.9005 | 1.9307 | 2.0605 | 2.0086 | 2.1383 | 0.92881 | 1.407 | 1.6751 | 1.6751 | 1.8538 | 1.8538 | 2019-07-08 15:00 | 2.1491 | 3.6879 | 6.2332 | 6.2332 | 6.2332 | 6.2332
2021-05-11 03:00 | 1.5226 | 1.8855 | 1.9155 | 2.0442 | 1.9927 | 2.1214 | 0.89451 | 1.355 | 1.6132 | 1.6132 | 1.7854 | 1.7854 | 2019-07-08 16:00 | 2.2253 | 3.8187 | 6.4542 | 6.4542 | 6.4542 | 6.4542
2021-05-11 04:00 | 1.5833 | 1.9606 | 1.9918 | 2.1257 | 2.0722 | 2.206 | 0.90023 | 1.3637 | 1.6235 | 1.6235 | 1.7968 | 1.7968 | 2019-07-08 17:00 | 2.2101 | 3.7925 | 6.41 | 6.41 | 6.41 | 6.41
2021-05-11 05:00 | 1.8319 | 2.2685 | 2.3046 | 2.4595 | 2.3976 | 2.5524 | 0.98311 | 1.4892 | 1.773 | 1.773 | 1.9622 | 1.9622 | 2019-07-08 18:00 | 2.2177 | 3.8056 | 6.4321 | 6.4321 | 6.4321 | 6.4321
2021-05-11 06:00 | 2.3549 | 2.9162 | 2.9626 | 3.1617 | 3.082 | 3.2811 | 1.2117 | 1.8356 | 2.1853 | 2.1853 | 2.4185 | 2.4185 | 2019-07-08 19:00 | 2.0348 | 3.4917 | 5.9016 | 5.9016 | 5.9016 | 5.9016
2021-05-11 07:00 | 2.6092 | 3.2311 | 3.2826 | 3.5032 | 3.4149 | 3.6355 | 1.5461 | 2.3421 | 2.7883 | 2.7883 | 3.0859 | 3.0859 | 2019-07-08 20:00 | 1.9357 | 3.3217 | 5.6143 | 5.6143 | 5.6143 | 5.6143
2021-05-11 08:00 | 2.6893 | 3.3302 | 3.3833 | 3.6106 | 3.5197 | 3.747 | 1.609 | 2.4373 | 2.9017 | 2.9017 | 3.2114 | 3.2114 | 2019-07-08 21:00 | 1.8367 | 3.1517 | 5.3269 | 5.3269 | 5.3269 | 5.3269
2021-05-11 09:00 | 2.7064 | 3.3515 | 3.4048 | 3.6336 | 3.5421 | 3.7709 | 1.5318 | 2.3204 | 2.7626 | 2.7626 | 3.0574 | 3.0574 | 2019-07-08 22:00 | 1.7452 | 2.9948 | 5.0617 | 5.0617 | 5.0617 | 5.0617
2021-05-11 10:00 | 2.5864 | 3.2028 | 3.2538 | 3.4725 | 3.385 | 3.6036 | 1.5061 | 2.2815 | 2.7162 | 2.7162 | 3.006 | 3.006 | 2019-07-08 23:00 | 1.5775 | 2.7071 | 4.5754 | 4.5754 | 4.5754 | 4.5754
2021-05-11 11:00 | 2.5549 | 3.1639 | 3.2143 | 3.4303 | 3.3439 | 3.5598 | 1.5547 | 2.355 | 2.8038 | 2.8038 | 3.103 | 3.103 | 2019-07-09 | 1.4023 | 2.4063 | 4.067 | 4.067 | 4.067 | 4.067
2021-05-11 12:00 | 2.5692 | 3.1816 | 3.2323 | 3.4494 | 3.3626 | 3.5798 | 1.5375 | 2.3291 | 2.7729 | 2.7729 | 3.0688 | 3.0688 | 2019-07-09 01:00 | 1.4099 | 2.4194 | 4.0891 | 4.0891 | 4.0891 | 4.0891
2021-05-11 13:00 | 2.5092 | 3.1073 | 3.1568 | 3.3689 | 3.284 | 3.4961 | 1.569 | 2.3767 | 2.8296 | 2.8296 | 3.1315 | 3.1315 | 2019-07-09 02:00 | 1.3565 | 2.3278 | 3.9344 | 3.9344 | 3.9344 | 3.9344
2021-05-11 14:00 | 2.4778 | 3.0683 | 3.1172 | 3.3267 | 3.2429 | 3.4523 | 1.5976 | 2.42 | 2.8811 | 2.8811 | 3.1885 | 3.1885 | 2019-07-09 03:00 | 1.3261 | 2.2755 | 3.846 | 3.846 | 3.846 | 3.846
2021-05-11 15:00 | 2.4206 | 2.9976 | 3.0453 | 3.2499 | 3.1681 | 3.3727 | 1.4461 | 2.1905 | 2.608 | 2.608 | 2.8862 | 2.8862 | 2019-07-09 04:00 | 1.4023 | 2.4063 | 4.067 | 4.067 | 4.067 | 4.067
2021-05-11 16:00 | 2.6435 | 3.2736 | 3.3257 | 3.5492 | 3.4598 | 3.6833 | 1.529 | 2.3161 | 2.7574 | 2.7574 | 3.0516 | 3.0516 | 2019-07-09 05:00 | 1.5318 | 2.6286 | 4.4428 | 4.4428 | 4.4428 | 4.4428
2021-05-11 17:00 | 2.9836 | 3.6947 | 3.7536 | 4.0058 | 3.9049 | 4.1571 | 1.8605 | 2.8183 | 3.3553 | 3.3553 | 3.7133 | 3.7133 | 2019-07-09 06:00 | 1.8443 | 3.1648 | 5.349 | 5.349 | 5.349 | 5.349
2021-05-11 18:00 | 3.2466 | 4.0203 | 4.0844 | 4.3588 | 4.249 | 4.5235 | 1.9948 | 3.0217 | 3.5975 | 3.5975 | 3.9814 | 3.9814 | 2019-07-09 07:00 | 2.1339 | 3.6618 | 6.189 | 6.189 | 6.189 | 6.189
2021-05-11 19:00 | 3.138 | 3.8859 | 3.9478 | 4.2131 | 4.107 | 4.3722 | 2.0377 | 3.0867 | 3.6748 | 3.6748 | 4.067 | 4.067 | 2019-07-09 08:00 | 2.2177 | 3.8056 | 6.4321 | 6.4321 | 6.4321 | 6.4321
2021-05-11 20:00 | 2.8207 | 3.493 | 3.5487 | 3.7871 | 3.6917 | 3.9302 | 1.9319 | 2.9265 | 3.4841 | 3.4841 | 3.8559 | 3.8559 | 2019-07-09 09:00 | 2.1949 | 3.7664 | 6.3658 | 6.3658 | 6.3658 | 6.3658
2021-05-11 21:00 | 2.5607 | 3.171 | 3.2215 | 3.4379 | 3.3514 | 3.5678 | 1.8833 | 2.8529 | 3.3965 | 3.3965 | 3.7589 | 3.7589 | 2019-07-09 10:00 | 2.111 | 3.6225 | 6.1227 | 6.1227 | 6.1227 | 6.1227
2021-05-11 22:00 | 2.2177 | 2.7463 | 2.79 | 2.9775 | 2.9025 | 3.09 | 1.6176 | 2.4503 | 2.9172 | 2.9172 | 3.2285 | 3.2285 | 2019-07-09 11:00 | 2.2711 | 3.8972 | 6.5868 | 6.5868 | 6.5868 | 6.5868
2021-05-11 23:00 | 2.0119 | 2.4915 | 2.5312 | 2.7012 | 2.6332 | 2.8033 | 1.2556 | 1.9019 | 2.2643 | 2.2643 | 2.506 | 2.506 | 2019-07-09 12:00 | 2.1796 | 3.7402 | 6.3216 | 6.3216 | 6.3216 | 6.3216
2021-05-12 | 1.7178 | 2.1273 | 2.1611 | 2.3064 | 2.2483 | 2.3935 | 1.0419 | 1.5782 | 1.879 | 1.879 | 2.0795 | 2.0795 | 2019-07-09 13:00 | 2.172 | 3.7271 | 6.2995 | 6.2995 | 6.2995 | 6.2995
2021-05-12 01:00 | 1.6261 | 2.0137 | 2.0458 | 2.1832 | 2.1283 | 2.2657 | 0.95464 | 1.4461 | 1.7217 | 1.7217 | 1.9054 | 1.9054 | 2019-07-09 14:00 | 2.1339 | 3.6618 | 6.189 | 6.189 | 6.189 | 6.189
2021-05-12 02:00 | 1.589 | 1.9677 | 1.999 | 2.1334 | 2.0796 | 2.214 | 0.90595 | 1.3723 | 1.6338 | 1.6338 | 1.8082 | 1.8082 | 2019-07-09 15:00 | 2.1644 | 3.7141 | 6.2774 | 6.2774 | 6.2774 | 6.2774
2021-05-12 03:00 | 1.5833 | 1.9606 | 1.9918 | 2.1257 | 2.0722 | 2.206 | 0.90309 | 1.368 | 1.6287 | 1.6287 | 1.8025 | 1.8025 | 2019-07-09 16:00 | 2.2711 | 3.8972 | 6.5868 | 6.5868 | 6.5868 | 6.5868
2021-05-12 04:00 | 1.709 | 2.1163 | 2.15 | 2.2945 | 2.2367 | 2.3812 | 0.8545 | 1.2944 | 1.5411 | 1.5411 | 1.7055 | 1.7055 | 2019-07-09 17:00 | 2.2482 | 3.8579 | 6.5205 | 6.5205 | 6.5205 | 6.5205
2021-05-12 05:00 | 2.0691 | 2.5623 | 2.6031 | 2.778 | 2.708 | 2.8829 | 0.96025 | 1.4546 | 1.7318 | 1.7318 | 1.9165 | 1.9165 | 2019-07-09 18:00 | 2.2939 | 3.9364 | 6.6531 | 6.6531 | 6.6531 | 6.6531
2021-05-12 06:00 | 2.6035 | 3.2241 | 3.2754 | 3.4955 | 3.4075 | 3.6275 | 1.2232 | 1.8529 | 2.2059 | 2.2059 | 2.4413 | 2.4413 | 2019-07-09 19:00 | 2.1872 | 3.7533 | 6.3437 | 6.3437 | 6.3437 | 6.3437
2021-05-12 07:00 | 3.0065 | 3.7231 | 3.7824 | 4.0365 | 3.9348 | 4.189 | 1.5947 | 2.4157 | 2.876 | 2.876 | 3.1828 | 3.1828 | 2019-07-09 20:00 | 2.1415 | 3.6748 | 6.2111 | 6.2111 | 6.2111 | 6.2111
2021-05-12 08:00 | 2.9208 | 3.6169 | 3.6745 | 3.9214 | 3.8226 | 4.0695 | 1.5604 | 2.3637 | 2.8141 | 2.8141 | 3.1144 | 3.1144 | 2019-07-09 21:00 | 2.0043 | 3.4394 | 5.8132 | 5.8132 | 5.8132 | 5.8132
2021-05-12 09:00 | 2.7264 | 3.3762 | 3.43 | 3.6605 | 3.5683 | 3.7988 | 1.4861 | 2.2511 | 2.6801 | 2.6801 | 2.9661 | 2.9661 | 2019-07-09 22:00 | 1.8443 | 3.1648 | 5.349 | 5.349 | 5.349 | 5.349
2021-05-12 10:00 | 2.5521 | 3.1604 | 3.2107 | 3.4264 | 3.3401 | 3.5559 | 1.5147 | 2.2944 | 2.7317 | 2.7317 | 3.0231 | 3.0231 | 2019-07-09 23:00 | 1.6004 | 2.7463 | 4.6417 | 4.6417 | 4.6417 | 4.6417
2021-05-12 11:00 | 2.4406 | 3.0223 | 3.0705 | 3.2768 | 3.1943 | 3.4006 | 1.4832 | 2.2468 | 2.675 | 2.675 | 2.9604 | 2.9604 | 2019-07-10 | 1.4556 | 2.4978 | 4.2218 | 4.2218 | 4.2218 | 4.2218
2021-05-12 12:00 | 2.5807 | 3.1957 | 3.2466 | 3.4648 | 3.3775 | 3.5957 | 1.4747 | 2.2338 | 2.6595 | 2.6595 | 2.9433 | 2.9433 | 2019-07-10 01:00 | 1.4023 | 2.4063 | 4.067 | 4.067 | 4.067 | 4.067
2021-05-12 13:00 | 2.3463 | 2.9055 | 2.9518 | 3.1502 | 3.0708 | 3.2692 | 1.4043 | 2.1273 | 2.5326 | 2.5326 | 2.8029 | 2.8029 | 2019-07-10 02:00 | 1.3413 | 2.3017 | 3.8902 | 3.8902 | 3.8902 | 3.8902
2021-05-12 14:00 | 2.3006 | 2.8489 | 2.8943 | 3.0888 | 3.011 | 3.2055 | 1.4061 | 2.1299 | 2.5358 | 2.5358 | 2.8064 | 2.8064 | 2019-07-10 03:00 | 1.3642 | 2.3409 | 3.9565 | 3.9565 | 3.9565 | 3.9565
2021-05-12 15:00 | 2.192 | 2.7144 | 2.7577 | 2.943 | 2.8688 | 3.0541 | 1.3632 | 2.065 | 2.4585 | 2.4585 | 2.7208 | 2.7208 | 2019-07-10 04:00 | 1.4251 | 2.4455 | 4.1333 | 4.1333 | 4.1333 | 4.1333
2021-05-12 16:00 | 2.4692 | 3.0577 | 3.1064 | 3.3152 | 3.2317 | 3.4404 | 1.629 | 2.4676 | 2.9378 | 2.9378 | 3.2513 | 3.2513 | 2019-07-10 05:00 | 1.608 | 2.7594 | 4.6638 | 4.6638 | 4.6638 | 4.6638
2021-05-12 17:00 | 2.8522 | 3.532 | 3.5882 | 3.8293 | 3.7329 | 3.974 | 1.8119 | 2.7447 | 3.2677 | 3.2677 | 3.6163 | 3.6163 | 2019-07-10 06:00 | 1.8443 | 3.1648 | 5.349 | 5.349 | 5.349 | 5.349
2021-05-12 18:00 | 3.0779 | 3.8115 | 3.8722 | 4.1324 | 4.0284 | 4.2885 | 1.9748 | 2.9914 | 3.5615 | 3.5615 | 3.9415 | 3.9415 | 2019-07-10 07:00 | 2.2177 | 3.8056 | 6.4321 | 6.4321 | 6.4321 | 6.4321
2021-05-12 19:00 | 2.9039 | 3.596 | 3.6533 | 3.8987 | 3.8005 | 4.046 | 1.9351 | 2.9313 | 3.4899 | 3.4899 | 3.8623 | 3.8623 | 2019-07-10 08:00 | 2.332 | 4.0018 | 6.7637 | 6.7637 | 6.7637 | 6.7637
2021-05-12 20:00 | 2.6721 | 3.309 | 3.3617 | 3.5876 | 3.4972 | 3.7231 | 1.8233 | 2.762 | 3.2883 | 3.2883 | 3.6392 | 3.6392 | 2019-07-10 09:00 | 2.332 | 4.0018 | 6.7637 | 6.7637 | 6.7637 | 6.7637
2021-05-12 21:00 | 2.4838 | 3.0758 | 3.1248 | 3.3347 | 3.2508 | 3.4607 | 1.7636 | 2.6715 | 3.1806 | 3.1806 | 3.52 | 3.52 | 2019-07-10 10:00 | 2.2711 | 3.8972 | 6.5868 | 6.5868 | 6.5868 | 6.5868
2021-05-12 22:00 | 2.1949 | 2.718 | 2.7613 | 2.9468 | 2.8726 | 3.0581 | 1.5575 | 2.3594 | 2.809 | 2.809 | 3.1087 | 3.1087 | 2019-07-10 11:00 | 2.2939 | 3.9364 | 6.6531 | 6.6531 | 6.6531 | 6.6531
2021-05-12 23:00 | 2.0264 | 2.5093 | 2.5493 | 2.7206 | 2.6521 | 2.8234 | 1.2689 | 1.9221 | 2.2884 | 2.2884 | 2.5326 | 2.5326 | 2019-07-10 12:00 | 2.2787 | 3.9102 | 6.6089 | 6.6089 | 6.6089 | 6.6089
2021-05-13 | 1.7087 | 2.116 | 2.1497 | 2.2942 | 2.2364 | 2.3808 | 1.0517 | 1.5931 | 1.8967 | 1.8967 | 2.0991 | 2.0991 | 2019-07-10 13:00 | 2.3168 | 3.9756 | 6.7195 | 6.7195 | 6.7195 | 6.7195
2021-05-13 01:00 | 1.5863 | 1.9643 | 1.9956 | 2.1297 | 2.0761 | 2.2102 | 1.0003 | 1.5152 | 1.804 | 1.804 | 1.9965 | 1.9965 | 2019-07-10 14:00 | 2.3244 | 3.9887 | 6.7416 | 6.7416 | 6.7416 | 6.7416
2021-05-13 02:00 | 1.5318 | 1.8969 | 1.9271 | 2.0566 | 2.0048 | 2.1343 | 0.91452 | 1.3853 | 1.6493 | 1.6493 | 1.8253 | 1.8253 | 2019-07-10 15:00 | 2.2482 | 3.8579 | 6.5205 | 6.5205 | 6.5205 | 6.5205
2021-05-13 03:00 | 1.5833 | 1.9606 | 1.9918 | 2.1257 | 2.0722 | 2.206 | 0.8888 | 1.3464 | 1.6029 | 1.6029 | 1.7739 | 1.7739 | 2019-07-10 16:00 | 2.2177 | 3.8056 | 6.4321 | 6.4321 | 6.4321 | 6.4321
2021-05-13 04:00 | 1.7288 | 2.1408 | 2.1749 | 2.321 | 2.2626 | 2.4087 | 0.91452 | 1.3853 | 1.6493 | 1.6493 | 1.8253 | 1.8253 | 2019-07-10 17:00 | 2.2406 | 3.8448 | 6.4984 | 6.4984 | 6.4984 | 6.4984
2021-05-13 05:00 | 2.0005 | 2.4773 | 2.5168 | 2.6859 | 2.6182 | 2.7874 | 1.0219 | 1.5479 | 1.8429 | 1.8429 | 2.0395 | 2.0395 | 2019-07-10 18:00 | 2.172 | 3.7271 | 6.2995 | 6.2995 | 6.2995 | 6.2995
2021-05-13 06:00 | 2.7221 | 3.3709 | 3.4246 | 3.6547 | 3.5626 | 3.7927 | 1.3897 | 2.1051 | 2.5063 | 2.5063 | 2.7737 | 2.7737 | 2019-07-10 19:00 | 2.0424 | 3.5048 | 5.9237 | 5.9237 | 5.9237 | 5.9237
2021-05-13 07:00 | 3.1522 | 3.9035 | 3.9657 | 4.2322 | 4.1256 | 4.3921 | 1.6576 | 2.5109 | 2.9894 | 2.9894 | 3.3083 | 3.3083 | 2019-07-10 20:00 | 2.0196 | 3.4656 | 5.8574 | 5.8574 | 5.8574 | 5.8574
2021-05-13 08:00 | 3.1865 | 3.946 | 4.0089 | 4.2782 | 4.1705 | 4.4399 | 1.649 | 2.4979 | 2.9739 | 2.9739 | 3.2912 | 3.2912 | 2019-07-10 21:00 | 1.8976 | 3.2563 | 5.5038 | 5.5038 | 5.5038 | 5.5038
2021-05-13 09:00 | 2.8064 | 3.4753 | 3.5307 | 3.7679 | 3.673 | 3.9103 | 1.5347 | 2.3247 | 2.7677 | 2.7677 | 3.0631 | 3.0631 | 2019-07-10 22:00 | 1.8976 | 3.2563 | 5.5038 | 5.5038 | 5.5038 | 5.5038
2021-05-13 10:00 | 2.5664 | 3.178 | 3.2287 | 3.4456 | 3.3588 | 3.5758 | 1.509 | 2.2858 | 2.7213 | 2.7213 | 3.0117 | 3.0117 | 2019-07-10 23:00 | 1.6157 | 2.7725 | 4.6859 | 4.6859 | 4.6859 | 4.6859
2021-05-13 11:00 | 2.3492 | 2.9091 | 2.9554 | 3.154 | 3.0746 | 3.2731 | 1.5147 | 2.2944 | 2.7317 | 2.7317 | 3.0231 | 3.0231 | 2019-07-11 | 1.4785 | 2.5371 | 4.2881 | 4.2881 | 4.2881 | 4.2881
2021-05-13 12:00 | 2.312 | 2.8631 | 2.9087 | 3.1041 | 3.0259 | 3.2214 | 1.4518 | 2.1992 | 2.6183 | 2.6183 | 2.8976 | 2.8976 | 2019-07-11 01:00 | 1.4327 | 2.4586 | 4.1555 | 4.1555 | 4.1555 | 4.1555
2021-05-13 13:00 | 2.4063 | 2.9799 | 3.0273 | 3.2307 | 3.1494 | 3.3528 | 1.4747 | 2.2338 | 2.6595 | 2.6595 | 2.9433 | 2.9433 | 2019-07-11 02:00 | 1.4099 | 2.4194 | 4.0891 | 4.0891 | 4.0891 | 4.0891
2021-05-13 14:00 | 2.3263 | 2.8808 | 2.9267 | 3.1233 | 3.0446 | 3.2413 | 1.4775 | 2.2382 | 2.6646 | 2.6646 | 2.949 | 2.949 | 2019-07-11 03:00 | 1.3642 | 2.3409 | 3.9565 | 3.9565 | 3.9565 | 3.9565
2021-05-13 15:00 | 2.3406 | 2.8985 | 2.9446 | 3.1425 | 3.0633 | 3.2612 | 1.5147 | 2.2944 | 2.7317 | 2.7317 | 3.0231 | 3.0231 | 2019-07-11 04:00 | 1.4937 | 2.5632 | 4.3323 | 4.3323 | 4.3323 | 4.3323
2021-05-13 16:00 | 2.5435 | 3.1497 | 3.1999 | 3.4149 | 3.3289 | 3.5439 | 1.6347 | 2.4763 | 2.9481 | 2.9481 | 3.2627 | 3.2627 | 2019-07-11 05:00 | 1.6538 | 2.8379 | 4.7965 | 4.7965 | 4.7965 | 4.7965
2021-05-13 17:00 | 3.138 | 3.8859 | 3.9477 | 4.213 | 4.1069 | 4.3722 | 1.809 | 2.7403 | 3.2625 | 3.2625 | 3.6106 | 3.6106 | 2019-07-11 06:00 | 1.9205 | 3.2956 | 5.5701 | 5.5701 | 5.5701 | 5.5701
2021-05-13 18:00 | 3.178 | 3.9354 | 3.9981 | 4.2667 | 4.1593 | 4.4279 | 2.0662 | 3.13 | 3.7264 | 3.7264 | 4.124 | 4.124 | 2019-07-11 07:00 | 2.2177 | 3.8056 | 6.4321 | 6.4321 | 6.4321 | 6.4321
2021-05-13 19:00 | 3.0122 | 3.7301 | 3.7896 | 4.0442 | 3.9423 | 4.197 | 2.0148 | 3.052 | 3.6336 | 3.6336 | 4.0213 | 4.0213 | 2019-07-11 08:00 | 2.3092 | 3.9625 | 6.6974 | 6.6974 | 6.6974 | 6.6974
2021-05-13 20:00 | 2.7921 | 3.4576 | 3.5127 | 3.7487 | 3.6543 | 3.8903 | 1.9805 | 3.0001 | 3.5718 | 3.5718 | 3.9529 | 3.9529 | 2019-07-11 09:00 | 2.2634 | 3.8841 | 6.5647 | 6.5647 | 6.5647 | 6.5647
2021-05-13 21:00 | 2.5149 | 3.1143 | 3.164 | 3.3765 | 3.2915 | 3.5041 | 1.8262 | 2.7663 | 3.2934 | 3.2934 | 3.6449 | 3.6449 | 2019-07-11 10:00 | 2.2177 | 3.8056 | 6.4321 | 6.4321 | 6.4321 | 6.4321
2021-05-13 22:00 | 2.2006 | 2.7251 | 2.7685 | 2.9545 | 2.8801 | 3.0661 | 1.6176 | 2.4503 | 2.9172 | 2.9172 | 3.2285 | 3.2285 | 2019-07-11 11:00 | 2.2787 | 3.9102 | 6.6089 | 6.6089 | 6.6089 | 6.6089
2021-05-13 23:00 | 2.0234 | 2.5056 | 2.5455 | 2.7166 | 2.6482 | 2.8192 | 1.2755 | 1.9321 | 2.3003 | 2.3003 | 2.5458 | 2.5458 | 2019-07-11 12:00 | 2.3015 | 3.9495 | 6.6753 | 6.6753 | 6.6753 | 6.6753
2021-05-14 | 1.7236 | 2.1344 | 2.1684 | 2.3141 | 2.2558 | 2.4015 | 1.0603 | 1.6061 | 1.9122 | 1.9122 | 2.1162 | 2.1162 | 2019-07-11 13:00 | 2.3244 | 3.9887 | 6.7416 | 6.7416 | 6.7416 | 6.7416
2021-05-14 01:00 | 1.6433 | 2.0349 | 2.0674 | 2.2063 | 2.1507 | 2.2896 | 0.97739 | 1.4806 | 1.7627 | 1.7627 | 1.9508 | 1.9508 | 2019-07-11 14:00 | 2.3778 | 4.0802 | 6.8963 | 6.8963 | 6.8963 | 6.8963
2021-05-14 02:00 | 1.6147 | 1.9995 | 2.0314 | 2.1679 | 2.1133 | 2.2498 | 0.87451 | 1.3247 | 1.5771 | 1.5771 | 1.7454 | 1.7454 | 2019-07-11 15:00 | 2.332 | 4.0018 | 6.7637 | 6.7637 | 6.7637 | 6.7637
2021-05-14 03:00 | 1.5718 | 1.9465 | 1.9775 | 2.1103 | 2.0572 | 2.1901 | 0.91452 | 1.3853 | 1.6493 | 1.6493 | 1.8253 | 1.8253 | 2019-07-11 16:00 | 2.3244 | 3.9887 | 6.7416 | 6.7416 | 6.7416 | 6.7416
2021-05-14 04:00 | 1.7547 | 2.173 | 2.2076 | 2.3559 | 2.2966 | 2.4449 | 0.88594 | 1.342 | 1.5978 | 1.5978 | 1.7682 | 1.7682 | 2019-07-11 17:00 | 2.2939 | 3.9364 | 6.6531 | 6.6531 | 6.6531 | 6.6531
2021-05-14 05:00 | 2.0403 | 2.5266 | 2.5669 | 2.7394 | 2.6704 | 2.8428 | 0.9974 | 1.5109 | 1.7988 | 1.7988 | 1.9907 | 1.9907 | 2019-07-11 18:00 | 2.2787 | 3.9102 | 6.6089 | 6.6089 | 6.6089 | 6.6089
2021-05-14 06:00 | 2.695 | 3.3373 | 3.3905 | 3.6183 | 3.5271 | 3.755 | 1.3042 | 1.9756 | 2.3521 | 2.3521 | 2.603 | 2.603 | 2019-07-11 19:00 | 2.1567 | 3.701 | 6.2553 | 6.2553 | 6.2553 | 6.2553
2021-05-14 07:00 | 3.0494 | 3.7761 | 3.8363 | 4.0941 | 3.991 | 4.2487 | 1.5575 | 2.3594 | 2.809 | 2.809 | 3.1087 | 3.1087 | 2019-07-11 20:00 | 2.0424 | 3.5048 | 5.9237 | 5.9237 | 5.9237 | 5.9237
2021-05-14 08:00 | 2.9951 | 3.7089 | 3.768 | 4.0212 | 3.9199 | 4.1731 | 1.569 | 2.3767 | 2.8296 | 2.8296 | 3.1315 | 3.1315 | 2019-07-11 21:00 | 1.951 | 3.3479 | 5.6585 | 5.6585 | 5.6585 | 5.6585
2021-05-14 09:00 | 2.7436 | 3.3975 | 3.4516 | 3.6835 | 3.5907 | 3.8227 | 1.5032 | 2.2771 | 2.711 | 2.711 | 3.0003 | 3.0003 | 2019-07-11 22:00 | 1.7071 | 2.9294 | 4.9512 | 4.9512 | 4.9512 | 4.9512
2021-05-14 10:00 | 2.6778 | 3.3161 | 3.3689 | 3.5953 | 3.5047 | 3.7311 | 1.5318 | 2.3204 | 2.7626 | 2.7626 | 3.0574 | 3.0574 | 2019-07-11 23:00 | 1.4937 | 2.5632 | 4.3323 | 4.3323 | 4.3323 | 4.3323
2021-05-14 11:00 | 2.4463 | 3.0294 | 3.0777 | 3.2845 | 3.2017 | 3.4085 | 1.5404 | 2.3334 | 2.778 | 2.778 | 3.0745 | 3.0745 | 2019-07-12 | 1.3413 | 2.3017 | 3.8902 | 3.8902 | 3.8902 | 3.8902
2021-05-14 12:00 | 2.5121 | 3.1108 | 3.1604 | 3.3727 | 3.2878 | 3.5001 | 1.5204 | 2.3031 | 2.742 | 2.742 | 3.0345 | 3.0345 | 2019-07-12 01:00 | 1.3184 | 2.2624 | 3.8239 | 3.8239 | 3.8239 | 3.8239
2021-05-14 13:00 | 2.4435 | 3.0259 | 3.0741 | 3.2806 | 3.198 | 3.4046 | 1.5032 | 2.2771 | 2.711 | 2.711 | 3.0003 | 3.0003 | 2019-07-12 02:00 | 1.2879 | 2.2101 | 3.7355 | 3.7355 | 3.7355 | 3.7355
2021-05-14 14:00 | 2.392 | 2.9622 | 3.0093 | 3.2116 | 3.1307 | 3.3329 | 1.5204 | 2.3031 | 2.742 | 2.742 | 3.0345 | 3.0345 | 2019-07-12 03:00 | 1.2498 | 2.1447 | 3.625 | 3.625 | 3.625 | 3.625
2021-05-14 15:00 | 2.5159 | 3.1155 | 3.1651 | 3.3778 | 3.2927 | 3.5054 | 1.489 | 2.2555 | 2.6853 | 2.6853 | 2.9718 | 2.9718 | 2019-07-12 04:00 | 1.2803 | 2.1971 | 3.7134 | 3.7134 | 3.7134 | 3.7134
2021-05-14 16:00 | 2.7721 | 3.4329 | 3.4875 | 3.7219 | 3.6281 | 3.8625 | 1.7262 | 2.6148 | 3.1131 | 3.1131 | 3.4452 | 3.4452 | 2019-07-12 05:00 | 1.5166 | 2.6025 | 4.3986 | 4.3986 | 4.3986 | 4.3986
2021-05-14 17:00 | 3.0694 | 3.8009 | 3.8615 | 4.1209 | 4.0171 | 4.2766 | 1.9719 | 2.9871 | 3.5563 | 3.5563 | 3.9358 | 3.9358 | 2019-07-12 06:00 | 1.7681 | 3.034 | 5.128 | 5.128 | 5.128 | 5.128
2021-05-14 18:00 | 3.1465 | 3.8965 | 3.9585 | 4.2245 | 4.1181 | 4.3841 | 2.1291 | 3.2252 | 3.8398 | 3.8398 | 4.2495 | 4.2495 | 2019-07-12 07:00 | 2.1339 | 3.6618 | 6.189 | 6.189 | 6.189 | 6.189
2021-05-14 19:00 | 2.9838 | 3.695 | 3.7538 | 4.0061 | 3.9052 | 4.1574 | 2.1748 | 3.2945 | 3.9222 | 3.9222 | 4.3408 | 4.3408 | 2019-07-12 08:00 | 2.332 | 4.0018 | 6.7637 | 6.7637 | 6.7637 | 6.7637
2021-05-14 20:00 | 2.7521 | 3.4081 | 3.4624 | 3.695 | 3.602 | 3.8346 | 2.1406 | 3.2425 | 3.8604 | 3.8604 | 4.2723 | 4.2723 | 2019-07-12 09:00 | 2.2482 | 3.8579 | 6.5205 | 6.5205 | 6.5205 | 6.5205
2021-05-14 21:00 | 2.5778 | 3.1922 | 3.243 | 3.461 | 3.3738 | 3.5917 | 1.9634 | 2.9741 | 3.5408 | 3.5408 | 3.9187 | 3.9187 | 2019-07-12 10:00 | 2.1034 | 3.6094 | 6.1006 | 6.1006 | 6.1006 | 6.1006
2021-05-14 22:00 | 2.3549 | 2.9162 | 2.9626 | 3.1617 | 3.082 | 3.2811 | 1.7176 | 2.6018 | 3.0976 | 3.0976 | 3.4281 | 3.4281 | 2019-07-12 11:00 | 2.2634 | 3.8841 | 6.5647 | 6.5647 | 6.5647 | 6.5647
2021-05-14 23:00 | 2.1063 | 2.6083 | 2.6498 | 2.8279 | 2.7566 | 2.9347 | 1.4632 | 2.2165 | 2.6389 | 2.6389 | 2.9205 | 2.9205 | 2019-07-12 12:00 | 2.2558 | 3.871 | 6.5426 | 6.5426 | 6.5426 | 6.5426
2021-05-15 | 1.8376 | 2.2756 | 2.3118 | 2.4672 | 2.405 | 2.5604 | 1.1948 | 1.8099 | 2.1548 | 2.1548 | 2.3847 | 2.3847 | 2019-07-12 13:00 | 2.0424 | 3.5048 | 5.9237 | 5.9237 | 5.9237 | 5.9237
2021-05-15 01:00 | 1.7233 | 2.134 | 2.168 | 2.3137 | 2.2554 | 2.4011 | 1.1231 | 1.7013 | 2.0255 | 2.0255 | 2.2417 | 2.2417 | 2019-07-12 14:00 | 2.0729 | 3.5571 | 6.0121 | 6.0121 | 6.0121 | 6.0121
2021-05-15 02:00 | 1.6604 | 2.0562 | 2.0889 | 2.2293 | 2.1731 | 2.3135 | 1.0032 | 1.5196 | 1.8092 | 1.8092 | 2.0022 | 2.0022 | 2019-07-12 15:00 | 2.1491 | 3.6879 | 6.2332 | 6.2332 | 6.2332 | 6.2332
2021-05-15 03:00 | 1.6376 | 2.0279 | 2.0602 | 2.1986 | 2.1432 | 2.2816 | 0.9631 | 1.4589 | 1.7369 | 1.7369 | 1.9223 | 1.9223 | 2019-07-12 16:00 | 2.2482 | 3.8579 | 6.5205 | 6.5205 | 6.5205 | 6.5205
2021-05-15 04:00 | 1.6661 | 2.0633 | 2.0961 | 2.237 | 2.1806 | 2.3215 | 0.98025 | 1.4849 | 1.7678 | 1.7678 | 1.9565 | 1.9565 | 2019-07-12 17:00 | 2.111 | 3.6225 | 6.1227 | 6.1227 | 6.1227 | 6.1227
2021-05-15 05:00 | 1.809 | 2.2402 | 2.2759 | 2.4288 | 2.3676 | 2.5206 | 1.0057 | 1.5234 | 1.8137 | 1.8137 | 2.0072 | 2.0072 | 2019-07-12 18:00 | 2.0272 | 3.4787 | 5.8795 | 5.8795 | 5.8795 | 5.8795
2021-05-15 06:00 | 2.0298 | 2.5136 | 2.5537 | 2.7252 | 2.6566 | 2.8282 | 1.2003 | 1.8182 | 2.1647 | 2.1647 | 2.3957 | 2.3957 | 2019-07-12 19:00 | 2.0043 | 3.4394 | 5.8132 | 5.8132 | 5.8132 | 5.8132
2021-05-15 07:00 | 2.2663 | 2.8064 | 2.8512 | 3.0427 | 2.9661 | 3.1577 | 1.4461 | 2.1905 | 2.608 | 2.608 | 2.8862 | 2.8862 | 2019-07-12 20:00 | 1.8748 | 3.2171 | 5.4375 | 5.4375 | 5.4375 | 5.4375
2021-05-15 08:00 | 2.4978 | 3.0931 | 3.1424 | 3.3535 | 3.2691 | 3.4802 | 1.6061 | 2.433 | 2.8966 | 2.8966 | 3.2057 | 3.2057 | 2019-07-12 21:00 | 1.7452 | 2.9948 | 5.0617 | 5.0617 | 5.0617 | 5.0617
2021-05-15 09:00 | 2.4235 | 3.0011 | 3.0489 | 3.2538 | 3.1718 | 3.3767 | 1.7147 | 2.5975 | 3.0924 | 3.0924 | 3.4224 | 3.4224 | 2019-07-12 22:00 | 1.6233 | 2.7855 | 4.708 | 4.708 | 4.708 | 4.708
2021-05-15 10:00 | 2.4035 | 2.9763 | 3.0237 | 3.2269 | 3.1456 | 3.3488 | 1.7947 | 2.7187 | 3.2368 | 3.2368 | 3.5821 | 3.5821 | 2019-07-12 23:00 | 1.4709 | 2.524 | 4.266 | 4.266 | 4.266 | 4.266
2021-05-15 11:00 | 2.2777 | 2.8206 | 2.8655 | 3.0581 | 2.9811 | 3.1736 | 1.8205 | 2.7577 | 3.2831 | 3.2831 | 3.6335 | 3.6335 | 2019-07-13 | 1.2879 | 2.2101 | 3.7355 | 3.7355 | 3.7355 | 3.7355
2021-05-15 12:00 | 2.3292 | 2.8843 | 2.9302 | 3.1271 | 3.0484 | 3.2453 | 1.8176 | 2.7533 | 3.278 | 3.278 | 3.6278 | 3.6278 | 2019-07-13 01:00 | 1.2575 | 2.1578 | 3.6471 | 3.6471 | 3.6471 | 3.6471
2021-05-15 13:00 | 2.0577 | 2.5481 | 2.5887 | 2.7626 | 2.6931 | 2.867 | 1.7947 | 2.7187 | 3.2368 | 3.2368 | 3.5821 | 3.5821 | 2019-07-13 02:00 | 1.1736 | 2.014 | 3.4039 | 3.4039 | 3.4039 | 3.4039
2021-05-15 14:00 | 2.0462 | 2.5339 | 2.5743 | 2.7473 | 2.6781 | 2.8511 | 1.7572 | 2.6619 | 3.1691 | 3.1691 | 3.5072 | 3.5072 | 2019-07-13 03:00 | 1.2498 | 2.1447 | 3.625 | 3.625 | 3.625 | 3.625
2021-05-15 15:00 | 2.0863 | 2.5835 | 2.6246 | 2.801 | 2.7305 | 2.9068 | 1.689 | 2.5585 | 3.0461 | 3.0461 | 3.3711 | 3.3711 | 2019-07-13 04:00 | 1.2575 | 2.1578 | 3.6471 | 3.6471 | 3.6471 | 3.6471
2021-05-15 16:00 | 2.3235 | 2.8772 | 2.9231 | 3.1195 | 3.0409 | 3.2373 | 1.8535 | 2.8076 | 3.3427 | 3.3427 | 3.6993 | 3.6993 | 2019-07-13 05:00 | 1.4099 | 2.4194 | 4.0891 | 4.0891 | 4.0891 | 4.0891
2021-05-15 17:00 | 2.8779 | 3.5638 | 3.6206 | 3.8638 | 3.7665 | 4.0098 | 2.172 | 3.2901 | 3.9171 | 3.9171 | 4.3351 | 4.3351 | 2019-07-13 06:00 | 1.4785 | 2.5371 | 4.2881 | 4.2881 | 4.2881 | 4.2881
2021-05-15 18:00 | 2.9208 | 3.6169 | 3.6745 | 3.9214 | 3.8226 | 4.0695 | 2.4749 | 3.749 | 4.4634 | 4.4634 | 4.9397 | 4.9397 | 2019-07-13 07:00 | 1.6614 | 2.8509 | 4.8186 | 4.8186 | 4.8186 | 4.8186
2021-05-15 19:00 | 2.8179 | 3.4895 | 3.5451 | 3.7833 | 3.688 | 3.9262 | 2.2091 | 3.3464 | 3.9841 | 3.9841 | 4.4092 | 4.4092 | 2019-07-13 08:00 | 1.7605 | 3.0209 | 5.1059 | 5.1059 | 5.1059 | 5.1059
2021-05-15 20:00 | 2.6524 | 3.2845 | 3.3369 | 3.5611 | 3.4714 | 3.6956 | 2.1463 | 3.2512 | 3.8707 | 3.8707 | 4.2837 | 4.2837 | 2019-07-13 09:00 | 1.9129 | 3.2825 | 5.548 | 5.548 | 5.548 | 5.548
2021-05-15 21:00 | 2.5664 | 3.178 | 3.2287 | 3.4456 | 3.3588 | 3.5758 | 2.0291 | 3.0737 | 3.6594 | 3.6594 | 4.0499 | 4.0499 | 2019-07-13 10:00 | 1.9967 | 3.4264 | 5.7911 | 5.7911 | 5.7911 | 5.7911
2021-05-15 22:00 | 2.5006 | 3.0966 | 3.146 | 3.3574 | 3.2728 | 3.4842 | 1.8691 | 2.8313 | 3.3708 | 3.3708 | 3.7304 | 3.7304 | 2019-07-13 11:00 | 2.0272 | 3.4787 | 5.8795 | 5.8795 | 5.8795 | 5.8795
2021-05-15 23:00 | 2.3162 | 2.8682 | 2.9139 | 3.1097 | 3.0314 | 3.2272 | 1.5547 | 2.355 | 2.8038 | 2.8038 | 3.103 | 3.103 | 2019-07-13 12:00 | 2.0196 | 3.4656 | 5.8574 | 5.8574 | 5.8574 | 5.8574
2021-05-16 | 2.1167 | 2.6211 | 2.6629 | 2.8418 | 2.7702 | 2.9492 | 1.3889 | 2.104 | 2.5049 | 2.5049 | 2.7722 | 2.7722 | 2019-07-13 13:00 | 1.9815 | 3.4002 | 5.7469 | 5.7469 | 5.7469 | 5.7469
2021-05-16 01:00 | 1.9977 | 2.4738 | 2.5132 | 2.682 | 2.6145 | 2.7834 | 1.2175 | 1.8442 | 2.1956 | 2.1956 | 2.4299 | 2.4299 | 2019-07-13 14:00 | 1.9357 | 3.3217 | 5.6143 | 5.6143 | 5.6143 | 5.6143
2021-05-16 02:00 | 1.8948 | 2.3464 | 2.3837 | 2.5439 | 2.4799 | 2.64 | 1.1832 | 1.7923 | 2.1338 | 2.1338 | 2.3615 | 2.3615 | 2019-07-13 15:00 | 1.9967 | 3.4264 | 5.7911 | 5.7911 | 5.7911 | 5.7911
2021-05-16 03:00 | 1.9176 | 2.3747 | 2.4125 | 2.5746 | 2.5098 | 2.6719 | 1.1317 | 1.7143 | 2.041 | 2.041 | 2.2588 | 2.2588 | 2019-07-13 16:00 | 2.0653 | 3.5441 | 5.99 | 5.99 | 5.99 | 5.99
2021-05-16 04:00 | 1.9429 | 2.4059 | 2.4442 | 2.6085 | 2.5428 | 2.707 | 1.1289 | 1.71 | 2.0359 | 2.0359 | 2.2531 | 2.2531 | 2019-07-13 17:00 | 2.0424 | 3.5048 | 5.9237 | 5.9237 | 5.9237 | 5.9237
2021-05-16 05:00 | 2.0199 | 2.5013 | 2.5411 | 2.7119 | 2.6436 | 2.8143 | 1.1089 | 1.6797 | 1.9998 | 1.9998 | 2.2132 | 2.2132 | 2019-07-13 18:00 | 1.9967 | 3.4264 | 5.7911 | 5.7911 | 5.7911 | 5.7911
2021-05-16 06:00 | 2.272 | 2.8135 | 2.8583 | 3.0504 | 2.9736 | 3.1656 | 1.2603 | 1.9091 | 2.2729 | 2.2729 | 2.5155 | 2.5155 | 2019-07-13 19:00 | 1.9053 | 3.2694 | 5.5259 | 5.5259 | 5.5259 | 5.5259
2021-05-16 07:00 | 2.5807 | 3.1957 | 3.2466 | 3.4648 | 3.3775 | 3.5957 | 1.5061 | 2.2815 | 2.7162 | 2.7162 | 3.006 | 3.006 | 2019-07-13 20:00 | 1.829 | 3.1386 | 5.3048 | 5.3048 | 5.3048 | 5.3048
2021-05-16 08:00 | 2.6578 | 3.2913 | 3.3437 | 3.5684 | 3.4785 | 3.7032 | 1.6633 | 2.5196 | 2.9997 | 2.9997 | 3.3197 | 3.3197 | 2019-07-13 21:00 | 1.7452 | 2.9948 | 5.0617 | 5.0617 | 5.0617 | 5.0617
2021-05-16 09:00 | 2.5978 | 3.217 | 3.2682 | 3.4878 | 3.4 | 3.6196 | 1.809 | 2.7403 | 3.2625 | 3.2625 | 3.6106 | 3.6106 | 2019-07-13 22:00 | 1.7147 | 2.9425 | 4.9733 | 4.9733 | 4.9733 | 4.9733
2021-05-16 10:00 | 2.5664 | 3.178 | 3.2287 | 3.4456 | 3.3588 | 3.5758 | 1.8948 | 2.8702 | 3.4171 | 3.4171 | 3.7818 | 3.7818 | 2019-07-13 23:00 | 1.4709 | 2.524 | 4.266 | 4.266 | 4.266 | 4.266
2021-05-16 11:00 | 2.2663 | 2.8064 | 2.8512 | 3.0427 | 2.9661 | 3.1577 | 1.9491 | 2.9525 | 3.5151 | 3.5151 | 3.8901 | 3.8901 | 2019-07-14 | 1.3565 | 2.3278 | 3.9344 | 3.9344 | 3.9344 | 3.9344
2021-05-16 12:00 | 2.1491 | 2.6613 | 2.7037 | 2.8854 | 2.8127 | 2.9944 | 1.8519 | 2.8053 | 3.3398 | 3.3398 | 3.6962 | 3.6962 | 2019-07-14 01:00 | 1.2346 | 2.1186 | 3.5808 | 3.5808 | 3.5808 | 3.5808
2021-05-16 13:00 | 2.1577 | 2.672 | 2.7145 | 2.8969 | 2.824 | 3.0064 | 1.8405 | 2.788 | 3.3192 | 3.3192 | 3.6734 | 3.6734 | 2019-07-14 02:00 | 1.2117 | 2.0794 | 3.5144 | 3.5144 | 3.5144 | 3.5144
2021-05-16 14:00 | 2.2463 | 2.7817 | 2.826 | 3.0159 | 2.9399 | 3.1298 | 1.8433 | 2.7923 | 3.3244 | 3.3244 | 3.6791 | 3.6791 | 2019-07-14 03:00 | 1.1889 | 2.0401 | 3.4481 | 3.4481 | 3.4481 | 3.4481
2021-05-16 15:00 | 2.4292 | 3.0082 | 3.0561 | 3.2614 | 3.1793 | 3.3846 | 1.8433 | 2.7923 | 3.3244 | 3.3244 | 3.6791 | 3.6791 | 2019-07-14 04:00 | 1.1889 | 2.0401 | 3.4481 | 3.4481 | 3.4481 | 3.4481
2021-05-16 16:00 | 2.9098 | 3.6033 | 3.6607 | 3.9066 | 3.8082 | 4.0542 | 2.1863 | 3.3118 | 3.9429 | 3.9429 | 4.3636 | 4.3636 | 2019-07-14 05:00 | 1.4175 | 2.4324 | 4.1112 | 4.1112 | 4.1112 | 4.1112
2021-05-16 17:00 | 3.4552 | 4.2787 | 4.3468 | 4.6389 | 4.5221 | 4.8142 | 2.4349 | 3.6884 | 4.3913 | 4.3913 | 4.8598 | 4.8598 | 2019-07-14 06:00 | 1.4251 | 2.4455 | 4.1333 | 4.1333 | 4.1333 | 4.1333
2021-05-16 18:00 | 3.5152 | 4.353 | 4.4223 | 4.7195 | 4.6006 | 4.8978 | 2.5549 | 3.8702 | 4.6077 | 4.6077 | 5.0994 | 5.0994 | 2019-07-14 07:00 | 1.6461 | 2.8248 | 4.7743 | 4.7743 | 4.7743 | 4.7743
2021-05-16 19:00 | 3.4609 | 4.2858 | 4.354 | 4.6466 | 4.5296 | 4.8221 | 2.5206 | 3.8183 | 4.5459 | 4.5459 | 5.0309 | 5.0309 | 2019-07-14 08:00 | 1.9053 | 3.2694 | 5.5259 | 5.5259 | 5.5259 | 5.5259
2021-05-16 20:00 | 3.1437 | 3.8929 | 3.9549 | 4.2207 | 4.1144 | 4.3801 | 2.4321 | 3.6841 | 4.3861 | 4.3861 | 4.8541 | 4.8541 | 2019-07-14 09:00 | 1.9129 | 3.2825 | 5.548 | 5.548 | 5.548 | 5.548
2021-05-16 21:00 | 2.9954 | 3.7093 | 3.7684 | 4.0216 | 3.9204 | 4.1736 | 2.1748 | 3.2945 | 3.9222 | 3.9222 | 4.3408 | 4.3408 | 2019-07-14 10:00 | 1.951 | 3.3479 | 5.6585 | 5.6585 | 5.6585 | 5.6585
2021-05-16 22:00 | 2.4778 | 3.0683 | 3.1172 | 3.3267 | 3.2429 | 3.4523 | 2.0348 | 3.0823 | 3.6697 | 3.6697 | 4.0613 | 4.0613 | 2019-07-14 11:00 | 1.9434 | 3.3348 | 5.6364 | 5.6364 | 5.6364 | 5.6364
2021-05-16 23:00 | 2.3063 | 2.856 | 2.9015 | 3.0964 | 3.0185 | 3.2134 | 1.6351 | 2.4768 | 2.9488 | 2.9488 | 3.2634 | 3.2634 | 2019-07-14 12:00 | 1.9815 | 3.4002 | 5.7469 | 5.7469 | 5.7469 | 5.7469
2021-05-17 | 2.0977 | 2.5976 | 2.639 | 2.8163 | 2.7454 | 2.9227 | 1.3261 | 2.0087 | 2.3915 | 2.3915 | 2.6467 | 2.6467 | 2019-07-14 13:00 | 2.0958 | 3.5964 | 6.0785 | 6.0785 | 6.0785 | 6.0785
2021-05-17 01:00 | 1.8862 | 2.3358 | 2.373 | 2.5324 | 2.4686 | 2.6281 | 1.1431 | 1.7317 | 2.0616 | 2.0616 | 2.2816 | 2.2816 | 2019-07-14 14:00 | 1.9815 | 3.4002 | 5.7469 | 5.7469 | 5.7469 | 5.7469
2021-05-17 02:00 | 1.8433 | 2.2827 | 2.319 | 2.4749 | 2.4125 | 2.5683 | 1.0603 | 1.6061 | 1.9122 | 1.9122 | 2.1162 | 2.1162 | 2019-07-14 15:00 | 2.0272 | 3.4787 | 5.8795 | 5.8795 | 5.8795 | 5.8795
2021-05-17 03:00 | 1.8662 | 2.311 | 2.3478 | 2.5055 | 2.4424 | 2.6002 | 1.0717 | 1.6234 | 1.9328 | 1.9328 | 2.139 | 2.139 | 2019-07-14 16:00 | 2.1339 | 3.6618 | 6.189 | 6.189 | 6.189 | 6.189
2021-05-17 04:00 | 1.9719 | 2.4419 | 2.4808 | 2.6475 | 2.5808 | 2.7475 | 1.0744 | 1.6275 | 1.9376 | 1.9376 | 2.1444 | 2.1444 | 2019-07-14 17:00 | 2.0501 | 3.5179 | 5.9458 | 5.9458 | 5.9458 | 5.9458
2021-05-17 05:00 | 2.4463 | 3.0294 | 3.0777 | 3.2845 | 3.2017 | 3.4085 | 1.2317 | 1.8659 | 2.2214 | 2.2214 | 2.4584 | 2.4584 | 2019-07-14 18:00 | 1.9891 | 3.4133 | 5.769 | 5.769 | 5.769 | 5.769
2021-05-17 06:00 | 3.178 | 3.9354 | 3.9981 | 4.2667 | 4.1593 | 4.4279 | 1.5061 | 2.2815 | 2.7162 | 2.7162 | 3.006 | 3.006 | 2019-07-14 19:00 | 1.9891 | 3.4133 | 5.769 | 5.769 | 5.769 | 5.769
2021-05-17 07:00 | 3.7067 | 4.5901 | 4.6632 | 4.9766 | 4.8512 | 5.1646 | 1.9148 | 2.9005 | 3.4532 | 3.4532 | 3.8217 | 3.8217 | 2019-07-14 20:00 | 1.8976 | 3.2563 | 5.5038 | 5.5038 | 5.5038 | 5.5038
2021-05-17 08:00 | 3.6066 | 4.4663 | 4.5374 | 4.8423 | 4.7203 | 5.0252 | 1.7605 | 2.6667 | 3.1749 | 3.1749 | 3.5137 | 3.5137 | 2019-07-14 21:00 | 1.7605 | 3.0209 | 5.1059 | 5.1059 | 5.1059 | 5.1059
2021-05-17 09:00 | 3.2723 | 4.0522 | 4.1167 | 4.3933 | 4.2827 | 4.5593 | 1.6233 | 2.4589 | 2.9275 | 2.9275 | 3.2399 | 3.2399 | 2019-07-14 22:00 | 1.5394 | 2.6417 | 4.4649 | 4.4649 | 4.4649 | 4.4649
2021-05-17 10:00 | 2.9722 | 3.6806 | 3.7392 | 3.9905 | 3.89 | 4.1412 | 1.6433 | 2.4893 | 2.9636 | 2.9636 | 3.2798 | 3.2798 | 2019-07-14 23:00 | 1.3946 | 2.3932 | 4.0449 | 4.0449 | 4.0449 | 4.0449
2021-05-17 11:00 | 2.7921 | 3.4576 | 3.5127 | 3.7487 | 3.6543 | 3.8903 | 1.689 | 2.5585 | 3.0461 | 3.0461 | 3.3711 | 3.3711 | 2019-07-15 | 1.2575 | 2.1578 | 3.6471 | 3.6471 | 3.6471 | 3.6471
2021-05-17 12:00 | 2.7407 | 3.3939 | 3.448 | 3.6797 | 3.587 | 3.8187 | 1.6747 | 2.5369 | 3.0203 | 3.0203 | 3.3426 | 3.3426 | 2019-07-15 01:00 | 1.3184 | 2.2624 | 3.8239 | 3.8239 | 3.8239 | 3.8239
2021-05-17 13:00 | 2.7464 | 3.401 | 3.4552 | 3.6873 | 3.5945 | 3.8266 | 1.6261 | 2.4633 | 2.9327 | 2.9327 | 3.2456 | 3.2456 | 2019-07-15 02:00 | 1.2194 | 2.0924 | 3.5366 | 3.5366 | 3.5366 | 3.5366
2021-05-17 14:00 | 2.6835 | 3.3231 | 3.3761 | 3.6029 | 3.5122 | 3.739 | 1.6318 | 2.4719 | 2.943 | 2.943 | 3.257 | 3.257 | 2019-07-15 03:00 | 1.2194 | 2.0924 | 3.5366 | 3.5366 | 3.5366 | 3.5366
2021-05-17 15:00 | 2.6771 | 3.3152 | 3.368 | 3.5943 | 3.5038 | 3.7301 | 1.6576 | 2.5109 | 2.9894 | 2.9894 | 3.3083 | 3.3083 | 2019-07-15 04:00 | 1.4785 | 2.5371 | 4.2881 | 4.2881 | 4.2881 | 4.2881
2021-05-17 16:00 | 3.0837 | 3.8186 | 3.8794 | 4.1401 | 4.0358 | 4.2965 | 2.0148 | 3.052 | 3.6336 | 3.6336 | 4.0213 | 4.0213 | 2019-07-15 05:00 | 1.5166 | 2.6025 | 4.3986 | 4.3986 | 4.3986 | 4.3986
2021-05-17 17:00 | 3.653 | 4.5237 | 4.5957 | 4.9045 | 4.781 | 5.0898 | 2.2006 | 3.3334 | 3.9686 | 3.9686 | 4.3921 | 4.3921 | 2019-07-15 06:00 | 1.7605 | 3.0209 | 5.1059 | 5.1059 | 5.1059 | 5.1059
2021-05-17 18:00 | 3.7524 | 4.6467 | 4.7208 | 5.038 | 4.9111 | 5.2283 | 2.4206 | 3.6668 | 4.3655 | 4.3655 | 4.8313 | 4.8313 | 2019-07-15 07:00 | 2.1415 | 3.6748 | 6.2111 | 6.2111 | 6.2111 | 6.2111
2021-05-17 19:00 | 3.655 | 4.5261 | 4.5982 | 4.9072 | 4.7836 | 5.0926 | 2.4921 | 3.775 | 4.4943 | 4.4943 | 4.9739 | 4.9739 | 2019-07-15 08:00 | 2.2253 | 3.8187 | 6.4542 | 6.4542 | 6.4542 | 6.4542
2021-05-17 20:00 | 3.3866 | 4.1937 | 4.2605 | 4.5468 | 4.4323 | 4.7186 | 2.3835 | 3.6105 | 4.2985 | 4.2985 | 4.7572 | 4.7572 | 2019-07-15 09:00 | 2.1949 | 3.7664 | 6.3658 | 6.3658 | 6.3658 | 6.3658
2021-05-17 21:00 | 3.0465 | 3.7726 | 3.8327 | 4.0902 | 3.9872 | 4.2447 | 2.2349 | 3.3854 | 4.0305 | 4.0305 | 4.4605 | 4.4605 | 2019-07-15 10:00 | 2.0882 | 3.5833 | 6.0564 | 6.0564 | 6.0564 | 6.0564
2021-05-17 22:00 | 2.6321 | 3.2594 | 3.3114 | 3.5339 | 3.4449 | 3.6674 | 1.9605 | 2.9698 | 3.5357 | 3.5357 | 3.913 | 3.913 | 2019-07-15 11:00 | 2.1034 | 3.6094 | 6.1006 | 6.1006 | 6.1006 | 6.1006
2021-05-17 23:00 | 2.4006 | 2.9728 | 3.0201 | 3.2231 | 3.1419 | 3.3448 | 1.5575 | 2.3594 | 2.809 | 2.809 | 3.1087 | 3.1087 | 2019-07-15 12:00 | 2.1567 | 3.701 | 6.2553 | 6.2553 | 6.2553 | 6.2553
2021-05-18 | 2.1234 | 2.6295 | 2.6714 | 2.8509 | 2.7791 | 2.9586 | 1.3032 | 1.9741 | 2.3503 | 2.3503 | 2.601 | 2.601 | 2019-07-15 13:00 | 2.0882 | 3.5833 | 6.0564 | 6.0564 | 6.0564 | 6.0564
2021-05-18 01:00 | 1.9434 | 2.4065 | 2.4449 | 2.6091 | 2.5434 | 2.7077 | 1.1717 | 1.7749 | 2.1132 | 2.1132 | 2.3386 | 2.3386 | 2019-07-15 14:00 | 2.1263 | 3.6487 | 6.1669 | 6.1669 | 6.1669 | 6.1669
2021-05-18 02:00 | 1.9519 | 2.4172 | 2.4557 | 2.6207 | 2.5547 | 2.7197 | 1.066 | 1.6148 | 1.9225 | 1.9225 | 2.1276 | 2.1276 | 2019-07-15 15:00 | 2.1263 | 3.6487 | 6.1669 | 6.1669 | 6.1669 | 6.1669
2021-05-18 03:00 | 2.0348 | 2.5198 | 2.5599 | 2.7319 | 2.6631 | 2.8351 | 1.0545 | 1.5974 | 1.9018 | 1.9018 | 2.1047 | 2.1047 | 2019-07-15 16:00 | 2.1034 | 3.6094 | 6.1006 | 6.1006 | 6.1006 | 6.1006
2021-05-18 04:00 | 2.1417 | 2.6522 | 2.6944 | 2.8754 | 2.803 | 2.9841 | 1.1689 | 1.7706 | 2.108 | 2.108 | 2.3329 | 2.3329 | 2019-07-15 17:00 | 2.1339 | 3.6618 | 6.189 | 6.189 | 6.189 | 6.189
2021-05-18 05:00 | 2.6273 | 3.2535 | 3.3053 | 3.5274 | 3.4385 | 3.6606 | 1.3089 | 1.9827 | 2.3606 | 2.3606 | 2.6124 | 2.6124 | 2019-07-15 18:00 | 2.1567 | 3.701 | 6.2553 | 6.2553 | 6.2553 | 6.2553
2021-05-18 06:00 | 3.5666 | 4.4167 | 4.4871 | 4.7886 | 4.668 | 4.9695 | 1.5318 | 2.3204 | 2.7626 | 2.7626 | 3.0574 | 3.0574 | 2019-07-15 19:00 | 2.0729 | 3.5571 | 6.0121 | 6.0121 | 6.0121 | 6.0121
2021-05-18 07:00 | 4.0668 | 5.036 | 5.1163 | 5.46 | 5.3225 | 5.6663 | 1.9376 | 2.9352 | 3.4945 | 3.4945 | 3.8673 | 3.8673 | 2019-07-15 20:00 | 2.0196 | 3.4656 | 5.8574 | 5.8574 | 5.8574 | 5.8574
2021-05-18 08:00 | 4.0668 | 5.036 | 5.1163 | 5.46 | 5.3225 | 5.6663 | 2.0148 | 3.052 | 3.6336 | 3.6336 | 4.0213 | 4.0213 | 2019-07-15 21:00 | 1.8443 | 3.1648 | 5.349 | 5.349 | 5.349 | 5.349
2021-05-18 09:00 | 3.8438 | 4.76 | 4.8358 | 5.1607 | 5.0308 | 5.3557 | 1.9434 | 2.9438 | 3.5048 | 3.5048 | 3.8787 | 3.8787 | 2019-07-15 22:00 | 1.6995 | 2.9163 | 4.9291 | 4.9291 | 4.9291 | 4.9291
2021-05-18 10:00 | 3.6009 | 4.4592 | 4.5302 | 4.8346 | 4.7128 | 5.0172 | 1.8433 | 2.7923 | 3.3244 | 3.3244 | 3.6791 | 3.6791 | 2019-07-15 23:00 | 1.4251 | 2.4455 | 4.1333 | 4.1333 | 4.1333 | 4.1333
2021-05-18 11:00 | 3.3151 | 4.1053 | 4.1707 | 4.4509 | 4.3388 | 4.619 | 1.8748 | 2.8399 | 3.3811 | 3.3811 | 3.7418 | 3.7418 | 2019-07-16 | 1.3184 | 2.2624 | 3.8239 | 3.8239 | 3.8239 | 3.8239
2021-05-18 12:00 | 3.1437 | 3.8929 | 3.9549 | 4.2207 | 4.1144 | 4.3801 | 1.7376 | 2.6321 | 3.1337 | 3.1337 | 3.468 | 3.468 | 2019-07-16 01:00 | 1.1813 | 2.027 | 3.426 | 3.426 | 3.426 | 3.426
2021-05-18 13:00 | 2.8607 | 3.5426 | 3.599 | 3.8408 | 3.7441 | 3.9859 | 1.6804 | 2.5455 | 3.0306 | 3.0306 | 3.354 | 3.354 | 2019-07-16 02:00 | 1.2498 | 2.1447 | 3.625 | 3.625 | 3.625 | 3.625
2021-05-18 14:00 | 2.8322 | 3.5072 | 3.563 | 3.8025 | 3.7067 | 3.9461 | 1.709 | 2.5888 | 3.0821 | 3.0821 | 3.411 | 3.411 | 2019-07-16 03:00 | 1.1813 | 2.027 | 3.426 | 3.426 | 3.426 | 3.426
2021-05-18 15:00 | 2.8979 | 3.5886 | 3.6457 | 3.8907 | 3.7927 | 4.0377 | 1.6747 | 2.5369 | 3.0203 | 3.0203 | 3.3426 | 3.3426 | 2019-07-16 04:00 | 1.2879 | 2.2101 | 3.7355 | 3.7355 | 3.7355 | 3.7355
2021-05-18 16:00 | 3.1122 | 3.854 | 3.9154 | 4.1785 | 4.0732 | 4.3363 | 1.9176 | 2.9048 | 3.4584 | 3.4584 | 3.8274 | 3.8274 | 2019-07-16 05:00 | 1.5013 | 2.5763 | 4.3544 | 4.3544 | 4.3544 | 4.3544
2021-05-18 17:00 | 3.7867 | 4.6892 | 4.7639 | 5.084 | 4.956 | 5.2761 | 2.3549 | 3.5672 | 4.247 | 4.247 | 4.7001 | 4.7001 | 2019-07-16 06:00 | 1.7528 | 3.0079 | 5.0838 | 5.0838 | 5.0838 | 5.0838
2021-05-18 18:00 | 3.9953 | 4.9476 | 5.0264 | 5.3641 | 5.229 | 5.5667 | 2.5578 | 3.8746 | 4.6129 | 4.6129 | 5.1051 | 5.1051 | 2019-07-16 07:00 | 2.0805 | 3.5702 | 6.0343 | 6.0343 | 6.0343 | 6.0343
2021-05-18 19:00 | 3.7695 | 4.668 | 4.7423 | 5.061 | 4.9335 | 5.2522 | 2.5778 | 3.9049 | 4.649 | 4.649 | 5.145 | 5.145 | 2019-07-16 08:00 | 2.2787 | 3.9102 | 6.6089 | 6.6089 | 6.6089 | 6.6089
2021-05-18 20:00 | 3.6209 | 4.484 | 4.5554 | 4.8615 | 4.739 | 5.0451 | 2.5006 | 3.788 | 4.5098 | 4.5098 | 4.991 | 4.991 | 2019-07-16 09:00 | 2.2482 | 3.8579 | 6.5205 | 6.5205 | 6.5205 | 6.5205
2021-05-18 21:00 | 3.1437 | 3.8929 | 3.9549 | 4.2207 | 4.1144 | 4.3801 | 2.3124 | 3.5028 | 4.1702 | 4.1702 | 4.6152 | 4.6152 | 2019-07-16 10:00 | 2.111 | 3.6225 | 6.1227 | 6.1227 | 6.1227 | 6.1227
2021-05-18 22:00 | 2.7893 | 3.4541 | 3.5091 | 3.7449 | 3.6506 | 3.8864 | 2.02 | 3.0599 | 3.643 | 3.643 | 4.0317 | 4.0317 | 2019-07-16 11:00 | 2.0882 | 3.5833 | 6.0564 | 6.0564 | 6.0564 | 6.0564
2021-05-18 23:00 | 2.4461 | 3.0291 | 3.0773 | 3.2841 | 3.2014 | 3.4081 | 1.666 | 2.5237 | 3.0046 | 3.0046 | 3.3252 | 3.3252 | 2019-07-16 12:00 | 2.111 | 3.6225 | 6.1227 | 6.1227 | 6.1227 | 6.1227
2021-05-19 | 2.1236 | 2.6298 | 2.6717 | 2.8512 | 2.7794 | 2.9589 | 1.3118 | 1.9871 | 2.3657 | 2.3657 | 2.6181 | 2.6181 | 2019-07-16 13:00 | 2.0805 | 3.5702 | 6.0343 | 6.0343 | 6.0343 | 6.0343
2021-05-19 01:00 | 2.0205 | 2.5021 | 2.5419 | 2.7127 | 2.6444 | 2.8152 | 1.1517 | 1.7446 | 2.0771 | 2.0771 | 2.2987 | 2.2987 | 2019-07-16 14:00 | 2.0805 | 3.5702 | 6.0343 | 6.0343 | 6.0343 | 6.0343
2021-05-19 02:00 | 2.0034 | 2.4809 | 2.5204 | 2.6897 | 2.622 | 2.7913 | 1.1259 | 1.7055 | 2.0304 | 2.0304 | 2.2471 | 2.2471 | 2019-07-16 15:00 | 2.0958 | 3.5964 | 6.0785 | 6.0785 | 6.0785 | 6.0785
2021-05-19 03:00 | 2.0748 | 2.5693 | 2.6103 | 2.7856 | 2.7155 | 2.8909 | 1.1517 | 1.7446 | 2.0771 | 2.0771 | 2.2987 | 2.2987 | 2019-07-16 16:00 | 2.0653 | 3.5441 | 5.99 | 5.99 | 5.99 | 5.99
2021-05-19 04:00 | 2.2377 | 2.7711 | 2.8152 | 3.0044 | 2.9287 | 3.1179 | 1.186 | 1.7966 | 2.1389 | 2.1389 | 2.3672 | 2.3672 | 2019-07-16 17:00 | 2.1186 | 3.6356 | 6.1448 | 6.1448 | 6.1448 | 6.1448
2021-05-19 05:00 | 2.5041 | 3.1009 | 3.1503 | 3.362 | 3.2773 | 3.489 | 1.2746 | 1.9308 | 2.2987 | 2.2987 | 2.544 | 2.544 | 2019-07-16 18:00 | 2.1186 | 3.6356 | 6.1448 | 6.1448 | 6.1448 | 6.1448
2021-05-19 06:00 | 3.5495 | 4.3955 | 4.4655 | 4.7655 | 4.6455 | 4.9456 | 1.6804 | 2.5455 | 3.0306 | 3.0306 | 3.354 | 3.354 | 2019-07-16 19:00 | 1.9738 | 3.3871 | 5.7248 | 5.7248 | 5.7248 | 5.7248
2021-05-19 07:00 | 4.1011 | 5.0785 | 5.1594 | 5.5061 | 5.3674 | 5.7141 | 2.0577 | 3.117 | 3.7109 | 3.7109 | 4.1069 | 4.1069 | 2019-07-16 20:00 | 1.8976 | 3.2563 | 5.5038 | 5.5038 | 5.5038 | 5.5038
2021-05-19 08:00 | 4.2668 | 5.2838 | 5.3679 | 5.7286 | 5.5843 | 5.945 | 2.1891 | 3.3161 | 3.948 | 3.948 | 4.3693 | 4.3693 | 2019-07-16 21:00 | 1.8138 | 3.1125 | 5.2606 | 5.2606 | 5.2606 | 5.2606
2021-05-19 09:00 | 4.0496 | 5.0148 | 5.0947 | 5.437 | 5.3001 | 5.6424 | 2.0691 | 3.1343 | 3.7315 | 3.7315 | 4.1297 | 4.1297 | 2019-07-16 22:00 | 1.6157 | 2.7725 | 4.6859 | 4.6859 | 4.6859 | 4.6859
2021-05-19 10:00 | 4.0639 | 5.0325 | 5.1127 | 5.4562 | 5.3188 | 5.6623 | 2.0434 | 3.0953 | 3.6852 | 3.6852 | 4.0784 | 4.0784 | 2019-07-16 23:00 | 1.4556 | 2.4978 | 4.2218 | 4.2218 | 4.2218 | 4.2218
2021-05-19 11:00 | 3.8953 | 4.8237 | 4.9005 | 5.2298 | 5.0981 | 5.4274 | 2.0691 | 3.1343 | 3.7315 | 3.7315 | 4.1297 | 4.1297 | 2019-07-17 | 1.2575 | 2.1578 | 3.6471 | 3.6471 | 3.6471 | 3.6471
2021-05-19 12:00 | 3.6895 | 4.5689 | 4.6417 | 4.9535 | 4.8288 | 5.1407 | 2.0691 | 3.1343 | 3.7315 | 3.7315 | 4.1297 | 4.1297 | 2019-07-17 01:00 | 1.227 | 2.1055 | 3.5587 | 3.5587 | 3.5587 | 3.5587
2021-05-19 13:00 | 3.318 | 4.1088 | 4.1743 | 4.4547 | 4.3425 | 4.623 | 1.8633 | 2.8226 | 3.3604 | 3.3604 | 3.719 | 3.719 | 2019-07-17 02:00 | 1.1813 | 2.027 | 3.426 | 3.426 | 3.426 | 3.426
2021-05-19 14:00 | 3.1465 | 3.8965 | 3.9585 | 4.2245 | 4.1181 | 4.3841 | 1.7347 | 2.6278 | 3.1285 | 3.1285 | 3.4623 | 3.4623 | 2019-07-17 03:00 | 1.1813 | 2.027 | 3.426 | 3.426 | 3.426 | 3.426
2021-05-19 15:00 | 3.0779 | 3.8115 | 3.8722 | 4.1324 | 4.0284 | 4.2885 | 1.8433 | 2.7923 | 3.3244 | 3.3244 | 3.6791 | 3.6791 | 2019-07-17 04:00 | 1.227 | 2.1055 | 3.5587 | 3.5587 | 3.5587 | 3.5587
2021-05-19 16:00 | 3.3952 | 4.2044 | 4.2713 | 4.5583 | 4.4435 | 4.7305 | 1.9834 | 3.0044 | 3.5769 | 3.5769 | 3.9586 | 3.9586 | 2019-07-17 05:00 | 1.509 | 2.5894 | 4.3765 | 4.3765 | 4.3765 | 4.3765
2021-05-19 17:00 | 3.8981 | 4.8272 | 4.9041 | 5.2336 | 5.1018 | 5.4314 | 2.4063 | 3.6451 | 4.3397 | 4.3397 | 4.8028 | 4.8028 | 2019-07-17 06:00 | 1.7757 | 3.0471 | 5.1501 | 5.1501 | 5.1501 | 5.1501
2021-05-19 18:00 | 4.0582 | 5.0254 | 5.1055 | 5.4485 | 5.3113 | 5.6543 | 2.5064 | 3.7967 | 4.5201 | 4.5201 | 5.0024 | 5.0024 | 2019-07-17 07:00 | 2.0501 | 3.5179 | 5.9458 | 5.9458 | 5.9458 | 5.9458
2021-05-19 19:00 | 3.9058 | 4.8367 | 4.9138 | 5.244 | 5.1119 | 5.4421 | 2.6207 | 3.9698 | 4.7263 | 4.7263 | 5.2306 | 5.2306 | 2019-07-17 08:00 | 2.1567 | 3.701 | 6.2553 | 6.2553 | 6.2553 | 6.2553
2021-05-19 20:00 | 3.7838 | 4.6857 | 4.7603 | 5.0802 | 4.9522 | 5.2721 | 2.5978 | 3.9352 | 4.685 | 4.685 | 5.185 | 5.185 | 2019-07-17 09:00 | 2.0882 | 3.5833 | 6.0564 | 6.0564 | 6.0564 | 6.0564
2021-05-19 21:00 | 3.3409 | 4.1371 | 4.203 | 4.4854 | 4.3725 | 4.6549 | 2.4149 | 3.6581 | 4.3552 | 4.3552 | 4.8199 | 4.8199 | 2019-07-17 10:00 | 2.1034 | 3.6094 | 6.1006 | 6.1006 | 6.1006 | 6.1006
2021-05-19 22:00 | 2.815 | 3.4859 | 3.5415 | 3.7794 | 3.6842 | 3.9222 | 2.1034 | 3.1862 | 3.7934 | 3.7934 | 4.1982 | 4.1982 | 2019-07-17 11:00 | 2.0958 | 3.5964 | 6.0785 | 6.0785 | 6.0785 | 6.0785
2021-05-19 23:00 | 2.5235 | 3.125 | 3.1747 | 3.3881 | 3.3027 | 3.516 | 1.8148 | 2.7491 | 3.273 | 3.273 | 3.6222 | 3.6222 | 2019-07-17 12:00 | 2.0882 | 3.5833 | 6.0564 | 6.0564 | 6.0564 | 6.0564
2021-05-20 | 2.1728 | 2.6906 | 2.7335 | 2.9171 | 2.8437 | 3.0273 | 1.4348 | 2.1734 | 2.5876 | 2.5876 | 2.8637 | 2.8637 | 2019-07-17 13:00 | 2.111 | 3.6225 | 6.1227 | 6.1227 | 6.1227 | 6.1227
2021-05-20 01:00 | 2.1348 | 2.6437 | 2.6858 | 2.8662 | 2.794 | 2.9745 | 1.2434 | 1.8835 | 2.2424 | 2.2424 | 2.4817 | 2.4817 | 2019-07-17 14:00 | 2.0882 | 3.5833 | 6.0564 | 6.0564 | 6.0564 | 6.0564
2021-05-20 02:00 | 1.9776 | 2.4489 | 2.4879 | 2.6551 | 2.5882 | 2.7554 | 1.1803 | 1.7879 | 2.1286 | 2.1286 | 2.3558 | 2.3558 | 2019-07-17 15:00 | 2.111 | 3.6225 | 6.1227 | 6.1227 | 6.1227 | 6.1227
2021-05-20 03:00 | 2.0691 | 2.5623 | 2.6031 | 2.778 | 2.708 | 2.8829 | 1.1917 | 1.8052 | 2.1492 | 2.1492 | 2.3786 | 2.3786 | 2019-07-17 16:00 | 2.1034 | 3.6094 | 6.1006 | 6.1006 | 6.1006 | 6.1006
2021-05-20 04:00 | 2.1606 | 2.6755 | 2.7181 | 2.9008 | 2.8277 | 3.0103 | 1.1599 | 1.7571 | 2.0919 | 2.0919 | 2.3151 | 2.3151 | 2019-07-17 17:00 | 2.1872 | 3.7533 | 6.3437 | 6.3437 | 6.3437 | 6.3437
2021-05-20 05:00 | 2.4834 | 3.0753 | 3.1242 | 3.3342 | 3.2502 | 3.4601 | 1.3804 | 2.091 | 2.4894 | 2.4894 | 2.755 | 2.755 | 2019-07-17 18:00 | 2.0729 | 3.5571 | 6.0121 | 6.0121 | 6.0121 | 6.0121
2021-05-20 06:00 | 3.4923 | 4.3247 | 4.3936 | 4.6888 | 4.5707 | 4.8659 | 1.6465 | 2.4942 | 2.9695 | 2.9695 | 3.2863 | 3.2863 | 2019-07-17 19:00 | 1.9662 | 3.374 | 5.7027 | 5.7027 | 5.7027 | 5.7027
2021-05-20 07:00 | 4.0896 | 5.0644 | 5.145 | 5.4907 | 5.3524 | 5.6981 | 2.1806 | 3.3031 | 3.9326 | 3.9326 | 4.3522 | 4.3522 | 2019-07-17 20:00 | 1.8595 | 3.191 | 5.3932 | 5.3932 | 5.3932 | 5.3932
2021-05-20 08:00 | 4.1011 | 5.0785 | 5.1594 | 5.5061 | 5.3674 | 5.7141 | 2.1606 | 3.2728 | 3.8965 | 3.8965 | 4.3122 | 4.3122 | 2019-07-17 21:00 | 1.8214 | 3.1256 | 5.2827 | 5.2827 | 5.2827 | 5.2827
2021-05-20 09:00 | 3.9538 | 4.8961 | 4.9741 | 5.3083 | 5.1746 | 5.5088 | 2.019 | 3.0583 | 3.6411 | 3.6411 | 4.0296 | 4.0296 | 2019-07-17 22:00 | 1.5852 | 2.7202 | 4.5975 | 4.5975 | 4.5975 | 4.5975
2021-05-20 10:00 | 3.7152 | 4.6007 | 4.674 | 4.9881 | 4.8625 | 5.1765 | 1.8919 | 2.8659 | 3.412 | 3.412 | 3.7761 | 3.7761 | 2019-07-17 23:00 | 1.3794 | 2.3671 | 4.0007 | 4.0007 | 4.0007 | 4.0007
2021-05-20 11:00 | 3.4237 | 4.2398 | 4.3073 | 4.5967 | 4.4809 | 4.7704 | 1.9176 | 2.9048 | 3.4584 | 3.4584 | 3.8274 | 3.8274 | 2019-07-18 | 1.3184 | 2.2624 | 3.8239 | 3.8239 | 3.8239 | 3.8239
2021-05-20 12:00 | 3.0722 | 3.8045 | 3.8651 | 4.1248 | 4.0209 | 4.2806 | 1.729 | 2.6191 | 3.1182 | 3.1182 | 3.4509 | 3.4509 | 2019-07-18 01:00 | 1.2498 | 2.1447 | 3.625 | 3.625 | 3.625 | 3.625
2021-05-20 13:00 | 3.138 | 3.8859 | 3.9477 | 4.213 | 4.1069 | 4.3722 | 1.8662 | 2.8269 | 3.3656 | 3.3656 | 3.7247 | 3.7247 | 2019-07-18 02:00 | 1.1736 | 2.014 | 3.4039 | 3.4039 | 3.4039 | 3.4039
2021-05-20 14:00 | 3.1294 | 3.8752 | 3.937 | 4.2015 | 4.0957 | 4.3602 | 1.8462 | 2.7966 | 3.3295 | 3.3295 | 3.6848 | 3.6848 | 2019-07-18 03:00 | 1.166 | 2.0009 | 3.3818 | 3.3818 | 3.3818 | 3.3818
2021-05-20 15:00 | 3.1408 | 3.8894 | 3.9513 | 4.2168 | 4.1106 | 4.3761 | 1.8748 | 2.8399 | 3.3811 | 3.3811 | 3.7418 | 3.7418 | 2019-07-18 04:00 | 1.1889 | 2.0401 | 3.4481 | 3.4481 | 3.4481 | 3.4481
2021-05-20 16:00 | 3.1951 | 3.9566 | 4.0197 | 4.2897 | 4.1817 | 4.4518 | 1.8862 | 2.8572 | 3.4017 | 3.4017 | 3.7647 | 3.7647 | 2019-07-18 05:00 | 1.4251 | 2.4455 | 4.1333 | 4.1333 | 4.1333 | 4.1333
2021-05-20 17:00 | 3.7695 | 4.668 | 4.7423 | 5.061 | 4.9335 | 5.2522 | 2.312 | 3.5023 | 4.1696 | 4.1696 | 4.6146 | 4.6146 | 2019-07-18 06:00 | 1.73 | 2.9686 | 5.0175 | 5.0175 | 5.0175 | 5.0175
2021-05-20 18:00 | 3.9725 | 4.9193 | 4.9976 | 5.3334 | 5.1991 | 5.5349 | 2.4806 | 3.7577 | 4.4737 | 4.4737 | 4.9511 | 4.9511 | 2019-07-18 07:00 | 2.0729 | 3.5571 | 6.0121 | 6.0121 | 6.0121 | 6.0121
2021-05-20 19:00 | 3.8438 | 4.76 | 4.8358 | 5.1607 | 5.0308 | 5.3557 | 2.5492 | 3.8616 | 4.5974 | 4.5974 | 5.088 | 5.088 | 2019-07-18 08:00 | 2.1339 | 3.6618 | 6.189 | 6.189 | 6.189 | 6.189
2021-05-20 20:00 | 3.5325 | 4.3744 | 4.4441 | 4.7427 | 4.6233 | 4.9219 | 2.4643 | 3.7329 | 4.4442 | 4.4442 | 4.9184 | 4.9184 | 2019-07-18 09:00 | 2.1567 | 3.701 | 6.2553 | 6.2553 | 6.2553 | 6.2553
2021-05-20 21:00 | 3.2326 | 4.0031 | 4.0668 | 4.3401 | 4.2308 | 4.5041 | 2.3149 | 3.5066 | 4.1748 | 4.1748 | 4.6203 | 4.6203 | 2019-07-18 10:00 | 2.0196 | 3.4656 | 5.8574 | 5.8574 | 5.8574 | 5.8574
2021-05-20 22:00 | 2.7293 | 3.3798 | 3.4336 | 3.6643 | 3.572 | 3.8027 | 1.9547 | 2.961 | 3.5252 | 3.5252 | 3.9013 | 3.9013 | 2019-07-18 11:00 | 2.0119 | 3.4525 | 5.8353 | 5.8353 | 5.8353 | 5.8353
2021-05-20 23:00 | 2.4463 | 3.0294 | 3.0777 | 3.2845 | 3.2017 | 3.4085 | 1.6355 | 2.4774 | 2.9495 | 2.9495 | 3.2642 | 3.2642 | 2019-07-18 12:00 | 2.1491 | 3.6879 | 6.2332 | 6.2332 | 6.2332 | 6.2332
2021-05-21 | 2.1348 | 2.6437 | 2.6858 | 2.8662 | 2.794 | 2.9745 | 1.3632 | 2.065 | 2.4585 | 2.4585 | 2.7208 | 2.7208 | 2019-07-18 13:00 | 2.1034 | 3.6094 | 6.1006 | 6.1006 | 6.1006 | 6.1006
2021-05-21 01:00 | 1.9948 | 2.4702 | 2.5096 | 2.6782 | 2.6108 | 2.7794 | 1.2379 | 1.8752 | 2.2325 | 2.2325 | 2.4707 | 2.4707 | 2019-07-18 14:00 | 2.0653 | 3.5441 | 5.99 | 5.99 | 5.99 | 5.99
2021-05-21 02:00 | 1.9834 | 2.4561 | 2.4952 | 2.6629 | 2.5958 | 2.7635 | 1.1146 | 1.6884 | 2.0101 | 2.0101 | 2.2246 | 2.2246 | 2019-07-18 15:00 | 2.1567 | 3.701 | 6.2553 | 6.2553 | 6.2553 | 6.2553
2021-05-21 03:00 | 2.0449 | 2.5323 | 2.5726 | 2.7455 | 2.6763 | 2.8492 | 1.1403 | 1.7273 | 2.0565 | 2.0565 | 2.2759 | 2.2759 | 2019-07-18 16:00 | 2.1186 | 3.6356 | 6.1448 | 6.1448 | 6.1448 | 6.1448
2021-05-21 04:00 | 2.1406 | 2.6507 | 2.693 | 2.8739 | 2.8015 | 2.9825 | 1.126 | 1.7057 | 2.0307 | 2.0307 | 2.2474 | 2.2474 | 2019-07-18 17:00 | 2.1644 | 3.7141 | 6.2774 | 6.2774 | 6.2774 | 6.2774
2021-05-21 05:00 | 2.4692 | 3.0577 | 3.1064 | 3.3152 | 3.2317 | 3.4404 | 1.2746 | 1.9308 | 2.2987 | 2.2987 | 2.544 | 2.544 | 2019-07-18 18:00 | 2.0653 | 3.5441 | 5.99 | 5.99 | 5.99 | 5.99
2021-05-21 06:00 | 3.5523 | 4.399 | 4.4691 | 4.7694 | 4.6493 | 4.9495 | 1.6433 | 2.4893 | 2.9636 | 2.9636 | 3.2798 | 3.2798 | 2019-07-18 19:00 | 2.0805 | 3.5702 | 6.0343 | 6.0343 | 6.0343 | 6.0343
2021-05-21 07:00 | 3.921 | 4.8555 | 4.9329 | 5.2643 | 5.1318 | 5.4632 | 2.0748 | 3.143 | 3.7419 | 3.7419 | 4.1411 | 4.1411 | 2019-07-18 20:00 | 1.9434 | 3.3348 | 5.6364 | 5.6364 | 5.6364 | 5.6364
2021-05-21 08:00 | 4.0039 | 4.9582 | 5.0372 | 5.3756 | 5.2402 | 5.5787 | 2.0691 | 3.1343 | 3.7315 | 3.7315 | 4.1297 | 4.1297 | 2019-07-18 21:00 | 1.8443 | 3.1648 | 5.349 | 5.349 | 5.349 | 5.349
2021-05-21 09:00 | 3.6467 | 4.5158 | 4.5877 | 4.896 | 4.7727 | 5.0809 | 1.8719 | 2.8356 | 3.3759 | 3.3759 | 3.7361 | 3.7361 | 2019-07-18 22:00 | 1.6461 | 2.8248 | 4.7743 | 4.7743 | 4.7743 | 4.7743
2021-05-21 10:00 | 3.4066 | 4.2185 | 4.2857 | 4.5737 | 4.4585 | 4.7465 | 1.829 | 2.7706 | 3.2986 | 3.2986 | 3.6506 | 3.6506 | 2019-07-18 23:00 | 1.5623 | 2.6809 | 4.5312 | 4.5312 | 4.5312 | 4.5312
2021-05-21 11:00 | 3.1065 | 3.8469 | 3.9082 | 4.1708 | 4.0658 | 4.3284 | 1.789 | 2.71 | 3.2264 | 3.2264 | 3.5707 | 3.5707 | 2019-07-19 | 1.3108 | 2.2494 | 3.8018 | 3.8018 | 3.8018 | 3.8018
2021-05-21 12:00 | 2.875 | 3.5603 | 3.617 | 3.86 | 3.7628 | 4.0058 | 1.6433 | 2.4893 | 2.9636 | 2.9636 | 3.2798 | 3.2798 | 2019-07-19 01:00 | 1.227 | 2.1055 | 3.5587 | 3.5587 | 3.5587 | 3.5587
2021-05-21 13:00 | 2.7464 | 3.401 | 3.4552 | 3.6873 | 3.5945 | 3.8266 | 1.6633 | 2.5196 | 2.9997 | 2.9997 | 3.3197 | 3.3197 | 2019-07-19 02:00 | 1.1889 | 2.0401 | 3.4481 | 3.4481 | 3.4481 | 3.4481
2021-05-21 14:00 | 2.6092 | 3.2311 | 3.2826 | 3.5032 | 3.4149 | 3.6355 | 1.6404 | 2.4849 | 2.9584 | 2.9584 | 3.2741 | 3.2741 | 2019-07-19 03:00 | 1.2956 | 2.2232 | 3.7576 | 3.7576 | 3.7576 | 3.7576
2021-05-21 15:00 | 2.5292 | 3.132 | 3.1819 | 3.3957 | 3.3102 | 3.524 | 1.6976 | 2.5715 | 3.0615 | 3.0615 | 3.3882 | 3.3882 | 2019-07-19 04:00 | 1.3032 | 2.2363 | 3.7797 | 3.7797 | 3.7797 | 3.7797
2021-05-21 16:00 | 2.9065 | 3.5992 | 3.6565 | 3.9022 | 3.8039 | 4.0496 | 1.8805 | 2.8486 | 3.3914 | 3.3914 | 3.7532 | 3.7532 | 2019-07-19 05:00 | 1.4175 | 2.4324 | 4.1112 | 4.1112 | 4.1112 | 4.1112
2021-05-21 17:00 | 3.3409 | 4.1371 | 4.203 | 4.4854 | 4.3725 | 4.6549 | 2.2777 | 3.4503 | 4.1078 | 4.1078 | 4.5461 | 4.5461 | 2019-07-19 06:00 | 1.7757 | 3.0471 | 5.1501 | 5.1501 | 5.1501 | 5.1501
2021-05-21 18:00 | 3.4152 | 4.2291 | 4.2965 | 4.5852 | 4.4697 | 4.7584 | 2.3806 | 3.6062 | 4.2933 | 4.2933 | 4.7514 | 4.7514 | 2019-07-19 07:00 | 2.1949 | 3.7664 | 6.3658 | 6.3658 | 6.3658 | 6.3658
2021-05-21 19:00 | 3.3809 | 4.1867 | 4.2534 | 4.5392 | 4.4248 | 4.7106 | 2.4578 | 3.7231 | 4.4325 | 4.4325 | 4.9055 | 4.9055 | 2019-07-19 08:00 | 2.172 | 3.7271 | 6.2995 | 6.2995 | 6.2995 | 6.2995
2021-05-21 20:00 | 3.0636 | 3.7938 | 3.8543 | 4.1132 | 4.0097 | 4.2686 | 2.3806 | 3.6062 | 4.2933 | 4.2933 | 4.7514 | 4.7514 | 2019-07-19 09:00 | 2.2406 | 3.8448 | 6.4984 | 6.4984 | 6.4984 | 6.4984
2021-05-21 21:00 | 2.8207 | 3.493 | 3.5487 | 3.7871 | 3.6917 | 3.9302 | 2.2371 | 3.3887 | 4.0344 | 4.0344 | 4.4649 | 4.4649 | 2019-07-19 10:00 | 2.0501 | 3.5179 | 5.9458 | 5.9458 | 5.9458 | 5.9458
2021-05-21 22:00 | 2.6038 | 3.2243 | 3.2757 | 3.4958 | 3.4078 | 3.6279 | 2.0405 | 3.091 | 3.68 | 3.68 | 4.0727 | 4.0727 | 2019-07-19 11:00 | 2.1644 | 3.7141 | 6.2774 | 6.2774 | 6.2774 | 6.2774
2021-05-21 23:00 | 2.3606 | 2.9232 | 2.9698 | 3.1693 | 3.0895 | 3.2891 | 1.6791 | 2.5435 | 3.0282 | 3.0282 | 3.3513 | 3.3513 | 2019-07-19 12:00 | 2.1415 | 3.6748 | 6.2111 | 6.2111 | 6.2111 | 6.2111
2021-05-22 | 2.0268 | 2.5099 | 2.5499 | 2.7212 | 2.6527 | 2.824 | 1.4547 | 2.2035 | 2.6234 | 2.6234 | 2.9033 | 2.9033 | 2019-07-19 13:00 | 2.111 | 3.6225 | 6.1227 | 6.1227 | 6.1227 | 6.1227
2021-05-22 01:00 | 1.8896 | 2.34 | 2.3773 | 2.537 | 2.4731 | 2.6329 | 1.2662 | 1.9181 | 2.2836 | 2.2836 | 2.5272 | 2.5272 | 2019-07-19 14:00 | 2.0501 | 3.5179 | 5.9458 | 5.9458 | 5.9458 | 5.9458
2021-05-22 02:00 | 1.8576 | 2.3004 | 2.337 | 2.494 | 2.4312 | 2.5883 | 1.0982 | 1.6636 | 1.9806 | 1.9806 | 2.1919 | 2.1919 | 2019-07-19 15:00 | 2.1415 | 3.6748 | 6.2111 | 6.2111 | 6.2111 | 6.2111
2021-05-22 03:00 | 1.8233 | 2.2579 | 2.2939 | 2.448 | 2.3863 | 2.5405 | 1.126 | 1.7057 | 2.0307 | 2.0307 | 2.2474 | 2.2474 | 2019-07-19 16:00 | 2.0958 | 3.5964 | 6.0785 | 6.0785 | 6.0785 | 6.0785
2021-05-22 04:00 | 1.8948 | 2.3464 | 2.3837 | 2.5439 | 2.4799 | 2.64 | 1.0946 | 1.6581 | 1.974 | 1.974 | 2.1846 | 2.1846 | 2019-07-19 17:00 | 2.111 | 3.6225 | 6.1227 | 6.1227 | 6.1227 | 6.1227
2021-05-22 05:00 | 2.0977 | 2.5976 | 2.639 | 2.8163 | 2.7454 | 2.9227 | 1.1654 | 1.7653 | 2.1017 | 2.1017 | 2.3259 | 2.3259 | 2019-07-19 18:00 | 2.111 | 3.6225 | 6.1227 | 6.1227 | 6.1227 | 6.1227
2021-05-22 06:00 | 2.322 | 2.8754 | 2.9212 | 3.1175 | 3.039 | 3.2353 | 1.3518 | 2.0477 | 2.4379 | 2.4379 | 2.698 | 2.698 | 2019-07-19 19:00 | 1.951 | 3.3479 | 5.6585 | 5.6585 | 5.6585 | 5.6585
2021-05-22 07:00 | 2.9179 | 3.6133 | 3.6709 | 3.9176 | 3.8189 | 4.0656 | 1.6776 | 2.5412 | 3.0254 | 3.0254 | 3.3483 | 3.3483 | 2019-07-19 20:00 | 1.9053 | 3.2694 | 5.5259 | 5.5259 | 5.5259 | 5.5259
2021-05-22 08:00 | 2.9265 | 3.624 | 3.6817 | 3.9291 | 3.8301 | 4.0775 | 1.8033 | 2.7317 | 3.2522 | 3.2522 | 3.5992 | 3.5992 | 2019-07-19 21:00 | 1.8214 | 3.1256 | 5.2827 | 5.2827 | 5.2827 | 5.2827
2021-05-22 09:00 | 2.7579 | 3.4152 | 3.4696 | 3.7027 | 3.6094 | 3.8426 | 1.8633 | 2.8226 | 3.3604 | 3.3604 | 3.719 | 3.719 | 2019-07-19 22:00 | 1.6004 | 2.7463 | 4.6417 | 4.6417 | 4.6417 | 4.6417
2021-05-22 10:00 | 2.6064 | 3.2276 | 3.279 | 3.4993 | 3.4112 | 3.6315 | 1.9319 | 2.9265 | 3.4841 | 3.4841 | 3.8559 | 3.8559 | 2019-07-19 23:00 | 1.4251 | 2.4455 | 4.1333 | 4.1333 | 4.1333 | 4.1333
2021-05-22 11:00 | 2.4178 | 2.994 | 3.0417 | 3.2461 | 3.1643 | 3.3687 | 1.9348 | 2.9308 | 3.4893 | 3.4893 | 3.8616 | 3.8616 | 2019-07-20 | 1.3565 | 2.3278 | 3.9344 | 3.9344 | 3.9344 | 3.9344
2021-05-22 12:00 | 2.3149 | 2.8666 | 2.9123 | 3.108 | 3.0297 | 3.2254 | 1.8919 | 2.8659 | 3.412 | 3.412 | 3.7761 | 3.7761 | 2019-07-20 01:00 | 1.2346 | 2.1186 | 3.5808 | 3.5808 | 3.5808 | 3.5808
2021-05-22 13:00 | 2.132 | 2.6401 | 2.6822 | 2.8624 | 2.7903 | 2.9705 | 1.8405 | 2.788 | 3.3192 | 3.3192 | 3.6734 | 3.6734 | 2019-07-20 02:00 | 1.1736 | 2.014 | 3.4039 | 3.4039 | 3.4039 | 3.4039
2021-05-22 14:00 | 2.0771 | 2.5721 | 2.6131 | 2.7887 | 2.7184 | 2.894 | 1.8719 | 2.8356 | 3.3759 | 3.3759 | 3.7361 | 3.7361 | 2019-07-20 03:00 | 1.2117 | 2.0794 | 3.5144 | 3.5144 | 3.5144 | 3.5144
2021-05-22 15:00 | 2.1463 | 2.6578 | 2.7001 | 2.8816 | 2.809 | 2.9904 | 1.8348 | 2.7793 | 3.3089 | 3.3089 | 3.662 | 3.662 | 2019-07-20 04:00 | 1.2727 | 2.184 | 3.6913 | 3.6913 | 3.6913 | 3.6913
2021-05-22 16:00 | 2.4578 | 3.0436 | 3.092 | 3.2998 | 3.2167 | 3.4245 | 1.9691 | 2.9828 | 3.5512 | 3.5512 | 3.9301 | 3.9301 | 2019-07-20 05:00 | 1.3565 | 2.3278 | 3.9344 | 3.9344 | 3.9344 | 3.9344
2021-05-22 17:00 | 2.9893 | 3.7018 | 3.7608 | 4.0135 | 3.9124 | 4.1651 | 2.2349 | 3.3854 | 4.0305 | 4.0305 | 4.4605 | 4.4605 | 2019-07-20 06:00 | 1.4327 | 2.4586 | 4.1555 | 4.1555 | 4.1555 | 4.1555
2021-05-22 18:00 | 3.0036 | 3.7195 | 3.7788 | 4.0327 | 3.9311 | 4.185 | 2.3635 | 3.5802 | 4.2624 | 4.2624 | 4.7172 | 4.7172 | 2019-07-20 07:00 | 1.7605 | 3.0209 | 5.1059 | 5.1059 | 5.1059 | 5.1059
2021-05-22 19:00 | 2.855 | 3.5355 | 3.5918 | 3.8331 | 3.7366 | 3.978 | 2.3206 | 3.5153 | 4.1851 | 4.1851 | 4.6317 | 4.6317 | 2019-07-20 08:00 | 1.89 | 3.2433 | 5.4817 | 5.4817 | 5.4817 | 5.4817
2021-05-22 20:00 | 2.7007 | 3.3444 | 3.3977 | 3.6259 | 3.5346 | 3.7629 | 2.252 | 3.4114 | 4.0614 | 4.0614 | 4.4948 | 4.4948 | 2019-07-20 09:00 | 2.0196 | 3.4656 | 5.8574 | 5.8574 | 5.8574 | 5.8574
2021-05-22 21:00 | 2.5492 | 3.1568 | 3.2071 | 3.4226 | 3.3364 | 3.5519 | 2.1491 | 3.2555 | 3.8759 | 3.8759 | 4.2894 | 4.2894 | 2019-07-20 10:00 | 1.9815 | 3.4002 | 5.7469 | 5.7469 | 5.7469 | 5.7469
2021-05-22 22:00 | 2.438 | 3.0191 | 3.0672 | 3.2733 | 3.1908 | 3.3969 | 2.0577 | 3.117 | 3.7109 | 3.7109 | 4.1069 | 4.1069 | 2019-07-20 11:00 | 2.0272 | 3.4787 | 5.8795 | 5.8795 | 5.8795 | 5.8795
2021-05-22 23:00 | 2.332 | 2.8878 | 2.9338 | 3.131 | 3.0521 | 3.2493 | 1.729 | 2.6191 | 3.1182 | 3.1182 | 3.4509 | 3.4509 | 2019-07-20 12:00 | 1.9129 | 3.2825 | 5.548 | 5.548 | 5.548 | 5.548
2021-05-23 | 2.0721 | 2.566 | 2.6069 | 2.782 | 2.712 | 2.8871 | 1.4004 | 2.1213 | 2.5255 | 2.5255 | 2.795 | 2.795 | 2019-07-20 13:00 | 1.9053 | 3.2694 | 5.5259 | 5.5259 | 5.5259 | 5.5259
2021-05-23 01:00 | 1.8719 | 2.3181 | 2.355 | 2.5132 | 2.4499 | 2.6082 | 1.3041 | 1.9754 | 2.3518 | 2.3518 | 2.6028 | 2.6028 | 2019-07-20 14:00 | 1.9434 | 3.3348 | 5.6364 | 5.6364 | 5.6364 | 5.6364
2021-05-23 02:00 | 1.8079 | 2.2388 | 2.2744 | 2.4272 | 2.3661 | 2.5189 | 1.1574 | 1.7533 | 2.0874 | 2.0874 | 2.3101 | 2.3101 | 2019-07-20 15:00 | 1.89 | 3.2433 | 5.4817 | 5.4817 | 5.4817 | 5.4817
2021-05-23 03:00 | 1.8748 | 2.3216 | 2.3586 | 2.5171 | 2.4537 | 2.6121 | 1.1974 | 1.8139 | 2.1596 | 2.1596 | 2.39 | 2.39 | 2019-07-20 16:00 | 1.8976 | 3.2563 | 5.5038 | 5.5038 | 5.5038 | 5.5038
2021-05-23 04:00 | 1.9405 | 2.403 | 2.4413 | 2.6053 | 2.5397 | 2.7037 | 1.2203 | 1.8485 | 2.2008 | 2.2008 | 2.4356 | 2.4356 | 2019-07-20 17:00 | 1.951 | 3.3479 | 5.6585 | 5.6585 | 5.6585 | 5.6585
2021-05-23 05:00 | 2.077 | 2.572 | 2.6129 | 2.7885 | 2.7183 | 2.8939 | 1.1632 | 1.762 | 2.0977 | 2.0977 | 2.3215 | 2.3215 | 2019-07-20 18:00 | 1.9129 | 3.2825 | 5.548 | 5.548 | 5.548 | 5.548
2021-05-23 06:00 | 2.2977 | 2.8454 | 2.8907 | 3.0849 | 3.0072 | 3.2015 | 1.285 | 1.9466 | 2.3175 | 2.3175 | 2.5648 | 2.5648 | 2019-07-20 19:00 | 1.8062 | 3.0994 | 5.2385 | 5.2385 | 5.2385 | 5.2385
2021-05-23 07:00 | 2.635 | 3.263 | 3.315 | 3.5377 | 3.4486 | 3.6713 | 1.5204 | 2.3031 | 2.742 | 2.742 | 3.0345 | 3.0345 | 2019-07-20 20:00 | 1.7909 | 3.0733 | 5.1943 | 5.1943 | 5.1943 | 5.1943
2021-05-23 08:00 | 2.7321 | 3.3833 | 3.4372 | 3.6682 | 3.5758 | 3.8067 | 1.7004 | 2.5758 | 3.0667 | 3.0667 | 3.3939 | 3.3939 | 2019-07-20 21:00 | 1.6995 | 2.9163 | 4.9291 | 4.9291 | 4.9291 | 4.9291
2021-05-23 09:00 | 2.6378 | 3.2665 | 3.3186 | 3.5415 | 3.4523 | 3.6753 | 1.8148 | 2.749 | 3.2728 | 3.2728 | 3.6221 | 3.6221 | 2019-07-20 22:00 | 1.6233 | 2.7855 | 4.708 | 4.708 | 4.708 | 4.708
2021-05-23 10:00 | 2.4978 | 3.0931 | 3.1424 | 3.3535 | 3.2691 | 3.4802 | 1.9605 | 2.9698 | 3.5357 | 3.5357 | 3.913 | 3.913 | 2019-07-20 23:00 | 1.4632 | 2.5109 | 4.2439 | 4.2439 | 4.2439 | 4.2439
2021-05-23 11:00 | 2.2406 | 2.7746 | 2.8188 | 3.0082 | 2.9324 | 3.1218 | 1.8719 | 2.8356 | 3.3759 | 3.3759 | 3.7361 | 3.7361 | 2019-07-21 | 1.3413 | 2.3017 | 3.8902 | 3.8902 | 3.8902 | 3.8902
2021-05-23 12:00 | 2.0434 | 2.5304 | 2.5707 | 2.7434 | 2.6743 | 2.8471 | 1.8205 | 2.7577 | 3.2831 | 3.2831 | 3.6335 | 3.6335 | 2019-07-21 01:00 | 1.2651 | 2.1709 | 3.6692 | 3.6692 | 3.6692 | 3.6692
2021-05-23 13:00 | 1.9789 | 2.4506 | 2.4896 | 2.6569 | 2.59 | 2.7573 | 1.898 | 2.8752 | 3.423 | 3.423 | 3.7883 | 3.7883 | 2019-07-21 02:00 | 1.2346 | 2.1186 | 3.5808 | 3.5808 | 3.5808 | 3.5808
2021-05-23 14:00 | 2.2149 | 2.7427 | 2.7864 | 2.9737 | 2.8988 | 3.086 | 1.9005 | 2.8789 | 3.4275 | 3.4275 | 3.7932 | 3.7932 | 2019-07-21 03:00 | 1.2346 | 2.1186 | 3.5808 | 3.5808 | 3.5808 | 3.5808
2021-05-23 15:00 | 2.1063 | 2.6083 | 2.6498 | 2.8279 | 2.7566 | 2.9347 | 1.8576 | 2.8139 | 3.3501 | 3.3501 | 3.7076 | 3.7076 | 2019-07-21 04:00 | 1.3184 | 2.2624 | 3.8239 | 3.8239 | 3.8239 | 3.8239
2021-05-23 16:00 | 2.545 | 3.1516 | 3.2018 | 3.4169 | 3.3309 | 3.546 | 2.0234 | 3.065 | 3.6491 | 3.6491 | 4.0384 | 4.0384 | 2019-07-21 05:00 | 1.3565 | 2.3278 | 3.9344 | 3.9344 | 3.9344 | 3.9344
2021-05-23 17:00 | 2.9836 | 3.6947 | 3.7536 | 4.0058 | 3.9049 | 4.1571 | 2.2663 | 3.433 | 4.0872 | 4.0872 | 4.5233 | 4.5233 | 2019-07-21 06:00 | 1.3794 | 2.3671 | 4.0007 | 4.0007 | 4.0007 | 4.0007
2021-05-23 18:00 | 3.1094 | 3.8505 | 3.9118 | 4.1746 | 4.0695 | 4.3323 | 2.3235 | 3.5196 | 4.1903 | 4.1903 | 4.6374 | 4.6374 | 2019-07-21 07:00 | 1.6842 | 2.8902 | 4.8849 | 4.8849 | 4.8849 | 4.8849
2021-05-23 19:00 | 2.9751 | 3.6841 | 3.7428 | 3.9943 | 3.8937 | 4.1452 | 2.3377 | 3.5412 | 4.216 | 4.216 | 4.6659 | 4.6659 | 2019-07-21 08:00 | 1.8138 | 3.1125 | 5.2606 | 5.2606 | 5.2606 | 5.2606
2021-05-23 20:00 | 2.7721 | 3.4329 | 3.4875 | 3.7219 | 3.6281 | 3.8625 | 2.252 | 3.4114 | 4.0614 | 4.0614 | 4.4948 | 4.4948 | 2019-07-21 09:00 | 1.8748 | 3.2171 | 5.4375 | 5.4375 | 5.4375 | 5.4375
2021-05-23 21:00 | 2.6207 | 3.2453 | 3.297 | 3.5185 | 3.4299 | 3.6514 | 2.0548 | 3.1126 | 3.7058 | 3.7058 | 4.1012 | 4.1012 | 2019-07-21 10:00 | 1.829 | 3.1386 | 5.3048 | 5.3048 | 5.3048 | 5.3048
2021-05-23 22:00 | 2.3349 | 2.8914 | 2.9374 | 3.1348 | 3.0559 | 3.2532 | 1.8405 | 2.788 | 3.3192 | 3.3192 | 3.6734 | 3.6734 | 2019-07-21 11:00 | 1.9053 | 3.2694 | 5.5259 | 5.5259 | 5.5259 | 5.5259
2021-05-23 23:00 | 2.1806 | 2.7003 | 2.7433 | 2.9276 | 2.8539 | 3.0382 | 1.6176 | 2.4503 | 2.9172 | 2.9172 | 3.2285 | 3.2285 | 2019-07-21 12:00 | 1.9434 | 3.3348 | 5.6364 | 5.6364 | 5.6364 | 5.6364
2021-05-24 | 1.9119 | 2.3676 | 2.4053 | 2.5669 | 2.5023 | 2.6639 | 1.2843 | 1.9454 | 2.3161 | 2.3161 | 2.5632 | 2.5632 | 2019-07-21 13:00 | 2.0119 | 3.4525 | 5.8353 | 5.8353 | 5.8353 | 5.8353
2021-05-24 01:00 | 1.7862 | 2.2119 | 2.2471 | 2.3981 | 2.3377 | 2.4887 | 1.1265 | 1.7064 | 2.0315 | 2.0315 | 2.2483 | 2.2483 | 2019-07-21 14:00 | 1.89 | 3.2433 | 5.4817 | 5.4817 | 5.4817 | 5.4817
2021-05-24 02:00 | 1.6919 | 2.0951 | 2.1285 | 2.2715 | 2.2143 | 2.3573 | 1.0514 | 1.5927 | 1.8962 | 1.8962 | 2.0985 | 2.0985 | 2019-07-21 15:00 | 1.9129 | 3.2825 | 5.548 | 5.548 | 5.548 | 5.548
2021-05-24 03:00 | 1.7433 | 2.1588 | 2.1932 | 2.3406 | 2.2816 | 2.429 | 1.0517 | 1.5931 | 1.8967 | 1.8967 | 2.0991 | 2.0991 | 2019-07-21 16:00 | 2.0043 | 3.4394 | 5.8132 | 5.8132 | 5.8132 | 5.8132
2021-05-24 04:00 | 1.8846 | 2.3337 | 2.3709 | 2.5302 | 2.4665 | 2.6258 | 1.0346 | 1.5671 | 1.8658 | 1.8658 | 2.0649 | 2.0649 | 2019-07-21 17:00 | 1.9738 | 3.3871 | 5.7248 | 5.7248 | 5.7248 | 5.7248
2021-05-24 05:00 | 2.2996 | 2.8477 | 2.8931 | 3.0875 | 3.0097 | 3.2041 | 1.1289 | 1.71 | 2.0359 | 2.0359 | 2.2531 | 2.2531 | 2019-07-21 18:00 | 1.9662 | 3.374 | 5.7027 | 5.7027 | 5.7027 | 5.7027
2021-05-24 06:00 | 3.0751 | 3.808 | 3.8686 | 4.1286 | 4.0246 | 4.2846 | 1.4204 | 2.1516 | 2.5616 | 2.5616 | 2.8349 | 2.8349 | 2019-07-21 19:00 | 1.89 | 3.2433 | 5.4817 | 5.4817 | 5.4817 | 5.4817
2021-05-24 07:00 | 3.3437 | 4.1407 | 4.2066 | 4.4893 | 4.3762 | 4.6589 | 1.809 | 2.7403 | 3.2625 | 3.2625 | 3.6106 | 3.6106 | 2019-07-21 20:00 | 1.7833 | 3.0602 | 5.1722 | 5.1722 | 5.1722 | 5.1722
2021-05-24 08:00 | 3.2666 | 4.0451 | 4.1095 | 4.3857 | 4.2752 | 4.5514 | 1.809 | 2.7403 | 3.2625 | 3.2625 | 3.6106 | 3.6106 | 2019-07-21 21:00 | 1.6614 | 2.8509 | 4.8186 | 4.8186 | 4.8186 | 4.8186
2021-05-24 09:00 | 3.1122 | 3.854 | 3.9154 | 4.1785 | 4.0732 | 4.3363 | 1.6976 | 2.5715 | 3.0615 | 3.0615 | 3.3882 | 3.3882 | 2019-07-21 22:00 | 1.4709 | 2.524 | 4.266 | 4.266 | 4.266 | 4.266
2021-05-24 10:00 | 3.0722 | 3.8045 | 3.8651 | 4.1248 | 4.0209 | 4.2806 | 1.729 | 2.6191 | 3.1182 | 3.1182 | 3.4509 | 3.4509 | 2019-07-21 23:00 | 1.3718 | 2.354 | 3.9786 | 3.9786 | 3.9786 | 3.9786
2021-05-24 11:00 | 2.9122 | 3.6063 | 3.6637 | 3.9099 | 3.8114 | 4.0576 | 1.709 | 2.5888 | 3.0821 | 3.0821 | 3.411 | 3.411 | 2019-07-22 | 1.2803 | 2.1971 | 3.7134 | 3.7134 | 3.7134 | 3.7134
2021-05-24 12:00 | 2.8579 | 3.539 | 3.5954 | 3.837 | 3.7403 | 3.9819 | 1.8633 | 2.8226 | 3.3604 | 3.3604 | 3.719 | 3.719 | 2019-07-22 01:00 | 1.2422 | 2.1317 | 3.6029 | 3.6029 | 3.6029 | 3.6029
2021-05-24 13:00 | 2.8064 | 3.4753 | 3.5307 | 3.7679 | 3.673 | 3.9103 | 1.7176 | 2.6018 | 3.0976 | 3.0976 | 3.4281 | 3.4281 | 2019-07-22 02:00 | 1.1736 | 2.014 | 3.4039 | 3.4039 | 3.4039 | 3.4039
2021-05-24 14:00 | 2.7178 | 3.3656 | 3.4192 | 3.649 | 3.5571 | 3.7868 | 1.6461 | 2.4936 | 2.9687 | 2.9687 | 3.2855 | 3.2855 | 2019-07-22 03:00 | 1.1736 | 2.014 | 3.4039 | 3.4039 | 3.4039 | 3.4039
2021-05-24 15:00 | 2.7264 | 3.3762 | 3.43 | 3.6605 | 3.5683 | 3.7988 | 1.7404 | 2.6364 | 3.1388 | 3.1388 | 3.4737 | 3.4737 | 2019-07-22 04:00 | 1.227 | 2.1055 | 3.5587 | 3.5587 | 3.5587 | 3.5587
2021-05-24 16:00 | 2.9522 | 3.6558 | 3.714 | 3.9636 | 3.8638 | 4.1133 | 1.8833 | 2.8529 | 3.3965 | 3.3965 | 3.7589 | 3.7589 | 2019-07-22 05:00 | 1.3642 | 2.3409 | 3.9565 | 3.9565 | 3.9565 | 3.9565
2021-05-24 17:00 | 3.4266 | 4.2433 | 4.3109 | 4.6005 | 4.4847 | 4.7743 | 2.1691 | 3.2858 | 3.9119 | 3.9119 | 4.3294 | 4.3294 | 2019-07-22 06:00 | 1.6842 | 2.8902 | 4.8849 | 4.8849 | 4.8849 | 4.8849
2021-05-24 18:00 | 3.6552 | 4.5264 | 4.5985 | 4.9075 | 4.7839 | 5.0929 | 2.2006 | 3.3334 | 3.9686 | 3.9686 | 4.3921 | 4.3921 | 2019-07-22 07:00 | 2.111 | 3.6225 | 6.1227 | 6.1227 | 6.1227 | 6.1227
2021-05-24 19:00 | 3.4237 | 4.2398 | 4.3073 | 4.5967 | 4.4809 | 4.7704 | 2.2606 | 3.4243 | 4.0769 | 4.0769 | 4.5119 | 4.5119 | 2019-07-22 08:00 | 2.2634 | 3.8841 | 6.5647 | 6.5647 | 6.5647 | 6.5647
2021-05-24 20:00 | 3.1065 | 3.8469 | 3.9082 | 4.1708 | 4.0658 | 4.3284 | 2.2749 | 3.446 | 4.1026 | 4.1026 | 4.5404 | 4.5404 | 2019-07-22 09:00 | 2.1796 | 3.7402 | 6.3216 | 6.3216 | 6.3216 | 6.3216
2021-05-24 21:00 | 2.855 | 3.5355 | 3.5918 | 3.8331 | 3.7366 | 3.978 | 2.0405 | 3.091 | 3.68 | 3.68 | 4.0727 | 4.0727 | 2019-07-22 10:00 | 2.0958 | 3.5964 | 6.0785 | 6.0785 | 6.0785 | 6.0785
2021-05-24 22:00 | 2.5206 | 3.1214 | 3.1711 | 3.3842 | 3.299 | 3.5121 | 1.8148 | 2.749 | 3.2728 | 3.2728 | 3.6221 | 3.6221 | 2019-07-22 11:00 | 2.1644 | 3.7141 | 6.2774 | 6.2774 | 6.2774 | 6.2774
2021-05-24 23:00 | 2.2406 | 2.7746 | 2.8188 | 3.0082 | 2.9324 | 3.1218 | 1.4351 | 2.1739 | 2.5881 | 2.5881 | 2.8643 | 2.8643 | 2019-07-22 12:00 | 2.1415 | 3.6748 | 6.2111 | 6.2111 | 6.2111 | 6.2111
2021-05-25 | 1.9044 | 2.3583 | 2.3958 | 2.5568 | 2.4924 | 2.6534 | 1.2289 | 1.8615 | 2.2162 | 2.2162 | 2.4527 | 2.4527 | 2019-07-22 13:00 | 2.1415 | 3.6748 | 6.2111 | 6.2111 | 6.2111 | 6.2111
2021-05-25 01:00 | 1.809 | 2.2402 | 2.2759 | 2.4288 | 2.3676 | 2.5206 | 1.0974 | 1.6624 | 1.9792 | 1.9792 | 2.1903 | 2.1903 | 2019-07-22 14:00 | 1.9815 | 3.4002 | 5.7469 | 5.7469 | 5.7469 | 5.7469
2021-05-25 02:00 | 1.7662 | 2.1871 | 2.222 | 2.3713 | 2.3115 | 2.4608 | 0.98321 | 1.4894 | 1.7732 | 1.7732 | 1.9624 | 1.9624 | 2019-07-22 15:00 | 2.0653 | 3.5441 | 5.99 | 5.99 | 5.99 | 5.99
2021-05-25 03:00 | 1.7605 | 2.18 | 2.2148 | 2.3636 | 2.3041 | 2.4529 | 0.99454 | 1.5065 | 1.7936 | 1.7936 | 1.985 | 1.985 | 2019-07-22 16:00 | 2.1034 | 3.6094 | 6.1006 | 6.1006 | 6.1006 | 6.1006
2021-05-25 04:00 | 1.9434 | 2.4065 | 2.4449 | 2.6091 | 2.5434 | 2.7077 | 1.046 | 1.5845 | 1.8864 | 1.8864 | 2.0877 | 2.0877 | 2019-07-22 17:00 | 2.1872 | 3.7533 | 6.3437 | 6.3437 | 6.3437 | 6.3437
2021-05-25 05:00 | 2.3168 | 2.869 | 2.9147 | 3.1106 | 3.0322 | 3.2281 | 1.1889 | 1.8009 | 2.1441 | 2.1441 | 2.3729 | 2.3729 | 2019-07-22 18:00 | 2.1949 | 3.7664 | 6.3658 | 6.3658 | 6.3658 | 6.3658
2021-05-25 06:00 | 3.2294 | 3.9991 | 4.0628 | 4.3358 | 4.2266 | 4.4996 | 1.5433 | 2.3377 | 2.7832 | 2.7832 | 3.0802 | 3.0802 | 2019-07-22 19:00 | 2.111 | 3.6225 | 6.1227 | 6.1227 | 6.1227 | 6.1227
2021-05-25 07:00 | 3.5695 | 4.4202 | 4.4907 | 4.7924 | 4.6717 | 4.9734 | 1.8948 | 2.8702 | 3.4171 | 3.4171 | 3.7818 | 3.7818 | 2019-07-22 20:00 | 1.9357 | 3.3217 | 5.6143 | 5.6143 | 5.6143 | 5.6143
2021-05-25 08:00 | 3.5838 | 4.4379 | 4.5086 | 4.8116 | 4.6904 | 4.9933 | 1.8405 | 2.788 | 3.3192 | 3.3192 | 3.6734 | 3.6734 | 2019-07-22 21:00 | 1.8671 | 3.204 | 5.4154 | 5.4154 | 5.4154 | 5.4154
2021-05-25 09:00 | 3.4523 | 4.2751 | 4.3432 | 4.6351 | 4.5183 | 4.8102 | 1.7576 | 2.6624 | 3.1697 | 3.1697 | 3.508 | 3.508 | 2019-07-22 22:00 | 1.7376 | 2.9817 | 5.0396 | 5.0396 | 5.0396 | 5.0396
2021-05-25 10:00 | 3.0808 | 3.8151 | 3.8758 | 4.1363 | 4.0321 | 4.2925 | 1.8405 | 2.788 | 3.3192 | 3.3192 | 3.6734 | 3.6734 | 2019-07-22 23:00 | 1.4556 | 2.4978 | 4.2218 | 4.2218 | 4.2218 | 4.2218
2021-05-25 11:00 | 2.8264 | 3.5001 | 3.5558 | 3.7948 | 3.6992 | 3.9381 | 1.6233 | 2.4589 | 2.9275 | 2.9275 | 3.2399 | 3.2399 | 2019-07-23 | 1.3413 | 2.3017 | 3.8902 | 3.8902 | 3.8902 | 3.8902
2021-05-25 12:00 | 2.6407 | 3.2701 | 3.3221 | 3.5454 | 3.4561 | 3.6793 | 1.589 | 2.407 | 2.8657 | 2.8657 | 3.1714 | 3.1714 | 2019-07-23 01:00 | 1.2575 | 2.1578 | 3.6471 | 3.6471 | 3.6471 | 3.6471
2021-05-25 13:00 | 2.5978 | 3.217 | 3.2682 | 3.4878 | 3.4 | 3.6196 | 1.5661 | 2.3724 | 2.8244 | 2.8244 | 3.1258 | 3.1258 | 2019-07-23 02:00 | 1.227 | 2.1055 | 3.5587 | 3.5587 | 3.5587 | 3.5587
2021-05-25 14:00 | 2.4749 | 3.0648 | 3.1136 | 3.3228 | 3.2391 | 3.4484 | 1.5261 | 2.3118 | 2.7523 | 2.7523 | 3.0459 | 3.0459 | 2019-07-23 03:00 | 1.2575 | 2.1578 | 3.6471 | 3.6471 | 3.6471 | 3.6471
2021-05-25 15:00 | 2.5402 | 3.1456 | 3.1957 | 3.4104 | 3.3245 | 3.5392 | 1.6147 | 2.446 | 2.912 | 2.912 | 3.2228 | 3.2228 | 2019-07-23 04:00 | 1.3261 | 2.2755 | 3.846 | 3.846 | 3.846 | 3.846
2021-05-25 16:00 | 2.7279 | 3.3781 | 3.4319 | 3.6625 | 3.5703 | 3.8009 | 1.8519 | 2.8053 | 3.3398 | 3.3398 | 3.6962 | 3.6962 | 2019-07-23 05:00 | 1.5242 | 2.6155 | 4.4207 | 4.4207 | 4.4207 | 4.4207
2021-05-25 17:00 | 3.158 | 3.9106 | 3.9729 | 4.2399 | 4.1331 | 4.4 | 2.032 | 3.078 | 3.6645 | 3.6645 | 4.0556 | 4.0556 | 2019-07-23 06:00 | 1.7071 | 2.9294 | 4.9512 | 4.9512 | 4.9512 | 4.9512
2021-05-25 18:00 | 3.3237 | 4.1159 | 4.1814 | 4.4624 | 4.35 | 4.631 | 2.1977 | 3.3291 | 3.9635 | 3.9635 | 4.3864 | 4.3864 | 2019-07-23 07:00 | 2.0729 | 3.5571 | 6.0121 | 6.0121 | 6.0121 | 6.0121
2021-05-25 19:00 | 3.2469 | 4.0208 | 4.0849 | 4.3593 | 4.2496 | 4.524 | 2.2177 | 3.3594 | 3.9996 | 3.9996 | 4.4263 | 4.4263 | 2019-07-23 08:00 | 2.172 | 3.7271 | 6.2995 | 6.2995 | 6.2995 | 6.2995
2021-05-25 20:00 | 3.0208 | 3.7408 | 3.8003 | 4.0557 | 3.9535 | 4.2089 | 2.0834 | 3.1559 | 3.7573 | 3.7573 | 4.1582 | 4.1582 | 2019-07-23 09:00 | 2.1186 | 3.6356 | 6.1448 | 6.1448 | 6.1448 | 6.1448
2021-05-25 21:00 | 2.6235 | 3.2488 | 3.3006 | 3.5224 | 3.4336 | 3.6554 | 1.9719 | 2.9871 | 3.5563 | 3.5563 | 3.9358 | 3.9358 | 2019-07-23 10:00 | 2.1034 | 3.6094 | 6.1006 | 6.1006 | 6.1006 | 6.1006
2021-05-25 22:00 | 2.3206 | 2.8737 | 2.9195 | 3.1156 | 3.0372 | 3.2333 | 1.8019 | 2.7295 | 3.2496 | 3.2496 | 3.5963 | 3.5963 | 2019-07-23 11:00 | 2.0805 | 3.5702 | 6.0343 | 6.0343 | 6.0343 | 6.0343
2021-05-25 23:00 | 2.1006 | 2.6013 | 2.6427 | 2.8203 | 2.7492 | 2.9268 | 1.4204 | 2.1516 | 2.5616 | 2.5616 | 2.8349 | 2.8349 | 2019-07-23 12:00 | 2.0729 | 3.5571 | 6.0121 | 6.0121 | 6.0121 | 6.0121
2021-05-26 | 1.8292 | 2.2652 | 2.3013 | 2.4559 | 2.394 | 2.5487 | 1.1203 | 1.697 | 2.0204 | 2.0204 | 2.236 | 2.236 | 2019-07-23 13:00 | 2.0958 | 3.5964 | 6.0785 | 6.0785 | 6.0785 | 6.0785
2021-05-26 01:00 | 1.7747 | 2.1977 | 2.2327 | 2.3828 | 2.3228 | 2.4728 | 1.0231 | 1.5498 | 1.8452 | 1.8452 | 2.042 | 2.042 | 2019-07-23 14:00 | 2.0805 | 3.5702 | 6.0343 | 6.0343 | 6.0343 | 6.0343
2021-05-26 02:00 | 1.6689 | 2.0667 | 2.0996 | 2.2407 | 2.1842 | 2.3253 | 0.96601 | 1.4633 | 1.7422 | 1.7422 | 1.928 | 1.928 | 2019-07-23 15:00 | 2.0653 | 3.5441 | 5.99 | 5.99 | 5.99 | 5.99
2021-05-26 03:00 | 1.6747 | 2.0739 | 2.1069 | 2.2485 | 2.1918 | 2.3334 | 0.94596 | 1.4329 | 1.706 | 1.706 | 1.888 | 1.888 | 2019-07-23 16:00 | 2.1491 | 3.6879 | 6.2332 | 6.2332 | 6.2332 | 6.2332
2021-05-26 04:00 | 1.8119 | 2.2437 | 2.2795 | 2.4326 | 2.3714 | 2.5245 | 1.0168 | 1.5403 | 1.8338 | 1.8338 | 2.0294 | 2.0294 | 2019-07-23 17:00 | 2.1567 | 3.701 | 6.2553 | 6.2553 | 6.2553 | 6.2553
2021-05-26 05:00 | 2.1348 | 2.6437 | 2.6858 | 2.8662 | 2.794 | 2.9745 | 1.0742 | 1.6273 | 1.9374 | 1.9374 | 2.1441 | 2.1441 | 2019-07-23 18:00 | 2.1644 | 3.7141 | 6.2774 | 6.2774 | 6.2774 | 6.2774
2021-05-26 06:00 | 2.9122 | 3.6063 | 3.6637 | 3.9099 | 3.8114 | 4.0576 | 1.4775 | 2.2382 | 2.6646 | 2.6646 | 2.949 | 2.949 | 2019-07-23 19:00 | 2.0805 | 3.5702 | 6.0343 | 6.0343 | 6.0343 | 6.0343
2021-05-26 07:00 | 3.2694 | 4.0486 | 4.1131 | 4.3895 | 4.279 | 4.5553 | 1.769 | 2.6797 | 3.1904 | 3.1904 | 3.5308 | 3.5308 | 2019-07-23 20:00 | 1.9281 | 3.3087 | 5.5922 | 5.5922 | 5.5922 | 5.5922
2021-05-26 08:00 | 3.2408 | 4.0133 | 4.0772 | 4.3511 | 4.2416 | 4.5155 | 1.7833 | 2.7014 | 3.2161 | 3.2161 | 3.5593 | 3.5593 | 2019-07-23 21:00 | 1.829 | 3.1386 | 5.3048 | 5.3048 | 5.3048 | 5.3048
2021-05-26 09:00 | 3.0065 | 3.7231 | 3.7824 | 4.0365 | 3.9348 | 4.189 | 1.7404 | 2.6364 | 3.1388 | 3.1388 | 3.4737 | 3.4737 | 2019-07-23 22:00 | 1.6309 | 2.7986 | 4.7301 | 4.7301 | 4.7301 | 4.7301
2021-05-26 10:00 | 2.8779 | 3.5638 | 3.6206 | 3.8638 | 3.7665 | 4.0098 | 1.6204 | 2.4546 | 2.9224 | 2.9224 | 3.2342 | 3.2342 | 2019-07-23 23:00 | 1.4327 | 2.4586 | 4.1555 | 4.1555 | 4.1555 | 4.1555
2021-05-26 11:00 | 2.6154 | 3.2388 | 3.2904 | 3.5115 | 3.4231 | 3.6442 | 1.6661 | 2.5239 | 3.0048 | 3.0048 | 3.3254 | 3.3254 | 2019-07-24 | 1.3413 | 2.3017 | 3.8902 | 3.8902 | 3.8902 | 3.8902
2021-05-26 12:00 | 2.5092 | 3.1073 | 3.1568 | 3.3689 | 3.284 | 3.4961 | 1.6147 | 2.446 | 2.912 | 2.912 | 3.2228 | 3.2228 | 2019-07-24 01:00 | 1.2575 | 2.1578 | 3.6471 | 3.6471 | 3.6471 | 3.6471
2021-05-26 13:00 | 2.5006 | 3.0966 | 3.146 | 3.3574 | 3.2728 | 3.4842 | 1.6461 | 2.4936 | 2.9687 | 2.9687 | 3.2855 | 3.2855 | 2019-07-24 02:00 | 1.2041 | 2.0663 | 3.4923 | 3.4923 | 3.4923 | 3.4923
2021-05-26 14:00 | 2.5978 | 3.217 | 3.2682 | 3.4878 | 3.4 | 3.6196 | 1.7919 | 2.7144 | 3.2316 | 3.2316 | 3.5764 | 3.5764 | 2019-07-24 03:00 | 1.1965 | 2.0532 | 3.4702 | 3.4702 | 3.4702 | 3.4702
2021-05-26 15:00 | 2.6521 | 3.2842 | 3.3365 | 3.5607 | 3.471 | 3.6952 | 1.7004 | 2.5758 | 3.0667 | 3.0667 | 3.3939 | 3.3939 | 2019-07-24 04:00 | 1.3032 | 2.2363 | 3.7797 | 3.7797 | 3.7797 | 3.7797
2021-05-26 16:00 | 2.9808 | 3.6912 | 3.75 | 4.002 | 3.9012 | 4.1532 | 1.9557 | 2.9625 | 3.527 | 3.527 | 3.9034 | 3.9034 | 2019-07-24 05:00 | 1.4556 | 2.4978 | 4.2218 | 4.2218 | 4.2218 | 4.2218
2021-05-26 17:00 | 3.5752 | 4.4273 | 4.4978 | 4.8001 | 4.6792 | 4.9814 | 2.1148 | 3.2036 | 3.814 | 3.814 | 4.221 | 4.221 | 2019-07-24 06:00 | 1.7147 | 2.9425 | 4.9733 | 4.9733 | 4.9733 | 4.9733
2021-05-26 18:00 | 3.5924 | 4.4486 | 4.5194 | 4.8231 | 4.7016 | 5.0053 | 2.2977 | 3.4806 | 4.1439 | 4.1439 | 4.586 | 4.586 | 2019-07-24 07:00 | 1.9738 | 3.3871 | 5.7248 | 5.7248 | 5.7248 | 5.7248
2021-05-26 19:00 | 3.4239 | 4.24 | 4.3075 | 4.597 | 4.4812 | 4.7706 | 2.3463 | 3.5542 | 4.2315 | 4.2315 | 4.683 | 4.683 | 2019-07-24 08:00 | 2.2177 | 3.8056 | 6.4321 | 6.4321 | 6.4321 | 6.4321
2021-05-26 20:00 | 3.1596 | 3.9127 | 3.975 | 4.2421 | 4.1352 | 4.4023 | 2.2777 | 3.4503 | 4.1078 | 4.1078 | 4.5461 | 4.5461 | 2019-07-24 09:00 | 2.1491 | 3.6879 | 6.2332 | 6.2332 | 6.2332 | 6.2332
2021-05-26 21:00 | 2.9094 | 3.6028 | 3.6602 | 3.9061 | 3.8077 | 4.0537 | 2.1263 | 3.2209 | 3.8346 | 3.8346 | 4.2438 | 4.2438 | 2019-07-24 10:00 | 2.1263 | 3.6487 | 6.1669 | 6.1669 | 6.1669 | 6.1669
2021-05-26 22:00 | 2.4592 | 3.0454 | 3.0939 | 3.3018 | 3.2186 | 3.4265 | 1.9228 | 2.9126 | 3.4676 | 3.4676 | 3.8376 | 3.8376 | 2019-07-24 11:00 | 2.1339 | 3.6618 | 6.189 | 6.189 | 6.189 | 6.189
2021-05-26 23:00 | 2.2927 | 2.8391 | 2.8844 | 3.0782 | 3.0006 | 3.1944 | 1.6176 | 2.4503 | 2.9172 | 2.9172 | 3.2285 | 3.2285 | 2019-07-24 12:00 | 2.1644 | 3.7141 | 6.2774 | 6.2774 | 6.2774 | 6.2774
2021-05-27 | 2.0358 | 2.521 | 2.5611 | 2.7332 | 2.6644 | 2.8365 | 1.2746 | 1.9308 | 2.2987 | 2.2987 | 2.544 | 2.544 | 2019-07-24 13:00 | 2.0958 | 3.5964 | 6.0785 | 6.0785 | 6.0785 | 6.0785
2021-05-27 01:00 | 1.9119 | 2.3676 | 2.4053 | 2.5669 | 2.5023 | 2.6639 | 1.1557 | 1.7507 | 2.0843 | 2.0843 | 2.3067 | 2.3067 | 2019-07-24 14:00 | 2.0577 | 3.531 | 5.9679 | 5.9679 | 5.9679 | 5.9679
2021-05-27 02:00 | 1.8754 | 2.3224 | 2.3594 | 2.518 | 2.4545 | 2.6131 | 1.0546 | 1.5974 | 1.9018 | 1.9018 | 2.1048 | 2.1048 | 2019-07-24 15:00 | 2.0577 | 3.531 | 5.9679 | 5.9679 | 5.9679 | 5.9679
2021-05-27 03:00 | 1.9462 | 2.4101 | 2.4485 | 2.613 | 2.5472 | 2.7117 | 1.0546 | 1.5974 | 1.9018 | 1.9018 | 2.1048 | 2.1048 | 2019-07-24 16:00 | 2.0196 | 3.4656 | 5.8574 | 5.8574 | 5.8574 | 5.8574
2021-05-27 04:00 | 2.1577 | 2.672 | 2.7145 | 2.8969 | 2.824 | 3.0064 | 1.0603 | 1.6061 | 1.9122 | 1.9122 | 2.1162 | 2.1162 | 2019-07-24 17:00 | 2.2025 | 3.7795 | 6.3879 | 6.3879 | 6.3879 | 6.3879
2021-05-27 05:00 | 2.4149 | 2.9905 | 3.0381 | 3.2422 | 3.1606 | 3.3647 | 1.195 | 1.8102 | 2.1551 | 2.1551 | 2.3851 | 2.3851 | 2019-07-24 18:00 | 2.1491 | 3.6879 | 6.2332 | 6.2332 | 6.2332 | 6.2332
2021-05-27 06:00 | 3.4638 | 4.2893 | 4.3576 | 4.6504 | 4.5333 | 4.8261 | 1.5461 | 2.3421 | 2.7883 | 2.7883 | 3.0859 | 3.0859 | 2019-07-24 19:00 | 2.1491 | 3.6879 | 6.2332 | 6.2332 | 6.2332 | 6.2332
2021-05-27 07:00 | 3.9896 | 4.9405 | 5.0192 | 5.3564 | 5.2215 | 5.5588 | 1.9691 | 2.9828 | 3.5512 | 3.5512 | 3.9301 | 3.9301 | 2019-07-24 20:00 | 1.89 | 3.2433 | 5.4817 | 5.4817 | 5.4817 | 5.4817
2021-05-27 08:00 | 3.9039 | 4.8343 | 4.9113 | 5.2413 | 5.1093 | 5.4393 | 2.0005 | 3.0304 | 3.6078 | 3.6078 | 3.9928 | 3.9928 | 2019-07-24 21:00 | 1.8824 | 3.2302 | 5.4596 | 5.4596 | 5.4596 | 5.4596
2021-05-27 09:00 | 3.5781 | 4.4309 | 4.5014 | 4.8039 | 4.6829 | 4.9854 | 1.8005 | 2.7274 | 3.2471 | 3.2471 | 3.5935 | 3.5935 | 2019-07-24 22:00 | 1.6385 | 2.8117 | 4.7522 | 4.7522 | 4.7522 | 4.7522
2021-05-27 10:00 | 3.3694 | 4.1725 | 4.239 | 4.5238 | 4.4099 | 4.6947 | 1.7283 | 2.618 | 3.1169 | 3.1169 | 3.4495 | 3.4495 | 2019-07-24 23:00 | 1.4251 | 2.4455 | 4.1333 | 4.1333 | 4.1333 | 4.1333
2021-05-27 11:00 | 2.9979 | 3.7124 | 3.7716 | 4.025 | 3.9236 | 4.177 | 1.7805 | 2.697 | 3.211 | 3.211 | 3.5536 | 3.5536 | 2019-07-25 | 1.3261 | 2.2755 | 3.846 | 3.846 | 3.846 | 3.846
2021-05-27 12:00 | 2.6807 | 3.3196 | 3.3725 | 3.5991 | 3.5084 | 3.7351 | 1.6747 | 2.5369 | 3.0203 | 3.0203 | 3.3426 | 3.3426 | 2019-07-25 01:00 | 1.2651 | 2.1709 | 3.6692 | 3.6692 | 3.6692 | 3.6692
2021-05-27 13:00 | 2.6435 | 3.2736 | 3.3257 | 3.5492 | 3.4598 | 3.6833 | 1.7119 | 2.5932 | 3.0873 | 3.0873 | 3.4167 | 3.4167 | 2019-07-25 02:00 | 1.2651 | 2.1709 | 3.6692 | 3.6692 | 3.6692 | 3.6692
2021-05-27 14:00 | 2.6092 | 3.2311 | 3.2826 | 3.5032 | 3.4149 | 3.6355 | 1.7547 | 2.6581 | 3.1646 | 3.1646 | 3.5023 | 3.5023 | 2019-07-25 03:00 | 1.227 | 2.1055 | 3.5587 | 3.5587 | 3.5587 | 3.5587
2021-05-27 15:00 | 2.7036 | 3.3479 | 3.4012 | 3.6298 | 3.5384 | 3.7669 | 1.6804 | 2.5455 | 3.0306 | 3.0306 | 3.354 | 3.354 | 2019-07-25 04:00 | 1.2041 | 2.0663 | 3.4923 | 3.4923 | 3.4923 | 3.4923
2021-05-27 16:00 | 3.2265 | 3.9956 | 4.0592 | 4.332 | 4.2229 | 4.4956 | 1.9691 | 2.9828 | 3.5512 | 3.5512 | 3.9301 | 3.9301 | 2019-07-25 05:00 | 1.4861 | 2.5501 | 4.3102 | 4.3102 | 4.3102 | 4.3102
2021-05-27 17:00 | 3.7067 | 4.5901 | 4.6632 | 4.9766 | 4.8512 | 5.1646 | 2.1977 | 3.3291 | 3.9635 | 3.9635 | 4.3864 | 4.3864 | 2019-07-25 06:00 | 1.7757 | 3.0471 | 5.1501 | 5.1501 | 5.1501 | 5.1501
2021-05-27 18:00 | 3.8724 | 4.7954 | 4.8718 | 5.1991 | 5.0682 | 5.3955 | 2.4178 | 3.6624 | 4.3603 | 4.3603 | 4.8256 | 4.8256 | 2019-07-25 07:00 | 2.0348 | 3.4917 | 5.9016 | 5.9016 | 5.9016 | 5.9016
2021-05-27 19:00 | 3.7724 | 4.6715 | 4.7459 | 5.0648 | 4.9373 | 5.2562 | 2.392 | 3.6235 | 4.314 | 4.314 | 4.7743 | 4.7743 | 2019-07-25 08:00 | 2.2177 | 3.8056 | 6.4321 | 6.4321 | 6.4321 | 6.4321
2021-05-27 20:00 | 3.4895 | 4.3212 | 4.39 | 4.685 | 4.567 | 4.8619 | 2.3749 | 3.5975 | 4.283 | 4.283 | 4.74 | 4.74 | 2019-07-25 09:00 | 2.1644 | 3.7141 | 6.2774 | 6.2774 | 6.2774 | 6.2774
2021-05-27 21:00 | 3.099 | 3.8376 | 3.8987 | 4.1607 | 4.0559 | 4.3178 | 2.1863 | 3.3118 | 3.9429 | 3.9429 | 4.3636 | 4.3636 | 2019-07-25 10:00 | 2.0805 | 3.5702 | 6.0343 | 6.0343 | 6.0343 | 6.0343
2021-05-27 22:00 | 2.6635 | 3.2984 | 3.3509 | 3.5761 | 3.486 | 3.7112 | 1.8833 | 2.8529 | 3.3965 | 3.3965 | 3.7589 | 3.7589 | 2019-07-25 11:00 | 2.1263 | 3.6487 | 6.1669 | 6.1669 | 6.1669 | 6.1669
2021-05-27 23:00 | 2.3778 | 2.9445 | 2.9914 | 3.1924 | 3.112 | 3.313 | 1.569 | 2.3767 | 2.8296 | 2.8296 | 3.1315 | 3.1315 | 2019-07-25 12:00 | 2.1872 | 3.7533 | 6.3437 | 6.3437 | 6.3437 | 6.3437
2021-05-28 | 2.0205 | 2.5021 | 2.5419 | 2.7127 | 2.6444 | 2.8152 | 1.3003 | 1.9698 | 2.3451 | 2.3451 | 2.5953 | 2.5953 | 2019-07-25 13:00 | 2.111 | 3.6225 | 6.1227 | 6.1227 | 6.1227 | 6.1227
2021-05-28 01:00 | 1.9033 | 2.357 | 2.3945 | 2.5554 | 2.4911 | 2.652 | 1.1547 | 1.7491 | 2.0824 | 2.0824 | 2.3046 | 2.3046 | 2019-07-25 14:00 | 2.0653 | 3.5441 | 5.99 | 5.99 | 5.99 | 5.99
2021-05-28 02:00 | 1.9005 | 2.3535 | 2.3909 | 2.5516 | 2.4873 | 2.648 | 1.0574 | 1.6018 | 1.907 | 1.907 | 2.1105 | 2.1105 | 2019-07-25 15:00 | 2.1339 | 3.6618 | 6.189 | 6.189 | 6.189 | 6.189
2021-05-28 03:00 | 1.8633 | 2.3074 | 2.3442 | 2.5017 | 2.4387 | 2.5962 | 1.0826 | 1.6399 | 1.9523 | 1.9523 | 2.1607 | 2.1607 | 2019-07-25 16:00 | 2.1339 | 3.6618 | 6.189 | 6.189 | 6.189 | 6.189
2021-05-28 04:00 | 2.083 | 2.5795 | 2.6206 | 2.7967 | 2.7263 | 2.9023 | 1.0831 | 1.6407 | 1.9534 | 1.9534 | 2.1618 | 2.1618 | 2019-07-25 17:00 | 2.172 | 3.7271 | 6.2995 | 6.2995 | 6.2995 | 6.2995
2021-05-28 05:00 | 2.4056 | 2.9789 | 3.0264 | 3.2297 | 3.1484 | 3.3518 | 1.206 | 1.8269 | 2.175 | 2.175 | 2.4071 | 2.4071 | 2019-07-25 18:00 | 2.1263 | 3.6487 | 6.1669 | 6.1669 | 6.1669 | 6.1669
2021-05-28 06:00 | 3.3094 | 4.0982 | 4.1635 | 4.4432 | 4.3313 | 4.6111 | 1.4232 | 2.1559 | 2.5667 | 2.5667 | 2.8406 | 2.8406 | 2019-07-25 19:00 | 2.0196 | 3.4656 | 5.8574 | 5.8574 | 5.8574 | 5.8574
2021-05-28 07:00 | 3.7152 | 4.6007 | 4.674 | 4.9881 | 4.8625 | 5.1765 | 1.9234 | 2.9135 | 3.4687 | 3.4687 | 3.8388 | 3.8388 | 2019-07-25 20:00 | 1.9053 | 3.2694 | 5.5259 | 5.5259 | 5.5259 | 5.5259
2021-05-28 08:00 | 3.6695 | 4.5441 | 4.6165 | 4.9267 | 4.8026 | 5.1128 | 1.849 | 2.8009 | 3.3347 | 3.3347 | 3.6905 | 3.6905 | 2019-07-25 21:00 | 1.8214 | 3.1256 | 5.2827 | 5.2827 | 5.2827 | 5.2827
2021-05-28 09:00 | 3.4666 | 4.2928 | 4.3612 | 4.6543 | 4.537 | 4.8301 | 1.7404 | 2.6364 | 3.1388 | 3.1388 | 3.4737 | 3.4737 | 2019-07-25 22:00 | 1.6004 | 2.7463 | 4.6417 | 4.6417 | 4.6417 | 4.6417
2021-05-28 10:00 | 3.1551 | 3.9071 | 3.9693 | 4.236 | 4.1293 | 4.3961 | 1.7262 | 2.6148 | 3.1131 | 3.1131 | 3.4452 | 3.4452 | 2019-07-25 23:00 | 1.4023 | 2.4063 | 4.067 | 4.067 | 4.067 | 4.067
2021-05-28 11:00 | 3.0081 | 3.7251 | 3.7844 | 4.0387 | 3.937 | 4.1913 | 1.7004 | 2.5758 | 3.0667 | 3.0667 | 3.3939 | 3.3939 | 2019-07-26 | 1.3337 | 2.2886 | 3.8681 | 3.8681 | 3.8681 | 3.8681
2021-05-28 12:00 | 2.8264 | 3.5001 | 3.5558 | 3.7948 | 3.6992 | 3.9381 | 1.6568 | 2.5098 | 2.988 | 2.988 | 3.3068 | 3.3068 | 2019-07-26 01:00 | 1.2727 | 2.184 | 3.6913 | 3.6913 | 3.6913 | 3.6913
2021-05-28 13:00 | 2.7121 | 3.3585 | 3.412 | 3.6413 | 3.5496 | 3.7789 | 1.7176 | 2.6018 | 3.0976 | 3.0976 | 3.4281 | 3.4281 | 2019-07-26 02:00 | 1.2727 | 2.184 | 3.6913 | 3.6913 | 3.6913 | 3.6913
2021-05-28 14:00 | 2.7407 | 3.3939 | 3.448 | 3.6797 | 3.587 | 3.8187 | 1.7062 | 2.5845 | 3.077 | 3.077 | 3.4053 | 3.4053 | 2019-07-26 03:00 | 1.227 | 2.1055 | 3.5587 | 3.5587 | 3.5587 | 3.5587
2021-05-28 15:00 | 2.7091 | 3.3548 | 3.4083 | 3.6373 | 3.5457 | 3.7747 | 1.7833 | 2.7014 | 3.2161 | 3.2161 | 3.5593 | 3.5593 | 2019-07-26 04:00 | 1.3184 | 2.2624 | 3.8239 | 3.8239 | 3.8239 | 3.8239
2021-05-28 16:00 | 3.1637 | 3.9177 | 3.9801 | 4.2475 | 4.1406 | 4.408 | 1.9748 | 2.9914 | 3.5615 | 3.5615 | 3.9415 | 3.9415 | 2019-07-26 05:00 | 1.5699 | 2.694 | 4.5533 | 4.5533 | 4.5533 | 4.5533
2021-05-28 17:00 | 3.478 | 4.307 | 4.3756 | 4.6696 | 4.552 | 4.846 | 2.3863 | 3.6148 | 4.3036 | 4.3036 | 4.7629 | 4.7629 | 2019-07-26 06:00 | 1.7376 | 2.9817 | 5.0396 | 5.0396 | 5.0396 | 5.0396
2021-05-28 18:00 | 3.5323 | 4.3742 | 4.4439 | 4.7425 | 4.6231 | 4.9217 | 2.5264 | 3.827 | 4.5562 | 4.5562 | 5.0424 | 5.0424 | 2019-07-26 07:00 | 2.0805 | 3.5702 | 6.0343 | 6.0343 | 6.0343 | 6.0343
2021-05-28 19:00 | 3.3894 | 4.1973 | 4.2641 | 4.5507 | 4.4361 | 4.7226 | 2.5321 | 3.8356 | 4.5665 | 4.5665 | 5.0538 | 5.0538 | 2019-07-26 08:00 | 2.2939 | 3.9364 | 6.6531 | 6.6531 | 6.6531 | 6.6531
2021-05-28 20:00 | 3.1694 | 3.9248 | 3.9873 | 4.2552 | 4.148 | 4.416 | 2.5749 | 3.9006 | 4.6438 | 4.6438 | 5.1393 | 5.1393 | 2019-07-26 09:00 | 2.2939 | 3.9364 | 6.6531 | 6.6531 | 6.6531 | 6.6531
2021-05-28 21:00 | 2.8865 | 3.5744 | 3.6314 | 3.8754 | 3.7778 | 4.0218 | 2.312 | 3.5023 | 4.1696 | 4.1696 | 4.6146 | 4.6146 | 2019-07-26 10:00 | 2.2558 | 3.871 | 6.5426 | 6.5426 | 6.5426 | 6.5426
2021-05-28 22:00 | 2.6408 | 3.2702 | 3.3223 | 3.5455 | 3.4562 | 3.6794 | 2.0748 | 3.143 | 3.7419 | 3.7419 | 4.1411 | 4.1411 | 2019-07-26 11:00 | 2.1034 | 3.6094 | 6.1006 | 6.1006 | 6.1006 | 6.1006
2021-05-28 23:00 | 2.4663 | 3.0542 | 3.1028 | 3.3113 | 3.2279 | 3.4364 | 1.8919 | 2.8659 | 3.412 | 3.412 | 3.7761 | 3.7761 | 2019-07-26 12:00 | 2.1644 | 3.7141 | 6.2774 | 6.2774 | 6.2774 | 6.2774
2021-05-29 | 2.1236 | 2.6298 | 2.6717 | 2.8512 | 2.7794 | 2.9589 | 1.4976 | 2.2686 | 2.7009 | 2.7009 | 2.9891 | 2.9891 | 2019-07-26 13:00 | 2.1796 | 3.7402 | 6.3216 | 6.3216 | 6.3216 | 6.3216
2021-05-29 01:00 | 2.0005 | 2.4773 | 2.5168 | 2.6859 | 2.6182 | 2.7874 | 1.3032 | 1.9741 | 2.3503 | 2.3503 | 2.601 | 2.601 | 2019-07-26 14:00 | 2.1339 | 3.6618 | 6.189 | 6.189 | 6.189 | 6.189
2021-05-29 02:00 | 1.8434 | 2.2827 | 2.3191 | 2.4749 | 2.4126 | 2.5684 | 1.169 | 1.7708 | 2.1082 | 2.1082 | 2.3331 | 2.3331 | 2019-07-26 15:00 | 2.2025 | 3.7795 | 6.3879 | 6.3879 | 6.3879 | 6.3879
2021-05-29 03:00 | 1.9345 | 2.3956 | 2.4338 | 2.5973 | 2.5319 | 2.6954 | 1.1117 | 1.684 | 2.0049 | 2.0049 | 2.2189 | 2.2189 | 2019-07-26 16:00 | 2.1949 | 3.7664 | 6.3658 | 6.3658 | 6.3658 | 6.3658
2021-05-29 04:00 | 1.9662 | 2.4349 | 2.4736 | 2.6398 | 2.5734 | 2.7396 | 1.1574 | 1.7533 | 2.0874 | 2.0874 | 2.3101 | 2.3101 | 2019-07-26 17:00 | 2.233 | 3.8318 | 6.4763 | 6.4763 | 6.4763 | 6.4763
2021-05-29 05:00 | 2.052 | 2.541 | 2.5815 | 2.755 | 2.6856 | 2.859 | 1.2432 | 1.8832 | 2.242 | 2.242 | 2.4812 | 2.4812 | 2019-07-26 18:00 | 2.1491 | 3.6879 | 6.2332 | 6.2332 | 6.2332 | 6.2332
2021-05-29 06:00 | 2.3949 | 2.9657 | 3.0129 | 3.2154 | 3.1344 | 3.3369 | 1.3938 | 2.1113 | 2.5136 | 2.5136 | 2.7818 | 2.7818 | 2019-07-26 19:00 | 2.0196 | 3.4656 | 5.8574 | 5.8574 | 5.8574 | 5.8574
2021-05-29 07:00 | 2.7464 | 3.401 | 3.4552 | 3.6873 | 3.5945 | 3.8266 | 1.7347 | 2.6278 | 3.1285 | 3.1285 | 3.4623 | 3.4623 | 2019-07-26 20:00 | 1.9357 | 3.3217 | 5.6143 | 5.6143 | 5.6143 | 5.6143
2021-05-29 08:00 | 2.8122 | 3.4824 | 3.5379 | 3.7756 | 3.6805 | 3.9182 | 1.8633 | 2.8226 | 3.3604 | 3.3604 | 3.719 | 3.719 | 2019-07-26 21:00 | 1.89 | 3.2433 | 5.4817 | 5.4817 | 5.4817 | 5.4817
2021-05-29 09:00 | 2.8322 | 3.5072 | 3.563 | 3.8025 | 3.7067 | 3.9461 | 1.9548 | 2.9611 | 3.5254 | 3.5254 | 3.9015 | 3.9015 | 2019-07-26 22:00 | 1.6766 | 2.8771 | 4.8628 | 4.8628 | 4.8628 | 4.8628
2021-05-29 10:00 | 2.7321 | 3.3833 | 3.4372 | 3.6682 | 3.5758 | 3.8067 | 2.0405 | 3.091 | 3.68 | 3.68 | 4.0727 | 4.0727 | 2019-07-26 23:00 | 1.4709 | 2.524 | 4.266 | 4.266 | 4.266 | 4.266
2021-05-29 11:00 | 2.4553 | 3.0406 | 3.089 | 3.2965 | 3.2135 | 3.4211 | 1.9891 | 3.0131 | 3.5872 | 3.5872 | 3.97 | 3.97 | 2019-07-27 | 1.3413 | 2.3017 | 3.8902 | 3.8902 | 3.8902 | 3.8902
2021-05-29 12:00 | 2.2349 | 2.7675 | 2.8116 | 3.0005 | 2.925 | 3.1139 | 1.9548 | 2.9611 | 3.5254 | 3.5254 | 3.9015 | 3.9015 | 2019-07-27 01:00 | 1.2575 | 2.1578 | 3.6471 | 3.6471 | 3.6471 | 3.6471
2021-05-29 13:00 | 2.2206 | 2.7498 | 2.7936 | 2.9813 | 2.9063 | 3.094 | 1.9405 | 2.9395 | 3.4996 | 3.4996 | 3.873 | 3.873 | 2019-07-27 02:00 | 1.227 | 2.1055 | 3.5587 | 3.5587 | 3.5587 | 3.5587
2021-05-29 14:00 | 2.2091 | 2.7357 | 2.7792 | 2.966 | 2.8913 | 3.078 | 1.8891 | 2.8616 | 3.4068 | 3.4068 | 3.7704 | 3.7704 | 2019-07-27 03:00 | 1.2422 | 2.1317 | 3.6029 | 3.6029 | 3.6029 | 3.6029
2021-05-29 15:00 | 2.2149 | 2.7427 | 2.7864 | 2.9737 | 2.8988 | 3.086 | 1.9062 | 2.8875 | 3.4378 | 3.4378 | 3.8046 | 3.8046 | 2019-07-27 04:00 | 1.3032 | 2.2363 | 3.7797 | 3.7797 | 3.7797 | 3.7797
2021-05-29 16:00 | 2.695 | 3.3373 | 3.3905 | 3.6183 | 3.5271 | 3.755 | 2.1891 | 3.3161 | 3.948 | 3.948 | 4.3693 | 4.3693 | 2019-07-27 05:00 | 1.3946 | 2.3932 | 4.0449 | 4.0449 | 4.0449 | 4.0449
2021-05-29 17:00 | 3.0351 | 3.7584 | 3.8183 | 4.0749 | 3.9723 | 4.2288 | 2.3863 | 3.6148 | 4.3036 | 4.3036 | 4.7629 | 4.7629 | 2019-07-27 06:00 | 1.4785 | 2.5371 | 4.2881 | 4.2881 | 4.2881 | 4.2881
2021-05-29 18:00 | 3.1322 | 3.8788 | 3.9406 | 4.2053 | 4.0994 | 4.3642 | 2.4721 | 3.7447 | 4.4583 | 4.4583 | 4.934 | 4.934 | 2019-07-27 07:00 | 1.6233 | 2.7855 | 4.708 | 4.708 | 4.708 | 4.708
2021-05-29 19:00 | 2.9479 | 3.6505 | 3.7086 | 3.9578 | 3.8582 | 4.1074 | 2.4121 | 3.6538 | 4.35 | 4.35 | 4.8142 | 4.8142 | 2019-07-27 08:00 | 1.8748 | 3.2171 | 5.4375 | 5.4375 | 5.4375 | 5.4375
2021-05-29 20:00 | 2.8636 | 3.5461 | 3.6026 | 3.8447 | 3.7478 | 3.9899 | 2.292 | 3.472 | 4.1336 | 4.1336 | 4.5746 | 4.5746 | 2019-07-27 09:00 | 1.9815 | 3.4002 | 5.7469 | 5.7469 | 5.7469 | 5.7469
2021-05-29 21:00 | 2.6521 | 3.2842 | 3.3365 | 3.5607 | 3.471 | 3.6952 | 2.2006 | 3.3334 | 3.9686 | 3.9686 | 4.3921 | 4.3921 | 2019-07-27 10:00 | 1.9967 | 3.4264 | 5.7911 | 5.7911 | 5.7911 | 5.7911
2021-05-29 22:00 | 2.6121 | 3.2347 | 3.2862 | 3.507 | 3.4187 | 3.6395 | 2.0177 | 3.0564 | 3.6388 | 3.6388 | 4.027 | 4.027 | 2019-07-27 11:00 | 1.9738 | 3.3871 | 5.7248 | 5.7248 | 5.7248 | 5.7248
2021-05-29 23:00 | 2.4551 | 3.0403 | 3.0887 | 3.2962 | 3.2132 | 3.4208 | 1.7272 | 2.6163 | 3.1149 | 3.1149 | 3.4473 | 3.4473 | 2019-07-27 12:00 | 1.8824 | 3.2302 | 5.4596 | 5.4596 | 5.4596 | 5.4596
2021-05-30 | 2.1449 | 2.6561 | 2.6984 | 2.8797 | 2.8072 | 2.9885 | 1.4175 | 2.1472 | 2.5564 | 2.5564 | 2.8292 | 2.8292 | 2019-07-27 13:00 | 1.8062 | 3.0994 | 5.2385 | 5.2385 | 5.2385 | 5.2385
2021-05-30 01:00 | 1.9948 | 2.4702 | 2.5096 | 2.6782 | 2.6108 | 2.7794 | 1.2232 | 1.8529 | 2.2059 | 2.2059 | 2.4413 | 2.4413 | 2019-07-27 14:00 | 1.8748 | 3.2171 | 5.4375 | 5.4375 | 5.4375 | 5.4375
2021-05-30 02:00 | 1.8897 | 2.3401 | 2.3774 | 2.5372 | 2.4733 | 2.633 | 1.1889 | 1.8009 | 2.1441 | 2.1441 | 2.3729 | 2.3729 | 2019-07-27 15:00 | 1.8824 | 3.2302 | 5.4596 | 5.4596 | 5.4596 | 5.4596
2021-05-30 03:00 | 1.9062 | 2.3605 | 2.3981 | 2.5593 | 2.4948 | 2.6559 | 1.1403 | 1.7273 | 2.0565 | 2.0565 | 2.2759 | 2.2759 | 2019-07-27 16:00 | 1.9434 | 3.3348 | 5.6364 | 5.6364 | 5.6364 | 5.6364
2021-05-30 04:00 | 1.9634 | 2.4313 | 2.47 | 2.636 | 2.5696 | 2.7356 | 1.1247 | 1.7037 | 2.0283 | 2.0283 | 2.2447 | 2.2447 | 2019-07-27 17:00 | 1.8595 | 3.191 | 5.3932 | 5.3932 | 5.3932 | 5.3932
2021-05-30 05:00 | 2.0618 | 2.5532 | 2.5938 | 2.7681 | 2.6984 | 2.8727 | 1.1711 | 1.774 | 2.1121 | 2.1121 | 2.3375 | 2.3375 | 2019-07-27 18:00 | 1.8595 | 3.191 | 5.3932 | 5.3932 | 5.3932 | 5.3932
2021-05-30 06:00 | 2.3463 | 2.9055 | 2.9518 | 3.1502 | 3.0708 | 3.2692 | 1.3429 | 2.0343 | 2.4219 | 2.4219 | 2.6803 | 2.6803 | 2019-07-27 19:00 | 1.6842 | 2.8902 | 4.8849 | 4.8849 | 4.8849 | 4.8849
2021-05-30 07:00 | 2.7493 | 3.4045 | 3.4588 | 3.6912 | 3.5982 | 3.8306 | 1.5318 | 2.3204 | 2.7626 | 2.7626 | 3.0574 | 3.0574 | 2019-07-27 20:00 | 1.7071 | 2.9294 | 4.9512 | 4.9512 | 4.9512 | 4.9512
2021-05-30 08:00 | 2.7893 | 3.4541 | 3.5091 | 3.7449 | 3.6506 | 3.8864 | 1.8519 | 2.8053 | 3.3398 | 3.3398 | 3.6962 | 3.6962 | 2019-07-27 21:00 | 1.5471 | 2.6548 | 4.487 | 4.487 | 4.487 | 4.487
2021-05-30 09:00 | 2.6748 | 3.3123 | 3.3651 | 3.5912 | 3.5007 | 3.7269 | 1.9519 | 2.9568 | 3.5202 | 3.5202 | 3.8958 | 3.8958 | 2019-07-27 22:00 | 1.4632 | 2.5109 | 4.2439 | 4.2439 | 4.2439 | 4.2439
2021-05-30 10:00 | 2.5635 | 3.1745 | 3.2251 | 3.4418 | 3.3551 | 3.5718 | 2.0091 | 3.0434 | 3.6233 | 3.6233 | 4.0099 | 4.0099 | 2019-07-27 23:00 | 1.4404 | 2.4717 | 4.1776 | 4.1776 | 4.1776 | 4.1776
2021-05-30 11:00 | 2.3177 | 2.8702 | 2.9159 | 3.1118 | 3.0334 | 3.2293 | 1.9977 | 3.0261 | 3.6027 | 3.6027 | 3.9871 | 3.9871 | 2019-07-28 | 1.2803 | 2.1971 | 3.7134 | 3.7134 | 3.7134 | 3.7134
2021-05-30 12:00 | 2.1949 | 2.718 | 2.7613 | 2.9468 | 2.8726 | 3.0581 | 1.9605 | 2.9698 | 3.5357 | 3.5357 | 3.913 | 3.913 | 2019-07-28 01:00 | 1.1965 | 2.0532 | 3.4702 | 3.4702 | 3.4702 | 3.4702
2021-05-30 13:00 | 2.0834 | 2.58 | 2.621 | 2.7972 | 2.7267 | 2.9028 | 1.9462 | 2.9481 | 3.5099 | 3.5099 | 3.8844 | 3.8844 | 2019-07-28 02:00 | 1.1813 | 2.027 | 3.426 | 3.426 | 3.426 | 3.426
2021-05-30 14:00 | 2.1055 | 2.6073 | 2.6489 | 2.8269 | 2.7557 | 2.9336 | 1.9805 | 3.0001 | 3.5718 | 3.5718 | 3.9529 | 3.9529 | 2019-07-28 03:00 | 1.2041 | 2.0663 | 3.4923 | 3.4923 | 3.4923 | 3.4923
2021-05-30 15:00 | 2.2537 | 2.7908 | 2.8353 | 3.0258 | 2.9496 | 3.1401 | 1.8576 | 2.8139 | 3.3501 | 3.3501 | 3.7076 | 3.7076 | 2019-07-28 04:00 | 1.227 | 2.1055 | 3.5587 | 3.5587 | 3.5587 | 3.5587
2021-05-30 16:00 | 2.5607 | 3.171 | 3.2215 | 3.4379 | 3.3514 | 3.5678 | 2.1205 | 3.2122 | 3.8243 | 3.8243 | 4.2324 | 4.2324 | 2019-07-28 05:00 | 1.3794 | 2.3671 | 4.0007 | 4.0007 | 4.0007 | 4.0007
2021-05-30 17:00 | 3.0408 | 3.7655 | 3.8255 | 4.0826 | 3.9797 | 4.2368 | 2.3835 | 3.6105 | 4.2985 | 4.2985 | 4.7572 | 4.7572 | 2019-07-28 06:00 | 1.4023 | 2.4063 | 4.067 | 4.067 | 4.067 | 4.067
2021-05-30 18:00 | 3.218 | 3.9849 | 4.0484 | 4.3204 | 4.2116 | 4.4837 | 2.5292 | 3.8313 | 4.5613 | 4.5613 | 5.0481 | 5.0481 | 2019-07-28 07:00 | 1.6538 | 2.8379 | 4.7965 | 4.7965 | 4.7965 | 4.7965
2021-05-30 19:00 | 3.1694 | 3.9248 | 3.9873 | 4.2552 | 4.148 | 4.416 | 2.5149 | 3.8096 | 4.5356 | 4.5356 | 5.0195 | 5.0195 | 2019-07-28 08:00 | 1.89 | 3.2433 | 5.4817 | 5.4817 | 5.4817 | 5.4817
2021-05-30 20:00 | 3.0093 | 3.7266 | 3.786 | 4.0403 | 3.9386 | 4.193 | 2.3435 | 3.5499 | 4.2263 | 4.2263 | 4.6773 | 4.6773 | 2019-07-28 09:00 | 1.9434 | 3.3348 | 5.6364 | 5.6364 | 5.6364 | 5.6364
2021-05-30 21:00 | 2.7779 | 3.4399 | 3.4947 | 3.7295 | 3.6356 | 3.8704 | 2.3177 | 3.5109 | 4.1799 | 4.1799 | 4.626 | 4.626 | 2019-07-28 10:00 | 1.8519 | 3.1779 | 5.3711 | 5.3711 | 5.3711 | 5.3711
2021-05-30 22:00 | 2.6292 | 3.2559 | 3.3078 | 3.53 | 3.4411 | 3.6634 | 1.9851 | 3.0071 | 3.5801 | 3.5801 | 3.9621 | 3.9621 | 2019-07-28 11:00 | 1.8976 | 3.2563 | 5.5038 | 5.5038 | 5.5038 | 5.5038
2021-05-30 23:00 | 2.4658 | 3.0535 | 3.1021 | 3.3105 | 3.2272 | 3.4356 | 1.7273 | 2.6165 | 3.1151 | 3.1151 | 3.4475 | 3.4475 | 2019-07-28 12:00 | 1.8976 | 3.2563 | 5.5038 | 5.5038 | 5.5038 | 5.5038
2021-05-31 | 2.1738 | 2.6919 | 2.7347 | 2.9185 | 2.845 | 3.0288 | 1.4432 | 2.1862 | 2.6028 | 2.6028 | 2.8805 | 2.8805 | 2019-07-28 13:00 | 1.8367 | 3.1517 | 5.3269 | 5.3269 | 5.3269 | 5.3269
2021-05-31 01:00 | 1.9977 | 2.4738 | 2.5132 | 2.682 | 2.6145 | 2.7834 | 1.3305 | 2.0154 | 2.3994 | 2.3994 | 2.6555 | 2.6555 | 2019-07-28 14:00 | 1.8595 | 3.191 | 5.3932 | 5.3932 | 5.3932 | 5.3932
2021-05-31 02:00 | 1.9719 | 2.4419 | 2.4808 | 2.6475 | 2.5808 | 2.7475 | 1.2291 | 1.8619 | 2.2167 | 2.2167 | 2.4532 | 2.4532 | 2019-07-28 15:00 | 1.8595 | 3.191 | 5.3932 | 5.3932 | 5.3932 | 5.3932
2021-05-31 03:00 | 1.9491 | 2.4136 | 2.4521 | 2.6168 | 2.5509 | 2.7157 | 1.1946 | 1.8096 | 2.1544 | 2.1544 | 2.3843 | 2.3843 | 2019-07-28 16:00 | 1.9129 | 3.2825 | 5.548 | 5.548 | 5.548 | 5.548
2021-05-31 04:00 | 1.9748 | 2.4455 | 2.4844 | 2.6514 | 2.5846 | 2.7515 | 1.266 | 1.9178 | 2.2832 | 2.2832 | 2.5269 | 2.5269 | 2019-07-28 17:00 | 1.9662 | 3.374 | 5.7027 | 5.7027 | 5.7027 | 5.7027
2021-05-31 05:00 | 2.2763 | 2.8188 | 2.8637 | 3.0562 | 2.9792 | 3.1716 | 1.306 | 1.9784 | 2.3554 | 2.3554 | 2.6067 | 2.6067 | 2019-07-28 18:00 | 1.9586 | 3.361 | 5.6806 | 5.6806 | 5.6806 | 5.6806
2021-05-31 06:00 | 2.6092 | 3.2311 | 3.2826 | 3.5032 | 3.4149 | 3.6355 | 1.4775 | 2.2382 | 2.6646 | 2.6646 | 2.949 | 2.949 | 2019-07-28 19:00 | 1.9662 | 3.374 | 5.7027 | 5.7027 | 5.7027 | 5.7027
2021-05-31 07:00 | 3.0608 | 3.7903 | 3.8507 | 4.1094 | 4.0059 | 4.2647 | 1.749 | 2.6494 | 3.1543 | 3.1543 | 3.4909 | 3.4909 | 2019-07-28 20:00 | 1.7986 | 3.0863 | 5.2164 | 5.2164 | 5.2164 | 5.2164
2021-05-31 08:00 | 3.2037 | 3.9673 | 4.0304 | 4.3013 | 4.1929 | 4.4637 | 1.9062 | 2.8875 | 3.4378 | 3.4378 | 3.8046 | 3.8046 | 2019-07-28 21:00 | 1.7681 | 3.034 | 5.128 | 5.128 | 5.128 | 5.128
2021-05-31 09:00 | 3.2065 | 3.9708 | 4.034 | 4.3051 | 4.1967 | 4.4677 | 1.9919 | 3.0174 | 3.5924 | 3.5924 | 3.9757 | 3.9757 | 2019-07-28 22:00 | 1.5394 | 2.6417 | 4.4649 | 4.4649 | 4.4649 | 4.4649
2021-05-31 10:00 | 3.1151 | 3.8575 | 3.919 | 4.1823 | 4.077 | 4.3403 | 2.1463 | 3.2512 | 3.8707 | 3.8707 | 4.2837 | 4.2837 | 2019-07-28 23:00 | 1.4175 | 2.4324 | 4.1112 | 4.1112 | 4.1112 | 4.1112
2021-05-31 11:00 | 2.7293 | 3.3798 | 3.4336 | 3.6643 | 3.572 | 3.8027 | 1.9834 | 3.0044 | 3.5769 | 3.5769 | 3.9586 | 3.9586 | 2019-07-29 | 1.3642 | 2.3409 | 3.9565 | 3.9565 | 3.9565 | 3.9565
2021-05-31 12:00 | 2.5349 | 3.1391 | 3.1891 | 3.4034 | 3.3177 | 3.532 | 2.0462 | 3.0997 | 3.6903 | 3.6903 | 4.0841 | 4.0841 | 2019-07-29 01:00 | 1.227 | 2.1055 | 3.5587 | 3.5587 | 3.5587 | 3.5587
2021-05-31 13:00 | 2.3377 | 2.8949 | 2.941 | 3.1387 | 3.0596 | 3.2572 | 2.0234 | 3.065 | 3.6491 | 3.6491 | 4.0384 | 4.0384 | 2019-07-29 02:00 | 1.227 | 2.1055 | 3.5587 | 3.5587 | 3.5587 | 3.5587
2021-05-31 14:00 | 2.3063 | 2.856 | 2.9015 | 3.0964 | 3.0185 | 3.2134 | 1.977 | 2.9948 | 3.5654 | 3.5654 | 3.9459 | 3.9459 | 2019-07-29 03:00 | 1.1736 | 2.014 | 3.4039 | 3.4039 | 3.4039 | 3.4039
2021-05-31 15:00 | 2.4378 | 3.0188 | 3.0669 | 3.2729 | 3.1905 | 3.3966 | 2.0548 | 3.1126 | 3.7058 | 3.7058 | 4.1012 | 4.1012 | 2019-07-29 04:00 | 1.2117 | 2.0794 | 3.5144 | 3.5144 | 3.5144 | 3.5144
2021-05-31 16:00 | 3.0052 | 3.7215 | 3.7808 | 4.0348 | 3.9332 | 4.1872 | 2.1348 | 3.2339 | 3.8501 | 3.8501 | 4.2609 | 4.2609 | 2019-07-29 05:00 | 1.4404 | 2.4717 | 4.1776 | 4.1776 | 4.1776 | 4.1776
2021-05-31 17:00 | 3.4956 | 4.3288 | 4.3977 | 4.6932 | 4.575 | 4.8705 | 2.5835 | 3.9135 | 4.6593 | 4.6593 | 5.1564 | 5.1564 | 2019-07-29 06:00 | 1.6385 | 2.8117 | 4.7522 | 4.7522 | 4.7522 | 4.7522
2021-05-31 18:00 | 3.6152 | 4.4769 | 4.5482 | 4.8538 | 4.7315 | 5.0371 | 2.6721 | 4.0477 | 4.8191 | 4.8191 | 5.3333 | 5.3333 | 2019-07-29 07:00 | 2.0729 | 3.5571 | 6.0121 | 6.0121 | 6.0121 | 6.0121
2021-05-31 19:00 | 3.5695 | 4.4202 | 4.4907 | 4.7924 | 4.6717 | 4.9734 | 2.595 | 3.9309 | 4.6799 | 4.6799 | 5.1793 | 5.1793 | 2019-07-29 08:00 | 2.2787 | 3.9102 | 6.6089 | 6.6089 | 6.6089 | 6.6089
2021-05-31 20:00 | 3.4037 | 4.215 | 4.2821 | 4.5698 | 4.4548 | 4.7425 | 2.4492 | 3.7101 | 4.417 | 4.417 | 4.8883 | 4.8883 | 2019-07-29 09:00 | 2.1491 | 3.6879 | 6.2332 | 6.2332 | 6.2332 | 6.2332
2021-05-31 21:00 | 3.0526 | 3.7802 | 3.8404 | 4.0984 | 3.9952 | 4.2533 | 2.3206 | 3.5153 | 4.1851 | 4.1851 | 4.6317 | 4.6317 | 2019-07-29 10:00 | 2.1186 | 3.6356 | 6.1448 | 6.1448 | 6.1448 | 6.1448
2021-05-31 22:00 | 2.6321 | 3.2594 | 3.3114 | 3.5339 | 3.4449 | 3.6674 | 1.9805 | 3.0001 | 3.5718 | 3.5718 | 3.9529 | 3.9529 | 2019-07-29 11:00 | 2.1263 | 3.6487 | 6.1669 | 6.1669 | 6.1669 | 6.1669
2021-05-31 23:00 | 2.4406 | 3.0223 | 3.0705 | 3.2768 | 3.1943 | 3.4006 | 1.6663 | 2.5241 | 3.005 | 3.005 | 3.3257 | 3.3257 | 2019-07-29 12:00 | 2.1415 | 3.6748 | 6.2111 | 6.2111 | 6.2111 | 6.2111
2021-06-01 | 2.1034 | 2.6047 | 2.6462 | 2.824 | 2.7529 | 2.9307 | 1.4489 | 2.1949 | 2.6131 | 2.6131 | 2.8919 | 2.8919 | 2019-07-29 13:00 | 2.3092 | 3.9625 | 6.6974 | 6.6974 | 6.6974 | 6.6974
2021-06-01 01:00 | 2.0834 | 2.58 | 2.621 | 2.7972 | 2.7267 | 2.9028 | 1.2633 | 1.9137 | 2.2783 | 2.2783 | 2.5214 | 2.5214 | 2019-07-29 14:00 | 2.1949 | 3.7664 | 6.3658 | 6.3658 | 6.3658 | 6.3658
2021-06-01 02:00 | 2.0062 | 2.4844 | 2.524 | 2.6936 | 2.6257 | 2.7953 | 1.2489 | 1.8919 | 2.2524 | 2.2524 | 2.4927 | 2.4927 | 2019-07-29 15:00 | 2.1567 | 3.701 | 6.2553 | 6.2553 | 6.2553 | 6.2553
2021-06-01 03:00 | 1.9691 | 2.4384 | 2.4772 | 2.6437 | 2.5771 | 2.7436 | 1.2517 | 1.8962 | 2.2575 | 2.2575 | 2.4984 | 2.4984 | 2019-07-29 16:00 | 2.1339 | 3.6618 | 6.189 | 6.189 | 6.189 | 6.189
2021-06-01 04:00 | 2.1606 | 2.6755 | 2.7181 | 2.9008 | 2.8277 | 3.0103 | 1.226 | 1.8572 | 2.2111 | 2.2111 | 2.447 | 2.447 | 2019-07-29 17:00 | 2.3168 | 3.9756 | 6.7195 | 6.7195 | 6.7195 | 6.7195
2021-06-01 05:00 | 2.6235 | 3.2488 | 3.3006 | 3.5224 | 3.4336 | 3.6554 | 1.4658 | 2.2204 | 2.6435 | 2.6435 | 2.9256 | 2.9256 | 2019-07-29 18:00 | 2.3015 | 3.9495 | 6.6753 | 6.6753 | 6.6753 | 6.6753
2021-06-01 06:00 | 3.8767 | 4.8007 | 4.8772 | 5.2049 | 5.0738 | 5.4015 | 1.8719 | 2.8356 | 3.3759 | 3.3759 | 3.7361 | 3.7361 | 2019-07-29 19:00 | 2.1491 | 3.6879 | 6.2332 | 6.2332 | 6.2332 | 6.2332
2021-06-01 07:00 | 4.5355 | 5.6164 | 5.7059 | 6.0893 | 5.9359 | 6.3193 | 2.3177 | 3.5109 | 4.1799 | 4.1799 | 4.626 | 4.626 | 2019-07-29 20:00 | 1.9357 | 3.3217 | 5.6143 | 5.6143 | 5.6143 | 5.6143
2021-06-01 08:00 | 4.4269 | 5.482 | 5.5693 | 5.9435 | 5.7938 | 6.168 | 2.232 | 3.3811 | 4.0253 | 4.0253 | 4.4548 | 4.4548 | 2019-07-29 21:00 | 1.8519 | 3.1779 | 5.3711 | 5.3711 | 5.3711 | 5.3711
2021-06-01 09:00 | 4.1725 | 5.167 | 5.2493 | 5.602 | 5.4609 | 5.8136 | 2.072 | 3.1386 | 3.7367 | 3.7367 | 4.1354 | 4.1354 | 2019-07-29 22:00 | 1.6842 | 2.8902 | 4.8849 | 4.8849 | 4.8849 | 4.8849
2021-06-01 10:00 | 3.9696 | 4.9157 | 4.994 | 5.3296 | 5.1953 | 5.5309 | 1.9891 | 3.0131 | 3.5872 | 3.5872 | 3.97 | 3.97 | 2019-07-29 23:00 | 1.3718 | 2.354 | 3.9786 | 3.9786 | 3.9786 | 3.9786
2021-06-01 11:00 | 3.6924 | 4.5724 | 4.6453 | 4.9574 | 4.8325 | 5.1447 | 1.9091 | 2.8919 | 3.4429 | 3.4429 | 3.8103 | 3.8103 | 2019-07-30 | 1.2803 | 2.1971 | 3.7134 | 3.7134 | 3.7134 | 3.7134
2021-06-01 12:00 | 3.5038 | 4.3389 | 4.408 | 4.7041 | 4.5857 | 4.8819 | 1.8148 | 2.749 | 3.2728 | 3.2728 | 3.6221 | 3.6221 | 2019-07-30 01:00 | 1.1965 | 2.0532 | 3.4702 | 3.4702 | 3.4702 | 3.4702
2021-06-01 13:00 | 3.4009 | 4.2114 | 4.2785 | 4.566 | 4.451 | 4.7385 | 1.8405 | 2.788 | 3.3192 | 3.3192 | 3.6734 | 3.6734 | 2019-07-30 02:00 | 1.1508 | 1.9747 | 3.3376 | 3.3376 | 3.3376 | 3.3376
2021-06-01 14:00 | 3.3266 | 4.1194 | 4.185 | 4.4662 | 4.3538 | 4.635 | 1.9091 | 2.8919 | 3.4429 | 3.4429 | 3.8103 | 3.8103 | 2019-07-30 03:00 | 1.1508 | 1.9747 | 3.3376 | 3.3376 | 3.3376 | 3.3376
2021-06-01 15:00 | 3.3552 | 4.1548 | 4.221 | 4.5046 | 4.3912 | 4.6748 | 1.9548 | 2.9611 | 3.5254 | 3.5254 | 3.9015 | 3.9015 | 2019-07-30 04:00 | 1.1889 | 2.0401 | 3.4481 | 3.4481 | 3.4481 | 3.4481
2021-06-01 16:00 | 3.5209 | 4.3601 | 4.4295 | 4.7272 | 4.6081 | 4.9057 | 2.1863 | 3.3118 | 3.9429 | 3.9429 | 4.3636 | 4.3636 | 2019-07-30 05:00 | 1.4251 | 2.4455 | 4.1333 | 4.1333 | 4.1333 | 4.1333
2021-06-01 17:00 | 4.2068 | 5.2095 | 5.2924 | 5.648 | 5.5058 | 5.8614 | 2.5235 | 3.8226 | 4.551 | 4.551 | 5.0366 | 5.0366 | 2019-07-30 06:00 | 1.8367 | 3.1517 | 5.3269 | 5.3269 | 5.3269 | 5.3269
2021-06-01 18:00 | 4.2039 | 5.2059 | 5.2888 | 5.6442 | 5.5021 | 5.8574 | 2.6493 | 4.0131 | 4.7778 | 4.7778 | 5.2876 | 5.2876 | 2019-07-30 07:00 | 2.1034 | 3.6094 | 6.1006 | 6.1006 | 6.1006 | 6.1006
2021-06-01 19:00 | 3.9582 | 4.9016 | 4.9796 | 5.3142 | 5.1804 | 5.515 | 2.6178 | 3.9655 | 4.7211 | 4.7211 | 5.2249 | 5.2249 | 2019-07-30 08:00 | 2.1644 | 3.7141 | 6.2774 | 6.2774 | 6.2774 | 6.2774
2021-06-01 20:00 | 3.5666 | 4.4167 | 4.4871 | 4.7886 | 4.668 | 4.9695 | 2.5206 | 3.8183 | 4.5459 | 4.5459 | 5.0309 | 5.0309 | 2019-07-30 09:00 | 2.1644 | 3.7141 | 6.2774 | 6.2774 | 6.2774 | 6.2774
2021-06-01 21:00 | 3.2265 | 3.9956 | 4.0592 | 4.332 | 4.2229 | 4.4956 | 2.3006 | 3.485 | 4.149 | 4.149 | 4.5917 | 4.5917 | 2019-07-30 10:00 | 2.1339 | 3.6618 | 6.189 | 6.189 | 6.189 | 6.189
2021-06-01 22:00 | 2.7036 | 3.3479 | 3.4012 | 3.6298 | 3.5384 | 3.7669 | 2.0262 | 3.0694 | 3.6542 | 3.6542 | 4.0441 | 4.0441 | 2019-07-30 11:00 | 2.0653 | 3.5441 | 5.99 | 5.99 | 5.99 | 5.99
2021-06-01 23:00 | 2.3749 | 2.9409 | 2.9878 | 3.1885 | 3.1082 | 3.309 | 1.7119 | 2.5932 | 3.0873 | 3.0873 | 3.4167 | 3.4167 | 2019-07-30 12:00 | 2.1263 | 3.6487 | 6.1669 | 6.1669 | 6.1669 | 6.1669
2021-06-02 | 2.0551 | 2.545 | 2.5855 | 2.7592 | 2.6897 | 2.8635 | 1.3632 | 2.065 | 2.4585 | 2.4585 | 2.7208 | 2.7208 | 2019-07-30 13:00 | 2.1415 | 3.6748 | 6.2111 | 6.2111 | 6.2111 | 6.2111
2021-06-02 01:00 | 1.8691 | 2.3145 | 2.3514 | 2.5094 | 2.4462 | 2.6042 | 1.2146 | 1.8399 | 2.1905 | 2.1905 | 2.4242 | 2.4242 | 2019-07-30 14:00 | 2.0882 | 3.5833 | 6.0564 | 6.0564 | 6.0564 | 6.0564
2021-06-02 02:00 | 1.7862 | 2.2119 | 2.2471 | 2.3981 | 2.3377 | 2.4887 | 1.1117 | 1.684 | 2.0049 | 2.0049 | 2.2189 | 2.2189 | 2019-07-30 15:00 | 2.0653 | 3.5441 | 5.99 | 5.99 | 5.99 | 5.99
2021-06-02 03:00 | 1.8462 | 2.2862 | 2.3226 | 2.4787 | 2.4163 | 2.5723 | 1.1574 | 1.7533 | 2.0874 | 2.0874 | 2.3101 | 2.3101 | 2019-07-30 16:00 | 2.0958 | 3.5964 | 6.0785 | 6.0785 | 6.0785 | 6.0785
2021-06-02 04:00 | 1.989 | 2.4631 | 2.5023 | 2.6704 | 2.6032 | 2.7713 | 1.1563 | 1.7515 | 2.0853 | 2.0853 | 2.3078 | 2.3078 | 2019-07-30 17:00 | 2.2558 | 3.871 | 6.5426 | 6.5426 | 6.5426 | 6.5426
2021-06-02 05:00 | 2.3262 | 2.8807 | 2.9265 | 3.1232 | 3.0445 | 3.2412 | 1.3599 | 2.0599 | 2.4524 | 2.4524 | 2.7141 | 2.7141 | 2019-07-30 18:00 | 2.2101 | 3.7925 | 6.41 | 6.41 | 6.41 | 6.41
2021-06-02 06:00 | 3.2494 | 4.0239 | 4.088 | 4.3627 | 4.2528 | 4.5275 | 1.5947 | 2.4157 | 2.876 | 2.876 | 3.1828 | 3.1828 | 2019-07-30 19:00 | 2.1949 | 3.7664 | 6.3658 | 6.3658 | 6.3658 | 6.3658
2021-06-02 07:00 | 3.9867 | 4.9369 | 5.0156 | 5.3526 | 5.2178 | 5.5548 | 1.8833 | 2.8529 | 3.3965 | 3.3965 | 3.7589 | 3.7589 | 2019-07-30 20:00 | 1.9815 | 3.4002 | 5.7469 | 5.7469 | 5.7469 | 5.7469
2021-06-02 08:00 | 3.7095 | 4.5937 | 4.6668 | 4.9804 | 4.855 | 5.1686 | 1.9519 | 2.9568 | 3.5202 | 3.5202 | 3.8958 | 3.8958 | 2019-07-30 21:00 | 1.9053 | 3.2694 | 5.5259 | 5.5259 | 5.5259 | 5.5259
2021-06-02 09:00 | 3.4466 | 4.2681 | 4.3361 | 4.6274 | 4.5109 | 4.8022 | 1.8576 | 2.8139 | 3.3501 | 3.3501 | 3.7076 | 3.7076 | 2019-07-30 22:00 | 1.6766 | 2.8771 | 4.8628 | 4.8628 | 4.8628 | 4.8628
2021-06-02 10:00 | 3.1351 | 3.8823 | 3.9442 | 4.2092 | 4.1032 | 4.3682 | 1.7404 | 2.6364 | 3.1388 | 3.1388 | 3.4737 | 3.4737 | 2019-07-30 23:00 | 1.4251 | 2.4455 | 4.1333 | 4.1333 | 4.1333 | 4.1333
2021-06-02 11:00 | 2.8122 | 3.4824 | 3.5379 | 3.7756 | 3.6805 | 3.9182 | 1.6804 | 2.5455 | 3.0306 | 3.0306 | 3.354 | 3.354 | 2019-07-31 | 1.3032 | 2.2363 | 3.7797 | 3.7797 | 3.7797 | 3.7797
2021-06-02 12:00 | 2.7036 | 3.3479 | 3.4012 | 3.6298 | 3.5384 | 3.7669 | 1.789 | 2.71 | 3.2264 | 3.2264 | 3.5707 | 3.5707 | 2019-07-31 01:00 | 1.1965 | 2.0532 | 3.4702 | 3.4702 | 3.4702 | 3.4702
2021-06-02 13:00 | 2.6007 | 3.2205 | 3.2718 | 3.4917 | 3.4037 | 3.6236 | 1.6833 | 2.5499 | 3.0357 | 3.0357 | 3.3597 | 3.3597 | 2019-07-31 02:00 | 1.1813 | 2.027 | 3.426 | 3.426 | 3.426 | 3.426
2021-06-02 14:00 | 2.5321 | 3.1356 | 3.1855 | 3.3996 | 3.3139 | 3.528 | 1.6661 | 2.5239 | 3.0048 | 3.0048 | 3.3254 | 3.3254 | 2019-07-31 03:00 | 1.1813 | 2.027 | 3.426 | 3.426 | 3.426 | 3.426
2021-06-02 15:00 | 2.6521 | 3.2842 | 3.3365 | 3.5607 | 3.471 | 3.6952 | 1.6204 | 2.4546 | 2.9224 | 2.9224 | 3.2342 | 3.2342 | 2019-07-31 04:00 | 1.2575 | 2.1578 | 3.6471 | 3.6471 | 3.6471 | 3.6471
2021-06-02 16:00 | 3.0799 | 3.814 | 3.8748 | 4.1351 | 4.031 | 4.2913 | 1.9285 | 2.9214 | 3.478 | 3.478 | 3.8491 | 3.8491 | 2019-07-31 05:00 | 1.509 | 2.5894 | 4.3765 | 4.3765 | 4.3765 | 4.3765
2021-06-02 17:00 | 3.5838 | 4.4379 | 4.5086 | 4.8116 | 4.6904 | 4.9933 | 2.2177 | 3.3594 | 3.9996 | 3.9996 | 4.4263 | 4.4263 | 2019-07-31 06:00 | 1.8062 | 3.0994 | 5.2385 | 5.2385 | 5.2385 | 5.2385
2021-06-02 18:00 | 3.7136 | 4.5987 | 4.672 | 4.9859 | 4.8603 | 5.1742 | 2.3692 | 3.5889 | 4.2727 | 4.2727 | 4.7286 | 4.7286 | 2019-07-31 07:00 | 2.111 | 3.6225 | 6.1227 | 6.1227 | 6.1227 | 6.1227
2021-06-02 19:00 | 3.7181 | 4.6043 | 4.6776 | 4.9919 | 4.8662 | 5.1805 | 2.4778 | 3.7534 | 4.4686 | 4.4686 | 4.9454 | 4.9454 | 2019-07-31 08:00 | 2.1949 | 3.7664 | 6.3658 | 6.3658 | 6.3658 | 6.3658
2021-06-02 20:00 | 3.318 | 4.1088 | 4.1743 | 4.4547 | 4.3425 | 4.623 | 2.4263 | 3.6754 | 4.3758 | 4.3758 | 4.8427 | 4.8427 | 2019-07-31 09:00 | 2.0501 | 3.5179 | 5.9458 | 5.9458 | 5.9458 | 5.9458
2021-06-02 21:00 | 2.893 | 3.5825 | 3.6395 | 3.8841 | 3.7863 | 4.0308 | 2.1891 | 3.3161 | 3.948 | 3.948 | 4.3693 | 4.3693 | 2019-07-31 10:00 | 2.0653 | 3.5441 | 5.99 | 5.99 | 5.99 | 5.99
2021-06-02 22:00 | 2.5892 | 3.2064 | 3.2574 | 3.4763 | 3.3888 | 3.6076 | 1.809 | 2.7403 | 3.2625 | 3.2625 | 3.6106 | 3.6106 | 2019-07-31 11:00 | 2.1034 | 3.6094 | 6.1006 | 6.1006 | 6.1006 | 6.1006
2021-06-02 23:00 | 2.1733 | 2.6913 | 2.7342 | 2.9179 | 2.8444 | 3.0282 | 1.6176 | 2.4503 | 2.9172 | 2.9172 | 3.2285 | 3.2285 | 2019-07-31 12:00 | 2.0043 | 3.4394 | 5.8132 | 5.8132 | 5.8132 | 5.8132
2021-06-03 | 1.8836 | 2.3326 | 2.3697 | 2.529 | 2.4653 | 2.6245 | 1.2645 | 1.9155 | 2.2805 | 2.2805 | 2.5238 | 2.5238 | 2019-07-31 13:00 | 1.9967 | 3.4264 | 5.7911 | 5.7911 | 5.7911 | 5.7911
2021-06-03 01:00 | 1.8176 | 2.2508 | 2.2867 | 2.4403 | 2.3789 | 2.5325 | 1.1552 | 1.75 | 2.0834 | 2.0834 | 2.3057 | 2.3057 | 2019-07-31 14:00 | 1.9662 | 3.374 | 5.7027 | 5.7027 | 5.7027 | 5.7027
2021-06-03 02:00 | 1.7433 | 2.1588 | 2.1932 | 2.3406 | 2.2816 | 2.429 | 1.0436 | 1.5809 | 1.8821 | 1.8821 | 2.083 | 2.083 | 2019-07-31 15:00 | 2.0043 | 3.4394 | 5.8132 | 5.8132 | 5.8132 | 5.8132
2021-06-03 03:00 | 1.7976 | 2.226 | 2.2615 | 2.4135 | 2.3527 | 2.5046 | 1.0631 | 1.6104 | 1.9173 | 1.9173 | 2.1219 | 2.1219 | 2019-07-31 16:00 | 2.0577 | 3.531 | 5.9679 | 5.9679 | 5.9679 | 5.9679
2021-06-03 04:00 | 1.8919 | 2.3428 | 2.3802 | 2.5401 | 2.4761 | 2.636 | 1.0946 | 1.6581 | 1.974 | 1.974 | 2.1846 | 2.1846 | 2019-07-31 17:00 | 2.1034 | 3.6094 | 6.1006 | 6.1006 | 6.1006 | 6.1006
2021-06-03 05:00 | 2.2049 | 2.7305 | 2.7739 | 2.9603 | 2.8858 | 3.0722 | 1.2271 | 1.8588 | 2.213 | 2.213 | 2.4491 | 2.4491 | 2019-07-31 18:00 | 2.1034 | 3.6094 | 6.1006 | 6.1006 | 6.1006 | 6.1006
2021-06-03 06:00 | 3.0279 | 3.7496 | 3.8093 | 4.0652 | 3.9629 | 4.2188 | 1.452 | 2.1995 | 2.6186 | 2.6186 | 2.898 | 2.898 | 2019-07-31 19:00 | 1.9434 | 3.3348 | 5.6364 | 5.6364 | 5.6364 | 5.6364
2021-06-03 07:00 | 3.5066 | 4.3424 | 4.4116 | 4.708 | 4.5894 | 4.8858 | 1.8605 | 2.8183 | 3.3553 | 3.3553 | 3.7133 | 3.7133 | 2019-07-31 20:00 | 1.8443 | 3.1648 | 5.349 | 5.349 | 5.349 | 5.349
2021-06-03 08:00 | 3.6181 | 4.4804 | 4.5518 | 4.8576 | 4.7353 | 5.0411 | 1.9777 | 2.9958 | 3.5666 | 3.5666 | 3.9472 | 3.9472 | 2019-07-31 21:00 | 1.7681 | 3.034 | 5.128 | 5.128 | 5.128 | 5.128
2021-06-03 09:00 | 3.6152 | 4.4769 | 4.5482 | 4.8538 | 4.7315 | 5.0371 | 1.8948 | 2.8702 | 3.4171 | 3.4171 | 3.7818 | 3.7818 | 2019-07-31 22:00 | 1.5471 | 2.6548 | 4.487 | 4.487 | 4.487 | 4.487
2021-06-03 10:00 | 3.5895 | 4.445 | 4.5158 | 4.8193 | 4.6979 | 5.0013 | 2.0434 | 3.0953 | 3.6852 | 3.6852 | 4.0784 | 4.0784 | 2019-07-31 23:00 | 1.4251 | 2.4455 | 4.1333 | 4.1333 | 4.1333 | 4.1333
2021-06-03 11:00 | 3.6152 | 4.4769 | 4.5482 | 4.8538 | 4.7315 | 5.0371 | 2.0234 | 3.065 | 3.6491 | 3.6491 | 4.0384 | 4.0384 | 2019-08-01 | 1.3489 | 2.3148 | 3.9123 | 3.9123 | 3.9123 | 3.9123
2021-06-03 12:00 | 3.5981 | 4.4556 | 4.5266 | 4.8308 | 4.7091 | 5.0133 | 2.1005 | 3.1819 | 3.7882 | 3.7882 | 4.1925 | 4.1925 | 2019-08-01 01:00 | 1.227 | 2.1055 | 3.5587 | 3.5587 | 3.5587 | 3.5587
2021-06-03 13:00 | 3.5009 | 4.3353 | 4.4044 | 4.7003 | 4.5819 | 4.8779 | 1.9862 | 3.0087 | 3.5821 | 3.5821 | 3.9643 | 3.9643 | 2019-08-01 02:00 | 1.1736 | 2.014 | 3.4039 | 3.4039 | 3.4039 | 3.4039
2021-06-03 14:00 | 3.3552 | 4.1548 | 4.221 | 4.5046 | 4.3912 | 4.6748 | 1.9062 | 2.8875 | 3.4378 | 3.4378 | 3.8046 | 3.8046 | 2019-08-01 03:00 | 1.1736 | 2.014 | 3.4039 | 3.4039 | 3.4039 | 3.4039
2021-06-03 15:00 | 3.2323 | 4.0026 | 4.0664 | 4.3396 | 4.2303 | 4.5036 | 1.8433 | 2.7923 | 3.3244 | 3.3244 | 3.6791 | 3.6791 | 2019-08-01 04:00 | 1.2498 | 2.1447 | 3.625 | 3.625 | 3.625 | 3.625
2021-06-03 16:00 | 3.4095 | 4.2221 | 4.2893 | 4.5775 | 4.4622 | 4.7504 | 1.9977 | 3.0261 | 3.6027 | 3.6027 | 3.9871 | 3.9871 | 2019-08-01 05:00 | 1.4709 | 2.524 | 4.266 | 4.266 | 4.266 | 4.266
2021-06-03 17:00 | 3.7924 | 4.6963 | 4.7711 | 5.0917 | 4.9634 | 5.284 | 2.2977 | 3.4806 | 4.1439 | 4.1439 | 4.586 | 4.586 | 2019-08-01 06:00 | 1.8214 | 3.1256 | 5.2827 | 5.2827 | 5.2827 | 5.2827
2021-06-03 18:00 | 3.8438 | 4.76 | 4.8358 | 5.1607 | 5.0308 | 5.3557 | 2.4035 | 3.6408 | 4.3346 | 4.3346 | 4.7971 | 4.7971 | 2019-08-01 07:00 | 2.2253 | 3.8187 | 6.4542 | 6.4542 | 6.4542 | 6.4542
2021-06-03 19:00 | 3.7817 | 4.683 | 4.7576 | 5.0773 | 4.9494 | 5.2691 | 2.4006 | 3.6365 | 4.3294 | 4.3294 | 4.7914 | 4.7914 | 2019-08-01 08:00 | 2.233 | 3.8318 | 6.4763 | 6.4763 | 6.4763 | 6.4763
2021-06-03 20:00 | 3.3752 | 4.1796 | 4.2462 | 4.5315 | 4.4174 | 4.7027 | 2.3349 | 3.5369 | 4.2109 | 4.2109 | 4.6602 | 4.6602 | 2019-08-01 09:00 | 2.0805 | 3.5702 | 6.0343 | 6.0343 | 6.0343 | 6.0343
2021-06-03 21:00 | 3.0697 | 3.8014 | 3.8619 | 4.1214 | 4.0176 | 4.2771 | 2.2263 | 3.3724 | 4.015 | 4.015 | 4.4434 | 4.4434 | 2019-08-01 10:00 | 2.0958 | 3.5964 | 6.0785 | 6.0785 | 6.0785 | 6.0785
2021-06-03 22:00 | 2.5549 | 3.1639 | 3.2143 | 3.4303 | 3.3439 | 3.5598 | 1.9748 | 2.9914 | 3.5615 | 3.5615 | 3.9415 | 3.9415 | 2019-08-01 11:00 | 2.1872 | 3.7533 | 6.3437 | 6.3437 | 6.3437 | 6.3437
2021-06-03 23:00 | 2.2614 | 2.8004 | 2.845 | 3.0361 | 2.9597 | 3.1508 | 1.5978 | 2.4204 | 2.8816 | 2.8816 | 3.189 | 3.189 | 2019-08-01 12:00 | 2.0577 | 3.531 | 5.9679 | 5.9679 | 5.9679 | 5.9679
2021-06-04 | 1.9977 | 2.4738 | 2.5132 | 2.682 | 2.6145 | 2.7834 | 1.3089 | 1.9827 | 2.3606 | 2.3606 | 2.6124 | 2.6124 | 2019-08-01 13:00 | 2.0729 | 3.5571 | 6.0121 | 6.0121 | 6.0121 | 6.0121
2021-06-04 01:00 | 1.8906 | 2.3412 | 2.3785 | 2.5383 | 2.4744 | 2.6342 | 1.1746 | 1.7793 | 2.1183 | 2.1183 | 2.3443 | 2.3443 | 2019-08-01 14:00 | 2.0729 | 3.5571 | 6.0121 | 6.0121 | 6.0121 | 6.0121
2021-06-04 02:00 | 1.8862 | 2.3358 | 2.373 | 2.5324 | 2.4686 | 2.6281 | 1.0888 | 1.6494 | 1.9637 | 1.9637 | 2.1732 | 2.1732 | 2019-08-01 15:00 | 2.0119 | 3.4525 | 5.8353 | 5.8353 | 5.8353 | 5.8353
2021-06-04 03:00 | 1.8746 | 2.3214 | 2.3583 | 2.5168 | 2.4534 | 2.6119 | 1.0863 | 1.6455 | 1.959 | 1.959 | 2.168 | 2.168 | 2019-08-01 16:00 | 2.0729 | 3.5571 | 6.0121 | 6.0121 | 6.0121 | 6.0121
2021-06-04 04:00 | 2.0262 | 2.5092 | 2.5491 | 2.7204 | 2.6519 | 2.8232 | 1.0974 | 1.6624 | 1.9792 | 1.9792 | 2.1903 | 2.1903 | 2019-08-01 17:00 | 2.1186 | 3.6356 | 6.1448 | 6.1448 | 6.1448 | 6.1448
2021-06-04 05:00 | 2.3744 | 2.9403 | 2.9871 | 3.1878 | 3.1075 | 3.3082 | 1.226 | 1.8572 | 2.2111 | 2.2111 | 2.447 | 2.447 | 2019-08-01 18:00 | 2.1186 | 3.6356 | 6.1448 | 6.1448 | 6.1448 | 6.1448
2021-06-04 06:00 | 3.1865 | 3.946 | 4.0089 | 4.2782 | 4.1705 | 4.4399 | 1.5232 | 2.3074 | 2.7471 | 2.7471 | 3.0402 | 3.0402 | 2019-08-01 19:00 | 1.9815 | 3.4002 | 5.7469 | 5.7469 | 5.7469 | 5.7469
2021-06-04 07:00 | 3.6352 | 4.5016 | 4.5733 | 4.8806 | 4.7577 | 5.065 | 1.9205 | 2.9092 | 3.4635 | 3.4635 | 3.8331 | 3.8331 | 2019-08-01 20:00 | 1.9815 | 3.4002 | 5.7469 | 5.7469 | 5.7469 | 5.7469
2021-06-04 08:00 | 3.7781 | 4.6786 | 4.7531 | 5.0725 | 4.9447 | 5.2641 | 1.8748 | 2.8399 | 3.3811 | 3.3811 | 3.7418 | 3.7418 | 2019-08-01 21:00 | 1.7605 | 3.0209 | 5.1059 | 5.1059 | 5.1059 | 5.1059
2021-06-04 09:00 | 3.5552 | 4.4026 | 4.4727 | 4.7732 | 4.653 | 4.9535 | 1.7605 | 2.6667 | 3.1749 | 3.1749 | 3.5137 | 3.5137 | 2019-08-01 22:00 | 1.509 | 2.5894 | 4.3765 | 4.3765 | 4.3765 | 4.3765
2021-06-04 10:00 | 3.5695 | 4.4202 | 4.4907 | 4.7924 | 4.6717 | 4.9734 | 1.8833 | 2.8529 | 3.3965 | 3.3965 | 3.7589 | 3.7589 | 2019-08-01 23:00 | 1.4556 | 2.4978 | 4.2218 | 4.2218 | 4.2218 | 4.2218
2021-06-04 11:00 | 3.5866 | 4.4415 | 4.5122 | 4.8154 | 4.6941 | 4.9973 | 1.9434 | 2.9438 | 3.5048 | 3.5048 | 3.8787 | 3.8787 | 2019-08-02 | 1.227 | 2.1055 | 3.5587 | 3.5587 | 3.5587 | 3.5587
2021-06-04 12:00 | 3.4009 | 4.2114 | 4.2785 | 4.566 | 4.451 | 4.7385 | 1.8891 | 2.8616 | 3.4068 | 3.4068 | 3.7704 | 3.7704 | 2019-08-02 01:00 | 1.1813 | 2.027 | 3.426 | 3.426 | 3.426 | 3.426
2021-06-04 13:00 | 3.2151 | 3.9814 | 4.0448 | 4.3166 | 4.2079 | 4.4797 | 1.8633 | 2.8226 | 3.3604 | 3.3604 | 3.719 | 3.719 | 2019-08-02 02:00 | 1.1355 | 1.9486 | 3.2934 | 3.2934 | 3.2934 | 3.2934
2021-06-04 14:00 | 3.0979 | 3.8363 | 3.8974 | 4.1593 | 4.0545 | 4.3164 | 1.8233 | 2.762 | 3.2883 | 3.2883 | 3.6392 | 3.6392 | 2019-08-02 03:00 | 1.1508 | 1.9747 | 3.3376 | 3.3376 | 3.3376 | 3.3376
2021-06-04 15:00 | 2.9493 | 3.6523 | 3.7105 | 3.9598 | 3.86 | 4.1094 | 1.8348 | 2.7793 | 3.3089 | 3.3089 | 3.662 | 3.662 | 2019-08-02 04:00 | 1.2346 | 2.1186 | 3.5808 | 3.5808 | 3.5808 | 3.5808
2021-06-04 16:00 | 3.1951 | 3.9566 | 4.0197 | 4.2897 | 4.1817 | 4.4518 | 1.9862 | 3.0087 | 3.5821 | 3.5821 | 3.9643 | 3.9643 | 2019-08-02 05:00 | 1.4861 | 2.5501 | 4.3102 | 4.3102 | 4.3102 | 4.3102
2021-06-04 17:00 | 3.498 | 4.3318 | 4.4008 | 4.6965 | 4.5782 | 4.8739 | 2.4035 | 3.6408 | 4.3346 | 4.3346 | 4.7971 | 4.7971 | 2019-08-02 06:00 | 1.7681 | 3.034 | 5.128 | 5.128 | 5.128 | 5.128
2021-06-04 18:00 | 3.5295 | 4.3707 | 4.4403 | 4.7387 | 4.6193 | 4.9177 | 2.4235 | 3.6711 | 4.3706 | 4.3706 | 4.837 | 4.837 | 2019-08-02 07:00 | 1.9815 | 3.4002 | 5.7469 | 5.7469 | 5.7469 | 5.7469
2021-06-04 19:00 | 3.4009 | 4.2114 | 4.2785 | 4.566 | 4.451 | 4.7385 | 2.4721 | 3.7447 | 4.4583 | 4.4583 | 4.934 | 4.934 | 2019-08-02 08:00 | 2.1644 | 3.7141 | 6.2774 | 6.2774 | 6.2774 | 6.2774
2021-06-04 20:00 | 3.1008 | 3.8398 | 3.901 | 4.1631 | 4.0583 | 4.3204 | 2.4521 | 3.7144 | 4.4222 | 4.4222 | 4.894 | 4.894 | 2019-08-02 09:00 | 2.0882 | 3.5833 | 6.0564 | 6.0564 | 6.0564 | 6.0564
2021-06-04 21:00 | 2.8639 | 3.5464 | 3.6029 | 3.845 | 3.7482 | 3.9903 | 2.3778 | 3.6018 | 4.2882 | 4.2882 | 4.7457 | 4.7457 | 2019-08-02 10:00 | 2.0882 | 3.5833 | 6.0564 | 6.0564 | 6.0564 | 6.0564
2021-06-04 22:00 | 2.5807 | 3.1957 | 3.2466 | 3.4648 | 3.3775 | 3.5957 | 2.1891 | 3.3161 | 3.948 | 3.948 | 4.3693 | 4.3693 | 2019-08-02 11:00 | 2.0729 | 3.5571 | 6.0121 | 6.0121 | 6.0121 | 6.0121
2021-06-04 23:00 | 2.5321 | 3.1356 | 3.1855 | 3.3996 | 3.3139 | 3.528 | 1.8033 | 2.7317 | 3.2522 | 3.2522 | 3.5992 | 3.5992 | 2019-08-02 12:00 | 2.0577 | 3.531 | 5.9679 | 5.9679 | 5.9679 | 5.9679
2021-06-05 | 2.1777 | 2.6967 | 2.7397 | 2.9238 | 2.8501 | 3.0342 | 1.4347 | 2.1732 | 2.5873 | 2.5873 | 2.8634 | 2.8634 | 2019-08-02 13:00 | 2.0424 | 3.5048 | 5.9237 | 5.9237 | 5.9237 | 5.9237
2021-06-05 01:00 | 2.0231 | 2.5052 | 2.5451 | 2.7162 | 2.6477 | 2.8188 | 1.2975 | 1.9654 | 2.3399 | 2.3399 | 2.5896 | 2.5896 | 2019-08-02 14:00 | 1.951 | 3.3479 | 5.6585 | 5.6585 | 5.6585 | 5.6585
2021-06-05 02:00 | 1.9748 | 2.4455 | 2.4844 | 2.6514 | 2.5846 | 2.7515 | 1.246 | 1.8875 | 2.2472 | 2.2472 | 2.4869 | 2.4869 | 2019-08-02 15:00 | 1.9662 | 3.374 | 5.7027 | 5.7027 | 5.7027 | 5.7027
2021-06-05 03:00 | 1.9519 | 2.4172 | 2.4557 | 2.6207 | 2.5547 | 2.7197 | 1.2203 | 1.8485 | 2.2008 | 2.2008 | 2.4356 | 2.4356 | 2019-08-02 16:00 | 2.0196 | 3.4656 | 5.8574 | 5.8574 | 5.8574 | 5.8574
2021-06-05 04:00 | 1.9977 | 2.4738 | 2.5132 | 2.682 | 2.6145 | 2.7834 | 1.2517 | 1.8962 | 2.2575 | 2.2575 | 2.4984 | 2.4984 | 2019-08-02 17:00 | 2.0729 | 3.5571 | 6.0121 | 6.0121 | 6.0121 | 6.0121
2021-06-05 05:00 | 2.1777 | 2.6967 | 2.7397 | 2.9238 | 2.8501 | 3.0342 | 1.2744 | 1.9305 | 2.2984 | 2.2984 | 2.5436 | 2.5436 | 2019-08-02 18:00 | 2.1491 | 3.6879 | 6.2332 | 6.2332 | 6.2332 | 6.2332
2021-06-05 06:00 | 2.4721 | 3.0613 | 3.11 | 3.319 | 3.2354 | 3.4444 | 1.5318 | 2.3204 | 2.7626 | 2.7626 | 3.0574 | 3.0574 | 2019-08-02 19:00 | 1.9281 | 3.3087 | 5.5922 | 5.5922 | 5.5922 | 5.5922
2021-06-05 07:00 | 3.158 | 3.9106 | 3.9729 | 4.2399 | 4.1331 | 4.4 | 1.8405 | 2.788 | 3.3192 | 3.3192 | 3.6734 | 3.6734 | 2019-08-02 20:00 | 1.7681 | 3.034 | 5.128 | 5.128 | 5.128 | 5.128
2021-06-05 08:00 | 3.2723 | 4.0522 | 4.1167 | 4.3933 | 4.2827 | 4.5593 | 2.0234 | 3.065 | 3.6491 | 3.6491 | 4.0384 | 4.0384 | 2019-08-02 21:00 | 1.7147 | 2.9425 | 4.9733 | 4.9733 | 4.9733 | 4.9733
2021-06-05 09:00 | 3.2037 | 3.9673 | 4.0304 | 4.3013 | 4.1929 | 4.4637 | 2.2063 | 3.3421 | 3.9789 | 3.9789 | 4.4035 | 4.4035 | 2019-08-02 22:00 | 1.6233 | 2.7855 | 4.708 | 4.708 | 4.708 | 4.708
2021-06-05 10:00 | 3.1037 | 3.8434 | 3.9046 | 4.167 | 4.062 | 4.3244 | 2.2892 | 3.4676 | 4.1284 | 4.1284 | 4.5689 | 4.5689 | 2019-08-02 23:00 | 1.448 | 2.4848 | 4.1997 | 4.1997 | 4.1997 | 4.1997
2021-06-05 11:00 | 2.7779 | 3.4399 | 3.4947 | 3.7295 | 3.6356 | 3.8704 | 2.152 | 3.2598 | 3.881 | 3.881 | 4.2951 | 4.2951 | 2019-08-03 | 1.3489 | 2.3148 | 3.9123 | 3.9123 | 3.9123 | 3.9123
2021-06-05 12:00 | 2.6378 | 3.2665 | 3.3186 | 3.5415 | 3.4523 | 3.6753 | 2.1148 | 3.2036 | 3.814 | 3.814 | 4.221 | 4.221 | 2019-08-03 01:00 | 1.227 | 2.1055 | 3.5587 | 3.5587 | 3.5587 | 3.5587
2021-06-05 13:00 | 2.5692 | 3.1816 | 3.2323 | 3.4494 | 3.3626 | 3.5798 | 2.0691 | 3.1343 | 3.7315 | 3.7315 | 4.1297 | 4.1297 | 2019-08-03 02:00 | 1.2117 | 2.0794 | 3.5144 | 3.5144 | 3.5144 | 3.5144
2021-06-05 14:00 | 2.5378 | 3.1427 | 3.1927 | 3.4072 | 3.3214 | 3.536 | 2.0491 | 3.104 | 3.6955 | 3.6955 | 4.0898 | 4.0898 | 2019-08-03 03:00 | 1.1889 | 2.0401 | 3.4481 | 3.4481 | 3.4481 | 3.4481
2021-06-05 15:00 | 2.7178 | 3.3656 | 3.4192 | 3.649 | 3.5571 | 3.7868 | 2.0948 | 3.1733 | 3.7779 | 3.7779 | 4.181 | 4.181 | 2019-08-03 04:00 | 1.2422 | 2.1317 | 3.6029 | 3.6029 | 3.6029 | 3.6029
2021-06-05 16:00 | 3.2494 | 4.0239 | 4.088 | 4.3627 | 4.2528 | 4.5275 | 2.4004 | 3.6362 | 4.329 | 4.329 | 4.791 | 4.791 | 2019-08-03 05:00 | 1.4785 | 2.5371 | 4.2881 | 4.2881 | 4.2881 | 4.2881
2021-06-05 17:00 | 3.6038 | 4.4627 | 4.5338 | 4.8384 | 4.7166 | 5.0212 | 2.6121 | 3.9568 | 4.7108 | 4.7108 | 5.2135 | 5.2135 | 2019-08-03 06:00 | 1.5623 | 2.6809 | 4.5312 | 4.5312 | 4.5312 | 4.5312
2021-06-05 18:00 | 3.4923 | 4.3247 | 4.3936 | 4.6888 | 4.5707 | 4.8659 | 2.6864 | 4.0694 | 4.8448 | 4.8448 | 5.3618 | 5.3618 | 2019-08-03 07:00 | 1.6842 | 2.8902 | 4.8849 | 4.8849 | 4.8849 | 4.8849
2021-06-05 19:00 | 3.3351 | 4.13 | 4.1958 | 4.4778 | 4.365 | 4.6469 | 2.6035 | 3.9438 | 4.6954 | 4.6954 | 5.1964 | 5.1964 | 2019-08-03 08:00 | 1.8748 | 3.2171 | 5.4375 | 5.4375 | 5.4375 | 5.4375
2021-06-05 20:00 | 3.3209 | 4.1124 | 4.1779 | 4.4586 | 4.3463 | 4.627 | 2.4692 | 3.7404 | 4.4531 | 4.4531 | 4.9283 | 4.9283 | 2019-08-03 09:00 | 1.9053 | 3.2694 | 5.5259 | 5.5259 | 5.5259 | 5.5259
2021-06-05 21:00 | 2.9836 | 3.6947 | 3.7536 | 4.0058 | 3.9049 | 4.1571 | 2.3978 | 3.6321 | 4.3243 | 4.3243 | 4.7857 | 4.7857 | 2019-08-03 10:00 | 2.0424 | 3.5048 | 5.9237 | 5.9237 | 5.9237 | 5.9237
2021-06-05 22:00 | 2.8007 | 3.4682 | 3.5235 | 3.7602 | 3.6655 | 3.9023 | 2.0891 | 3.1646 | 3.7676 | 3.7676 | 4.1696 | 4.1696 | 2019-08-03 11:00 | 2.0196 | 3.4656 | 5.8574 | 5.8574 | 5.8574 | 5.8574
2021-06-05 23:00 | 2.6092 | 3.2311 | 3.2826 | 3.5032 | 3.4149 | 3.6355 | 1.8633 | 2.8226 | 3.3604 | 3.3604 | 3.719 | 3.719 | 2019-08-03 12:00 | 1.8976 | 3.2563 | 5.5038 | 5.5038 | 5.5038 | 5.5038
2021-06-06 | 2.332 | 2.8878 | 2.9338 | 3.131 | 3.0521 | 3.2493 | 1.612 | 2.4418 | 2.9071 | 2.9071 | 3.2173 | 3.2173 | 2019-08-03 13:00 | 1.8367 | 3.1517 | 5.3269 | 5.3269 | 5.3269 | 5.3269
2021-06-06 01:00 | 2.1264 | 2.6332 | 2.6751 | 2.8548 | 2.783 | 2.9627 | 1.441 | 2.1828 | 2.5988 | 2.5988 | 2.8761 | 2.8761 | 2019-08-03 14:00 | 1.89 | 3.2433 | 5.4817 | 5.4817 | 5.4817 | 5.4817
2021-06-06 02:00 | 2.0491 | 2.5375 | 2.5779 | 2.7511 | 2.6818 | 2.855 | 1.3003 | 1.9698 | 2.3451 | 2.3451 | 2.5953 | 2.5953 | 2019-08-03 15:00 | 1.8824 | 3.2302 | 5.4596 | 5.4596 | 5.4596 | 5.4596
2021-06-06 03:00 | 2.0119 | 2.4915 | 2.5312 | 2.7012 | 2.6332 | 2.8033 | 1.2575 | 1.9048 | 2.2678 | 2.2678 | 2.5098 | 2.5098 | 2019-08-03 16:00 | 1.9434 | 3.3348 | 5.6364 | 5.6364 | 5.6364 | 5.6364
2021-06-06 04:00 | 2.112 | 2.6153 | 2.657 | 2.8355 | 2.7641 | 2.9426 | 1.2775 | 1.9351 | 2.3039 | 2.3039 | 2.5497 | 2.5497 | 2019-08-03 17:00 | 1.9891 | 3.4133 | 5.769 | 5.769 | 5.769 | 5.769
2021-06-06 05:00 | 2.2263 | 2.7569 | 2.8008 | 2.989 | 2.9137 | 3.1019 | 1.3611 | 2.0619 | 2.4548 | 2.4548 | 2.7167 | 2.7167 | 2019-08-03 18:00 | 1.8748 | 3.2171 | 5.4375 | 5.4375 | 5.4375 | 5.4375
2021-06-06 06:00 | 2.4635 | 3.0506 | 3.0992 | 3.3075 | 3.2242 | 3.4324 | 1.4547 | 2.2035 | 2.6234 | 2.6234 | 2.9033 | 2.9033 | 2019-08-03 19:00 | 1.7909 | 3.0733 | 5.1943 | 5.1943 | 5.1943 | 5.1943
2021-06-06 07:00 | 2.8207 | 3.493 | 3.5487 | 3.7871 | 3.6917 | 3.9302 | 1.7455 | 2.6442 | 3.148 | 3.148 | 3.4839 | 3.4839 | 2019-08-03 20:00 | 1.6842 | 2.8902 | 4.8849 | 4.8849 | 4.8849 | 4.8849
2021-06-06 08:00 | 2.955 | 3.6594 | 3.7176 | 3.9674 | 3.8675 | 4.1173 | 1.9691 | 2.9828 | 3.5512 | 3.5512 | 3.9301 | 3.9301 | 2019-08-03 21:00 | 1.6461 | 2.8248 | 4.7743 | 4.7743 | 4.7743 | 4.7743
2021-06-06 09:00 | 2.9007 | 3.5921 | 3.6493 | 3.8945 | 3.7965 | 4.0417 | 2.0805 | 3.1516 | 3.7522 | 3.7522 | 4.1525 | 4.1525 | 2019-08-03 22:00 | 1.5699 | 2.694 | 4.5533 | 4.5533 | 4.5533 | 4.5533
2021-06-06 10:00 | 2.8264 | 3.5001 | 3.5558 | 3.7948 | 3.6992 | 3.9381 | 2.2349 | 3.3854 | 4.0305 | 4.0305 | 4.4605 | 4.4605 | 2019-08-03 23:00 | 1.3718 | 2.354 | 3.9786 | 3.9786 | 3.9786 | 3.9786
2021-06-06 11:00 | 2.6064 | 3.2276 | 3.279 | 3.4993 | 3.4112 | 3.6315 | 2.092 | 3.1689 | 3.7728 | 3.7728 | 4.1753 | 4.1753 | 2019-08-04 | 1.3261 | 2.2755 | 3.846 | 3.846 | 3.846 | 3.846
2021-06-06 12:00 | 2.3835 | 2.9515 | 2.9986 | 3.2 | 3.1195 | 3.3209 | 2.0348 | 3.0823 | 3.6697 | 3.6697 | 4.0613 | 4.0613 | 2019-08-04 01:00 | 1.2727 | 2.184 | 3.6913 | 3.6913 | 3.6913 | 3.6913
2021-06-06 13:00 | 2.3006 | 2.8489 | 2.8943 | 3.0888 | 3.011 | 3.2055 | 1.9834 | 3.0044 | 3.5769 | 3.5769 | 3.9586 | 3.9586 | 2019-08-04 02:00 | 1.1889 | 2.0401 | 3.4481 | 3.4481 | 3.4481 | 3.4481
2021-06-06 14:00 | 2.2434 | 2.7781 | 2.8224 | 3.012 | 2.9362 | 3.1258 | 1.9519 | 2.9568 | 3.5202 | 3.5202 | 3.8958 | 3.8958 | 2019-08-04 03:00 | 1.2041 | 2.0663 | 3.4923 | 3.4923 | 3.4923 | 3.4923
2021-06-06 15:00 | 2.3949 | 2.9657 | 3.0129 | 3.2154 | 3.1344 | 3.3369 | 1.9576 | 2.9655 | 3.5305 | 3.5305 | 3.9073 | 3.9073 | 2019-08-04 04:00 | 1.2041 | 2.0663 | 3.4923 | 3.4923 | 3.4923 | 3.4923
2021-06-06 16:00 | 2.9229 | 3.6196 | 3.6772 | 3.9243 | 3.8255 | 4.0726 | 2.3092 | 3.4979 | 4.1645 | 4.1645 | 4.6088 | 4.6088 | 2019-08-04 05:00 | 1.4023 | 2.4063 | 4.067 | 4.067 | 4.067 | 4.067
2021-06-06 17:00 | 3.5009 | 4.3353 | 4.4044 | 4.7003 | 4.5819 | 4.8779 | 2.4378 | 3.6928 | 4.3964 | 4.3964 | 4.8655 | 4.8655 | 2019-08-04 06:00 | 1.4937 | 2.5632 | 4.3323 | 4.3323 | 4.3323 | 4.3323
2021-06-06 18:00 | 3.438 | 4.2575 | 4.3253 | 4.6159 | 4.4996 | 4.7903 | 2.5464 | 3.8573 | 4.5923 | 4.5923 | 5.0823 | 5.0823 | 2019-08-04 07:00 | 1.5699 | 2.694 | 4.5533 | 4.5533 | 4.5533 | 4.5533
2021-06-06 19:00 | 3.2694 | 4.0486 | 4.1131 | 4.3895 | 4.279 | 4.5553 | 2.6064 | 3.9482 | 4.7005 | 4.7005 | 5.2021 | 5.2021 | 2019-08-04 08:00 | 1.8367 | 3.1517 | 5.3269 | 5.3269 | 5.3269 | 5.3269
2021-06-06 20:00 | 3.1294 | 3.8752 | 3.937 | 4.2015 | 4.0957 | 4.3602 | 2.5349 | 3.8399 | 4.5717 | 4.5717 | 5.0595 | 5.0595 | 2019-08-04 09:00 | 1.9281 | 3.3087 | 5.5922 | 5.5922 | 5.5922 | 5.5922
2021-06-06 21:00 | 2.8633 | 3.5457 | 3.6022 | 3.8442 | 3.7474 | 3.9895 | 2.3206 | 3.5153 | 4.1851 | 4.1851 | 4.6317 | 4.6317 | 2019-08-04 10:00 | 2.0043 | 3.4394 | 5.8132 | 5.8132 | 5.8132 | 5.8132
2021-06-06 22:00 | 2.5428 | 3.1488 | 3.199 | 3.4139 | 3.3279 | 3.5429 | 2.0548 | 3.1126 | 3.7058 | 3.7058 | 4.1012 | 4.1012 | 2019-08-04 11:00 | 1.8824 | 3.2302 | 5.4596 | 5.4596 | 5.4596 | 5.4596
2021-06-06 23:00 | 2.3341 | 2.8904 | 2.9364 | 3.1337 | 3.0548 | 3.2521 | 1.7033 | 2.5802 | 3.0718 | 3.0718 | 3.3996 | 3.3996 | 2019-08-04 12:00 | 1.7986 | 3.0863 | 5.2164 | 5.2164 | 5.2164 | 5.2164
2021-06-07 | 2.0177 | 2.4986 | 2.5383 | 2.7089 | 2.6407 | 2.8112 | 1.4461 | 2.1905 | 2.608 | 2.608 | 2.8862 | 2.8862 | 2019-08-04 13:00 | 1.829 | 3.1386 | 5.3048 | 5.3048 | 5.3048 | 5.3048
2021-06-07 01:00 | 1.9462 | 2.4101 | 2.4485 | 2.613 | 2.5472 | 2.7117 | 1.2775 | 1.9351 | 2.3039 | 2.3039 | 2.5497 | 2.5497 | 2019-08-04 14:00 | 1.8519 | 3.1779 | 5.3711 | 5.3711 | 5.3711 | 5.3711
2021-06-07 02:00 | 1.8776 | 2.3251 | 2.3622 | 2.5209 | 2.4574 | 2.6161 | 1.1946 | 1.8096 | 2.1544 | 2.1544 | 2.3843 | 2.3843 | 2019-08-04 15:00 | 1.8824 | 3.2302 | 5.4596 | 5.4596 | 5.4596 | 5.4596
2021-06-07 03:00 | 1.8433 | 2.2827 | 2.319 | 2.4749 | 2.4125 | 2.5683 | 1.1517 | 1.7446 | 2.0771 | 2.0771 | 2.2987 | 2.2987 | 2019-08-04 16:00 | 1.8824 | 3.2302 | 5.4596 | 5.4596 | 5.4596 | 5.4596
2021-06-07 04:00 | 1.9348 | 2.3959 | 2.4341 | 2.5976 | 2.5322 | 2.6958 | 1.1946 | 1.8096 | 2.1544 | 2.1544 | 2.3843 | 2.3843 | 2019-08-04 17:00 | 1.9205 | 3.2956 | 5.5701 | 5.5701 | 5.5701 | 5.5701
2021-06-07 05:00 | 2.3863 | 2.9551 | 3.0022 | 3.2039 | 3.1232 | 3.3249 | 1.2603 | 1.9091 | 2.2729 | 2.2729 | 2.5155 | 2.5155 | 2019-08-04 18:00 | 1.951 | 3.3479 | 5.6585 | 5.6585 | 5.6585 | 5.6585
2021-06-07 06:00 | 3.4752 | 4.3035 | 4.372 | 4.6658 | 4.5483 | 4.842 | 1.6437 | 2.49 | 2.9644 | 2.9644 | 3.2807 | 3.2807 | 2019-08-04 19:00 | 1.89 | 3.2433 | 5.4817 | 5.4817 | 5.4817 | 5.4817
2021-06-07 07:00 | 3.8553 | 4.7742 | 4.8502 | 5.1761 | 5.0457 | 5.3716 | 2.0234 | 3.065 | 3.6491 | 3.6491 | 4.0384 | 4.0384 | 2019-08-04 20:00 | 1.7909 | 3.0733 | 5.1943 | 5.1943 | 5.1943 | 5.1943
2021-06-07 08:00 | 4.0239 | 4.983 | 5.0623 | 5.4025 | 5.2664 | 5.6066 | 1.9977 | 3.0261 | 3.6027 | 3.6027 | 3.9871 | 3.9871 | 2019-08-04 21:00 | 1.6995 | 2.9163 | 4.9291 | 4.9291 | 4.9291 | 4.9291
2021-06-07 09:00 | 3.921 | 4.8555 | 4.9329 | 5.2643 | 5.1318 | 5.4632 | 1.9491 | 2.9525 | 3.5151 | 3.5151 | 3.8901 | 3.8901 | 2019-08-04 22:00 | 1.5623 | 2.6809 | 4.5312 | 4.5312 | 4.5312 | 4.5312
2021-06-07 10:00 | 3.9496 | 4.8909 | 4.9688 | 5.3027 | 5.1692 | 5.503 | 2.1177 | 3.2079 | 3.8192 | 3.8192 | 4.2267 | 4.2267 | 2019-08-04 23:00 | 1.3794 | 2.3671 | 4.0007 | 4.0007 | 4.0007 | 4.0007
2021-06-07 11:00 | 3.7753 | 4.6751 | 4.7495 | 5.0687 | 4.941 | 5.2601 | 2.0377 | 3.0867 | 3.6748 | 3.6748 | 4.067 | 4.067 | 2019-08-05 | 1.3032 | 2.2363 | 3.7797 | 3.7797 | 3.7797 | 3.7797
2021-06-07 12:00 | 3.5066 | 4.3424 | 4.4116 | 4.708 | 4.5894 | 4.8858 | 1.9291 | 2.9222 | 3.479 | 3.479 | 3.8502 | 3.8502 | 2019-08-05 01:00 | 1.2498 | 2.1447 | 3.625 | 3.625 | 3.625 | 3.625
2021-06-07 13:00 | 3.0322 | 3.7549 | 3.8147 | 4.071 | 3.9685 | 4.2248 | 1.7747 | 2.6884 | 3.2007 | 3.2007 | 3.5422 | 3.5422 | 2019-08-05 02:00 | 1.1584 | 1.9878 | 3.3597 | 3.3597 | 3.3597 | 3.3597
2021-06-07 14:00 | 2.9293 | 3.6275 | 3.6853 | 3.9329 | 3.8339 | 4.0815 | 1.7662 | 2.6754 | 3.1852 | 3.1852 | 3.5251 | 3.5251 | 2019-08-05 03:00 | 1.1584 | 1.9878 | 3.3597 | 3.3597 | 3.3597 | 3.3597
2021-06-07 15:00 | 3.1751 | 3.9319 | 3.9945 | 4.2629 | 4.1555 | 4.4239 | 1.7519 | 2.6538 | 3.1594 | 3.1594 | 3.4966 | 3.4966 | 2019-08-05 04:00 | 1.1813 | 2.027 | 3.426 | 3.426 | 3.426 | 3.426
2021-06-07 16:00 | 3.5323 | 4.3742 | 4.4439 | 4.7425 | 4.6231 | 4.9217 | 2.0608 | 3.1217 | 3.7165 | 3.7165 | 4.1131 | 4.1131 | 2019-08-05 05:00 | 1.448 | 2.4848 | 4.1997 | 4.1997 | 4.1997 | 4.1997
2021-06-07 17:00 | 4.1068 | 5.0856 | 5.1666 | 5.5137 | 5.3749 | 5.722 | 2.3692 | 3.5889 | 4.2727 | 4.2727 | 4.7286 | 4.7286 | 2019-08-05 06:00 | 1.7223 | 2.9556 | 4.9954 | 4.9954 | 4.9954 | 4.9954
2021-06-07 18:00 | 4.0925 | 5.0679 | 5.1486 | 5.4946 | 5.3562 | 5.7021 | 2.5635 | 3.8832 | 4.6232 | 4.6232 | 5.1165 | 5.1165 | 2019-08-05 07:00 | 2.0882 | 3.5833 | 6.0564 | 6.0564 | 6.0564 | 6.0564
2021-06-07 19:00 | 3.981 | 4.9299 | 5.0084 | 5.3449 | 5.2103 | 5.5468 | 2.5892 | 3.9222 | 4.6696 | 4.6696 | 5.1678 | 5.1678 | 2019-08-05 08:00 | 2.2482 | 3.8579 | 6.5205 | 6.5205 | 6.5205 | 6.5205
2021-06-07 20:00 | 3.7124 | 4.5972 | 4.6704 | 4.9842 | 4.8587 | 5.1725 | 2.4692 | 3.7404 | 4.4531 | 4.4531 | 4.9283 | 4.9283 | 2019-08-05 09:00 | 2.2101 | 3.7925 | 6.41 | 6.41 | 6.41 | 6.41
2021-06-07 21:00 | 3.2923 | 4.077 | 4.1419 | 4.4202 | 4.3089 | 4.5872 | 2.4292 | 3.6798 | 4.381 | 4.381 | 4.8484 | 4.8484 | 2019-08-05 10:00 | 2.1491 | 3.6879 | 6.2332 | 6.2332 | 6.2332 | 6.2332
2021-06-07 22:00 | 2.9068 | 3.5996 | 3.657 | 3.9027 | 3.8044 | 4.0501 | 2.1091 | 3.1949 | 3.8037 | 3.8037 | 4.2096 | 4.2096 | 2019-08-05 11:00 | 2.1567 | 3.701 | 6.2553 | 6.2553 | 6.2553 | 6.2553
2021-06-07 23:00 | 2.4806 | 3.0719 | 3.1208 | 3.3305 | 3.2466 | 3.4563 | 1.7547 | 2.6581 | 3.1646 | 3.1646 | 3.5023 | 3.5023 | 2019-08-05 12:00 | 2.1186 | 3.6356 | 6.1448 | 6.1448 | 6.1448 | 6.1448
2021-06-08 | 2.1561 | 2.67 | 2.7125 | 2.8948 | 2.8219 | 3.0042 | 1.4146 | 2.1429 | 2.5513 | 2.5513 | 2.8235 | 2.8235 | 2019-08-05 13:00 | 2.1339 | 3.6618 | 6.189 | 6.189 | 6.189 | 6.189
2021-06-08 01:00 | 1.9605 | 2.4278 | 2.4664 | 2.6322 | 2.5659 | 2.7316 | 1.2379 | 1.8751 | 2.2324 | 2.2324 | 2.4706 | 2.4706 | 2019-08-05 14:00 | 2.0958 | 3.5964 | 6.0785 | 6.0785 | 6.0785 | 6.0785
2021-06-08 02:00 | 1.9405 | 2.403 | 2.4413 | 2.6053 | 2.5397 | 2.7037 | 1.226 | 1.8572 | 2.2111 | 2.2111 | 2.447 | 2.447 | 2019-08-05 15:00 | 2.0958 | 3.5964 | 6.0785 | 6.0785 | 6.0785 | 6.0785
2021-06-08 03:00 | 1.9576 | 2.4242 | 2.4628 | 2.6283 | 2.5621 | 2.7276 | 1.166 | 1.7663 | 2.1029 | 2.1029 | 2.3272 | 2.3272 | 2019-08-05 16:00 | 2.0958 | 3.5964 | 6.0785 | 6.0785 | 6.0785 | 6.0785
2021-06-08 04:00 | 1.9576 | 2.4242 | 2.4628 | 2.6283 | 2.5621 | 2.7276 | 1.1801 | 1.7877 | 2.1283 | 2.1283 | 2.3554 | 2.3554 | 2019-08-05 17:00 | 2.1872 | 3.7533 | 6.3437 | 6.3437 | 6.3437 | 6.3437
2021-06-08 05:00 | 2.5474 | 3.1546 | 3.2048 | 3.4202 | 3.334 | 3.5494 | 1.3232 | 2.0044 | 2.3863 | 2.3863 | 2.641 | 2.641 | 2019-08-05 18:00 | 2.1872 | 3.7533 | 6.3437 | 6.3437 | 6.3437 | 6.3437
2021-06-08 06:00 | 3.5238 | 4.3636 | 4.4331 | 4.731 | 4.6119 | 4.9097 | 1.7347 | 2.6278 | 3.1285 | 3.1285 | 3.4623 | 3.4623 | 2019-08-05 19:00 | 2.0501 | 3.5179 | 5.9458 | 5.9458 | 5.9458 | 5.9458
2021-06-08 07:00 | 4.1868 | 5.1847 | 5.2673 | 5.6212 | 5.4796 | 5.8335 | 2.0548 | 3.1126 | 3.7058 | 3.7058 | 4.1012 | 4.1012 | 2019-08-05 20:00 | 1.9891 | 3.4133 | 5.769 | 5.769 | 5.769 | 5.769
2021-06-08 08:00 | 4.2697 | 5.2873 | 5.3715 | 5.7325 | 5.5881 | 5.949 | 2.1148 | 3.2036 | 3.814 | 3.814 | 4.221 | 4.221 | 2019-08-05 21:00 | 1.9053 | 3.2694 | 5.5259 | 5.5259 | 5.5259 | 5.5259
2021-06-08 09:00 | 3.981 | 4.9299 | 5.0084 | 5.3449 | 5.2103 | 5.5468 | 1.8948 | 2.8702 | 3.4171 | 3.4171 | 3.7818 | 3.7818 | 2019-08-05 22:00 | 1.7147 | 2.9425 | 4.9733 | 4.9733 | 4.9733 | 4.9733
2021-06-08 10:00 | 3.6638 | 4.537 | 4.6093 | 4.919 | 4.7951 | 5.1048 | 1.9005 | 2.8789 | 3.4275 | 3.4275 | 3.7932 | 3.7932 | 2019-08-05 23:00 | 1.4785 | 2.5371 | 4.2881 | 4.2881 | 4.2881 | 4.2881
2021-06-08 11:00 | 3.6324 | 4.4981 | 4.5698 | 4.8768 | 4.754 | 5.061 | 1.9291 | 2.9222 | 3.479 | 3.479 | 3.8502 | 3.8502 | 2019-08-06 | 1.3489 | 2.3148 | 3.9123 | 3.9123 | 3.9123 | 3.9123
2021-06-08 12:00 | 3.2466 | 4.0203 | 4.0844 | 4.3588 | 4.249 | 4.5235 | 1.8433 | 2.7923 | 3.3244 | 3.3244 | 3.6791 | 3.6791 | 2019-08-06 01:00 | 1.2346 | 2.1186 | 3.5808 | 3.5808 | 3.5808 | 3.5808
2021-06-08 13:00 | 3.1265 | 3.8717 | 3.9334 | 4.1977 | 4.0919 | 4.3562 | 1.7719 | 2.6841 | 3.1955 | 3.1955 | 3.5365 | 3.5365 | 2019-08-06 02:00 | 1.2575 | 2.1578 | 3.6471 | 3.6471 | 3.6471 | 3.6471
2021-06-08 14:00 | 2.9636 | 3.67 | 3.7284 | 3.979 | 3.8787 | 4.1293 | 1.789 | 2.71 | 3.2264 | 3.2264 | 3.5707 | 3.5707 | 2019-08-06 03:00 | 1.2346 | 2.1186 | 3.5808 | 3.5808 | 3.5808 | 3.5808
2021-06-08 15:00 | 2.9951 | 3.7089 | 3.768 | 4.0212 | 3.9199 | 4.1731 | 1.709 | 2.5888 | 3.0821 | 3.0821 | 3.411 | 3.411 | 2019-08-06 04:00 | 1.2346 | 2.1186 | 3.5808 | 3.5808 | 3.5808 | 3.5808
2021-06-08 16:00 | 3.478 | 4.307 | 4.3756 | 4.6696 | 4.552 | 4.846 | 1.9948 | 3.0217 | 3.5975 | 3.5975 | 3.9814 | 3.9814 | 2019-08-06 05:00 | 1.5166 | 2.6025 | 4.3986 | 4.3986 | 4.3986 | 4.3986
2021-06-08 17:00 | 4.1011 | 5.0785 | 5.1594 | 5.5061 | 5.3674 | 5.7141 | 2.3835 | 3.6105 | 4.2985 | 4.2985 | 4.7572 | 4.7572 | 2019-08-06 06:00 | 1.8214 | 3.1256 | 5.2827 | 5.2827 | 5.2827 | 5.2827
2021-06-08 18:00 | 4.2068 | 5.2095 | 5.2924 | 5.648 | 5.5058 | 5.8614 | 2.4749 | 3.749 | 4.4634 | 4.4634 | 4.9397 | 4.9397 | 2019-08-06 07:00 | 2.1186 | 3.6356 | 6.1448 | 6.1448 | 6.1448 | 6.1448
2021-06-08 19:00 | 4.194 | 5.1936 | 5.2763 | 5.6309 | 5.489 | 5.8436 | 2.4521 | 3.7144 | 4.4222 | 4.4222 | 4.894 | 4.894 | 2019-08-06 08:00 | 2.2482 | 3.8579 | 6.5205 | 6.5205 | 6.5205 | 6.5205
2021-06-08 20:00 | 3.6781 | 4.5547 | 4.6273 | 4.9382 | 4.8138 | 5.1248 | 2.4263 | 3.6754 | 4.3758 | 4.3758 | 4.8427 | 4.8427 | 2019-08-06 09:00 | 2.1644 | 3.7141 | 6.2774 | 6.2774 | 6.2774 | 6.2774
2021-06-08 21:00 | 3.178 | 3.9354 | 3.9981 | 4.2667 | 4.1593 | 4.4279 | 2.2806 | 3.4546 | 4.1129 | 4.1129 | 4.5518 | 4.5518 | 2019-08-06 10:00 | 2.1034 | 3.6094 | 6.1006 | 6.1006 | 6.1006 | 6.1006
2021-06-08 22:00 | 2.715 | 3.3621 | 3.4156 | 3.6451 | 3.5533 | 3.7828 | 2.0034 | 3.0347 | 3.613 | 3.613 | 3.9985 | 3.9985 | 2019-08-06 11:00 | 2.0729 | 3.5571 | 6.0121 | 6.0121 | 6.0121 | 6.0121
2021-06-08 23:00 | 2.3705 | 2.9355 | 2.9823 | 3.1827 | 3.1025 | 3.3029 | 1.6751 | 2.5375 | 3.021 | 3.021 | 3.3434 | 3.3434 | 2019-08-06 12:00 | 2.0729 | 3.5571 | 6.0121 | 6.0121 | 6.0121 | 6.0121
2021-06-09 | 2.092 | 2.5906 | 2.6318 | 2.8087 | 2.7379 | 2.9148 | 1.4032 | 2.1256 | 2.5306 | 2.5306 | 2.8007 | 2.8007 | 2019-08-06 13:00 | 2.0653 | 3.5441 | 5.99 | 5.99 | 5.99 | 5.99
2021-06-09 01:00 | 1.9676 | 2.4366 | 2.4754 | 2.6417 | 2.5752 | 2.7415 | 1.2265 | 1.8578 | 2.2119 | 2.2119 | 2.4479 | 2.4479 | 2019-08-06 14:00 | 2.0805 | 3.5702 | 6.0343 | 6.0343 | 6.0343 | 6.0343
2021-06-09 02:00 | 1.8519 | 2.2933 | 2.3298 | 2.4864 | 2.4237 | 2.5803 | 1.0946 | 1.6581 | 1.974 | 1.974 | 2.1846 | 2.1846 | 2019-08-06 15:00 | 2.1186 | 3.6356 | 6.1448 | 6.1448 | 6.1448 | 6.1448
2021-06-09 03:00 | 1.9033 | 2.357 | 2.3945 | 2.5554 | 2.4911 | 2.652 | 1.1374 | 1.723 | 2.0513 | 2.0513 | 2.2702 | 2.2702 | 2019-08-06 16:00 | 2.111 | 3.6225 | 6.1227 | 6.1227 | 6.1227 | 6.1227
2021-06-09 04:00 | 1.9805 | 2.4525 | 2.4916 | 2.659 | 2.5921 | 2.7595 | 1.1489 | 1.7403 | 2.0719 | 2.0719 | 2.293 | 2.293 | 2019-08-06 17:00 | 2.1567 | 3.701 | 6.2553 | 6.2553 | 6.2553 | 6.2553
2021-06-09 05:00 | 2.4521 | 3.0365 | 3.0849 | 3.2921 | 3.2092 | 3.4165 | 1.4089 | 2.1343 | 2.541 | 2.541 | 2.8121 | 2.8121 | 2019-08-06 18:00 | 2.1339 | 3.6618 | 6.189 | 6.189 | 6.189 | 6.189
2021-06-09 06:00 | 3.3866 | 4.1937 | 4.2605 | 4.5468 | 4.4323 | 4.7186 | 1.679 | 2.5434 | 3.028 | 3.028 | 3.3511 | 3.3511 | 2019-08-06 19:00 | 2.1263 | 3.6487 | 6.1669 | 6.1669 | 6.1669 | 6.1669
2021-06-09 07:00 | 4.1782 | 5.1741 | 5.2565 | 5.6097 | 5.4684 | 5.8216 | 2.0005 | 3.0304 | 3.6078 | 3.6078 | 3.9928 | 3.9928 | 2019-08-06 20:00 | 2.0043 | 3.4394 | 5.8132 | 5.8132 | 5.8132 | 5.8132
2021-06-09 08:00 | 4.0868 | 5.0608 | 5.1414 | 5.4869 | 5.3487 | 5.6942 | 2.0434 | 3.0953 | 3.6852 | 3.6852 | 4.0784 | 4.0784 | 2019-08-06 21:00 | 1.8824 | 3.2302 | 5.4596 | 5.4596 | 5.4596 | 5.4596
2021-06-09 09:00 | 3.961 | 4.9051 | 4.9832 | 5.3181 | 5.1841 | 5.519 | 1.9691 | 2.9828 | 3.5512 | 3.5512 | 3.9301 | 3.9301 | 2019-08-06 22:00 | 1.6461 | 2.8248 | 4.7743 | 4.7743 | 4.7743 | 4.7743
2021-06-09 10:00 | 3.981 | 4.9299 | 5.0084 | 5.3449 | 5.2103 | 5.5468 | 2.0434 | 3.0953 | 3.6852 | 3.6852 | 4.0784 | 4.0784 | 2019-08-06 23:00 | 1.4937 | 2.5632 | 4.3323 | 4.3323 | 4.3323 | 4.3323
2021-06-09 11:00 | 3.8639 | 4.7848 | 4.861 | 5.1876 | 5.057 | 5.3836 | 2.1777 | 3.2988 | 3.9274 | 3.9274 | 4.3465 | 4.3465 | 2019-08-07 | 1.3794 | 2.3671 | 4.0007 | 4.0007 | 4.0007 | 4.0007
2021-06-09 12:00 | 3.7267 | 4.6149 | 4.6884 | 5.0034 | 4.8774 | 5.1924 | 2.0748 | 3.143 | 3.7419 | 3.7419 | 4.1411 | 4.1411 | 2019-08-07 01:00 | 1.2651 | 2.1709 | 3.6692 | 3.6692 | 3.6692 | 3.6692
2021-06-09 13:00 | 3.6238 | 4.4875 | 4.559 | 4.8653 | 4.7428 | 5.0491 | 1.9091 | 2.8919 | 3.4429 | 3.4429 | 3.8103 | 3.8103 | 2019-08-07 02:00 | 1.2117 | 2.0794 | 3.5144 | 3.5144 | 3.5144 | 3.5144
2021-06-09 14:00 | 3.4723 | 4.2999 | 4.3684 | 4.6619 | 4.5445 | 4.8381 | 1.9805 | 3.0001 | 3.5718 | 3.5718 | 3.9529 | 3.9529 | 2019-08-07 03:00 | 1.227 | 2.1055 | 3.5587 | 3.5587 | 3.5587 | 3.5587
2021-06-09 15:00 | 3.4723 | 4.2999 | 4.3684 | 4.6619 | 4.5445 | 4.8381 | 1.9205 | 2.9092 | 3.4635 | 3.4635 | 3.8331 | 3.8331 | 2019-08-07 04:00 | 1.2956 | 2.2232 | 3.7576 | 3.7576 | 3.7576 | 3.7576
2021-06-09 16:00 | 3.9725 | 4.9193 | 4.9976 | 5.3334 | 5.1991 | 5.5349 | 2.3463 | 3.5542 | 4.2315 | 4.2315 | 4.683 | 4.683 | 2019-08-07 05:00 | 1.6004 | 2.7463 | 4.6417 | 4.6417 | 4.6417 | 4.6417
2021-06-09 17:00 | 4.2725 | 5.2909 | 5.3751 | 5.7363 | 5.5918 | 5.953 | 2.6435 | 4.0045 | 4.7675 | 4.7675 | 5.2762 | 5.2762 | 2019-08-07 06:00 | 1.7909 | 3.0733 | 5.1943 | 5.1943 | 5.1943 | 5.1943
2021-06-09 18:00 | 4.4583 | 5.5209 | 5.6088 | 5.9857 | 5.8349 | 6.2118 | 2.7207 | 4.1213 | 4.9067 | 4.9067 | 5.4302 | 5.4302 | 2019-08-07 07:00 | 2.1567 | 3.701 | 6.2553 | 6.2553 | 6.2553 | 6.2553
2021-06-09 19:00 | 4.2297 | 5.2378 | 5.3212 | 5.6787 | 5.5357 | 5.8933 | 2.6778 | 4.0564 | 4.8294 | 4.8294 | 5.3447 | 5.3447 | 2019-08-07 08:00 | 2.2406 | 3.8448 | 6.4984 | 6.4984 | 6.4984 | 6.4984
2021-06-09 20:00 | 3.8038 | 4.7104 | 4.7855 | 5.107 | 4.9784 | 5.3 | 2.6019 | 3.9414 | 4.6924 | 4.6924 | 5.1931 | 5.1931 | 2019-08-07 09:00 | 2.1644 | 3.7141 | 6.2774 | 6.2774 | 6.2774 | 6.2774
2021-06-09 21:00 | 3.4392 | 4.2589 | 4.3268 | 4.6175 | 4.5012 | 4.7919 | 2.5224 | 3.8209 | 4.549 | 4.549 | 5.0344 | 5.0344 | 2019-08-07 10:00 | 2.0653 | 3.5441 | 5.99 | 5.99 | 5.99 | 5.99
2021-06-09 22:00 | 2.8612 | 3.5431 | 3.5996 | 3.8414 | 3.7447 | 3.9865 | 2.1777 | 3.2988 | 3.9274 | 3.9274 | 4.3465 | 4.3465 | 2019-08-07 11:00 | 2.0348 | 3.4917 | 5.9016 | 5.9016 | 5.9016 | 5.9016
2021-06-09 23:00 | 2.4847 | 3.0769 | 3.1259 | 3.336 | 3.252 | 3.462 | 1.8776 | 2.8442 | 3.3862 | 3.3862 | 3.7475 | 3.7475 | 2019-08-07 12:00 | 2.0805 | 3.5702 | 6.0343 | 6.0343 | 6.0343 | 6.0343
2021-06-10 | 2.1863 | 2.7074 | 2.7505 | 2.9353 | 2.8614 | 3.0462 | 1.5575 | 2.3594 | 2.809 | 2.809 | 3.1087 | 3.1087 | 2019-08-07 13:00 | 2.0043 | 3.4394 | 5.8132 | 5.8132 | 5.8132 | 5.8132
2021-06-10 01:00 | 1.9834 | 2.4561 | 2.4952 | 2.6629 | 2.5958 | 2.7635 | 1.3575 | 2.0563 | 2.4482 | 2.4482 | 2.7094 | 2.7094 | 2019-08-07 14:00 | 2.0958 | 3.5964 | 6.0785 | 6.0785 | 6.0785 | 6.0785
2021-06-10 02:00 | 1.9062 | 2.3605 | 2.3981 | 2.5593 | 2.4948 | 2.6559 | 1.2489 | 1.8918 | 2.2523 | 2.2523 | 2.4927 | 2.4927 | 2019-08-07 15:00 | 2.0424 | 3.5048 | 5.9237 | 5.9237 | 5.9237 | 5.9237
2021-06-10 03:00 | 1.9376 | 2.3995 | 2.4377 | 2.6015 | 2.536 | 2.6997 | 1.2375 | 1.8745 | 2.2317 | 2.2317 | 2.4698 | 2.4698 | 2019-08-07 16:00 | 2.1339 | 3.6618 | 6.189 | 6.189 | 6.189 | 6.189
2021-06-10 04:00 | 1.9348 | 2.3959 | 2.4341 | 2.5976 | 2.5322 | 2.6958 | 1.2449 | 1.8858 | 2.2452 | 2.2452 | 2.4847 | 2.4847 | 2019-08-07 17:00 | 2.1644 | 3.7141 | 6.2774 | 6.2774 | 6.2774 | 6.2774
2021-06-10 05:00 | 2.5264 | 3.1285 | 3.1783 | 3.3919 | 3.3065 | 3.52 | 1.3461 | 2.039 | 2.4276 | 2.4276 | 2.6866 | 2.6866 | 2019-08-07 18:00 | 2.1339 | 3.6618 | 6.189 | 6.189 | 6.189 | 6.189
2021-06-10 06:00 | 3.5181 | 4.3565 | 4.4259 | 4.7233 | 4.6044 | 4.9018 | 1.7004 | 2.5758 | 3.0667 | 3.0667 | 3.3939 | 3.3939 | 2019-08-07 19:00 | 2.0501 | 3.5179 | 5.9458 | 5.9458 | 5.9458 | 5.9458
2021-06-10 07:00 | 4.1725 | 5.167 | 5.2493 | 5.602 | 5.4609 | 5.8136 | 2.032 | 3.078 | 3.6645 | 3.6645 | 4.0556 | 4.0556 | 2019-08-07 20:00 | 1.9586 | 3.361 | 5.6806 | 5.6806 | 5.6806 | 5.6806
2021-06-10 08:00 | 4.1868 | 5.1847 | 5.2673 | 5.6212 | 5.4796 | 5.8335 | 2.0662 | 3.13 | 3.7264 | 3.7264 | 4.124 | 4.124 | 2019-08-07 21:00 | 1.951 | 3.3479 | 5.6585 | 5.6585 | 5.6585 | 5.6585
2021-06-10 09:00 | 3.9296 | 4.8662 | 4.9437 | 5.2759 | 5.143 | 5.4752 | 1.8691 | 2.8313 | 3.3708 | 3.3708 | 3.7304 | 3.7304 | 2019-08-07 22:00 | 1.6614 | 2.8509 | 4.8186 | 4.8186 | 4.8186 | 4.8186
2021-06-10 10:00 | 3.781 | 4.6821 | 4.7567 | 5.0763 | 4.9485 | 5.2681 | 1.9576 | 2.9655 | 3.5305 | 3.5305 | 3.9073 | 3.9073 | 2019-08-07 23:00 | 1.4709 | 2.524 | 4.266 | 4.266 | 4.266 | 4.266
2021-06-10 11:00 | 3.7353 | 4.6255 | 4.6992 | 5.0149 | 4.8886 | 5.2044 | 2.0291 | 3.0737 | 3.6594 | 3.6594 | 4.0499 | 4.0499 | 2019-08-08 | 1.3946 | 2.3932 | 4.0449 | 4.0449 | 4.0449 | 4.0449
2021-06-10 12:00 | 3.7581 | 4.6538 | 4.728 | 5.0456 | 4.9186 | 5.2362 | 2.0662 | 3.13 | 3.7264 | 3.7264 | 4.124 | 4.124 | 2019-08-08 01:00 | 1.2422 | 2.1317 | 3.6029 | 3.6029 | 3.6029 | 3.6029
2021-06-10 13:00 | 3.8038 | 4.7104 | 4.7855 | 5.107 | 4.9784 | 5.3 | 2.112 | 3.1992 | 3.8089 | 3.8089 | 4.2153 | 4.2153 | 2019-08-08 02:00 | 1.2194 | 2.0924 | 3.5366 | 3.5366 | 3.5366 | 3.5366
2021-06-10 14:00 | 3.7638 | 4.6609 | 4.7351 | 5.0533 | 4.926 | 5.2442 | 2.1348 | 3.2339 | 3.8501 | 3.8501 | 4.2609 | 4.2609 | 2019-08-08 03:00 | 1.2194 | 2.0924 | 3.5366 | 3.5366 | 3.5366 | 3.5366
2021-06-10 15:00 | 3.7753 | 4.6751 | 4.7495 | 5.0687 | 4.941 | 5.2601 | 2.1205 | 3.2122 | 3.8243 | 3.8243 | 4.2324 | 4.2324 | 2019-08-08 04:00 | 1.3108 | 2.2494 | 3.8018 | 3.8018 | 3.8018 | 3.8018
2021-06-10 16:00 | 4.1125 | 5.0927 | 5.1738 | 5.5214 | 5.3824 | 5.73 | 2.3395 | 3.5438 | 4.2191 | 4.2191 | 4.6693 | 4.6693 | 2019-08-08 05:00 | 1.5775 | 2.7071 | 4.5754 | 4.5754 | 4.5754 | 4.5754
2021-06-10 17:00 | 4.5012 | 5.574 | 5.6628 | 6.0433 | 5.8911 | 6.2715 | 2.7064 | 4.0997 | 4.8809 | 4.8809 | 5.4017 | 5.4017 | 2019-08-08 06:00 | 1.6461 | 2.8248 | 4.7743 | 4.7743 | 4.7743 | 4.7743
2021-06-10 18:00 | 4.5583 | 5.6448 | 5.7347 | 6.12 | 5.9659 | 6.3512 | 2.715 | 4.1127 | 4.8964 | 4.8964 | 5.4188 | 5.4188 | 2019-08-08 07:00 | 2.0653 | 3.5441 | 5.99 | 5.99 | 5.99 | 5.99
2021-06-10 19:00 | 4.2945 | 5.3181 | 5.4028 | 5.7658 | 5.6206 | 5.9836 | 2.6464 | 4.0088 | 4.7727 | 4.7727 | 5.2819 | 5.2819 | 2019-08-08 08:00 | 2.2939 | 3.9364 | 6.6531 | 6.6531 | 6.6531 | 6.6531
2021-06-10 20:00 | 3.9982 | 4.9511 | 5.03 | 5.3679 | 5.2328 | 5.5707 | 2.6292 | 3.9828 | 4.7417 | 4.7417 | 5.2477 | 5.2477 | 2019-08-08 09:00 | 2.3168 | 3.9756 | 6.7195 | 6.7195 | 6.7195 | 6.7195
2021-06-10 21:00 | 3.557 | 4.4048 | 4.475 | 4.7757 | 4.6554 | 4.9561 | 2.4175 | 3.6621 | 4.3599 | 4.3599 | 4.8251 | 4.8251 | 2019-08-08 10:00 | 2.172 | 3.7271 | 6.2995 | 6.2995 | 6.2995 | 6.2995
2021-06-10 22:00 | 2.917 | 3.6123 | 3.6698 | 3.9164 | 3.8177 | 4.0643 | 2.1291 | 3.2252 | 3.8398 | 3.8398 | 4.2495 | 4.2495 | 2019-08-08 11:00 | 2.2101 | 3.7925 | 6.41 | 6.41 | 6.41 | 6.41
2021-06-10 23:00 | 2.5819 | 3.1973 | 3.2482 | 3.4665 | 3.3792 | 3.5974 | 1.8324 | 2.7757 | 3.3046 | 3.3046 | 3.6572 | 3.6572 | 2019-08-08 12:00 | 2.1949 | 3.7664 | 6.3658 | 6.3658 | 6.3658 | 6.3658
2021-06-11 | 2.2063 | 2.7321 | 2.7756 | 2.9621 | 2.8875 | 3.0741 | 1.4832 | 2.2468 | 2.675 | 2.675 | 2.9604 | 2.9604 | 2019-08-08 13:00 | 2.1644 | 3.7141 | 6.2774 | 6.2774 | 6.2774 | 6.2774
2021-06-11 01:00 | 2.0634 | 2.5552 | 2.5959 | 2.7703 | 2.7005 | 2.875 | 1.3004 | 1.9698 | 2.3452 | 2.3452 | 2.5954 | 2.5954 | 2019-08-08 14:00 | 2.1491 | 3.6879 | 6.2332 | 6.2332 | 6.2332 | 6.2332
2021-06-11 02:00 | 1.9405 | 2.403 | 2.4413 | 2.6053 | 2.5397 | 2.7037 | 1.1867 | 1.7976 | 2.1401 | 2.1401 | 2.3684 | 2.3684 | 2019-08-08 15:00 | 2.0653 | 3.5441 | 5.99 | 5.99 | 5.99 | 5.99
2021-06-11 03:00 | 1.9376 | 2.3995 | 2.4377 | 2.6015 | 2.536 | 2.6997 | 1.1689 | 1.7706 | 2.108 | 2.108 | 2.3329 | 2.3329 | 2019-08-08 16:00 | 2.0729 | 3.5571 | 6.0121 | 6.0121 | 6.0121 | 6.0121
2021-06-11 04:00 | 1.9548 | 2.4207 | 2.4593 | 2.6245 | 2.5584 | 2.7236 | 1.2003 | 1.8182 | 2.1647 | 2.1647 | 2.3957 | 2.3957 | 2019-08-08 17:00 | 2.2177 | 3.8056 | 6.4321 | 6.4321 | 6.4321 | 6.4321
2021-06-11 05:00 | 2.3537 | 2.9146 | 2.9611 | 3.16 | 3.0804 | 3.2794 | 1.3203 | 2.0001 | 2.3812 | 2.3812 | 2.6353 | 2.6353 | 2019-08-08 18:00 | 2.2177 | 3.8056 | 6.4321 | 6.4321 | 6.4321 | 6.4321
2021-06-11 06:00 | 3.2694 | 4.0486 | 4.1131 | 4.3895 | 4.279 | 4.5553 | 1.7147 | 2.5975 | 3.0924 | 3.0924 | 3.4224 | 3.4224 | 2019-08-08 19:00 | 2.1263 | 3.6487 | 6.1669 | 6.1669 | 6.1669 | 6.1669
2021-06-11 07:00 | 3.7867 | 4.6892 | 4.7639 | 5.084 | 4.956 | 5.2761 | 1.9919 | 3.0174 | 3.5924 | 3.5924 | 3.9757 | 3.9757 | 2019-08-08 20:00 | 2.0348 | 3.4917 | 5.9016 | 5.9016 | 5.9016 | 5.9016
2021-06-11 08:00 | 3.9182 | 4.852 | 4.9293 | 5.2605 | 5.128 | 5.4592 | 2.0462 | 3.0997 | 3.6903 | 3.6903 | 4.0841 | 4.0841 | 2019-08-08 21:00 | 1.8748 | 3.2171 | 5.4375 | 5.4375 | 5.4375 | 5.4375
2021-06-11 09:00 | 3.7181 | 4.6043 | 4.6776 | 4.9919 | 4.8662 | 5.1805 | 1.8891 | 2.8616 | 3.4068 | 3.4068 | 3.7704 | 3.7704 | 2019-08-08 22:00 | 1.669 | 2.864 | 4.8407 | 4.8407 | 4.8407 | 4.8407
2021-06-11 10:00 | 3.3866 | 4.1937 | 4.2605 | 4.5468 | 4.4323 | 4.7186 | 1.809 | 2.7403 | 3.2625 | 3.2625 | 3.6106 | 3.6106 | 2019-08-08 23:00 | 1.4556 | 2.4978 | 4.2218 | 4.2218 | 4.2218 | 4.2218
2021-06-11 11:00 | 3.278 | 4.0593 | 4.1239 | 4.401 | 4.2902 | 4.5673 | 1.8948 | 2.8702 | 3.4171 | 3.4171 | 3.7818 | 3.7818 | 2019-08-09 | 1.3946 | 2.3932 | 4.0449 | 4.0449 | 4.0449 | 4.0449
2021-06-11 12:00 | 3.1637 | 3.9177 | 3.9801 | 4.2475 | 4.1406 | 4.408 | 1.9748 | 2.9914 | 3.5615 | 3.5615 | 3.9415 | 3.9415 | 2019-08-09 01:00 | 1.2346 | 2.1186 | 3.5808 | 3.5808 | 3.5808 | 3.5808
2021-06-11 13:00 | 3.198 | 3.9602 | 4.0233 | 4.2936 | 4.1855 | 4.4558 | 1.9434 | 2.9438 | 3.5048 | 3.5048 | 3.8787 | 3.8787 | 2019-08-09 02:00 | 1.2041 | 2.0663 | 3.4923 | 3.4923 | 3.4923 | 3.4923
2021-06-11 14:00 | 3.238 | 4.0097 | 4.0736 | 4.3473 | 4.2378 | 4.5115 | 1.9662 | 2.9784 | 3.546 | 3.546 | 3.9244 | 3.9244 | 2019-08-09 03:00 | 1.1813 | 2.027 | 3.426 | 3.426 | 3.426 | 3.426
2021-06-11 15:00 | 3.1751 | 3.9319 | 3.9945 | 4.2629 | 4.1555 | 4.4239 | 1.9376 | 2.9352 | 3.4945 | 3.4945 | 3.8673 | 3.8673 | 2019-08-09 04:00 | 1.2651 | 2.1709 | 3.6692 | 3.6692 | 3.6692 | 3.6692
2021-06-11 16:00 | 3.3494 | 4.1477 | 4.2138 | 4.4969 | 4.3837 | 4.6668 | 2.2577 | 3.42 | 4.0717 | 4.0717 | 4.5062 | 4.5062 | 2019-08-09 05:00 | 1.5394 | 2.6417 | 4.4649 | 4.4649 | 4.4649 | 4.4649
2021-06-11 17:00 | 3.6667 | 4.5406 | 4.6129 | 4.9229 | 4.7989 | 5.1088 | 2.3692 | 3.5889 | 4.2727 | 4.2727 | 4.7286 | 4.7286 | 2019-08-09 06:00 | 1.7223 | 2.9556 | 4.9954 | 4.9954 | 4.9954 | 4.9954
2021-06-11 18:00 | 3.6381 | 4.5052 | 4.5769 | 4.8845 | 4.7615 | 5.069 | 2.4778 | 3.7534 | 4.4686 | 4.4686 | 4.9454 | 4.9454 | 2019-08-09 07:00 | 2.0653 | 3.5441 | 5.99 | 5.99 | 5.99 | 5.99
2021-06-11 19:00 | 3.4723 | 4.2999 | 4.3684 | 4.6619 | 4.5445 | 4.8381 | 2.4892 | 3.7707 | 4.4892 | 4.4892 | 4.9682 | 4.9682 | 2019-08-09 08:00 | 2.2634 | 3.8841 | 6.5647 | 6.5647 | 6.5647 | 6.5647
2021-06-11 20:00 | 3.2951 | 4.0805 | 4.1455 | 4.424 | 4.3126 | 4.5912 | 2.5578 | 3.8746 | 4.6129 | 4.6129 | 5.1051 | 5.1051 | 2019-08-09 09:00 | 2.1949 | 3.7664 | 6.3658 | 6.3658 | 6.3658 | 6.3658
2021-06-11 21:00 | 3.0579 | 3.7868 | 3.8471 | 4.1056 | 4.0022 | 4.2607 | 2.3149 | 3.5066 | 4.1748 | 4.1748 | 4.6203 | 4.6203 | 2019-08-09 10:00 | 2.1872 | 3.7533 | 6.3437 | 6.3437 | 6.3437 | 6.3437
2021-06-11 22:00 | 2.6798 | 3.3185 | 3.3713 | 3.5979 | 3.5072 | 3.7338 | 2.1291 | 3.2252 | 3.8398 | 3.8398 | 4.2495 | 4.2495 | 2019-08-09 11:00 | 2.0196 | 3.4656 | 5.8574 | 5.8574 | 5.8574 | 5.8574
2021-06-11 23:00 | 2.4749 | 3.0648 | 3.1136 | 3.3228 | 3.2391 | 3.4484 | 1.7947 | 2.7187 | 3.2368 | 3.2368 | 3.5821 | 3.5821 | 2019-08-09 12:00 | 2.0805 | 3.5702 | 6.0343 | 6.0343 | 6.0343 | 6.0343
2021-06-12 | 2.058 | 2.5485 | 2.5891 | 2.7631 | 2.6935 | 2.8674 | 1.5604 | 2.3637 | 2.8141 | 2.8141 | 3.1144 | 3.1144 | 2019-08-09 13:00 | 2.0805 | 3.5702 | 6.0343 | 6.0343 | 6.0343 | 6.0343
2021-06-12 01:00 | 1.8805 | 2.3287 | 2.3658 | 2.5247 | 2.4611 | 2.6201 | 1.3861 | 2.0996 | 2.4997 | 2.4997 | 2.7664 | 2.7664 | 2019-08-09 14:00 | 2.0424 | 3.5048 | 5.9237 | 5.9237 | 5.9237 | 5.9237
2021-06-12 02:00 | 1.8519 | 2.2933 | 2.3298 | 2.4864 | 2.4237 | 2.5803 | 1.2575 | 1.9048 | 2.2678 | 2.2678 | 2.5098 | 2.5098 | 2019-08-09 15:00 | 2.0501 | 3.5179 | 5.9458 | 5.9458 | 5.9458 | 5.9458
2021-06-12 03:00 | 1.809 | 2.2402 | 2.2759 | 2.4288 | 2.3676 | 2.5206 | 1.2232 | 1.8529 | 2.2059 | 2.2059 | 2.4413 | 2.4413 | 2019-08-09 16:00 | 2.1872 | 3.7533 | 6.3437 | 6.3437 | 6.3437 | 6.3437
2021-06-12 04:00 | 1.8363 | 2.274 | 2.3102 | 2.4654 | 2.4033 | 2.5586 | 1.1832 | 1.7923 | 2.1338 | 2.1338 | 2.3615 | 2.3615 | 2019-08-09 17:00 | 2.1796 | 3.7402 | 6.3216 | 6.3216 | 6.3216 | 6.3216
2021-06-12 05:00 | 2.0405 | 2.5269 | 2.5671 | 2.7396 | 2.6706 | 2.8431 | 1.2232 | 1.8529 | 2.2059 | 2.2059 | 2.4413 | 2.4413 | 2019-08-09 18:00 | 2.172 | 3.7271 | 6.2995 | 6.2995 | 6.2995 | 6.2995
2021-06-12 06:00 | 2.2732 | 2.815 | 2.8598 | 3.052 | 2.9751 | 3.1673 | 1.4518 | 2.1992 | 2.6183 | 2.6183 | 2.8976 | 2.8976 | 2019-08-09 19:00 | 1.9815 | 3.4002 | 5.7469 | 5.7469 | 5.7469 | 5.7469
2021-06-12 07:00 | 2.5635 | 3.1745 | 3.2251 | 3.4418 | 3.3551 | 3.5718 | 1.6285 | 2.4669 | 2.9369 | 2.9369 | 3.2503 | 3.2503 | 2019-08-09 20:00 | 1.8595 | 3.191 | 5.3932 | 5.3932 | 5.3932 | 5.3932
2021-06-12 08:00 | 2.8064 | 3.4753 | 3.5307 | 3.7679 | 3.673 | 3.9103 | 1.8462 | 2.7966 | 3.3295 | 3.3295 | 3.6848 | 3.6848 | 2019-08-09 21:00 | 1.8595 | 3.191 | 5.3932 | 5.3932 | 5.3932 | 5.3932
2021-06-12 09:00 | 2.9636 | 3.67 | 3.7284 | 3.979 | 3.8787 | 4.1293 | 2.1034 | 3.1862 | 3.7934 | 3.7934 | 4.1982 | 4.1982 | 2019-08-09 22:00 | 1.7147 | 2.9425 | 4.9733 | 4.9733 | 4.9733 | 4.9733
2021-06-12 10:00 | 3.1008 | 3.8398 | 3.901 | 4.1631 | 4.0583 | 4.3204 | 2.2063 | 3.3421 | 3.9789 | 3.9789 | 4.4035 | 4.4035 | 2019-08-09 23:00 | 1.6157 | 2.7725 | 4.6859 | 4.6859 | 4.6859 | 4.6859
2021-06-12 11:00 | 3.1094 | 3.8505 | 3.9118 | 4.1746 | 4.0695 | 4.3323 | 2.2291 | 3.3767 | 4.0202 | 4.0202 | 4.4491 | 4.4491 | 2019-08-10 | 1.4023 | 2.4063 | 4.067 | 4.067 | 4.067 | 4.067
2021-06-12 12:00 | 3.1665 | 3.9212 | 3.9837 | 4.2514 | 4.1443 | 4.412 | 2.3692 | 3.5889 | 4.2727 | 4.2727 | 4.7286 | 4.7286 | 2019-08-10 01:00 | 1.387 | 2.3801 | 4.0228 | 4.0228 | 4.0228 | 4.0228
2021-06-12 13:00 | 3.0788 | 3.8125 | 3.8733 | 4.1335 | 4.0294 | 4.2897 | 2.3263 | 3.5239 | 4.1954 | 4.1954 | 4.6431 | 4.6431 | 2019-08-10 02:00 | 1.3108 | 2.2494 | 3.8018 | 3.8018 | 3.8018 | 3.8018
2021-06-12 14:00 | 3.0294 | 3.7514 | 3.8111 | 4.0672 | 3.9648 | 4.2209 | 2.3835 | 3.6105 | 4.2985 | 4.2985 | 4.7572 | 4.7572 | 2019-08-10 03:00 | 1.2346 | 2.1186 | 3.5808 | 3.5808 | 3.5808 | 3.5808
2021-06-12 15:00 | 2.8236 | 3.4966 | 3.5523 | 3.7909 | 3.6955 | 3.9342 | 2.3006 | 3.485 | 4.149 | 4.149 | 4.5917 | 4.5917 | 2019-08-10 04:00 | 1.2346 | 2.1186 | 3.5808 | 3.5808 | 3.5808 | 3.5808
2021-06-12 16:00 | 2.8779 | 3.5638 | 3.6206 | 3.8638 | 3.7665 | 4.0098 | 2.4321 | 3.6841 | 4.3861 | 4.3861 | 4.8541 | 4.8541 | 2019-08-10 05:00 | 1.4632 | 2.5109 | 4.2439 | 4.2439 | 4.2439 | 4.2439
2021-06-12 17:00 | 3.1465 | 3.8965 | 3.9585 | 4.2245 | 4.1181 | 4.3841 | 2.5635 | 3.8832 | 4.6232 | 4.6232 | 5.1165 | 5.1165 | 2019-08-10 06:00 | 1.6233 | 2.7855 | 4.708 | 4.708 | 4.708 | 4.708
2021-06-12 18:00 | 3.1808 | 3.9389 | 4.0017 | 4.2706 | 4.163 | 4.4319 | 2.5092 | 3.801 | 4.5253 | 4.5253 | 5.0081 | 5.0081 | 2019-08-10 07:00 | 1.7147 | 2.9425 | 4.9733 | 4.9733 | 4.9733 | 4.9733
2021-06-12 19:00 | 3.0751 | 3.808 | 3.8686 | 4.1286 | 4.0246 | 4.2846 | 2.4321 | 3.6841 | 4.3861 | 4.3861 | 4.8541 | 4.8541 | 2019-08-10 08:00 | 1.8519 | 3.1779 | 5.3711 | 5.3711 | 5.3711 | 5.3711
2021-06-12 20:00 | 2.9065 | 3.5992 | 3.6565 | 3.9022 | 3.8039 | 4.0496 | 2.2863 | 3.4633 | 4.1233 | 4.1233 | 4.5632 | 4.5632 | 2019-08-10 09:00 | 1.8671 | 3.204 | 5.4154 | 5.4154 | 5.4154 | 5.4154
2021-06-12 21:00 | 2.7093 | 3.355 | 3.4084 | 3.6375 | 3.5459 | 3.7749 | 2.1977 | 3.3291 | 3.9635 | 3.9635 | 4.3864 | 4.3864 | 2019-08-10 10:00 | 1.9053 | 3.2694 | 5.5259 | 5.5259 | 5.5259 | 5.5259
2021-06-12 22:00 | 2.4525 | 3.037 | 3.0853 | 3.2927 | 3.2097 | 3.417 | 1.9862 | 3.0087 | 3.5821 | 3.5821 | 3.9643 | 3.9643 | 2019-08-10 11:00 | 1.9053 | 3.2694 | 5.5259 | 5.5259 | 5.5259 | 5.5259
2021-06-12 23:00 | 2.4035 | 2.9763 | 3.0237 | 3.2269 | 3.1456 | 3.3488 | 1.769 | 2.6797 | 3.1904 | 3.1904 | 3.5308 | 3.5308 | 2019-08-10 12:00 | 1.8671 | 3.204 | 5.4154 | 5.4154 | 5.4154 | 5.4154
2021-06-13 | 2.0119 | 2.4915 | 2.5312 | 2.7012 | 2.6332 | 2.8033 | 1.537 | 2.3282 | 2.7719 | 2.7719 | 3.0676 | 3.0676 | 2019-08-10 13:00 | 1.9662 | 3.374 | 5.7027 | 5.7027 | 5.7027 | 5.7027
2021-06-13 01:00 | 1.9033 | 2.357 | 2.3945 | 2.5554 | 2.4911 | 2.652 | 1.4061 | 2.1299 | 2.5358 | 2.5358 | 2.8064 | 2.8064 | 2019-08-10 14:00 | 1.9967 | 3.4264 | 5.7911 | 5.7911 | 5.7911 | 5.7911
2021-06-13 02:00 | 1.8691 | 2.3145 | 2.3514 | 2.5094 | 2.4462 | 2.6042 | 1.286 | 1.9481 | 2.3193 | 2.3193 | 2.5668 | 2.5668 | 2019-08-10 15:00 | 1.9815 | 3.4002 | 5.7469 | 5.7469 | 5.7469 | 5.7469
2021-06-13 03:00 | 1.8378 | 2.2758 | 2.312 | 2.4674 | 2.4052 | 2.5606 | 1.2375 | 1.8745 | 2.2317 | 2.2317 | 2.4698 | 2.4698 | 2019-08-10 16:00 | 2.0119 | 3.4525 | 5.8353 | 5.8353 | 5.8353 | 5.8353
2021-06-13 04:00 | 1.8576 | 2.3004 | 2.337 | 2.494 | 2.4312 | 2.5883 | 1.2289 | 1.8616 | 2.2163 | 2.2163 | 2.4528 | 2.4528 | 2019-08-10 17:00 | 1.9281 | 3.3087 | 5.5922 | 5.5922 | 5.5922 | 5.5922
2021-06-13 05:00 | 1.9793 | 2.4511 | 2.4901 | 2.6574 | 2.5905 | 2.7578 | 1.2346 | 1.8702 | 2.2266 | 2.2266 | 2.4641 | 2.4641 | 2019-08-10 18:00 | 1.9205 | 3.2956 | 5.5701 | 5.5701 | 5.5701 | 5.5701
2021-06-13 06:00 | 2.2118 | 2.739 | 2.7827 | 2.9696 | 2.8948 | 3.0818 | 1.3432 | 2.0347 | 2.4224 | 2.4224 | 2.6809 | 2.6809 | 2019-08-10 19:00 | 1.7833 | 3.0602 | 5.1722 | 5.1722 | 5.1722 | 5.1722
2021-06-13 07:00 | 2.4792 | 3.0702 | 3.1191 | 3.3286 | 3.2448 | 3.4544 | 1.6604 | 2.5152 | 2.9945 | 2.9945 | 3.314 | 3.314 | 2019-08-10 20:00 | 1.7223 | 2.9556 | 4.9954 | 4.9954 | 4.9954 | 4.9954
2021-06-13 08:00 | 2.5807 | 3.1957 | 3.2466 | 3.4648 | 3.3775 | 3.5957 | 1.7404 | 2.6364 | 3.1388 | 3.1388 | 3.4737 | 3.4737 | 2019-08-10 21:00 | 1.6004 | 2.7463 | 4.6417 | 4.6417 | 4.6417 | 4.6417
2021-06-13 09:00 | 2.5464 | 3.1533 | 3.2035 | 3.4188 | 3.3327 | 3.5479 | 1.8605 | 2.8183 | 3.3553 | 3.3553 | 3.7133 | 3.7133 | 2019-08-10 22:00 | 1.6004 | 2.7463 | 4.6417 | 4.6417 | 4.6417 | 4.6417
2021-06-13 10:00 | 2.4121 | 2.9869 | 3.0345 | 3.2384 | 3.1569 | 3.3608 | 1.9662 | 2.9784 | 3.546 | 3.546 | 3.9244 | 3.9244 | 2019-08-10 23:00 | 1.4861 | 2.5501 | 4.3102 | 4.3102 | 4.3102 | 4.3102
2021-06-13 11:00 | 2.1606 | 2.6755 | 2.7181 | 2.9008 | 2.8277 | 3.0103 | 1.9348 | 2.9308 | 3.4893 | 3.4893 | 3.8616 | 3.8616 | 2019-08-11 | 1.4023 | 2.4063 | 4.067 | 4.067 | 4.067 | 4.067
2021-06-13 12:00 | 2.0091 | 2.4879 | 2.5276 | 2.6974 | 2.6295 | 2.7993 | 1.8833 | 2.8529 | 3.3965 | 3.3965 | 3.7589 | 3.7589 | 2019-08-11 01:00 | 1.3108 | 2.2494 | 3.8018 | 3.8018 | 3.8018 | 3.8018
2021-06-13 13:00 | 1.9719 | 2.4419 | 2.4808 | 2.6475 | 2.5808 | 2.7475 | 1.8576 | 2.8139 | 3.3501 | 3.3501 | 3.7076 | 3.7076 | 2019-08-11 02:00 | 1.2194 | 2.0924 | 3.5366 | 3.5366 | 3.5366 | 3.5366
2021-06-13 14:00 | 2.0234 | 2.5056 | 2.5455 | 2.7166 | 2.6482 | 2.8192 | 1.8776 | 2.8442 | 3.3862 | 3.3862 | 3.7475 | 3.7475 | 2019-08-11 03:00 | 1.2041 | 2.0663 | 3.4923 | 3.4923 | 3.4923 | 3.4923
2021-06-13 15:00 | 2.1491 | 2.6613 | 2.7037 | 2.8854 | 2.8127 | 2.9944 | 1.9033 | 2.8832 | 3.4326 | 3.4326 | 3.7989 | 3.7989 | 2019-08-11 04:00 | 1.2041 | 2.0663 | 3.4923 | 3.4923 | 3.4923 | 3.4923
2021-06-13 16:00 | 2.5921 | 3.2099 | 3.261 | 3.4801 | 3.3925 | 3.6116 | 2.2034 | 3.3378 | 3.9738 | 3.9738 | 4.3978 | 4.3978 | 2019-08-11 05:00 | 1.3794 | 2.3671 | 4.0007 | 4.0007 | 4.0007 | 4.0007
2021-06-13 17:00 | 3.0322 | 3.7549 | 3.8147 | 4.071 | 3.9685 | 4.2248 | 2.2977 | 3.4806 | 4.1439 | 4.1439 | 4.586 | 4.586 | 2019-08-11 06:00 | 1.4785 | 2.5371 | 4.2881 | 4.2881 | 4.2881 | 4.2881
2021-06-13 18:00 | 3.0208 | 3.7408 | 3.8003 | 4.0557 | 3.9535 | 4.2089 | 2.3949 | 3.6278 | 4.3191 | 4.3191 | 4.78 | 4.78 | 2019-08-11 07:00 | 1.7071 | 2.9294 | 4.9512 | 4.9512 | 4.9512 | 4.9512
2021-06-13 19:00 | 2.9636 | 3.67 | 3.7284 | 3.979 | 3.8787 | 4.1293 | 2.3149 | 3.5066 | 4.1748 | 4.1748 | 4.6203 | 4.6203 | 2019-08-11 08:00 | 1.9357 | 3.3217 | 5.6143 | 5.6143 | 5.6143 | 5.6143
2021-06-13 20:00 | 2.7493 | 3.4045 | 3.4588 | 3.6912 | 3.5982 | 3.8306 | 2.1949 | 3.3248 | 3.9583 | 3.9583 | 4.3807 | 4.3807 | 2019-08-11 09:00 | 2.0501 | 3.5179 | 5.9458 | 5.9458 | 5.9458 | 5.9458
2021-06-13 21:00 | 2.6264 | 3.2524 | 3.3042 | 3.5262 | 3.4374 | 3.6594 | 2.0863 | 3.1603 | 3.7625 | 3.7625 | 4.1639 | 4.1639 | 2019-08-11 10:00 | 1.9205 | 3.2956 | 5.5701 | 5.5701 | 5.5701 | 5.5701
2021-06-13 22:00 | 2.3892 | 2.9586 | 3.0058 | 3.2077 | 3.1269 | 3.3289 | 1.849 | 2.8009 | 3.3347 | 3.3347 | 3.6905 | 3.6905 | 2019-08-11 11:00 | 1.951 | 3.3479 | 5.6585 | 5.6585 | 5.6585 | 5.6585
2021-06-13 23:00 | 2.3349 | 2.8914 | 2.9374 | 3.1348 | 3.0559 | 3.2532 | 1.5976 | 2.42 | 2.8811 | 2.8811 | 3.1885 | 3.1885 | 2019-08-11 12:00 | 1.9357 | 3.3217 | 5.6143 | 5.6143 | 5.6143 | 5.6143
2021-06-14 | 1.9838 | 2.4566 | 2.4957 | 2.6634 | 2.5964 | 2.7641 | 1.3546 | 2.052 | 2.443 | 2.443 | 2.7037 | 2.7037 | 2019-08-11 13:00 | 1.8138 | 3.1125 | 5.2606 | 5.2606 | 5.2606 | 5.2606
2021-06-14 01:00 | 1.8519 | 2.2933 | 2.3298 | 2.4864 | 2.4237 | 2.5803 | 1.2089 | 1.8312 | 2.1802 | 2.1802 | 2.4128 | 2.4128 | 2019-08-11 14:00 | 1.9357 | 3.3217 | 5.6143 | 5.6143 | 5.6143 | 5.6143
2021-06-14 02:00 | 1.7433 | 2.1588 | 2.1932 | 2.3406 | 2.2816 | 2.429 | 1.1031 | 1.671 | 1.9895 | 1.9895 | 2.2017 | 2.2017 | 2019-08-11 15:00 | 1.9815 | 3.4002 | 5.7469 | 5.7469 | 5.7469 | 5.7469
2021-06-14 03:00 | 1.7176 | 2.127 | 2.1608 | 2.306 | 2.2479 | 2.3931 | 1.0946 | 1.6581 | 1.974 | 1.974 | 2.1846 | 2.1846 | 2019-08-11 16:00 | 2.0119 | 3.4525 | 5.8353 | 5.8353 | 5.8353 | 5.8353
2021-06-14 04:00 | 1.7859 | 2.2115 | 2.2468 | 2.3977 | 2.3373 | 2.4883 | 1.0803 | 1.6364 | 1.9482 | 1.9482 | 2.1561 | 2.1561 | 2019-08-11 17:00 | 2.0196 | 3.4656 | 5.8574 | 5.8574 | 5.8574 | 5.8574
2021-06-14 05:00 | 1.9291 | 2.3888 | 2.4269 | 2.59 | 2.5247 | 2.6878 | 1.1517 | 1.7446 | 2.0771 | 2.0771 | 2.2987 | 2.2987 | 2019-08-11 18:00 | 2.0196 | 3.4656 | 5.8574 | 5.8574 | 5.8574 | 5.8574
2021-06-14 06:00 | 2.2834 | 2.8277 | 2.8727 | 3.0657 | 2.9885 | 3.1816 | 1.266 | 1.9178 | 2.2832 | 2.2832 | 2.5269 | 2.5269 | 2019-08-11 19:00 | 1.89 | 3.2433 | 5.4817 | 5.4817 | 5.4817 | 5.4817
2021-06-14 07:00 | 2.4949 | 3.0896 | 3.1388 | 3.3497 | 3.2653 | 3.4762 | 1.4404 | 2.1819 | 2.5976 | 2.5976 | 2.8748 | 2.8748 | 2019-08-11 20:00 | 1.8443 | 3.1648 | 5.349 | 5.349 | 5.349 | 5.349
2021-06-14 08:00 | 2.8865 | 3.5744 | 3.6314 | 3.8754 | 3.7778 | 4.0218 | 1.7547 | 2.6581 | 3.1646 | 3.1646 | 3.5023 | 3.5023 | 2019-08-11 21:00 | 1.7986 | 3.0863 | 5.2164 | 5.2164 | 5.2164 | 5.2164
2021-06-14 09:00 | 2.9979 | 3.7124 | 3.7716 | 4.025 | 3.9236 | 4.177 | 1.8691 | 2.8313 | 3.3708 | 3.3708 | 3.7304 | 3.7304 | 2019-08-11 22:00 | 1.608 | 2.7594 | 4.6638 | 4.6638 | 4.6638 | 4.6638
2021-06-14 10:00 | 2.9865 | 3.6983 | 3.7572 | 4.0096 | 3.9087 | 4.1611 | 2.0377 | 3.0867 | 3.6748 | 3.6748 | 4.067 | 4.067 | 2019-08-11 23:00 | 1.3413 | 2.3017 | 3.8902 | 3.8902 | 3.8902 | 3.8902
2021-06-14 11:00 | 2.8807 | 3.5673 | 3.6242 | 3.8677 | 3.7703 | 4.0138 | 2.0777 | 3.1473 | 3.747 | 3.747 | 4.1468 | 4.1468 | 2019-08-12 | 1.3108 | 2.2494 | 3.8018 | 3.8018 | 3.8018 | 3.8018
2021-06-14 12:00 | 2.6407 | 3.2701 | 3.3221 | 3.5454 | 3.4561 | 3.6793 | 2.0348 | 3.0823 | 3.6697 | 3.6697 | 4.0613 | 4.0613 | 2019-08-12 01:00 | 1.1889 | 2.0401 | 3.4481 | 3.4481 | 3.4481 | 3.4481
2021-06-14 13:00 | 2.6178 | 3.2418 | 3.2934 | 3.5147 | 3.4262 | 3.6475 | 2.0548 | 3.1126 | 3.7058 | 3.7058 | 4.1012 | 4.1012 | 2019-08-12 02:00 | 1.1813 | 2.027 | 3.426 | 3.426 | 3.426 | 3.426
2021-06-14 14:00 | 2.5692 | 3.1816 | 3.2323 | 3.4494 | 3.3626 | 3.5798 | 1.9977 | 3.0261 | 3.6027 | 3.6027 | 3.9871 | 3.9871 | 2019-08-12 03:00 | 1.1584 | 1.9878 | 3.3597 | 3.3597 | 3.3597 | 3.3597
2021-06-14 15:00 | 2.6664 | 3.3019 | 3.3545 | 3.5799 | 3.4897 | 3.7151 | 2.0977 | 3.1776 | 3.7831 | 3.7831 | 4.1867 | 4.1867 | 2019-08-12 04:00 | 1.2879 | 2.2101 | 3.7355 | 3.7355 | 3.7355 | 3.7355
2021-06-14 16:00 | 2.9636 | 3.67 | 3.7284 | 3.979 | 3.8787 | 4.1293 | 2.2577 | 3.42 | 4.0717 | 4.0717 | 4.5062 | 4.5062 | 2019-08-12 05:00 | 1.4785 | 2.5371 | 4.2881 | 4.2881 | 4.2881 | 4.2881
2021-06-14 17:00 | 3.398 | 4.2079 | 4.2749 | 4.5622 | 4.4473 | 4.7345 | 2.3944 | 3.6271 | 4.3183 | 4.3183 | 4.779 | 4.779 | 2019-08-12 06:00 | 1.7376 | 2.9817 | 5.0396 | 5.0396 | 5.0396 | 5.0396
2021-06-14 18:00 | 3.5752 | 4.4273 | 4.4978 | 4.8001 | 4.6792 | 4.9814 | 2.5092 | 3.801 | 4.5253 | 4.5253 | 5.0081 | 5.0081 | 2019-08-12 07:00 | 1.9967 | 3.4264 | 5.7911 | 5.7911 | 5.7911 | 5.7911
2021-06-14 19:00 | 3.4352 | 4.2539 | 4.3217 | 4.6121 | 4.4959 | 4.7863 | 2.5149 | 3.8096 | 4.5356 | 4.5356 | 5.0195 | 5.0195 | 2019-08-12 08:00 | 2.0882 | 3.5833 | 6.0564 | 6.0564 | 6.0564 | 6.0564
2021-06-14 20:00 | 3.2466 | 4.0203 | 4.0844 | 4.3588 | 4.249 | 4.5235 | 2.3778 | 3.6018 | 4.2882 | 4.2882 | 4.7457 | 4.7457 | 2019-08-12 09:00 | 2.1644 | 3.7141 | 6.2774 | 6.2774 | 6.2774 | 6.2774
2021-06-14 21:00 | 2.9093 | 3.6027 | 3.6601 | 3.906 | 3.8077 | 4.0536 | 2.2102 | 3.348 | 3.986 | 3.986 | 4.4113 | 4.4113 | 2019-08-12 10:00 | 2.1415 | 3.6748 | 6.2111 | 6.2111 | 6.2111 | 6.2111
2021-06-14 22:00 | 2.5092 | 3.1073 | 3.1568 | 3.3689 | 3.284 | 3.4961 | 1.9662 | 2.9784 | 3.546 | 3.546 | 3.9244 | 3.9244 | 2019-08-12 11:00 | 2.0805 | 3.5702 | 6.0343 | 6.0343 | 6.0343 | 6.0343
2021-06-14 23:00 | 2.3292 | 2.8843 | 2.9302 | 3.1271 | 3.0484 | 3.2453 | 1.6072 | 2.4345 | 2.8984 | 2.8984 | 3.2077 | 3.2077 | 2019-08-12 12:00 | 2.0653 | 3.5441 | 5.99 | 5.99 | 5.99 | 5.99
2021-06-15 | 1.9882 | 2.4621 | 2.5013 | 2.6694 | 2.6021 | 2.7702 | 1.3832 | 2.0953 | 2.4946 | 2.4946 | 2.7607 | 2.7607 | 2019-08-12 13:00 | 2.0805 | 3.5702 | 6.0343 | 6.0343 | 6.0343 | 6.0343
2021-06-15 01:00 | 1.9062 | 2.3605 | 2.3981 | 2.5593 | 2.4948 | 2.6559 | 1.2087 | 1.831 | 2.1799 | 2.1799 | 2.4125 | 2.4125 | 2019-08-12 14:00 | 2.0196 | 3.4656 | 5.8574 | 5.8574 | 5.8574 | 5.8574
2021-06-15 02:00 | 1.7852 | 2.2107 | 2.2459 | 2.3968 | 2.3365 | 2.4874 | 1.1461 | 1.7361 | 2.0669 | 2.0669 | 2.2875 | 2.2875 | 2019-08-12 15:00 | 2.1644 | 3.7141 | 6.2774 | 6.2774 | 6.2774 | 6.2774
2021-06-15 03:00 | 1.7947 | 2.2225 | 2.2579 | 2.4096 | 2.3489 | 2.5007 | 1.0403 | 1.5758 | 1.8761 | 1.8761 | 2.0763 | 2.0763 | 2019-08-12 16:00 | 2.0043 | 3.4394 | 5.8132 | 5.8132 | 5.8132 | 5.8132
2021-06-15 04:00 | 1.8319 | 2.2685 | 2.3046 | 2.4595 | 2.3976 | 2.5524 | 1.0962 | 1.6605 | 1.9769 | 1.9769 | 2.1878 | 2.1878 | 2019-08-12 17:00 | 2.2025 | 3.7795 | 6.3879 | 6.3879 | 6.3879 | 6.3879
2021-06-15 05:00 | 2.2547 | 2.7921 | 2.8366 | 3.0272 | 2.951 | 3.1416 | 1.1374 | 1.723 | 2.0513 | 2.0513 | 2.2701 | 2.2701 | 2019-08-12 18:00 | 2.1949 | 3.7664 | 6.3658 | 6.3658 | 6.3658 | 6.3658
2021-06-15 06:00 | 3.3609 | 4.1619 | 4.2282 | 4.5123 | 4.3987 | 4.6828 | 1.529 | 2.3161 | 2.7574 | 2.7574 | 3.0516 | 3.0516 | 2019-08-12 19:00 | 2.1339 | 3.6618 | 6.189 | 6.189 | 6.189 | 6.189
2021-06-15 07:00 | 3.8038 | 4.7104 | 4.7855 | 5.107 | 4.9784 | 5.3 | 1.8376 | 2.7836 | 3.3141 | 3.3141 | 3.6677 | 3.6677 | 2019-08-12 20:00 | 1.9815 | 3.4002 | 5.7469 | 5.7469 | 5.7469 | 5.7469
2021-06-15 08:00 | 3.8639 | 4.7848 | 4.861 | 5.1876 | 5.057 | 5.3836 | 1.829 | 2.7706 | 3.2986 | 3.2986 | 3.6506 | 3.6506 | 2019-08-12 21:00 | 1.8748 | 3.2171 | 5.4375 | 5.4375 | 5.4375 | 5.4375
2021-06-15 09:00 | 3.7724 | 4.6715 | 4.7459 | 5.0648 | 4.9373 | 5.2562 | 1.8062 | 2.736 | 3.2574 | 3.2574 | 3.6049 | 3.6049 | 2019-08-12 22:00 | 1.669 | 2.864 | 4.8407 | 4.8407 | 4.8407 | 4.8407
2021-06-15 10:00 | 3.5695 | 4.4202 | 4.4907 | 4.7924 | 4.6717 | 4.9734 | 1.7976 | 2.723 | 3.2419 | 3.2419 | 3.5878 | 3.5878 | 2019-08-12 23:00 | 1.448 | 2.4848 | 4.1997 | 4.1997 | 4.1997 | 4.1997
2021-06-15 11:00 | 3.4437 | 4.2645 | 4.3325 | 4.6236 | 4.5071 | 4.7982 | 1.8005 | 2.7274 | 3.2471 | 3.2471 | 3.5935 | 3.5935 | 2019-08-13 | 1.2727 | 2.184 | 3.6913 | 3.6913 | 3.6913 | 3.6913
2021-06-15 12:00 | 3.0722 | 3.8045 | 3.8651 | 4.1248 | 4.0209 | 4.2806 | 1.7376 | 2.6321 | 3.1337 | 3.1337 | 3.468 | 3.468 | 2019-08-13 01:00 | 1.2498 | 2.1447 | 3.625 | 3.625 | 3.625 | 3.625
2021-06-15 13:00 | 2.7607 | 3.4187 | 3.4732 | 3.7065 | 3.6132 | 3.8465 | 1.6947 | 2.5672 | 3.0564 | 3.0564 | 3.3825 | 3.3825 | 2019-08-13 02:00 | 1.1736 | 2.014 | 3.4039 | 3.4039 | 3.4039 | 3.4039
2021-06-15 14:00 | 2.8607 | 3.5426 | 3.599 | 3.8408 | 3.7441 | 3.9859 | 1.6169 | 2.4492 | 2.9159 | 2.9159 | 3.2271 | 3.2271 | 2019-08-13 03:00 | 1.1736 | 2.014 | 3.4039 | 3.4039 | 3.4039 | 3.4039
2021-06-15 15:00 | 2.8036 | 3.4718 | 3.5271 | 3.7641 | 3.6693 | 3.9063 | 1.6576 | 2.5109 | 2.9894 | 2.9894 | 3.3083 | 3.3083 | 2019-08-13 04:00 | 1.2346 | 2.1186 | 3.5808 | 3.5808 | 3.5808 | 3.5808
2021-06-15 16:00 | 3.1351 | 3.8823 | 3.9442 | 4.2092 | 4.1032 | 4.3682 | 1.9296 | 2.923 | 3.48 | 3.48 | 3.8513 | 3.8513 | 2019-08-13 05:00 | 1.5623 | 2.6809 | 4.5312 | 4.5312 | 4.5312 | 4.5312
2021-06-15 17:00 | 3.7353 | 4.6255 | 4.6992 | 5.0149 | 4.8886 | 5.2044 | 2.252 | 3.4114 | 4.0614 | 4.0614 | 4.4948 | 4.4948 | 2019-08-13 06:00 | 1.6995 | 2.9163 | 4.9291 | 4.9291 | 4.9291 | 4.9291
2021-06-15 18:00 | 3.8924 | 4.8202 | 4.8969 | 5.226 | 5.0944 | 5.4234 | 2.5121 | 3.8053 | 4.5304 | 4.5304 | 5.0138 | 5.0138 | 2019-08-13 07:00 | 1.9967 | 3.4264 | 5.7911 | 5.7911 | 5.7911 | 5.7911
2021-06-15 19:00 | 3.7171 | 4.603 | 4.6763 | 4.9905 | 4.8649 | 5.1791 | 2.5349 | 3.8399 | 4.5717 | 4.5717 | 5.0595 | 5.0595 | 2019-08-13 08:00 | 2.0882 | 3.5833 | 6.0564 | 6.0564 | 6.0564 | 6.0564
2021-06-15 20:00 | 3.6238 | 4.4875 | 4.559 | 4.8653 | 4.7428 | 5.0491 | 2.4463 | 3.7057 | 4.4119 | 4.4119 | 4.8826 | 4.8826 | 2019-08-13 09:00 | 2.1644 | 3.7141 | 6.2774 | 6.2774 | 6.2774 | 6.2774
2021-06-15 21:00 | 3.3066 | 4.0947 | 4.1599 | 4.4394 | 4.3276 | 4.6071 | 2.312 | 3.5023 | 4.1696 | 4.1696 | 4.6146 | 4.6146 | 2019-08-13 10:00 | 2.0958 | 3.5964 | 6.0785 | 6.0785 | 6.0785 | 6.0785
2021-06-15 22:00 | 2.8064 | 3.4753 | 3.5307 | 3.7679 | 3.673 | 3.9103 | 2.0119 | 3.0477 | 3.6285 | 3.6285 | 4.0156 | 4.0156 | 2019-08-13 11:00 | 2.0501 | 3.5179 | 5.9458 | 5.9458 | 5.9458 | 5.9458
2021-06-15 23:00 | 2.4291 | 3.0081 | 3.056 | 3.2613 | 3.1792 | 3.3845 | 1.7519 | 2.6538 | 3.1594 | 3.1594 | 3.4966 | 3.4966 | 2019-08-13 12:00 | 2.0729 | 3.5571 | 6.0121 | 6.0121 | 6.0121 | 6.0121
2021-06-16 | 2.1132 | 2.6168 | 2.6585 | 2.8372 | 2.7657 | 2.9443 | 1.3918 | 2.1083 | 2.51 | 2.51 | 2.7779 | 2.7779 | 2019-08-13 13:00 | 2.0729 | 3.5571 | 6.0121 | 6.0121 | 6.0121 | 6.0121
2021-06-16 01:00 | 2.0034 | 2.4809 | 2.5204 | 2.6897 | 2.622 | 2.7913 | 1.2889 | 1.9524 | 2.3245 | 2.3245 | 2.5725 | 2.5725 | 2019-08-13 14:00 | 2.0653 | 3.5441 | 5.99 | 5.99 | 5.99 | 5.99
2021-06-16 02:00 | 1.9348 | 2.3959 | 2.4341 | 2.5976 | 2.5322 | 2.6958 | 1.2175 | 1.8442 | 2.1956 | 2.1956 | 2.4299 | 2.4299 | 2019-08-13 15:00 | 1.9967 | 3.4264 | 5.7911 | 5.7911 | 5.7911 | 5.7911
2021-06-16 03:00 | 1.8862 | 2.3358 | 2.373 | 2.5324 | 2.4686 | 2.6281 | 1.1174 | 1.6927 | 2.0152 | 2.0152 | 2.2303 | 2.2303 | 2019-08-13 16:00 | 2.0882 | 3.5833 | 6.0564 | 6.0564 | 6.0564 | 6.0564
2021-06-16 04:00 | 1.9603 | 2.4275 | 2.4662 | 2.6319 | 2.5656 | 2.7313 | 1.1431 | 1.7317 | 2.0616 | 2.0616 | 2.2816 | 2.2816 | 2019-08-13 17:00 | 2.111 | 3.6225 | 6.1227 | 6.1227 | 6.1227 | 6.1227
2021-06-16 05:00 | 2.3487 | 2.9084 | 2.9548 | 3.1533 | 3.0739 | 3.2724 | 1.3089 | 1.9827 | 2.3606 | 2.3606 | 2.6124 | 2.6124 | 2019-08-13 18:00 | 2.111 | 3.6225 | 6.1227 | 6.1227 | 6.1227 | 6.1227
2021-06-16 06:00 | 3.3723 | 4.1761 | 4.2426 | 4.5276 | 4.4136 | 4.6987 | 1.649 | 2.4979 | 2.9739 | 2.9739 | 3.2912 | 3.2912 | 2019-08-13 19:00 | 2.0958 | 3.5964 | 6.0785 | 6.0785 | 6.0785 | 6.0785
2021-06-16 07:00 | 4.0868 | 5.0608 | 5.1414 | 5.4869 | 5.3487 | 5.6942 | 2.112 | 3.1992 | 3.8089 | 3.8089 | 4.2153 | 4.2153 | 2019-08-13 20:00 | 1.951 | 3.3479 | 5.6585 | 5.6585 | 5.6585 | 5.6585
2021-06-16 08:00 | 4.0782 | 5.0502 | 5.1306 | 5.4754 | 5.3375 | 5.6822 | 2.1606 | 3.2728 | 3.8965 | 3.8965 | 4.3122 | 4.3122 | 2019-08-13 21:00 | 1.9357 | 3.3217 | 5.6143 | 5.6143 | 5.6143 | 5.6143
2021-06-16 09:00 | 3.9496 | 4.8909 | 4.9688 | 5.3027 | 5.1692 | 5.503 | 1.9548 | 2.9611 | 3.5254 | 3.5254 | 3.9015 | 3.9015 | 2019-08-13 22:00 | 1.7376 | 2.9817 | 5.0396 | 5.0396 | 5.0396 | 5.0396
2021-06-16 10:00 | 3.9382 | 4.8768 | 4.9545 | 5.2874 | 5.1542 | 5.4871 | 1.9491 | 2.9525 | 3.5151 | 3.5151 | 3.8901 | 3.8901 | 2019-08-13 23:00 | 1.4556 | 2.4978 | 4.2218 | 4.2218 | 4.2218 | 4.2218
2021-06-16 11:00 | 3.6438 | 4.5123 | 4.5841 | 4.8922 | 4.7689 | 5.077 | 1.8862 | 2.8572 | 3.4017 | 3.4017 | 3.7647 | 3.7647 | 2019-08-14 | 1.3718 | 2.354 | 3.9786 | 3.9786 | 3.9786 | 3.9786
2021-06-16 12:00 | 3.7495 | 4.6432 | 4.7172 | 5.0341 | 4.9073 | 5.2243 | 1.9519 | 2.9568 | 3.5202 | 3.5202 | 3.8958 | 3.8958 | 2019-08-14 01:00 | 1.2727 | 2.184 | 3.6913 | 3.6913 | 3.6913 | 3.6913
2021-06-16 13:00 | 3.6867 | 4.5653 | 4.6381 | 4.9497 | 4.8251 | 5.1367 | 1.9605 | 2.9698 | 3.5357 | 3.5357 | 3.913 | 3.913 | 2019-08-14 02:00 | 1.2498 | 2.1447 | 3.625 | 3.625 | 3.625 | 3.625
2021-06-16 14:00 | 3.6124 | 4.4733 | 4.5446 | 4.8499 | 4.7278 | 5.0332 | 1.9919 | 3.0174 | 3.5924 | 3.5924 | 3.9757 | 3.9757 | 2019-08-14 03:00 | 1.2498 | 2.1447 | 3.625 | 3.625 | 3.625 | 3.625
2021-06-16 15:00 | 3.6352 | 4.5016 | 4.5733 | 4.8806 | 4.7577 | 5.065 | 2.1205 | 3.2122 | 3.8243 | 3.8243 | 4.2324 | 4.2324 | 2019-08-14 04:00 | 1.2498 | 2.1447 | 3.625 | 3.625 | 3.625 | 3.625
2021-06-16 16:00 | 3.8953 | 4.8237 | 4.9005 | 5.2298 | 5.0981 | 5.4274 | 2.4721 | 3.7447 | 4.4583 | 4.4583 | 4.934 | 4.934 | 2019-08-14 05:00 | 1.5928 | 2.7332 | 4.6196 | 4.6196 | 4.6196 | 4.6196
2021-06-16 17:00 | 4.2697 | 5.2873 | 5.3715 | 5.7325 | 5.5881 | 5.949 | 2.5064 | 3.7967 | 4.5201 | 4.5201 | 5.0024 | 5.0024 | 2019-08-14 06:00 | 1.7833 | 3.0602 | 5.1722 | 5.1722 | 5.1722 | 5.1722
2021-06-16 18:00 | 4.2611 | 5.2767 | 5.3607 | 5.7209 | 5.5769 | 5.9371 | 2.7207 | 4.1213 | 4.9067 | 4.9067 | 5.4302 | 5.4302 | 2019-08-14 07:00 | 2.0119 | 3.4525 | 5.8353 | 5.8353 | 5.8353 | 5.8353
2021-06-16 19:00 | 4.0996 | 5.0767 | 5.1576 | 5.5042 | 5.3655 | 5.7121 | 2.6721 | 4.0477 | 4.8191 | 4.8191 | 5.3333 | 5.3333 | 2019-08-14 08:00 | 2.3015 | 3.9495 | 6.6753 | 6.6753 | 6.6753 | 6.6753
2021-06-16 20:00 | 3.5466 | 4.3919 | 4.4619 | 4.7617 | 4.6418 | 4.9416 | 2.5178 | 3.814 | 4.5407 | 4.5407 | 5.0252 | 5.0252 | 2019-08-14 09:00 | 2.2558 | 3.871 | 6.5426 | 6.5426 | 6.5426 | 6.5426
2021-06-16 21:00 | 3.138 | 3.8859 | 3.9477 | 4.213 | 4.1069 | 4.3722 | 2.3749 | 3.5975 | 4.283 | 4.283 | 4.74 | 4.74 | 2019-08-14 10:00 | 2.2634 | 3.8841 | 6.5647 | 6.5647 | 6.5647 | 6.5647
2021-06-16 22:00 | 2.6521 | 3.2842 | 3.3365 | 3.5607 | 3.471 | 3.6952 | 2.0377 | 3.0867 | 3.6748 | 3.6748 | 4.067 | 4.067 | 2019-08-14 11:00 | 2.2177 | 3.8056 | 6.4321 | 6.4321 | 6.4321 | 6.4321
2021-06-16 23:00 | 2.5121 | 3.1108 | 3.1604 | 3.3727 | 3.2878 | 3.5001 | 1.7748 | 2.6885 | 3.2007 | 3.2007 | 3.5423 | 3.5423 | 2019-08-14 12:00 | 2.2101 | 3.7925 | 6.41 | 6.41 | 6.41 | 6.41
2021-06-17 | 2.1063 | 2.6083 | 2.6498 | 2.8279 | 2.7566 | 2.9347 | 1.4261 | 2.1602 | 2.5719 | 2.5719 | 2.8463 | 2.8463 | 2019-08-14 13:00 | 2.1796 | 3.7402 | 6.3216 | 6.3216 | 6.3216 | 6.3216
2021-06-17 01:00 | 1.9348 | 2.3959 | 2.4341 | 2.5976 | 2.5322 | 2.6958 | 1.3123 | 1.9878 | 2.3666 | 2.3666 | 2.6191 | 2.6191 | 2019-08-14 14:00 | 2.2025 | 3.7795 | 6.3879 | 6.3879 | 6.3879 | 6.3879
2021-06-17 02:00 | 1.8604 | 2.3039 | 2.3406 | 2.4978 | 2.4349 | 2.5922 | 1.1946 | 1.8096 | 2.1544 | 2.1544 | 2.3843 | 2.3843 | 2019-08-14 15:00 | 2.1415 | 3.6748 | 6.2111 | 6.2111 | 6.2111 | 6.2111
2021-06-17 03:00 | 1.9462 | 2.4101 | 2.4485 | 2.613 | 2.5472 | 2.7117 | 1.1889 | 1.8009 | 2.1441 | 2.1441 | 2.3729 | 2.3729 | 2019-08-14 16:00 | 2.1186 | 3.6356 | 6.1448 | 6.1448 | 6.1448 | 6.1448
2021-06-17 04:00 | 1.9604 | 2.4277 | 2.4663 | 2.6321 | 2.5658 | 2.7315 | 1.2289 | 1.8615 | 2.2162 | 2.2162 | 2.4527 | 2.4527 | 2019-08-14 17:00 | 2.2634 | 3.8841 | 6.5647 | 6.5647 | 6.5647 | 6.5647
2021-06-17 05:00 | 2.3692 | 2.9338 | 2.9806 | 3.1808 | 3.1007 | 3.301 | 1.3173 | 1.9954 | 2.3757 | 2.3757 | 2.6292 | 2.6292 | 2019-08-14 18:00 | 2.233 | 3.8318 | 6.4763 | 6.4763 | 6.4763 | 6.4763
2021-06-17 06:00 | 3.3884 | 4.196 | 4.2628 | 4.5492 | 4.4347 | 4.7211 | 1.629 | 2.4676 | 2.9378 | 2.9378 | 3.2513 | 3.2513 | 2019-08-14 19:00 | 2.172 | 3.7271 | 6.2995 | 6.2995 | 6.2995 | 6.2995
2021-06-17 07:00 | 4.0039 | 4.9582 | 5.0372 | 5.3756 | 5.2402 | 5.5787 | 2.0377 | 3.0867 | 3.6748 | 3.6748 | 4.067 | 4.067 | 2019-08-14 20:00 | 2.0119 | 3.4525 | 5.8353 | 5.8353 | 5.8353 | 5.8353
2021-06-17 08:00 | 4.1296 | 5.1139 | 5.1954 | 5.5444 | 5.4048 | 5.7539 | 2.0662 | 3.13 | 3.7264 | 3.7264 | 4.124 | 4.124 | 2019-08-14 21:00 | 1.8748 | 3.2171 | 5.4375 | 5.4375 | 5.4375 | 5.4375
2021-06-17 09:00 | 3.7867 | 4.6892 | 4.7639 | 5.084 | 4.956 | 5.2761 | 1.8348 | 2.7793 | 3.3089 | 3.3089 | 3.662 | 3.662 | 2019-08-14 22:00 | 1.7833 | 3.0602 | 5.1722 | 5.1722 | 5.1722 | 5.1722
2021-06-17 10:00 | 3.7324 | 4.622 | 4.6956 | 5.0111 | 4.8849 | 5.2004 | 1.9205 | 2.9092 | 3.4635 | 3.4635 | 3.8331 | 3.8331 | 2019-08-14 23:00 | 1.6004 | 2.7463 | 4.6417 | 4.6417 | 4.6417 | 4.6417
2021-06-17 11:00 | 3.5323 | 4.3742 | 4.4439 | 4.7425 | 4.6231 | 4.9217 | 2.0005 | 3.0304 | 3.6078 | 3.6078 | 3.9928 | 3.9928 | 2019-08-15 | 1.3565 | 2.3278 | 3.9344 | 3.9344 | 3.9344 | 3.9344
2021-06-17 12:00 | 3.3809 | 4.1867 | 4.2534 | 4.5392 | 4.4248 | 4.7106 | 1.9319 | 2.9265 | 3.4841 | 3.4841 | 3.8559 | 3.8559 | 2019-08-15 01:00 | 1.2194 | 2.0924 | 3.5366 | 3.5366 | 3.5366 | 3.5366
2021-06-17 13:00 | 3.4237 | 4.2398 | 4.3073 | 4.5967 | 4.4809 | 4.7704 | 1.9062 | 2.8875 | 3.4378 | 3.4378 | 3.8046 | 3.8046 | 2019-08-15 02:00 | 1.2041 | 2.0663 | 3.4923 | 3.4923 | 3.4923 | 3.4923
2021-06-17 14:00 | 3.4752 | 4.3035 | 4.372 | 4.6658 | 4.5483 | 4.842 | 2.0005 | 3.0304 | 3.6078 | 3.6078 | 3.9928 | 3.9928 | 2019-08-15 03:00 | 1.2498 | 2.1447 | 3.625 | 3.625 | 3.625 | 3.625
2021-06-17 15:00 | 3.4095 | 4.2221 | 4.2893 | 4.5775 | 4.4622 | 4.7504 | 1.9376 | 2.9352 | 3.4945 | 3.4945 | 3.8673 | 3.8673 | 2019-08-15 04:00 | 1.3184 | 2.2624 | 3.8239 | 3.8239 | 3.8239 | 3.8239
2021-06-17 16:00 | 3.8124 | 4.7211 | 4.7963 | 5.1185 | 4.9896 | 5.3119 | 2.1548 | 3.2642 | 3.8862 | 3.8862 | 4.3008 | 4.3008 | 2019-08-15 05:00 | 1.5394 | 2.6417 | 4.4649 | 4.4649 | 4.4649 | 4.4649
2021-06-17 17:00 | 4.1239 | 5.1068 | 5.1882 | 5.5368 | 5.3973 | 5.7459 | 2.4549 | 3.7187 | 4.4273 | 4.4273 | 4.8998 | 4.8998 | 2019-08-15 06:00 | 1.8062 | 3.0994 | 5.2385 | 5.2385 | 5.2385 | 5.2385
2021-06-17 18:00 | 4.1554 | 5.1457 | 5.2277 | 5.579 | 5.4385 | 5.7897 | 2.6921 | 4.078 | 4.8551 | 4.8551 | 5.3732 | 5.3732 | 2019-08-15 07:00 | 2.1491 | 3.6879 | 6.2332 | 6.2332 | 6.2332 | 6.2332
2021-06-17 19:00 | 4.0413 | 5.0045 | 5.0842 | 5.4258 | 5.2892 | 5.6308 | 2.6835 | 4.0651 | 4.8397 | 4.8397 | 5.3561 | 5.3561 | 2019-08-15 08:00 | 2.2863 | 3.9233 | 6.631 | 6.631 | 6.631 | 6.631
2021-06-17 20:00 | 3.7274 | 4.6158 | 4.6893 | 5.0044 | 4.8784 | 5.1934 | 2.5978 | 3.9352 | 4.685 | 4.685 | 5.185 | 5.185 | 2019-08-15 09:00 | 2.2482 | 3.8579 | 6.5205 | 6.5205 | 6.5205 | 6.5205
2021-06-17 21:00 | 3.4066 | 4.2185 | 4.2857 | 4.5737 | 4.4585 | 4.7465 | 2.4292 | 3.6798 | 4.381 | 4.381 | 4.8484 | 4.8484 | 2019-08-15 10:00 | 2.1491 | 3.6879 | 6.2332 | 6.2332 | 6.2332 | 6.2332
2021-06-17 22:00 | 2.7721 | 3.4329 | 3.4875 | 3.7219 | 3.6281 | 3.8625 | 2.0764 | 3.1454 | 3.7448 | 3.7448 | 4.1443 | 4.1443 | 2019-08-15 11:00 | 2.0424 | 3.5048 | 5.9237 | 5.9237 | 5.9237 | 5.9237
2021-06-17 23:00 | 2.5206 | 3.1214 | 3.1711 | 3.3842 | 3.299 | 3.5121 | 1.6886 | 2.558 | 3.0454 | 3.0454 | 3.3703 | 3.3703 | 2019-08-15 12:00 | 2.1491 | 3.6879 | 6.2332 | 6.2332 | 6.2332 | 6.2332
2021-06-18 | 2.132 | 2.6401 | 2.6822 | 2.8624 | 2.7903 | 2.9705 | 1.5328 | 2.3219 | 2.7643 | 2.7643 | 3.0593 | 3.0593 | 2019-08-15 13:00 | 2.1491 | 3.6879 | 6.2332 | 6.2332 | 6.2332 | 6.2332
2021-06-18 01:00 | 2.092 | 2.5906 | 2.6318 | 2.8087 | 2.7379 | 2.9148 | 1.3008 | 1.9705 | 2.3459 | 2.3459 | 2.5963 | 2.5963 | 2019-08-15 14:00 | 2.1034 | 3.6094 | 6.1006 | 6.1006 | 6.1006 | 6.1006
2021-06-18 02:00 | 2.0005 | 2.4773 | 2.5168 | 2.6859 | 2.6182 | 2.7874 | 1.266 | 1.9178 | 2.2832 | 2.2832 | 2.5269 | 2.5269 | 2019-08-15 15:00 | 1.9738 | 3.3871 | 5.7248 | 5.7248 | 5.7248 | 5.7248
2021-06-18 03:00 | 1.9161 | 2.3728 | 2.4106 | 2.5725 | 2.5077 | 2.6697 | 1.246 | 1.8875 | 2.2472 | 2.2472 | 2.4869 | 2.4869 | 2019-08-15 16:00 | 2.0882 | 3.5833 | 6.0564 | 6.0564 | 6.0564 | 6.0564
2021-06-18 04:00 | 1.9939 | 2.4692 | 2.5085 | 2.677 | 2.6096 | 2.7782 | 1.2546 | 1.9005 | 2.2626 | 2.2626 | 2.5041 | 2.5041 | 2019-08-15 17:00 | 2.1034 | 3.6094 | 6.1006 | 6.1006 | 6.1006 | 6.1006
2021-06-18 05:00 | 2.3978 | 2.9692 | 3.0165 | 3.2192 | 3.1382 | 3.3408 | 1.3454 | 2.0381 | 2.4264 | 2.4264 | 2.6853 | 2.6853 | 2019-08-15 18:00 | 2.1644 | 3.7141 | 6.2774 | 6.2774 | 6.2774 | 6.2774
2021-06-18 06:00 | 3.3752 | 4.1796 | 4.2462 | 4.5315 | 4.4174 | 4.7027 | 1.7519 | 2.6538 | 3.1594 | 3.1594 | 3.4966 | 3.4966 | 2019-08-15 19:00 | 2.1644 | 3.7141 | 6.2774 | 6.2774 | 6.2774 | 6.2774
2021-06-18 07:00 | 4.0125 | 4.9688 | 5.0479 | 5.3871 | 5.2515 | 5.5906 | 2.0517 | 3.1079 | 3.7001 | 3.7001 | 4.0949 | 4.0949 | 2019-08-15 20:00 | 1.9586 | 3.361 | 5.6806 | 5.6806 | 5.6806 | 5.6806
2021-06-18 08:00 | 4.1325 | 5.1174 | 5.1989 | 5.5483 | 5.4085 | 5.7579 | 2.0748 | 3.143 | 3.7419 | 3.7419 | 4.1411 | 4.1411 | 2019-08-15 21:00 | 1.8519 | 3.1779 | 5.3711 | 5.3711 | 5.3711 | 5.3711
2021-06-18 09:00 | 3.6009 | 4.4592 | 4.5302 | 4.8346 | 4.7128 | 5.0172 | 1.769 | 2.6797 | 3.1904 | 3.1904 | 3.5308 | 3.5308 | 2019-08-15 22:00 | 1.7452 | 2.9948 | 5.0617 | 5.0617 | 5.0617 | 5.0617
2021-06-18 10:00 | 3.3637 | 4.1654 | 4.2318 | 4.5161 | 4.4024 | 4.6867 | 1.7576 | 2.6624 | 3.1697 | 3.1697 | 3.508 | 3.508 | 2019-08-15 23:00 | 1.5242 | 2.6155 | 4.4207 | 4.4207 | 4.4207 | 4.4207
2021-06-18 11:00 | 3.0779 | 3.8115 | 3.8722 | 4.1324 | 4.0284 | 4.2885 | 1.8262 | 2.7663 | 3.2934 | 3.2934 | 3.6449 | 3.6449 | 2019-08-16 | 1.3413 | 2.3017 | 3.8902 | 3.8902 | 3.8902 | 3.8902
2021-06-18 12:00 | 3.1637 | 3.9177 | 3.9801 | 4.2475 | 4.1406 | 4.408 | 1.9691 | 2.9828 | 3.5512 | 3.5512 | 3.9301 | 3.9301 | 2019-08-16 01:00 | 1.2346 | 2.1186 | 3.5808 | 3.5808 | 3.5808 | 3.5808
2021-06-18 13:00 | 3.2265 | 3.9956 | 4.0592 | 4.332 | 4.2229 | 4.4956 | 1.8862 | 2.8572 | 3.4017 | 3.4017 | 3.7647 | 3.7647 | 2019-08-16 02:00 | 1.166 | 2.0009 | 3.3818 | 3.3818 | 3.3818 | 3.3818
2021-06-18 14:00 | 3.1094 | 3.8505 | 3.9118 | 4.1746 | 4.0695 | 4.3323 | 1.9148 | 2.9005 | 3.4532 | 3.4532 | 3.8217 | 3.8217 | 2019-08-16 03:00 | 1.2117 | 2.0794 | 3.5144 | 3.5144 | 3.5144 | 3.5144
2021-06-18 15:00 | 3.1494 | 3.9 | 3.9621 | 4.2284 | 4.1219 | 4.3881 | 1.9376 | 2.9352 | 3.4945 | 3.4945 | 3.8673 | 3.8673 | 2019-08-16 04:00 | 1.2956 | 2.2232 | 3.7576 | 3.7576 | 3.7576 | 3.7576
2021-06-18 16:00 | 3.6267 | 4.491 | 4.5626 | 4.8691 | 4.7465 | 5.0531 | 2.1491 | 3.2555 | 3.8759 | 3.8759 | 4.2894 | 4.2894 | 2019-08-16 05:00 | 1.4327 | 2.4586 | 4.1555 | 4.1555 | 4.1555 | 4.1555
2021-06-18 17:00 | 3.8496 | 4.7671 | 4.843 | 5.1684 | 5.0383 | 5.3637 | 2.4235 | 3.6711 | 4.3706 | 4.3706 | 4.837 | 4.837 | 2019-08-16 06:00 | 1.8062 | 3.0994 | 5.2385 | 5.2385 | 5.2385 | 5.2385
2021-06-18 18:00 | 3.8153 | 4.7246 | 4.7999 | 5.1224 | 4.9934 | 5.3159 | 2.5892 | 3.9222 | 4.6696 | 4.6696 | 5.1678 | 5.1678 | 2019-08-16 07:00 | 2.0805 | 3.5702 | 6.0343 | 6.0343 | 6.0343 | 6.0343
2021-06-18 19:00 | 3.5922 | 4.4484 | 4.5192 | 4.8229 | 4.7014 | 5.0051 | 2.5692 | 3.8919 | 4.6335 | 4.6335 | 5.1279 | 5.1279 | 2019-08-16 08:00 | 2.2025 | 3.7795 | 6.3879 | 6.3879 | 6.3879 | 6.3879
2021-06-18 20:00 | 3.3209 | 4.1124 | 4.1779 | 4.4586 | 4.3463 | 4.627 | 2.5407 | 3.8486 | 4.582 | 4.582 | 5.0709 | 5.0709 | 2019-08-16 09:00 | 2.1491 | 3.6879 | 6.2332 | 6.2332 | 6.2332 | 6.2332
2021-06-18 21:00 | 3.0922 | 3.8292 | 3.8902 | 4.1516 | 4.0471 | 4.3085 | 2.4235 | 3.6711 | 4.3706 | 4.3706 | 4.837 | 4.837 | 2019-08-16 10:00 | 1.9891 | 3.4133 | 5.769 | 5.769 | 5.769 | 5.769
2021-06-18 22:00 | 2.6178 | 3.2418 | 3.2934 | 3.5147 | 3.4262 | 3.6475 | 2.2949 | 3.4763 | 4.1387 | 4.1387 | 4.5803 | 4.5803 | 2019-08-16 11:00 | 2.0272 | 3.4787 | 5.8795 | 5.8795 | 5.8795 | 5.8795
2021-06-18 23:00 | 2.4063 | 2.9799 | 3.0273 | 3.2307 | 3.1494 | 3.3528 | 1.6954 | 2.5682 | 3.0575 | 3.0575 | 3.3838 | 3.3838 | 2019-08-16 12:00 | 1.9967 | 3.4264 | 5.7911 | 5.7911 | 5.7911 | 5.7911
2021-06-19 | 2.0977 | 2.5976 | 2.639 | 2.8163 | 2.7454 | 2.9227 | 1.5175 | 2.2988 | 2.7368 | 2.7368 | 3.0288 | 3.0288 | 2019-08-16 13:00 | 2.0882 | 3.5833 | 6.0564 | 6.0564 | 6.0564 | 6.0564
2021-06-19 01:00 | 1.9405 | 2.403 | 2.4413 | 2.6053 | 2.5397 | 2.7037 | 1.3346 | 2.0217 | 2.4069 | 2.4069 | 2.6638 | 2.6638 | 2019-08-16 14:00 | 2.0119 | 3.4525 | 5.8353 | 5.8353 | 5.8353 | 5.8353
2021-06-19 02:00 | 1.8548 | 2.2968 | 2.3334 | 2.4902 | 2.4275 | 2.5843 | 1.2432 | 1.8832 | 2.242 | 2.242 | 2.4812 | 2.4812 | 2019-08-16 15:00 | 2.0805 | 3.5702 | 6.0343 | 6.0343 | 6.0343 | 6.0343
2021-06-19 03:00 | 1.8119 | 2.2437 | 2.2795 | 2.4326 | 2.3714 | 2.5245 | 1.1282 | 1.709 | 2.0346 | 2.0346 | 2.2517 | 2.2517 | 2019-08-16 16:00 | 2.1491 | 3.6879 | 6.2332 | 6.2332 | 6.2332 | 6.2332
2021-06-19 04:00 | 1.8148 | 2.2473 | 2.2831 | 2.4365 | 2.3751 | 2.5285 | 1.2489 | 1.8918 | 2.2523 | 2.2523 | 2.4927 | 2.4927 | 2019-08-16 17:00 | 2.111 | 3.6225 | 6.1227 | 6.1227 | 6.1227 | 6.1227
2021-06-19 05:00 | 2.0186 | 2.4998 | 2.5396 | 2.7102 | 2.642 | 2.8126 | 1.2489 | 1.8918 | 2.2523 | 2.2523 | 2.4927 | 2.4927 | 2019-08-16 18:00 | 2.0424 | 3.5048 | 5.9237 | 5.9237 | 5.9237 | 5.9237
2021-06-19 06:00 | 2.3092 | 2.8595 | 2.9051 | 3.1003 | 3.0222 | 3.2174 | 1.4861 | 2.2511 | 2.6801 | 2.6801 | 2.9661 | 2.9661 | 2019-08-16 19:00 | 1.9738 | 3.3871 | 5.7248 | 5.7248 | 5.7248 | 5.7248
2021-06-19 07:00 | 2.815 | 3.4859 | 3.5415 | 3.7794 | 3.6842 | 3.9222 | 1.6372 | 2.4801 | 2.9527 | 2.9527 | 3.2677 | 3.2677 | 2019-08-16 20:00 | 1.8062 | 3.0994 | 5.2385 | 5.2385 | 5.2385 | 5.2385
2021-06-19 08:00 | 2.9579 | 3.6629 | 3.7212 | 3.9713 | 3.8713 | 4.1213 | 1.8976 | 2.8745 | 3.4223 | 3.4223 | 3.7875 | 3.7875 | 2019-08-16 21:00 | 1.8062 | 3.0994 | 5.2385 | 5.2385 | 5.2385 | 5.2385
2021-06-19 09:00 | 2.8636 | 3.5461 | 3.6026 | 3.8447 | 3.7478 | 3.9899 | 1.9977 | 3.0261 | 3.6027 | 3.6027 | 3.9871 | 3.9871 | 2019-08-16 22:00 | 1.6461 | 2.8248 | 4.7743 | 4.7743 | 4.7743 | 4.7743
2021-06-19 10:00 | 2.8522 | 3.532 | 3.5882 | 3.8293 | 3.7329 | 3.974 | 2.072 | 3.1386 | 3.7367 | 3.7367 | 4.1354 | 4.1354 | 2019-08-16 23:00 | 1.5013 | 2.5763 | 4.3544 | 4.3544 | 4.3544 | 4.3544
2021-06-19 11:00 | 2.5807 | 3.1957 | 3.2466 | 3.4648 | 3.3775 | 3.5957 | 2.1177 | 3.2079 | 3.8192 | 3.8192 | 4.2267 | 4.2267 | 2019-08-17 | 1.3261 | 2.2755 | 3.846 | 3.846 | 3.846 | 3.846
2021-06-19 12:00 | 2.4235 | 3.0011 | 3.0489 | 3.2538 | 3.1718 | 3.3767 | 2.0748 | 3.143 | 3.7419 | 3.7419 | 4.1411 | 4.1411 | 2019-08-17 01:00 | 1.2422 | 2.1317 | 3.6029 | 3.6029 | 3.6029 | 3.6029
2021-06-19 13:00 | 2.3349 | 2.8914 | 2.9374 | 3.1348 | 3.0559 | 3.2532 | 1.9919 | 3.0174 | 3.5924 | 3.5924 | 3.9757 | 3.9757 | 2019-08-17 02:00 | 1.1736 | 2.014 | 3.4039 | 3.4039 | 3.4039 | 3.4039
2021-06-19 14:00 | 2.4492 | 3.0329 | 3.0813 | 3.2883 | 3.2055 | 3.4125 | 2.0062 | 3.0391 | 3.6182 | 3.6182 | 4.0042 | 4.0042 | 2019-08-17 03:00 | 1.2194 | 2.0924 | 3.5366 | 3.5366 | 3.5366 | 3.5366
2021-06-19 15:00 | 2.4806 | 3.0719 | 3.1208 | 3.3305 | 3.2466 | 3.4563 | 2.112 | 3.1992 | 3.8089 | 3.8089 | 4.2153 | 4.2153 | 2019-08-17 04:00 | 1.2422 | 2.1317 | 3.6029 | 3.6029 | 3.6029 | 3.6029
2021-06-19 16:00 | 2.8979 | 3.5886 | 3.6457 | 3.8907 | 3.7927 | 4.0377 | 2.3663 | 3.5845 | 4.2676 | 4.2676 | 4.7229 | 4.7229 | 2019-08-17 05:00 | 1.3489 | 2.3148 | 3.9123 | 3.9123 | 3.9123 | 3.9123
2021-06-19 17:00 | 3.2694 | 4.0486 | 4.1131 | 4.3895 | 4.279 | 4.5553 | 2.4921 | 3.775 | 4.4943 | 4.4943 | 4.9739 | 4.9739 | 2019-08-17 06:00 | 1.4327 | 2.4586 | 4.1555 | 4.1555 | 4.1555 | 4.1555
2021-06-19 18:00 | 3.2923 | 4.077 | 4.1419 | 4.4202 | 4.3089 | 4.5872 | 2.4435 | 3.7014 | 4.4067 | 4.4067 | 4.8769 | 4.8769 | 2019-08-17 07:00 | 1.6842 | 2.8902 | 4.8849 | 4.8849 | 4.8849 | 4.8849
2021-06-19 19:00 | 3.1608 | 3.9142 | 3.9765 | 4.2437 | 4.1368 | 4.404 | 2.3435 | 3.5499 | 4.2263 | 4.2263 | 4.6773 | 4.6773 | 2019-08-17 08:00 | 1.829 | 3.1386 | 5.3048 | 5.3048 | 5.3048 | 5.3048
2021-06-19 20:00 | 3.0751 | 3.808 | 3.8686 | 4.1286 | 4.0246 | 4.2846 | 2.232 | 3.3811 | 4.0253 | 4.0253 | 4.4548 | 4.4548 | 2019-08-17 09:00 | 1.8214 | 3.1256 | 5.2827 | 5.2827 | 5.2827 | 5.2827
2021-06-19 21:00 | 2.6607 | 3.2948 | 3.3473 | 3.5722 | 3.4823 | 3.7072 | 2.1949 | 3.3248 | 3.9583 | 3.9583 | 4.3807 | 4.3807 | 2019-08-17 10:00 | 1.8519 | 3.1779 | 5.3711 | 5.3711 | 5.3711 | 5.3711
2021-06-19 22:00 | 2.4835 | 3.0754 | 3.1244 | 3.3343 | 3.2504 | 3.4603 | 2.0405 | 3.091 | 3.68 | 3.68 | 4.0727 | 4.0727 | 2019-08-17 11:00 | 1.8595 | 3.191 | 5.3932 | 5.3932 | 5.3932 | 5.3932
2021-06-19 23:00 | 2.2749 | 2.8171 | 2.8619 | 3.0542 | 2.9773 | 3.1696 | 1.7204 | 2.6061 | 3.1027 | 3.1027 | 3.4337 | 3.4337 | 2019-08-17 12:00 | 1.8671 | 3.204 | 5.4154 | 5.4154 | 5.4154 | 5.4154
2021-06-20 | 2.132 | 2.6401 | 2.6822 | 2.8624 | 2.7903 | 2.9705 | 1.4461 | 2.1905 | 2.608 | 2.608 | 2.8862 | 2.8862 | 2019-08-17 13:00 | 1.7757 | 3.0471 | 5.1501 | 5.1501 | 5.1501 | 5.1501
2021-06-20 01:00 | 1.8633 | 2.3074 | 2.3442 | 2.5017 | 2.4387 | 2.5962 | 1.2803 | 1.9394 | 2.309 | 2.309 | 2.5554 | 2.5554 | 2019-08-17 14:00 | 1.7757 | 3.0471 | 5.1501 | 5.1501 | 5.1501 | 5.1501
2021-06-20 02:00 | 1.8405 | 2.2791 | 2.3154 | 2.471 | 2.4088 | 2.5644 | 1.2232 | 1.8529 | 2.2059 | 2.2059 | 2.4413 | 2.4413 | 2019-08-17 15:00 | 1.8214 | 3.1256 | 5.2827 | 5.2827 | 5.2827 | 5.2827
2021-06-20 03:00 | 1.7976 | 2.226 | 2.2615 | 2.4135 | 2.3527 | 2.5046 | 1.1517 | 1.7446 | 2.0771 | 2.0771 | 2.2987 | 2.2987 | 2019-08-17 16:00 | 1.8671 | 3.204 | 5.4154 | 5.4154 | 5.4154 | 5.4154
2021-06-20 04:00 | 1.8262 | 2.2614 | 2.2975 | 2.4518 | 2.3901 | 2.5445 | 1.1517 | 1.7446 | 2.0771 | 2.0771 | 2.2987 | 2.2987 | 2019-08-17 17:00 | 1.7986 | 3.0863 | 5.2164 | 5.2164 | 5.2164 | 5.2164
2021-06-20 05:00 | 1.9119 | 2.3676 | 2.4053 | 2.5669 | 2.5023 | 2.6639 | 1.1974 | 1.8138 | 2.1595 | 2.1595 | 2.3899 | 2.3899 | 2019-08-17 18:00 | 1.8214 | 3.1256 | 5.2827 | 5.2827 | 5.2827 | 5.2827
2021-06-20 06:00 | 2.2156 | 2.7436 | 2.7873 | 2.9746 | 2.8997 | 3.087 | 1.4032 | 2.1256 | 2.5306 | 2.5306 | 2.8007 | 2.8007 | 2019-08-17 19:00 | 1.7757 | 3.0471 | 5.1501 | 5.1501 | 5.1501 | 5.1501
2021-06-20 07:00 | 2.3806 | 2.948 | 2.995 | 3.1962 | 3.1157 | 3.317 | 1.5375 | 2.3291 | 2.7729 | 2.7729 | 3.0688 | 3.0688 | 2019-08-17 20:00 | 1.8062 | 3.0994 | 5.2385 | 5.2385 | 5.2385 | 5.2385
2021-06-20 08:00 | 2.5549 | 3.1639 | 3.2143 | 3.4303 | 3.3439 | 3.5598 | 1.729 | 2.6191 | 3.1182 | 3.1182 | 3.4509 | 3.4509 | 2019-08-17 21:00 | 1.6614 | 2.8509 | 4.8186 | 4.8186 | 4.8186 | 4.8186
2021-06-20 09:00 | 2.5321 | 3.1356 | 3.1855 | 3.3996 | 3.3139 | 3.528 | 1.8033 | 2.7317 | 3.2522 | 3.2522 | 3.5992 | 3.5992 | 2019-08-17 22:00 | 1.5394 | 2.6417 | 4.4649 | 4.4649 | 4.4649 | 4.4649
2021-06-20 10:00 | 2.53 | 3.1331 | 3.183 | 3.3968 | 3.3113 | 3.5252 | 2.072 | 3.1386 | 3.7367 | 3.7367 | 4.1354 | 4.1354 | 2019-08-17 23:00 | 1.3565 | 2.3278 | 3.9344 | 3.9344 | 3.9344 | 3.9344
2021-06-20 11:00 | 2.5521 | 3.1604 | 3.2107 | 3.4264 | 3.3401 | 3.5559 | 2.1891 | 3.3161 | 3.948 | 3.948 | 4.3693 | 4.3693 | 2019-08-18 | 1.3108 | 2.2494 | 3.8018 | 3.8018 | 3.8018 | 3.8018
2021-06-20 12:00 | 2.2349 | 2.7675 | 2.8116 | 3.0005 | 2.925 | 3.1139 | 2.0748 | 3.143 | 3.7419 | 3.7419 | 4.1411 | 4.1411 | 2019-08-18 01:00 | 1.1889 | 2.0401 | 3.4481 | 3.4481 | 3.4481 | 3.4481
2021-06-20 13:00 | 2.392 | 2.9622 | 3.0093 | 3.2116 | 3.1307 | 3.3329 | 2.092 | 3.1689 | 3.7728 | 3.7728 | 4.1753 | 4.1753 | 2019-08-18 02:00 | 1.1736 | 2.014 | 3.4039 | 3.4039 | 3.4039 | 3.4039
2021-06-20 14:00 | 2.392 | 2.9622 | 3.0093 | 3.2116 | 3.1307 | 3.3329 | 2.0662 | 3.13 | 3.7264 | 3.7264 | 4.124 | 4.124 | 2019-08-18 03:00 | 1.2041 | 2.0663 | 3.4923 | 3.4923 | 3.4923 | 3.4923
2021-06-20 15:00 | 2.4549 | 3.04 | 3.0884 | 3.296 | 3.213 | 3.4205 | 2.0748 | 3.143 | 3.7419 | 3.7419 | 4.1411 | 4.1411 | 2019-08-18 04:00 | 1.227 | 2.1055 | 3.5587 | 3.5587 | 3.5587 | 3.5587
2021-06-20 16:00 | 2.8429 | 3.5205 | 3.5765 | 3.8169 | 3.7207 | 3.961 | 2.3377 | 3.5412 | 4.216 | 4.216 | 4.6659 | 4.6659 | 2019-08-18 05:00 | 1.2879 | 2.2101 | 3.7355 | 3.7355 | 3.7355 | 3.7355
2021-06-20 17:00 | 3.2151 | 3.9814 | 4.0448 | 4.3166 | 4.2079 | 4.4797 | 2.6178 | 3.9655 | 4.7211 | 4.7211 | 5.2249 | 5.2249 | 2019-08-18 06:00 | 1.4099 | 2.4194 | 4.0891 | 4.0891 | 4.0891 | 4.0891
2021-06-20 18:00 | 3.2694 | 4.0486 | 4.1131 | 4.3895 | 4.279 | 4.5553 | 2.6721 | 4.0477 | 4.8191 | 4.8191 | 5.3333 | 5.3333 | 2019-08-18 07:00 | 1.6233 | 2.7855 | 4.708 | 4.708 | 4.708 | 4.708
2021-06-20 19:00 | 3.1665 | 3.9212 | 3.9837 | 4.2514 | 4.1443 | 4.412 | 2.6007 | 3.9395 | 4.6902 | 4.6902 | 5.1907 | 5.1907 | 2019-08-18 08:00 | 1.8062 | 3.0994 | 5.2385 | 5.2385 | 5.2385 | 5.2385
2021-06-20 20:00 | 3.0665 | 3.7974 | 3.8579 | 4.1171 | 4.0134 | 4.2726 | 2.4549 | 3.7187 | 4.4273 | 4.4273 | 4.8998 | 4.8998 | 2019-08-18 09:00 | 1.8824 | 3.2302 | 5.4596 | 5.4596 | 5.4596 | 5.4596
2021-06-20 21:00 | 2.7776 | 3.4396 | 3.4944 | 3.7292 | 3.6353 | 3.8701 | 2.2977 | 3.4806 | 4.1439 | 4.1439 | 4.586 | 4.586 | 2019-08-18 10:00 | 1.9053 | 3.2694 | 5.5259 | 5.5259 | 5.5259 | 5.5259
2021-06-20 22:00 | 2.4874 | 3.0802 | 3.1293 | 3.3396 | 3.2555 | 3.4657 | 1.9454 | 2.9469 | 3.5084 | 3.5084 | 3.8828 | 3.8828 | 2019-08-18 11:00 | 1.9053 | 3.2694 | 5.5259 | 5.5259 | 5.5259 | 5.5259
2021-06-20 23:00 | 2.3558 | 2.9172 | 2.9637 | 3.1628 | 3.0832 | 3.2823 | 1.649 | 2.4979 | 2.9739 | 2.9739 | 3.2912 | 3.2912 | 2019-08-18 12:00 | 1.8367 | 3.1517 | 5.3269 | 5.3269 | 5.3269 | 5.3269
2021-06-21 | 2.0262 | 2.5092 | 2.5491 | 2.7204 | 2.6519 | 2.8232 | 1.5014 | 2.2743 | 2.7077 | 2.7077 | 2.9966 | 2.9966 | 2019-08-18 13:00 | 1.8748 | 3.2171 | 5.4375 | 5.4375 | 5.4375 | 5.4375
2021-06-21 01:00 | 1.9148 | 2.3711 | 2.4089 | 2.5708 | 2.506 | 2.6679 | 1.2603 | 1.9091 | 2.2729 | 2.2729 | 2.5155 | 2.5155 | 2019-08-18 14:00 | 1.8824 | 3.2302 | 5.4596 | 5.4596 | 5.4596 | 5.4596
2021-06-21 02:00 | 1.9176 | 2.3747 | 2.4125 | 2.5746 | 2.5098 | 2.6719 | 1.2032 | 1.8226 | 2.1699 | 2.1699 | 2.4014 | 2.4014 | 2019-08-18 15:00 | 1.8519 | 3.1779 | 5.3711 | 5.3711 | 5.3711 | 5.3711
2021-06-21 03:00 | 1.9033 | 2.357 | 2.3945 | 2.5554 | 2.4911 | 2.652 | 1.1717 | 1.7749 | 2.1132 | 2.1132 | 2.3386 | 2.3386 | 2019-08-18 16:00 | 1.8671 | 3.204 | 5.4154 | 5.4154 | 5.4154 | 5.4154
2021-06-21 04:00 | 1.9719 | 2.4419 | 2.4808 | 2.6475 | 2.5808 | 2.7475 | 1.2089 | 1.8312 | 2.1802 | 2.1802 | 2.4128 | 2.4128 | 2019-08-18 17:00 | 1.9053 | 3.2694 | 5.5259 | 5.5259 | 5.5259 | 5.5259
2021-06-21 05:00 | 2.4073 | 2.9811 | 3.0286 | 3.2321 | 3.1507 | 3.3542 | 1.3778 | 2.0871 | 2.4848 | 2.4848 | 2.75 | 2.75 | 2019-08-18 18:00 | 1.9129 | 3.2825 | 5.548 | 5.548 | 5.548 | 5.548
2021-06-21 06:00 | 3.6038 | 4.4627 | 4.5338 | 4.8384 | 4.7166 | 5.0212 | 1.8005 | 2.7274 | 3.2471 | 3.2471 | 3.5935 | 3.5935 | 2019-08-18 19:00 | 1.8214 | 3.1256 | 5.2827 | 5.2827 | 5.2827 | 5.2827
2021-06-21 07:00 | 4.0982 | 5.075 | 5.1558 | 5.5022 | 5.3637 | 5.7101 | 2.1806 | 3.3031 | 3.9326 | 3.9326 | 4.3522 | 4.3522 | 2019-08-18 20:00 | 1.7452 | 2.9948 | 5.0617 | 5.0617 | 5.0617 | 5.0617
2021-06-21 08:00 | 4.2297 | 5.2378 | 5.3212 | 5.6787 | 5.5357 | 5.8933 | 2.1263 | 3.2209 | 3.8346 | 3.8346 | 4.2438 | 4.2438 | 2019-08-18 21:00 | 1.7071 | 2.9294 | 4.9512 | 4.9512 | 4.9512 | 4.9512
2021-06-21 09:00 | 3.7695 | 4.668 | 4.7423 | 5.061 | 4.9335 | 5.2522 | 1.9948 | 3.0217 | 3.5975 | 3.5975 | 3.9814 | 3.9814 | 2019-08-18 22:00 | 1.5699 | 2.694 | 4.5533 | 4.5533 | 4.5533 | 4.5533
2021-06-21 10:00 | 3.6495 | 4.5193 | 4.5913 | 4.8998 | 4.7764 | 5.0849 | 1.8348 | 2.7793 | 3.3089 | 3.3089 | 3.662 | 3.662 | 2019-08-18 23:00 | 1.448 | 2.4848 | 4.1997 | 4.1997 | 4.1997 | 4.1997
2021-06-21 11:00 | 3.378 | 4.1831 | 4.2498 | 4.5353 | 4.4211 | 4.7066 | 1.8948 | 2.8702 | 3.4171 | 3.4171 | 3.7818 | 3.7818 | 2019-08-19 | 1.2651 | 2.1709 | 3.6692 | 3.6692 | 3.6692 | 3.6692
2021-06-21 12:00 | 3.358 | 4.1584 | 4.2246 | 4.5085 | 4.3949 | 4.6788 | 1.9205 | 2.9092 | 3.4635 | 3.4635 | 3.8331 | 3.8331 | 2019-08-19 01:00 | 1.1965 | 2.0532 | 3.4702 | 3.4702 | 3.4702 | 3.4702
2021-06-21 13:00 | 3.3323 | 4.1265 | 4.1922 | 4.4739 | 4.3612 | 4.6429 | 1.8776 | 2.8442 | 3.3862 | 3.3862 | 3.7475 | 3.7475 | 2019-08-19 02:00 | 1.2651 | 2.1709 | 3.6692 | 3.6692 | 3.6692 | 3.6692
2021-06-21 14:00 | 3.2694 | 4.0486 | 4.1131 | 4.3895 | 4.279 | 4.5553 | 2.0119 | 3.0477 | 3.6285 | 3.6285 | 4.0156 | 4.0156 | 2019-08-19 03:00 | 1.166 | 2.0009 | 3.3818 | 3.3818 | 3.3818 | 3.3818
2021-06-21 15:00 | 3.198 | 3.9602 | 4.0233 | 4.2936 | 4.1855 | 4.4558 | 1.8319 | 2.775 | 3.3038 | 3.3038 | 3.6563 | 3.6563 | 2019-08-19 04:00 | 1.2498 | 2.1447 | 3.625 | 3.625 | 3.625 | 3.625
2021-06-21 16:00 | 3.5295 | 4.3707 | 4.4403 | 4.7387 | 4.6193 | 4.9177 | 2.072 | 3.1386 | 3.7367 | 3.7367 | 4.1354 | 4.1354 | 2019-08-19 05:00 | 1.4709 | 2.524 | 4.266 | 4.266 | 4.266 | 4.266
2021-06-21 17:00 | 4.1211 | 5.1033 | 5.1846 | 5.5329 | 5.3936 | 5.742 | 2.4006 | 3.6365 | 4.3294 | 4.3294 | 4.7914 | 4.7914 | 2019-08-19 06:00 | 1.8519 | 3.1779 | 5.3711 | 5.3711 | 5.3711 | 5.3711
2021-06-21 18:00 | 4.2925 | 5.3156 | 5.4003 | 5.7632 | 5.618 | 5.9809 | 2.6407 | 4.0001 | 4.7624 | 4.7624 | 5.2705 | 5.2705 | 2019-08-19 07:00 | 1.9967 | 3.4264 | 5.7911 | 5.7911 | 5.7911 | 5.7911
2021-06-21 19:00 | 4.2411 | 5.2519 | 5.3356 | 5.6941 | 5.5507 | 5.9092 | 2.7036 | 4.0954 | 4.8757 | 4.8757 | 5.396 | 5.396 | 2019-08-19 08:00 | 2.0882 | 3.5833 | 6.0564 | 6.0564 | 6.0564 | 6.0564
2021-06-21 20:00 | 3.8324 | 4.7458 | 4.8214 | 5.1454 | 5.0158 | 5.3398 | 2.5921 | 3.9265 | 4.6747 | 4.6747 | 5.1735 | 5.1735 | 2019-08-19 09:00 | 2.0729 | 3.5571 | 6.0121 | 6.0121 | 6.0121 | 6.0121
2021-06-21 21:00 | 3.278 | 4.0593 | 4.1239 | 4.401 | 4.2902 | 4.5673 | 2.3492 | 3.5585 | 4.2366 | 4.2366 | 4.6887 | 4.6887 | 2019-08-19 10:00 | 2.1263 | 3.6487 | 6.1669 | 6.1669 | 6.1669 | 6.1669
2021-06-21 22:00 | 2.8922 | 3.5815 | 3.6385 | 3.883 | 3.7852 | 4.0297 | 2.152 | 3.2598 | 3.881 | 3.881 | 4.2951 | 4.2951 | 2019-08-19 11:00 | 2.0577 | 3.531 | 5.9679 | 5.9679 | 5.9679 | 5.9679
2021-06-21 23:00 | 2.5499 | 3.1576 | 3.2079 | 3.4235 | 3.3372 | 3.5528 | 1.7976 | 2.723 | 3.2419 | 3.2419 | 3.5878 | 3.5878 | 2019-08-19 12:00 | 2.1872 | 3.7533 | 6.3437 | 6.3437 | 6.3437 | 6.3437
2021-06-22 | 2.1577 | 2.672 | 2.7145 | 2.8969 | 2.824 | 3.0064 | 1.4823 | 2.2455 | 2.6733 | 2.6733 | 2.9586 | 2.9586 | 2019-08-19 13:00 | 2.1339 | 3.6618 | 6.189 | 6.189 | 6.189 | 6.189
2021-06-22 01:00 | 2.1005 | 2.6012 | 2.6426 | 2.8202 | 2.7492 | 2.9267 | 1.3403 | 2.0304 | 2.4173 | 2.4173 | 2.6752 | 2.6752 | 2019-08-19 14:00 | 1.9967 | 3.4264 | 5.7911 | 5.7911 | 5.7911 | 5.7911
2021-06-22 02:00 | 1.9748 | 2.4455 | 2.4844 | 2.6514 | 2.5846 | 2.7515 | 1.1546 | 1.749 | 2.0822 | 2.0822 | 2.3044 | 2.3044 | 2019-08-19 15:00 | 2.0501 | 3.5179 | 5.9458 | 5.9458 | 5.9458 | 5.9458
2021-06-22 03:00 | 1.9285 | 2.3881 | 2.4262 | 2.5892 | 2.524 | 2.687 | 1.1774 | 1.7836 | 2.1235 | 2.1235 | 2.3501 | 2.3501 | 2019-08-19 16:00 | 2.0882 | 3.5833 | 6.0564 | 6.0564 | 6.0564 | 6.0564
2021-06-22 04:00 | 1.9719 | 2.4419 | 2.4808 | 2.6475 | 2.5808 | 2.7475 | 1.1574 | 1.7533 | 2.0874 | 2.0874 | 2.3101 | 2.3101 | 2019-08-19 17:00 | 2.1034 | 3.6094 | 6.1006 | 6.1006 | 6.1006 | 6.1006
2021-06-22 05:00 | 2.4549 | 3.04 | 3.0884 | 3.296 | 3.213 | 3.4205 | 1.3603 | 2.0607 | 2.4533 | 2.4533 | 2.7151 | 2.7151 | 2019-08-19 18:00 | 2.1567 | 3.701 | 6.2553 | 6.2553 | 6.2553 | 6.2553
2021-06-22 06:00 | 3.4923 | 4.3247 | 4.3936 | 4.6888 | 4.5707 | 4.8659 | 1.6833 | 2.5499 | 3.0357 | 3.0357 | 3.3597 | 3.3597 | 2019-08-19 19:00 | 2.0805 | 3.5702 | 6.0343 | 6.0343 | 6.0343 | 6.0343
2021-06-22 07:00 | 3.9496 | 4.8909 | 4.9688 | 5.3027 | 5.1692 | 5.503 | 2.0491 | 3.104 | 3.6955 | 3.6955 | 4.0898 | 4.0898 | 2019-08-19 20:00 | 1.9738 | 3.3871 | 5.7248 | 5.7248 | 5.7248 | 5.7248
2021-06-22 08:00 | 3.9839 | 4.9334 | 5.012 | 5.3488 | 5.214 | 5.5508 | 2.0491 | 3.104 | 3.6955 | 3.6955 | 4.0898 | 4.0898 | 2019-08-19 21:00 | 1.8976 | 3.2563 | 5.5038 | 5.5038 | 5.5038 | 5.5038
2021-06-22 09:00 | 3.6895 | 4.5689 | 4.6417 | 4.9535 | 4.8288 | 5.1407 | 1.9291 | 2.9222 | 3.479 | 3.479 | 3.8502 | 3.8502 | 2019-08-19 22:00 | 1.6385 | 2.8117 | 4.7522 | 4.7522 | 4.7522 | 4.7522
2021-06-22 10:00 | 3.3437 | 4.1407 | 4.2066 | 4.4893 | 4.3762 | 4.6589 | 1.9062 | 2.8875 | 3.4378 | 3.4378 | 3.8046 | 3.8046 | 2019-08-19 23:00 | 1.4632 | 2.5109 | 4.2439 | 4.2439 | 4.2439 | 4.2439
2021-06-22 11:00 | 3.138 | 3.8859 | 3.9477 | 4.213 | 4.1069 | 4.3722 | 1.769 | 2.6797 | 3.1904 | 3.1904 | 3.5308 | 3.5308 | 2019-08-20 | 1.3413 | 2.3017 | 3.8902 | 3.8902 | 3.8902 | 3.8902
2021-06-22 12:00 | 3.1923 | 3.9531 | 4.0161 | 4.2859 | 4.178 | 4.4478 | 1.9005 | 2.8789 | 3.4275 | 3.4275 | 3.7932 | 3.7932 | 2019-08-20 01:00 | 1.2727 | 2.184 | 3.6913 | 3.6913 | 3.6913 | 3.6913
2021-06-22 13:00 | 3.0294 | 3.7514 | 3.8111 | 4.0672 | 3.9648 | 4.2209 | 1.9805 | 3.0001 | 3.5718 | 3.5718 | 3.9529 | 3.9529 | 2019-08-20 02:00 | 1.2041 | 2.0663 | 3.4923 | 3.4923 | 3.4923 | 3.4923
2021-06-22 14:00 | 2.915 | 3.6098 | 3.6673 | 3.9137 | 3.8152 | 4.0616 | 1.7719 | 2.6841 | 3.1955 | 3.1955 | 3.5365 | 3.5365 | 2019-08-20 03:00 | 1.2041 | 2.0663 | 3.4923 | 3.4923 | 3.4923 | 3.4923
2021-06-22 15:00 | 3.0665 | 3.7974 | 3.8579 | 4.1171 | 4.0134 | 4.2726 | 1.7862 | 2.7057 | 3.2213 | 3.2213 | 3.565 | 3.565 | 2019-08-20 04:00 | 1.2651 | 2.1709 | 3.6692 | 3.6692 | 3.6692 | 3.6692
2021-06-22 16:00 | 3.4585 | 4.2828 | 4.351 | 4.6433 | 4.5264 | 4.8187 | 2.0005 | 3.0304 | 3.6078 | 3.6078 | 3.9928 | 3.9928 | 2019-08-20 05:00 | 1.5699 | 2.694 | 4.5533 | 4.5533 | 4.5533 | 4.5533
2021-06-22 17:00 | 3.9439 | 4.8839 | 4.9617 | 5.295 | 5.1617 | 5.4951 | 2.4521 | 3.7144 | 4.4222 | 4.4222 | 4.894 | 4.894 | 2019-08-20 06:00 | 1.7376 | 2.9817 | 5.0396 | 5.0396 | 5.0396 | 5.0396
2021-06-22 18:00 | 4.0039 | 4.9582 | 5.0372 | 5.3756 | 5.2402 | 5.5787 | 2.6092 | 3.9525 | 4.7057 | 4.7057 | 5.2078 | 5.2078 | 2019-08-20 07:00 | 1.9967 | 3.4264 | 5.7911 | 5.7911 | 5.7911 | 5.7911
2021-06-22 19:00 | 3.98 | 4.9286 | 5.0071 | 5.3436 | 5.209 | 5.5454 | 2.7321 | 4.1387 | 4.9273 | 4.9273 | 5.453 | 5.453 | 2019-08-20 08:00 | 2.0653 | 3.5441 | 5.99 | 5.99 | 5.99 | 5.99
2021-06-22 20:00 | 3.6038 | 4.4627 | 4.5338 | 4.8384 | 4.7166 | 5.0212 | 2.615 | 3.9612 | 4.716 | 4.716 | 5.2192 | 5.2192 | 2019-08-20 09:00 | 1.9815 | 3.4002 | 5.7469 | 5.7469 | 5.7469 | 5.7469
2021-06-22 21:00 | 3.2123 | 3.9779 | 4.0412 | 4.3128 | 4.2042 | 4.4757 | 2.3863 | 3.6148 | 4.3036 | 4.3036 | 4.7629 | 4.7629 | 2019-08-20 10:00 | 2.0119 | 3.4525 | 5.8353 | 5.8353 | 5.8353 | 5.8353
2021-06-22 22:00 | 2.7693 | 3.4293 | 3.4839 | 3.718 | 3.6244 | 3.8585 | 2.072 | 3.1386 | 3.7367 | 3.7367 | 4.1354 | 4.1354 | 2019-08-20 11:00 | 2.0043 | 3.4394 | 5.8132 | 5.8132 | 5.8132 | 5.8132
2021-06-22 23:00 | 2.3806 | 2.948 | 2.995 | 3.1962 | 3.1157 | 3.317 | 1.7662 | 2.6754 | 3.1852 | 3.1852 | 3.5251 | 3.5251 | 2019-08-20 12:00 | 2.0501 | 3.5179 | 5.9458 | 5.9458 | 5.9458 | 5.9458
2021-06-23 | 2.0874 | 2.5849 | 2.6261 | 2.8026 | 2.732 | 2.9084 | 1.4775 | 2.2382 | 2.6646 | 2.6646 | 2.949 | 2.949 | 2019-08-20 13:00 | 1.9586 | 3.361 | 5.6806 | 5.6806 | 5.6806 | 5.6806
2021-06-23 01:00 | 1.9634 | 2.4313 | 2.47 | 2.636 | 2.5696 | 2.7356 | 1.266 | 1.9178 | 2.2832 | 2.2832 | 2.5269 | 2.5269 | 2019-08-20 14:00 | 2.0272 | 3.4787 | 5.8795 | 5.8795 | 5.8795 | 5.8795
2021-06-23 02:00 | 1.8605 | 2.3039 | 2.3406 | 2.4979 | 2.435 | 2.5922 | 1.1717 | 1.7749 | 2.1132 | 2.1132 | 2.3386 | 2.3386 | 2019-08-20 15:00 | 2.0196 | 3.4656 | 5.8574 | 5.8574 | 5.8574 | 5.8574
2021-06-23 03:00 | 1.9033 | 2.357 | 2.3945 | 2.5554 | 2.4911 | 2.652 | 1.1431 | 1.7317 | 2.0616 | 2.0616 | 2.2816 | 2.2816 | 2019-08-20 16:00 | 1.9891 | 3.4133 | 5.769 | 5.769 | 5.769 | 5.769
2021-06-23 04:00 | 1.9823 | 2.4547 | 2.4938 | 2.6614 | 2.5943 | 2.7619 | 1.1403 | 1.7273 | 2.0565 | 2.0565 | 2.2759 | 2.2759 | 2019-08-20 17:00 | 2.2253 | 3.8187 | 6.4542 | 6.4542 | 6.4542 | 6.4542
2021-06-23 05:00 | 2.4349 | 3.0153 | 3.0633 | 3.2691 | 3.1868 | 3.3926 | 1.3375 | 2.026 | 2.4121 | 2.4121 | 2.6695 | 2.6695 | 2019-08-20 18:00 | 2.2253 | 3.8187 | 6.4542 | 6.4542 | 6.4542 | 6.4542
2021-06-23 06:00 | 3.4926 | 4.325 | 4.3939 | 4.6892 | 4.5711 | 4.8663 | 1.6804 | 2.5455 | 3.0306 | 3.0306 | 3.354 | 3.354 | 2019-08-20 19:00 | 2.0653 | 3.5441 | 5.99 | 5.99 | 5.99 | 5.99
2021-06-23 07:00 | 4.0096 | 4.9653 | 5.0443 | 5.3833 | 5.2477 | 5.5867 | 1.9605 | 2.9698 | 3.5357 | 3.5357 | 3.913 | 3.913 | 2019-08-20 20:00 | 1.9967 | 3.4264 | 5.7911 | 5.7911 | 5.7911 | 5.7911
2021-06-23 08:00 | 3.9896 | 4.9405 | 5.0192 | 5.3564 | 5.2215 | 5.5588 | 2.0605 | 3.1213 | 3.7161 | 3.7161 | 4.1126 | 4.1126 | 2019-08-20 21:00 | 1.9129 | 3.2825 | 5.548 | 5.548 | 5.548 | 5.548
2021-06-23 09:00 | 3.8953 | 4.8237 | 4.9005 | 5.2298 | 5.0981 | 5.4274 | 1.9376 | 2.9352 | 3.4945 | 3.4945 | 3.8673 | 3.8673 | 2019-08-20 22:00 | 1.73 | 2.9686 | 5.0175 | 5.0175 | 5.0175 | 5.0175
2021-06-23 10:00 | 3.8438 | 4.76 | 4.8358 | 5.1607 | 5.0308 | 5.3557 | 1.9605 | 2.9698 | 3.5357 | 3.5357 | 3.913 | 3.913 | 2019-08-20 23:00 | 1.5166 | 2.6025 | 4.3986 | 4.3986 | 4.3986 | 4.3986
2021-06-23 11:00 | 3.7324 | 4.622 | 4.6956 | 5.0111 | 4.8849 | 5.2004 | 2.0348 | 3.0823 | 3.6697 | 3.6697 | 4.0613 | 4.0613 | 2019-08-21 | 1.387 | 2.3801 | 4.0228 | 4.0228 | 4.0228 | 4.0228
2021-06-23 12:00 | 3.6295 | 4.4946 | 4.5662 | 4.873 | 4.7502 | 5.0571 | 1.9977 | 3.0261 | 3.6027 | 3.6027 | 3.9871 | 3.9871 | 2019-08-21 01:00 | 1.2346 | 2.1186 | 3.5808 | 3.5808 | 3.5808 | 3.5808
2021-06-23 13:00 | 3.5952 | 4.4521 | 4.523 | 4.8269 | 4.7054 | 5.0093 | 1.9548 | 2.9611 | 3.5254 | 3.5254 | 3.9015 | 3.9015 | 2019-08-21 02:00 | 1.2346 | 2.1186 | 3.5808 | 3.5808 | 3.5808 | 3.5808
2021-06-23 14:00 | 3.4923 | 4.3247 | 4.3936 | 4.6888 | 4.5707 | 4.8659 | 2.0177 | 3.0564 | 3.6388 | 3.6388 | 4.027 | 4.027 | 2019-08-21 03:00 | 1.227 | 2.1055 | 3.5587 | 3.5587 | 3.5587 | 3.5587
2021-06-23 15:00 | 3.3468 | 4.1445 | 4.2105 | 4.4934 | 4.3803 | 4.6632 | 1.9291 | 2.9222 | 3.479 | 3.479 | 3.8502 | 3.8502 | 2019-08-21 04:00 | 1.3184 | 2.2624 | 3.8239 | 3.8239 | 3.8239 | 3.8239
2021-06-23 16:00 | 3.7579 | 4.6535 | 4.7277 | 5.0453 | 4.9183 | 5.2359 | 2.1434 | 3.2469 | 3.8655 | 3.8655 | 4.278 | 4.278 | 2019-08-21 05:00 | 1.5471 | 2.6548 | 4.487 | 4.487 | 4.487 | 4.487
2021-06-23 17:00 | 4.1153 | 5.0962 | 5.1774 | 5.5253 | 5.3861 | 5.734 | 2.4778 | 3.7534 | 4.4686 | 4.4686 | 4.9454 | 4.9454 | 2019-08-21 06:00 | 1.7452 | 2.9948 | 5.0617 | 5.0617 | 5.0617 | 5.0617
2021-06-23 18:00 | 4.1068 | 5.0856 | 5.1666 | 5.5137 | 5.3749 | 5.722 | 2.5835 | 3.9135 | 4.6593 | 4.6593 | 5.1564 | 5.1564 | 2019-08-21 07:00 | 2.0501 | 3.5179 | 5.9458 | 5.9458 | 5.9458 | 5.9458
2021-06-23 19:00 | 3.8639 | 4.7848 | 4.861 | 5.1876 | 5.057 | 5.3836 | 2.5549 | 3.8702 | 4.6077 | 4.6077 | 5.0994 | 5.0994 | 2019-08-21 08:00 | 2.1415 | 3.6748 | 6.2111 | 6.2111 | 6.2111 | 6.2111
2021-06-23 20:00 | 3.4752 | 4.3035 | 4.372 | 4.6658 | 4.5483 | 4.842 | 2.3645 | 3.5818 | 4.2643 | 4.2643 | 4.7193 | 4.7193 | 2019-08-21 09:00 | 2.1796 | 3.7402 | 6.3216 | 6.3216 | 6.3216 | 6.3216
2021-06-23 21:00 | 3.1837 | 3.9425 | 4.0053 | 4.2744 | 4.1667 | 4.4359 | 2.332 | 3.5326 | 4.2057 | 4.2057 | 4.6545 | 4.6545 | 2019-08-21 10:00 | 2.0729 | 3.5571 | 6.0121 | 6.0121 | 6.0121 | 6.0121
2021-06-23 22:00 | 2.6962 | 3.3388 | 3.392 | 3.6199 | 3.5287 | 3.7566 | 2.0262 | 3.0694 | 3.6542 | 3.6542 | 4.0441 | 4.0441 | 2019-08-21 11:00 | 1.9967 | 3.4264 | 5.7911 | 5.7911 | 5.7911 | 5.7911
2021-06-23 23:00 | 2.2749 | 2.8171 | 2.8619 | 3.0542 | 2.9773 | 3.1696 | 1.6061 | 2.433 | 2.8966 | 2.8966 | 3.2057 | 3.2057 | 2019-08-21 12:00 | 1.9967 | 3.4264 | 5.7911 | 5.7911 | 5.7911 | 5.7911
2021-06-24 | 2.0827 | 2.5791 | 2.6202 | 2.7963 | 2.7258 | 2.9019 | 1.3432 | 2.0347 | 2.4224 | 2.4224 | 2.6809 | 2.6809 | 2019-08-21 13:00 | 2.0424 | 3.5048 | 5.9237 | 5.9237 | 5.9237 | 5.9237
2021-06-24 01:00 | 2.2586 | 2.797 | 2.8415 | 3.0324 | 2.9561 | 3.147 | 1.3376 | 2.0263 | 2.4124 | 2.4124 | 2.6698 | 2.6698 | 2019-08-21 14:00 | 2.0272 | 3.4787 | 5.8795 | 5.8795 | 5.8795 | 5.8795
2021-06-24 02:00 | 2.4346 | 3.0148 | 3.0628 | 3.2686 | 3.1863 | 3.3921 | 1.3945 | 2.1124 | 2.5149 | 2.5149 | 2.7833 | 2.7833 | 2019-08-21 15:00 | 1.9967 | 3.4264 | 5.7911 | 5.7911 | 5.7911 | 5.7911
2021-06-24 03:00 | 2.6105 | 3.2327 | 3.2842 | 3.5048 | 3.4166 | 3.6372 | 1.4514 | 2.1986 | 2.6175 | 2.6175 | 2.8968 | 2.8968 | 2019-08-21 16:00 | 2.0958 | 3.5964 | 6.0785 | 6.0785 | 6.0785 | 6.0785
2021-06-24 04:00 | 2.7864 | 3.4505 | 3.5055 | 3.741 | 3.6468 | 3.8823 | 1.5083 | 2.2847 | 2.7201 | 2.7201 | 3.0103 | 3.0103 | 2019-08-21 17:00 | 2.1415 | 3.6748 | 6.2111 | 6.2111 | 6.2111 | 6.2111
2021-06-24 05:00 | 2.9623 | 3.6684 | 3.7268 | 3.9772 | 3.877 | 4.1275 | 1.5651 | 2.3709 | 2.8226 | 2.8226 | 3.1238 | 3.1238 | 2019-08-21 18:00 | 2.1491 | 3.6879 | 6.2332 | 6.2332 | 6.2332 | 6.2332
2021-06-24 06:00 | 3.1382 | 3.8862 | 3.9481 | 4.2134 | 4.1073 | 4.3726 | 1.622 | 2.457 | 2.9252 | 2.9252 | 3.2373 | 3.2373 | 2019-08-21 19:00 | 2.0958 | 3.5964 | 6.0785 | 6.0785 | 6.0785 | 6.0785
2021-06-24 07:00 | 3.3142 | 4.1041 | 4.1694 | 4.4496 | 4.3375 | 4.6177 | 1.6789 | 2.5432 | 3.0278 | 3.0278 | 3.3508 | 3.3508 | 2019-08-21 20:00 | 1.9662 | 3.374 | 5.7027 | 5.7027 | 5.7027 | 5.7027
2021-06-24 08:00 | 3.5152 | 4.353 | 4.4223 | 4.7195 | 4.6006 | 4.8978 | 1.8662 | 2.8269 | 3.3656 | 3.3656 | 3.7247 | 3.7247 | 2019-08-21 21:00 | 1.9053 | 3.2694 | 5.5259 | 5.5259 | 5.5259 | 5.5259
2021-06-24 09:00 | 3.5866 | 4.4415 | 4.5122 | 4.8154 | 4.6941 | 4.9973 | 1.8891 | 2.8616 | 3.4068 | 3.4068 | 3.7704 | 3.7704 | 2019-08-21 22:00 | 1.7071 | 2.9294 | 4.9512 | 4.9512 | 4.9512 | 4.9512
2021-06-24 10:00 | 3.5581 | 4.4061 | 4.4763 | 4.777 | 4.6567 | 4.9575 | 1.8862 | 2.8572 | 3.4017 | 3.4017 | 3.7647 | 3.7647 | 2019-08-21 23:00 | 1.4785 | 2.5371 | 4.2881 | 4.2881 | 4.2881 | 4.2881
2021-06-24 11:00 | 3.5724 | 4.4238 | 4.4942 | 4.7962 | 4.6754 | 4.9774 | 2.0348 | 3.0823 | 3.6697 | 3.6697 | 4.0613 | 4.0613 | 2019-08-22 | 1.3337 | 2.2886 | 3.8681 | 3.8681 | 3.8681 | 3.8681
2021-06-24 12:00 | 3.5295 | 4.3707 | 4.4403 | 4.7387 | 4.6193 | 4.9177 | 2.152 | 3.2598 | 3.881 | 3.881 | 4.2951 | 4.2951 | 2019-08-22 01:00 | 1.3032 | 2.2363 | 3.7797 | 3.7797 | 3.7797 | 3.7797
2021-06-24 13:00 | 3.4809 | 4.3105 | 4.3792 | 4.6734 | 4.5557 | 4.85 | 2.1606 | 3.2728 | 3.8965 | 3.8965 | 4.3122 | 4.3122 | 2019-08-22 02:00 | 1.1813 | 2.027 | 3.426 | 3.426 | 3.426 | 3.426
2021-06-24 14:00 | 3.3237 | 4.1159 | 4.1814 | 4.4624 | 4.35 | 4.631 | 2.0348 | 3.0823 | 3.6697 | 3.6697 | 4.0613 | 4.0613 | 2019-08-22 03:00 | 1.2194 | 2.0924 | 3.5366 | 3.5366 | 3.5366 | 3.5366
2021-06-24 15:00 | 3.3923 | 4.2008 | 4.2677 | 4.5545 | 4.4398 | 4.7266 | 1.9462 | 2.9481 | 3.5099 | 3.5099 | 3.8844 | 3.8844 | 2019-08-22 04:00 | 1.2727 | 2.184 | 3.6913 | 3.6913 | 3.6913 | 3.6913
2021-06-24 16:00 | 3.5409 | 4.3849 | 4.4547 | 4.754 | 4.6343 | 4.9336 | 2.0662 | 3.13 | 3.7264 | 3.7264 | 4.124 | 4.124 | 2019-08-22 05:00 | 1.5394 | 2.6417 | 4.4649 | 4.4649 | 4.4649 | 4.4649
2021-06-24 17:00 | 3.7638 | 4.6609 | 4.7351 | 5.0533 | 4.926 | 5.2442 | 2.2977 | 3.4806 | 4.1439 | 4.1439 | 4.586 | 4.586 | 2019-08-22 06:00 | 1.5623 | 2.6809 | 4.5312 | 4.5312 | 4.5312 | 4.5312
2021-06-24 18:00 | 4.0382 | 5.0006 | 5.0803 | 5.4217 | 5.2851 | 5.6265 | 2.4978 | 3.7837 | 4.5047 | 4.5047 | 4.9853 | 4.9853 | 2019-08-22 07:00 | 2.1034 | 3.6094 | 6.1006 | 6.1006 | 6.1006 | 6.1006
2021-06-24 19:00 | 3.7381 | 4.6291 | 4.7028 | 5.0188 | 4.8924 | 5.2084 | 2.5064 | 3.7967 | 4.5201 | 4.5201 | 5.0024 | 5.0024 | 2019-08-22 08:00 | 2.0882 | 3.5833 | 6.0564 | 6.0564 | 6.0564 | 6.0564
2021-06-24 20:00 | 3.3272 | 4.1202 | 4.1858 | 4.4671 | 4.3546 | 4.6358 | 2.4721 | 3.7447 | 4.4583 | 4.4583 | 4.934 | 4.934 | 2019-08-22 09:00 | 2.0272 | 3.4787 | 5.8795 | 5.8795 | 5.8795 | 5.8795
2021-06-24 21:00 | 3.0322 | 3.7549 | 3.8147 | 4.071 | 3.9685 | 4.2248 | 2.272 | 3.4417 | 4.0975 | 4.0975 | 4.5347 | 4.5347 | 2019-08-22 10:00 | 2.0958 | 3.5964 | 6.0785 | 6.0785 | 6.0785 | 6.0785
2021-06-24 22:00 | 2.6823 | 3.3216 | 3.3745 | 3.6013 | 3.5106 | 3.7373 | 1.9293 | 2.9224 | 3.4793 | 3.4793 | 3.8506 | 3.8506 | 2019-08-22 11:00 | 1.9738 | 3.3871 | 5.7248 | 5.7248 | 5.7248 | 5.7248
2021-06-24 23:00 | 2.4063 | 2.9799 | 3.0273 | 3.2307 | 3.1494 | 3.3528 | 1.6861 | 2.5542 | 3.0409 | 3.0409 | 3.3654 | 3.3654 | 2019-08-22 12:00 | 2.172 | 3.7271 | 6.2995 | 6.2995 | 6.2995 | 6.2995
2021-06-25 | 2.0891 | 2.587 | 2.6282 | 2.8048 | 2.7342 | 2.9108 | 1.4204 | 2.1516 | 2.5616 | 2.5616 | 2.8349 | 2.8349 | 2019-08-22 13:00 | 1.9815 | 3.4002 | 5.7469 | 5.7469 | 5.7469 | 5.7469
2021-06-25 01:00 | 1.9091 | 2.3641 | 2.4017 | 2.5631 | 2.4986 | 2.6599 | 1.206 | 1.8269 | 2.175 | 2.175 | 2.4071 | 2.4071 | 2019-08-22 14:00 | 2.0653 | 3.5441 | 5.99 | 5.99 | 5.99 | 5.99
2021-06-25 02:00 | 1.9005 | 2.3535 | 2.3909 | 2.5516 | 2.4873 | 2.648 | 1.126 | 1.7057 | 2.0307 | 2.0307 | 2.2474 | 2.2474 | 2019-08-22 15:00 | 2.0653 | 3.5441 | 5.99 | 5.99 | 5.99 | 5.99
2021-06-25 03:00 | 1.8891 | 2.3393 | 2.3766 | 2.5362 | 2.4724 | 2.6321 | 1.1117 | 1.684 | 2.0049 | 2.0049 | 2.2189 | 2.2189 | 2019-08-22 16:00 | 2.0196 | 3.4656 | 5.8574 | 5.8574 | 5.8574 | 5.8574
2021-06-25 04:00 | 1.9481 | 2.4124 | 2.4509 | 2.6155 | 2.5497 | 2.7144 | 1.1031 | 1.671 | 1.9895 | 1.9895 | 2.2017 | 2.2017 | 2019-08-22 17:00 | 1.951 | 3.3479 | 5.6585 | 5.6585 | 5.6585 | 5.6585
2021-06-25 05:00 | 2.2949 | 2.8418 | 2.8871 | 3.0811 | 3.0035 | 3.1975 | 1.2517 | 1.8962 | 2.2575 | 2.2575 | 2.4984 | 2.4984 | 2019-08-22 18:00 | 2.0043 | 3.4394 | 5.8132 | 5.8132 | 5.8132 | 5.8132
2021-06-25 06:00 | 3.1437 | 3.8929 | 3.9549 | 4.2207 | 4.1144 | 4.3801 | 1.5833 | 2.3983 | 2.8554 | 2.8554 | 3.16 | 3.16 | 2019-08-22 19:00 | 1.951 | 3.3479 | 5.6585 | 5.6585 | 5.6585 | 5.6585
2021-06-25 07:00 | 3.6181 | 4.4804 | 4.5518 | 4.8576 | 4.7353 | 5.0411 | 1.8948 | 2.8702 | 3.4171 | 3.4171 | 3.7818 | 3.7818 | 2019-08-22 20:00 | 1.9129 | 3.2825 | 5.548 | 5.548 | 5.548 | 5.548
2021-06-25 08:00 | 3.7981 | 4.7034 | 4.7783 | 5.0994 | 4.9709 | 5.292 | 1.9662 | 2.9784 | 3.546 | 3.546 | 3.9244 | 3.9244 | 2019-08-22 21:00 | 1.7986 | 3.0863 | 5.2164 | 5.2164 | 5.2164 | 5.2164
2021-06-25 09:00 | 3.7067 | 4.5901 | 4.6632 | 4.9766 | 4.8512 | 5.1646 | 1.8233 | 2.762 | 3.2883 | 3.2883 | 3.6392 | 3.6392 | 2019-08-22 22:00 | 1.5699 | 2.694 | 4.5533 | 4.5533 | 4.5533 | 4.5533
2021-06-25 10:00 | 3.4952 | 4.3282 | 4.3972 | 4.6926 | 4.5744 | 4.8699 | 1.8719 | 2.8356 | 3.3759 | 3.3759 | 3.7361 | 3.7361 | 2019-08-22 23:00 | 1.509 | 2.5894 | 4.3765 | 4.3765 | 4.3765 | 4.3765
2021-06-25 11:00 | 3.2608 | 4.038 | 4.1024 | 4.378 | 4.2677 | 4.5434 | 1.809 | 2.7403 | 3.2625 | 3.2625 | 3.6106 | 3.6106 | 2019-08-23 | 1.3261 | 2.2755 | 3.846 | 3.846 | 3.846 | 3.846
2021-06-25 12:00 | 3.2208 | 3.9885 | 4.052 | 4.3243 | 4.2154 | 4.4876 | 1.8348 | 2.7793 | 3.3089 | 3.3089 | 3.662 | 3.662 | 2019-08-23 01:00 | 1.2575 | 2.1578 | 3.6471 | 3.6471 | 3.6471 | 3.6471
2021-06-25 13:00 | 3.2437 | 4.0168 | 4.0808 | 4.355 | 4.2453 | 4.5195 | 1.9148 | 2.9005 | 3.4532 | 3.4532 | 3.8217 | 3.8217 | 2019-08-23 02:00 | 1.1736 | 2.014 | 3.4039 | 3.4039 | 3.4039 | 3.4039
2021-06-25 14:00 | 3.2951 | 4.0805 | 4.1455 | 4.424 | 4.3126 | 4.5912 | 2.0234 | 3.065 | 3.6491 | 3.6491 | 4.0384 | 4.0384 | 2019-08-23 03:00 | 1.2117 | 2.0794 | 3.5144 | 3.5144 | 3.5144 | 3.5144
2021-06-25 15:00 | 3.4037 | 4.215 | 4.2821 | 4.5698 | 4.4548 | 4.7425 | 1.9348 | 2.9308 | 3.4893 | 3.4893 | 3.8616 | 3.8616 | 2019-08-23 04:00 | 1.2651 | 2.1709 | 3.6692 | 3.6692 | 3.6692 | 3.6692
2021-06-25 16:00 | 3.6181 | 4.4804 | 4.5518 | 4.8576 | 4.7353 | 5.0411 | 2.1291 | 3.2252 | 3.8398 | 3.8398 | 4.2495 | 4.2495 | 2019-08-23 05:00 | 1.509 | 2.5894 | 4.3765 | 4.3765 | 4.3765 | 4.3765
2021-06-25 17:00 | 4.0439 | 5.0077 | 5.0875 | 5.4293 | 5.2926 | 5.6344 | 2.4921 | 3.775 | 4.4943 | 4.4943 | 4.9739 | 4.9739 | 2019-08-23 06:00 | 1.6995 | 2.9163 | 4.9291 | 4.9291 | 4.9291 | 4.9291
2021-06-25 18:00 | 3.9953 | 4.9476 | 5.0264 | 5.3641 | 5.229 | 5.5667 | 2.6464 | 4.0088 | 4.7727 | 4.7727 | 5.2819 | 5.2819 | 2019-08-23 07:00 | 1.9891 | 3.4133 | 5.769 | 5.769 | 5.769 | 5.769
2021-06-25 19:00 | 3.6581 | 4.53 | 4.6021 | 4.9113 | 4.7876 | 5.0969 | 2.6235 | 3.9741 | 4.7314 | 4.7314 | 5.2363 | 5.2363 | 2019-08-23 08:00 | 2.1186 | 3.6356 | 6.1448 | 6.1448 | 6.1448 | 6.1448
2021-06-25 20:00 | 3.3952 | 4.2044 | 4.2713 | 4.5583 | 4.4435 | 4.7305 | 2.5578 | 3.8746 | 4.6129 | 4.6129 | 5.1051 | 5.1051 | 2019-08-23 09:00 | 2.0805 | 3.5702 | 6.0343 | 6.0343 | 6.0343 | 6.0343
2021-06-25 21:00 | 3.1294 | 3.8752 | 3.937 | 4.2015 | 4.0957 | 4.3602 | 2.5149 | 3.8096 | 4.5356 | 4.5356 | 5.0195 | 5.0195 | 2019-08-23 10:00 | 2.0805 | 3.5702 | 6.0343 | 6.0343 | 6.0343 | 6.0343
2021-06-25 22:00 | 2.7444 | 3.3984 | 3.4526 | 3.6846 | 3.5918 | 3.8238 | 2.1406 | 3.2425 | 3.8604 | 3.8604 | 4.2723 | 4.2723 | 2019-08-23 11:00 | 2.0043 | 3.4394 | 5.8132 | 5.8132 | 5.8132 | 5.8132
2021-06-25 23:00 | 2.5563 | 3.1656 | 3.216 | 3.4321 | 3.3457 | 3.5618 | 1.8633 | 2.8226 | 3.3604 | 3.3604 | 3.719 | 3.719 | 2019-08-23 12:00 | 2.0501 | 3.5179 | 5.9458 | 5.9458 | 5.9458 | 5.9458
2021-06-26 | 2.2006 | 2.7251 | 2.7685 | 2.9545 | 2.8801 | 3.0661 | 1.5121 | 2.2905 | 2.727 | 2.727 | 3.0179 | 3.0179 | 2019-08-23 13:00 | 1.9815 | 3.4002 | 5.7469 | 5.7469 | 5.7469 | 5.7469
2021-06-26 01:00 | 2.0434 | 2.5304 | 2.5707 | 2.7434 | 2.6743 | 2.8471 | 1.3261 | 2.0087 | 2.3915 | 2.3915 | 2.6467 | 2.6467 | 2019-08-23 14:00 | 2.0348 | 3.4917 | 5.9016 | 5.9016 | 5.9016 | 5.9016
2021-06-26 02:00 | 1.9462 | 2.4101 | 2.4485 | 2.613 | 2.5472 | 2.7117 | 1.2289 | 1.8615 | 2.2162 | 2.2162 | 2.4527 | 2.4527 | 2019-08-23 15:00 | 1.9815 | 3.4002 | 5.7469 | 5.7469 | 5.7469 | 5.7469
2021-06-26 03:00 | 1.9634 | 2.4313 | 2.47 | 2.636 | 2.5696 | 2.7356 | 1.1374 | 1.723 | 2.0513 | 2.0513 | 2.2702 | 2.2702 | 2019-08-23 16:00 | 1.9967 | 3.4264 | 5.7911 | 5.7911 | 5.7911 | 5.7911
2021-06-26 04:00 | 1.9491 | 2.4136 | 2.4521 | 2.6168 | 2.5509 | 2.7157 | 1.1315 | 1.714 | 2.0406 | 2.0406 | 2.2584 | 2.2584 | 2019-08-23 17:00 | 2.0119 | 3.4525 | 5.8353 | 5.8353 | 5.8353 | 5.8353
2021-06-26 05:00 | 2.1546 | 2.6681 | 2.7106 | 2.8928 | 2.8199 | 3.002 | 1.1832 | 1.7923 | 2.1338 | 2.1338 | 2.3615 | 2.3615 | 2019-08-23 18:00 | 2.0272 | 3.4787 | 5.8795 | 5.8795 | 5.8795 | 5.8795
2021-06-26 06:00 | 2.3978 | 2.9692 | 3.0165 | 3.2192 | 3.1382 | 3.3408 | 1.39 | 2.1056 | 2.5068 | 2.5068 | 2.7743 | 2.7743 | 2019-08-23 19:00 | 2.0272 | 3.4787 | 5.8795 | 5.8795 | 5.8795 | 5.8795
2021-06-26 07:00 | 2.8036 | 3.4718 | 3.5271 | 3.7641 | 3.6693 | 3.9063 | 1.7486 | 2.6488 | 3.1535 | 3.1535 | 3.49 | 3.49 | 2019-08-23 20:00 | 1.829 | 3.1386 | 5.3048 | 5.3048 | 5.3048 | 5.3048
2021-06-26 08:00 | 2.8464 | 3.5249 | 3.581 | 3.8216 | 3.7254 | 3.966 | 1.9297 | 2.9232 | 3.4802 | 3.4802 | 3.8516 | 3.8516 | 2019-08-23 21:00 | 1.8138 | 3.1125 | 5.2606 | 5.2606 | 5.2606 | 5.2606
2021-06-26 09:00 | 3.0808 | 3.8151 | 3.8758 | 4.1363 | 4.0321 | 4.2925 | 2.0805 | 3.1516 | 3.7522 | 3.7522 | 4.1525 | 4.1525 | 2019-08-23 22:00 | 1.6614 | 2.8509 | 4.8186 | 4.8186 | 4.8186 | 4.8186
2021-06-26 10:00 | 3.1065 | 3.8469 | 3.9082 | 4.1708 | 4.0658 | 4.3284 | 2.1463 | 3.2512 | 3.8707 | 3.8707 | 4.2837 | 4.2837 | 2019-08-23 23:00 | 1.4937 | 2.5632 | 4.3323 | 4.3323 | 4.3323 | 4.3323
2021-06-26 11:00 | 3.1551 | 3.9071 | 3.9693 | 4.236 | 4.1293 | 4.3961 | 2.2177 | 3.3594 | 3.9996 | 3.9996 | 4.4263 | 4.4263 | 2019-08-24 | 1.3565 | 2.3278 | 3.9344 | 3.9344 | 3.9344 | 3.9344
2021-06-26 12:00 | 2.7579 | 3.4152 | 3.4696 | 3.7027 | 3.6094 | 3.8426 | 2.2177 | 3.3594 | 3.9996 | 3.9996 | 4.4263 | 4.4263 | 2019-08-24 01:00 | 1.2879 | 2.2101 | 3.7355 | 3.7355 | 3.7355 | 3.7355
2021-06-26 13:00 | 2.6921 | 3.3338 | 3.3869 | 3.6144 | 3.5234 | 3.751 | 2.1977 | 3.3291 | 3.9635 | 3.9635 | 4.3864 | 4.3864 | 2019-08-24 02:00 | 1.1965 | 2.0532 | 3.4702 | 3.4702 | 3.4702 | 3.4702
2021-06-26 14:00 | 2.4989 | 3.0944 | 3.1437 | 3.355 | 3.2705 | 3.4817 | 2.1177 | 3.2079 | 3.8192 | 3.8192 | 4.2267 | 4.2267 | 2019-08-24 03:00 | 1.2117 | 2.0794 | 3.5144 | 3.5144 | 3.5144 | 3.5144
2021-06-26 15:00 | 2.6607 | 3.2948 | 3.3473 | 3.5722 | 3.4823 | 3.7072 | 2.0748 | 3.143 | 3.7419 | 3.7419 | 4.1411 | 4.1411 | 2019-08-24 04:00 | 1.1965 | 2.0532 | 3.4702 | 3.4702 | 3.4702 | 3.4702
2021-06-26 16:00 | 2.9493 | 3.6523 | 3.7105 | 3.9598 | 3.86 | 4.1094 | 2.3006 | 3.485 | 4.149 | 4.149 | 4.5917 | 4.5917 | 2019-08-24 05:00 | 1.387 | 2.3801 | 4.0228 | 4.0228 | 4.0228 | 4.0228
2021-06-26 17:00 | 3.3666 | 4.169 | 4.2354 | 4.52 | 4.4061 | 4.6907 | 2.5378 | 3.8443 | 4.5768 | 4.5768 | 5.0652 | 5.0652 | 2019-08-24 06:00 | 1.4632 | 2.5109 | 4.2439 | 4.2439 | 4.2439 | 4.2439
2021-06-26 18:00 | 3.3237 | 4.1159 | 4.1814 | 4.4624 | 4.35 | 4.631 | 2.6207 | 3.9698 | 4.7263 | 4.7263 | 5.2306 | 5.2306 | 2019-08-24 07:00 | 1.7376 | 2.9817 | 5.0396 | 5.0396 | 5.0396 | 5.0396
2021-06-26 19:00 | 3.2065 | 3.9708 | 4.034 | 4.3051 | 4.1967 | 4.4677 | 2.4435 | 3.7014 | 4.4067 | 4.4067 | 4.8769 | 4.8769 | 2019-08-24 08:00 | 1.7605 | 3.0209 | 5.1059 | 5.1059 | 5.1059 | 5.1059
2021-06-26 20:00 | 3.0665 | 3.7974 | 3.8579 | 4.1171 | 4.0134 | 4.2726 | 2.4292 | 3.6798 | 4.381 | 4.381 | 4.8484 | 4.8484 | 2019-08-24 09:00 | 1.8519 | 3.1779 | 5.3711 | 5.3711 | 5.3711 | 5.3711
2021-06-26 21:00 | 2.8865 | 3.5744 | 3.6314 | 3.8754 | 3.7778 | 4.0218 | 2.2149 | 3.3551 | 3.9944 | 3.9944 | 4.4206 | 4.4206 | 2019-08-24 10:00 | 1.829 | 3.1386 | 5.3048 | 5.3048 | 5.3048 | 5.3048
2021-06-26 22:00 | 2.6409 | 3.2703 | 3.3224 | 3.5456 | 3.4563 | 3.6796 | 2.0948 | 3.1733 | 3.7779 | 3.7779 | 4.181 | 4.181 | 2019-08-24 11:00 | 1.8595 | 3.191 | 5.3932 | 5.3932 | 5.3932 | 5.3932
2021-06-26 23:00 | 2.5122 | 3.111 | 3.1605 | 3.3729 | 3.2879 | 3.5003 | 1.7633 | 2.6711 | 3.1801 | 3.1801 | 3.5194 | 3.5194 | 2019-08-24 12:00 | 1.8214 | 3.1256 | 5.2827 | 5.2827 | 5.2827 | 5.2827
2021-06-27 | 2.2263 | 2.7569 | 2.8008 | 2.989 | 2.9137 | 3.1019 | 1.5175 | 2.2988 | 2.7368 | 2.7368 | 3.0288 | 3.0288 | 2019-08-24 13:00 | 1.8138 | 3.1125 | 5.2606 | 5.2606 | 5.2606 | 5.2606
2021-06-27 01:00 | 2.1177 | 2.6224 | 2.6642 | 2.8432 | 2.7716 | 2.9506 | 1.2889 | 1.9524 | 2.3245 | 2.3245 | 2.5725 | 2.5725 | 2019-08-24 14:00 | 1.7986 | 3.0863 | 5.2164 | 5.2164 | 5.2164 | 5.2164
2021-06-27 02:00 | 1.9319 | 2.3924 | 2.4305 | 2.5938 | 2.5285 | 2.6918 | 1.2603 | 1.9091 | 2.2729 | 2.2729 | 2.5155 | 2.5155 | 2019-08-24 15:00 | 1.7909 | 3.0733 | 5.1943 | 5.1943 | 5.1943 | 5.1943
2021-06-27 03:00 | 1.9519 | 2.4172 | 2.4557 | 2.6207 | 2.5547 | 2.7197 | 1.186 | 1.7966 | 2.1389 | 2.1389 | 2.3672 | 2.3672 | 2019-08-24 16:00 | 1.89 | 3.2433 | 5.4817 | 5.4817 | 5.4817 | 5.4817
2021-06-27 04:00 | 2.0034 | 2.4809 | 2.5204 | 2.6897 | 2.622 | 2.7913 | 1.2232 | 1.8529 | 2.2059 | 2.2059 | 2.4413 | 2.4413 | 2019-08-24 17:00 | 1.9053 | 3.2694 | 5.5259 | 5.5259 | 5.5259 | 5.5259
2021-06-27 05:00 | 2.1146 | 2.6185 | 2.6603 | 2.839 | 2.7675 | 2.9463 | 1.186 | 1.7965 | 2.1388 | 2.1388 | 2.3671 | 2.3671 | 2019-08-24 18:00 | 1.9053 | 3.2694 | 5.5259 | 5.5259 | 5.5259 | 5.5259
2021-06-27 06:00 | 2.4035 | 2.9763 | 3.0237 | 3.2269 | 3.1456 | 3.3488 | 1.3146 | 1.9913 | 2.3708 | 2.3708 | 2.6238 | 2.6238 | 2019-08-24 19:00 | 1.8214 | 3.1256 | 5.2827 | 5.2827 | 5.2827 | 5.2827
2021-06-27 07:00 | 2.615 | 3.2382 | 3.2898 | 3.5108 | 3.4224 | 3.6435 | 1.5346 | 2.3246 | 2.7676 | 2.7676 | 3.0629 | 3.0629 | 2019-08-24 20:00 | 1.7909 | 3.0733 | 5.1943 | 5.1943 | 5.1943 | 5.1943
2021-06-27 08:00 | 2.715 | 3.3621 | 3.4156 | 3.6451 | 3.5533 | 3.7828 | 1.7402 | 2.6361 | 3.1384 | 3.1384 | 3.4732 | 3.4732 | 2019-08-24 21:00 | 1.73 | 2.9686 | 5.0175 | 5.0175 | 5.0175 | 5.0175
2021-06-27 09:00 | 2.6664 | 3.3019 | 3.3545 | 3.5799 | 3.4897 | 3.7151 | 1.9119 | 2.8962 | 3.4481 | 3.4481 | 3.816 | 3.816 | 2019-08-24 22:00 | 1.608 | 2.7594 | 4.6638 | 4.6638 | 4.6638 | 4.6638
2021-06-27 10:00 | 2.7207 | 3.3692 | 3.4228 | 3.6528 | 3.5608 | 3.7908 | 2.0891 | 3.1646 | 3.7676 | 3.7676 | 4.1696 | 4.1696 | 2019-08-24 23:00 | 1.4251 | 2.4455 | 4.1333 | 4.1333 | 4.1333 | 4.1333
2021-06-27 11:00 | 2.4578 | 3.0436 | 3.092 | 3.2998 | 3.2167 | 3.4245 | 2.072 | 3.1386 | 3.7367 | 3.7367 | 4.1354 | 4.1354 | 2019-08-25 | 1.3413 | 2.3017 | 3.8902 | 3.8902 | 3.8902 | 3.8902
2021-06-27 12:00 | 2.332 | 2.8878 | 2.9338 | 3.131 | 3.0521 | 3.2493 | 2.0262 | 3.0694 | 3.6542 | 3.6542 | 4.0441 | 4.0441 | 2019-08-25 01:00 | 1.2346 | 2.1186 | 3.5808 | 3.5808 | 3.5808 | 3.5808
2021-06-27 13:00 | 2.2291 | 2.7604 | 2.8044 | 2.9928 | 2.9175 | 3.1059 | 2.0348 | 3.0823 | 3.6697 | 3.6697 | 4.0613 | 4.0613 | 2019-08-25 02:00 | 1.227 | 2.1055 | 3.5587 | 3.5587 | 3.5587 | 3.5587
2021-06-27 14:00 | 2.2349 | 2.7675 | 2.8116 | 3.0005 | 2.925 | 3.1139 | 2.0091 | 3.0434 | 3.6233 | 3.6233 | 4.0099 | 4.0099 | 2019-08-25 03:00 | 1.227 | 2.1055 | 3.5587 | 3.5587 | 3.5587 | 3.5587
2021-06-27 15:00 | 2.4835 | 3.0754 | 3.1244 | 3.3343 | 3.2504 | 3.4603 | 2.0291 | 3.0737 | 3.6594 | 3.6594 | 4.0499 | 4.0499 | 2019-08-25 04:00 | 1.3337 | 2.2886 | 3.8681 | 3.8681 | 3.8681 | 3.8681
2021-06-27 16:00 | 2.9093 | 3.6027 | 3.6601 | 3.906 | 3.8077 | 4.0536 | 2.3016 | 3.4864 | 4.1508 | 4.1508 | 4.5937 | 4.5937 | 2019-08-25 05:00 | 1.4251 | 2.4455 | 4.1333 | 4.1333 | 4.1333 | 4.1333
2021-06-27 17:00 | 3.5123 | 4.3495 | 4.4187 | 4.7157 | 4.5969 | 4.8938 | 2.6607 | 4.0304 | 4.7984 | 4.7984 | 5.3104 | 5.3104 | 2019-08-25 06:00 | 1.4709 | 2.524 | 4.266 | 4.266 | 4.266 | 4.266
2021-06-27 18:00 | 3.6009 | 4.4592 | 4.5302 | 4.8346 | 4.7128 | 5.0172 | 2.6559 | 4.0231 | 4.7898 | 4.7898 | 5.3009 | 5.3009 | 2019-08-25 07:00 | 1.7452 | 2.9948 | 5.0617 | 5.0617 | 5.0617 | 5.0617
2021-06-27 19:00 | 3.438 | 4.2575 | 4.3253 | 4.6159 | 4.4996 | 4.7903 | 2.615 | 3.9612 | 4.716 | 4.716 | 5.2192 | 5.2192 | 2019-08-25 08:00 | 1.8138 | 3.1125 | 5.2606 | 5.2606 | 5.2606 | 5.2606
2021-06-27 20:00 | 3.258 | 4.0345 | 4.0988 | 4.3742 | 4.264 | 4.5394 | 2.4492 | 3.7101 | 4.417 | 4.417 | 4.8883 | 4.8883 | 2019-08-25 09:00 | 1.7376 | 2.9817 | 5.0396 | 5.0396 | 5.0396 | 5.0396
2021-06-27 21:00 | 3.1951 | 3.9566 | 4.0197 | 4.2897 | 4.1817 | 4.4518 | 2.3539 | 3.5656 | 4.2451 | 4.2451 | 4.6981 | 4.6981 | 2019-08-25 10:00 | 1.8214 | 3.1256 | 5.2827 | 5.2827 | 5.2827 | 5.2827
2021-06-27 22:00 | 2.8207 | 3.493 | 3.5487 | 3.7871 | 3.6917 | 3.9302 | 2.0794 | 3.1499 | 3.7502 | 3.7502 | 4.1503 | 4.1503 | 2019-08-25 11:00 | 1.8367 | 3.1517 | 5.3269 | 5.3269 | 5.3269 | 5.3269
2021-06-27 23:00 | 2.6067 | 3.228 | 3.2794 | 3.4997 | 3.4116 | 3.6319 | 1.6807 | 2.5459 | 3.0311 | 3.0311 | 3.3545 | 3.3545 | 2019-08-25 12:00 | 1.8671 | 3.204 | 5.4154 | 5.4154 | 5.4154 | 5.4154
2021-06-28 | 2.172 | 2.6897 | 2.7325 | 2.9161 | 2.8427 | 3.0263 | 1.3926 | 2.1095 | 2.5115 | 2.5115 | 2.7795 | 2.7795 | 2019-08-25 13:00 | 1.8595 | 3.191 | 5.3932 | 5.3932 | 5.3932 | 5.3932
2021-06-28 01:00 | 2.0062 | 2.4844 | 2.524 | 2.6936 | 2.6257 | 2.7953 | 1.2146 | 1.8399 | 2.1905 | 2.1905 | 2.4242 | 2.4242 | 2019-08-25 14:00 | 1.8062 | 3.0994 | 5.2385 | 5.2385 | 5.2385 | 5.2385
2021-06-28 02:00 | 1.9406 | 2.4031 | 2.4413 | 2.6054 | 2.5398 | 2.7038 | 1.1803 | 1.7879 | 2.1286 | 2.1286 | 2.3558 | 2.3558 | 2019-08-25 15:00 | 1.7452 | 2.9948 | 5.0617 | 5.0617 | 5.0617 | 5.0617
2021-06-28 03:00 | 2.0034 | 2.4809 | 2.5204 | 2.6897 | 2.622 | 2.7913 | 1.1146 | 1.6884 | 2.0101 | 2.0101 | 2.2246 | 2.2246 | 2019-08-25 16:00 | 1.7605 | 3.0209 | 5.1059 | 5.1059 | 5.1059 | 5.1059
2021-06-28 04:00 | 2.072 | 2.5658 | 2.6067 | 2.7818 | 2.7118 | 2.8869 | 1.2003 | 1.8182 | 2.1647 | 2.1647 | 2.3957 | 2.3957 | 2019-08-25 17:00 | 1.8214 | 3.1256 | 5.2827 | 5.2827 | 5.2827 | 5.2827
2021-06-28 05:00 | 2.5549 | 3.1639 | 3.2143 | 3.4303 | 3.3439 | 3.5598 | 1.3533 | 2.05 | 2.4407 | 2.4407 | 2.7011 | 2.7011 | 2019-08-25 18:00 | 1.8214 | 3.1256 | 5.2827 | 5.2827 | 5.2827 | 5.2827
2021-06-28 06:00 | 3.318 | 4.1088 | 4.1743 | 4.4547 | 4.3425 | 4.623 | 1.669 | 2.5282 | 3.01 | 3.01 | 3.3311 | 3.3311 | 2019-08-25 19:00 | 1.8367 | 3.1517 | 5.3269 | 5.3269 | 5.3269 | 5.3269
2021-06-28 07:00 | 4.0725 | 5.0431 | 5.1234 | 5.4677 | 5.33 | 5.6743 | 2.072 | 3.1386 | 3.7367 | 3.7367 | 4.1354 | 4.1354 | 2019-08-25 20:00 | 1.7757 | 3.0471 | 5.1501 | 5.1501 | 5.1501 | 5.1501
2021-06-28 08:00 | 4.3811 | 5.4253 | 5.5117 | 5.8821 | 5.734 | 6.1043 | 2.1148 | 3.2036 | 3.814 | 3.814 | 4.221 | 4.221 | 2019-08-25 21:00 | 1.669 | 2.864 | 4.8407 | 4.8407 | 4.8407 | 4.8407
2021-06-28 09:00 | 4.1696 | 5.1634 | 5.2457 | 5.5982 | 5.4572 | 5.8096 | 2.0634 | 3.1256 | 3.7212 | 3.7212 | 4.1183 | 4.1183 | 2019-08-25 22:00 | 1.5471 | 2.6548 | 4.487 | 4.487 | 4.487 | 4.487
2021-06-28 10:00 | 3.9553 | 4.898 | 4.976 | 5.3104 | 5.1766 | 5.511 | 1.9777 | 2.9958 | 3.5666 | 3.5666 | 3.9472 | 3.9472 | 2019-08-25 23:00 | 1.3642 | 2.3409 | 3.9565 | 3.9565 | 3.9565 | 3.9565
2021-06-28 11:00 | 3.5581 | 4.4061 | 4.4763 | 4.777 | 4.6567 | 4.9575 | 1.9405 | 2.9395 | 3.4996 | 3.4996 | 3.873 | 3.873 | 2019-08-26 | 1.2879 | 2.2101 | 3.7355 | 3.7355 | 3.7355 | 3.7355
2021-06-28 12:00 | 3.2808 | 4.0628 | 4.1275 | 4.4049 | 4.2939 | 4.5713 | 1.8776 | 2.8442 | 3.3862 | 3.3862 | 3.7475 | 3.7475 | 2019-08-26 01:00 | 1.2194 | 2.0924 | 3.5366 | 3.5366 | 3.5366 | 3.5366
2021-06-28 13:00 | 3.1322 | 3.8788 | 3.9406 | 4.2053 | 4.0994 | 4.3642 | 1.8233 | 2.762 | 3.2883 | 3.2883 | 3.6392 | 3.6392 | 2019-08-26 02:00 | 1.2194 | 2.0924 | 3.5366 | 3.5366 | 3.5366 | 3.5366
2021-06-28 14:00 | 3.218 | 3.9849 | 4.0484 | 4.3204 | 4.2116 | 4.4837 | 1.9119 | 2.8962 | 3.4481 | 3.4481 | 3.816 | 3.816 | 2019-08-26 03:00 | 1.1965 | 2.0532 | 3.4702 | 3.4702 | 3.4702 | 3.4702
2021-06-28 15:00 | 3.3666 | 4.169 | 4.2354 | 4.52 | 4.4061 | 4.6907 | 1.9605 | 2.9698 | 3.5357 | 3.5357 | 3.913 | 3.913 | 2019-08-26 04:00 | 1.2879 | 2.2101 | 3.7355 | 3.7355 | 3.7355 | 3.7355
2021-06-28 16:00 | 3.6667 | 4.5406 | 4.6129 | 4.9229 | 4.7989 | 5.1088 | 2.1377 | 3.2382 | 3.8552 | 3.8552 | 4.2666 | 4.2666 | 2019-08-26 05:00 | 1.4937 | 2.5632 | 4.3323 | 4.3323 | 4.3323 | 4.3323
2021-06-28 17:00 | 4.001 | 4.9546 | 5.0336 | 5.3718 | 5.2365 | 5.5747 | 2.4178 | 3.6624 | 4.3603 | 4.3603 | 4.8256 | 4.8256 | 2019-08-26 06:00 | 1.6309 | 2.7986 | 4.7301 | 4.7301 | 4.7301 | 4.7301
2021-06-28 18:00 | 4.0582 | 5.0254 | 5.1055 | 5.4485 | 5.3113 | 5.6543 | 2.6407 | 4.0001 | 4.7624 | 4.7624 | 5.2705 | 5.2705 | 2019-08-26 07:00 | 2.0043 | 3.4394 | 5.8132 | 5.8132 | 5.8132 | 5.8132
2021-06-28 19:00 | 3.9696 | 4.9157 | 4.994 | 5.3296 | 5.1953 | 5.5309 | 2.6721 | 4.0477 | 4.8191 | 4.8191 | 5.3333 | 5.3333 | 2019-08-26 08:00 | 2.2101 | 3.7925 | 6.41 | 6.41 | 6.41 | 6.41
2021-06-28 20:00 | 3.5952 | 4.4521 | 4.523 | 4.8269 | 4.7054 | 5.0093 | 2.4778 | 3.7534 | 4.4686 | 4.4686 | 4.9454 | 4.9454 | 2019-08-26 09:00 | 2.1872 | 3.7533 | 6.3437 | 6.3437 | 6.3437 | 6.3437
2021-06-28 21:00 | 3.2808 | 4.0628 | 4.1275 | 4.4049 | 4.2939 | 4.5713 | 2.3863 | 3.6148 | 4.3036 | 4.3036 | 4.7628 | 4.7628 | 2019-08-26 10:00 | 2.1491 | 3.6879 | 6.2332 | 6.2332 | 6.2332 | 6.2332
2021-06-28 22:00 | 2.855 | 3.5355 | 3.5918 | 3.8331 | 3.7366 | 3.978 | 2.0291 | 3.0737 | 3.6594 | 3.6594 | 4.0499 | 4.0499 | 2019-08-26 11:00 | 2.1339 | 3.6618 | 6.189 | 6.189 | 6.189 | 6.189
2021-06-28 23:00 | 2.595 | 3.2134 | 3.2646 | 3.484 | 3.3962 | 3.6156 | 1.7547 | 2.6581 | 3.1646 | 3.1646 | 3.5023 | 3.5023 | 2019-08-26 12:00 | 2.2025 | 3.7795 | 6.3879 | 6.3879 | 6.3879 | 6.3879
2021-06-29 | 2.2577 | 2.7958 | 2.8403 | 3.0311 | 2.9548 | 3.1456 | 1.4547 | 2.2035 | 2.6234 | 2.6234 | 2.9033 | 2.9033 | 2019-08-26 13:00 | 2.0729 | 3.5571 | 6.0121 | 6.0121 | 6.0121 | 6.0121
2021-06-29 01:00 | 2.1298 | 2.6375 | 2.6795 | 2.8595 | 2.7875 | 2.9675 | 1.2889 | 1.9524 | 2.3245 | 2.3245 | 2.5725 | 2.5725 | 2019-08-26 14:00 | 2.0882 | 3.5833 | 6.0564 | 6.0564 | 6.0564 | 6.0564
2021-06-29 02:00 | 2.0748 | 2.5693 | 2.6103 | 2.7856 | 2.7155 | 2.8909 | 1.1689 | 1.7706 | 2.108 | 2.108 | 2.3329 | 2.3329 | 2019-08-26 15:00 | 2.0501 | 3.5179 | 5.9458 | 5.9458 | 5.9458 | 5.9458
2021-06-29 03:00 | 2.1005 | 2.6012 | 2.6426 | 2.8202 | 2.7492 | 2.9267 | 1.186 | 1.7966 | 2.1389 | 2.1389 | 2.3672 | 2.3672 | 2019-08-26 16:00 | 2.0577 | 3.531 | 5.9679 | 5.9679 | 5.9679 | 5.9679
2021-06-29 04:00 | 2.112 | 2.6153 | 2.657 | 2.8355 | 2.7641 | 2.9426 | 1.2003 | 1.8182 | 2.1647 | 2.1647 | 2.3957 | 2.3957 | 2019-08-26 17:00 | 2.111 | 3.6225 | 6.1227 | 6.1227 | 6.1227 | 6.1227
2021-06-29 05:00 | 2.5721 | 3.1851 | 3.2359 | 3.4533 | 3.3663 | 3.5837 | 1.3488 | 2.0432 | 2.4325 | 2.4325 | 2.6921 | 2.6921 | 2019-08-26 18:00 | 2.1186 | 3.6356 | 6.1448 | 6.1448 | 6.1448 | 6.1448
2021-06-29 06:00 | 3.436 | 4.255 | 4.3227 | 4.6132 | 4.497 | 4.7875 | 1.6569 | 2.5099 | 2.9882 | 2.9882 | 3.307 | 3.307 | 2019-08-26 19:00 | 1.9967 | 3.4264 | 5.7911 | 5.7911 | 5.7911 | 5.7911
2021-06-29 07:00 | 4.1096 | 5.0891 | 5.1702 | 5.5176 | 5.3786 | 5.726 | 2.2034 | 3.3378 | 3.9738 | 3.9738 | 4.3978 | 4.3978 | 2019-08-26 20:00 | 1.9053 | 3.2694 | 5.5259 | 5.5259 | 5.5259 | 5.5259
2021-06-29 08:00 | 4.2497 | 5.2625 | 5.3464 | 5.7056 | 5.5619 | 5.9211 | 2.2206 | 3.3637 | 4.0047 | 4.0047 | 4.432 | 4.432 | 2019-08-26 21:00 | 1.7605 | 3.0209 | 5.1059 | 5.1059 | 5.1059 | 5.1059
2021-06-29 09:00 | 4.0953 | 5.0714 | 5.1522 | 5.4984 | 5.3599 | 5.7061 | 2.0291 | 3.0737 | 3.6594 | 3.6594 | 4.0499 | 4.0499 | 2019-08-26 22:00 | 1.7147 | 2.9425 | 4.9733 | 4.9733 | 4.9733 | 4.9733
2021-06-29 10:00 | 3.921 | 4.8555 | 4.9329 | 5.2643 | 5.1318 | 5.4632 | 2.0405 | 3.091 | 3.68 | 3.68 | 4.0727 | 4.0727 | 2019-08-26 23:00 | 1.4556 | 2.4978 | 4.2218 | 4.2218 | 4.2218 | 4.2218
2021-06-29 11:00 | 3.6952 | 4.576 | 4.6489 | 4.9612 | 4.8363 | 5.1486 | 2.0605 | 3.1213 | 3.7161 | 3.7161 | 4.1126 | 4.1126 | 2019-08-27 | 1.3261 | 2.2755 | 3.846 | 3.846 | 3.846 | 3.846
2021-06-29 12:00 | 3.3949 | 4.2041 | 4.2711 | 4.558 | 4.4433 | 4.7302 | 2.0005 | 3.0304 | 3.6078 | 3.6078 | 3.9928 | 3.9928 | 2019-08-27 01:00 | 1.2879 | 2.2101 | 3.7355 | 3.7355 | 3.7355 | 3.7355
2021-06-29 13:00 | 3.0294 | 3.7514 | 3.8111 | 4.0672 | 3.9648 | 4.2209 | 1.8891 | 2.8616 | 3.4068 | 3.4068 | 3.7704 | 3.7704 | 2019-08-27 02:00 | 1.2041 | 2.0663 | 3.4923 | 3.4923 | 3.4923 | 3.4923
2021-06-29 14:00 | 2.9608 | 3.6664 | 3.7248 | 3.9751 | 3.875 | 4.1253 | 1.7805 | 2.697 | 3.211 | 3.211 | 3.5536 | 3.5536 | 2019-08-27 03:00 | 1.2194 | 2.0924 | 3.5366 | 3.5366 | 3.5366 | 3.5366
2021-06-29 15:00 | 3.1923 | 3.9531 | 4.0161 | 4.2859 | 4.178 | 4.4478 | 1.9548 | 2.9611 | 3.5254 | 3.5254 | 3.9015 | 3.9015 | 2019-08-27 04:00 | 1.2498 | 2.1447 | 3.625 | 3.625 | 3.625 | 3.625
2021-06-29 16:00 | 3.418 | 4.2327 | 4.3001 | 4.589 | 4.4735 | 4.7624 | 2.1548 | 3.2642 | 3.8862 | 3.8862 | 4.3008 | 4.3008 | 2019-08-27 05:00 | 1.4937 | 2.5632 | 4.3323 | 4.3323 | 4.3323 | 4.3323
2021-06-29 17:00 | 3.9267 | 4.8626 | 4.9401 | 5.272 | 5.1392 | 5.4712 | 2.4263 | 3.6754 | 4.3758 | 4.3758 | 4.8427 | 4.8427 | 2019-08-27 06:00 | 1.6995 | 2.9163 | 4.9291 | 4.9291 | 4.9291 | 4.9291
2021-06-29 18:00 | 4.0639 | 5.0325 | 5.1127 | 5.4562 | 5.3188 | 5.6623 | 2.4978 | 3.7837 | 4.5047 | 4.5047 | 4.9853 | 4.9853 | 2019-08-27 07:00 | 2.0882 | 3.5833 | 6.0564 | 6.0564 | 6.0564 | 6.0564
2021-06-29 19:00 | 3.8939 | 4.822 | 4.8988 | 5.2279 | 5.0963 | 5.4254 | 2.5178 | 3.814 | 4.5407 | 4.5407 | 5.0252 | 5.0252 | 2019-08-27 08:00 | 2.2787 | 3.9102 | 6.6089 | 6.6089 | 6.6089 | 6.6089
2021-06-29 20:00 | 3.5449 | 4.3898 | 4.4597 | 4.7594 | 4.6395 | 4.9392 | 2.4721 | 3.7447 | 4.4583 | 4.4583 | 4.934 | 4.934 | 2019-08-27 09:00 | 2.172 | 3.7271 | 6.2995 | 6.2995 | 6.2995 | 6.2995
2021-06-29 21:00 | 2.9322 | 3.631 | 3.6889 | 3.9367 | 3.8376 | 4.0855 | 2.2806 | 3.4546 | 4.1129 | 4.1129 | 4.5518 | 4.5518 | 2019-08-27 10:00 | 2.1872 | 3.7533 | 6.3437 | 6.3437 | 6.3437 | 6.3437
2021-06-29 22:00 | 2.6178 | 3.2418 | 3.2934 | 3.5147 | 3.4262 | 3.6475 | 1.9836 | 3.0048 | 3.5774 | 3.5774 | 3.9591 | 3.9591 | 2019-08-27 11:00 | 2.1415 | 3.6748 | 6.2111 | 6.2111 | 6.2111 | 6.2111
2021-06-29 23:00 | 2.2807 | 2.8243 | 2.8693 | 3.0621 | 2.985 | 3.1778 | 1.592 | 2.4115 | 2.871 | 2.871 | 3.1774 | 3.1774 | 2019-08-27 12:00 | 2.0805 | 3.5702 | 6.0343 | 6.0343 | 6.0343 | 6.0343
2021-06-30 | 1.9662 | 2.4349 | 2.4736 | 2.6398 | 2.5734 | 2.7396 | 1.3417 | 2.0325 | 2.4198 | 2.4198 | 2.678 | 2.678 | 2019-08-27 13:00 | 2.1796 | 3.7402 | 6.3216 | 6.3216 | 6.3216 | 6.3216
2021-06-30 01:00 | 1.8205 | 2.2544 | 2.2903 | 2.4442 | 2.3826 | 2.5365 | 1.1832 | 1.7923 | 2.1338 | 2.1338 | 2.3615 | 2.3615 | 2019-08-27 14:00 | 2.1491 | 3.6879 | 6.2332 | 6.2332 | 6.2332 | 6.2332
2021-06-30 02:00 | 1.7633 | 2.1836 | 2.2184 | 2.3674 | 2.3078 | 2.4569 | 1.0718 | 1.6235 | 1.9329 | 1.9329 | 2.1392 | 2.1392 | 2019-08-27 15:00 | 2.0653 | 3.5441 | 5.99 | 5.99 | 5.99 | 5.99
2021-06-30 03:00 | 1.789 | 2.2154 | 2.2507 | 2.4019 | 2.3415 | 2.4927 | 1.0717 | 1.6234 | 1.9328 | 1.9328 | 2.139 | 2.139 | 2019-08-27 16:00 | 2.0196 | 3.4656 | 5.8574 | 5.8574 | 5.8574 | 5.8574
2021-06-30 04:00 | 1.8116 | 2.2434 | 2.2791 | 2.4323 | 2.371 | 2.5242 | 1.0831 | 1.6407 | 1.9534 | 1.9534 | 2.1618 | 2.1618 | 2019-08-27 17:00 | 2.0348 | 3.4917 | 5.9016 | 5.9016 | 5.9016 | 5.9016
2021-06-30 05:00 | 2.3738 | 2.9396 | 2.9864 | 3.1871 | 3.1068 | 3.3075 | 1.2432 | 1.8832 | 2.242 | 2.242 | 2.4812 | 2.4812 | 2019-08-27 18:00 | 2.1339 | 3.6618 | 6.189 | 6.189 | 6.189 | 6.189
2021-06-30 06:00 | 3.1179 | 3.8611 | 3.9226 | 4.1861 | 4.0807 | 4.3443 | 1.4861 | 2.2511 | 2.6801 | 2.6801 | 2.9661 | 2.9661 | 2019-08-27 19:00 | 2.0348 | 3.4917 | 5.9016 | 5.9016 | 5.9016 | 5.9016
2021-06-30 07:00 | 3.6238 | 4.4875 | 4.559 | 4.8653 | 4.7428 | 5.0491 | 1.9662 | 2.9784 | 3.546 | 3.546 | 3.9244 | 3.9244 | 2019-08-27 20:00 | 1.9967 | 3.4264 | 5.7911 | 5.7911 | 5.7911 | 5.7911
2021-06-30 08:00 | 3.6867 | 4.5653 | 4.6381 | 4.9497 | 4.8251 | 5.1367 | 1.9576 | 2.9655 | 3.5305 | 3.5305 | 3.9073 | 3.9073 | 2019-08-27 21:00 | 1.9434 | 3.3348 | 5.6364 | 5.6364 | 5.6364 | 5.6364
2021-06-30 09:00 | 3.4409 | 4.261 | 4.3289 | 4.6197 | 4.5034 | 4.7942 | 1.8462 | 2.7966 | 3.3295 | 3.3295 | 3.6848 | 3.6848 | 2019-08-27 22:00 | 1.7223 | 2.9556 | 4.9954 | 4.9954 | 4.9954 | 4.9954
2021-06-30 10:00 | 3.3494 | 4.1477 | 4.2138 | 4.4969 | 4.3837 | 4.6668 | 1.8605 | 2.8183 | 3.3553 | 3.3553 | 3.7133 | 3.7133 | 2019-08-27 23:00 | 1.5928 | 2.7332 | 4.6196 | 4.6196 | 4.6196 | 4.6196
2021-06-30 11:00 | 2.9779 | 3.6877 | 3.7464 | 3.9981 | 3.8974 | 4.1492 | 1.849 | 2.8009 | 3.3347 | 3.3347 | 3.6905 | 3.6905 | 2019-08-28 | 1.4099 | 2.4194 | 4.0891 | 4.0891 | 4.0891 | 4.0891
2021-06-30 12:00 | 2.9179 | 3.6133 | 3.6709 | 3.9176 | 3.8189 | 4.0656 | 1.9091 | 2.8919 | 3.4429 | 3.4429 | 3.8103 | 3.8103 | 2019-08-28 01:00 | 1.2803 | 2.1971 | 3.7134 | 3.7134 | 3.7134 | 3.7134
2021-06-30 13:00 | 2.715 | 3.3621 | 3.4156 | 3.6451 | 3.5533 | 3.7828 | 1.7662 | 2.6754 | 3.1852 | 3.1852 | 3.5251 | 3.5251 | 2019-08-28 02:00 | 1.2498 | 2.1447 | 3.625 | 3.625 | 3.625 | 3.625
2021-06-30 14:00 | 2.7436 | 3.3975 | 3.4516 | 3.6835 | 3.5907 | 3.8227 | 1.7233 | 2.6105 | 3.1079 | 3.1079 | 3.4395 | 3.4395 | 2019-08-28 03:00 | 1.2422 | 2.1317 | 3.6029 | 3.6029 | 3.6029 | 3.6029
2021-06-30 15:00 | 2.8464 | 3.5249 | 3.581 | 3.8216 | 3.7254 | 3.966 | 1.7547 | 2.6581 | 3.1646 | 3.1646 | 3.5023 | 3.5023 | 2019-08-28 04:00 | 1.3184 | 2.2624 | 3.8239 | 3.8239 | 3.8239 | 3.8239
2021-06-30 16:00 | 3.0151 | 3.7337 | 3.7931 | 4.048 | 3.9461 | 4.2009 | 2.0205 | 3.0607 | 3.6439 | 3.6439 | 4.0327 | 4.0327 | 2019-08-28 05:00 | 1.5394 | 2.6417 | 4.4649 | 4.4649 | 4.4649 | 4.4649
2021-06-30 17:00 | 3.5895 | 4.445 | 4.5158 | 4.8193 | 4.6979 | 5.0013 | 2.2492 | 3.407 | 4.0562 | 4.0562 | 4.4891 | 4.4891 | 2019-08-28 06:00 | 1.8519 | 3.1779 | 5.3711 | 5.3711 | 5.3711 | 5.3711
2021-06-30 18:00 | 3.5838 | 4.4379 | 4.5086 | 4.8116 | 4.6904 | 4.9933 | 2.3463 | 3.5542 | 4.2315 | 4.2315 | 4.683 | 4.683 | 2019-08-28 07:00 | 1.9738 | 3.3871 | 5.7248 | 5.7248 | 5.7248 | 5.7248
2021-06-30 19:00 | 3.5381 | 4.3813 | 4.4511 | 4.7502 | 4.6306 | 4.9296 | 2.4063 | 3.6451 | 4.3397 | 4.3397 | 4.8028 | 4.8028 | 2019-08-28 08:00 | 2.2177 | 3.8056 | 6.4321 | 6.4321 | 6.4321 | 6.4321
2021-06-30 20:00 | 3.0985 | 3.837 | 3.8981 | 4.1601 | 4.0553 | 4.3172 | 2.3406 | 3.5456 | 4.2212 | 4.2212 | 4.6716 | 4.6716 | 2019-08-28 09:00 | 2.2634 | 3.8841 | 6.5647 | 6.5647 | 6.5647 | 6.5647
2021-06-30 21:00 | 2.7721 | 3.4329 | 3.4875 | 3.7219 | 3.6281 | 3.8625 | 2.2434 | 3.3984 | 4.0459 | 4.0459 | 4.4777 | 4.4777 | 2019-08-28 10:00 | 2.0805 | 3.5702 | 6.0343 | 6.0343 | 6.0343 | 6.0343
2021-06-30 22:00 | 2.4296 | 3.0087 | 3.0566 | 3.262 | 3.1799 | 3.3852 | 1.8691 | 2.8313 | 3.3708 | 3.3708 | 3.7304 | 3.7304 | 2019-08-28 11:00 | 2.1034 | 3.6094 | 6.1006 | 6.1006 | 6.1006 | 6.1006
2021-06-30 23:00 | 2.2352 | 2.7679 | 2.812 | 3.001 | 2.9254 | 3.1143 | 1.5633 | 2.368 | 2.8193 | 2.8193 | 3.1201 | 3.1201 | 2019-08-28 12:00 | 2.0653 | 3.5441 | 5.99 | 5.99 | 5.99 | 5.99
2021-07-01 | 1.9179 | 2.3751 | 2.4129 | 2.575 | 2.5102 | 2.6723 | 1.2925 | 1.9578 | 2.3309 | 2.3309 | 2.5796 | 2.5796 | 2019-08-28 13:00 | 2.0348 | 3.4917 | 5.9016 | 5.9016 | 5.9016 | 5.9016
2021-07-01 01:00 | 1.7949 | 2.2226 | 2.258 | 2.4098 | 2.3491 | 2.5008 | 1.1346 | 1.7187 | 2.0462 | 2.0462 | 2.2645 | 2.2645 | 2019-08-28 14:00 | 2.0196 | 3.4656 | 5.8574 | 5.8574 | 5.8574 | 5.8574
2021-07-01 02:00 | 1.7404 | 2.1553 | 2.1896 | 2.3367 | 2.2779 | 2.425 | 1.0517 | 1.5931 | 1.8967 | 1.8967 | 2.0991 | 2.0991 | 2019-08-28 15:00 | 1.9891 | 3.4133 | 5.769 | 5.769 | 5.769 | 5.769
2021-07-01 03:00 | 1.7262 | 2.1376 | 2.1716 | 2.3175 | 2.2592 | 2.4051 | 1.0346 | 1.5671 | 1.8658 | 1.8658 | 2.0649 | 2.0649 | 2019-08-28 16:00 | 2.0501 | 3.5179 | 5.9458 | 5.9458 | 5.9458 | 5.9458
2021-07-01 04:00 | 1.7947 | 2.2225 | 2.2579 | 2.4096 | 2.3489 | 2.5006 | 1.0374 | 1.5715 | 1.8709 | 1.8709 | 2.0706 | 2.0706 | 2019-08-28 17:00 | 2.0882 | 3.5833 | 6.0564 | 6.0564 | 6.0564 | 6.0564
2021-07-01 05:00 | 2.1891 | 2.7108 | 2.754 | 2.9391 | 2.865 | 3.0501 | 1.206 | 1.8269 | 2.175 | 2.175 | 2.4071 | 2.4071 | 2019-08-28 18:00 | 2.0882 | 3.5833 | 6.0564 | 6.0564 | 6.0564 | 6.0564
2021-07-01 06:00 | 3.0391 | 3.7635 | 3.8234 | 4.0803 | 3.9775 | 4.2345 | 1.5298 | 2.3174 | 2.7589 | 2.7589 | 3.0533 | 3.0533 | 2019-08-28 19:00 | 1.9815 | 3.4002 | 5.7469 | 5.7469 | 5.7469 | 5.7469
2021-07-01 07:00 | 3.6781 | 4.5547 | 4.6273 | 4.9382 | 4.8138 | 5.1248 | 1.8119 | 2.7447 | 3.2677 | 3.2677 | 3.6163 | 3.6163 | 2019-08-28 20:00 | 1.9357 | 3.3217 | 5.6143 | 5.6143 | 5.6143 | 5.6143
2021-07-01 08:00 | 3.7867 | 4.6892 | 4.7639 | 5.084 | 4.956 | 5.2761 | 1.9205 | 2.9092 | 3.4635 | 3.4635 | 3.8331 | 3.8331 | 2019-08-28 21:00 | 1.829 | 3.1386 | 5.3048 | 5.3048 | 5.3048 | 5.3048
2021-07-01 09:00 | 3.4676 | 4.2941 | 4.3625 | 4.6556 | 4.5384 | 4.8315 | 1.8605 | 2.8183 | 3.3553 | 3.3553 | 3.7133 | 3.7133 | 2019-08-28 22:00 | 1.6538 | 2.8379 | 4.7965 | 4.7965 | 4.7965 | 4.7965
2021-07-01 10:00 | 3.6124 | 4.4733 | 4.5446 | 4.8499 | 4.7278 | 5.0332 | 1.9691 | 2.9828 | 3.5512 | 3.5512 | 3.9301 | 3.9301 | 2019-08-28 23:00 | 1.5318 | 2.6286 | 4.4428 | 4.4428 | 4.4428 | 4.4428
2021-07-01 11:00 | 3.6352 | 4.5016 | 4.5733 | 4.8806 | 4.7577 | 5.065 | 2.0863 | 3.1603 | 3.7625 | 3.7625 | 4.1639 | 4.1639 | 2019-08-29 | 1.3413 | 2.3017 | 3.8902 | 3.8902 | 3.8902 | 3.8902
2021-07-01 12:00 | 3.5066 | 4.3424 | 4.4116 | 4.708 | 4.5894 | 4.8858 | 2.0748 | 3.143 | 3.7419 | 3.7419 | 4.1411 | 4.1411 | 2019-08-29 01:00 | 1.2346 | 2.1186 | 3.5808 | 3.5808 | 3.5808 | 3.5808
2021-07-01 13:00 | 3.4152 | 4.2291 | 4.2965 | 4.5852 | 4.4697 | 4.7584 | 2.0005 | 3.0304 | 3.6078 | 3.6078 | 3.9928 | 3.9928 | 2019-08-29 02:00 | 1.166 | 2.0009 | 3.3818 | 3.3818 | 3.3818 | 3.3818
2021-07-01 14:00 | 3.2751 | 4.0557 | 4.1203 | 4.3972 | 4.2864 | 4.5633 | 2.0005 | 3.0304 | 3.6078 | 3.6078 | 3.9928 | 3.9928 | 2019-08-29 03:00 | 1.166 | 2.0009 | 3.3818 | 3.3818 | 3.3818 | 3.3818
2021-07-01 15:00 | 3.2894 | 4.0734 | 4.1383 | 4.4164 | 4.3051 | 4.5832 | 1.9033 | 2.8832 | 3.4326 | 3.4326 | 3.7989 | 3.7989 | 2019-08-29 04:00 | 1.1889 | 2.0401 | 3.4481 | 3.4481 | 3.4481 | 3.4481
2021-07-01 16:00 | 3.5352 | 4.3778 | 4.4475 | 4.7463 | 4.6268 | 4.9257 | 1.9805 | 3.0001 | 3.5718 | 3.5718 | 3.9529 | 3.9529 | 2019-08-29 05:00 | 1.4632 | 2.5109 | 4.2439 | 4.2439 | 4.2439 | 4.2439
2021-07-01 17:00 | 3.7038 | 4.5866 | 4.6596 | 4.9727 | 4.8475 | 5.1606 | 2.3292 | 3.5282 | 4.2006 | 4.2006 | 4.6488 | 4.6488 | 2019-08-29 06:00 | 1.6233 | 2.7855 | 4.708 | 4.708 | 4.708 | 4.708
2021-07-01 18:00 | 3.7124 | 4.5972 | 4.6704 | 4.9842 | 4.8587 | 5.1725 | 2.4463 | 3.7057 | 4.4119 | 4.4119 | 4.8826 | 4.8826 | 2019-08-29 07:00 | 2.0958 | 3.5964 | 6.0785 | 6.0785 | 6.0785 | 6.0785
2021-07-01 19:00 | 3.4905 | 4.3224 | 4.3913 | 4.6863 | 4.5683 | 4.8634 | 2.4121 | 3.6538 | 4.35 | 4.35 | 4.8142 | 4.8142 | 2019-08-29 08:00 | 2.2711 | 3.8972 | 6.5868 | 6.5868 | 6.5868 | 6.5868
2021-07-01 20:00 | 3.2608 | 4.038 | 4.1024 | 4.378 | 4.2677 | 4.5434 | 2.3578 | 3.5715 | 4.2521 | 4.2521 | 4.7058 | 4.7058 | 2019-08-29 09:00 | 2.1949 | 3.7664 | 6.3658 | 6.3658 | 6.3658 | 6.3658
2021-07-01 21:00 | 2.8464 | 3.5249 | 3.581 | 3.8216 | 3.7254 | 3.966 | 2.1977 | 3.3291 | 3.9635 | 3.9635 | 4.3864 | 4.3864 | 2019-08-29 10:00 | 2.1415 | 3.6748 | 6.2111 | 6.2111 | 6.2111 | 6.2111
2021-07-01 22:00 | 2.4406 | 3.0223 | 3.0705 | 3.2768 | 3.1943 | 3.4006 | 1.9719 | 2.9871 | 3.5563 | 3.5563 | 3.9358 | 3.9358 | 2019-08-29 11:00 | 2.1339 | 3.6618 | 6.189 | 6.189 | 6.189 | 6.189
2021-07-01 23:00 | 2.1732 | 2.6912 | 2.7341 | 2.9178 | 2.8443 | 3.028 | 1.6118 | 2.4416 | 2.9069 | 2.9069 | 3.2171 | 3.2171 | 2019-08-29 12:00 | 2.0958 | 3.5964 | 6.0785 | 6.0785 | 6.0785 | 6.0785
2021-07-02 | 1.8576 | 2.3004 | 2.337 | 2.494 | 2.4312 | 2.5883 | 1.333 | 2.0193 | 2.4041 | 2.4041 | 2.6606 | 2.6606 | 2019-08-29 13:00 | 2.0501 | 3.5179 | 5.9458 | 5.9458 | 5.9458 | 5.9458
2021-07-02 01:00 | 1.8005 | 2.2296 | 2.2651 | 2.4173 | 2.3564 | 2.5086 | 1.1317 | 1.7143 | 2.041 | 2.041 | 2.2588 | 2.2588 | 2019-08-29 14:00 | 2.1034 | 3.6094 | 6.1006 | 6.1006 | 6.1006 | 6.1006
2021-07-02 02:00 | 1.7433 | 2.1588 | 2.1932 | 2.3406 | 2.2816 | 2.429 | 1.0803 | 1.6364 | 1.9482 | 1.9482 | 2.1561 | 2.1561 | 2019-08-29 15:00 | 2.1034 | 3.6094 | 6.1006 | 6.1006 | 6.1006 | 6.1006
2021-07-02 03:00 | 1.7547 | 2.173 | 2.2076 | 2.3559 | 2.2966 | 2.4449 | 1.0576 | 1.6021 | 1.9074 | 1.9074 | 2.1109 | 2.1109 | 2019-08-29 16:00 | 1.9967 | 3.4264 | 5.7911 | 5.7911 | 5.7911 | 5.7911
2021-07-02 04:00 | 1.749 | 2.1659 | 2.2004 | 2.3482 | 2.2891 | 2.4369 | 1.0303 | 1.5606 | 1.858 | 1.858 | 2.0563 | 2.0563 | 2019-08-29 17:00 | 2.0196 | 3.4656 | 5.8574 | 5.8574 | 5.8574 | 5.8574
2021-07-02 05:00 | 2.1548 | 2.6684 | 2.7109 | 2.8931 | 2.8202 | 3.0024 | 1.18 | 1.7874 | 2.128 | 2.128 | 2.3551 | 2.3551 | 2019-08-29 18:00 | 2.0196 | 3.4656 | 5.8574 | 5.8574 | 5.8574 | 5.8574
2021-07-02 06:00 | 3.1808 | 3.9389 | 4.0017 | 4.2706 | 4.163 | 4.4319 | 1.4947 | 2.2641 | 2.6956 | 2.6956 | 2.9832 | 2.9832 | 2019-08-29 19:00 | 1.9967 | 3.4264 | 5.7911 | 5.7911 | 5.7911 | 5.7911
2021-07-02 07:00 | 3.5466 | 4.3919 | 4.4619 | 4.7617 | 4.6418 | 4.9416 | 1.8519 | 2.8053 | 3.3398 | 3.3398 | 3.6962 | 3.6962 | 2019-08-29 20:00 | 1.9053 | 3.2694 | 5.5259 | 5.5259 | 5.5259 | 5.5259
2021-07-02 08:00 | 3.5066 | 4.3424 | 4.4116 | 4.708 | 4.5894 | 4.8858 | 1.8662 | 2.8269 | 3.3656 | 3.3656 | 3.7247 | 3.7247 | 2019-08-29 21:00 | 1.8138 | 3.1125 | 5.2606 | 5.2606 | 5.2606 | 5.2606
2021-07-02 09:00 | 3.3552 | 4.1548 | 4.221 | 4.5046 | 4.3912 | 4.6748 | 1.829 | 2.7706 | 3.2986 | 3.2986 | 3.6506 | 3.6506 | 2019-08-29 22:00 | 1.6538 | 2.8379 | 4.7965 | 4.7965 | 4.7965 | 4.7965
2021-07-02 10:00 | 3.3894 | 4.1973 | 4.2641 | 4.5507 | 4.4361 | 4.7226 | 1.9091 | 2.8919 | 3.4429 | 3.4429 | 3.8103 | 3.8103 | 2019-08-29 23:00 | 1.5394 | 2.6417 | 4.4649 | 4.4649 | 4.4649 | 4.4649
2021-07-02 11:00 | 3.2073 | 3.9718 | 4.035 | 4.3061 | 4.1977 | 4.4688 | 1.8948 | 2.8702 | 3.4171 | 3.4171 | 3.7818 | 3.7818 | 2019-08-30 | 1.3718 | 2.354 | 3.9786 | 3.9786 | 3.9786 | 3.9786
2021-07-02 12:00 | 3.0379 | 3.762 | 3.8219 | 4.0787 | 3.976 | 4.2328 | 1.9148 | 2.9005 | 3.4532 | 3.4532 | 3.8217 | 3.8217 | 2019-08-30 01:00 | 1.2575 | 2.1578 | 3.6471 | 3.6471 | 3.6471 | 3.6471
2021-07-02 13:00 | 3.0465 | 3.7726 | 3.8327 | 4.0902 | 3.9872 | 4.2447 | 1.9319 | 2.9265 | 3.4841 | 3.4841 | 3.8559 | 3.8559 | 2019-08-30 02:00 | 1.1584 | 1.9878 | 3.3597 | 3.3597 | 3.3597 | 3.3597
2021-07-02 14:00 | 2.9893 | 3.7018 | 3.7608 | 4.0135 | 3.9124 | 4.1651 | 1.8576 | 2.8139 | 3.3501 | 3.3501 | 3.7076 | 3.7076 | 2019-08-30 03:00 | 1.1813 | 2.027 | 3.426 | 3.426 | 3.426 | 3.426
2021-07-02 15:00 | 2.9665 | 3.6735 | 3.732 | 3.9828 | 3.8825 | 4.1332 | 1.8548 | 2.8096 | 3.345 | 3.345 | 3.7019 | 3.7019 | 2019-08-30 04:00 | 1.2422 | 2.1317 | 3.6029 | 3.6029 | 3.6029 | 3.6029
2021-07-02 16:00 | 3.2094 | 3.9743 | 4.0376 | 4.3089 | 4.2004 | 4.4717 | 2.1234 | 3.2165 | 3.8295 | 3.8295 | 4.2381 | 4.2381 | 2019-08-30 05:00 | 1.4861 | 2.5501 | 4.3102 | 4.3102 | 4.3102 | 4.3102
2021-07-02 17:00 | 3.6667 | 4.5406 | 4.6129 | 4.9229 | 4.7989 | 5.1088 | 2.3578 | 3.5715 | 4.2521 | 4.2521 | 4.7058 | 4.7058 | 2019-08-30 06:00 | 1.9053 | 3.2694 | 5.5259 | 5.5259 | 5.5259 | 5.5259
2021-07-02 18:00 | 3.6609 | 4.5335 | 4.6057 | 4.9152 | 4.7914 | 5.1009 | 2.4806 | 3.7577 | 4.4737 | 4.4737 | 4.9511 | 4.9511 | 2019-08-30 07:00 | 2.1949 | 3.7664 | 6.3658 | 6.3658 | 6.3658 | 6.3658
2021-07-02 19:00 | 3.4209 | 4.2362 | 4.3037 | 4.5929 | 4.4772 | 4.7664 | 2.4606 | 3.7274 | 4.4377 | 4.4377 | 4.9112 | 4.9112 | 2019-08-30 08:00 | 2.2863 | 3.9233 | 6.631 | 6.631 | 6.631 | 6.631
2021-07-02 20:00 | 3.1065 | 3.8469 | 3.9082 | 4.1708 | 4.0658 | 4.3284 | 2.4378 | 3.6928 | 4.3964 | 4.3964 | 4.8655 | 4.8655 | 2019-08-30 09:00 | 2.3397 | 4.0149 | 6.7858 | 6.7858 | 6.7858 | 6.7858
2021-07-02 21:00 | 3.0465 | 3.7726 | 3.8327 | 4.0902 | 3.9872 | 4.2447 | 2.2634 | 3.4287 | 4.082 | 4.082 | 4.5176 | 4.5176 | 2019-08-30 10:00 | 2.2482 | 3.8579 | 6.5205 | 6.5205 | 6.5205 | 6.5205
2021-07-02 22:00 | 2.5864 | 3.2028 | 3.2538 | 3.4725 | 3.385 | 3.6036 | 2.0362 | 3.0845 | 3.6722 | 3.6722 | 4.064 | 4.064 | 2019-08-30 11:00 | 2.2177 | 3.8056 | 6.4321 | 6.4321 | 6.4321 | 6.4321
2021-07-02 23:00 | 2.3949 | 2.9657 | 3.0129 | 3.2154 | 3.1344 | 3.3369 | 1.639 | 2.4827 | 2.9558 | 2.9558 | 3.2712 | 3.2712 | 2019-08-30 12:00 | 2.1567 | 3.701 | 6.2553 | 6.2553 | 6.2553 | 6.2553
2021-07-03 | 2.0361 | 2.5213 | 2.5615 | 2.7336 | 2.6648 | 2.8369 | 1.3914 | 2.1077 | 2.5093 | 2.5093 | 2.777 | 2.777 | 2019-08-30 13:00 | 2.1491 | 3.6879 | 6.2332 | 6.2332 | 6.2332 | 6.2332
2021-07-03 01:00 | 1.8919 | 2.3428 | 2.3802 | 2.5401 | 2.4761 | 2.636 | 1.2326 | 1.8672 | 2.223 | 2.223 | 2.4601 | 2.4601 | 2019-08-30 14:00 | 2.1644 | 3.7141 | 6.2774 | 6.2774 | 6.2774 | 6.2774
2021-07-03 02:00 | 1.829 | 2.265 | 2.3011 | 2.4557 | 2.3938 | 2.5484 | 1.1431 | 1.7317 | 2.0616 | 2.0616 | 2.2816 | 2.2816 | 2019-08-30 15:00 | 2.2025 | 3.7795 | 6.3879 | 6.3879 | 6.3879 | 6.3879
2021-07-03 03:00 | 1.7719 | 2.1942 | 2.2291 | 2.3789 | 2.319 | 2.4688 | 1.1089 | 1.6797 | 1.9998 | 1.9998 | 2.2132 | 2.2132 | 2019-08-30 16:00 | 2.1644 | 3.7141 | 6.2774 | 6.2774 | 6.2774 | 6.2774
2021-07-03 04:00 | 1.8205 | 2.2544 | 2.2903 | 2.4442 | 2.3826 | 2.5365 | 1.0774 | 1.6321 | 1.9431 | 1.9431 | 2.1504 | 2.1504 | 2019-08-30 17:00 | 2.1186 | 3.6356 | 6.1448 | 6.1448 | 6.1448 | 6.1448
2021-07-03 05:00 | 1.9571 | 2.4235 | 2.4621 | 2.6275 | 2.5614 | 2.7268 | 1.1117 | 1.684 | 2.0049 | 2.0049 | 2.2189 | 2.2189 | 2019-08-30 18:00 | 2.1415 | 3.6748 | 6.2111 | 6.2111 | 6.2111 | 6.2111
2021-07-03 06:00 | 2.2863 | 2.8312 | 2.8763 | 3.0696 | 2.9923 | 3.1855 | 1.3032 | 1.9741 | 2.3503 | 2.3503 | 2.601 | 2.601 | 2019-08-30 19:00 | 2.0729 | 3.5571 | 6.0121 | 6.0121 | 6.0121 | 6.0121
2021-07-03 07:00 | 2.6635 | 3.2984 | 3.3509 | 3.5761 | 3.486 | 3.7112 | 1.669 | 2.5282 | 3.01 | 3.01 | 3.3311 | 3.3311 | 2019-08-30 20:00 | 1.9738 | 3.3871 | 5.7248 | 5.7248 | 5.7248 | 5.7248
2021-07-03 08:00 | 2.6778 | 3.3161 | 3.3689 | 3.5953 | 3.5047 | 3.7311 | 1.749 | 2.6494 | 3.1543 | 3.1543 | 3.4909 | 3.4909 | 2019-08-30 21:00 | 1.8367 | 3.1517 | 5.3269 | 5.3269 | 5.3269 | 5.3269
2021-07-03 09:00 | 2.7807 | 3.4435 | 3.4983 | 3.7334 | 3.6394 | 3.8744 | 1.8719 | 2.8356 | 3.3759 | 3.3759 | 3.7361 | 3.7361 | 2019-08-30 22:00 | 1.7833 | 3.0602 | 5.1722 | 5.1722 | 5.1722 | 5.1722
2021-07-03 10:00 | 2.6778 | 3.3161 | 3.3689 | 3.5953 | 3.5047 | 3.7311 | 1.9605 | 2.9698 | 3.5357 | 3.5357 | 3.913 | 3.913 | 2019-08-30 23:00 | 1.5928 | 2.7332 | 4.6196 | 4.6196 | 4.6196 | 4.6196
2021-07-03 11:00 | 2.4978 | 3.0931 | 3.1424 | 3.3535 | 3.2691 | 3.4802 | 2.032 | 3.078 | 3.6645 | 3.6645 | 4.0556 | 4.0556 | 2019-08-31 | 1.4556 | 2.4978 | 4.2218 | 4.2218 | 4.2218 | 4.2218
2021-07-03 12:00 | 2.4606 | 3.0471 | 3.0956 | 3.3036 | 3.2204 | 3.4284 | 2.0234 | 3.065 | 3.6491 | 3.6491 | 4.0384 | 4.0384 | 2019-08-31 01:00 | 1.3794 | 2.3671 | 4.0007 | 4.0007 | 4.0007 | 4.0007
2021-07-03 13:00 | 2.5064 | 3.1037 | 3.1532 | 3.365 | 3.2803 | 3.4922 | 1.9919 | 3.0174 | 3.5924 | 3.5924 | 3.9757 | 3.9757 | 2019-08-31 02:00 | 1.3108 | 2.2494 | 3.8018 | 3.8018 | 3.8018 | 3.8018
2021-07-03 14:00 | 2.4406 | 3.0223 | 3.0705 | 3.2768 | 3.1943 | 3.4006 | 1.9719 | 2.9871 | 3.5563 | 3.5563 | 3.9358 | 3.9358 | 2019-08-31 03:00 | 1.3718 | 2.354 | 3.9786 | 3.9786 | 3.9786 | 3.9786
2021-07-03 15:00 | 2.8607 | 3.5426 | 3.599 | 3.8408 | 3.7441 | 3.9859 | 2.0798 | 3.1506 | 3.7509 | 3.7509 | 4.1511 | 4.1511 | 2019-08-31 04:00 | 1.3946 | 2.3932 | 4.0449 | 4.0449 | 4.0449 | 4.0449
2021-07-03 16:00 | 2.8979 | 3.5886 | 3.6457 | 3.8907 | 3.7927 | 4.0377 | 2.3406 | 3.5456 | 4.2212 | 4.2212 | 4.6716 | 4.6716 | 2019-08-31 05:00 | 1.509 | 2.5894 | 4.3765 | 4.3765 | 4.3765 | 4.3765
2021-07-03 17:00 | 3.2977 | 4.0837 | 4.1488 | 4.4275 | 4.316 | 4.5948 | 2.7178 | 4.117 | 4.9015 | 4.9015 | 5.4245 | 5.4245 | 2019-08-31 06:00 | 1.608 | 2.7594 | 4.6638 | 4.6638 | 4.6638 | 4.6638
2021-07-03 18:00 | 3.298 | 4.084 | 4.1491 | 4.4279 | 4.3164 | 4.5952 | 2.6407 | 4.0001 | 4.7624 | 4.7624 | 5.2705 | 5.2705 | 2019-08-31 07:00 | 1.6233 | 2.7855 | 4.708 | 4.708 | 4.708 | 4.708
2021-07-03 19:00 | 3.1865 | 3.946 | 4.0089 | 4.2782 | 4.1705 | 4.4399 | 2.6292 | 3.9828 | 4.7417 | 4.7417 | 5.2477 | 5.2477 | 2019-08-31 08:00 | 1.8671 | 3.204 | 5.4154 | 5.4154 | 5.4154 | 5.4154
2021-07-03 20:00 | 2.9893 | 3.7018 | 3.7608 | 4.0135 | 3.9124 | 4.1651 | 2.3635 | 3.5802 | 4.2624 | 4.2624 | 4.7172 | 4.7172 | 2019-08-31 09:00 | 1.9967 | 3.4264 | 5.7911 | 5.7911 | 5.7911 | 5.7911
2021-07-03 21:00 | 2.8347 | 3.5103 | 3.5662 | 3.8059 | 3.71 | 3.9496 | 2.2492 | 3.407 | 4.0562 | 4.0562 | 4.4891 | 4.4891 | 2019-08-31 10:00 | 1.9129 | 3.2825 | 5.548 | 5.548 | 5.548 | 5.548
2021-07-03 22:00 | 2.6535 | 3.2859 | 3.3382 | 3.5625 | 3.4728 | 3.6971 | 2.0262 | 3.0694 | 3.6542 | 3.6542 | 4.0441 | 4.0441 | 2019-08-31 11:00 | 2.0119 | 3.4525 | 5.8353 | 5.8353 | 5.8353 | 5.8353
2021-07-03 23:00 | 2.4224 | 2.9998 | 3.0476 | 3.2523 | 3.1704 | 3.3752 | 1.8376 | 2.7836 | 3.3141 | 3.3141 | 3.6677 | 3.6677 | 2019-08-31 12:00 | 1.8824 | 3.2302 | 5.4596 | 5.4596 | 5.4596 | 5.4596
2021-07-04 | 2.2323 | 2.7644 | 2.8084 | 2.9971 | 2.9216 | 3.1103 | 1.5404 | 2.3334 | 2.778 | 2.778 | 3.0745 | 3.0745 | 2019-08-31 13:00 | 1.8824 | 3.2302 | 5.4596 | 5.4596 | 5.4596 | 5.4596
2021-07-04 01:00 | 2.0119 | 2.4915 | 2.5312 | 2.7012 | 2.6332 | 2.8033 | 1.3175 | 1.9957 | 2.376 | 2.376 | 2.6295 | 2.6295 | 2019-08-31 14:00 | 1.8824 | 3.2302 | 5.4596 | 5.4596 | 5.4596 | 5.4596
2021-07-04 02:00 | 2.0034 | 2.4809 | 2.5204 | 2.6897 | 2.622 | 2.7913 | 1.2832 | 1.9438 | 2.3142 | 2.3142 | 2.5611 | 2.5611 | 2019-08-31 15:00 | 1.8595 | 3.191 | 5.3932 | 5.3932 | 5.3932 | 5.3932
2021-07-04 03:00 | 1.8976 | 2.3499 | 2.3873 | 2.5478 | 2.4836 | 2.644 | 1.1603 | 1.7576 | 2.0925 | 2.0925 | 2.3158 | 2.3158 | 2019-08-31 16:00 | 1.8138 | 3.1125 | 5.2606 | 5.2606 | 5.2606 | 5.2606
2021-07-04 04:00 | 1.9234 | 2.3818 | 2.4197 | 2.5823 | 2.5173 | 2.6798 | 1.1974 | 1.8139 | 2.1596 | 2.1596 | 2.39 | 2.39 | 2019-08-31 17:00 | 1.951 | 3.3479 | 5.6585 | 5.6585 | 5.6585 | 5.6585
2021-07-04 05:00 | 2.0377 | 2.5233 | 2.5635 | 2.7358 | 2.6669 | 2.8391 | 1.2317 | 1.8659 | 2.2214 | 2.2214 | 2.4584 | 2.4584 | 2019-08-31 18:00 | 1.951 | 3.3479 | 5.6585 | 5.6585 | 5.6585 | 5.6585
2021-07-04 06:00 | 2.3035 | 2.8525 | 2.8979 | 3.0926 | 3.0147 | 3.2094 | 1.3203 | 2.0001 | 2.3812 | 2.3812 | 2.6353 | 2.6353 | 2019-08-31 19:00 | 1.8519 | 3.1779 | 5.3711 | 5.3711 | 5.3711 | 5.3711
2021-07-04 07:00 | 2.5235 | 3.125 | 3.1747 | 3.3881 | 3.3027 | 3.516 | 1.5204 | 2.3031 | 2.742 | 2.742 | 3.0345 | 3.0345 | 2019-08-31 20:00 | 1.8824 | 3.2302 | 5.4596 | 5.4596 | 5.4596 | 5.4596
2021-07-04 08:00 | 2.635 | 3.263 | 3.315 | 3.5377 | 3.4486 | 3.6713 | 1.8543 | 2.809 | 3.3442 | 3.3442 | 3.7011 | 3.7011 | 2019-08-31 21:00 | 1.7833 | 3.0602 | 5.1722 | 5.1722 | 5.1722 | 5.1722
2021-07-04 09:00 | 2.7623 | 3.4207 | 3.4752 | 3.7087 | 3.6153 | 3.8488 | 2.0091 | 3.0434 | 3.6233 | 3.6233 | 4.0099 | 4.0099 | 2019-08-31 22:00 | 1.7147 | 2.9425 | 4.9733 | 4.9733 | 4.9733 | 4.9733
2021-07-04 10:00 | 2.895 | 3.585 | 3.6421 | 3.8869 | 3.789 | 4.0337 | 2.2063 | 3.3421 | 3.9789 | 3.9789 | 4.4035 | 4.4035 | 2019-08-31 23:00 | 1.5318 | 2.6286 | 4.4428 | 4.4428 | 4.4428 | 4.4428
2021-07-04 11:00 | 2.7921 | 3.4576 | 3.5127 | 3.7487 | 3.6543 | 3.8903 | 2.1034 | 3.1862 | 3.7934 | 3.7934 | 4.1982 | 4.1982 | 2019-09-01 | 1.448 | 2.4848 | 4.1997 | 4.1997 | 4.1997 | 4.1997
2021-07-04 12:00 | 2.5521 | 3.1604 | 3.2107 | 3.4264 | 3.3401 | 3.5559 | 2.072 | 3.1386 | 3.7367 | 3.7367 | 4.1354 | 4.1354 | 2019-09-01 01:00 | 1.3337 | 2.2886 | 3.8681 | 3.8681 | 3.8681 | 3.8681
2021-07-04 13:00 | 2.7493 | 3.4045 | 3.4588 | 3.6912 | 3.5982 | 3.8306 | 2.1891 | 3.3161 | 3.948 | 3.948 | 4.3693 | 4.3693 | 2019-09-01 02:00 | 1.3184 | 2.2624 | 3.8239 | 3.8239 | 3.8239 | 3.8239
2021-07-04 14:00 | 2.7321 | 3.3833 | 3.4372 | 3.6682 | 3.5758 | 3.8067 | 2.1834 | 3.3075 | 3.9377 | 3.9377 | 4.3579 | 4.3579 | 2019-09-01 03:00 | 1.2879 | 2.2101 | 3.7355 | 3.7355 | 3.7355 | 3.7355
2021-07-04 15:00 | 2.8779 | 3.5638 | 3.6206 | 3.8638 | 3.7665 | 4.0098 | 2.1463 | 3.2512 | 3.8707 | 3.8707 | 4.2837 | 4.2837 | 2019-09-01 04:00 | 1.3718 | 2.354 | 3.9786 | 3.9786 | 3.9786 | 3.9786
2021-07-04 16:00 | 3.2065 | 3.9708 | 4.034 | 4.3051 | 4.1967 | 4.4677 | 2.5549 | 3.8702 | 4.6077 | 4.6077 | 5.0994 | 5.0994 | 2019-09-01 05:00 | 1.4175 | 2.4324 | 4.1112 | 4.1112 | 4.1112 | 4.1112
2021-07-04 17:00 | 3.5695 | 4.4202 | 4.4907 | 4.7924 | 4.6717 | 4.9734 | 2.7321 | 4.1387 | 4.9273 | 4.9273 | 5.453 | 5.453 | 2019-09-01 06:00 | 1.5699 | 2.694 | 4.5533 | 4.5533 | 4.5533 | 4.5533
2021-07-04 18:00 | 3.741 | 4.6326 | 4.7064 | 5.0226 | 4.8961 | 5.2124 | 2.7064 | 4.0997 | 4.8809 | 4.8809 | 5.4017 | 5.4017 | 2019-09-01 07:00 | 1.6233 | 2.7855 | 4.708 | 4.708 | 4.708 | 4.708
2021-07-04 19:00 | 3.6352 | 4.5016 | 4.5733 | 4.8806 | 4.7577 | 5.065 | 2.6378 | 3.9958 | 4.7572 | 4.7572 | 5.2648 | 5.2648 | 2019-09-01 08:00 | 1.8443 | 3.1648 | 5.349 | 5.349 | 5.349 | 5.349
2021-07-04 20:00 | 3.358 | 4.1584 | 4.2246 | 4.5085 | 4.3949 | 4.6788 | 2.5778 | 3.9049 | 4.649 | 4.649 | 5.145 | 5.145 | 2019-09-01 09:00 | 1.9129 | 3.2825 | 5.548 | 5.548 | 5.548 | 5.548
2021-07-04 21:00 | 3.0531 | 3.7808 | 3.841 | 4.0991 | 3.9958 | 4.2539 | 2.4463 | 3.7057 | 4.4119 | 4.4119 | 4.8826 | 4.8826 | 2019-09-01 10:00 | 1.9281 | 3.3087 | 5.5922 | 5.5922 | 5.5922 | 5.5922
2021-07-04 22:00 | 2.6835 | 3.3231 | 3.3761 | 3.6029 | 3.5122 | 3.739 | 2.052 | 3.1083 | 3.7006 | 3.7006 | 4.0955 | 4.0955 | 2019-09-01 11:00 | 1.8595 | 3.191 | 5.3932 | 5.3932 | 5.3932 | 5.3932
2021-07-04 23:00 | 2.4892 | 3.0825 | 3.1316 | 3.342 | 3.2578 | 3.4683 | 1.7439 | 2.6417 | 3.1451 | 3.1451 | 3.4807 | 3.4807 | 2019-09-01 12:00 | 1.8138 | 3.1125 | 5.2606 | 5.2606 | 5.2606 | 5.2606
2021-07-05 | 2.1377 | 2.6472 | 2.6894 | 2.8701 | 2.7978 | 2.9785 | 1.4604 | 2.2122 | 2.6337 | 2.6337 | 2.9148 | 2.9148 | 2019-09-01 13:00 | 1.8519 | 3.1779 | 5.3711 | 5.3711 | 5.3711 | 5.3711
2021-07-05 01:00 | 2.0177 | 2.4986 | 2.5383 | 2.7089 | 2.6407 | 2.8112 | 1.2632 | 1.9135 | 2.2781 | 2.2781 | 2.5212 | 2.5212 | 2019-09-01 14:00 | 1.9053 | 3.2694 | 5.5259 | 5.5259 | 5.5259 | 5.5259
2021-07-05 02:00 | 1.9634 | 2.4313 | 2.47 | 2.636 | 2.5696 | 2.7356 | 1.1717 | 1.7749 | 2.1132 | 2.1132 | 2.3386 | 2.3386 | 2019-09-01 15:00 | 1.8824 | 3.2302 | 5.4596 | 5.4596 | 5.4596 | 5.4596
2021-07-05 03:00 | 1.9205 | 2.3782 | 2.4161 | 2.5785 | 2.5135 | 2.6759 | 1.1374 | 1.723 | 2.0513 | 2.0513 | 2.2702 | 2.2702 | 2019-09-01 16:00 | 1.9281 | 3.3087 | 5.5922 | 5.5922 | 5.5922 | 5.5922
2021-07-05 04:00 | 1.989 | 2.4631 | 2.5023 | 2.6705 | 2.6032 | 2.7713 | 1.1717 | 1.7749 | 2.1132 | 2.1132 | 2.3386 | 2.3386 | 2019-09-01 17:00 | 1.9053 | 3.2694 | 5.5259 | 5.5259 | 5.5259 | 5.5259
2021-07-05 05:00 | 2.4757 | 3.0658 | 3.1146 | 3.3239 | 3.2402 | 3.4495 | 1.3546 | 2.052 | 2.443 | 2.443 | 2.7037 | 2.7037 | 2019-09-01 18:00 | 1.89 | 3.2433 | 5.4817 | 5.4817 | 5.4817 | 5.4817
2021-07-05 06:00 | 3.3552 | 4.1548 | 4.221 | 4.5046 | 4.3912 | 4.6748 | 1.7404 | 2.6364 | 3.1388 | 3.1388 | 3.4737 | 3.4737 | 2019-09-01 19:00 | 1.8214 | 3.1256 | 5.2827 | 5.2827 | 5.2827 | 5.2827
2021-07-05 07:00 | 4.1754 | 5.1705 | 5.2529 | 5.6058 | 5.4647 | 5.8176 | 2.112 | 3.1992 | 3.8089 | 3.8089 | 4.2153 | 4.2153 | 2019-09-01 20:00 | 1.73 | 2.9686 | 5.0175 | 5.0175 | 5.0175 | 5.0175
2021-07-05 08:00 | 4.3125 | 5.3404 | 5.4255 | 5.79 | 5.6442 | 6.0087 | 2.0891 | 3.1646 | 3.7676 | 3.7676 | 4.1696 | 4.1696 | 2019-09-01 21:00 | 1.6919 | 2.9032 | 4.907 | 4.907 | 4.907 | 4.907
2021-07-05 09:00 | 4.0039 | 4.9582 | 5.0372 | 5.3756 | 5.2402 | 5.5787 | 1.9434 | 2.9438 | 3.5048 | 3.5048 | 3.8787 | 3.8787 | 2019-09-01 22:00 | 1.608 | 2.7594 | 4.6638 | 4.6638 | 4.6638 | 4.6638
2021-07-05 10:00 | 3.6467 | 4.5158 | 4.5877 | 4.896 | 4.7727 | 5.0809 | 1.9176 | 2.9048 | 3.4584 | 3.4584 | 3.8274 | 3.8274 | 2019-09-01 23:00 | 1.5242 | 2.6155 | 4.4207 | 4.4207 | 4.4207 | 4.4207
2021-07-05 11:00 | 3.4009 | 4.2114 | 4.2785 | 4.566 | 4.451 | 4.7385 | 1.8833 | 2.8529 | 3.3965 | 3.3965 | 3.7589 | 3.7589 | 2019-09-02 | 1.4327 | 2.4586 | 4.1555 | 4.1555 | 4.1555 | 4.1555
2021-07-05 12:00 | 3.2351 | 4.0062 | 4.07 | 4.3435 | 4.2341 | 4.5075 | 1.8405 | 2.788 | 3.3192 | 3.3192 | 3.6734 | 3.6734 | 2019-09-02 01:00 | 1.3261 | 2.2755 | 3.846 | 3.846 | 3.846 | 3.846
2021-07-05 13:00 | 3.1037 | 3.8434 | 3.9046 | 4.167 | 4.062 | 4.3244 | 1.8919 | 2.8659 | 3.412 | 3.412 | 3.7761 | 3.7761 | 2019-09-02 02:00 | 1.387 | 2.3801 | 4.0228 | 4.0228 | 4.0228 | 4.0228
2021-07-05 14:00 | 3.0294 | 3.7514 | 3.8111 | 4.0672 | 3.9648 | 4.2209 | 1.8862 | 2.8572 | 3.4017 | 3.4017 | 3.7647 | 3.7647 | 2019-09-02 03:00 | 1.3032 | 2.2363 | 3.7797 | 3.7797 | 3.7797 | 3.7797
2021-07-05 15:00 | 3.2065 | 3.9708 | 4.034 | 4.3051 | 4.1967 | 4.4677 | 1.845 | 2.7949 | 3.3274 | 3.3274 | 3.6825 | 3.6825 | 2019-09-02 04:00 | 1.3489 | 2.3148 | 3.9123 | 3.9123 | 3.9123 | 3.9123
2021-07-05 16:00 | 3.5381 | 4.3813 | 4.4511 | 4.7502 | 4.6306 | 4.9296 | 2.0856 | 3.1593 | 3.7613 | 3.7613 | 4.1627 | 4.1627 | 2019-09-02 05:00 | 1.6157 | 2.7725 | 4.6859 | 4.6859 | 4.6859 | 4.6859
2021-07-05 17:00 | 4.1125 | 5.0927 | 5.1738 | 5.5214 | 5.3824 | 5.73 | 2.4721 | 3.7447 | 4.4583 | 4.4583 | 4.934 | 4.934 | 2019-09-02 06:00 | 1.829 | 3.1386 | 5.3048 | 5.3048 | 5.3048 | 5.3048
2021-07-05 18:00 | 4.3183 | 5.3475 | 5.4326 | 5.7977 | 5.6517 | 6.0167 | 2.675 | 4.0521 | 4.8242 | 4.8242 | 5.339 | 5.339 | 2019-09-02 07:00 | 2.0577 | 3.531 | 5.9679 | 5.9679 | 5.9679 | 5.9679
2021-07-05 19:00 | 4.061 | 5.029 | 5.1091 | 5.4524 | 5.315 | 5.6583 | 2.7664 | 4.1906 | 4.9891 | 4.9891 | 5.5215 | 5.5215 | 2019-09-02 08:00 | 2.1415 | 3.6748 | 6.2111 | 6.2111 | 6.2111 | 6.2111
2021-07-05 20:00 | 3.8584 | 4.7781 | 4.8542 | 5.1803 | 5.0499 | 5.376 | 2.6778 | 4.0564 | 4.8294 | 4.8294 | 5.3447 | 5.3447 | 2019-09-02 09:00 | 2.1186 | 3.6356 | 6.1448 | 6.1448 | 6.1448 | 6.1448
2021-07-05 21:00 | 3.4067 | 4.2187 | 4.2859 | 4.5738 | 4.4587 | 4.7466 | 2.4692 | 3.7404 | 4.4531 | 4.4531 | 4.9283 | 4.9283 | 2019-09-02 10:00 | 2.172 | 3.7271 | 6.2995 | 6.2995 | 6.2995 | 6.2995
2021-07-05 22:00 | 2.7836 | 3.447 | 3.5019 | 3.7372 | 3.6431 | 3.8784 | 2.1005 | 3.1819 | 3.7882 | 3.7882 | 4.1925 | 4.1925 | 2019-09-02 11:00 | 2.1263 | 3.6487 | 6.1669 | 6.1669 | 6.1669 | 6.1669
2021-07-05 23:00 | 2.5213 | 3.1223 | 3.172 | 3.3851 | 3.2999 | 3.513 | 1.7576 | 2.6624 | 3.1697 | 3.1697 | 3.508 | 3.508 | 2019-09-02 12:00 | 2.1567 | 3.701 | 6.2553 | 6.2553 | 6.2553 | 6.2553
2021-07-06 | 2.312 | 2.8631 | 2.9087 | 3.1041 | 3.0259 | 3.2214 | 1.5204 | 2.3031 | 2.742 | 2.742 | 3.0345 | 3.0345 | 2019-09-02 13:00 | 2.1644 | 3.7141 | 6.2774 | 6.2774 | 6.2774 | 6.2774
2021-07-06 01:00 | 2.1548 | 2.6684 | 2.7109 | 2.8931 | 2.8202 | 3.0024 | 1.3318 | 2.0174 | 2.4018 | 2.4018 | 2.6581 | 2.6581 | 2019-09-02 14:00 | 2.1567 | 3.701 | 6.2553 | 6.2553 | 6.2553 | 6.2553
2021-07-06 02:00 | 2.072 | 2.5658 | 2.6067 | 2.7818 | 2.7118 | 2.8869 | 1.2517 | 1.8962 | 2.2575 | 2.2575 | 2.4984 | 2.4984 | 2019-09-02 15:00 | 2.1339 | 3.6618 | 6.189 | 6.189 | 6.189 | 6.189
2021-07-06 03:00 | 2.0863 | 2.5835 | 2.6246 | 2.801 | 2.7305 | 2.9068 | 1.1946 | 1.8096 | 2.1544 | 2.1544 | 2.3843 | 2.3843 | 2019-09-02 16:00 | 2.1034 | 3.6094 | 6.1006 | 6.1006 | 6.1006 | 6.1006
2021-07-06 04:00 | 2.192 | 2.7144 | 2.7577 | 2.943 | 2.8688 | 3.0541 | 1.2032 | 1.8226 | 2.1699 | 2.1699 | 2.4014 | 2.4014 | 2019-09-02 17:00 | 2.172 | 3.7271 | 6.2995 | 6.2995 | 6.2995 | 6.2995
2021-07-06 05:00 | 2.7052 | 3.3499 | 3.4033 | 3.6319 | 3.5405 | 3.7691 | 1.3831 | 2.0951 | 2.4943 | 2.4943 | 2.7605 | 2.7605 | 2019-09-02 18:00 | 2.1796 | 3.7402 | 6.3216 | 6.3216 | 6.3216 | 6.3216
2021-07-06 06:00 | 3.7492 | 4.6428 | 4.7167 | 5.0337 | 4.9069 | 5.2238 | 1.7862 | 2.7057 | 3.2213 | 3.2213 | 3.565 | 3.565 | 2019-09-02 19:00 | 2.0043 | 3.4394 | 5.8132 | 5.8132 | 5.8132 | 5.8132
2021-07-06 07:00 | 4.4857 | 5.5548 | 5.6433 | 6.0225 | 5.8708 | 6.25 | 2.1834 | 3.3075 | 3.9377 | 3.9377 | 4.3579 | 4.3579 | 2019-09-02 20:00 | 1.9129 | 3.2825 | 5.548 | 5.548 | 5.548 | 5.548
2021-07-06 08:00 | 4.6441 | 5.7509 | 5.8425 | 6.2351 | 6.0781 | 6.4706 | 2.2149 | 3.3551 | 3.9944 | 3.9944 | 4.4206 | 4.4206 | 2019-09-02 21:00 | 1.8443 | 3.1648 | 5.349 | 5.349 | 5.349 | 5.349
2021-07-06 09:00 | 4.4783 | 5.5457 | 5.634 | 6.0126 | 5.8611 | 6.2397 | 2.1291 | 3.2252 | 3.8398 | 3.8398 | 4.2495 | 4.2495 | 2019-09-02 22:00 | 1.6842 | 2.8902 | 4.8849 | 4.8849 | 4.8849 | 4.8849
2021-07-06 10:00 | 4.5355 | 5.6164 | 5.7059 | 6.0893 | 5.9359 | 6.3193 | 2.212 | 3.3508 | 3.9892 | 3.9892 | 4.4149 | 4.4149 | 2019-09-02 23:00 | 1.7376 | 2.9817 | 5.0396 | 5.0396 | 5.0396 | 5.0396
2021-07-06 11:00 | 4.4354 | 5.4926 | 5.5801 | 5.955 | 5.805 | 6.18 | 2.3063 | 3.4936 | 4.1593 | 4.1593 | 4.6031 | 4.6031 | 2019-09-03 | 1.3794 | 2.3671 | 4.0007 | 4.0007 | 4.0007 | 4.0007
2021-07-06 12:00 | 4.2611 | 5.2767 | 5.3607 | 5.7209 | 5.5769 | 5.9371 | 2.2692 | 3.4373 | 4.0923 | 4.0923 | 4.529 | 4.529 | 2019-09-03 01:00 | 1.387 | 2.3801 | 4.0228 | 4.0228 | 4.0228 | 4.0228
2021-07-06 13:00 | 4.1725 | 5.167 | 5.2493 | 5.602 | 5.4609 | 5.8136 | 2.2777 | 3.4503 | 4.1078 | 4.1078 | 4.5461 | 4.5461 | 2019-09-03 02:00 | 1.2803 | 2.1971 | 3.7134 | 3.7134 | 3.7134 | 3.7134
2021-07-06 14:00 | 4.1096 | 5.0891 | 5.1702 | 5.5176 | 5.3786 | 5.726 | 2.1691 | 3.2858 | 3.9119 | 3.9119 | 4.3294 | 4.3294 | 2019-09-03 03:00 | 1.3337 | 2.2886 | 3.8681 | 3.8681 | 3.8681 | 3.8681
2021-07-06 15:00 | 3.901 | 4.8308 | 4.9077 | 5.2375 | 5.1056 | 5.4353 | 2.0691 | 3.1343 | 3.7315 | 3.7315 | 4.1297 | 4.1297 | 2019-09-03 04:00 | 1.3946 | 2.3932 | 4.0449 | 4.0449 | 4.0449 | 4.0449
2021-07-06 16:00 | 4.2582 | 5.2732 | 5.3571 | 5.7171 | 5.5731 | 5.9331 | 2.3692 | 3.5889 | 4.2727 | 4.2727 | 4.7286 | 4.7286 | 2019-09-03 05:00 | 1.5623 | 2.6809 | 4.5312 | 4.5312 | 4.5312 | 4.5312
2021-07-06 17:00 | 4.5983 | 5.6943 | 5.785 | 6.1737 | 6.0182 | 6.4069 | 2.8293 | 4.2858 | 5.1025 | 5.1025 | 5.647 | 5.647 | 2019-09-03 06:00 | 1.7909 | 3.0733 | 5.1943 | 5.1943 | 5.1943 | 5.1943
2021-07-06 18:00 | 4.6355 | 5.7403 | 5.8317 | 6.2236 | 6.0668 | 6.4587 | 2.8865 | 4.3724 | 5.2056 | 5.2056 | 5.7611 | 5.7611 | 2019-09-03 07:00 | 2.0196 | 3.4656 | 5.8574 | 5.8574 | 5.8574 | 5.8574
2021-07-06 19:00 | 4.5253 | 5.6038 | 5.6931 | 6.0756 | 5.9226 | 6.3051 | 2.9893 | 4.5283 | 5.3912 | 5.3912 | 5.9664 | 5.9664 | 2019-09-03 08:00 | 2.1949 | 3.7664 | 6.3658 | 6.3658 | 6.3658 | 6.3658
2021-07-06 20:00 | 4.0639 | 5.0325 | 5.1127 | 5.4562 | 5.3188 | 5.6623 | 2.7293 | 4.1343 | 4.9221 | 4.9221 | 5.4473 | 5.4473 | 2019-09-03 09:00 | 2.1415 | 3.6748 | 6.2111 | 6.2111 | 6.2111 | 6.2111
2021-07-06 21:00 | 3.5107 | 4.3474 | 4.4166 | 4.7134 | 4.5947 | 4.8915 | 2.5864 | 3.9179 | 4.6644 | 4.6644 | 5.1621 | 5.1621 | 2019-09-03 10:00 | 2.0958 | 3.5964 | 6.0785 | 6.0785 | 6.0785 | 6.0785
2021-07-06 22:00 | 2.9836 | 3.6947 | 3.7536 | 4.0058 | 3.9049 | 4.1571 | 2.3635 | 3.5802 | 4.2624 | 4.2624 | 4.7172 | 4.7172 | 2019-09-03 11:00 | 2.111 | 3.6225 | 6.1227 | 6.1227 | 6.1227 | 6.1227
2021-07-06 23:00 | 2.7355 | 3.3875 | 3.4415 | 3.6727 | 3.5802 | 3.8115 | 1.9602 | 2.9693 | 3.5351 | 3.5351 | 3.9123 | 3.9123 | 2019-09-03 12:00 | 2.1872 | 3.7533 | 6.3437 | 6.3437 | 6.3437 | 6.3437
2021-07-07 | 2.3603 | 2.9229 | 2.9694 | 3.1689 | 3.0891 | 3.2886 | 1.629 | 2.4676 | 2.9378 | 2.9378 | 3.2513 | 3.2513 | 2019-09-03 13:00 | 2.1872 | 3.7533 | 6.3437 | 6.3437 | 6.3437 | 6.3437
2021-07-07 01:00 | 2.2406 | 2.7746 | 2.8188 | 3.0082 | 2.9324 | 3.1218 | 1.3512 | 2.0469 | 2.4369 | 2.4369 | 2.6969 | 2.6969 | 2019-09-03 14:00 | 2.1872 | 3.7533 | 6.3437 | 6.3437 | 6.3437 | 6.3437
2021-07-07 02:00 | 2.1977 | 2.7215 | 2.7649 | 2.9506 | 2.8763 | 3.0621 | 1.3461 | 2.039 | 2.4276 | 2.4276 | 2.6866 | 2.6866 | 2019-09-03 15:00 | 2.2253 | 3.8187 | 6.4542 | 6.4542 | 6.4542 | 6.4542
2021-07-07 03:00 | 2.1777 | 2.6967 | 2.7397 | 2.9238 | 2.8501 | 3.0342 | 1.3146 | 1.9914 | 2.3709 | 2.3709 | 2.6238 | 2.6238 | 2019-09-03 16:00 | 2.2787 | 3.9102 | 6.6089 | 6.6089 | 6.6089 | 6.6089
2021-07-07 04:00 | 2.2892 | 2.8348 | 2.8799 | 3.0734 | 2.996 | 3.1895 | 1.3289 | 2.013 | 2.3966 | 2.3966 | 2.6524 | 2.6524 | 2019-09-03 17:00 | 2.1339 | 3.6618 | 6.189 | 6.189 | 6.189 | 6.189
2021-07-07 05:00 | 2.8654 | 3.5483 | 3.6048 | 3.847 | 3.7502 | 3.9924 | 1.4575 | 2.2079 | 2.6286 | 2.6286 | 2.909 | 2.909 | 2019-09-03 18:00 | 2.0882 | 3.5833 | 6.0564 | 6.0564 | 6.0564 | 6.0564
2021-07-07 06:00 | 4.21 | 5.2134 | 5.2964 | 5.6523 | 5.51 | 5.8658 | 1.7805 | 2.697 | 3.211 | 3.211 | 3.5536 | 3.5536 | 2019-09-03 19:00 | 1.9129 | 3.2825 | 5.548 | 5.548 | 5.548 | 5.548
2021-07-07 07:00 | 4.6441 | 5.7509 | 5.8425 | 6.2351 | 6.0781 | 6.4706 | 2.3092 | 3.4979 | 4.1645 | 4.1645 | 4.6088 | 4.6088 | 2019-09-03 20:00 | 1.8976 | 3.2563 | 5.5038 | 5.5038 | 5.5038 | 5.5038
2021-07-07 08:00 | 4.7641 | 5.8996 | 5.9935 | 6.3963 | 6.2352 | 6.6379 | 2.3063 | 3.4936 | 4.1593 | 4.1593 | 4.6031 | 4.6031 | 2019-09-03 21:00 | 1.7986 | 3.0863 | 5.2164 | 5.2164 | 5.2164 | 5.2164
2021-07-07 09:00 | 4.5069 | 5.5811 | 5.6699 | 6.0509 | 5.8985 | 6.2795 | 2.2377 | 3.3897 | 4.0356 | 4.0356 | 4.4662 | 4.4662 | 2019-09-03 22:00 | 1.7681 | 3.034 | 5.128 | 5.128 | 5.128 | 5.128
2021-07-07 10:00 | 4.0953 | 5.0714 | 5.1522 | 5.4984 | 5.3599 | 5.7061 | 1.9748 | 2.9914 | 3.5615 | 3.5615 | 3.9415 | 3.9415 | 2019-09-03 23:00 | 1.5852 | 2.7202 | 4.5975 | 4.5975 | 4.5975 | 4.5975
2021-07-07 11:00 | 3.8667 | 4.7883 | 4.8646 | 5.1914 | 5.0607 | 5.3876 | 2.0177 | 3.0564 | 3.6388 | 3.6388 | 4.027 | 4.027 | 2019-09-04 | 1.5013 | 2.5763 | 4.3544 | 4.3544 | 4.3544 | 4.3544
2021-07-07 12:00 | 3.3123 | 4.1017 | 4.1671 | 4.4471 | 4.3351 | 4.6151 | 1.9091 | 2.8919 | 3.4429 | 3.4429 | 3.8103 | 3.8103 | 2019-09-04 01:00 | 1.3946 | 2.3932 | 4.0449 | 4.0449 | 4.0449 | 4.0449
2021-07-07 13:00 | 3.1808 | 3.9389 | 4.0017 | 4.2706 | 4.163 | 4.4319 | 1.9977 | 3.0261 | 3.6027 | 3.6027 | 3.9871 | 3.9871 | 2019-09-04 02:00 | 1.3261 | 2.2755 | 3.846 | 3.846 | 3.846 | 3.846
2021-07-07 14:00 | 3.3437 | 4.1407 | 4.2066 | 4.4893 | 4.3762 | 4.6589 | 1.9376 | 2.9352 | 3.4945 | 3.4945 | 3.8673 | 3.8673 | 2019-09-04 03:00 | 1.3337 | 2.2886 | 3.8681 | 3.8681 | 3.8681 | 3.8681
2021-07-07 15:00 | 3.2683 | 4.0473 | 4.1118 | 4.3881 | 4.2776 | 4.5538 | 1.8433 | 2.7923 | 3.3244 | 3.3244 | 3.6791 | 3.6791 | 2019-09-04 04:00 | 1.3032 | 2.2363 | 3.7797 | 3.7797 | 3.7797 | 3.7797
2021-07-07 16:00 | 3.7051 | 4.5882 | 4.6612 | 4.9744 | 4.8492 | 5.1624 | 2.3206 | 3.5153 | 4.1851 | 4.1851 | 4.6317 | 4.6317 | 2019-09-04 05:00 | 1.5775 | 2.7071 | 4.5754 | 4.5754 | 4.5754 | 4.5754
2021-07-07 17:00 | 4.1199 | 5.1019 | 5.1831 | 5.5314 | 5.3921 | 5.7403 | 2.6207 | 3.9698 | 4.7263 | 4.7263 | 5.2306 | 5.2306 | 2019-09-04 06:00 | 1.6919 | 2.9032 | 4.907 | 4.907 | 4.907 | 4.907
2021-07-07 18:00 | 4.3497 | 5.3864 | 5.4722 | 5.8399 | 5.6928 | 6.0605 | 2.8636 | 4.3378 | 5.1644 | 5.1644 | 5.7154 | 5.7154 | 2019-09-04 07:00 | 2.0424 | 3.5048 | 5.9237 | 5.9237 | 5.9237 | 5.9237
2021-07-07 19:00 | 4.0881 | 5.0624 | 5.1431 | 5.4887 | 5.3504 | 5.696 | 2.8779 | 4.3594 | 5.1901 | 5.1901 | 5.7439 | 5.7439 | 2019-09-04 08:00 | 2.1949 | 3.7664 | 6.3658 | 6.3658 | 6.3658 | 6.3658
2021-07-07 20:00 | 3.9278 | 4.864 | 4.9414 | 5.2735 | 5.1407 | 5.4727 | 2.8579 | 4.3291 | 5.1541 | 5.1541 | 5.704 | 5.704 | 2019-09-04 09:00 | 2.2025 | 3.7795 | 6.3879 | 6.3879 | 6.3879 | 6.3879
2021-07-07 21:00 | 3.5352 | 4.3778 | 4.4475 | 4.7463 | 4.6268 | 4.9257 | 2.5978 | 3.9352 | 4.685 | 4.685 | 5.185 | 5.185 | 2019-09-04 10:00 | 2.0729 | 3.5571 | 6.0121 | 6.0121 | 6.0121 | 6.0121
2021-07-07 22:00 | 2.9979 | 3.7124 | 3.7716 | 4.025 | 3.9236 | 4.177 | 2.2577 | 3.42 | 4.0717 | 4.0717 | 4.5062 | 4.5062 | 2019-09-04 11:00 | 2.1644 | 3.7141 | 6.2774 | 6.2774 | 6.2774 | 6.2774
2021-07-07 23:00 | 2.6467 | 3.2776 | 3.3298 | 3.5535 | 3.464 | 3.6877 | 1.9348 | 2.9308 | 3.4893 | 3.4893 | 3.8616 | 3.8616 | 2019-09-04 12:00 | 2.0729 | 3.5571 | 6.0121 | 6.0121 | 6.0121 | 6.0121
2021-07-08 | 2.3406 | 2.8985 | 2.9446 | 3.1425 | 3.0633 | 3.2612 | 1.6719 | 2.5325 | 3.0151 | 3.0151 | 3.3368 | 3.3368 | 2019-09-04 13:00 | 2.1415 | 3.6748 | 6.2111 | 6.2111 | 6.2111 | 6.2111
2021-07-08 01:00 | 2.2177 | 2.7463 | 2.79 | 2.9775 | 2.9025 | 3.09 | 1.4204 | 2.1516 | 2.5616 | 2.5616 | 2.8349 | 2.8349 | 2019-09-04 14:00 | 2.172 | 3.7271 | 6.2995 | 6.2995 | 6.2995 | 6.2995
2021-07-08 02:00 | 2.112 | 2.6153 | 2.657 | 2.8355 | 2.7641 | 2.9426 | 1.3118 | 1.9871 | 2.3657 | 2.3657 | 2.6181 | 2.6181 | 2019-09-04 15:00 | 2.0958 | 3.5964 | 6.0785 | 6.0785 | 6.0785 | 6.0785
2021-07-08 03:00 | 2.0691 | 2.5623 | 2.6031 | 2.778 | 2.708 | 2.8829 | 1.2628 | 1.9128 | 2.2773 | 2.2773 | 2.5203 | 2.5203 | 2019-09-04 16:00 | 2.0805 | 3.5702 | 6.0343 | 6.0343 | 6.0343 | 6.0343
2021-07-08 04:00 | 2.2206 | 2.7498 | 2.7936 | 2.9813 | 2.9063 | 3.094 | 1.2601 | 1.9087 | 2.2725 | 2.2725 | 2.5149 | 2.5149 | 2019-09-04 17:00 | 2.0501 | 3.5179 | 5.9458 | 5.9458 | 5.9458 | 5.9458
2021-07-08 05:00 | 2.7579 | 3.4152 | 3.4696 | 3.7027 | 3.6094 | 3.8426 | 1.5126 | 2.2913 | 2.7279 | 2.7279 | 3.019 | 3.019 | 2019-09-04 18:00 | 1.9815 | 3.4002 | 5.7469 | 5.7469 | 5.7469 | 5.7469
2021-07-08 06:00 | 4.1011 | 5.0785 | 5.1594 | 5.5061 | 5.3674 | 5.7141 | 1.92 | 2.9084 | 3.4626 | 3.4626 | 3.8321 | 3.8321 | 2019-09-04 19:00 | 1.9357 | 3.3217 | 5.6143 | 5.6143 | 5.6143 | 5.6143
2021-07-08 07:00 | 4.8098 | 5.9562 | 6.0511 | 6.4576 | 6.295 | 6.7016 | 2.372 | 3.5932 | 4.2779 | 4.2779 | 4.7343 | 4.7343 | 2019-09-04 20:00 | 1.9357 | 3.3217 | 5.6143 | 5.6143 | 5.6143 | 5.6143
2021-07-08 08:00 | 4.967 | 6.1508 | 6.2488 | 6.6687 | 6.5007 | 6.9206 | 2.3892 | 3.6192 | 4.3088 | 4.3088 | 4.7686 | 4.7686 | 2019-09-04 21:00 | 1.7605 | 3.0209 | 5.1059 | 5.1059 | 5.1059 | 5.1059
2021-07-08 09:00 | 4.6069 | 5.7049 | 5.7958 | 6.1852 | 6.0294 | 6.4189 | 2.3377 | 3.5412 | 4.216 | 4.216 | 4.6659 | 4.6659 | 2019-09-04 22:00 | 1.5852 | 2.7202 | 4.5975 | 4.5975 | 4.5975 | 4.5975
2021-07-08 10:00 | 4.2125 | 5.2165 | 5.2996 | 5.6557 | 5.5133 | 5.8694 | 2.0234 | 3.065 | 3.6491 | 3.6491 | 4.0384 | 4.0384 | 2019-09-04 23:00 | 1.4709 | 2.524 | 4.266 | 4.266 | 4.266 | 4.266
2021-07-08 11:00 | 3.9067 | 4.8379 | 4.9149 | 5.2452 | 5.1131 | 5.4433 | 2.1091 | 3.1949 | 3.8037 | 3.8037 | 4.2096 | 4.2096 | 2019-09-05 | 1.3413 | 2.3017 | 3.8902 | 3.8902 | 3.8902 | 3.8902
2021-07-08 12:00 | 3.7095 | 4.5937 | 4.6668 | 4.9804 | 4.855 | 5.1686 | 1.9834 | 3.0044 | 3.5769 | 3.5769 | 3.9586 | 3.9586 | 2019-09-05 01:00 | 1.2879 | 2.2101 | 3.7355 | 3.7355 | 3.7355 | 3.7355
2021-07-08 13:00 | 3.3523 | 4.1513 | 4.2174 | 4.5008 | 4.3874 | 4.6708 | 2.0462 | 3.0997 | 3.6903 | 3.6903 | 4.0841 | 4.0841 | 2019-09-05 02:00 | 1.2498 | 2.1447 | 3.625 | 3.625 | 3.625 | 3.625
2021-07-08 14:00 | 3.2866 | 4.0699 | 4.1347 | 4.4125 | 4.3014 | 4.5792 | 1.9462 | 2.9481 | 3.5099 | 3.5099 | 3.8844 | 3.8844 | 2019-09-05 03:00 | 1.227 | 2.1055 | 3.5587 | 3.5587 | 3.5587 | 3.5587
2021-07-08 15:00 | 3.3723 | 4.1761 | 4.2426 | 4.5276 | 4.4136 | 4.6987 | 1.9291 | 2.9222 | 3.479 | 3.479 | 3.8502 | 3.8502 | 2019-09-05 04:00 | 1.2727 | 2.184 | 3.6913 | 3.6913 | 3.6913 | 3.6913
2021-07-08 16:00 | 3.7421 | 4.634 | 4.7078 | 5.0242 | 4.8976 | 5.214 | 2.1859 | 3.3113 | 3.9422 | 3.9422 | 4.3629 | 4.3629 | 2019-09-05 05:00 | 1.4861 | 2.5501 | 4.3102 | 4.3102 | 4.3102 | 4.3102
2021-07-08 17:00 | 4.3354 | 5.3687 | 5.4542 | 5.8207 | 5.6741 | 6.0406 | 2.5864 | 3.9179 | 4.6644 | 4.6644 | 5.1621 | 5.1621 | 2019-09-05 06:00 | 1.6614 | 2.8509 | 4.8186 | 4.8186 | 4.8186 | 4.8186
2021-07-08 18:00 | 4.4783 | 5.5457 | 5.634 | 6.0126 | 5.8611 | 6.2397 | 2.8579 | 4.3291 | 5.1541 | 5.1541 | 5.704 | 5.704 | 2019-09-05 07:00 | 1.9434 | 3.3348 | 5.6364 | 5.6364 | 5.6364 | 5.6364
2021-07-08 19:00 | 4.1674 | 5.1607 | 5.2428 | 5.5951 | 5.4542 | 5.8065 | 2.8865 | 4.3724 | 5.2056 | 5.2056 | 5.7611 | 5.7611 | 2019-09-05 08:00 | 2.1339 | 3.6618 | 6.189 | 6.189 | 6.189 | 6.189
2021-07-08 20:00 | 3.9704 | 4.9167 | 4.995 | 5.3306 | 5.1964 | 5.532 | 2.8979 | 4.3897 | 5.2262 | 5.2262 | 5.7839 | 5.7839 | 2019-09-05 09:00 | 2.111 | 3.6225 | 6.1227 | 6.1227 | 6.1227 | 6.1227
2021-07-08 21:00 | 3.5724 | 4.4238 | 4.4942 | 4.7962 | 4.6754 | 4.9774 | 2.6378 | 3.9958 | 4.7572 | 4.7572 | 5.2648 | 5.2648 | 2019-09-05 10:00 | 2.1339 | 3.6618 | 6.189 | 6.189 | 6.189 | 6.189
2021-07-08 22:00 | 3.0665 | 3.7974 | 3.8579 | 4.1171 | 4.0134 | 4.2726 | 2.4153 | 3.6587 | 4.3559 | 4.3559 | 4.8207 | 4.8207 | 2019-09-05 11:00 | 2.1034 | 3.6094 | 6.1006 | 6.1006 | 6.1006 | 6.1006
2021-07-08 23:00 | 2.6635 | 3.2984 | 3.3509 | 3.5761 | 3.486 | 3.7112 | 1.9407 | 2.9398 | 3.5 | 3.5 | 3.8735 | 3.8735 | 2019-09-05 12:00 | 2.3015 | 3.9495 | 6.6753 | 6.6753 | 6.6753 | 6.6753
2021-07-09 | 2.3578 | 2.9197 | 2.9662 | 3.1655 | 3.0858 | 3.2851 | 1.5318 | 2.3204 | 2.7626 | 2.7626 | 3.0574 | 3.0574 | 2019-09-05 13:00 | 2.172 | 3.7271 | 6.2995 | 6.2995 | 6.2995 | 6.2995
2021-07-09 01:00 | 2.2549 | 2.7923 | 2.8368 | 3.0274 | 2.9511 | 3.1417 | 1.4032 | 2.1256 | 2.5306 | 2.5306 | 2.8007 | 2.8007 | 2019-09-05 14:00 | 2.2101 | 3.7925 | 6.41 | 6.41 | 6.41 | 6.41
2021-07-09 02:00 | 2.2299 | 2.7614 | 2.8054 | 2.9939 | 2.9185 | 3.107 | 1.3118 | 1.9871 | 2.3657 | 2.3657 | 2.6181 | 2.6181 | 2019-09-05 15:00 | 2.1186 | 3.6356 | 6.1448 | 6.1448 | 6.1448 | 6.1448
2021-07-09 03:00 | 2.1806 | 2.7003 | 2.7433 | 2.9276 | 2.8539 | 3.0382 | 1.2575 | 1.9048 | 2.2678 | 2.2678 | 2.5098 | 2.5098 | 2019-09-05 16:00 | 2.1872 | 3.7533 | 6.3437 | 6.3437 | 6.3437 | 6.3437
2021-07-09 04:00 | 2.2831 | 2.8272 | 2.8722 | 3.0652 | 2.988 | 3.181 | 1.3261 | 2.0087 | 2.3915 | 2.3915 | 2.6467 | 2.6467 | 2019-09-05 17:00 | 2.1034 | 3.6094 | 6.1006 | 6.1006 | 6.1006 | 6.1006
2021-07-09 05:00 | 2.835 | 3.5107 | 3.5666 | 3.8063 | 3.7104 | 3.9501 | 1.4989 | 2.2705 | 2.7031 | 2.7031 | 2.9915 | 2.9915 | 2019-09-05 18:00 | 1.9891 | 3.4133 | 5.769 | 5.769 | 5.769 | 5.769
2021-07-09 06:00 | 3.7653 | 4.6627 | 4.737 | 5.0553 | 4.928 | 5.2462 | 1.8776 | 2.8442 | 3.3862 | 3.3862 | 3.7475 | 3.7475 | 2019-09-05 19:00 | 1.8748 | 3.2171 | 5.4375 | 5.4375 | 5.4375 | 5.4375
2021-07-09 07:00 | 4.4783 | 5.5457 | 5.634 | 6.0126 | 5.8611 | 6.2397 | 2.2949 | 3.4763 | 4.1387 | 4.1387 | 4.5803 | 4.5803 | 2019-09-05 20:00 | 1.8443 | 3.1648 | 5.349 | 5.349 | 5.349 | 5.349
2021-07-09 08:00 | 4.5412 | 5.6235 | 5.7131 | 6.097 | 5.9434 | 6.3273 | 2.2692 | 3.4373 | 4.0923 | 4.0923 | 4.529 | 4.529 | 2019-09-05 21:00 | 1.7757 | 3.0471 | 5.1501 | 5.1501 | 5.1501 | 5.1501
2021-07-09 09:00 | 4.4097 | 5.4607 | 5.5477 | 5.9205 | 5.7714 | 6.1441 | 2.2749 | 3.446 | 4.1026 | 4.1026 | 4.5404 | 4.5404 | 2019-09-05 22:00 | 1.6233 | 2.7855 | 4.708 | 4.708 | 4.708 | 4.708
2021-07-09 10:00 | 4.2925 | 5.3156 | 5.4003 | 5.7632 | 5.618 | 5.9809 | 2.2034 | 3.3378 | 3.9738 | 3.9738 | 4.3978 | 4.3978 | 2019-09-05 23:00 | 1.5242 | 2.6155 | 4.4207 | 4.4207 | 4.4207 | 4.4207
2021-07-09 11:00 | 3.6181 | 4.4804 | 4.5518 | 4.8576 | 4.7353 | 5.0411 | 2.0177 | 3.0564 | 3.6388 | 3.6388 | 4.027 | 4.027 | 2019-09-06 | 1.3184 | 2.2624 | 3.8239 | 3.8239 | 3.8239 | 3.8239
2021-07-09 12:00 | 3.3237 | 4.1159 | 4.1814 | 4.4624 | 4.35 | 4.631 | 2.0091 | 3.0434 | 3.6233 | 3.6233 | 4.0099 | 4.0099 | 2019-09-06 01:00 | 1.2575 | 2.1578 | 3.6471 | 3.6471 | 3.6471 | 3.6471
2021-07-09 13:00 | 3.1351 | 3.8823 | 3.9442 | 4.2092 | 4.1032 | 4.3682 | 2.0291 | 3.0737 | 3.6594 | 3.6594 | 4.0499 | 4.0499 | 2019-09-06 02:00 | 1.2575 | 2.1578 | 3.6471 | 3.6471 | 3.6471 | 3.6471
2021-07-09 14:00 | 3.1522 | 3.9035 | 3.9657 | 4.2322 | 4.1256 | 4.3921 | 2.0119 | 3.0477 | 3.6285 | 3.6285 | 4.0156 | 4.0156 | 2019-09-06 03:00 | 1.2041 | 2.0663 | 3.4923 | 3.4923 | 3.4923 | 3.4923
2021-07-09 15:00 | 3.1637 | 3.9177 | 3.9801 | 4.2475 | 4.1406 | 4.408 | 2.0548 | 3.1126 | 3.7058 | 3.7058 | 4.1012 | 4.1012 | 2019-09-06 04:00 | 1.2956 | 2.2232 | 3.7576 | 3.7576 | 3.7576 | 3.7576
2021-07-09 16:00 | 3.5749 | 4.427 | 4.4975 | 4.7997 | 4.6788 | 4.981 | 2.3823 | 3.6087 | 4.2963 | 4.2963 | 4.7547 | 4.7547 | 2019-09-06 05:00 | 1.5166 | 2.6025 | 4.3986 | 4.3986 | 4.3986 | 4.3986
2021-07-09 17:00 | 3.8067 | 4.714 | 4.7891 | 5.1109 | 4.9821 | 5.3039 | 2.6407 | 4.0001 | 4.7624 | 4.7624 | 5.2705 | 5.2705 | 2019-09-06 06:00 | 1.6919 | 2.9032 | 4.907 | 4.907 | 4.907 | 4.907
2021-07-09 18:00 | 3.8181 | 4.7281 | 4.8035 | 5.1262 | 4.9971 | 5.3199 | 2.7121 | 4.1083 | 4.8912 | 4.8912 | 5.4131 | 5.4131 | 2019-09-06 07:00 | 1.9205 | 3.2956 | 5.5701 | 5.5701 | 5.5701 | 5.5701
2021-07-09 19:00 | 3.6041 | 4.4631 | 4.5342 | 4.8389 | 4.717 | 5.0217 | 2.7979 | 4.2382 | 5.0458 | 5.0458 | 5.5842 | 5.5842 | 2019-09-06 08:00 | 2.0729 | 3.5571 | 6.0121 | 6.0121 | 6.0121 | 6.0121
2021-07-09 20:00 | 3.3323 | 4.1265 | 4.1922 | 4.4739 | 4.3612 | 4.6429 | 2.7464 | 4.1603 | 4.9531 | 4.9531 | 5.4816 | 5.4816 | 2019-09-06 09:00 | 2.0958 | 3.5964 | 6.0785 | 6.0785 | 6.0785 | 6.0785
2021-07-09 21:00 | 3.0779 | 3.8115 | 3.8722 | 4.1324 | 4.0284 | 4.2885 | 2.5235 | 3.8226 | 4.551 | 4.551 | 5.0366 | 5.0366 | 2019-09-06 10:00 | 2.233 | 3.8318 | 6.4763 | 6.4763 | 6.4763 | 6.4763
2021-07-09 22:00 | 2.6778 | 3.3161 | 3.3689 | 3.5953 | 3.5047 | 3.7311 | 2.2464 | 3.4028 | 4.0513 | 4.0513 | 4.4835 | 4.4835 | 2019-09-06 11:00 | 2.3778 | 4.0802 | 6.8963 | 6.8963 | 6.8963 | 6.8963
2021-07-09 23:00 | 2.5178 | 3.1179 | 3.1675 | 3.3804 | 3.2952 | 3.5081 | 1.8409 | 2.7886 | 3.32 | 3.32 | 3.6743 | 3.6743 | 2019-09-06 12:00 | 2.1796 | 3.7402 | 6.3216 | 6.3216 | 6.3216 | 6.3216
2021-07-10 | 2.2216 | 2.7511 | 2.7949 | 2.9827 | 2.9076 | 3.0954 | 1.5693 | 2.3771 | 2.8301 | 2.8301 | 3.1321 | 3.1321 | 2019-09-06 13:00 | 2.1872 | 3.7533 | 6.3437 | 6.3437 | 6.3437 | 6.3437
2021-07-10 01:00 | 2.0891 | 2.587 | 2.6282 | 2.8048 | 2.7342 | 2.9108 | 1.4004 | 2.1213 | 2.5255 | 2.5255 | 2.795 | 2.795 | 2019-09-06 14:00 | 2.0729 | 3.5571 | 6.0121 | 6.0121 | 6.0121 | 6.0121
2021-07-10 02:00 | 2.032 | 2.5162 | 2.5563 | 2.7281 | 2.6594 | 2.8312 | 1.2689 | 1.9221 | 2.2884 | 2.2884 | 2.5326 | 2.5326 | 2019-09-06 15:00 | 2.1491 | 3.6879 | 6.2332 | 6.2332 | 6.2332 | 6.2332
2021-07-10 03:00 | 1.9719 | 2.4419 | 2.4808 | 2.6475 | 2.5808 | 2.7475 | 1.2832 | 1.9438 | 2.3142 | 2.3142 | 2.5611 | 2.5611 | 2019-09-06 16:00 | 2.1186 | 3.6356 | 6.1448 | 6.1448 | 6.1448 | 6.1448
2021-07-10 04:00 | 2.0748 | 2.5693 | 2.6103 | 2.7856 | 2.7155 | 2.8909 | 1.2432 | 1.8832 | 2.242 | 2.242 | 2.4812 | 2.4812 | 2019-09-06 17:00 | 2.1186 | 3.6356 | 6.1448 | 6.1448 | 6.1448 | 6.1448
2021-07-10 05:00 | 2.2263 | 2.7569 | 2.8008 | 2.989 | 2.9137 | 3.1019 | 1.2603 | 1.9091 | 2.2729 | 2.2729 | 2.5155 | 2.5155 | 2019-09-06 18:00 | 2.0882 | 3.5833 | 6.0564 | 6.0564 | 6.0564 | 6.0564
2021-07-10 06:00 | 2.5435 | 3.1497 | 3.1999 | 3.4149 | 3.3289 | 3.5439 | 1.5194 | 2.3016 | 2.7402 | 2.7402 | 3.0326 | 3.0326 | 2019-09-06 19:00 | 1.9738 | 3.3871 | 5.7248 | 5.7248 | 5.7248 | 5.7248
2021-07-10 07:00 | 3.0579 | 3.7868 | 3.8471 | 4.1056 | 4.0022 | 4.2607 | 1.9154 | 2.9015 | 3.4544 | 3.4544 | 3.8229 | 3.8229 | 2019-09-06 20:00 | 1.7986 | 3.0863 | 5.2164 | 5.2164 | 5.2164 | 5.2164
2021-07-10 08:00 | 3.0522 | 3.7797 | 3.8399 | 4.0979 | 3.9947 | 4.2527 | 2.0034 | 3.0347 | 3.613 | 3.613 | 3.9985 | 3.9985 | 2019-09-06 21:00 | 1.7147 | 2.9425 | 4.9733 | 4.9733 | 4.9733 | 4.9733
2021-07-10 09:00 | 2.9665 | 3.6735 | 3.732 | 3.9828 | 3.8825 | 4.1332 | 2.0875 | 3.1621 | 3.7646 | 3.7646 | 4.1663 | 4.1663 | 2019-09-06 22:00 | 1.5852 | 2.7202 | 4.5975 | 4.5975 | 4.5975 | 4.5975
2021-07-10 10:00 | 2.9465 | 3.6487 | 3.7069 | 3.9559 | 3.8563 | 4.1054 | 2.1205 | 3.2122 | 3.8243 | 3.8243 | 4.2324 | 4.2324 | 2019-09-06 23:00 | 1.5852 | 2.7202 | 4.5975 | 4.5975 | 4.5975 | 4.5975
2021-07-10 11:00 | 2.7921 | 3.4576 | 3.5127 | 3.7487 | 3.6543 | 3.8903 | 2.1663 | 3.2815 | 3.9068 | 3.9068 | 4.3236 | 4.3236 | 2019-09-07 | 1.3184 | 2.2624 | 3.8239 | 3.8239 | 3.8239 | 3.8239
2021-07-10 12:00 | 2.7326 | 3.3839 | 3.4378 | 3.6688 | 3.5764 | 3.8074 | 2.312 | 3.5023 | 4.1696 | 4.1696 | 4.6146 | 4.6146 | 2019-09-07 01:00 | 1.3413 | 2.3017 | 3.8902 | 3.8902 | 3.8902 | 3.8902
2021-07-10 13:00 | 2.7979 | 3.4647 | 3.5199 | 3.7564 | 3.6618 | 3.8983 | 2.3235 | 3.5196 | 4.1903 | 4.1903 | 4.6374 | 4.6374 | 2019-09-07 02:00 | 1.2727 | 2.184 | 3.6913 | 3.6913 | 3.6913 | 3.6913
2021-07-10 14:00 | 2.7178 | 3.3656 | 3.4192 | 3.649 | 3.5571 | 3.7868 | 2.2263 | 3.3724 | 4.015 | 4.015 | 4.4434 | 4.4434 | 2019-09-07 03:00 | 1.3184 | 2.2624 | 3.8239 | 3.8239 | 3.8239 | 3.8239
2021-07-10 15:00 | 2.7007 | 3.3444 | 3.3977 | 3.6259 | 3.5346 | 3.7629 | 2.232 | 3.3811 | 4.0253 | 4.0253 | 4.4548 | 4.4548 | 2019-09-07 04:00 | 1.2575 | 2.1578 | 3.6471 | 3.6471 | 3.6471 | 3.6471
2021-07-10 16:00 | 2.8893 | 3.578 | 3.6349 | 3.8792 | 3.7815 | 4.0257 | 2.4268 | 3.6762 | 4.3767 | 4.3767 | 4.8437 | 4.8437 | 2019-09-07 05:00 | 1.3946 | 2.3932 | 4.0449 | 4.0449 | 4.0449 | 4.0449
2021-07-10 17:00 | 3.3552 | 4.1548 | 4.221 | 4.5046 | 4.3912 | 4.6748 | 2.5921 | 3.9265 | 4.6747 | 4.6747 | 5.1735 | 5.1735 | 2019-09-07 06:00 | 1.4404 | 2.4717 | 4.1776 | 4.1776 | 4.1776 | 4.1776
2021-07-10 18:00 | 3.298 | 4.084 | 4.1491 | 4.4279 | 4.3164 | 4.5952 | 2.6578 | 4.0261 | 4.7933 | 4.7933 | 5.3047 | 5.3047 | 2019-09-07 07:00 | 1.6614 | 2.8509 | 4.8186 | 4.8186 | 4.8186 | 4.8186
2021-07-10 19:00 | 3.2951 | 4.0805 | 4.1455 | 4.424 | 4.3126 | 4.5912 | 2.6578 | 4.0261 | 4.7933 | 4.7933 | 5.3047 | 5.3047 | 2019-09-07 08:00 | 1.7681 | 3.034 | 5.128 | 5.128 | 5.128 | 5.128
2021-07-10 20:00 | 3.0008 | 3.716 | 3.7752 | 4.0288 | 3.9274 | 4.181 | 2.5064 | 3.7967 | 4.5201 | 4.5201 | 5.0024 | 5.0024 | 2019-09-07 09:00 | 1.9434 | 3.3348 | 5.6364 | 5.6364 | 5.6364 | 5.6364
2021-07-10 21:00 | 2.9237 | 3.6205 | 3.6782 | 3.9254 | 3.8265 | 4.0736 | 2.3663 | 3.5845 | 4.2676 | 4.2676 | 4.7229 | 4.7229 | 2019-09-07 10:00 | 1.8519 | 3.1779 | 5.3711 | 5.3711 | 5.3711 | 5.3711
2021-07-10 22:00 | 2.715 | 3.3621 | 3.4156 | 3.6451 | 3.5533 | 3.7828 | 2.2377 | 3.3897 | 4.0356 | 4.0356 | 4.4662 | 4.4662 | 2019-09-07 11:00 | 1.9053 | 3.2694 | 5.5259 | 5.5259 | 5.5259 | 5.5259
2021-07-10 23:00 | 2.6467 | 3.2775 | 3.3297 | 3.5534 | 3.4639 | 3.6876 | 1.9834 | 3.0044 | 3.5769 | 3.5769 | 3.9586 | 3.9586 | 2019-09-07 12:00 | 1.8824 | 3.2302 | 5.4596 | 5.4596 | 5.4596 | 5.4596
2021-07-11 | 2.4035 | 2.9763 | 3.0237 | 3.2269 | 3.1456 | 3.3488 | 1.6606 | 2.5154 | 2.9947 | 2.9947 | 3.3143 | 3.3143 | 2019-09-07 13:00 | 1.9434 | 3.3348 | 5.6364 | 5.6364 | 5.6364 | 5.6364
2021-07-11 01:00 | 2.1977 | 2.7215 | 2.7649 | 2.9506 | 2.8763 | 3.0621 | 1.4352 | 2.174 | 2.5883 | 2.5883 | 2.8645 | 2.8645 | 2019-09-07 14:00 | 1.9129 | 3.2825 | 5.548 | 5.548 | 5.548 | 5.548
2021-07-11 02:00 | 2.0748 | 2.5693 | 2.6103 | 2.7856 | 2.7155 | 2.8909 | 1.3346 | 2.0217 | 2.4069 | 2.4069 | 2.6638 | 2.6638 | 2019-09-07 15:00 | 1.9129 | 3.2825 | 5.548 | 5.548 | 5.548 | 5.548
2021-07-11 03:00 | 1.9843 | 2.4572 | 2.4964 | 2.6641 | 2.597 | 2.7647 | 1.2432 | 1.8832 | 2.242 | 2.242 | 2.4812 | 2.4812 | 2019-09-07 16:00 | 1.9357 | 3.3217 | 5.6143 | 5.6143 | 5.6143 | 5.6143
2021-07-11 04:00 | 2.152 | 2.6649 | 2.7073 | 2.8892 | 2.8165 | 2.9984 | 1.2232 | 1.8529 | 2.2059 | 2.2059 | 2.4413 | 2.4413 | 2019-09-07 17:00 | 1.9281 | 3.3087 | 5.5922 | 5.5922 | 5.5922 | 5.5922
2021-07-11 05:00 | 2.1949 | 2.718 | 2.7613 | 2.9468 | 2.8726 | 3.0581 | 1.306 | 1.9784 | 2.3554 | 2.3554 | 2.6067 | 2.6067 | 2019-09-07 18:00 | 1.8824 | 3.2302 | 5.4596 | 5.4596 | 5.4596 | 5.4596
2021-07-11 06:00 | 2.4521 | 3.0365 | 3.0849 | 3.2921 | 3.2092 | 3.4165 | 1.4298 | 2.1658 | 2.5785 | 2.5785 | 2.8537 | 2.8537 | 2019-09-07 19:00 | 1.8138 | 3.1125 | 5.2606 | 5.2606 | 5.2606 | 5.2606
2021-07-11 07:00 | 2.8036 | 3.4718 | 3.5271 | 3.7641 | 3.6693 | 3.9063 | 1.7062 | 2.5845 | 3.077 | 3.077 | 3.4053 | 3.4053 | 2019-09-07 20:00 | 1.7909 | 3.0733 | 5.1943 | 5.1943 | 5.1943 | 5.1943
2021-07-11 08:00 | 2.8379 | 3.5143 | 3.5702 | 3.8101 | 3.7142 | 3.9541 | 1.9319 | 2.9264 | 3.484 | 3.484 | 3.8558 | 3.8558 | 2019-09-07 21:00 | 1.6919 | 2.9032 | 4.907 | 4.907 | 4.907 | 4.907
2021-07-11 09:00 | 2.8464 | 3.5249 | 3.581 | 3.8216 | 3.7254 | 3.966 | 2.0405 | 3.091 | 3.68 | 3.68 | 4.0727 | 4.0727 | 2019-09-07 22:00 | 1.5699 | 2.694 | 4.5533 | 4.5533 | 4.5533 | 4.5533
2021-07-11 10:00 | 2.9465 | 3.6487 | 3.7069 | 3.9559 | 3.8563 | 4.1054 | 2.2434 | 3.3984 | 4.0459 | 4.0459 | 4.4777 | 4.4777 | 2019-09-07 23:00 | 1.5166 | 2.6025 | 4.3986 | 4.3986 | 4.3986 | 4.3986
2021-07-11 11:00 | 2.695 | 3.3373 | 3.3905 | 3.6183 | 3.5271 | 3.755 | 2.152 | 3.2598 | 3.881 | 3.881 | 4.2951 | 4.2951 | 2019-09-08 | 1.3718 | 2.354 | 3.9786 | 3.9786 | 3.9786 | 3.9786
2021-07-11 12:00 | 2.5721 | 3.1851 | 3.2359 | 3.4533 | 3.3663 | 3.5837 | 2.2034 | 3.3378 | 3.9738 | 3.9738 | 4.3978 | 4.3978 | 2019-09-08 01:00 | 1.2575 | 2.1578 | 3.6471 | 3.6471 | 3.6471 | 3.6471
2021-07-11 13:00 | 2.4949 | 3.0896 | 3.1388 | 3.3497 | 3.2653 | 3.4762 | 2.3006 | 3.485 | 4.149 | 4.149 | 4.5917 | 4.5917 | 2019-09-08 02:00 | 1.2879 | 2.2101 | 3.7355 | 3.7355 | 3.7355 | 3.7355
2021-07-11 14:00 | 2.5835 | 3.1993 | 3.2502 | 3.4686 | 3.3813 | 3.5997 | 2.2206 | 3.3637 | 4.0047 | 4.0047 | 4.432 | 4.432 | 2019-09-08 03:00 | 1.227 | 2.1055 | 3.5587 | 3.5587 | 3.5587 | 3.5587
2021-07-11 15:00 | 2.5235 | 3.125 | 3.1747 | 3.3881 | 3.3027 | 3.516 | 2.1977 | 3.3291 | 3.9635 | 3.9635 | 4.3864 | 4.3864 | 2019-09-08 04:00 | 1.3413 | 2.3017 | 3.8902 | 3.8902 | 3.8902 | 3.8902
2021-07-11 16:00 | 2.8865 | 3.5744 | 3.6314 | 3.8754 | 3.7778 | 4.0218 | 2.4178 | 3.6624 | 4.3603 | 4.3603 | 4.8256 | 4.8256 | 2019-09-08 05:00 | 1.387 | 2.3801 | 4.0228 | 4.0228 | 4.0228 | 4.0228
2021-07-11 17:00 | 3.4323 | 4.2504 | 4.3181 | 4.6082 | 4.4922 | 4.7823 | 2.6991 | 4.0886 | 4.8677 | 4.8677 | 5.3871 | 5.3871 | 2019-09-08 06:00 | 1.448 | 2.4848 | 4.1997 | 4.1997 | 4.1997 | 4.1997
2021-07-11 18:00 | 3.5638 | 4.4132 | 4.4835 | 4.7847 | 4.6642 | 4.9655 | 2.7178 | 4.117 | 4.9015 | 4.9015 | 5.4245 | 5.4245 | 2019-09-08 07:00 | 1.608 | 2.7594 | 4.6638 | 4.6638 | 4.6638 | 4.6638
2021-07-11 19:00 | 3.5581 | 4.4061 | 4.4763 | 4.777 | 4.6567 | 4.9575 | 2.7178 | 4.117 | 4.9015 | 4.9015 | 5.4245 | 5.4245 | 2019-09-08 08:00 | 1.8214 | 3.1256 | 5.2827 | 5.2827 | 5.2827 | 5.2827
2021-07-11 20:00 | 3.2808 | 4.0628 | 4.1275 | 4.4049 | 4.2939 | 4.5713 | 2.6464 | 4.0088 | 4.7727 | 4.7727 | 5.2819 | 5.2819 | 2019-09-08 09:00 | 1.8062 | 3.0994 | 5.2385 | 5.2385 | 5.2385 | 5.2385
2021-07-11 21:00 | 3.0808 | 3.8151 | 3.8758 | 4.1363 | 4.0321 | 4.2925 | 2.4378 | 3.6928 | 4.3964 | 4.3964 | 4.8655 | 4.8655 | 2019-09-08 10:00 | 1.8443 | 3.1648 | 5.349 | 5.349 | 5.349 | 5.349
2021-07-11 22:00 | 2.7378 | 3.3904 | 3.4444 | 3.6758 | 3.5833 | 3.8147 | 2.0721 | 3.1388 | 3.7369 | 3.7369 | 4.1357 | 4.1357 | 2019-09-08 11:00 | 1.8214 | 3.1256 | 5.2827 | 5.2827 | 5.2827 | 5.2827
2021-07-11 23:00 | 2.5092 | 3.1073 | 3.1568 | 3.3689 | 3.284 | 3.4961 | 1.8405 | 2.788 | 3.3192 | 3.3192 | 3.6734 | 3.6734 | 2019-09-08 12:00 | 1.8824 | 3.2302 | 5.4596 | 5.4596 | 5.4596 | 5.4596
2021-07-12 | 2.1634 | 2.679 | 2.7217 | 2.9046 | 2.8314 | 3.0143 | 1.5604 | 2.3637 | 2.8141 | 2.8141 | 3.1144 | 3.1144 | 2019-09-08 13:00 | 1.7681 | 3.034 | 5.128 | 5.128 | 5.128 | 5.128
2021-07-12 01:00 | 2.0834 | 2.58 | 2.621 | 2.7972 | 2.7267 | 2.9028 | 1.3232 | 2.0044 | 2.3863 | 2.3863 | 2.641 | 2.641 | 2019-09-08 14:00 | 1.8367 | 3.1517 | 5.3269 | 5.3269 | 5.3269 | 5.3269
2021-07-12 02:00 | 1.9891 | 2.4632 | 2.5024 | 2.6705 | 2.6033 | 2.7714 | 1.2413 | 1.8803 | 2.2386 | 2.2386 | 2.4774 | 2.4774 | 2019-09-08 15:00 | 1.9357 | 3.3217 | 5.6143 | 5.6143 | 5.6143 | 5.6143
2021-07-12 03:00 | 1.9586 | 2.4254 | 2.464 | 2.6296 | 2.5634 | 2.729 | 1.2032 | 1.8226 | 2.1699 | 2.1699 | 2.4014 | 2.4014 | 2019-09-08 16:00 | 1.9891 | 3.4133 | 5.769 | 5.769 | 5.769 | 5.769
2021-07-12 04:00 | 2.1491 | 2.6613 | 2.7037 | 2.8854 | 2.8127 | 2.9944 | 1.2654 | 1.9168 | 2.2821 | 2.2821 | 2.5256 | 2.5256 | 2019-09-08 17:00 | 1.9738 | 3.3871 | 5.7248 | 5.7248 | 5.7248 | 5.7248
2021-07-12 05:00 | 2.6292 | 3.2559 | 3.3078 | 3.53 | 3.4411 | 3.6634 | 1.4575 | 2.2079 | 2.6286 | 2.6286 | 2.909 | 2.909 | 2019-09-08 18:00 | 1.9738 | 3.3871 | 5.7248 | 5.7248 | 5.7248 | 5.7248
2021-07-12 06:00 | 3.961 | 4.9051 | 4.9832 | 5.3181 | 5.1841 | 5.519 | 1.7719 | 2.6841 | 3.1955 | 3.1955 | 3.5365 | 3.5365 | 2019-09-08 19:00 | 1.8824 | 3.2302 | 5.4596 | 5.4596 | 5.4596 | 5.4596
2021-07-12 07:00 | 4.5069 | 5.5811 | 5.6699 | 6.0509 | 5.8985 | 6.2795 | 2.1377 | 3.2382 | 3.8552 | 3.8552 | 4.2666 | 4.2666 | 2019-09-08 20:00 | 1.8671 | 3.204 | 5.4154 | 5.4154 | 5.4154 | 5.4154
2021-07-12 08:00 | 4.4554 | 5.5173 | 5.6052 | 5.9819 | 5.8312 | 6.2078 | 2.2463 | 3.4027 | 4.0511 | 4.0511 | 4.4834 | 4.4834 | 2019-09-08 21:00 | 1.7681 | 3.034 | 5.128 | 5.128 | 5.128 | 5.128
2021-07-12 09:00 | 4.2897 | 5.3121 | 5.3967 | 5.7593 | 5.6143 | 5.9769 | 2.0662 | 3.13 | 3.7264 | 3.7264 | 4.124 | 4.124 | 2019-09-08 22:00 | 1.6766 | 2.8771 | 4.8628 | 4.8628 | 4.8628 | 4.8628
2021-07-12 10:00 | 4.0182 | 4.9759 | 5.0551 | 5.3948 | 5.2589 | 5.5986 | 1.9919 | 3.0174 | 3.5924 | 3.5924 | 3.9757 | 3.9757 | 2019-09-08 23:00 | 1.4861 | 2.5501 | 4.3102 | 4.3102 | 4.3102 | 4.3102
2021-07-12 11:00 | 3.5638 | 4.4132 | 4.4835 | 4.7847 | 4.6642 | 4.9655 | 2.0205 | 3.0607 | 3.6439 | 3.6439 | 4.0327 | 4.0327 | 2019-09-09 | 1.387 | 2.3801 | 4.0228 | 4.0228 | 4.0228 | 4.0228
2021-07-12 12:00 | 3.3437 | 4.1407 | 4.2066 | 4.4893 | 4.3762 | 4.6589 | 1.9033 | 2.8832 | 3.4326 | 3.4326 | 3.7989 | 3.7989 | 2019-09-09 01:00 | 1.2422 | 2.1317 | 3.6029 | 3.6029 | 3.6029 | 3.6029
2021-07-12 13:00 | 3.2351 | 4.0062 | 4.07 | 4.3435 | 4.2341 | 4.5075 | 1.8405 | 2.788 | 3.3192 | 3.3192 | 3.6734 | 3.6734 | 2019-09-09 02:00 | 1.3184 | 2.2624 | 3.8239 | 3.8239 | 3.8239 | 3.8239
2021-07-12 14:00 | 2.9498 | 3.6529 | 3.7111 | 3.9604 | 3.8607 | 4.11 | 1.9148 | 2.9005 | 3.4532 | 3.4532 | 3.8217 | 3.8217 | 2019-09-09 03:00 | 1.2422 | 2.1317 | 3.6029 | 3.6029 | 3.6029 | 3.6029
2021-07-12 15:00 | 3.1237 | 3.8682 | 3.9298 | 4.1938 | 4.0882 | 4.3523 | 1.7862 | 2.7057 | 3.2213 | 3.2213 | 3.565 | 3.565 | 2019-09-09 04:00 | 1.3413 | 2.3017 | 3.8902 | 3.8902 | 3.8902 | 3.8902
2021-07-12 16:00 | 3.6024 | 4.461 | 4.5321 | 4.8366 | 4.7148 | 5.0193 | 1.9634 | 2.9741 | 3.5408 | 3.5408 | 3.9187 | 3.9187 | 2019-09-09 05:00 | 1.4709 | 2.524 | 4.266 | 4.266 | 4.266 | 4.266
2021-07-12 17:00 | 4.2525 | 5.2661 | 5.35 | 5.7094 | 5.5656 | 5.9251 | 2.4121 | 3.6538 | 4.35 | 4.35 | 4.8142 | 4.8142 | 2019-09-09 06:00 | 1.7147 | 2.9425 | 4.9733 | 4.9733 | 4.9733 | 4.9733
2021-07-12 18:00 | 4.244 | 5.2555 | 5.3392 | 5.6979 | 5.5544 | 5.9132 | 2.6493 | 4.0131 | 4.7778 | 4.7778 | 5.2876 | 5.2876 | 2019-09-09 07:00 | 1.9053 | 3.2694 | 5.5259 | 5.5259 | 5.5259 | 5.5259
2021-07-12 19:00 | 4.0363 | 4.9983 | 5.0779 | 5.4191 | 5.2826 | 5.6238 | 2.5979 | 3.9353 | 4.6852 | 4.6852 | 5.1851 | 5.1851 | 2019-09-09 08:00 | 2.0805 | 3.5702 | 6.0343 | 6.0343 | 6.0343 | 6.0343
2021-07-12 20:00 | 3.7543 | 4.6491 | 4.7231 | 5.0405 | 4.9135 | 5.2309 | 2.5607 | 3.8789 | 4.618 | 4.618 | 5.1108 | 5.1108 | 2019-09-09 09:00 | 2.1796 | 3.7402 | 6.3216 | 6.3216 | 6.3216 | 6.3216
2021-07-12 21:00 | 3.3209 | 4.1124 | 4.1779 | 4.4586 | 4.3463 | 4.627 | 2.3463 | 3.5542 | 4.2315 | 4.2315 | 4.683 | 4.683 | 2019-09-09 10:00 | 2.0577 | 3.531 | 5.9679 | 5.9679 | 5.9679 | 5.9679
2021-07-12 22:00 | 2.9865 | 3.6983 | 3.7572 | 4.0096 | 3.9087 | 4.1611 | 2.0223 | 3.0634 | 3.6472 | 3.6472 | 4.0364 | 4.0364 | 2019-09-09 11:00 | 2.233 | 3.8318 | 6.4763 | 6.4763 | 6.4763 | 6.4763
2021-07-12 23:00 | 2.5764 | 3.1904 | 3.2412 | 3.459 | 3.3719 | 3.5897 | 1.7376 | 2.6321 | 3.1337 | 3.1337 | 3.468 | 3.468 | 2019-09-09 12:00 | 2.1872 | 3.7533 | 6.3437 | 6.3437 | 6.3437 | 6.3437
2021-07-13 | 2.2963 | 2.8436 | 2.8889 | 3.083 | 3.0054 | 3.1995 | 1.3946 | 2.1126 | 2.5152 | 2.5152 | 2.7836 | 2.7836 | 2019-09-09 13:00 | 2.1491 | 3.6879 | 6.2332 | 6.2332 | 6.2332 | 6.2332
2021-07-13 01:00 | 2.1406 | 2.6508 | 2.693 | 2.874 | 2.8016 | 2.9825 | 1.1889 | 1.8009 | 2.1441 | 2.1441 | 2.3729 | 2.3729 | 2019-09-09 14:00 | 2.2863 | 3.9233 | 6.631 | 6.631 | 6.631 | 6.631
2021-07-13 02:00 | 2.1005 | 2.6012 | 2.6426 | 2.8202 | 2.7492 | 2.9267 | 1.1346 | 1.7187 | 2.0462 | 2.0462 | 2.2645 | 2.2645 | 2019-09-09 15:00 | 2.2025 | 3.7795 | 6.3879 | 6.3879 | 6.3879 | 6.3879
2021-07-13 03:00 | 2.1148 | 2.6189 | 2.6606 | 2.8394 | 2.7679 | 2.9466 | 1.086 | 1.6451 | 1.9585 | 1.9585 | 2.1675 | 2.1675 | 2019-09-09 16:00 | 2.2101 | 3.7925 | 6.41 | 6.41 | 6.41 | 6.41
2021-07-13 04:00 | 2.1736 | 2.6916 | 2.7345 | 2.9183 | 2.8448 | 3.0285 | 1.1489 | 1.7403 | 2.0719 | 2.0719 | 2.293 | 2.293 | 2019-09-09 17:00 | 2.2101 | 3.7925 | 6.41 | 6.41 | 6.41 | 6.41
2021-07-13 05:00 | 2.7407 | 3.3939 | 3.448 | 3.6797 | 3.587 | 3.8187 | 1.3175 | 1.9957 | 2.376 | 2.376 | 2.6295 | 2.6295 | 2019-09-09 18:00 | 2.2177 | 3.8056 | 6.4321 | 6.4321 | 6.4321 | 6.4321
2021-07-13 06:00 | 3.6295 | 4.4946 | 4.5662 | 4.873 | 4.7502 | 5.0571 | 1.7555 | 2.6592 | 3.1659 | 3.1659 | 3.5037 | 3.5037 | 2019-09-09 19:00 | 2.111 | 3.6225 | 6.1227 | 6.1227 | 6.1227 | 6.1227
2021-07-13 07:00 | 4.0868 | 5.0608 | 5.1414 | 5.4869 | 5.3487 | 5.6942 | 2.1463 | 3.2512 | 3.8707 | 3.8707 | 4.2837 | 4.2837 | 2019-09-09 20:00 | 2.0272 | 3.4787 | 5.8795 | 5.8795 | 5.8795 | 5.8795
2021-07-13 08:00 | 4.0725 | 5.0431 | 5.1234 | 5.4677 | 5.33 | 5.6743 | 2.0161 | 3.054 | 3.636 | 3.636 | 4.024 | 4.024 | 2019-09-09 21:00 | 1.9586 | 3.361 | 5.6806 | 5.6806 | 5.6806 | 5.6806
2021-07-13 09:00 | 3.6903 | 4.5698 | 4.6426 | 4.9546 | 4.8298 | 5.1418 | 1.8519 | 2.8053 | 3.3398 | 3.3398 | 3.6962 | 3.6962 | 2019-09-09 22:00 | 1.8214 | 3.1256 | 5.2827 | 5.2827 | 5.2827 | 5.2827
2021-07-13 10:00 | 3.4695 | 4.2964 | 4.3648 | 4.6581 | 4.5408 | 4.8341 | 1.8005 | 2.7274 | 3.2471 | 3.2471 | 3.5935 | 3.5935 | 2019-09-09 23:00 | 1.7757 | 3.0471 | 5.1501 | 5.1501 | 5.1501 | 5.1501
2021-07-13 11:00 | 3.3637 | 4.1654 | 4.2318 | 4.5161 | 4.4024 | 4.6867 | 1.9062 | 2.8875 | 3.4378 | 3.4378 | 3.8046 | 3.8046 | 2019-09-10 | 1.6004 | 2.7463 | 4.6417 | 4.6417 | 4.6417 | 4.6417
2021-07-13 12:00 | 3.3123 | 4.1017 | 4.1671 | 4.4471 | 4.3351 | 4.6151 | 1.9748 | 2.9914 | 3.5615 | 3.5615 | 3.9415 | 3.9415 | 2019-09-10 01:00 | 1.4785 | 2.5371 | 4.2881 | 4.2881 | 4.2881 | 4.2881
2021-07-13 13:00 | 3.1722 | 3.9283 | 3.9909 | 4.2591 | 4.1518 | 4.4199 | 1.8833 | 2.8529 | 3.3965 | 3.3965 | 3.7589 | 3.7589 | 2019-09-10 02:00 | 1.4785 | 2.5371 | 4.2881 | 4.2881 | 4.2881 | 4.2881
2021-07-13 14:00 | 3.2494 | 4.0239 | 4.088 | 4.3627 | 4.2528 | 4.5275 | 1.8805 | 2.8486 | 3.3914 | 3.3914 | 3.7532 | 3.7532 | 2019-09-10 03:00 | 1.4251 | 2.4455 | 4.1333 | 4.1333 | 4.1333 | 4.1333
2021-07-13 15:00 | 3.0294 | 3.7514 | 3.8111 | 4.0672 | 3.9648 | 4.2209 | 1.8207 | 2.758 | 3.2836 | 3.2836 | 3.634 | 3.634 | 2019-09-10 04:00 | 1.5318 | 2.6286 | 4.4428 | 4.4428 | 4.4428 | 4.4428
2021-07-13 16:00 | 3.4552 | 4.2787 | 4.3468 | 4.6389 | 4.5221 | 4.8142 | 2.0805 | 3.1516 | 3.7522 | 3.7522 | 4.1525 | 4.1525 | 2019-09-10 05:00 | 1.7376 | 2.9817 | 5.0396 | 5.0396 | 5.0396 | 5.0396
2021-07-13 17:00 | 3.7553 | 4.6503 | 4.7244 | 5.0418 | 4.9148 | 5.2323 | 2.4404 | 3.6967 | 4.4011 | 4.4011 | 4.8707 | 4.8707 | 2019-09-10 06:00 | 1.9967 | 3.4264 | 5.7911 | 5.7911 | 5.7911 | 5.7911
2021-07-13 18:00 | 4.001 | 4.9546 | 5.0336 | 5.3718 | 5.2365 | 5.5747 | 2.5492 | 3.8616 | 4.5974 | 4.5974 | 5.088 | 5.088 | 2019-09-10 07:00 | 2.0653 | 3.5441 | 5.99 | 5.99 | 5.99 | 5.99
2021-07-13 19:00 | 3.8553 | 4.7742 | 4.8502 | 5.1761 | 5.0457 | 5.3716 | 2.6207 | 3.9698 | 4.7263 | 4.7263 | 5.2306 | 5.2306 | 2019-09-10 08:00 | 2.3168 | 3.9756 | 6.7195 | 6.7195 | 6.7195 | 6.7195
2021-07-13 20:00 | 3.6724 | 4.5477 | 4.6201 | 4.9305 | 4.8064 | 5.1168 | 2.5178 | 3.814 | 4.5407 | 4.5407 | 5.0252 | 5.0252 | 2019-09-10 09:00 | 2.2634 | 3.8841 | 6.5647 | 6.5647 | 6.5647 | 6.5647
2021-07-13 21:00 | 3.3209 | 4.1124 | 4.1779 | 4.4586 | 4.3463 | 4.627 | 2.332 | 3.5326 | 4.2057 | 4.2057 | 4.6545 | 4.6545 | 2019-09-10 10:00 | 2.2863 | 3.9233 | 6.631 | 6.631 | 6.631 | 6.631
2021-07-13 22:00 | 2.8036 | 3.4718 | 3.5271 | 3.7641 | 3.6693 | 3.9063 | 2.1429 | 3.246 | 3.8646 | 3.8646 | 4.2769 | 4.2769 | 2019-09-10 11:00 | 2.2787 | 3.9102 | 6.6089 | 6.6089 | 6.6089 | 6.6089
2021-07-13 23:00 | 2.4896 | 3.083 | 3.1321 | 3.3426 | 3.2584 | 3.4688 | 1.7547 | 2.6581 | 3.1646 | 3.1646 | 3.5023 | 3.5023 | 2019-09-10 12:00 | 2.3625 | 4.0541 | 6.8521 | 6.8521 | 6.8521 | 6.8521
2021-07-14 | 2.1977 | 2.7215 | 2.7649 | 2.9506 | 2.8763 | 3.0621 | 1.3632 | 2.065 | 2.4585 | 2.4585 | 2.7208 | 2.7208 | 2019-09-10 13:00 | 2.2177 | 3.8056 | 6.4321 | 6.4321 | 6.4321 | 6.4321
2021-07-14 01:00 | 2.0177 | 2.4986 | 2.5383 | 2.7089 | 2.6407 | 2.8112 | 1.1546 | 1.749 | 2.0822 | 2.0822 | 2.3044 | 2.3044 | 2019-09-10 14:00 | 2.2558 | 3.871 | 6.5426 | 6.5426 | 6.5426 | 6.5426
2021-07-14 02:00 | 2.0079 | 2.4865 | 2.5261 | 2.6958 | 2.6279 | 2.7976 | 1.1146 | 1.6884 | 2.0101 | 2.0101 | 2.2246 | 2.2246 | 2019-09-10 15:00 | 2.2634 | 3.8841 | 6.5647 | 6.5647 | 6.5647 | 6.5647
2021-07-14 03:00 | 1.9919 | 2.4667 | 2.506 | 2.6744 | 2.607 | 2.7754 | 1.1403 | 1.7273 | 2.0565 | 2.0565 | 2.2759 | 2.2759 | 2019-09-10 16:00 | 2.2787 | 3.9102 | 6.6089 | 6.6089 | 6.6089 | 6.6089
2021-07-14 04:00 | 2.1663 | 2.6826 | 2.7253 | 2.9084 | 2.8352 | 3.0183 | 1.1374 | 1.723 | 2.0513 | 2.0513 | 2.2702 | 2.2702 | 2019-09-10 17:00 | 2.3244 | 3.9887 | 6.7416 | 6.7416 | 6.7416 | 6.7416
2021-07-14 05:00 | 2.5831 | 3.1988 | 3.2497 | 3.4681 | 3.3807 | 3.5991 | 1.323 | 2.0041 | 2.386 | 2.386 | 2.6406 | 2.6406 | 2019-09-10 18:00 | 2.3473 | 4.0279 | 6.8079 | 6.8079 | 6.8079 | 6.8079
2021-07-14 06:00 | 3.5152 | 4.353 | 4.4223 | 4.7195 | 4.6006 | 4.8978 | 1.6661 | 2.5239 | 3.0048 | 3.0048 | 3.3254 | 3.3254 | 2019-09-10 19:00 | 2.2101 | 3.7925 | 6.41 | 6.41 | 6.41 | 6.41
2021-07-14 07:00 | 4.0125 | 4.9688 | 5.0479 | 5.3871 | 5.2515 | 5.5906 | 2.1577 | 3.2685 | 3.8913 | 3.8913 | 4.3065 | 4.3065 | 2019-09-10 20:00 | 2.1872 | 3.7533 | 6.3437 | 6.3437 | 6.3437 | 6.3437
2021-07-14 08:00 | 4.0868 | 5.0608 | 5.1414 | 5.4869 | 5.3487 | 5.6942 | 2.1263 | 3.2209 | 3.8346 | 3.8346 | 4.2438 | 4.2438 | 2019-09-10 21:00 | 2.0882 | 3.5833 | 6.0564 | 6.0564 | 6.0564 | 6.0564
2021-07-14 09:00 | 3.9267 | 4.8626 | 4.9401 | 5.272 | 5.1392 | 5.4712 | 1.8833 | 2.8529 | 3.3965 | 3.3965 | 3.7589 | 3.7589 | 2019-09-10 22:00 | 1.9967 | 3.4264 | 5.7911 | 5.7911 | 5.7911 | 5.7911
2021-07-14 10:00 | 3.6038 | 4.4627 | 4.5338 | 4.8384 | 4.7166 | 5.0212 | 1.9605 | 2.9698 | 3.5357 | 3.5357 | 3.913 | 3.913 | 2019-09-10 23:00 | 1.7605 | 3.0209 | 5.1059 | 5.1059 | 5.1059 | 5.1059
2021-07-14 11:00 | 3.4638 | 4.2893 | 4.3576 | 4.6504 | 4.5333 | 4.8261 | 1.9862 | 3.0087 | 3.5821 | 3.5821 | 3.9643 | 3.9643 | 2019-09-11 | 1.6233 | 2.7855 | 4.708 | 4.708 | 4.708 | 4.708
2021-07-14 12:00 | 3.7638 | 4.6609 | 4.7351 | 5.0533 | 4.926 | 5.2442 | 2.0805 | 3.1516 | 3.7522 | 3.7522 | 4.1525 | 4.1525 | 2019-09-11 01:00 | 1.4937 | 2.5632 | 4.3323 | 4.3323 | 4.3323 | 4.3323
2021-07-14 13:00 | 3.7353 | 4.6255 | 4.6992 | 5.0149 | 4.8886 | 5.2044 | 2.0491 | 3.104 | 3.6955 | 3.6955 | 4.0898 | 4.0898 | 2019-09-11 02:00 | 1.4861 | 2.5501 | 4.3102 | 4.3102 | 4.3102 | 4.3102
2021-07-14 14:00 | 3.6467 | 4.5158 | 4.5877 | 4.896 | 4.7727 | 5.0809 | 2.0119 | 3.0477 | 3.6285 | 3.6285 | 4.0156 | 4.0156 | 2019-09-11 03:00 | 1.5471 | 2.6548 | 4.487 | 4.487 | 4.487 | 4.487
2021-07-14 15:00 | 3.6324 | 4.4981 | 4.5698 | 4.8768 | 4.754 | 5.061 | 2.0548 | 3.1126 | 3.7058 | 3.7058 | 4.1012 | 4.1012 | 2019-09-11 04:00 | 1.5013 | 2.5763 | 4.3544 | 4.3544 | 4.3544 | 4.3544
2021-07-14 16:00 | 3.8781 | 4.8025 | 4.879 | 5.2068 | 5.0757 | 5.4035 | 2.212 | 3.3508 | 3.9892 | 3.9892 | 4.4149 | 4.4149 | 2019-09-11 05:00 | 1.8214 | 3.1256 | 5.2827 | 5.2827 | 5.2827 | 5.2827
2021-07-14 17:00 | 4.3229 | 5.3532 | 5.4385 | 5.8039 | 5.6577 | 6.0232 | 2.5807 | 3.9092 | 4.6541 | 4.6541 | 5.1507 | 5.1507 | 2019-09-11 06:00 | 1.9281 | 3.3087 | 5.5922 | 5.5922 | 5.5922 | 5.5922
2021-07-14 18:00 | 4.324 | 5.3546 | 5.4398 | 5.8054 | 5.6592 | 6.0247 | 2.7036 | 4.0954 | 4.8757 | 4.8757 | 5.396 | 5.396 | 2019-09-11 07:00 | 2.1491 | 3.6879 | 6.2332 | 6.2332 | 6.2332 | 6.2332
2021-07-14 19:00 | 3.9839 | 4.9334 | 5.012 | 5.3488 | 5.214 | 5.5508 | 2.715 | 4.1127 | 4.8964 | 4.8964 | 5.4188 | 5.4188 | 2019-09-11 08:00 | 2.4082 | 4.1326 | 6.9847 | 6.9847 | 6.9847 | 6.9847
2021-07-14 20:00 | 3.6352 | 4.5016 | 4.5733 | 4.8806 | 4.7577 | 5.065 | 2.5778 | 3.9049 | 4.649 | 4.649 | 5.145 | 5.145 | 2019-09-11 09:00 | 2.4082 | 4.1326 | 6.9847 | 6.9847 | 6.9847 | 6.9847
2021-07-14 21:00 | 3.1751 | 3.9319 | 3.9945 | 4.2629 | 4.1555 | 4.4239 | 2.3978 | 3.6321 | 4.3243 | 4.3243 | 4.7857 | 4.7857 | 2019-09-11 10:00 | 2.4463 | 4.1979 | 7.0952 | 7.0952 | 7.0952 | 7.0952
2021-07-14 22:00 | 2.8379 | 3.5143 | 3.5702 | 3.8101 | 3.7142 | 3.9541 | 2.0605 | 3.1213 | 3.7161 | 3.7161 | 4.1126 | 4.1126 | 2019-09-11 11:00 | 2.4159 | 4.1456 | 7.0068 | 7.0068 | 7.0068 | 7.0068
2021-07-14 23:00 | 2.5249 | 3.1267 | 3.1765 | 3.39 | 3.3046 | 3.518 | 1.8122 | 2.7451 | 3.2681 | 3.2681 | 3.6169 | 3.6169 | 2019-09-11 12:00 | 2.2558 | 3.871 | 6.5426 | 6.5426 | 6.5426 | 6.5426
2021-07-15 | 2.1458 | 2.6573 | 2.6996 | 2.881 | 2.8084 | 2.9898 | 1.3808 | 2.0917 | 2.4903 | 2.4903 | 2.756 | 2.756 | 2019-09-11 13:00 | 2.3015 | 3.9495 | 6.6753 | 6.6753 | 6.6753 | 6.6753
2021-07-15 01:00 | 1.9977 | 2.4738 | 2.5132 | 2.682 | 2.6145 | 2.7834 | 1.2292 | 1.862 | 2.2168 | 2.2168 | 2.4533 | 2.4533 | 2019-09-11 14:00 | 2.3168 | 3.9756 | 6.7195 | 6.7195 | 6.7195 | 6.7195
2021-07-15 02:00 | 1.8548 | 2.2968 | 2.3334 | 2.4902 | 2.4275 | 2.5843 | 1.106 | 1.6754 | 1.9946 | 1.9946 | 2.2075 | 2.2075 | 2019-09-11 15:00 | 2.2787 | 3.9102 | 6.6089 | 6.6089 | 6.6089 | 6.6089
2021-07-15 03:00 | 1.8548 | 2.2968 | 2.3334 | 2.4902 | 2.4275 | 2.5843 | 1.0517 | 1.5931 | 1.8967 | 1.8967 | 2.0991 | 2.0991 | 2019-09-11 16:00 | 2.3473 | 4.0279 | 6.8079 | 6.8079 | 6.8079 | 6.8079
2021-07-15 04:00 | 1.9253 | 2.3842 | 2.4221 | 2.5849 | 2.5198 | 2.6825 | 1.1289 | 1.71 | 2.0359 | 2.0359 | 2.2531 | 2.2531 | 2019-09-11 17:00 | 2.3549 | 4.041 | 6.83 | 6.83 | 6.83 | 6.83
2021-07-15 05:00 | 2.3379 | 2.8951 | 2.9412 | 3.1388 | 3.0598 | 3.2574 | 1.246 | 1.8875 | 2.2472 | 2.2472 | 2.4869 | 2.4869 | 2019-09-11 18:00 | 2.3854 | 4.0933 | 6.9184 | 6.9184 | 6.9184 | 6.9184
2021-07-15 06:00 | 3.3526 | 4.1517 | 4.2178 | 4.5012 | 4.3879 | 4.6713 | 1.5549 | 2.3553 | 2.8041 | 2.8041 | 3.1033 | 3.1033 | 2019-09-11 19:00 | 2.2482 | 3.8579 | 6.5205 | 6.5205 | 6.5205 | 6.5205
2021-07-15 07:00 | 3.721 | 4.6078 | 4.6812 | 4.9958 | 4.8699 | 5.1845 | 1.9148 | 2.9005 | 3.4532 | 3.4532 | 3.8217 | 3.8217 | 2019-09-11 20:00 | 2.0196 | 3.4656 | 5.8574 | 5.8574 | 5.8574 | 5.8574
2021-07-15 08:00 | 3.7381 | 4.6291 | 4.7028 | 5.0188 | 4.8924 | 5.2084 | 1.9033 | 2.8832 | 3.4326 | 3.4326 | 3.7989 | 3.7989 | 2019-09-11 21:00 | 1.9967 | 3.4264 | 5.7911 | 5.7911 | 5.7911 | 5.7911
2021-07-15 09:00 | 3.6981 | 4.5795 | 4.6524 | 4.9651 | 4.84 | 5.1526 | 1.8605 | 2.8183 | 3.3553 | 3.3553 | 3.7133 | 3.7133 | 2019-09-11 22:00 | 1.8595 | 3.191 | 5.3932 | 5.3932 | 5.3932 | 5.3932
2021-07-15 10:00 | 3.3494 | 4.1477 | 4.2138 | 4.4969 | 4.3837 | 4.6668 | 1.729 | 2.6191 | 3.1182 | 3.1182 | 3.4509 | 3.4509 | 2019-09-11 23:00 | 1.8748 | 3.2171 | 5.4375 | 5.4375 | 5.4375 | 5.4375
2021-07-15 11:00 | 3.138 | 3.8859 | 3.9477 | 4.213 | 4.1069 | 4.3722 | 1.8005 | 2.7274 | 3.2471 | 3.2471 | 3.5935 | 3.5935 | 2019-09-12 | 1.6004 | 2.7463 | 4.6417 | 4.6417 | 4.6417 | 4.6417
2021-07-15 12:00 | 3.2408 | 4.0133 | 4.0772 | 4.3511 | 4.2416 | 4.5155 | 1.7519 | 2.6538 | 3.1594 | 3.1594 | 3.4966 | 3.4966 | 2019-09-12 01:00 | 1.509 | 2.5894 | 4.3765 | 4.3765 | 4.3765 | 4.3765
2021-07-15 13:00 | 2.895 | 3.585 | 3.6421 | 3.8869 | 3.789 | 4.0337 | 1.7204 | 2.6061 | 3.1027 | 3.1027 | 3.4338 | 3.4338 | 2019-09-12 02:00 | 1.4861 | 2.5501 | 4.3102 | 4.3102 | 4.3102 | 4.3102
2021-07-15 14:00 | 2.8293 | 3.5036 | 3.5594 | 3.7986 | 3.7029 | 3.9421 | 1.689 | 2.5585 | 3.0461 | 3.0461 | 3.3711 | 3.3711 | 2019-09-12 03:00 | 1.4175 | 2.4324 | 4.1112 | 4.1112 | 4.1112 | 4.1112
2021-07-15 15:00 | 3.0694 | 3.8009 | 3.8615 | 4.1209 | 4.0171 | 4.2766 | 1.7547 | 2.6581 | 3.1646 | 3.1646 | 3.5023 | 3.5023 | 2019-09-12 04:00 | 1.5318 | 2.6286 | 4.4428 | 4.4428 | 4.4428 | 4.4428
2021-07-15 16:00 | 3.2808 | 4.0628 | 4.1275 | 4.4049 | 4.2939 | 4.5713 | 1.9834 | 3.0044 | 3.5769 | 3.5769 | 3.9586 | 3.9586 | 2019-09-12 05:00 | 1.73 | 2.9686 | 5.0175 | 5.0175 | 5.0175 | 5.0175
2021-07-15 17:00 | 3.821 | 4.7317 | 4.807 | 5.13 | 5.0008 | 5.3238 | 2.2692 | 3.4373 | 4.0923 | 4.0923 | 4.529 | 4.529 | 2019-09-12 06:00 | 1.8824 | 3.2302 | 5.4596 | 5.4596 | 5.4596 | 5.4596
2021-07-15 18:00 | 3.9467 | 4.8874 | 4.9652 | 5.2989 | 5.1654 | 5.4991 | 2.3978 | 3.6321 | 4.3243 | 4.3243 | 4.7857 | 4.7857 | 2019-09-12 07:00 | 2.2939 | 3.9364 | 6.6531 | 6.6531 | 6.6531 | 6.6531
2021-07-15 19:00 | 3.682 | 4.5596 | 4.6323 | 4.9435 | 4.819 | 5.1303 | 2.3663 | 3.5845 | 4.2676 | 4.2676 | 4.7229 | 4.7229 | 2019-09-12 08:00 | 2.3092 | 3.9625 | 6.6974 | 6.6974 | 6.6974 | 6.6974
2021-07-15 20:00 | 3.398 | 4.2079 | 4.2749 | 4.5622 | 4.4473 | 4.7345 | 2.2806 | 3.4546 | 4.1129 | 4.1129 | 4.5518 | 4.5518 | 2019-09-12 09:00 | 2.3168 | 3.9756 | 6.7195 | 6.7195 | 6.7195 | 6.7195
2021-07-15 21:00 | 3.0122 | 3.7301 | 3.7896 | 4.0442 | 3.9423 | 4.197 | 2.2777 | 3.4503 | 4.1078 | 4.1078 | 4.5461 | 4.5461 | 2019-09-12 10:00 | 2.2101 | 3.7925 | 6.41 | 6.41 | 6.41 | 6.41
2021-07-15 22:00 | 2.6893 | 3.3302 | 3.3833 | 3.6106 | 3.5197 | 3.747 | 1.9891 | 3.0131 | 3.5872 | 3.5872 | 3.97 | 3.97 | 2019-09-12 11:00 | 2.2939 | 3.9364 | 6.6531 | 6.6531 | 6.6531 | 6.6531
2021-07-15 23:00 | 2.3835 | 2.9515 | 2.9986 | 3.2 | 3.1195 | 3.3209 | 1.6947 | 2.5672 | 3.0564 | 3.0564 | 3.3825 | 3.3825 | 2019-09-12 12:00 | 2.2634 | 3.8841 | 6.5647 | 6.5647 | 6.5647 | 6.5647
2021-07-16 | 2.1606 | 2.6755 | 2.7181 | 2.9008 | 2.8277 | 3.0103 | 1.3118 | 1.9871 | 2.3657 | 2.3657 | 2.6181 | 2.6181 | 2019-09-12 13:00 | 2.1567 | 3.701 | 6.2553 | 6.2553 | 6.2553 | 6.2553
2021-07-16 01:00 | 1.9462 | 2.4101 | 2.4485 | 2.613 | 2.5472 | 2.7117 | 1.1946 | 1.8096 | 2.1544 | 2.1544 | 2.3843 | 2.3843 | 2019-09-12 14:00 | 2.1872 | 3.7533 | 6.3437 | 6.3437 | 6.3437 | 6.3437
2021-07-16 02:00 | 1.8633 | 2.3074 | 2.3442 | 2.5017 | 2.4387 | 2.5962 | 1.0888 | 1.6494 | 1.9637 | 1.9637 | 2.1732 | 2.1732 | 2019-09-12 15:00 | 2.1491 | 3.6879 | 6.2332 | 6.2332 | 6.2332 | 6.2332
2021-07-16 03:00 | 1.8633 | 2.3074 | 2.3442 | 2.5017 | 2.4387 | 2.5962 | 1.0774 | 1.6321 | 1.9431 | 1.9431 | 2.1504 | 2.1504 | 2019-09-12 16:00 | 2.2711 | 3.8972 | 6.5868 | 6.5868 | 6.5868 | 6.5868
2021-07-16 04:00 | 1.9119 | 2.3676 | 2.4053 | 2.5669 | 2.5023 | 2.6639 | 1.086 | 1.6451 | 1.9585 | 1.9585 | 2.1675 | 2.1675 | 2019-09-12 17:00 | 2.2558 | 3.871 | 6.5426 | 6.5426 | 6.5426 | 6.5426
2021-07-16 05:00 | 2.2492 | 2.7852 | 2.8296 | 3.0197 | 2.9437 | 3.1338 | 1.1944 | 1.8093 | 2.1541 | 2.1541 | 2.3839 | 2.3839 | 2019-09-12 18:00 | 2.2253 | 3.8187 | 6.4542 | 6.4542 | 6.4542 | 6.4542
2021-07-16 06:00 | 3.2362 | 4.0076 | 4.0714 | 4.345 | 4.2355 | 4.5091 | 1.4632 | 2.2165 | 2.6389 | 2.6389 | 2.9205 | 2.9205 | 2019-09-12 19:00 | 2.1567 | 3.701 | 6.2553 | 6.2553 | 6.2553 | 6.2553
2021-07-16 07:00 | 3.701 | 4.583 | 4.656 | 4.9689 | 4.8438 | 5.1566 | 1.9205 | 2.9092 | 3.4635 | 3.4635 | 3.8331 | 3.8331 | 2019-09-12 20:00 | 2.1186 | 3.6356 | 6.1448 | 6.1448 | 6.1448 | 6.1448
2021-07-16 08:00 | 3.7867 | 4.6892 | 4.7639 | 5.084 | 4.956 | 5.2761 | 1.9405 | 2.9395 | 3.4996 | 3.4996 | 3.873 | 3.873 | 2019-09-12 21:00 | 1.9053 | 3.2694 | 5.5259 | 5.5259 | 5.5259 | 5.5259
2021-07-16 09:00 | 3.6467 | 4.5158 | 4.5877 | 4.896 | 4.7727 | 5.0809 | 1.849 | 2.8009 | 3.3347 | 3.3347 | 3.6905 | 3.6905 | 2019-09-12 22:00 | 1.8367 | 3.1517 | 5.3269 | 5.3269 | 5.3269 | 5.3269
2021-07-16 10:00 | 3.5066 | 4.3424 | 4.4116 | 4.708 | 4.5894 | 4.8858 | 1.8433 | 2.7923 | 3.3244 | 3.3244 | 3.6791 | 3.6791 | 2019-09-12 23:00 | 1.7376 | 2.9817 | 5.0396 | 5.0396 | 5.0396 | 5.0396
2021-07-16 11:00 | 3.341 | 4.1373 | 4.2032 | 4.4856 | 4.3726 | 4.655 | 1.9605 | 2.9698 | 3.5357 | 3.5357 | 3.913 | 3.913 | 2019-09-13 | 1.5775 | 2.7071 | 4.5754 | 4.5754 | 4.5754 | 4.5754
2021-07-16 12:00 | 3.4952 | 4.3282 | 4.3972 | 4.6926 | 4.5744 | 4.8699 | 2.1177 | 3.2079 | 3.8192 | 3.8192 | 4.2267 | 4.2267 | 2019-09-13 01:00 | 1.3642 | 2.3409 | 3.9565 | 3.9565 | 3.9565 | 3.9565
2021-07-16 13:00 | 3.5381 | 4.3813 | 4.4511 | 4.7502 | 4.6306 | 4.9296 | 2.0119 | 3.0477 | 3.6285 | 3.6285 | 4.0156 | 4.0156 | 2019-09-13 02:00 | 1.3489 | 2.3148 | 3.9123 | 3.9123 | 3.9123 | 3.9123
2021-07-16 14:00 | 3.6181 | 4.4804 | 4.5518 | 4.8576 | 4.7353 | 5.0411 | 2.0834 | 3.1559 | 3.7573 | 3.7573 | 4.1582 | 4.1582 | 2019-09-13 03:00 | 1.3489 | 2.3148 | 3.9123 | 3.9123 | 3.9123 | 3.9123
2021-07-16 15:00 | 3.6924 | 4.5724 | 4.6453 | 4.9574 | 4.8325 | 5.1447 | 2.1148 | 3.2036 | 3.814 | 3.814 | 4.221 | 4.221 | 2019-09-13 04:00 | 1.3718 | 2.354 | 3.9786 | 3.9786 | 3.9786 | 3.9786
2021-07-16 16:00 | 3.9843 | 4.934 | 5.0126 | 5.3494 | 5.2146 | 5.5515 | 2.272 | 3.4417 | 4.0975 | 4.0975 | 4.5347 | 4.5347 | 2019-09-13 05:00 | 1.6614 | 2.8509 | 4.8186 | 4.8186 | 4.8186 | 4.8186
2021-07-16 17:00 | 4.1125 | 5.0927 | 5.1738 | 5.5214 | 5.3824 | 5.73 | 2.7121 | 4.1083 | 4.8912 | 4.8912 | 5.4131 | 5.4131 | 2019-09-13 06:00 | 1.7833 | 3.0602 | 5.1722 | 5.1722 | 5.1722 | 5.1722
2021-07-16 18:00 | 4.0382 | 5.0006 | 5.0803 | 5.4217 | 5.2851 | 5.6265 | 2.8179 | 4.2685 | 5.0819 | 5.0819 | 5.6242 | 5.6242 | 2019-09-13 07:00 | 2.0196 | 3.4656 | 5.8574 | 5.8574 | 5.8574 | 5.8574
2021-07-16 19:00 | 3.841 | 4.7565 | 4.8322 | 5.1569 | 5.027 | 5.3517 | 2.7893 | 4.2252 | 5.0304 | 5.0304 | 5.5671 | 5.5671 | 2019-09-13 08:00 | 2.1872 | 3.7533 | 6.3437 | 6.3437 | 6.3437 | 6.3437
2021-07-16 20:00 | 3.4695 | 4.2964 | 4.3648 | 4.6581 | 4.5408 | 4.8341 | 2.6607 | 4.0304 | 4.7984 | 4.7984 | 5.3104 | 5.3104 | 2019-09-13 09:00 | 2.2863 | 3.9233 | 6.631 | 6.631 | 6.631 | 6.631
2021-07-16 21:00 | 3.1037 | 3.8434 | 3.9046 | 4.167 | 4.062 | 4.3244 | 2.4806 | 3.7577 | 4.4737 | 4.4737 | 4.9511 | 4.9511 | 2019-09-13 10:00 | 2.3015 | 3.9495 | 6.6753 | 6.6753 | 6.6753 | 6.6753
2021-07-16 22:00 | 2.6978 | 3.3408 | 3.3941 | 3.6221 | 3.5309 | 3.7589 | 2.2663 | 3.433 | 4.0872 | 4.0872 | 4.5233 | 4.5233 | 2019-09-13 11:00 | 2.1339 | 3.6618 | 6.189 | 6.189 | 6.189 | 6.189
2021-07-16 23:00 | 2.5201 | 3.1207 | 3.1704 | 3.3834 | 3.2982 | 3.5112 | 1.9181 | 2.9056 | 3.4592 | 3.4592 | 3.8284 | 3.8284 | 2019-09-13 12:00 | 2.1644 | 3.7141 | 6.2774 | 6.2774 | 6.2774 | 6.2774
2021-07-17 | 2.2463 | 2.7817 | 2.826 | 3.0159 | 2.9399 | 3.1298 | 1.5604 | 2.3637 | 2.8141 | 2.8141 | 3.1144 | 3.1144 | 2019-09-13 13:00 | 2.1644 | 3.7141 | 6.2774 | 6.2774 | 6.2774 | 6.2774
2021-07-17 01:00 | 2.0577 | 2.5481 | 2.5887 | 2.7626 | 2.6931 | 2.867 | 1.4323 | 2.1696 | 2.5831 | 2.5831 | 2.8587 | 2.8587 | 2019-09-13 14:00 | 2.1644 | 3.7141 | 6.2774 | 6.2774 | 6.2774 | 6.2774
2021-07-17 02:00 | 2.0148 | 2.495 | 2.5348 | 2.7051 | 2.6369 | 2.8073 | 1.2435 | 1.8836 | 2.2425 | 2.2425 | 2.4818 | 2.4818 | 2019-09-13 15:00 | 2.3244 | 3.9887 | 6.7416 | 6.7416 | 6.7416 | 6.7416
2021-07-17 03:00 | 1.9348 | 2.3959 | 2.4341 | 2.5976 | 2.5322 | 2.6958 | 1.1976 | 1.8142 | 2.1598 | 2.1598 | 2.3903 | 2.3903 | 2019-09-13 16:00 | 2.2025 | 3.7795 | 6.3879 | 6.3879 | 6.3879 | 6.3879
2021-07-17 04:00 | 1.9434 | 2.4065 | 2.4449 | 2.6091 | 2.5434 | 2.7077 | 1.2232 | 1.8529 | 2.2059 | 2.2059 | 2.4413 | 2.4413 | 2019-09-13 17:00 | 2.2253 | 3.8187 | 6.4542 | 6.4542 | 6.4542 | 6.4542
2021-07-17 05:00 | 2.0748 | 2.5693 | 2.6103 | 2.7856 | 2.7155 | 2.8909 | 1.2803 | 1.9394 | 2.309 | 2.309 | 2.5554 | 2.5554 | 2019-09-13 18:00 | 2.0805 | 3.5702 | 6.0343 | 6.0343 | 6.0343 | 6.0343
2021-07-17 06:00 | 2.4065 | 2.9801 | 3.0276 | 3.231 | 3.1496 | 3.3531 | 1.5604 | 2.3637 | 2.8141 | 2.8141 | 3.1144 | 3.1144 | 2019-09-13 19:00 | 1.9586 | 3.361 | 5.6806 | 5.6806 | 5.6806 | 5.6806
2021-07-17 07:00 | 3.0522 | 3.7797 | 3.8399 | 4.0979 | 3.9947 | 4.2527 | 1.7433 | 2.6408 | 3.144 | 3.144 | 3.4794 | 3.4794 | 2019-09-13 20:00 | 1.8367 | 3.1517 | 5.3269 | 5.3269 | 5.3269 | 5.3269
2021-07-17 08:00 | 3.0808 | 3.8151 | 3.8758 | 4.1363 | 4.0321 | 4.2925 | 1.8948 | 2.8702 | 3.4171 | 3.4171 | 3.7818 | 3.7818 | 2019-09-13 21:00 | 1.829 | 3.1386 | 5.3048 | 5.3048 | 5.3048 | 5.3048
2021-07-17 09:00 | 3.5552 | 4.4026 | 4.4727 | 4.7732 | 4.653 | 4.9535 | 2.2577 | 3.42 | 4.0717 | 4.0717 | 4.5062 | 4.5062 | 2019-09-13 22:00 | 1.7681 | 3.034 | 5.128 | 5.128 | 5.128 | 5.128
2021-07-17 10:00 | 3.6066 | 4.4663 | 4.5374 | 4.8423 | 4.7203 | 5.0252 | 2.4178 | 3.6624 | 4.3603 | 4.3603 | 4.8256 | 4.8256 | 2019-09-13 23:00 | 1.5242 | 2.6155 | 4.4207 | 4.4207 | 4.4207 | 4.4207
2021-07-17 11:00 | 3.5809 | 4.4344 | 4.505 | 4.8077 | 4.6867 | 4.9894 | 2.5292 | 3.8313 | 4.5613 | 4.5613 | 5.0481 | 5.0481 | 2019-09-14 | 1.4327 | 2.4586 | 4.1555 | 4.1555 | 4.1555 | 4.1555
2021-07-17 12:00 | 3.1408 | 3.8894 | 3.9513 | 4.2168 | 4.1106 | 4.3761 | 2.3749 | 3.5975 | 4.283 | 4.283 | 4.74 | 4.74 | 2019-09-14 01:00 | 1.3718 | 2.354 | 3.9786 | 3.9786 | 3.9786 | 3.9786
2021-07-17 13:00 | 3.0636 | 3.7938 | 3.8543 | 4.1132 | 4.0097 | 4.2686 | 2.3377 | 3.5412 | 4.216 | 4.216 | 4.6659 | 4.6659 | 2019-09-14 02:00 | 1.3337 | 2.2886 | 3.8681 | 3.8681 | 3.8681 | 3.8681
2021-07-17 14:00 | 3.0522 | 3.7797 | 3.8399 | 4.0979 | 3.9947 | 4.2527 | 2.2549 | 3.4157 | 4.0666 | 4.0666 | 4.5005 | 4.5005 | 2019-09-14 03:00 | 1.3337 | 2.2886 | 3.8681 | 3.8681 | 3.8681 | 3.8681
2021-07-17 15:00 | 2.9751 | 3.6841 | 3.7428 | 3.9943 | 3.8937 | 4.1452 | 2.2634 | 3.4287 | 4.082 | 4.082 | 4.5176 | 4.5176 | 2019-09-14 04:00 | 1.3565 | 2.3278 | 3.9344 | 3.9344 | 3.9344 | 3.9344
2021-07-17 16:00 | 3.218 | 3.9849 | 4.0484 | 4.3204 | 4.2116 | 4.4837 | 2.5635 | 3.8832 | 4.6232 | 4.6232 | 5.1165 | 5.1165 | 2019-09-14 05:00 | 1.5852 | 2.7202 | 4.5975 | 4.5975 | 4.5975 | 4.5975
2021-07-17 17:00 | 3.5323 | 4.3742 | 4.4439 | 4.7425 | 4.6231 | 4.9217 | 2.7521 | 4.169 | 4.9634 | 4.9634 | 5.493 | 5.493 | 2019-09-14 06:00 | 1.5547 | 2.6678 | 4.5091 | 4.5091 | 4.5091 | 4.5091
2021-07-17 18:00 | 3.5238 | 4.3636 | 4.4331 | 4.731 | 4.6119 | 4.9097 | 2.6721 | 4.0477 | 4.8191 | 4.8191 | 5.3333 | 5.3333 | 2019-09-14 07:00 | 1.7986 | 3.0863 | 5.2164 | 5.2164 | 5.2164 | 5.2164
2021-07-17 19:00 | 3.4095 | 4.2221 | 4.2893 | 4.5775 | 4.4622 | 4.7504 | 2.6978 | 4.0867 | 4.8654 | 4.8654 | 5.3846 | 5.3846 | 2019-09-14 08:00 | 1.9434 | 3.3348 | 5.6364 | 5.6364 | 5.6364 | 5.6364
2021-07-17 20:00 | 3.3323 | 4.1265 | 4.1922 | 4.4739 | 4.3612 | 4.6429 | 2.595 | 3.9309 | 4.6799 | 4.6799 | 5.1793 | 5.1793 | 2019-09-14 09:00 | 1.9891 | 3.4133 | 5.769 | 5.769 | 5.769 | 5.769
2021-07-17 21:00 | 2.9893 | 3.7018 | 3.7608 | 4.0135 | 3.9124 | 4.1651 | 2.4293 | 3.6799 | 4.3811 | 4.3811 | 4.8486 | 4.8486 | 2019-09-14 10:00 | 1.9967 | 3.4264 | 5.7911 | 5.7911 | 5.7911 | 5.7911
2021-07-17 22:00 | 2.7121 | 3.3585 | 3.412 | 3.6413 | 3.5496 | 3.7789 | 2.2406 | 3.394 | 4.0408 | 4.0408 | 4.472 | 4.472 | 2019-09-14 11:00 | 2.0043 | 3.4394 | 5.8132 | 5.8132 | 5.8132 | 5.8132
2021-07-17 23:00 | 2.5464 | 3.1533 | 3.2035 | 3.4188 | 3.3327 | 3.5479 | 1.9062 | 2.8875 | 3.4378 | 3.4378 | 3.8046 | 3.8046 | 2019-09-14 12:00 | 2.0119 | 3.4525 | 5.8353 | 5.8353 | 5.8353 | 5.8353
2021-07-18 | 2.3018 | 2.8504 | 2.8958 | 3.0904 | 3.0126 | 3.2071 | 1.609 | 2.4373 | 2.9017 | 2.9017 | 3.2114 | 3.2114 | 2019-09-14 13:00 | 2.0196 | 3.4656 | 5.8574 | 5.8574 | 5.8574 | 5.8574
2021-07-18 01:00 | 2.0548 | 2.5446 | 2.5851 | 2.7588 | 2.6893 | 2.863 | 1.3918 | 2.1083 | 2.51 | 2.51 | 2.7779 | 2.7779 | 2019-09-14 14:00 | 2.0501 | 3.5179 | 5.9458 | 5.9458 | 5.9458 | 5.9458
2021-07-18 02:00 | 1.9891 | 2.4632 | 2.5024 | 2.6705 | 2.6033 | 2.7714 | 1.2605 | 1.9095 | 2.2733 | 2.2733 | 2.5159 | 2.5159 | 2019-09-14 15:00 | 2.111 | 3.6225 | 6.1227 | 6.1227 | 6.1227 | 6.1227
2021-07-18 03:00 | 1.8835 | 2.3324 | 2.3696 | 2.5288 | 2.4651 | 2.6243 | 1.206 | 1.8269 | 2.175 | 2.175 | 2.4071 | 2.4071 | 2019-09-14 16:00 | 1.9967 | 3.4264 | 5.7911 | 5.7911 | 5.7911 | 5.7911
2021-07-18 04:00 | 1.9348 | 2.3959 | 2.4341 | 2.5976 | 2.5322 | 2.6958 | 1.2289 | 1.8615 | 2.2162 | 2.2162 | 2.4527 | 2.4527 | 2019-09-14 17:00 | 1.9738 | 3.3871 | 5.7248 | 5.7248 | 5.7248 | 5.7248
2021-07-18 05:00 | 2.0062 | 2.4844 | 2.524 | 2.6936 | 2.6257 | 2.7953 | 1.2003 | 1.8182 | 2.1647 | 2.1647 | 2.3957 | 2.3957 | 2019-09-14 18:00 | 1.9662 | 3.374 | 5.7027 | 5.7027 | 5.7027 | 5.7027
2021-07-18 06:00 | 2.2577 | 2.7958 | 2.8404 | 3.0312 | 2.9549 | 3.1457 | 1.3575 | 2.0563 | 2.4482 | 2.4482 | 2.7094 | 2.7094 | 2019-09-14 19:00 | 1.9281 | 3.3087 | 5.5922 | 5.5922 | 5.5922 | 5.5922
2021-07-18 07:00 | 2.5162 | 3.116 | 3.1656 | 3.3783 | 3.2932 | 3.5059 | 1.729 | 2.6191 | 3.1182 | 3.1182 | 3.4509 | 3.4509 | 2019-09-14 20:00 | 1.7833 | 3.0602 | 5.1722 | 5.1722 | 5.1722 | 5.1722
2021-07-18 08:00 | 2.6721 | 3.309 | 3.3617 | 3.5876 | 3.4972 | 3.7231 | 1.7633 | 2.6711 | 3.1801 | 3.1801 | 3.5194 | 3.5194 | 2019-09-14 21:00 | 1.7605 | 3.0209 | 5.1059 | 5.1059 | 5.1059 | 5.1059
2021-07-18 09:00 | 2.7264 | 3.3762 | 3.43 | 3.6605 | 3.5683 | 3.7988 | 2.0148 | 3.052 | 3.6336 | 3.6336 | 4.0213 | 4.0213 | 2019-09-14 22:00 | 1.6766 | 2.8771 | 4.8628 | 4.8628 | 4.8628 | 4.8628
2021-07-18 10:00 | 2.7293 | 3.3798 | 3.4336 | 3.6643 | 3.572 | 3.8027 | 2.0805 | 3.1516 | 3.7522 | 3.7522 | 4.1525 | 4.1525 | 2019-09-14 23:00 | 1.6309 | 2.7986 | 4.7301 | 4.7301 | 4.7301 | 4.7301
2021-07-18 11:00 | 2.5807 | 3.1957 | 3.2466 | 3.4648 | 3.3775 | 3.5957 | 2.2034 | 3.3378 | 3.9738 | 3.9738 | 4.3978 | 4.3978 | 2019-09-15 | 1.4632 | 2.5109 | 4.2439 | 4.2439 | 4.2439 | 4.2439
2021-07-18 12:00 | 2.4692 | 3.0577 | 3.1064 | 3.3152 | 3.2317 | 3.4404 | 2.1263 | 3.2209 | 3.8346 | 3.8346 | 4.2438 | 4.2438 | 2019-09-15 01:00 | 1.387 | 2.3801 | 4.0228 | 4.0228 | 4.0228 | 4.0228
2021-07-18 13:00 | 2.4406 | 3.0223 | 3.0705 | 3.2768 | 3.1943 | 3.4006 | 2.0062 | 3.0391 | 3.6182 | 3.6182 | 4.0042 | 4.0042 | 2019-09-15 02:00 | 1.3032 | 2.2363 | 3.7797 | 3.7797 | 3.7797 | 3.7797
2021-07-18 14:00 | 2.1491 | 2.6613 | 2.7037 | 2.8854 | 2.8127 | 2.9944 | 2.0805 | 3.1516 | 3.7522 | 3.7522 | 4.1525 | 4.1525 | 2019-09-15 03:00 | 1.3261 | 2.2755 | 3.846 | 3.846 | 3.846 | 3.846
2021-07-18 15:00 | 2.3907 | 2.9605 | 3.0076 | 3.2097 | 3.1289 | 3.331 | 2.1548 | 3.2642 | 3.8862 | 3.8862 | 4.3008 | 4.3008 | 2019-09-15 04:00 | 1.4099 | 2.4194 | 4.0891 | 4.0891 | 4.0891 | 4.0891
2021-07-18 16:00 | 2.8733 | 3.5581 | 3.6147 | 3.8576 | 3.7605 | 4.0034 | 2.3492 | 3.5585 | 4.2366 | 4.2366 | 4.6887 | 4.6887 | 2019-09-15 05:00 | 1.4556 | 2.4978 | 4.2218 | 4.2218 | 4.2218 | 4.2218
2021-07-18 17:00 | 3.5209 | 4.3601 | 4.4295 | 4.7272 | 4.6081 | 4.9057 | 2.6207 | 3.9698 | 4.7263 | 4.7263 | 5.2306 | 5.2306 | 2019-09-15 06:00 | 1.4709 | 2.524 | 4.266 | 4.266 | 4.266 | 4.266
2021-07-18 18:00 | 3.5409 | 4.3849 | 4.4547 | 4.754 | 4.6343 | 4.9336 | 2.8036 | 4.2469 | 5.0561 | 5.0561 | 5.5956 | 5.5956 | 2019-09-15 07:00 | 1.6538 | 2.8379 | 4.7965 | 4.7965 | 4.7965 | 4.7965
2021-07-18 19:00 | 3.3723 | 4.1761 | 4.2426 | 4.5276 | 4.4136 | 4.6987 | 2.8122 | 4.2599 | 5.0716 | 5.0716 | 5.6128 | 5.6128 | 2019-09-15 08:00 | 1.7757 | 3.0471 | 5.1501 | 5.1501 | 5.1501 | 5.1501
2021-07-18 20:00 | 3.2094 | 3.9743 | 4.0376 | 4.3089 | 4.2004 | 4.4717 | 2.6978 | 4.0867 | 4.8654 | 4.8654 | 5.3846 | 5.3846 | 2019-09-15 09:00 | 1.8824 | 3.2302 | 5.4596 | 5.4596 | 5.4596 | 5.4596
2021-07-18 21:00 | 3.0408 | 3.7655 | 3.8255 | 4.0826 | 3.9797 | 4.2368 | 2.5149 | 3.8096 | 4.5356 | 4.5356 | 5.0195 | 5.0195 | 2019-09-15 10:00 | 1.9967 | 3.4264 | 5.7911 | 5.7911 | 5.7911 | 5.7911
2021-07-18 22:00 | 2.7178 | 3.3656 | 3.4192 | 3.649 | 3.5571 | 3.7868 | 2.1291 | 3.2252 | 3.8398 | 3.8398 | 4.2495 | 4.2495 | 2019-09-15 11:00 | 2.0805 | 3.5702 | 6.0343 | 6.0343 | 6.0343 | 6.0343
2021-07-18 23:00 | 2.5235 | 3.125 | 3.1747 | 3.3881 | 3.3027 | 3.516 | 1.749 | 2.6494 | 3.1543 | 3.1543 | 3.4909 | 3.4909 | 2019-09-15 12:00 | 1.9967 | 3.4264 | 5.7911 | 5.7911 | 5.7911 | 5.7911
2021-07-19 | 2.192 | 2.7144 | 2.7577 | 2.943 | 2.8688 | 3.0541 | 1.3754 | 2.0835 | 2.4805 | 2.4805 | 2.7452 | 2.7452 | 2019-09-15 13:00 | 2.111 | 3.6225 | 6.1227 | 6.1227 | 6.1227 | 6.1227
2021-07-19 01:00 | 1.9897 | 2.4639 | 2.5032 | 2.6714 | 2.6041 | 2.7723 | 1.2317 | 1.8657 | 2.2213 | 2.2213 | 2.4583 | 2.4583 | 2019-09-15 14:00 | 2.0424 | 3.5048 | 5.9237 | 5.9237 | 5.9237 | 5.9237
2021-07-19 02:00 | 2.0005 | 2.4773 | 2.5168 | 2.6859 | 2.6182 | 2.7874 | 1.1603 | 1.7576 | 2.0925 | 2.0925 | 2.3158 | 2.3158 | 2019-09-15 15:00 | 2.0653 | 3.5441 | 5.99 | 5.99 | 5.99 | 5.99
2021-07-19 03:00 | 1.8943 | 2.3458 | 2.3831 | 2.5433 | 2.4792 | 2.6393 | 1.1603 | 1.7576 | 2.0925 | 2.0925 | 2.3158 | 2.3158 | 2019-09-15 16:00 | 2.0119 | 3.4525 | 5.8353 | 5.8353 | 5.8353 | 5.8353
2021-07-19 04:00 | 1.9955 | 2.4712 | 2.5105 | 2.6792 | 2.6117 | 2.7804 | 1.1632 | 1.762 | 2.0977 | 2.0977 | 2.3215 | 2.3215 | 2019-09-15 17:00 | 1.9967 | 3.4264 | 5.7911 | 5.7911 | 5.7911 | 5.7911
2021-07-19 05:00 | 2.5864 | 3.2028 | 3.2538 | 3.4725 | 3.385 | 3.6036 | 1.3232 | 2.0044 | 2.3863 | 2.3863 | 2.641 | 2.641 | 2019-09-15 18:00 | 1.951 | 3.3479 | 5.6585 | 5.6585 | 5.6585 | 5.6585
2021-07-19 06:00 | 3.5146 | 4.3523 | 4.4216 | 4.7187 | 4.5998 | 4.8969 | 1.7596 | 2.6655 | 3.1734 | 3.1734 | 3.512 | 3.512 | 2019-09-15 19:00 | 1.9053 | 3.2694 | 5.5259 | 5.5259 | 5.5259 | 5.5259
2021-07-19 07:00 | 4.404 | 5.4536 | 5.5405 | 5.9128 | 5.7639 | 6.1362 | 2.2406 | 3.394 | 4.0408 | 4.0408 | 4.472 | 4.472 | 2019-09-15 20:00 | 1.7681 | 3.034 | 5.128 | 5.128 | 5.128 | 5.128
2021-07-19 08:00 | 4.5069 | 5.5811 | 5.6699 | 6.0509 | 5.8985 | 6.2795 | 2.1291 | 3.2252 | 3.8398 | 3.8398 | 4.2495 | 4.2495 | 2019-09-15 21:00 | 1.6842 | 2.8902 | 4.8849 | 4.8849 | 4.8849 | 4.8849
2021-07-19 09:00 | 4.3697 | 5.4112 | 5.4974 | 5.8668 | 5.719 | 6.0884 | 2.0262 | 3.0694 | 3.6542 | 3.6542 | 4.0441 | 4.0441 | 2019-09-15 22:00 | 1.6157 | 2.7725 | 4.6859 | 4.6859 | 4.6859 | 4.6859
2021-07-19 10:00 | 4.3754 | 5.4183 | 5.5046 | 5.8744 | 5.7265 | 6.0963 | 2.1491 | 3.2555 | 3.8759 | 3.8759 | 4.2894 | 4.2894 | 2019-09-15 23:00 | 1.509 | 2.5894 | 4.3765 | 4.3765 | 4.3765 | 4.3765
2021-07-19 11:00 | 4.2611 | 5.2767 | 5.3607 | 5.7209 | 5.5769 | 5.9371 | 2.1891 | 3.3161 | 3.948 | 3.948 | 4.3693 | 4.3693 | 2019-09-16 | 1.4175 | 2.4324 | 4.1112 | 4.1112 | 4.1112 | 4.1112
2021-07-19 12:00 | 4.0382 | 5.0006 | 5.0803 | 5.4217 | 5.2851 | 5.6265 | 2.152 | 3.2598 | 3.881 | 3.881 | 4.2951 | 4.2951 | 2019-09-16 01:00 | 1.3337 | 2.2886 | 3.8681 | 3.8681 | 3.8681 | 3.8681
2021-07-19 13:00 | 4.021 | 4.9794 | 5.0587 | 5.3986 | 5.2627 | 5.6026 | 2.1291 | 3.2252 | 3.8398 | 3.8398 | 4.2495 | 4.2495 | 2019-09-16 02:00 | 1.3413 | 2.3017 | 3.8902 | 3.8902 | 3.8902 | 3.8902
2021-07-19 14:00 | 3.921 | 4.8555 | 4.9329 | 5.2643 | 5.1318 | 5.4632 | 2.1348 | 3.2339 | 3.8501 | 3.8501 | 4.2609 | 4.2609 | 2019-09-16 03:00 | 1.3413 | 2.3017 | 3.8902 | 3.8902 | 3.8902 | 3.8902
2021-07-19 15:00 | 3.8524 | 4.7706 | 4.8466 | 5.1723 | 5.042 | 5.3676 | 2.1463 | 3.2512 | 3.8707 | 3.8707 | 4.2837 | 4.2837 | 2019-09-16 04:00 | 1.3413 | 2.3017 | 3.8902 | 3.8902 | 3.8902 | 3.8902
2021-07-19 16:00 | 4.1411 | 5.1281 | 5.2097 | 5.5598 | 5.4198 | 5.7698 | 2.3063 | 3.4936 | 4.1593 | 4.1593 | 4.6031 | 4.6031 | 2019-09-16 05:00 | 1.5166 | 2.6025 | 4.3986 | 4.3986 | 4.3986 | 4.3986
2021-07-19 17:00 | 4.5412 | 5.6235 | 5.7131 | 6.097 | 5.9434 | 6.3273 | 2.6578 | 4.0261 | 4.7933 | 4.7933 | 5.3047 | 5.3047 | 2019-09-16 06:00 | 1.7071 | 2.9294 | 4.9512 | 4.9512 | 4.9512 | 4.9512
2021-07-19 18:00 | 4.6812 | 5.7969 | 5.8893 | 6.285 | 6.1267 | 6.5224 | 2.8722 | 4.3508 | 5.1798 | 5.1798 | 5.7325 | 5.7325 | 2019-09-16 07:00 | 2.0882 | 3.5833 | 6.0564 | 6.0564 | 6.0564 | 6.0564
2021-07-19 19:00 | 4.4411 | 5.4997 | 5.5873 | 5.9627 | 5.8125 | 6.1879 | 2.8179 | 4.2685 | 5.0819 | 5.0819 | 5.6242 | 5.6242 | 2019-09-16 08:00 | 2.1034 | 3.6094 | 6.1006 | 6.1006 | 6.1006 | 6.1006
2021-07-19 20:00 | 3.981 | 4.9299 | 5.0084 | 5.3449 | 5.2103 | 5.5468 | 2.7121 | 4.1083 | 4.8912 | 4.8912 | 5.4131 | 5.4131 | 2019-09-16 09:00 | 2.1567 | 3.701 | 6.2553 | 6.2553 | 6.2553 | 6.2553
2021-07-19 21:00 | 3.6359 | 4.5025 | 4.5742 | 4.8816 | 4.7586 | 5.066 | 2.5578 | 3.8746 | 4.6129 | 4.6129 | 5.1051 | 5.1051 | 2019-09-16 10:00 | 2.1872 | 3.7533 | 6.3437 | 6.3437 | 6.3437 | 6.3437
2021-07-19 22:00 | 3.0208 | 3.7408 | 3.8003 | 4.0557 | 3.9535 | 4.2089 | 2.2034 | 3.3378 | 3.9738 | 3.9738 | 4.3978 | 4.3978 | 2019-09-16 11:00 | 2.1796 | 3.7402 | 6.3216 | 6.3216 | 6.3216 | 6.3216
2021-07-19 23:00 | 2.6064 | 3.2276 | 3.279 | 3.4993 | 3.4112 | 3.6315 | 1.8405 | 2.788 | 3.3192 | 3.3192 | 3.6734 | 3.6734 | 2019-09-16 12:00 | 2.1796 | 3.7402 | 6.3216 | 6.3216 | 6.3216 | 6.3216
2021-07-20 | 2.3663 | 2.9303 | 2.977 | 3.177 | 3.097 | 3.297 | 1.4233 | 2.1561 | 2.5669 | 2.5669 | 2.8408 | 2.8408 | 2019-09-16 13:00 | 2.2177 | 3.8056 | 6.4321 | 6.4321 | 6.4321 | 6.4321
2021-07-20 01:00 | 2.1548 | 2.6684 | 2.7109 | 2.8931 | 2.8202 | 3.0024 | 1.3095 | 1.9836 | 2.3616 | 2.3616 | 2.6136 | 2.6136 | 2019-09-16 14:00 | 2.1872 | 3.7533 | 6.3437 | 6.3437 | 6.3437 | 6.3437
2021-07-20 02:00 | 2.0948 | 2.5941 | 2.6354 | 2.8125 | 2.7417 | 2.9188 | 1.2216 | 1.8505 | 2.2032 | 2.2032 | 2.4383 | 2.4383 | 2019-09-16 15:00 | 2.172 | 3.7271 | 6.2995 | 6.2995 | 6.2995 | 6.2995
2021-07-20 03:00 | 2.0863 | 2.5835 | 2.6246 | 2.801 | 2.7305 | 2.9068 | 1.2232 | 1.8529 | 2.2059 | 2.2059 | 2.4413 | 2.4413 | 2019-09-16 16:00 | 2.0882 | 3.5833 | 6.0564 | 6.0564 | 6.0564 | 6.0564
2021-07-20 04:00 | 2.2091 | 2.7357 | 2.7792 | 2.966 | 2.8913 | 3.078 | 1.1746 | 1.7793 | 2.1183 | 2.1183 | 2.3443 | 2.3443 | 2019-09-16 17:00 | 2.111 | 3.6225 | 6.1227 | 6.1227 | 6.1227 | 6.1227
2021-07-20 05:00 | 2.5759 | 3.1899 | 3.2407 | 3.4584 | 3.3713 | 3.5891 | 1.4032 | 2.1256 | 2.5306 | 2.5306 | 2.8007 | 2.8007 | 2019-09-16 18:00 | 2.0958 | 3.5964 | 6.0785 | 6.0785 | 6.0785 | 6.0785
2021-07-20 06:00 | 3.8496 | 4.7671 | 4.843 | 5.1684 | 5.0383 | 5.3637 | 1.7719 | 2.6841 | 3.1955 | 3.1955 | 3.5365 | 3.5365 | 2019-09-16 19:00 | 1.9738 | 3.3871 | 5.7248 | 5.7248 | 5.7248 | 5.7248
2021-07-20 07:00 | 4.4269 | 5.482 | 5.5693 | 5.9435 | 5.7938 | 6.168 | 2.172 | 3.2901 | 3.9171 | 3.9171 | 4.3351 | 4.3351 | 2019-09-16 20:00 | 1.8214 | 3.1256 | 5.2827 | 5.2827 | 5.2827 | 5.2827
2021-07-20 08:00 | 4.544 | 5.6271 | 5.7167 | 6.1008 | 5.9472 | 6.3313 | 2.152 | 3.2598 | 3.881 | 3.881 | 4.2951 | 4.2951 | 2019-09-16 21:00 | 1.7986 | 3.0863 | 5.2164 | 5.2164 | 5.2164 | 5.2164
2021-07-20 09:00 | 4.5269 | 5.6058 | 5.6951 | 6.0778 | 5.9247 | 6.3074 | 2.0577 | 3.117 | 3.7109 | 3.7109 | 4.1069 | 4.1069 | 2019-09-16 22:00 | 1.7376 | 2.9817 | 5.0396 | 5.0396 | 5.0396 | 5.0396
2021-07-20 10:00 | 4.5297 | 5.6094 | 5.6987 | 6.0816 | 5.9285 | 6.3114 | 2.0834 | 3.1559 | 3.7573 | 3.7573 | 4.1582 | 4.1582 | 2019-09-16 23:00 | 1.509 | 2.5894 | 4.3765 | 4.3765 | 4.3765 | 4.3765
2021-07-20 11:00 | 4.3183 | 5.3475 | 5.4326 | 5.7977 | 5.6517 | 6.0167 | 2.1406 | 3.2425 | 3.8604 | 3.8604 | 4.2723 | 4.2723 | 2019-09-17 | 1.4023 | 2.4063 | 4.067 | 4.067 | 4.067 | 4.067
2021-07-20 12:00 | 4.1754 | 5.1705 | 5.2529 | 5.6058 | 5.4647 | 5.8176 | 2.1463 | 3.2512 | 3.8707 | 3.8707 | 4.2837 | 4.2837 | 2019-09-17 01:00 | 1.3337 | 2.2886 | 3.8681 | 3.8681 | 3.8681 | 3.8681
2021-07-20 13:00 | 4.1325 | 5.1174 | 5.1989 | 5.5483 | 5.4085 | 5.7579 | 2.2006 | 3.3334 | 3.9686 | 3.9686 | 4.3921 | 4.3921 | 2019-09-17 02:00 | 1.227 | 2.1055 | 3.5587 | 3.5587 | 3.5587 | 3.5587
2021-07-20 14:00 | 4.0382 | 5.0006 | 5.0803 | 5.4217 | 5.2851 | 5.6265 | 2.1005 | 3.1819 | 3.7882 | 3.7882 | 4.1925 | 4.1925 | 2019-09-17 03:00 | 1.227 | 2.1055 | 3.5587 | 3.5587 | 3.5587 | 3.5587
2021-07-20 15:00 | 4.0067 | 4.9617 | 5.0408 | 5.3795 | 5.244 | 5.5827 | 2.0577 | 3.117 | 3.7109 | 3.7109 | 4.1069 | 4.1069 | 2019-09-17 04:00 | 1.3108 | 2.2494 | 3.8018 | 3.8018 | 3.8018 | 3.8018
2021-07-20 16:00 | 4.1411 | 5.1281 | 5.2097 | 5.5598 | 5.4198 | 5.7698 | 2.312 | 3.5023 | 4.1696 | 4.1696 | 4.6146 | 4.6146 | 2019-09-17 05:00 | 1.5166 | 2.6025 | 4.3986 | 4.3986 | 4.3986 | 4.3986
2021-07-20 17:00 | 4.7669 | 5.9031 | 5.9971 | 6.4001 | 6.2389 | 6.6419 | 2.755 | 4.1733 | 4.9685 | 4.9685 | 5.4987 | 5.4987 | 2019-09-17 06:00 | 1.7909 | 3.0733 | 5.1943 | 5.1943 | 5.1943 | 5.1943
2021-07-20 18:00 | 4.7212 | 5.8465 | 5.9396 | 6.3387 | 6.1791 | 6.5782 | 2.7664 | 4.1906 | 4.9891 | 4.9891 | 5.5215 | 5.5215 | 2019-09-17 07:00 | 2.0882 | 3.5833 | 6.0564 | 6.0564 | 6.0564 | 6.0564
2021-07-20 19:00 | 4.4588 | 5.5215 | 5.6094 | 5.9863 | 5.8356 | 6.2125 | 2.815 | 4.2642 | 5.0768 | 5.0768 | 5.6185 | 5.6185 | 2019-09-17 08:00 | 2.1567 | 3.701 | 6.2553 | 6.2553 | 6.2553 | 6.2553
2021-07-20 20:00 | 4.1211 | 5.1033 | 5.1846 | 5.5329 | 5.3936 | 5.742 | 2.7607 | 4.1819 | 4.9788 | 4.9788 | 5.5101 | 5.5101 | 2019-09-17 09:00 | 2.1949 | 3.7664 | 6.3658 | 6.3658 | 6.3658 | 6.3658
2021-07-20 21:00 | 3.6025 | 4.4611 | 4.5322 | 4.8367 | 4.7149 | 5.0194 | 2.4806 | 3.7577 | 4.4737 | 4.4737 | 4.9511 | 4.9511 | 2019-09-17 10:00 | 2.2558 | 3.871 | 6.5426 | 6.5426 | 6.5426 | 6.5426
2021-07-20 22:00 | 3.218 | 3.9849 | 4.0484 | 4.3204 | 4.2116 | 4.4837 | 2.2177 | 3.3594 | 3.9996 | 3.9996 | 4.4263 | 4.4263 | 2019-09-17 11:00 | 2.2025 | 3.7795 | 6.3879 | 6.3879 | 6.3879 | 6.3879
2021-07-20 23:00 | 2.7293 | 3.3798 | 3.4336 | 3.6643 | 3.572 | 3.8027 | 1.8576 | 2.8139 | 3.3501 | 3.3501 | 3.7076 | 3.7076 | 2019-09-17 12:00 | 2.1491 | 3.6879 | 6.2332 | 6.2332 | 6.2332 | 6.2332
2021-07-21 | 2.3048 | 2.8541 | 2.8996 | 3.0944 | 3.0165 | 3.2113 | 1.4861 | 2.2511 | 2.6801 | 2.6801 | 2.9661 | 2.9661 | 2019-09-17 13:00 | 2.1644 | 3.7141 | 6.2774 | 6.2774 | 6.2774 | 6.2774
2021-07-21 01:00 | 2.112 | 2.6153 | 2.657 | 2.8355 | 2.7641 | 2.9426 | 1.3432 | 2.0347 | 2.4224 | 2.4224 | 2.6809 | 2.6809 | 2019-09-17 14:00 | 2.0882 | 3.5833 | 6.0564 | 6.0564 | 6.0564 | 6.0564
2021-07-21 02:00 | 2.0374 | 2.523 | 2.5632 | 2.7354 | 2.6665 | 2.8387 | 1.3032 | 1.9741 | 2.3503 | 2.3503 | 2.601 | 2.601 | 2019-09-17 15:00 | 2.0577 | 3.531 | 5.9679 | 5.9679 | 5.9679 | 5.9679
2021-07-21 03:00 | 2.1263 | 2.633 | 2.675 | 2.8547 | 2.7828 | 2.9626 | 1.2317 | 1.8659 | 2.2214 | 2.2214 | 2.4584 | 2.4584 | 2019-09-17 16:00 | 2.1034 | 3.6094 | 6.1006 | 6.1006 | 6.1006 | 6.1006
2021-07-21 04:00 | 2.1548 | 2.6684 | 2.7109 | 2.8931 | 2.8202 | 3.0024 | 1.2489 | 1.8918 | 2.2523 | 2.2523 | 2.4927 | 2.4927 | 2019-09-17 17:00 | 2.0424 | 3.5048 | 5.9237 | 5.9237 | 5.9237 | 5.9237
2021-07-21 05:00 | 2.8636 | 3.5461 | 3.6026 | 3.8447 | 3.7478 | 3.9899 | 1.3954 | 2.1137 | 2.5165 | 2.5165 | 2.785 | 2.785 | 2019-09-17 18:00 | 2.1567 | 3.701 | 6.2553 | 6.2553 | 6.2553 | 6.2553
2021-07-21 06:00 | 3.9039 | 4.8343 | 4.9113 | 5.2413 | 5.1093 | 5.4393 | 1.8319 | 2.775 | 3.3038 | 3.3038 | 3.6563 | 3.6563 | 2019-09-17 19:00 | 2.111 | 3.6225 | 6.1227 | 6.1227 | 6.1227 | 6.1227
2021-07-21 07:00 | 4.9013 | 6.0694 | 6.1661 | 6.5804 | 6.4147 | 6.829 | 2.2892 | 3.4676 | 4.1284 | 4.1284 | 4.5689 | 4.5689 | 2019-09-17 20:00 | 1.9586 | 3.361 | 5.6806 | 5.6806 | 5.6806 | 5.6806
2021-07-21 08:00 | 4.7755 | 5.9137 | 6.0079 | 6.4116 | 6.2501 | 6.6538 | 2.1863 | 3.3118 | 3.9429 | 3.9429 | 4.3636 | 4.3636 | 2019-09-17 21:00 | 1.9129 | 3.2825 | 5.548 | 5.548 | 5.548 | 5.548
2021-07-21 09:00 | 4.3325 | 5.3652 | 5.4506 | 5.8169 | 5.6704 | 6.0366 | 2.0062 | 3.0391 | 3.6182 | 3.6182 | 4.0042 | 4.0042 | 2019-09-17 22:00 | 1.7071 | 2.9294 | 4.9512 | 4.9512 | 4.9512 | 4.9512
2021-07-21 10:00 | 4.021 | 4.9794 | 5.0587 | 5.3986 | 5.2627 | 5.6026 | 2.0234 | 3.065 | 3.6491 | 3.6491 | 4.0384 | 4.0384 | 2019-09-17 23:00 | 1.509 | 2.5894 | 4.3765 | 4.3765 | 4.3765 | 4.3765
2021-07-21 11:00 | 3.6124 | 4.4733 | 4.5446 | 4.8499 | 4.7278 | 5.0332 | 1.9834 | 3.0044 | 3.5769 | 3.5769 | 3.9586 | 3.9586 | 2019-09-18 | 1.3413 | 2.3017 | 3.8902 | 3.8902 | 3.8902 | 3.8902
2021-07-21 12:00 | 3.5952 | 4.4521 | 4.523 | 4.8269 | 4.7054 | 5.0093 | 1.9576 | 2.9655 | 3.5305 | 3.5305 | 3.9073 | 3.9073 | 2019-09-18 01:00 | 1.2956 | 2.2232 | 3.7576 | 3.7576 | 3.7576 | 3.7576
2021-07-21 13:00 | 3.2951 | 4.0805 | 4.1455 | 4.424 | 4.3126 | 4.5912 | 1.9148 | 2.9005 | 3.4532 | 3.4532 | 3.8217 | 3.8217 | 2019-09-18 02:00 | 1.2651 | 2.1709 | 3.6692 | 3.6692 | 3.6692 | 3.6692
2021-07-21 14:00 | 3.2637 | 4.0416 | 4.1059 | 4.3818 | 4.2715 | 4.5474 | 1.8548 | 2.8096 | 3.345 | 3.345 | 3.7019 | 3.7019 | 2019-09-18 03:00 | 1.2651 | 2.1709 | 3.6692 | 3.6692 | 3.6692 | 3.6692
2021-07-21 15:00 | 3.378 | 4.1831 | 4.2498 | 4.5353 | 4.4211 | 4.7066 | 1.8205 | 2.7577 | 3.2831 | 3.2831 | 3.6335 | 3.6335 | 2019-09-18 04:00 | 1.3108 | 2.2494 | 3.8018 | 3.8018 | 3.8018 | 3.8018
2021-07-21 16:00 | 3.7267 | 4.6149 | 4.6884 | 5.0034 | 4.8774 | 5.1924 | 2.0491 | 3.104 | 3.6955 | 3.6955 | 4.0898 | 4.0898 | 2019-09-18 05:00 | 1.4175 | 2.4324 | 4.1112 | 4.1112 | 4.1112 | 4.1112
2021-07-21 17:00 | 4.4269 | 5.482 | 5.5693 | 5.9435 | 5.7938 | 6.168 | 2.4606 | 3.7274 | 4.4377 | 4.4377 | 4.9112 | 4.9112 | 2019-09-18 06:00 | 1.6538 | 2.8379 | 4.7965 | 4.7965 | 4.7965 | 4.7965
2021-07-21 18:00 | 4.504 | 5.5775 | 5.6664 | 6.0471 | 5.8948 | 6.2755 | 2.7979 | 4.2382 | 5.0458 | 5.0458 | 5.5842 | 5.5842 | 2019-09-18 07:00 | 1.9662 | 3.374 | 5.7027 | 5.7027 | 5.7027 | 5.7027
2021-07-21 19:00 | 4.4697 | 5.535 | 5.6232 | 6.001 | 5.8499 | 6.2277 | 2.7378 | 4.1473 | 4.9376 | 4.9376 | 5.4645 | 5.4645 | 2019-09-18 08:00 | 2.172 | 3.7271 | 6.2995 | 6.2995 | 6.2995 | 6.2995
2021-07-21 20:00 | 4.0296 | 4.99 | 5.0695 | 5.4101 | 5.2739 | 5.6145 | 2.635 | 3.9915 | 4.752 | 4.752 | 5.2591 | 5.2591 | 2019-09-18 09:00 | 2.1034 | 3.6094 | 6.1006 | 6.1006 | 6.1006 | 6.1006
2021-07-21 21:00 | 3.681 | 4.5583 | 4.6309 | 4.942 | 4.8176 | 5.1287 | 2.6407 | 4.0001 | 4.7624 | 4.7624 | 5.2705 | 5.2705 | 2019-09-18 10:00 | 2.0119 | 3.4525 | 5.8353 | 5.8353 | 5.8353 | 5.8353
2021-07-21 22:00 | 3.2055 | 3.9695 | 4.0327 | 4.3037 | 4.1953 | 4.4663 | 2.2749 | 3.446 | 4.1026 | 4.1026 | 4.5404 | 4.5404 | 2019-09-18 11:00 | 2.0424 | 3.5048 | 5.9237 | 5.9237 | 5.9237 | 5.9237
2021-07-21 23:00 | 2.875 | 3.5603 | 3.617 | 3.86 | 3.7628 | 4.0058 | 1.9405 | 2.9395 | 3.4996 | 3.4996 | 3.873 | 3.873 | 2019-09-18 12:00 | 2.0882 | 3.5833 | 6.0564 | 6.0564 | 6.0564 | 6.0564
2021-07-22 | 2.4692 | 3.0577 | 3.1064 | 3.3152 | 3.2317 | 3.4404 | 1.6633 | 2.5196 | 2.9997 | 2.9997 | 3.3197 | 3.3197 | 2019-09-18 13:00 | 2.111 | 3.6225 | 6.1227 | 6.1227 | 6.1227 | 6.1227
2021-07-22 01:00 | 2.2549 | 2.7923 | 2.8368 | 3.0274 | 2.9511 | 3.1417 | 1.4384 | 2.1788 | 2.594 | 2.594 | 2.8708 | 2.8708 | 2019-09-18 14:00 | 2.1034 | 3.6094 | 6.1006 | 6.1006 | 6.1006 | 6.1006
2021-07-22 02:00 | 2.2377 | 2.7711 | 2.8152 | 3.0044 | 2.9287 | 3.1179 | 1.3575 | 2.0563 | 2.4482 | 2.4482 | 2.7094 | 2.7094 | 2019-09-18 15:00 | 2.111 | 3.6225 | 6.1227 | 6.1227 | 6.1227 | 6.1227
2021-07-22 03:00 | 2.212 | 2.7392 | 2.7828 | 2.9698 | 2.895 | 3.082 | 1.2946 | 1.9611 | 2.3348 | 2.3348 | 2.5839 | 2.5839 | 2019-09-18 16:00 | 2.1415 | 3.6748 | 6.2111 | 6.2111 | 6.2111 | 6.2111
2021-07-22 04:00 | 2.3287 | 2.8837 | 2.9297 | 3.1265 | 3.0478 | 3.2446 | 1.3203 | 2.0001 | 2.3812 | 2.3812 | 2.6353 | 2.6353 | 2019-09-18 17:00 | 2.0577 | 3.531 | 5.9679 | 5.9679 | 5.9679 | 5.9679
2021-07-22 05:00 | 2.8236 | 3.4966 | 3.5523 | 3.7909 | 3.6955 | 3.9342 | 1.4961 | 2.2662 | 2.6981 | 2.6981 | 2.986 | 2.986 | 2019-09-18 18:00 | 2.0119 | 3.4525 | 5.8353 | 5.8353 | 5.8353 | 5.8353
2021-07-22 06:00 | 4.2125 | 5.2165 | 5.2996 | 5.6557 | 5.5133 | 5.8694 | 1.8919 | 2.8659 | 3.412 | 3.412 | 3.7761 | 3.7761 | 2019-09-18 19:00 | 2.0805 | 3.5702 | 6.0343 | 6.0343 | 6.0343 | 6.0343
2021-07-22 07:00 | 5.0499 | 6.2535 | 6.3531 | 6.78 | 6.6092 | 7.0361 | 2.3006 | 3.485 | 4.149 | 4.149 | 4.5917 | 4.5917 | 2019-09-18 20:00 | 1.9586 | 3.361 | 5.6806 | 5.6806 | 5.6806 | 5.6806
2021-07-22 08:00 | 5.0699 | 6.2782 | 6.3782 | 6.8068 | 6.6354 | 7.064 | 2.3235 | 3.5196 | 4.1903 | 4.1903 | 4.6374 | 4.6374 | 2019-09-18 21:00 | 1.7452 | 2.9948 | 5.0617 | 5.0617 | 5.0617 | 5.0617
2021-07-22 09:00 | 4.8527 | 6.0093 | 6.105 | 6.5152 | 6.3511 | 6.7613 | 2.0977 | 3.1776 | 3.7831 | 3.7831 | 4.1867 | 4.1867 | 2019-09-18 22:00 | 1.6385 | 2.8117 | 4.7522 | 4.7522 | 4.7522 | 4.7522
2021-07-22 10:00 | 4.5097 | 5.5846 | 5.6735 | 6.0548 | 5.9023 | 6.2835 | 2.0234 | 3.065 | 3.6491 | 3.6491 | 4.0384 | 4.0384 | 2019-09-18 23:00 | 1.5928 | 2.7332 | 4.6196 | 4.6196 | 4.6196 | 4.6196
2021-07-22 11:00 | 4.0782 | 5.0502 | 5.1306 | 5.4754 | 5.3375 | 5.6822 | 1.9977 | 3.0261 | 3.6027 | 3.6027 | 3.9871 | 3.9871 | 2019-09-19 | 1.3794 | 2.3671 | 4.0007 | 4.0007 | 4.0007 | 4.0007
2021-07-22 12:00 | 3.8181 | 4.7281 | 4.8035 | 5.1262 | 4.9971 | 5.3199 | 1.9234 | 2.9135 | 3.4687 | 3.4687 | 3.8388 | 3.8388 | 2019-09-19 01:00 | 1.2422 | 2.1317 | 3.6029 | 3.6029 | 3.6029 | 3.6029
2021-07-22 13:00 | 3.4323 | 4.2504 | 4.3181 | 4.6082 | 4.4922 | 4.7823 | 1.9005 | 2.8789 | 3.4275 | 3.4275 | 3.7932 | 3.7932 | 2019-09-19 02:00 | 1.1889 | 2.0401 | 3.4481 | 3.4481 | 3.4481 | 3.4481
2021-07-22 14:00 | 3.6524 | 4.5229 | 4.5949 | 4.9037 | 4.7802 | 5.0889 | 1.9262 | 2.9178 | 3.4738 | 3.4738 | 3.8445 | 3.8445 | 2019-09-19 03:00 | 1.2346 | 2.1186 | 3.5808 | 3.5808 | 3.5808 | 3.5808
2021-07-22 15:00 | 3.6924 | 4.5724 | 4.6453 | 4.9574 | 4.8325 | 5.1447 | 1.9091 | 2.8919 | 3.4429 | 3.4429 | 3.8103 | 3.8103 | 2019-09-19 04:00 | 1.3718 | 2.354 | 3.9786 | 3.9786 | 3.9786 | 3.9786
2021-07-22 16:00 | 3.9804 | 4.929 | 5.0075 | 5.344 | 5.2094 | 5.5459 | 2.1663 | 3.2815 | 3.9068 | 3.9068 | 4.3236 | 4.3236 | 2019-09-19 05:00 | 1.5166 | 2.6025 | 4.3986 | 4.3986 | 4.3986 | 4.3986
2021-07-22 17:00 | 4.5783 | 5.6695 | 5.7598 | 6.1469 | 5.992 | 6.3791 | 2.5549 | 3.8702 | 4.6077 | 4.6077 | 5.0994 | 5.0994 | 2019-09-19 06:00 | 1.6233 | 2.7855 | 4.708 | 4.708 | 4.708 | 4.708
2021-07-22 18:00 | 4.6669 | 5.7792 | 5.8713 | 6.2658 | 6.108 | 6.5025 | 2.8836 | 4.3681 | 5.2005 | 5.2005 | 5.7554 | 5.7554 | 2019-09-19 07:00 | 2.0501 | 3.5179 | 5.9458 | 5.9458 | 5.9458 | 5.9458
2021-07-22 19:00 | 4.4812 | 5.5492 | 5.6376 | 6.0164 | 5.8649 | 6.2437 | 2.7979 | 4.2382 | 5.0458 | 5.0458 | 5.5842 | 5.5842 | 2019-09-19 08:00 | 2.0805 | 3.5702 | 6.0343 | 6.0343 | 6.0343 | 6.0343
2021-07-22 20:00 | 4.3668 | 5.4076 | 5.4938 | 5.8629 | 5.7153 | 6.0844 | 2.7407 | 4.1516 | 4.9428 | 4.9428 | 5.4702 | 5.4702 | 2019-09-19 09:00 | 2.233 | 3.8318 | 6.4763 | 6.4763 | 6.4763 | 6.4763
2021-07-22 21:00 | 3.769 | 4.6673 | 4.7416 | 5.0602 | 4.9328 | 5.2514 | 2.6092 | 3.9525 | 4.7057 | 4.7057 | 5.2078 | 5.2078 | 2019-09-19 10:00 | 2.1415 | 3.6748 | 6.2111 | 6.2111 | 6.2111 | 6.2111
2021-07-22 22:00 | 3.2798 | 4.0616 | 4.1262 | 4.4035 | 4.2926 | 4.5699 | 2.4492 | 3.7101 | 4.417 | 4.417 | 4.8883 | 4.8883 | 2019-09-19 11:00 | 2.1263 | 3.6487 | 6.1669 | 6.1669 | 6.1669 | 6.1669
2021-07-22 23:00 | 2.8713 | 3.5556 | 3.6122 | 3.855 | 3.7579 | 4.0006 | 1.9097 | 2.8928 | 3.4441 | 3.4441 | 3.8116 | 3.8116 | 2019-09-19 12:00 | 2.1415 | 3.6748 | 6.2111 | 6.2111 | 6.2111 | 6.2111
2021-07-23 | 2.5549 | 3.1639 | 3.2143 | 3.4303 | 3.3439 | 3.5598 | 1.529 | 2.3161 | 2.7574 | 2.7574 | 3.0516 | 3.0516 | 2019-09-19 13:00 | 2.111 | 3.6225 | 6.1227 | 6.1227 | 6.1227 | 6.1227
2021-07-23 01:00 | 2.292 | 2.8383 | 2.8835 | 3.0773 | 2.9998 | 3.1935 | 1.2718 | 1.9265 | 2.2936 | 2.2936 | 2.5383 | 2.5383 | 2019-09-19 14:00 | 2.1263 | 3.6487 | 6.1669 | 6.1669 | 6.1669 | 6.1669
2021-07-23 02:00 | 2.2492 | 2.7852 | 2.8296 | 3.0197 | 2.9437 | 3.1338 | 1.2918 | 1.9568 | 2.3296 | 2.3296 | 2.5782 | 2.5782 | 2019-09-19 15:00 | 2.0729 | 3.5571 | 6.0121 | 6.0121 | 6.0121 | 6.0121
2021-07-23 03:00 | 2.2234 | 2.7534 | 2.7972 | 2.9852 | 2.91 | 3.0979 | 1.2228 | 1.8524 | 2.2053 | 2.2053 | 2.4406 | 2.4406 | 2019-09-19 16:00 | 2.1339 | 3.6618 | 6.189 | 6.189 | 6.189 | 6.189
2021-07-23 04:00 | 2.2465 | 2.7819 | 2.8262 | 3.0161 | 2.9402 | 3.1301 | 1.2546 | 1.9005 | 2.2626 | 2.2626 | 2.5041 | 2.5041 | 2019-09-19 17:00 | 2.1263 | 3.6487 | 6.1669 | 6.1669 | 6.1669 | 6.1669
2021-07-23 05:00 | 2.7921 | 3.4576 | 3.5127 | 3.7487 | 3.6543 | 3.8903 | 1.3868 | 2.1007 | 2.501 | 2.501 | 2.7679 | 2.7679 | 2019-09-19 18:00 | 2.0882 | 3.5833 | 6.0564 | 6.0564 | 6.0564 | 6.0564
2021-07-23 06:00 | 3.781 | 4.6821 | 4.7567 | 5.0763 | 4.9485 | 5.2681 | 1.7262 | 2.6148 | 3.1131 | 3.1131 | 3.4452 | 3.4452 | 2019-09-19 19:00 | 2.0043 | 3.4394 | 5.8132 | 5.8132 | 5.8132 | 5.8132
2021-07-23 07:00 | 4.4469 | 5.5067 | 5.5944 | 5.9703 | 5.82 | 6.1959 | 2.2177 | 3.3594 | 3.9996 | 3.9996 | 4.4263 | 4.4263 | 2019-09-19 20:00 | 1.9738 | 3.3871 | 5.7248 | 5.7248 | 5.7248 | 5.7248
2021-07-23 08:00 | 4.604 | 5.7014 | 5.7922 | 6.1814 | 6.0257 | 6.4149 | 2.2149 | 3.3551 | 3.9944 | 3.9944 | 4.4206 | 4.4206 | 2019-09-19 21:00 | 1.8062 | 3.0994 | 5.2385 | 5.2385 | 5.2385 | 5.2385
2021-07-23 09:00 | 4.6155 | 5.7155 | 5.8066 | 6.1967 | 6.0407 | 6.4308 | 2.1691 | 3.2858 | 3.9119 | 3.9119 | 4.3294 | 4.3294 | 2019-09-19 22:00 | 1.6919 | 2.9032 | 4.907 | 4.907 | 4.907 | 4.907
2021-07-23 10:00 | 4.7098 | 5.8323 | 5.9252 | 6.3234 | 6.1641 | 6.5622 | 2.2291 | 3.3767 | 4.0202 | 4.0202 | 4.4491 | 4.4491 | 2019-09-19 23:00 | 1.5242 | 2.6155 | 4.4207 | 4.4207 | 4.4207 | 4.4207
2021-07-23 11:00 | 4.5155 | 5.5917 | 5.6807 | 6.0624 | 5.9098 | 6.2915 | 2.352 | 3.5629 | 4.2418 | 4.2418 | 4.6944 | 4.6944 | 2019-09-20 | 1.3489 | 2.3148 | 3.9123 | 3.9123 | 3.9123 | 3.9123
2021-07-23 12:00 | 4.504 | 5.5775 | 5.6664 | 6.0471 | 5.8948 | 6.2755 | 2.3035 | 3.4893 | 4.1542 | 4.1542 | 4.5974 | 4.5974 | 2019-09-20 01:00 | 1.2117 | 2.0794 | 3.5144 | 3.5144 | 3.5144 | 3.5144
2021-07-23 13:00 | 4.5926 | 5.6872 | 5.7778 | 6.166 | 6.0107 | 6.399 | 2.3749 | 3.5975 | 4.283 | 4.283 | 4.74 | 4.74 | 2019-09-20 02:00 | 1.2803 | 2.1971 | 3.7134 | 3.7134 | 3.7134 | 3.7134
2021-07-23 14:00 | 4.4126 | 5.4643 | 5.5513 | 5.9243 | 5.7751 | 6.1481 | 2.3778 | 3.6018 | 4.2882 | 4.2882 | 4.7457 | 4.7457 | 2019-09-20 03:00 | 1.2194 | 2.0924 | 3.5366 | 3.5366 | 3.5366 | 3.5366
2021-07-23 15:00 | 4.2554 | 5.2696 | 5.3536 | 5.7133 | 5.5694 | 5.9291 | 2.3035 | 3.4893 | 4.1542 | 4.1542 | 4.5974 | 4.5974 | 2019-09-20 04:00 | 1.2422 | 2.1317 | 3.6029 | 3.6029 | 3.6029 | 3.6029
2021-07-23 16:00 | 4.1725 | 5.167 | 5.2493 | 5.602 | 5.4609 | 5.8136 | 2.4121 | 3.6538 | 4.35 | 4.35 | 4.8142 | 4.8142 | 2019-09-20 05:00 | 1.5013 | 2.5763 | 4.3544 | 4.3544 | 4.3544 | 4.3544
2021-07-23 17:00 | 4.5497 | 5.6341 | 5.7239 | 6.1085 | 5.9546 | 6.3392 | 2.7264 | 4.13 | 4.917 | 4.917 | 5.4416 | 5.4416 | 2019-09-20 06:00 | 1.6538 | 2.8379 | 4.7965 | 4.7965 | 4.7965 | 4.7965
2021-07-23 18:00 | 4.4411 | 5.4997 | 5.5873 | 5.9627 | 5.8125 | 6.1879 | 2.875 | 4.3551 | 5.185 | 5.185 | 5.7382 | 5.7382 | 2019-09-20 07:00 | 1.9662 | 3.374 | 5.7027 | 5.7027 | 5.7027 | 5.7027
2021-07-23 19:00 | 4.244 | 5.2555 | 5.3392 | 5.6979 | 5.5544 | 5.9132 | 2.9379 | 4.4504 | 5.2984 | 5.2984 | 5.8637 | 5.8637 | 2019-09-20 08:00 | 2.2787 | 3.9102 | 6.6089 | 6.6089 | 6.6089 | 6.6089
2021-07-23 20:00 | 3.761 | 4.6574 | 4.7315 | 5.0495 | 4.9223 | 5.2402 | 2.7264 | 4.13 | 4.917 | 4.917 | 5.4416 | 5.4416 | 2019-09-20 09:00 | 2.2406 | 3.8448 | 6.4984 | 6.4984 | 6.4984 | 6.4984
2021-07-23 21:00 | 3.5066 | 4.3424 | 4.4116 | 4.708 | 4.5894 | 4.8858 | 2.7036 | 4.0954 | 4.8757 | 4.8757 | 5.396 | 5.396 | 2019-09-20 10:00 | 2.1339 | 3.6618 | 6.189 | 6.189 | 6.189 | 6.189
2021-07-23 22:00 | 3.0151 | 3.7337 | 3.7931 | 4.048 | 3.9461 | 4.2009 | 2.3492 | 3.5585 | 4.2366 | 4.2366 | 4.6887 | 4.6887 | 2019-09-20 11:00 | 2.3015 | 3.9495 | 6.6753 | 6.6753 | 6.6753 | 6.6753
2021-07-23 23:00 | 2.7009 | 3.3447 | 3.398 | 3.6263 | 3.535 | 3.7633 | 1.9891 | 3.0131 | 3.5872 | 3.5872 | 3.97 | 3.97 | 2019-09-20 12:00 | 2.2482 | 3.8579 | 6.5205 | 6.5205 | 6.5205 | 6.5205
2021-07-24 | 2.392 | 2.9622 | 3.0093 | 3.2116 | 3.1307 | 3.3329 | 1.5947 | 2.4157 | 2.876 | 2.876 | 3.1828 | 3.1828 | 2019-09-20 13:00 | 2.332 | 4.0018 | 6.7637 | 6.7637 | 6.7637 | 6.7637
2021-07-24 01:00 | 2.1131 | 2.6168 | 2.6584 | 2.8371 | 2.7656 | 2.9442 | 1.378 | 2.0875 | 2.4852 | 2.4852 | 2.7504 | 2.7504 | 2019-09-20 14:00 | 2.1796 | 3.7402 | 6.3216 | 6.3216 | 6.3216 | 6.3216
2021-07-24 02:00 | 2.0405 | 2.5269 | 2.5671 | 2.7396 | 2.6706 | 2.8431 | 1.266 | 1.9178 | 2.2832 | 2.2832 | 2.5269 | 2.5269 | 2019-09-20 15:00 | 2.2406 | 3.8448 | 6.4984 | 6.4984 | 6.4984 | 6.4984
2021-07-24 03:00 | 2.0062 | 2.4844 | 2.524 | 2.6936 | 2.6257 | 2.7953 | 1.1803 | 1.7879 | 2.1286 | 2.1286 | 2.3558 | 2.3558 | 2019-09-20 16:00 | 2.1644 | 3.7141 | 6.2774 | 6.2774 | 6.2774 | 6.2774
2021-07-24 04:00 | 2.0491 | 2.5375 | 2.5779 | 2.7511 | 2.6818 | 2.855 | 1.1774 | 1.7836 | 2.1235 | 2.1235 | 2.3501 | 2.3501 | 2019-09-20 17:00 | 2.0805 | 3.5702 | 6.0343 | 6.0343 | 6.0343 | 6.0343
2021-07-24 05:00 | 2.1691 | 2.6861 | 2.7289 | 2.9123 | 2.8389 | 3.0223 | 1.2117 | 1.8354 | 2.1852 | 2.1852 | 2.4184 | 2.4184 | 2019-09-20 18:00 | 2.0348 | 3.4917 | 5.9016 | 5.9016 | 5.9016 | 5.9016
2021-07-24 06:00 | 2.5578 | 3.1674 | 3.2179 | 3.4341 | 3.3476 | 3.5638 | 1.4003 | 2.1212 | 2.5254 | 2.5254 | 2.7949 | 2.7949 | 2019-09-20 19:00 | 1.9815 | 3.4002 | 5.7469 | 5.7469 | 5.7469 | 5.7469
2021-07-24 07:00 | 2.9208 | 3.6169 | 3.6745 | 3.9214 | 3.8226 | 4.0695 | 1.8176 | 2.7533 | 3.278 | 3.278 | 3.6278 | 3.6278 | 2019-09-20 20:00 | 1.7452 | 2.9948 | 5.0617 | 5.0617 | 5.0617 | 5.0617
2021-07-24 08:00 | 3.1894 | 3.9496 | 4.0125 | 4.2821 | 4.1742 | 4.4438 | 1.8919 | 2.8659 | 3.412 | 3.412 | 3.7761 | 3.7761 | 2019-09-20 21:00 | 1.7071 | 2.9294 | 4.9512 | 4.9512 | 4.9512 | 4.9512
2021-07-24 09:00 | 3.2208 | 3.9885 | 4.052 | 4.3243 | 4.2154 | 4.4876 | 2.0548 | 3.1126 | 3.7058 | 3.7058 | 4.1012 | 4.1012 | 2019-09-20 22:00 | 1.5547 | 2.6678 | 4.5091 | 4.5091 | 4.5091 | 4.5091
2021-07-24 10:00 | 3.498 | 4.3318 | 4.4008 | 4.6965 | 4.5782 | 4.8739 | 2.3063 | 3.4936 | 4.1593 | 4.1593 | 4.6031 | 4.6031 | 2019-09-20 23:00 | 1.4251 | 2.4455 | 4.1333 | 4.1333 | 4.1333 | 4.1333
2021-07-24 11:00 | 3.5981 | 4.4556 | 4.5266 | 4.8308 | 4.7091 | 5.0133 | 2.4121 | 3.6538 | 4.35 | 4.35 | 4.8142 | 4.8142 | 2019-09-21 | 1.3642 | 2.3409 | 3.9565 | 3.9565 | 3.9565 | 3.9565
2021-07-24 12:00 | 3.3552 | 4.1548 | 4.221 | 4.5046 | 4.3912 | 4.6748 | 2.4578 | 3.7231 | 4.4325 | 4.4325 | 4.9055 | 4.9055 | 2019-09-21 01:00 | 1.3032 | 2.2363 | 3.7797 | 3.7797 | 3.7797 | 3.7797
2021-07-24 13:00 | 3.2694 | 4.0486 | 4.1131 | 4.3895 | 4.279 | 4.5553 | 2.4378 | 3.6928 | 4.3964 | 4.3964 | 4.8655 | 4.8655 | 2019-09-21 02:00 | 1.3184 | 2.2624 | 3.8239 | 3.8239 | 3.8239 | 3.8239
2021-07-24 14:00 | 3.1722 | 3.9283 | 3.9909 | 4.2591 | 4.1518 | 4.4199 | 2.2263 | 3.3724 | 4.015 | 4.015 | 4.4434 | 4.4434 | 2019-09-21 03:00 | 1.2879 | 2.2101 | 3.7355 | 3.7355 | 3.7355 | 3.7355
2021-07-24 15:00 | 3.1637 | 3.9177 | 3.9801 | 4.2475 | 4.1406 | 4.408 | 2.3263 | 3.5239 | 4.1954 | 4.1954 | 4.6431 | 4.6431 | 2019-09-21 04:00 | 1.3184 | 2.2624 | 3.8239 | 3.8239 | 3.8239 | 3.8239
2021-07-24 16:00 | 3.5466 | 4.3919 | 4.4619 | 4.7617 | 4.6418 | 4.9416 | 2.5717 | 3.8956 | 4.6379 | 4.6379 | 5.1328 | 5.1328 | 2019-09-21 05:00 | 1.4251 | 2.4455 | 4.1333 | 4.1333 | 4.1333 | 4.1333
2021-07-24 17:00 | 3.9239 | 4.8591 | 4.9365 | 5.2682 | 5.1355 | 5.4672 | 2.715 | 4.1127 | 4.8964 | 4.8964 | 5.4188 | 5.4188 | 2019-09-21 06:00 | 1.4861 | 2.5501 | 4.3102 | 4.3102 | 4.3102 | 4.3102
2021-07-24 18:00 | 3.8465 | 4.7633 | 4.8392 | 5.1643 | 5.0342 | 5.3594 | 2.775 | 4.2036 | 5.0046 | 5.0046 | 5.5386 | 5.5386 | 2019-09-21 07:00 | 1.6842 | 2.8902 | 4.8849 | 4.8849 | 4.8849 | 4.8849
2021-07-24 19:00 | 3.4638 | 4.2893 | 4.3576 | 4.6504 | 4.5333 | 4.8261 | 2.7007 | 4.091 | 4.8706 | 4.8706 | 5.3903 | 5.3903 | 2019-09-21 08:00 | 1.7986 | 3.0863 | 5.2164 | 5.2164 | 5.2164 | 5.2164
2021-07-24 20:00 | 3.3037 | 4.0911 | 4.1563 | 4.4356 | 4.3238 | 4.6031 | 2.675 | 4.0521 | 4.8242 | 4.8242 | 5.339 | 5.339 | 2019-09-21 09:00 | 1.8824 | 3.2302 | 5.4596 | 5.4596 | 5.4596 | 5.4596
2021-07-24 21:00 | 3.1465 | 3.8965 | 3.9585 | 4.2245 | 4.1181 | 4.3841 | 2.4949 | 3.7793 | 4.4995 | 4.4995 | 4.9796 | 4.9796 | 2019-09-21 10:00 | 2.0805 | 3.5702 | 6.0343 | 6.0343 | 6.0343 | 6.0343
2021-07-24 22:00 | 2.875 | 3.5603 | 3.617 | 3.86 | 3.7628 | 4.0058 | 2.2406 | 3.394 | 4.0408 | 4.0408 | 4.472 | 4.472 | 2019-09-21 11:00 | 2.111 | 3.6225 | 6.1227 | 6.1227 | 6.1227 | 6.1227
2021-07-24 23:00 | 2.6635 | 3.2984 | 3.3509 | 3.5761 | 3.486 | 3.7112 | 1.9091 | 2.8919 | 3.4429 | 3.4429 | 3.8103 | 3.8103 | 2019-09-21 12:00 | 2.0805 | 3.5702 | 6.0343 | 6.0343 | 6.0343 | 6.0343
2021-07-25 | 2.2929 | 2.8395 | 2.8847 | 3.0785 | 3.001 | 3.1948 | 1.6919 | 2.5628 | 3.0512 | 3.0512 | 3.3768 | 3.3768 | 2019-09-21 13:00 | 2.0348 | 3.4917 | 5.9016 | 5.9016 | 5.9016 | 5.9016
2021-07-25 01:00 | 2.1748 | 2.6932 | 2.7361 | 2.9199 | 2.8464 | 3.0303 | 1.4175 | 2.1472 | 2.5564 | 2.5564 | 2.8292 | 2.8292 | 2019-09-21 14:00 | 2.0805 | 3.5702 | 6.0343 | 6.0343 | 6.0343 | 6.0343
2021-07-25 02:00 | 2.0177 | 2.4986 | 2.5383 | 2.7089 | 2.6407 | 2.8112 | 1.3203 | 2.0001 | 2.3812 | 2.3812 | 2.6353 | 2.6353 | 2019-09-21 15:00 | 2.0577 | 3.531 | 5.9679 | 5.9679 | 5.9679 | 5.9679
2021-07-25 03:00 | 2.072 | 2.5658 | 2.6067 | 2.7818 | 2.7118 | 2.8869 | 1.2632 | 1.9135 | 2.2781 | 2.2781 | 2.5212 | 2.5212 | 2019-09-21 16:00 | 2.0043 | 3.4394 | 5.8132 | 5.8132 | 5.8132 | 5.8132
2021-07-25 04:00 | 2.0863 | 2.5835 | 2.6246 | 2.801 | 2.7305 | 2.9068 | 1.2432 | 1.8832 | 2.242 | 2.242 | 2.4812 | 2.4812 | 2019-09-21 17:00 | 1.9891 | 3.4133 | 5.769 | 5.769 | 5.769 | 5.769
2021-07-25 05:00 | 2.2863 | 2.8312 | 2.8763 | 3.0696 | 2.9923 | 3.1855 | 1.3089 | 1.9827 | 2.3606 | 2.3606 | 2.6124 | 2.6124 | 2019-09-21 18:00 | 1.951 | 3.3479 | 5.6585 | 5.6585 | 5.6585 | 5.6585
2021-07-25 06:00 | 2.4892 | 3.0825 | 3.1316 | 3.342 | 3.2578 | 3.4683 | 1.4632 | 2.2165 | 2.6389 | 2.6389 | 2.9205 | 2.9205 | 2019-09-21 19:00 | 1.8976 | 3.2563 | 5.5038 | 5.5038 | 5.5038 | 5.5038
2021-07-25 07:00 | 2.8179 | 3.4895 | 3.5451 | 3.7833 | 3.688 | 3.9262 | 1.6461 | 2.4936 | 2.9687 | 2.9687 | 3.2855 | 3.2855 | 2019-09-21 20:00 | 1.8367 | 3.1517 | 5.3269 | 5.3269 | 5.3269 | 5.3269
2021-07-25 08:00 | 3.1722 | 3.9283 | 3.9909 | 4.2591 | 4.1518 | 4.4199 | 2.1005 | 3.1819 | 3.7882 | 3.7882 | 4.1925 | 4.1925 | 2019-09-21 21:00 | 1.7223 | 2.9556 | 4.9954 | 4.9954 | 4.9954 | 4.9954
2021-07-25 09:00 | 3.3924 | 4.201 | 4.2679 | 4.5546 | 4.4399 | 4.7267 | 2.1863 | 3.3118 | 3.9429 | 3.9429 | 4.3636 | 4.3636 | 2019-09-21 22:00 | 1.5699 | 2.694 | 4.5533 | 4.5533 | 4.5533 | 4.5533
2021-07-25 10:00 | 3.4752 | 4.3035 | 4.372 | 4.6658 | 4.5483 | 4.842 | 2.5035 | 3.7923 | 4.515 | 4.515 | 4.9967 | 4.9967 | 2019-09-21 23:00 | 1.4861 | 2.5501 | 4.3102 | 4.3102 | 4.3102 | 4.3102
2021-07-25 11:00 | 3.3637 | 4.1654 | 4.2318 | 4.5161 | 4.4024 | 4.6867 | 2.5664 | 3.8876 | 4.6284 | 4.6284 | 5.1222 | 5.1222 | 2019-09-22 | 1.3794 | 2.3671 | 4.0007 | 4.0007 | 4.0007 | 4.0007
2021-07-25 12:00 | 3.3066 | 4.0947 | 4.1599 | 4.4394 | 4.3276 | 4.6071 | 2.4463 | 3.7057 | 4.4119 | 4.4119 | 4.8826 | 4.8826 | 2019-09-22 01:00 | 1.3565 | 2.3278 | 3.9344 | 3.9344 | 3.9344 | 3.9344
2021-07-25 13:00 | 3.1494 | 3.9 | 3.9621 | 4.2284 | 4.1219 | 4.3881 | 2.4549 | 3.7187 | 4.4273 | 4.4273 | 4.8998 | 4.8998 | 2019-09-22 02:00 | 1.2575 | 2.1578 | 3.6471 | 3.6471 | 3.6471 | 3.6471
2021-07-25 14:00 | 3.2666 | 4.0451 | 4.1095 | 4.3857 | 4.2752 | 4.5514 | 2.5149 | 3.8096 | 4.5356 | 4.5356 | 5.0195 | 5.0195 | 2019-09-22 03:00 | 1.2879 | 2.2101 | 3.7355 | 3.7355 | 3.7355 | 3.7355
2021-07-25 15:00 | 3.3466 | 4.1442 | 4.2102 | 4.4931 | 4.38 | 4.6628 | 2.5149 | 3.8096 | 4.5356 | 4.5356 | 5.0195 | 5.0195 | 2019-09-22 04:00 | 1.2346 | 2.1186 | 3.5808 | 3.5808 | 3.5808 | 3.5808
2021-07-25 16:00 | 3.5441 | 4.3888 | 4.4587 | 4.7583 | 4.6385 | 4.9381 | 2.7093 | 4.104 | 4.8861 | 4.8861 | 5.4074 | 5.4074 | 2019-09-22 05:00 | 1.4099 | 2.4194 | 4.0891 | 4.0891 | 4.0891 | 4.0891
2021-07-25 17:00 | 3.9696 | 4.9157 | 4.994 | 5.3296 | 5.1953 | 5.5309 | 2.9383 | 4.4509 | 5.299 | 5.299 | 5.8645 | 5.8645 | 2019-09-22 06:00 | 1.3794 | 2.3671 | 4.0007 | 4.0007 | 4.0007 | 4.0007
2021-07-25 18:00 | 4.0668 | 5.036 | 5.1163 | 5.46 | 5.3225 | 5.6663 | 3.1179 | 4.7231 | 5.6231 | 5.6231 | 6.2231 | 6.2231 | 2019-09-22 07:00 | 1.6233 | 2.7855 | 4.708 | 4.708 | 4.708 | 4.708
2021-07-25 19:00 | 3.9153 | 4.8485 | 4.9257 | 5.2567 | 5.1243 | 5.4553 | 3.0408 | 4.6062 | 5.4839 | 5.4839 | 6.0691 | 6.0691 | 2019-09-22 08:00 | 1.7833 | 3.0602 | 5.1722 | 5.1722 | 5.1722 | 5.1722
2021-07-25 20:00 | 3.6295 | 4.4946 | 4.5662 | 4.873 | 4.7502 | 5.0571 | 2.8722 | 4.3508 | 5.1798 | 5.1798 | 5.7325 | 5.7325 | 2019-09-22 09:00 | 1.8443 | 3.1648 | 5.349 | 5.349 | 5.349 | 5.349
2021-07-25 21:00 | 3.464 | 4.2896 | 4.358 | 4.6508 | 4.5336 | 4.8265 | 2.6721 | 4.0477 | 4.8191 | 4.8191 | 5.3333 | 5.3333 | 2019-09-22 10:00 | 1.8367 | 3.1517 | 5.3269 | 5.3269 | 5.3269 | 5.3269
2021-07-25 22:00 | 3.0408 | 3.7655 | 3.8255 | 4.0826 | 3.9797 | 4.2368 | 2.272 | 3.4417 | 4.0975 | 4.0975 | 4.5347 | 4.5347 | 2019-09-22 11:00 | 1.8519 | 3.1779 | 5.3711 | 5.3711 | 5.3711 | 5.3711
2021-07-25 23:00 | 2.7864 | 3.4506 | 3.5055 | 3.7411 | 3.6468 | 3.8824 | 2.0005 | 3.0304 | 3.6078 | 3.6078 | 3.9928 | 3.9928 | 2019-09-22 12:00 | 1.7833 | 3.0602 | 5.1722 | 5.1722 | 5.1722 | 5.1722
2021-07-26 | 2.2759 | 2.8183 | 2.8632 | 3.0556 | 2.9787 | 3.1711 | 1.5724 | 2.3819 | 2.8358 | 2.8358 | 3.1384 | 3.1384 | 2019-09-22 13:00 | 1.8671 | 3.204 | 5.4154 | 5.4154 | 5.4154 | 5.4154
2021-07-26 01:00 | 2.0006 | 2.4774 | 2.5169 | 2.686 | 2.6184 | 2.7875 | 1.4604 | 2.2122 | 2.6337 | 2.6337 | 2.9148 | 2.9148 | 2019-09-22 14:00 | 1.8595 | 3.191 | 5.3932 | 5.3932 | 5.3932 | 5.3932
2021-07-26 02:00 | 2.0005 | 2.4773 | 2.5168 | 2.6859 | 2.6182 | 2.7874 | 1.2689 | 1.9221 | 2.2884 | 2.2884 | 2.5326 | 2.5326 | 2019-09-22 15:00 | 1.8671 | 3.204 | 5.4154 | 5.4154 | 5.4154 | 5.4154
2021-07-26 03:00 | 1.9691 | 2.4384 | 2.4772 | 2.6437 | 2.5771 | 2.7436 | 1.2517 | 1.8962 | 2.2575 | 2.2575 | 2.4984 | 2.4984 | 2019-09-22 16:00 | 1.8367 | 3.1517 | 5.3269 | 5.3269 | 5.3269 | 5.3269
2021-07-26 04:00 | 2.0541 | 2.5437 | 2.5842 | 2.7579 | 2.6884 | 2.8621 | 1.2575 | 1.9048 | 2.2678 | 2.2678 | 2.5098 | 2.5098 | 2019-09-22 17:00 | 1.7681 | 3.034 | 5.128 | 5.128 | 5.128 | 5.128
2021-07-26 05:00 | 2.5464 | 3.1533 | 3.2035 | 3.4188 | 3.3327 | 3.5479 | 1.3603 | 2.0606 | 2.4532 | 2.4532 | 2.715 | 2.715 | 2019-09-22 18:00 | 1.8519 | 3.1779 | 5.3711 | 5.3711 | 5.3711 | 5.3711
2021-07-26 06:00 | 3.7695 | 4.668 | 4.7423 | 5.061 | 4.9335 | 5.2522 | 1.7428 | 2.64 | 3.1431 | 3.1431 | 3.4785 | 3.4785 | 2019-09-22 19:00 | 1.7376 | 2.9817 | 5.0396 | 5.0396 | 5.0396 | 5.0396
2021-07-26 07:00 | 4.3611 | 5.4006 | 5.4866 | 5.8552 | 5.7078 | 6.0764 | 2.172 | 3.2901 | 3.9171 | 3.9171 | 4.3351 | 4.3351 | 2019-09-22 20:00 | 1.7147 | 2.9425 | 4.9733 | 4.9733 | 4.9733 | 4.9733
2021-07-26 08:00 | 4.4354 | 5.4926 | 5.5801 | 5.955 | 5.805 | 6.18 | 2.1606 | 3.2728 | 3.8965 | 3.8965 | 4.3122 | 4.3122 | 2019-09-22 21:00 | 1.6919 | 2.9032 | 4.907 | 4.907 | 4.907 | 4.907
2021-07-26 09:00 | 4.3068 | 5.3333 | 5.4183 | 5.7823 | 5.6367 | 6.0008 | 2.0605 | 3.1213 | 3.7161 | 3.7161 | 4.1126 | 4.1126 | 2019-09-22 22:00 | 1.5699 | 2.694 | 4.5533 | 4.5533 | 4.5533 | 4.5533
2021-07-26 10:00 | 3.8553 | 4.7742 | 4.8502 | 5.1761 | 5.0457 | 5.3716 | 1.9262 | 2.9178 | 3.4738 | 3.4738 | 3.8445 | 3.8445 | 2019-09-22 23:00 | 1.4099 | 2.4194 | 4.0891 | 4.0891 | 4.0891 | 4.0891
2021-07-26 11:00 | 3.7724 | 4.6715 | 4.7459 | 5.0648 | 4.9373 | 5.2562 | 2.032 | 3.078 | 3.6645 | 3.6645 | 4.0556 | 4.0556 | 2019-09-23 | 1.3489 | 2.3148 | 3.9123 | 3.9123 | 3.9123 | 3.9123
2021-07-26 12:00 | 3.7267 | 4.6149 | 4.6884 | 5.0034 | 4.8774 | 5.1924 | 1.9719 | 2.9871 | 3.5563 | 3.5563 | 3.9358 | 3.9358 | 2019-09-23 01:00 | 1.1965 | 2.0532 | 3.4702 | 3.4702 | 3.4702 | 3.4702
2021-07-26 13:00 | 3.6781 | 4.5547 | 4.6273 | 4.9382 | 4.8138 | 5.1248 | 1.9948 | 3.0217 | 3.5975 | 3.5975 | 3.9814 | 3.9814 | 2019-09-23 02:00 | 1.1965 | 2.0532 | 3.4702 | 3.4702 | 3.4702 | 3.4702
2021-07-26 14:00 | 3.5066 | 4.3424 | 4.4116 | 4.708 | 4.5894 | 4.8858 | 2.0005 | 3.0304 | 3.6078 | 3.6078 | 3.9928 | 3.9928 | 2019-09-23 03:00 | 1.227 | 2.1055 | 3.5587 | 3.5587 | 3.5587 | 3.5587
2021-07-26 15:00 | 3.5866 | 4.4415 | 4.5122 | 4.8154 | 4.6941 | 4.9973 | 1.9834 | 3.0044 | 3.5769 | 3.5769 | 3.9586 | 3.9586 | 2019-09-23 04:00 | 1.2651 | 2.1709 | 3.6692 | 3.6692 | 3.6692 | 3.6692
2021-07-26 16:00 | 3.9925 | 4.944 | 5.0228 | 5.3603 | 5.2253 | 5.5628 | 2.2903 | 3.4693 | 4.1304 | 4.1304 | 4.5711 | 4.5711 | 2019-09-23 05:00 | 1.4556 | 2.4978 | 4.2218 | 4.2218 | 4.2218 | 4.2218
2021-07-26 17:00 | 4.2154 | 5.2201 | 5.3032 | 5.6596 | 5.517 | 5.8734 | 2.615 | 3.9612 | 4.716 | 4.716 | 5.2192 | 5.2192 | 2019-09-23 06:00 | 1.6538 | 2.8379 | 4.7965 | 4.7965 | 4.7965 | 4.7965
2021-07-26 18:00 | 4.2354 | 5.2448 | 5.3284 | 5.6864 | 5.5432 | 5.9012 | 2.7236 | 4.1257 | 4.9118 | 4.9118 | 5.4359 | 5.4359 | 2019-09-23 07:00 | 1.9205 | 3.2956 | 5.5701 | 5.5701 | 5.5701 | 5.5701
2021-07-26 19:00 | 4.1096 | 5.0891 | 5.1702 | 5.5176 | 5.3786 | 5.726 | 2.6835 | 4.0651 | 4.8397 | 4.8397 | 5.3561 | 5.3561 | 2019-09-23 08:00 | 2.1491 | 3.6879 | 6.2332 | 6.2332 | 6.2332 | 6.2332
2021-07-26 20:00 | 3.7181 | 4.6043 | 4.6776 | 4.9919 | 4.8662 | 5.1805 | 2.655 | 4.0218 | 4.7881 | 4.7881 | 5.299 | 5.299 | 2019-09-23 09:00 | 2.1872 | 3.7533 | 6.3437 | 6.3437 | 6.3437 | 6.3437
2021-07-26 21:00 | 3.331 | 4.1249 | 4.1906 | 4.4722 | 4.3596 | 4.6412 | 2.4692 | 3.7404 | 4.4531 | 4.4531 | 4.9283 | 4.9283 | 2019-09-23 10:00 | 2.1415 | 3.6748 | 6.2111 | 6.2111 | 6.2111 | 6.2111
2021-07-26 22:00 | 2.7979 | 3.4647 | 3.5199 | 3.7564 | 3.6618 | 3.8983 | 2.2063 | 3.3421 | 3.9789 | 3.9789 | 4.4035 | 4.4035 | 2019-09-23 11:00 | 2.172 | 3.7271 | 6.2995 | 6.2995 | 6.2995 | 6.2995
2021-07-26 23:00 | 2.5206 | 3.1214 | 3.1711 | 3.3842 | 3.299 | 3.5121 | 1.7233 | 2.6105 | 3.1079 | 3.1079 | 3.4395 | 3.4395 | 2019-09-23 12:00 | 2.1872 | 3.7533 | 6.3437 | 6.3437 | 6.3437 | 6.3437
2021-07-27 | 2.1402 | 2.6503 | 2.6925 | 2.8734 | 2.801 | 2.982 | 1.4347 | 2.1732 | 2.5873 | 2.5873 | 2.8634 | 2.8634 | 2019-09-23 13:00 | 2.1491 | 3.6879 | 6.2332 | 6.2332 | 6.2332 | 6.2332
2021-07-27 01:00 | 1.9348 | 2.3959 | 2.4341 | 2.5976 | 2.5322 | 2.6958 | 1.2178 | 1.8447 | 2.1962 | 2.1962 | 2.4305 | 2.4305 | 2019-09-23 14:00 | 2.1872 | 3.7533 | 6.3437 | 6.3437 | 6.3437 | 6.3437
2021-07-27 02:00 | 1.8976 | 2.3499 | 2.3873 | 2.5478 | 2.4836 | 2.644 | 1.1851 | 1.7952 | 2.1373 | 2.1373 | 2.3653 | 2.3653 | 2019-09-23 15:00 | 2.0882 | 3.5833 | 6.0564 | 6.0564 | 6.0564 | 6.0564
2021-07-27 03:00 | 1.8519 | 2.2933 | 2.3298 | 2.4864 | 2.4237 | 2.5803 | 1.1003 | 1.6667 | 1.9843 | 1.9843 | 2.196 | 2.196 | 2019-09-23 16:00 | 2.0577 | 3.531 | 5.9679 | 5.9679 | 5.9679 | 5.9679
2021-07-27 04:00 | 1.9318 | 2.3923 | 2.4304 | 2.5937 | 2.5283 | 2.6916 | 1.1689 | 1.7706 | 2.108 | 2.108 | 2.3329 | 2.3329 | 2019-09-23 17:00 | 2.0119 | 3.4525 | 5.8353 | 5.8353 | 5.8353 | 5.8353
2021-07-27 05:00 | 2.4378 | 3.0188 | 3.0669 | 3.2729 | 3.1905 | 3.3966 | 1.2428 | 1.8826 | 2.2413 | 2.2413 | 2.4804 | 2.4804 | 2019-09-23 18:00 | 2.0729 | 3.5571 | 6.0121 | 6.0121 | 6.0121 | 6.0121
2021-07-27 06:00 | 3.6183 | 4.4807 | 4.5521 | 4.858 | 4.7356 | 5.0415 | 1.6776 | 2.5412 | 3.0254 | 3.0254 | 3.3483 | 3.3483 | 2019-09-23 19:00 | 2.0119 | 3.4525 | 5.8353 | 5.8353 | 5.8353 | 5.8353
2021-07-27 07:00 | 4.0496 | 5.0148 | 5.0947 | 5.437 | 5.3001 | 5.6424 | 2.0205 | 3.0607 | 3.6439 | 3.6439 | 4.0327 | 4.0327 | 2019-09-23 20:00 | 1.951 | 3.3479 | 5.6585 | 5.6585 | 5.6585 | 5.6585
2021-07-27 08:00 | 4.0496 | 5.0148 | 5.0947 | 5.437 | 5.3001 | 5.6424 | 2.0805 | 3.1516 | 3.7522 | 3.7522 | 4.1525 | 4.1525 | 2019-09-23 21:00 | 1.8519 | 3.1779 | 5.3711 | 5.3711 | 5.3711 | 5.3711
2021-07-27 09:00 | 3.7867 | 4.6892 | 4.7639 | 5.084 | 4.956 | 5.2761 | 1.8319 | 2.775 | 3.3038 | 3.3038 | 3.6563 | 3.6563 | 2019-09-23 22:00 | 1.6919 | 2.9032 | 4.907 | 4.907 | 4.907 | 4.907
2021-07-27 10:00 | 3.6209 | 4.484 | 4.5554 | 4.8615 | 4.739 | 5.0451 | 1.7947 | 2.7187 | 3.2368 | 3.2368 | 3.5821 | 3.5821 | 2019-09-23 23:00 | 1.4709 | 2.524 | 4.266 | 4.266 | 4.266 | 4.266
2021-07-27 11:00 | 3.1465 | 3.8965 | 3.9585 | 4.2245 | 4.1181 | 4.3841 | 1.8005 | 2.7274 | 3.2471 | 3.2471 | 3.5935 | 3.5935 | 2019-09-24 | 1.3642 | 2.3409 | 3.9565 | 3.9565 | 3.9565 | 3.9565
2021-07-27 12:00 | 2.9893 | 3.7018 | 3.7608 | 4.0135 | 3.9124 | 4.1651 | 1.6747 | 2.5369 | 3.0203 | 3.0203 | 3.3426 | 3.3426 | 2019-09-24 01:00 | 1.2879 | 2.2101 | 3.7355 | 3.7355 | 3.7355 | 3.7355
2021-07-27 13:00 | 2.8436 | 3.5213 | 3.5774 | 3.8178 | 3.7216 | 3.962 | 1.7462 | 2.6451 | 3.1491 | 3.1491 | 3.4852 | 3.4852 | 2019-09-24 02:00 | 1.2498 | 2.1447 | 3.625 | 3.625 | 3.625 | 3.625
2021-07-27 14:00 | 2.895 | 3.585 | 3.6421 | 3.8869 | 3.789 | 4.0337 | 1.7404 | 2.6364 | 3.1388 | 3.1388 | 3.4737 | 3.4737 | 2019-09-24 03:00 | 1.2422 | 2.1317 | 3.6029 | 3.6029 | 3.6029 | 3.6029
2021-07-27 15:00 | 2.8522 | 3.532 | 3.5882 | 3.8293 | 3.7329 | 3.974 | 1.6804 | 2.5455 | 3.0306 | 3.0306 | 3.354 | 3.354 | 2019-09-24 04:00 | 1.2651 | 2.1709 | 3.6692 | 3.6692 | 3.6692 | 3.6692
2021-07-27 16:00 | 3.1694 | 3.9248 | 3.9873 | 4.2552 | 4.148 | 4.416 | 1.9691 | 2.9828 | 3.5512 | 3.5512 | 3.9301 | 3.9301 | 2019-09-24 05:00 | 1.5471 | 2.6548 | 4.487 | 4.487 | 4.487 | 4.487
2021-07-27 17:00 | 3.5924 | 4.4486 | 4.5194 | 4.8231 | 4.7016 | 5.0053 | 2.332 | 3.5326 | 4.2057 | 4.2057 | 4.6545 | 4.6545 | 2019-09-24 06:00 | 1.7223 | 2.9556 | 4.9954 | 4.9954 | 4.9954 | 4.9954
2021-07-27 18:00 | 3.901 | 4.8308 | 4.9077 | 5.2375 | 5.1056 | 5.4353 | 2.4892 | 3.7707 | 4.4892 | 4.4892 | 4.9682 | 4.9682 | 2019-09-24 07:00 | 1.9281 | 3.3087 | 5.5922 | 5.5922 | 5.5922 | 5.5922
2021-07-27 19:00 | 3.8324 | 4.7458 | 4.8214 | 5.1454 | 5.0158 | 5.3398 | 2.5292 | 3.8313 | 4.5613 | 4.5613 | 5.0481 | 5.0481 | 2019-09-24 08:00 | 2.1949 | 3.7664 | 6.3658 | 6.3658 | 6.3658 | 6.3658
2021-07-27 20:00 | 3.5724 | 4.4238 | 4.4942 | 4.7962 | 4.6754 | 4.9774 | 2.4092 | 3.6495 | 4.3449 | 4.3449 | 4.8085 | 4.8085 | 2019-09-24 09:00 | 2.1644 | 3.7141 | 6.2774 | 6.2774 | 6.2774 | 6.2774
2021-07-27 21:00 | 3.3325 | 4.1268 | 4.1925 | 4.4742 | 4.3615 | 4.6432 | 2.3978 | 3.6321 | 4.3243 | 4.3243 | 4.7857 | 4.7857 | 2019-09-24 10:00 | 2.2025 | 3.7795 | 6.3879 | 6.3879 | 6.3879 | 6.3879
2021-07-27 22:00 | 2.795 | 3.4612 | 3.5163 | 3.7526 | 3.6581 | 3.8943 | 2.1377 | 3.2382 | 3.8552 | 3.8552 | 4.2666 | 4.2666 | 2019-09-24 11:00 | 2.1796 | 3.7402 | 6.3216 | 6.3216 | 6.3216 | 6.3216
2021-07-27 23:00 | 2.4835 | 3.0754 | 3.1244 | 3.3343 | 3.2504 | 3.4603 | 1.6547 | 2.5066 | 2.9842 | 2.9842 | 3.3026 | 3.3026 | 2019-09-24 12:00 | 2.1567 | 3.701 | 6.2553 | 6.2553 | 6.2553 | 6.2553
2021-07-28 | 2.0805 | 2.5764 | 2.6174 | 2.7933 | 2.723 | 2.8988 | 1.3003 | 1.9698 | 2.3451 | 2.3451 | 2.5953 | 2.5953 | 2019-09-24 13:00 | 2.2406 | 3.8448 | 6.4984 | 6.4984 | 6.4984 | 6.4984
2021-07-28 01:00 | 1.8748 | 2.3216 | 2.3586 | 2.5171 | 2.4537 | 2.6121 | 1.1748 | 1.7796 | 2.1187 | 2.1187 | 2.3448 | 2.3448 | 2019-09-24 14:00 | 2.2634 | 3.8841 | 6.5647 | 6.5647 | 6.5647 | 6.5647
2021-07-28 02:00 | 1.8405 | 2.2791 | 2.3154 | 2.471 | 2.4088 | 2.5644 | 1.066 | 1.6148 | 1.9225 | 1.9225 | 2.1276 | 2.1276 | 2019-09-24 15:00 | 2.1872 | 3.7533 | 6.3437 | 6.3437 | 6.3437 | 6.3437
2021-07-28 03:00 | 1.8405 | 2.2791 | 2.3154 | 2.471 | 2.4088 | 2.5644 | 1.0746 | 1.6278 | 1.9379 | 1.9379 | 2.1447 | 2.1447 | 2019-09-24 16:00 | 2.1949 | 3.7664 | 6.3658 | 6.3658 | 6.3658 | 6.3658
2021-07-28 04:00 | 1.9434 | 2.4065 | 2.4449 | 2.6091 | 2.5434 | 2.7077 | 1.0814 | 1.6381 | 1.9503 | 1.9503 | 2.1584 | 2.1584 | 2019-09-24 17:00 | 2.1491 | 3.6879 | 6.2332 | 6.2332 | 6.2332 | 6.2332
2021-07-28 05:00 | 2.4214 | 2.9985 | 3.0463 | 3.251 | 3.1691 | 3.3738 | 1.2996 | 1.9687 | 2.3438 | 2.3438 | 2.5939 | 2.5939 | 2019-09-24 18:00 | 2.1339 | 3.6618 | 6.189 | 6.189 | 6.189 | 6.189
2021-07-28 06:00 | 3.6095 | 4.4698 | 4.541 | 4.8461 | 4.7241 | 5.0292 | 1.6404 | 2.4849 | 2.9584 | 2.9584 | 3.2741 | 3.2741 | 2019-09-24 19:00 | 1.951 | 3.3479 | 5.6585 | 5.6585 | 5.6585 | 5.6585
2021-07-28 07:00 | 4.0753 | 5.0467 | 5.127 | 5.4715 | 5.3337 | 5.6782 | 1.9348 | 2.9308 | 3.4893 | 3.4893 | 3.8616 | 3.8616 | 2019-09-24 20:00 | 1.8976 | 3.2563 | 5.5038 | 5.5038 | 5.5038 | 5.5038
2021-07-28 08:00 | 3.8667 | 4.7883 | 4.8646 | 5.1914 | 5.0607 | 5.3876 | 1.9348 | 2.9308 | 3.4893 | 3.4893 | 3.8616 | 3.8616 | 2019-09-24 21:00 | 1.8671 | 3.204 | 5.4154 | 5.4154 | 5.4154 | 5.4154
2021-07-28 09:00 | 3.8438 | 4.76 | 4.8358 | 5.1607 | 5.0308 | 5.3557 | 2.0119 | 3.0477 | 3.6285 | 3.6285 | 4.0156 | 4.0156 | 2019-09-24 22:00 | 1.7452 | 2.9948 | 5.0617 | 5.0617 | 5.0617 | 5.0617
2021-07-28 10:00 | 3.861 | 4.7812 | 4.8574 | 5.1838 | 5.0532 | 5.3796 | 1.9605 | 2.9698 | 3.5357 | 3.5357 | 3.913 | 3.913 | 2019-09-24 23:00 | 1.5318 | 2.6286 | 4.4428 | 4.4428 | 4.4428 | 4.4428
2021-07-28 11:00 | 3.5409 | 4.3849 | 4.4547 | 4.754 | 4.6343 | 4.9336 | 1.9376 | 2.9352 | 3.4945 | 3.4945 | 3.8673 | 3.8673 | 2019-09-25 | 1.4251 | 2.4455 | 4.1333 | 4.1333 | 4.1333 | 4.1333
2021-07-28 12:00 | 3.6752 | 4.5512 | 4.6237 | 4.9344 | 4.8101 | 5.1208 | 2.112 | 3.1992 | 3.8089 | 3.8089 | 4.2153 | 4.2153 | 2019-09-25 01:00 | 1.3032 | 2.2363 | 3.7797 | 3.7797 | 3.7797 | 3.7797
2021-07-28 13:00 | 3.7581 | 4.6538 | 4.728 | 5.0456 | 4.9186 | 5.2362 | 2.0977 | 3.1776 | 3.7831 | 3.7831 | 4.1867 | 4.1867 | 2019-09-25 02:00 | 1.3032 | 2.2363 | 3.7797 | 3.7797 | 3.7797 | 3.7797
2021-07-28 14:00 | 3.6781 | 4.5547 | 4.6273 | 4.9382 | 4.8138 | 5.1248 | 2.1091 | 3.1949 | 3.8037 | 3.8037 | 4.2096 | 4.2096 | 2019-09-25 03:00 | 1.2575 | 2.1578 | 3.6471 | 3.6471 | 3.6471 | 3.6471
2021-07-28 15:00 | 3.6867 | 4.5653 | 4.6381 | 4.9497 | 4.8251 | 5.1367 | 2.0462 | 3.0997 | 3.6903 | 3.6903 | 4.0841 | 4.0841 | 2019-09-25 04:00 | 1.3184 | 2.2624 | 3.8239 | 3.8239 | 3.8239 | 3.8239
2021-07-28 16:00 | 3.9153 | 4.8485 | 4.9257 | 5.2567 | 5.1243 | 5.4553 | 2.2641 | 3.4297 | 4.0833 | 4.0833 | 4.519 | 4.519 | 2019-09-25 05:00 | 1.3946 | 2.3932 | 4.0449 | 4.0449 | 4.0449 | 4.0449
2021-07-28 17:00 | 4.4411 | 5.4997 | 5.5873 | 5.9627 | 5.8125 | 6.1879 | 2.5492 | 3.8616 | 4.5974 | 4.5974 | 5.088 | 5.088 | 2019-09-25 06:00 | 1.6538 | 2.8379 | 4.7965 | 4.7965 | 4.7965 | 4.7965
2021-07-28 18:00 | 4.3325 | 5.3652 | 5.4506 | 5.8169 | 5.6704 | 6.0366 | 2.6664 | 4.0391 | 4.8087 | 4.8087 | 5.3219 | 5.3219 | 2019-09-25 07:00 | 1.9053 | 3.2694 | 5.5259 | 5.5259 | 5.5259 | 5.5259
2021-07-28 19:00 | 4.1325 | 5.1174 | 5.1989 | 5.5483 | 5.4085 | 5.7579 | 2.6035 | 3.9438 | 4.6954 | 4.6954 | 5.1964 | 5.1964 | 2019-09-25 08:00 | 2.233 | 3.8318 | 6.4763 | 6.4763 | 6.4763 | 6.4763
2021-07-28 20:00 | 3.9296 | 4.8662 | 4.9437 | 5.2759 | 5.143 | 5.4752 | 2.5692 | 3.8919 | 4.6335 | 4.6335 | 5.1279 | 5.1279 | 2019-09-25 09:00 | 2.0958 | 3.5964 | 6.0785 | 6.0785 | 6.0785 | 6.0785
2021-07-28 21:00 | 3.3817 | 4.1878 | 4.2545 | 4.5403 | 4.426 | 4.7118 | 2.3606 | 3.5759 | 4.2573 | 4.2573 | 4.7115 | 4.7115 | 2019-09-25 10:00 | 2.1796 | 3.7402 | 6.3216 | 6.3216 | 6.3216 | 6.3216
2021-07-28 22:00 | 2.9608 | 3.6664 | 3.7248 | 3.9751 | 3.875 | 4.1253 | 2.0377 | 3.0868 | 3.675 | 3.675 | 4.0671 | 4.0671 | 2019-09-25 11:00 | 2.111 | 3.6225 | 6.1227 | 6.1227 | 6.1227 | 6.1227
2021-07-28 23:00 | 2.7441 | 3.3981 | 3.4522 | 3.6842 | 3.5914 | 3.8234 | 1.7492 | 2.6497 | 3.1546 | 3.1546 | 3.4912 | 3.4912 | 2019-09-25 12:00 | 2.172 | 3.7271 | 6.2995 | 6.2995 | 6.2995 | 6.2995
2021-07-29 | 2.3435 | 2.902 | 2.9482 | 3.1463 | 3.0671 | 3.2652 | 1.4032 | 2.1256 | 2.5306 | 2.5306 | 2.8007 | 2.8007 | 2019-09-25 13:00 | 2.172 | 3.7271 | 6.2995 | 6.2995 | 6.2995 | 6.2995
2021-07-29 01:00 | 2.1834 | 2.7038 | 2.7469 | 2.9315 | 2.8576 | 3.0422 | 1.3832 | 2.0953 | 2.4946 | 2.4946 | 2.7607 | 2.7607 | 2019-09-25 14:00 | 2.1796 | 3.7402 | 6.3216 | 6.3216 | 6.3216 | 6.3216
2021-07-29 02:00 | 2.1091 | 2.6118 | 2.6534 | 2.8317 | 2.7604 | 2.9387 | 1.2289 | 1.8615 | 2.2162 | 2.2162 | 2.4527 | 2.4527 | 2019-09-25 15:00 | 2.172 | 3.7271 | 6.2995 | 6.2995 | 6.2995 | 6.2995
2021-07-29 03:00 | 2.1005 | 2.6012 | 2.6426 | 2.8202 | 2.7492 | 2.9267 | 1.1317 | 1.7143 | 2.041 | 2.041 | 2.2588 | 2.2588 | 2019-09-25 16:00 | 2.1644 | 3.7141 | 6.2774 | 6.2774 | 6.2774 | 6.2774
2021-07-29 04:00 | 2.2857 | 2.8305 | 2.8756 | 3.0688 | 2.9915 | 3.1848 | 1.1603 | 1.7576 | 2.0925 | 2.0925 | 2.3158 | 2.3158 | 2019-09-25 17:00 | 2.1034 | 3.6094 | 6.1006 | 6.1006 | 6.1006 | 6.1006
2021-07-29 05:00 | 2.7378 | 3.3904 | 3.4444 | 3.6758 | 3.5833 | 3.8147 | 1.2946 | 1.9611 | 2.3348 | 2.3348 | 2.5839 | 2.5839 | 2019-09-25 18:00 | 2.1034 | 3.6094 | 6.1006 | 6.1006 | 6.1006 | 6.1006
2021-07-29 06:00 | 3.6724 | 4.5477 | 4.6201 | 4.9305 | 4.8064 | 5.1168 | 1.7051 | 2.5828 | 3.075 | 3.075 | 3.4031 | 3.4031 | 2019-09-25 19:00 | 1.9586 | 3.361 | 5.6806 | 5.6806 | 5.6806 | 5.6806
2021-07-29 07:00 | 4.2868 | 5.3085 | 5.3931 | 5.7555 | 5.6105 | 5.9729 | 1.9834 | 3.0044 | 3.5769 | 3.5769 | 3.9586 | 3.9586 | 2019-09-25 20:00 | 1.9053 | 3.2694 | 5.5259 | 5.5259 | 5.5259 | 5.5259
2021-07-29 08:00 | 4.3068 | 5.3333 | 5.4183 | 5.7823 | 5.6367 | 6.0008 | 2.0291 | 3.0737 | 3.6594 | 3.6594 | 4.0499 | 4.0499 | 2019-09-25 21:00 | 1.8748 | 3.2171 | 5.4375 | 5.4375 | 5.4375 | 5.4375
2021-07-29 09:00 | 3.9124 | 4.8449 | 4.9221 | 5.2528 | 5.1205 | 5.4513 | 1.8376 | 2.7836 | 3.3141 | 3.3141 | 3.6677 | 3.6677 | 2019-09-25 22:00 | 1.6766 | 2.8771 | 4.8628 | 4.8628 | 4.8628 | 4.8628
2021-07-29 10:00 | 3.5752 | 4.4273 | 4.4978 | 4.8001 | 4.6792 | 4.9814 | 1.7919 | 2.7144 | 3.2316 | 3.2316 | 3.5764 | 3.5764 | 2019-09-25 23:00 | 1.4709 | 2.524 | 4.266 | 4.266 | 4.266 | 4.266
2021-07-29 11:00 | 3.3323 | 4.1265 | 4.1922 | 4.4739 | 4.3612 | 4.6429 | 1.8205 | 2.7577 | 3.2831 | 3.2831 | 3.6335 | 3.6335 | 2019-09-26 | 1.387 | 2.3801 | 4.0228 | 4.0228 | 4.0228 | 4.0228
2021-07-29 12:00 | 3.1322 | 3.8788 | 3.9406 | 4.2053 | 4.0994 | 4.3642 | 1.7433 | 2.6408 | 3.144 | 3.144 | 3.4794 | 3.4794 | 2019-09-26 01:00 | 1.2117 | 2.0794 | 3.5144 | 3.5144 | 3.5144 | 3.5144
2021-07-29 13:00 | 2.9836 | 3.6947 | 3.7536 | 4.0058 | 3.9049 | 4.1571 | 1.749 | 2.6494 | 3.1543 | 3.1543 | 3.4909 | 3.4909 | 2019-09-26 02:00 | 1.2117 | 2.0794 | 3.5144 | 3.5144 | 3.5144 | 3.5144
2021-07-29 14:00 | 2.875 | 3.5603 | 3.617 | 3.86 | 3.7628 | 4.0058 | 1.7262 | 2.6148 | 3.1131 | 3.1131 | 3.4452 | 3.4452 | 2019-09-26 03:00 | 1.1584 | 1.9878 | 3.3597 | 3.3597 | 3.3597 | 3.3597
2021-07-29 15:00 | 3.0722 | 3.8045 | 3.8651 | 4.1248 | 4.0209 | 4.2806 | 1.689 | 2.5585 | 3.0461 | 3.0461 | 3.3711 | 3.3711 | 2019-09-26 04:00 | 1.1736 | 2.014 | 3.4039 | 3.4039 | 3.4039 | 3.4039
2021-07-29 16:00 | 3.5266 | 4.3671 | 4.4367 | 4.7348 | 4.6155 | 4.9137 | 1.8776 | 2.8442 | 3.3862 | 3.3862 | 3.7475 | 3.7475 | 2019-09-26 05:00 | 1.3946 | 2.3932 | 4.0449 | 4.0449 | 4.0449 | 4.0449
2021-07-29 17:00 | 4.0811 | 5.0537 | 5.1342 | 5.4792 | 5.3412 | 5.6862 | 2.4006 | 3.6365 | 4.3294 | 4.3294 | 4.7914 | 4.7914 | 2019-09-26 06:00 | 1.6385 | 2.8117 | 4.7522 | 4.7522 | 4.7522 | 4.7522
2021-07-29 18:00 | 4.2297 | 5.2378 | 5.3212 | 5.6787 | 5.5357 | 5.8933 | 2.6092 | 3.9525 | 4.7057 | 4.7057 | 5.2078 | 5.2078 | 2019-09-26 07:00 | 1.951 | 3.3479 | 5.6585 | 5.6585 | 5.6585 | 5.6585
2021-07-29 19:00 | 4.0353 | 4.9971 | 5.0767 | 5.4178 | 5.2814 | 5.6225 | 2.695 | 4.0824 | 4.8603 | 4.8603 | 5.3789 | 5.3789 | 2019-09-26 08:00 | 2.1415 | 3.6748 | 6.2111 | 6.2111 | 6.2111 | 6.2111
2021-07-29 20:00 | 3.7249 | 4.6127 | 4.6862 | 5.0011 | 4.8751 | 5.19 | 2.5921 | 3.9265 | 4.6747 | 4.6747 | 5.1735 | 5.1735 | 2019-09-26 09:00 | 2.1263 | 3.6487 | 6.1669 | 6.1669 | 6.1669 | 6.1669
2021-07-29 21:00 | 3.4569 | 4.2808 | 4.3489 | 4.6412 | 4.5243 | 4.8165 | 2.4606 | 3.7274 | 4.4377 | 4.4377 | 4.9112 | 4.9112 | 2019-09-26 10:00 | 2.1339 | 3.6618 | 6.189 | 6.189 | 6.189 | 6.189
2021-07-29 22:00 | 2.9122 | 3.6063 | 3.6637 | 3.9099 | 3.8114 | 4.0576 | 2.172 | 3.2901 | 3.9171 | 3.9171 | 4.3351 | 4.3351 | 2019-09-26 11:00 | 2.1644 | 3.7141 | 6.2774 | 6.2774 | 6.2774 | 6.2774
2021-07-29 23:00 | 2.6189 | 3.2431 | 3.2948 | 3.5162 | 3.4276 | 3.649 | 1.915 | 2.9008 | 3.4536 | 3.4536 | 3.8221 | 3.8221 | 2019-09-26 12:00 | 2.1034 | 3.6094 | 6.1006 | 6.1006 | 6.1006 | 6.1006
2021-07-30 | 2.2949 | 2.8418 | 2.8871 | 3.0811 | 3.0035 | 3.1975 | 1.5433 | 2.3377 | 2.7832 | 2.7832 | 3.0802 | 3.0802 | 2019-09-26 13:00 | 2.0958 | 3.5964 | 6.0785 | 6.0785 | 6.0785 | 6.0785
2021-07-30 01:00 | 2.172 | 2.6897 | 2.7325 | 2.9161 | 2.8427 | 3.0263 | 1.3033 | 1.9742 | 2.3504 | 2.3504 | 2.6012 | 2.6012 | 2019-09-26 14:00 | 2.2101 | 3.7925 | 6.41 | 6.41 | 6.41 | 6.41
2021-07-30 02:00 | 2.1322 | 2.6404 | 2.6824 | 2.8627 | 2.7906 | 2.9708 | 1.2375 | 1.8745 | 2.2317 | 2.2317 | 2.4698 | 2.4698 | 2019-09-26 15:00 | 2.1491 | 3.6879 | 6.2332 | 6.2332 | 6.2332 | 6.2332
2021-07-30 03:00 | 2.1548 | 2.6684 | 2.7109 | 2.8931 | 2.8202 | 3.0024 | 1.2117 | 1.8356 | 2.1853 | 2.1853 | 2.4185 | 2.4185 | 2019-09-26 16:00 | 2.1949 | 3.7664 | 6.3658 | 6.3658 | 6.3658 | 6.3658
2021-07-30 04:00 | 2.41 | 2.9844 | 3.0319 | 3.2357 | 3.1542 | 3.3579 | 1.2288 | 1.8614 | 2.2161 | 2.2161 | 2.4526 | 2.4526 | 2019-09-26 17:00 | 2.0272 | 3.4787 | 5.8795 | 5.8795 | 5.8795 | 5.8795
2021-07-30 05:00 | 2.8397 | 3.5166 | 3.5726 | 3.8126 | 3.7166 | 3.9567 | 1.4229 | 2.1554 | 2.5662 | 2.5662 | 2.84 | 2.84 | 2019-09-26 18:00 | 1.9662 | 3.374 | 5.7027 | 5.7027 | 5.7027 | 5.7027
2021-07-30 06:00 | 4.1525 | 5.1422 | 5.2241 | 5.5751 | 5.4347 | 5.7858 | 1.769 | 2.6797 | 3.1904 | 3.1904 | 3.5308 | 3.5308 | 2019-09-26 19:00 | 1.9662 | 3.374 | 5.7027 | 5.7027 | 5.7027 | 5.7027
2021-07-30 07:00 | 4.8584 | 6.0164 | 6.1122 | 6.5229 | 6.3586 | 6.7693 | 2.2349 | 3.3854 | 4.0305 | 4.0305 | 4.4605 | 4.4605 | 2019-09-26 20:00 | 1.8062 | 3.0994 | 5.2385 | 5.2385 | 5.2385 | 5.2385
2021-07-30 08:00 | 4.7641 | 5.8996 | 5.9935 | 6.3963 | 6.2352 | 6.6379 | 2.2549 | 3.4157 | 4.0666 | 4.0666 | 4.5005 | 4.5005 | 2019-09-26 21:00 | 1.7681 | 3.034 | 5.128 | 5.128 | 5.128 | 5.128
2021-07-30 09:00 | 4.4783 | 5.5457 | 5.634 | 6.0126 | 5.8611 | 6.2397 | 2.0577 | 3.117 | 3.7109 | 3.7109 | 4.1069 | 4.1069 | 2019-09-26 22:00 | 1.5394 | 2.6417 | 4.4649 | 4.4649 | 4.4649 | 4.4649
2021-07-30 10:00 | 4.1582 | 5.1493 | 5.2313 | 5.5828 | 5.4422 | 5.7937 | 1.9348 | 2.9308 | 3.4893 | 3.4893 | 3.8616 | 3.8616 | 2019-09-26 23:00 | 1.4937 | 2.5632 | 4.3323 | 4.3323 | 4.3323 | 4.3323
2021-07-30 11:00 | 3.6524 | 4.5229 | 4.5949 | 4.9037 | 4.7802 | 5.0889 | 2.0291 | 3.0737 | 3.6594 | 3.6594 | 4.0499 | 4.0499 | 2019-09-27 | 1.3565 | 2.3278 | 3.9344 | 3.9344 | 3.9344 | 3.9344
2021-07-30 12:00 | 3.3957 | 4.205 | 4.272 | 4.559 | 4.4442 | 4.7312 | 1.8976 | 2.8745 | 3.4223 | 3.4223 | 3.7875 | 3.7875 | 2019-09-27 01:00 | 1.2575 | 2.1578 | 3.6471 | 3.6471 | 3.6471 | 3.6471
2021-07-30 13:00 | 3.1179 | 3.8611 | 3.9226 | 4.1861 | 4.0807 | 4.3443 | 1.8119 | 2.7447 | 3.2677 | 3.2677 | 3.6163 | 3.6163 | 2019-09-27 02:00 | 1.2041 | 2.0663 | 3.4923 | 3.4923 | 3.4923 | 3.4923
2021-07-30 14:00 | 3.0408 | 3.7655 | 3.8255 | 4.0826 | 3.9797 | 4.2368 | 1.8348 | 2.7793 | 3.3089 | 3.3089 | 3.662 | 3.662 | 2019-09-27 03:00 | 1.2194 | 2.0924 | 3.5366 | 3.5366 | 3.5366 | 3.5366
2021-07-30 15:00 | 3.0636 | 3.7938 | 3.8543 | 4.1132 | 4.0097 | 4.2686 | 1.7976 | 2.723 | 3.2419 | 3.2419 | 3.5878 | 3.5878 | 2019-09-27 04:00 | 1.2575 | 2.1578 | 3.6471 | 3.6471 | 3.6471 | 3.6471
2021-07-30 16:00 | 3.4209 | 4.2362 | 4.3037 | 4.5929 | 4.4772 | 4.7664 | 2.0948 | 3.1733 | 3.7779 | 3.7779 | 4.181 | 4.181 | 2019-09-27 05:00 | 1.4099 | 2.4194 | 4.0891 | 4.0891 | 4.0891 | 4.0891
2021-07-30 17:00 | 3.8981 | 4.8272 | 4.9041 | 5.2336 | 5.1018 | 5.4314 | 2.3778 | 3.6018 | 4.2882 | 4.2882 | 4.7457 | 4.7457 | 2019-09-27 06:00 | 1.6919 | 2.9032 | 4.907 | 4.907 | 4.907 | 4.907
2021-07-30 18:00 | 3.9839 | 4.9334 | 5.012 | 5.3488 | 5.214 | 5.5508 | 2.5721 | 3.8962 | 4.6387 | 4.6387 | 5.1336 | 5.1336 | 2019-09-27 07:00 | 1.8519 | 3.1779 | 5.3711 | 5.3711 | 5.3711 | 5.3711
2021-07-30 19:00 | 3.7638 | 4.6609 | 4.7351 | 5.0533 | 4.926 | 5.2442 | 2.6607 | 4.0304 | 4.7984 | 4.7984 | 5.3104 | 5.3104 | 2019-09-27 08:00 | 2.0501 | 3.5179 | 5.9458 | 5.9458 | 5.9458 | 5.9458
2021-07-30 20:00 | 3.5181 | 4.3565 | 4.4259 | 4.7233 | 4.6044 | 4.9018 | 2.6064 | 3.9482 | 4.7005 | 4.7005 | 5.2021 | 5.2021 | 2019-09-27 09:00 | 2.1034 | 3.6094 | 6.1006 | 6.1006 | 6.1006 | 6.1006
2021-07-30 21:00 | 3.1808 | 3.9389 | 4.0017 | 4.2706 | 4.163 | 4.4319 | 2.4892 | 3.7707 | 4.4892 | 4.4892 | 4.9682 | 4.9682 | 2019-09-27 10:00 | 2.0348 | 3.4917 | 5.9016 | 5.9016 | 5.9016 | 5.9016
2021-07-30 22:00 | 2.9322 | 3.631 | 3.6889 | 3.9367 | 3.8376 | 4.0855 | 2.3247 | 3.5214 | 4.1924 | 4.1924 | 4.6398 | 4.6398 | 2019-09-27 11:00 | 2.0882 | 3.5833 | 6.0564 | 6.0564 | 6.0564 | 6.0564
2021-07-30 23:00 | 2.6693 | 3.3055 | 3.3581 | 3.5837 | 3.4935 | 3.7191 | 1.8274 | 2.7681 | 3.2956 | 3.2956 | 3.6472 | 3.6472 | 2019-09-27 12:00 | 2.2253 | 3.8187 | 6.4542 | 6.4542 | 6.4542 | 6.4542
2021-07-31 | 2.332 | 2.8878 | 2.9338 | 3.131 | 3.0521 | 3.2493 | 1.6318 | 2.4719 | 2.943 | 2.943 | 3.257 | 3.257 | 2019-09-27 13:00 | 2.0805 | 3.5702 | 6.0343 | 6.0343 | 6.0343 | 6.0343
2021-07-31 01:00 | 2.0977 | 2.5976 | 2.639 | 2.8163 | 2.7454 | 2.9227 | 1.4056 | 2.1292 | 2.5349 | 2.5349 | 2.8054 | 2.8054 | 2019-09-27 14:00 | 2.1339 | 3.6618 | 6.189 | 6.189 | 6.189 | 6.189
2021-07-31 02:00 | 2.0177 | 2.4986 | 2.5383 | 2.7089 | 2.6407 | 2.8112 | 1.2949 | 1.9616 | 2.3354 | 2.3354 | 2.5846 | 2.5846 | 2019-09-27 15:00 | 2.1339 | 3.6618 | 6.189 | 6.189 | 6.189 | 6.189
2021-07-31 03:00 | 1.9408 | 2.4034 | 2.4416 | 2.6057 | 2.5401 | 2.7041 | 1.2403 | 1.8788 | 2.2369 | 2.2369 | 2.4755 | 2.4755 | 2019-09-27 16:00 | 2.1186 | 3.6356 | 6.1448 | 6.1448 | 6.1448 | 6.1448
2021-07-31 04:00 | 2.0018 | 2.479 | 2.5185 | 2.6877 | 2.62 | 2.7892 | 1.2403 | 1.8788 | 2.2369 | 2.2369 | 2.4755 | 2.4755 | 2019-09-27 17:00 | 2.0348 | 3.4917 | 5.9016 | 5.9016 | 5.9016 | 5.9016
2021-07-31 05:00 | 2.2091 | 2.7357 | 2.7792 | 2.966 | 2.8913 | 3.078 | 1.2775 | 1.9351 | 2.3038 | 2.3038 | 2.5497 | 2.5497 | 2019-09-27 18:00 | 1.8595 | 3.191 | 5.3932 | 5.3932 | 5.3932 | 5.3932
2021-07-31 06:00 | 2.5549 | 3.1639 | 3.2143 | 3.4303 | 3.3439 | 3.5598 | 1.4747 | 2.2338 | 2.6595 | 2.6595 | 2.9433 | 2.9433 | 2019-09-27 19:00 | 1.8214 | 3.1256 | 5.2827 | 5.2827 | 5.2827 | 5.2827
2021-07-31 07:00 | 3.0065 | 3.7231 | 3.7824 | 4.0365 | 3.9348 | 4.189 | 1.8805 | 2.8486 | 3.3914 | 3.3914 | 3.7532 | 3.7532 | 2019-09-27 20:00 | 1.6995 | 2.9163 | 4.9291 | 4.9291 | 4.9291 | 4.9291
2021-07-31 08:00 | 3.1608 | 3.9142 | 3.9765 | 4.2437 | 4.1368 | 4.404 | 2.0177 | 3.0564 | 3.6388 | 3.6388 | 4.027 | 4.027 | 2019-09-27 21:00 | 1.6995 | 2.9163 | 4.9291 | 4.9291 | 4.9291 | 4.9291
2021-07-31 09:00 | 3.158 | 3.9106 | 3.9729 | 4.2399 | 4.1331 | 4.4 | 2.0863 | 3.1603 | 3.7625 | 3.7625 | 4.1639 | 4.1639 | 2019-09-27 22:00 | 1.5013 | 2.5763 | 4.3544 | 4.3544 | 4.3544 | 4.3544
2021-07-31 10:00 | 3.2523 | 4.0274 | 4.0916 | 4.3665 | 4.2565 | 4.5314 | 2.4006 | 3.6365 | 4.3294 | 4.3294 | 4.7914 | 4.7914 | 2019-09-27 23:00 | 1.3413 | 2.3017 | 3.8902 | 3.8902 | 3.8902 | 3.8902
2021-07-31 11:00 | 3.2494 | 4.0239 | 4.088 | 4.3627 | 4.2528 | 4.5275 | 2.332 | 3.5326 | 4.2057 | 4.2057 | 4.6545 | 4.6545 | 2019-09-28 | 1.2879 | 2.2101 | 3.7355 | 3.7355 | 3.7355 | 3.7355
2021-07-31 12:00 | 3.0265 | 3.7478 | 3.8075 | 4.0634 | 3.961 | 4.2169 | 2.2892 | 3.4676 | 4.1284 | 4.1284 | 4.5689 | 4.5689 | 2019-09-28 01:00 | 1.2041 | 2.0663 | 3.4923 | 3.4923 | 3.4923 | 3.4923
2021-07-31 13:00 | 2.6864 | 3.3267 | 3.3797 | 3.6068 | 3.5159 | 3.743 | 2.212 | 3.3508 | 3.9892 | 3.9892 | 4.4149 | 4.4149 | 2019-09-28 02:00 | 1.1889 | 2.0401 | 3.4481 | 3.4481 | 3.4481 | 3.4481
2021-07-31 14:00 | 2.6207 | 3.2453 | 3.297 | 3.5185 | 3.4299 | 3.6514 | 2.1553 | 3.2649 | 3.887 | 3.887 | 4.3018 | 4.3018 | 2019-09-28 03:00 | 1.2803 | 2.1971 | 3.7134 | 3.7134 | 3.7134 | 3.7134
2021-07-31 15:00 | 2.5692 | 3.1816 | 3.2323 | 3.4494 | 3.3626 | 3.5798 | 2.1863 | 3.3118 | 3.9429 | 3.9429 | 4.3636 | 4.3636 | 2019-09-28 04:00 | 1.2194 | 2.0924 | 3.5366 | 3.5366 | 3.5366 | 3.5366
2021-07-31 16:00 | 2.6607 | 3.2948 | 3.3473 | 3.5722 | 3.4823 | 3.7072 | 2.2949 | 3.4763 | 4.1387 | 4.1387 | 4.5803 | 4.5803 | 2019-09-28 05:00 | 1.2498 | 2.1447 | 3.625 | 3.625 | 3.625 | 3.625
2021-07-31 17:00 | 3.0379 | 3.762 | 3.8219 | 4.0787 | 3.976 | 4.2328 | 2.4521 | 3.7144 | 4.4222 | 4.4222 | 4.894 | 4.894 | 2019-09-28 06:00 | 1.387 | 2.3801 | 4.0228 | 4.0228 | 4.0228 | 4.0228
2021-07-31 18:00 | 3.2694 | 4.0486 | 4.1131 | 4.3895 | 4.279 | 4.5553 | 2.6178 | 3.9655 | 4.7211 | 4.7211 | 5.2249 | 5.2249 | 2019-09-28 07:00 | 1.5471 | 2.6548 | 4.487 | 4.487 | 4.487 | 4.487
2021-07-31 19:00 | 3.1322 | 3.8788 | 3.9406 | 4.2053 | 4.0994 | 4.3642 | 2.5835 | 3.9135 | 4.6593 | 4.6593 | 5.1564 | 5.1564 | 2019-09-28 08:00 | 1.669 | 2.864 | 4.8407 | 4.8407 | 4.8407 | 4.8407
2021-07-31 20:00 | 3.0008 | 3.716 | 3.7752 | 4.0288 | 3.9274 | 4.181 | 2.4292 | 3.6798 | 4.381 | 4.381 | 4.8484 | 4.8484 | 2019-09-28 09:00 | 1.8443 | 3.1648 | 5.349 | 5.349 | 5.349 | 5.349
2021-07-31 21:00 | 2.8722 | 3.5567 | 3.6134 | 3.8562 | 3.7591 | 4.0018 | 2.2663 | 3.433 | 4.0872 | 4.0872 | 4.5233 | 4.5233 | 2019-09-28 10:00 | 1.8214 | 3.1256 | 5.2827 | 5.2827 | 5.2827 | 5.2827
2021-07-31 22:00 | 2.5835 | 3.1993 | 3.2502 | 3.4686 | 3.3813 | 3.5997 | 2.092 | 3.1689 | 3.7728 | 3.7728 | 4.1753 | 4.1753 | 2019-09-28 11:00 | 1.8824 | 3.2302 | 5.4596 | 5.4596 | 5.4596 | 5.4596
2021-07-31 23:00 | 2.43 | 3.0091 | 3.0571 | 3.2625 | 3.1803 | 3.3857 | 1.7035 | 2.5804 | 3.0722 | 3.0722 | 3.4 | 3.4 | 2019-09-28 12:00 | 1.8443 | 3.1648 | 5.349 | 5.349 | 5.349 | 5.349
2021-08-01 | 2.1063 | 2.6083 | 2.6498 | 2.8279 | 2.7566 | 2.9347 | 1.5178 | 2.2991 | 2.7372 | 2.7372 | 3.0293 | 3.0293 | 2019-09-28 13:00 | 1.8214 | 3.1256 | 5.2827 | 5.2827 | 5.2827 | 5.2827
2021-08-01 01:00 | 1.9605 | 2.4278 | 2.4664 | 2.6322 | 2.5659 | 2.7316 | 1.3146 | 1.9914 | 2.3709 | 2.3709 | 2.6238 | 2.6238 | 2019-09-28 14:00 | 1.7681 | 3.034 | 5.128 | 5.128 | 5.128 | 5.128
2021-08-01 02:00 | 1.8862 | 2.3358 | 2.373 | 2.5324 | 2.4686 | 2.6281 | 1.2203 | 1.8485 | 2.2008 | 2.2008 | 2.4356 | 2.4356 | 2019-09-28 15:00 | 1.8824 | 3.2302 | 5.4596 | 5.4596 | 5.4596 | 5.4596
2021-08-01 03:00 | 1.8233 | 2.2579 | 2.2939 | 2.448 | 2.3863 | 2.5405 | 1.1717 | 1.7749 | 2.1132 | 2.1132 | 2.3386 | 2.3386 | 2019-09-28 16:00 | 1.8671 | 3.204 | 5.4154 | 5.4154 | 5.4154 | 5.4154
2021-08-01 04:00 | 1.9062 | 2.3605 | 2.3981 | 2.5593 | 2.4948 | 2.6559 | 1.1689 | 1.7706 | 2.108 | 2.108 | 2.3329 | 2.3329 | 2019-09-28 17:00 | 1.9053 | 3.2694 | 5.5259 | 5.5259 | 5.5259 | 5.5259
2021-08-01 05:00 | 1.9829 | 2.4555 | 2.4946 | 2.6622 | 2.5952 | 2.7628 | 1.1888 | 1.8008 | 2.1439 | 2.1439 | 2.3727 | 2.3727 | 2019-09-28 18:00 | 1.9586 | 3.361 | 5.6806 | 5.6806 | 5.6806 | 5.6806
2021-08-01 06:00 | 2.1847 | 2.7055 | 2.7486 | 2.9332 | 2.8594 | 3.044 | 1.2918 | 1.9568 | 2.3296 | 2.3296 | 2.5782 | 2.5782 | 2019-09-28 19:00 | 1.9815 | 3.4002 | 5.7469 | 5.7469 | 5.7469 | 5.7469
2021-08-01 07:00 | 2.5866 | 3.2031 | 3.2541 | 3.4728 | 3.3853 | 3.6039 | 1.549 | 2.3464 | 2.7935 | 2.7935 | 3.0916 | 3.0916 | 2019-09-28 20:00 | 1.73 | 2.9686 | 5.0175 | 5.0175 | 5.0175 | 5.0175
2021-08-01 08:00 | 2.6378 | 3.2665 | 3.3186 | 3.5415 | 3.4523 | 3.6753 | 1.7605 | 2.6667 | 3.1749 | 3.1749 | 3.5137 | 3.5137 | 2019-09-28 21:00 | 1.6461 | 2.8248 | 4.7743 | 4.7743 | 4.7743 | 4.7743
2021-08-01 09:00 | 2.895 | 3.585 | 3.6421 | 3.8869 | 3.789 | 4.0337 | 2.0177 | 3.0564 | 3.6388 | 3.6388 | 4.027 | 4.027 | 2019-09-28 22:00 | 1.5775 | 2.7071 | 4.5754 | 4.5754 | 4.5754 | 4.5754
2021-08-01 10:00 | 2.955 | 3.6594 | 3.7176 | 3.9674 | 3.8675 | 4.1173 | 2.2606 | 3.4243 | 4.0769 | 4.0769 | 4.5119 | 4.5119 | 2019-09-28 23:00 | 1.4327 | 2.4586 | 4.1555 | 4.1555 | 4.1555 | 4.1555
2021-08-01 11:00 | 2.9265 | 3.624 | 3.6817 | 3.9291 | 3.8301 | 4.0775 | 2.3435 | 3.5499 | 4.2263 | 4.2263 | 4.6773 | 4.6773 | 2019-09-29 | 1.3261 | 2.2755 | 3.846 | 3.846 | 3.846 | 3.846
2021-08-01 12:00 | 2.9379 | 3.6381 | 3.6961 | 3.9444 | 3.8451 | 4.0934 | 2.3749 | 3.5975 | 4.283 | 4.283 | 4.74 | 4.74 | 2019-09-29 01:00 | 1.2194 | 2.0924 | 3.5366 | 3.5366 | 3.5366 | 3.5366
2021-08-01 13:00 | 2.9122 | 3.6063 | 3.6637 | 3.9099 | 3.8114 | 4.0576 | 2.3635 | 3.5802 | 4.2624 | 4.2624 | 4.7172 | 4.7172 | 2019-09-29 02:00 | 1.1431 | 1.9617 | 3.3155 | 3.3155 | 3.3155 | 3.3155
2021-08-01 14:00 | 2.8693 | 3.5532 | 3.6098 | 3.8523 | 3.7553 | 3.9979 | 2.2749 | 3.446 | 4.1026 | 4.1026 | 4.5404 | 4.5404 | 2019-09-29 03:00 | 1.1508 | 1.9747 | 3.3376 | 3.3376 | 3.3376 | 3.3376
2021-08-01 15:00 | 2.7064 | 3.3515 | 3.4048 | 3.6336 | 3.5421 | 3.7709 | 2.1406 | 3.2425 | 3.8604 | 3.8604 | 4.2723 | 4.2723 | 2019-09-29 04:00 | 1.1889 | 2.0401 | 3.4481 | 3.4481 | 3.4481 | 3.4481
2021-08-01 16:00 | 2.9876 | 3.6997 | 3.7586 | 4.0111 | 3.9101 | 4.1627 | 2.372 | 3.5932 | 4.2779 | 4.2779 | 4.7343 | 4.7343 | 2019-09-29 05:00 | 1.2803 | 2.1971 | 3.7134 | 3.7134 | 3.7134 | 3.7134
2021-08-01 17:00 | 3.4523 | 4.2751 | 4.3432 | 4.6351 | 4.5183 | 4.8102 | 2.4892 | 3.7707 | 4.4892 | 4.4892 | 4.9682 | 4.9682 | 2019-09-29 06:00 | 1.3184 | 2.2624 | 3.8239 | 3.8239 | 3.8239 | 3.8239
2021-08-01 18:00 | 3.701 | 4.583 | 4.656 | 4.9689 | 4.8438 | 5.1566 | 2.6521 | 4.0174 | 4.783 | 4.783 | 5.2933 | 5.2933 | 2019-09-29 07:00 | 1.5013 | 2.5763 | 4.3544 | 4.3544 | 4.3544 | 4.3544
2021-08-01 19:00 | 3.5209 | 4.3601 | 4.4295 | 4.7272 | 4.6081 | 4.9057 | 2.635 | 3.9915 | 4.752 | 4.752 | 5.2591 | 5.2591 | 2019-09-29 08:00 | 1.6995 | 2.9163 | 4.9291 | 4.9291 | 4.9291 | 4.9291
2021-08-01 20:00 | 3.3437 | 4.1407 | 4.2066 | 4.4893 | 4.3762 | 4.6589 | 2.5664 | 3.8876 | 4.6284 | 4.6284 | 5.1222 | 5.1222 | 2019-09-29 09:00 | 1.7833 | 3.0602 | 5.1722 | 5.1722 | 5.1722 | 5.1722
2021-08-01 21:00 | 3.1551 | 3.9071 | 3.9693 | 4.236 | 4.1293 | 4.3961 | 2.4542 | 3.7176 | 4.426 | 4.426 | 4.8983 | 4.8983 | 2019-09-29 10:00 | 1.9586 | 3.361 | 5.6806 | 5.6806 | 5.6806 | 5.6806
2021-08-01 22:00 | 2.7979 | 3.4647 | 3.5199 | 3.7564 | 3.6618 | 3.8983 | 2.0634 | 3.1256 | 3.7212 | 3.7212 | 4.1183 | 4.1183 | 2019-09-29 11:00 | 1.8976 | 3.2563 | 5.5038 | 5.5038 | 5.5038 | 5.5038
2021-08-01 23:00 | 2.5889 | 3.206 | 3.257 | 3.4759 | 3.3884 | 3.6072 | 1.7464 | 2.6454 | 3.1495 | 3.1495 | 3.4856 | 3.4856 | 2019-09-29 12:00 | 1.8595 | 3.191 | 5.3932 | 5.3932 | 5.3932 | 5.3932
2021-08-02 | 2.2634 | 2.8029 | 2.8476 | 3.0389 | 2.9624 | 3.1537 | 1.5318 | 2.3204 | 2.7626 | 2.7626 | 3.0574 | 3.0574 | 2019-09-29 13:00 | 1.9205 | 3.2956 | 5.5701 | 5.5701 | 5.5701 | 5.5701
2021-08-02 01:00 | 2.0834 | 2.58 | 2.621 | 2.7972 | 2.7267 | 2.9028 | 1.3032 | 1.9741 | 2.3503 | 2.3503 | 2.601 | 2.601 | 2019-09-29 14:00 | 1.9053 | 3.2694 | 5.5259 | 5.5259 | 5.5259 | 5.5259
2021-08-02 02:00 | 2.0005 | 2.4773 | 2.5168 | 2.6859 | 2.6182 | 2.7874 | 1.2317 | 1.8659 | 2.2214 | 2.2214 | 2.4584 | 2.4584 | 2019-09-29 15:00 | 1.7833 | 3.0602 | 5.1722 | 5.1722 | 5.1722 | 5.1722
2021-08-02 03:00 | 1.9719 | 2.4419 | 2.4808 | 2.6475 | 2.5808 | 2.7475 | 1.1692 | 1.7711 | 2.1086 | 2.1086 | 2.3335 | 2.3335 | 2019-09-29 16:00 | 1.89 | 3.2433 | 5.4817 | 5.4817 | 5.4817 | 5.4817
2021-08-02 04:00 | 2.0405 | 2.5269 | 2.5671 | 2.7396 | 2.6706 | 2.8431 | 1.1746 | 1.7793 | 2.1183 | 2.1183 | 2.3443 | 2.3443 | 2019-09-29 17:00 | 1.7909 | 3.0733 | 5.1943 | 5.1943 | 5.1943 | 5.1943
2021-08-02 05:00 | 2.6462 | 3.2769 | 3.3291 | 3.5528 | 3.4633 | 3.687 | 1.3602 | 2.0604 | 2.453 | 2.453 | 2.7147 | 2.7147 | 2019-09-29 18:00 | 1.73 | 2.9686 | 5.0175 | 5.0175 | 5.0175 | 5.0175
2021-08-02 06:00 | 4.0896 | 5.0644 | 5.145 | 5.4907 | 5.3524 | 5.6981 | 1.7272 | 2.6164 | 3.115 | 3.115 | 3.4474 | 3.4474 | 2019-09-29 19:00 | 1.7986 | 3.0863 | 5.2164 | 5.2164 | 5.2164 | 5.2164
2021-08-02 07:00 | 4.5583 | 5.6448 | 5.7347 | 6.12 | 5.9659 | 6.3512 | 2.2463 | 3.4027 | 4.0511 | 4.0511 | 4.4834 | 4.4834 | 2019-09-29 20:00 | 1.6157 | 2.7725 | 4.6859 | 4.6859 | 4.6859 | 4.6859
2021-08-02 08:00 | 4.7126 | 5.8359 | 5.9288 | 6.3272 | 6.1678 | 6.5662 | 2.2834 | 3.459 | 4.1181 | 4.1181 | 4.5575 | 4.5575 | 2019-09-29 21:00 | 1.5242 | 2.6155 | 4.4207 | 4.4207 | 4.4207 | 4.4207
2021-08-02 09:00 | 4.5669 | 5.6554 | 5.7454 | 6.1315 | 5.9771 | 6.3631 | 2.1806 | 3.3031 | 3.9326 | 3.9326 | 4.3522 | 4.3522 | 2019-09-29 22:00 | 1.4937 | 2.5632 | 4.3323 | 4.3323 | 4.3323 | 4.3323
2021-08-02 10:00 | 4.2297 | 5.2378 | 5.3212 | 5.6787 | 5.5357 | 5.8933 | 1.9634 | 2.9741 | 3.5408 | 3.5408 | 3.9187 | 3.9187 | 2019-09-29 23:00 | 1.3261 | 2.2755 | 3.846 | 3.846 | 3.846 | 3.846
2021-08-02 11:00 | 4.0096 | 4.9653 | 5.0443 | 5.3833 | 5.2477 | 5.5867 | 1.9834 | 3.0044 | 3.5769 | 3.5769 | 3.9586 | 3.9586 | 2019-09-30 | 1.2498 | 2.1447 | 3.625 | 3.625 | 3.625 | 3.625
2021-08-02 12:00 | 3.6038 | 4.4627 | 4.5338 | 4.8384 | 4.7166 | 5.0212 | 1.8633 | 2.8226 | 3.3604 | 3.3604 | 3.719 | 3.719 | 2019-09-30 01:00 | 1.2956 | 2.2232 | 3.7576 | 3.7576 | 3.7576 | 3.7576
2021-08-02 13:00 | 3.138 | 3.8859 | 3.9477 | 4.213 | 4.1069 | 4.3722 | 1.8691 | 2.8313 | 3.3708 | 3.3708 | 3.7304 | 3.7304 | 2019-09-30 02:00 | 1.2041 | 2.0663 | 3.4923 | 3.4923 | 3.4923 | 3.4923
2021-08-02 14:00 | 3.0036 | 3.7195 | 3.7788 | 4.0327 | 3.9311 | 4.185 | 1.7462 | 2.6451 | 3.1491 | 3.1491 | 3.4852 | 3.4852 | 2019-09-30 03:00 | 1.2194 | 2.0924 | 3.5366 | 3.5366 | 3.5366 | 3.5366
2021-08-02 15:00 | 3.0722 | 3.8045 | 3.8651 | 4.1248 | 4.0209 | 4.2806 | 1.729 | 2.6191 | 3.1182 | 3.1182 | 3.4509 | 3.4509 | 2019-09-30 04:00 | 1.2041 | 2.0663 | 3.4923 | 3.4923 | 3.4923 | 3.4923
2021-08-02 16:00 | 3.4266 | 4.2433 | 4.3109 | 4.6005 | 4.4847 | 4.7743 | 1.8919 | 2.8659 | 3.412 | 3.412 | 3.7761 | 3.7761 | 2019-09-30 05:00 | 1.3718 | 2.354 | 3.9786 | 3.9786 | 3.9786 | 3.9786
2021-08-02 17:00 | 3.9696 | 4.9157 | 4.994 | 5.3296 | 5.1953 | 5.5309 | 2.2806 | 3.4546 | 4.1129 | 4.1129 | 4.5518 | 4.5518 | 2019-09-30 06:00 | 1.6842 | 2.8902 | 4.8849 | 4.8849 | 4.8849 | 4.8849
2021-08-02 18:00 | 4.2268 | 5.2342 | 5.3176 | 5.6749 | 5.532 | 5.8893 | 2.5549 | 3.8702 | 4.6077 | 4.6077 | 5.0994 | 5.0994 | 2019-09-30 07:00 | 1.8367 | 3.1517 | 5.3269 | 5.3269 | 5.3269 | 5.3269
2021-08-02 19:00 | 4.054 | 5.0202 | 5.1001 | 5.4428 | 5.3058 | 5.6485 | 2.635 | 3.9915 | 4.752 | 4.752 | 5.2591 | 5.2591 | 2019-09-30 08:00 | 2.0043 | 3.4394 | 5.8132 | 5.8132 | 5.8132 | 5.8132
2021-08-02 20:00 | 3.6924 | 4.5724 | 4.6453 | 4.9574 | 4.8325 | 5.1447 | 2.5178 | 3.814 | 4.5407 | 4.5407 | 5.0252 | 5.0252 | 2019-09-30 09:00 | 1.9738 | 3.3871 | 5.7248 | 5.7248 | 5.7248 | 5.7248
2021-08-02 21:00 | 3.4123 | 4.2256 | 4.2929 | 4.5814 | 4.466 | 4.7544 | 2.3578 | 3.5715 | 4.2521 | 4.2521 | 4.7058 | 4.7058 | 2019-09-30 10:00 | 2.0653 | 3.5441 | 5.99 | 5.99 | 5.99 | 5.99
2021-08-02 22:00 | 2.7521 | 3.4081 | 3.4624 | 3.695 | 3.602 | 3.8346 | 1.9634 | 2.9741 | 3.5408 | 3.5408 | 3.9187 | 3.9187 | 2019-09-30 11:00 | 1.9967 | 3.4264 | 5.7911 | 5.7911 | 5.7911 | 5.7911
2021-08-02 23:00 | 2.4293 | 3.0083 | 3.0562 | 3.2616 | 3.1794 | 3.3848 | 1.6861 | 2.5542 | 3.0409 | 3.0409 | 3.3654 | 3.3654 | 2019-09-30 12:00 | 2.0577 | 3.531 | 5.9679 | 5.9679 | 5.9679 | 5.9679
2021-08-03 | 2.1394 | 2.6493 | 2.6915 | 2.8723 | 2.8 | 2.9808 | 1.3232 | 2.0044 | 2.3863 | 2.3863 | 2.641 | 2.641 | 2019-09-30 13:00 | 2.0196 | 3.4656 | 5.8574 | 5.8574 | 5.8574 | 5.8574
2021-08-03 01:00 | 1.8948 | 2.3464 | 2.3837 | 2.5439 | 2.4799 | 2.64 | 1.2865 | 1.9488 | 2.3201 | 2.3201 | 2.5677 | 2.5677 | 2019-09-30 14:00 | 2.0348 | 3.4917 | 5.9016 | 5.9016 | 5.9016 | 5.9016
2021-08-03 02:00 | 1.8433 | 2.2827 | 2.319 | 2.4749 | 2.4125 | 2.5683 | 1.1174 | 1.6927 | 2.0152 | 2.0152 | 2.2303 | 2.2303 | 2019-09-30 15:00 | 2.0729 | 3.5571 | 6.0121 | 6.0121 | 6.0121 | 6.0121
2021-08-03 03:00 | 1.8593 | 2.3024 | 2.3391 | 2.4962 | 2.4334 | 2.5905 | 1.0946 | 1.6581 | 1.974 | 1.974 | 2.1846 | 2.1846 | 2019-09-30 16:00 | 2.0958 | 3.5964 | 6.0785 | 6.0785 | 6.0785 | 6.0785
2021-08-03 04:00 | 1.9844 | 2.4574 | 2.4965 | 2.6643 | 2.5972 | 2.7649 | 1.126 | 1.7057 | 2.0307 | 2.0307 | 2.2474 | 2.2474 | 2019-09-30 17:00 | 2.0043 | 3.4394 | 5.8132 | 5.8132 | 5.8132 | 5.8132
2021-08-03 05:00 | 2.3936 | 2.9641 | 3.0113 | 3.2137 | 3.1327 | 3.3351 | 1.2541 | 1.8997 | 2.2617 | 2.2617 | 2.503 | 2.503 | 2019-09-30 18:00 | 1.9738 | 3.3871 | 5.7248 | 5.7248 | 5.7248 | 5.7248
2021-08-03 06:00 | 3.6038 | 4.4627 | 4.5338 | 4.8384 | 4.7166 | 5.0212 | 1.5833 | 2.3983 | 2.8554 | 2.8554 | 3.16 | 3.16 | 2019-09-30 19:00 | 1.89 | 3.2433 | 5.4817 | 5.4817 | 5.4817 | 5.4817
2021-08-03 07:00 | 4.0582 | 5.0254 | 5.1055 | 5.4485 | 5.3113 | 5.6543 | 1.9548 | 2.9611 | 3.5254 | 3.5254 | 3.9015 | 3.9015 | 2019-09-30 20:00 | 1.8443 | 3.1648 | 5.349 | 5.349 | 5.349 | 5.349
2021-08-03 08:00 | 4.0153 | 4.9723 | 5.0515 | 5.391 | 5.2552 | 5.5946 | 2.0234 | 3.065 | 3.6491 | 3.6491 | 4.0384 | 4.0384 | 2019-09-30 21:00 | 1.7605 | 3.0209 | 5.1059 | 5.1059 | 5.1059 | 5.1059
2021-08-03 09:00 | 3.8953 | 4.8237 | 4.9005 | 5.2298 | 5.0981 | 5.4274 | 1.8919 | 2.8659 | 3.412 | 3.412 | 3.7761 | 3.7761 | 2019-09-30 22:00 | 1.6233 | 2.7855 | 4.708 | 4.708 | 4.708 | 4.708
2021-08-03 10:00 | 3.821 | 4.7317 | 4.807 | 5.13 | 5.0008 | 5.3238 | 1.8405 | 2.788 | 3.3192 | 3.3192 | 3.6734 | 3.6734 | 2019-09-30 23:00 | 1.4556 | 2.4978 | 4.2218 | 4.2218 | 4.2218 | 4.2218
2021-08-03 11:00 | 3.8381 | 4.7529 | 4.8286 | 5.1531 | 5.0233 | 5.3477 | 1.9576 | 2.9655 | 3.5305 | 3.5305 | 3.9073 | 3.9073 | 2019-10-01 | 1.3489 | 2.2106 | 3.6288 | 3.6288 | 3.6288 | 3.6288
2021-08-03 12:00 | 3.8553 | 4.7742 | 4.8502 | 5.1761 | 5.0457 | 5.3716 | 1.9376 | 2.9352 | 3.4945 | 3.4945 | 3.8673 | 3.8673 | 2019-10-01 01:00 | 1.3337 | 2.1856 | 3.5878 | 3.5878 | 3.5878 | 3.5878
2021-08-03 13:00 | 3.4866 | 4.3176 | 4.3864 | 4.6811 | 4.5632 | 4.858 | 1.9805 | 3.0001 | 3.5718 | 3.5718 | 3.9529 | 3.9529 | 2019-10-01 02:00 | 1.227 | 2.0108 | 3.3007 | 3.3007 | 3.3007 | 3.3007
2021-08-03 14:00 | 3.3523 | 4.1513 | 4.2174 | 4.5008 | 4.3874 | 4.6708 | 1.8405 | 2.788 | 3.3192 | 3.3192 | 3.6734 | 3.6734 | 2019-10-01 03:00 | 1.227 | 2.0108 | 3.3007 | 3.3007 | 3.3007 | 3.3007
2021-08-03 15:00 | 3.4437 | 4.2645 | 4.3325 | 4.6236 | 4.5071 | 4.7982 | 1.9605 | 2.9698 | 3.5357 | 3.5357 | 3.913 | 3.913 | 2019-10-01 04:00 | 1.2498 | 2.0483 | 3.3622 | 3.3622 | 3.3622 | 3.3622
2021-08-03 16:00 | 3.6267 | 4.491 | 4.5626 | 4.8691 | 4.7465 | 5.0531 | 2.1806 | 3.3031 | 3.9326 | 3.9326 | 4.3522 | 4.3522 | 2019-10-01 05:00 | 1.4251 | 2.3355 | 3.8338 | 3.8338 | 3.8338 | 3.8338
2021-08-03 17:00 | 4.2239 | 5.2307 | 5.314 | 5.6711 | 5.5282 | 5.8853 | 2.4806 | 3.7577 | 4.4737 | 4.4737 | 4.9511 | 4.9511 | 2019-10-01 06:00 | 1.5928 | 2.6103 | 4.2848 | 4.2848 | 4.2848 | 4.2848
2021-08-03 18:00 | 4.4783 | 5.5457 | 5.634 | 6.0126 | 5.8611 | 6.2397 | 2.7207 | 4.1213 | 4.9067 | 4.9067 | 5.4302 | 5.4302 | 2019-10-01 07:00 | 1.9129 | 3.1348 | 5.1459 | 5.1459 | 5.1459 | 5.1459
2021-08-03 19:00 | 4.404 | 5.4536 | 5.5405 | 5.9128 | 5.7639 | 6.1362 | 2.8036 | 4.2469 | 5.0561 | 5.0561 | 5.5956 | 5.5956 | 2019-10-01 08:00 | 2.0653 | 3.3846 | 5.5559 | 5.5559 | 5.5559 | 5.5559
2021-08-03 20:00 | 3.9067 | 4.8379 | 4.9149 | 5.2452 | 5.1131 | 5.4433 | 2.6407 | 4.0001 | 4.7624 | 4.7624 | 5.2705 | 5.2705 | 2019-10-01 09:00 | 2.0501 | 3.3597 | 5.5149 | 5.5149 | 5.5149 | 5.5149
2021-08-03 21:00 | 3.6033 | 4.4622 | 4.5332 | 4.8378 | 4.716 | 5.0206 | 2.4778 | 3.7534 | 4.4686 | 4.4686 | 4.9454 | 4.9454 | 2019-10-01 10:00 | 2.0424 | 3.3472 | 5.4944 | 5.4944 | 5.4944 | 5.4944
2021-08-03 22:00 | 3.0465 | 3.7726 | 3.8327 | 4.0902 | 3.9872 | 4.2447 | 2.1663 | 3.2815 | 3.9068 | 3.9068 | 4.3236 | 4.3236 | 2019-10-01 11:00 | 2.1415 | 3.5095 | 5.7609 | 5.7609 | 5.7609 | 5.7609
2021-08-03 23:00 | 2.6321 | 3.2594 | 3.3114 | 3.5339 | 3.4449 | 3.6674 | 1.7702 | 2.6815 | 3.1925 | 3.1925 | 3.5331 | 3.5331 | 2019-10-01 12:00 | 2.1796 | 3.572 | 5.8634 | 5.8634 | 5.8634 | 5.8634
2021-08-04 | 2.2145 | 2.7424 | 2.786 | 2.9732 | 2.8984 | 3.0856 | 1.529 | 2.3161 | 2.7574 | 2.7574 | 3.0516 | 3.0516 | 2019-10-01 13:00 | 2.1567 | 3.5345 | 5.8019 | 5.8019 | 5.8019 | 5.8019
2021-08-04 01:00 | 2.0748 | 2.5693 | 2.6103 | 2.7856 | 2.7155 | 2.8909 | 1.2718 | 1.9265 | 2.2936 | 2.2936 | 2.5383 | 2.5383 | 2019-10-01 14:00 | 2.1263 | 3.4845 | 5.7199 | 5.7199 | 5.7199 | 5.7199
2021-08-04 02:00 | 2.0234 | 2.5056 | 2.5455 | 2.7166 | 2.6482 | 2.8192 | 1.1517 | 1.7446 | 2.0771 | 2.0771 | 2.2987 | 2.2987 | 2019-10-01 15:00 | 2.1415 | 3.5095 | 5.7609 | 5.7609 | 5.7609 | 5.7609
2021-08-04 03:00 | 1.9834 | 2.4561 | 2.4952 | 2.6629 | 2.5958 | 2.7635 | 1.1489 | 1.7403 | 2.0719 | 2.0719 | 2.293 | 2.293 | 2019-10-01 16:00 | 2.1339 | 3.497 | 5.7404 | 5.7404 | 5.7404 | 5.7404
2021-08-04 04:00 | 2.1194 | 2.6245 | 2.6663 | 2.8455 | 2.7738 | 2.953 | 1.2203 | 1.8485 | 2.2008 | 2.2008 | 2.4356 | 2.4356 | 2019-10-01 17:00 | 2.0501 | 3.3597 | 5.5149 | 5.5149 | 5.5149 | 5.5149
2021-08-04 05:00 | 2.7321 | 3.3833 | 3.4372 | 3.6682 | 3.5758 | 3.8067 | 1.4338 | 2.1719 | 2.5858 | 2.5858 | 2.8617 | 2.8617 | 2019-10-01 18:00 | 2.0119 | 3.2972 | 5.4124 | 5.4124 | 5.4124 | 5.4124
2021-08-04 06:00 | 3.9782 | 4.9263 | 5.0048 | 5.3411 | 5.2066 | 5.5429 | 1.8948 | 2.8702 | 3.4171 | 3.4171 | 3.7818 | 3.7818 | 2019-10-01 19:00 | 1.9738 | 3.2348 | 5.3099 | 5.3099 | 5.3099 | 5.3099
2021-08-04 07:00 | 4.4183 | 5.4713 | 5.5585 | 5.932 | 5.7826 | 6.1561 | 2.1548 | 3.2642 | 3.8862 | 3.8862 | 4.3008 | 4.3008 | 2019-10-01 20:00 | 1.8519 | 3.0349 | 4.9819 | 4.9819 | 4.9819 | 4.9819
2021-08-04 08:00 | 4.3468 | 5.3829 | 5.4686 | 5.8361 | 5.6891 | 6.0565 | 2.1205 | 3.2122 | 3.8243 | 3.8243 | 4.2324 | 4.2324 | 2019-10-01 21:00 | 1.7376 | 2.8476 | 4.6744 | 4.6744 | 4.6744 | 4.6744
2021-08-04 09:00 | 4.0039 | 4.9582 | 5.0372 | 5.3756 | 5.2402 | 5.5787 | 1.9005 | 2.8789 | 3.4275 | 3.4275 | 3.7932 | 3.7932 | 2019-10-01 22:00 | 1.6309 | 2.6727 | 4.3873 | 4.3873 | 4.3873 | 4.3873
2021-08-04 10:00 | 3.8353 | 4.7494 | 4.825 | 5.1492 | 5.0196 | 5.3438 | 1.9176 | 2.9048 | 3.4584 | 3.4584 | 3.8274 | 3.8274 | 2019-10-01 23:00 | 1.5166 | 2.4854 | 4.0798 | 4.0798 | 4.0798 | 4.0798
2021-08-04 11:00 | 3.5009 | 4.3353 | 4.4044 | 4.7003 | 4.5819 | 4.8779 | 1.8691 | 2.8313 | 3.3708 | 3.3708 | 3.7304 | 3.7304 | 2019-10-02 | 1.3718 | 2.2481 | 3.6903 | 3.6903 | 3.6903 | 3.6903
2021-08-04 12:00 | 3.2751 | 4.0557 | 4.1203 | 4.3972 | 4.2864 | 4.5633 | 1.829 | 2.7706 | 3.2986 | 3.2986 | 3.6506 | 3.6506 | 2019-10-02 01:00 | 1.2575 | 2.0608 | 3.3828 | 3.3828 | 3.3828 | 3.3828
2021-08-04 13:00 | 3.2351 | 4.0062 | 4.07 | 4.3435 | 4.2341 | 4.5075 | 1.8405 | 2.788 | 3.3192 | 3.3192 | 3.6734 | 3.6734 | 2019-10-02 02:00 | 1.2194 | 1.9983 | 3.2802 | 3.2802 | 3.2802 | 3.2802
2021-08-04 14:00 | 3.4923 | 4.3247 | 4.3936 | 4.6888 | 4.5707 | 4.8659 | 1.9091 | 2.8919 | 3.4429 | 3.4429 | 3.8103 | 3.8103 | 2019-10-02 03:00 | 1.2041 | 1.9733 | 3.2392 | 3.2392 | 3.2392 | 3.2392
2021-08-04 15:00 | 3.398 | 4.2079 | 4.2749 | 4.5622 | 4.4473 | 4.7345 | 1.789 | 2.71 | 3.2264 | 3.2264 | 3.5707 | 3.5707 | 2019-10-02 04:00 | 1.2194 | 1.9983 | 3.2802 | 3.2802 | 3.2802 | 3.2802
2021-08-04 16:00 | 3.7027 | 4.5852 | 4.6582 | 4.9712 | 4.846 | 5.159 | 2.0577 | 3.117 | 3.7109 | 3.7109 | 4.1069 | 4.1069 | 2019-10-02 05:00 | 1.387 | 2.2731 | 3.7313 | 3.7313 | 3.7313 | 3.7313
2021-08-04 17:00 | 4.3169 | 5.3458 | 5.4309 | 5.7958 | 5.6499 | 6.0148 | 2.6092 | 3.9525 | 4.7057 | 4.7057 | 5.2078 | 5.2078 | 2019-10-02 06:00 | 1.5471 | 2.5353 | 4.1618 | 4.1618 | 4.1618 | 4.1618
2021-08-04 18:00 | 4.5212 | 5.5987 | 5.6879 | 6.0701 | 5.9172 | 6.2994 | 2.7407 | 4.1516 | 4.9428 | 4.9428 | 5.4702 | 5.4702 | 2019-10-02 07:00 | 1.9891 | 3.2597 | 5.3509 | 5.3509 | 5.3509 | 5.3509
2021-08-04 19:00 | 4.3808 | 5.4249 | 5.5113 | 5.8816 | 5.7335 | 6.1038 | 2.7636 | 4.1863 | 4.984 | 4.984 | 5.5158 | 5.5158 | 2019-10-02 08:00 | 2.0043 | 3.2847 | 5.3919 | 5.3919 | 5.3919 | 5.3919
2021-08-04 20:00 | 3.8958 | 4.8244 | 4.9012 | 5.2305 | 5.0988 | 5.4281 | 2.6407 | 4.0001 | 4.7624 | 4.7624 | 5.2705 | 5.2705 | 2019-10-02 09:00 | 1.9815 | 3.2472 | 5.3304 | 5.3304 | 5.3304 | 5.3304
2021-08-04 21:00 | 3.6695 | 4.5441 | 4.6165 | 4.9267 | 4.8026 | 5.1128 | 2.3949 | 3.6278 | 4.3191 | 4.3191 | 4.78 | 4.78 | 2019-10-02 10:00 | 2.0958 | 3.4346 | 5.6379 | 5.6379 | 5.6379 | 5.6379
2021-08-04 22:00 | 3.0579 | 3.7868 | 3.8471 | 4.1056 | 4.0022 | 4.2607 | 2.1295 | 3.2258 | 3.8405 | 3.8405 | 4.2502 | 4.2502 | 2019-10-02 11:00 | 2.1796 | 3.572 | 5.8634 | 5.8634 | 5.8634 | 5.8634
2021-08-04 23:00 | 2.6656 | 3.301 | 3.3536 | 3.5789 | 3.4888 | 3.7141 | 1.7947 | 2.7187 | 3.2368 | 3.2368 | 3.5821 | 3.5821 | 2019-10-02 12:00 | 2.1796 | 3.572 | 5.8634 | 5.8634 | 5.8634 | 5.8634
2021-08-05 | 2.2634 | 2.8029 | 2.8476 | 3.0389 | 2.9624 | 3.1537 | 1.4975 | 2.2685 | 2.7007 | 2.7007 | 2.9889 | 2.9889 | 2019-10-02 13:00 | 2.111 | 3.4596 | 5.6789 | 5.6789 | 5.6789 | 5.6789
2021-08-05 01:00 | 2.1063 | 2.6083 | 2.6498 | 2.8279 | 2.7566 | 2.9347 | 1.2746 | 1.9308 | 2.2987 | 2.2987 | 2.544 | 2.544 | 2019-10-02 14:00 | 2.1263 | 3.4845 | 5.7199 | 5.7199 | 5.7199 | 5.7199
2021-08-05 02:00 | 2.0062 | 2.4844 | 2.524 | 2.6936 | 2.6257 | 2.7953 | 1.1661 | 1.7665 | 2.1031 | 2.1031 | 2.3275 | 2.3275 | 2019-10-02 15:00 | 2.1949 | 3.597 | 5.9044 | 5.9044 | 5.9044 | 5.9044
2021-08-05 03:00 | 1.9491 | 2.4136 | 2.4521 | 2.6168 | 2.5509 | 2.7157 | 1.1231 | 1.7012 | 2.0254 | 2.0254 | 2.2415 | 2.2415 | 2019-10-02 16:00 | 2.2253 | 3.6469 | 5.9865 | 5.9865 | 5.9865 | 5.9865
2021-08-05 04:00 | 2.0889 | 2.5868 | 2.628 | 2.8046 | 2.7339 | 2.9105 | 1.206 | 1.8269 | 2.175 | 2.175 | 2.4071 | 2.4071 | 2019-10-02 17:00 | 2.0348 | 3.3347 | 5.4739 | 5.4739 | 5.4739 | 5.4739
2021-08-05 05:00 | 2.5635 | 3.1745 | 3.2251 | 3.4418 | 3.3551 | 3.5718 | 1.3373 | 2.0258 | 2.4119 | 2.4119 | 2.6692 | 2.6692 | 2019-10-02 18:00 | 2.0119 | 3.2972 | 5.4124 | 5.4124 | 5.4124 | 5.4124
2021-08-05 06:00 | 3.9782 | 4.9263 | 5.0048 | 5.3411 | 5.2066 | 5.5429 | 1.6147 | 2.446 | 2.912 | 2.912 | 3.2228 | 3.2228 | 2019-10-02 19:00 | 2.0729 | 3.3971 | 5.5764 | 5.5764 | 5.5764 | 5.5764
2021-08-05 07:00 | 4.4183 | 5.4713 | 5.5585 | 5.932 | 5.7826 | 6.1561 | 2.152 | 3.2598 | 3.881 | 3.881 | 4.2951 | 4.2951 | 2019-10-02 20:00 | 1.7757 | 2.91 | 4.7769 | 4.7769 | 4.7769 | 4.7769
2021-08-05 08:00 | 4.3468 | 5.3829 | 5.4686 | 5.8361 | 5.6891 | 6.0565 | 2.0205 | 3.0607 | 3.6439 | 3.6439 | 4.0327 | 4.0327 | 2019-10-02 21:00 | 1.73 | 2.8351 | 4.6538 | 4.6538 | 4.6538 | 4.6538
2021-08-05 09:00 | 4.0039 | 4.9582 | 5.0372 | 5.3756 | 5.2402 | 5.5787 | 1.8433 | 2.7923 | 3.3244 | 3.3244 | 3.6791 | 3.6791 | 2019-10-02 22:00 | 1.5394 | 2.5229 | 4.1413 | 4.1413 | 4.1413 | 4.1413
2021-08-05 10:00 | 2.2017 | 2.7264 | 2.7699 | 2.956 | 2.8815 | 3.0677 | 1.8148 | 2.749 | 3.2728 | 3.2728 | 3.6221 | 3.6221 | 2019-10-02 23:00 | 1.4556 | 2.3855 | 3.9158 | 3.9158 | 3.9158 | 3.9158
2021-08-05 11:00 | 3.4952 | 4.3282 | 4.3972 | 4.6926 | 4.5744 | 4.8699 | 1.7833 | 2.7014 | 3.2161 | 3.2161 | 3.5593 | 3.5593 | 2019-10-03 | 1.2651 | 2.0732 | 3.4033 | 3.4033 | 3.4033 | 3.4033
2021-08-05 12:00 | 3.0179 | 3.7372 | 3.7967 | 4.0519 | 3.9498 | 4.2049 | 1.7262 | 2.6148 | 3.1131 | 3.1131 | 3.4452 | 3.4452 | 2019-10-03 01:00 | 1.2727 | 2.0857 | 3.4238 | 3.4238 | 3.4238 | 3.4238
2021-08-05 13:00 | 2.895 | 3.585 | 3.6421 | 3.8869 | 3.789 | 4.0337 | 1.7004 | 2.5758 | 3.0667 | 3.0667 | 3.3939 | 3.3939 | 2019-10-03 02:00 | 1.2117 | 1.9858 | 3.2597 | 3.2597 | 3.2597 | 3.2597
2021-08-05 14:00 | 2.8693 | 3.5532 | 3.6098 | 3.8523 | 3.7553 | 3.9979 | 1.6376 | 2.4806 | 2.9533 | 2.9533 | 3.2684 | 3.2684 | 2019-10-03 03:00 | 1.2498 | 2.0483 | 3.3622 | 3.3622 | 3.3622 | 3.3622
2021-08-05 15:00 | 3.3351 | 4.13 | 4.1958 | 4.4778 | 4.365 | 4.6469 | 1.6776 | 2.5412 | 3.0254 | 3.0254 | 3.3483 | 3.3483 | 2019-10-03 04:00 | 1.2575 | 2.0608 | 3.3828 | 3.3828 | 3.3828 | 3.3828
2021-08-05 16:00 | 3.2008 | 3.9637 | 4.0268 | 4.2974 | 4.1892 | 4.4598 | 1.9091 | 2.8919 | 3.4429 | 3.4429 | 3.8103 | 3.8103 | 2019-10-03 05:00 | 1.3642 | 2.2356 | 3.6698 | 3.6698 | 3.6698 | 3.6698
2021-08-05 17:00 | 4.0067 | 4.9617 | 5.0408 | 5.3795 | 5.244 | 5.5827 | 2.3463 | 3.5542 | 4.2315 | 4.2315 | 4.683 | 4.683 | 2019-10-03 06:00 | 1.5699 | 2.5728 | 4.2233 | 4.2233 | 4.2233 | 4.2233
2021-08-05 18:00 | 4.1325 | 5.1174 | 5.1989 | 5.5483 | 5.4085 | 5.7579 | 2.4864 | 3.7663 | 4.484 | 4.484 | 4.9625 | 4.9625 | 2019-10-03 07:00 | 1.8671 | 3.0599 | 5.0229 | 5.0229 | 5.0229 | 5.0229
2021-08-05 19:00 | 4.0278 | 4.9878 | 5.0672 | 5.4077 | 5.2715 | 5.612 | 2.6178 | 3.9655 | 4.7211 | 4.7211 | 5.2249 | 5.2249 | 2019-10-03 08:00 | 2.0805 | 3.4096 | 5.5969 | 5.5969 | 5.5969 | 5.5969
2021-08-05 20:00 | 3.721 | 4.6078 | 4.6812 | 4.9958 | 4.8699 | 5.1845 | 2.4806 | 3.7577 | 4.4737 | 4.4737 | 4.9511 | 4.9511 | 2019-10-03 09:00 | 2.172 | 3.5595 | 5.8429 | 5.8429 | 5.8429 | 5.8429
2021-08-05 21:00 | 3.3894 | 4.1973 | 4.2641 | 4.5507 | 4.4361 | 4.7226 | 2.3045 | 3.4909 | 4.1561 | 4.1561 | 4.5995 | 4.5995 | 2019-10-03 10:00 | 2.3168 | 3.7968 | 6.2325 | 6.2325 | 6.2325 | 6.2325
2021-08-05 22:00 | 2.8893 | 3.578 | 3.6349 | 3.8792 | 3.7815 | 4.0257 | 2.0366 | 3.085 | 3.6729 | 3.6729 | 4.0648 | 4.0648 | 2019-10-03 11:00 | 2.2482 | 3.6844 | 6.048 | 6.048 | 6.048 | 6.048
2021-08-05 23:00 | 2.5379 | 3.1428 | 3.1929 | 3.4074 | 3.3216 | 3.5361 | 1.7004 | 2.5758 | 3.0667 | 3.0667 | 3.3939 | 3.3939 | 2019-10-03 12:00 | 2.5226 | 4.134 | 6.786 | 6.786 | 6.786 | 6.786
2021-08-06 | 2.292 | 2.8383 | 2.8835 | 3.0773 | 2.9998 | 3.1935 | 1.5175 | 2.2988 | 2.7368 | 2.7368 | 3.0288 | 3.0288 | 2019-10-03 13:00 | 2.6674 | 4.3713 | 7.1755 | 7.1755 | 7.1755 | 7.1755
2021-08-06 01:00 | 2.0748 | 2.5693 | 2.6103 | 2.7856 | 2.7155 | 2.8909 | 1.2317 | 1.8659 | 2.2214 | 2.2214 | 2.4584 | 2.4584 | 2019-10-03 14:00 | 2.6826 | 4.3963 | 7.2165 | 7.2165 | 7.2165 | 7.2165
2021-08-06 02:00 | 1.9977 | 2.4738 | 2.5132 | 2.682 | 2.6145 | 2.7834 | 1.206 | 1.8269 | 2.175 | 2.175 | 2.4071 | 2.4071 | 2019-10-03 15:00 | 2.675 | 4.3838 | 7.196 | 7.196 | 7.196 | 7.196
2021-08-06 03:00 | 2.0805 | 2.5764 | 2.6174 | 2.7933 | 2.723 | 2.8988 | 1.1546 | 1.749 | 2.0822 | 2.0822 | 2.3044 | 2.3044 | 2019-10-03 16:00 | 2.6292 | 4.3088 | 7.073 | 7.073 | 7.073 | 7.073
2021-08-06 04:00 | 2.1234 | 2.6295 | 2.6714 | 2.8509 | 2.7791 | 2.9586 | 1.1774 | 1.7836 | 2.1235 | 2.1235 | 2.3501 | 2.3501 | 2019-10-03 17:00 | 2.3778 | 3.8967 | 6.3965 | 6.3965 | 6.3965 | 6.3965
2021-08-06 05:00 | 2.6171 | 3.2409 | 3.2925 | 3.5137 | 3.4252 | 3.6465 | 1.3146 | 1.9914 | 2.3709 | 2.3709 | 2.6238 | 2.6238 | 2019-10-03 18:00 | 2.111 | 3.4596 | 5.6789 | 5.6789 | 5.6789 | 5.6789
2021-08-06 06:00 | 3.3723 | 4.1761 | 4.2426 | 4.5276 | 4.4136 | 4.6987 | 1.585 | 2.401 | 2.8585 | 2.8585 | 3.1635 | 3.1635 | 2019-10-03 19:00 | 2.0196 | 3.3097 | 5.4329 | 5.4329 | 5.4329 | 5.4329
2021-08-06 07:00 | 3.9439 | 4.8839 | 4.9617 | 5.295 | 5.1617 | 5.4951 | 1.9691 | 2.9828 | 3.5512 | 3.5512 | 3.9301 | 3.9301 | 2019-10-03 20:00 | 1.89 | 3.0974 | 5.0844 | 5.0844 | 5.0844 | 5.0844
2021-08-06 08:00 | 4.0182 | 4.9759 | 5.0551 | 5.3948 | 5.2589 | 5.5986 | 2.0119 | 3.0477 | 3.6285 | 3.6285 | 4.0156 | 4.0156 | 2019-10-03 21:00 | 1.7376 | 2.8476 | 4.6744 | 4.6744 | 4.6744 | 4.6744
2021-08-06 09:00 | 3.4609 | 4.2858 | 4.354 | 4.6466 | 4.5296 | 4.8221 | 1.8005 | 2.7274 | 3.2471 | 3.2471 | 3.5935 | 3.5935 | 2019-10-03 22:00 | 1.5699 | 2.5728 | 4.2233 | 4.2233 | 4.2233 | 4.2233
2021-08-06 10:00 | 3.1865 | 3.946 | 4.0089 | 4.2782 | 4.1705 | 4.4399 | 1.7376 | 2.6321 | 3.1337 | 3.1337 | 3.468 | 3.468 | 2019-10-03 23:00 | 1.448 | 2.373 | 3.8953 | 3.8953 | 3.8953 | 3.8953
2021-08-06 11:00 | 2.8807 | 3.5673 | 3.6242 | 3.8677 | 3.7703 | 4.0138 | 1.7147 | 2.5975 | 3.0924 | 3.0924 | 3.4224 | 3.4224 | 2019-10-04 | 1.2956 | 2.1232 | 3.4853 | 3.4853 | 3.4853 | 3.4853
2021-08-06 12:00 | 2.7064 | 3.3515 | 3.4048 | 3.6336 | 3.5421 | 3.7709 | 1.6661 | 2.5239 | 3.0048 | 3.0048 | 3.3254 | 3.3254 | 2019-10-04 01:00 | 1.2575 | 2.0608 | 3.3828 | 3.3828 | 3.3828 | 3.3828
2021-08-06 13:00 | 2.6693 | 3.3055 | 3.3581 | 3.5837 | 3.4935 | 3.7191 | 1.6433 | 2.4893 | 2.9636 | 2.9636 | 3.2798 | 3.2798 | 2019-10-04 02:00 | 1.2041 | 1.9733 | 3.2392 | 3.2392 | 3.2392 | 3.2392
2021-08-06 14:00 | 2.4892 | 3.0825 | 3.1316 | 3.342 | 3.2578 | 3.4683 | 1.6204 | 2.4546 | 2.9224 | 2.9224 | 3.2342 | 3.2342 | 2019-10-04 03:00 | 1.2422 | 2.0358 | 3.3417 | 3.3417 | 3.3417 | 3.3417
2021-08-06 15:00 | 2.5855 | 3.2018 | 3.2528 | 3.4713 | 3.3839 | 3.6025 | 1.6318 | 2.4719 | 2.943 | 2.943 | 3.257 | 3.257 | 2019-10-04 04:00 | 1.3261 | 2.1732 | 3.5673 | 3.5673 | 3.5673 | 3.5673
2021-08-06 16:00 | 3.0036 | 3.7195 | 3.7788 | 4.0327 | 3.9311 | 4.185 | 1.9283 | 2.921 | 3.4776 | 3.4776 | 3.8487 | 3.8487 | 2019-10-04 05:00 | 1.4023 | 2.2981 | 3.7723 | 3.7723 | 3.7723 | 3.7723
2021-08-06 17:00 | 3.4952 | 4.3282 | 4.3972 | 4.6926 | 4.5744 | 4.8699 | 2.3035 | 3.4893 | 4.1542 | 4.1542 | 4.5974 | 4.5974 | 2019-10-04 06:00 | 1.5394 | 2.5229 | 4.1413 | 4.1413 | 4.1413 | 4.1413
2021-08-06 18:00 | 3.7181 | 4.6043 | 4.6776 | 4.9919 | 4.8662 | 5.1805 | 2.5721 | 3.8962 | 4.6387 | 4.6387 | 5.1336 | 5.1336 | 2019-10-04 07:00 | 1.9053 | 3.1224 | 5.1254 | 5.1254 | 5.1254 | 5.1254
2021-08-06 19:00 | 3.681 | 4.5583 | 4.6309 | 4.942 | 4.8176 | 5.1287 | 2.6235 | 3.9741 | 4.7314 | 4.7314 | 5.2363 | 5.2363 | 2019-10-04 08:00 | 2.1186 | 3.4721 | 5.6994 | 5.6994 | 5.6994 | 5.6994
2021-08-06 20:00 | 3.2751 | 4.0557 | 4.1203 | 4.3972 | 4.2864 | 4.5633 | 2.4835 | 3.762 | 4.4789 | 4.4789 | 4.9568 | 4.9568 | 2019-10-04 09:00 | 2.1872 | 3.5845 | 5.8839 | 5.8839 | 5.8839 | 5.8839
2021-08-06 21:00 | 3.153 | 3.9045 | 3.9667 | 4.2332 | 4.1266 | 4.3932 | 2.4263 | 3.6754 | 4.3758 | 4.3758 | 4.8427 | 4.8427 | 2019-10-04 10:00 | 2.4006 | 3.9342 | 6.458 | 6.458 | 6.458 | 6.458
2021-08-06 22:00 | 2.6407 | 3.2701 | 3.3221 | 3.5454 | 3.4561 | 3.6793 | 2.1205 | 3.2122 | 3.8243 | 3.8243 | 4.2324 | 4.2324 | 2019-10-04 11:00 | 2.5073 | 4.109 | 6.745 | 6.745 | 6.745 | 6.745
2021-08-06 23:00 | 2.5035 | 3.1002 | 3.1496 | 3.3612 | 3.2765 | 3.4882 | 1.8319 | 2.775 | 3.3038 | 3.3038 | 3.6563 | 3.6563 | 2019-10-04 12:00 | 2.5683 | 4.2089 | 6.909 | 6.909 | 6.909 | 6.909
2021-08-07 | 2.1612 | 2.6763 | 2.719 | 2.9016 | 2.8286 | 3.0113 | 1.5238 | 2.3082 | 2.7481 | 2.7481 | 3.0413 | 3.0413 | 2019-10-04 13:00 | 2.5988 | 4.2589 | 6.991 | 6.991 | 6.991 | 6.991
2021-08-07 01:00 | 1.9662 | 2.4349 | 2.4736 | 2.6398 | 2.5734 | 2.7396 | 1.3034 | 1.9744 | 2.3506 | 2.3506 | 2.6014 | 2.6014 | 2019-10-04 14:00 | 2.5911 | 4.2464 | 6.9705 | 6.9705 | 6.9705 | 6.9705
2021-08-07 02:00 | 1.9462 | 2.4101 | 2.4485 | 2.613 | 2.5472 | 2.7117 | 1.155 | 1.7496 | 2.083 | 2.083 | 2.3052 | 2.3052 | 2019-10-04 15:00 | 2.5302 | 4.1465 | 6.8065 | 6.8065 | 6.8065 | 6.8065
2021-08-07 03:00 | 1.9491 | 2.4136 | 2.4521 | 2.6168 | 2.5509 | 2.7157 | 1.1917 | 1.8052 | 2.1492 | 2.1492 | 2.3786 | 2.3786 | 2019-10-04 16:00 | 2.2558 | 3.6969 | 6.0685 | 6.0685 | 6.0685 | 6.0685
2021-08-07 04:00 | 2.0777 | 2.5729 | 2.6139 | 2.7895 | 2.7192 | 2.8949 | 1.166 | 1.7663 | 2.1029 | 2.1029 | 2.3272 | 2.3272 | 2019-10-04 17:00 | 2.0958 | 3.4346 | 5.6379 | 5.6379 | 5.6379 | 5.6379
2021-08-07 05:00 | 2.1976 | 2.7214 | 2.7647 | 2.9505 | 2.8762 | 3.062 | 1.2113 | 1.8349 | 2.1846 | 2.1846 | 2.4177 | 2.4177 | 2019-10-04 18:00 | 2.1796 | 3.572 | 5.8634 | 5.8634 | 5.8634 | 5.8634
2021-08-07 06:00 | 2.6127 | 3.2354 | 3.2869 | 3.5078 | 3.4195 | 3.6403 | 1.5118 | 2.2901 | 2.7265 | 2.7265 | 3.0174 | 3.0174 | 2019-10-04 19:00 | 1.9434 | 3.1848 | 5.2279 | 5.2279 | 5.2279 | 5.2279
2021-08-07 07:00 | 3.0036 | 3.7195 | 3.7788 | 4.0327 | 3.9311 | 4.185 | 1.7547 | 2.6581 | 3.1646 | 3.1646 | 3.5023 | 3.5023 | 2019-10-04 20:00 | 1.6919 | 2.7726 | 4.5513 | 4.5513 | 4.5513 | 4.5513
2021-08-07 08:00 | 3.0722 | 3.8045 | 3.8651 | 4.1248 | 4.0209 | 4.2806 | 1.9091 | 2.8919 | 3.4429 | 3.4429 | 3.8103 | 3.8103 | 2019-10-04 21:00 | 1.5699 | 2.5728 | 4.2233 | 4.2233 | 4.2233 | 4.2233
2021-08-07 09:00 | 2.9379 | 3.6381 | 3.6961 | 3.9444 | 3.8451 | 4.0934 | 1.9662 | 2.9784 | 3.546 | 3.546 | 3.9244 | 3.9244 | 2019-10-04 22:00 | 1.4709 | 2.4105 | 3.9568 | 3.9568 | 3.9568 | 3.9568
2021-08-07 10:00 | 2.6721 | 3.309 | 3.3617 | 3.5876 | 3.4972 | 3.7231 | 2.0548 | 3.1126 | 3.7058 | 3.7058 | 4.1012 | 4.1012 | 2019-10-04 23:00 | 1.387 | 2.2731 | 3.7313 | 3.7313 | 3.7313 | 3.7313
2021-08-07 11:00 | 2.4949 | 3.0896 | 3.1388 | 3.3497 | 3.2653 | 3.4762 | 2.0977 | 3.1776 | 3.7831 | 3.7831 | 4.1867 | 4.1867 | 2019-10-05 | 1.3413 | 2.1981 | 3.6083 | 3.6083 | 3.6083 | 3.6083
2021-08-07 12:00 | 2.2349 | 2.7675 | 2.8116 | 3.0005 | 2.925 | 3.1139 | 2.0091 | 3.0434 | 3.6233 | 3.6233 | 4.0099 | 4.0099 | 2019-10-05 01:00 | 1.2956 | 2.1232 | 3.4853 | 3.4853 | 3.4853 | 3.4853
2021-08-07 13:00 | 2.152 | 2.6649 | 2.7073 | 2.8892 | 2.8165 | 2.9984 | 2.0119 | 3.0477 | 3.6285 | 3.6285 | 4.0156 | 4.0156 | 2019-10-05 02:00 | 1.2727 | 2.0857 | 3.4238 | 3.4238 | 3.4238 | 3.4238
2021-08-07 14:00 | 2.2149 | 2.7427 | 2.7864 | 2.9737 | 2.8988 | 3.086 | 1.9033 | 2.8832 | 3.4326 | 3.4326 | 3.7989 | 3.7989 | 2019-10-05 03:00 | 1.227 | 2.0108 | 3.3007 | 3.3007 | 3.3007 | 3.3007
2021-08-07 15:00 | 2.3206 | 2.8737 | 2.9195 | 3.1156 | 3.0372 | 3.2333 | 2.0062 | 3.0391 | 3.6182 | 3.6182 | 4.0042 | 4.0042 | 2019-10-05 04:00 | 1.3032 | 2.1357 | 3.5058 | 3.5058 | 3.5058 | 3.5058
2021-08-07 16:00 | 2.7293 | 3.3798 | 3.4336 | 3.6643 | 3.572 | 3.8027 | 2.1263 | 3.2209 | 3.8346 | 3.8346 | 4.2438 | 4.2438 | 2019-10-05 05:00 | 1.4251 | 2.3355 | 3.8338 | 3.8338 | 3.8338 | 3.8338
2021-08-07 17:00 | 3.2694 | 4.0486 | 4.1131 | 4.3895 | 4.279 | 4.5553 | 2.4178 | 3.6624 | 4.3603 | 4.3603 | 4.8256 | 4.8256 | 2019-10-05 06:00 | 1.4556 | 2.3855 | 3.9158 | 3.9158 | 3.9158 | 3.9158
2021-08-07 18:00 | 3.3809 | 4.1867 | 4.2534 | 4.5392 | 4.4248 | 4.7106 | 2.5921 | 3.9265 | 4.6747 | 4.6747 | 5.1735 | 5.1735 | 2019-10-05 07:00 | 1.6309 | 2.6727 | 4.3873 | 4.3873 | 4.3873 | 4.3873
2021-08-07 19:00 | 3.2621 | 4.0396 | 4.104 | 4.3797 | 4.2694 | 4.5452 | 2.5635 | 3.8832 | 4.6232 | 4.6232 | 5.1165 | 5.1165 | 2019-10-05 08:00 | 1.7681 | 2.8975 | 4.7564 | 4.7564 | 4.7564 | 4.7564
2021-08-07 20:00 | 2.9979 | 3.7124 | 3.7716 | 4.025 | 3.9236 | 4.177 | 2.4892 | 3.7707 | 4.4892 | 4.4892 | 4.9682 | 4.9682 | 2019-10-05 09:00 | 1.7757 | 2.91 | 4.7769 | 4.7769 | 4.7769 | 4.7769
2021-08-07 21:00 | 2.8979 | 3.5886 | 3.6457 | 3.8907 | 3.7927 | 4.0377 | 2.3349 | 3.5369 | 4.2109 | 4.2109 | 4.6602 | 4.6602 | 2019-10-05 10:00 | 1.9205 | 3.1473 | 5.1664 | 5.1664 | 5.1664 | 5.1664
2021-08-07 22:00 | 2.7836 | 3.447 | 3.5019 | 3.7372 | 3.6431 | 3.8784 | 2.0863 | 3.1603 | 3.7625 | 3.7625 | 4.1639 | 4.1639 | 2019-10-05 11:00 | 1.9662 | 3.2223 | 5.2894 | 5.2894 | 5.2894 | 5.2894
2021-08-07 23:00 | 2.5892 | 3.2064 | 3.2574 | 3.4763 | 3.3888 | 3.6076 | 1.795 | 2.719 | 3.2371 | 3.2371 | 3.5826 | 3.5826 | 2019-10-05 12:00 | 1.9129 | 3.1348 | 5.1459 | 5.1459 | 5.1459 | 5.1459
2021-08-08 | 2.2834 | 2.8277 | 2.8727 | 3.0657 | 2.9885 | 3.1816 | 1.5749 | 2.3857 | 2.8403 | 2.8403 | 3.1433 | 3.1433 | 2019-10-05 13:00 | 1.9129 | 3.1348 | 5.1459 | 5.1459 | 5.1459 | 5.1459
2021-08-08 01:00 | 2.0977 | 2.5976 | 2.639 | 2.8163 | 2.7454 | 2.9227 | 1.3487 | 2.043 | 2.4323 | 2.4323 | 2.6918 | 2.6918 | 2019-10-05 14:00 | 1.9205 | 3.1473 | 5.1664 | 5.1664 | 5.1664 | 5.1664
2021-08-08 02:00 | 2.0834 | 2.58 | 2.621 | 2.7972 | 2.7267 | 2.9028 | 1.2354 | 1.8714 | 2.228 | 2.228 | 2.4658 | 2.4658 | 2019-10-05 15:00 | 1.9053 | 3.1224 | 5.1254 | 5.1254 | 5.1254 | 5.1254
2021-08-08 03:00 | 2.0175 | 2.4983 | 2.5381 | 2.7087 | 2.6405 | 2.811 | 1.2403 | 1.8788 | 2.2369 | 2.2369 | 2.4755 | 2.4755 | 2019-10-05 16:00 | 1.9662 | 3.2223 | 5.2894 | 5.2894 | 5.2894 | 5.2894
2021-08-08 04:00 | 2.1293 | 2.6368 | 2.6788 | 2.8588 | 2.7868 | 2.9667 | 1.2117 | 1.8356 | 2.1853 | 2.1853 | 2.4185 | 2.4185 | 2019-10-05 17:00 | 1.8519 | 3.0349 | 4.9819 | 4.9819 | 4.9819 | 4.9819
2021-08-08 05:00 | 2.2777 | 2.8206 | 2.8655 | 3.0581 | 2.9811 | 3.1736 | 1.2231 | 1.8528 | 2.2059 | 2.2059 | 2.4413 | 2.4413 | 2019-10-05 18:00 | 1.8062 | 2.96 | 4.8589 | 4.8589 | 4.8589 | 4.8589
2021-08-08 06:00 | 2.4606 | 3.0471 | 3.0956 | 3.3036 | 3.2204 | 3.4284 | 1.4089 | 2.1343 | 2.541 | 2.541 | 2.8121 | 2.8121 | 2019-10-05 19:00 | 1.7147 | 2.8101 | 4.6128 | 4.6128 | 4.6128 | 4.6128
2021-08-08 07:00 | 2.7768 | 3.4386 | 3.4934 | 3.7281 | 3.6342 | 3.8689 | 1.6233 | 2.4589 | 2.9275 | 2.9275 | 3.2399 | 3.2399 | 2019-10-05 20:00 | 1.6004 | 2.6228 | 4.3053 | 4.3053 | 4.3053 | 4.3053
2021-08-08 08:00 | 2.9007 | 3.592 | 3.6492 | 3.8944 | 3.7964 | 4.0416 | 1.9634 | 2.9741 | 3.5408 | 3.5408 | 3.9187 | 3.9187 | 2019-10-05 21:00 | 1.5547 | 2.5478 | 4.1823 | 4.1823 | 4.1823 | 4.1823
2021-08-08 09:00 | 3.0151 | 3.7337 | 3.7931 | 4.048 | 3.9461 | 4.2009 | 2.0291 | 3.0737 | 3.6594 | 3.6594 | 4.0499 | 4.0499 | 2019-10-05 22:00 | 1.509 | 2.4729 | 4.0593 | 4.0593 | 4.0593 | 4.0593
2021-08-08 10:00 | 3.0779 | 3.8115 | 3.8722 | 4.1324 | 4.0284 | 4.2885 | 2.2034 | 3.3378 | 3.9738 | 3.9738 | 4.3978 | 4.3978 | 2019-10-05 23:00 | 1.4251 | 2.3355 | 3.8338 | 3.8338 | 3.8338 | 3.8338
2021-08-08 11:00 | 3.0551 | 3.7832 | 3.8435 | 4.1017 | 3.9984 | 4.2567 | 2.212 | 3.3508 | 3.9892 | 3.9892 | 4.4149 | 4.4149 | 2019-10-06 | 1.3489 | 2.2106 | 3.6288 | 3.6288 | 3.6288 | 3.6288
2021-08-08 12:00 | 3.0636 | 3.7938 | 3.8543 | 4.1132 | 4.0097 | 4.2686 | 2.3778 | 3.6018 | 4.2882 | 4.2882 | 4.7457 | 4.7457 | 2019-10-06 01:00 | 1.227 | 2.0108 | 3.3007 | 3.3007 | 3.3007 | 3.3007
2021-08-08 13:00 | 2.9693 | 3.6771 | 3.7356 | 3.9866 | 3.8862 | 4.1372 | 2.4378 | 3.6928 | 4.3964 | 4.3964 | 4.8655 | 4.8655 | 2019-10-06 03:00 | 1.227 | 2.0108 | 3.3007 | 3.3007 | 3.3007 | 3.3007
2021-08-08 14:00 | 2.8688 | 3.5526 | 3.6092 | 3.8517 | 3.7547 | 3.9972 | 2.2616 | 3.4259 | 4.0787 | 4.0787 | 4.5139 | 4.5139 | 2019-10-06 04:00 | 1.2727 | 2.0857 | 3.4238 | 3.4238 | 3.4238 | 3.4238
2021-08-08 15:00 | 2.8293 | 3.5036 | 3.5594 | 3.7986 | 3.7029 | 3.9421 | 2.1606 | 3.2728 | 3.8965 | 3.8965 | 4.3122 | 4.3122 | 2019-10-06 05:00 | 1.3108 | 2.1482 | 3.5263 | 3.5263 | 3.5263 | 3.5263
2021-08-08 16:00 | 3.1008 | 3.8398 | 3.901 | 4.1631 | 4.0583 | 4.3204 | 2.372 | 3.5932 | 4.2779 | 4.2779 | 4.7343 | 4.7343 | 2019-10-06 06:00 | 1.4327 | 2.348 | 3.8543 | 3.8543 | 3.8543 | 3.8543
2021-08-08 17:00 | 3.4295 | 4.2468 | 4.3145 | 4.6044 | 4.4884 | 4.7783 | 2.6607 | 4.0304 | 4.7984 | 4.7984 | 5.3104 | 5.3104 | 2019-10-06 07:00 | 1.5623 | 2.5603 | 4.2028 | 4.2028 | 4.2028 | 4.2028
2021-08-08 18:00 | 3.498 | 4.3318 | 4.4008 | 4.6965 | 4.5782 | 4.8739 | 2.695 | 4.0824 | 4.8603 | 4.8603 | 5.3789 | 5.3789 | 2019-10-06 08:00 | 1.7986 | 2.9475 | 4.8384 | 4.8384 | 4.8384 | 4.8384
2021-08-08 19:00 | 3.3837 | 4.1902 | 4.257 | 4.543 | 4.4286 | 4.7146 | 2.6529 | 4.0186 | 4.7844 | 4.7844 | 5.2949 | 5.2949 | 2019-10-06 09:00 | 1.8519 | 3.0349 | 4.9819 | 4.9819 | 4.9819 | 4.9819
2021-08-08 20:00 | 3.2494 | 4.0239 | 4.088 | 4.3627 | 4.2528 | 4.5275 | 2.5235 | 3.8226 | 4.551 | 4.551 | 5.0366 | 5.0366 | 2019-10-06 10:00 | 1.9205 | 3.1473 | 5.1664 | 5.1664 | 5.1664 | 5.1664
2021-08-08 21:00 | 3.0494 | 3.7761 | 3.8363 | 4.0941 | 3.991 | 4.2487 | 2.3122 | 3.5025 | 4.1699 | 4.1699 | 4.6149 | 4.6149 | 2019-10-06 11:00 | 2.0577 | 3.3721 | 5.5354 | 5.5354 | 5.5354 | 5.5354
2021-08-08 22:00 | 2.6321 | 3.2594 | 3.3114 | 3.5339 | 3.4449 | 3.6674 | 2.0394 | 3.0893 | 3.678 | 3.678 | 4.0704 | 4.0704 | 2019-10-06 12:00 | 2.0882 | 3.4221 | 5.6174 | 5.6174 | 5.6174 | 5.6174
2021-08-08 23:00 | 2.4263 | 3.0046 | 3.0525 | 3.2576 | 3.1756 | 3.3807 | 1.7197 | 2.605 | 3.1013 | 3.1013 | 3.4323 | 3.4323 | 2019-10-06 13:00 | 2.0501 | 3.3597 | 5.5149 | 5.5149 | 5.5149 | 5.5149
2021-08-09 | 2.1348 | 2.6437 | 2.6858 | 2.8662 | 2.794 | 2.9745 | 1.3516 | 2.0474 | 2.4376 | 2.4376 | 2.6977 | 2.6977 | 2019-10-06 14:00 | 2.0348 | 3.3347 | 5.4739 | 5.4739 | 5.4739 | 5.4739
2021-08-09 01:00 | 1.9148 | 2.3711 | 2.4089 | 2.5708 | 2.506 | 2.6679 | 1.2146 | 1.8399 | 2.1905 | 2.1905 | 2.4242 | 2.4242 | 2019-10-06 15:00 | 2.0196 | 3.3097 | 5.4329 | 5.4329 | 5.4329 | 5.4329
2021-08-09 02:00 | 1.8891 | 2.3393 | 2.3766 | 2.5362 | 2.4724 | 2.6321 | 1.152 | 1.745 | 2.0775 | 2.0775 | 2.2992 | 2.2992 | 2019-10-06 16:00 | 1.9967 | 3.2722 | 5.3714 | 5.3714 | 5.3714 | 5.3714
2021-08-09 03:00 | 1.8691 | 2.3145 | 2.3514 | 2.5094 | 2.4462 | 2.6042 | 1.106 | 1.6754 | 1.9946 | 1.9946 | 2.2075 | 2.2075 | 2019-10-06 17:00 | 1.9967 | 3.2722 | 5.3714 | 5.3714 | 5.3714 | 5.3714
2021-08-09 04:00 | 2.0455 | 2.533 | 2.5734 | 2.7463 | 2.6771 | 2.85 | 1.1117 | 1.684 | 2.0049 | 2.0049 | 2.2189 | 2.2189 | 2019-10-06 18:00 | 1.8214 | 2.985 | 4.8999 | 4.8999 | 4.8999 | 4.8999
2021-08-09 05:00 | 2.4462 | 3.0292 | 3.0775 | 3.2843 | 3.2016 | 3.4083 | 1.2401 | 1.8785 | 2.2365 | 2.2365 | 2.4751 | 2.4751 | 2019-10-06 19:00 | 1.829 | 2.9975 | 4.9204 | 4.9204 | 4.9204 | 4.9204
2021-08-09 06:00 | 3.5209 | 4.3601 | 4.4295 | 4.7272 | 4.6081 | 4.9057 | 1.5538 | 2.3536 | 2.8021 | 2.8021 | 3.1011 | 3.1011 | 2019-10-06 20:00 | 1.8062 | 2.96 | 4.8589 | 4.8589 | 4.8589 | 4.8589
2021-08-09 07:00 | 3.9382 | 4.8768 | 4.9545 | 5.2874 | 5.1542 | 5.4871 | 2.0977 | 3.1776 | 3.7831 | 3.7831 | 4.1867 | 4.1867 | 2019-10-06 21:00 | 1.7071 | 2.7976 | 4.5923 | 4.5923 | 4.5923 | 4.5923
2021-08-09 08:00 | 3.9839 | 4.9334 | 5.012 | 5.3488 | 5.214 | 5.5508 | 2.1177 | 3.2079 | 3.8192 | 3.8192 | 4.2267 | 4.2267 | 2019-10-06 22:00 | 1.5547 | 2.5478 | 4.1823 | 4.1823 | 4.1823 | 4.1823
2021-08-09 09:00 | 3.801 | 4.7069 | 4.7819 | 5.1032 | 4.9747 | 5.296 | 1.9119 | 2.8962 | 3.4481 | 3.4481 | 3.816 | 3.816 | 2019-10-06 23:00 | 1.4251 | 2.3355 | 3.8338 | 3.8338 | 3.8338 | 3.8338
2021-08-09 10:00 | 3.3409 | 4.1371 | 4.203 | 4.4854 | 4.3725 | 4.6549 | 1.8062 | 2.736 | 3.2574 | 3.2574 | 3.6049 | 3.6049 | 2019-10-07 | 1.3413 | 2.1981 | 3.6083 | 3.6083 | 3.6083 | 3.6083
2021-08-09 11:00 | 2.9722 | 3.6806 | 3.7392 | 3.9905 | 3.89 | 4.1412 | 1.829 | 2.7706 | 3.2986 | 3.2986 | 3.6506 | 3.6506 | 2019-10-07 01:00 | 1.2803 | 2.0982 | 3.4443 | 3.4443 | 3.4443 | 3.4443
2021-08-09 12:00 | 3.0208 | 3.7408 | 3.8003 | 4.0557 | 3.9535 | 4.2089 | 1.749 | 2.6494 | 3.1543 | 3.1543 | 3.4909 | 3.4909 | 2019-10-07 02:00 | 1.2194 | 1.9983 | 3.2802 | 3.2802 | 3.2802 | 3.2802
2021-08-09 13:00 | 2.8607 | 3.5426 | 3.599 | 3.8408 | 3.7441 | 3.9859 | 1.729 | 2.6191 | 3.1182 | 3.1182 | 3.4509 | 3.4509 | 2019-10-07 03:00 | 1.2041 | 1.9733 | 3.2392 | 3.2392 | 3.2392 | 3.2392
2021-08-09 14:00 | 2.7178 | 3.3656 | 3.4192 | 3.649 | 3.5571 | 3.7868 | 1.7119 | 2.5932 | 3.0873 | 3.0873 | 3.4167 | 3.4167 | 2019-10-07 04:00 | 1.2041 | 1.9733 | 3.2392 | 3.2392 | 3.2392 | 3.2392
2021-08-09 15:00 | 2.7464 | 3.401 | 3.4552 | 3.6873 | 3.5945 | 3.8266 | 1.7062 | 2.5845 | 3.077 | 3.077 | 3.4053 | 3.4053 | 2019-10-07 05:00 | 1.3337 | 2.1856 | 3.5878 | 3.5878 | 3.5878 | 3.5878
2021-08-09 16:00 | 3.0579 | 3.7868 | 3.8471 | 4.1056 | 4.0022 | 4.2607 | 1.8605 | 2.8183 | 3.3553 | 3.3553 | 3.7133 | 3.7133 | 2019-10-07 06:00 | 1.4556 | 2.3855 | 3.9158 | 3.9158 | 3.9158 | 3.9158
2021-08-09 17:00 | 3.7267 | 4.6149 | 4.6884 | 5.0034 | 4.8774 | 5.1924 | 2.2463 | 3.4027 | 4.0511 | 4.0511 | 4.4834 | 4.4834 | 2019-10-07 07:00 | 1.5852 | 2.5978 | 4.2643 | 4.2643 | 4.2643 | 4.2643
2021-08-09 18:00 | 3.9182 | 4.852 | 4.9293 | 5.2605 | 5.128 | 5.4592 | 2.4435 | 3.7014 | 4.4067 | 4.4067 | 4.8769 | 4.8769 | 2019-10-07 08:00 | 1.7681 | 2.8975 | 4.7564 | 4.7564 | 4.7564 | 4.7564
2021-08-09 19:00 | 3.7596 | 4.6556 | 4.7298 | 5.0476 | 4.9205 | 5.2383 | 2.4263 | 3.6754 | 4.3758 | 4.3758 | 4.8427 | 4.8427 | 2019-10-07 09:00 | 1.8443 | 3.0224 | 4.9614 | 4.9614 | 4.9614 | 4.9614
2021-08-09 20:00 | 3.6381 | 4.5052 | 4.5769 | 4.8845 | 4.7615 | 5.069 | 2.3635 | 3.5802 | 4.2624 | 4.2624 | 4.7172 | 4.7172 | 2019-10-07 10:00 | 1.8748 | 3.0724 | 5.0434 | 5.0434 | 5.0434 | 5.0434
2021-08-09 21:00 | 3.338 | 4.1336 | 4.1994 | 4.4816 | 4.3687 | 4.6509 | 2.2549 | 3.4157 | 4.0666 | 4.0666 | 4.5005 | 4.5005 | 2019-10-07 11:00 | 1.8671 | 3.0599 | 5.0229 | 5.0229 | 5.0229 | 5.0229
2021-08-09 22:00 | 2.9236 | 3.6204 | 3.6781 | 3.9252 | 3.8264 | 4.0735 | 1.9805 | 3.0001 | 3.5718 | 3.5718 | 3.9529 | 3.9529 | 2019-10-07 12:00 | 2.0501 | 3.3597 | 5.5149 | 5.5149 | 5.5149 | 5.5149
2021-08-09 23:00 | 2.4497 | 3.0336 | 3.0819 | 3.289 | 3.2062 | 3.4133 | 1.6576 | 2.5109 | 2.9894 | 2.9894 | 3.3083 | 3.3083 | 2019-10-07 13:00 | 2.0196 | 3.3097 | 5.4329 | 5.4329 | 5.4329 | 5.4329
2021-08-10 | 2.1777 | 2.6967 | 2.7397 | 2.9238 | 2.8501 | 3.0342 | 1.3295 | 2.014 | 2.3978 | 2.3978 | 2.6536 | 2.6536 | 2019-10-07 14:00 | 1.9662 | 3.2223 | 5.2894 | 5.2894 | 5.2894 | 5.2894
2021-08-10 01:00 | 1.9919 | 2.4667 | 2.506 | 2.6744 | 2.607 | 2.7754 | 1.126 | 1.7057 | 2.0307 | 2.0307 | 2.2474 | 2.2474 | 2019-10-07 15:00 | 1.9129 | 3.1348 | 5.1459 | 5.1459 | 5.1459 | 5.1459
2021-08-10 02:00 | 1.9891 | 2.4632 | 2.5024 | 2.6705 | 2.6033 | 2.7714 | 1.0974 | 1.6624 | 1.9792 | 1.9792 | 2.1903 | 2.1903 | 2019-10-07 16:00 | 1.9357 | 3.1723 | 5.2074 | 5.2074 | 5.2074 | 5.2074
2021-08-10 03:00 | 2.0234 | 2.5056 | 2.5455 | 2.7166 | 2.6482 | 2.8192 | 1.0523 | 1.5941 | 1.8979 | 1.8979 | 2.1004 | 2.1004 | 2019-10-07 17:00 | 1.8824 | 3.0849 | 5.0639 | 5.0639 | 5.0639 | 5.0639
2021-08-10 04:00 | 2.112 | 2.6153 | 2.657 | 2.8355 | 2.7641 | 2.9426 | 1.1632 | 1.762 | 2.0977 | 2.0977 | 2.3215 | 2.3215 | 2019-10-07 18:00 | 1.7452 | 2.8601 | 4.6949 | 4.6949 | 4.6949 | 4.6949
2021-08-10 05:00 | 2.7521 | 3.4081 | 3.4624 | 3.695 | 3.602 | 3.8346 | 1.2918 | 1.9568 | 2.3296 | 2.3296 | 2.5782 | 2.5782 | 2019-10-07 19:00 | 1.7147 | 2.8101 | 4.6128 | 4.6128 | 4.6128 | 4.6128
2021-08-10 06:00 | 3.6867 | 4.5653 | 4.6381 | 4.9497 | 4.8251 | 5.1367 | 1.6604 | 2.5152 | 2.9945 | 2.9945 | 3.314 | 3.314 | 2019-10-07 20:00 | 1.6004 | 2.6228 | 4.3053 | 4.3053 | 4.3053 | 4.3053
2021-08-10 07:00 | 4.3868 | 5.4324 | 5.5189 | 5.8898 | 5.7414 | 6.1123 | 2.0062 | 3.0391 | 3.6182 | 3.6182 | 4.0042 | 4.0042 | 2019-10-07 21:00 | 1.5166 | 2.4854 | 4.0798 | 4.0798 | 4.0798 | 4.0798
2021-08-10 08:00 | 4.2782 | 5.2979 | 5.3823 | 5.744 | 5.5993 | 5.961 | 2.1291 | 3.2252 | 3.8398 | 3.8398 | 4.2495 | 4.2495 | 2019-10-07 22:00 | 1.4251 | 2.3355 | 3.8338 | 3.8338 | 3.8338 | 3.8338
2021-08-10 09:00 | 3.7267 | 4.6149 | 4.6884 | 5.0034 | 4.8774 | 5.1924 | 1.8433 | 2.7923 | 3.3244 | 3.3244 | 3.6791 | 3.6791 | 2019-10-07 23:00 | 1.3718 | 2.2481 | 3.6903 | 3.6903 | 3.6903 | 3.6903
2021-08-10 10:00 | 3.358 | 4.1584 | 4.2246 | 4.5085 | 4.3949 | 4.6788 | 1.7004 | 2.5758 | 3.0667 | 3.0667 | 3.3939 | 3.3939 | 2019-10-08 | 1.2803 | 2.0982 | 3.4443 | 3.4443 | 3.4443 | 3.4443
2021-08-10 11:00 | 2.9579 | 3.6629 | 3.7212 | 3.9713 | 3.8713 | 4.1213 | 1.7462 | 2.6451 | 3.1491 | 3.1491 | 3.4852 | 3.4852 | 2019-10-08 01:00 | 1.2194 | 1.9983 | 3.2802 | 3.2802 | 3.2802 | 3.2802
2021-08-10 12:00 | 2.8093 | 3.4789 | 3.5343 | 3.7718 | 3.6768 | 3.9142 | 1.5947 | 2.4157 | 2.876 | 2.876 | 3.1828 | 3.1828 | 2019-10-08 02:00 | 1.1813 | 1.9359 | 3.1777 | 3.1777 | 3.1777 | 3.1777
2021-08-10 13:00 | 2.6407 | 3.2701 | 3.3221 | 3.5454 | 3.4561 | 3.6793 | 1.5947 | 2.4157 | 2.876 | 2.876 | 3.1828 | 3.1828 | 2019-10-08 03:00 | 1.1889 | 1.9483 | 3.1982 | 3.1982 | 3.1982 | 3.1982
2021-08-10 14:00 | 2.6493 | 3.2807 | 3.3329 | 3.5569 | 3.4673 | 3.6913 | 1.6204 | 2.4546 | 2.9224 | 2.9224 | 3.2342 | 3.2342 | 2019-10-08 04:00 | 1.2575 | 2.0608 | 3.3828 | 3.3828 | 3.3828 | 3.3828
2021-08-10 15:00 | 2.6778 | 3.3161 | 3.3689 | 3.5953 | 3.5047 | 3.7311 | 1.5976 | 2.42 | 2.8811 | 2.8811 | 3.1885 | 3.1885 | 2019-10-08 05:00 | 1.3413 | 2.1981 | 3.6083 | 3.6083 | 3.6083 | 3.6083
2021-08-10 16:00 | 3.0351 | 3.7584 | 3.8183 | 4.0749 | 3.9723 | 4.2288 | 1.7372 | 2.6316 | 3.133 | 3.133 | 3.4673 | 3.4673 | 2019-10-08 06:00 | 1.5699 | 2.5728 | 4.2233 | 4.2233 | 4.2233 | 4.2233
2021-08-10 17:00 | 3.741 | 4.6326 | 4.7064 | 5.0226 | 4.8961 | 5.2124 | 2.1348 | 3.2339 | 3.8501 | 3.8501 | 4.2609 | 4.2609 | 2019-10-08 07:00 | 1.9129 | 3.1348 | 5.1459 | 5.1459 | 5.1459 | 5.1459
2021-08-10 18:00 | 3.8581 | 4.7777 | 4.8538 | 5.1799 | 5.0495 | 5.3756 | 2.2892 | 3.4676 | 4.1284 | 4.1284 | 4.5689 | 4.5689 | 2019-10-08 08:00 | 1.9967 | 3.2722 | 5.3714 | 5.3714 | 5.3714 | 5.3714
2021-08-10 19:00 | 3.7353 | 4.6256 | 4.6992 | 5.015 | 4.8887 | 5.2044 | 2.3949 | 3.6278 | 4.3191 | 4.3191 | 4.78 | 4.78 | 2019-10-08 09:00 | 2.0424 | 3.3472 | 5.4944 | 5.4944 | 5.4944 | 5.4944
2021-08-10 20:00 | 3.4609 | 4.2858 | 4.354 | 4.6466 | 4.5296 | 4.8221 | 2.312 | 3.5023 | 4.1696 | 4.1696 | 4.6146 | 4.6146 | 2019-10-08 10:00 | 2.0958 | 3.4346 | 5.6379 | 5.6379 | 5.6379 | 5.6379
2021-08-10 21:00 | 3.1351 | 3.8823 | 3.9442 | 4.2092 | 4.1032 | 4.3682 | 2.292 | 3.472 | 4.1336 | 4.1336 | 4.5746 | 4.5746 | 2019-10-08 11:00 | 2.1415 | 3.5095 | 5.7609 | 5.7609 | 5.7609 | 5.7609
2021-08-10 22:00 | 2.8207 | 3.493 | 3.5487 | 3.7871 | 3.6917 | 3.9302 | 1.8298 | 2.7718 | 3.3 | 3.3 | 3.6521 | 3.6521 | 2019-10-08 12:00 | 2.2482 | 3.6844 | 6.048 | 6.048 | 6.048 | 6.048
2021-08-10 23:00 | 2.4051 | 2.9783 | 3.0257 | 3.229 | 3.1477 | 3.351 | 1.5914 | 2.4106 | 2.8699 | 2.8699 | 3.1762 | 3.1762 | 2019-10-08 13:00 | 2.1796 | 3.572 | 5.8634 | 5.8634 | 5.8634 | 5.8634
2021-08-11 | 2.1129 | 2.6165 | 2.6582 | 2.8368 | 2.7654 | 2.944 | 1.3548 | 2.0522 | 2.4433 | 2.4433 | 2.704 | 2.704 | 2019-10-08 14:00 | 2.172 | 3.5595 | 5.8429 | 5.8429 | 5.8429 | 5.8429
2021-08-11 01:00 | 1.9691 | 2.4384 | 2.4772 | 2.6437 | 2.5771 | 2.7436 | 1.2003 | 1.8182 | 2.1647 | 2.1647 | 2.3957 | 2.3957 | 2019-10-08 15:00 | 2.1415 | 3.5095 | 5.7609 | 5.7609 | 5.7609 | 5.7609
2021-08-11 02:00 | 1.9062 | 2.3605 | 2.3981 | 2.5593 | 2.4948 | 2.6559 | 1.1203 | 1.697 | 2.0204 | 2.0204 | 2.236 | 2.236 | 2019-10-08 16:00 | 2.0729 | 3.3971 | 5.5764 | 5.5764 | 5.5764 | 5.5764
2021-08-11 03:00 | 1.9033 | 2.357 | 2.3945 | 2.5554 | 2.4911 | 2.652 | 1.0974 | 1.6624 | 1.9792 | 1.9792 | 2.1903 | 2.1903 | 2019-10-08 17:00 | 2.0424 | 3.3472 | 5.4944 | 5.4944 | 5.4944 | 5.4944
2021-08-11 04:00 | 2.0766 | 2.5715 | 2.6124 | 2.788 | 2.7178 | 2.8933 | 1.1289 | 1.71 | 2.0359 | 2.0359 | 2.2531 | 2.2531 | 2019-10-08 18:00 | 1.9129 | 3.1348 | 5.1459 | 5.1459 | 5.1459 | 5.1459
2021-08-11 05:00 | 2.5264 | 3.1285 | 3.1783 | 3.3919 | 3.3065 | 3.52 | 1.323 | 2.0041 | 2.3859 | 2.3859 | 2.6405 | 2.6405 | 2019-10-08 19:00 | 1.8214 | 2.985 | 4.8999 | 4.8999 | 4.8999 | 4.8999
2021-08-11 06:00 | 3.5095 | 4.3459 | 4.4152 | 4.7118 | 4.5931 | 4.8898 | 1.5653 | 2.3711 | 2.8229 | 2.8229 | 3.1241 | 3.1241 | 2019-10-08 20:00 | 1.8595 | 3.0474 | 5.0024 | 5.0024 | 5.0024 | 5.0024
2021-08-11 07:00 | 3.921 | 4.8555 | 4.9329 | 5.2643 | 5.1318 | 5.4632 | 1.9462 | 2.9481 | 3.5099 | 3.5099 | 3.8844 | 3.8844 | 2019-10-08 21:00 | 1.8443 | 3.0224 | 4.9614 | 4.9614 | 4.9614 | 4.9614
2021-08-11 08:00 | 3.8781 | 4.8025 | 4.879 | 5.2068 | 5.0757 | 5.4035 | 1.9119 | 2.8962 | 3.4481 | 3.4481 | 3.816 | 3.816 | 2019-10-08 22:00 | 1.6004 | 2.6228 | 4.3053 | 4.3053 | 4.3053 | 4.3053
2021-08-11 09:00 | 3.3923 | 4.2008 | 4.2677 | 4.5545 | 4.4398 | 4.7266 | 1.7719 | 2.6841 | 3.1955 | 3.1955 | 3.5365 | 3.5365 | 2019-10-08 23:00 | 1.4861 | 2.4354 | 3.9978 | 3.9978 | 3.9978 | 3.9978
2021-08-11 10:00 | 3.0351 | 3.7584 | 3.8183 | 4.0749 | 3.9723 | 4.2288 | 1.6661 | 2.5239 | 3.0048 | 3.0048 | 3.3254 | 3.3254 | 2019-10-09 | 1.3489 | 2.2106 | 3.6288 | 3.6288 | 3.6288 | 3.6288
2021-08-11 11:00 | 2.8493 | 3.5284 | 3.5846 | 3.8255 | 3.7291 | 3.97 | 1.729 | 2.6191 | 3.1182 | 3.1182 | 3.4509 | 3.4509 | 2019-10-09 01:00 | 1.2422 | 2.0358 | 3.3417 | 3.3417 | 3.3417 | 3.3417
2021-08-11 12:00 | 2.7407 | 3.3939 | 3.448 | 3.6797 | 3.587 | 3.8187 | 1.629 | 2.4676 | 2.9378 | 2.9378 | 3.2513 | 3.2513 | 2019-10-09 02:00 | 1.227 | 2.0108 | 3.3007 | 3.3007 | 3.3007 | 3.3007
2021-08-11 13:00 | 2.755 | 3.4116 | 3.466 | 3.6989 | 3.6057 | 3.8386 | 1.7062 | 2.5845 | 3.077 | 3.077 | 3.4053 | 3.4053 | 2019-10-09 03:00 | 1.2194 | 1.9983 | 3.2802 | 3.2802 | 3.2802 | 3.2802
2021-08-11 14:00 | 2.6578 | 3.2913 | 3.3437 | 3.5684 | 3.4785 | 3.7032 | 1.5976 | 2.42 | 2.8811 | 2.8811 | 3.1885 | 3.1885 | 2019-10-09 04:00 | 1.2346 | 2.0233 | 3.3212 | 3.3212 | 3.3212 | 3.3212
2021-08-11 15:00 | 2.7036 | 3.3479 | 3.4012 | 3.6298 | 3.5384 | 3.7669 | 1.6376 | 2.4806 | 2.9533 | 2.9533 | 3.2684 | 3.2684 | 2019-10-09 05:00 | 1.387 | 2.2731 | 3.7313 | 3.7313 | 3.7313 | 3.7313
2021-08-11 16:00 | 2.8693 | 3.5532 | 3.6098 | 3.8523 | 3.7553 | 3.9979 | 1.9005 | 2.8789 | 3.4275 | 3.4275 | 3.7932 | 3.7932 | 2019-10-09 06:00 | 1.5166 | 2.4854 | 4.0798 | 4.0798 | 4.0798 | 4.0798
2021-08-11 17:00 | 3.3694 | 4.1725 | 4.239 | 4.5238 | 4.4099 | 4.6947 | 2.0147 | 3.0518 | 3.6333 | 3.6333 | 4.021 | 4.021 | 2019-10-09 07:00 | 1.8062 | 2.96 | 4.8589 | 4.8589 | 4.8589 | 4.8589
2021-08-11 18:00 | 3.5323 | 4.3742 | 4.4439 | 4.7425 | 4.6231 | 4.9217 | 2.2377 | 3.3897 | 4.0356 | 4.0356 | 4.4662 | 4.4662 | 2019-10-09 08:00 | 1.9815 | 3.2472 | 5.3304 | 5.3304 | 5.3304 | 5.3304
2021-08-11 19:00 | 3.4872 | 4.3184 | 4.3872 | 4.682 | 4.564 | 4.8588 | 2.192 | 3.3204 | 3.9532 | 3.9532 | 4.375 | 4.375 | 2019-10-09 09:00 | 2.0577 | 3.3721 | 5.5354 | 5.5354 | 5.5354 | 5.5354
2021-08-11 20:00 | 3.1749 | 3.9316 | 3.9943 | 4.2626 | 4.1553 | 4.4237 | 2.1834 | 3.3075 | 3.9377 | 3.9377 | 4.3579 | 4.3579 | 2019-10-09 10:00 | 1.9967 | 3.2722 | 5.3714 | 5.3714 | 5.3714 | 5.3714
2021-08-11 21:00 | 2.855 | 3.5355 | 3.5918 | 3.8331 | 3.7366 | 3.978 | 2.0234 | 3.065 | 3.6491 | 3.6491 | 4.0384 | 4.0384 | 2019-10-09 11:00 | 2.0043 | 3.2847 | 5.3919 | 5.3919 | 5.3919 | 5.3919
2021-08-11 22:00 | 2.392 | 2.9622 | 3.0093 | 3.2116 | 3.1307 | 3.3329 | 1.7262 | 2.6148 | 3.1131 | 3.1131 | 3.4452 | 3.4452 | 2019-10-09 12:00 | 2.0805 | 3.4096 | 5.5969 | 5.5969 | 5.5969 | 5.5969
2021-08-11 23:00 | 2.2006 | 2.7251 | 2.7685 | 2.9545 | 2.8801 | 3.0661 | 1.4918 | 2.2598 | 2.6904 | 2.6904 | 2.9775 | 2.9775 | 2019-10-09 13:00 | 2.3854 | 3.9092 | 6.417 | 6.417 | 6.417 | 6.417
2021-08-12 | 1.9519 | 2.4172 | 2.4557 | 2.6207 | 2.5547 | 2.7197 | 1.3039 | 1.9751 | 2.3514 | 2.3514 | 2.6023 | 2.6023 | 2019-10-09 14:00 | 2.3015 | 3.7718 | 6.1915 | 6.1915 | 6.1915 | 6.1915
2021-08-12 01:00 | 1.7947 | 2.2225 | 2.2579 | 2.4096 | 2.3489 | 2.5007 | 1.1271 | 1.7073 | 2.0327 | 2.0327 | 2.2496 | 2.2496 | 2019-10-09 15:00 | 2.1263 | 3.4845 | 5.7199 | 5.7199 | 5.7199 | 5.7199
2021-08-12 02:00 | 1.8376 | 2.2756 | 2.3118 | 2.4672 | 2.405 | 2.5604 | 1.0746 | 1.6278 | 1.9379 | 1.9379 | 2.1447 | 2.1447 | 2019-10-09 16:00 | 2.0729 | 3.3971 | 5.5764 | 5.5764 | 5.5764 | 5.5764
2021-08-12 03:00 | 1.8262 | 2.2614 | 2.2975 | 2.4518 | 2.3901 | 2.5445 | 0.98882 | 1.4979 | 1.7833 | 1.7833 | 1.9736 | 1.9736 | 2019-10-09 17:00 | 1.9967 | 3.2722 | 5.3714 | 5.3714 | 5.3714 | 5.3714
2021-08-12 04:00 | 1.9003 | 2.3532 | 2.3906 | 2.5513 | 2.487 | 2.6477 | 1.0403 | 1.5758 | 1.8761 | 1.8761 | 2.0763 | 2.0763 | 2019-10-09 18:00 | 1.8824 | 3.0849 | 5.0639 | 5.0639 | 5.0639 | 5.0639
2021-08-12 05:00 | 2.3463 | 2.9055 | 2.9518 | 3.1502 | 3.0708 | 3.2692 | 1.1574 | 1.7533 | 2.0874 | 2.0874 | 2.3101 | 2.3101 | 2019-10-09 19:00 | 1.89 | 3.0974 | 5.0844 | 5.0844 | 5.0844 | 5.0844
2021-08-12 06:00 | 3.3368 | 4.1322 | 4.198 | 4.48 | 4.3672 | 4.6493 | 1.5098 | 2.2871 | 2.7229 | 2.7229 | 3.0134 | 3.0134 | 2019-10-09 20:00 | 1.8062 | 2.96 | 4.8589 | 4.8589 | 4.8589 | 4.8589
2021-08-12 07:00 | 3.6409 | 4.5087 | 4.5805 | 4.8883 | 4.7652 | 5.073 | 1.7947 | 2.7187 | 3.2368 | 3.2368 | 3.5821 | 3.5821 | 2019-10-09 21:00 | 1.7071 | 2.7976 | 4.5923 | 4.5923 | 4.5923 | 4.5923
2021-08-12 08:00 | 3.7238 | 4.6114 | 4.6848 | 4.9996 | 4.8737 | 5.1885 | 1.8719 | 2.8356 | 3.3759 | 3.3759 | 3.7361 | 3.7361 | 2019-10-09 22:00 | 1.6004 | 2.6228 | 4.3053 | 4.3053 | 4.3053 | 4.3053
2021-08-12 09:00 | 3.2151 | 3.9814 | 4.0448 | 4.3166 | 4.2079 | 4.4797 | 1.7204 | 2.6061 | 3.1027 | 3.1027 | 3.4338 | 3.4338 | 2019-10-09 23:00 | 1.4556 | 2.3855 | 3.9158 | 3.9158 | 3.9158 | 3.9158
2021-08-12 10:00 | 3.0465 | 3.7726 | 3.8327 | 4.0902 | 3.9872 | 4.2447 | 1.6776 | 2.5412 | 3.0254 | 3.0254 | 3.3483 | 3.3483 | 2019-10-10 | 1.3261 | 2.1732 | 3.5673 | 3.5673 | 3.5673 | 3.5673
2021-08-12 11:00 | 2.7979 | 3.4647 | 3.5199 | 3.7564 | 3.6618 | 3.8983 | 1.6261 | 2.4633 | 2.9327 | 2.9327 | 3.2456 | 3.2456 | 2019-10-10 01:00 | 1.2651 | 2.0732 | 3.4033 | 3.4033 | 3.4033 | 3.4033
2021-08-12 12:00 | 2.4949 | 3.0896 | 3.1388 | 3.3497 | 3.2653 | 3.4762 | 1.4861 | 2.2511 | 2.6801 | 2.6801 | 2.9661 | 2.9661 | 2019-10-10 02:00 | 1.2041 | 1.9733 | 3.2392 | 3.2392 | 3.2392 | 3.2392
2021-08-12 13:00 | 2.4549 | 3.04 | 3.0884 | 3.296 | 3.213 | 3.4205 | 1.4661 | 2.2208 | 2.644 | 2.644 | 2.9262 | 2.9262 | 2019-10-10 03:00 | 1.1736 | 1.9234 | 3.1572 | 3.1572 | 3.1572 | 3.1572
2021-08-12 14:00 | 2.4463 | 3.0294 | 3.0777 | 3.2845 | 3.2017 | 3.4085 | 1.5347 | 2.3247 | 2.7677 | 2.7677 | 3.0631 | 3.0631 | 2019-10-10 04:00 | 1.3184 | 2.1607 | 3.5468 | 3.5468 | 3.5468 | 3.5468
2021-08-12 15:00 | 2.4806 | 3.0719 | 3.1208 | 3.3305 | 3.2466 | 3.4563 | 1.6176 | 2.4503 | 2.9172 | 2.9172 | 3.2285 | 3.2285 | 2019-10-10 05:00 | 1.4251 | 2.3355 | 3.8338 | 3.8338 | 3.8338 | 3.8338
2021-08-12 16:00 | 2.4304 | 3.0097 | 3.0576 | 3.2631 | 3.1809 | 3.3864 | 1.669 | 2.5282 | 3.01 | 3.01 | 3.3311 | 3.3311 | 2019-10-10 06:00 | 1.509 | 2.4729 | 4.0593 | 4.0593 | 4.0593 | 4.0593
2021-08-12 17:00 | 3.1054 | 3.8455 | 3.9067 | 4.1692 | 4.0642 | 4.3267 | 2.0034 | 3.0347 | 3.613 | 3.613 | 3.9985 | 3.9985 | 2019-10-10 07:00 | 1.8976 | 3.1099 | 5.1049 | 5.1049 | 5.1049 | 5.1049
2021-08-12 18:00 | 3.278 | 4.0593 | 4.1239 | 4.401 | 4.2902 | 4.5673 | 2.1997 | 3.3321 | 3.9671 | 3.9671 | 4.3904 | 4.3904 | 2019-10-10 08:00 | 2.0805 | 3.4096 | 5.5969 | 5.5969 | 5.5969 | 5.5969
2021-08-12 19:00 | 3.2723 | 4.0522 | 4.1167 | 4.3933 | 4.2827 | 4.5593 | 2.2749 | 3.446 | 4.1026 | 4.1026 | 4.5404 | 4.5404 | 2019-10-10 09:00 | 2.0272 | 3.3222 | 5.4534 | 5.4534 | 5.4534 | 5.4534
2021-08-12 20:00 | 2.9779 | 3.6877 | 3.7464 | 3.9981 | 3.8974 | 4.1492 | 2.1891 | 3.3161 | 3.948 | 3.948 | 4.3693 | 4.3693 | 2019-10-10 10:00 | 2.0882 | 3.4221 | 5.6174 | 5.6174 | 5.6174 | 5.6174
2021-08-12 21:00 | 2.7893 | 3.4541 | 3.5091 | 3.7449 | 3.6506 | 3.8864 | 1.9668 | 2.9793 | 3.547 | 3.547 | 3.9255 | 3.9255 | 2019-10-10 11:00 | 2.0729 | 3.3971 | 5.5764 | 5.5764 | 5.5764 | 5.5764
2021-08-12 22:00 | 2.5206 | 3.1214 | 3.1711 | 3.3842 | 3.299 | 3.5121 | 1.749 | 2.6494 | 3.1543 | 3.1543 | 3.4909 | 3.4909 | 2019-10-10 12:00 | 2.172 | 3.5595 | 5.8429 | 5.8429 | 5.8429 | 5.8429
2021-08-12 23:00 | 2.3292 | 2.8843 | 2.9302 | 3.1271 | 3.0484 | 3.2453 | 1.5322 | 2.3209 | 2.7632 | 2.7632 | 3.058 | 3.058 | 2019-10-10 13:00 | 2.172 | 3.5595 | 5.8429 | 5.8429 | 5.8429 | 5.8429
2021-08-13 | 2.0291 | 2.5127 | 2.5527 | 2.7243 | 2.6556 | 2.8272 | 1.312 | 1.9874 | 2.3661 | 2.3661 | 2.6185 | 2.6185 | 2019-10-10 14:00 | 2.1186 | 3.4721 | 5.6994 | 5.6994 | 5.6994 | 5.6994
2021-08-13 01:00 | 1.9148 | 2.3711 | 2.4089 | 2.5708 | 2.506 | 2.6679 | 1.1272 | 1.7074 | 2.0328 | 2.0328 | 2.2497 | 2.2497 | 2019-10-10 15:00 | 2.2025 | 3.6094 | 5.9249 | 5.9249 | 5.9249 | 5.9249
2021-08-13 02:00 | 1.9234 | 2.3818 | 2.4197 | 2.5823 | 2.5173 | 2.6798 | 1.1373 | 1.7228 | 2.051 | 2.051 | 2.2699 | 2.2699 | 2019-10-10 16:00 | 2.1034 | 3.4471 | 5.6584 | 5.6584 | 5.6584 | 5.6584
2021-08-13 03:00 | 1.9376 | 2.3995 | 2.4377 | 2.6015 | 2.536 | 2.6997 | 1.1374 | 1.723 | 2.0513 | 2.0513 | 2.2702 | 2.2702 | 2019-10-10 17:00 | 2.0729 | 3.3971 | 5.5764 | 5.5764 | 5.5764 | 5.5764
2021-08-13 04:00 | 2.0148 | 2.495 | 2.5348 | 2.7051 | 2.6369 | 2.8073 | 1.1289 | 1.71 | 2.0359 | 2.0359 | 2.2531 | 2.2531 | 2019-10-10 18:00 | 1.9053 | 3.1224 | 5.1254 | 5.1254 | 5.1254 | 5.1254
2021-08-13 05:00 | 2.2377 | 2.7711 | 2.8152 | 3.0044 | 2.9287 | 3.1179 | 1.2146 | 1.8399 | 2.1905 | 2.1905 | 2.4242 | 2.4242 | 2019-10-10 19:00 | 1.8595 | 3.0474 | 5.0024 | 5.0024 | 5.0024 | 5.0024
2021-08-13 06:00 | 2.8278 | 3.5018 | 3.5576 | 3.7966 | 3.701 | 3.94 | 1.3575 | 2.0563 | 2.4482 | 2.4482 | 2.7094 | 2.7094 | 2019-10-10 20:00 | 1.7605 | 2.8851 | 4.7359 | 4.7359 | 4.7359 | 4.7359
2021-08-13 07:00 | 3.3409 | 4.1371 | 4.203 | 4.4854 | 4.3725 | 4.6549 | 1.6804 | 2.5455 | 3.0306 | 3.0306 | 3.354 | 3.354 | 2019-10-10 21:00 | 1.6538 | 2.7102 | 4.4488 | 4.4488 | 4.4488 | 4.4488
2021-08-13 08:00 | 3.6038 | 4.4627 | 4.5338 | 4.8384 | 4.7166 | 5.0212 | 1.8519 | 2.8053 | 3.3398 | 3.3398 | 3.6962 | 3.6962 | 2019-10-10 22:00 | 1.6157 | 2.6478 | 4.3463 | 4.3463 | 4.3463 | 4.3463
2021-08-13 09:00 | 3.5915 | 4.4474 | 4.5183 | 4.8219 | 4.7004 | 5.004 | 1.9977 | 3.0261 | 3.6027 | 3.6027 | 3.9871 | 3.9871 | 2019-10-10 23:00 | 1.4327 | 2.348 | 3.8543 | 3.8543 | 3.8543 | 3.8543
2021-08-13 10:00 | 3.1351 | 3.8823 | 3.9442 | 4.2092 | 4.1032 | 4.3682 | 1.7919 | 2.7144 | 3.2316 | 3.2316 | 3.5764 | 3.5764 | 2019-10-11 | 1.2727 | 2.0857 | 3.4238 | 3.4238 | 3.4238 | 3.4238
2021-08-13 11:00 | 2.7664 | 3.4258 | 3.4803 | 3.7142 | 3.6207 | 3.8545 | 1.6661 | 2.5239 | 3.0048 | 3.0048 | 3.3254 | 3.3254 | 2019-10-11 01:00 | 1.2879 | 2.1107 | 3.4648 | 3.4648 | 3.4648 | 3.4648
2021-08-13 12:00 | 2.352 | 2.9126 | 2.959 | 3.1578 | 3.0783 | 3.2771 | 1.6719 | 2.5325 | 3.0151 | 3.0151 | 3.3368 | 3.3368 | 2019-10-11 02:00 | 1.1508 | 1.8859 | 3.0957 | 3.0957 | 3.0957 | 3.0957
2021-08-13 13:00 | 2.2182 | 2.7469 | 2.7907 | 2.9782 | 2.9032 | 3.0907 | 1.5347 | 2.3247 | 2.7677 | 2.7677 | 3.0631 | 3.0631 | 2019-10-11 03:00 | 1.1889 | 1.9483 | 3.1982 | 3.1982 | 3.1982 | 3.1982
2021-08-13 14:00 | 2.1577 | 2.672 | 2.7145 | 2.8969 | 2.824 | 3.0064 | 1.4947 | 2.2641 | 2.6956 | 2.6956 | 2.9832 | 2.9832 | 2019-10-11 04:00 | 1.2575 | 2.0608 | 3.3828 | 3.3828 | 3.3828 | 3.3828
2021-08-13 15:00 | 2.1834 | 2.7038 | 2.7469 | 2.9315 | 2.8576 | 3.0422 | 1.5357 | 2.3262 | 2.7695 | 2.7695 | 3.065 | 3.065 | 2019-10-11 05:00 | 1.4099 | 2.3105 | 3.7928 | 3.7928 | 3.7928 | 3.7928
2021-08-13 16:00 | 2.615 | 3.2382 | 3.2898 | 3.5108 | 3.4224 | 3.6435 | 1.6332 | 2.474 | 2.9455 | 2.9455 | 3.2598 | 3.2598 | 2019-10-11 06:00 | 1.4937 | 2.4479 | 4.0183 | 4.0183 | 4.0183 | 4.0183
2021-08-13 17:00 | 3.2208 | 3.9885 | 4.052 | 4.3243 | 4.2154 | 4.4876 | 1.9391 | 2.9374 | 3.4971 | 3.4971 | 3.8703 | 3.8703 | 2019-10-11 07:00 | 1.9129 | 3.1348 | 5.1459 | 5.1459 | 5.1459 | 5.1459
2021-08-13 18:00 | 3.3494 | 4.1477 | 4.2138 | 4.4969 | 4.3837 | 4.6668 | 2.2091 | 3.3464 | 3.9841 | 3.9841 | 4.4092 | 4.4092 | 2019-10-11 08:00 | 2.0043 | 3.2847 | 5.3919 | 5.3919 | 5.3919 | 5.3919
2021-08-13 19:00 | 3.2834 | 4.0659 | 4.1307 | 4.4083 | 4.2972 | 4.5748 | 2.2034 | 3.3378 | 3.9738 | 3.9738 | 4.3978 | 4.3978 | 2019-10-11 09:00 | 2.0348 | 3.3347 | 5.4739 | 5.4739 | 5.4739 | 5.4739
2021-08-13 20:00 | 3.0894 | 3.8257 | 3.8866 | 4.1478 | 4.0433 | 4.3045 | 2.0548 | 3.1126 | 3.7058 | 3.7058 | 4.1012 | 4.1012 | 2019-10-11 10:00 | 1.9967 | 3.2722 | 5.3714 | 5.3714 | 5.3714 | 5.3714
2021-08-13 21:00 | 2.8722 | 3.5567 | 3.6134 | 3.8562 | 3.7591 | 4.0018 | 1.8809 | 2.8492 | 3.3921 | 3.3921 | 3.754 | 3.754 | 2019-10-11 11:00 | 2.0348 | 3.3347 | 5.4739 | 5.4739 | 5.4739 | 5.4739
2021-08-13 22:00 | 2.6292 | 3.2559 | 3.3078 | 3.53 | 3.4411 | 3.6634 | 1.649 | 2.4979 | 2.9739 | 2.9739 | 3.2912 | 3.2912 | 2019-10-11 12:00 | 2.111 | 3.4596 | 5.6789 | 5.6789 | 5.6789 | 5.6789
2021-08-13 23:00 | 2.3492 | 2.9091 | 2.9554 | 3.154 | 3.0746 | 3.2731 | 1.5175 | 2.2988 | 2.7368 | 2.7368 | 3.0288 | 3.0288 | 2019-10-11 13:00 | 2.1186 | 3.4721 | 5.6994 | 5.6994 | 5.6994 | 5.6994
2021-08-14 | 2.1577 | 2.672 | 2.7145 | 2.8969 | 2.824 | 3.0064 | 1.3489 | 2.0433 | 2.4327 | 2.4327 | 2.6923 | 2.6923 | 2019-10-11 14:00 | 2.111 | 3.4596 | 5.6789 | 5.6789 | 5.6789 | 5.6789
2021-08-14 01:00 | 1.9777 | 2.449 | 2.488 | 2.6552 | 2.5883 | 2.7555 | 1.1297 | 1.7112 | 2.0373 | 2.0373 | 2.2547 | 2.2547 | 2019-10-11 15:00 | 2.0958 | 3.4346 | 5.6379 | 5.6379 | 5.6379 | 5.6379
2021-08-14 02:00 | 1.9691 | 2.4384 | 2.4772 | 2.6437 | 2.5771 | 2.7436 | 1.1203 | 1.697 | 2.0204 | 2.0204 | 2.236 | 2.236 | 2019-10-11 16:00 | 2.1034 | 3.4471 | 5.6584 | 5.6584 | 5.6584 | 5.6584
2021-08-14 03:00 | 1.9777 | 2.449 | 2.488 | 2.6552 | 2.5883 | 2.7555 | 1.1346 | 1.7187 | 2.0462 | 2.0462 | 2.2645 | 2.2645 | 2019-10-11 17:00 | 1.9662 | 3.2223 | 5.2894 | 5.2894 | 5.2894 | 5.2894
2021-08-14 04:00 | 2.0148 | 2.495 | 2.5348 | 2.7051 | 2.6369 | 2.8073 | 1.1203 | 1.697 | 2.0204 | 2.0204 | 2.236 | 2.236 | 2019-10-11 18:00 | 1.9281 | 3.1598 | 5.1869 | 5.1869 | 5.1869 | 5.1869
2021-08-14 05:00 | 2.2098 | 2.7365 | 2.7801 | 2.9669 | 2.8922 | 3.079 | 1.1996 | 1.8171 | 2.1633 | 2.1633 | 2.3942 | 2.3942 | 2019-10-11 19:00 | 1.9053 | 3.1224 | 5.1254 | 5.1254 | 5.1254 | 5.1254
2021-08-14 06:00 | 2.4092 | 2.9834 | 3.0309 | 3.2346 | 3.1531 | 3.3568 | 1.2882 | 1.9514 | 2.3232 | 2.3232 | 2.5711 | 2.5711 | 2019-10-11 20:00 | 1.8748 | 3.0724 | 5.0434 | 5.0434 | 5.0434 | 5.0434
2021-08-14 07:00 | 2.7178 | 3.3656 | 3.4192 | 3.649 | 3.5571 | 3.7868 | 1.549 | 2.3464 | 2.7935 | 2.7935 | 3.0916 | 3.0916 | 2019-10-11 21:00 | 1.6614 | 2.7227 | 4.4693 | 4.4693 | 4.4693 | 4.4693
2021-08-14 08:00 | 2.775 | 3.4364 | 3.4911 | 3.7257 | 3.6319 | 3.8665 | 1.5633 | 2.368 | 2.8193 | 2.8193 | 3.1201 | 3.1201 | 2019-10-11 22:00 | 1.6004 | 2.6228 | 4.3053 | 4.3053 | 4.3053 | 4.3053
2021-08-14 09:00 | 2.6778 | 3.3161 | 3.3689 | 3.5953 | 3.5047 | 3.7311 | 1.5775 | 2.3897 | 2.845 | 2.845 | 3.1486 | 3.1486 | 2019-10-11 23:00 | 1.448 | 2.373 | 3.8953 | 3.8953 | 3.8953 | 3.8953
2021-08-14 10:00 | 2.5892 | 3.2064 | 3.2574 | 3.4763 | 3.3888 | 3.6076 | 1.669 | 2.5282 | 3.01 | 3.01 | 3.3311 | 3.3311 | 2019-10-12 | 1.3261 | 2.1732 | 3.5673 | 3.5673 | 3.5673 | 3.5673
2021-08-14 11:00 | 2.4292 | 3.0082 | 3.0561 | 3.2614 | 3.1793 | 3.3846 | 1.6433 | 2.4893 | 2.9636 | 2.9636 | 3.2798 | 3.2798 | 2019-10-12 01:00 | 1.2803 | 2.0982 | 3.4443 | 3.4443 | 3.4443 | 3.4443
2021-08-14 12:00 | 2.2492 | 2.7852 | 2.8296 | 3.0197 | 2.9437 | 3.1338 | 1.5976 | 2.42 | 2.8811 | 2.8811 | 3.1885 | 3.1885 | 2019-10-12 02:00 | 1.1508 | 1.8859 | 3.0957 | 3.0957 | 3.0957 | 3.0957
2021-08-14 13:00 | 2.0377 | 2.5233 | 2.5635 | 2.7358 | 2.6669 | 2.8391 | 1.4832 | 2.2468 | 2.675 | 2.675 | 2.9604 | 2.9604 | 2019-10-12 03:00 | 1.1736 | 1.9234 | 3.1572 | 3.1572 | 3.1572 | 3.1572
2021-08-14 14:00 | 2.0177 | 2.4986 | 2.5383 | 2.7089 | 2.6407 | 2.8112 | 1.466 | 2.2207 | 2.6438 | 2.6438 | 2.9259 | 2.9259 | 2019-10-12 04:00 | 1.1584 | 1.8984 | 3.1162 | 3.1162 | 3.1162 | 3.1162
2021-08-14 15:00 | 2.132 | 2.6401 | 2.6822 | 2.8624 | 2.7903 | 2.9705 | 1.569 | 2.3767 | 2.8296 | 2.8296 | 3.1315 | 3.1315 | 2019-10-12 05:00 | 1.3642 | 2.2356 | 3.6698 | 3.6698 | 3.6698 | 3.6698
2021-08-14 16:00 | 2.4178 | 2.994 | 3.0417 | 3.2461 | 3.1643 | 3.3687 | 1.8205 | 2.7577 | 3.2831 | 3.2831 | 3.6335 | 3.6335 | 2019-10-12 06:00 | 1.3642 | 2.2356 | 3.6698 | 3.6698 | 3.6698 | 3.6698
2021-08-14 17:00 | 3.2064 | 3.9707 | 4.0339 | 4.305 | 4.1965 | 4.4676 | 2.0434 | 3.0953 | 3.6852 | 3.6852 | 4.0784 | 4.0784 | 2019-10-12 07:00 | 1.5852 | 2.5978 | 4.2643 | 4.2643 | 4.2643 | 4.2643
2021-08-14 18:00 | 3.318 | 4.1088 | 4.1743 | 4.4547 | 4.3425 | 4.623 | 2.2892 | 3.4676 | 4.1284 | 4.1284 | 4.5689 | 4.5689 | 2019-10-12 08:00 | 1.7452 | 2.8601 | 4.6949 | 4.6949 | 4.6949 | 4.6949
2021-08-14 19:00 | 3.2008 | 3.9637 | 4.0268 | 4.2974 | 4.1892 | 4.4598 | 2.2434 | 3.3984 | 4.0459 | 4.0459 | 4.4777 | 4.4777 | 2019-10-12 09:00 | 1.8595 | 3.0474 | 5.0024 | 5.0024 | 5.0024 | 5.0024
2021-08-14 20:00 | 2.9665 | 3.6735 | 3.732 | 3.9828 | 3.8825 | 4.1332 | 2.0119 | 3.0477 | 3.6285 | 3.6285 | 4.0156 | 4.0156 | 2019-10-12 10:00 | 2.0805 | 3.4096 | 5.5969 | 5.5969 | 5.5969 | 5.5969
2021-08-14 21:00 | 2.8036 | 3.4718 | 3.5271 | 3.7641 | 3.6693 | 3.9063 | 1.9291 | 2.9222 | 3.479 | 3.479 | 3.8502 | 3.8502 | 2019-10-12 11:00 | 1.9434 | 3.1848 | 5.2279 | 5.2279 | 5.2279 | 5.2279
2021-08-14 22:00 | 2.5349 | 3.1391 | 3.1891 | 3.4034 | 3.3177 | 3.532 | 1.7776 | 2.6927 | 3.2058 | 3.2058 | 3.5479 | 3.5479 | 2019-10-12 12:00 | 1.7909 | 2.935 | 4.8179 | 4.8179 | 4.8179 | 4.8179
2021-08-14 23:00 | 2.376 | 2.9423 | 2.9892 | 3.1901 | 3.1097 | 3.3106 | 1.4797 | 2.2414 | 2.6685 | 2.6685 | 2.9533 | 2.9533 | 2019-10-12 13:00 | 1.8062 | 2.96 | 4.8589 | 4.8589 | 4.8589 | 4.8589
2021-08-15 | 2.172 | 2.6897 | 2.7325 | 2.9161 | 2.8427 | 3.0263 | 1.3605 | 2.061 | 2.4537 | 2.4537 | 2.7155 | 2.7155 | 2019-10-12 14:00 | 1.8214 | 2.985 | 4.8999 | 4.8999 | 4.8999 | 4.8999
2021-08-15 01:00 | 1.9748 | 2.4455 | 2.4844 | 2.6514 | 2.5846 | 2.7515 | 1.2346 | 1.8702 | 2.2266 | 2.2266 | 2.4641 | 2.4641 | 2019-10-12 15:00 | 1.7986 | 2.9475 | 4.8384 | 4.8384 | 4.8384 | 4.8384
2021-08-15 02:00 | 1.9605 | 2.4278 | 2.4664 | 2.6322 | 2.5659 | 2.7316 | 1.1432 | 1.7317 | 2.0617 | 2.0617 | 2.2817 | 2.2817 | 2019-10-12 16:00 | 1.7681 | 2.8975 | 4.7564 | 4.7564 | 4.7564 | 4.7564
2021-08-15 03:00 | 1.9491 | 2.4136 | 2.4521 | 2.6168 | 2.5509 | 2.7157 | 1.1231 | 1.7013 | 2.0255 | 2.0255 | 2.2417 | 2.2417 | 2019-10-12 17:00 | 1.7681 | 2.8975 | 4.7564 | 4.7564 | 4.7564 | 4.7564
2021-08-15 04:00 | 2.0148 | 2.495 | 2.5348 | 2.7051 | 2.6369 | 2.8073 | 1.0974 | 1.6624 | 1.9792 | 1.9792 | 2.1903 | 2.1903 | 2019-10-12 18:00 | 1.6995 | 2.7851 | 4.5718 | 4.5718 | 4.5718 | 4.5718
2021-08-15 05:00 | 2.1434 | 2.6543 | 2.6965 | 2.8777 | 2.8053 | 2.9864 | 1.1716 | 1.7748 | 2.113 | 2.113 | 2.3385 | 2.3385 | 2019-10-12 19:00 | 1.6995 | 2.7851 | 4.5718 | 4.5718 | 4.5718 | 4.5718
2021-08-15 06:00 | 2.4149 | 2.9905 | 3.0381 | 3.2422 | 3.1606 | 3.3647 | 1.2744 | 1.9305 | 2.2984 | 2.2984 | 2.5436 | 2.5436 | 2019-10-12 20:00 | 1.6842 | 2.7602 | 4.5308 | 4.5308 | 4.5308 | 4.5308
2021-08-15 07:00 | 2.6664 | 3.3019 | 3.3545 | 3.5799 | 3.4897 | 3.7151 | 1.4661 | 2.2208 | 2.644 | 2.644 | 2.9262 | 2.9262 | 2019-10-12 21:00 | 1.6157 | 2.6478 | 4.3463 | 4.3463 | 4.3463 | 4.3463
2021-08-15 08:00 | 3.0208 | 3.7408 | 3.8003 | 4.0557 | 3.9535 | 4.2089 | 1.6118 | 2.4416 | 2.9069 | 2.9069 | 3.2171 | 3.2171 | 2019-10-12 22:00 | 1.5471 | 2.5353 | 4.1618 | 4.1618 | 4.1618 | 4.1618
2021-08-15 09:00 | 3.0465 | 3.7726 | 3.8327 | 4.0902 | 3.9872 | 4.2447 | 1.749 | 2.6494 | 3.1543 | 3.1543 | 3.4909 | 3.4909 | 2019-10-12 23:00 | 1.3413 | 2.1981 | 3.6083 | 3.6083 | 3.6083 | 3.6083
2021-08-15 10:00 | 2.8207 | 3.493 | 3.5487 | 3.7871 | 3.6917 | 3.9302 | 1.7781 | 2.6934 | 3.2067 | 3.2067 | 3.5489 | 3.5489 | 2019-10-13 | 1.2346 | 2.0233 | 3.3212 | 3.3212 | 3.3212 | 3.3212
2021-08-15 11:00 | 2.4406 | 3.0223 | 3.0705 | 3.2768 | 3.1943 | 3.4006 | 1.7805 | 2.697 | 3.211 | 3.211 | 3.5536 | 3.5536 | 2019-10-13 01:00 | 1.2117 | 1.9858 | 3.2597 | 3.2597 | 3.2597 | 3.2597
2021-08-15 12:00 | 2.0634 | 2.5552 | 2.5959 | 2.7703 | 2.7005 | 2.875 | 1.5663 | 2.3727 | 2.8248 | 2.8248 | 3.1262 | 3.1262 | 2019-10-13 02:00 | 1.1431 | 1.8734 | 3.0752 | 3.0752 | 3.0752 | 3.0752
2021-08-15 13:00 | 1.9891 | 2.4632 | 2.5024 | 2.6705 | 2.6033 | 2.7714 | 1.5718 | 2.381 | 2.8347 | 2.8347 | 3.1372 | 3.1372 | 2019-10-13 03:00 | 1.1203 | 1.8359 | 3.0137 | 3.0137 | 3.0137 | 3.0137
2021-08-15 14:00 | 2.0634 | 2.5552 | 2.5959 | 2.7703 | 2.7005 | 2.875 | 1.4832 | 2.2468 | 2.675 | 2.675 | 2.9604 | 2.9604 | 2019-10-13 04:00 | 1.2194 | 1.9983 | 3.2802 | 3.2802 | 3.2802 | 3.2802
2021-08-15 15:00 | 2.3406 | 2.8985 | 2.9446 | 3.1425 | 3.0633 | 3.2612 | 1.6257 | 2.4627 | 2.9319 | 2.9319 | 3.2448 | 3.2448 | 2019-10-13 05:00 | 1.3108 | 2.1482 | 3.5263 | 3.5263 | 3.5263 | 3.5263
2021-08-15 16:00 | 2.7321 | 3.3833 | 3.4372 | 3.6682 | 3.5758 | 3.8067 | 1.8262 | 2.7663 | 3.2934 | 3.2934 | 3.6449 | 3.6449 | 2019-10-13 06:00 | 1.3489 | 2.2106 | 3.6288 | 3.6288 | 3.6288 | 3.6288
2021-08-15 17:00 | 3.3523 | 4.1513 | 4.2174 | 4.5008 | 4.3874 | 4.6708 | 2.1606 | 3.2728 | 3.8965 | 3.8965 | 4.3122 | 4.3122 | 2019-10-13 07:00 | 1.4632 | 2.398 | 3.9363 | 3.9363 | 3.9363 | 3.9363
2021-08-15 18:00 | 3.3952 | 4.2044 | 4.2713 | 4.5583 | 4.4435 | 4.7305 | 2.3235 | 3.5196 | 4.1903 | 4.1903 | 4.6374 | 4.6374 | 2019-10-13 08:00 | 1.6766 | 2.7477 | 4.5103 | 4.5103 | 4.5103 | 4.5103
2021-08-15 19:00 | 3.4066 | 4.2185 | 4.2857 | 4.5737 | 4.4585 | 4.7465 | 2.3463 | 3.5542 | 4.2315 | 4.2315 | 4.683 | 4.683 | 2019-10-13 09:00 | 1.7376 | 2.8476 | 4.6744 | 4.6744 | 4.6744 | 4.6744
2021-08-15 20:00 | 3.0494 | 3.7761 | 3.8363 | 4.0941 | 3.991 | 4.2487 | 2.0863 | 3.1603 | 3.7625 | 3.7625 | 4.1639 | 4.1639 | 2019-10-13 10:00 | 1.7605 | 2.8851 | 4.7359 | 4.7359 | 4.7359 | 4.7359
2021-08-15 21:00 | 2.8179 | 3.4895 | 3.5451 | 3.7833 | 3.688 | 3.9262 | 1.8809 | 2.8492 | 3.3921 | 3.3921 | 3.754 | 3.754 | 2019-10-13 11:00 | 1.7605 | 2.8851 | 4.7359 | 4.7359 | 4.7359 | 4.7359
2021-08-15 22:00 | 2.4818 | 3.0733 | 3.1223 | 3.3321 | 3.2482 | 3.458 | 1.6719 | 2.5325 | 3.0151 | 3.0151 | 3.3368 | 3.3368 | 2019-10-13 12:00 | 1.829 | 2.9975 | 4.9204 | 4.9204 | 4.9204 | 4.9204
2021-08-15 23:00 | 2.2577 | 2.7958 | 2.8404 | 3.0312 | 2.9549 | 3.1457 | 1.4863 | 2.2515 | 2.6805 | 2.6805 | 2.9665 | 2.9665 | 2019-10-13 13:00 | 1.829 | 2.9975 | 4.9204 | 4.9204 | 4.9204 | 4.9204
2021-08-16 | 1.9512 | 2.4162 | 2.4547 | 2.6197 | 2.5537 | 2.7186 | 1.2331 | 1.8679 | 2.2238 | 2.2238 | 2.4611 | 2.4611 | 2019-10-13 14:00 | 2.0119 | 3.2972 | 5.4124 | 5.4124 | 5.4124 | 5.4124
2021-08-16 01:00 | 1.8005 | 2.2296 | 2.2651 | 2.4173 | 2.3564 | 2.5086 | 1.1031 | 1.671 | 1.9895 | 1.9895 | 2.2017 | 2.2017 | 2019-10-13 15:00 | 1.951 | 3.1973 | 5.2484 | 5.2484 | 5.2484 | 5.2484
2021-08-16 02:00 | 1.809 | 2.2402 | 2.2759 | 2.4288 | 2.3676 | 2.5206 | 1.0288 | 1.5585 | 1.8555 | 1.8555 | 2.0534 | 2.0534 | 2019-10-13 16:00 | 1.951 | 3.1973 | 5.2484 | 5.2484 | 5.2484 | 5.2484
2021-08-16 03:00 | 1.7833 | 2.2084 | 2.2435 | 2.3943 | 2.334 | 2.4847 | 1.0403 | 1.5758 | 1.8761 | 1.8761 | 2.0763 | 2.0763 | 2019-10-13 17:00 | 1.9053 | 3.1224 | 5.1254 | 5.1254 | 5.1254 | 5.1254
2021-08-16 04:00 | 1.8385 | 2.2767 | 2.3129 | 2.4684 | 2.4062 | 2.5616 | 1.0888 | 1.6494 | 1.9637 | 1.9637 | 2.1732 | 2.1732 | 2019-10-13 18:00 | 1.7376 | 2.8476 | 4.6744 | 4.6744 | 4.6744 | 4.6744
2021-08-16 05:00 | 2.1548 | 2.6684 | 2.7109 | 2.8931 | 2.8202 | 3.0024 | 1.1031 | 1.671 | 1.9895 | 1.9895 | 2.2017 | 2.2017 | 2019-10-13 19:00 | 1.7452 | 2.8601 | 4.6949 | 4.6949 | 4.6949 | 4.6949
2021-08-16 06:00 | 2.6551 | 3.2879 | 3.3403 | 3.5647 | 3.4749 | 3.6994 | 1.2632 | 1.9135 | 2.2781 | 2.2781 | 2.5212 | 2.5212 | 2019-10-13 20:00 | 1.7528 | 2.8726 | 4.7154 | 4.7154 | 4.7154 | 4.7154
2021-08-16 07:00 | 3.0494 | 3.7761 | 3.8363 | 4.0941 | 3.991 | 4.2487 | 1.6833 | 2.5499 | 3.0357 | 3.0357 | 3.3597 | 3.3597 | 2019-10-13 21:00 | 1.6309 | 2.6727 | 4.3873 | 4.3873 | 4.3873 | 4.3873
2021-08-16 08:00 | 3.0351 | 3.7584 | 3.8183 | 4.0749 | 3.9723 | 4.2288 | 1.709 | 2.5888 | 3.0821 | 3.0821 | 3.411 | 3.411 | 2019-10-13 22:00 | 1.5242 | 2.4979 | 4.1003 | 4.1003 | 4.1003 | 4.1003
2021-08-16 09:00 | 2.8807 | 3.5673 | 3.6242 | 3.8677 | 3.7703 | 4.0138 | 1.6204 | 2.4546 | 2.9224 | 2.9224 | 3.2342 | 3.2342 | 2019-10-13 23:00 | 1.3337 | 2.1856 | 3.5878 | 3.5878 | 3.5878 | 3.5878
2021-08-16 10:00 | 2.7264 | 3.3762 | 3.43 | 3.6605 | 3.5683 | 3.7988 | 1.569 | 2.3767 | 2.8296 | 2.8296 | 3.1315 | 3.1315 | 2019-10-14 | 1.2803 | 2.0982 | 3.4443 | 3.4443 | 3.4443 | 3.4443
2021-08-16 11:00 | 2.4492 | 3.0329 | 3.0813 | 3.2883 | 3.2055 | 3.4125 | 1.4975 | 2.2685 | 2.7007 | 2.7007 | 2.9889 | 2.9889 | 2019-10-14 01:00 | 1.1813 | 1.9359 | 3.1777 | 3.1777 | 3.1777 | 3.1777
2021-08-16 12:00 | 2.3549 | 2.9162 | 2.9626 | 3.1617 | 3.082 | 3.2811 | 1.616 | 2.448 | 2.9144 | 2.9144 | 3.2254 | 3.2254 | 2019-10-14 02:00 | 1.1203 | 1.8359 | 3.0137 | 3.0137 | 3.0137 | 3.0137
2021-08-16 13:00 | 2.2692 | 2.81 | 2.8547 | 3.0466 | 2.9698 | 3.1617 | 1.6204 | 2.4546 | 2.9224 | 2.9224 | 3.2342 | 3.2342 | 2019-10-14 03:00 | 1.1431 | 1.8734 | 3.0752 | 3.0752 | 3.0752 | 3.0752
2021-08-16 14:00 | 2.332 | 2.8878 | 2.9338 | 3.131 | 3.0521 | 3.2493 | 1.5661 | 2.3724 | 2.8244 | 2.8244 | 3.1258 | 3.1258 | 2019-10-14 04:00 | 1.2194 | 1.9983 | 3.2802 | 3.2802 | 3.2802 | 3.2802
2021-08-16 15:00 | 2.3149 | 2.8666 | 2.9123 | 3.108 | 3.0297 | 3.2254 | 1.6033 | 2.4286 | 2.8914 | 2.8914 | 3.2 | 3.2 | 2019-10-14 05:00 | 1.3184 | 2.1607 | 3.5468 | 3.5468 | 3.5468 | 3.5468
2021-08-16 16:00 | 2.8636 | 3.5461 | 3.6026 | 3.8447 | 3.7478 | 3.9899 | 1.6797 | 2.5444 | 3.0293 | 3.0293 | 3.3525 | 3.3525 | 2019-10-14 06:00 | 1.5242 | 2.4979 | 4.1003 | 4.1003 | 4.1003 | 4.1003
2021-08-16 17:00 | 3.4128 | 4.2262 | 4.2936 | 4.5821 | 4.4667 | 4.7552 | 2.109 | 3.1948 | 3.8036 | 3.8036 | 4.2094 | 4.2094 | 2019-10-14 07:00 | 1.8062 | 2.96 | 4.8589 | 4.8589 | 4.8589 | 4.8589
2021-08-16 18:00 | 3.5066 | 4.3424 | 4.4116 | 4.708 | 4.5894 | 4.8858 | 2.3177 | 3.5109 | 4.1799 | 4.1799 | 4.626 | 4.626 | 2019-10-14 08:00 | 2.0272 | 3.3222 | 5.4534 | 5.4534 | 5.4534 | 5.4534
2021-08-16 19:00 | 3.4175 | 4.232 | 4.2994 | 4.5883 | 4.4727 | 4.7616 | 2.2034 | 3.3378 | 3.9738 | 3.9738 | 4.3978 | 4.3978 | 2019-10-14 09:00 | 2.0272 | 3.3222 | 5.4534 | 5.4534 | 5.4534 | 5.4534
2021-08-16 20:00 | 3.1608 | 3.9142 | 3.9765 | 4.2437 | 4.1368 | 4.404 | 2.1663 | 3.2815 | 3.9068 | 3.9068 | 4.3236 | 4.3236 | 2019-10-14 10:00 | 1.9281 | 3.1598 | 5.1869 | 5.1869 | 5.1869 | 5.1869
2021-08-16 21:00 | 2.8436 | 3.5213 | 3.5774 | 3.8178 | 3.7216 | 3.962 | 2.0405 | 3.091 | 3.68 | 3.68 | 4.0727 | 4.0727 | 2019-10-14 11:00 | 2.2177 | 3.6344 | 5.966 | 5.966 | 5.966 | 5.966
2021-08-16 22:00 | 2.4721 | 3.0613 | 3.11 | 3.319 | 3.2354 | 3.4444 | 1.7404 | 2.6364 | 3.1388 | 3.1388 | 3.4737 | 3.4737 | 2019-10-14 12:00 | 2.2558 | 3.6969 | 6.0685 | 6.0685 | 6.0685 | 6.0685
2021-08-16 23:00 | 2.3006 | 2.8489 | 2.8943 | 3.0888 | 3.011 | 3.2055 | 1.489 | 2.2555 | 2.6853 | 2.6853 | 2.9718 | 2.9718 | 2019-10-14 13:00 | 2.1186 | 3.4721 | 5.6994 | 5.6994 | 5.6994 | 5.6994
2021-08-17 | 1.9297 | 2.3896 | 2.4276 | 2.5908 | 2.5255 | 2.6886 | 1.2784 | 1.9366 | 2.3056 | 2.3056 | 2.5516 | 2.5516 | 2019-10-14 14:00 | 2.4997 | 4.0965 | 6.7245 | 6.7245 | 6.7245 | 6.7245
2021-08-17 01:00 | 1.8721 | 2.3183 | 2.3552 | 2.5135 | 2.4502 | 2.6084 | 1.146 | 1.736 | 2.0668 | 2.0668 | 2.2873 | 2.2873 | 2019-10-14 15:00 | 2.2787 | 3.7343 | 6.13 | 6.13 | 6.13 | 6.13
2021-08-17 02:00 | 1.8348 | 2.2721 | 2.3082 | 2.4633 | 2.4013 | 2.5564 | 1.0574 | 1.6018 | 1.907 | 1.907 | 2.1105 | 2.1105 | 2019-10-14 16:00 | 2.2482 | 3.6844 | 6.048 | 6.048 | 6.048 | 6.048
2021-08-17 03:00 | 1.8033 | 2.2331 | 2.2687 | 2.4211 | 2.3602 | 2.5126 | 1.1031 | 1.671 | 1.9895 | 1.9895 | 2.2017 | 2.2017 | 2019-10-14 17:00 | 2.2177 | 3.6344 | 5.966 | 5.966 | 5.966 | 5.966
2021-08-17 04:00 | 1.8576 | 2.3004 | 2.337 | 2.494 | 2.4312 | 2.5883 | 1.0803 | 1.6364 | 1.9482 | 1.9482 | 2.1561 | 2.1561 | 2019-10-14 18:00 | 2.0348 | 3.3347 | 5.4739 | 5.4739 | 5.4739 | 5.4739
2021-08-17 05:00 | 2.0462 | 2.5339 | 2.5743 | 2.7473 | 2.6781 | 2.8511 | 1.1146 | 1.6884 | 2.0101 | 2.0101 | 2.2246 | 2.2246 | 2019-10-14 19:00 | 2.0196 | 3.3097 | 5.4329 | 5.4329 | 5.4329 | 5.4329
2021-08-17 06:00 | 2.649 | 3.2803 | 3.3326 | 3.5565 | 3.4669 | 3.6909 | 1.3614 | 2.0622 | 2.4552 | 2.4552 | 2.7172 | 2.7172 | 2019-10-14 20:00 | 1.7986 | 2.9475 | 4.8384 | 4.8384 | 4.8384 | 4.8384
2021-08-17 07:00 | 3.0694 | 3.8009 | 3.8615 | 4.1209 | 4.0171 | 4.2766 | 1.6461 | 2.4936 | 2.9687 | 2.9687 | 3.2855 | 3.2855 | 2019-10-14 21:00 | 1.7071 | 2.7976 | 4.5923 | 4.5923 | 4.5923 | 4.5923
2021-08-17 08:00 | 3.1179 | 3.8611 | 3.9226 | 4.1861 | 4.0807 | 4.3443 | 1.729 | 2.6191 | 3.1182 | 3.1182 | 3.4509 | 3.4509 | 2019-10-14 22:00 | 1.6461 | 2.6977 | 4.4283 | 4.4283 | 4.4283 | 4.4283
2021-08-17 09:00 | 2.8722 | 3.5567 | 3.6134 | 3.8562 | 3.7591 | 4.0018 | 1.7004 | 2.5758 | 3.0667 | 3.0667 | 3.3939 | 3.3939 | 2019-10-14 23:00 | 1.509 | 2.4729 | 4.0593 | 4.0593 | 4.0593 | 4.0593
2021-08-17 10:00 | 2.6978 | 3.3408 | 3.3941 | 3.6221 | 3.5309 | 3.7589 | 1.6004 | 2.4243 | 2.8863 | 2.8863 | 3.1942 | 3.1942 | 2019-10-15 | 1.3565 | 2.2231 | 3.6493 | 3.6493 | 3.6493 | 3.6493
2021-08-17 11:00 | 2.4292 | 3.0082 | 3.0561 | 3.2614 | 3.1793 | 3.3846 | 1.5232 | 2.3074 | 2.7471 | 2.7471 | 3.0402 | 3.0402 | 2019-10-15 01:00 | 1.2651 | 2.0732 | 3.4033 | 3.4033 | 3.4033 | 3.4033
2021-08-17 12:00 | 2.1777 | 2.6967 | 2.7397 | 2.9238 | 2.8501 | 3.0342 | 1.5204 | 2.3031 | 2.742 | 2.742 | 3.0345 | 3.0345 | 2019-10-15 02:00 | 1.2575 | 2.0608 | 3.3828 | 3.3828 | 3.3828 | 3.3828
2021-08-17 13:00 | 2.1463 | 2.6578 | 2.7001 | 2.8816 | 2.809 | 2.9904 | 1.4375 | 2.1776 | 2.5925 | 2.5925 | 2.8691 | 2.8691 | 2019-10-15 03:00 | 1.2194 | 1.9983 | 3.2802 | 3.2802 | 3.2802 | 3.2802
2021-08-17 14:00 | 2.092 | 2.5906 | 2.6318 | 2.8087 | 2.7379 | 2.9148 | 1.4061 | 2.1299 | 2.5358 | 2.5358 | 2.8064 | 2.8064 | 2019-10-15 04:00 | 1.2879 | 2.1107 | 3.4648 | 3.4648 | 3.4648 | 3.4648
2021-08-17 15:00 | 2.1234 | 2.6295 | 2.6714 | 2.8509 | 2.7791 | 2.9586 | 1.5204 | 2.3031 | 2.742 | 2.742 | 3.0345 | 3.0345 | 2019-10-15 05:00 | 1.4632 | 2.398 | 3.9363 | 3.9363 | 3.9363 | 3.9363
2021-08-17 16:00 | 2.4892 | 3.0825 | 3.1316 | 3.342 | 3.2578 | 3.4683 | 1.5947 | 2.4157 | 2.876 | 2.876 | 3.1828 | 3.1828 | 2019-10-15 06:00 | 1.6004 | 2.6228 | 4.3053 | 4.3053 | 4.3053 | 4.3053
2021-08-17 17:00 | 3.1637 | 3.9177 | 3.9801 | 4.2475 | 4.1406 | 4.408 | 1.9482 | 2.9512 | 3.5136 | 3.5136 | 3.8885 | 3.8885 | 2019-10-15 07:00 | 1.9053 | 3.1224 | 5.1254 | 5.1254 | 5.1254 | 5.1254
2021-08-17 18:00 | 3.4295 | 4.2468 | 4.3145 | 4.6044 | 4.4884 | 4.7783 | 2.1795 | 3.3015 | 3.9307 | 3.9307 | 4.3501 | 4.3501 | 2019-10-15 08:00 | 2.1949 | 3.597 | 5.9044 | 5.9044 | 5.9044 | 5.9044
2021-08-17 19:00 | 3.3666 | 4.169 | 4.2354 | 4.52 | 4.4061 | 4.6907 | 2.2434 | 3.3984 | 4.0459 | 4.0459 | 4.4777 | 4.4777 | 2019-10-15 09:00 | 2.1339 | 3.497 | 5.7404 | 5.7404 | 5.7404 | 5.7404
2021-08-17 20:00 | 3.0301 | 3.7523 | 3.8121 | 4.0682 | 3.9658 | 4.2219 | 2.1148 | 3.2036 | 3.814 | 3.814 | 4.221 | 4.221 | 2019-10-15 10:00 | 2.1949 | 3.597 | 5.9044 | 5.9044 | 5.9044 | 5.9044
2021-08-17 21:00 | 2.8093 | 3.4789 | 3.5343 | 3.7718 | 3.6768 | 3.9142 | 1.8919 | 2.8659 | 3.412 | 3.412 | 3.7761 | 3.7761 | 2019-10-15 11:00 | 2.2711 | 3.7218 | 6.1095 | 6.1095 | 6.1095 | 6.1095
2021-08-17 22:00 | 2.5378 | 3.1427 | 3.1927 | 3.4072 | 3.3214 | 3.536 | 1.8148 | 2.749 | 3.2728 | 3.2728 | 3.6221 | 3.6221 | 2019-10-15 12:00 | 2.3015 | 3.7718 | 6.1915 | 6.1915 | 6.1915 | 6.1915
2021-08-17 23:00 | 2.4263 | 3.0046 | 3.0525 | 3.2576 | 3.1756 | 3.3807 | 1.5061 | 2.2815 | 2.7162 | 2.7162 | 3.006 | 3.006 | 2019-10-15 13:00 | 2.4387 | 3.9966 | 6.5605 | 6.5605 | 6.5605 | 6.5605
2021-08-18 | 2.1063 | 2.6083 | 2.6498 | 2.8279 | 2.7566 | 2.9347 | 1.3403 | 2.0304 | 2.4173 | 2.4173 | 2.6752 | 2.6752 | 2019-10-15 14:00 | 2.4463 | 4.0091 | 6.581 | 6.581 | 6.581 | 6.581
2021-08-18 01:00 | 1.9948 | 2.4702 | 2.5096 | 2.6782 | 2.6108 | 2.7794 | 1.1231 | 1.7013 | 2.0255 | 2.0255 | 2.2417 | 2.2417 | 2019-10-15 15:00 | 2.3778 | 3.8967 | 6.3965 | 6.3965 | 6.3965 | 6.3965
2021-08-18 02:00 | 1.9348 | 2.3959 | 2.4341 | 2.5976 | 2.5322 | 2.6958 | 1.0888 | 1.6494 | 1.9637 | 1.9637 | 2.1732 | 2.1732 | 2019-10-15 16:00 | 2.3701 | 3.8842 | 6.376 | 6.376 | 6.376 | 6.376
2021-08-18 03:00 | 1.9176 | 2.3747 | 2.4125 | 2.5746 | 2.5098 | 2.6719 | 1.0917 | 1.6537 | 1.9688 | 1.9688 | 2.1789 | 2.1789 | 2019-10-15 17:00 | 2.332 | 3.8218 | 6.2735 | 6.2735 | 6.2735 | 6.2735
2021-08-18 04:00 | 1.9862 | 2.4596 | 2.4988 | 2.6667 | 2.5995 | 2.7674 | 1.1117 | 1.684 | 2.0049 | 2.0049 | 2.2189 | 2.2189 | 2019-10-15 18:00 | 2.2177 | 3.6344 | 5.966 | 5.966 | 5.966 | 5.966
2021-08-18 05:00 | 2.2395 | 2.7733 | 2.8175 | 3.0068 | 2.9311 | 3.1204 | 1.2146 | 1.8399 | 2.1905 | 2.1905 | 2.4242 | 2.4242 | 2019-10-15 19:00 | 2.1339 | 3.497 | 5.7404 | 5.7404 | 5.7404 | 5.7404
2021-08-18 06:00 | 2.8748 | 3.56 | 3.6167 | 3.8597 | 3.7625 | 4.0055 | 1.3861 | 2.0996 | 2.4997 | 2.4997 | 2.7664 | 2.7664 | 2019-10-15 20:00 | 1.9738 | 3.2348 | 5.3099 | 5.3099 | 5.3099 | 5.3099
2021-08-18 07:00 | 3.338 | 4.1336 | 4.1994 | 4.4816 | 4.3687 | 4.6509 | 1.7176 | 2.6018 | 3.0976 | 3.0976 | 3.4281 | 3.4281 | 2019-10-15 21:00 | 1.9357 | 3.1723 | 5.2074 | 5.2074 | 5.2074 | 5.2074
2021-08-18 08:00 | 3.2951 | 4.0805 | 4.1455 | 4.424 | 4.3126 | 4.5912 | 1.7947 | 2.7187 | 3.2368 | 3.2368 | 3.5821 | 3.5821 | 2019-10-15 22:00 | 1.6919 | 2.7726 | 4.5513 | 4.5513 | 4.5513 | 4.5513
2021-08-18 09:00 | 3.138 | 3.8859 | 3.9477 | 4.213 | 4.1069 | 4.3722 | 1.7433 | 2.6408 | 3.144 | 3.144 | 3.4794 | 3.4794 | 2019-10-15 23:00 | 1.5547 | 2.5478 | 4.1823 | 4.1823 | 4.1823 | 4.1823
2021-08-18 10:00 | 2.9236 | 3.6204 | 3.6781 | 3.9252 | 3.8264 | 4.0735 | 1.7033 | 2.5802 | 3.0718 | 3.0718 | 3.3996 | 3.3996 | 2019-10-16 | 1.4175 | 2.323 | 3.8133 | 3.8133 | 3.8133 | 3.8133
2021-08-18 11:00 | 2.5092 | 3.1073 | 3.1568 | 3.3689 | 3.284 | 3.4961 | 1.589 | 2.407 | 2.8657 | 2.8657 | 3.1714 | 3.1714 | 2019-10-16 01:00 | 1.3032 | 2.1357 | 3.5058 | 3.5058 | 3.5058 | 3.5058
2021-08-18 12:00 | 2.352 | 2.9126 | 2.959 | 3.1578 | 3.0783 | 3.2771 | 1.5461 | 2.3421 | 2.7883 | 2.7883 | 3.0859 | 3.0859 | 2019-10-16 02:00 | 1.2422 | 2.0358 | 3.3417 | 3.3417 | 3.3417 | 3.3417
2021-08-18 13:00 | 2.1205 | 2.626 | 2.6678 | 2.847 | 2.7753 | 2.9546 | 1.4518 | 2.1992 | 2.6183 | 2.6183 | 2.8976 | 2.8976 | 2019-10-16 03:00 | 1.2422 | 2.0358 | 3.3417 | 3.3417 | 3.3417 | 3.3417
2021-08-18 14:00 | 2.1406 | 2.6507 | 2.693 | 2.8739 | 2.8015 | 2.9825 | 1.3918 | 2.1083 | 2.51 | 2.51 | 2.7779 | 2.7779 | 2019-10-16 04:00 | 1.2879 | 2.1107 | 3.4648 | 3.4648 | 3.4648 | 3.4648
2021-08-18 15:00 | 2.1949 | 2.718 | 2.7613 | 2.9468 | 2.8726 | 3.0581 | 1.4604 | 2.2122 | 2.6337 | 2.6337 | 2.9148 | 2.9148 | 2019-10-16 05:00 | 1.4709 | 2.4105 | 3.9568 | 3.9568 | 3.9568 | 3.9568
2021-08-18 16:00 | 2.6304 | 3.2573 | 3.3092 | 3.5316 | 3.4426 | 3.665 | 1.5404 | 2.3334 | 2.778 | 2.778 | 3.0745 | 3.0745 | 2019-10-16 06:00 | 1.6461 | 2.6977 | 4.4283 | 4.4283 | 4.4283 | 4.4283
2021-08-18 17:00 | 3.2351 | 4.0062 | 4.07 | 4.3435 | 4.2341 | 4.5075 | 1.9805 | 3.0001 | 3.5718 | 3.5718 | 3.9529 | 3.9529 | 2019-10-16 07:00 | 2.0196 | 3.3097 | 5.4329 | 5.4329 | 5.4329 | 5.4329
2021-08-18 18:00 | 3.4495 | 4.2716 | 4.3396 | 4.6312 | 4.5146 | 4.8062 | 2.2234 | 3.3681 | 4.0099 | 4.0099 | 4.4377 | 4.4377 | 2019-10-16 08:00 | 2.1644 | 3.547 | 5.8224 | 5.8224 | 5.8224 | 5.8224
2021-08-18 19:00 | 3.3644 | 4.1663 | 4.2327 | 4.5171 | 4.4033 | 4.6877 | 2.172 | 3.2901 | 3.9171 | 3.9171 | 4.3351 | 4.3351 | 2019-10-16 09:00 | 2.1949 | 3.597 | 5.9044 | 5.9044 | 5.9044 | 5.9044
2021-08-18 20:00 | 2.9979 | 3.7124 | 3.7716 | 4.025 | 3.9236 | 4.177 | 2.0101 | 3.0449 | 3.6251 | 3.6251 | 4.012 | 4.012 | 2019-10-16 10:00 | 2.2863 | 3.7468 | 6.1505 | 6.1505 | 6.1505 | 6.1505
2021-08-18 21:00 | 2.8322 | 3.5072 | 3.563 | 3.8025 | 3.7067 | 3.9461 | 1.8948 | 2.8702 | 3.4171 | 3.4171 | 3.7818 | 3.7818 | 2019-10-16 11:00 | 2.3168 | 3.7968 | 6.2325 | 6.2325 | 6.2325 | 6.2325
2021-08-18 22:00 | 2.5264 | 3.1285 | 3.1783 | 3.3919 | 3.3065 | 3.52 | 1.7462 | 2.6451 | 3.1491 | 3.1491 | 3.4852 | 3.4852 | 2019-10-16 12:00 | 2.3549 | 3.8592 | 6.335 | 6.335 | 6.335 | 6.335
2021-08-18 23:00 | 2.3292 | 2.8843 | 2.9302 | 3.1271 | 3.0484 | 3.2453 | 1.5347 | 2.3247 | 2.7677 | 2.7677 | 3.0631 | 3.0631 | 2019-10-16 13:00 | 2.3625 | 3.8717 | 6.3555 | 6.3555 | 6.3555 | 6.3555
2021-08-19 | 2.1205 | 2.626 | 2.6678 | 2.847 | 2.7753 | 2.9546 | 1.2548 | 1.9008 | 2.2631 | 2.2631 | 2.5045 | 2.5045 | 2019-10-16 14:00 | 2.2025 | 3.6094 | 5.9249 | 5.9249 | 5.9249 | 5.9249
2021-08-19 01:00 | 1.9605 | 2.4278 | 2.4664 | 2.6322 | 2.5659 | 2.7316 | 1.1438 | 1.7327 | 2.0629 | 2.0629 | 2.283 | 2.283 | 2019-10-16 15:00 | 2.2558 | 3.6969 | 6.0685 | 6.0685 | 6.0685 | 6.0685
2021-08-19 02:00 | 1.8748 | 2.3216 | 2.3586 | 2.5171 | 2.4537 | 2.6121 | 1.0917 | 1.6537 | 1.9688 | 1.9688 | 2.1789 | 2.1789 | 2019-10-16 16:00 | 2.2558 | 3.6969 | 6.0685 | 6.0685 | 6.0685 | 6.0685
2021-08-19 03:00 | 1.8976 | 2.3499 | 2.3873 | 2.5478 | 2.4836 | 2.644 | 1.0974 | 1.6624 | 1.9792 | 1.9792 | 2.1903 | 2.1903 | 2019-10-16 17:00 | 2.1339 | 3.497 | 5.7404 | 5.7404 | 5.7404 | 5.7404
2021-08-19 04:00 | 1.9748 | 2.4455 | 2.4844 | 2.6514 | 2.5846 | 2.7515 | 1.166 | 1.7663 | 2.1029 | 2.1029 | 2.3272 | 2.3272 | 2019-10-16 18:00 | 1.9129 | 3.1348 | 5.1459 | 5.1459 | 5.1459 | 5.1459
2021-08-19 05:00 | 2.2234 | 2.7534 | 2.7972 | 2.9852 | 2.91 | 3.0979 | 1.2175 | 1.8442 | 2.1956 | 2.1956 | 2.4299 | 2.4299 | 2019-10-16 19:00 | 1.8062 | 2.96 | 4.8589 | 4.8589 | 4.8589 | 4.8589
2021-08-19 06:00 | 2.7212 | 3.3697 | 3.4234 | 3.6534 | 3.5614 | 3.7914 | 1.3793 | 2.0893 | 2.4875 | 2.4875 | 2.7529 | 2.7529 | 2019-10-16 20:00 | 1.8519 | 3.0349 | 4.9819 | 4.9819 | 4.9819 | 4.9819
2021-08-19 07:00 | 3.2751 | 4.0557 | 4.1203 | 4.3972 | 4.2864 | 4.5633 | 1.6461 | 2.4936 | 2.9687 | 2.9687 | 3.2855 | 3.2855 | 2019-10-16 21:00 | 1.7452 | 2.8601 | 4.6949 | 4.6949 | 4.6949 | 4.6949
2021-08-19 08:00 | 3.3666 | 4.169 | 4.2354 | 4.52 | 4.4061 | 4.6907 | 1.8205 | 2.7577 | 3.2831 | 3.2831 | 3.6335 | 3.6335 | 2019-10-16 22:00 | 1.6842 | 2.7602 | 4.5308 | 4.5308 | 4.5308 | 4.5308
2021-08-19 09:00 | 3.3237 | 4.1159 | 4.1814 | 4.4624 | 4.35 | 4.631 | 1.7747 | 2.6884 | 3.2007 | 3.2007 | 3.5422 | 3.5422 | 2019-10-16 23:00 | 1.5471 | 2.5353 | 4.1618 | 4.1618 | 4.1618 | 4.1618
2021-08-19 10:00 | 3.0093 | 3.7266 | 3.786 | 4.0403 | 3.9386 | 4.193 | 1.769 | 2.6797 | 3.1904 | 3.1904 | 3.5308 | 3.5308 | 2019-10-17 | 1.509 | 2.4729 | 4.0593 | 4.0593 | 4.0593 | 4.0593
2021-08-19 11:00 | 2.6578 | 3.2913 | 3.3437 | 3.5684 | 3.4785 | 3.7032 | 1.5718 | 2.381 | 2.8347 | 2.8347 | 3.1372 | 3.1372 | 2019-10-17 01:00 | 1.4556 | 2.3855 | 3.9158 | 3.9158 | 3.9158 | 3.9158
2021-08-19 12:00 | 2.2663 | 2.8064 | 2.8512 | 3.0427 | 2.9661 | 3.1577 | 1.5547 | 2.355 | 2.8038 | 2.8038 | 3.103 | 3.103 | 2019-10-17 02:00 | 1.3261 | 2.1732 | 3.5673 | 3.5673 | 3.5673 | 3.5673
2021-08-19 13:00 | 2.1348 | 2.6437 | 2.6858 | 2.8662 | 2.794 | 2.9745 | 1.4089 | 2.1343 | 2.541 | 2.541 | 2.8121 | 2.8121 | 2019-10-17 03:00 | 1.3261 | 2.1732 | 3.5673 | 3.5673 | 3.5673 | 3.5673
2021-08-19 14:00 | 2.1606 | 2.6755 | 2.7181 | 2.9008 | 2.8277 | 3.0103 | 1.4432 | 2.1862 | 2.6028 | 2.6028 | 2.8805 | 2.8805 | 2019-10-17 04:00 | 1.387 | 2.2731 | 3.7313 | 3.7313 | 3.7313 | 3.7313
2021-08-19 15:00 | 2.1815 | 2.7015 | 2.7445 | 2.9289 | 2.8552 | 3.0396 | 1.4575 | 2.2079 | 2.6286 | 2.6286 | 2.909 | 2.909 | 2019-10-17 05:00 | 1.4556 | 2.3855 | 3.9158 | 3.9158 | 3.9158 | 3.9158
2021-08-19 16:00 | 2.5069 | 3.1045 | 3.1539 | 3.3658 | 3.2811 | 3.493 | 1.6376 | 2.4806 | 2.9533 | 2.9533 | 3.2684 | 3.2684 | 2019-10-17 06:00 | 1.5852 | 2.5978 | 4.2643 | 4.2643 | 4.2643 | 4.2643
2021-08-19 17:00 | 3.3466 | 4.1442 | 4.2102 | 4.4931 | 4.38 | 4.6628 | 1.9511 | 2.9555 | 3.5187 | 3.5187 | 3.8941 | 3.8941 | 2019-10-17 07:00 | 2.0119 | 3.2972 | 5.4124 | 5.4124 | 5.4124 | 5.4124
2021-08-19 18:00 | 3.5295 | 4.3707 | 4.4403 | 4.7387 | 4.6193 | 4.9177 | 2.1949 | 3.3248 | 3.9583 | 3.9583 | 4.3807 | 4.3807 | 2019-10-17 08:00 | 2.1415 | 3.5095 | 5.7609 | 5.7609 | 5.7609 | 5.7609
2021-08-19 19:00 | 3.3723 | 4.1761 | 4.2426 | 4.5276 | 4.4136 | 4.6987 | 2.2206 | 3.3637 | 4.0047 | 4.0047 | 4.432 | 4.432 | 2019-10-17 09:00 | 2.233 | 3.6594 | 6.007 | 6.007 | 6.007 | 6.007
2021-08-19 20:00 | 3.1837 | 3.9425 | 4.0053 | 4.2744 | 4.1667 | 4.4359 | 2.1606 | 3.2728 | 3.8965 | 3.8965 | 4.3122 | 4.3122 | 2019-10-17 10:00 | 2.1796 | 3.572 | 5.8634 | 5.8634 | 5.8634 | 5.8634
2021-08-19 21:00 | 2.8436 | 3.5213 | 3.5774 | 3.8178 | 3.7216 | 3.962 | 1.8862 | 2.8572 | 3.4017 | 3.4017 | 3.7647 | 3.7647 | 2019-10-17 11:00 | 2.172 | 3.5595 | 5.8429 | 5.8429 | 5.8429 | 5.8429
2021-08-19 22:00 | 2.4737 | 3.0633 | 3.1121 | 3.3212 | 3.2376 | 3.4467 | 1.704 | 2.5813 | 3.0731 | 3.0731 | 3.4011 | 3.4011 | 2019-10-17 12:00 | 2.1491 | 3.522 | 5.7814 | 5.7814 | 5.7814 | 5.7814
2021-08-19 23:00 | 2.2692 | 2.81 | 2.8547 | 3.0466 | 2.9698 | 3.1617 | 1.489 | 2.2555 | 2.6853 | 2.6853 | 2.9718 | 2.9718 | 2019-10-17 13:00 | 2.1644 | 3.547 | 5.8224 | 5.8224 | 5.8224 | 5.8224
2021-08-20 | 2.072 | 2.5658 | 2.6067 | 2.7818 | 2.7118 | 2.8869 | 1.3175 | 1.9957 | 2.376 | 2.376 | 2.6295 | 2.6295 | 2019-10-17 14:00 | 2.111 | 3.4596 | 5.6789 | 5.6789 | 5.6789 | 5.6789
2021-08-20 01:00 | 1.8976 | 2.3499 | 2.3873 | 2.5478 | 2.4836 | 2.644 | 1.135 | 1.7193 | 2.0469 | 2.0469 | 2.2653 | 2.2653 | 2019-10-17 15:00 | 2.1034 | 3.4471 | 5.6584 | 5.6584 | 5.6584 | 5.6584
2021-08-20 02:00 | 1.8919 | 2.3428 | 2.3802 | 2.5401 | 2.4761 | 2.636 | 1.066 | 1.6148 | 1.9225 | 1.9225 | 2.1276 | 2.1276 | 2019-10-17 16:00 | 2.0577 | 3.3721 | 5.5354 | 5.5354 | 5.5354 | 5.5354
2021-08-20 03:00 | 1.8548 | 2.2968 | 2.3334 | 2.4902 | 2.4275 | 2.5843 | 1.0517 | 1.5931 | 1.8967 | 1.8967 | 2.0991 | 2.0991 | 2019-10-17 17:00 | 2.0196 | 3.3097 | 5.4329 | 5.4329 | 5.4329 | 5.4329
2021-08-20 04:00 | 2.0208 | 2.5024 | 2.5422 | 2.7131 | 2.6447 | 2.8155 | 1.0717 | 1.6234 | 1.9328 | 1.9328 | 2.139 | 2.139 | 2019-10-17 18:00 | 1.9053 | 3.1224 | 5.1254 | 5.1254 | 5.1254 | 5.1254
2021-08-20 05:00 | 2.2142 | 2.742 | 2.7857 | 2.9728 | 2.898 | 3.0851 | 1.1551 | 1.7497 | 2.0831 | 2.0831 | 2.3054 | 2.3054 | 2019-10-17 19:00 | 1.9967 | 3.2722 | 5.3714 | 5.3714 | 5.3714 | 5.3714
2021-08-20 06:00 | 2.7369 | 3.3892 | 3.4432 | 3.6746 | 3.582 | 3.8134 | 1.286 | 1.9481 | 2.3193 | 2.3193 | 2.5668 | 2.5668 | 2019-10-17 20:00 | 1.829 | 2.9975 | 4.9204 | 4.9204 | 4.9204 | 4.9204
2021-08-20 07:00 | 3.2065 | 3.9708 | 4.034 | 4.3051 | 4.1967 | 4.4677 | 1.669 | 2.5282 | 3.01 | 3.01 | 3.3311 | 3.3311 | 2019-10-17 21:00 | 1.7757 | 2.91 | 4.7769 | 4.7769 | 4.7769 | 4.7769
2021-08-20 08:00 | 3.186 | 3.9454 | 4.0082 | 4.2775 | 4.1698 | 4.4391 | 1.6519 | 2.5022 | 2.979 | 2.979 | 3.2969 | 3.2969 | 2019-10-17 22:00 | 1.6766 | 2.7477 | 4.5103 | 4.5103 | 4.5103 | 4.5103
2021-08-20 09:00 | 3.1179 | 3.8611 | 3.9226 | 4.1861 | 4.0807 | 4.3443 | 1.6147 | 2.446 | 2.912 | 2.912 | 3.2228 | 3.2228 | 2019-10-17 23:00 | 1.5928 | 2.6103 | 4.2848 | 4.2848 | 4.2848 | 4.2848
2021-08-20 10:00 | 2.715 | 3.3621 | 3.4156 | 3.6451 | 3.5533 | 3.7828 | 1.6233 | 2.4589 | 2.9275 | 2.9275 | 3.2399 | 3.2399 | 2019-10-18 | 1.4099 | 2.3105 | 3.7928 | 3.7928 | 3.7928 | 3.7928
2021-08-20 11:00 | 2.312 | 2.8631 | 2.9087 | 3.1041 | 3.0259 | 3.2214 | 1.3832 | 2.0953 | 2.4946 | 2.4946 | 2.7607 | 2.7607 | 2019-10-18 01:00 | 1.3184 | 2.1607 | 3.5468 | 3.5468 | 3.5468 | 3.5468
2021-08-20 12:00 | 2.2063 | 2.7321 | 2.7756 | 2.9621 | 2.8875 | 3.0741 | 1.4032 | 2.1256 | 2.5306 | 2.5306 | 2.8007 | 2.8007 | 2019-10-18 02:00 | 1.2879 | 2.1107 | 3.4648 | 3.4648 | 3.4648 | 3.4648
2021-08-20 13:00 | 2.1463 | 2.6578 | 2.7001 | 2.8816 | 2.809 | 2.9904 | 1.3775 | 2.0866 | 2.4843 | 2.4843 | 2.7493 | 2.7493 | 2019-10-18 03:00 | 1.2879 | 2.1107 | 3.4648 | 3.4648 | 3.4648 | 3.4648
2021-08-20 14:00 | 2.1663 | 2.6826 | 2.7253 | 2.9084 | 2.8352 | 3.0183 | 1.3461 | 2.039 | 2.4276 | 2.4276 | 2.6866 | 2.6866 | 2019-10-18 04:00 | 1.3413 | 2.1981 | 3.6083 | 3.6083 | 3.6083 | 3.6083
2021-08-20 15:00 | 2.2377 | 2.7711 | 2.8152 | 3.0044 | 2.9287 | 3.1179 | 1.4347 | 2.1732 | 2.5873 | 2.5873 | 2.8634 | 2.8634 | 2019-10-18 05:00 | 1.4556 | 2.3855 | 3.9158 | 3.9158 | 3.9158 | 3.9158
2021-08-20 16:00 | 2.5092 | 3.1073 | 3.1568 | 3.3689 | 3.284 | 3.4961 | 1.5661 | 2.3724 | 2.8244 | 2.8244 | 3.1258 | 3.1258 | 2019-10-18 06:00 | 1.7071 | 2.7976 | 4.5923 | 4.5923 | 4.5923 | 4.5923
2021-08-20 17:00 | 2.9836 | 3.6947 | 3.7536 | 4.0058 | 3.9049 | 4.1571 | 1.9902 | 3.0148 | 3.5892 | 3.5892 | 3.9722 | 3.9722 | 2019-10-18 07:00 | 1.9815 | 3.2472 | 5.3304 | 5.3304 | 5.3304 | 5.3304
2021-08-20 18:00 | 3.158 | 3.9106 | 3.9729 | 4.2399 | 4.1331 | 4.4 | 1.9919 | 3.0174 | 3.5924 | 3.5924 | 3.9757 | 3.9757 | 2019-10-18 08:00 | 2.111 | 3.4596 | 5.6789 | 5.6789 | 5.6789 | 5.6789
2021-08-20 19:00 | 3.03 | 3.7522 | 3.8119 | 4.0681 | 3.9656 | 4.2218 | 2.0005 | 3.0304 | 3.6078 | 3.6078 | 3.9928 | 3.9928 | 2019-10-18 09:00 | 2.0653 | 3.3846 | 5.5559 | 5.5559 | 5.5559 | 5.5559
2021-08-20 20:00 | 2.855 | 3.5355 | 3.5918 | 3.8331 | 3.7366 | 3.978 | 2.0034 | 3.0347 | 3.613 | 3.613 | 3.9985 | 3.9985 | 2019-10-18 10:00 | 2.1415 | 3.5095 | 5.7609 | 5.7609 | 5.7609 | 5.7609
2021-08-20 21:00 | 2.6259 | 3.2518 | 3.3036 | 3.5255 | 3.4367 | 3.6587 | 1.789 | 2.71 | 3.2264 | 3.2264 | 3.5707 | 3.5707 | 2019-10-18 11:00 | 2.172 | 3.5595 | 5.8429 | 5.8429 | 5.8429 | 5.8429
2021-08-20 22:00 | 2.3292 | 2.8843 | 2.9302 | 3.1271 | 3.0484 | 3.2453 | 1.5804 | 2.394 | 2.8502 | 2.8502 | 3.1543 | 3.1543 | 2019-10-18 12:00 | 2.172 | 3.5595 | 5.8429 | 5.8429 | 5.8429 | 5.8429
2021-08-20 23:00 | 2.2263 | 2.7569 | 2.8008 | 2.989 | 2.9137 | 3.1019 | 1.4159 | 2.1449 | 2.5536 | 2.5536 | 2.826 | 2.826 | 2019-10-18 13:00 | 2.0958 | 3.4346 | 5.6379 | 5.6379 | 5.6379 | 5.6379
2021-08-21 | 1.9662 | 2.4349 | 2.4736 | 2.6398 | 2.5734 | 2.7396 | 1.2203 | 1.8485 | 2.2008 | 2.2008 | 2.4356 | 2.4356 | 2019-10-18 14:00 | 2.2025 | 3.6094 | 5.9249 | 5.9249 | 5.9249 | 5.9249
2021-08-21 01:00 | 1.8037 | 2.2336 | 2.2691 | 2.4216 | 2.3606 | 2.5131 | 1.0974 | 1.6624 | 1.9792 | 1.9792 | 2.1903 | 2.1903 | 2019-10-18 15:00 | 2.1339 | 3.497 | 5.7404 | 5.7404 | 5.7404 | 5.7404
2021-08-21 02:00 | 1.729 | 2.1411 | 2.1752 | 2.3214 | 2.2629 | 2.4091 | 0.98325 | 1.4894 | 1.7732 | 1.7732 | 1.9625 | 1.9625 | 2019-10-18 16:00 | 2.0348 | 3.3347 | 5.4739 | 5.4739 | 5.4739 | 5.4739
2021-08-21 03:00 | 1.729 | 2.1411 | 2.1752 | 2.3214 | 2.2629 | 2.4091 | 1.0031 | 1.5195 | 1.8091 | 1.8091 | 2.0021 | 2.0021 | 2019-10-18 17:00 | 2.0196 | 3.3097 | 5.4329 | 5.4329 | 5.4329 | 5.4329
2021-08-21 04:00 | 1.7176 | 2.127 | 2.1608 | 2.306 | 2.2479 | 2.3931 | 0.96882 | 1.4676 | 1.7472 | 1.7472 | 1.9337 | 1.9337 | 2019-10-18 18:00 | 1.8443 | 3.0224 | 4.9614 | 4.9614 | 4.9614 | 4.9614
2021-08-21 05:00 | 1.8776 | 2.3251 | 2.3622 | 2.5209 | 2.4574 | 2.6161 | 0.96025 | 1.4546 | 1.7318 | 1.7318 | 1.9165 | 1.9165 | 2019-10-18 19:00 | 1.89 | 3.0974 | 5.0844 | 5.0844 | 5.0844 | 5.0844
2021-08-21 06:00 | 2.0034 | 2.4809 | 2.5204 | 2.6897 | 2.622 | 2.7913 | 1.0717 | 1.6234 | 1.9328 | 1.9328 | 2.139 | 2.139 | 2019-10-18 20:00 | 1.8214 | 2.985 | 4.8999 | 4.8999 | 4.8999 | 4.8999
2021-08-21 07:00 | 2.1891 | 2.7109 | 2.7541 | 2.9391 | 2.8651 | 3.0502 | 1.2359 | 1.8721 | 2.2288 | 2.2288 | 2.4666 | 2.4666 | 2019-10-18 21:00 | 1.7147 | 2.8101 | 4.6128 | 4.6128 | 4.6128 | 4.6128
2021-08-21 08:00 | 2.1434 | 2.6543 | 2.6965 | 2.8777 | 2.8053 | 2.9864 | 1.3175 | 1.9957 | 2.376 | 2.376 | 2.6295 | 2.6295 | 2019-10-18 22:00 | 1.6995 | 2.7851 | 4.5718 | 4.5718 | 4.5718 | 4.5718
2021-08-21 09:00 | 2.052 | 2.541 | 2.5815 | 2.755 | 2.6856 | 2.859 | 1.286 | 1.9481 | 2.3193 | 2.3193 | 2.5668 | 2.5668 | 2019-10-18 23:00 | 1.509 | 2.4729 | 4.0593 | 4.0593 | 4.0593 | 4.0593
2021-08-21 10:00 | 2.0262 | 2.5092 | 2.5491 | 2.7204 | 2.6519 | 2.8232 | 1.3689 | 2.0737 | 2.4688 | 2.4688 | 2.7322 | 2.7322 | 2019-10-19 | 1.3946 | 2.2856 | 3.7518 | 3.7518 | 3.7518 | 3.7518
2021-08-21 11:00 | 1.8805 | 2.3287 | 2.3658 | 2.5247 | 2.4611 | 2.6201 | 1.3575 | 2.0563 | 2.4482 | 2.4482 | 2.7094 | 2.7094 | 2019-10-19 01:00 | 1.3413 | 2.1981 | 3.6083 | 3.6083 | 3.6083 | 3.6083
2021-08-21 12:00 | 1.9919 | 2.4667 | 2.506 | 2.6744 | 2.607 | 2.7754 | 1.3632 | 2.065 | 2.4585 | 2.4585 | 2.7208 | 2.7208 | 2019-10-19 02:00 | 1.2575 | 2.0608 | 3.3828 | 3.3828 | 3.3828 | 3.3828
2021-08-21 13:00 | 1.8862 | 2.3358 | 2.373 | 2.5324 | 2.4686 | 2.6281 | 1.4089 | 2.1343 | 2.541 | 2.541 | 2.8121 | 2.8121 | 2019-10-19 03:00 | 1.3184 | 2.1607 | 3.5468 | 3.5468 | 3.5468 | 3.5468
2021-08-21 14:00 | 2.0234 | 2.5056 | 2.5455 | 2.7166 | 2.6482 | 2.8192 | 1.3461 | 2.039 | 2.4276 | 2.4276 | 2.6866 | 2.6866 | 2019-10-19 04:00 | 1.2956 | 2.1232 | 3.4853 | 3.4853 | 3.4853 | 3.4853
2021-08-21 15:00 | 2.0491 | 2.5375 | 2.5779 | 2.7511 | 2.6818 | 2.855 | 1.4146 | 2.1429 | 2.5513 | 2.5513 | 2.8235 | 2.8235 | 2019-10-19 05:00 | 1.4327 | 2.348 | 3.8543 | 3.8543 | 3.8543 | 3.8543
2021-08-21 16:00 | 2.1606 | 2.6755 | 2.7181 | 2.9008 | 2.8277 | 3.0103 | 1.4775 | 2.2382 | 2.6646 | 2.6646 | 2.949 | 2.949 | 2019-10-19 06:00 | 1.4937 | 2.4479 | 4.0183 | 4.0183 | 4.0183 | 4.0183
2021-08-21 17:00 | 2.7411 | 3.3944 | 3.4485 | 3.6802 | 3.5875 | 3.8192 | 1.7739 | 2.6871 | 3.1991 | 3.1991 | 3.5405 | 3.5405 | 2019-10-19 07:00 | 1.6385 | 2.6852 | 4.4078 | 4.4078 | 4.4078 | 4.4078
2021-08-21 18:00 | 2.8693 | 3.5532 | 3.6098 | 3.8523 | 3.7553 | 3.9979 | 1.9662 | 2.9784 | 3.546 | 3.546 | 3.9244 | 3.9244 | 2019-10-19 08:00 | 1.8595 | 3.0474 | 5.0024 | 5.0024 | 5.0024 | 5.0024
2021-08-21 19:00 | 2.7579 | 3.4152 | 3.4696 | 3.7027 | 3.6094 | 3.8426 | 1.9234 | 2.9135 | 3.4687 | 3.4687 | 3.8388 | 3.8388 | 2019-10-19 09:00 | 1.7833 | 2.9225 | 4.7974 | 4.7974 | 4.7974 | 4.7974
2021-08-21 20:00 | 2.6635 | 3.2984 | 3.3509 | 3.5761 | 3.486 | 3.7112 | 1.7498 | 2.6506 | 3.1557 | 3.1557 | 3.4924 | 3.4924 | 2019-10-19 10:00 | 1.8976 | 3.1099 | 5.1049 | 5.1049 | 5.1049 | 5.1049
2021-08-21 21:00 | 2.4006 | 2.9728 | 3.0201 | 3.2231 | 3.1419 | 3.3448 | 1.6955 | 2.5684 | 3.0578 | 3.0578 | 3.3841 | 3.3841 | 2019-10-19 11:00 | 1.8671 | 3.0599 | 5.0229 | 5.0229 | 5.0229 | 5.0229
2021-08-21 22:00 | 2.2892 | 2.8348 | 2.8799 | 3.0734 | 2.996 | 3.1895 | 1.5375 | 2.3291 | 2.7729 | 2.7729 | 3.0688 | 3.0688 | 2019-10-19 12:00 | 1.9205 | 3.1473 | 5.1664 | 5.1664 | 5.1664 | 5.1664
2021-08-21 23:00 | 2.1891 | 2.7109 | 2.7541 | 2.9391 | 2.8651 | 3.0502 | 1.3432 | 2.0347 | 2.4224 | 2.4224 | 2.6809 | 2.6809 | 2019-10-19 13:00 | 1.9053 | 3.1224 | 5.1254 | 5.1254 | 5.1254 | 5.1254
2021-08-22 | 1.8633 | 2.3074 | 2.3442 | 2.5017 | 2.4387 | 2.5962 | 1.2489 | 1.8918 | 2.2523 | 2.2523 | 2.4927 | 2.4927 | 2019-10-19 14:00 | 1.829 | 2.9975 | 4.9204 | 4.9204 | 4.9204 | 4.9204
2021-08-22 01:00 | 1.8176 | 2.2508 | 2.2867 | 2.4403 | 2.3789 | 2.5325 | 1.0603 | 1.6061 | 1.9122 | 1.9122 | 2.1162 | 2.1162 | 2019-10-19 15:00 | 1.951 | 3.1973 | 5.2484 | 5.2484 | 5.2484 | 5.2484
2021-08-22 02:00 | 1.7204 | 2.1305 | 2.1644 | 2.3099 | 2.2517 | 2.3971 | 1.0037 | 1.5203 | 1.81 | 1.81 | 2.0032 | 2.0032 | 2019-10-19 16:00 | 2.0272 | 3.3222 | 5.4534 | 5.4534 | 5.4534 | 5.4534
2021-08-22 03:00 | 1.7119 | 2.1199 | 2.1536 | 2.2984 | 2.2405 | 2.3852 | 0.96268 | 1.4583 | 1.7361 | 1.7361 | 1.9214 | 1.9214 | 2019-10-19 17:00 | 1.8519 | 3.0349 | 4.9819 | 4.9819 | 4.9819 | 4.9819
2021-08-22 04:00 | 1.8061 | 2.2366 | 2.2722 | 2.4249 | 2.3638 | 2.5165 | 0.9631 | 1.4589 | 1.7369 | 1.7369 | 1.9223 | 1.9223 | 2019-10-19 18:00 | 1.8367 | 3.0099 | 4.9409 | 4.9409 | 4.9409 | 4.9409
2021-08-22 05:00 | 1.8748 | 2.3216 | 2.3586 | 2.5171 | 2.4537 | 2.6121 | 1.043 | 1.58 | 1.881 | 1.881 | 2.0818 | 2.0818 | 2019-10-19 19:00 | 1.6919 | 2.7726 | 4.5513 | 4.5513 | 4.5513 | 4.5513
2021-08-22 06:00 | 2.0405 | 2.5268 | 2.5671 | 2.7396 | 2.6706 | 2.8431 | 1.1346 | 1.7187 | 2.0462 | 2.0462 | 2.2645 | 2.2645 | 2019-10-19 20:00 | 1.7605 | 2.8851 | 4.7359 | 4.7359 | 4.7359 | 4.7359
2021-08-22 07:00 | 2.2349 | 2.7675 | 2.8116 | 3.0005 | 2.925 | 3.1139 | 1.1974 | 1.8139 | 2.1596 | 2.1596 | 2.39 | 2.39 | 2019-10-19 21:00 | 1.6919 | 2.7726 | 4.5513 | 4.5513 | 4.5513 | 4.5513
2021-08-22 08:00 | 2.2091 | 2.7357 | 2.7792 | 2.966 | 2.8913 | 3.078 | 1.3832 | 2.0953 | 2.4946 | 2.4946 | 2.7607 | 2.7607 | 2019-10-19 22:00 | 1.6157 | 2.6478 | 4.3463 | 4.3463 | 4.3463 | 4.3463
2021-08-22 09:00 | 2.1977 | 2.7215 | 2.7649 | 2.9506 | 2.8763 | 3.0621 | 1.3889 | 2.104 | 2.5049 | 2.5049 | 2.7722 | 2.7722 | 2019-10-19 23:00 | 1.6004 | 2.6228 | 4.3053 | 4.3053 | 4.3053 | 4.3053
2021-08-22 10:00 | 2.0377 | 2.5233 | 2.5635 | 2.7358 | 2.6669 | 2.8391 | 1.4432 | 2.1862 | 2.6028 | 2.6028 | 2.8805 | 2.8805 | 2019-10-20 | 1.3946 | 2.2856 | 3.7518 | 3.7518 | 3.7518 | 3.7518
2021-08-22 11:00 | 1.8098 | 2.2412 | 2.2769 | 2.4298 | 2.3687 | 2.5216 | 1.3489 | 2.0433 | 2.4327 | 2.4327 | 2.6923 | 2.6923 | 2019-10-20 01:00 | 1.3032 | 2.1357 | 3.5058 | 3.5058 | 3.5058 | 3.5058
2021-08-22 12:00 | 1.8176 | 2.2508 | 2.2867 | 2.4403 | 2.3789 | 2.5325 | 1.3232 | 2.0044 | 2.3863 | 2.3863 | 2.641 | 2.641 | 2019-10-20 02:00 | 1.2575 | 2.0608 | 3.3828 | 3.3828 | 3.3828 | 3.3828
2021-08-22 13:00 | 1.7376 | 2.1517 | 2.186 | 2.3329 | 2.2741 | 2.421 | 1.3261 | 2.0087 | 2.3915 | 2.3915 | 2.6467 | 2.6467 | 2019-10-20 03:00 | 1.2575 | 2.0608 | 3.3828 | 3.3828 | 3.3828 | 3.3828
2021-08-22 14:00 | 1.7147 | 2.1234 | 2.1572 | 2.3022 | 2.2442 | 2.3892 | 1.2632 | 1.9135 | 2.2781 | 2.2781 | 2.5212 | 2.5212 | 2019-10-20 04:00 | 1.3108 | 2.1482 | 3.5263 | 3.5263 | 3.5263 | 3.5263
2021-08-22 15:00 | 1.7919 | 2.219 | 2.2543 | 2.4058 | 2.3452 | 2.4967 | 1.3518 | 2.0477 | 2.4379 | 2.4379 | 2.698 | 2.698 | 2019-10-20 05:00 | 1.4556 | 2.3855 | 3.9158 | 3.9158 | 3.9158 | 3.9158
2021-08-22 16:00 | 2.0348 | 2.5198 | 2.5599 | 2.7319 | 2.6631 | 2.8351 | 1.4661 | 2.2208 | 2.644 | 2.644 | 2.9262 | 2.9262 | 2019-10-20 06:00 | 1.3794 | 2.2606 | 3.7108 | 3.7108 | 3.7108 | 3.7108
2021-08-22 17:00 | 2.6864 | 3.3267 | 3.3797 | 3.6068 | 3.5159 | 3.743 | 1.6433 | 2.4893 | 2.9636 | 2.9636 | 3.2798 | 3.2798 | 2019-10-20 07:00 | 1.5928 | 2.6103 | 4.2848 | 4.2848 | 4.2848 | 4.2848
2021-08-22 18:00 | 2.9122 | 3.6063 | 3.6637 | 3.9099 | 3.8114 | 4.0576 | 1.8319 | 2.775 | 3.3038 | 3.3038 | 3.6563 | 3.6563 | 2019-10-20 08:00 | 1.8595 | 3.0474 | 5.0024 | 5.0024 | 5.0024 | 5.0024
2021-08-22 19:00 | 2.7921 | 3.4576 | 3.5127 | 3.7487 | 3.6543 | 3.8903 | 1.809 | 2.7403 | 3.2625 | 3.2625 | 3.6106 | 3.6106 | 2019-10-20 09:00 | 1.8367 | 3.0099 | 4.9409 | 4.9409 | 4.9409 | 4.9409
2021-08-22 20:00 | 2.5321 | 3.1356 | 3.1855 | 3.3996 | 3.3139 | 3.528 | 1.8005 | 2.7274 | 3.2471 | 3.2471 | 3.5935 | 3.5935 | 2019-10-20 10:00 | 1.8671 | 3.0599 | 5.0229 | 5.0229 | 5.0229 | 5.0229
2021-08-22 21:00 | 2.3778 | 2.9445 | 2.9914 | 3.1924 | 3.112 | 3.313 | 1.649 | 2.4979 | 2.9739 | 2.9739 | 3.2912 | 3.2912 | 2019-10-20 11:00 | 1.8367 | 3.0099 | 4.9409 | 4.9409 | 4.9409 | 4.9409
2021-08-22 22:00 | 2.1463 | 2.6578 | 2.7001 | 2.8816 | 2.809 | 2.9904 | 1.4804 | 2.2425 | 2.6698 | 2.6698 | 2.9547 | 2.9547 | 2019-10-20 12:00 | 1.829 | 2.9975 | 4.9204 | 4.9204 | 4.9204 | 4.9204
2021-08-22 23:00 | 1.9949 | 2.4704 | 2.5098 | 2.6784 | 2.6109 | 2.7796 | 1.2291 | 1.8618 | 2.2166 | 2.2166 | 2.4531 | 2.4531 | 2019-10-20 13:00 | 1.8519 | 3.0349 | 4.9819 | 4.9819 | 4.9819 | 4.9819
2021-08-23 | 1.8262 | 2.2614 | 2.2975 | 2.4518 | 2.3901 | 2.5445 | 1.1004 | 1.6669 | 1.9845 | 1.9845 | 2.1962 | 2.1962 | 2019-10-20 14:00 | 1.8824 | 3.0849 | 5.0639 | 5.0639 | 5.0639 | 5.0639
2021-08-23 01:00 | 1.669 | 2.0668 | 2.0997 | 2.2408 | 2.1844 | 2.3254 | 0.97453 | 1.4762 | 1.7575 | 1.7575 | 1.9451 | 1.9451 | 2019-10-20 15:00 | 1.8824 | 3.0849 | 5.0639 | 5.0639 | 5.0639 | 5.0639
2021-08-23 02:00 | 1.6002 | 1.9816 | 2.0132 | 2.1485 | 2.0944 | 2.2296 | 0.94348 | 1.4292 | 1.7015 | 1.7015 | 1.8831 | 1.8831 | 2019-10-20 16:00 | 1.9053 | 3.1224 | 5.1254 | 5.1254 | 5.1254 | 5.1254
2021-08-23 03:00 | 1.6033 | 1.9854 | 2.017 | 2.1525 | 2.0983 | 2.2339 | 0.86594 | 1.3117 | 1.5617 | 1.5617 | 1.7283 | 1.7283 | 2019-10-20 17:00 | 1.8367 | 3.0099 | 4.9409 | 4.9409 | 4.9409 | 4.9409
2021-08-23 04:00 | 1.6853 | 2.0869 | 2.1202 | 2.2627 | 2.2057 | 2.3481 | 0.86879 | 1.3161 | 1.5668 | 1.5668 | 1.734 | 1.734 | 2019-10-20 18:00 | 1.6842 | 2.7602 | 4.5308 | 4.5308 | 4.5308 | 4.5308
2021-08-23 05:00 | 1.8116 | 2.2434 | 2.2792 | 2.4323 | 2.3711 | 2.5242 | 0.8888 | 1.3464 | 1.6029 | 1.6029 | 1.7739 | 1.7739 | 2019-10-20 19:00 | 1.7605 | 2.8851 | 4.7359 | 4.7359 | 4.7359 | 4.7359
2021-08-23 06:00 | 2.2692 | 2.81 | 2.8547 | 3.0466 | 2.9698 | 3.1617 | 1.0203 | 1.5455 | 1.84 | 1.84 | 2.0363 | 2.0363 | 2019-10-20 20:00 | 1.6842 | 2.7602 | 4.5308 | 4.5308 | 4.5308 | 4.5308
2021-08-23 07:00 | 2.3949 | 2.9657 | 3.0129 | 3.2154 | 3.1344 | 3.3369 | 1.2346 | 1.8702 | 2.2266 | 2.2266 | 2.4641 | 2.4641 | 2019-10-20 21:00 | 1.6842 | 2.7602 | 4.5308 | 4.5308 | 4.5308 | 4.5308
2021-08-23 08:00 | 2.3635 | 2.9268 | 2.9734 | 3.1732 | 3.0933 | 3.2931 | 1.2937 | 1.9596 | 2.333 | 2.333 | 2.582 | 2.582 | 2019-10-20 22:00 | 1.5623 | 2.5603 | 4.2028 | 4.2028 | 4.2028 | 4.2028
2021-08-23 09:00 | 2.132 | 2.6401 | 2.6822 | 2.8624 | 2.7903 | 2.9705 | 1.3289 | 2.013 | 2.3966 | 2.3966 | 2.6524 | 2.6524 | 2019-10-20 23:00 | 1.4937 | 2.4479 | 4.0183 | 4.0183 | 4.0183 | 4.0183
2021-08-23 10:00 | 2.0177 | 2.4986 | 2.5383 | 2.7089 | 2.6407 | 2.8112 | 1.1632 | 1.762 | 2.0977 | 2.0977 | 2.3215 | 2.3215 | 2019-10-21 | 1.3946 | 2.2856 | 3.7518 | 3.7518 | 3.7518 | 3.7518
2021-08-23 11:00 | 1.8748 | 2.3216 | 2.3586 | 2.5171 | 2.4537 | 2.6121 | 1.186 | 1.7966 | 2.1389 | 2.1389 | 2.3672 | 2.3672 | 2019-10-21 01:00 | 1.2879 | 2.1107 | 3.4648 | 3.4648 | 3.4648 | 3.4648
2021-08-23 12:00 | 2.0605 | 2.5516 | 2.5923 | 2.7665 | 2.6968 | 2.871 | 1.3403 | 2.0304 | 2.4173 | 2.4173 | 2.6752 | 2.6752 | 2019-10-21 02:00 | 1.2575 | 2.0608 | 3.3828 | 3.3828 | 3.3828 | 3.3828
2021-08-23 13:00 | 2.0291 | 2.5127 | 2.5527 | 2.7243 | 2.6556 | 2.8272 | 1.3346 | 2.0217 | 2.4069 | 2.4069 | 2.6638 | 2.6638 | 2019-10-21 03:00 | 1.2422 | 2.0358 | 3.3417 | 3.3417 | 3.3417 | 3.3417
2021-08-23 14:00 | 2.0948 | 2.5941 | 2.6354 | 2.8125 | 2.7417 | 2.9188 | 1.3203 | 2.0001 | 2.3812 | 2.3812 | 2.6353 | 2.6353 | 2019-10-21 04:00 | 1.2956 | 2.1232 | 3.4853 | 3.4853 | 3.4853 | 3.4853
2021-08-23 15:00 | 2.192 | 2.7144 | 2.7577 | 2.943 | 2.8688 | 3.0541 | 1.3603 | 2.0607 | 2.4533 | 2.4533 | 2.7151 | 2.7151 | 2019-10-21 05:00 | 1.4937 | 2.4479 | 4.0183 | 4.0183 | 4.0183 | 4.0183
2021-08-23 16:00 | 2.3292 | 2.8843 | 2.9302 | 3.1271 | 3.0484 | 3.2453 | 1.4747 | 2.2338 | 2.6595 | 2.6595 | 2.9433 | 2.9433 | 2019-10-21 06:00 | 1.6157 | 2.6478 | 4.3463 | 4.3463 | 4.3463 | 4.3463
2021-08-23 17:00 | 2.835 | 3.5107 | 3.5666 | 3.8063 | 3.7104 | 3.9501 | 1.6919 | 2.5628 | 3.0512 | 3.0512 | 3.3768 | 3.3768 | 2019-10-21 07:00 | 1.9129 | 3.1348 | 5.1459 | 5.1459 | 5.1459 | 5.1459
2021-08-23 18:00 | 3.0979 | 3.8363 | 3.8974 | 4.1593 | 4.0545 | 4.3164 | 1.8719 | 2.8356 | 3.3759 | 3.3759 | 3.7361 | 3.7361 | 2019-10-21 08:00 | 2.1339 | 3.497 | 5.7404 | 5.7404 | 5.7404 | 5.7404
2021-08-23 19:00 | 2.9336 | 3.6328 | 3.6906 | 3.9386 | 3.8394 | 4.0874 | 1.8348 | 2.7793 | 3.3089 | 3.3089 | 3.662 | 3.662 | 2019-10-21 09:00 | 2.0805 | 3.4096 | 5.5969 | 5.5969 | 5.5969 | 5.5969
2021-08-23 20:00 | 2.8493 | 3.5284 | 3.5846 | 3.8255 | 3.7291 | 3.97 | 1.809 | 2.7403 | 3.2625 | 3.2625 | 3.6106 | 3.6106 | 2019-10-21 10:00 | 2.0882 | 3.4221 | 5.6174 | 5.6174 | 5.6174 | 5.6174
2021-08-23 21:00 | 2.4978 | 3.0931 | 3.1424 | 3.3535 | 3.2691 | 3.4802 | 1.6493 | 2.4984 | 2.9745 | 2.9745 | 3.2918 | 3.2918 | 2019-10-21 11:00 | 2.0577 | 3.3721 | 5.5354 | 5.5354 | 5.5354 | 5.5354
2021-08-23 22:00 | 2.2234 | 2.7534 | 2.7972 | 2.9852 | 2.91 | 3.0979 | 1.4146 | 2.1429 | 2.5513 | 2.5513 | 2.8235 | 2.8235 | 2019-10-21 12:00 | 2.1796 | 3.572 | 5.8634 | 5.8634 | 5.8634 | 5.8634
2021-08-23 23:00 | 2.1177 | 2.6224 | 2.6642 | 2.8432 | 2.7716 | 2.9506 | 1.2575 | 1.9048 | 2.2678 | 2.2678 | 2.5098 | 2.5098 | 2019-10-21 13:00 | 2.172 | 3.5595 | 5.8429 | 5.8429 | 5.8429 | 5.8429
2021-08-24 | 1.8862 | 2.3358 | 2.373 | 2.5324 | 2.4686 | 2.6281 | 1.0747 | 1.628 | 1.9382 | 1.9382 | 2.145 | 2.145 | 2019-10-21 14:00 | 2.233 | 3.6594 | 6.007 | 6.007 | 6.007 | 6.007
2021-08-24 01:00 | 1.7605 | 2.18 | 2.2148 | 2.3636 | 2.3041 | 2.4529 | 0.96596 | 1.4632 | 1.7421 | 1.7421 | 1.928 | 1.928 | 2019-10-21 15:00 | 2.2482 | 3.6844 | 6.048 | 6.048 | 6.048 | 6.048
2021-08-24 02:00 | 1.729 | 2.1411 | 2.1752 | 2.3214 | 2.2629 | 2.4091 | 0.94881 | 1.4373 | 1.7111 | 1.7111 | 1.8937 | 1.8937 | 2019-10-21 16:00 | 2.2253 | 3.6469 | 5.9865 | 5.9865 | 5.9865 | 5.9865
2021-08-24 03:00 | 1.6547 | 2.0491 | 2.0818 | 2.2217 | 2.1657 | 2.3056 | 0.95453 | 1.4459 | 1.7215 | 1.7215 | 1.9051 | 1.9051 | 2019-10-21 17:00 | 2.1567 | 3.5345 | 5.8019 | 5.8019 | 5.8019 | 5.8019
2021-08-24 04:00 | 1.786 | 2.2117 | 2.247 | 2.3979 | 2.3375 | 2.4885 | 0.95453 | 1.4459 | 1.7215 | 1.7215 | 1.9051 | 1.9051 | 2019-10-21 18:00 | 2.0958 | 3.4346 | 5.6379 | 5.6379 | 5.6379 | 5.6379
2021-08-24 05:00 | 1.9363 | 2.3978 | 2.436 | 2.5997 | 2.5342 | 2.6979 | 1.0403 | 1.5758 | 1.8761 | 1.8761 | 2.0763 | 2.0763 | 2019-10-21 19:00 | 2.0043 | 3.2847 | 5.3919 | 5.3919 | 5.3919 | 5.3919
2021-08-24 06:00 | 2.5635 | 3.1745 | 3.2251 | 3.4418 | 3.3551 | 3.5718 | 1.1632 | 1.762 | 2.0977 | 2.0977 | 2.3215 | 2.3215 | 2019-10-21 20:00 | 1.9357 | 3.1723 | 5.2074 | 5.2074 | 5.2074 | 5.2074
2021-08-24 07:00 | 2.9751 | 3.6841 | 3.7428 | 3.9943 | 3.8937 | 4.1452 | 1.5833 | 2.3983 | 2.8554 | 2.8554 | 3.16 | 3.16 | 2019-10-21 21:00 | 1.8062 | 2.96 | 4.8589 | 4.8589 | 4.8589 | 4.8589
2021-08-24 08:00 | 3.3752 | 4.1796 | 4.2462 | 4.5315 | 4.4174 | 4.7027 | 1.7347 | 2.6278 | 3.1285 | 3.1285 | 3.4623 | 3.4623 | 2019-10-21 22:00 | 1.5394 | 2.5229 | 4.1413 | 4.1413 | 4.1413 | 4.1413
2021-08-24 09:00 | 3.4495 | 4.2716 | 4.3396 | 4.6312 | 4.5146 | 4.8062 | 1.8319 | 2.775 | 3.3038 | 3.3038 | 3.6563 | 3.6563 | 2019-10-21 23:00 | 1.4709 | 2.4105 | 3.9568 | 3.9568 | 3.9568 | 3.9568
2021-08-24 10:00 | 3.5238 | 4.3636 | 4.4331 | 4.731 | 4.6119 | 4.9097 | 1.8405 | 2.788 | 3.3192 | 3.3192 | 3.6734 | 3.6734 | 2019-10-22 | 1.3565 | 2.2231 | 3.6493 | 3.6493 | 3.6493 | 3.6493
2021-08-24 11:00 | 3.4237 | 4.2398 | 4.3073 | 4.5967 | 4.4809 | 4.7704 | 1.8919 | 2.8659 | 3.412 | 3.412 | 3.7761 | 3.7761 | 2019-10-22 01:00 | 1.2346 | 2.0233 | 3.3212 | 3.3212 | 3.3212 | 3.3212
2021-08-24 12:00 | 3.3952 | 4.2044 | 4.2713 | 4.5583 | 4.4435 | 4.7305 | 1.8833 | 2.8529 | 3.3965 | 3.3965 | 3.7589 | 3.7589 | 2019-10-22 02:00 | 1.1965 | 1.9608 | 3.2187 | 3.2187 | 3.2187 | 3.2187
2021-08-24 13:00 | 3.2494 | 4.0239 | 4.088 | 4.3627 | 4.2528 | 4.5275 | 1.9319 | 2.9265 | 3.4841 | 3.4841 | 3.8559 | 3.8559 | 2019-10-22 03:00 | 1.166 | 1.9109 | 3.1367 | 3.1367 | 3.1367 | 3.1367
2021-08-24 14:00 | 3.0808 | 3.8151 | 3.8758 | 4.1363 | 4.0321 | 4.2925 | 1.7947 | 2.7187 | 3.2368 | 3.2368 | 3.5821 | 3.5821 | 2019-10-22 04:00 | 1.2575 | 2.0608 | 3.3828 | 3.3828 | 3.3828 | 3.3828
2021-08-24 15:00 | 3.0951 | 3.8328 | 3.8938 | 4.1555 | 4.0508 | 4.3124 | 1.8233 | 2.762 | 3.2883 | 3.2883 | 3.6392 | 3.6392 | 2019-10-22 05:00 | 1.3794 | 2.2606 | 3.7108 | 3.7108 | 3.7108 | 3.7108
2021-08-24 16:00 | 3.2637 | 4.0416 | 4.1059 | 4.3818 | 4.2715 | 4.5474 | 1.8376 | 2.7836 | 3.3141 | 3.3141 | 3.6677 | 3.6677 | 2019-10-22 06:00 | 1.5775 | 2.5853 | 4.2438 | 4.2438 | 4.2438 | 4.2438
2021-08-24 17:00 | 3.7438 | 4.6361 | 4.71 | 5.0264 | 4.8999 | 5.2163 | 2.1606 | 3.2728 | 3.8965 | 3.8965 | 4.3122 | 4.3122 | 2019-10-22 07:00 | 1.9967 | 3.2722 | 5.3714 | 5.3714 | 5.3714 | 5.3714
2021-08-24 18:00 | 3.8581 | 4.7777 | 4.8538 | 5.1799 | 5.0495 | 5.3756 | 2.2091 | 3.3464 | 3.9841 | 3.9841 | 4.4092 | 4.4092 | 2019-10-22 08:00 | 2.0501 | 3.3597 | 5.5149 | 5.5149 | 5.5149 | 5.5149
2021-08-24 19:00 | 3.6609 | 4.5335 | 4.6057 | 4.9152 | 4.7914 | 5.1009 | 2.2949 | 3.4763 | 4.1387 | 4.1387 | 4.5803 | 4.5803 | 2019-10-22 09:00 | 2.1263 | 3.4845 | 5.7199 | 5.7199 | 5.7199 | 5.7199
2021-08-24 20:00 | 3.263 | 4.0407 | 4.1051 | 4.3809 | 4.2706 | 4.5464 | 2.2034 | 3.3378 | 3.9738 | 3.9738 | 4.3978 | 4.3978 | 2019-10-22 10:00 | 2.1567 | 3.5345 | 5.8019 | 5.8019 | 5.8019 | 5.8019
2021-08-24 21:00 | 2.9007 | 3.5921 | 3.6493 | 3.8945 | 3.7965 | 4.0417 | 2.0091 | 3.0434 | 3.6233 | 3.6233 | 4.0099 | 4.0099 | 2019-10-22 11:00 | 2.2177 | 3.6344 | 5.966 | 5.966 | 5.966 | 5.966
2021-08-24 22:00 | 2.6178 | 3.2418 | 3.2934 | 3.5147 | 3.4262 | 3.6475 | 1.7179 | 2.6023 | 3.0981 | 3.0981 | 3.4287 | 3.4287 | 2019-10-22 12:00 | 2.2787 | 3.7343 | 6.13 | 6.13 | 6.13 | 6.13
2021-08-24 23:00 | 2.3792 | 2.9463 | 2.9932 | 3.1943 | 3.1139 | 3.315 | 1.4547 | 2.2035 | 2.6234 | 2.6234 | 2.9033 | 2.9033 | 2019-10-22 13:00 | 2.2406 | 3.6719 | 6.0275 | 6.0275 | 6.0275 | 6.0275
2021-08-25 | 2.0634 | 2.5552 | 2.5959 | 2.7703 | 2.7005 | 2.875 | 1.1834 | 1.7927 | 2.1343 | 2.1343 | 2.362 | 2.362 | 2019-10-22 14:00 | 2.2253 | 3.6469 | 5.9865 | 5.9865 | 5.9865 | 5.9865
2021-08-25 01:00 | 1.8862 | 2.3358 | 2.373 | 2.5324 | 2.4686 | 2.6281 | 1.1203 | 1.6971 | 2.0205 | 2.0205 | 2.2361 | 2.2361 | 2019-10-22 15:00 | 2.2177 | 3.6344 | 5.966 | 5.966 | 5.966 | 5.966
2021-08-25 02:00 | 1.8119 | 2.2437 | 2.2795 | 2.4326 | 2.3714 | 2.5245 | 1.0888 | 1.6494 | 1.9637 | 1.9637 | 2.1732 | 2.1732 | 2019-10-22 16:00 | 2.1415 | 3.5095 | 5.7609 | 5.7609 | 5.7609 | 5.7609
2021-08-25 03:00 | 1.8148 | 2.2473 | 2.2831 | 2.4365 | 2.3751 | 2.5285 | 1.1117 | 1.684 | 2.0049 | 2.0049 | 2.2189 | 2.2189 | 2019-10-22 17:00 | 2.1644 | 3.547 | 5.8224 | 5.8224 | 5.8224 | 5.8224
2021-08-25 04:00 | 1.8518 | 2.2932 | 2.3297 | 2.4862 | 2.4236 | 2.5801 | 1.0717 | 1.6234 | 1.9328 | 1.9328 | 2.139 | 2.139 | 2019-10-22 18:00 | 2.1644 | 3.547 | 5.8224 | 5.8224 | 5.8224 | 5.8224
2021-08-25 05:00 | 2.0571 | 2.5474 | 2.588 | 2.7619 | 2.6923 | 2.8662 | 1.1431 | 1.7317 | 2.0616 | 2.0616 | 2.2816 | 2.2816 | 2019-10-22 19:00 | 1.951 | 3.1973 | 5.2484 | 5.2484 | 5.2484 | 5.2484
2021-08-25 06:00 | 2.5607 | 3.171 | 3.2215 | 3.4379 | 3.3514 | 3.5678 | 1.2683 | 1.9213 | 2.2874 | 2.2874 | 2.5315 | 2.5315 | 2019-10-22 20:00 | 1.89 | 3.0974 | 5.0844 | 5.0844 | 5.0844 | 5.0844
2021-08-25 07:00 | 3.2265 | 3.9956 | 4.0592 | 4.332 | 4.2229 | 4.4956 | 1.5727 | 2.3823 | 2.8363 | 2.8363 | 3.1389 | 3.1389 | 2019-10-22 21:00 | 1.6309 | 2.6727 | 4.3873 | 4.3873 | 4.3873 | 4.3873
2021-08-25 08:00 | 3.2923 | 4.077 | 4.1419 | 4.4202 | 4.3089 | 4.5872 | 1.8062 | 2.736 | 3.2574 | 3.2574 | 3.6049 | 3.6049 | 2019-10-22 22:00 | 1.5852 | 2.5978 | 4.2643 | 4.2643 | 4.2643 | 4.2643
2021-08-25 09:00 | 3.2123 | 3.9779 | 4.0412 | 4.3128 | 4.2042 | 4.4757 | 1.8462 | 2.7966 | 3.3295 | 3.3295 | 3.6848 | 3.6848 | 2019-10-22 23:00 | 1.4556 | 2.3855 | 3.9158 | 3.9158 | 3.9158 | 3.9158
2021-08-25 10:00 | 3.1151 | 3.8575 | 3.919 | 4.1823 | 4.077 | 4.3403 | 1.7833 | 2.7014 | 3.2161 | 3.2161 | 3.5593 | 3.5593 | 2019-10-23 | 1.3261 | 2.1732 | 3.5673 | 3.5673 | 3.5673 | 3.5673
2021-08-25 11:00 | 3.0334 | 3.7563 | 3.8162 | 4.0726 | 3.97 | 4.2265 | 1.789 | 2.71 | 3.2264 | 3.2264 | 3.5707 | 3.5707 | 2019-10-23 01:00 | 1.227 | 2.0108 | 3.3007 | 3.3007 | 3.3007 | 3.3007
2021-08-25 12:00 | 2.9665 | 3.6735 | 3.732 | 3.9828 | 3.8825 | 4.1332 | 1.709 | 2.5888 | 3.0821 | 3.0821 | 3.411 | 3.411 | 2019-10-23 02:00 | 1.2194 | 1.9983 | 3.2802 | 3.2802 | 3.2802 | 3.2802
2021-08-25 13:00 | 2.8179 | 3.4895 | 3.5451 | 3.7833 | 3.688 | 3.9262 | 1.6833 | 2.5499 | 3.0357 | 3.0357 | 3.3597 | 3.3597 | 2019-10-23 03:00 | 1.2041 | 1.9733 | 3.2392 | 3.2392 | 3.2392 | 3.2392
2021-08-25 14:00 | 2.5378 | 3.1427 | 3.1927 | 3.4072 | 3.3214 | 3.536 | 1.6233 | 2.4589 | 2.9275 | 2.9275 | 3.2399 | 3.2399 | 2019-10-23 04:00 | 1.227 | 2.0108 | 3.3007 | 3.3007 | 3.3007 | 3.3007
2021-08-25 15:00 | 2.5378 | 3.1427 | 3.1927 | 3.4072 | 3.3214 | 3.536 | 1.6118 | 2.4416 | 2.9069 | 2.9069 | 3.2171 | 3.2171 | 2019-10-23 05:00 | 1.3718 | 2.2481 | 3.6903 | 3.6903 | 3.6903 | 3.6903
2021-08-25 16:00 | 2.7607 | 3.4187 | 3.4732 | 3.7065 | 3.6132 | 3.8465 | 1.7376 | 2.6321 | 3.1337 | 3.1337 | 3.468 | 3.468 | 2019-10-23 06:00 | 1.6004 | 2.6228 | 4.3053 | 4.3053 | 4.3053 | 4.3053
2021-08-25 17:00 | 3.3237 | 4.1159 | 4.1814 | 4.4624 | 4.35 | 4.631 | 2.032 | 3.078 | 3.6645 | 3.6645 | 4.0556 | 4.0556 | 2019-10-23 07:00 | 1.8748 | 3.0724 | 5.0434 | 5.0434 | 5.0434 | 5.0434
2021-08-25 18:00 | 3.498 | 4.3318 | 4.4008 | 4.6965 | 4.5782 | 4.8739 | 2.0977 | 3.1776 | 3.7831 | 3.7831 | 4.1867 | 4.1867 | 2019-10-23 08:00 | 2.0653 | 3.3846 | 5.5559 | 5.5559 | 5.5559 | 5.5559
2021-08-25 19:00 | 3.2913 | 4.0757 | 4.1406 | 4.4188 | 4.3075 | 4.5858 | 2.0977 | 3.1776 | 3.7831 | 3.7831 | 4.1867 | 4.1867 | 2019-10-23 09:00 | 2.1339 | 3.497 | 5.7404 | 5.7404 | 5.7404 | 5.7404
2021-08-25 20:00 | 3.0579 | 3.7868 | 3.8471 | 4.1056 | 4.0022 | 4.2607 | 2.1234 | 3.2165 | 3.8295 | 3.8295 | 4.2381 | 4.2381 | 2019-10-23 10:00 | 2.1491 | 3.522 | 5.7814 | 5.7814 | 5.7814 | 5.7814
2021-08-25 21:00 | 2.8036 | 3.4718 | 3.5271 | 3.7641 | 3.6693 | 3.9063 | 1.8833 | 2.8529 | 3.3965 | 3.3965 | 3.7589 | 3.7589 | 2019-10-23 11:00 | 2.1567 | 3.5345 | 5.8019 | 5.8019 | 5.8019 | 5.8019
2021-08-25 22:00 | 2.4663 | 3.0542 | 3.1028 | 3.3113 | 3.2279 | 3.4364 | 1.7062 | 2.5845 | 3.077 | 3.077 | 3.4053 | 3.4053 | 2019-10-23 12:00 | 2.1415 | 3.5095 | 5.7609 | 5.7609 | 5.7609 | 5.7609
2021-08-25 23:00 | 2.2979 | 2.8456 | 2.891 | 3.0852 | 3.0075 | 3.2018 | 1.5575 | 2.3594 | 2.809 | 2.809 | 3.1087 | 3.1087 | 2019-10-23 13:00 | 2.5226 | 4.134 | 6.786 | 6.786 | 6.786 | 6.786
2021-08-26 | 2.0276 | 2.5108 | 2.5508 | 2.7222 | 2.6536 | 2.825 | 1.2557 | 1.9021 | 2.2645 | 2.2645 | 2.5062 | 2.5062 | 2019-10-23 14:00 | 2.4006 | 3.9342 | 6.458 | 6.458 | 6.458 | 6.458
2021-08-26 01:00 | 1.8548 | 2.2968 | 2.3334 | 2.4902 | 2.4275 | 2.5843 | 1.1803 | 1.7879 | 2.1286 | 2.1286 | 2.3558 | 2.3558 | 2019-10-23 15:00 | 2.2787 | 3.7343 | 6.13 | 6.13 | 6.13 | 6.13
2021-08-26 02:00 | 1.8433 | 2.2827 | 2.319 | 2.4749 | 2.4125 | 2.5683 | 1.1031 | 1.671 | 1.9895 | 1.9895 | 2.2017 | 2.2017 | 2019-10-23 16:00 | 2.2634 | 3.7094 | 6.089 | 6.089 | 6.089 | 6.089
2021-08-26 03:00 | 1.8776 | 2.3251 | 2.3622 | 2.5209 | 2.4574 | 2.6161 | 1.0431 | 1.5801 | 1.8812 | 1.8812 | 2.082 | 2.082 | 2019-10-23 17:00 | 2.1872 | 3.5845 | 5.8839 | 5.8839 | 5.8839 | 5.8839
2021-08-26 04:00 | 1.8719 | 2.3181 | 2.355 | 2.5132 | 2.4499 | 2.6082 | 1.0631 | 1.6104 | 1.9173 | 1.9173 | 2.1219 | 2.1219 | 2019-10-23 18:00 | 1.951 | 3.1973 | 5.2484 | 5.2484 | 5.2484 | 5.2484
2021-08-26 05:00 | 2.1601 | 2.675 | 2.7176 | 2.9002 | 2.8272 | 3.0098 | 1.1517 | 1.7446 | 2.0771 | 2.0771 | 2.2987 | 2.2987 | 2019-10-23 19:00 | 1.8671 | 3.0599 | 5.0229 | 5.0229 | 5.0229 | 5.0229
2021-08-26 06:00 | 2.8007 | 3.4682 | 3.5235 | 3.7602 | 3.6655 | 3.9023 | 1.2575 | 1.9048 | 2.2678 | 2.2678 | 2.5098 | 2.5098 | 2019-10-23 20:00 | 1.9281 | 3.1598 | 5.1869 | 5.1869 | 5.1869 | 5.1869
2021-08-26 07:00 | 3.2837 | 4.0663 | 4.1311 | 4.4087 | 4.2977 | 4.5752 | 1.609 | 2.4373 | 2.9017 | 2.9017 | 3.2114 | 3.2114 | 2019-10-23 21:00 | 1.7452 | 2.8601 | 4.6949 | 4.6949 | 4.6949 | 4.6949
2021-08-26 08:00 | 3.2094 | 3.9743 | 4.0376 | 4.3089 | 4.2004 | 4.4717 | 1.6804 | 2.5455 | 3.0306 | 3.0306 | 3.354 | 3.354 | 2019-10-23 22:00 | 1.5242 | 2.4979 | 4.1003 | 4.1003 | 4.1003 | 4.1003
2021-08-26 09:00 | 2.9007 | 3.5921 | 3.6493 | 3.8945 | 3.7965 | 4.0417 | 1.5518 | 2.3507 | 2.7987 | 2.7987 | 3.0973 | 3.0973 | 2019-10-23 23:00 | 1.3946 | 2.2856 | 3.7518 | 3.7518 | 3.7518 | 3.7518
2021-08-26 10:00 | 2.5807 | 3.1957 | 3.2466 | 3.4648 | 3.3775 | 3.5957 | 1.5347 | 2.3247 | 2.7677 | 2.7677 | 3.0631 | 3.0631 | 2019-10-24 | 1.3108 | 2.1482 | 3.5263 | 3.5263 | 3.5263 | 3.5263
2021-08-26 11:00 | 2.312 | 2.8631 | 2.9087 | 3.1041 | 3.0259 | 3.2214 | 1.5318 | 2.3204 | 2.7626 | 2.7626 | 3.0574 | 3.0574 | 2019-10-24 01:00 | 1.3032 | 2.1357 | 3.5058 | 3.5058 | 3.5058 | 3.5058
2021-08-26 12:00 | 2.3063 | 2.856 | 2.9015 | 3.0964 | 3.0185 | 3.2134 | 1.5661 | 2.3724 | 2.8244 | 2.8244 | 3.1258 | 3.1258 | 2019-10-24 02:00 | 1.2041 | 1.9733 | 3.2392 | 3.2392 | 3.2392 | 3.2392
2021-08-26 13:00 | 2.3949 | 2.9657 | 3.0129 | 3.2154 | 3.1344 | 3.3369 | 1.5775 | 2.3897 | 2.845 | 2.845 | 3.1486 | 3.1486 | 2019-10-24 03:00 | 1.227 | 2.0108 | 3.3007 | 3.3007 | 3.3007 | 3.3007
2021-08-26 14:00 | 2.4635 | 3.0506 | 3.0992 | 3.3075 | 3.2242 | 3.4324 | 1.649 | 2.4979 | 2.9739 | 2.9739 | 3.2912 | 3.2912 | 2019-10-24 04:00 | 1.2651 | 2.0732 | 3.4033 | 3.4033 | 3.4033 | 3.4033
2021-08-26 15:00 | 2.595 | 3.2134 | 3.2646 | 3.484 | 3.3962 | 3.6156 | 1.7323 | 2.6241 | 3.1241 | 3.1241 | 3.4574 | 3.4574 | 2019-10-24 05:00 | 1.3946 | 2.2856 | 3.7518 | 3.7518 | 3.7518 | 3.7518
2021-08-26 16:00 | 2.7664 | 3.4258 | 3.4803 | 3.7142 | 3.6207 | 3.8545 | 1.8462 | 2.7966 | 3.3295 | 3.3295 | 3.6848 | 3.6848 | 2019-10-24 06:00 | 1.5699 | 2.5728 | 4.2233 | 4.2233 | 4.2233 | 4.2233
2021-08-26 17:00 | 3.2466 | 4.0203 | 4.0844 | 4.3588 | 4.249 | 4.5235 | 2.0434 | 3.0953 | 3.6852 | 3.6852 | 4.0784 | 4.0784 | 2019-10-24 07:00 | 1.9738 | 3.2348 | 5.3099 | 5.3099 | 5.3099 | 5.3099
2021-08-26 18:00 | 3.4838 | 4.3141 | 4.3828 | 4.6773 | 4.5595 | 4.854 | 2.1463 | 3.2512 | 3.8707 | 3.8707 | 4.2837 | 4.2837 | 2019-10-24 08:00 | 2.0272 | 3.3222 | 5.4534 | 5.4534 | 5.4534 | 5.4534
2021-08-26 19:00 | 3.2694 | 4.0486 | 4.1131 | 4.3895 | 4.279 | 4.5553 | 2.2234 | 3.3681 | 4.0099 | 4.0099 | 4.4377 | 4.4377 | 2019-10-24 09:00 | 2.1644 | 3.547 | 5.8224 | 5.8224 | 5.8224 | 5.8224
2021-08-26 20:00 | 3.0294 | 3.7514 | 3.8111 | 4.0672 | 3.9648 | 4.2209 | 2.0805 | 3.1516 | 3.7522 | 3.7522 | 4.1525 | 4.1525 | 2019-10-24 10:00 | 2.2177 | 3.6344 | 5.966 | 5.966 | 5.966 | 5.966
2021-08-26 21:00 | 2.6794 | 3.318 | 3.3709 | 3.5974 | 3.5068 | 3.7333 | 1.9062 | 2.8875 | 3.4378 | 3.4378 | 3.8046 | 3.8046 | 2019-10-24 11:00 | 2.2711 | 3.7218 | 6.1095 | 6.1095 | 6.1095 | 6.1095
2021-08-26 22:00 | 2.4263 | 3.0046 | 3.0525 | 3.2576 | 3.1756 | 3.3807 | 1.6412 | 2.4861 | 2.9599 | 2.9599 | 3.2757 | 3.2757 | 2019-10-24 12:00 | 2.332 | 3.8218 | 6.2735 | 6.2735 | 6.2735 | 6.2735
2021-08-26 23:00 | 2.1609 | 2.6759 | 2.7185 | 2.9012 | 2.8281 | 3.0108 | 1.4474 | 2.1925 | 2.6103 | 2.6103 | 2.8888 | 2.8888 | 2019-10-24 13:00 | 2.2634 | 3.7094 | 6.089 | 6.089 | 6.089 | 6.089
2021-08-27 | 1.9719 | 2.4419 | 2.4808 | 2.6475 | 2.5808 | 2.7475 | 1.2089 | 1.8312 | 2.1802 | 2.1802 | 2.4128 | 2.4128 | 2019-10-24 14:00 | 2.3168 | 3.7968 | 6.2325 | 6.2325 | 6.2325 | 6.2325
2021-08-27 01:00 | 1.8548 | 2.2968 | 2.3334 | 2.4902 | 2.4275 | 2.5843 | 1.0774 | 1.6321 | 1.9431 | 1.9431 | 2.1504 | 2.1504 | 2019-10-24 15:00 | 2.2863 | 3.7468 | 6.1505 | 6.1505 | 6.1505 | 6.1505
2021-08-27 02:00 | 1.7262 | 2.1376 | 2.1716 | 2.3175 | 2.2592 | 2.4051 | 1.0116 | 1.5324 | 1.8244 | 1.8244 | 2.0191 | 2.0191 | 2019-10-24 16:00 | 2.2787 | 3.7343 | 6.13 | 6.13 | 6.13 | 6.13
2021-08-27 03:00 | 1.6833 | 2.0845 | 2.1177 | 2.26 | 2.2031 | 2.3454 | 0.98597 | 1.4935 | 1.7781 | 1.7781 | 1.9679 | 1.9679 | 2019-10-24 17:00 | 2.3854 | 3.9092 | 6.417 | 6.417 | 6.417 | 6.417
2021-08-27 04:00 | 1.7347 | 2.1482 | 2.1824 | 2.329 | 2.2704 | 2.417 | 1.0317 | 1.5628 | 1.8606 | 1.8606 | 2.0591 | 2.0591 | 2019-10-24 18:00 | 2.2177 | 3.6344 | 5.966 | 5.966 | 5.966 | 5.966
2021-08-27 05:00 | 1.991 | 2.4655 | 2.5048 | 2.6731 | 2.6057 | 2.774 | 1.0688 | 1.6191 | 1.9276 | 1.9276 | 2.1333 | 2.1333 | 2019-10-24 19:00 | 1.9891 | 3.2597 | 5.3509 | 5.3509 | 5.3509 | 5.3509
2021-08-27 06:00 | 2.4121 | 2.9869 | 3.0345 | 3.2384 | 3.1569 | 3.3608 | 1.2317 | 1.8659 | 2.2214 | 2.2214 | 2.4584 | 2.4584 | 2019-10-24 20:00 | 1.9891 | 3.2597 | 5.3509 | 5.3509 | 5.3509 | 5.3509
2021-08-27 07:00 | 2.8007 | 3.4682 | 3.5235 | 3.7602 | 3.6655 | 3.9023 | 1.5433 | 2.3377 | 2.7832 | 2.7832 | 3.0802 | 3.0802 | 2019-10-24 21:00 | 1.7681 | 2.8975 | 4.7564 | 4.7564 | 4.7564 | 4.7564
2021-08-27 08:00 | 2.9208 | 3.6169 | 3.6745 | 3.9214 | 3.8226 | 4.0695 | 1.609 | 2.4373 | 2.9017 | 2.9017 | 3.2114 | 3.2114 | 2019-10-24 22:00 | 1.6842 | 2.7602 | 4.5308 | 4.5308 | 4.5308 | 4.5308
2021-08-27 09:00 | 2.935 | 3.6346 | 3.6925 | 3.9406 | 3.8413 | 4.0894 | 1.5947 | 2.4157 | 2.876 | 2.876 | 3.1828 | 3.1828 | 2019-10-24 23:00 | 1.5394 | 2.5229 | 4.1413 | 4.1413 | 4.1413 | 4.1413
2021-08-27 10:00 | 2.7093 | 3.355 | 3.4084 | 3.6375 | 3.5459 | 3.7749 | 1.6176 | 2.4503 | 2.9172 | 2.9172 | 3.2285 | 3.2285 | 2019-10-25 | 1.387 | 2.2731 | 3.7313 | 3.7313 | 3.7313 | 3.7313
2021-08-27 11:00 | 2.6178 | 3.2418 | 3.2934 | 3.5147 | 3.4262 | 3.6475 | 1.629 | 2.4676 | 2.9378 | 2.9378 | 3.2513 | 3.2513 | 2019-10-25 01:00 | 1.2879 | 2.1107 | 3.4648 | 3.4648 | 3.4648 | 3.4648
2021-08-27 12:00 | 2.6721 | 3.309 | 3.3617 | 3.5876 | 3.4972 | 3.7231 | 1.629 | 2.4676 | 2.9378 | 2.9378 | 3.2513 | 3.2513 | 2019-10-25 02:00 | 1.3108 | 2.1482 | 3.5263 | 3.5263 | 3.5263 | 3.5263
2021-08-27 13:00 | 2.7807 | 3.4435 | 3.4983 | 3.7334 | 3.6394 | 3.8744 | 1.669 | 2.5282 | 3.01 | 3.01 | 3.3311 | 3.3311 | 2019-10-25 03:00 | 1.2651 | 2.0732 | 3.4033 | 3.4033 | 3.4033 | 3.4033
2021-08-27 14:00 | 2.5921 | 3.2099 | 3.261 | 3.4801 | 3.3925 | 3.6116 | 1.6261 | 2.4633 | 2.9327 | 2.9327 | 3.2456 | 3.2456 | 2019-10-25 04:00 | 1.3718 | 2.2481 | 3.6903 | 3.6903 | 3.6903 | 3.6903
2021-08-27 15:00 | 2.695 | 3.3373 | 3.3905 | 3.6183 | 3.5271 | 3.755 | 1.6804 | 2.5455 | 3.0306 | 3.0306 | 3.354 | 3.354 | 2019-10-25 05:00 | 1.4404 | 2.3605 | 3.8748 | 3.8748 | 3.8748 | 3.8748
2021-08-27 16:00 | 2.9522 | 3.6558 | 3.714 | 3.9636 | 3.8638 | 4.1133 | 1.8691 | 2.8313 | 3.3708 | 3.3708 | 3.7304 | 3.7304 | 2019-10-25 06:00 | 1.5547 | 2.5478 | 4.1823 | 4.1823 | 4.1823 | 4.1823
2021-08-27 17:00 | 3.2694 | 4.0486 | 4.1131 | 4.3895 | 4.279 | 4.5553 | 1.9576 | 2.9655 | 3.5305 | 3.5305 | 3.9073 | 3.9073 | 2019-10-25 07:00 | 1.9053 | 3.1224 | 5.1254 | 5.1254 | 5.1254 | 5.1254
2021-08-27 18:00 | 3.298 | 4.084 | 4.1491 | 4.4279 | 4.3164 | 4.5952 | 2.2149 | 3.3551 | 3.9944 | 3.9944 | 4.4206 | 4.4206 | 2019-10-25 08:00 | 2.111 | 3.4596 | 5.6789 | 5.6789 | 5.6789 | 5.6789
2021-08-27 19:00 | 3.1808 | 3.9389 | 4.0017 | 4.2706 | 4.163 | 4.4319 | 2.2263 | 3.3724 | 4.015 | 4.015 | 4.4434 | 4.4434 | 2019-10-25 09:00 | 2.2482 | 3.6844 | 6.048 | 6.048 | 6.048 | 6.048
2021-08-27 20:00 | 2.9814 | 3.692 | 3.7508 | 4.0028 | 3.902 | 4.154 | 2.0205 | 3.0607 | 3.6439 | 3.6439 | 4.0327 | 4.0327 | 2019-10-25 10:00 | 2.2787 | 3.7343 | 6.13 | 6.13 | 6.13 | 6.13
2021-08-27 21:00 | 2.7454 | 3.3997 | 3.4539 | 3.686 | 3.5931 | 3.8252 | 1.8719 | 2.8356 | 3.3759 | 3.3759 | 3.7361 | 3.7361 | 2019-10-25 11:00 | 2.3168 | 3.7968 | 6.2325 | 6.2325 | 6.2325 | 6.2325
2021-08-27 22:00 | 2.5006 | 3.0966 | 3.146 | 3.3574 | 3.2728 | 3.4842 | 1.7062 | 2.5845 | 3.077 | 3.077 | 3.4053 | 3.4053 | 2019-10-25 12:00 | 2.3625 | 3.8717 | 6.3555 | 6.3555 | 6.3555 | 6.3555
2021-08-27 23:00 | 2.2175 | 2.746 | 2.7897 | 2.9772 | 2.9022 | 3.0896 | 1.5118 | 2.2901 | 2.7265 | 2.7265 | 3.0174 | 3.0174 | 2019-10-25 13:00 | 2.3549 | 3.8592 | 6.335 | 6.335 | 6.335 | 6.335
2021-08-28 | 2.0691 | 2.5623 | 2.6031 | 2.778 | 2.7081 | 2.883 | 1.2892 | 1.9529 | 2.325 | 2.325 | 2.5731 | 2.5731 | 2019-10-25 14:00 | 2.4463 | 4.0091 | 6.581 | 6.581 | 6.581 | 6.581
2021-08-28 01:00 | 1.8748 | 2.3216 | 2.3586 | 2.5171 | 2.4537 | 2.6121 | 1.1522 | 1.7454 | 2.078 | 2.078 | 2.2997 | 2.2997 | 2019-10-25 15:00 | 2.4387 | 3.9966 | 6.5605 | 6.5605 | 6.5605 | 6.5605
2021-08-28 02:00 | 1.728 | 2.1398 | 2.1739 | 2.3199 | 2.2615 | 2.4076 | 1.0888 | 1.6494 | 1.9637 | 1.9637 | 2.1732 | 2.1732 | 2019-10-25 16:00 | 2.2025 | 3.6094 | 5.9249 | 5.9249 | 5.9249 | 5.9249
2021-08-28 03:00 | 1.7062 | 2.1128 | 2.1465 | 2.2907 | 2.233 | 2.3772 | 0.97453 | 1.4762 | 1.7575 | 1.7575 | 1.9451 | 1.9451 | 2019-10-25 17:00 | 2.1263 | 3.4845 | 5.7199 | 5.7199 | 5.7199 | 5.7199
2021-08-28 04:00 | 1.7529 | 2.1707 | 2.2053 | 2.3535 | 2.2942 | 2.4424 | 1.0374 | 1.5715 | 1.8709 | 1.8709 | 2.0706 | 2.0706 | 2019-10-25 18:00 | 1.9967 | 3.2722 | 5.3714 | 5.3714 | 5.3714 | 5.3714
2021-08-28 05:00 | 1.8919 | 2.3428 | 2.3802 | 2.5401 | 2.4761 | 2.636 | 1.066 | 1.6148 | 1.9225 | 1.9225 | 2.1276 | 2.1276 | 2019-10-25 19:00 | 2.0272 | 3.3222 | 5.4534 | 5.4534 | 5.4534 | 5.4534
2021-08-28 06:00 | 2.1434 | 2.6543 | 2.6965 | 2.8777 | 2.8053 | 2.9864 | 1.1146 | 1.6884 | 2.0101 | 2.0101 | 2.2246 | 2.2246 | 2019-10-25 20:00 | 1.8443 | 3.0224 | 4.9614 | 4.9614 | 4.9614 | 4.9614
2021-08-28 07:00 | 2.4518 | 3.0362 | 3.0845 | 3.2918 | 3.2089 | 3.4162 | 1.3175 | 1.9957 | 2.376 | 2.376 | 2.6295 | 2.6295 | 2019-10-25 21:00 | 1.8519 | 3.0349 | 4.9819 | 4.9819 | 4.9819 | 4.9819
2021-08-28 08:00 | 2.4864 | 3.079 | 3.128 | 3.3382 | 3.2541 | 3.4643 | 1.3575 | 2.0563 | 2.4482 | 2.4482 | 2.7094 | 2.7094 | 2019-10-25 22:00 | 1.7452 | 2.8601 | 4.6949 | 4.6949 | 4.6949 | 4.6949
2021-08-28 09:00 | 2.4721 | 3.0613 | 3.11 | 3.319 | 3.2354 | 3.4444 | 1.6033 | 2.4286 | 2.8914 | 2.8914 | 3.2 | 3.2 | 2019-10-25 23:00 | 1.6309 | 2.6727 | 4.3873 | 4.3873 | 4.3873 | 4.3873
2021-08-28 10:00 | 2.392 | 2.9622 | 3.0093 | 3.2116 | 3.1307 | 3.3329 | 1.589 | 2.407 | 2.8657 | 2.8657 | 3.1714 | 3.1714 | 2019-10-26 | 1.4099 | 2.3105 | 3.7928 | 3.7928 | 3.7928 | 3.7928
2021-08-28 11:00 | 2.2577 | 2.7958 | 2.8404 | 3.0312 | 2.9549 | 3.1457 | 1.6061 | 2.433 | 2.8966 | 2.8966 | 3.2057 | 3.2057 | 2019-10-26 01:00 | 1.3642 | 2.2356 | 3.6698 | 3.6698 | 3.6698 | 3.6698
2021-08-28 12:00 | 2.3235 | 2.8772 | 2.9231 | 3.1195 | 3.0409 | 3.2373 | 1.6404 | 2.4849 | 2.9584 | 2.9584 | 3.2741 | 3.2741 | 2019-10-26 02:00 | 1.3337 | 2.1856 | 3.5878 | 3.5878 | 3.5878 | 3.5878
2021-08-28 13:00 | 2.2634 | 2.8029 | 2.8476 | 3.0389 | 2.9624 | 3.1537 | 1.5861 | 2.4027 | 2.8605 | 2.8605 | 3.1657 | 3.1657 | 2019-10-26 03:00 | 1.3794 | 2.2606 | 3.7108 | 3.7108 | 3.7108 | 3.7108
2021-08-28 14:00 | 2.2663 | 2.8064 | 2.8512 | 3.0427 | 2.9661 | 3.1577 | 1.6176 | 2.4503 | 2.9172 | 2.9172 | 3.2285 | 3.2285 | 2019-10-26 04:00 | 1.3413 | 2.1981 | 3.6083 | 3.6083 | 3.6083 | 3.6083
2021-08-28 15:00 | 2.3006 | 2.8489 | 2.8943 | 3.0888 | 3.011 | 3.2055 | 1.5518 | 2.3507 | 2.7987 | 2.7987 | 3.0973 | 3.0973 | 2019-10-26 05:00 | 1.4556 | 2.3855 | 3.9158 | 3.9158 | 3.9158 | 3.9158
2021-08-28 16:00 | 2.5292 | 3.132 | 3.1819 | 3.3957 | 3.3102 | 3.524 | 1.7119 | 2.5932 | 3.0873 | 3.0873 | 3.4167 | 3.4167 | 2019-10-26 06:00 | 1.4023 | 2.2981 | 3.7723 | 3.7723 | 3.7723 | 3.7723
2021-08-28 17:00 | 2.9836 | 3.6947 | 3.7536 | 4.0058 | 3.9049 | 4.1571 | 1.8576 | 2.8139 | 3.3501 | 3.3501 | 3.7076 | 3.7076 | 2019-10-26 07:00 | 1.6538 | 2.7102 | 4.4488 | 4.4488 | 4.4488 | 4.4488
2021-08-28 18:00 | 3.198 | 3.9602 | 4.0233 | 4.2936 | 4.1855 | 4.4558 | 2.1005 | 3.1819 | 3.7882 | 3.7882 | 4.1925 | 4.1925 | 2019-10-26 08:00 | 1.8062 | 2.96 | 4.8589 | 4.8589 | 4.8589 | 4.8589
2021-08-28 19:00 | 3.0008 | 3.716 | 3.7752 | 4.0288 | 3.9274 | 4.181 | 2.132 | 3.2295 | 3.8449 | 3.8449 | 4.2552 | 4.2552 | 2019-10-26 09:00 | 1.8443 | 3.0224 | 4.9614 | 4.9614 | 4.9614 | 4.9614
2021-08-28 20:00 | 2.8493 | 3.5284 | 3.5846 | 3.8255 | 3.7291 | 3.97 | 1.9348 | 2.9308 | 3.4893 | 3.4893 | 3.8616 | 3.8616 | 2019-10-26 10:00 | 1.951 | 3.1973 | 5.2484 | 5.2484 | 5.2484 | 5.2484
2021-08-28 21:00 | 2.6721 | 3.309 | 3.3617 | 3.5876 | 3.4972 | 3.7231 | 1.829 | 2.7706 | 3.2986 | 3.2986 | 3.6506 | 3.6506 | 2019-10-26 11:00 | 1.9434 | 3.1848 | 5.2279 | 5.2279 | 5.2279 | 5.2279
2021-08-28 22:00 | 2.4837 | 3.0757 | 3.1246 | 3.3346 | 3.2506 | 3.4606 | 1.6861 | 2.5542 | 3.0409 | 3.0409 | 3.3654 | 3.3654 | 2019-10-26 12:00 | 1.89 | 3.0974 | 5.0844 | 5.0844 | 5.0844 | 5.0844
2021-08-28 23:00 | 2.2863 | 2.8312 | 2.8763 | 3.0696 | 2.9923 | 3.1855 | 1.4132 | 2.1407 | 2.5487 | 2.5487 | 2.8206 | 2.8206 | 2019-10-26 13:00 | 1.9738 | 3.2348 | 5.3099 | 5.3099 | 5.3099 | 5.3099
2021-08-29 | 2.0662 | 2.5587 | 2.5995 | 2.7741 | 2.7043 | 2.8789 | 1.2764 | 1.9334 | 2.3019 | 2.3019 | 2.5475 | 2.5475 | 2019-10-26 14:00 | 1.89 | 3.0974 | 5.0844 | 5.0844 | 5.0844 | 5.0844
2021-08-29 01:00 | 1.8891 | 2.3393 | 2.3766 | 2.5362 | 2.4724 | 2.6321 | 1.126 | 1.7057 | 2.0307 | 2.0307 | 2.2474 | 2.2474 | 2019-10-26 15:00 | 1.829 | 2.9975 | 4.9204 | 4.9204 | 4.9204 | 4.9204
2021-08-29 02:00 | 1.7833 | 2.2084 | 2.2435 | 2.3943 | 2.334 | 2.4847 | 1.0603 | 1.6061 | 1.9122 | 1.9122 | 2.1162 | 2.1162 | 2019-10-26 16:00 | 1.9129 | 3.1348 | 5.1459 | 5.1459 | 5.1459 | 5.1459
2021-08-29 03:00 | 1.7605 | 2.18 | 2.2148 | 2.3636 | 2.3041 | 2.4529 | 1.0374 | 1.5715 | 1.8709 | 1.8709 | 2.0706 | 2.0706 | 2019-10-26 17:00 | 1.7909 | 2.935 | 4.8179 | 4.8179 | 4.8179 | 4.8179
2021-08-29 04:00 | 1.8175 | 2.2507 | 2.2865 | 2.4401 | 2.3787 | 2.5323 | 1.026 | 1.5542 | 1.8503 | 1.8503 | 2.0477 | 2.0477 | 2019-10-26 18:00 | 1.7605 | 2.8851 | 4.7359 | 4.7359 | 4.7359 | 4.7359
2021-08-29 05:00 | 1.926 | 2.3851 | 2.4231 | 2.5859 | 2.5208 | 2.6836 | 1.046 | 1.5845 | 1.8864 | 1.8864 | 2.0877 | 2.0877 | 2019-10-26 19:00 | 1.73 | 2.8351 | 4.6538 | 4.6538 | 4.6538 | 4.6538
2021-08-29 06:00 | 2.1388 | 2.6486 | 2.6908 | 2.8716 | 2.7992 | 2.98 | 1.0932 | 1.656 | 1.9715 | 1.9715 | 2.1819 | 2.1819 | 2019-10-26 20:00 | 1.6233 | 2.6602 | 4.3668 | 4.3668 | 4.3668 | 4.3668
2021-08-29 07:00 | 2.3749 | 2.9409 | 2.9878 | 3.1885 | 3.1082 | 3.309 | 1.3261 | 2.0087 | 2.3915 | 2.3915 | 2.6467 | 2.6467 | 2019-10-26 21:00 | 1.6842 | 2.7602 | 4.5308 | 4.5308 | 4.5308 | 4.5308
2021-08-29 08:00 | 2.5521 | 3.1604 | 3.2107 | 3.4264 | 3.3401 | 3.5559 | 1.4318 | 2.1689 | 2.5822 | 2.5822 | 2.8577 | 2.8577 | 2019-10-26 22:00 | 1.5547 | 2.5478 | 4.1823 | 4.1823 | 4.1823 | 4.1823
2021-08-29 09:00 | 2.8449 | 3.5229 | 3.579 | 3.8195 | 3.7233 | 3.9638 | 1.6461 | 2.4936 | 2.9687 | 2.9687 | 3.2855 | 3.2855 | 2019-10-26 23:00 | 1.509 | 2.4729 | 4.0593 | 4.0593 | 4.0593 | 4.0593
2021-08-29 10:00 | 2.855 | 3.5355 | 3.5918 | 3.8331 | 3.7366 | 3.978 | 1.7919 | 2.7144 | 3.2316 | 3.2316 | 3.5764 | 3.5764 | 2019-10-27 | 1.4251 | 2.3355 | 3.8338 | 3.8338 | 3.8338 | 3.8338
2021-08-29 11:00 | 2.9007 | 3.5921 | 3.6493 | 3.8945 | 3.7965 | 4.0417 | 1.8633 | 2.8226 | 3.3604 | 3.3604 | 3.719 | 3.719 | 2019-10-27 01:00 | 1.2879 | 2.1107 | 3.4648 | 3.4648 | 3.4648 | 3.4648
2021-08-29 12:00 | 3.1208 | 3.8646 | 3.9262 | 4.19 | 4.0845 | 4.3483 | 1.9891 | 3.0131 | 3.5872 | 3.5872 | 3.97 | 3.97 | 2019-10-27 02:00 | 1.3565 | 2.2231 | 3.6493 | 3.6493 | 3.6493 | 3.6493
2021-08-29 13:00 | 3.158 | 3.9106 | 3.9729 | 4.2399 | 4.1331 | 4.4 | 2.052 | 3.1083 | 3.7006 | 3.7006 | 4.0955 | 4.0955 | 2019-10-27 03:00 | 1.2727 | 2.0857 | 3.4238 | 3.4238 | 3.4238 | 3.4238
2021-08-29 14:00 | 3.1751 | 3.9319 | 3.9945 | 4.2629 | 4.1555 | 4.4239 | 2.0338 | 3.0807 | 3.6678 | 3.6678 | 4.0591 | 4.0591 | 2019-10-27 04:00 | 1.2575 | 2.0608 | 3.3828 | 3.3828 | 3.3828 | 3.3828
2021-08-29 15:00 | 3.0579 | 3.7868 | 3.8471 | 4.1056 | 4.0022 | 4.2607 | 1.9548 | 2.9611 | 3.5254 | 3.5254 | 3.9015 | 3.9015 | 2019-10-27 05:00 | 1.4099 | 2.3105 | 3.7928 | 3.7928 | 3.7928 | 3.7928
2021-08-29 16:00 | 3.0494 | 3.7761 | 3.8363 | 4.0941 | 3.991 | 4.2487 | 2.0777 | 3.1473 | 3.747 | 3.747 | 4.1468 | 4.1468 | 2019-10-27 06:00 | 1.3718 | 2.2481 | 3.6903 | 3.6903 | 3.6903 | 3.6903
2021-08-29 17:00 | 3.498 | 4.3318 | 4.4008 | 4.6965 | 4.5782 | 4.8739 | 2.1748 | 3.2945 | 3.9222 | 3.9222 | 4.3408 | 4.3408 | 2019-10-27 07:00 | 1.7071 | 2.7976 | 4.5923 | 4.5923 | 4.5923 | 4.5923
2021-08-29 18:00 | 3.5523 | 4.399 | 4.4691 | 4.7694 | 4.6493 | 4.9495 | 2.2977 | 3.4806 | 4.1439 | 4.1439 | 4.586 | 4.586 | 2019-10-27 08:00 | 1.669 | 2.7352 | 4.4898 | 4.4898 | 4.4898 | 4.4898
2021-08-29 19:00 | 3.3676 | 4.1703 | 4.2367 | 4.5214 | 4.4075 | 4.6922 | 2.3206 | 3.5153 | 4.1851 | 4.1851 | 4.6317 | 4.6317 | 2019-10-27 09:00 | 1.8443 | 3.0224 | 4.9614 | 4.9614 | 4.9614 | 4.9614
2021-08-29 20:00 | 3.0894 | 3.8257 | 3.8866 | 4.1478 | 4.0433 | 4.3045 | 2.1537 | 3.2624 | 3.884 | 3.884 | 4.2985 | 4.2985 | 2019-10-27 10:00 | 1.8443 | 3.0224 | 4.9614 | 4.9614 | 4.9614 | 4.9614
2021-08-29 21:00 | 2.855 | 3.5355 | 3.5918 | 3.8331 | 3.7366 | 3.978 | 1.9788 | 2.9975 | 3.5686 | 3.5686 | 3.9494 | 3.9494 | 2019-10-27 11:00 | 1.8671 | 3.0599 | 5.0229 | 5.0229 | 5.0229 | 5.0229
2021-08-29 22:00 | 2.5808 | 3.1959 | 3.2468 | 3.465 | 3.3777 | 3.5959 | 1.7776 | 2.6927 | 3.2058 | 3.2058 | 3.5479 | 3.5479 | 2019-10-27 12:00 | 1.9281 | 3.1598 | 5.1869 | 5.1869 | 5.1869 | 5.1869
2021-08-29 23:00 | 2.2816 | 2.8254 | 2.8704 | 3.0633 | 2.9862 | 3.179 | 1.509 | 2.2858 | 2.7213 | 2.7213 | 3.0117 | 3.0117 | 2019-10-27 13:00 | 1.8748 | 3.0724 | 5.0434 | 5.0434 | 5.0434 | 5.0434
2021-08-30 | 2.0119 | 2.4915 | 2.5312 | 2.7012 | 2.6332 | 2.8033 | 1.3261 | 2.0087 | 2.3915 | 2.3915 | 2.6467 | 2.6467 | 2019-10-27 14:00 | 2.0196 | 3.3097 | 5.4329 | 5.4329 | 5.4329 | 5.4329
2021-08-30 01:00 | 1.9148 | 2.3711 | 2.4089 | 2.5708 | 2.506 | 2.6679 | 1.1489 | 1.7403 | 2.0719 | 2.0719 | 2.293 | 2.293 | 2019-10-27 15:00 | 1.8595 | 3.0474 | 5.0024 | 5.0024 | 5.0024 | 5.0024
2021-08-30 02:00 | 1.8576 | 2.3004 | 2.337 | 2.494 | 2.4312 | 2.5883 | 1.0145 | 1.5368 | 1.8297 | 1.8297 | 2.0249 | 2.0249 | 2019-10-27 16:00 | 1.89 | 3.0974 | 5.0844 | 5.0844 | 5.0844 | 5.0844
2021-08-30 03:00 | 1.809 | 2.2402 | 2.2759 | 2.4288 | 2.3676 | 2.5206 | 1.0003 | 1.5152 | 1.8039 | 1.8039 | 1.9964 | 1.9964 | 2019-10-27 17:00 | 1.7757 | 2.91 | 4.7769 | 4.7769 | 4.7769 | 4.7769
2021-08-30 04:00 | 1.8994 | 2.3521 | 2.3896 | 2.5502 | 2.4859 | 2.6465 | 1.0546 | 1.5974 | 1.9018 | 1.9018 | 2.1048 | 2.1048 | 2019-10-27 18:00 | 1.669 | 2.7352 | 4.4898 | 4.4898 | 4.4898 | 4.4898
2021-08-30 05:00 | 2.092 | 2.5906 | 2.6318 | 2.8087 | 2.7379 | 2.9148 | 1.0746 | 1.6278 | 1.9379 | 1.9379 | 2.1447 | 2.1447 | 2019-10-27 19:00 | 1.669 | 2.7352 | 4.4898 | 4.4898 | 4.4898 | 4.4898
2021-08-30 06:00 | 2.7178 | 3.3656 | 3.4192 | 3.649 | 3.5571 | 3.7868 | 1.2689 | 1.9221 | 2.2884 | 2.2884 | 2.5326 | 2.5326 | 2019-10-27 20:00 | 1.6538 | 2.7102 | 4.4488 | 4.4488 | 4.4488 | 4.4488
2021-08-30 07:00 | 3.3494 | 4.1477 | 4.2138 | 4.4969 | 4.3837 | 4.6668 | 1.709 | 2.5888 | 3.0821 | 3.0821 | 3.411 | 3.411 | 2019-10-27 21:00 | 1.6157 | 2.6478 | 4.3463 | 4.3463 | 4.3463 | 4.3463
2021-08-30 08:00 | 3.6066 | 4.4663 | 4.5374 | 4.8423 | 4.7203 | 5.0252 | 1.8833 | 2.8529 | 3.3965 | 3.3965 | 3.7589 | 3.7589 | 2019-10-27 22:00 | 1.5166 | 2.4854 | 4.0798 | 4.0798 | 4.0798 | 4.0798
2021-08-30 09:00 | 3.6295 | 4.4946 | 4.5662 | 4.873 | 4.7502 | 5.0571 | 1.8833 | 2.8529 | 3.3965 | 3.3965 | 3.7589 | 3.7589 | 2019-10-27 23:00 | 1.4175 | 2.323 | 3.8133 | 3.8133 | 3.8133 | 3.8133
2021-08-30 10:00 | 3.4952 | 4.3282 | 4.3972 | 4.6926 | 4.5744 | 4.8699 | 1.9405 | 2.9395 | 3.4996 | 3.4996 | 3.873 | 3.873 | 2019-10-28 | 1.3261 | 2.1732 | 3.5673 | 3.5673 | 3.5673 | 3.5673
2021-08-30 11:00 | 3.1271 | 3.8724 | 3.9341 | 4.1984 | 4.0927 | 4.357 | 1.7805 | 2.697 | 3.211 | 3.211 | 3.5536 | 3.5536 | 2019-10-28 01:00 | 1.2194 | 1.9983 | 3.2802 | 3.2802 | 3.2802 | 3.2802
2021-08-30 12:00 | 2.6893 | 3.3302 | 3.3833 | 3.6106 | 3.5197 | 3.747 | 1.6919 | 2.5628 | 3.0512 | 3.0512 | 3.3768 | 3.3768 | 2019-10-28 02:00 | 1.2803 | 2.0982 | 3.4443 | 3.4443 | 3.4443 | 3.4443
2021-08-30 13:00 | 2.5521 | 3.1604 | 3.2107 | 3.4264 | 3.3401 | 3.5559 | 1.6633 | 2.5196 | 2.9997 | 2.9997 | 3.3197 | 3.3197 | 2019-10-28 03:00 | 1.2194 | 1.9983 | 3.2802 | 3.2802 | 3.2802 | 3.2802
2021-08-30 14:00 | 2.5407 | 3.1462 | 3.1963 | 3.4111 | 3.3252 | 3.5399 | 1.6633 | 2.5196 | 2.9997 | 2.9997 | 3.3197 | 3.3197 | 2019-10-28 04:00 | 1.3108 | 2.1482 | 3.5263 | 3.5263 | 3.5263 | 3.5263
2021-08-30 15:00 | 2.5664 | 3.178 | 3.2287 | 3.4456 | 3.3588 | 3.5758 | 1.6719 | 2.5325 | 3.0151 | 3.0151 | 3.3368 | 3.3368 | 2019-10-28 05:00 | 1.4327 | 2.348 | 3.8543 | 3.8543 | 3.8543 | 3.8543
2021-08-30 16:00 | 2.7378 | 3.3903 | 3.4443 | 3.6757 | 3.5832 | 3.8146 | 1.7919 | 2.7144 | 3.2316 | 3.2316 | 3.5764 | 3.5764 | 2019-10-28 06:00 | 1.5547 | 2.5478 | 4.1823 | 4.1823 | 4.1823 | 4.1823
2021-08-30 17:00 | 3.5066 | 4.3424 | 4.4116 | 4.708 | 4.5894 | 4.8858 | 2.1034 | 3.1862 | 3.7934 | 3.7934 | 4.1982 | 4.1982 | 2019-10-28 07:00 | 1.9129 | 3.1348 | 5.1459 | 5.1459 | 5.1459 | 5.1459
2021-08-30 18:00 | 3.6267 | 4.491 | 4.5626 | 4.8691 | 4.7465 | 5.0531 | 2.4235 | 3.6711 | 4.3706 | 4.3706 | 4.837 | 4.837 | 2019-10-28 08:00 | 2.1644 | 3.547 | 5.8224 | 5.8224 | 5.8224 | 5.8224
2021-08-30 19:00 | 3.5181 | 4.3565 | 4.4259 | 4.7233 | 4.6044 | 4.9018 | 2.2834 | 3.459 | 4.1181 | 4.1181 | 4.5575 | 4.5575 | 2019-10-28 09:00 | 2.1339 | 3.497 | 5.7404 | 5.7404 | 5.7404 | 5.7404
2021-08-30 20:00 | 3.0379 | 3.762 | 3.8219 | 4.0787 | 3.976 | 4.2328 | 2.1377 | 3.2382 | 3.8552 | 3.8552 | 4.2666 | 4.2666 | 2019-10-28 10:00 | 2.1644 | 3.547 | 5.8224 | 5.8224 | 5.8224 | 5.8224
2021-08-30 21:00 | 2.9074 | 3.6004 | 3.6578 | 3.9035 | 3.8052 | 4.051 | 2.0034 | 3.0347 | 3.613 | 3.613 | 3.9985 | 3.9985 | 2019-10-28 11:00 | 2.233 | 3.6594 | 6.007 | 6.007 | 6.007 | 6.007
2021-08-30 22:00 | 2.5607 | 3.171 | 3.2215 | 3.4379 | 3.3514 | 3.5678 | 1.7204 | 2.6061 | 3.1027 | 3.1027 | 3.4338 | 3.4338 | 2019-10-28 12:00 | 2.2406 | 3.6719 | 6.0275 | 6.0275 | 6.0275 | 6.0275
2021-08-30 23:00 | 2.3041 | 2.8533 | 2.8987 | 3.0935 | 3.0156 | 3.2103 | 1.4756 | 2.2353 | 2.6613 | 2.6613 | 2.9452 | 2.9452 | 2019-10-28 13:00 | 2.172 | 3.5595 | 5.8429 | 5.8429 | 5.8429 | 5.8429
2021-08-31 | 2.0091 | 2.4879 | 2.5276 | 2.6974 | 2.6295 | 2.7993 | 1.2318 | 1.8659 | 2.2215 | 2.2215 | 2.4585 | 2.4585 | 2019-10-28 14:00 | 2.2634 | 3.7094 | 6.089 | 6.089 | 6.089 | 6.089
2021-08-31 01:00 | 1.8691 | 2.3146 | 2.3515 | 2.5095 | 2.4463 | 2.6043 | 1.0831 | 1.6407 | 1.9534 | 1.9534 | 2.1618 | 2.1618 | 2019-10-28 15:00 | 2.1491 | 3.522 | 5.7814 | 5.7814 | 5.7814 | 5.7814
2021-08-31 02:00 | 1.8433 | 2.2827 | 2.319 | 2.4749 | 2.4125 | 2.5683 | 1.0803 | 1.6364 | 1.9482 | 1.9482 | 2.1561 | 2.1561 | 2019-10-28 16:00 | 2.1415 | 3.5095 | 5.7609 | 5.7609 | 5.7609 | 5.7609
2021-08-31 03:00 | 1.8262 | 2.2614 | 2.2975 | 2.4518 | 2.3901 | 2.5445 | 1.0658 | 1.6145 | 1.9221 | 1.9221 | 2.1272 | 2.1272 | 2019-10-28 17:00 | 2.0577 | 3.3721 | 5.5354 | 5.5354 | 5.5354 | 5.5354
2021-08-31 04:00 | 1.9656 | 2.4341 | 2.4729 | 2.639 | 2.5726 | 2.7387 | 1.066 | 1.6148 | 1.9225 | 1.9225 | 2.1276 | 2.1276 | 2019-10-28 18:00 | 1.9891 | 3.2597 | 5.3509 | 5.3509 | 5.3509 | 5.3509
2021-08-31 05:00 | 2.208 | 2.7342 | 2.7778 | 2.9644 | 2.8898 | 3.0764 | 1.1374 | 1.723 | 2.0513 | 2.0513 | 2.2702 | 2.2702 | 2019-10-28 19:00 | 1.9434 | 3.1848 | 5.2279 | 5.2279 | 5.2279 | 5.2279
2021-08-31 06:00 | 2.7405 | 3.3937 | 3.4478 | 3.6794 | 3.5868 | 3.8184 | 1.3403 | 2.0304 | 2.4173 | 2.4173 | 2.6752 | 2.6752 | 2019-10-28 20:00 | 1.89 | 3.0974 | 5.0844 | 5.0844 | 5.0844 | 5.0844
2021-08-31 07:00 | 3.378 | 4.1831 | 4.2498 | 4.5353 | 4.4211 | 4.7066 | 1.6376 | 2.4806 | 2.9533 | 2.9533 | 3.2684 | 3.2684 | 2019-10-28 21:00 | 1.7909 | 2.935 | 4.8179 | 4.8179 | 4.8179 | 4.8179
2021-08-31 08:00 | 3.2037 | 3.9673 | 4.0304 | 4.3013 | 4.1929 | 4.4637 | 1.6947 | 2.5672 | 3.0564 | 3.0564 | 3.3825 | 3.3825 | 2019-10-28 22:00 | 1.5852 | 2.5978 | 4.2643 | 4.2643 | 4.2643 | 4.2643
2021-08-31 09:00 | 2.9282 | 3.6261 | 3.6839 | 3.9314 | 3.8324 | 4.0799 | 1.6604 | 2.5152 | 2.9945 | 2.9945 | 3.314 | 3.314 | 2019-10-28 23:00 | 1.4556 | 2.3855 | 3.9158 | 3.9158 | 3.9158 | 3.9158
2021-08-31 10:00 | 2.6835 | 3.3231 | 3.3761 | 3.6029 | 3.5122 | 3.739 | 1.5861 | 2.4027 | 2.8605 | 2.8605 | 3.1657 | 3.1657 | 2019-10-29 | 1.3718 | 2.2481 | 3.6903 | 3.6903 | 3.6903 | 3.6903
2021-08-31 11:00 | 2.3778 | 2.9445 | 2.9914 | 3.1924 | 3.112 | 3.313 | 1.4289 | 2.1646 | 2.577 | 2.577 | 2.852 | 2.852 | 2019-10-29 01:00 | 1.2346 | 2.0233 | 3.3212 | 3.3212 | 3.3212 | 3.3212
2021-08-31 12:00 | 2.0291 | 2.5127 | 2.5527 | 2.7243 | 2.6556 | 2.8272 | 1.4689 | 2.2252 | 2.6492 | 2.6492 | 2.9319 | 2.9319 | 2019-10-29 02:00 | 1.2422 | 2.0358 | 3.3417 | 3.3417 | 3.3417 | 3.3417
2021-08-31 13:00 | 2.112 | 2.6153 | 2.657 | 2.8355 | 2.7641 | 2.9426 | 1.4375 | 2.1776 | 2.5925 | 2.5925 | 2.8691 | 2.8691 | 2019-10-29 03:00 | 1.2575 | 2.0608 | 3.3828 | 3.3828 | 3.3828 | 3.3828
2021-08-31 14:00 | 2.2034 | 2.7286 | 2.7721 | 2.9583 | 2.8838 | 3.0701 | 1.4089 | 2.1343 | 2.541 | 2.541 | 2.8121 | 2.8121 | 2019-10-29 04:00 | 1.3489 | 2.2106 | 3.6288 | 3.6288 | 3.6288 | 3.6288
2021-08-31 15:00 | 2.2091 | 2.7357 | 2.7792 | 2.966 | 2.8913 | 3.078 | 1.4508 | 2.1977 | 2.6165 | 2.6165 | 2.8957 | 2.8957 | 2019-10-29 05:00 | 1.3946 | 2.2856 | 3.7518 | 3.7518 | 3.7518 | 3.7518
2021-08-31 16:00 | 2.3549 | 2.9162 | 2.9626 | 3.1617 | 3.082 | 3.2811 | 1.5518 | 2.3507 | 2.7987 | 2.7987 | 3.0973 | 3.0973 | 2019-10-29 06:00 | 1.5928 | 2.6103 | 4.2848 | 4.2848 | 4.2848 | 4.2848
2021-08-31 17:00 | 3.0722 | 3.8045 | 3.8651 | 4.1248 | 4.0209 | 4.2806 | 1.8947 | 2.8701 | 3.417 | 3.417 | 3.7816 | 3.7816 | 2019-10-29 07:00 | 1.8519 | 3.0349 | 4.9819 | 4.9819 | 4.9819 | 4.9819
2021-08-31 18:00 | 3.3009 | 4.0876 | 4.1527 | 4.4317 | 4.3201 | 4.5991 | 2.0748 | 3.143 | 3.7419 | 3.7419 | 4.1411 | 4.1411 | 2019-10-29 08:00 | 2.0805 | 3.4096 | 5.5969 | 5.5969 | 5.5969 | 5.5969
2021-08-31 19:00 | 3.2094 | 3.9743 | 4.0376 | 4.3089 | 4.2004 | 4.4717 | 2.0662 | 3.13 | 3.7264 | 3.7264 | 4.124 | 4.124 | 2019-10-29 09:00 | 2.1186 | 3.4721 | 5.6994 | 5.6994 | 5.6994 | 5.6994
2021-08-31 20:00 | 2.875 | 3.5603 | 3.617 | 3.86 | 3.7628 | 4.0058 | 1.9262 | 2.9178 | 3.4738 | 3.4738 | 3.8445 | 3.8445 | 2019-10-29 10:00 | 2.0882 | 3.4221 | 5.6174 | 5.6174 | 5.6174 | 5.6174
2021-08-31 21:00 | 2.7423 | 3.3959 | 3.45 | 3.6818 | 3.5891 | 3.8209 | 1.9206 | 2.9094 | 3.4638 | 3.4638 | 3.8334 | 3.8334 | 2019-10-29 11:00 | 2.1186 | 3.4721 | 5.6994 | 5.6994 | 5.6994 | 5.6994
2021-08-31 22:00 | 2.3663 | 2.9303 | 2.977 | 3.177 | 3.097 | 3.297 | 1.6176 | 2.4503 | 2.9172 | 2.9172 | 3.2285 | 3.2285 | 2019-10-29 12:00 | 2.0196 | 3.3097 | 5.4329 | 5.4329 | 5.4329 | 5.4329
2021-08-31 23:00 | 2.2552 | 2.7927 | 2.8372 | 3.0278 | 2.9516 | 3.1422 | 1.394 | 2.1116 | 2.514 | 2.514 | 2.7822 | 2.7822 | 2019-10-29 13:00 | 2.1949 | 3.597 | 5.9044 | 5.9044 | 5.9044 | 5.9044
2021-09-01 | 1.8672 | 2.3123 | 2.3491 | 2.5069 | 2.4438 | 2.6016 | 1.1976 | 1.8141 | 2.1598 | 2.1598 | 2.3902 | 2.3902 | 2019-10-29 14:00 | 2.2177 | 3.6344 | 5.966 | 5.966 | 5.966 | 5.966
2021-09-01 01:00 | 1.7805 | 2.2048 | 2.2399 | 2.3904 | 2.3302 | 2.4807 | 1.0145 | 1.5368 | 1.8297 | 1.8297 | 2.0249 | 2.0249 | 2019-10-29 15:00 | 2.2025 | 3.6094 | 5.9249 | 5.9249 | 5.9249 | 5.9249
2021-09-01 02:00 | 1.6919 | 2.0951 | 2.1285 | 2.2715 | 2.2143 | 2.3573 | 0.96308 | 1.4589 | 1.7369 | 1.7369 | 1.9222 | 1.9222 | 2019-10-29 16:00 | 2.4616 | 4.0341 | 6.622 | 6.622 | 6.622 | 6.622
2021-09-01 03:00 | 1.7062 | 2.1128 | 2.1465 | 2.2907 | 2.233 | 2.3772 | 0.97707 | 1.4801 | 1.7621 | 1.7621 | 1.9501 | 1.9501 | 2019-10-29 17:00 | 2.2253 | 3.6469 | 5.9865 | 5.9865 | 5.9865 | 5.9865
2021-09-01 04:00 | 1.7833 | 2.2084 | 2.2435 | 2.3943 | 2.334 | 2.4847 | 0.97739 | 1.4806 | 1.7627 | 1.7627 | 1.9508 | 1.9508 | 2019-10-29 18:00 | 1.9967 | 3.2722 | 5.3714 | 5.3714 | 5.3714 | 5.3714
2021-09-01 05:00 | 1.9805 | 2.4525 | 2.4916 | 2.659 | 2.5921 | 2.7595 | 1.0854 | 1.6442 | 1.9575 | 1.9575 | 2.1664 | 2.1664 | 2019-10-29 19:00 | 1.9053 | 3.1224 | 5.1254 | 5.1254 | 5.1254 | 5.1254
2021-09-01 06:00 | 2.5121 | 3.1108 | 3.1604 | 3.3727 | 3.2878 | 3.5001 | 1.2203 | 1.8485 | 2.2008 | 2.2008 | 2.4356 | 2.4356 | 2019-10-29 20:00 | 1.8443 | 3.0224 | 4.9614 | 4.9614 | 4.9614 | 4.9614
2021-09-01 07:00 | 2.7636 | 3.4222 | 3.4768 | 3.7104 | 3.6169 | 3.8505 | 1.4118 | 2.1386 | 2.5461 | 2.5461 | 2.8178 | 2.8178 | 2019-10-29 21:00 | 1.73 | 2.8351 | 4.6538 | 4.6538 | 4.6538 | 4.6538
2021-09-01 08:00 | 2.7064 | 3.3515 | 3.4048 | 3.6336 | 3.5421 | 3.7709 | 1.4718 | 2.2295 | 2.6543 | 2.6543 | 2.9376 | 2.9376 | 2019-10-29 22:00 | 1.5471 | 2.5353 | 4.1618 | 4.1618 | 4.1618 | 4.1618
2021-09-01 09:00 | 2.4149 | 2.9905 | 3.0381 | 3.2422 | 3.1606 | 3.3647 | 1.3689 | 2.0737 | 2.4688 | 2.4688 | 2.7322 | 2.7322 | 2019-10-29 23:00 | 1.4023 | 2.2981 | 3.7723 | 3.7723 | 3.7723 | 3.7723
2021-09-01 10:00 | 2.2263 | 2.7569 | 2.8008 | 2.989 | 2.9137 | 3.1019 | 1.3861 | 2.0996 | 2.4997 | 2.4997 | 2.7664 | 2.7664 | 2019-10-30 | 1.2956 | 2.1232 | 3.4853 | 3.4853 | 3.4853 | 3.4853
2021-09-01 11:00 | 1.9376 | 2.3995 | 2.4377 | 2.6015 | 2.536 | 2.6997 | 1.2689 | 1.9221 | 2.2884 | 2.2884 | 2.5326 | 2.5326 | 2019-10-30 01:00 | 1.2575 | 2.0608 | 3.3828 | 3.3828 | 3.3828 | 3.3828
2021-09-01 12:00 | 1.8062 | 2.2367 | 2.2723 | 2.425 | 2.3639 | 2.5166 | 1.3118 | 1.9871 | 2.3657 | 2.3657 | 2.6181 | 2.6181 | 2019-10-30 02:00 | 1.2041 | 1.9733 | 3.2392 | 3.2392 | 3.2392 | 3.2392
2021-09-01 13:00 | 1.689 | 2.0916 | 2.1249 | 2.2677 | 2.2105 | 2.3533 | 1.206 | 1.8269 | 2.175 | 2.175 | 2.4071 | 2.4071 | 2019-10-30 03:00 | 1.1584 | 1.8984 | 3.1162 | 3.1162 | 3.1162 | 3.1162
2021-09-01 14:00 | 1.6463 | 2.0387 | 2.0712 | 2.2104 | 2.1547 | 2.2939 | 1.2146 | 1.8399 | 2.1905 | 2.1905 | 2.4242 | 2.4242 | 2019-10-30 04:00 | 1.2346 | 2.0233 | 3.3212 | 3.3212 | 3.3212 | 3.3212
2021-09-01 15:00 | 1.7319 | 2.1446 | 2.1788 | 2.3252 | 2.2666 | 2.413 | 1.226 | 1.8572 | 2.2111 | 2.2111 | 2.447 | 2.447 | 2019-10-30 05:00 | 1.3184 | 2.1607 | 3.5468 | 3.5468 | 3.5468 | 3.5468
2021-09-01 16:00 | 1.9176 | 2.3747 | 2.4125 | 2.5746 | 2.5098 | 2.6719 | 1.3146 | 1.9914 | 2.3709 | 2.3709 | 2.6238 | 2.6238 | 2019-10-30 06:00 | 1.5242 | 2.4979 | 4.1003 | 4.1003 | 4.1003 | 4.1003
2021-09-01 17:00 | 2.5206 | 3.1214 | 3.1711 | 3.3842 | 3.299 | 3.5121 | 1.5147 | 2.2944 | 2.7317 | 2.7317 | 3.0231 | 3.0231 | 2019-10-30 07:00 | 1.8367 | 3.0099 | 4.9409 | 4.9409 | 4.9409 | 4.9409
2021-09-01 18:00 | 2.7264 | 3.3762 | 3.43 | 3.6605 | 3.5683 | 3.7988 | 1.7833 | 2.7014 | 3.2161 | 3.2161 | 3.5593 | 3.5593 | 2019-10-30 08:00 | 2.0653 | 3.3846 | 5.5559 | 5.5559 | 5.5559 | 5.5559
2021-09-01 19:00 | 2.6322 | 3.2596 | 3.3115 | 3.534 | 3.445 | 3.6675 | 1.7747 | 2.6884 | 3.2007 | 3.2007 | 3.5422 | 3.5422 | 2019-10-30 09:00 | 2.1034 | 3.4471 | 5.6584 | 5.6584 | 5.6584 | 5.6584
2021-09-01 20:00 | 2.4692 | 3.0577 | 3.1064 | 3.3152 | 3.2317 | 3.4404 | 1.7776 | 2.6927 | 3.2058 | 3.2058 | 3.5479 | 3.5479 | 2019-10-30 10:00 | 2.1567 | 3.5345 | 5.8019 | 5.8019 | 5.8019 | 5.8019
2021-09-01 21:00 | 2.3435 | 2.902 | 2.9482 | 3.1463 | 3.0671 | 3.2652 | 1.6519 | 2.5022 | 2.979 | 2.979 | 3.2969 | 3.2969 | 2019-10-30 11:00 | 2.233 | 3.6594 | 6.007 | 6.007 | 6.007 | 6.007
2021-09-01 22:00 | 2.0873 | 2.5848 | 2.626 | 2.8024 | 2.7319 | 2.9083 | 1.4718 | 2.2295 | 2.6543 | 2.6543 | 2.9376 | 2.9376 | 2019-10-30 12:00 | 2.4082 | 3.9467 | 6.4785 | 6.4785 | 6.4785 | 6.4785
2021-09-01 23:00 | 2.0099 | 2.4889 | 2.5285 | 2.6984 | 2.6305 | 2.8004 | 1.3003 | 1.9698 | 2.3451 | 2.3451 | 2.5953 | 2.5953 | 2019-10-30 13:00 | 2.4387 | 3.9966 | 6.5605 | 6.5605 | 6.5605 | 6.5605
2021-09-02 | 1.7805 | 2.2048 | 2.2399 | 2.3904 | 2.3302 | 2.4807 | 1.1348 | 1.719 | 2.0466 | 2.0466 | 2.2649 | 2.2649 | 2019-10-30 14:00 | 2.4082 | 3.9467 | 6.4785 | 6.4785 | 6.4785 | 6.4785
2021-09-02 01:00 | 1.6118 | 1.996 | 2.0278 | 2.1641 | 2.1096 | 2.2458 | 0.9974 | 1.5109 | 1.7988 | 1.7988 | 1.9907 | 1.9907 | 2019-10-30 15:00 | 2.393 | 3.9217 | 6.4375 | 6.4375 | 6.4375 | 6.4375
2021-09-02 02:00 | 1.6068 | 1.9898 | 2.0215 | 2.1573 | 2.103 | 2.2388 | 0.9631 | 1.4589 | 1.7369 | 1.7369 | 1.9223 | 1.9223 | 2019-10-30 16:00 | 2.3701 | 3.8842 | 6.376 | 6.376 | 6.376 | 6.376
2021-09-02 03:00 | 1.6233 | 2.0102 | 2.0422 | 2.1794 | 2.1245 | 2.2617 | 0.91738 | 1.3896 | 1.6545 | 1.6545 | 1.831 | 1.831 | 2019-10-30 17:00 | 2.233 | 3.6594 | 6.007 | 6.007 | 6.007 | 6.007
2021-09-02 04:00 | 1.6716 | 2.07 | 2.103 | 2.2443 | 2.1878 | 2.3291 | 0.90844 | 1.3761 | 1.6383 | 1.6383 | 1.8131 | 1.8131 | 2019-10-30 18:00 | 1.9815 | 3.2472 | 5.3304 | 5.3304 | 5.3304 | 5.3304
2021-09-02 05:00 | 1.8914 | 2.3422 | 2.3795 | 2.5394 | 2.4754 | 2.6353 | 0.98882 | 1.4979 | 1.7833 | 1.7833 | 1.9736 | 1.9736 | 2019-10-30 19:00 | 1.951 | 3.1973 | 5.2484 | 5.2484 | 5.2484 | 5.2484
2021-09-02 06:00 | 2.3206 | 2.8737 | 2.9195 | 3.1156 | 3.0372 | 3.2333 | 1.1231 | 1.7012 | 2.0254 | 2.0254 | 2.2415 | 2.2415 | 2019-10-30 20:00 | 1.8748 | 3.0724 | 5.0434 | 5.0434 | 5.0434 | 5.0434
2021-09-02 07:00 | 2.7007 | 3.3444 | 3.3977 | 3.6259 | 3.5346 | 3.7629 | 1.3603 | 2.0607 | 2.4533 | 2.4533 | 2.7151 | 2.7151 | 2019-10-30 21:00 | 1.7681 | 2.8975 | 4.7564 | 4.7564 | 4.7564 | 4.7564
2021-09-02 08:00 | 2.6264 | 3.2524 | 3.3042 | 3.5262 | 3.4374 | 3.6594 | 1.4261 | 2.1602 | 2.5719 | 2.5719 | 2.8463 | 2.8463 | 2019-10-30 22:00 | 1.5623 | 2.5603 | 4.2028 | 4.2028 | 4.2028 | 4.2028
2021-09-02 09:00 | 2.4092 | 2.9834 | 3.0309 | 3.2346 | 3.1531 | 3.3568 | 1.4547 | 2.2035 | 2.6234 | 2.6234 | 2.9033 | 2.9033 | 2019-10-30 23:00 | 1.4023 | 2.2981 | 3.7723 | 3.7723 | 3.7723 | 3.7723
2021-09-02 10:00 | 2.1406 | 2.6507 | 2.693 | 2.8739 | 2.8015 | 2.9825 | 1.3632 | 2.065 | 2.4585 | 2.4585 | 2.7208 | 2.7208 | 2019-10-31 | 1.2498 | 2.0483 | 3.3622 | 3.3622 | 3.3622 | 3.3622
2021-09-02 11:00 | 1.9919 | 2.4667 | 2.506 | 2.6744 | 2.607 | 2.7754 | 1.3032 | 1.9741 | 2.3503 | 2.3503 | 2.601 | 2.601 | 2019-10-31 01:00 | 1.2346 | 2.0233 | 3.3212 | 3.3212 | 3.3212 | 3.3212
2021-09-02 12:00 | 1.7862 | 2.2119 | 2.2471 | 2.3981 | 2.3377 | 2.4887 | 1.246 | 1.8875 | 2.2472 | 2.2472 | 2.4869 | 2.4869 | 2019-10-31 02:00 | 1.1889 | 1.9483 | 3.1982 | 3.1982 | 3.1982 | 3.1982
2021-09-02 13:00 | 1.7576 | 2.1765 | 2.2112 | 2.3597 | 2.3003 | 2.4489 | 1.2289 | 1.8615 | 2.2162 | 2.2162 | 2.4527 | 2.4527 | 2019-10-31 03:00 | 1.1736 | 1.9234 | 3.1572 | 3.1572 | 3.1572 | 3.1572
2021-09-02 14:00 | 1.6547 | 2.0491 | 2.0817 | 2.2216 | 2.1657 | 2.3055 | 1.1832 | 1.7923 | 2.1338 | 2.1338 | 2.3615 | 2.3615 | 2019-10-31 04:00 | 1.1813 | 1.9359 | 3.1777 | 3.1777 | 3.1777 | 3.1777
2021-09-02 15:00 | 1.6919 | 2.0951 | 2.1285 | 2.2715 | 2.2143 | 2.3573 | 1.1632 | 1.762 | 2.0977 | 2.0977 | 2.3215 | 2.3215 | 2019-10-31 05:00 | 1.3337 | 2.1856 | 3.5878 | 3.5878 | 3.5878 | 3.5878
2021-09-02 16:00 | 1.883 | 2.3318 | 2.3689 | 2.5281 | 2.4644 | 2.6236 | 1.2274 | 1.8593 | 2.2136 | 2.2136 | 2.4498 | 2.4498 | 2019-10-31 06:00 | 1.5318 | 2.5104 | 4.1208 | 4.1208 | 4.1208 | 4.1208
2021-09-02 17:00 | 2.3549 | 2.9162 | 2.9626 | 3.1617 | 3.082 | 3.2811 | 1.4032 | 2.1256 | 2.5306 | 2.5306 | 2.8007 | 2.8007 | 2019-10-31 07:00 | 1.8519 | 3.0349 | 4.9819 | 4.9819 | 4.9819 | 4.9819
2021-09-02 18:00 | 2.6207 | 3.2453 | 3.297 | 3.5185 | 3.4299 | 3.6514 | 1.669 | 2.5282 | 3.01 | 3.01 | 3.3311 | 3.3311 | 2019-10-31 08:00 | 2.0043 | 3.2847 | 5.3919 | 5.3919 | 5.3919 | 5.3919
2021-09-02 19:00 | 2.5178 | 3.1179 | 3.1675 | 3.3804 | 3.2952 | 3.5081 | 1.649 | 2.4979 | 2.9739 | 2.9739 | 3.2912 | 3.2912 | 2019-10-31 09:00 | 2.2482 | 3.6844 | 6.048 | 6.048 | 6.048 | 6.048
2021-09-02 20:00 | 2.292 | 2.8383 | 2.8835 | 3.0773 | 2.9998 | 3.1935 | 1.669 | 2.5282 | 3.01 | 3.01 | 3.3311 | 3.3311 | 2019-10-31 10:00 | 2.2558 | 3.6969 | 6.0685 | 6.0685 | 6.0685 | 6.0685
2021-09-02 21:00 | 2.2177 | 2.7463 | 2.79 | 2.9775 | 2.9025 | 3.09 | 1.5604 | 2.3637 | 2.8141 | 2.8141 | 3.1144 | 3.1144 | 2019-10-31 11:00 | 2.3549 | 3.8592 | 6.335 | 6.335 | 6.335 | 6.335
2021-09-02 22:00 | 2.0377 | 2.5233 | 2.5635 | 2.7358 | 2.6669 | 2.8391 | 1.3946 | 2.1126 | 2.5152 | 2.5152 | 2.7836 | 2.7836 | 2019-10-31 12:00 | 2.4082 | 3.9467 | 6.4785 | 6.4785 | 6.4785 | 6.4785
2021-09-02 23:00 | 1.9348 | 2.3959 | 2.4341 | 2.5976 | 2.5322 | 2.6958 | 1.2718 | 1.9265 | 2.2936 | 2.2936 | 2.5383 | 2.5383 | 2019-10-31 13:00 | 2.4997 | 4.0965 | 6.7245 | 6.7245 | 6.7245 | 6.7245
2021-09-03 | 1.6347 | 2.0243 | 2.0566 | 2.1948 | 2.1395 | 2.2777 | 1.0078 | 1.5266 | 1.8175 | 1.8175 | 2.0114 | 2.0114 | 2019-10-31 14:00 | 2.4387 | 3.9966 | 6.5605 | 6.5605 | 6.5605 | 6.5605
2021-09-03 01:00 | 1.6118 | 1.996 | 2.0278 | 2.1641 | 2.1096 | 2.2458 | 0.88022 | 1.3334 | 1.5874 | 1.5874 | 1.7568 | 1.7568 | 2019-10-31 15:00 | 2.4159 | 3.9591 | 6.499 | 6.499 | 6.499 | 6.499
2021-09-03 02:00 | 1.5518 | 1.9217 | 1.9523 | 2.0835 | 2.031 | 2.1622 | 0.89166 | 1.3507 | 1.6081 | 1.6081 | 1.7796 | 1.7796 | 2019-10-31 16:00 | 2.4006 | 3.9342 | 6.458 | 6.458 | 6.458 | 6.458
2021-09-03 03:00 | 1.5604 | 1.9323 | 1.9631 | 2.095 | 2.0422 | 2.1741 | 0.82307 | 1.2468 | 1.4844 | 1.4844 | 1.6428 | 1.6428 | 2019-10-31 17:00 | 2.2558 | 3.6969 | 6.0685 | 6.0685 | 6.0685 | 6.0685
2021-09-03 04:00 | 1.6204 | 2.0066 | 2.0386 | 2.1756 | 2.1208 | 2.2578 | 0.85736 | 1.2987 | 1.5462 | 1.5462 | 1.7112 | 1.7112 | 2019-10-31 18:00 | 2.0958 | 3.4346 | 5.6379 | 5.6379 | 5.6379 | 5.6379
2021-09-03 05:00 | 1.7772 | 2.2008 | 2.2358 | 2.386 | 2.326 | 2.4762 | 0.87737 | 1.329 | 1.5823 | 1.5823 | 1.7511 | 1.7511 | 2019-10-31 19:00 | 1.9205 | 3.1473 | 5.1664 | 5.1664 | 5.1664 | 5.1664
2021-09-03 06:00 | 2.0805 | 2.5764 | 2.6174 | 2.7933 | 2.723 | 2.8988 | 1.0203 | 1.5455 | 1.84 | 1.84 | 2.0363 | 2.0363 | 2019-10-31 20:00 | 1.9053 | 3.1224 | 5.1254 | 5.1254 | 5.1254 | 5.1254
2021-09-03 07:00 | 2.2692 | 2.81 | 2.8547 | 3.0466 | 2.9698 | 3.1617 | 1.206 | 1.8269 | 2.175 | 2.175 | 2.4071 | 2.4071 | 2019-10-31 21:00 | 1.8062 | 2.96 | 4.8589 | 4.8589 | 4.8589 | 4.8589
2021-09-03 08:00 | 2.3063 | 2.856 | 2.9015 | 3.0964 | 3.0185 | 3.2134 | 1.2975 | 1.9654 | 2.3399 | 2.3399 | 2.5896 | 2.5896 | 2019-10-31 22:00 | 1.509 | 2.4729 | 4.0593 | 4.0593 | 4.0593 | 4.0593
2021-09-03 09:00 | 1.9948 | 2.4702 | 2.5096 | 2.6782 | 2.6108 | 2.7794 | 1.2946 | 1.9611 | 2.3348 | 2.3348 | 2.5839 | 2.5839 | 2019-10-31 23:00 | 1.4251 | 2.3355 | 3.8338 | 3.8338 | 3.8338 | 3.8338
2021-09-03 10:00 | 2.0548 | 2.5446 | 2.5851 | 2.7588 | 2.6893 | 2.863 | 1.2775 | 1.9351 | 2.3039 | 2.3039 | 2.5497 | 2.5497 | 2019-11-01 | 1.2803 | 2.0982 | 3.4443 | 3.4443 | 3.4443 | 3.4443
2021-09-03 11:00 | 1.8633 | 2.3074 | 2.3442 | 2.5017 | 2.4387 | 2.5962 | 1.2946 | 1.9611 | 2.3348 | 2.3348 | 2.5839 | 2.5839 | 2019-11-01 01:00 | 1.227 | 2.0108 | 3.3007 | 3.3007 | 3.3007 | 3.3007
2021-09-03 12:00 | 1.8891 | 2.3393 | 2.3766 | 2.5362 | 2.4724 | 2.6321 | 1.2946 | 1.9611 | 2.3348 | 2.3348 | 2.5839 | 2.5839 | 2019-11-01 02:00 | 1.2194 | 1.9983 | 3.2802 | 3.2802 | 3.2802 | 3.2802
2021-09-03 13:00 | 1.7805 | 2.2048 | 2.2399 | 2.3904 | 2.3302 | 2.4807 | 1.3375 | 2.026 | 2.4121 | 2.4121 | 2.6695 | 2.6695 | 2019-11-01 03:00 | 1.166 | 1.9109 | 3.1367 | 3.1367 | 3.1367 | 3.1367
2021-09-03 14:00 | 1.7576 | 2.1765 | 2.2112 | 2.3597 | 2.3003 | 2.4489 | 1.3603 | 2.0607 | 2.4533 | 2.4533 | 2.7151 | 2.7151 | 2019-11-01 04:00 | 1.2575 | 2.0608 | 3.3828 | 3.3828 | 3.3828 | 3.3828
2021-09-03 15:00 | 1.7633 | 2.1836 | 2.2184 | 2.3674 | 2.3078 | 2.4569 | 1.2575 | 1.9048 | 2.2678 | 2.2678 | 2.5098 | 2.5098 | 2019-11-01 05:00 | 1.2879 | 2.1107 | 3.4648 | 3.4648 | 3.4648 | 3.4648
2021-09-03 16:00 | 1.8262 | 2.2614 | 2.2975 | 2.4518 | 2.3901 | 2.5445 | 1.208 | 1.8299 | 2.1786 | 2.1786 | 2.4111 | 2.4111 | 2019-11-01 06:00 | 1.5852 | 2.5978 | 4.2643 | 4.2643 | 4.2643 | 4.2643
2021-09-03 17:00 | 2.2434 | 2.7781 | 2.8224 | 3.012 | 2.9362 | 3.1258 | 1.3752 | 2.0831 | 2.4801 | 2.4801 | 2.7447 | 2.7447 | 2019-11-01 07:00 | 1.9586 | 3.2098 | 5.2689 | 5.2689 | 5.2689 | 5.2689
2021-09-03 18:00 | 2.5521 | 3.1604 | 3.2107 | 3.4264 | 3.3401 | 3.5559 | 1.5318 | 2.3204 | 2.7626 | 2.7626 | 3.0574 | 3.0574 | 2019-11-01 08:00 | 2.1491 | 3.522 | 5.7814 | 5.7814 | 5.7814 | 5.7814
2021-09-03 19:00 | 2.4949 | 3.0896 | 3.1388 | 3.3497 | 3.2653 | 3.4762 | 1.5433 | 2.3377 | 2.7832 | 2.7832 | 3.0802 | 3.0802 | 2019-11-01 09:00 | 2.233 | 3.6594 | 6.007 | 6.007 | 6.007 | 6.007
2021-09-03 20:00 | 2.2606 | 2.7994 | 2.844 | 3.0351 | 2.9586 | 3.1497 | 1.549 | 2.3464 | 2.7935 | 2.7935 | 3.0916 | 3.0916 | 2019-11-01 10:00 | 2.2482 | 3.6844 | 6.048 | 6.048 | 6.048 | 6.048
2021-09-03 21:00 | 2.1348 | 2.6437 | 2.6858 | 2.8662 | 2.794 | 2.9745 | 1.4461 | 2.1905 | 2.608 | 2.608 | 2.8862 | 2.8862 | 2019-11-01 11:00 | 2.3701 | 3.8842 | 6.376 | 6.376 | 6.376 | 6.376
2021-09-03 22:00 | 2.0405 | 2.5269 | 2.5671 | 2.7396 | 2.6706 | 2.8431 | 1.2832 | 1.9438 | 2.3142 | 2.3142 | 2.5611 | 2.5611 | 2019-11-01 12:00 | 2.3092 | 3.7843 | 6.212 | 6.212 | 6.212 | 6.212
2021-09-03 23:00 | 2.0291 | 2.5127 | 2.5527 | 2.7243 | 2.6556 | 2.8272 | 1.1374 | 1.723 | 2.0513 | 2.0513 | 2.2702 | 2.2702 | 2019-11-01 13:00 | 2.3549 | 3.8592 | 6.335 | 6.335 | 6.335 | 6.335
2021-09-04 | 1.7464 | 2.1626 | 2.1971 | 2.3447 | 2.2856 | 2.4333 | 1.0317 | 1.5628 | 1.8606 | 1.8606 | 2.0591 | 2.0591 | 2019-11-01 14:00 | 2.4082 | 3.9467 | 6.4785 | 6.4785 | 6.4785 | 6.4785
2021-09-04 01:00 | 1.6461 | 2.0385 | 2.0709 | 2.2101 | 2.1544 | 2.2936 | 0.88022 | 1.3334 | 1.5874 | 1.5874 | 1.7568 | 1.7568 | 2019-11-01 15:00 | 2.3701 | 3.8842 | 6.376 | 6.376 | 6.376 | 6.376
2021-09-04 02:00 | 1.5804 | 1.9571 | 1.9883 | 2.1218 | 2.0684 | 2.202 | 0.84879 | 1.2857 | 1.5308 | 1.5308 | 1.6941 | 1.6941 | 2019-11-01 16:00 | 2.3701 | 3.8842 | 6.376 | 6.376 | 6.376 | 6.376
2021-09-04 03:00 | 1.5433 | 1.9111 | 1.9415 | 2.072 | 2.0198 | 2.1502 | 0.80306 | 1.2165 | 1.4483 | 1.4483 | 1.6028 | 1.6028 | 2019-11-01 17:00 | 2.2939 | 3.7593 | 6.171 | 6.171 | 6.171 | 6.171
2021-09-04 04:00 | 1.5575 | 1.9288 | 1.9595 | 2.0912 | 2.0385 | 2.1702 | 0.78591 | 1.1905 | 1.4174 | 1.4174 | 1.5686 | 1.5686 | 2019-11-01 18:00 | 2.1415 | 3.5095 | 5.7609 | 5.7609 | 5.7609 | 5.7609
2021-09-04 05:00 | 1.5833 | 1.9606 | 1.9918 | 2.1257 | 2.0722 | 2.206 | 0.8345 | 1.2641 | 1.505 | 1.505 | 1.6656 | 1.6656 | 2019-11-01 19:00 | 1.951 | 3.1973 | 5.2484 | 5.2484 | 5.2484 | 5.2484
2021-09-04 06:00 | 1.7547 | 2.173 | 2.2076 | 2.3559 | 2.2966 | 2.4449 | 0.89828 | 1.3607 | 1.62 | 1.62 | 1.7929 | 1.7929 | 2019-11-01 20:00 | 1.9281 | 3.1598 | 5.1869 | 5.1869 | 5.1869 | 5.1869
2021-09-04 07:00 | 1.9119 | 2.3676 | 2.4053 | 2.5669 | 2.5023 | 2.6639 | 1.0574 | 1.6018 | 1.907 | 1.907 | 2.1105 | 2.1105 | 2019-11-01 21:00 | 1.8214 | 2.985 | 4.8999 | 4.8999 | 4.8999 | 4.8999
2021-09-04 08:00 | 2.1291 | 2.6366 | 2.6786 | 2.8586 | 2.7866 | 2.9665 | 1.1689 | 1.7706 | 2.108 | 2.108 | 2.3329 | 2.3329 | 2019-11-01 22:00 | 1.608 | 2.6353 | 4.3258 | 4.3258 | 4.3258 | 4.3258
2021-09-04 09:00 | 2.4235 | 3.0011 | 3.0489 | 3.2538 | 3.1718 | 3.3767 | 1.2948 | 1.9614 | 2.3351 | 2.3351 | 2.5843 | 2.5843 | 2019-11-01 23:00 | 1.4709 | 2.4105 | 3.9568 | 3.9568 | 3.9568 | 3.9568
2021-09-04 10:00 | 2.5607 | 3.171 | 3.2215 | 3.4379 | 3.3514 | 3.5678 | 1.509 | 2.2858 | 2.7213 | 2.7213 | 3.0117 | 3.0117 | 2019-11-02 | 1.3718 | 2.2481 | 3.6903 | 3.6903 | 3.6903 | 3.6903
2021-09-04 11:00 | 2.5492 | 3.1568 | 3.2071 | 3.4226 | 3.3364 | 3.5519 | 1.5747 | 2.3854 | 2.8399 | 2.8399 | 3.1429 | 3.1429 | 2019-11-02 01:00 | 1.2879 | 2.1107 | 3.4648 | 3.4648 | 3.4648 | 3.4648
2021-09-04 12:00 | 2.7036 | 3.3479 | 3.4012 | 3.6298 | 3.5384 | 3.7669 | 1.6176 | 2.4503 | 2.9172 | 2.9172 | 3.2285 | 3.2285 | 2019-11-02 02:00 | 1.2879 | 2.1107 | 3.4648 | 3.4648 | 3.4648 | 3.4648
2021-09-04 13:00 | 2.6835 | 3.3231 | 3.3761 | 3.6029 | 3.5122 | 3.739 | 1.6719 | 2.5325 | 3.0151 | 3.0151 | 3.3368 | 3.3368 | 2019-11-02 03:00 | 1.3108 | 2.1482 | 3.5263 | 3.5263 | 3.5263 | 3.5263
2021-09-04 14:00 | 2.6521 | 3.2842 | 3.3365 | 3.5607 | 3.471 | 3.6952 | 1.6061 | 2.433 | 2.8966 | 2.8966 | 3.2057 | 3.2057 | 2019-11-02 04:00 | 1.3718 | 2.2481 | 3.6903 | 3.6903 | 3.6903 | 3.6903
2021-09-04 15:00 | 2.6007 | 3.2205 | 3.2718 | 3.4917 | 3.4037 | 3.6236 | 1.6204 | 2.4546 | 2.9224 | 2.9224 | 3.2342 | 3.2342 | 2019-11-02 05:00 | 1.2727 | 2.0857 | 3.4238 | 3.4238 | 3.4238 | 3.4238
2021-09-04 16:00 | 2.6321 | 3.2594 | 3.3114 | 3.5339 | 3.4449 | 3.6674 | 1.6945 | 2.5669 | 3.056 | 3.056 | 3.3821 | 3.3821 | 2019-11-02 06:00 | 1.3337 | 2.1856 | 3.5878 | 3.5878 | 3.5878 | 3.5878
2021-09-04 17:00 | 2.9436 | 3.6452 | 3.7033 | 3.9521 | 3.8526 | 4.1014 | 1.8119 | 2.7447 | 3.2677 | 3.2677 | 3.6163 | 3.6163 | 2019-11-02 07:00 | 1.5852 | 2.5978 | 4.2643 | 4.2643 | 4.2643 | 4.2643
2021-09-04 18:00 | 2.9808 | 3.6912 | 3.75 | 4.002 | 3.9012 | 4.1532 | 1.8833 | 2.8529 | 3.3965 | 3.3965 | 3.7589 | 3.7589 | 2019-11-02 08:00 | 1.7452 | 2.8601 | 4.6949 | 4.6949 | 4.6949 | 4.6949
2021-09-04 19:00 | 2.815 | 3.4859 | 3.5415 | 3.7794 | 3.6842 | 3.9222 | 1.7862 | 2.7057 | 3.2213 | 3.2213 | 3.565 | 3.565 | 2019-11-02 09:00 | 1.89 | 3.0974 | 5.0844 | 5.0844 | 5.0844 | 5.0844
2021-09-04 20:00 | 2.6039 | 3.2245 | 3.2758 | 3.4959 | 3.4079 | 3.628 | 1.6719 | 2.5325 | 3.0151 | 3.0151 | 3.3368 | 3.3368 | 2019-11-02 10:00 | 2.0272 | 3.3222 | 5.4534 | 5.4534 | 5.4534 | 5.4534
2021-09-04 21:00 | 2.3578 | 2.9197 | 2.9662 | 3.1655 | 3.0858 | 3.2851 | 1.5818 | 2.3961 | 2.8527 | 2.8527 | 3.1571 | 3.1571 | 2019-11-02 11:00 | 2.0729 | 3.3971 | 5.5764 | 5.5764 | 5.5764 | 5.5764
2021-09-04 22:00 | 2.2434 | 2.7781 | 2.8224 | 3.012 | 2.9362 | 3.1258 | 1.4404 | 2.1819 | 2.5976 | 2.5976 | 2.8748 | 2.8748 | 2019-11-02 12:00 | 2.0958 | 3.4346 | 5.6379 | 5.6379 | 5.6379 | 5.6379
2021-09-04 23:00 | 2.1147 | 2.6187 | 2.6604 | 2.8391 | 2.7676 | 2.9464 | 1.2689 | 1.9221 | 2.2884 | 2.2884 | 2.5326 | 2.5326 | 2019-11-02 13:00 | 2.1796 | 3.572 | 5.8634 | 5.8634 | 5.8634 | 5.8634
2021-09-05 | 1.8033 | 2.2331 | 2.2687 | 2.4211 | 2.3602 | 2.5126 | 1.098 | 1.6633 | 1.9803 | 1.9803 | 2.1916 | 2.1916 | 2019-11-02 14:00 | 2.0958 | 3.4346 | 5.6379 | 5.6379 | 5.6379 | 5.6379
2021-09-05 01:00 | 1.6924 | 2.0957 | 2.1291 | 2.2722 | 2.2149 | 2.358 | 0.96596 | 1.4632 | 1.7421 | 1.7421 | 1.928 | 1.928 | 2019-11-02 15:00 | 2.1339 | 3.497 | 5.7404 | 5.7404 | 5.7404 | 5.7404
2021-09-05 02:00 | 1.6776 | 2.0774 | 2.1105 | 2.2523 | 2.1956 | 2.3374 | 0.85829 | 1.3001 | 1.5479 | 1.5479 | 1.7131 | 1.7131 | 2019-11-02 16:00 | 2.1034 | 3.4471 | 5.6584 | 5.6584 | 5.6584 | 5.6584
2021-09-05 03:00 | 1.6557 | 2.0503 | 2.083 | 2.2229 | 2.1669 | 2.3069 | 0.84021 | 1.2728 | 1.5153 | 1.5153 | 1.677 | 1.677 | 2019-11-02 17:00 | 1.9738 | 3.2348 | 5.3099 | 5.3099 | 5.3099 | 5.3099
2021-09-05 04:00 | 1.7233 | 2.134 | 2.168 | 2.3137 | 2.2554 | 2.4011 | 0.89166 | 1.3507 | 1.6081 | 1.6081 | 1.7796 | 1.7796 | 2019-11-02 18:00 | 1.9053 | 3.1224 | 5.1254 | 5.1254 | 5.1254 | 5.1254
2021-09-05 05:00 | 1.7633 | 2.1836 | 2.2184 | 2.3674 | 2.3078 | 2.4569 | 0.92811 | 1.4059 | 1.6738 | 1.6738 | 1.8524 | 1.8524 | 2019-11-02 19:00 | 1.6995 | 2.7851 | 4.5718 | 4.5718 | 4.5718 | 4.5718
2021-09-05 06:00 | 1.9291 | 2.3888 | 2.4269 | 2.59 | 2.5247 | 2.6878 | 0.9431 | 1.4286 | 1.7008 | 1.7008 | 1.8823 | 1.8823 | 2019-11-02 20:00 | 1.7071 | 2.7976 | 4.5923 | 4.5923 | 4.5923 | 4.5923
2021-09-05 07:00 | 2.1777 | 2.6967 | 2.7397 | 2.9238 | 2.8501 | 3.0342 | 1.1685 | 1.77 | 2.1073 | 2.1073 | 2.3322 | 2.3322 | 2019-11-02 21:00 | 1.6385 | 2.6852 | 4.4078 | 4.4078 | 4.4078 | 4.4078
2021-09-05 08:00 | 2.2577 | 2.7958 | 2.8404 | 3.0312 | 2.9549 | 3.1457 | 1.2575 | 1.9048 | 2.2678 | 2.2678 | 2.5098 | 2.5098 | 2019-11-02 22:00 | 1.5318 | 2.5104 | 4.1208 | 4.1208 | 4.1208 | 4.1208
2021-09-05 09:00 | 2.2892 | 2.8348 | 2.8799 | 3.0734 | 2.996 | 3.1895 | 1.3175 | 1.9957 | 2.376 | 2.376 | 2.6295 | 2.6295 | 2019-11-02 23:00 | 1.4556 | 2.3855 | 3.9158 | 3.9158 | 3.9158 | 3.9158
2021-09-05 10:00 | 2.3949 | 2.9657 | 3.0129 | 3.2154 | 3.1344 | 3.3369 | 1.5175 | 2.2988 | 2.7368 | 2.7368 | 3.0288 | 3.0288 | 2019-11-03 | 1.3642 | 2.2356 | 3.6698 | 3.6698 | 3.6698 | 3.6698
2021-09-05 11:00 | 2.7921 | 3.4576 | 3.5127 | 3.7487 | 3.6543 | 3.8903 | 1.6804 | 2.5455 | 3.0306 | 3.0306 | 3.354 | 3.354 | 2019-11-03 01:00 | 1.3032 | 2.1357 | 3.5058 | 3.5058 | 3.5058 | 3.5058
2021-09-05 12:00 | 2.9007 | 3.5921 | 3.6493 | 3.8945 | 3.7965 | 4.0417 | 1.8348 | 2.7793 | 3.3089 | 3.3089 | 3.662 | 3.662 | 2019-11-03 02:00 | 1.3032 | 2.1357 | 3.5058 | 3.5058 | 3.5058 | 3.5058
2021-09-05 13:00 | 2.9007 | 3.5921 | 3.6493 | 3.8945 | 3.7965 | 4.0417 | 1.8833 | 2.8529 | 3.3965 | 3.3965 | 3.7589 | 3.7589 | 2019-11-03 03:00 | 1.2727 | 2.0857 | 3.4238 | 3.4238 | 3.4238 | 3.4238
2021-09-05 14:00 | 2.835 | 3.5107 | 3.5666 | 3.8063 | 3.7104 | 3.9501 | 1.8605 | 2.8183 | 3.3553 | 3.3553 | 3.7133 | 3.7133 | 2019-11-03 04:00 | 1.3337 | 2.1856 | 3.5878 | 3.5878 | 3.5878 | 3.5878
2021-09-05 15:00 | 2.5435 | 3.1497 | 3.1999 | 3.4149 | 3.3289 | 3.5439 | 1.7464 | 2.6455 | 3.1496 | 3.1496 | 3.4856 | 3.4856 | 2019-11-03 05:00 | 1.3794 | 2.2606 | 3.7108 | 3.7108 | 3.7108 | 3.7108
2021-09-05 16:00 | 2.5006 | 3.0966 | 3.146 | 3.3574 | 3.2728 | 3.4842 | 1.6976 | 2.5715 | 3.0615 | 3.0615 | 3.3882 | 3.3882 | 2019-11-03 06:00 | 1.3565 | 2.2231 | 3.6493 | 3.6493 | 3.6493 | 3.6493
2021-09-05 17:00 | 3.0866 | 3.8222 | 3.8831 | 4.144 | 4.0396 | 4.3006 | 1.7776 | 2.6927 | 3.2058 | 3.2058 | 3.5479 | 3.5479 | 2019-11-03 07:00 | 1.7147 | 2.8101 | 4.6128 | 4.6128 | 4.6128 | 4.6128
2021-09-05 18:00 | 3.358 | 4.1584 | 4.2246 | 4.5085 | 4.3949 | 4.6788 | 2.0091 | 3.0434 | 3.6233 | 3.6233 | 4.0099 | 4.0099 | 2019-11-03 08:00 | 1.829 | 2.9975 | 4.9204 | 4.9204 | 4.9204 | 4.9204
2021-09-05 19:00 | 3.1923 | 3.9531 | 4.0161 | 4.2859 | 4.178 | 4.4478 | 2.0491 | 3.104 | 3.6955 | 3.6955 | 4.0898 | 4.0898 | 2019-11-03 09:00 | 2.0119 | 3.2972 | 5.4124 | 5.4124 | 5.4124 | 5.4124
2021-09-05 20:00 | 3.0722 | 3.8045 | 3.8651 | 4.1248 | 4.0209 | 4.2806 | 1.9205 | 2.9092 | 3.4635 | 3.4635 | 3.8331 | 3.8331 | 2019-11-03 10:00 | 2.111 | 3.4596 | 5.6789 | 5.6789 | 5.6789 | 5.6789
2021-09-05 21:00 | 2.8436 | 3.5213 | 3.5774 | 3.8178 | 3.7216 | 3.962 | 1.9148 | 2.9005 | 3.4532 | 3.4532 | 3.8217 | 3.8217 | 2019-11-03 11:00 | 2.111 | 3.4596 | 5.6789 | 5.6789 | 5.6789 | 5.6789
2021-09-05 22:00 | 2.4157 | 2.9915 | 3.0392 | 3.2434 | 3.1617 | 3.3659 | 1.5833 | 2.3983 | 2.8554 | 2.8554 | 3.16 | 3.16 | 2019-11-03 12:00 | 2.1186 | 3.4721 | 5.6994 | 5.6994 | 5.6994 | 5.6994
2021-09-05 23:00 | 2.247 | 2.7825 | 2.8268 | 3.0168 | 2.9408 | 3.1308 | 1.4358 | 2.175 | 2.5894 | 2.5894 | 2.8657 | 2.8657 | 2019-11-03 13:00 | 1.9738 | 3.2348 | 5.3099 | 5.3099 | 5.3099 | 5.3099
2021-09-06 | 2.0291 | 2.5127 | 2.5527 | 2.7243 | 2.6556 | 2.8272 | 1.2353 | 1.8713 | 2.2279 | 2.2279 | 2.4656 | 2.4656 | 2019-11-03 14:00 | 2.0348 | 3.3347 | 5.4739 | 5.4739 | 5.4739 | 5.4739
2021-09-06 01:00 | 1.8519 | 2.2933 | 2.3298 | 2.4864 | 2.4237 | 2.5803 | 1.0519 | 1.5935 | 1.8971 | 1.8971 | 2.0996 | 2.0996 | 2019-11-03 15:00 | 2.0348 | 3.3347 | 5.4739 | 5.4739 | 5.4739 | 5.4739
2021-09-06 02:00 | 1.8005 | 2.2296 | 2.2651 | 2.4173 | 2.3564 | 2.5086 | 0.99454 | 1.5065 | 1.7936 | 1.7936 | 1.985 | 1.985 | 2019-11-03 16:00 | 1.9738 | 3.2348 | 5.3099 | 5.3099 | 5.3099 | 5.3099
2021-09-06 03:00 | 1.7919 | 2.219 | 2.2543 | 2.4058 | 2.3452 | 2.4967 | 0.97739 | 1.4806 | 1.7627 | 1.7627 | 1.9508 | 1.9508 | 2019-11-03 17:00 | 1.9738 | 3.2348 | 5.3099 | 5.3099 | 5.3099 | 5.3099
2021-09-06 04:00 | 1.8175 | 2.2507 | 2.2865 | 2.4401 | 2.3787 | 2.5323 | 0.98597 | 1.4935 | 1.7781 | 1.7781 | 1.9679 | 1.9679 | 2019-11-03 18:00 | 1.7147 | 2.8101 | 4.6128 | 4.6128 | 4.6128 | 4.6128
2021-09-06 05:00 | 2.129 | 2.6364 | 2.6784 | 2.8584 | 2.7864 | 2.9664 | 1.0803 | 1.6364 | 1.9482 | 1.9482 | 2.1561 | 2.1561 | 2019-11-03 19:00 | 1.7071 | 2.7976 | 4.5923 | 4.5923 | 4.5923 | 4.5923
2021-09-06 06:00 | 2.5092 | 3.1073 | 3.1568 | 3.3689 | 3.284 | 3.4961 | 1.1517 | 1.7446 | 2.0771 | 2.0771 | 2.2987 | 2.2987 | 2019-11-03 20:00 | 1.7757 | 2.91 | 4.7769 | 4.7769 | 4.7769 | 4.7769
2021-09-06 07:00 | 2.9122 | 3.6063 | 3.6637 | 3.9099 | 3.8114 | 4.0576 | 1.489 | 2.2555 | 2.6853 | 2.6853 | 2.9718 | 2.9718 | 2019-11-03 21:00 | 1.669 | 2.7352 | 4.4898 | 4.4898 | 4.4898 | 4.4898
2021-09-06 08:00 | 2.8836 | 3.5709 | 3.6278 | 3.8715 | 3.774 | 4.0178 | 1.589 | 2.407 | 2.8657 | 2.8657 | 3.1714 | 3.1714 | 2019-11-03 22:00 | 1.5166 | 2.4854 | 4.0798 | 4.0798 | 4.0798 | 4.0798
2021-09-06 09:00 | 2.6264 | 3.2524 | 3.3042 | 3.5262 | 3.4374 | 3.6594 | 1.4947 | 2.2641 | 2.6956 | 2.6956 | 2.9832 | 2.9832 | 2019-11-03 23:00 | 1.4556 | 2.3855 | 3.9158 | 3.9158 | 3.9158 | 3.9158
2021-09-06 10:00 | 2.392 | 2.9622 | 3.0093 | 3.2116 | 3.1307 | 3.3329 | 1.4032 | 2.1256 | 2.5306 | 2.5306 | 2.8007 | 2.8007 | 2019-11-04 | 1.387 | 2.2731 | 3.7313 | 3.7313 | 3.7313 | 3.7313
2021-09-06 11:00 | 2.1977 | 2.7215 | 2.7649 | 2.9506 | 2.8763 | 3.0621 | 1.4347 | 2.1732 | 2.5873 | 2.5873 | 2.8634 | 2.8634 | 2019-11-04 01:00 | 1.3261 | 2.1732 | 3.5673 | 3.5673 | 3.5673 | 3.5673
2021-09-06 12:00 | 2.032 | 2.5162 | 2.5563 | 2.7281 | 2.6594 | 2.8312 | 1.5004 | 2.2728 | 2.7059 | 2.7059 | 2.9946 | 2.9946 | 2019-11-04 02:00 | 1.3184 | 2.1607 | 3.5468 | 3.5468 | 3.5468 | 3.5468
2021-09-06 13:00 | 1.9519 | 2.4172 | 2.4557 | 2.6207 | 2.5547 | 2.7197 | 1.3804 | 2.091 | 2.4894 | 2.4894 | 2.755 | 2.755 | 2019-11-04 03:00 | 1.3032 | 2.1357 | 3.5058 | 3.5058 | 3.5058 | 3.5058
2021-09-06 14:00 | 1.9348 | 2.3959 | 2.4341 | 2.5976 | 2.5322 | 2.6958 | 1.2975 | 1.9654 | 2.3399 | 2.3399 | 2.5896 | 2.5896 | 2019-11-04 04:00 | 1.3718 | 2.2481 | 3.6903 | 3.6903 | 3.6903 | 3.6903
2021-09-06 15:00 | 1.9919 | 2.4667 | 2.506 | 2.6744 | 2.607 | 2.7754 | 1.3603 | 2.0607 | 2.4533 | 2.4533 | 2.7151 | 2.7151 | 2019-11-04 05:00 | 1.3718 | 2.2481 | 3.6903 | 3.6903 | 3.6903 | 3.6903
2021-09-06 16:00 | 2.2977 | 2.8454 | 2.8907 | 3.0849 | 3.0072 | 3.2015 | 1.4032 | 2.1256 | 2.5306 | 2.5306 | 2.8007 | 2.8007 | 2019-11-04 06:00 | 1.5775 | 2.5853 | 4.2438 | 4.2438 | 4.2438 | 4.2438
2021-09-06 17:00 | 2.8493 | 3.5284 | 3.5846 | 3.8255 | 3.7291 | 3.97 | 1.6931 | 2.5647 | 3.0535 | 3.0535 | 3.3793 | 3.3793 | 2019-11-04 07:00 | 1.9205 | 3.1473 | 5.1664 | 5.1664 | 5.1664 | 5.1664
2021-09-06 18:00 | 3.2894 | 4.0734 | 4.1383 | 4.4164 | 4.3051 | 4.5832 | 2.0205 | 3.0607 | 3.6439 | 3.6439 | 4.0327 | 4.0327 | 2019-11-04 08:00 | 2.111 | 3.4596 | 5.6789 | 5.6789 | 5.6789 | 5.6789
2021-09-06 19:00 | 3.2294 | 3.9991 | 4.0628 | 4.3358 | 4.2266 | 4.4996 | 2.1348 | 3.2339 | 3.8501 | 3.8501 | 4.2609 | 4.2609 | 2019-11-04 09:00 | 2.172 | 3.5595 | 5.8429 | 5.8429 | 5.8429 | 5.8429
2021-09-06 20:00 | 3.0008 | 3.716 | 3.7752 | 4.0288 | 3.9274 | 4.181 | 1.952 | 2.957 | 3.5204 | 3.5204 | 3.896 | 3.896 | 2019-11-04 10:00 | 2.2558 | 3.6969 | 6.0685 | 6.0685 | 6.0685 | 6.0685
2021-09-06 21:00 | 2.855 | 3.5355 | 3.5918 | 3.8331 | 3.7366 | 3.978 | 1.8663 | 2.8271 | 3.3659 | 3.3659 | 3.725 | 3.725 | 2019-11-04 11:00 | 2.1949 | 3.597 | 5.9044 | 5.9044 | 5.9044 | 5.9044
2021-09-06 22:00 | 2.6092 | 3.2311 | 3.2826 | 3.5032 | 3.4149 | 3.6355 | 1.6347 | 2.4763 | 2.9482 | 2.9482 | 3.2627 | 3.2627 | 2019-11-04 12:00 | 2.2177 | 3.6344 | 5.966 | 5.966 | 5.966 | 5.966
2021-09-06 23:00 | 2.3464 | 2.9057 | 2.9519 | 3.1503 | 3.0709 | 3.2693 | 1.4261 | 2.1602 | 2.5719 | 2.5719 | 2.8463 | 2.8463 | 2019-11-04 13:00 | 2.2253 | 3.6469 | 5.9865 | 5.9865 | 5.9865 | 5.9865
2021-09-07 | 1.9793 | 2.451 | 2.4901 | 2.6574 | 2.5905 | 2.7578 | 1.2071 | 1.8285 | 2.1769 | 2.1769 | 2.4092 | 2.4092 | 2019-11-04 14:00 | 2.2177 | 3.6344 | 5.966 | 5.966 | 5.966 | 5.966
2021-09-07 01:00 | 1.9291 | 2.3888 | 2.4269 | 2.59 | 2.5247 | 2.6878 | 1.0831 | 1.6407 | 1.9534 | 1.9534 | 2.1618 | 2.1618 | 2019-11-04 15:00 | 2.1949 | 3.597 | 5.9044 | 5.9044 | 5.9044 | 5.9044
2021-09-07 02:00 | 1.8552 | 2.2974 | 2.3339 | 2.4908 | 2.428 | 2.5849 | 1.0088 | 1.5282 | 1.8194 | 1.8194 | 2.0135 | 2.0135 | 2019-11-04 16:00 | 2.1415 | 3.5095 | 5.7609 | 5.7609 | 5.7609 | 5.7609
2021-09-07 03:00 | 1.8776 | 2.3251 | 2.3622 | 2.5209 | 2.4574 | 2.6161 | 0.98025 | 1.4849 | 1.7678 | 1.7678 | 1.9565 | 1.9565 | 2019-11-04 17:00 | 2.1263 | 3.4845 | 5.7199 | 5.7199 | 5.7199 | 5.7199
2021-09-07 04:00 | 1.952 | 2.4172 | 2.4557 | 2.6207 | 2.5547 | 2.7198 | 1.0403 | 1.5758 | 1.8761 | 1.8761 | 2.0763 | 2.0763 | 2019-11-04 18:00 | 1.8367 | 3.0099 | 4.9409 | 4.9409 | 4.9409 | 4.9409
2021-09-07 05:00 | 2.1256 | 2.6323 | 2.6742 | 2.8539 | 2.782 | 2.9617 | 1.0574 | 1.6018 | 1.907 | 1.907 | 2.1105 | 2.1105 | 2019-11-04 19:00 | 1.829 | 2.9975 | 4.9204 | 4.9204 | 4.9204 | 4.9204
2021-09-07 06:00 | 2.7579 | 3.4152 | 3.4696 | 3.7027 | 3.6094 | 3.8426 | 1.2317 | 1.8659 | 2.2214 | 2.2214 | 2.4584 | 2.4584 | 2019-11-04 20:00 | 1.73 | 2.8351 | 4.6538 | 4.6538 | 4.6538 | 4.6538
2021-09-07 07:00 | 3.0751 | 3.808 | 3.8686 | 4.1286 | 4.0246 | 4.2846 | 1.5118 | 2.2901 | 2.7265 | 2.7265 | 3.0174 | 3.0174 | 2019-11-04 21:00 | 1.6233 | 2.6602 | 4.3668 | 4.3668 | 4.3668 | 4.3668
2021-09-07 08:00 | 2.955 | 3.6594 | 3.7176 | 3.9674 | 3.8675 | 4.1173 | 1.5118 | 2.2901 | 2.7265 | 2.7265 | 3.0174 | 3.0174 | 2019-11-04 22:00 | 1.4709 | 2.4105 | 3.9568 | 3.9568 | 3.9568 | 3.9568
2021-09-07 09:00 | 2.8122 | 3.4824 | 3.5379 | 3.7756 | 3.6805 | 3.9182 | 1.5204 | 2.3031 | 2.742 | 2.742 | 3.0345 | 3.0345 | 2019-11-04 23:00 | 1.3565 | 2.2231 | 3.6493 | 3.6493 | 3.6493 | 3.6493
2021-09-07 10:00 | 2.4406 | 3.0223 | 3.0705 | 3.2768 | 3.1943 | 3.4006 | 1.4575 | 2.2079 | 2.6286 | 2.6286 | 2.909 | 2.909 | 2019-11-05 | 1.2727 | 2.0857 | 3.4238 | 3.4238 | 3.4238 | 3.4238
2021-09-07 11:00 | 2.3606 | 2.9232 | 2.9698 | 3.1693 | 3.0895 | 3.2891 | 1.4032 | 2.1256 | 2.5306 | 2.5306 | 2.8007 | 2.8007 | 2019-11-05 01:00 | 1.1889 | 1.9483 | 3.1982 | 3.1982 | 3.1982 | 3.1982
2021-09-07 12:00 | 2.1091 | 2.6118 | 2.6534 | 2.8317 | 2.7604 | 2.9387 | 1.4146 | 2.1429 | 2.5513 | 2.5513 | 2.8235 | 2.8235 | 2019-11-05 02:00 | 1.1889 | 1.9483 | 3.1982 | 3.1982 | 3.1982 | 3.1982
2021-09-07 13:00 | 1.9628 | 2.4307 | 2.4694 | 2.6353 | 2.5689 | 2.7349 | 1.3289 | 2.013 | 2.3966 | 2.3966 | 2.6524 | 2.6524 | 2019-11-05 03:00 | 1.166 | 1.9109 | 3.1367 | 3.1367 | 3.1367 | 3.1367
2021-09-07 14:00 | 1.8862 | 2.3358 | 2.373 | 2.5324 | 2.4686 | 2.6281 | 1.2546 | 1.9005 | 2.2626 | 2.2626 | 2.5041 | 2.5041 | 2019-11-05 04:00 | 1.2422 | 2.0358 | 3.3417 | 3.3417 | 3.3417 | 3.3417
2021-09-07 15:00 | 1.8948 | 2.3464 | 2.3837 | 2.5439 | 2.4799 | 2.64 | 1.2718 | 1.9265 | 2.2936 | 2.2936 | 2.5383 | 2.5383 | 2019-11-05 05:00 | 1.3261 | 2.1732 | 3.5673 | 3.5673 | 3.5673 | 3.5673
2021-09-07 16:00 | 2.2063 | 2.7321 | 2.7756 | 2.9621 | 2.8875 | 3.0741 | 1.3775 | 2.0866 | 2.4843 | 2.4843 | 2.7493 | 2.7493 | 2019-11-05 06:00 | 1.4023 | 2.2981 | 3.7723 | 3.7723 | 3.7723 | 3.7723
2021-09-07 17:00 | 2.7714 | 3.4319 | 3.4866 | 3.7208 | 3.6271 | 3.8614 | 1.7033 | 2.5802 | 3.0718 | 3.0718 | 3.3996 | 3.3996 | 2019-11-05 07:00 | 1.8214 | 2.985 | 4.8999 | 4.8999 | 4.8999 | 4.8999
2021-09-07 18:00 | 3.2208 | 3.9885 | 4.052 | 4.3243 | 4.2154 | 4.4876 | 1.9376 | 2.9352 | 3.4945 | 3.4945 | 3.8673 | 3.8673 | 2019-11-05 08:00 | 2.0882 | 3.4221 | 5.6174 | 5.6174 | 5.6174 | 5.6174
2021-09-07 19:00 | 3.1203 | 3.864 | 3.9255 | 4.1893 | 4.0838 | 4.3475 | 1.9302 | 2.9239 | 3.4811 | 3.4811 | 3.8525 | 3.8525 | 2019-11-05 09:00 | 2.1034 | 3.4471 | 5.6584 | 5.6584 | 5.6584 | 5.6584
2021-09-07 20:00 | 2.8064 | 3.4753 | 3.5307 | 3.7679 | 3.673 | 3.9103 | 1.9291 | 2.9222 | 3.479 | 3.479 | 3.8502 | 3.8502 | 2019-11-05 10:00 | 2.0577 | 3.3721 | 5.5354 | 5.5354 | 5.5354 | 5.5354
2021-09-07 21:00 | 2.5235 | 3.125 | 3.1747 | 3.3881 | 3.3027 | 3.516 | 1.749 | 2.6494 | 3.1543 | 3.1543 | 3.4909 | 3.4909 | 2019-11-05 11:00 | 2.0501 | 3.3597 | 5.5149 | 5.5149 | 5.5149 | 5.5149
2021-09-07 22:00 | 2.3292 | 2.8843 | 2.9302 | 3.1271 | 3.0484 | 3.2453 | 1.5004 | 2.2728 | 2.7059 | 2.7059 | 2.9946 | 2.9946 | 2019-11-05 12:00 | 2.1263 | 3.4845 | 5.7199 | 5.7199 | 5.7199 | 5.7199
2021-09-07 23:00 | 2.181 | 2.7008 | 2.7438 | 2.9281 | 2.8544 | 3.0388 | 1.3661 | 2.0693 | 2.4636 | 2.4636 | 2.7265 | 2.7265 | 2019-11-05 13:00 | 2.1186 | 3.4721 | 5.6994 | 5.6994 | 5.6994 | 5.6994
2021-09-08 | 1.8695 | 2.3151 | 2.352 | 2.5101 | 2.4468 | 2.6049 | 1.166 | 1.7663 | 2.1029 | 2.1029 | 2.3272 | 2.3272 | 2019-11-05 14:00 | 2.1872 | 3.5845 | 5.8839 | 5.8839 | 5.8839 | 5.8839
2021-09-08 01:00 | 1.7376 | 2.1517 | 2.186 | 2.3328 | 2.2741 | 2.421 | 1.0177 | 1.5417 | 1.8354 | 1.8354 | 2.0313 | 2.0313 | 2019-11-05 15:00 | 2.172 | 3.5595 | 5.8429 | 5.8429 | 5.8429 | 5.8429
2021-09-08 02:00 | 1.769 | 2.1907 | 2.2255 | 2.3751 | 2.3153 | 2.4648 | 0.97453 | 1.4762 | 1.7575 | 1.7575 | 1.9451 | 1.9451 | 2019-11-05 16:00 | 2.0882 | 3.4221 | 5.6174 | 5.6174 | 5.6174 | 5.6174
2021-09-08 03:00 | 1.7547 | 2.173 | 2.2076 | 2.3559 | 2.2966 | 2.4449 | 0.97168 | 1.4719 | 1.7524 | 1.7524 | 1.9394 | 1.9394 | 2019-11-05 17:00 | 2.0424 | 3.3472 | 5.4944 | 5.4944 | 5.4944 | 5.4944
2021-09-08 04:00 | 1.8223 | 2.2567 | 2.2926 | 2.4467 | 2.385 | 2.5391 | 0.9974 | 1.5109 | 1.7988 | 1.7988 | 1.9907 | 1.9907 | 2019-11-05 18:00 | 1.8214 | 2.985 | 4.8999 | 4.8999 | 4.8999 | 4.8999
2021-09-08 05:00 | 2.0456 | 2.5331 | 2.5735 | 2.7464 | 2.6772 | 2.8501 | 1.0448 | 1.5827 | 1.8843 | 1.8843 | 2.0854 | 2.0854 | 2019-11-05 19:00 | 1.7986 | 2.9475 | 4.8384 | 4.8384 | 4.8384 | 4.8384
2021-09-08 06:00 | 2.5464 | 3.1533 | 3.2035 | 3.4188 | 3.3327 | 3.5479 | 1.2232 | 1.8529 | 2.2059 | 2.2059 | 2.4413 | 2.4413 | 2019-11-05 20:00 | 1.8367 | 3.0099 | 4.9409 | 4.9409 | 4.9409 | 4.9409
2021-09-08 07:00 | 3.0408 | 3.7655 | 3.8255 | 4.0826 | 3.9797 | 4.2368 | 1.6118 | 2.4416 | 2.9069 | 2.9069 | 3.2171 | 3.2171 | 2019-11-05 21:00 | 1.6538 | 2.7102 | 4.4488 | 4.4488 | 4.4488 | 4.4488
2021-09-08 08:00 | 3.2123 | 3.9779 | 4.0412 | 4.3128 | 4.2042 | 4.4757 | 1.7519 | 2.6538 | 3.1594 | 3.1594 | 3.4966 | 3.4966 | 2019-11-05 22:00 | 1.5928 | 2.6103 | 4.2848 | 4.2848 | 4.2848 | 4.2848
2021-09-08 09:00 | 3.3323 | 4.1265 | 4.1922 | 4.4739 | 4.3612 | 4.6429 | 1.7947 | 2.7187 | 3.2368 | 3.2368 | 3.5821 | 3.5821 | 2019-11-05 23:00 | 1.4327 | 2.348 | 3.8543 | 3.8543 | 3.8543 | 3.8543
2021-09-08 10:00 | 3.3637 | 4.1654 | 4.2318 | 4.5161 | 4.4024 | 4.6867 | 1.9148 | 2.9005 | 3.4532 | 3.4532 | 3.8217 | 3.8217 | 2019-11-06 | 1.2346 | 2.0233 | 3.3212 | 3.3212 | 3.3212 | 3.3212
2021-09-08 11:00 | 3.2237 | 3.992 | 4.0556 | 4.3281 | 4.2191 | 4.4916 | 1.7233 | 2.6105 | 3.1079 | 3.1079 | 3.4395 | 3.4395 | 2019-11-06 01:00 | 1.166 | 1.9109 | 3.1367 | 3.1367 | 3.1367 | 3.1367
2021-09-08 12:00 | 2.6864 | 3.3267 | 3.3797 | 3.6068 | 3.5159 | 3.743 | 1.6204 | 2.4546 | 2.9224 | 2.9224 | 3.2342 | 3.2342 | 2019-11-06 02:00 | 1.1965 | 1.9608 | 3.2187 | 3.2187 | 3.2187 | 3.2187
2021-09-08 13:00 | 2.3549 | 2.9162 | 2.9626 | 3.1617 | 3.082 | 3.2811 | 1.5633 | 2.368 | 2.8193 | 2.8193 | 3.1201 | 3.1201 | 2019-11-06 03:00 | 1.1965 | 1.9608 | 3.2187 | 3.2187 | 3.2187 | 3.2187
2021-09-08 14:00 | 2.1891 | 2.7109 | 2.7541 | 2.9391 | 2.8651 | 3.0502 | 1.4461 | 2.1905 | 2.608 | 2.608 | 2.8862 | 2.8862 | 2019-11-06 04:00 | 1.1736 | 1.9234 | 3.1572 | 3.1572 | 3.1572 | 3.1572
2021-09-08 15:00 | 2.1491 | 2.6613 | 2.7037 | 2.8854 | 2.8127 | 2.9944 | 1.4032 | 2.1256 | 2.5306 | 2.5306 | 2.8007 | 2.8007 | 2019-11-06 05:00 | 1.2498 | 2.0483 | 3.3622 | 3.3622 | 3.3622 | 3.3622
2021-09-08 16:00 | 2.343 | 2.9015 | 2.9477 | 3.1458 | 3.0665 | 3.2646 | 1.4832 | 2.2468 | 2.675 | 2.675 | 2.9604 | 2.9604 | 2019-11-06 06:00 | 1.4023 | 2.2981 | 3.7723 | 3.7723 | 3.7723 | 3.7723
2021-09-08 17:00 | 2.9005 | 3.5918 | 3.649 | 3.8942 | 3.7961 | 4.0413 | 1.7347 | 2.6278 | 3.1285 | 3.1285 | 3.4623 | 3.4623 | 2019-11-06 07:00 | 1.8976 | 3.1099 | 5.1049 | 5.1049 | 5.1049 | 5.1049
2021-09-08 18:00 | 3.2265 | 3.9956 | 4.0592 | 4.332 | 4.2229 | 4.4956 | 2.0863 | 3.1603 | 3.7625 | 3.7625 | 4.1639 | 4.1639 | 2019-11-06 08:00 | 2.0958 | 3.4346 | 5.6379 | 5.6379 | 5.6379 | 5.6379
2021-09-08 19:00 | 3.1756 | 3.9325 | 3.9952 | 4.2636 | 4.1562 | 4.4247 | 2.0748 | 3.143 | 3.7419 | 3.7419 | 4.1411 | 4.1411 | 2019-11-06 09:00 | 2.111 | 3.4596 | 5.6789 | 5.6789 | 5.6789 | 5.6789
2021-09-08 20:00 | 2.9036 | 3.5957 | 3.6529 | 3.8984 | 3.8002 | 4.0456 | 1.8722 | 2.836 | 3.3764 | 3.3764 | 3.7367 | 3.7367 | 2019-11-06 10:00 | 2.172 | 3.5595 | 5.8429 | 5.8429 | 5.8429 | 5.8429
2021-09-08 21:00 | 2.715 | 3.3621 | 3.4156 | 3.6451 | 3.5533 | 3.7828 | 1.7662 | 2.6754 | 3.1852 | 3.1852 | 3.5251 | 3.5251 | 2019-11-06 11:00 | 2.172 | 3.5595 | 5.8429 | 5.8429 | 5.8429 | 5.8429
2021-09-08 22:00 | 2.372 | 2.9374 | 2.9842 | 3.1847 | 3.1045 | 3.305 | 1.4861 | 2.2511 | 2.6801 | 2.6801 | 2.9661 | 2.9661 | 2019-11-06 12:00 | 2.1491 | 3.522 | 5.7814 | 5.7814 | 5.7814 | 5.7814
2021-09-08 23:00 | 2.2063 | 2.7321 | 2.7756 | 2.9621 | 2.8875 | 3.0741 | 1.342 | 2.0329 | 2.4203 | 2.4203 | 2.6785 | 2.6785 | 2019-11-06 13:00 | 2.1796 | 3.572 | 5.8634 | 5.8634 | 5.8634 | 5.8634
2021-09-09 | 1.9519 | 2.4172 | 2.4557 | 2.6207 | 2.5547 | 2.7197 | 1.2146 | 1.8399 | 2.1905 | 2.1905 | 2.4242 | 2.4242 | 2019-11-06 14:00 | 2.1796 | 3.572 | 5.8634 | 5.8634 | 5.8634 | 5.8634
2021-09-09 01:00 | 1.8433 | 2.2827 | 2.319 | 2.4749 | 2.4125 | 2.5683 | 1.0917 | 1.6537 | 1.9688 | 1.9688 | 2.1789 | 2.1789 | 2019-11-06 15:00 | 2.111 | 3.4596 | 5.6789 | 5.6789 | 5.6789 | 5.6789
2021-09-09 02:00 | 1.7805 | 2.2048 | 2.2399 | 2.3904 | 2.3302 | 2.4807 | 1.0145 | 1.5368 | 1.8297 | 1.8297 | 2.0249 | 2.0249 | 2019-11-06 16:00 | 2.1872 | 3.5845 | 5.8839 | 5.8839 | 5.8839 | 5.8839
2021-09-09 03:00 | 1.8119 | 2.2437 | 2.2795 | 2.4326 | 2.3714 | 2.5245 | 1.0117 | 1.5325 | 1.8245 | 1.8245 | 2.0192 | 2.0192 | 2019-11-06 17:00 | 2.0348 | 3.3347 | 5.4739 | 5.4739 | 5.4739 | 5.4739
2021-09-09 04:00 | 1.8725 | 2.3188 | 2.3557 | 2.514 | 2.4507 | 2.609 | 1.026 | 1.5542 | 1.8503 | 1.8503 | 2.0477 | 2.0477 | 2019-11-06 18:00 | 1.9662 | 3.2223 | 5.2894 | 5.2894 | 5.2894 | 5.2894
2021-09-09 05:00 | 2.0917 | 2.5902 | 2.6315 | 2.8083 | 2.7376 | 2.9144 | 1.0831 | 1.6407 | 1.9534 | 1.9534 | 2.1618 | 2.1618 | 2019-11-06 19:00 | 1.8671 | 3.0599 | 5.0229 | 5.0229 | 5.0229 | 5.0229
2021-09-09 06:00 | 2.5006 | 3.0966 | 3.146 | 3.3574 | 3.2728 | 3.4842 | 1.2003 | 1.8182 | 2.1647 | 2.1647 | 2.3957 | 2.3957 | 2019-11-06 20:00 | 1.829 | 2.9975 | 4.9204 | 4.9204 | 4.9204 | 4.9204
2021-09-09 07:00 | 2.9236 | 3.6204 | 3.6781 | 3.9252 | 3.8264 | 4.0735 | 1.4975 | 2.2685 | 2.7007 | 2.7007 | 2.9889 | 2.9889 | 2019-11-06 21:00 | 1.73 | 2.8351 | 4.6538 | 4.6538 | 4.6538 | 4.6538
2021-09-09 08:00 | 2.8807 | 3.5673 | 3.6242 | 3.8677 | 3.7703 | 4.0138 | 1.589 | 2.407 | 2.8657 | 2.8657 | 3.1714 | 3.1714 | 2019-11-06 22:00 | 1.5928 | 2.6103 | 4.2848 | 4.2848 | 4.2848 | 4.2848
2021-09-09 09:00 | 2.635 | 3.263 | 3.315 | 3.5377 | 3.4486 | 3.6713 | 1.4518 | 2.1992 | 2.6183 | 2.6183 | 2.8976 | 2.8976 | 2019-11-06 23:00 | 1.4632 | 2.398 | 3.9363 | 3.9363 | 3.9363 | 3.9363
2021-09-09 10:00 | 2.4463 | 3.0294 | 3.0777 | 3.2845 | 3.2017 | 3.4085 | 1.5204 | 2.3031 | 2.742 | 2.742 | 3.0345 | 3.0345 | 2019-11-07 | 1.2956 | 2.1232 | 3.4853 | 3.4853 | 3.4853 | 3.4853
2021-09-09 11:00 | 2.4292 | 3.0082 | 3.0561 | 3.2614 | 3.1793 | 3.3846 | 1.5747 | 2.3854 | 2.8399 | 2.8399 | 3.1429 | 3.1429 | 2019-11-07 01:00 | 1.227 | 2.0108 | 3.3007 | 3.3007 | 3.3007 | 3.3007
2021-09-09 12:00 | 2.2749 | 2.8171 | 2.8619 | 3.0542 | 2.9773 | 3.1696 | 1.4489 | 2.1949 | 2.6131 | 2.6131 | 2.8919 | 2.8919 | 2019-11-07 02:00 | 1.2194 | 1.9983 | 3.2802 | 3.2802 | 3.2802 | 3.2802
2021-09-09 13:00 | 2.112 | 2.6153 | 2.657 | 2.8355 | 2.7641 | 2.9426 | 1.4575 | 2.2079 | 2.6286 | 2.6286 | 2.909 | 2.909 | 2019-11-07 03:00 | 1.1965 | 1.9608 | 3.2187 | 3.2187 | 3.2187 | 3.2187
2021-09-09 14:00 | 2.1034 | 2.6047 | 2.6462 | 2.824 | 2.7529 | 2.9307 | 1.3804 | 2.091 | 2.4894 | 2.4894 | 2.755 | 2.755 | 2019-11-07 04:00 | 1.2879 | 2.1107 | 3.4648 | 3.4648 | 3.4648 | 3.4648
2021-09-09 15:00 | 1.7576 | 2.1765 | 2.2112 | 2.3597 | 2.3003 | 2.4489 | 1.3518 | 2.0477 | 2.4379 | 2.4379 | 2.698 | 2.698 | 2019-11-07 05:00 | 1.3337 | 2.1856 | 3.5878 | 3.5878 | 3.5878 | 3.5878
2021-09-09 16:00 | 1.9448 | 2.4083 | 2.4466 | 2.611 | 2.5453 | 2.7097 | 1.4004 | 2.1213 | 2.5255 | 2.5255 | 2.795 | 2.795 | 2019-11-07 06:00 | 1.5471 | 2.5353 | 4.1618 | 4.1618 | 4.1618 | 4.1618
2021-09-09 17:00 | 2.695 | 3.3373 | 3.3905 | 3.6183 | 3.5271 | 3.755 | 1.5633 | 2.368 | 2.8193 | 2.8193 | 3.1201 | 3.1201 | 2019-11-07 07:00 | 1.9586 | 3.2098 | 5.2689 | 5.2689 | 5.2689 | 5.2689
2021-09-09 18:00 | 3.0351 | 3.7584 | 3.8183 | 4.0749 | 3.9723 | 4.2288 | 1.8433 | 2.7923 | 3.3244 | 3.3244 | 3.6791 | 3.6791 | 2019-11-07 08:00 | 2.0272 | 3.3222 | 5.4534 | 5.4534 | 5.4534 | 5.4534
2021-09-09 19:00 | 2.7717 | 3.4323 | 3.487 | 3.7213 | 3.6276 | 3.8619 | 1.8719 | 2.8356 | 3.3759 | 3.3759 | 3.7361 | 3.7361 | 2019-11-07 09:00 | 2.1415 | 3.5095 | 5.7609 | 5.7609 | 5.7609 | 5.7609
2021-09-09 20:00 | 2.5978 | 3.217 | 3.2682 | 3.4878 | 3.4 | 3.6196 | 1.8319 | 2.775 | 3.3038 | 3.3038 | 3.6563 | 3.6563 | 2019-11-07 10:00 | 1.9967 | 3.2722 | 5.3714 | 5.3714 | 5.3714 | 5.3714
2021-09-09 21:00 | 2.3606 | 2.9232 | 2.9698 | 3.1693 | 3.0895 | 3.2891 | 1.6421 | 2.4875 | 2.9615 | 2.9615 | 3.2775 | 3.2775 | 2019-11-07 11:00 | 1.9662 | 3.2223 | 5.2894 | 5.2894 | 5.2894 | 5.2894
2021-09-09 22:00 | 2.2034 | 2.7286 | 2.7721 | 2.9583 | 2.8838 | 3.0701 | 1.4832 | 2.2468 | 2.675 | 2.675 | 2.9604 | 2.9604 | 2019-11-07 12:00 | 2.0119 | 3.2972 | 5.4124 | 5.4124 | 5.4124 | 5.4124
2021-09-09 23:00 | 2.0437 | 2.5308 | 2.5711 | 2.7439 | 2.6748 | 2.8475 | 1.2807 | 1.94 | 2.3096 | 2.3096 | 2.5561 | 2.5561 | 2019-11-07 13:00 | 1.9891 | 3.2597 | 5.3509 | 5.3509 | 5.3509 | 5.3509
2021-09-10 | 1.7404 | 2.1553 | 2.1896 | 2.3367 | 2.2779 | 2.425 | 1.1146 | 1.6884 | 2.0101 | 2.0101 | 2.2246 | 2.2246 | 2019-11-07 14:00 | 2.1644 | 3.547 | 5.8224 | 5.8224 | 5.8224 | 5.8224
2021-09-10 01:00 | 1.6033 | 1.9854 | 2.017 | 2.1525 | 2.0983 | 2.2339 | 0.98025 | 1.4849 | 1.7678 | 1.7678 | 1.9565 | 1.9565 | 2019-11-07 15:00 | 2.0043 | 3.2847 | 5.3919 | 5.3919 | 5.3919 | 5.3919
2021-09-10 02:00 | 1.5547 | 1.9252 | 1.9559 | 2.0873 | 2.0347 | 2.1662 | 0.9368 | 1.4191 | 1.6895 | 1.6895 | 1.8698 | 1.8698 | 2019-11-07 16:00 | 2.1034 | 3.4471 | 5.6584 | 5.6584 | 5.6584 | 5.6584
2021-09-10 03:00 | 1.5604 | 1.9323 | 1.9631 | 2.095 | 2.0422 | 2.1741 | 0.84021 | 1.2728 | 1.5153 | 1.5153 | 1.677 | 1.677 | 2019-11-07 17:00 | 2.1034 | 3.4471 | 5.6584 | 5.6584 | 5.6584 | 5.6584
2021-09-10 04:00 | 1.5861 | 1.9642 | 1.9954 | 2.1295 | 2.0759 | 2.21 | 0.86022 | 1.3031 | 1.5514 | 1.5514 | 1.7169 | 1.7169 | 2019-11-07 18:00 | 1.9053 | 3.1224 | 5.1254 | 5.1254 | 5.1254 | 5.1254
2021-09-10 05:00 | 1.769 | 2.1907 | 2.2255 | 2.3751 | 2.3153 | 2.4648 | 0.95167 | 1.4416 | 1.7163 | 1.7163 | 1.8994 | 1.8994 | 2019-11-07 19:00 | 1.8214 | 2.985 | 4.8999 | 4.8999 | 4.8999 | 4.8999
2021-09-10 06:00 | 2.2149 | 2.7427 | 2.7864 | 2.9737 | 2.8988 | 3.086 | 1.0516 | 1.5929 | 1.8964 | 1.8964 | 2.0988 | 2.0988 | 2019-11-07 20:00 | 1.7757 | 2.91 | 4.7769 | 4.7769 | 4.7769 | 4.7769
2021-09-10 07:00 | 2.4635 | 3.0506 | 3.0992 | 3.3075 | 3.2242 | 3.4324 | 1.4004 | 2.1213 | 2.5255 | 2.5255 | 2.795 | 2.795 | 2019-11-07 21:00 | 1.669 | 2.7352 | 4.4898 | 4.4898 | 4.4898 | 4.4898
2021-09-10 08:00 | 2.3406 | 2.8985 | 2.9446 | 3.1425 | 3.0633 | 3.2612 | 1.4547 | 2.2035 | 2.6234 | 2.6234 | 2.9033 | 2.9033 | 2019-11-07 22:00 | 1.5166 | 2.4854 | 4.0798 | 4.0798 | 4.0798 | 4.0798
2021-09-10 09:00 | 2.1148 | 2.6189 | 2.6606 | 2.8394 | 2.7679 | 2.9466 | 1.3718 | 2.078 | 2.4739 | 2.4739 | 2.7379 | 2.7379 | 2019-11-07 23:00 | 1.5394 | 2.5229 | 4.1413 | 4.1413 | 4.1413 | 4.1413
2021-09-10 10:00 | 1.9777 | 2.449 | 2.488 | 2.6552 | 2.5883 | 2.7555 | 1.2746 | 1.9308 | 2.2987 | 2.2987 | 2.544 | 2.544 | 2019-11-08 | 1.3413 | 2.1981 | 3.6083 | 3.6083 | 3.6083 | 3.6083
2021-09-10 11:00 | 2.0062 | 2.4844 | 2.524 | 2.6936 | 2.6257 | 2.7953 | 1.2975 | 1.9654 | 2.3399 | 2.3399 | 2.5896 | 2.5896 | 2019-11-08 01:00 | 1.227 | 2.0108 | 3.3007 | 3.3007 | 3.3007 | 3.3007
2021-09-10 12:00 | 2.0691 | 2.5623 | 2.6031 | 2.778 | 2.708 | 2.8829 | 1.4204 | 2.1516 | 2.5616 | 2.5616 | 2.8349 | 2.8349 | 2019-11-08 02:00 | 1.2041 | 1.9733 | 3.2392 | 3.2392 | 3.2392 | 3.2392
2021-09-10 13:00 | 1.975 | 2.4457 | 2.4847 | 2.6516 | 2.5848 | 2.7518 | 1.3118 | 1.9871 | 2.3657 | 2.3657 | 2.6181 | 2.6181 | 2019-11-08 03:00 | 1.2346 | 2.0233 | 3.3212 | 3.3212 | 3.3212 | 3.3212
2021-09-10 14:00 | 1.7805 | 2.2048 | 2.2399 | 2.3904 | 2.3302 | 2.4807 | 1.3289 | 2.013 | 2.3966 | 2.3966 | 2.6524 | 2.6524 | 2019-11-08 04:00 | 1.2498 | 2.0483 | 3.3622 | 3.3622 | 3.3622 | 3.3622
2021-09-10 15:00 | 1.7805 | 2.2048 | 2.2399 | 2.3904 | 2.3302 | 2.4807 | 1.2718 | 1.9265 | 2.2936 | 2.2936 | 2.5383 | 2.5383 | 2019-11-08 05:00 | 1.3032 | 2.1357 | 3.5058 | 3.5058 | 3.5058 | 3.5058
2021-09-10 16:00 | 1.8319 | 2.2685 | 2.3046 | 2.4595 | 2.3976 | 2.5524 | 1.306 | 1.9784 | 2.3554 | 2.3554 | 2.6067 | 2.6067 | 2019-11-08 06:00 | 1.5852 | 2.5978 | 4.2643 | 4.2643 | 4.2643 | 4.2643
2021-09-10 17:00 | 2.2006 | 2.7251 | 2.7685 | 2.9545 | 2.8801 | 3.0661 | 1.4442 | 2.1877 | 2.6045 | 2.6045 | 2.8824 | 2.8824 | 2019-11-08 07:00 | 1.8748 | 3.0724 | 5.0434 | 5.0434 | 5.0434 | 5.0434
2021-09-10 18:00 | 2.6521 | 3.2842 | 3.3365 | 3.5607 | 3.471 | 3.6952 | 1.6747 | 2.5369 | 3.0203 | 3.0203 | 3.3426 | 3.3426 | 2019-11-08 08:00 | 2.0577 | 3.3721 | 5.5354 | 5.5354 | 5.5354 | 5.5354
2021-09-10 19:00 | 2.4578 | 3.0436 | 3.092 | 3.2998 | 3.2167 | 3.4245 | 1.6719 | 2.5325 | 3.0151 | 3.0151 | 3.3368 | 3.3368 | 2019-11-08 09:00 | 2.0348 | 3.3347 | 5.4739 | 5.4739 | 5.4739 | 5.4739
2021-09-10 20:00 | 2.4149 | 2.9905 | 3.0381 | 3.2422 | 3.1606 | 3.3647 | 1.5449 | 2.3402 | 2.7862 | 2.7862 | 3.0835 | 3.0835 | 2019-11-08 10:00 | 2.0577 | 3.3721 | 5.5354 | 5.5354 | 5.5354 | 5.5354
2021-09-10 21:00 | 2.172 | 2.6897 | 2.7325 | 2.9161 | 2.8427 | 3.0263 | 1.4575 | 2.2079 | 2.6286 | 2.6286 | 2.909 | 2.909 | 2019-11-08 11:00 | 2.0882 | 3.4221 | 5.6174 | 5.6174 | 5.6174 | 5.6174
2021-09-10 22:00 | 2.0863 | 2.5835 | 2.6246 | 2.801 | 2.7305 | 2.9068 | 1.4089 | 2.1343 | 2.541 | 2.541 | 2.8121 | 2.8121 | 2019-11-08 12:00 | 2.0882 | 3.4221 | 5.6174 | 5.6174 | 5.6174 | 5.6174
2021-09-10 23:00 | 1.9228 | 2.3811 | 2.4191 | 2.5816 | 2.5166 | 2.6791 | 1.2718 | 1.9265 | 2.2936 | 2.2936 | 2.5383 | 2.5383 | 2019-11-08 13:00 | 2.0958 | 3.4346 | 5.6379 | 5.6379 | 5.6379 | 5.6379
2021-09-11 | 1.7147 | 2.1234 | 2.1572 | 2.3022 | 2.2442 | 2.3892 | 1.0546 | 1.5974 | 1.9018 | 1.9018 | 2.1048 | 2.1048 | 2019-11-08 14:00 | 2.0501 | 3.3597 | 5.5149 | 5.5149 | 5.5149 | 5.5149
2021-09-11 01:00 | 1.5232 | 1.8863 | 1.9163 | 2.0451 | 1.9936 | 2.1224 | 0.92428 | 1.4001 | 1.6669 | 1.6669 | 1.8448 | 1.8448 | 2019-11-08 15:00 | 2.0272 | 3.3222 | 5.4534 | 5.4534 | 5.4534 | 5.4534
2021-09-11 02:00 | 1.5375 | 1.904 | 1.9343 | 2.0643 | 2.0123 | 2.1423 | 0.86879 | 1.3161 | 1.5668 | 1.5668 | 1.734 | 1.734 | 2019-11-08 16:00 | 1.9815 | 3.2472 | 5.3304 | 5.3304 | 5.3304 | 5.3304
2021-09-11 03:00 | 1.5375 | 1.904 | 1.9343 | 2.0643 | 2.0123 | 2.1423 | 0.87165 | 1.3204 | 1.572 | 1.572 | 1.7397 | 1.7397 | 2019-11-08 17:00 | 1.7986 | 2.9475 | 4.8384 | 4.8384 | 4.8384 | 4.8384
2021-09-11 04:00 | 1.5632 | 1.9357 | 1.9666 | 2.0987 | 2.0458 | 2.178 | 0.82592 | 1.2511 | 1.4895 | 1.4895 | 1.6485 | 1.6485 | 2019-11-08 18:00 | 1.7681 | 2.8975 | 4.7564 | 4.7564 | 4.7564 | 4.7564
2021-09-11 05:00 | 1.6861 | 2.088 | 2.1213 | 2.2638 | 2.2068 | 2.3493 | 0.89451 | 1.355 | 1.6132 | 1.6132 | 1.7854 | 1.7854 | 2019-11-08 19:00 | 1.6842 | 2.7602 | 4.5308 | 4.5308 | 4.5308 | 4.5308
2021-09-11 06:00 | 1.8262 | 2.2614 | 2.2975 | 2.4518 | 2.3901 | 2.5445 | 0.94024 | 1.4243 | 1.6957 | 1.6957 | 1.8766 | 1.8766 | 2019-11-08 20:00 | 1.6461 | 2.6977 | 4.4283 | 4.4283 | 4.4283 | 4.4283
2021-09-11 07:00 | 1.9348 | 2.3959 | 2.4341 | 2.5976 | 2.5322 | 2.6958 | 1.0974 | 1.6624 | 1.9792 | 1.9792 | 2.1903 | 2.1903 | 2019-11-08 21:00 | 1.6461 | 2.6977 | 4.4283 | 4.4283 | 4.4283 | 4.4283
2021-09-11 08:00 | 1.8176 | 2.2508 | 2.2867 | 2.4403 | 2.3789 | 2.5325 | 1.1774 | 1.7836 | 2.1235 | 2.1235 | 2.3501 | 2.3501 | 2019-11-08 22:00 | 1.5547 | 2.5478 | 4.1823 | 4.1823 | 4.1823 | 4.1823
2021-09-11 09:00 | 1.7862 | 2.2119 | 2.2471 | 2.3981 | 2.3377 | 2.4887 | 1.2432 | 1.8832 | 2.242 | 2.242 | 2.4812 | 2.4812 | 2019-11-08 23:00 | 1.4327 | 2.348 | 3.8543 | 3.8543 | 3.8543 | 3.8543
2021-09-11 10:00 | 1.7805 | 2.2048 | 2.2399 | 2.3904 | 2.3302 | 2.4807 | 1.3603 | 2.0607 | 2.4533 | 2.4533 | 2.7151 | 2.7151 | 2019-11-09 | 1.3184 | 2.1607 | 3.5468 | 3.5468 | 3.5468 | 3.5468
2021-09-11 11:00 | 1.6719 | 2.0703 | 2.1033 | 2.2446 | 2.1881 | 2.3294 | 1.3489 | 2.0433 | 2.4327 | 2.4327 | 2.6923 | 2.6923 | 2019-11-09 01:00 | 1.2194 | 1.9983 | 3.2802 | 3.2802 | 3.2802 | 3.2802
2021-09-11 12:00 | 1.5747 | 1.95 | 1.9811 | 2.1142 | 2.0609 | 2.194 | 1.286 | 1.9481 | 2.3193 | 2.3193 | 2.5668 | 2.5668 | 2019-11-09 02:00 | 1.2117 | 1.9858 | 3.2597 | 3.2597 | 3.2597 | 3.2597
2021-09-11 13:00 | 1.5032 | 1.8615 | 1.8912 | 2.0183 | 1.9674 | 2.0945 | 1.2689 | 1.9221 | 2.2884 | 2.2884 | 2.5326 | 2.5326 | 2019-11-09 03:00 | 1.1431 | 1.8734 | 3.0752 | 3.0752 | 3.0752 | 3.0752
2021-09-11 14:00 | 1.5061 | 1.8651 | 1.8948 | 2.0221 | 1.9712 | 2.0985 | 1.2203 | 1.8485 | 2.2008 | 2.2008 | 2.4356 | 2.4356 | 2019-11-09 04:00 | 1.1736 | 1.9234 | 3.1572 | 3.1572 | 3.1572 | 3.1572
2021-09-11 15:00 | 1.5718 | 1.9465 | 1.9775 | 2.1103 | 2.0572 | 2.1901 | 1.1946 | 1.8096 | 2.1544 | 2.1544 | 2.3843 | 2.3843 | 2019-11-09 05:00 | 1.2422 | 2.0358 | 3.3417 | 3.3417 | 3.3417 | 3.3417
2021-09-11 16:00 | 1.6661 | 2.0633 | 2.0961 | 2.237 | 2.1806 | 2.3215 | 1.186 | 1.7966 | 2.1389 | 2.1389 | 2.3672 | 2.3672 | 2019-11-09 06:00 | 1.2879 | 2.1107 | 3.4648 | 3.4648 | 3.4648 | 3.4648
2021-09-11 17:00 | 2.0634 | 2.5552 | 2.5959 | 2.7703 | 2.7005 | 2.875 | 1.3975 | 2.1169 | 2.5203 | 2.5203 | 2.7893 | 2.7893 | 2019-11-09 07:00 | 1.5928 | 2.6103 | 4.2848 | 4.2848 | 4.2848 | 4.2848
2021-09-11 18:00 | 2.4121 | 2.9869 | 3.0345 | 3.2384 | 3.1569 | 3.3608 | 1.6061 | 2.433 | 2.8966 | 2.8966 | 3.2057 | 3.2057 | 2019-11-09 08:00 | 1.7376 | 2.8476 | 4.6744 | 4.6744 | 4.6744 | 4.6744
2021-09-11 19:00 | 2.3349 | 2.8914 | 2.9374 | 3.1348 | 3.0559 | 3.2532 | 1.5861 | 2.4027 | 2.8605 | 2.8605 | 3.1657 | 3.1657 | 2019-11-09 09:00 | 1.7833 | 2.9225 | 4.7974 | 4.7974 | 4.7974 | 4.7974
2021-09-11 20:00 | 2.1695 | 2.6866 | 2.7294 | 2.9127 | 2.8394 | 3.0228 | 1.4366 | 2.1762 | 2.5909 | 2.5909 | 2.8674 | 2.8674 | 2019-11-09 10:00 | 1.7376 | 2.8476 | 4.6744 | 4.6744 | 4.6744 | 4.6744
2021-09-11 21:00 | 2.0605 | 2.5516 | 2.5923 | 2.7665 | 2.6968 | 2.871 | 1.4375 | 2.1776 | 2.5925 | 2.5925 | 2.8691 | 2.8691 | 2019-11-09 11:00 | 1.7909 | 2.935 | 4.8179 | 4.8179 | 4.8179 | 4.8179
2021-09-11 22:00 | 1.9434 | 2.4065 | 2.4449 | 2.6091 | 2.5434 | 2.7077 | 1.286 | 1.9481 | 2.3193 | 2.3193 | 2.5668 | 2.5668 | 2019-11-09 12:00 | 1.7986 | 2.9475 | 4.8384 | 4.8384 | 4.8384 | 4.8384
2021-09-11 23:00 | 1.8234 | 2.2579 | 2.2939 | 2.448 | 2.3864 | 2.5405 | 1.1374 | 1.723 | 2.0513 | 2.0513 | 2.2702 | 2.2702 | 2019-11-09 13:00 | 1.8214 | 2.985 | 4.8999 | 4.8999 | 4.8999 | 4.8999
2021-09-12 | 1.6261 | 2.0137 | 2.0458 | 2.1832 | 2.1283 | 2.2657 | 1.0374 | 1.5715 | 1.8709 | 1.8709 | 2.0706 | 2.0706 | 2019-11-09 14:00 | 1.7376 | 2.8476 | 4.6744 | 4.6744 | 4.6744 | 4.6744
2021-09-12 01:00 | 1.5518 | 1.9217 | 1.9523 | 2.0835 | 2.031 | 2.1622 | 0.89169 | 1.3507 | 1.6081 | 1.6081 | 1.7797 | 1.7797 | 2019-11-09 15:00 | 1.7757 | 2.91 | 4.7769 | 4.7769 | 4.7769 | 4.7769
2021-09-12 02:00 | 1.4659 | 1.8153 | 1.8442 | 1.9682 | 1.9186 | 2.0425 | 0.79157 | 1.1991 | 1.4276 | 1.4276 | 1.5799 | 1.5799 | 2019-11-09 16:00 | 1.7833 | 2.9225 | 4.7974 | 4.7974 | 4.7974 | 4.7974
2021-09-12 03:00 | 1.4689 | 1.8191 | 1.848 | 1.9722 | 1.9225 | 2.0467 | 0.79163 | 1.1992 | 1.4277 | 1.4277 | 1.58 | 1.58 | 2019-11-09 17:00 | 1.6995 | 2.7851 | 4.5718 | 4.5718 | 4.5718 | 4.5718
2021-09-12 04:00 | 1.4489 | 1.7943 | 1.8229 | 1.9453 | 1.8964 | 2.0188 | 0.81735 | 1.2381 | 1.4741 | 1.4741 | 1.6313 | 1.6313 | 2019-11-09 18:00 | 1.5547 | 2.5478 | 4.1823 | 4.1823 | 4.1823 | 4.1823
2021-09-12 05:00 | 1.4975 | 1.8544 | 1.884 | 2.0106 | 1.9599 | 2.0865 | 0.81735 | 1.2381 | 1.4741 | 1.4741 | 1.6313 | 1.6313 | 2019-11-09 19:00 | 1.5699 | 2.5728 | 4.2233 | 4.2233 | 4.2233 | 4.2233
2021-09-12 06:00 | 1.6461 | 2.0385 | 2.0709 | 2.2101 | 2.1544 | 2.2936 | 0.86022 | 1.3031 | 1.5514 | 1.5514 | 1.7169 | 1.7169 | 2019-11-09 20:00 | 1.5623 | 2.5603 | 4.2028 | 4.2028 | 4.2028 | 4.2028
2021-09-12 07:00 | 1.6633 | 2.0597 | 2.0925 | 2.2331 | 2.1769 | 2.3175 | 0.88308 | 1.3377 | 1.5926 | 1.5926 | 1.7625 | 1.7625 | 2019-11-09 21:00 | 1.5013 | 2.4604 | 4.0388 | 4.0388 | 4.0388 | 4.0388
2021-09-12 08:00 | 1.6661 | 2.0633 | 2.0961 | 2.237 | 2.1806 | 2.3215 | 1.003 | 1.5193 | 1.8088 | 1.8088 | 2.0018 | 2.0018 | 2019-11-09 22:00 | 1.4861 | 2.4354 | 3.9978 | 3.9978 | 3.9978 | 3.9978
2021-09-12 09:00 | 1.7119 | 2.1199 | 2.1536 | 2.2984 | 2.2405 | 2.3852 | 1.1489 | 1.7403 | 2.0719 | 2.0719 | 2.293 | 2.293 | 2019-11-09 23:00 | 1.3184 | 2.1607 | 3.5468 | 3.5468 | 3.5468 | 3.5468
2021-09-12 10:00 | 1.729 | 2.1411 | 2.1752 | 2.3214 | 2.2629 | 2.4091 | 1.2289 | 1.8615 | 2.2162 | 2.2162 | 2.4527 | 2.4527 | 2019-11-10 | 1.2575 | 2.0608 | 3.3828 | 3.3828 | 3.3828 | 3.3828
2021-09-12 11:00 | 1.7033 | 2.1093 | 2.1429 | 2.2868 | 2.2292 | 2.3732 | 1.2803 | 1.9394 | 2.309 | 2.309 | 2.5554 | 2.5554 | 2019-11-10 01:00 | 1.1813 | 1.9359 | 3.1777 | 3.1777 | 3.1777 | 3.1777
2021-09-12 12:00 | 1.729 | 2.1411 | 2.1752 | 2.3214 | 2.2629 | 2.4091 | 1.2832 | 1.9438 | 2.3142 | 2.3142 | 2.5611 | 2.5611 | 2019-11-10 02:00 | 1.1508 | 1.8859 | 3.0957 | 3.0957 | 3.0957 | 3.0957
2021-09-12 13:00 | 1.789 | 2.2154 | 2.2507 | 2.4019 | 2.3415 | 2.4927 | 1.3289 | 2.013 | 2.3966 | 2.3966 | 2.6524 | 2.6524 | 2019-11-10 03:00 | 1.1203 | 1.8359 | 3.0137 | 3.0137 | 3.0137 | 3.0137
2021-09-12 14:00 | 1.9205 | 2.3782 | 2.4161 | 2.5785 | 2.5135 | 2.6759 | 1.2718 | 1.9265 | 2.2936 | 2.2936 | 2.5383 | 2.5383 | 2019-11-10 04:00 | 1.1431 | 1.8734 | 3.0752 | 3.0752 | 3.0752 | 3.0752
2021-09-12 15:00 | 2.0316 | 2.5159 | 2.5559 | 2.7277 | 2.659 | 2.8307 | 1.3918 | 2.1083 | 2.51 | 2.51 | 2.7779 | 2.7779 | 2019-11-10 05:00 | 1.2041 | 1.9733 | 3.2392 | 3.2392 | 3.2392 | 3.2392
2021-09-12 16:00 | 2.2291 | 2.7604 | 2.8044 | 2.9928 | 2.9175 | 3.1059 | 1.5004 | 2.2728 | 2.7059 | 2.7059 | 2.9946 | 2.9946 | 2019-11-10 06:00 | 1.2575 | 2.0608 | 3.3828 | 3.3828 | 3.3828 | 3.3828
2021-09-12 17:00 | 2.6092 | 3.2311 | 3.2826 | 3.5032 | 3.4149 | 3.6355 | 1.6376 | 2.4806 | 2.9533 | 2.9533 | 3.2684 | 3.2684 | 2019-11-10 07:00 | 1.5318 | 2.5104 | 4.1208 | 4.1208 | 4.1208 | 4.1208
2021-09-12 18:00 | 2.8979 | 3.5886 | 3.6457 | 3.8907 | 3.7927 | 4.0377 | 1.829 | 2.7706 | 3.2986 | 3.2986 | 3.6506 | 3.6506 | 2019-11-10 08:00 | 1.6766 | 2.7477 | 4.5103 | 4.5103 | 4.5103 | 4.5103
2021-09-12 19:00 | 2.8296 | 3.504 | 3.5598 | 3.799 | 3.7033 | 3.9425 | 1.7776 | 2.6927 | 3.2058 | 3.2058 | 3.5479 | 3.5479 | 2019-11-10 09:00 | 1.7376 | 2.8476 | 4.6744 | 4.6744 | 4.6744 | 4.6744
2021-09-12 20:00 | 2.5292 | 3.132 | 3.1819 | 3.3957 | 3.3102 | 3.524 | 1.6804 | 2.5455 | 3.0306 | 3.0306 | 3.354 | 3.354 | 2019-11-10 10:00 | 1.8443 | 3.0224 | 4.9614 | 4.9614 | 4.9614 | 4.9614
2021-09-12 21:00 | 2.3463 | 2.9055 | 2.9518 | 3.1502 | 3.0708 | 3.2692 | 1.5661 | 2.3724 | 2.8244 | 2.8244 | 3.1258 | 3.1258 | 2019-11-10 11:00 | 1.7681 | 2.8975 | 4.7564 | 4.7564 | 4.7564 | 4.7564
2021-09-12 22:00 | 2.1463 | 2.6578 | 2.7001 | 2.8816 | 2.809 | 2.9904 | 1.3718 | 2.078 | 2.4739 | 2.4739 | 2.7379 | 2.7379 | 2019-11-10 12:00 | 1.8443 | 3.0224 | 4.9614 | 4.9614 | 4.9614 | 4.9614
2021-09-12 23:00 | 1.955 | 2.421 | 2.4595 | 2.6248 | 2.5587 | 2.7239 | 1.2546 | 1.9005 | 2.2627 | 2.2627 | 2.5041 | 2.5041 | 2019-11-10 13:00 | 1.7909 | 2.935 | 4.8179 | 4.8179 | 4.8179 | 4.8179
2021-09-13 | 1.7919 | 2.219 | 2.2543 | 2.4058 | 2.3452 | 2.4967 | 1.1231 | 1.7013 | 2.0255 | 2.0255 | 2.2417 | 2.2417 | 2019-11-10 14:00 | 1.7986 | 2.9475 | 4.8384 | 4.8384 | 4.8384 | 4.8384
2021-09-13 01:00 | 1.6633 | 2.0597 | 2.0925 | 2.2331 | 2.1769 | 2.3175 | 0.98366 | 1.4901 | 1.774 | 1.774 | 1.9633 | 1.9633 | 2019-11-10 15:00 | 1.7986 | 2.9475 | 4.8384 | 4.8384 | 4.8384 | 4.8384
2021-09-13 02:00 | 1.6433 | 2.0349 | 2.0674 | 2.2063 | 2.1507 | 2.2896 | 0.97739 | 1.4806 | 1.7627 | 1.7627 | 1.9508 | 1.9508 | 2019-11-10 16:00 | 1.7528 | 2.8726 | 4.7154 | 4.7154 | 4.7154 | 4.7154
2021-09-13 03:00 | 1.6547 | 2.0491 | 2.0817 | 2.2216 | 2.1657 | 2.3055 | 0.94358 | 1.4293 | 1.7017 | 1.7017 | 1.8833 | 1.8833 | 2019-11-10 17:00 | 1.7757 | 2.91 | 4.7769 | 4.7769 | 4.7769 | 4.7769
2021-09-13 04:00 | 1.7119 | 2.1199 | 2.1536 | 2.2984 | 2.2405 | 2.3852 | 0.88022 | 1.3334 | 1.5874 | 1.5874 | 1.7568 | 1.7568 | 2019-11-10 18:00 | 1.5775 | 2.5853 | 4.2438 | 4.2438 | 4.2438 | 4.2438
2021-09-13 05:00 | 1.929 | 2.3887 | 2.4268 | 2.5898 | 2.5246 | 2.6876 | 0.99168 | 1.5022 | 1.7885 | 1.7885 | 1.9793 | 1.9793 | 2019-11-10 19:00 | 1.5166 | 2.4854 | 4.0798 | 4.0798 | 4.0798 | 4.0798
2021-09-13 06:00 | 2.4606 | 3.0471 | 3.0956 | 3.3036 | 3.2204 | 3.4284 | 1.0773 | 1.632 | 1.9429 | 1.9429 | 2.1503 | 2.1503 | 2019-11-10 20:00 | 1.5394 | 2.5229 | 4.1413 | 4.1413 | 4.1413 | 4.1413
2021-09-13 07:00 | 2.8522 | 3.532 | 3.5882 | 3.8293 | 3.7329 | 3.974 | 1.4118 | 2.1386 | 2.5461 | 2.5461 | 2.8178 | 2.8178 | 2019-11-10 21:00 | 1.509 | 2.4729 | 4.0593 | 4.0593 | 4.0593 | 4.0593
2021-09-13 08:00 | 3.1179 | 3.8611 | 3.9226 | 4.1861 | 4.0807 | 4.3443 | 1.5633 | 2.368 | 2.8193 | 2.8193 | 3.1201 | 3.1201 | 2019-11-10 22:00 | 1.4556 | 2.3855 | 3.9158 | 3.9158 | 3.9158 | 3.9158
2021-09-13 09:00 | 3.2551 | 4.031 | 4.0952 | 4.3703 | 4.2603 | 4.5354 | 1.7347 | 2.6278 | 3.1285 | 3.1285 | 3.4623 | 3.4623 | 2019-11-10 23:00 | 1.3032 | 2.1357 | 3.5058 | 3.5058 | 3.5058 | 3.5058
2021-09-13 10:00 | 3.3323 | 4.1265 | 4.1922 | 4.4739 | 4.3612 | 4.6429 | 1.729 | 2.6191 | 3.1182 | 3.1182 | 3.4509 | 3.4509 | 2019-11-11 | 1.2498 | 2.0483 | 3.3622 | 3.3622 | 3.3622 | 3.3622
2021-09-13 11:00 | 2.7921 | 3.4576 | 3.5127 | 3.7487 | 3.6543 | 3.8903 | 1.5833 | 2.3983 | 2.8554 | 2.8554 | 3.16 | 3.16 | 2019-11-11 01:00 | 1.166 | 1.9109 | 3.1367 | 3.1367 | 3.1367 | 3.1367
2021-09-13 12:00 | 2.8179 | 3.4895 | 3.5451 | 3.7833 | 3.688 | 3.9262 | 1.6376 | 2.4806 | 2.9533 | 2.9533 | 3.2684 | 3.2684 | 2019-11-11 02:00 | 1.1355 | 1.8609 | 3.0547 | 3.0547 | 3.0547 | 3.0547
2021-09-13 13:00 | 2.815 | 3.4859 | 3.5415 | 3.7794 | 3.6842 | 3.9222 | 1.6318 | 2.4719 | 2.943 | 2.943 | 3.257 | 3.257 | 2019-11-11 03:00 | 1.1203 | 1.8359 | 3.0137 | 3.0137 | 3.0137 | 3.0137
2021-09-13 14:00 | 2.8093 | 3.4789 | 3.5343 | 3.7718 | 3.6768 | 3.9142 | 1.6176 | 2.4503 | 2.9172 | 2.9172 | 3.2285 | 3.2285 | 2019-11-11 04:00 | 1.1508 | 1.8859 | 3.0957 | 3.0957 | 3.0957 | 3.0957
2021-09-13 15:00 | 2.4235 | 3.0011 | 3.0489 | 3.2538 | 3.1718 | 3.3767 | 1.5321 | 2.3208 | 2.763 | 2.763 | 3.0578 | 3.0578 | 2019-11-11 05:00 | 1.2498 | 2.0483 | 3.3622 | 3.3622 | 3.3622 | 3.3622
2021-09-13 16:00 | 2.5545 | 3.1633 | 3.2137 | 3.4296 | 3.3432 | 3.5592 | 1.6537 | 2.505 | 2.9823 | 2.9823 | 3.3005 | 3.3005 | 2019-11-11 06:00 | 1.4556 | 2.3855 | 3.9158 | 3.9158 | 3.9158 | 3.9158
2021-09-13 17:00 | 3.1721 | 3.9281 | 3.9906 | 4.2588 | 4.1515 | 4.4197 | 1.8205 | 2.7577 | 3.2831 | 3.2831 | 3.6335 | 3.6335 | 2019-11-11 07:00 | 1.8062 | 2.96 | 4.8589 | 4.8589 | 4.8589 | 4.8589
2021-09-13 18:00 | 3.3037 | 4.0911 | 4.1563 | 4.4356 | 4.3238 | 4.6031 | 1.9891 | 3.0131 | 3.5872 | 3.5872 | 3.97 | 3.97 | 2019-11-11 08:00 | 2.0577 | 3.3721 | 5.5354 | 5.5354 | 5.5354 | 5.5354
2021-09-13 19:00 | 3.2637 | 4.0416 | 4.1059 | 4.3818 | 4.2715 | 4.5474 | 2.0062 | 3.0391 | 3.6182 | 3.6182 | 4.0042 | 4.0042 | 2019-11-11 09:00 | 1.9738 | 3.2348 | 5.3099 | 5.3099 | 5.3099 | 5.3099
2021-09-13 20:00 | 2.9722 | 3.6806 | 3.7392 | 3.9905 | 3.89 | 4.1412 | 1.8694 | 2.8318 | 3.3714 | 3.3714 | 3.7311 | 3.7311 | 2019-11-11 10:00 | 2.0653 | 3.3846 | 5.5559 | 5.5559 | 5.5559 | 5.5559
2021-09-13 21:00 | 2.7321 | 3.3833 | 3.4372 | 3.6682 | 3.5758 | 3.8067 | 1.6861 | 2.5542 | 3.0409 | 3.0409 | 3.3654 | 3.3654 | 2019-11-11 11:00 | 2.1034 | 3.4471 | 5.6584 | 5.6584 | 5.6584 | 5.6584
2021-09-13 22:00 | 2.3663 | 2.9303 | 2.977 | 3.177 | 3.097 | 3.297 | 1.4778 | 2.2385 | 2.6651 | 2.6651 | 2.9495 | 2.9495 | 2019-11-11 12:00 | 2.1415 | 3.5095 | 5.7609 | 5.7609 | 5.7609 | 5.7609
2021-09-13 23:00 | 2.1808 | 2.7005 | 2.7435 | 2.9279 | 2.8541 | 3.0385 | 1.3347 | 2.0219 | 2.4072 | 2.4072 | 2.664 | 2.664 | 2019-11-11 13:00 | 2.233 | 3.6594 | 6.007 | 6.007 | 6.007 | 6.007
2021-09-14 | 1.8664 | 2.3112 | 2.348 | 2.5058 | 2.4427 | 2.6005 | 1.166 | 1.7663 | 2.1029 | 2.1029 | 2.3272 | 2.3272 | 2019-11-11 14:00 | 2.2177 | 3.6344 | 5.966 | 5.966 | 5.966 | 5.966
2021-09-14 01:00 | 1.7633 | 2.1836 | 2.2184 | 2.3674 | 2.3078 | 2.4569 | 1.0413 | 1.5774 | 1.878 | 1.878 | 2.0784 | 2.0784 | 2019-11-11 15:00 | 2.1415 | 3.5095 | 5.7609 | 5.7609 | 5.7609 | 5.7609
2021-09-14 02:00 | 1.7462 | 2.1623 | 2.1968 | 2.3444 | 2.2854 | 2.433 | 0.98025 | 1.4849 | 1.7678 | 1.7678 | 1.9565 | 1.9565 | 2019-11-11 16:00 | 2.2177 | 3.6344 | 5.966 | 5.966 | 5.966 | 5.966
2021-09-14 03:00 | 1.7407 | 2.1556 | 2.1899 | 2.3371 | 2.2782 | 2.4253 | 0.90889 | 1.3768 | 1.6391 | 1.6391 | 1.814 | 1.814 | 2019-11-11 17:00 | 2.2101 | 3.6219 | 5.9454 | 5.9454 | 5.9454 | 5.9454
2021-09-14 04:00 | 1.8423 | 2.2814 | 2.3177 | 2.4735 | 2.4112 | 2.5669 | 0.96269 | 1.4583 | 1.7362 | 1.7362 | 1.9214 | 1.9214 | 2019-11-11 18:00 | 1.9662 | 3.2223 | 5.2894 | 5.2894 | 5.2894 | 5.2894
2021-09-14 05:00 | 1.9719 | 2.4419 | 2.4808 | 2.6475 | 2.5808 | 2.7475 | 1.1003 | 1.6667 | 1.9843 | 1.9843 | 2.196 | 2.196 | 2019-11-11 19:00 | 1.8824 | 3.0849 | 5.0639 | 5.0639 | 5.0639 | 5.0639
2021-09-14 06:00 | 2.6321 | 3.2594 | 3.3114 | 3.5339 | 3.4449 | 3.6674 | 1.1945 | 1.8094 | 2.1542 | 2.1542 | 2.3841 | 2.3841 | 2019-11-11 20:00 | 1.7909 | 2.935 | 4.8179 | 4.8179 | 4.8179 | 4.8179
2021-09-14 07:00 | 2.9007 | 3.5921 | 3.6493 | 3.8945 | 3.7965 | 4.0417 | 1.4004 | 2.1213 | 2.5255 | 2.5255 | 2.795 | 2.795 | 2019-11-11 21:00 | 1.7147 | 2.8101 | 4.6128 | 4.6128 | 4.6128 | 4.6128
2021-09-14 08:00 | 3.1237 | 3.8682 | 3.9298 | 4.1938 | 4.0882 | 4.3523 | 1.5804 | 2.394 | 2.8502 | 2.8502 | 3.1543 | 3.1543 | 2019-11-11 22:00 | 1.5166 | 2.4854 | 4.0798 | 4.0798 | 4.0798 | 4.0798
2021-09-14 09:00 | 2.8693 | 3.5532 | 3.6098 | 3.8523 | 3.7553 | 3.9979 | 1.5861 | 2.4027 | 2.8605 | 2.8605 | 3.1657 | 3.1657 | 2019-11-11 23:00 | 1.3794 | 2.2606 | 3.7108 | 3.7108 | 3.7108 | 3.7108
2021-09-14 10:00 | 2.6778 | 3.3161 | 3.3689 | 3.5953 | 3.5047 | 3.7311 | 1.4832 | 2.2468 | 2.675 | 2.675 | 2.9604 | 2.9604 | 2019-11-12 | 1.3184 | 2.1607 | 3.5468 | 3.5468 | 3.5468 | 3.5468
2021-09-14 11:00 | 2.4978 | 3.0931 | 3.1424 | 3.3535 | 3.2691 | 3.4802 | 1.5032 | 2.2771 | 2.711 | 2.711 | 3.0003 | 3.0003 | 2019-11-12 01:00 | 1.2422 | 2.0358 | 3.3417 | 3.3417 | 3.3417 | 3.3417
2021-09-14 12:00 | 2.3663 | 2.9303 | 2.977 | 3.177 | 3.097 | 3.297 | 1.4689 | 2.2252 | 2.6492 | 2.6492 | 2.9319 | 2.9319 | 2019-11-12 02:00 | 1.2498 | 2.0483 | 3.3622 | 3.3622 | 3.3622 | 3.3622
2021-09-14 13:00 | 2.0205 | 2.5021 | 2.5419 | 2.7127 | 2.6444 | 2.8152 | 1.3403 | 2.0304 | 2.4173 | 2.4173 | 2.6752 | 2.6752 | 2019-11-12 03:00 | 1.2346 | 2.0233 | 3.3212 | 3.3212 | 3.3212 | 3.3212
2021-09-14 14:00 | 2.0834 | 2.58 | 2.621 | 2.7972 | 2.7267 | 2.9028 | 1.3661 | 2.0693 | 2.4636 | 2.4636 | 2.7265 | 2.7265 | 2019-11-12 04:00 | 1.3261 | 2.1732 | 3.5673 | 3.5673 | 3.5673 | 3.5673
2021-09-14 15:00 | 2.1434 | 2.6543 | 2.6965 | 2.8777 | 2.8053 | 2.9864 | 1.4232 | 2.1559 | 2.5667 | 2.5667 | 2.8406 | 2.8406 | 2019-11-12 05:00 | 1.3489 | 2.2106 | 3.6288 | 3.6288 | 3.6288 | 3.6288
2021-09-14 16:00 | 2.3235 | 2.8772 | 2.9231 | 3.1195 | 3.0409 | 3.2373 | 1.5575 | 2.3594 | 2.809 | 2.809 | 3.1087 | 3.1087 | 2019-11-12 06:00 | 1.5394 | 2.5229 | 4.1413 | 4.1413 | 4.1413 | 4.1413
2021-09-14 17:00 | 2.9951 | 3.7089 | 3.768 | 4.0212 | 3.9199 | 4.1731 | 1.669 | 2.5282 | 3.01 | 3.01 | 3.3311 | 3.3311 | 2019-11-12 07:00 | 1.9053 | 3.1224 | 5.1254 | 5.1254 | 5.1254 | 5.1254
2021-09-14 18:00 | 3.2294 | 3.9991 | 4.0628 | 4.3358 | 4.2266 | 4.4996 | 2.0634 | 3.1256 | 3.7212 | 3.7212 | 4.1183 | 4.1183 | 2019-11-12 08:00 | 1.9891 | 3.2597 | 5.3509 | 5.3509 | 5.3509 | 5.3509
2021-09-14 19:00 | 3.2094 | 3.9743 | 4.0376 | 4.3089 | 4.2004 | 4.4717 | 2.0691 | 3.1343 | 3.7315 | 3.7315 | 4.1297 | 4.1297 | 2019-11-12 09:00 | 2.1415 | 3.5095 | 5.7609 | 5.7609 | 5.7609 | 5.7609
2021-09-14 20:00 | 2.8802 | 3.5667 | 3.6235 | 3.867 | 3.7696 | 4.0131 | 1.9605 | 2.9698 | 3.5357 | 3.5357 | 3.913 | 3.913 | 2019-11-12 10:00 | 2.172 | 3.5595 | 5.8429 | 5.8429 | 5.8429 | 5.8429
2021-09-14 21:00 | 2.695 | 3.3373 | 3.3905 | 3.6183 | 3.5271 | 3.755 | 1.7119 | 2.5932 | 3.0873 | 3.0873 | 3.4167 | 3.4167 | 2019-11-12 11:00 | 2.3244 | 3.8093 | 6.253 | 6.253 | 6.253 | 6.253
2021-09-14 22:00 | 2.3616 | 2.9245 | 2.9711 | 3.1707 | 3.0909 | 3.2905 | 1.5915 | 2.4109 | 2.8703 | 2.8703 | 3.1765 | 3.1765 | 2019-11-12 12:00 | 2.3092 | 3.7843 | 6.212 | 6.212 | 6.212 | 6.212
2021-09-14 23:00 | 2.2463 | 2.7817 | 2.826 | 3.0159 | 2.9399 | 3.1298 | 1.4204 | 2.1516 | 2.5616 | 2.5616 | 2.8349 | 2.8349 | 2019-11-12 13:00 | 2.2482 | 3.6844 | 6.048 | 6.048 | 6.048 | 6.048
2021-09-15 | 1.9234 | 2.3819 | 2.4198 | 2.5824 | 2.5174 | 2.68 | 1.2319 | 1.866 | 2.2216 | 2.2216 | 2.4587 | 2.4587 | 2019-11-12 14:00 | 2.2863 | 3.7468 | 6.1505 | 6.1505 | 6.1505 | 6.1505
2021-09-15 01:00 | 1.8433 | 2.2827 | 2.319 | 2.4749 | 2.4125 | 2.5683 | 1.0784 | 1.6336 | 1.9449 | 1.9449 | 2.1524 | 2.1524 | 2019-11-12 15:00 | 2.2253 | 3.6469 | 5.9865 | 5.9865 | 5.9865 | 5.9865
2021-09-15 02:00 | 1.7633 | 2.1836 | 2.2184 | 2.3674 | 2.3078 | 2.4569 | 1.0374 | 1.5715 | 1.8709 | 1.8709 | 2.0706 | 2.0706 | 2019-11-12 16:00 | 2.2482 | 3.6844 | 6.048 | 6.048 | 6.048 | 6.048
2021-09-15 03:00 | 1.7776 | 2.2013 | 2.2363 | 2.3866 | 2.3265 | 2.4768 | 1.0231 | 1.5498 | 1.8452 | 1.8452 | 2.042 | 2.042 | 2019-11-12 17:00 | 2.1796 | 3.572 | 5.8634 | 5.8634 | 5.8634 | 5.8634
2021-09-15 04:00 | 1.8662 | 2.311 | 2.3478 | 2.5055 | 2.4424 | 2.6002 | 1.0203 | 1.5455 | 1.84 | 1.84 | 2.0363 | 2.0363 | 2019-11-12 18:00 | 2.0348 | 3.3347 | 5.4739 | 5.4739 | 5.4739 | 5.4739
2021-09-15 05:00 | 2.0931 | 2.592 | 2.6333 | 2.8102 | 2.7394 | 2.9163 | 1.063 | 1.6103 | 1.9171 | 1.9171 | 2.1217 | 2.1217 | 2019-11-12 19:00 | 1.8824 | 3.0849 | 5.0639 | 5.0639 | 5.0639 | 5.0639
2021-09-15 06:00 | 2.5721 | 3.1851 | 3.2359 | 3.4533 | 3.3663 | 3.5837 | 1.3318 | 2.0174 | 2.4018 | 2.4018 | 2.6581 | 2.6581 | 2019-11-12 20:00 | 1.8976 | 3.1099 | 5.1049 | 5.1049 | 5.1049 | 5.1049
2021-09-15 07:00 | 2.9493 | 3.6523 | 3.7105 | 3.9598 | 3.86 | 4.1094 | 1.4489 | 2.1949 | 2.6131 | 2.6131 | 2.8919 | 2.8919 | 2019-11-12 21:00 | 1.6919 | 2.7726 | 4.5513 | 4.5513 | 4.5513 | 4.5513
2021-09-15 08:00 | 3.0722 | 3.8045 | 3.8651 | 4.1248 | 4.0209 | 4.2806 | 1.5918 | 2.4113 | 2.8708 | 2.8708 | 3.1771 | 3.1771 | 2019-11-12 22:00 | 1.4861 | 2.4354 | 3.9978 | 3.9978 | 3.9978 | 3.9978
2021-09-15 09:00 | 2.6092 | 3.2311 | 3.2826 | 3.5032 | 3.4149 | 3.6355 | 1.5356 | 2.3261 | 2.7694 | 2.7694 | 3.0649 | 3.0649 | 2019-11-12 23:00 | 1.4175 | 2.323 | 3.8133 | 3.8133 | 3.8133 | 3.8133
2021-09-15 10:00 | 2.5549 | 3.1639 | 3.2143 | 3.4303 | 3.3439 | 3.5598 | 1.5232 | 2.3074 | 2.7471 | 2.7471 | 3.0402 | 3.0402 | 2019-11-13 | 1.3184 | 2.1607 | 3.5468 | 3.5468 | 3.5468 | 3.5468
2021-09-15 11:00 | 2.2091 | 2.7357 | 2.7792 | 2.966 | 2.8913 | 3.078 | 1.3575 | 2.0563 | 2.4482 | 2.4482 | 2.7094 | 2.7094 | 2019-11-13 01:00 | 1.227 | 2.0108 | 3.3007 | 3.3007 | 3.3007 | 3.3007
2021-09-15 12:00 | 2.0577 | 2.5481 | 2.5887 | 2.7626 | 2.6931 | 2.867 | 1.3804 | 2.091 | 2.4894 | 2.4894 | 2.755 | 2.755 | 2019-11-13 02:00 | 1.1736 | 1.9234 | 3.1572 | 3.1572 | 3.1572 | 3.1572
2021-09-15 13:00 | 2.1434 | 2.6543 | 2.6965 | 2.8777 | 2.8053 | 2.9864 | 1.3946 | 2.1126 | 2.5152 | 2.5152 | 2.7836 | 2.7836 | 2019-11-13 03:00 | 1.1431 | 1.8734 | 3.0752 | 3.0752 | 3.0752 | 3.0752
2021-09-15 14:00 | 1.9005 | 2.3535 | 2.3909 | 2.5516 | 2.4873 | 2.648 | 1.3003 | 1.9698 | 2.3451 | 2.3451 | 2.5953 | 2.5953 | 2019-11-13 04:00 | 1.2346 | 2.0233 | 3.3212 | 3.3212 | 3.3212 | 3.3212
2021-09-15 15:00 | 2.0548 | 2.5446 | 2.5851 | 2.7588 | 2.6893 | 2.863 | 1.3375 | 2.026 | 2.4121 | 2.4121 | 2.6695 | 2.6695 | 2019-11-13 05:00 | 1.3032 | 2.1357 | 3.5058 | 3.5058 | 3.5058 | 3.5058
2021-09-15 16:00 | 2.2508 | 2.7872 | 2.8316 | 3.0219 | 2.9458 | 3.1361 | 1.5004 | 2.2728 | 2.7059 | 2.7059 | 2.9946 | 2.9946 | 2019-11-13 06:00 | 1.6233 | 2.6602 | 4.3668 | 4.3668 | 4.3668 | 4.3668
2021-09-15 17:00 | 2.8084 | 3.4777 | 3.5331 | 3.7705 | 3.6755 | 3.9129 | 1.7347 | 2.6278 | 3.1285 | 3.1285 | 3.4623 | 3.4623 | 2019-11-13 07:00 | 1.9129 | 3.1348 | 5.1459 | 5.1459 | 5.1459 | 5.1459
2021-09-15 18:00 | 3.198 | 3.9602 | 4.0233 | 4.2936 | 4.1855 | 4.4558 | 1.9862 | 3.0087 | 3.5821 | 3.5821 | 3.9643 | 3.9643 | 2019-11-13 08:00 | 2.0043 | 3.2847 | 5.3919 | 5.3919 | 5.3919 | 5.3919
2021-09-15 19:00 | 3.0755 | 3.8085 | 3.8691 | 4.1291 | 4.0251 | 4.2851 | 1.9977 | 3.0261 | 3.6027 | 3.6027 | 3.9871 | 3.9871 | 2019-11-13 09:00 | 2.1644 | 3.547 | 5.8224 | 5.8224 | 5.8224 | 5.8224
2021-09-15 20:00 | 2.815 | 3.4859 | 3.5415 | 3.7794 | 3.6842 | 3.9222 | 1.9148 | 2.9005 | 3.4532 | 3.4532 | 3.8217 | 3.8217 | 2019-11-13 10:00 | 2.1034 | 3.4471 | 5.6584 | 5.6584 | 5.6584 | 5.6584
2021-09-15 21:00 | 2.6207 | 3.2453 | 3.297 | 3.5185 | 3.4299 | 3.6514 | 1.8691 | 2.8313 | 3.3708 | 3.3708 | 3.7304 | 3.7304 | 2019-11-13 11:00 | 2.1034 | 3.4471 | 5.6584 | 5.6584 | 5.6584 | 5.6584
2021-09-15 22:00 | 2.3287 | 2.8837 | 2.9297 | 3.1265 | 3.0478 | 3.2446 | 1.6576 | 2.5109 | 2.9894 | 2.9894 | 3.3083 | 3.3083 | 2019-11-13 12:00 | 2.1567 | 3.5345 | 5.8019 | 5.8019 | 5.8019 | 5.8019
2021-09-15 23:00 | 2.1606 | 2.6755 | 2.7181 | 2.9008 | 2.8277 | 3.0103 | 1.3832 | 2.0953 | 2.4946 | 2.4946 | 2.7607 | 2.7607 | 2019-11-13 13:00 | 2.1034 | 3.4471 | 5.6584 | 5.6584 | 5.6584 | 5.6584
2021-09-16 | 1.8549 | 2.297 | 2.3336 | 2.4904 | 2.4277 | 2.5845 | 1.158 | 1.7542 | 2.0884 | 2.0884 | 2.3113 | 2.3113 | 2019-11-13 14:00 | 2.1034 | 3.4471 | 5.6584 | 5.6584 | 5.6584 | 5.6584
2021-09-16 01:00 | 1.6804 | 2.0809 | 2.1141 | 2.2561 | 2.1993 | 2.3414 | 1.0145 | 1.5368 | 1.8297 | 1.8297 | 2.0249 | 2.0249 | 2019-11-13 15:00 | 2.0805 | 3.4096 | 5.5969 | 5.5969 | 5.5969 | 5.5969
2021-09-16 02:00 | 1.6204 | 2.0066 | 2.0386 | 2.1756 | 2.1208 | 2.2578 | 0.93749 | 1.4201 | 1.6907 | 1.6907 | 1.8711 | 1.8711 | 2019-11-13 16:00 | 2.0805 | 3.4096 | 5.5969 | 5.5969 | 5.5969 | 5.5969
2021-09-16 03:00 | 1.64 | 2.0309 | 2.0632 | 2.2018 | 2.1464 | 2.285 | 0.9088 | 1.3767 | 1.639 | 1.639 | 1.8139 | 1.8139 | 2019-11-13 17:00 | 2.0119 | 3.2972 | 5.4124 | 5.4124 | 5.4124 | 5.4124
2021-09-16 04:00 | 1.7014 | 2.1069 | 2.1404 | 2.2843 | 2.2267 | 2.3706 | 0.91738 | 1.3896 | 1.6545 | 1.6545 | 1.831 | 1.831 | 2019-11-13 18:00 | 1.8671 | 3.0599 | 5.0229 | 5.0229 | 5.0229 | 5.0229
2021-09-16 05:00 | 1.8262 | 2.2614 | 2.2975 | 2.4518 | 2.3901 | 2.5445 | 0.98597 | 1.4935 | 1.7781 | 1.7781 | 1.9679 | 1.9679 | 2019-11-13 19:00 | 1.7757 | 2.91 | 4.7769 | 4.7769 | 4.7769 | 4.7769
2021-09-16 06:00 | 2.2863 | 2.8312 | 2.8763 | 3.0696 | 2.9923 | 3.1855 | 1.0831 | 1.6407 | 1.9534 | 1.9534 | 2.1618 | 2.1618 | 2019-11-13 20:00 | 1.7757 | 2.91 | 4.7769 | 4.7769 | 4.7769 | 4.7769
2021-09-16 07:00 | 2.5178 | 3.1179 | 3.1675 | 3.3804 | 3.2952 | 3.5081 | 1.3718 | 2.078 | 2.4739 | 2.4739 | 2.7379 | 2.7379 | 2019-11-13 21:00 | 1.6309 | 2.6727 | 4.3873 | 4.3873 | 4.3873 | 4.3873
2021-09-16 08:00 | 2.5149 | 3.1143 | 3.164 | 3.3765 | 3.2915 | 3.5041 | 1.3661 | 2.0693 | 2.4636 | 2.4636 | 2.7265 | 2.7265 | 2019-11-13 22:00 | 1.5166 | 2.4854 | 4.0798 | 4.0798 | 4.0798 | 4.0798
2021-09-16 09:00 | 2.392 | 2.9622 | 3.0093 | 3.2116 | 3.1307 | 3.3329 | 1.3832 | 2.0953 | 2.4946 | 2.4946 | 2.7607 | 2.7607 | 2019-11-13 23:00 | 1.4099 | 2.3105 | 3.7928 | 3.7928 | 3.7928 | 3.7928
2021-09-16 10:00 | 2.4663 | 3.0542 | 3.1028 | 3.3113 | 3.2279 | 3.4364 | 1.4404 | 2.1819 | 2.5976 | 2.5976 | 2.8748 | 2.8748 | 2019-11-14 | 1.3337 | 2.1856 | 3.5878 | 3.5878 | 3.5878 | 3.5878
2021-09-16 11:00 | 2.2949 | 2.8418 | 2.8871 | 3.0811 | 3.0035 | 3.1975 | 1.3775 | 2.0866 | 2.4843 | 2.4843 | 2.7493 | 2.7493 | 2019-11-14 01:00 | 1.2498 | 2.0483 | 3.3622 | 3.3622 | 3.3622 | 3.3622
2021-09-16 12:00 | 2.4178 | 2.994 | 3.0417 | 3.2461 | 3.1643 | 3.3687 | 1.4975 | 2.2685 | 2.7007 | 2.7007 | 2.9889 | 2.9889 | 2019-11-14 02:00 | 1.2194 | 1.9983 | 3.2802 | 3.2802 | 3.2802 | 3.2802
2021-09-16 13:00 | 2.3578 | 2.9197 | 2.9662 | 3.1655 | 3.0858 | 3.2851 | 1.4689 | 2.2252 | 2.6492 | 2.6492 | 2.9319 | 2.9319 | 2019-11-14 03:00 | 1.2194 | 1.9983 | 3.2802 | 3.2802 | 3.2802 | 3.2802
2021-09-16 14:00 | 2.2177 | 2.7463 | 2.79 | 2.9775 | 2.9025 | 3.09 | 1.2718 | 1.9265 | 2.2936 | 2.2936 | 2.5383 | 2.5383 | 2019-11-14 04:00 | 1.1965 | 1.9608 | 3.2187 | 3.2187 | 3.2187 | 3.2187
2021-09-16 15:00 | 1.9491 | 2.4136 | 2.4521 | 2.6168 | 2.5509 | 2.7157 | 1.306 | 1.9784 | 2.3554 | 2.3554 | 2.6067 | 2.6067 | 2019-11-14 05:00 | 1.2727 | 2.0857 | 3.4238 | 3.4238 | 3.4238 | 3.4238
2021-09-16 16:00 | 2.157 | 2.6711 | 2.7136 | 2.896 | 2.823 | 3.0054 | 1.3832 | 2.0953 | 2.4946 | 2.4946 | 2.7607 | 2.7607 | 2019-11-14 06:00 | 1.5242 | 2.4979 | 4.1003 | 4.1003 | 4.1003 | 4.1003
2021-09-16 17:00 | 2.5892 | 3.2064 | 3.2574 | 3.4763 | 3.3888 | 3.6076 | 1.6602 | 2.5149 | 2.9941 | 2.9941 | 3.3136 | 3.3136 | 2019-11-14 07:00 | 1.8824 | 3.0849 | 5.0639 | 5.0639 | 5.0639 | 5.0639
2021-09-16 18:00 | 2.9636 | 3.67 | 3.7284 | 3.979 | 3.8787 | 4.1293 | 1.849 | 2.8009 | 3.3347 | 3.3347 | 3.6905 | 3.6905 | 2019-11-14 08:00 | 1.9891 | 3.2597 | 5.3509 | 5.3509 | 5.3509 | 5.3509
2021-09-16 19:00 | 2.9379 | 3.6381 | 3.6961 | 3.9444 | 3.8451 | 4.0934 | 1.8633 | 2.8226 | 3.3604 | 3.3604 | 3.719 | 3.719 | 2019-11-14 09:00 | 2.0805 | 3.4096 | 5.5969 | 5.5969 | 5.5969 | 5.5969
2021-09-16 20:00 | 2.7893 | 3.4541 | 3.5091 | 3.7449 | 3.6506 | 3.8864 | 1.829 | 2.7706 | 3.2986 | 3.2986 | 3.6506 | 3.6506 | 2019-11-14 10:00 | 2.0577 | 3.3721 | 5.5354 | 5.5354 | 5.5354 | 5.5354
2021-09-16 21:00 | 2.5464 | 3.1533 | 3.2035 | 3.4188 | 3.3327 | 3.5479 | 1.7662 | 2.6754 | 3.1852 | 3.1852 | 3.5251 | 3.5251 | 2019-11-14 11:00 | 2.0882 | 3.4221 | 5.6174 | 5.6174 | 5.6174 | 5.6174
2021-09-16 22:00 | 2.3149 | 2.8666 | 2.9123 | 3.108 | 3.0297 | 3.2254 | 1.4261 | 2.1602 | 2.5719 | 2.5719 | 2.8463 | 2.8463 | 2019-11-14 12:00 | 2.1872 | 3.5845 | 5.8839 | 5.8839 | 5.8839 | 5.8839
2021-09-16 23:00 | 2.0748 | 2.5693 | 2.6103 | 2.7856 | 2.7155 | 2.8909 | 1.3146 | 1.9914 | 2.3709 | 2.3709 | 2.6238 | 2.6238 | 2019-11-14 13:00 | 2.2177 | 3.6344 | 5.966 | 5.966 | 5.966 | 5.966
2021-09-17 | 1.7892 | 2.2156 | 2.2509 | 2.4021 | 2.3416 | 2.4929 | 1.1546 | 1.749 | 2.0822 | 2.0822 | 2.3044 | 2.3044 | 2019-11-14 14:00 | 2.1415 | 3.5095 | 5.7609 | 5.7609 | 5.7609 | 5.7609
2021-09-17 01:00 | 1.7547 | 2.173 | 2.2076 | 2.3559 | 2.2966 | 2.4449 | 0.9432 | 1.4288 | 1.701 | 1.701 | 1.8825 | 1.8825 | 2019-11-14 15:00 | 2.1644 | 3.547 | 5.8224 | 5.8224 | 5.8224 | 5.8224
2021-09-17 02:00 | 1.6719 | 2.0703 | 2.1033 | 2.2446 | 2.1881 | 2.3294 | 0.91743 | 1.3897 | 1.6545 | 1.6545 | 1.8311 | 1.8311 | 2019-11-14 16:00 | 2.172 | 3.5595 | 5.8429 | 5.8429 | 5.8429 | 5.8429
2021-09-17 03:00 | 1.6633 | 2.0597 | 2.0925 | 2.2331 | 2.1769 | 2.3175 | 0.91452 | 1.3853 | 1.6493 | 1.6493 | 1.8253 | 1.8253 | 2019-11-14 17:00 | 2.1186 | 3.4721 | 5.6994 | 5.6994 | 5.6994 | 5.6994
2021-09-17 04:00 | 1.709 | 2.1163 | 2.15 | 2.2945 | 2.2367 | 2.3812 | 0.88594 | 1.342 | 1.5978 | 1.5978 | 1.7682 | 1.7682 | 2019-11-14 18:00 | 1.8748 | 3.0724 | 5.0434 | 5.0434 | 5.0434 | 5.0434
2021-09-17 05:00 | 1.8919 | 2.3428 | 2.3802 | 2.5401 | 2.4761 | 2.636 | 0.92881 | 1.407 | 1.6751 | 1.6751 | 1.8538 | 1.8538 | 2019-11-14 19:00 | 1.8138 | 2.9725 | 4.8794 | 4.8794 | 4.8794 | 4.8794
2021-09-17 06:00 | 2.3892 | 2.9586 | 3.0058 | 3.2077 | 3.1269 | 3.3289 | 1.0916 | 1.6536 | 1.9686 | 1.9686 | 2.1787 | 2.1787 | 2019-11-14 20:00 | 1.7528 | 2.8726 | 4.7154 | 4.7154 | 4.7154 | 4.7154
2021-09-17 07:00 | 2.4463 | 3.0294 | 3.0777 | 3.2845 | 3.2017 | 3.4085 | 1.3003 | 1.9698 | 2.3451 | 2.3451 | 2.5953 | 2.5953 | 2019-11-14 21:00 | 1.6538 | 2.7102 | 4.4488 | 4.4488 | 4.4488 | 4.4488
2021-09-17 08:00 | 2.3892 | 2.9586 | 3.0058 | 3.2077 | 3.1269 | 3.3289 | 1.3718 | 2.078 | 2.4739 | 2.4739 | 2.7379 | 2.7379 | 2019-11-14 22:00 | 1.5394 | 2.5229 | 4.1413 | 4.1413 | 4.1413 | 4.1413
2021-09-17 09:00 | 2.2834 | 2.8277 | 2.8727 | 3.0657 | 2.9885 | 3.1816 | 1.2775 | 1.9351 | 2.3039 | 2.3039 | 2.5497 | 2.5497 | 2019-11-14 23:00 | 1.4023 | 2.2981 | 3.7723 | 3.7723 | 3.7723 | 3.7723
2021-09-17 10:00 | 2.0691 | 2.5623 | 2.6031 | 2.778 | 2.708 | 2.8829 | 1.2775 | 1.9351 | 2.3039 | 2.3039 | 2.5497 | 2.5497 | 2019-11-15 | 1.2422 | 2.0358 | 3.3417 | 3.3417 | 3.3417 | 3.3417
2021-09-17 11:00 | 1.8891 | 2.3393 | 2.3766 | 2.5362 | 2.4724 | 2.6321 | 1.3318 | 2.0174 | 2.4018 | 2.4018 | 2.6581 | 2.6581 | 2019-11-15 01:00 | 1.2422 | 2.0358 | 3.3417 | 3.3417 | 3.3417 | 3.3417
2021-09-17 12:00 | 1.8576 | 2.3004 | 2.337 | 2.494 | 2.4312 | 2.5883 | 1.2432 | 1.8832 | 2.242 | 2.242 | 2.4812 | 2.4812 | 2019-11-15 02:00 | 1.1813 | 1.9359 | 3.1777 | 3.1777 | 3.1777 | 3.1777
2021-09-17 13:00 | 1.7319 | 2.1446 | 2.1788 | 2.3252 | 2.2666 | 2.413 | 1.2489 | 1.8918 | 2.2523 | 2.2523 | 2.4927 | 2.4927 | 2019-11-15 03:00 | 1.1431 | 1.8734 | 3.0752 | 3.0752 | 3.0752 | 3.0752
2021-09-17 14:00 | 1.8005 | 2.2296 | 2.2651 | 2.4173 | 2.3564 | 2.5086 | 1.1774 | 1.7836 | 2.1235 | 2.1235 | 2.3501 | 2.3501 | 2019-11-15 04:00 | 1.2575 | 2.0608 | 3.3828 | 3.3828 | 3.3828 | 3.3828
2021-09-17 15:00 | 1.8805 | 2.3287 | 2.3658 | 2.5247 | 2.4611 | 2.6201 | 1.266 | 1.9178 | 2.2832 | 2.2832 | 2.5269 | 2.5269 | 2019-11-15 05:00 | 1.2651 | 2.0732 | 3.4033 | 3.4033 | 3.4033 | 3.4033
2021-09-17 16:00 | 2.0234 | 2.5056 | 2.5455 | 2.7166 | 2.6482 | 2.8192 | 1.3318 | 2.0174 | 2.4018 | 2.4018 | 2.6581 | 2.6581 | 2019-11-15 06:00 | 1.4861 | 2.4354 | 3.9978 | 3.9978 | 3.9978 | 3.9978
2021-09-17 17:00 | 2.451 | 3.0352 | 3.0836 | 3.2908 | 3.2079 | 3.4151 | 1.5833 | 2.3983 | 2.8554 | 2.8554 | 3.16 | 3.16 | 2019-11-15 07:00 | 1.8443 | 3.0224 | 4.9614 | 4.9614 | 4.9614 | 4.9614
2021-09-17 18:00 | 2.6893 | 3.3302 | 3.3833 | 3.6106 | 3.5197 | 3.747 | 1.7833 | 2.7014 | 3.2161 | 3.2161 | 3.5593 | 3.5593 | 2019-11-15 08:00 | 1.9738 | 3.2348 | 5.3099 | 5.3099 | 5.3099 | 5.3099
2021-09-17 19:00 | 2.6092 | 3.2311 | 3.2826 | 3.5032 | 3.4149 | 3.6355 | 1.7062 | 2.5845 | 3.077 | 3.077 | 3.4053 | 3.4053 | 2019-11-15 09:00 | 1.9815 | 3.2472 | 5.3304 | 5.3304 | 5.3304 | 5.3304
2021-09-17 20:00 | 2.4349 | 3.0153 | 3.0633 | 3.2691 | 3.1868 | 3.3926 | 1.5718 | 2.381 | 2.8347 | 2.8347 | 3.1372 | 3.1372 | 2019-11-15 10:00 | 2.0882 | 3.4221 | 5.6174 | 5.6174 | 5.6174 | 5.6174
2021-09-17 21:00 | 2.2663 | 2.8064 | 2.8512 | 3.0427 | 2.9661 | 3.1577 | 1.569 | 2.3767 | 2.8296 | 2.8296 | 3.1315 | 3.1315 | 2019-11-15 11:00 | 2.1263 | 3.4845 | 5.7199 | 5.7199 | 5.7199 | 5.7199
2021-09-17 22:00 | 2.0662 | 2.5587 | 2.5995 | 2.7741 | 2.7043 | 2.8789 | 1.3261 | 2.0087 | 2.3915 | 2.3915 | 2.6467 | 2.6467 | 2019-11-15 12:00 | 2.2025 | 3.6094 | 5.9249 | 5.9249 | 5.9249 | 5.9249
2021-09-17 23:00 | 1.9556 | 2.4217 | 2.4602 | 2.6256 | 2.5594 | 2.7247 | 1.2352 | 1.871 | 2.2276 | 2.2276 | 2.4653 | 2.4653 | 2019-11-15 13:00 | 2.2482 | 3.6844 | 6.048 | 6.048 | 6.048 | 6.048
2021-09-18 | 1.7319 | 2.1447 | 2.1788 | 2.3252 | 2.2667 | 2.4131 | 1.0261 | 1.5543 | 1.8505 | 1.8505 | 2.0479 | 2.0479 | 2019-11-15 14:00 | 2.1796 | 3.572 | 5.8634 | 5.8634 | 5.8634 | 5.8634
2021-09-18 01:00 | 1.5861 | 1.9642 | 1.9954 | 2.1295 | 2.0759 | 2.21 | 0.92023 | 1.394 | 1.6596 | 1.6596 | 1.8367 | 1.8367 | 2019-11-15 15:00 | 2.2482 | 3.6844 | 6.048 | 6.048 | 6.048 | 6.048
2021-09-18 02:00 | 1.5433 | 1.9111 | 1.9415 | 2.072 | 2.0198 | 2.1502 | 0.88022 | 1.3334 | 1.5874 | 1.5874 | 1.7568 | 1.7568 | 2019-11-15 16:00 | 2.2482 | 3.6844 | 6.048 | 6.048 | 6.048 | 6.048
2021-09-18 03:00 | 1.5347 | 1.9005 | 1.9307 | 2.0605 | 2.0086 | 2.1383 | 0.82592 | 1.2511 | 1.4895 | 1.4895 | 1.6485 | 1.6485 | 2019-11-15 17:00 | 2.0501 | 3.3597 | 5.5149 | 5.5149 | 5.5149 | 5.5149
2021-09-18 04:00 | 1.5175 | 1.8792 | 1.9092 | 2.0374 | 1.9861 | 2.1144 | 0.80878 | 1.2251 | 1.4586 | 1.4586 | 1.6142 | 1.6142 | 2019-11-15 18:00 | 1.9205 | 3.1473 | 5.1664 | 5.1664 | 5.1664 | 5.1664
2021-09-18 05:00 | 1.6685 | 2.0661 | 2.0991 | 2.2401 | 2.1837 | 2.3247 | 0.88022 | 1.3334 | 1.5874 | 1.5874 | 1.7568 | 1.7568 | 2019-11-15 19:00 | 1.8671 | 3.0599 | 5.0229 | 5.0229 | 5.0229 | 5.0229
2021-09-18 06:00 | 1.8519 | 2.2933 | 2.3298 | 2.4864 | 2.4237 | 2.5803 | 0.96596 | 1.4632 | 1.7421 | 1.7421 | 1.928 | 1.928 | 2019-11-15 20:00 | 1.7681 | 2.8975 | 4.7564 | 4.7564 | 4.7564 | 4.7564
2021-09-18 07:00 | 2.0062 | 2.4844 | 2.524 | 2.6936 | 2.6257 | 2.7953 | 1.026 | 1.5542 | 1.8503 | 1.8503 | 2.0477 | 2.0477 | 2019-11-15 21:00 | 1.6385 | 2.6852 | 4.4078 | 4.4078 | 4.4078 | 4.4078
2021-09-18 08:00 | 2.2206 | 2.7498 | 2.7936 | 2.9813 | 2.9063 | 3.094 | 1.2632 | 1.9135 | 2.2781 | 2.2781 | 2.5212 | 2.5212 | 2019-11-15 22:00 | 1.5699 | 2.5728 | 4.2233 | 4.2233 | 4.2233 | 4.2233
2021-09-18 09:00 | 2.4582 | 3.0441 | 3.0926 | 3.3004 | 3.2173 | 3.4251 | 1.3832 | 2.0953 | 2.4946 | 2.4946 | 2.7607 | 2.7607 | 2019-11-15 23:00 | 1.4785 | 2.4229 | 3.9773 | 3.9773 | 3.9773 | 3.9773
2021-09-18 10:00 | 2.4749 | 3.0648 | 3.1136 | 3.3228 | 3.2391 | 3.4484 | 1.5918 | 2.4113 | 2.8708 | 2.8708 | 3.1771 | 3.1771 | 2019-11-16 | 1.3413 | 2.1981 | 3.6083 | 3.6083 | 3.6083 | 3.6083
2021-09-18 11:00 | 2.3435 | 2.902 | 2.9482 | 3.1463 | 3.0671 | 3.2652 | 1.5775 | 2.3897 | 2.845 | 2.845 | 3.1486 | 3.1486 | 2019-11-16 01:00 | 1.2879 | 2.1107 | 3.4648 | 3.4648 | 3.4648 | 3.4648
2021-09-18 12:00 | 2.2863 | 2.8312 | 2.8763 | 3.0696 | 2.9923 | 3.1855 | 1.5347 | 2.3247 | 2.7677 | 2.7677 | 3.0631 | 3.0631 | 2019-11-16 02:00 | 1.2575 | 2.0608 | 3.3828 | 3.3828 | 3.3828 | 3.3828
2021-09-18 13:00 | 2.0691 | 2.5623 | 2.6031 | 2.778 | 2.708 | 2.8829 | 1.5118 | 2.2901 | 2.7265 | 2.7265 | 3.0174 | 3.0174 | 2019-11-16 03:00 | 1.2422 | 2.0358 | 3.3417 | 3.3417 | 3.3417 | 3.3417
2021-09-18 14:00 | 2.132 | 2.6401 | 2.6822 | 2.8624 | 2.7903 | 2.9705 | 1.4632 | 2.2165 | 2.6389 | 2.6389 | 2.9205 | 2.9205 | 2019-11-16 04:00 | 1.227 | 2.0108 | 3.3007 | 3.3007 | 3.3007 | 3.3007
2021-09-18 15:00 | 2.0662 | 2.5587 | 2.5995 | 2.7741 | 2.7043 | 2.8789 | 1.3232 | 2.0044 | 2.3863 | 2.3863 | 2.641 | 2.641 | 2019-11-16 05:00 | 1.4175 | 2.323 | 3.8133 | 3.8133 | 3.8133 | 3.8133
2021-09-18 16:00 | 2.1863 | 2.7074 | 2.7505 | 2.9353 | 2.8614 | 3.0462 | 1.3861 | 2.0996 | 2.4997 | 2.4997 | 2.7664 | 2.7664 | 2019-11-16 06:00 | 1.3565 | 2.2231 | 3.6493 | 3.6493 | 3.6493 | 3.6493
2021-09-18 17:00 | 2.5807 | 3.1957 | 3.2466 | 3.4648 | 3.3775 | 3.5957 | 1.6176 | 2.4503 | 2.9172 | 2.9172 | 3.2285 | 3.2285 | 2019-11-16 07:00 | 1.5775 | 2.5853 | 4.2438 | 4.2438 | 4.2438 | 4.2438
2021-09-18 18:00 | 2.8865 | 3.5744 | 3.6314 | 3.8754 | 3.7778 | 4.0218 | 1.8548 | 2.8096 | 3.345 | 3.345 | 3.7019 | 3.7019 | 2019-11-16 08:00 | 1.7986 | 2.9475 | 4.8384 | 4.8384 | 4.8384 | 4.8384
2021-09-18 19:00 | 2.8207 | 3.493 | 3.5487 | 3.7871 | 3.6917 | 3.9302 | 1.849 | 2.8009 | 3.3347 | 3.3347 | 3.6905 | 3.6905 | 2019-11-16 09:00 | 1.7986 | 2.9475 | 4.8384 | 4.8384 | 4.8384 | 4.8384
2021-09-18 20:00 | 2.6978 | 3.3408 | 3.3941 | 3.6221 | 3.5309 | 3.7589 | 1.7376 | 2.6321 | 3.1337 | 3.1337 | 3.468 | 3.468 | 2019-11-16 10:00 | 1.8824 | 3.0849 | 5.0639 | 5.0639 | 5.0639 | 5.0639
2021-09-18 21:00 | 2.4378 | 3.0188 | 3.0669 | 3.2729 | 3.1905 | 3.3966 | 1.5976 | 2.42 | 2.8811 | 2.8811 | 3.1885 | 3.1885 | 2019-11-16 11:00 | 2.0272 | 3.3222 | 5.4534 | 5.4534 | 5.4534 | 5.4534
2021-09-18 22:00 | 2.3177 | 2.8702 | 2.9159 | 3.1118 | 3.0334 | 3.2293 | 1.4747 | 2.2338 | 2.6595 | 2.6595 | 2.9433 | 2.9433 | 2019-11-16 12:00 | 2.0043 | 3.2847 | 5.3919 | 5.3919 | 5.3919 | 5.3919
2021-09-18 23:00 | 2.1606 | 2.6755 | 2.7181 | 2.9008 | 2.8277 | 3.0103 | 1.2317 | 1.8659 | 2.2214 | 2.2214 | 2.4584 | 2.4584 | 2019-11-16 13:00 | 1.8976 | 3.1099 | 5.1049 | 5.1049 | 5.1049 | 5.1049
2021-09-19 | 1.8693 | 2.3148 | 2.3517 | 2.5097 | 2.4465 | 2.6045 | 1.1146 | 1.6884 | 2.0101 | 2.0101 | 2.2246 | 2.2246 | 2019-11-16 14:00 | 1.9434 | 3.1848 | 5.2279 | 5.2279 | 5.2279 | 5.2279
2021-09-19 01:00 | 1.7233 | 2.134 | 2.168 | 2.3137 | 2.2554 | 2.4011 | 1.0069 | 1.5253 | 1.816 | 1.816 | 2.0097 | 2.0097 | 2019-11-16 15:00 | 1.8976 | 3.1099 | 5.1049 | 5.1049 | 5.1049 | 5.1049
2021-09-19 02:00 | 1.6633 | 2.0597 | 2.0925 | 2.2331 | 2.1769 | 2.3175 | 0.92317 | 1.3984 | 1.6649 | 1.6649 | 1.8425 | 1.8425 | 2019-11-16 16:00 | 1.9357 | 3.1723 | 5.2074 | 5.2074 | 5.2074 | 5.2074
2021-09-19 03:00 | 1.6519 | 2.0456 | 2.0781 | 2.2178 | 2.1619 | 2.3016 | 0.89737 | 1.3593 | 1.6184 | 1.6184 | 1.7911 | 1.7911 | 2019-11-16 17:00 | 1.8214 | 2.985 | 4.8999 | 4.8999 | 4.8999 | 4.8999
2021-09-19 04:00 | 1.709 | 2.1163 | 2.15 | 2.2945 | 2.2367 | 2.3812 | 0.89169 | 1.3507 | 1.6081 | 1.6081 | 1.7797 | 1.7797 | 2019-11-16 18:00 | 1.6766 | 2.7477 | 4.5103 | 4.5103 | 4.5103 | 4.5103
2021-09-19 05:00 | 1.809 | 2.2402 | 2.2759 | 2.4288 | 2.3676 | 2.5206 | 0.96599 | 1.4633 | 1.7421 | 1.7421 | 1.928 | 1.928 | 2019-11-16 19:00 | 1.6004 | 2.6228 | 4.3053 | 4.3053 | 4.3053 | 4.3053
2021-09-19 06:00 | 1.978 | 2.4495 | 2.4885 | 2.6557 | 2.5888 | 2.756 | 0.97739 | 1.4806 | 1.7627 | 1.7627 | 1.9508 | 1.9508 | 2019-11-16 20:00 | 1.6004 | 2.6228 | 4.3053 | 4.3053 | 4.3053 | 4.3053
2021-09-19 07:00 | 1.9977 | 2.4738 | 2.5132 | 2.682 | 2.6145 | 2.7834 | 1.0944 | 1.6578 | 1.9737 | 1.9737 | 2.1843 | 2.1843 | 2019-11-16 21:00 | 1.509 | 2.4729 | 4.0593 | 4.0593 | 4.0593 | 4.0593
2021-09-19 08:00 | 2.1463 | 2.6578 | 2.7001 | 2.8816 | 2.809 | 2.9904 | 1.1574 | 1.7533 | 2.0874 | 2.0874 | 2.3101 | 2.3101 | 2019-11-16 22:00 | 1.4099 | 2.3105 | 3.7928 | 3.7928 | 3.7928 | 3.7928
2021-09-19 09:00 | 2.2892 | 2.8348 | 2.8799 | 3.0734 | 2.996 | 3.1895 | 1.4245 | 2.1579 | 2.5691 | 2.5691 | 2.8432 | 2.8432 | 2019-11-16 23:00 | 1.3565 | 2.2231 | 3.6493 | 3.6493 | 3.6493 | 3.6493
2021-09-19 10:00 | 2.232 | 2.764 | 2.808 | 2.9967 | 2.9212 | 3.1099 | 1.4261 | 2.1602 | 2.5719 | 2.5719 | 2.8463 | 2.8463 | 2019-11-17 | 1.3184 | 2.1607 | 3.5468 | 3.5468 | 3.5468 | 3.5468
2021-09-19 11:00 | 2.1377 | 2.6472 | 2.6894 | 2.8701 | 2.7978 | 2.9785 | 1.4604 | 2.2122 | 2.6337 | 2.6337 | 2.9148 | 2.9148 | 2019-11-17 01:00 | 1.227 | 2.0108 | 3.3007 | 3.3007 | 3.3007 | 3.3007
2021-09-19 12:00 | 2.1005 | 2.6012 | 2.6426 | 2.8202 | 2.7492 | 2.9267 | 1.4689 | 2.2252 | 2.6492 | 2.6492 | 2.9319 | 2.9319 | 2019-11-17 02:00 | 1.1736 | 1.9234 | 3.1572 | 3.1572 | 3.1572 | 3.1572
2021-09-19 13:00 | 2.0148 | 2.495 | 2.5348 | 2.7051 | 2.6369 | 2.8073 | 1.3718 | 2.078 | 2.4739 | 2.4739 | 2.7379 | 2.7379 | 2019-11-17 03:00 | 1.166 | 1.9109 | 3.1367 | 3.1367 | 3.1367 | 3.1367
2021-09-19 14:00 | 1.9205 | 2.3782 | 2.4161 | 2.5785 | 2.5135 | 2.6759 | 1.3718 | 2.078 | 2.4739 | 2.4739 | 2.7379 | 2.7379 | 2019-11-17 04:00 | 1.1889 | 1.9483 | 3.1982 | 3.1982 | 3.1982 | 3.1982
2021-09-19 15:00 | 1.9634 | 2.4313 | 2.47 | 2.636 | 2.5696 | 2.7356 | 1.3889 | 2.104 | 2.5049 | 2.5049 | 2.7722 | 2.7722 | 2019-11-17 05:00 | 1.2041 | 1.9733 | 3.2392 | 3.2392 | 3.2392 | 3.2392
2021-09-19 16:00 | 2.0948 | 2.5941 | 2.6354 | 2.8125 | 2.7417 | 2.9188 | 1.4518 | 2.1992 | 2.6183 | 2.6183 | 2.8976 | 2.8976 | 2019-11-17 06:00 | 1.3718 | 2.2481 | 3.6903 | 3.6903 | 3.6903 | 3.6903
2021-09-19 17:00 | 2.6763 | 3.3141 | 3.3669 | 3.5932 | 3.5027 | 3.7289 | 1.6864 | 2.5545 | 3.0413 | 3.0413 | 3.3658 | 3.3658 | 2019-11-17 07:00 | 1.5928 | 2.6103 | 4.2848 | 4.2848 | 4.2848 | 4.2848
2021-09-19 18:00 | 3.0236 | 3.7443 | 3.8039 | 4.0595 | 3.9573 | 4.2129 | 1.9548 | 2.9611 | 3.5254 | 3.5254 | 3.9015 | 3.9015 | 2019-11-17 08:00 | 1.7452 | 2.8601 | 4.6949 | 4.6949 | 4.6949 | 4.6949
2021-09-19 19:00 | 2.9293 | 3.6275 | 3.6853 | 3.9329 | 3.8339 | 4.0815 | 1.9148 | 2.9005 | 3.4532 | 3.4532 | 3.8217 | 3.8217 | 2019-11-17 09:00 | 1.8214 | 2.985 | 4.8999 | 4.8999 | 4.8999 | 4.8999
2021-09-19 20:00 | 2.5892 | 3.2064 | 3.2574 | 3.4763 | 3.3888 | 3.6076 | 1.6776 | 2.5412 | 3.0254 | 3.0254 | 3.3483 | 3.3483 | 2019-11-17 10:00 | 1.9129 | 3.1348 | 5.1459 | 5.1459 | 5.1459 | 5.1459
2021-09-19 21:00 | 2.5035 | 3.1002 | 3.1496 | 3.3612 | 3.2765 | 3.4882 | 1.5947 | 2.4157 | 2.876 | 2.876 | 3.1828 | 3.1828 | 2019-11-17 11:00 | 1.9738 | 3.2348 | 5.3099 | 5.3099 | 5.3099 | 5.3099
2021-09-19 22:00 | 2.2434 | 2.7781 | 2.8224 | 3.012 | 2.9362 | 3.1258 | 1.4204 | 2.1516 | 2.5616 | 2.5616 | 2.8349 | 2.8349 | 2019-11-17 12:00 | 1.8976 | 3.1099 | 5.1049 | 5.1049 | 5.1049 | 5.1049
2021-09-19 23:00 | 2.1377 | 2.6472 | 2.6894 | 2.8701 | 2.7978 | 2.9785 | 1.246 | 1.8875 | 2.2472 | 2.2472 | 2.4869 | 2.4869 | 2019-11-17 13:00 | 1.8748 | 3.0724 | 5.0434 | 5.0434 | 5.0434 | 5.0434
2021-09-20 | 1.7776 | 2.2013 | 2.2363 | 2.3866 | 2.3265 | 2.4768 | 1.1101 | 1.6816 | 2.002 | 2.002 | 2.2157 | 2.2157 | 2019-11-17 14:00 | 1.9205 | 3.1473 | 5.1664 | 5.1664 | 5.1664 | 5.1664
2021-09-20 01:00 | 1.6547 | 2.0491 | 2.0817 | 2.2216 | 2.1657 | 2.3055 | 0.88997 | 1.3481 | 1.605 | 1.605 | 1.7763 | 1.7763 | 2019-11-17 15:00 | 1.9129 | 3.1348 | 5.1459 | 5.1459 | 5.1459 | 5.1459
2021-09-20 02:00 | 1.6233 | 2.0102 | 2.0422 | 2.1794 | 2.1245 | 2.2617 | 0.88594 | 1.342 | 1.5978 | 1.5978 | 1.7682 | 1.7682 | 2019-11-17 16:00 | 1.9205 | 3.1473 | 5.1664 | 5.1664 | 5.1664 | 5.1664
2021-09-20 03:00 | 1.6576 | 2.0526 | 2.0853 | 2.2254 | 2.1694 | 2.3095 | 0.86022 | 1.3031 | 1.5514 | 1.5514 | 1.7169 | 1.7169 | 2019-11-17 17:00 | 1.8443 | 3.0224 | 4.9614 | 4.9614 | 4.9614 | 4.9614
2021-09-20 04:00 | 1.7233 | 2.134 | 2.168 | 2.3137 | 2.2554 | 2.4011 | 0.88308 | 1.3377 | 1.5926 | 1.5926 | 1.7625 | 1.7625 | 2019-11-17 18:00 | 1.6538 | 2.7102 | 4.4488 | 4.4488 | 4.4488 | 4.4488
2021-09-20 05:00 | 1.9388 | 2.401 | 2.4392 | 2.6031 | 2.5375 | 2.7014 | 0.90595 | 1.3723 | 1.6338 | 1.6338 | 1.8082 | 1.8082 | 2019-11-17 19:00 | 1.5852 | 2.5978 | 4.2643 | 4.2643 | 4.2643 | 4.2643
2021-09-20 06:00 | 2.2006 | 2.7251 | 2.7685 | 2.9545 | 2.8801 | 3.0661 | 1.0283 | 1.5576 | 1.8545 | 1.8545 | 2.0523 | 2.0523 | 2019-11-17 20:00 | 1.6461 | 2.6977 | 4.4283 | 4.4283 | 4.4283 | 4.4283
2021-09-20 07:00 | 2.4035 | 2.9763 | 3.0237 | 3.2269 | 3.1456 | 3.3488 | 1.2603 | 1.9091 | 2.2729 | 2.2729 | 2.5155 | 2.5155 | 2019-11-17 21:00 | 1.5242 | 2.4979 | 4.1003 | 4.1003 | 4.1003 | 4.1003
2021-09-20 08:00 | 2.4435 | 3.0259 | 3.0741 | 3.2806 | 3.198 | 3.4046 | 1.3603 | 2.0607 | 2.4533 | 2.4533 | 2.7151 | 2.7151 | 2019-11-17 22:00 | 1.4099 | 2.3105 | 3.7928 | 3.7928 | 3.7928 | 3.7928
2021-09-20 09:00 | 2.2492 | 2.7852 | 2.8296 | 3.0197 | 2.9437 | 3.1338 | 1.315 | 1.992 | 2.3716 | 2.3716 | 2.6247 | 2.6247 | 2019-11-17 23:00 | 1.3184 | 2.1607 | 3.5468 | 3.5468 | 3.5468 | 3.5468
2021-09-20 10:00 | 2.2177 | 2.7463 | 2.79 | 2.9775 | 2.9025 | 3.09 | 1.3089 | 1.9827 | 2.3606 | 2.3606 | 2.6124 | 2.6124 | 2019-11-18 | 1.2956 | 2.1232 | 3.4853 | 3.4853 | 3.4853 | 3.4853
2021-09-20 11:00 | 2.132 | 2.6401 | 2.6822 | 2.8624 | 2.7903 | 2.9705 | 1.3889 | 2.104 | 2.5049 | 2.5049 | 2.7722 | 2.7722 | 2019-11-18 01:00 | 1.2194 | 1.9983 | 3.2802 | 3.2802 | 3.2802 | 3.2802
2021-09-20 12:00 | 2.2549 | 2.7923 | 2.8368 | 3.0274 | 2.9511 | 3.1417 | 1.5804 | 2.394 | 2.8502 | 2.8502 | 3.1543 | 3.1543 | 2019-11-18 02:00 | 1.1889 | 1.9483 | 3.1982 | 3.1982 | 3.1982 | 3.1982
2021-09-20 13:00 | 2.4521 | 3.0365 | 3.0849 | 3.2921 | 3.2092 | 3.4165 | 1.6833 | 2.5499 | 3.0357 | 3.0357 | 3.3597 | 3.3597 | 2019-11-18 03:00 | 1.227 | 2.0108 | 3.3007 | 3.3007 | 3.3007 | 3.3007
2021-09-20 14:00 | 2.6664 | 3.3019 | 3.3545 | 3.5799 | 3.4897 | 3.7151 | 1.6376 | 2.4806 | 2.9533 | 2.9533 | 3.2684 | 3.2684 | 2019-11-18 04:00 | 1.2194 | 1.9983 | 3.2802 | 3.2802 | 3.2802 | 3.2802
2021-09-20 15:00 | 2.7378 | 3.3904 | 3.4444 | 3.6758 | 3.5833 | 3.8147 | 1.7033 | 2.5802 | 3.0718 | 3.0718 | 3.3996 | 3.3996 | 2019-11-18 05:00 | 1.2727 | 2.0857 | 3.4238 | 3.4238 | 3.4238 | 3.4238
2021-09-20 16:00 | 2.7654 | 3.4245 | 3.479 | 3.7128 | 3.6193 | 3.8531 | 1.7433 | 2.6408 | 3.144 | 3.144 | 3.4794 | 3.4794 | 2019-11-18 06:00 | 1.5166 | 2.4854 | 4.0798 | 4.0798 | 4.0798 | 4.0798
2021-09-20 17:00 | 3.2894 | 4.0734 | 4.1383 | 4.4164 | 4.3051 | 4.5832 | 1.7956 | 2.7199 | 3.2382 | 3.2382 | 3.5837 | 3.5837 | 2019-11-18 07:00 | 1.8595 | 3.0474 | 5.0024 | 5.0024 | 5.0024 | 5.0024
2021-09-20 18:00 | 3.6209 | 4.484 | 4.5554 | 4.8615 | 4.739 | 5.0451 | 2.0491 | 3.104 | 3.6955 | 3.6955 | 4.0898 | 4.0898 | 2019-11-18 08:00 | 2.0577 | 3.3721 | 5.5354 | 5.5354 | 5.5354 | 5.5354
2021-09-20 19:00 | 3.4752 | 4.3035 | 4.372 | 4.6658 | 4.5483 | 4.842 | 2.072 | 3.1386 | 3.7367 | 3.7367 | 4.1354 | 4.1354 | 2019-11-18 09:00 | 2.1644 | 3.547 | 5.8224 | 5.8224 | 5.8224 | 5.8224
2021-09-20 20:00 | 3.1065 | 3.8469 | 3.9082 | 4.1708 | 4.0658 | 4.3284 | 1.9234 | 2.9135 | 3.4687 | 3.4687 | 3.8388 | 3.8388 | 2019-11-18 10:00 | 2.0882 | 3.4221 | 5.6174 | 5.6174 | 5.6174 | 5.6174
2021-09-20 21:00 | 2.8194 | 3.4914 | 3.547 | 3.7853 | 3.69 | 3.9283 | 1.9005 | 2.8789 | 3.4275 | 3.4275 | 3.7932 | 3.7932 | 2019-11-18 11:00 | 2.1644 | 3.547 | 5.8224 | 5.8224 | 5.8224 | 5.8224
2021-09-20 22:00 | 2.5149 | 3.1143 | 3.164 | 3.3765 | 3.2915 | 3.5041 | 1.549 | 2.3464 | 2.7935 | 2.7935 | 3.0916 | 3.0916 | 2019-11-18 12:00 | 2.1872 | 3.5845 | 5.8839 | 5.8839 | 5.8839 | 5.8839
2021-09-20 23:00 | 2.2013 | 2.7259 | 2.7694 | 2.9554 | 2.881 | 3.0671 | 1.4089 | 2.1343 | 2.541 | 2.541 | 2.8121 | 2.8121 | 2019-11-18 13:00 | 2.1949 | 3.597 | 5.9044 | 5.9044 | 5.9044 | 5.9044
2021-09-21 | 1.9319 | 2.3924 | 2.4305 | 2.5938 | 2.5285 | 2.6918 | 1.1291 | 1.7104 | 2.0363 | 2.0363 | 2.2536 | 2.2536 | 2019-11-18 14:00 | 2.2177 | 3.6344 | 5.966 | 5.966 | 5.966 | 5.966
2021-09-21 01:00 | 1.8376 | 2.2756 | 2.3118 | 2.4672 | 2.405 | 2.5604 | 1.0475 | 1.5868 | 1.8892 | 1.8892 | 2.0908 | 2.0908 | 2019-11-18 15:00 | 2.2253 | 3.6469 | 5.9865 | 5.9865 | 5.9865 | 5.9865
2021-09-21 02:00 | 1.8576 | 2.3004 | 2.337 | 2.494 | 2.4312 | 2.5883 | 0.97947 | 1.4837 | 1.7664 | 1.7664 | 1.9549 | 1.9549 | 2019-11-18 16:00 | 2.2177 | 3.6344 | 5.966 | 5.966 | 5.966 | 5.966
2021-09-21 03:00 | 1.8262 | 2.2614 | 2.2975 | 2.4518 | 2.3901 | 2.5445 | 0.98025 | 1.4849 | 1.7678 | 1.7678 | 1.9565 | 1.9565 | 2019-11-18 17:00 | 2.1644 | 3.547 | 5.8224 | 5.8224 | 5.8224 | 5.8224
2021-09-21 04:00 | 1.8748 | 2.3216 | 2.3586 | 2.5171 | 2.4537 | 2.6121 | 0.96882 | 1.4676 | 1.7472 | 1.7472 | 1.9337 | 1.9337 | 2019-11-18 18:00 | 2.0043 | 3.2847 | 5.3919 | 5.3919 | 5.3919 | 5.3919
2021-09-21 05:00 | 2.1621 | 2.6775 | 2.7201 | 2.9029 | 2.8298 | 3.0125 | 1.0805 | 1.6368 | 1.9487 | 1.9487 | 2.1567 | 2.1567 | 2019-11-18 19:00 | 1.9053 | 3.1224 | 5.1254 | 5.1254 | 5.1254 | 5.1254
2021-09-21 06:00 | 2.7979 | 3.4647 | 3.5199 | 3.7564 | 3.6618 | 3.8983 | 1.2232 | 1.8529 | 2.2059 | 2.2059 | 2.4413 | 2.4413 | 2019-11-18 20:00 | 1.8671 | 3.0599 | 5.0229 | 5.0229 | 5.0229 | 5.0229
2021-09-21 07:00 | 3.0694 | 3.8009 | 3.8615 | 4.1209 | 4.0171 | 4.2766 | 1.4224 | 2.1547 | 2.5653 | 2.5653 | 2.839 | 2.839 | 2019-11-18 21:00 | 1.8138 | 2.9725 | 4.8794 | 4.8794 | 4.8794 | 4.8794
2021-09-21 08:00 | 2.9379 | 3.6381 | 3.6961 | 3.9444 | 3.8451 | 4.0934 | 1.5547 | 2.355 | 2.8038 | 2.8038 | 3.103 | 3.103 | 2019-11-18 22:00 | 1.5166 | 2.4854 | 4.0798 | 4.0798 | 4.0798 | 4.0798
2021-09-21 09:00 | 3.0351 | 3.7584 | 3.8183 | 4.0749 | 3.9723 | 4.2288 | 1.5861 | 2.4027 | 2.8605 | 2.8605 | 3.1657 | 3.1657 | 2019-11-18 23:00 | 1.448 | 2.373 | 3.8953 | 3.8953 | 3.8953 | 3.8953
2021-09-21 10:00 | 3.1208 | 3.8646 | 3.9262 | 4.19 | 4.0845 | 4.3483 | 1.6719 | 2.5325 | 3.0151 | 3.0151 | 3.3368 | 3.3368 | 2019-11-19 | 1.2956 | 2.1232 | 3.4853 | 3.4853 | 3.4853 | 3.4853
2021-09-21 11:00 | 2.9608 | 3.6664 | 3.7248 | 3.9751 | 3.875 | 4.1253 | 1.5861 | 2.4027 | 2.8605 | 2.8605 | 3.1657 | 3.1657 | 2019-11-19 01:00 | 1.2956 | 2.1232 | 3.4853 | 3.4853 | 3.4853 | 3.4853
2021-09-21 12:00 | 2.5549 | 3.1639 | 3.2143 | 3.4303 | 3.3439 | 3.5598 | 1.4947 | 2.2641 | 2.6956 | 2.6956 | 2.9832 | 2.9832 | 2019-11-19 02:00 | 1.2422 | 2.0358 | 3.3417 | 3.3417 | 3.3417 | 3.3417
2021-09-21 13:00 | 2.5921 | 3.2099 | 3.261 | 3.4801 | 3.3925 | 3.6116 | 1.5433 | 2.3377 | 2.7832 | 2.7832 | 3.0802 | 3.0802 | 2019-11-19 03:00 | 1.2041 | 1.9733 | 3.2392 | 3.2392 | 3.2392 | 3.2392
2021-09-21 14:00 | 2.2234 | 2.7534 | 2.7972 | 2.9852 | 2.91 | 3.0979 | 1.4287 | 2.1643 | 2.5767 | 2.5767 | 2.8516 | 2.8516 | 2019-11-19 04:00 | 1.2194 | 1.9983 | 3.2802 | 3.2802 | 3.2802 | 3.2802
2021-09-21 15:00 | 2.2749 | 2.8171 | 2.8619 | 3.0542 | 2.9773 | 3.1696 | 1.4604 | 2.2122 | 2.6337 | 2.6337 | 2.9148 | 2.9148 | 2019-11-19 05:00 | 1.2879 | 2.1107 | 3.4648 | 3.4648 | 3.4648 | 3.4648
2021-09-21 16:00 | 2.4349 | 3.0153 | 3.0633 | 3.2691 | 3.1868 | 3.3926 | 1.5056 | 2.2806 | 2.7152 | 2.7152 | 3.0049 | 3.0049 | 2019-11-19 06:00 | 1.5623 | 2.5603 | 4.2028 | 4.2028 | 4.2028 | 4.2028
2021-09-21 17:00 | 2.8522 | 3.532 | 3.5882 | 3.8293 | 3.7329 | 3.974 | 1.729 | 2.6191 | 3.1182 | 3.1182 | 3.4509 | 3.4509 | 2019-11-19 07:00 | 1.9357 | 3.1723 | 5.2074 | 5.2074 | 5.2074 | 5.2074
2021-09-21 18:00 | 3.3209 | 4.1124 | 4.1779 | 4.4586 | 4.3463 | 4.627 | 1.9576 | 2.9655 | 3.5305 | 3.5305 | 3.9073 | 3.9073 | 2019-11-19 08:00 | 2.1339 | 3.497 | 5.7404 | 5.7404 | 5.7404 | 5.7404
2021-09-21 19:00 | 3.2103 | 3.9754 | 4.0387 | 4.3101 | 4.2016 | 4.4729 | 2.0462 | 3.0997 | 3.6903 | 3.6903 | 4.0841 | 4.0841 | 2019-11-19 09:00 | 2.2482 | 3.6844 | 6.048 | 6.048 | 6.048 | 6.048
2021-09-21 20:00 | 3.0093 | 3.7266 | 3.786 | 4.0403 | 3.9386 | 4.193 | 1.9777 | 2.9958 | 3.5666 | 3.5666 | 3.9472 | 3.9472 | 2019-11-19 10:00 | 2.2406 | 3.6719 | 6.0275 | 6.0275 | 6.0275 | 6.0275
2021-09-21 21:00 | 2.7526 | 3.4087 | 3.463 | 3.6957 | 3.6026 | 3.8353 | 1.7547 | 2.6581 | 3.1646 | 3.1646 | 3.5023 | 3.5023 | 2019-11-19 11:00 | 2.3168 | 3.7968 | 6.2325 | 6.2325 | 6.2325 | 6.2325
2021-09-21 22:00 | 2.4932 | 3.0874 | 3.1366 | 3.3473 | 3.263 | 3.4738 | 1.5747 | 2.3854 | 2.8399 | 2.8399 | 3.1429 | 3.1429 | 2019-11-19 12:00 | 2.3549 | 3.8592 | 6.335 | 6.335 | 6.335 | 6.335
2021-09-21 23:00 | 2.2463 | 2.7817 | 2.826 | 3.0159 | 2.9399 | 3.1298 | 1.412 | 2.139 | 2.5466 | 2.5466 | 2.8183 | 2.8183 | 2019-11-19 13:00 | 2.3625 | 3.8717 | 6.3555 | 6.3555 | 6.3555 | 6.3555
2021-09-22 | 1.9805 | 2.4525 | 2.4916 | 2.659 | 2.5921 | 2.7595 | 1.1632 | 1.762 | 2.0977 | 2.0977 | 2.3215 | 2.3215 | 2019-11-19 14:00 | 2.4768 | 4.0591 | 6.663 | 6.663 | 6.663 | 6.663
2021-09-22 01:00 | 1.8776 | 2.3252 | 2.3622 | 2.5209 | 2.4574 | 2.6161 | 1.1517 | 1.7447 | 2.0771 | 2.0771 | 2.2987 | 2.2987 | 2019-11-19 15:00 | 2.4311 | 3.9841 | 6.54 | 6.54 | 6.54 | 6.54
2021-09-22 02:00 | 1.8319 | 2.2685 | 2.3046 | 2.4595 | 2.3976 | 2.5524 | 0.99454 | 1.5065 | 1.7936 | 1.7936 | 1.985 | 1.985 | 2019-11-19 16:00 | 2.4082 | 3.9467 | 6.4785 | 6.4785 | 6.4785 | 6.4785
2021-09-22 03:00 | 1.8148 | 2.2473 | 2.2831 | 2.4365 | 2.3751 | 2.5285 | 1.0003 | 1.5152 | 1.8039 | 1.8039 | 1.9964 | 1.9964 | 2019-11-19 17:00 | 2.3168 | 3.7968 | 6.2325 | 6.2325 | 6.2325 | 6.2325
2021-09-22 04:00 | 1.9291 | 2.3888 | 2.4269 | 2.59 | 2.5247 | 2.6878 | 1.0117 | 1.5325 | 1.8245 | 1.8245 | 2.0192 | 2.0192 | 2019-11-19 18:00 | 2.1034 | 3.4471 | 5.6584 | 5.6584 | 5.6584 | 5.6584
2021-09-22 05:00 | 2.1227 | 2.6286 | 2.6705 | 2.8499 | 2.7781 | 2.9576 | 1.0403 | 1.5758 | 1.8761 | 1.8761 | 2.0763 | 2.0763 | 2019-11-19 19:00 | 1.9586 | 3.2098 | 5.2689 | 5.2689 | 5.2689 | 5.2689
2021-09-22 06:00 | 2.694 | 3.336 | 3.3892 | 3.6169 | 3.5258 | 3.7535 | 1.2317 | 1.8659 | 2.2214 | 2.2214 | 2.4584 | 2.4584 | 2019-11-19 20:00 | 1.9205 | 3.1473 | 5.1664 | 5.1664 | 5.1664 | 5.1664
2021-09-22 07:00 | 2.9722 | 3.6806 | 3.7392 | 3.9905 | 3.89 | 4.1412 | 1.4204 | 2.1516 | 2.5616 | 2.5616 | 2.8349 | 2.8349 | 2019-11-19 21:00 | 1.8519 | 3.0349 | 4.9819 | 4.9819 | 4.9819 | 4.9819
2021-09-22 08:00 | 2.9808 | 3.6912 | 3.75 | 4.002 | 3.9012 | 4.1532 | 1.5433 | 2.3377 | 2.7832 | 2.7832 | 3.0802 | 3.0802 | 2019-11-19 22:00 | 1.5699 | 2.5728 | 4.2233 | 4.2233 | 4.2233 | 4.2233
2021-09-22 09:00 | 2.6778 | 3.3161 | 3.3689 | 3.5953 | 3.5047 | 3.7311 | 1.4832 | 2.2468 | 2.675 | 2.675 | 2.9604 | 2.9604 | 2019-11-19 23:00 | 1.4861 | 2.4354 | 3.9978 | 3.9978 | 3.9978 | 3.9978
2021-09-22 10:00 | 2.3892 | 2.9586 | 3.0058 | 3.2077 | 3.1269 | 3.3289 | 1.4404 | 2.1819 | 2.5976 | 2.5976 | 2.8748 | 2.8748 | 2019-11-20 | 1.3794 | 2.2606 | 3.7108 | 3.7108 | 3.7108 | 3.7108
2021-09-22 11:00 | 2.1148 | 2.6189 | 2.6606 | 2.8394 | 2.7679 | 2.9466 | 1.3318 | 2.0174 | 2.4018 | 2.4018 | 2.6581 | 2.6581 | 2019-11-20 01:00 | 1.2727 | 2.0857 | 3.4238 | 3.4238 | 3.4238 | 3.4238
2021-09-22 12:00 | 2.0405 | 2.5269 | 2.5671 | 2.7396 | 2.6706 | 2.8431 | 1.3518 | 2.0477 | 2.4379 | 2.4379 | 2.698 | 2.698 | 2019-11-20 02:00 | 1.2498 | 2.0483 | 3.3622 | 3.3622 | 3.3622 | 3.3622
2021-09-22 13:00 | 1.9519 | 2.4172 | 2.4557 | 2.6207 | 2.5547 | 2.7197 | 1.2457 | 1.887 | 2.2466 | 2.2466 | 2.4863 | 2.4863 | 2019-11-20 03:00 | 1.1889 | 1.9483 | 3.1982 | 3.1982 | 3.1982 | 3.1982
2021-09-22 14:00 | 1.7947 | 2.2225 | 2.2579 | 2.4096 | 2.3489 | 2.5007 | 1.2803 | 1.9394 | 2.309 | 2.309 | 2.5554 | 2.5554 | 2019-11-20 04:00 | 1.1889 | 1.9483 | 3.1982 | 3.1982 | 3.1982 | 3.1982
2021-09-22 15:00 | 1.8719 | 2.3181 | 2.355 | 2.5132 | 2.4499 | 2.6082 | 1.2117 | 1.8356 | 2.1853 | 2.1853 | 2.4185 | 2.4185 | 2019-11-20 05:00 | 1.3184 | 2.1607 | 3.5468 | 3.5468 | 3.5468 | 3.5468
2021-09-22 16:00 | 2.2177 | 2.7463 | 2.79 | 2.9775 | 2.9025 | 3.09 | 1.4575 | 2.2079 | 2.6286 | 2.6286 | 2.909 | 2.909 | 2019-11-20 06:00 | 1.5318 | 2.5104 | 4.1208 | 4.1208 | 4.1208 | 4.1208
2021-09-22 17:00 | 2.7579 | 3.4152 | 3.4696 | 3.7027 | 3.6094 | 3.8426 | 1.5575 | 2.3594 | 2.809 | 2.809 | 3.1087 | 3.1087 | 2019-11-20 07:00 | 1.8671 | 3.0599 | 5.0229 | 5.0229 | 5.0229 | 5.0229
2021-09-22 18:00 | 3.1151 | 3.8575 | 3.919 | 4.1823 | 4.077 | 4.3403 | 1.9119 | 2.8962 | 3.4481 | 3.4481 | 3.816 | 3.816 | 2019-11-20 08:00 | 2.1644 | 3.547 | 5.8224 | 5.8224 | 5.8224 | 5.8224
2021-09-22 19:00 | 3.0209 | 3.7409 | 3.8004 | 4.0558 | 3.9537 | 4.209 | 1.9491 | 2.9525 | 3.5151 | 3.5151 | 3.8901 | 3.8901 | 2019-11-20 09:00 | 2.1872 | 3.5845 | 5.8839 | 5.8839 | 5.8839 | 5.8839
2021-09-22 20:00 | 2.7921 | 3.4576 | 3.5127 | 3.7487 | 3.6543 | 3.8903 | 1.9348 | 2.9308 | 3.4893 | 3.4893 | 3.8616 | 3.8616 | 2019-11-20 10:00 | 2.1949 | 3.597 | 5.9044 | 5.9044 | 5.9044 | 5.9044
2021-09-22 21:00 | 2.5864 | 3.2028 | 3.2538 | 3.4725 | 3.385 | 3.6036 | 1.7805 | 2.697 | 3.211 | 3.211 | 3.5536 | 3.5536 | 2019-11-20 11:00 | 2.3092 | 3.7843 | 6.212 | 6.212 | 6.212 | 6.212
2021-09-22 22:00 | 2.3035 | 2.8525 | 2.8979 | 3.0926 | 3.0147 | 3.2094 | 1.4747 | 2.2338 | 2.6595 | 2.6595 | 2.9433 | 2.9433 | 2019-11-20 12:00 | 2.172 | 3.5595 | 5.8429 | 5.8429 | 5.8429 | 5.8429
2021-09-22 23:00 | 2.1263 | 2.633 | 2.675 | 2.8547 | 2.7828 | 2.9626 | 1.2746 | 1.9308 | 2.2987 | 2.2987 | 2.544 | 2.544 | 2019-11-20 13:00 | 2.2863 | 3.7468 | 6.1505 | 6.1505 | 6.1505 | 6.1505
2021-09-23 | 1.8319 | 2.2685 | 2.3046 | 2.4595 | 2.3976 | 2.5524 | 1.1491 | 1.7406 | 2.0723 | 2.0723 | 2.2934 | 2.2934 | 2019-11-20 14:00 | 2.3473 | 3.8467 | 6.3145 | 6.3145 | 6.3145 | 6.3145
2021-09-23 01:00 | 1.7462 | 2.1623 | 2.1968 | 2.3444 | 2.2854 | 2.433 | 0.99454 | 1.5065 | 1.7936 | 1.7936 | 1.985 | 1.985 | 2019-11-20 15:00 | 2.4387 | 3.9966 | 6.5605 | 6.5605 | 6.5605 | 6.5605
2021-09-23 02:00 | 1.729 | 2.1411 | 2.1752 | 2.3214 | 2.2629 | 2.4091 | 0.8888 | 1.3464 | 1.6029 | 1.6029 | 1.7739 | 1.7739 | 2019-11-20 16:00 | 2.3625 | 3.8717 | 6.3555 | 6.3555 | 6.3555 | 6.3555
2021-09-23 03:00 | 1.6776 | 2.0774 | 2.1105 | 2.2523 | 2.1956 | 2.3374 | 0.89737 | 1.3593 | 1.6184 | 1.6184 | 1.7911 | 1.7911 | 2019-11-20 17:00 | 2.3625 | 3.8717 | 6.3555 | 6.3555 | 6.3555 | 6.3555
2021-09-23 04:00 | 1.7605 | 2.18 | 2.2148 | 2.3636 | 2.3041 | 2.4529 | 0.89166 | 1.3507 | 1.6081 | 1.6081 | 1.7796 | 1.7796 | 2019-11-20 18:00 | 2.1263 | 3.4845 | 5.7199 | 5.7199 | 5.7199 | 5.7199
2021-09-23 05:00 | 1.9091 | 2.3641 | 2.4017 | 2.5631 | 2.4986 | 2.6599 | 0.96124 | 1.4561 | 1.7336 | 1.7336 | 1.9185 | 1.9185 | 2019-11-20 19:00 | 2.0119 | 3.2972 | 5.4124 | 5.4124 | 5.4124 | 5.4124
2021-09-23 06:00 | 2.4121 | 2.9869 | 3.0345 | 3.2384 | 3.1569 | 3.3608 | 1.0717 | 1.6234 | 1.9328 | 1.9328 | 2.139 | 2.139 | 2019-11-20 20:00 | 2.0196 | 3.3097 | 5.4329 | 5.4329 | 5.4329 | 5.4329
2021-09-23 07:00 | 2.8807 | 3.5673 | 3.6242 | 3.8677 | 3.7703 | 4.0138 | 1.4547 | 2.2035 | 2.6234 | 2.6234 | 2.9033 | 2.9033 | 2019-11-20 21:00 | 1.89 | 3.0974 | 5.0844 | 5.0844 | 5.0844 | 5.0844
2021-09-23 08:00 | 2.9322 | 3.631 | 3.6889 | 3.9367 | 3.8376 | 4.0855 | 1.509 | 2.2858 | 2.7213 | 2.7213 | 3.0117 | 3.0117 | 2019-11-20 22:00 | 1.7223 | 2.8226 | 4.6333 | 4.6333 | 4.6333 | 4.6333
2021-09-23 09:00 | 2.9326 | 3.6315 | 3.6894 | 3.9373 | 3.8381 | 4.086 | 1.5375 | 2.3291 | 2.7729 | 2.7729 | 3.0688 | 3.0688 | 2019-11-20 23:00 | 1.5394 | 2.5229 | 4.1413 | 4.1413 | 4.1413 | 4.1413
2021-09-23 10:00 | 3.0036 | 3.7195 | 3.7788 | 4.0327 | 3.9311 | 4.185 | 1.6261 | 2.4633 | 2.9327 | 2.9327 | 3.2456 | 3.2456 | 2019-11-21 | 1.4632 | 2.398 | 3.9363 | 3.9363 | 3.9363 | 3.9363
2021-09-23 11:00 | 2.6978 | 3.3408 | 3.3941 | 3.6221 | 3.5309 | 3.7589 | 1.4975 | 2.2685 | 2.7007 | 2.7007 | 2.9889 | 2.9889 | 2019-11-21 01:00 | 1.387 | 2.2731 | 3.7313 | 3.7313 | 3.7313 | 3.7313
2021-09-23 12:00 | 2.0748 | 2.5693 | 2.6103 | 2.7856 | 2.7155 | 2.8909 | 1.3718 | 2.078 | 2.4739 | 2.4739 | 2.7379 | 2.7379 | 2019-11-21 02:00 | 1.2956 | 2.1232 | 3.4853 | 3.4853 | 3.4853 | 3.4853
2021-09-23 13:00 | 1.9262 | 2.3853 | 2.4233 | 2.5861 | 2.521 | 2.6838 | 1.2803 | 1.9394 | 2.309 | 2.309 | 2.5554 | 2.5554 | 2019-11-21 03:00 | 1.2575 | 2.0608 | 3.3828 | 3.3828 | 3.3828 | 3.3828
2021-09-23 14:00 | 1.8005 | 2.2296 | 2.2651 | 2.4173 | 2.3564 | 2.5086 | 1.2317 | 1.8659 | 2.2214 | 2.2214 | 2.4584 | 2.4584 | 2019-11-21 04:00 | 1.2651 | 2.0732 | 3.4033 | 3.4033 | 3.4033 | 3.4033
2021-09-23 15:00 | 1.9091 | 2.3641 | 2.4017 | 2.5631 | 2.4986 | 2.6599 | 1.246 | 1.8875 | 2.2472 | 2.2472 | 2.4869 | 2.4869 | 2019-11-21 05:00 | 1.3261 | 2.1732 | 3.5673 | 3.5673 | 3.5673 | 3.5673
2021-09-23 16:00 | 2.1348 | 2.6437 | 2.6858 | 2.8662 | 2.794 | 2.9745 | 1.3689 | 2.0737 | 2.4688 | 2.4688 | 2.7322 | 2.7322 | 2019-11-21 06:00 | 1.509 | 2.4729 | 4.0593 | 4.0593 | 4.0593 | 4.0593
2021-09-23 17:00 | 2.4168 | 2.9928 | 3.0405 | 3.2448 | 3.163 | 3.3673 | 1.5404 | 2.3334 | 2.778 | 2.778 | 3.0745 | 3.0745 | 2019-11-21 07:00 | 1.9434 | 3.1848 | 5.2279 | 5.2279 | 5.2279 | 5.2279
2021-09-23 18:00 | 2.8264 | 3.5001 | 3.5558 | 3.7948 | 3.6992 | 3.9381 | 1.8262 | 2.7663 | 3.2934 | 3.2934 | 3.6449 | 3.6449 | 2019-11-21 08:00 | 2.1796 | 3.572 | 5.8634 | 5.8634 | 5.8634 | 5.8634
2021-09-23 19:00 | 2.7121 | 3.3585 | 3.412 | 3.6413 | 3.5496 | 3.7789 | 1.8148 | 2.749 | 3.2728 | 3.2728 | 3.6221 | 3.6221 | 2019-11-21 09:00 | 2.2863 | 3.7468 | 6.1505 | 6.1505 | 6.1505 | 6.1505
2021-09-23 20:00 | 2.5749 | 3.1887 | 3.2395 | 3.4571 | 3.3701 | 3.5877 | 1.7147 | 2.5975 | 3.0924 | 3.0924 | 3.4224 | 3.4224 | 2019-11-21 10:00 | 2.4235 | 3.9716 | 6.5195 | 6.5195 | 6.5195 | 6.5195
2021-09-23 21:00 | 2.4378 | 3.0188 | 3.0669 | 3.2729 | 3.1905 | 3.3966 | 1.6096 | 2.4382 | 2.9028 | 2.9028 | 3.2125 | 3.2125 | 2019-11-21 11:00 | 2.4921 | 4.084 | 6.704 | 6.704 | 6.704 | 6.704
2021-09-23 22:00 | 2.1891 | 2.7109 | 2.7541 | 2.9391 | 2.8651 | 3.0502 | 1.3403 | 2.0304 | 2.4173 | 2.4173 | 2.6752 | 2.6752 | 2019-11-21 12:00 | 2.4997 | 4.0965 | 6.7245 | 6.7245 | 6.7245 | 6.7245
2021-09-23 23:00 | 2.1148 | 2.6189 | 2.6606 | 2.8394 | 2.7679 | 2.9466 | 1.1528 | 1.7462 | 2.0789 | 2.0789 | 2.3008 | 2.3008 | 2019-11-21 13:00 | 2.5149 | 4.1215 | 6.7655 | 6.7655 | 6.7655 | 6.7655
2021-09-24 | 1.8462 | 2.2862 | 2.3226 | 2.4787 | 2.4163 | 2.5723 | 1.089 | 1.6496 | 1.964 | 1.964 | 2.1735 | 2.1735 | 2019-11-21 14:00 | 2.5378 | 4.159 | 6.827 | 6.827 | 6.827 | 6.827
2021-09-24 01:00 | 1.6547 | 2.0491 | 2.0817 | 2.2216 | 2.1657 | 2.3055 | 0.95453 | 1.4459 | 1.7215 | 1.7215 | 1.9051 | 1.9051 | 2019-11-21 15:00 | 2.5988 | 4.2589 | 6.991 | 6.991 | 6.991 | 6.991
2021-09-24 02:00 | 1.6461 | 2.0385 | 2.0709 | 2.2101 | 2.1544 | 2.2936 | 0.87165 | 1.3204 | 1.572 | 1.572 | 1.7397 | 1.7397 | 2019-11-21 16:00 | 2.614 | 4.2839 | 7.032 | 7.032 | 7.032 | 7.032
2021-09-24 03:00 | 1.6404 | 2.0314 | 2.0638 | 2.2024 | 2.147 | 2.2856 | 0.85165 | 1.2901 | 1.5359 | 1.5359 | 1.6998 | 1.6998 | 2019-11-21 17:00 | 2.6369 | 4.3213 | 7.0935 | 7.0935 | 7.0935 | 7.0935
2021-09-24 04:00 | 1.6976 | 2.1022 | 2.1357 | 2.2792 | 2.2218 | 2.3653 | 0.8372 | 1.2682 | 1.5099 | 1.5099 | 1.671 | 1.671 | 2019-11-21 18:00 | 2.332 | 3.8218 | 6.2735 | 6.2735 | 6.2735 | 6.2735
2021-09-24 05:00 | 1.7947 | 2.2225 | 2.2579 | 2.4096 | 2.3489 | 2.5007 | 0.92248 | 1.3974 | 1.6637 | 1.6637 | 1.8412 | 1.8412 | 2019-11-21 19:00 | 2.2101 | 3.6219 | 5.9454 | 5.9454 | 5.9454 | 5.9454
2021-09-24 06:00 | 2.3177 | 2.8702 | 2.9159 | 3.1118 | 3.0334 | 3.2293 | 1.0288 | 1.5585 | 1.8555 | 1.8555 | 2.0534 | 2.0534 | 2019-11-21 20:00 | 2.172 | 3.5595 | 5.8429 | 5.8429 | 5.8429 | 5.8429
2021-09-24 07:00 | 2.3663 | 2.9303 | 2.977 | 3.177 | 3.097 | 3.297 | 1.1546 | 1.749 | 2.0822 | 2.0822 | 2.3044 | 2.3044 | 2019-11-21 21:00 | 2.0805 | 3.4096 | 5.5969 | 5.5969 | 5.5969 | 5.5969
2021-09-24 08:00 | 2.2977 | 2.8454 | 2.8907 | 3.0849 | 3.0072 | 3.2015 | 1.2089 | 1.8312 | 2.1802 | 2.1802 | 2.4128 | 2.4128 | 2019-11-21 22:00 | 1.7833 | 2.9225 | 4.7974 | 4.7974 | 4.7974 | 4.7974
2021-09-24 09:00 | 2.0834 | 2.58 | 2.621 | 2.7972 | 2.7267 | 2.9028 | 1.2975 | 1.9654 | 2.3399 | 2.3399 | 2.5896 | 2.5896 | 2019-11-21 23:00 | 1.5852 | 2.5978 | 4.2643 | 4.2643 | 4.2643 | 4.2643
2021-09-24 10:00 | 2.072 | 2.5658 | 2.6067 | 2.7818 | 2.7118 | 2.8869 | 1.3546 | 2.052 | 2.443 | 2.443 | 2.7037 | 2.7037 | 2019-11-22 | 1.5013 | 2.4604 | 4.0388 | 4.0388 | 4.0388 | 4.0388
2021-09-24 11:00 | 2.0148 | 2.495 | 2.5348 | 2.7051 | 2.6369 | 2.8073 | 1.2546 | 1.9005 | 2.2626 | 2.2626 | 2.5041 | 2.5041 | 2019-11-22 01:00 | 1.4023 | 2.2981 | 3.7723 | 3.7723 | 3.7723 | 3.7723
2021-09-24 12:00 | 1.9862 | 2.4596 | 2.4988 | 2.6667 | 2.5995 | 2.7674 | 1.2317 | 1.8659 | 2.2214 | 2.2214 | 2.4584 | 2.4584 | 2019-11-22 02:00 | 1.2803 | 2.0982 | 3.4443 | 3.4443 | 3.4443 | 3.4443
2021-09-24 13:00 | 1.9719 | 2.4419 | 2.4808 | 2.6475 | 2.5808 | 2.7475 | 1.2918 | 1.9568 | 2.3296 | 2.3296 | 2.5782 | 2.5782 | 2019-11-22 03:00 | 1.2803 | 2.0982 | 3.4443 | 3.4443 | 3.4443 | 3.4443
2021-09-24 14:00 | 1.9262 | 2.3853 | 2.4233 | 2.5861 | 2.521 | 2.6838 | 1.2146 | 1.8399 | 2.1905 | 2.1905 | 2.4242 | 2.4242 | 2019-11-22 04:00 | 1.3337 | 2.1856 | 3.5878 | 3.5878 | 3.5878 | 3.5878
2021-09-24 15:00 | 2.0005 | 2.4773 | 2.5168 | 2.6859 | 2.6182 | 2.7874 | 1.2346 | 1.8702 | 2.2266 | 2.2266 | 2.4641 | 2.4641 | 2019-11-22 05:00 | 1.4556 | 2.3855 | 3.9158 | 3.9158 | 3.9158 | 3.9158
2021-09-24 16:00 | 1.9862 | 2.4596 | 2.4988 | 2.6667 | 2.5995 | 2.7674 | 1.3575 | 2.0563 | 2.4482 | 2.4482 | 2.7094 | 2.7094 | 2019-11-22 06:00 | 1.5166 | 2.4854 | 4.0798 | 4.0798 | 4.0798 | 4.0798
2021-09-24 17:00 | 2.392 | 2.9622 | 3.0093 | 3.2116 | 3.1307 | 3.3329 | 1.4632 | 2.2165 | 2.6389 | 2.6389 | 2.9205 | 2.9205 | 2019-11-22 07:00 | 1.9053 | 3.1224 | 5.1254 | 5.1254 | 5.1254 | 5.1254
2021-09-24 18:00 | 2.5549 | 3.1639 | 3.2143 | 3.4303 | 3.3439 | 3.5598 | 1.6747 | 2.5369 | 3.0203 | 3.0203 | 3.3426 | 3.3426 | 2019-11-22 08:00 | 2.233 | 3.6594 | 6.007 | 6.007 | 6.007 | 6.007
2021-09-24 19:00 | 2.4855 | 3.0779 | 3.1269 | 3.337 | 3.253 | 3.4631 | 1.6404 | 2.4849 | 2.9584 | 2.9584 | 3.2741 | 3.2741 | 2019-11-22 09:00 | 2.3015 | 3.7718 | 6.1915 | 6.1915 | 6.1915 | 6.1915
2021-09-24 20:00 | 2.2953 | 2.8424 | 2.8877 | 3.0817 | 3.0041 | 3.1981 | 1.5918 | 2.4113 | 2.8708 | 2.8708 | 3.1771 | 3.1771 | 2019-11-22 10:00 | 2.4006 | 3.9342 | 6.458 | 6.458 | 6.458 | 6.458
2021-09-24 21:00 | 2.1977 | 2.7215 | 2.7649 | 2.9506 | 2.8763 | 3.0621 | 1.4347 | 2.1732 | 2.5873 | 2.5873 | 2.8634 | 2.8634 | 2019-11-22 11:00 | 2.5302 | 4.1465 | 6.8065 | 6.8065 | 6.8065 | 6.8065
2021-09-24 22:00 | 2.0691 | 2.5623 | 2.6031 | 2.778 | 2.708 | 2.8829 | 1.2885 | 1.9518 | 2.3237 | 2.3237 | 2.5717 | 2.5717 | 2019-11-22 12:00 | 2.5759 | 4.2214 | 6.9295 | 6.9295 | 6.9295 | 6.9295
2021-09-24 23:00 | 2.0262 | 2.5092 | 2.5491 | 2.7204 | 2.6519 | 2.8232 | 1.1431 | 1.7317 | 2.0616 | 2.0616 | 2.2816 | 2.2816 | 2019-11-22 13:00 | 2.5835 | 4.2339 | 6.95 | 6.95 | 6.95 | 6.95
2021-09-25 | 1.7033 | 2.1093 | 2.1429 | 2.2868 | 2.2292 | 2.3732 | 1.0176 | 1.5415 | 1.8352 | 1.8352 | 2.031 | 2.031 | 2019-11-22 14:00 | 2.5378 | 4.159 | 6.827 | 6.827 | 6.827 | 6.827
2021-09-25 01:00 | 1.5985 | 1.9794 | 2.011 | 2.1461 | 2.092 | 2.2272 | 0.89459 | 1.3551 | 1.6134 | 1.6134 | 1.7855 | 1.7855 | 2019-11-22 15:00 | 2.4921 | 4.084 | 6.704 | 6.704 | 6.704 | 6.704
2021-09-25 02:00 | 1.5518 | 1.9217 | 1.9523 | 2.0835 | 2.031 | 2.1622 | 0.88308 | 1.3377 | 1.5926 | 1.5926 | 1.7625 | 1.7625 | 2019-11-22 16:00 | 2.4616 | 4.0341 | 6.622 | 6.622 | 6.622 | 6.622
2021-09-25 03:00 | 1.5318 | 1.8969 | 1.9271 | 2.0566 | 2.0048 | 2.1343 | 0.80599 | 1.2209 | 1.4536 | 1.4536 | 1.6087 | 1.6087 | 2019-11-22 17:00 | 2.3701 | 3.8842 | 6.376 | 6.376 | 6.376 | 6.376
2021-09-25 04:00 | 1.5775 | 1.9535 | 1.9847 | 2.118 | 2.0647 | 2.198 | 0.87451 | 1.3247 | 1.5771 | 1.5771 | 1.7454 | 1.7454 | 2019-11-22 18:00 | 2.0729 | 3.3971 | 5.5764 | 5.5764 | 5.5764 | 5.5764
2021-09-25 05:00 | 1.7033 | 2.1093 | 2.1429 | 2.2868 | 2.2292 | 2.3732 | 0.87737 | 1.329 | 1.5823 | 1.5823 | 1.7511 | 1.7511 | 2019-11-22 19:00 | 2.0043 | 3.2847 | 5.3919 | 5.3919 | 5.3919 | 5.3919
2021-09-25 06:00 | 1.9033 | 2.357 | 2.3945 | 2.5554 | 2.4911 | 2.652 | 0.94195 | 1.4269 | 1.6988 | 1.6988 | 1.88 | 1.88 | 2019-11-22 20:00 | 1.9357 | 3.1723 | 5.2074 | 5.2074 | 5.2074 | 5.2074
2021-09-25 07:00 | 1.9291 | 2.3888 | 2.4269 | 2.59 | 2.5247 | 2.6878 | 1.0288 | 1.5585 | 1.8555 | 1.8555 | 2.0534 | 2.0534 | 2019-11-22 21:00 | 1.8748 | 3.0724 | 5.0434 | 5.0434 | 5.0434 | 5.0434
2021-09-25 08:00 | 1.8805 | 2.3287 | 2.3658 | 2.5247 | 2.4611 | 2.6201 | 1.1203 | 1.697 | 2.0204 | 2.0204 | 2.236 | 2.236 | 2019-11-22 22:00 | 1.6614 | 2.7227 | 4.4693 | 4.4693 | 4.4693 | 4.4693
2021-09-25 09:00 | 1.7862 | 2.2119 | 2.2471 | 2.3981 | 2.3377 | 2.4887 | 1.1673 | 1.7682 | 2.1051 | 2.1051 | 2.3297 | 2.3297 | 2019-11-22 23:00 | 1.4709 | 2.4105 | 3.9568 | 3.9568 | 3.9568 | 3.9568
2021-09-25 10:00 | 1.7547 | 2.173 | 2.2076 | 2.3559 | 2.2966 | 2.4449 | 1.2975 | 1.9654 | 2.3399 | 2.3399 | 2.5896 | 2.5896 | 2019-11-23 | 1.4327 | 2.348 | 3.8543 | 3.8543 | 3.8543 | 3.8543
2021-09-25 11:00 | 1.7176 | 2.127 | 2.1608 | 2.306 | 2.2479 | 2.3931 | 1.3318 | 2.0174 | 2.4018 | 2.4018 | 2.6581 | 2.6581 | 2019-11-23 01:00 | 1.387 | 2.2731 | 3.7313 | 3.7313 | 3.7313 | 3.7313
2021-09-25 12:00 | 1.6147 | 1.9995 | 2.0314 | 2.1679 | 2.1133 | 2.2498 | 1.2746 | 1.9308 | 2.2987 | 2.2987 | 2.544 | 2.544 | 2019-11-23 02:00 | 1.3794 | 2.2606 | 3.7108 | 3.7108 | 3.7108 | 3.7108
2021-09-25 13:00 | 1.6318 | 2.0208 | 2.053 | 2.1909 | 2.1357 | 2.2737 | 1.206 | 1.8269 | 2.175 | 2.175 | 2.4071 | 2.4071 | 2019-11-23 03:00 | 1.3184 | 2.1607 | 3.5468 | 3.5468 | 3.5468 | 3.5468
2021-09-25 14:00 | 1.7689 | 2.1904 | 2.2253 | 2.3749 | 2.3151 | 2.4646 | 1.3661 | 2.0693 | 2.4636 | 2.4636 | 2.7265 | 2.7265 | 2019-11-23 04:00 | 1.3642 | 2.2356 | 3.6698 | 3.6698 | 3.6698 | 3.6698
2021-09-25 15:00 | 1.9091 | 2.3641 | 2.4017 | 2.5631 | 2.4986 | 2.6599 | 1.3032 | 1.9741 | 2.3503 | 2.3503 | 2.601 | 2.601 | 2019-11-23 05:00 | 1.3642 | 2.2356 | 3.6698 | 3.6698 | 3.6698 | 3.6698
2021-09-25 16:00 | 2.152 | 2.6649 | 2.7073 | 2.8892 | 2.8165 | 2.9984 | 1.4432 | 2.1861 | 2.6027 | 2.6027 | 2.8804 | 2.8804 | 2019-11-23 06:00 | 1.4175 | 2.323 | 3.8133 | 3.8133 | 3.8133 | 3.8133
2021-09-25 17:00 | 2.5678 | 3.1798 | 3.2304 | 3.4475 | 3.3607 | 3.5777 | 1.5747 | 2.3854 | 2.8399 | 2.8399 | 3.1429 | 3.1429 | 2019-11-23 07:00 | 1.6614 | 2.7227 | 4.4693 | 4.4693 | 4.4693 | 4.4693
2021-09-25 18:00 | 2.8665 | 3.5496 | 3.6062 | 3.8485 | 3.7516 | 3.9939 | 1.8319 | 2.775 | 3.3038 | 3.3038 | 3.6563 | 3.6563 | 2019-11-23 08:00 | 1.8595 | 3.0474 | 5.0024 | 5.0024 | 5.0024 | 5.0024
2021-09-25 19:00 | 2.7378 | 3.3904 | 3.4444 | 3.6758 | 3.5833 | 3.8147 | 1.8262 | 2.7663 | 3.2934 | 3.2934 | 3.6449 | 3.6449 | 2019-11-23 09:00 | 1.9891 | 3.2597 | 5.3509 | 5.3509 | 5.3509 | 5.3509
2021-09-25 20:00 | 2.4436 | 3.026 | 3.0742 | 3.2808 | 3.1982 | 3.4047 | 1.7062 | 2.5845 | 3.077 | 3.077 | 3.4053 | 3.4053 | 2019-11-23 10:00 | 2.0805 | 3.4096 | 5.5969 | 5.5969 | 5.5969 | 5.5969
2021-09-25 21:00 | 2.4092 | 2.9834 | 3.0309 | 3.2346 | 3.1531 | 3.3568 | 1.569 | 2.3767 | 2.8296 | 2.8296 | 3.1315 | 3.1315 | 2019-11-23 11:00 | 2.1186 | 3.4721 | 5.6994 | 5.6994 | 5.6994 | 5.6994
2021-09-25 22:00 | 2.2406 | 2.7746 | 2.8188 | 3.0082 | 2.9324 | 3.1218 | 1.3919 | 2.1084 | 2.5102 | 2.5102 | 2.778 | 2.778 | 2019-11-23 12:00 | 2.172 | 3.5595 | 5.8429 | 5.8429 | 5.8429 | 5.8429
2021-09-25 23:00 | 2.1463 | 2.6578 | 2.7001 | 2.8816 | 2.809 | 2.9904 | 1.2375 | 1.8745 | 2.2317 | 2.2317 | 2.4698 | 2.4698 | 2019-11-23 13:00 | 2.2025 | 3.6094 | 5.9249 | 5.9249 | 5.9249 | 5.9249
2021-09-26 | 1.9262 | 2.3853 | 2.4233 | 2.5861 | 2.521 | 2.6838 | 1.1203 | 1.697 | 2.0204 | 2.0204 | 2.236 | 2.236 | 2019-11-23 14:00 | 2.2482 | 3.6844 | 6.048 | 6.048 | 6.048 | 6.048
2021-09-26 01:00 | 1.7147 | 2.1234 | 2.1572 | 2.3022 | 2.2442 | 2.3892 | 0.98025 | 1.4849 | 1.7678 | 1.7678 | 1.9565 | 1.9565 | 2019-11-23 15:00 | 2.2025 | 3.6094 | 5.9249 | 5.9249 | 5.9249 | 5.9249
2021-09-26 02:00 | 1.6833 | 2.0845 | 2.1177 | 2.26 | 2.2031 | 2.3454 | 0.87452 | 1.3247 | 1.5772 | 1.5772 | 1.7455 | 1.7455 | 2019-11-23 16:00 | 2.2177 | 3.6344 | 5.966 | 5.966 | 5.966 | 5.966
2021-09-26 03:00 | 1.6633 | 2.0597 | 2.0925 | 2.2331 | 2.1769 | 2.3175 | 0.81164 | 1.2295 | 1.4638 | 1.4638 | 1.6199 | 1.6199 | 2019-11-23 17:00 | 2.1034 | 3.4471 | 5.6584 | 5.6584 | 5.6584 | 5.6584
2021-09-26 04:00 | 1.7147 | 2.1234 | 2.1572 | 2.3022 | 2.2442 | 2.3892 | 0.88308 | 1.3377 | 1.5926 | 1.5926 | 1.7625 | 1.7625 | 2019-11-23 18:00 | 1.9357 | 3.1723 | 5.2074 | 5.2074 | 5.2074 | 5.2074
2021-09-26 05:00 | 1.7719 | 2.1942 | 2.2291 | 2.3789 | 2.319 | 2.4688 | 0.86532 | 1.3108 | 1.5606 | 1.5606 | 1.7271 | 1.7271 | 2019-11-23 19:00 | 1.829 | 2.9975 | 4.9204 | 4.9204 | 4.9204 | 4.9204
2021-09-26 06:00 | 1.8432 | 2.2826 | 2.3189 | 2.4747 | 2.4124 | 2.5682 | 0.8888 | 1.3464 | 1.6029 | 1.6029 | 1.7739 | 1.7739 | 2019-11-23 20:00 | 1.7223 | 2.8226 | 4.6333 | 4.6333 | 4.6333 | 4.6333
2021-09-26 07:00 | 1.9005 | 2.3535 | 2.3909 | 2.5516 | 2.4873 | 2.648 | 1.0317 | 1.5628 | 1.8606 | 1.8606 | 2.0591 | 2.0591 | 2019-11-23 21:00 | 1.6842 | 2.7602 | 4.5308 | 4.5308 | 4.5308 | 4.5308
2021-09-26 08:00 | 1.9719 | 2.4419 | 2.4808 | 2.6475 | 2.5808 | 2.7475 | 1.0888 | 1.6494 | 1.9637 | 1.9637 | 2.1732 | 2.1732 | 2019-11-23 22:00 | 1.6385 | 2.6852 | 4.4078 | 4.4078 | 4.4078 | 4.4078
2021-09-26 09:00 | 2.0262 | 2.5092 | 2.5491 | 2.7204 | 2.6519 | 2.8232 | 1.1258 | 1.7053 | 2.0303 | 2.0303 | 2.2469 | 2.2469 | 2019-11-23 23:00 | 1.4556 | 2.3855 | 3.9158 | 3.9158 | 3.9158 | 3.9158
2021-09-26 10:00 | 2.0834 | 2.58 | 2.621 | 2.7972 | 2.7267 | 2.9028 | 1.2432 | 1.8832 | 2.242 | 2.242 | 2.4812 | 2.4812 | 2019-11-24 | 1.4327 | 2.348 | 3.8543 | 3.8543 | 3.8543 | 3.8543
2021-09-26 11:00 | 1.8948 | 2.3464 | 2.3837 | 2.5439 | 2.4799 | 2.64 | 1.2546 | 1.9005 | 2.2626 | 2.2626 | 2.5041 | 2.5041 | 2019-11-24 01:00 | 1.3337 | 2.1856 | 3.5878 | 3.5878 | 3.5878 | 3.5878
2021-09-26 12:00 | 1.7919 | 2.219 | 2.2543 | 2.4058 | 2.3452 | 2.4967 | 1.2489 | 1.8918 | 2.2523 | 2.2523 | 2.4927 | 2.4927 | 2019-11-24 02:00 | 1.2041 | 1.9733 | 3.2392 | 3.2392 | 3.2392 | 3.2392
2021-09-26 13:00 | 1.6804 | 2.0809 | 2.1141 | 2.2561 | 2.1993 | 2.3414 | 1.1746 | 1.7793 | 2.1183 | 2.1183 | 2.3443 | 2.3443 | 2019-11-24 03:00 | 1.2194 | 1.9983 | 3.2802 | 3.2802 | 3.2802 | 3.2802
2021-09-26 14:00 | 1.6347 | 2.0243 | 2.0566 | 2.1948 | 2.1395 | 2.2777 | 1.2232 | 1.8529 | 2.2059 | 2.2059 | 2.4413 | 2.4413 | 2019-11-24 04:00 | 1.2422 | 2.0358 | 3.3417 | 3.3417 | 3.3417 | 3.3417
2021-09-26 15:00 | 1.7747 | 2.1977 | 2.2327 | 2.3828 | 2.3228 | 2.4728 | 1.3032 | 1.9741 | 2.3503 | 2.3503 | 2.601 | 2.601 | 2019-11-24 05:00 | 1.2879 | 2.1107 | 3.4648 | 3.4648 | 3.4648 | 3.4648
2021-09-26 16:00 | 2.0231 | 2.5053 | 2.5452 | 2.7162 | 2.6478 | 2.8188 | 1.4261 | 2.1602 | 2.5719 | 2.5719 | 2.8463 | 2.8463 | 2019-11-24 06:00 | 1.3108 | 2.1482 | 3.5263 | 3.5263 | 3.5263 | 3.5263
2021-09-26 17:00 | 2.6821 | 3.3213 | 3.3742 | 3.6009 | 3.5102 | 3.737 | 1.6631 | 2.5192 | 2.9993 | 2.9993 | 3.3193 | 3.3193 | 2019-11-24 07:00 | 1.5928 | 2.6103 | 4.2848 | 4.2848 | 4.2848 | 4.2848
2021-09-26 18:00 | 2.9922 | 3.7054 | 3.7644 | 4.0173 | 3.9161 | 4.1691 | 1.9119 | 2.8962 | 3.4481 | 3.4481 | 3.816 | 3.816 | 2019-11-24 08:00 | 1.6842 | 2.7602 | 4.5308 | 4.5308 | 4.5308 | 4.5308
2021-09-26 19:00 | 2.9751 | 3.6841 | 3.7428 | 3.9943 | 3.8937 | 4.1452 | 1.8745 | 2.8395 | 3.3805 | 3.3805 | 3.7412 | 3.7412 | 2019-11-24 09:00 | 1.8443 | 3.0224 | 4.9614 | 4.9614 | 4.9614 | 4.9614
2021-09-26 20:00 | 2.755 | 3.4116 | 3.466 | 3.6989 | 3.6057 | 3.8386 | 1.8748 | 2.8399 | 3.3811 | 3.3811 | 3.7418 | 3.7418 | 2019-11-24 10:00 | 1.7376 | 2.8476 | 4.6744 | 4.6744 | 4.6744 | 4.6744
2021-09-26 21:00 | 2.5378 | 3.1427 | 3.1927 | 3.4072 | 3.3214 | 3.536 | 1.6607 | 2.5156 | 2.9949 | 2.9949 | 3.3145 | 3.3145 | 2019-11-24 11:00 | 1.9434 | 3.1848 | 5.2279 | 5.2279 | 5.2279 | 5.2279
2021-09-26 22:00 | 2.3206 | 2.8737 | 2.9195 | 3.1156 | 3.0372 | 3.2333 | 1.4689 | 2.2252 | 2.6492 | 2.6492 | 2.9319 | 2.9319 | 2019-11-24 12:00 | 1.89 | 3.0974 | 5.0844 | 5.0844 | 5.0844 | 5.0844
2021-09-26 23:00 | 2.1406 | 2.6507 | 2.693 | 2.8739 | 2.8015 | 2.9825 | 1.2975 | 1.9654 | 2.3399 | 2.3399 | 2.5896 | 2.5896 | 2019-11-24 13:00 | 1.9281 | 3.1598 | 5.1869 | 5.1869 | 5.1869 | 5.1869
2021-09-27 | 1.9148 | 2.3712 | 2.409 | 2.5708 | 2.5061 | 2.668 | 1.1431 | 1.7317 | 2.0616 | 2.0616 | 2.2816 | 2.2816 | 2019-11-24 14:00 | 1.9129 | 3.1348 | 5.1459 | 5.1459 | 5.1459 | 5.1459
2021-09-27 01:00 | 1.8205 | 2.2544 | 2.2903 | 2.4442 | 2.3826 | 2.5365 | 0.94881 | 1.4373 | 1.7111 | 1.7111 | 1.8937 | 1.8937 | 2019-11-24 15:00 | 2.1263 | 3.4845 | 5.7199 | 5.7199 | 5.7199 | 5.7199
2021-09-27 02:00 | 1.709 | 2.1163 | 2.15 | 2.2945 | 2.2367 | 2.3812 | 0.90309 | 1.368 | 1.6287 | 1.6287 | 1.8025 | 1.8025 | 2019-11-24 16:00 | 2.1034 | 3.4471 | 5.6584 | 5.6584 | 5.6584 | 5.6584
2021-09-27 03:00 | 1.7009 | 2.1063 | 2.1398 | 2.2836 | 2.2261 | 2.3699 | 0.89451 | 1.355 | 1.6132 | 1.6132 | 1.7854 | 1.7854 | 2019-11-24 17:00 | 1.9129 | 3.1348 | 5.1459 | 5.1459 | 5.1459 | 5.1459
2021-09-27 04:00 | 1.729 | 2.1411 | 2.1752 | 2.3214 | 2.2629 | 2.4091 | 0.89166 | 1.3507 | 1.6081 | 1.6081 | 1.7796 | 1.7796 | 2019-11-24 18:00 | 1.7452 | 2.8601 | 4.6949 | 4.6949 | 4.6949 | 4.6949
2021-09-27 05:00 | 1.9227 | 2.381 | 2.4189 | 2.5815 | 2.5165 | 2.679 | 0.93452 | 1.4156 | 1.6854 | 1.6854 | 1.8652 | 1.8652 | 2019-11-24 19:00 | 1.6842 | 2.7602 | 4.5308 | 4.5308 | 4.5308 | 4.5308
2021-09-27 06:00 | 2.4006 | 2.9728 | 3.0201 | 3.2231 | 3.1419 | 3.3448 | 1.0746 | 1.6278 | 1.9379 | 1.9379 | 2.1447 | 2.1447 | 2019-11-24 20:00 | 1.8214 | 2.985 | 4.8999 | 4.8999 | 4.8999 | 4.8999
2021-09-27 07:00 | 2.5892 | 3.2064 | 3.2574 | 3.4763 | 3.3888 | 3.6076 | 1.2117 | 1.8356 | 2.1853 | 2.1853 | 2.4185 | 2.4185 | 2019-11-24 21:00 | 1.7757 | 2.91 | 4.7769 | 4.7769 | 4.7769 | 4.7769
2021-09-27 08:00 | 2.5864 | 3.2028 | 3.2538 | 3.4725 | 3.385 | 3.6036 | 1.3089 | 1.9827 | 2.3606 | 2.3606 | 2.6124 | 2.6124 | 2019-11-24 22:00 | 1.5318 | 2.5104 | 4.1208 | 4.1208 | 4.1208 | 4.1208
2021-09-27 09:00 | 2.372 | 2.9374 | 2.9842 | 3.1847 | 3.1045 | 3.305 | 1.3804 | 2.091 | 2.4894 | 2.4894 | 2.755 | 2.755 | 2019-11-24 23:00 | 1.4556 | 2.3855 | 3.9158 | 3.9158 | 3.9158 | 3.9158
2021-09-27 10:00 | 2.1606 | 2.6755 | 2.7181 | 2.9008 | 2.8277 | 3.0103 | 1.3118 | 1.9871 | 2.3657 | 2.3657 | 2.6181 | 2.6181 | 2019-11-25 | 1.3718 | 2.2481 | 3.6903 | 3.6903 | 3.6903 | 3.6903
2021-09-27 11:00 | 2.1291 | 2.6366 | 2.6786 | 2.8586 | 2.7866 | 2.9665 | 1.3289 | 2.013 | 2.3966 | 2.3966 | 2.6524 | 2.6524 | 2019-11-25 01:00 | 1.4175 | 2.323 | 3.8133 | 3.8133 | 3.8133 | 3.8133
2021-09-27 12:00 | 2.0091 | 2.4879 | 2.5276 | 2.6974 | 2.6295 | 2.7993 | 1.3603 | 2.0607 | 2.4533 | 2.4533 | 2.7151 | 2.7151 | 2019-11-25 02:00 | 1.3337 | 2.1856 | 3.5878 | 3.5878 | 3.5878 | 3.5878
2021-09-27 13:00 | 1.9634 | 2.4313 | 2.47 | 2.636 | 2.5696 | 2.7356 | 1.3718 | 2.078 | 2.4739 | 2.4739 | 2.7379 | 2.7379 | 2019-11-25 03:00 | 1.2803 | 2.0982 | 3.4443 | 3.4443 | 3.4443 | 3.4443
2021-09-27 14:00 | 1.8205 | 2.2544 | 2.2903 | 2.4442 | 2.3826 | 2.5365 | 1.2575 | 1.9048 | 2.2678 | 2.2678 | 2.5098 | 2.5098 | 2019-11-25 04:00 | 1.3032 | 2.1357 | 3.5058 | 3.5058 | 3.5058 | 3.5058
2021-09-27 15:00 | 1.8433 | 2.2827 | 2.319 | 2.4749 | 2.4125 | 2.5683 | 1.3775 | 2.0866 | 2.4843 | 2.4843 | 2.7493 | 2.7493 | 2019-11-25 05:00 | 1.4861 | 2.4354 | 3.9978 | 3.9978 | 3.9978 | 3.9978
2021-09-27 16:00 | 1.9491 | 2.4136 | 2.4521 | 2.6168 | 2.5509 | 2.7157 | 1.2975 | 1.9654 | 2.3399 | 2.3399 | 2.5896 | 2.5896 | 2019-11-25 06:00 | 1.5928 | 2.6103 | 4.2848 | 4.2848 | 4.2848 | 4.2848
2021-09-27 17:00 | 2.4949 | 3.0896 | 3.1388 | 3.3497 | 3.2653 | 3.4762 | 1.5843 | 2.3999 | 2.8572 | 2.8572 | 3.162 | 3.162 | 2019-11-25 07:00 | 1.9129 | 3.1348 | 5.1459 | 5.1459 | 5.1459 | 5.1459
2021-09-27 18:00 | 2.9007 | 3.5921 | 3.6493 | 3.8945 | 3.7965 | 4.0417 | 1.8576 | 2.8139 | 3.3501 | 3.3501 | 3.7076 | 3.7076 | 2019-11-25 08:00 | 2.233 | 3.6594 | 6.007 | 6.007 | 6.007 | 6.007
2021-09-27 19:00 | 2.7962 | 3.4627 | 3.5178 | 3.7542 | 3.6596 | 3.896 | 1.8005 | 2.7274 | 3.2471 | 3.2471 | 3.5935 | 3.5935 | 2019-11-25 09:00 | 2.332 | 3.8218 | 6.2735 | 6.2735 | 6.2735 | 6.2735
2021-09-27 20:00 | 2.6578 | 3.2913 | 3.3437 | 3.5684 | 3.4785 | 3.7032 | 1.7662 | 2.6754 | 3.1852 | 3.1852 | 3.5251 | 3.5251 | 2019-11-25 10:00 | 2.3092 | 3.7843 | 6.212 | 6.212 | 6.212 | 6.212
2021-09-27 21:00 | 2.392 | 2.9622 | 3.0093 | 3.2116 | 3.1307 | 3.3329 | 1.5318 | 2.3204 | 2.7626 | 2.7626 | 3.0574 | 3.0574 | 2019-11-25 11:00 | 2.4006 | 3.9342 | 6.458 | 6.458 | 6.458 | 6.458
2021-09-27 22:00 | 2.3006 | 2.8489 | 2.8943 | 3.0888 | 3.011 | 3.2055 | 1.3747 | 2.0824 | 2.4792 | 2.4792 | 2.7438 | 2.7438 | 2019-11-25 12:00 | 2.4235 | 3.9716 | 6.5195 | 6.5195 | 6.5195 | 6.5195
2021-09-27 23:00 | 1.9634 | 2.4313 | 2.47 | 2.636 | 2.5696 | 2.7356 | 1.2546 | 1.9005 | 2.2626 | 2.2626 | 2.5041 | 2.5041 | 2019-11-25 13:00 | 2.6445 | 4.3338 | 7.114 | 7.114 | 7.114 | 7.114
2021-09-28 | 1.729 | 2.1411 | 2.1752 | 2.3214 | 2.2629 | 2.4091 | 1.1031 | 1.671 | 1.9895 | 1.9895 | 2.2017 | 2.2017 | 2019-11-25 14:00 | 2.7283 | 4.4712 | 7.3396 | 7.3396 | 7.3396 | 7.3396
2021-09-28 01:00 | 1.6147 | 1.9995 | 2.0314 | 2.1679 | 2.1133 | 2.2498 | 0.94596 | 1.4329 | 1.706 | 1.706 | 1.888 | 1.888 | 2019-11-25 15:00 | 2.7131 | 4.4462 | 7.2986 | 7.2986 | 7.2986 | 7.2986
2021-09-28 02:00 | 1.549 | 1.9182 | 1.9487 | 2.0796 | 2.0273 | 2.1582 | 0.87165 | 1.3204 | 1.572 | 1.572 | 1.7397 | 1.7397 | 2019-11-25 16:00 | 2.6597 | 4.3588 | 7.155 | 7.155 | 7.155 | 7.155
2021-09-28 03:00 | 1.5753 | 1.9508 | 1.9819 | 2.115 | 2.0618 | 2.1949 | 0.86879 | 1.3161 | 1.5668 | 1.5668 | 1.734 | 1.734 | 2019-11-25 17:00 | 2.4997 | 4.0965 | 6.7245 | 6.7245 | 6.7245 | 6.7245
2021-09-28 04:00 | 1.6745 | 2.0736 | 2.1066 | 2.2482 | 2.1916 | 2.3331 | 0.89451 | 1.355 | 1.6132 | 1.6132 | 1.7854 | 1.7854 | 2019-11-25 18:00 | 2.4006 | 3.9342 | 6.458 | 6.458 | 6.458 | 6.458
2021-09-28 05:00 | 1.8805 | 2.3287 | 2.3658 | 2.5247 | 2.4611 | 2.6201 | 0.90856 | 1.3763 | 1.6385 | 1.6385 | 1.8134 | 1.8134 | 2019-11-25 19:00 | 2.2406 | 3.6719 | 6.0275 | 6.0275 | 6.0275 | 6.0275
2021-09-28 06:00 | 2.2549 | 2.7923 | 2.8368 | 3.0274 | 2.9511 | 3.1417 | 1.0888 | 1.6494 | 1.9637 | 1.9637 | 2.1732 | 2.1732 | 2019-11-25 20:00 | 2.2253 | 3.6469 | 5.9865 | 5.9865 | 5.9865 | 5.9865
2021-09-28 07:00 | 2.5892 | 3.2064 | 3.2574 | 3.4763 | 3.3888 | 3.6076 | 1.2546 | 1.9005 | 2.2626 | 2.2626 | 2.5041 | 2.5041 | 2019-11-25 21:00 | 2.0882 | 3.4221 | 5.6174 | 5.6174 | 5.6174 | 5.6174
2021-09-28 08:00 | 2.5235 | 3.125 | 3.1747 | 3.3881 | 3.3027 | 3.516 | 1.3203 | 2.0001 | 2.3812 | 2.3812 | 2.6353 | 2.6353 | 2019-11-25 22:00 | 1.8671 | 3.0599 | 5.0229 | 5.0229 | 5.0229 | 5.0229
2021-09-28 09:00 | 2.3663 | 2.9303 | 2.977 | 3.177 | 3.097 | 3.297 | 1.2605 | 1.9094 | 2.2733 | 2.2733 | 2.5159 | 2.5159 | 2019-11-25 23:00 | 1.6995 | 2.7851 | 4.5718 | 4.5718 | 4.5718 | 4.5718
2021-09-28 10:00 | 2.2463 | 2.7817 | 2.826 | 3.0159 | 2.9399 | 3.1298 | 1.3403 | 2.0304 | 2.4173 | 2.4173 | 2.6752 | 2.6752 | 2019-11-26 | 1.5928 | 2.6103 | 4.2848 | 4.2848 | 4.2848 | 4.2848
2021-09-28 11:00 | 2.2006 | 2.7251 | 2.7685 | 2.9545 | 2.8801 | 3.0661 | 1.3196 | 1.9989 | 2.3798 | 2.3798 | 2.6338 | 2.6338 | 2019-11-26 01:00 | 1.5166 | 2.4854 | 4.0798 | 4.0798 | 4.0798 | 4.0798
2021-09-28 12:00 | 2.1863 | 2.7074 | 2.7505 | 2.9353 | 2.8614 | 3.0462 | 1.3003 | 1.9698 | 2.3451 | 2.3451 | 2.5953 | 2.5953 | 2019-11-26 02:00 | 1.4937 | 2.4479 | 4.0183 | 4.0183 | 4.0183 | 4.0183
2021-09-28 13:00 | 2.0005 | 2.4773 | 2.5168 | 2.6859 | 2.6182 | 2.7874 | 1.1946 | 1.8096 | 2.1544 | 2.1544 | 2.3843 | 2.3843 | 2019-11-26 03:00 | 1.4327 | 2.348 | 3.8543 | 3.8543 | 3.8543 | 3.8543
2021-09-28 14:00 | 1.7119 | 2.1199 | 2.1536 | 2.2984 | 2.2405 | 2.3852 | 1.1717 | 1.7749 | 2.1132 | 2.1132 | 2.3386 | 2.3386 | 2019-11-26 04:00 | 1.4709 | 2.4105 | 3.9568 | 3.9568 | 3.9568 | 3.9568
2021-09-28 15:00 | 1.7947 | 2.2225 | 2.2579 | 2.4096 | 2.3489 | 2.5007 | 1.1803 | 1.788 | 2.1287 | 2.1287 | 2.3558 | 2.3558 | 2019-11-26 05:00 | 1.5318 | 2.5104 | 4.1208 | 4.1208 | 4.1208 | 4.1208
2021-09-28 16:00 | 1.9062 | 2.3605 | 2.3981 | 2.5593 | 2.4948 | 2.6559 | 1.3032 | 1.9741 | 2.3503 | 2.3503 | 2.601 | 2.601 | 2019-11-26 06:00 | 1.73 | 2.8351 | 4.6538 | 4.6538 | 4.6538 | 4.6538
2021-09-28 17:00 | 2.352 | 2.9126 | 2.959 | 3.1578 | 3.0783 | 3.2771 | 1.4318 | 2.1689 | 2.5822 | 2.5822 | 2.8577 | 2.8577 | 2019-11-26 07:00 | 2.2025 | 3.6094 | 5.9249 | 5.9249 | 5.9249 | 5.9249
2021-09-28 18:00 | 2.7093 | 3.355 | 3.4084 | 3.6375 | 3.5459 | 3.7749 | 1.6945 | 2.5669 | 3.056 | 3.056 | 3.3821 | 3.3821 | 2019-11-26 08:00 | 2.5073 | 4.109 | 6.745 | 6.745 | 6.745 | 6.745
2021-09-28 19:00 | 2.5583 | 3.168 | 3.2185 | 3.4347 | 3.3482 | 3.5645 | 1.7947 | 2.7187 | 3.2368 | 3.2368 | 3.5821 | 3.5821 | 2019-11-26 09:00 | 2.4616 | 4.0341 | 6.622 | 6.622 | 6.622 | 6.622
2021-09-28 20:00 | 2.392 | 2.9622 | 3.0093 | 3.2116 | 3.1307 | 3.3329 | 1.6004 | 2.4243 | 2.8863 | 2.8863 | 3.1942 | 3.1942 | 2019-11-26 10:00 | 2.5302 | 4.1465 | 6.8065 | 6.8065 | 6.8065 | 6.8065
2021-09-28 21:00 | 2.192 | 2.7144 | 2.7577 | 2.943 | 2.8688 | 3.0541 | 1.4375 | 2.1776 | 2.5925 | 2.5925 | 2.8691 | 2.8691 | 2019-11-26 11:00 | 2.5226 | 4.134 | 6.786 | 6.786 | 6.786 | 6.786
2021-09-28 22:00 | 2.032 | 2.5162 | 2.5563 | 2.7281 | 2.6594 | 2.8312 | 1.2925 | 1.9579 | 2.331 | 2.331 | 2.5797 | 2.5797 | 2019-11-26 12:00 | 2.454 | 4.0216 | 6.6015 | 6.6015 | 6.6015 | 6.6015
2021-09-28 23:00 | 1.9085 | 2.3634 | 2.4011 | 2.5624 | 2.4979 | 2.6592 | 1.1006 | 1.6672 | 1.9849 | 1.9849 | 2.1967 | 2.1967 | 2019-11-26 13:00 | 2.3549 | 3.8592 | 6.335 | 6.335 | 6.335 | 6.335
2021-09-29 | 1.7062 | 2.1128 | 2.1465 | 2.2907 | 2.233 | 2.3772 | 0.95075 | 1.4402 | 1.7146 | 1.7146 | 1.8976 | 1.8976 | 2019-11-26 14:00 | 2.3168 | 3.7968 | 6.2325 | 6.2325 | 6.2325 | 6.2325
2021-09-29 01:00 | 1.5547 | 1.9252 | 1.9559 | 2.0873 | 2.0347 | 2.1662 | 0.87737 | 1.329 | 1.5823 | 1.5823 | 1.7511 | 1.7511 | 2019-11-26 15:00 | 2.2711 | 3.7218 | 6.1095 | 6.1095 | 6.1095 | 6.1095
2021-09-29 02:00 | 1.5518 | 1.9217 | 1.9523 | 2.0835 | 2.031 | 2.1622 | 0.80592 | 1.2208 | 1.4534 | 1.4534 | 1.6085 | 1.6085 | 2019-11-26 16:00 | 2.3015 | 3.7718 | 6.1915 | 6.1915 | 6.1915 | 6.1915
2021-09-29 03:00 | 1.5175 | 1.8792 | 1.9092 | 2.0374 | 1.9861 | 2.1144 | 0.79163 | 1.1992 | 1.4277 | 1.4277 | 1.58 | 1.58 | 2019-11-26 17:00 | 2.1491 | 3.522 | 5.7814 | 5.7814 | 5.7814 | 5.7814
2021-09-29 04:00 | 1.5204 | 1.8828 | 1.9127 | 2.0413 | 1.9899 | 2.1184 | 0.80592 | 1.2208 | 1.4534 | 1.4534 | 1.6085 | 1.6085 | 2019-11-26 18:00 | 2.0119 | 3.2972 | 5.4124 | 5.4124 | 5.4124 | 5.4124
2021-09-29 05:00 | 1.591 | 1.9702 | 2.0016 | 2.1361 | 2.0823 | 2.2168 | 0.79892 | 1.2102 | 1.4408 | 1.4408 | 1.5946 | 1.5946 | 2019-11-26 19:00 | 1.89 | 3.0974 | 5.0844 | 5.0844 | 5.0844 | 5.0844
2021-09-29 06:00 | 1.9176 | 2.3747 | 2.4125 | 2.5746 | 2.5098 | 2.6719 | 0.93452 | 1.4156 | 1.6854 | 1.6854 | 1.8652 | 1.8652 | 2019-11-26 20:00 | 1.8367 | 3.0099 | 4.9409 | 4.9409 | 4.9409 | 4.9409
2021-09-29 07:00 | 2.2206 | 2.7498 | 2.7936 | 2.9813 | 2.9063 | 3.094 | 1.1566 | 1.7521 | 2.0859 | 2.0859 | 2.3085 | 2.3085 | 2019-11-26 21:00 | 1.8062 | 2.96 | 4.8589 | 4.8589 | 4.8589 | 4.8589
2021-09-29 08:00 | 2.4349 | 3.0153 | 3.0633 | 3.2691 | 3.1868 | 3.3926 | 1.3318 | 2.0174 | 2.4018 | 2.4018 | 2.6581 | 2.6581 | 2019-11-26 22:00 | 1.6919 | 2.7726 | 4.5513 | 4.5513 | 4.5513 | 4.5513
2021-09-29 09:00 | 2.5006 | 3.0966 | 3.146 | 3.3574 | 3.2728 | 3.4842 | 1.3432 | 2.0347 | 2.4224 | 2.4224 | 2.6809 | 2.6809 | 2019-11-26 23:00 | 1.5166 | 2.4854 | 4.0798 | 4.0798 | 4.0798 | 4.0798
2021-09-29 10:00 | 2.5035 | 3.1002 | 3.1496 | 3.3612 | 3.2765 | 3.4882 | 1.5461 | 2.3421 | 2.7883 | 2.7883 | 3.0859 | 3.0859 | 2019-11-27 | 1.4251 | 2.3355 | 3.8338 | 3.8338 | 3.8338 | 3.8338
2021-09-29 11:00 | 2.6893 | 3.3302 | 3.3833 | 3.6106 | 3.5197 | 3.747 | 1.5261 | 2.3118 | 2.7523 | 2.7523 | 3.0459 | 3.0459 | 2019-11-27 01:00 | 1.2727 | 2.0857 | 3.4238 | 3.4238 | 3.4238 | 3.4238
2021-09-29 12:00 | 2.6635 | 3.2984 | 3.3509 | 3.5761 | 3.486 | 3.7112 | 1.5118 | 2.2901 | 2.7265 | 2.7265 | 3.0174 | 3.0174 | 2019-11-27 02:00 | 1.3565 | 2.2231 | 3.6493 | 3.6493 | 3.6493 | 3.6493
2021-09-29 13:00 | 2.5607 | 3.171 | 3.2215 | 3.4379 | 3.3514 | 3.5678 | 1.4575 | 2.2079 | 2.6286 | 2.6286 | 2.909 | 2.909 | 2019-11-27 03:00 | 1.3032 | 2.1357 | 3.5058 | 3.5058 | 3.5058 | 3.5058
2021-09-29 14:00 | 2.4178 | 2.994 | 3.0417 | 3.2461 | 3.1643 | 3.3687 | 1.4318 | 2.1689 | 2.5822 | 2.5822 | 2.8577 | 2.8577 | 2019-11-27 04:00 | 1.3337 | 2.1856 | 3.5878 | 3.5878 | 3.5878 | 3.5878
2021-09-29 15:00 | 2.372 | 2.9374 | 2.9842 | 3.1847 | 3.1045 | 3.305 | 1.3861 | 2.0996 | 2.4997 | 2.4997 | 2.7664 | 2.7664 | 2019-11-27 05:00 | 1.4251 | 2.3355 | 3.8338 | 3.8338 | 3.8338 | 3.8338
2021-09-29 16:00 | 2.4031 | 2.9758 | 3.0232 | 3.2264 | 3.1451 | 3.3483 | 1.4461 | 2.1905 | 2.608 | 2.608 | 2.8862 | 2.8862 | 2019-11-27 06:00 | 1.6461 | 2.6977 | 4.4283 | 4.4283 | 4.4283 | 4.4283
2021-09-29 17:00 | 2.7376 | 3.3901 | 3.444 | 3.6755 | 3.5829 | 3.8143 | 1.5833 | 2.3983 | 2.8554 | 2.8554 | 3.16 | 3.16 | 2019-11-27 07:00 | 1.9281 | 3.1598 | 5.1869 | 5.1869 | 5.1869 | 5.1869
2021-09-29 18:00 | 2.9665 | 3.6735 | 3.732 | 3.9828 | 3.8825 | 4.1332 | 1.7047 | 2.5823 | 3.0744 | 3.0744 | 3.4024 | 3.4024 | 2019-11-27 08:00 | 2.2177 | 3.6344 | 5.966 | 5.966 | 5.966 | 5.966
2021-09-29 19:00 | 2.8304 | 3.505 | 3.5608 | 3.8001 | 3.7044 | 3.9436 | 1.7976 | 2.723 | 3.2419 | 3.2419 | 3.5878 | 3.5878 | 2019-11-27 09:00 | 2.1644 | 3.547 | 5.8224 | 5.8224 | 5.8224 | 5.8224
2021-09-29 20:00 | 2.4978 | 3.0931 | 3.1424 | 3.3535 | 3.2691 | 3.4802 | 1.6748 | 2.537 | 3.0205 | 3.0205 | 3.3428 | 3.3428 | 2019-11-27 10:00 | 2.2025 | 3.6094 | 5.9249 | 5.9249 | 5.9249 | 5.9249
2021-09-29 21:00 | 2.3376 | 2.8947 | 2.9408 | 3.1384 | 3.0594 | 3.257 | 1.4918 | 2.2598 | 2.6904 | 2.6904 | 2.9775 | 2.9775 | 2019-11-27 11:00 | 2.2253 | 3.6469 | 5.9865 | 5.9865 | 5.9865 | 5.9865
2021-09-29 22:00 | 2.1406 | 2.6507 | 2.693 | 2.8739 | 2.8015 | 2.9825 | 1.3089 | 1.9827 | 2.3606 | 2.3606 | 2.6124 | 2.6124 | 2019-11-27 12:00 | 2.2482 | 3.6844 | 6.048 | 6.048 | 6.048 | 6.048
2021-09-29 23:00 | 1.9718 | 2.4417 | 2.4806 | 2.6473 | 2.5806 | 2.7473 | 1.1869 | 1.7979 | 2.1405 | 2.1405 | 2.3689 | 2.3689 | 2019-11-27 13:00 | 2.2939 | 3.7593 | 6.171 | 6.171 | 6.171 | 6.171
2021-09-30 | 1.6471 | 2.0397 | 2.0722 | 2.2114 | 2.1557 | 2.2949 | 0.98627 | 1.494 | 1.7787 | 1.7787 | 1.9685 | 1.9685 | 2019-11-27 14:00 | 2.332 | 3.8218 | 6.2735 | 6.2735 | 6.2735 | 6.2735
2021-09-30 01:00 | 1.6025 | 1.9844 | 2.016 | 2.1515 | 2.0973 | 2.2328 | 0.83481 | 1.2646 | 1.5055 | 1.5055 | 1.6662 | 1.6662 | 2019-11-27 15:00 | 2.3092 | 3.7843 | 6.212 | 6.212 | 6.212 | 6.212
2021-09-30 02:00 | 1.5175 | 1.8792 | 1.9092 | 2.0374 | 1.9861 | 2.1144 | 0.82307 | 1.2468 | 1.4844 | 1.4844 | 1.6428 | 1.6428 | 2019-11-27 16:00 | 2.3397 | 3.8343 | 6.294 | 6.294 | 6.294 | 6.294
2021-09-30 03:00 | 1.529 | 1.8934 | 1.9235 | 2.0528 | 2.0011 | 2.1303 | 0.81735 | 1.2381 | 1.4741 | 1.4741 | 1.6313 | 1.6313 | 2019-11-27 17:00 | 2.2863 | 3.7468 | 6.1505 | 6.1505 | 6.1505 | 6.1505
2021-09-30 04:00 | 1.5661 | 1.9394 | 1.9703 | 2.1027 | 2.0497 | 2.1821 | 0.81449 | 1.2338 | 1.4689 | 1.4689 | 1.6256 | 1.6256 | 2019-11-27 18:00 | 2.1567 | 3.5345 | 5.8019 | 5.8019 | 5.8019 | 5.8019
2021-09-30 05:00 | 1.7233 | 2.134 | 2.168 | 2.3137 | 2.2554 | 2.4011 | 0.89166 | 1.3507 | 1.6081 | 1.6081 | 1.7796 | 1.7796 | 2019-11-27 19:00 | 1.9662 | 3.2223 | 5.2894 | 5.2894 | 5.2894 | 5.2894
2021-09-30 06:00 | 2.0777 | 2.5729 | 2.6139 | 2.7895 | 2.7192 | 2.8949 | 0.97168 | 1.4719 | 1.7524 | 1.7524 | 1.9394 | 1.9394 | 2019-11-27 20:00 | 1.9205 | 3.1473 | 5.1664 | 5.1664 | 5.1664 | 5.1664
2021-09-30 07:00 | 2.3149 | 2.8666 | 2.9123 | 3.108 | 3.0297 | 3.2254 | 1.1632 | 1.762 | 2.0977 | 2.0977 | 2.3215 | 2.3215 | 2019-11-27 21:00 | 1.8367 | 3.0099 | 4.9409 | 4.9409 | 4.9409 | 4.9409
2021-09-30 08:00 | 2.4292 | 3.0082 | 3.0561 | 3.2614 | 3.1793 | 3.3846 | 1.3203 | 2.0001 | 2.3812 | 2.3812 | 2.6353 | 2.6353 | 2019-11-27 22:00 | 1.7376 | 2.8476 | 4.6744 | 4.6744 | 4.6744 | 4.6744
2021-09-30 09:00 | 2.4435 | 3.0259 | 3.0741 | 3.2806 | 3.198 | 3.4046 | 1.3804 | 2.091 | 2.4894 | 2.4894 | 2.755 | 2.755 | 2019-11-27 23:00 | 1.5547 | 2.5478 | 4.1823 | 4.1823 | 4.1823 | 4.1823
2021-09-30 10:00 | 2.4063 | 2.9799 | 3.0273 | 3.2307 | 3.1494 | 3.3528 | 1.4289 | 2.1646 | 2.577 | 2.577 | 2.852 | 2.852 | 2019-11-28 | 1.4251 | 2.3355 | 3.8338 | 3.8338 | 3.8338 | 3.8338
2021-09-30 11:00 | 2.2777 | 2.8206 | 2.8655 | 3.0581 | 2.9811 | 3.1736 | 1.3447 | 2.037 | 2.4252 | 2.4252 | 2.6839 | 2.6839 | 2019-11-28 01:00 | 1.3565 | 2.2231 | 3.6493 | 3.6493 | 3.6493 | 3.6493
2021-09-30 12:00 | 2.1691 | 2.6861 | 2.7289 | 2.9123 | 2.8389 | 3.0223 | 1.3546 | 2.052 | 2.443 | 2.443 | 2.7037 | 2.7037 | 2019-11-28 02:00 | 1.3032 | 2.1357 | 3.5058 | 3.5058 | 3.5058 | 3.5058
2021-09-30 13:00 | 2.0005 | 2.4773 | 2.5168 | 2.6859 | 2.6182 | 2.7874 | 1.3146 | 1.9914 | 2.3709 | 2.3709 | 2.6238 | 2.6238 | 2019-11-28 03:00 | 1.2651 | 2.0732 | 3.4033 | 3.4033 | 3.4033 | 3.4033
2021-09-30 14:00 | 1.9017 | 2.355 | 2.3925 | 2.5533 | 2.489 | 2.6497 | 1.3289 | 2.013 | 2.3966 | 2.3966 | 2.6524 | 2.6524 | 2019-11-28 04:00 | 1.2879 | 2.1107 | 3.4648 | 3.4648 | 3.4648 | 3.4648
2021-09-30 15:00 | 2.1806 | 2.7003 | 2.7433 | 2.9276 | 2.8539 | 3.0382 | 1.4089 | 2.1343 | 2.541 | 2.541 | 2.8121 | 2.8121 | 2019-11-28 05:00 | 1.3642 | 2.2356 | 3.6698 | 3.6698 | 3.6698 | 3.6698
2021-09-30 16:00 | 2.1891 | 2.7109 | 2.7541 | 2.9391 | 2.8651 | 3.0502 | 1.3003 | 1.9698 | 2.3451 | 2.3451 | 2.5953 | 2.5953 | 2019-11-28 06:00 | 1.6614 | 2.7227 | 4.4693 | 4.4693 | 4.4693 | 4.4693
2021-09-30 17:00 | 2.4035 | 2.9763 | 3.0237 | 3.2269 | 3.1456 | 3.3488 | 1.3489 | 2.0433 | 2.4327 | 2.4327 | 2.6923 | 2.6923 | 2019-11-28 07:00 | 1.9434 | 3.1848 | 5.2279 | 5.2279 | 5.2279 | 5.2279
2021-09-30 18:00 | 2.8264 | 3.5001 | 3.5558 | 3.7948 | 3.6992 | 3.9381 | 1.7147 | 2.5975 | 3.0924 | 3.0924 | 3.4224 | 3.4224 | 2019-11-28 08:00 | 2.2101 | 3.6219 | 5.9454 | 5.9454 | 5.9454 | 5.9454
2021-09-30 19:00 | 2.7436 | 3.3975 | 3.4516 | 3.6835 | 3.5907 | 3.8227 | 1.809 | 2.7403 | 3.2625 | 3.2625 | 3.6106 | 3.6106 | 2019-11-28 09:00 | 2.1339 | 3.497 | 5.7404 | 5.7404 | 5.7404 | 5.7404
2021-09-30 20:00 | 2.5121 | 3.1108 | 3.1604 | 3.3727 | 3.2878 | 3.5001 | 1.709 | 2.5888 | 3.0821 | 3.0821 | 3.411 | 3.411 | 2019-11-28 10:00 | 2.3625 | 3.8717 | 6.3555 | 6.3555 | 6.3555 | 6.3555
2021-09-30 21:00 | 2.4149 | 2.9905 | 3.0381 | 3.2422 | 3.1606 | 3.3647 | 1.5259 | 2.3115 | 2.7519 | 2.7519 | 3.0455 | 3.0455 | 2019-11-28 11:00 | 2.3092 | 3.7843 | 6.212 | 6.212 | 6.212 | 6.212
2021-09-30 22:00 | 2.2091 | 2.7357 | 2.7792 | 2.966 | 2.8913 | 3.078 | 1.3461 | 2.039 | 2.4276 | 2.4276 | 2.6866 | 2.6866 | 2019-11-28 12:00 | 2.332 | 3.8218 | 6.2735 | 6.2735 | 6.2735 | 6.2735
2021-09-30 23:00 | 1.9634 | 2.4313 | 2.47 | 2.636 | 2.5696 | 2.7356 | 1.166 | 1.7663 | 2.1029 | 2.1029 | 2.3272 | 2.3272 | 2019-11-28 13:00 | 2.454 | 4.0216 | 6.6015 | 6.6015 | 6.6015 | 6.6015
2021-10-01 | 1.7404 | 2.1179 | 2.0723 | 2.2289 | 2.1114 | 2.2681 | 1.126 | 1.9309 | 2.3826 | 2.3826 | 2.6838 | 2.6838 | 2019-11-28 14:00 | 2.4311 | 3.9841 | 6.54 | 6.54 | 6.54 | 6.54
2021-10-01 01:00 | 1.669 | 2.031 | 1.9872 | 2.1374 | 2.0247 | 2.175 | 0.94596 | 1.6222 | 2.0017 | 2.0017 | 2.2546 | 2.2546 | 2019-11-28 15:00 | 2.4616 | 4.0341 | 6.622 | 6.622 | 6.622 | 6.622
2021-10-01 02:00 | 1.6061 | 1.9545 | 1.9123 | 2.0569 | 1.9485 | 2.093 | 0.84884 | 1.4556 | 1.7962 | 1.7962 | 2.0232 | 2.0232 | 2019-11-28 16:00 | 2.5378 | 4.159 | 6.827 | 6.827 | 6.827 | 6.827
2021-10-01 03:00 | 1.6059 | 1.9542 | 1.9121 | 2.0566 | 1.9482 | 2.0927 | 0.77451 | 1.3282 | 1.6389 | 1.6389 | 1.846 | 1.846 | 2019-11-28 17:00 | 2.4159 | 3.9591 | 6.499 | 6.499 | 6.499 | 6.499
2021-10-01 04:00 | 1.6061 | 1.9545 | 1.9123 | 2.0569 | 1.9485 | 2.093 | 0.82021 | 1.4065 | 1.7356 | 1.7356 | 1.9549 | 1.9549 | 2019-11-28 18:00 | 2.1949 | 3.597 | 5.9044 | 5.9044 | 5.9044 | 5.9044
2021-10-01 05:00 | 1.6856 | 2.0512 | 2.007 | 2.1587 | 2.0449 | 2.1966 | 0.86171 | 1.4777 | 1.8234 | 1.8234 | 2.0539 | 2.0539 | 2019-11-28 19:00 | 2.1796 | 3.572 | 5.8634 | 5.8634 | 5.8634 | 5.8634
2021-10-01 06:00 | 2.032 | 2.4727 | 2.4193 | 2.6022 | 2.4651 | 2.6479 | 0.9431 | 1.6173 | 1.9956 | 1.9956 | 2.2478 | 2.2478 | 2019-11-28 20:00 | 1.9891 | 3.2597 | 5.3509 | 5.3509 | 5.3509 | 5.3509
2021-10-01 07:00 | 2.1577 | 2.6257 | 2.5691 | 2.7632 | 2.6176 | 2.8118 | 1.1289 | 1.9358 | 2.3887 | 2.3887 | 2.6906 | 2.6906 | 2019-11-28 21:00 | 1.9129 | 3.1348 | 5.1459 | 5.1459 | 5.1459 | 5.1459
2021-10-01 08:00 | 2.1806 | 2.6535 | 2.5963 | 2.7925 | 2.6453 | 2.8416 | 1.206 | 2.0681 | 2.552 | 2.552 | 2.8745 | 2.8745 | 2019-11-28 22:00 | 1.6995 | 2.7851 | 4.5718 | 4.5718 | 4.5718 | 4.5718
2021-10-01 09:00 | 2.0691 | 2.5179 | 2.4636 | 2.6498 | 2.5101 | 2.6963 | 1.2432 | 2.1318 | 2.6306 | 2.6306 | 2.9631 | 2.9631 | 2019-11-28 23:00 | 1.5166 | 2.4854 | 4.0798 | 4.0798 | 4.0798 | 4.0798
2021-10-01 10:00 | 1.9434 | 2.3649 | 2.3139 | 2.4888 | 2.3576 | 2.5325 | 1.1574 | 1.9848 | 2.4492 | 2.4492 | 2.7587 | 2.7587 | 2019-11-29 | 1.3642 | 2.2356 | 3.6698 | 3.6698 | 3.6698 | 3.6698
2021-10-01 11:00 | 1.9805 | 2.4101 | 2.3581 | 2.5363 | 2.4026 | 2.5809 | 1.2403 | 2.1269 | 2.6245 | 2.6245 | 2.9562 | 2.9562 | 2019-11-29 01:00 | 1.3108 | 2.1482 | 3.5263 | 3.5263 | 3.5263 | 3.5263
2021-10-01 12:00 | 2.092 | 2.5457 | 2.4908 | 2.6791 | 2.5379 | 2.7261 | 1.2803 | 2.1956 | 2.7092 | 2.7092 | 3.0516 | 3.0516 | 2019-11-29 02:00 | 1.3184 | 2.1607 | 3.5468 | 3.5468 | 3.5468 | 3.5468
2021-10-01 13:00 | 2.3092 | 2.81 | 2.7494 | 2.9572 | 2.8014 | 3.0092 | 1.3718 | 2.3524 | 2.9027 | 2.9027 | 3.2696 | 3.2696 | 2019-11-29 03:00 | 1.227 | 2.0108 | 3.3007 | 3.3007 | 3.3007 | 3.3007
2021-10-01 14:00 | 2.1949 | 2.6709 | 2.6133 | 2.8108 | 2.6627 | 2.8602 | 1.3518 | 2.3181 | 2.8604 | 2.8604 | 3.2219 | 3.2219 | 2019-11-29 04:00 | 1.227 | 2.0108 | 3.3007 | 3.3007 | 3.3007 | 3.3007
2021-10-01 15:00 | 1.9719 | 2.3996 | 2.3479 | 2.5254 | 2.3922 | 2.5697 | 1.2375 | 2.122 | 2.6185 | 2.6185 | 2.9494 | 2.9494 | 2019-11-29 05:00 | 1.3261 | 2.1732 | 3.5673 | 3.5673 | 3.5673 | 3.5673
2021-10-01 16:00 | 2.0366 | 2.4784 | 2.4249 | 2.6082 | 2.4707 | 2.654 | 1.3167 | 2.2579 | 2.7861 | 2.7861 | 3.1382 | 3.1382 | 2019-11-29 06:00 | 1.5394 | 2.5229 | 4.1413 | 4.1413 | 4.1413 | 4.1413
2021-10-01 17:00 | 2.372 | 2.8865 | 2.8243 | 3.0377 | 2.8776 | 3.0911 | 1.4432 | 2.4749 | 3.0539 | 3.0539 | 3.4399 | 3.4399 | 2019-11-29 07:00 | 1.9053 | 3.1224 | 5.1254 | 5.1254 | 5.1254 | 5.1254
2021-10-01 18:00 | 2.6664 | 3.2447 | 3.1747 | 3.4147 | 3.2347 | 3.4747 | 1.6261 | 2.7886 | 3.4409 | 3.4409 | 3.8758 | 3.8758 | 2019-11-29 08:00 | 2.3244 | 3.8093 | 6.253 | 6.253 | 6.253 | 6.253
2021-10-01 19:00 | 2.5635 | 3.1195 | 3.0522 | 3.283 | 3.1099 | 3.3406 | 1.6833 | 2.8866 | 3.5619 | 3.5619 | 4.0121 | 4.0121 | 2019-11-29 09:00 | 2.3244 | 3.8093 | 6.253 | 6.253 | 6.253 | 6.253
2021-10-01 20:00 | 2.5578 | 3.1126 | 3.0454 | 3.2756 | 3.103 | 3.3332 | 1.629 | 2.7935 | 3.447 | 3.447 | 3.8826 | 3.8826 | 2019-11-29 10:00 | 2.4006 | 3.9342 | 6.458 | 6.458 | 6.458 | 6.458
2021-10-01 21:00 | 2.3035 | 2.8031 | 2.7426 | 2.9499 | 2.7944 | 3.0017 | 1.4204 | 2.4357 | 3.0055 | 3.0055 | 3.3854 | 3.3854 | 2019-11-29 11:00 | 2.4845 | 4.0716 | 6.6835 | 6.6835 | 6.6835 | 6.6835
2021-10-01 22:00 | 2.1406 | 2.6048 | 2.5486 | 2.7413 | 2.5968 | 2.7895 | 1.3003 | 2.2299 | 2.7515 | 2.7515 | 3.0993 | 3.0993 | 2019-11-29 12:00 | 2.4921 | 4.084 | 6.704 | 6.704 | 6.704 | 6.704
2021-10-01 23:00 | 1.9777 | 2.4066 | 2.3547 | 2.5327 | 2.3992 | 2.5772 | 1.1231 | 1.926 | 2.3766 | 2.3766 | 2.677 | 2.677 | 2019-11-29 13:00 | 2.4921 | 4.084 | 6.704 | 6.704 | 6.704 | 6.704
2021-10-02 | 1.7462 | 2.1249 | 2.0791 | 2.2362 | 2.1184 | 2.2755 | 0.97475 | 1.6715 | 2.0626 | 2.0626 | 2.3233 | 2.3233 | 2019-11-29 14:00 | 2.4997 | 4.0965 | 6.7245 | 6.7245 | 6.7245 | 6.7245
2021-10-02 01:00 | 1.6347 | 1.9893 | 1.9464 | 2.0935 | 1.9831 | 2.1303 | 0.91688 | 1.5723 | 1.9401 | 1.9401 | 2.1853 | 2.1853 | 2019-11-29 15:00 | 2.5607 | 4.1964 | 6.8885 | 6.8885 | 6.8885 | 6.8885
2021-10-02 02:00 | 1.6004 | 1.9475 | 1.9055 | 2.0496 | 1.9415 | 2.0856 | 0.82592 | 1.4163 | 1.7477 | 1.7477 | 1.9686 | 1.9686 | 2019-11-29 16:00 | 2.5607 | 4.1964 | 6.8885 | 6.8885 | 6.8885 | 6.8885
2021-10-02 03:00 | 1.5347 | 1.8675 | 1.8273 | 1.9654 | 1.8618 | 1.9999 | 0.84593 | 1.4506 | 1.79 | 1.79 | 2.0162 | 2.0162 | 2019-11-29 17:00 | 2.4311 | 3.9841 | 6.54 | 6.54 | 6.54 | 6.54
2021-10-02 04:00 | 1.5575 | 1.8954 | 1.8545 | 1.9947 | 1.8895 | 2.0297 | 0.82307 | 1.4114 | 1.7416 | 1.7416 | 1.9617 | 1.9617 | 2019-11-29 18:00 | 2.2711 | 3.7218 | 6.1095 | 6.1095 | 6.1095 | 6.1095
2021-10-02 05:00 | 1.5833 | 1.9267 | 1.8851 | 2.0276 | 1.9207 | 2.0632 | 0.84021 | 1.4408 | 1.7779 | 1.7779 | 2.0026 | 2.0026 | 2019-11-29 19:00 | 2.0805 | 3.4096 | 5.5969 | 5.5969 | 5.5969 | 5.5969
2021-10-02 06:00 | 1.6804 | 2.0449 | 2.0008 | 2.152 | 2.0386 | 2.1898 | 0.86022 | 1.4751 | 1.8202 | 1.8202 | 2.0503 | 2.0503 | 2019-11-29 20:00 | 1.951 | 3.1973 | 5.2484 | 5.2484 | 5.2484 | 5.2484
2021-10-02 07:00 | 1.7807 | 2.1669 | 2.1201 | 2.2804 | 2.1602 | 2.3204 | 0.96596 | 1.6565 | 2.044 | 2.044 | 2.3023 | 2.3023 | 2019-11-29 21:00 | 1.9357 | 3.1723 | 5.2074 | 5.2074 | 5.2074 | 5.2074
2021-10-02 08:00 | 1.8519 | 2.2536 | 2.205 | 2.3716 | 2.2466 | 2.4133 | 1.0945 | 1.8768 | 2.3159 | 2.3159 | 2.6086 | 2.6086 | 2019-11-29 22:00 | 1.6842 | 2.7602 | 4.5308 | 4.5308 | 4.5308 | 4.5308
2021-10-02 09:00 | 1.9319 | 2.351 | 2.3002 | 2.4741 | 2.3437 | 2.5176 | 1.1717 | 2.0093 | 2.4794 | 2.4794 | 2.7928 | 2.7928 | 2019-11-29 23:00 | 1.5318 | 2.5104 | 4.1208 | 4.1208 | 4.1208 | 4.1208
2021-10-02 10:00 | 1.9977 | 2.4309 | 2.3785 | 2.5583 | 2.4235 | 2.6032 | 1.3032 | 2.2348 | 2.7576 | 2.7576 | 3.1061 | 3.1061 | 2019-11-30 | 1.4251 | 2.3355 | 3.8338 | 3.8338 | 3.8338 | 3.8338
2021-10-02 11:00 | 1.9777 | 2.4066 | 2.3547 | 2.5327 | 2.3992 | 2.5772 | 1.3575 | 2.3279 | 2.8725 | 2.8725 | 3.2355 | 3.2355 | 2019-11-30 01:00 | 1.4175 | 2.323 | 3.8133 | 3.8133 | 3.8133 | 3.8133
2021-10-02 12:00 | 2.0891 | 2.5422 | 2.4874 | 2.6754 | 2.5344 | 2.7224 | 1.3718 | 2.3524 | 2.9027 | 2.9027 | 3.2696 | 3.2696 | 2019-11-30 02:00 | 1.3261 | 2.1732 | 3.5673 | 3.5673 | 3.5673 | 3.5673
2021-10-02 13:00 | 2.0891 | 2.5422 | 2.4874 | 2.6754 | 2.5344 | 2.7224 | 1.3461 | 2.3083 | 2.8483 | 2.8483 | 3.2083 | 3.2083 | 2019-11-30 03:00 | 1.2346 | 2.0233 | 3.3212 | 3.3212 | 3.3212 | 3.3212
2021-10-02 14:00 | 1.9691 | 2.3962 | 2.3445 | 2.5217 | 2.3888 | 2.566 | 1.3375 | 2.2936 | 2.8301 | 2.8301 | 3.1878 | 3.1878 | 2019-11-30 04:00 | 1.3413 | 2.1981 | 3.6083 | 3.6083 | 3.6083 | 3.6083
2021-10-02 15:00 | 1.9883 | 2.4195 | 2.3674 | 2.5463 | 2.4121 | 2.591 | 1.3775 | 2.3622 | 2.9148 | 2.9148 | 3.2832 | 3.2832 | 2019-11-30 05:00 | 1.4099 | 2.3105 | 3.7928 | 3.7928 | 3.7928 | 3.7928
2021-10-02 16:00 | 2.0634 | 2.5109 | 2.4568 | 2.6425 | 2.5032 | 2.6889 | 1.4347 | 2.4602 | 3.0357 | 3.0357 | 3.4194 | 3.4194 | 2019-11-30 06:00 | 1.3337 | 2.1856 | 3.5878 | 3.5878 | 3.5878 | 3.5878
2021-10-02 17:00 | 2.332 | 2.8378 | 2.7766 | 2.9865 | 2.8291 | 3.039 | 1.4832 | 2.5435 | 3.1385 | 3.1385 | 3.5352 | 3.5352 | 2019-11-30 07:00 | 1.6842 | 2.7602 | 4.5308 | 4.5308 | 4.5308 | 4.5308
2021-10-02 18:00 | 2.5607 | 3.1161 | 3.0488 | 3.2793 | 3.1065 | 3.3369 | 1.6719 | 2.867 | 3.5377 | 3.5377 | 3.9848 | 3.9848 | 2019-11-30 08:00 | 1.8748 | 3.0724 | 5.0434 | 5.0434 | 5.0434 | 5.0434
2021-10-02 19:00 | 2.5235 | 3.0708 | 3.0046 | 3.2317 | 3.0614 | 3.2885 | 1.6519 | 2.8327 | 3.4953 | 3.4953 | 3.9371 | 3.9371 | 2019-11-30 09:00 | 1.9281 | 3.1598 | 5.1869 | 5.1869 | 5.1869 | 5.1869
2021-10-02 20:00 | 2.283 | 2.7782 | 2.7183 | 2.9237 | 2.7696 | 2.9751 | 1.5318 | 2.6268 | 3.2414 | 3.2414 | 3.651 | 3.651 | 2019-11-30 10:00 | 2.0196 | 3.3097 | 5.4329 | 5.4329 | 5.4329 | 5.4329
2021-10-02 21:00 | 2.1348 | 2.5979 | 2.5418 | 2.734 | 2.5899 | 2.782 | 1.4175 | 2.4308 | 2.9995 | 2.9995 | 3.3786 | 3.3786 | 2019-11-30 11:00 | 1.9662 | 3.2223 | 5.2894 | 5.2894 | 5.2894 | 5.2894
2021-10-02 22:00 | 2.0662 | 2.5144 | 2.4602 | 2.6461 | 2.5067 | 2.6926 | 1.286 | 2.2054 | 2.7213 | 2.7213 | 3.0652 | 3.0652 | 2019-11-30 12:00 | 1.9967 | 3.2722 | 5.3714 | 5.3714 | 5.3714 | 5.3714
2021-10-02 23:00 | 1.9662 | 2.3927 | 2.3411 | 2.518 | 2.3853 | 2.5623 | 1.1717 | 2.0093 | 2.4794 | 2.4794 | 2.7928 | 2.7928 | 2019-11-30 13:00 | 1.9662 | 3.2223 | 5.2894 | 5.2894 | 5.2894 | 5.2894
2021-10-03 | 1.7719 | 2.1562 | 2.1097 | 2.2692 | 2.1496 | 2.309 | 1.0181 | 1.7459 | 2.1543 | 2.1543 | 2.4266 | 2.4266 | 2019-11-30 14:00 | 1.9129 | 3.1348 | 5.1459 | 5.1459 | 5.1459 | 5.1459
2021-10-03 01:00 | 1.6 | 1.9471 | 1.9051 | 2.0491 | 1.9411 | 2.0851 | 0.86032 | 1.4753 | 1.8204 | 1.8204 | 2.0505 | 2.0505 | 2019-11-30 15:00 | 1.9281 | 3.1598 | 5.1869 | 5.1869 | 5.1869 | 5.1869
2021-10-03 03:00 | 1.6004 | 1.9475 | 1.9055 | 2.0496 | 1.9415 | 2.0856 | 0.8345 | 1.431 | 1.7658 | 1.7658 | 1.989 | 1.989 | 2019-11-30 16:00 | 1.9662 | 3.2223 | 5.2894 | 5.2894 | 5.2894 | 5.2894
2021-10-03 04:00 | 1.5404 | 1.8745 | 1.8341 | 1.9727 | 1.8687 | 2.0074 | 0.80592 | 1.382 | 1.7053 | 1.7053 | 1.9209 | 1.9209 | 2019-11-30 17:00 | 1.8976 | 3.1099 | 5.1049 | 5.1049 | 5.1049 | 5.1049
2021-10-03 05:00 | 1.5967 | 1.943 | 1.9011 | 2.0448 | 1.937 | 2.0807 | 0.82592 | 1.4163 | 1.7477 | 1.7477 | 1.9686 | 1.9686 | 2019-11-30 18:00 | 1.8138 | 2.9725 | 4.8794 | 4.8794 | 4.8794 | 4.8794
2021-10-03 06:00 | 1.669 | 2.031 | 1.9872 | 2.1374 | 2.0247 | 2.175 | 0.82878 | 1.4212 | 1.7537 | 1.7537 | 1.9754 | 1.9754 | 2019-11-30 19:00 | 1.7528 | 2.8726 | 4.7154 | 4.7154 | 4.7154 | 4.7154
2021-10-03 07:00 | 1.769 | 2.1527 | 2.1063 | 2.2655 | 2.1461 | 2.3053 | 0.92309 | 1.583 | 1.9533 | 1.9533 | 2.2002 | 2.2002 | 2019-11-30 20:00 | 1.608 | 2.6353 | 4.3258 | 4.3258 | 4.3258 | 4.3258
2021-10-03 08:00 | 1.849 | 2.2501 | 2.2016 | 2.368 | 2.2432 | 2.4096 | 1.0403 | 1.7839 | 2.2012 | 2.2012 | 2.4794 | 2.4794 | 2019-11-30 21:00 | 1.6309 | 2.6727 | 4.3873 | 4.3873 | 4.3873 | 4.3873
2021-10-03 09:00 | 1.9519 | 2.3753 | 2.3241 | 2.4997 | 2.368 | 2.5437 | 1.1346 | 1.9456 | 2.4008 | 2.4008 | 2.7042 | 2.7042 | 2019-11-30 22:00 | 1.5166 | 2.4854 | 4.0798 | 4.0798 | 4.0798 | 4.0798
2021-10-03 10:00 | 1.9319 | 2.351 | 2.3002 | 2.4741 | 2.3437 | 2.5176 | 1.2632 | 2.1662 | 2.6729 | 2.6729 | 3.0107 | 3.0107 | 2019-11-30 23:00 | 1.4937 | 2.4479 | 4.0183 | 4.0183 | 4.0183 | 4.0183
2021-10-03 11:00 | 2.0377 | 2.4796 | 2.4261 | 2.6095 | 2.472 | 2.6554 | 1.3089 | 2.2446 | 2.7697 | 2.7697 | 3.1197 | 3.1197 | 2019-12-01 | 1.3565 | 2.2231 | 3.6493 | 3.6493 | 3.6493 | 3.6493
2021-10-03 12:00 | 1.8662 | 2.271 | 2.222 | 2.3899 | 2.264 | 2.4319 | 1.2575 | 2.1564 | 2.6608 | 2.6608 | 2.9971 | 2.9971 | 2019-12-01 01:00 | 1.3261 | 2.1732 | 3.5673 | 3.5673 | 3.5673 | 3.5673
2021-10-03 13:00 | 1.7119 | 2.0832 | 2.0382 | 2.1923 | 2.0767 | 2.2308 | 1.2403 | 2.1269 | 2.6245 | 2.6245 | 2.9562 | 2.9562 | 2019-12-01 02:00 | 1.2727 | 2.0857 | 3.4238 | 3.4238 | 3.4238 | 3.4238
2021-10-03 14:00 | 1.7919 | 2.1805 | 2.1335 | 2.2948 | 2.1738 | 2.3351 | 1.2546 | 2.1515 | 2.6548 | 2.6548 | 2.9903 | 2.9903 | 2019-12-01 03:00 | 1.2575 | 2.0608 | 3.3828 | 3.3828 | 3.3828 | 3.3828
2021-10-03 15:00 | 1.8948 | 2.3057 | 2.256 | 2.4265 | 2.2986 | 2.4692 | 1.3661 | 2.3426 | 2.8906 | 2.8906 | 3.256 | 3.256 | 2019-12-01 04:00 | 1.3337 | 2.1856 | 3.5878 | 3.5878 | 3.5878 | 3.5878
2021-10-03 16:00 | 1.8862 | 2.2953 | 2.2458 | 2.4156 | 2.2882 | 2.458 | 1.3804 | 2.3671 | 2.9208 | 2.9208 | 3.29 | 3.29 | 2019-12-01 05:00 | 1.3565 | 2.2231 | 3.6493 | 3.6493 | 3.6493 | 3.6493
2021-10-03 17:00 | 2.0447 | 2.4882 | 2.4345 | 2.6185 | 2.4805 | 2.6645 | 1.3346 | 2.2887 | 2.8241 | 2.8241 | 3.181 | 3.181 | 2019-12-01 06:00 | 1.2803 | 2.0982 | 3.4443 | 3.4443 | 3.4443 | 3.4443
2021-10-03 18:00 | 2.2591 | 2.7491 | 2.6898 | 2.8931 | 2.7406 | 2.944 | 1.4318 | 2.4553 | 3.0297 | 3.0297 | 3.4126 | 3.4126 | 2019-12-01 07:00 | 1.6309 | 2.6727 | 4.3873 | 4.3873 | 4.3873 | 4.3873
2021-10-03 19:00 | 2.3035 | 2.8031 | 2.7426 | 2.9499 | 2.7944 | 3.0017 | 1.649 | 2.8278 | 3.4893 | 3.4893 | 3.9303 | 3.9303 | 2019-12-01 08:00 | 1.6842 | 2.7602 | 4.5308 | 4.5308 | 4.5308 | 4.5308
2021-10-03 20:00 | 2.3035 | 2.8031 | 2.7426 | 2.9499 | 2.7944 | 3.0017 | 1.6776 | 2.8768 | 3.5498 | 3.5498 | 3.9984 | 3.9984 | 2019-12-01 09:00 | 1.7986 | 2.9475 | 4.8384 | 4.8384 | 4.8384 | 4.8384
2021-10-03 21:00 | 2.132 | 2.5944 | 2.5384 | 2.7303 | 2.5864 | 2.7783 | 1.4407 | 2.4706 | 3.0485 | 3.0485 | 3.4338 | 3.4338 | 2019-12-01 10:00 | 1.8062 | 2.96 | 4.8589 | 4.8589 | 4.8589 | 4.8589
2021-10-03 22:00 | 2.0462 | 2.4901 | 2.4364 | 2.6205 | 2.4824 | 2.6666 | 1.2432 | 2.1318 | 2.6306 | 2.6306 | 2.9631 | 2.9631 | 2019-12-01 11:00 | 1.9053 | 3.1224 | 5.1254 | 5.1254 | 5.1254 | 5.1254
2021-10-03 23:00 | 1.9033 | 2.3162 | 2.2662 | 2.4375 | 2.309 | 2.4803 | 1.1546 | 1.9799 | 2.4431 | 2.4431 | 2.7519 | 2.7519 | 2019-12-01 12:00 | 1.8748 | 3.0724 | 5.0434 | 5.0434 | 5.0434 | 5.0434
2021-10-04 | 1.7719 | 2.1562 | 2.1097 | 2.2692 | 2.1496 | 2.309 | 1.0176 | 1.7451 | 2.1533 | 2.1533 | 2.4255 | 2.4255 | 2019-12-01 13:00 | 1.8214 | 2.985 | 4.8999 | 4.8999 | 4.8999 | 4.8999
2021-10-04 01:00 | 1.5718 | 1.9128 | 1.8715 | 2.013 | 1.9069 | 2.0483 | 0.9431 | 1.6173 | 1.9956 | 1.9956 | 2.2478 | 2.2478 | 2019-12-01 14:00 | 1.7681 | 2.8975 | 4.7564 | 4.7564 | 4.7564 | 4.7564
2021-10-04 02:00 | 1.5118 | 1.8397 | 1.8 | 1.9361 | 1.8341 | 1.9701 | 0.79735 | 1.3673 | 1.6872 | 1.6872 | 1.9004 | 1.9004 | 2019-12-01 15:00 | 1.8214 | 2.985 | 4.8999 | 4.8999 | 4.8999 | 4.8999
2021-10-04 03:00 | 1.5204 | 1.8502 | 1.8102 | 1.9471 | 1.8445 | 1.9813 | 0.77442 | 1.328 | 1.6387 | 1.6387 | 1.8458 | 1.8458 | 2019-12-01 16:00 | 1.9053 | 3.1224 | 5.1254 | 5.1254 | 5.1254 | 5.1254
2021-10-04 04:00 | 1.5575 | 1.8954 | 1.8545 | 1.9947 | 1.8895 | 2.0297 | 0.77448 | 1.3281 | 1.6388 | 1.6388 | 1.8459 | 1.8459 | 2019-12-01 17:00 | 1.6842 | 2.7602 | 4.5308 | 4.5308 | 4.5308 | 4.5308
2021-10-04 05:00 | 1.5542 | 1.8913 | 1.8505 | 1.9904 | 1.8855 | 2.0254 | 0.74016 | 1.2693 | 1.5662 | 1.5662 | 1.7641 | 1.7641 | 2019-12-01 18:00 | 1.6004 | 2.6228 | 4.3053 | 4.3053 | 4.3053 | 4.3053
2021-10-04 06:00 | 1.629 | 1.9823 | 1.9396 | 2.0862 | 1.9762 | 2.1228 | 0.81164 | 1.3918 | 1.7174 | 1.7174 | 1.9345 | 1.9345 | 2019-12-01 19:00 | 1.5471 | 2.5353 | 4.1618 | 4.1618 | 4.1618 | 4.1618
2021-10-04 07:00 | 1.7633 | 2.1458 | 2.0995 | 2.2582 | 2.1392 | 2.2979 | 0.88838 | 1.5234 | 1.8798 | 1.8798 | 2.1174 | 2.1174 | 2019-12-01 20:00 | 1.5547 | 2.5478 | 4.1823 | 4.1823 | 4.1823 | 4.1823
2021-10-04 08:00 | 1.8319 | 2.2292 | 2.1811 | 2.346 | 2.2224 | 2.3872 | 0.9431 | 1.6173 | 1.9956 | 1.9956 | 2.2478 | 2.2478 | 2019-12-01 21:00 | 1.5547 | 2.5478 | 4.1823 | 4.1823 | 4.1823 | 4.1823
2021-10-04 09:00 | 1.8062 | 2.1979 | 2.1505 | 2.3131 | 2.1912 | 2.3537 | 1.0946 | 1.877 | 2.3161 | 2.3161 | 2.6089 | 2.6089 | 2019-12-01 22:00 | 1.4023 | 2.2981 | 3.7723 | 3.7723 | 3.7723 | 3.7723
2021-10-04 10:00 | 1.8548 | 2.2571 | 2.2084 | 2.3753 | 2.2501 | 2.417 | 1.1603 | 1.9897 | 2.4552 | 2.4552 | 2.7655 | 2.7655 | 2019-12-01 23:00 | 1.387 | 2.2731 | 3.7313 | 3.7313 | 3.7313 | 3.7313
2021-10-04 11:00 | 1.9062 | 2.3197 | 2.2696 | 2.4412 | 2.3125 | 2.4841 | 1.1889 | 2.0387 | 2.5157 | 2.5157 | 2.8336 | 2.8336 | 2019-12-02 | 1.3184 | 2.1607 | 3.5468 | 3.5468 | 3.5468 | 3.5468
2021-10-04 12:00 | 1.809 | 2.2014 | 2.1539 | 2.3167 | 2.1946 | 2.3574 | 1.1746 | 2.0142 | 2.4854 | 2.4854 | 2.7996 | 2.7996 | 2019-12-02 01:00 | 1.2803 | 2.0982 | 3.4443 | 3.4443 | 3.4443 | 3.4443
2021-10-04 13:00 | 1.5061 | 1.8328 | 1.7932 | 1.9288 | 1.8271 | 1.9627 | 1.126 | 1.9309 | 2.3826 | 2.3826 | 2.6838 | 2.6838 | 2019-12-02 02:00 | 1.2422 | 2.0358 | 3.3417 | 3.3417 | 3.3417 | 3.3417
2021-10-04 14:00 | 1.4689 | 1.7876 | 1.749 | 1.8812 | 1.7821 | 1.9143 | 1.1374 | 1.9505 | 2.4068 | 2.4068 | 2.711 | 2.711 | 2019-12-02 03:00 | 1.2194 | 1.9983 | 3.2802 | 3.2802 | 3.2802 | 3.2802
2021-10-04 15:00 | 1.709 | 2.0797 | 2.0348 | 2.1886 | 2.0733 | 2.2271 | 1.1689 | 2.0044 | 2.4733 | 2.4733 | 2.786 | 2.786 | 2019-12-02 04:00 | 1.2727 | 2.0857 | 3.4238 | 3.4238 | 3.4238 | 3.4238
2021-10-04 16:00 | 1.6833 | 2.0484 | 2.0042 | 2.1557 | 2.0421 | 2.1936 | 1.306 | 2.2397 | 2.7636 | 2.7636 | 3.1129 | 3.1129 | 2019-12-02 05:00 | 1.387 | 2.2731 | 3.7313 | 3.7313 | 3.7313 | 3.7313
2021-10-04 17:00 | 2.0428 | 2.4858 | 2.4322 | 2.616 | 2.4782 | 2.662 | 1.3432 | 2.3034 | 2.8422 | 2.8422 | 3.2015 | 3.2015 | 2019-12-02 06:00 | 1.4709 | 2.4105 | 3.9568 | 3.9568 | 3.9568 | 3.9568
2021-10-04 18:00 | 2.3492 | 2.8587 | 2.797 | 3.0085 | 2.8499 | 3.0613 | 1.6318 | 2.7984 | 3.453 | 3.453 | 3.8894 | 3.8894 | 2019-12-02 07:00 | 1.9434 | 3.1848 | 5.2279 | 5.2279 | 5.2279 | 5.2279
2021-10-04 19:00 | 2.5064 | 3.05 | 2.9842 | 3.2098 | 3.0406 | 3.2662 | 1.7776 | 3.0483 | 3.7614 | 3.7614 | 4.2368 | 4.2368 | 2019-12-02 08:00 | 2.0348 | 3.3347 | 5.4739 | 5.4739 | 5.4739 | 5.4739
2021-10-04 20:00 | 2.4635 | 2.9978 | 2.9331 | 3.1549 | 2.9886 | 3.2103 | 1.7119 | 2.9356 | 3.6223 | 3.6223 | 4.0802 | 4.0802 | 2019-12-02 09:00 | 2.0348 | 3.3347 | 5.4739 | 5.4739 | 5.4739 | 5.4739
2021-10-04 21:00 | 2.3006 | 2.7996 | 2.7392 | 2.9462 | 2.791 | 2.998 | 1.489 | 2.5533 | 3.1506 | 3.1506 | 3.5489 | 3.5489 | 2019-12-02 10:00 | 2.0805 | 3.4096 | 5.5969 | 5.5969 | 5.5969 | 5.5969
2021-10-04 22:00 | 2.1177 | 2.577 | 2.5214 | 2.712 | 2.5691 | 2.7597 | 1.3183 | 2.2607 | 2.7895 | 2.7895 | 3.1421 | 3.1421 | 2019-12-02 11:00 | 2.0653 | 3.3846 | 5.5559 | 5.5559 | 5.5559 | 5.5559
2021-10-04 23:00 | 1.9119 | 2.3266 | 2.2764 | 2.4485 | 2.3194 | 2.4915 | 1.2146 | 2.0828 | 2.5701 | 2.5701 | 2.8949 | 2.8949 | 2019-12-02 12:00 | 2.1491 | 3.522 | 5.7814 | 5.7814 | 5.7814 | 5.7814
2021-10-05 | 1.8176 | 2.2118 | 2.1641 | 2.3277 | 2.205 | 2.3686 | 1.0817 | 1.855 | 2.289 | 2.289 | 2.5783 | 2.5783 | 2019-12-02 13:00 | 2.0577 | 3.3721 | 5.5354 | 5.5354 | 5.5354 | 5.5354
2021-10-05 01:00 | 1.6353 | 1.99 | 1.9471 | 2.0943 | 1.9839 | 2.131 | 0.93167 | 1.5977 | 1.9714 | 1.9714 | 2.2206 | 2.2206 | 2019-12-02 14:00 | 2.0196 | 3.3097 | 5.4329 | 5.4329 | 5.4329 | 5.4329
2021-10-05 02:00 | 1.6061 | 1.9545 | 1.9123 | 2.0569 | 1.9485 | 2.093 | 0.82878 | 1.4212 | 1.7537 | 1.7537 | 1.9754 | 1.9754 | 2019-12-02 15:00 | 1.9738 | 3.2348 | 5.3099 | 5.3099 | 5.3099 | 5.3099
2021-10-05 03:00 | 1.5661 | 1.9058 | 1.8647 | 2.0056 | 1.8999 | 2.0409 | 0.79735 | 1.3673 | 1.6872 | 1.6872 | 1.9004 | 1.9004 | 2019-12-02 16:00 | 1.9053 | 3.1224 | 5.1254 | 5.1254 | 5.1254 | 5.1254
2021-10-05 04:00 | 1.5232 | 1.8535 | 1.8135 | 1.9506 | 1.8478 | 1.9849 | 0.79156 | 1.3574 | 1.675 | 1.675 | 1.8867 | 1.8867 | 2019-12-02 17:00 | 1.8367 | 3.0099 | 4.9409 | 4.9409 | 4.9409 | 4.9409
2021-10-05 05:00 | 1.6661 | 2.0275 | 1.9838 | 2.1337 | 2.0213 | 2.1712 | 0.863 | 1.4799 | 1.8261 | 1.8261 | 2.0569 | 2.0569 | 2019-12-02 18:00 | 1.7757 | 2.91 | 4.7769 | 4.7769 | 4.7769 | 4.7769
2021-10-05 06:00 | 2.0001 | 2.434 | 2.3815 | 2.5615 | 2.4265 | 2.6065 | 0.89737 | 1.5388 | 1.8988 | 1.8988 | 2.1388 | 2.1388 | 2019-12-02 19:00 | 1.7909 | 2.935 | 4.8179 | 4.8179 | 4.8179 | 4.8179
2021-10-05 07:00 | 2.3063 | 2.8065 | 2.746 | 2.9536 | 2.7979 | 3.0055 | 1.2032 | 2.0632 | 2.5459 | 2.5459 | 2.8677 | 2.8677 | 2019-12-02 20:00 | 1.73 | 2.8351 | 4.6538 | 4.6538 | 4.6538 | 4.6538
2021-10-05 08:00 | 2.6493 | 3.2239 | 3.1543 | 3.3928 | 3.2139 | 3.4524 | 1.3403 | 2.2985 | 2.8362 | 2.8362 | 3.1947 | 3.1947 | 2019-12-02 21:00 | 1.6385 | 2.6852 | 4.4078 | 4.4078 | 4.4078 | 4.4078
2021-10-05 09:00 | 2.6435 | 3.2169 | 3.1475 | 3.3854 | 3.207 | 3.4449 | 1.3918 | 2.3867 | 2.945 | 2.945 | 3.3173 | 3.3173 | 2019-12-02 22:00 | 1.5318 | 2.5104 | 4.1208 | 4.1208 | 4.1208 | 4.1208
2021-10-05 10:00 | 2.5521 | 3.1056 | 3.0386 | 3.2683 | 3.0961 | 3.3257 | 1.3718 | 2.3524 | 2.9027 | 2.9027 | 3.2696 | 3.2696 | 2019-12-02 23:00 | 1.3946 | 2.2856 | 3.7518 | 3.7518 | 3.7518 | 3.7518
2021-10-05 11:00 | 2.2177 | 2.6987 | 2.6405 | 2.8401 | 2.6904 | 2.89 | 1.3175 | 2.2593 | 2.7878 | 2.7878 | 3.1402 | 3.1402 | 2019-12-03 | 1.3032 | 2.1357 | 3.5058 | 3.5058 | 3.5058 | 3.5058
2021-10-05 12:00 | 2.1691 | 2.6396 | 2.5827 | 2.7779 | 2.6315 | 2.8267 | 1.2803 | 2.1956 | 2.7092 | 2.7092 | 3.0516 | 3.0516 | 2019-12-03 01:00 | 1.2422 | 2.0358 | 3.3417 | 3.3417 | 3.3417 | 3.3417
2021-10-05 13:00 | 1.9176 | 2.3336 | 2.2832 | 2.4558 | 2.3264 | 2.499 | 1.3232 | 2.2691 | 2.7999 | 2.7999 | 3.1538 | 3.1538 | 2019-12-03 02:00 | 1.1355 | 1.8609 | 3.0547 | 3.0547 | 3.0547 | 3.0547
2021-10-05 14:00 | 1.7433 | 2.1214 | 2.0757 | 2.2326 | 2.1149 | 2.2718 | 1.2517 | 2.1466 | 2.6487 | 2.6487 | 2.9835 | 2.9835 | 2019-12-03 03:00 | 1.166 | 1.9109 | 3.1367 | 3.1367 | 3.1367 | 3.1367
2021-10-05 15:00 | 1.7576 | 2.1388 | 2.0927 | 2.2509 | 2.1322 | 2.2904 | 1.2317 | 2.1122 | 2.6064 | 2.6064 | 2.9358 | 2.9358 | 2019-12-03 04:00 | 1.166 | 1.9109 | 3.1367 | 3.1367 | 3.1367 | 3.1367
2021-10-05 16:00 | 2.1346 | 2.5976 | 2.5416 | 2.7337 | 2.5896 | 2.7817 | 1.3461 | 2.3083 | 2.8483 | 2.8483 | 3.2083 | 3.2083 | 2019-12-03 05:00 | 1.2727 | 2.0857 | 3.4238 | 3.4238 | 3.4238 | 3.4238
2021-10-05 17:00 | 2.5835 | 3.1439 | 3.0761 | 3.3086 | 3.1342 | 3.3667 | 1.6233 | 2.7837 | 3.4349 | 3.4349 | 3.869 | 3.869 | 2019-12-03 06:00 | 1.5699 | 2.5728 | 4.2233 | 4.2233 | 4.2233 | 4.2233
2021-10-05 18:00 | 2.8493 | 3.4673 | 3.3925 | 3.649 | 3.4566 | 3.7131 | 1.7462 | 2.9944 | 3.6949 | 3.6949 | 4.1619 | 4.1619 | 2019-12-03 07:00 | 1.8595 | 3.0474 | 5.0024 | 5.0024 | 5.0024 | 5.0024
2021-10-05 19:00 | 2.8464 | 3.4638 | 3.3891 | 3.6453 | 3.4532 | 3.7093 | 1.8605 | 3.1904 | 3.9368 | 3.9368 | 4.4344 | 4.4344 | 2019-12-03 08:00 | 1.951 | 3.1973 | 5.2484 | 5.2484 | 5.2484 | 5.2484
2021-10-05 20:00 | 2.7207 | 3.3108 | 3.2394 | 3.4843 | 3.3006 | 3.5455 | 1.7662 | 3.0287 | 3.7372 | 3.7372 | 4.2096 | 4.2096 | 2019-12-03 09:00 | 1.9967 | 3.2722 | 5.3714 | 5.3714 | 5.3714 | 5.3714
2021-10-05 21:00 | 2.5521 | 3.1056 | 3.0386 | 3.2683 | 3.0961 | 3.3257 | 1.5977 | 2.7398 | 3.3807 | 3.3807 | 3.808 | 3.808 | 2019-12-03 10:00 | 2.0043 | 3.2847 | 5.3919 | 5.3919 | 5.3919 | 5.3919
2021-10-05 22:00 | 2.3322 | 2.8381 | 2.7769 | 2.9868 | 2.8293 | 3.0392 | 1.4146 | 2.4259 | 2.9934 | 2.9934 | 3.3718 | 3.3718 | 2019-12-03 11:00 | 2.0043 | 3.2847 | 5.3919 | 5.3919 | 5.3919 | 5.3919
2021-10-05 23:00 | 1.9777 | 2.4066 | 2.3547 | 2.5327 | 2.3992 | 2.5772 | 1.2203 | 2.0926 | 2.5822 | 2.5822 | 2.9086 | 2.9086 | 2019-12-03 12:00 | 1.9815 | 3.2472 | 5.3304 | 5.3304 | 5.3304 | 5.3304
2021-10-06 | 1.9148 | 2.3301 | 2.2798 | 2.4522 | 2.3229 | 2.4952 | 1.0794 | 1.851 | 2.2841 | 2.2841 | 2.5728 | 2.5728 | 2019-12-03 13:00 | 2.0577 | 3.3721 | 5.5354 | 5.5354 | 5.5354 | 5.5354
2021-10-06 01:00 | 1.7038 | 2.0734 | 2.0287 | 2.182 | 2.067 | 2.2204 | 0.98311 | 1.6859 | 2.0803 | 2.0803 | 2.3432 | 2.3432 | 2019-12-03 14:00 | 2.0348 | 3.3347 | 5.4739 | 5.4739 | 5.4739 | 5.4739
2021-10-06 02:00 | 1.6261 | 1.9788 | 1.9361 | 2.0825 | 1.9727 | 2.1191 | 0.88021 | 1.5094 | 1.8625 | 1.8625 | 2.0979 | 2.0979 | 2019-12-03 15:00 | 2.0501 | 3.3597 | 5.5149 | 5.5149 | 5.5149 | 5.5149
2021-10-06 03:00 | 1.6061 | 1.9544 | 1.9123 | 2.0568 | 1.9484 | 2.0929 | 0.88022 | 1.5094 | 1.8626 | 1.8626 | 2.098 | 2.098 | 2019-12-03 16:00 | 2.0805 | 3.4096 | 5.5969 | 5.5969 | 5.5969 | 5.5969
2021-10-06 04:00 | 1.6576 | 2.0171 | 1.9736 | 2.1228 | 2.0109 | 2.1601 | 0.84593 | 1.4506 | 1.79 | 1.79 | 2.0162 | 2.0162 | 2019-12-03 17:00 | 1.9357 | 3.1723 | 5.2074 | 5.2074 | 5.2074 | 5.2074
2021-10-06 05:00 | 1.843 | 2.2427 | 2.1943 | 2.3602 | 2.2358 | 2.4016 | 0.95739 | 1.6418 | 2.0258 | 2.0258 | 2.2819 | 2.2819 | 2019-12-03 18:00 | 1.8062 | 2.96 | 4.8589 | 4.8589 | 4.8589 | 4.8589
2021-10-06 06:00 | 2.2434 | 2.73 | 2.6711 | 2.873 | 2.7216 | 2.9235 | 1.0717 | 1.8378 | 2.2677 | 2.2677 | 2.5544 | 2.5544 | 2019-12-03 19:00 | 1.8214 | 2.985 | 4.8999 | 4.8999 | 4.8999 | 4.8999
2021-10-06 07:00 | 2.6693 | 3.2482 | 3.1781 | 3.4184 | 3.2382 | 3.4784 | 1.3589 | 2.3302 | 2.8754 | 2.8754 | 3.2388 | 3.2388 | 2019-12-03 20:00 | 1.7376 | 2.8476 | 4.6744 | 4.6744 | 4.6744 | 4.6744
2021-10-06 08:00 | 2.6921 | 3.276 | 3.2054 | 3.4477 | 3.2659 | 3.5082 | 1.3661 | 2.3426 | 2.8906 | 2.8906 | 3.256 | 3.256 | 2019-12-03 21:00 | 1.5623 | 2.5603 | 4.2028 | 4.2028 | 4.2028 | 4.2028
2021-10-06 09:00 | 2.372 | 2.8865 | 2.8243 | 3.0377 | 2.8776 | 3.0911 | 1.4004 | 2.4014 | 2.9632 | 2.9632 | 3.3377 | 3.3377 | 2019-12-03 22:00 | 1.4937 | 2.4479 | 4.0183 | 4.0183 | 4.0183 | 4.0183
2021-10-06 10:00 | 2.0177 | 2.4553 | 2.4023 | 2.5839 | 2.4477 | 2.6293 | 1.3232 | 2.2691 | 2.7999 | 2.7999 | 3.1538 | 3.1538 | 2019-12-03 23:00 | 1.3718 | 2.2481 | 3.6903 | 3.6903 | 3.6903 | 3.6903
2021-10-06 11:00 | 1.8976 | 2.3092 | 2.2594 | 2.4302 | 2.3021 | 2.4729 | 1.1946 | 2.0485 | 2.5278 | 2.5278 | 2.8473 | 2.8473 | 2019-12-04 | 1.3108 | 2.1482 | 3.5263 | 3.5263 | 3.5263 | 3.5263
2021-10-06 12:00 | 1.7776 | 2.1632 | 2.1165 | 2.2765 | 2.1565 | 2.3165 | 1.1774 | 2.0191 | 2.4915 | 2.4915 | 2.8064 | 2.8064 | 2019-12-04 01:00 | 1.1965 | 1.9608 | 3.2187 | 3.2187 | 3.2187 | 3.2187
2021-10-06 13:00 | 1.6576 | 2.0171 | 1.9736 | 2.1228 | 2.0109 | 2.1601 | 1.1117 | 1.9064 | 2.3524 | 2.3524 | 2.6497 | 2.6497 | 2019-12-04 02:00 | 1.1965 | 1.9608 | 3.2187 | 3.2187 | 3.2187 | 3.2187
2021-10-06 14:00 | 1.609 | 1.958 | 1.9157 | 2.0605 | 1.9519 | 2.0967 | 1.1089 | 1.9015 | 2.3464 | 2.3464 | 2.6429 | 2.6429 | 2019-12-04 03:00 | 1.1736 | 1.9234 | 3.1572 | 3.1572 | 3.1572 | 3.1572
2021-10-06 15:00 | 1.5518 | 1.8884 | 1.8477 | 1.9873 | 1.8826 | 2.0223 | 1.0688 | 1.8329 | 2.2617 | 2.2617 | 2.5475 | 2.5475 | 2019-12-04 04:00 | 1.1736 | 1.9234 | 3.1572 | 3.1572 | 3.1572 | 3.1572
2021-10-06 16:00 | 1.7233 | 2.0971 | 2.0518 | 2.2069 | 2.0906 | 2.2457 | 1.1717 | 2.0093 | 2.4794 | 2.4794 | 2.7928 | 2.7928 | 2019-12-04 05:00 | 1.227 | 2.0108 | 3.3007 | 3.3007 | 3.3007 | 3.3007
2021-10-06 17:00 | 2.0119 | 2.4483 | 2.3955 | 2.5766 | 2.4408 | 2.6219 | 1.2739 | 2.1845 | 2.6955 | 2.6955 | 3.0362 | 3.0362 | 2019-12-04 06:00 | 1.4404 | 2.3605 | 3.8748 | 3.8748 | 3.8748 | 3.8748
2021-10-06 18:00 | 2.343 | 2.8512 | 2.7897 | 3.0006 | 2.8424 | 3.0533 | 1.4921 | 2.5586 | 3.1572 | 3.1572 | 3.5563 | 3.5563 | 2019-12-04 07:00 | 1.7452 | 2.8601 | 4.6949 | 4.6949 | 4.6949 | 4.6949
2021-10-06 19:00 | 2.5064 | 3.05 | 2.9842 | 3.2098 | 3.0406 | 3.2662 | 1.7119 | 2.9356 | 3.6223 | 3.6223 | 4.0802 | 4.0802 | 2019-12-04 08:00 | 1.9586 | 3.2098 | 5.2689 | 5.2689 | 5.2689 | 5.2689
2021-10-06 20:00 | 2.4321 | 2.9596 | 2.8957 | 3.1146 | 2.9504 | 3.1693 | 1.649 | 2.8278 | 3.4893 | 3.4893 | 3.9303 | 3.9303 | 2019-12-04 09:00 | 2.0653 | 3.3846 | 5.5559 | 5.5559 | 5.5559 | 5.5559
2021-10-06 21:00 | 2.2692 | 2.7613 | 2.7018 | 2.906 | 2.7528 | 2.957 | 1.5318 | 2.6268 | 3.2414 | 3.2414 | 3.651 | 3.651 | 2019-12-04 10:00 | 2.1415 | 3.5095 | 5.7609 | 5.7609 | 5.7609 | 5.7609
2021-10-06 22:00 | 2.1434 | 2.6083 | 2.552 | 2.7449 | 2.6003 | 2.7932 | 1.3095 | 2.2456 | 2.771 | 2.771 | 3.1212 | 3.1212 | 2019-12-04 11:00 | 2.1263 | 3.4845 | 5.7199 | 5.7199 | 5.7199 | 5.7199
2021-10-06 23:00 | 1.8862 | 2.2953 | 2.2458 | 2.4156 | 2.2882 | 2.458 | 1.1185 | 1.918 | 2.3667 | 2.3667 | 2.6659 | 2.6659 | 2019-12-04 12:00 | 2.1339 | 3.497 | 5.7404 | 5.7404 | 5.7404 | 5.7404
2021-10-07 | 1.7666 | 2.1497 | 2.1033 | 2.2623 | 2.1431 | 2.3021 | 1.0346 | 1.7741 | 2.1891 | 2.1891 | 2.4658 | 2.4658 | 2019-12-04 13:00 | 2.0196 | 3.3097 | 5.4329 | 5.4329 | 5.4329 | 5.4329
2021-10-07 01:00 | 1.6461 | 2.0032 | 1.96 | 2.1081 | 1.997 | 2.1452 | 0.89183 | 1.5294 | 1.8871 | 1.8871 | 2.1257 | 2.1257 | 2019-12-04 14:00 | 2.111 | 3.4596 | 5.6789 | 5.6789 | 5.6789 | 5.6789
2021-10-07 02:00 | 1.5575 | 1.8954 | 1.8545 | 1.9947 | 1.8895 | 2.0297 | 0.84307 | 1.4457 | 1.7839 | 1.7839 | 2.0094 | 2.0094 | 2019-12-04 15:00 | 2.1872 | 3.5845 | 5.8839 | 5.8839 | 5.8839 | 5.8839
2021-10-07 03:00 | 1.5747 | 1.9162 | 1.8749 | 2.0166 | 1.9103 | 2.0521 | 0.82592 | 1.4163 | 1.7477 | 1.7477 | 1.9686 | 1.9686 | 2019-12-04 16:00 | 2.1034 | 3.4471 | 5.6584 | 5.6584 | 5.6584 | 5.6584
2021-10-07 04:00 | 1.5833 | 1.9267 | 1.8851 | 2.0276 | 1.9207 | 2.0632 | 0.8171 | 1.4012 | 1.729 | 1.729 | 1.9475 | 1.9475 | 2019-12-04 17:00 | 1.9967 | 3.2722 | 5.3714 | 5.3714 | 5.3714 | 5.3714
2021-10-07 05:00 | 1.6903 | 2.0569 | 2.0125 | 2.1647 | 2.0506 | 2.2027 | 0.89728 | 1.5387 | 1.8986 | 1.8986 | 2.1386 | 2.1386 | 2019-12-04 18:00 | 1.9662 | 3.2223 | 5.2894 | 5.2894 | 5.2894 | 5.2894
2021-10-07 06:00 | 2.0005 | 2.4344 | 2.3819 | 2.562 | 2.4269 | 2.607 | 0.95453 | 1.6369 | 2.0198 | 2.0198 | 2.2751 | 2.2751 | 2019-12-04 19:00 | 1.7833 | 2.9225 | 4.7974 | 4.7974 | 4.7974 | 4.7974
2021-10-07 07:00 | 2.272 | 2.7648 | 2.7052 | 2.9096 | 2.7563 | 2.9608 | 1.2175 | 2.0877 | 2.5761 | 2.5761 | 2.9018 | 2.9018 | 2019-12-04 20:00 | 1.7833 | 2.9225 | 4.7974 | 4.7974 | 4.7974 | 4.7974
2021-10-07 08:00 | 2.2549 | 2.7439 | 2.6848 | 2.8877 | 2.7355 | 2.9384 | 1.2918 | 2.2152 | 2.7334 | 2.7334 | 3.0789 | 3.0789 | 2019-12-04 21:00 | 1.6995 | 2.7851 | 4.5718 | 4.5718 | 4.5718 | 4.5718
2021-10-07 09:00 | 2.1548 | 2.6222 | 2.5657 | 2.7596 | 2.6141 | 2.8081 | 1.2375 | 2.122 | 2.6185 | 2.6185 | 2.9494 | 2.9494 | 2019-12-04 22:00 | 1.4861 | 2.4354 | 3.9978 | 3.9978 | 3.9978 | 3.9978
2021-10-07 10:00 | 1.8719 | 2.2779 | 2.2288 | 2.3973 | 2.2709 | 2.4394 | 1.2232 | 2.0975 | 2.5882 | 2.5882 | 2.9154 | 2.9154 | 2019-12-04 23:00 | 1.3718 | 2.2481 | 3.6903 | 3.6903 | 3.6903 | 3.6903
2021-10-07 11:00 | 1.8633 | 2.2675 | 2.2186 | 2.3863 | 2.2605 | 2.4282 | 1.2032 | 2.0632 | 2.5459 | 2.5459 | 2.8677 | 2.8677 | 2019-12-05 | 1.2346 | 2.0233 | 3.3212 | 3.3212 | 3.3212 | 3.3212
2021-10-07 12:00 | 1.7119 | 2.0832 | 2.0382 | 2.1923 | 2.0767 | 2.2308 | 1.1089 | 1.9015 | 2.3464 | 2.3464 | 2.6429 | 2.6429 | 2019-12-05 01:00 | 1.2194 | 1.9983 | 3.2802 | 3.2802 | 3.2802 | 3.2802
2021-10-07 13:00 | 1.549 | 1.8849 | 1.8443 | 1.9837 | 1.8791 | 2.0185 | 1.0917 | 1.8721 | 2.3101 | 2.3101 | 2.602 | 2.602 | 2019-12-05 02:00 | 1.1508 | 1.8859 | 3.0957 | 3.0957 | 3.0957 | 3.0957
2021-10-07 14:00 | 1.4775 | 1.798 | 1.7592 | 1.8922 | 1.7925 | 1.9254 | 1.0431 | 1.7888 | 2.2073 | 2.2073 | 2.4862 | 2.4862 | 2019-12-05 03:00 | 1.1355 | 1.8609 | 3.0547 | 3.0547 | 3.0547 | 3.0547
2021-10-07 15:00 | 1.5061 | 1.8328 | 1.7932 | 1.9288 | 1.8271 | 1.9627 | 0.98597 | 1.6908 | 2.0863 | 2.0863 | 2.35 | 2.35 | 2019-12-05 04:00 | 1.2727 | 2.0857 | 3.4238 | 3.4238 | 3.4238 | 3.4238
2021-10-07 16:00 | 1.5804 | 1.9232 | 1.8817 | 2.0239 | 1.9173 | 2.0595 | 1.0888 | 1.8672 | 2.304 | 2.304 | 2.5952 | 2.5952 | 2019-12-05 05:00 | 1.2879 | 2.1107 | 3.4648 | 3.4648 | 3.4648 | 3.4648
2021-10-07 17:00 | 1.9691 | 2.3962 | 2.3445 | 2.5217 | 2.3888 | 2.566 | 1.2317 | 2.1122 | 2.6064 | 2.6064 | 2.9358 | 2.9358 | 2019-12-05 06:00 | 1.4099 | 2.3105 | 3.7928 | 3.7928 | 3.7928 | 3.7928
2021-10-07 18:00 | 2.2149 | 2.6953 | 2.6371 | 2.8364 | 2.6869 | 2.8863 | 1.3975 | 2.3965 | 2.9571 | 2.9571 | 3.3309 | 3.3309 | 2019-12-05 07:00 | 1.7605 | 2.8851 | 4.7359 | 4.7359 | 4.7359 | 4.7359
2021-10-07 19:00 | 2.3549 | 2.8657 | 2.8038 | 3.0158 | 2.8568 | 3.0688 | 1.5833 | 2.715 | 3.3502 | 3.3502 | 3.7736 | 3.7736 | 2019-12-05 08:00 | 2.0196 | 3.3097 | 5.4329 | 5.4329 | 5.4329 | 5.4329
2021-10-07 20:00 | 2.3435 | 2.8518 | 2.7902 | 3.0011 | 2.843 | 3.0539 | 1.6033 | 2.7494 | 3.3925 | 3.3925 | 3.8213 | 3.8213 | 2019-12-05 09:00 | 2.1796 | 3.572 | 5.8634 | 5.8634 | 5.8634 | 5.8634
2021-10-07 21:00 | 2.1663 | 2.6361 | 2.5793 | 2.7742 | 2.628 | 2.823 | 1.4175 | 2.4308 | 2.9995 | 2.9995 | 3.3786 | 3.3786 | 2019-12-05 10:00 | 2.1034 | 3.4471 | 5.6584 | 5.6584 | 5.6584 | 5.6584
2021-10-07 22:00 | 1.9472 | 2.3695 | 2.3184 | 2.4937 | 2.3622 | 2.5375 | 1.3411 | 2.2999 | 2.8379 | 2.8379 | 3.1966 | 3.1966 | 2019-12-05 11:00 | 2.1034 | 3.4471 | 5.6584 | 5.6584 | 5.6584 | 5.6584
2021-10-07 23:00 | 1.8033 | 2.1945 | 2.1471 | 2.3094 | 2.1877 | 2.35 | 1.0603 | 1.8182 | 2.2435 | 2.2435 | 2.5271 | 2.5271 | 2019-12-05 12:00 | 2.1034 | 3.4471 | 5.6584 | 5.6584 | 5.6584 | 5.6584
2021-10-08 | 1.7449 | 2.1233 | 2.0775 | 2.2346 | 2.1168 | 2.2738 | 1.0603 | 1.8182 | 2.2435 | 2.2435 | 2.5271 | 2.5271 | 2019-12-05 13:00 | 2.2025 | 3.6094 | 5.9249 | 5.9249 | 5.9249 | 5.9249
2021-10-08 01:00 | 1.589 | 1.9336 | 1.8919 | 2.0349 | 1.9277 | 2.0707 | 0.8917 | 1.5291 | 1.8868 | 1.8868 | 2.1253 | 2.1253 | 2019-12-05 14:00 | 2.0958 | 3.4346 | 5.6379 | 5.6379 | 5.6379 | 5.6379
2021-10-08 02:00 | 1.5204 | 1.8502 | 1.8102 | 1.9471 | 1.8445 | 1.9813 | 0.81735 | 1.4016 | 1.7295 | 1.7295 | 1.9481 | 1.9481 | 2019-12-05 15:00 | 2.1491 | 3.522 | 5.7814 | 5.7814 | 5.7814 | 5.7814
2021-10-08 03:00 | 1.5034 | 1.8295 | 1.79 | 1.9253 | 1.8238 | 1.9592 | 0.79449 | 1.3624 | 1.6811 | 1.6811 | 1.8936 | 1.8936 | 2019-12-05 16:00 | 2.1567 | 3.5345 | 5.8019 | 5.8019 | 5.8019 | 5.8019
2021-10-08 04:00 | 1.6033 | 1.951 | 1.9089 | 2.0532 | 1.945 | 2.0893 | 0.84307 | 1.4457 | 1.7839 | 1.7839 | 2.0094 | 2.0094 | 2019-12-05 17:00 | 2.1034 | 3.4471 | 5.6584 | 5.6584 | 5.6584 | 5.6584
2021-10-08 05:00 | 1.7486 | 2.1279 | 2.082 | 2.2394 | 2.1214 | 2.2787 | 0.92002 | 1.5777 | 1.9468 | 1.9468 | 2.1928 | 2.1928 | 2019-12-05 18:00 | 1.8976 | 3.1099 | 5.1049 | 5.1049 | 5.1049 | 5.1049
2021-10-08 06:00 | 2.0348 | 2.4762 | 2.4227 | 2.6059 | 2.4685 | 2.6517 | 1.0256 | 1.7588 | 2.1703 | 2.1703 | 2.4446 | 2.4446 | 2019-12-05 19:00 | 1.829 | 2.9975 | 4.9204 | 4.9204 | 4.9204 | 4.9204
2021-10-08 07:00 | 2.352 | 2.8622 | 2.8004 | 3.0121 | 2.8534 | 3.065 | 1.2718 | 2.1809 | 2.691 | 2.691 | 3.0312 | 3.0312 | 2019-12-05 20:00 | 1.7681 | 2.8975 | 4.7564 | 4.7564 | 4.7564 | 4.7564
2021-10-08 08:00 | 2.3778 | 2.8935 | 2.8311 | 3.0451 | 2.8846 | 3.0986 | 1.2975 | 2.225 | 2.7455 | 2.7455 | 3.0925 | 3.0925 | 2019-12-05 21:00 | 1.6309 | 2.6727 | 4.3873 | 4.3873 | 4.3873 | 4.3873
2021-10-08 09:00 | 2.2834 | 2.7787 | 2.7188 | 2.9243 | 2.7702 | 2.9757 | 1.2803 | 2.1956 | 2.7092 | 2.7092 | 3.0516 | 3.0516 | 2019-12-05 22:00 | 1.509 | 2.4729 | 4.0593 | 4.0593 | 4.0593 | 4.0593
2021-10-08 10:00 | 1.9719 | 2.3996 | 2.3479 | 2.5254 | 2.3922 | 2.5697 | 1.2546 | 2.1515 | 2.6548 | 2.6548 | 2.9903 | 2.9903 | 2019-12-05 23:00 | 1.4099 | 2.3105 | 3.7928 | 3.7928 | 3.7928 | 3.7928
2021-10-08 11:00 | 1.8976 | 2.3092 | 2.2594 | 2.4302 | 2.3021 | 2.4729 | 1.1917 | 2.0436 | 2.5217 | 2.5217 | 2.8404 | 2.8404 | 2019-12-06 | 1.2575 | 2.0608 | 3.3828 | 3.3828 | 3.3828 | 3.3828
2021-10-08 12:00 | 1.849 | 2.2501 | 2.2016 | 2.368 | 2.2432 | 2.4096 | 1.146 | 1.9652 | 2.425 | 2.425 | 2.7315 | 2.7315 | 2019-12-06 01:00 | 1.2651 | 2.0732 | 3.4033 | 3.4033 | 3.4033 | 3.4033
2021-10-08 13:00 | 1.6747 | 2.038 | 1.994 | 2.1447 | 2.0317 | 2.1824 | 1.146 | 1.9652 | 2.425 | 2.425 | 2.7315 | 2.7315 | 2019-12-06 02:00 | 1.1508 | 1.8859 | 3.0957 | 3.0957 | 3.0957 | 3.0957
2021-10-08 14:00 | 1.609 | 1.958 | 1.9157 | 2.0605 | 1.9519 | 2.0967 | 1.1403 | 1.9554 | 2.4129 | 2.4129 | 2.7178 | 2.7178 | 2019-12-06 03:00 | 1.1736 | 1.9234 | 3.1572 | 3.1572 | 3.1572 | 3.1572
2021-10-08 15:00 | 1.5661 | 1.9058 | 1.8647 | 2.0056 | 1.8999 | 2.0409 | 1.1517 | 1.975 | 2.4371 | 2.4371 | 2.7451 | 2.7451 | 2019-12-06 04:00 | 1.227 | 2.0108 | 3.3007 | 3.3007 | 3.3007 | 3.3007
2021-10-08 16:00 | 1.6261 | 1.9788 | 1.9361 | 2.0825 | 1.9727 | 2.1191 | 1.1146 | 1.9113 | 2.3584 | 2.3584 | 2.6565 | 2.6565 | 2019-12-06 05:00 | 1.2651 | 2.0732 | 3.4033 | 3.4033 | 3.4033 | 3.4033
2021-10-08 17:00 | 1.834 | 2.2318 | 2.1837 | 2.3487 | 2.2249 | 2.39 | 1.188 | 2.0372 | 2.5138 | 2.5138 | 2.8316 | 2.8316 | 2019-12-06 06:00 | 1.4785 | 2.4229 | 3.9773 | 3.9773 | 3.9773 | 3.9773
2021-10-08 18:00 | 2.2177 | 2.6987 | 2.6405 | 2.8401 | 2.6904 | 2.89 | 1.3746 | 2.3573 | 2.9088 | 2.9088 | 3.2764 | 3.2764 | 2019-12-06 07:00 | 1.8824 | 3.0849 | 5.0639 | 5.0639 | 5.0639 | 5.0639
2021-10-08 19:00 | 2.3549 | 2.8657 | 2.8038 | 3.0158 | 2.8568 | 3.0688 | 1.549 | 2.6562 | 3.2776 | 3.2776 | 3.6919 | 3.6919 | 2019-12-06 08:00 | 2.0729 | 3.3971 | 5.5764 | 5.5764 | 5.5764 | 5.5764
2021-10-08 20:00 | 2.2549 | 2.7439 | 2.6848 | 2.8877 | 2.7355 | 2.9384 | 1.5347 | 2.6317 | 3.2474 | 3.2474 | 3.6578 | 3.6578 | 2019-12-06 09:00 | 2.1644 | 3.547 | 5.8224 | 5.8224 | 5.8224 | 5.8224
2021-10-08 21:00 | 2.1291 | 2.5909 | 2.535 | 2.7266 | 2.5829 | 2.7746 | 1.4975 | 2.568 | 3.1688 | 3.1688 | 3.5693 | 3.5693 | 2019-12-06 10:00 | 2.2634 | 3.7094 | 6.089 | 6.089 | 6.089 | 6.089
2021-10-08 22:00 | 1.9805 | 2.4101 | 2.3581 | 2.5363 | 2.4026 | 2.5809 | 1.3461 | 2.3083 | 2.8483 | 2.8483 | 3.2083 | 3.2083 | 2019-12-06 11:00 | 2.3625 | 3.8717 | 6.3555 | 6.3555 | 6.3555 | 6.3555
2021-10-08 23:00 | 1.8633 | 2.2675 | 2.2186 | 2.3863 | 2.2605 | 2.4282 | 1.1289 | 1.9358 | 2.3887 | 2.3887 | 2.6906 | 2.6906 | 2019-12-06 12:00 | 2.2101 | 3.6219 | 5.9454 | 5.9454 | 5.9454 | 5.9454
2021-10-09 | 1.7438 | 2.122 | 2.0763 | 2.2332 | 2.1155 | 2.2724 | 1.006 | 1.7251 | 2.1286 | 2.1286 | 2.3977 | 2.3977 | 2019-12-06 13:00 | 2.2101 | 3.6219 | 5.9454 | 5.9454 | 5.9454 | 5.9454
2021-10-09 01:00 | 1.6233 | 1.9754 | 1.9327 | 2.0788 | 1.9693 | 2.1154 | 0.91166 | 1.5634 | 1.9291 | 1.9291 | 2.1729 | 2.1729 | 2019-12-06 14:00 | 2.1491 | 3.522 | 5.7814 | 5.7814 | 5.7814 | 5.7814
2021-10-09 02:00 | 1.5775 | 1.9197 | 1.8783 | 2.0203 | 1.9138 | 2.0558 | 0.87451 | 1.4996 | 1.8505 | 1.8505 | 2.0844 | 2.0844 | 2019-12-06 15:00 | 2.233 | 3.6594 | 6.007 | 6.007 | 6.007 | 6.007
2021-10-09 03:00 | 1.5775 | 1.9197 | 1.8783 | 2.0203 | 1.9138 | 2.0558 | 0.80025 | 1.3723 | 1.6933 | 1.6933 | 1.9074 | 1.9074 | 2019-12-06 16:00 | 2.1491 | 3.522 | 5.7814 | 5.7814 | 5.7814 | 5.7814
2021-10-09 04:00 | 1.5775 | 1.9197 | 1.8783 | 2.0203 | 1.9138 | 2.0558 | 0.74864 | 1.2838 | 1.5841 | 1.5841 | 1.7844 | 1.7844 | 2019-12-06 17:00 | 2.0805 | 3.4096 | 5.5969 | 5.5969 | 5.5969 | 5.5969
2021-10-09 05:00 | 1.6941 | 2.0615 | 2.0171 | 2.1695 | 2.0552 | 2.2076 | 0.82592 | 1.4163 | 1.7477 | 1.7477 | 1.9686 | 1.9686 | 2019-12-06 18:00 | 1.8671 | 3.0599 | 5.0229 | 5.0229 | 5.0229 | 5.0229
2021-10-09 06:00 | 1.8691 | 2.2744 | 2.2254 | 2.3936 | 2.2674 | 2.4356 | 0.91738 | 1.5732 | 1.9412 | 1.9412 | 2.1865 | 2.1865 | 2019-12-06 19:00 | 1.8824 | 3.0849 | 5.0639 | 5.0639 | 5.0639 | 5.0639
2021-10-09 07:00 | 1.9291 | 2.3475 | 2.2968 | 2.4705 | 2.3402 | 2.5139 | 0.9974 | 1.7104 | 2.1105 | 2.1105 | 2.3773 | 2.3773 | 2019-12-06 20:00 | 1.6995 | 2.7851 | 4.5718 | 4.5718 | 4.5718 | 4.5718
2021-10-09 08:00 | 2.0119 | 2.4483 | 2.3955 | 2.5766 | 2.4408 | 2.6219 | 1.0888 | 1.8672 | 2.304 | 2.304 | 2.5952 | 2.5952 | 2019-12-06 21:00 | 1.6766 | 2.7477 | 4.5103 | 4.5103 | 4.5103 | 4.5103
2021-10-09 09:00 | 1.9405 | 2.3614 | 2.3104 | 2.4851 | 2.3541 | 2.5288 | 1.1317 | 1.9407 | 2.3947 | 2.3947 | 2.6974 | 2.6974 | 2019-12-06 22:00 | 1.5166 | 2.4854 | 4.0798 | 4.0798 | 4.0798 | 4.0798
2021-10-09 10:00 | 1.8005 | 2.191 | 2.1437 | 2.3058 | 2.1842 | 2.3463 | 1.266 | 2.1711 | 2.679 | 2.679 | 3.0176 | 3.0176 | 2019-12-06 23:00 | 1.4251 | 2.3355 | 3.8338 | 3.8338 | 3.8338 | 3.8338
2021-10-09 11:00 | 1.7776 | 2.1632 | 2.1165 | 2.2765 | 2.1565 | 2.3165 | 1.2403 | 2.1269 | 2.6245 | 2.6245 | 2.9562 | 2.9562 | 2019-12-07 | 1.2575 | 2.0608 | 3.3828 | 3.3828 | 3.3828 | 3.3828
2021-10-09 12:00 | 1.5518 | 1.8884 | 1.8477 | 1.9873 | 1.8826 | 2.0223 | 1.1974 | 2.0534 | 2.5338 | 2.5338 | 2.8541 | 2.8541 | 2019-12-07 01:00 | 1.1889 | 1.9483 | 3.1982 | 3.1982 | 3.1982 | 3.1982
2021-10-09 13:00 | 1.4832 | 1.8049 | 1.766 | 1.8995 | 1.7994 | 1.9329 | 1.186 | 2.0338 | 2.5096 | 2.5096 | 2.8268 | 2.8268 | 2019-12-07 02:00 | 1.1508 | 1.8859 | 3.0957 | 3.0957 | 3.0957 | 3.0957
2021-10-09 14:00 | 1.3975 | 1.7006 | 1.6639 | 1.7897 | 1.6954 | 1.8211 | 1.1317 | 1.9407 | 2.3947 | 2.3947 | 2.6974 | 2.6974 | 2019-12-07 03:00 | 1.1355 | 1.8609 | 3.0547 | 3.0547 | 3.0547 | 3.0547
2021-10-09 15:00 | 1.3889 | 1.6902 | 1.6537 | 1.7787 | 1.685 | 1.81 | 1.0966 | 1.8806 | 2.3205 | 2.3205 | 2.6138 | 2.6138 | 2019-12-07 04:00 | 1.1279 | 1.8484 | 3.0342 | 3.0342 | 3.0342 | 3.0342
2021-10-09 16:00 | 1.5633 | 1.9023 | 1.8613 | 2.002 | 1.8965 | 2.0372 | 1.1803 | 2.024 | 2.4975 | 2.4975 | 2.8132 | 2.8132 | 2019-12-07 05:00 | 1.2194 | 1.9983 | 3.2802 | 3.2802 | 3.2802 | 3.2802
2021-10-09 17:00 | 1.7547 | 2.1353 | 2.0893 | 2.2472 | 2.1288 | 2.2867 | 1.2003 | 2.0583 | 2.5399 | 2.5399 | 2.8609 | 2.8609 | 2019-12-07 06:00 | 1.3032 | 2.1357 | 3.5058 | 3.5058 | 3.5058 | 3.5058
2021-10-09 18:00 | 2.0034 | 2.4379 | 2.3853 | 2.5656 | 2.4304 | 2.6107 | 1.286 | 2.2054 | 2.7213 | 2.7213 | 3.0652 | 3.0652 | 2019-12-07 07:00 | 1.5471 | 2.5353 | 4.1618 | 4.1618 | 4.1618 | 4.1618
2021-10-09 19:00 | 2.1148 | 2.5735 | 2.518 | 2.7083 | 2.5656 | 2.7559 | 1.4775 | 2.5337 | 3.1265 | 3.1265 | 3.5216 | 3.5216 | 2019-12-07 08:00 | 1.7071 | 2.7976 | 4.5923 | 4.5923 | 4.5923 | 4.5923
2021-10-09 20:00 | 2.0805 | 2.5318 | 2.4772 | 2.6644 | 2.524 | 2.7112 | 1.4661 | 2.5141 | 3.1023 | 3.1023 | 3.4944 | 3.4944 | 2019-12-07 09:00 | 1.829 | 2.9975 | 4.9204 | 4.9204 | 4.9204 | 4.9204
2021-10-09 21:00 | 1.9891 | 2.4205 | 2.3683 | 2.5473 | 2.4131 | 2.5921 | 1.3461 | 2.3083 | 2.8483 | 2.8483 | 3.2083 | 3.2083 | 2019-12-07 10:00 | 1.8824 | 3.0849 | 5.0639 | 5.0639 | 5.0639 | 5.0639
2021-10-09 22:00 | 1.8348 | 2.2327 | 2.1845 | 2.3497 | 2.2258 | 2.391 | 1.1549 | 1.9805 | 2.4438 | 2.4438 | 2.7527 | 2.7527 | 2019-12-07 11:00 | 1.9586 | 3.2098 | 5.2689 | 5.2689 | 5.2689 | 5.2689
2021-10-09 23:00 | 1.7576 | 2.1388 | 2.0927 | 2.2509 | 2.1322 | 2.2904 | 1.0831 | 1.8574 | 2.2919 | 2.2919 | 2.5816 | 2.5816 | 2019-12-07 12:00 | 1.9738 | 3.2348 | 5.3099 | 5.3099 | 5.3099 | 5.3099
2021-10-10 | 1.669 | 2.031 | 1.9872 | 2.1374 | 2.0247 | 2.175 | 0.95739 | 1.6418 | 2.0258 | 2.0258 | 2.2819 | 2.2819 | 2019-12-07 13:00 | 2.0501 | 3.3597 | 5.5149 | 5.5149 | 5.5149 | 5.5149
2021-10-10 01:00 | 1.5604 | 1.8988 | 1.8579 | 1.9983 | 1.893 | 2.0334 | 0.84879 | 1.4555 | 1.796 | 1.796 | 2.0231 | 2.0231 | 2019-12-07 14:00 | 2.0119 | 3.2972 | 5.4124 | 5.4124 | 5.4124 | 5.4124
2021-10-10 02:00 | 1.4918 | 1.8154 | 1.7762 | 1.9105 | 1.8098 | 1.944 | 0.80306 | 1.3771 | 1.6993 | 1.6993 | 1.9141 | 1.9141 | 2019-12-07 15:00 | 2.0729 | 3.3971 | 5.5764 | 5.5764 | 5.5764 | 5.5764
2021-10-10 03:00 | 1.4547 | 1.7702 | 1.732 | 1.8629 | 1.7647 | 1.8956 | 0.79163 | 1.3575 | 1.6751 | 1.6751 | 1.8868 | 1.8868 | 2019-12-07 16:00 | 2.0501 | 3.3597 | 5.5149 | 5.5149 | 5.5149 | 5.5149
2021-10-10 04:00 | 1.4535 | 1.7688 | 1.7306 | 1.8614 | 1.7633 | 1.8941 | 0.76305 | 1.3085 | 1.6146 | 1.6146 | 1.8187 | 1.8187 | 2019-12-07 17:00 | 1.9891 | 3.2597 | 5.3509 | 5.3509 | 5.3509 | 5.3509
2021-10-10 05:00 | 1.542 | 1.8765 | 1.836 | 1.9748 | 1.8707 | 2.0095 | 0.77448 | 1.3281 | 1.6388 | 1.6388 | 1.8459 | 1.8459 | 2019-12-07 18:00 | 1.7681 | 2.8975 | 4.7564 | 4.7564 | 4.7564 | 4.7564
2021-10-10 06:00 | 1.5661 | 1.9058 | 1.8647 | 2.0056 | 1.8999 | 2.0409 | 0.74108 | 1.2708 | 1.5681 | 1.5681 | 1.7663 | 1.7663 | 2019-12-07 19:00 | 1.669 | 2.7352 | 4.4898 | 4.4898 | 4.4898 | 4.4898
2021-10-10 07:00 | 1.689 | 2.0553 | 2.011 | 2.163 | 2.049 | 2.201 | 0.86863 | 1.4896 | 1.838 | 1.838 | 2.0703 | 2.0703 | 2019-12-07 20:00 | 1.7376 | 2.8476 | 4.6744 | 4.6744 | 4.6744 | 4.6744
2021-10-10 08:00 | 1.7711 | 2.1553 | 2.1088 | 2.2682 | 2.1486 | 2.308 | 1.0195 | 1.7483 | 2.1573 | 2.1573 | 2.43 | 2.43 | 2019-12-07 21:00 | 1.7452 | 2.8601 | 4.6949 | 4.6949 | 4.6949 | 4.6949
2021-10-10 09:00 | 1.7747 | 2.1597 | 2.1131 | 2.2728 | 2.153 | 2.3127 | 1.1089 | 1.9015 | 2.3464 | 2.3464 | 2.6429 | 2.6429 | 2019-12-07 22:00 | 1.5775 | 2.5853 | 4.2438 | 4.2438 | 4.2438 | 4.2438
2021-10-10 10:00 | 1.7947 | 2.184 | 2.1369 | 2.2984 | 2.1773 | 2.3388 | 1.1146 | 1.9113 | 2.3584 | 2.3584 | 2.6565 | 2.6565 | 2019-12-07 23:00 | 1.4632 | 2.398 | 3.9363 | 3.9363 | 3.9363 | 3.9363
2021-10-10 11:00 | 1.9405 | 2.3614 | 2.3104 | 2.4851 | 2.3541 | 2.5288 | 1.266 | 2.1711 | 2.679 | 2.679 | 3.0176 | 3.0176 | 2019-12-08 | 1.387 | 2.2731 | 3.7313 | 3.7313 | 3.7313 | 3.7313
2021-10-10 12:00 | 1.8176 | 2.2118 | 2.1641 | 2.3277 | 2.205 | 2.3686 | 1.1917 | 2.0436 | 2.5217 | 2.5217 | 2.8404 | 2.8404 | 2019-12-08 01:00 | 1.3108 | 2.1482 | 3.5263 | 3.5263 | 3.5263 | 3.5263
2021-10-10 13:00 | 1.8805 | 2.2884 | 2.239 | 2.4082 | 2.2813 | 2.4505 | 1.3432 | 2.3034 | 2.8422 | 2.8422 | 3.2015 | 3.2015 | 2019-12-08 02:00 | 1.3184 | 2.1607 | 3.5468 | 3.5468 | 3.5468 | 3.5468
2021-10-10 14:00 | 1.8233 | 2.2188 | 2.1709 | 2.335 | 2.212 | 2.3761 | 1.2546 | 2.1515 | 2.6548 | 2.6548 | 2.9903 | 2.9903 | 2019-12-08 03:00 | 1.2346 | 2.0233 | 3.3212 | 3.3212 | 3.3212 | 3.3212
2021-10-10 15:00 | 1.7833 | 2.1701 | 2.1233 | 2.2838 | 2.1634 | 2.3239 | 1.2603 | 2.1613 | 2.6669 | 2.6669 | 3.0039 | 3.0039 | 2019-12-08 04:00 | 1.3108 | 2.1482 | 3.5263 | 3.5263 | 3.5263 | 3.5263
2021-10-10 16:00 | 1.8988 | 2.3107 | 2.2609 | 2.4318 | 2.3036 | 2.4745 | 1.3032 | 2.2348 | 2.7576 | 2.7576 | 3.1061 | 3.1061 | 2019-12-08 05:00 | 1.3108 | 2.1482 | 3.5263 | 3.5263 | 3.5263 | 3.5263
2021-10-10 17:00 | 2.1691 | 2.6396 | 2.5827 | 2.7779 | 2.6315 | 2.8267 | 1.4261 | 2.4455 | 3.0176 | 3.0176 | 3.399 | 3.399 | 2019-12-08 06:00 | 1.3489 | 2.2106 | 3.6288 | 3.6288 | 3.6288 | 3.6288
2021-10-10 18:00 | 2.2749 | 2.7683 | 2.7086 | 2.9133 | 2.7598 | 2.9645 | 1.4154 | 2.4271 | 2.9949 | 2.9949 | 3.3735 | 3.3735 | 2019-12-08 07:00 | 1.5699 | 2.5728 | 4.2233 | 4.2233 | 4.2233 | 4.2233
2021-10-10 19:00 | 2.3377 | 2.8448 | 2.7834 | 2.9938 | 2.836 | 3.0464 | 1.5518 | 2.6611 | 3.2837 | 3.2837 | 3.6987 | 3.6987 | 2019-12-08 08:00 | 1.8138 | 2.9725 | 4.8794 | 4.8794 | 4.8794 | 4.8794
2021-10-10 20:00 | 2.1777 | 2.65 | 2.5929 | 2.7889 | 2.6419 | 2.8379 | 1.4575 | 2.4994 | 3.0841 | 3.0841 | 3.4739 | 3.4739 | 2019-12-08 09:00 | 1.8138 | 2.9725 | 4.8794 | 4.8794 | 4.8794 | 4.8794
2021-10-10 21:00 | 2.0211 | 2.4595 | 2.4065 | 2.5884 | 2.4519 | 2.6338 | 1.3403 | 2.2985 | 2.8362 | 2.8362 | 3.1947 | 3.1947 | 2019-12-08 10:00 | 1.9586 | 3.2098 | 5.2689 | 5.2689 | 5.2689 | 5.2689
2021-10-10 22:00 | 1.8919 | 2.3023 | 2.2526 | 2.4229 | 2.2952 | 2.4654 | 1.1974 | 2.0534 | 2.5338 | 2.5338 | 2.8541 | 2.8541 | 2019-12-08 11:00 | 1.9586 | 3.2098 | 5.2689 | 5.2689 | 5.2689 | 5.2689
2021-10-10 23:00 | 1.7204 | 2.0936 | 2.0484 | 2.2033 | 2.0871 | 2.242 | 0.99273 | 1.7024 | 2.1006 | 2.1006 | 2.3661 | 2.3661 | 2019-12-08 12:00 | 1.9815 | 3.2472 | 5.3304 | 5.3304 | 5.3304 | 5.3304
2021-10-11 | 1.6633 | 2.024 | 1.9804 | 2.1301 | 2.0178 | 2.1675 | 0.97168 | 1.6663 | 2.0561 | 2.0561 | 2.316 | 2.316 | 2019-12-08 13:00 | 1.9891 | 3.2597 | 5.3509 | 5.3509 | 5.3509 | 5.3509
2021-10-11 01:00 | 1.5514 | 1.8879 | 1.8472 | 1.9868 | 1.8821 | 2.0218 | 0.83164 | 1.4261 | 1.7598 | 1.7598 | 1.9822 | 1.9822 | 2019-12-08 14:00 | 1.9891 | 3.2597 | 5.3509 | 5.3509 | 5.3509 | 5.3509
2021-10-11 02:00 | 1.5518 | 1.8884 | 1.8477 | 1.9873 | 1.8826 | 2.0223 | 0.82021 | 1.4065 | 1.7356 | 1.7356 | 1.9549 | 1.9549 | 2019-12-08 15:00 | 2.0424 | 3.3472 | 5.4944 | 5.4944 | 5.4944 | 5.4944
2021-10-11 03:00 | 1.5086 | 1.8358 | 1.7962 | 1.932 | 1.8302 | 1.966 | 0.77734 | 1.333 | 1.6449 | 1.6449 | 1.8528 | 1.8528 | 2019-12-08 16:00 | 2.0043 | 3.2847 | 5.3919 | 5.3919 | 5.3919 | 5.3919
2021-10-11 04:00 | 1.5247 | 1.8554 | 1.8153 | 1.9525 | 1.8496 | 1.9869 | 0.75518 | 1.295 | 1.598 | 1.598 | 1.7999 | 1.7999 | 2019-12-08 17:00 | 1.9738 | 3.2348 | 5.3099 | 5.3099 | 5.3099 | 5.3099
2021-10-11 05:00 | 1.6861 | 2.0519 | 2.0076 | 2.1594 | 2.0455 | 2.1973 | 0.82963 | 1.4227 | 1.7555 | 1.7555 | 1.9774 | 1.9774 | 2019-12-08 18:00 | 1.7605 | 2.8851 | 4.7359 | 4.7359 | 4.7359 | 4.7359
2021-10-11 06:00 | 2.0119 | 2.4483 | 2.3955 | 2.5766 | 2.4408 | 2.6219 | 0.92309 | 1.583 | 1.9533 | 1.9533 | 2.2002 | 2.2002 | 2019-12-08 19:00 | 1.7986 | 2.9475 | 4.8384 | 4.8384 | 4.8384 | 4.8384
2021-10-11 07:00 | 2.272 | 2.7648 | 2.7052 | 2.9096 | 2.7563 | 2.9608 | 1.1203 | 1.9211 | 2.3705 | 2.3705 | 2.6702 | 2.6702 | 2019-12-08 20:00 | 1.7605 | 2.8851 | 4.7359 | 4.7359 | 4.7359 | 4.7359
2021-10-11 08:00 | 2.2692 | 2.7613 | 2.7018 | 2.906 | 2.7528 | 2.957 | 1.2632 | 2.1662 | 2.6729 | 2.6729 | 3.0107 | 3.0107 | 2019-12-08 21:00 | 1.6385 | 2.6852 | 4.4078 | 4.4078 | 4.4078 | 4.4078
2021-10-11 09:00 | 2.2006 | 2.6779 | 2.6201 | 2.8181 | 2.6696 | 2.8677 | 1.2689 | 2.176 | 2.685 | 2.685 | 3.0244 | 3.0244 | 2019-12-08 22:00 | 1.4937 | 2.4479 | 4.0183 | 4.0183 | 4.0183 | 4.0183
2021-10-11 10:00 | 2.0691 | 2.5179 | 2.4636 | 2.6498 | 2.5101 | 2.6963 | 1.2403 | 2.1269 | 2.6245 | 2.6245 | 2.9562 | 2.9562 | 2019-12-08 23:00 | 1.4327 | 2.348 | 3.8543 | 3.8543 | 3.8543 | 3.8543
2021-10-11 11:00 | 2.0205 | 2.4588 | 2.4057 | 2.5876 | 2.4512 | 2.633 | 1.2918 | 2.2152 | 2.7334 | 2.7334 | 3.0789 | 3.0789 | 2019-12-09 | 1.3565 | 2.2231 | 3.6493 | 3.6493 | 3.6493 | 3.6493
2021-10-11 12:00 | 2.1348 | 2.5979 | 2.5418 | 2.734 | 2.5899 | 2.782 | 1.3518 | 2.3181 | 2.8604 | 2.8604 | 3.2219 | 3.2219 | 2019-12-09 01:00 | 1.3184 | 2.1607 | 3.5468 | 3.5468 | 3.5468 | 3.5468
2021-10-11 13:00 | 1.9576 | 2.3823 | 2.3309 | 2.5071 | 2.3749 | 2.5511 | 1.286 | 2.2054 | 2.7213 | 2.7213 | 3.0652 | 3.0652 | 2019-12-09 02:00 | 1.3108 | 2.1482 | 3.5263 | 3.5263 | 3.5263 | 3.5263
2021-10-11 14:00 | 1.9491 | 2.3718 | 2.3207 | 2.4961 | 2.3645 | 2.5399 | 1.306 | 2.2397 | 2.7636 | 2.7636 | 3.1129 | 3.1129 | 2019-12-09 03:00 | 1.2727 | 2.0857 | 3.4238 | 3.4238 | 3.4238 | 3.4238
2021-10-11 15:00 | 1.9376 | 2.3579 | 2.307 | 2.4814 | 2.3506 | 2.525 | 1.3003 | 2.2299 | 2.7515 | 2.7515 | 3.0993 | 3.0993 | 2019-12-09 04:00 | 1.3413 | 2.1981 | 3.6083 | 3.6083 | 3.6083 | 3.6083
2021-10-11 16:00 | 1.8948 | 2.3057 | 2.256 | 2.4265 | 2.2986 | 2.4692 | 1.3746 | 2.3573 | 2.9088 | 2.9088 | 3.2764 | 3.2764 | 2019-12-09 05:00 | 1.3413 | 2.1981 | 3.6083 | 3.6083 | 3.6083 | 3.6083
2021-10-11 17:00 | 2.232 | 2.7161 | 2.6575 | 2.8584 | 2.7077 | 2.9086 | 1.4204 | 2.4357 | 3.0055 | 3.0055 | 3.3854 | 3.3854 | 2019-12-09 06:00 | 1.5623 | 2.5603 | 4.2028 | 4.2028 | 4.2028 | 4.2028
2021-10-11 18:00 | 2.5692 | 3.1265 | 3.0591 | 3.2903 | 3.1169 | 3.3481 | 1.4918 | 2.5582 | 3.1567 | 3.1567 | 3.5557 | 3.5557 | 2019-12-09 07:00 | 1.951 | 3.1973 | 5.2484 | 5.2484 | 5.2484 | 5.2484
2021-10-11 19:00 | 2.6235 | 3.1926 | 3.1237 | 3.3598 | 3.1827 | 3.4188 | 1.689 | 2.8964 | 3.574 | 3.574 | 4.0257 | 4.0257 | 2019-12-09 08:00 | 2.1796 | 3.572 | 5.8634 | 5.8634 | 5.8634 | 5.8634
2021-10-11 20:00 | 2.5664 | 3.123 | 3.0556 | 3.2866 | 3.1134 | 3.3444 | 1.689 | 2.8964 | 3.574 | 3.574 | 4.0257 | 4.0257 | 2019-12-09 09:00 | 2.3092 | 3.7843 | 6.212 | 6.212 | 6.212 | 6.212
2021-10-11 21:00 | 2.3751 | 2.8902 | 2.8279 | 3.0416 | 2.8813 | 3.0951 | 1.4975 | 2.568 | 3.1688 | 3.1688 | 3.5693 | 3.5693 | 2019-12-09 10:00 | 2.2863 | 3.7468 | 6.1505 | 6.1505 | 6.1505 | 6.1505
2021-10-11 22:00 | 2.146 | 2.6114 | 2.5551 | 2.7482 | 2.6034 | 2.7965 | 1.3261 | 2.274 | 2.8059 | 2.8059 | 3.1606 | 3.1606 | 2019-12-09 11:00 | 2.3625 | 3.8717 | 6.3555 | 6.3555 | 6.3555 | 6.3555
2021-10-11 23:00 | 1.91 | 2.3243 | 2.2742 | 2.4461 | 2.3171 | 2.489 | 1.201 | 2.0596 | 2.5414 | 2.5414 | 2.8626 | 2.8626 | 2019-12-09 12:00 | 2.4997 | 4.0965 | 6.7245 | 6.7245 | 6.7245 | 6.7245
2021-10-12 | 1.8119 | 2.2049 | 2.1573 | 2.3204 | 2.1981 | 2.3612 | 1.0346 | 1.7742 | 2.1892 | 2.1892 | 2.4659 | 2.4659 | 2019-12-09 13:00 | 2.393 | 3.9217 | 6.4375 | 6.4375 | 6.4375 | 6.4375
2021-10-12 01:00 | 1.6205 | 1.9719 | 1.9294 | 2.0752 | 1.9658 | 2.1117 | 0.93862 | 1.6096 | 1.9861 | 1.9861 | 2.2372 | 2.2372 | 2019-12-09 14:00 | 2.454 | 4.0216 | 6.6015 | 6.6015 | 6.6015 | 6.6015
2021-10-12 02:00 | 1.5575 | 1.8954 | 1.8545 | 1.9947 | 1.8895 | 2.0297 | 0.86879 | 1.4898 | 1.8384 | 1.8384 | 2.0707 | 2.0707 | 2019-12-09 15:00 | 2.4463 | 4.0091 | 6.581 | 6.581 | 6.581 | 6.581
2021-10-12 03:00 | 1.4918 | 1.8154 | 1.7762 | 1.9105 | 1.8098 | 1.944 | 0.82307 | 1.4114 | 1.7416 | 1.7416 | 1.9617 | 1.9617 | 2019-12-09 16:00 | 2.4692 | 4.0466 | 6.6425 | 6.6425 | 6.6425 | 6.6425
2021-10-12 04:00 | 1.509 | 1.8362 | 1.7966 | 1.9324 | 1.8306 | 1.9664 | 0.8345 | 1.431 | 1.7658 | 1.7658 | 1.989 | 1.989 | 2019-12-09 17:00 | 2.3168 | 3.7968 | 6.2325 | 6.2325 | 6.2325 | 6.2325
2021-10-12 05:00 | 1.6742 | 2.0374 | 1.9934 | 2.1441 | 2.0311 | 2.1818 | 0.89164 | 1.529 | 1.8867 | 1.8867 | 2.1252 | 2.1252 | 2019-12-09 18:00 | 2.2482 | 3.6844 | 6.048 | 6.048 | 6.048 | 6.048
2021-10-12 06:00 | 2.0548 | 2.5005 | 2.4466 | 2.6315 | 2.4928 | 2.6777 | 1.086 | 1.8623 | 2.298 | 2.298 | 2.5884 | 2.5884 | 2019-12-09 19:00 | 1.9205 | 3.1473 | 5.1664 | 5.1664 | 5.1664 | 5.1664
2021-10-12 07:00 | 2.4406 | 2.97 | 2.9059 | 3.1256 | 2.9608 | 3.1805 | 1.2517 | 2.1466 | 2.6487 | 2.6487 | 2.9835 | 2.9835 | 2019-12-09 20:00 | 1.9281 | 3.1598 | 5.1869 | 5.1869 | 5.1869 | 5.1869
2021-10-12 08:00 | 2.5835 | 3.1439 | 3.0761 | 3.3086 | 3.1342 | 3.3667 | 1.3661 | 2.3426 | 2.8906 | 2.8906 | 3.256 | 3.256 | 2019-12-09 21:00 | 1.9281 | 3.1598 | 5.1869 | 5.1869 | 5.1869 | 5.1869
2021-10-12 09:00 | 2.7036 | 3.2899 | 3.219 | 3.4623 | 3.2798 | 3.5231 | 1.4232 | 2.4406 | 3.0116 | 3.0116 | 3.3922 | 3.3922 | 2019-12-09 22:00 | 1.6461 | 2.6977 | 4.4283 | 4.4283 | 4.4283 | 4.4283
2021-10-12 10:00 | 2.6178 | 3.1856 | 3.1169 | 3.3525 | 3.1758 | 3.4114 | 1.4489 | 2.4847 | 3.066 | 3.066 | 3.4535 | 3.4535 | 2019-12-09 23:00 | 1.4937 | 2.4479 | 4.0183 | 4.0183 | 4.0183 | 4.0183
2021-10-12 11:00 | 2.4835 | 3.0222 | 2.957 | 3.1805 | 3.0128 | 3.2364 | 1.5604 | 2.6758 | 3.3018 | 3.3018 | 3.7192 | 3.7192 | 2019-12-10 | 1.4175 | 2.323 | 3.8133 | 3.8133 | 3.8133 | 3.8133
2021-10-12 12:00 | 2.5321 | 3.0813 | 3.0148 | 3.2427 | 3.0718 | 3.2997 | 1.5747 | 2.7003 | 3.3321 | 3.3321 | 3.7532 | 3.7532 | 2019-12-10 01:00 | 1.3184 | 2.1607 | 3.5468 | 3.5468 | 3.5468 | 3.5468
2021-10-12 13:00 | 2.4206 | 2.9456 | 2.8821 | 3.1 | 2.9366 | 3.1544 | 1.4289 | 2.4504 | 3.0236 | 3.0236 | 3.4058 | 3.4058 | 2019-12-10 02:00 | 1.3261 | 2.1732 | 3.5673 | 3.5673 | 3.5673 | 3.5673
2021-10-12 14:00 | 2.3292 | 2.8344 | 2.7732 | 2.9828 | 2.8256 | 3.0353 | 1.3946 | 2.3916 | 2.9511 | 2.9511 | 3.3241 | 3.3241 | 2019-12-10 03:00 | 1.2803 | 2.0982 | 3.4443 | 3.4443 | 3.4443 | 3.4443
2021-10-12 15:00 | 2.2549 | 2.7439 | 2.6848 | 2.8877 | 2.7355 | 2.9384 | 1.3546 | 2.323 | 2.8664 | 2.8664 | 3.2287 | 3.2287 | 2019-12-10 04:00 | 1.2727 | 2.0857 | 3.4238 | 3.4238 | 3.4238 | 3.4238
2021-10-12 16:00 | 2.3149 | 2.817 | 2.7562 | 2.9645 | 2.8083 | 3.0166 | 1.4489 | 2.4847 | 3.066 | 3.066 | 3.4535 | 3.4535 | 2019-12-10 05:00 | 1.387 | 2.2731 | 3.7313 | 3.7313 | 3.7313 | 3.7313
2021-10-12 17:00 | 2.5264 | 3.0743 | 3.008 | 3.2354 | 3.0649 | 3.2922 | 1.5775 | 2.7052 | 3.3381 | 3.3381 | 3.76 | 3.76 | 2019-12-10 06:00 | 1.4556 | 2.3855 | 3.9158 | 3.9158 | 3.9158 | 3.9158
2021-10-12 18:00 | 2.7093 | 3.2969 | 3.2258 | 3.4696 | 3.2867 | 3.5306 | 1.6919 | 2.9013 | 3.58 | 3.58 | 4.0325 | 4.0325 | 2019-12-10 07:00 | 1.7833 | 2.9225 | 4.7974 | 4.7974 | 4.7974 | 4.7974
2021-10-12 19:00 | 2.7378 | 3.3317 | 3.2598 | 3.5062 | 3.3214 | 3.5678 | 1.7833 | 3.0581 | 3.7735 | 3.7735 | 4.2505 | 4.2505 | 2019-12-10 08:00 | 2.0958 | 3.4346 | 5.6379 | 5.6379 | 5.6379 | 5.6379
2021-10-12 20:00 | 2.6092 | 3.1752 | 3.1067 | 3.3415 | 3.1654 | 3.4002 | 1.7062 | 2.9258 | 3.6102 | 3.6102 | 4.0665 | 4.0665 | 2019-12-10 09:00 | 2.2939 | 3.7593 | 6.171 | 6.171 | 6.171 | 6.171
2021-10-12 21:00 | 2.4692 | 3.0048 | 2.94 | 3.1622 | 2.9955 | 3.2177 | 1.5518 | 2.6611 | 3.2837 | 3.2837 | 3.6987 | 3.6987 | 2019-12-10 10:00 | 2.3473 | 3.8467 | 6.3145 | 6.3145 | 6.3145 | 6.3145
2021-10-12 22:00 | 2.1912 | 2.6664 | 2.6089 | 2.8061 | 2.6582 | 2.8554 | 1.2913 | 2.2144 | 2.7325 | 2.7325 | 3.0779 | 3.0779 | 2019-12-10 11:00 | 2.5378 | 4.159 | 6.827 | 6.827 | 6.827 | 6.827
2021-10-12 23:00 | 1.9262 | 2.344 | 2.2934 | 2.4668 | 2.3368 | 2.5101 | 1.1403 | 1.9554 | 2.4129 | 2.4129 | 2.7178 | 2.7178 | 2019-12-10 12:00 | 2.5454 | 4.1715 | 6.8475 | 6.8475 | 6.8475 | 6.8475
2021-10-13 | 1.8519 | 2.2536 | 2.205 | 2.3716 | 2.2466 | 2.4133 | 1.0689 | 1.8329 | 2.2617 | 2.2617 | 2.5476 | 2.5476 | 2019-12-10 13:00 | 2.6674 | 4.3713 | 7.1755 | 7.1755 | 7.1755 | 7.1755
2021-10-13 01:00 | 1.6948 | 2.0623 | 2.0179 | 2.1704 | 2.056 | 2.2085 | 0.92343 | 1.5835 | 1.954 | 1.954 | 2.201 | 2.201 | 2019-12-10 14:00 | 2.6674 | 4.3713 | 7.1755 | 7.1755 | 7.1755 | 7.1755
2021-10-13 02:00 | 1.5976 | 1.9441 | 1.9021 | 2.0459 | 1.9381 | 2.0818 | 0.84593 | 1.4506 | 1.79 | 1.79 | 2.0162 | 2.0162 | 2019-12-10 15:00 | 2.5607 | 4.1964 | 6.8885 | 6.8885 | 6.8885 | 6.8885
2021-10-13 03:00 | 1.5661 | 1.9058 | 1.8647 | 2.0056 | 1.8999 | 2.0409 | 0.81735 | 1.4016 | 1.7295 | 1.7295 | 1.9481 | 1.9481 | 2019-12-10 16:00 | 2.5607 | 4.1964 | 6.8885 | 6.8885 | 6.8885 | 6.8885
2021-10-13 04:00 | 1.5775 | 1.9197 | 1.8783 | 2.0203 | 1.9138 | 2.0558 | 0.87331 | 1.4976 | 1.8479 | 1.8479 | 2.0815 | 2.0815 | 2019-12-10 17:00 | 2.5683 | 4.2089 | 6.909 | 6.909 | 6.909 | 6.909
2021-10-13 05:00 | 1.7319 | 2.1075 | 2.0621 | 2.2179 | 2.101 | 2.2569 | 0.88594 | 1.5192 | 1.8747 | 1.8747 | 2.1116 | 2.1116 | 2019-12-10 18:00 | 2.3625 | 3.8717 | 6.3555 | 6.3555 | 6.3555 | 6.3555
2021-10-13 06:00 | 2.0462 | 2.4901 | 2.4364 | 2.6205 | 2.4824 | 2.6666 | 1.0279 | 1.7627 | 2.175 | 2.175 | 2.45 | 2.45 | 2019-12-10 19:00 | 2.1339 | 3.497 | 5.7404 | 5.7404 | 5.7404 | 5.7404
2021-10-13 07:00 | 2.5264 | 3.0743 | 3.008 | 3.2354 | 3.0649 | 3.2922 | 1.2117 | 2.0779 | 2.5641 | 2.5641 | 2.8881 | 2.8881 | 2019-12-10 20:00 | 1.9357 | 3.1723 | 5.2074 | 5.2074 | 5.2074 | 5.2074
2021-10-13 08:00 | 2.7405 | 3.3349 | 3.2629 | 3.5096 | 3.3246 | 3.5712 | 1.3261 | 2.274 | 2.8059 | 2.8059 | 3.1606 | 3.1606 | 2019-12-10 21:00 | 1.9357 | 3.1723 | 5.2074 | 5.2074 | 5.2074 | 5.2074
2021-10-13 09:00 | 2.7864 | 3.3908 | 3.3177 | 3.5684 | 3.3804 | 3.6311 | 1.4861 | 2.5484 | 3.1446 | 3.1446 | 3.542 | 3.542 | 2019-12-10 22:00 | 1.7071 | 2.7976 | 4.5923 | 4.5923 | 4.5923 | 4.5923
2021-10-13 10:00 | 2.7464 | 3.3421 | 3.27 | 3.5172 | 3.3318 | 3.579 | 1.4404 | 2.47 | 3.0478 | 3.0478 | 3.4331 | 3.4331 | 2019-12-10 23:00 | 1.5166 | 2.4854 | 4.0798 | 4.0798 | 4.0798 | 4.0798
2021-10-13 11:00 | 2.6207 | 3.1891 | 3.1203 | 3.3562 | 3.1793 | 3.4151 | 1.4947 | 2.5631 | 3.1627 | 3.1627 | 3.5625 | 3.5625 | 2019-12-11 | 1.4175 | 2.323 | 3.8133 | 3.8133 | 3.8133 | 3.8133
2021-10-13 12:00 | 2.595 | 3.1578 | 3.0897 | 3.3232 | 3.1481 | 3.3816 | 1.5159 | 2.5995 | 3.2076 | 3.2076 | 3.613 | 3.613 | 2019-12-11 01:00 | 1.3489 | 2.2106 | 3.6288 | 3.6288 | 3.6288 | 3.6288
2021-10-13 13:00 | 2.4806 | 3.0187 | 2.9536 | 3.1768 | 3.0094 | 3.2326 | 1.5232 | 2.6121 | 3.2232 | 3.2232 | 3.6306 | 3.6306 | 2019-12-11 02:00 | 1.2803 | 2.0982 | 3.4443 | 3.4443 | 3.4443 | 3.4443
2021-10-13 14:00 | 2.2463 | 2.7335 | 2.6745 | 2.8767 | 2.7251 | 2.9272 | 1.3518 | 2.3181 | 2.8604 | 2.8604 | 3.2219 | 3.2219 | 2019-12-11 03:00 | 1.2803 | 2.0982 | 3.4443 | 3.4443 | 3.4443 | 3.4443
2021-10-13 15:00 | 2.2063 | 2.6848 | 2.6269 | 2.8255 | 2.6765 | 2.8751 | 1.4118 | 2.421 | 2.9874 | 2.9874 | 3.3649 | 3.3649 | 2019-12-11 04:00 | 1.2727 | 2.0857 | 3.4238 | 3.4238 | 3.4238 | 3.4238
2021-10-13 16:00 | 2.3149 | 2.817 | 2.7562 | 2.9645 | 2.8083 | 3.0166 | 1.509 | 2.5876 | 3.193 | 3.193 | 3.5965 | 3.5965 | 2019-12-11 05:00 | 1.3261 | 2.1732 | 3.5673 | 3.5673 | 3.5673 | 3.5673
2021-10-13 17:00 | 2.4635 | 2.9978 | 2.9331 | 3.1549 | 2.9886 | 3.2103 | 1.5604 | 2.6758 | 3.3018 | 3.3018 | 3.7192 | 3.7192 | 2019-12-11 06:00 | 1.509 | 2.4729 | 4.0593 | 4.0593 | 4.0593 | 4.0593
2021-10-13 18:00 | 2.6493 | 3.2239 | 3.1543 | 3.3928 | 3.2139 | 3.4524 | 1.6719 | 2.867 | 3.5377 | 3.5377 | 3.9848 | 3.9848 | 2019-12-11 07:00 | 1.8062 | 2.96 | 4.8589 | 4.8589 | 4.8589 | 4.8589
2021-10-13 19:00 | 2.7236 | 3.3143 | 3.2428 | 3.4879 | 3.3041 | 3.5492 | 1.7462 | 2.9944 | 3.6949 | 3.6949 | 4.1619 | 4.1619 | 2019-12-11 08:00 | 2.0729 | 3.3971 | 5.5764 | 5.5764 | 5.5764 | 5.5764
2021-10-13 20:00 | 2.5435 | 3.0952 | 3.0284 | 3.2573 | 3.0857 | 3.3146 | 1.749 | 2.9993 | 3.7009 | 3.7009 | 4.1687 | 4.1687 | 2019-12-11 09:00 | 2.0424 | 3.3472 | 5.4944 | 5.4944 | 5.4944 | 5.4944
2021-10-13 21:00 | 2.3835 | 2.9004 | 2.8379 | 3.0524 | 2.8915 | 3.106 | 1.5604 | 2.6758 | 3.3018 | 3.3018 | 3.7192 | 3.7192 | 2019-12-11 10:00 | 2.1186 | 3.4721 | 5.6994 | 5.6994 | 5.6994 | 5.6994
2021-10-13 22:00 | 2.2406 | 2.7266 | 2.6677 | 2.8694 | 2.7181 | 2.9198 | 1.2889 | 2.2103 | 2.7273 | 2.7273 | 3.072 | 3.072 | 2019-12-11 11:00 | 2.1949 | 3.597 | 5.9044 | 5.9044 | 5.9044 | 5.9044
2021-10-13 23:00 | 1.9005 | 2.3127 | 2.2628 | 2.4339 | 2.3056 | 2.4766 | 1.0946 | 1.877 | 2.3161 | 2.3161 | 2.6089 | 2.6089 | 2019-12-11 12:00 | 2.2787 | 3.7343 | 6.13 | 6.13 | 6.13 | 6.13
2021-10-14 | 1.7456 | 2.1242 | 2.0783 | 2.2354 | 2.1176 | 2.2747 | 1.011 | 1.7338 | 2.1394 | 2.1394 | 2.4098 | 2.4098 | 2019-12-11 13:00 | 2.332 | 3.8218 | 6.2735 | 6.2735 | 6.2735 | 6.2735
2021-10-14 01:00 | 1.6033 | 1.951 | 1.9089 | 2.0532 | 1.945 | 2.0893 | 0.90595 | 1.5536 | 1.917 | 1.917 | 2.1593 | 2.1593 | 2019-12-11 14:00 | 2.393 | 3.9217 | 6.4375 | 6.4375 | 6.4375 | 6.4375
2021-10-14 02:00 | 1.5518 | 1.8884 | 1.8477 | 1.9873 | 1.8826 | 2.0223 | 0.8345 | 1.431 | 1.7658 | 1.7658 | 1.989 | 1.989 | 2019-12-11 15:00 | 2.5302 | 4.1465 | 6.8065 | 6.8065 | 6.8065 | 6.8065
2021-10-14 03:00 | 1.5232 | 1.8536 | 1.8136 | 1.9507 | 1.8479 | 1.985 | 0.78591 | 1.3477 | 1.663 | 1.663 | 1.8732 | 1.8732 | 2019-12-11 16:00 | 2.393 | 3.9217 | 6.4375 | 6.4375 | 6.4375 | 6.4375
2021-10-14 04:00 | 1.6318 | 1.9858 | 1.943 | 2.0898 | 1.9797 | 2.1265 | 0.79163 | 1.3575 | 1.6751 | 1.6751 | 1.8868 | 1.8868 | 2019-12-11 17:00 | 2.3244 | 3.8093 | 6.253 | 6.253 | 6.253 | 6.253
2021-10-14 05:00 | 1.7747 | 2.1597 | 2.1131 | 2.2728 | 2.153 | 2.3127 | 0.92595 | 1.5879 | 1.9593 | 1.9593 | 2.207 | 2.207 | 2019-12-11 18:00 | 2.1034 | 3.4471 | 5.6584 | 5.6584 | 5.6584 | 5.6584
2021-10-14 06:00 | 1.9605 | 2.3857 | 2.3343 | 2.5107 | 2.3784 | 2.5548 | 1.0231 | 1.7545 | 2.1649 | 2.1649 | 2.4386 | 2.4386 | 2019-12-11 19:00 | 2.0043 | 3.2847 | 5.3919 | 5.3919 | 5.3919 | 5.3919
2021-10-14 07:00 | 2.5121 | 3.0569 | 2.991 | 3.2171 | 3.0475 | 3.2736 | 1.3161 | 2.2568 | 2.7848 | 2.7848 | 3.1368 | 3.1368 | 2019-12-11 20:00 | 1.9281 | 3.1598 | 5.1869 | 5.1869 | 5.1869 | 5.1869
2021-10-14 08:00 | 2.6635 | 3.2413 | 3.1713 | 3.4111 | 3.2313 | 3.471 | 1.3689 | 2.3475 | 2.8967 | 2.8967 | 3.2628 | 3.2628 | 2019-12-11 21:00 | 1.8367 | 3.0099 | 4.9409 | 4.9409 | 4.9409 | 4.9409
2021-10-14 09:00 | 2.6321 | 3.203 | 3.1339 | 3.3708 | 3.1931 | 3.43 | 1.4232 | 2.4406 | 3.0116 | 3.0116 | 3.3922 | 3.3922 | 2019-12-11 22:00 | 1.6309 | 2.6727 | 4.3873 | 4.3873 | 4.3873 | 4.3873
2021-10-14 10:00 | 2.6721 | 3.2517 | 3.1815 | 3.422 | 3.2417 | 3.4822 | 1.4575 | 2.4994 | 3.0841 | 3.0841 | 3.4739 | 3.4739 | 2019-12-11 23:00 | 1.4937 | 2.4479 | 4.0183 | 4.0183 | 4.0183 | 4.0183
2021-10-14 11:00 | 2.6292 | 3.1995 | 3.1305 | 3.3671 | 3.1897 | 3.4263 | 1.4718 | 2.5239 | 3.1144 | 3.1144 | 3.508 | 3.508 | 2019-12-12 | 1.3489 | 2.2106 | 3.6288 | 3.6288 | 3.6288 | 3.6288
2021-10-14 12:00 | 2.6693 | 3.2482 | 3.1781 | 3.4184 | 3.2382 | 3.4784 | 1.6147 | 2.769 | 3.4167 | 3.4167 | 3.8486 | 3.8486 | 2019-12-12 01:00 | 1.3032 | 2.1357 | 3.5058 | 3.5058 | 3.5058 | 3.5058
2021-10-14 13:00 | 2.4788 | 3.0164 | 2.9514 | 3.1745 | 3.0071 | 3.2302 | 1.509 | 2.5876 | 3.193 | 3.193 | 3.5965 | 3.5965 | 2019-12-12 02:00 | 1.2422 | 2.0358 | 3.3417 | 3.3417 | 3.3417 | 3.3417
2021-10-14 14:00 | 2.4235 | 2.9491 | 2.8855 | 3.1036 | 2.94 | 3.1582 | 1.4289 | 2.4504 | 3.0236 | 3.0236 | 3.4058 | 3.4058 | 2019-12-12 03:00 | 1.2727 | 2.0857 | 3.4238 | 3.4238 | 3.4238 | 3.4238
2021-10-14 15:00 | 2.0777 | 2.5283 | 2.4738 | 2.6608 | 2.5205 | 2.7075 | 1.3461 | 2.3083 | 2.8483 | 2.8483 | 3.2083 | 3.2083 | 2019-12-12 04:00 | 1.3413 | 2.1981 | 3.6083 | 3.6083 | 3.6083 | 3.6083
2021-10-14 16:00 | 2.1148 | 2.5735 | 2.518 | 2.7083 | 2.5656 | 2.7559 | 1.3375 | 2.2936 | 2.8301 | 2.8301 | 3.1878 | 3.1878 | 2019-12-12 05:00 | 1.3489 | 2.2106 | 3.6288 | 3.6288 | 3.6288 | 3.6288
2021-10-14 17:00 | 2.1234 | 2.584 | 2.5282 | 2.7193 | 2.576 | 2.7671 | 1.4089 | 2.4161 | 2.9813 | 2.9813 | 3.3581 | 3.3581 | 2019-12-12 06:00 | 1.5166 | 2.4854 | 4.0798 | 4.0798 | 4.0798 | 4.0798
2021-10-14 18:00 | 2.4749 | 3.0117 | 2.9468 | 3.1695 | 3.0024 | 3.2252 | 1.569 | 2.6905 | 3.32 | 3.32 | 3.7396 | 3.7396 | 2019-12-12 07:00 | 1.8443 | 3.0224 | 4.9614 | 4.9614 | 4.9614 | 4.9614
2021-10-14 19:00 | 2.5607 | 3.1161 | 3.0488 | 3.2793 | 3.1065 | 3.3369 | 1.6004 | 2.7445 | 3.3865 | 3.3865 | 3.8145 | 3.8145 | 2019-12-12 08:00 | 2.1644 | 3.547 | 5.8224 | 5.8224 | 5.8224 | 5.8224
2021-10-14 20:00 | 2.4035 | 2.9248 | 2.8617 | 3.078 | 2.9158 | 3.1321 | 1.5833 | 2.715 | 3.3502 | 3.3502 | 3.7736 | 3.7736 | 2019-12-12 09:00 | 2.1644 | 3.547 | 5.8224 | 5.8224 | 5.8224 | 5.8224
2021-10-14 21:00 | 2.3006 | 2.7996 | 2.7392 | 2.9462 | 2.791 | 2.998 | 1.4146 | 2.4259 | 2.9934 | 2.9934 | 3.3718 | 3.3718 | 2019-12-12 10:00 | 2.1491 | 3.522 | 5.7814 | 5.7814 | 5.7814 | 5.7814
2021-10-14 22:00 | 2.1463 | 2.6118 | 2.5554 | 2.7486 | 2.6037 | 2.7969 | 1.2965 | 2.2233 | 2.7434 | 2.7434 | 3.0901 | 3.0901 | 2019-12-12 11:00 | 2.2482 | 3.6844 | 6.048 | 6.048 | 6.048 | 6.048
2021-10-14 23:00 | 1.9462 | 2.3683 | 2.3173 | 2.4924 | 2.361 | 2.5362 | 1.106 | 1.8966 | 2.3403 | 2.3403 | 2.6361 | 2.6361 | 2019-12-12 12:00 | 2.3092 | 3.7843 | 6.212 | 6.212 | 6.212 | 6.212
2021-10-15 | 1.8548 | 2.2571 | 2.2084 | 2.3753 | 2.2501 | 2.417 | 1.0003 | 1.7153 | 2.1166 | 2.1166 | 2.3841 | 2.3841 | 2019-12-12 13:00 | 2.3244 | 3.8093 | 6.253 | 6.253 | 6.253 | 6.253
2021-10-15 01:00 | 1.6776 | 2.0414 | 1.9974 | 2.1484 | 2.0351 | 2.1861 | 0.90885 | 1.5585 | 1.9231 | 1.9231 | 2.1662 | 2.1662 | 2019-12-12 14:00 | 2.5683 | 4.2089 | 6.909 | 6.909 | 6.909 | 6.909
2021-10-15 02:00 | 1.6404 | 1.9962 | 1.9532 | 2.1008 | 1.9901 | 2.1377 | 0.82022 | 1.4066 | 1.7356 | 1.7356 | 1.955 | 1.955 | 2019-12-12 15:00 | 2.6674 | 4.3713 | 7.1755 | 7.1755 | 7.1755 | 7.1755
2021-10-15 03:00 | 1.6318 | 1.9858 | 1.943 | 2.0898 | 1.9797 | 2.1265 | 0.80878 | 1.3869 | 1.7114 | 1.7114 | 1.9277 | 1.9277 | 2019-12-12 16:00 | 2.5911 | 4.2464 | 6.9705 | 6.9705 | 6.9705 | 6.9705
2021-10-15 04:00 | 1.6347 | 1.9893 | 1.9464 | 2.0935 | 1.9831 | 2.1303 | 0.79735 | 1.3673 | 1.6872 | 1.6872 | 1.9004 | 1.9004 | 2019-12-12 17:00 | 2.393 | 3.9217 | 6.4375 | 6.4375 | 6.4375 | 6.4375
2021-10-15 05:00 | 1.7404 | 2.1179 | 2.0723 | 2.2289 | 2.1114 | 2.2681 | 0.88303 | 1.5143 | 1.8685 | 1.8685 | 2.1047 | 2.1047 | 2019-12-12 18:00 | 2.2558 | 3.6969 | 6.0685 | 6.0685 | 6.0685 | 6.0685
2021-10-15 06:00 | 2.112 | 2.5701 | 2.5146 | 2.7047 | 2.5621 | 2.7522 | 1.026 | 1.7594 | 2.171 | 2.171 | 2.4454 | 2.4454 | 2019-12-12 19:00 | 2.0805 | 3.4096 | 5.5969 | 5.5969 | 5.5969 | 5.5969
2021-10-15 07:00 | 2.5349 | 3.0848 | 3.0182 | 3.2464 | 3.0753 | 3.3034 | 1.3175 | 2.2593 | 2.7878 | 2.7878 | 3.1402 | 3.1402 | 2019-12-12 20:00 | 1.9815 | 3.2472 | 5.3304 | 5.3304 | 5.3304 | 5.3304
2021-10-15 08:00 | 2.8093 | 3.4186 | 3.3449 | 3.5977 | 3.4081 | 3.6609 | 1.4146 | 2.4259 | 2.9934 | 2.9934 | 3.3718 | 3.3718 | 2019-12-12 21:00 | 1.9357 | 3.1723 | 5.2074 | 5.2074 | 5.2074 | 5.2074
2021-10-15 09:00 | 2.7407 | 3.3352 | 3.2632 | 3.5099 | 3.3249 | 3.5715 | 1.4489 | 2.4847 | 3.066 | 3.066 | 3.4535 | 3.4535 | 2019-12-12 22:00 | 1.6614 | 2.7227 | 4.4693 | 4.4693 | 4.4693 | 4.4693
2021-10-15 10:00 | 2.4149 | 2.9387 | 2.8753 | 3.0926 | 2.9296 | 3.147 | 1.4432 | 2.4749 | 3.0539 | 3.0539 | 3.4399 | 3.4399 | 2019-12-12 23:00 | 1.5013 | 2.4604 | 4.0388 | 4.0388 | 4.0388 | 4.0388
2021-10-15 11:00 | 2.5378 | 3.0882 | 3.0216 | 3.25 | 3.0787 | 3.3071 | 1.5976 | 2.7395 | 3.3804 | 3.3804 | 3.8077 | 3.8077 | 2019-12-13 | 1.3946 | 2.2856 | 3.7518 | 3.7518 | 3.7518 | 3.7518
2021-10-15 12:00 | 2.5149 | 3.0604 | 2.9944 | 3.2207 | 3.051 | 3.2773 | 1.5375 | 2.6366 | 3.2534 | 3.2534 | 3.6647 | 3.6647 | 2019-12-13 01:00 | 1.3413 | 2.1981 | 3.6083 | 3.6083 | 3.6083 | 3.6083
2021-10-15 13:00 | 2.4835 | 3.0222 | 2.957 | 3.1805 | 3.0128 | 3.2364 | 1.5833 | 2.715 | 3.3502 | 3.3502 | 3.7736 | 3.7736 | 2019-12-13 02:00 | 1.2498 | 2.0483 | 3.3622 | 3.3622 | 3.3622 | 3.3622
2021-10-15 14:00 | 2.292 | 2.7892 | 2.729 | 2.9353 | 2.7806 | 2.9868 | 1.549 | 2.6562 | 3.2776 | 3.2776 | 3.6919 | 3.6919 | 2019-12-13 03:00 | 1.2422 | 2.0358 | 3.3417 | 3.3417 | 3.3417 | 3.3417
2021-10-15 15:00 | 2.1577 | 2.6257 | 2.5691 | 2.7632 | 2.6176 | 2.8118 | 1.3489 | 2.3132 | 2.8543 | 2.8543 | 3.2151 | 3.2151 | 2019-12-13 04:00 | 1.2727 | 2.0857 | 3.4238 | 3.4238 | 3.4238 | 3.4238
2021-10-15 16:00 | 2.1977 | 2.6744 | 2.6167 | 2.8145 | 2.6661 | 2.8639 | 1.4318 | 2.4553 | 3.0297 | 3.0297 | 3.4126 | 3.4126 | 2019-12-13 05:00 | 1.4023 | 2.2981 | 3.7723 | 3.7723 | 3.7723 | 3.7723
2021-10-15 17:00 | 2.392 | 2.9109 | 2.8481 | 3.0634 | 2.9019 | 3.1172 | 1.5604 | 2.6758 | 3.3018 | 3.3018 | 3.7192 | 3.7192 | 2019-12-13 06:00 | 1.5166 | 2.4854 | 4.0798 | 4.0798 | 4.0798 | 4.0798
2021-10-15 18:00 | 2.6092 | 3.1752 | 3.1067 | 3.3415 | 3.1654 | 3.4002 | 1.6776 | 2.8768 | 3.5498 | 3.5498 | 3.9984 | 3.9984 | 2019-12-13 07:00 | 1.8595 | 3.0474 | 5.0024 | 5.0024 | 5.0024 | 5.0024
2021-10-15 19:00 | 2.6978 | 3.283 | 3.2122 | 3.455 | 3.2729 | 3.5157 | 1.8033 | 3.0924 | 3.8158 | 3.8158 | 4.2981 | 4.2981 | 2019-12-13 08:00 | 2.1644 | 3.547 | 5.8224 | 5.8224 | 5.8224 | 5.8224
2021-10-15 20:00 | 2.6178 | 3.1856 | 3.1169 | 3.3525 | 3.1758 | 3.4114 | 1.7719 | 3.0385 | 3.7493 | 3.7493 | 4.2232 | 4.2232 | 2019-12-13 09:00 | 2.2558 | 3.6969 | 6.0685 | 6.0685 | 6.0685 | 6.0685
2021-10-15 21:00 | 2.3978 | 2.9178 | 2.8549 | 3.0707 | 2.9088 | 3.1246 | 1.7147 | 2.9405 | 3.6284 | 3.6284 | 4.087 | 4.087 | 2019-12-13 10:00 | 2.2787 | 3.7343 | 6.13 | 6.13 | 6.13 | 6.13
2021-10-15 22:00 | 2.2377 | 2.7231 | 2.6643 | 2.8657 | 2.7147 | 2.9161 | 1.4518 | 2.4896 | 3.072 | 3.072 | 3.4603 | 3.4603 | 2019-12-13 11:00 | 2.2406 | 3.6719 | 6.0275 | 6.0275 | 6.0275 | 6.0275
2021-10-15 23:00 | 2.0377 | 2.4796 | 2.4261 | 2.6095 | 2.472 | 2.6554 | 1.2546 | 2.1515 | 2.6548 | 2.6548 | 2.9903 | 2.9903 | 2019-12-13 12:00 | 2.332 | 3.8218 | 6.2735 | 6.2735 | 6.2735 | 6.2735
2021-10-16 | 1.9033 | 2.3162 | 2.2662 | 2.4375 | 2.309 | 2.4803 | 1.126 | 1.9309 | 2.3826 | 2.3826 | 2.6838 | 2.6838 | 2019-12-13 13:00 | 2.2482 | 3.6844 | 6.048 | 6.048 | 6.048 | 6.048
2021-10-16 01:00 | 1.749 | 2.1284 | 2.0825 | 2.2399 | 2.1218 | 2.2792 | 1.0517 | 1.8035 | 2.2254 | 2.2254 | 2.5067 | 2.5067 | 2019-12-13 14:00 | 2.393 | 3.9217 | 6.4375 | 6.4375 | 6.4375 | 6.4375
2021-10-16 02:00 | 1.7004 | 2.0693 | 2.0246 | 2.1777 | 2.0629 | 2.2159 | 0.93452 | 1.6026 | 1.9775 | 1.9775 | 2.2274 | 2.2274 | 2019-12-13 15:00 | 2.3778 | 3.8967 | 6.3965 | 6.3965 | 6.3965 | 6.3965
2021-10-16 03:00 | 1.6233 | 1.9754 | 1.9328 | 2.0789 | 1.9693 | 2.1154 | 0.89166 | 1.529 | 1.8868 | 1.8868 | 2.1252 | 2.1252 | 2019-12-13 16:00 | 2.454 | 4.0216 | 6.6015 | 6.6015 | 6.6015 | 6.6015
2021-10-16 04:00 | 1.6776 | 2.0414 | 1.9974 | 2.1484 | 2.0351 | 2.1861 | 0.82307 | 1.4114 | 1.7416 | 1.7416 | 1.9617 | 1.9617 | 2019-12-13 17:00 | 2.3244 | 3.8093 | 6.253 | 6.253 | 6.253 | 6.253
2021-10-16 05:00 | 1.7487 | 2.128 | 2.0821 | 2.2395 | 2.1215 | 2.2789 | 0.93167 | 1.5977 | 1.9714 | 1.9714 | 2.2206 | 2.2206 | 2019-12-13 18:00 | 2.0729 | 3.3971 | 5.5764 | 5.5764 | 5.5764 | 5.5764
2021-10-16 06:00 | 1.8976 | 2.3092 | 2.2594 | 2.4302 | 2.3021 | 2.4729 | 0.97739 | 1.6761 | 2.0682 | 2.0682 | 2.3296 | 2.3296 | 2019-12-13 19:00 | 1.9205 | 3.1473 | 5.1664 | 5.1664 | 5.1664 | 5.1664
2021-10-16 07:00 | 2.092 | 2.5457 | 2.4908 | 2.6791 | 2.5379 | 2.7261 | 1.1117 | 1.9064 | 2.3524 | 2.3524 | 2.6497 | 2.6497 | 2019-12-13 20:00 | 1.9129 | 3.1348 | 5.1459 | 5.1459 | 5.1459 | 5.1459
2021-10-16 08:00 | 2.1348 | 2.5979 | 2.5418 | 2.734 | 2.5899 | 2.782 | 1.2139 | 2.0816 | 2.5686 | 2.5686 | 2.8932 | 2.8932 | 2019-12-13 21:00 | 1.829 | 2.9975 | 4.9204 | 4.9204 | 4.9204 | 4.9204
2021-10-16 09:00 | 2.2692 | 2.7613 | 2.7018 | 2.906 | 2.7528 | 2.957 | 1.3775 | 2.3622 | 2.9148 | 2.9148 | 3.2832 | 3.2832 | 2019-12-13 22:00 | 1.73 | 2.8351 | 4.6538 | 4.6538 | 4.6538 | 4.6538
2021-10-16 10:00 | 2.1463 | 2.6118 | 2.5554 | 2.7486 | 2.6037 | 2.7969 | 1.4547 | 2.4945 | 3.0781 | 3.0781 | 3.4671 | 3.4671 | 2019-12-13 23:00 | 1.5699 | 2.5728 | 4.2233 | 4.2233 | 4.2233 | 4.2233
2021-10-16 11:00 | 2.1463 | 2.6118 | 2.5554 | 2.7486 | 2.6037 | 2.7969 | 1.489 | 2.5533 | 3.1506 | 3.1506 | 3.5489 | 3.5489 | 2019-12-14 | 1.4861 | 2.4354 | 3.9978 | 3.9978 | 3.9978 | 3.9978
2021-10-16 12:00 | 1.9834 | 2.4136 | 2.3615 | 2.54 | 2.4061 | 2.5846 | 1.5004 | 2.5729 | 3.1748 | 3.1748 | 3.5761 | 3.5761 | 2019-12-14 01:00 | 1.4556 | 2.3855 | 3.9158 | 3.9158 | 3.9158 | 3.9158
2021-10-16 13:00 | 1.7204 | 2.0936 | 2.0484 | 2.2033 | 2.0871 | 2.242 | 1.3861 | 2.3769 | 2.9329 | 2.9329 | 3.3036 | 3.3036 | 2019-12-14 02:00 | 1.3794 | 2.2606 | 3.7108 | 3.7108 | 3.7108 | 3.7108
2021-10-16 14:00 | 1.7719 | 2.1562 | 2.1097 | 2.2692 | 2.1496 | 2.309 | 1.3546 | 2.323 | 2.8664 | 2.8664 | 3.2287 | 3.2287 | 2019-12-14 03:00 | 1.3718 | 2.2481 | 3.6903 | 3.6903 | 3.6903 | 3.6903
2021-10-16 15:00 | 1.7633 | 2.1458 | 2.0995 | 2.2582 | 2.1392 | 2.2979 | 1.3232 | 2.2691 | 2.7999 | 2.7999 | 3.1538 | 3.1538 | 2019-12-14 04:00 | 1.4175 | 2.323 | 3.8133 | 3.8133 | 3.8133 | 3.8133
2021-10-16 16:00 | 1.9148 | 2.3301 | 2.2798 | 2.4522 | 2.3229 | 2.4952 | 1.3575 | 2.3279 | 2.8725 | 2.8725 | 3.2355 | 3.2355 | 2019-12-14 05:00 | 1.4709 | 2.4105 | 3.9568 | 3.9568 | 3.9568 | 3.9568
2021-10-16 17:00 | 2.1463 | 2.6118 | 2.5554 | 2.7486 | 2.6037 | 2.7969 | 1.4461 | 2.4798 | 3.0599 | 3.0599 | 3.4467 | 3.4467 | 2019-12-14 06:00 | 1.4709 | 2.4105 | 3.9568 | 3.9568 | 3.9568 | 3.9568
2021-10-16 18:00 | 2.3149 | 2.817 | 2.7562 | 2.9645 | 2.8083 | 3.0166 | 1.5633 | 2.6807 | 3.3079 | 3.3079 | 3.726 | 3.726 | 2019-12-14 07:00 | 1.7223 | 2.8226 | 4.6333 | 4.6333 | 4.6333 | 4.6333
2021-10-16 19:00 | 2.3774 | 2.8931 | 2.8307 | 3.0447 | 2.8842 | 3.0982 | 1.6804 | 2.8817 | 3.5558 | 3.5558 | 4.0052 | 4.0052 | 2019-12-14 08:00 | 1.8824 | 3.0849 | 5.0639 | 5.0639 | 5.0639 | 5.0639
2021-10-16 20:00 | 2.4092 | 2.9317 | 2.8685 | 3.0853 | 2.9227 | 3.1395 | 1.6176 | 2.7739 | 3.4228 | 3.4228 | 3.8554 | 3.8554 | 2019-12-14 09:00 | 1.8976 | 3.1099 | 5.1049 | 5.1049 | 5.1049 | 5.1049
2021-10-16 21:00 | 2.2463 | 2.7335 | 2.6745 | 2.8767 | 2.7251 | 2.9272 | 1.5461 | 2.6513 | 3.2716 | 3.2716 | 3.6851 | 3.6851 | 2019-12-14 10:00 | 2.0196 | 3.3097 | 5.4329 | 5.4329 | 5.4329 | 5.4329
2021-10-16 22:00 | 2.0262 | 2.4657 | 2.4125 | 2.5949 | 2.4581 | 2.6405 | 1.4146 | 2.4259 | 2.9934 | 2.9934 | 3.3718 | 3.3718 | 2019-12-14 11:00 | 2.0805 | 3.4096 | 5.5969 | 5.5969 | 5.5969 | 5.5969
2021-10-16 23:00 | 1.9348 | 2.3544 | 2.3036 | 2.4778 | 2.3472 | 2.5213 | 1.1974 | 2.0534 | 2.5338 | 2.5338 | 2.8541 | 2.8541 | 2019-12-14 12:00 | 2.1034 | 3.4471 | 5.6584 | 5.6584 | 5.6584 | 5.6584
2021-10-17 | 1.8462 | 2.2466 | 2.1982 | 2.3643 | 2.2397 | 2.4059 | 1.0719 | 1.8381 | 2.2681 | 2.2681 | 2.5548 | 2.5548 | 2019-12-14 13:00 | 2.0729 | 3.3971 | 5.5764 | 5.5764 | 5.5764 | 5.5764
2021-10-17 01:00 | 1.7008 | 2.0697 | 2.025 | 2.1781 | 2.0633 | 2.2164 | 0.94326 | 1.6175 | 1.996 | 1.996 | 2.2482 | 2.2482 | 2019-12-14 14:00 | 2.2025 | 3.6094 | 5.9249 | 5.9249 | 5.9249 | 5.9249
2021-10-17 02:00 | 1.5976 | 1.9441 | 1.9021 | 2.0459 | 1.9381 | 2.0818 | 0.91017 | 1.5608 | 1.9259 | 1.9259 | 2.1693 | 2.1693 | 2019-12-14 15:00 | 2.1491 | 3.522 | 5.7814 | 5.7814 | 5.7814 | 5.7814
2021-10-17 03:00 | 1.6176 | 1.9684 | 1.9259 | 2.0715 | 1.9623 | 2.1079 | 0.86022 | 1.4751 | 1.8202 | 1.8202 | 2.0503 | 2.0503 | 2019-12-14 16:00 | 2.1567 | 3.5345 | 5.8019 | 5.8019 | 5.8019 | 5.8019
2021-10-17 04:00 | 1.629 | 1.9823 | 1.9396 | 2.0862 | 1.9762 | 2.1228 | 0.82592 | 1.4163 | 1.7477 | 1.7477 | 1.9686 | 1.9686 | 2019-12-14 17:00 | 2.0729 | 3.3971 | 5.5764 | 5.5764 | 5.5764 | 5.5764
2021-10-17 05:00 | 1.7143 | 2.0862 | 2.0412 | 2.1954 | 2.0797 | 2.234 | 0.91452 | 1.5683 | 1.9351 | 1.9351 | 2.1797 | 2.1797 | 2019-12-14 18:00 | 1.8824 | 3.0849 | 5.0639 | 5.0639 | 5.0639 | 5.0639
2021-10-17 06:00 | 1.906 | 2.3194 | 2.2694 | 2.4409 | 2.3122 | 2.4838 | 0.92881 | 1.5928 | 1.9654 | 1.9654 | 2.2138 | 2.2138 | 2019-12-14 19:00 | 1.8214 | 2.985 | 4.8999 | 4.8999 | 4.8999 | 4.8999
2021-10-17 07:00 | 1.9234 | 2.3405 | 2.29 | 2.4631 | 2.3333 | 2.5064 | 1.0031 | 1.7201 | 2.1226 | 2.1226 | 2.3908 | 2.3908 | 2019-12-14 20:00 | 1.8595 | 3.0474 | 5.0024 | 5.0024 | 5.0024 | 5.0024
2021-10-17 08:00 | 1.9777 | 2.4066 | 2.3547 | 2.5327 | 2.3992 | 2.5772 | 1.0746 | 1.8427 | 2.2738 | 2.2738 | 2.5612 | 2.5612 | 2019-12-14 21:00 | 1.7376 | 2.8476 | 4.6744 | 4.6744 | 4.6744 | 4.6744
2021-10-17 09:00 | 1.9234 | 2.3405 | 2.29 | 2.4631 | 2.3333 | 2.5064 | 1.246 | 2.1367 | 2.6366 | 2.6366 | 2.9699 | 2.9699 | 2019-12-14 22:00 | 1.6614 | 2.7227 | 4.4693 | 4.4693 | 4.4693 | 4.4693
2021-10-17 10:00 | 1.7805 | 2.1666 | 2.1199 | 2.2801 | 2.16 | 2.3202 | 1.3775 | 2.3622 | 2.9148 | 2.9148 | 3.2832 | 3.2832 | 2019-12-14 23:00 | 1.6309 | 2.6727 | 4.3873 | 4.3873 | 4.3873 | 4.3873
2021-10-17 11:00 | 1.7747 | 2.1597 | 2.1131 | 2.2728 | 2.153 | 2.3127 | 1.3861 | 2.3769 | 2.9329 | 2.9329 | 3.3036 | 3.3036 | 2019-12-15 | 1.4861 | 2.4354 | 3.9978 | 3.9978 | 3.9978 | 3.9978
2021-10-17 12:00 | 1.6719 | 2.0345 | 1.9906 | 2.1411 | 2.0282 | 2.1787 | 1.2931 | 2.2174 | 2.7361 | 2.7361 | 3.082 | 3.082 | 2019-12-15 01:00 | 1.4785 | 2.4229 | 3.9773 | 3.9773 | 3.9773 | 3.9773
2021-10-17 13:00 | 1.5833 | 1.9267 | 1.8851 | 2.0276 | 1.9207 | 2.0632 | 1.3375 | 2.2936 | 2.8301 | 2.8301 | 3.1878 | 3.1878 | 2019-12-15 02:00 | 1.4023 | 2.2981 | 3.7723 | 3.7723 | 3.7723 | 3.7723
2021-10-17 14:00 | 1.4404 | 1.7528 | 1.715 | 1.8446 | 1.7474 | 1.877 | 1.2232 | 2.0975 | 2.5882 | 2.5882 | 2.9154 | 2.9154 | 2019-12-15 03:00 | 1.3946 | 2.2856 | 3.7518 | 3.7518 | 3.7518 | 3.7518
2021-10-17 15:00 | 1.4375 | 1.7493 | 1.7116 | 1.8409 | 1.7439 | 1.8733 | 1.1317 | 1.9407 | 2.3947 | 2.3947 | 2.6974 | 2.6974 | 2019-12-15 04:00 | 1.4023 | 2.2981 | 3.7723 | 3.7723 | 3.7723 | 3.7723
2021-10-17 16:00 | 1.689 | 2.0553 | 2.011 | 2.163 | 2.049 | 2.201 | 1.2395 | 2.1255 | 2.6228 | 2.6228 | 2.9543 | 2.9543 | 2019-12-15 05:00 | 1.509 | 2.4729 | 4.0593 | 4.0593 | 4.0593 | 4.0593
2021-10-17 17:00 | 1.9442 | 2.3659 | 2.3148 | 2.4898 | 2.3586 | 2.5336 | 1.4089 | 2.4161 | 2.9813 | 2.9813 | 3.3581 | 3.3581 | 2019-12-15 06:00 | 1.509 | 2.4729 | 4.0593 | 4.0593 | 4.0593 | 4.0593
2021-10-17 18:00 | 2.2091 | 2.6883 | 2.6303 | 2.8291 | 2.68 | 2.8788 | 1.4604 | 2.5043 | 3.0902 | 3.0902 | 3.4807 | 3.4807 | 2019-12-15 07:00 | 1.7681 | 2.8975 | 4.7564 | 4.7564 | 4.7564 | 4.7564
2021-10-17 19:00 | 2.4292 | 2.9561 | 2.8923 | 3.1109 | 2.947 | 3.1656 | 1.549 | 2.6562 | 3.2776 | 3.2776 | 3.6919 | 3.6919 | 2019-12-15 08:00 | 1.8976 | 3.1099 | 5.1049 | 5.1049 | 5.1049 | 5.1049
2021-10-17 20:00 | 2.4063 | 2.9283 | 2.8651 | 3.0817 | 2.9192 | 3.1358 | 1.629 | 2.7935 | 3.447 | 3.447 | 3.8826 | 3.8826 | 2019-12-15 09:00 | 2.0424 | 3.3472 | 5.4944 | 5.4944 | 5.4944 | 5.4944
2021-10-17 21:00 | 2.2026 | 2.6804 | 2.6226 | 2.8208 | 2.6721 | 2.8704 | 1.5175 | 2.6023 | 3.2111 | 3.2111 | 3.617 | 3.617 | 2019-12-15 10:00 | 1.9662 | 3.2223 | 5.2894 | 5.2894 | 5.2894 | 5.2894
2021-10-17 22:00 | 2.0578 | 2.5041 | 2.4501 | 2.6353 | 2.4964 | 2.6816 | 1.3118 | 2.2495 | 2.7757 | 2.7757 | 3.1265 | 3.1265 | 2019-12-15 11:00 | 2.0577 | 3.3721 | 5.5354 | 5.5354 | 5.5354 | 5.5354
2021-10-17 23:00 | 1.849 | 2.2501 | 2.2016 | 2.368 | 2.2432 | 2.4096 | 1.1546 | 1.9799 | 2.4431 | 2.4431 | 2.7519 | 2.7519 | 2019-12-15 12:00 | 2.0043 | 3.2847 | 5.3919 | 5.3919 | 5.3919 | 5.3919
2021-10-18 | 1.7347 | 2.111 | 2.0655 | 2.2216 | 2.1045 | 2.2606 | 1.0203 | 1.7496 | 2.1589 | 2.1589 | 2.4317 | 2.4317 | 2019-12-15 13:00 | 1.9357 | 3.1723 | 5.2074 | 5.2074 | 5.2074 | 5.2074
2021-10-18 01:00 | 1.5663 | 1.906 | 1.8649 | 2.0059 | 1.9002 | 2.0411 | 0.92323 | 1.5832 | 1.9536 | 1.9536 | 2.2005 | 2.2005 | 2019-12-15 14:00 | 2.0043 | 3.2847 | 5.3919 | 5.3919 | 5.3919 | 5.3919
2021-10-18 02:00 | 1.5061 | 1.8328 | 1.7932 | 1.9288 | 1.8271 | 1.9627 | 0.82592 | 1.4163 | 1.7477 | 1.7477 | 1.9686 | 1.9686 | 2019-12-15 15:00 | 2.0424 | 3.3472 | 5.4944 | 5.4944 | 5.4944 | 5.4944
2021-10-18 03:00 | 1.529 | 1.8606 | 1.8205 | 1.9581 | 1.8549 | 1.9925 | 0.81735 | 1.4016 | 1.7295 | 1.7295 | 1.9481 | 1.9481 | 2019-12-15 16:00 | 2.0272 | 3.3222 | 5.4534 | 5.4534 | 5.4534 | 5.4534
2021-10-18 04:00 | 1.5833 | 1.9267 | 1.8851 | 2.0276 | 1.9207 | 2.0632 | 0.79163 | 1.3575 | 1.6751 | 1.6751 | 1.8868 | 1.8868 | 2019-12-15 17:00 | 1.9967 | 3.2722 | 5.3714 | 5.3714 | 5.3714 | 5.3714
2021-10-18 05:00 | 1.7319 | 2.1075 | 2.0621 | 2.2179 | 2.101 | 2.2569 | 0.89737 | 1.5388 | 1.8988 | 1.8988 | 2.1388 | 2.1388 | 2019-12-15 18:00 | 1.8443 | 3.0224 | 4.9614 | 4.9614 | 4.9614 | 4.9614
2021-10-18 06:00 | 2.0765 | 2.5269 | 2.4724 | 2.6592 | 2.5191 | 2.706 | 0.98597 | 1.6908 | 2.0863 | 2.0863 | 2.35 | 2.35 | 2019-12-15 19:00 | 1.669 | 2.7352 | 4.4898 | 4.4898 | 4.4898 | 4.4898
2021-10-18 07:00 | 2.4035 | 2.9248 | 2.8617 | 3.078 | 2.9158 | 3.1321 | 1.2403 | 2.1269 | 2.6245 | 2.6245 | 2.9562 | 2.9562 | 2019-12-15 20:00 | 1.73 | 2.8351 | 4.6538 | 4.6538 | 4.6538 | 4.6538
2021-10-18 08:00 | 2.4663 | 3.0013 | 2.9366 | 3.1585 | 2.992 | 3.214 | 1.3632 | 2.3377 | 2.8846 | 2.8846 | 3.2491 | 3.2491 | 2019-12-15 21:00 | 1.7376 | 2.8476 | 4.6744 | 4.6744 | 4.6744 | 4.6744
2021-10-18 09:00 | 2.4035 | 2.9248 | 2.8617 | 3.078 | 2.9158 | 3.1321 | 1.2718 | 2.1809 | 2.691 | 2.691 | 3.0312 | 3.0312 | 2019-12-15 22:00 | 1.5699 | 2.5728 | 4.2233 | 4.2233 | 4.2233 | 4.2233
2021-10-18 10:00 | 2.032 | 2.4727 | 2.4193 | 2.6022 | 2.4651 | 2.6479 | 1.2517 | 2.1466 | 2.6487 | 2.6487 | 2.9835 | 2.9835 | 2019-12-15 23:00 | 1.5013 | 2.4604 | 4.0388 | 4.0388 | 4.0388 | 4.0388
2021-10-18 11:00 | 1.9119 | 2.3266 | 2.2764 | 2.4485 | 2.3194 | 2.4915 | 1.2746 | 2.1858 | 2.6971 | 2.6971 | 3.038 | 3.038 | 2019-12-16 | 1.4099 | 2.3105 | 3.7928 | 3.7928 | 3.7928 | 3.7928
2021-10-18 12:00 | 1.8519 | 2.2536 | 2.205 | 2.3716 | 2.2466 | 2.4133 | 1.226 | 2.1024 | 2.5943 | 2.5943 | 2.9222 | 2.9222 | 2019-12-16 01:00 | 1.3032 | 2.1357 | 3.5058 | 3.5058 | 3.5058 | 3.5058
2021-10-18 13:00 | 1.7833 | 2.1701 | 2.1233 | 2.2838 | 2.1634 | 2.3239 | 1.2718 | 2.1809 | 2.691 | 2.691 | 3.0312 | 3.0312 | 2019-12-16 02:00 | 1.2575 | 2.0608 | 3.3828 | 3.3828 | 3.3828 | 3.3828
2021-10-18 14:00 | 1.5947 | 1.9406 | 1.8987 | 2.0422 | 1.9346 | 2.0781 | 1.1632 | 1.9946 | 2.4612 | 2.4612 | 2.7723 | 2.7723 | 2019-12-16 03:00 | 1.2575 | 2.0608 | 3.3828 | 3.3828 | 3.3828 | 3.3828
2021-10-18 15:00 | 1.6861 | 2.0519 | 2.0076 | 2.1594 | 2.0455 | 2.1973 | 1.1431 | 1.9603 | 2.4189 | 2.4189 | 2.7246 | 2.7246 | 2019-12-16 04:00 | 1.2727 | 2.0857 | 3.4238 | 3.4238 | 3.4238 | 3.4238
2021-10-18 16:00 | 1.7833 | 2.1701 | 2.1233 | 2.2838 | 2.1634 | 2.3239 | 1.1852 | 2.0325 | 2.508 | 2.508 | 2.825 | 2.825 | 2019-12-16 05:00 | 1.3108 | 2.1482 | 3.5263 | 3.5263 | 3.5263 | 3.5263
2021-10-18 17:00 | 1.9919 | 2.424 | 2.3717 | 2.551 | 2.4165 | 2.5958 | 1.2946 | 2.2201 | 2.7394 | 2.7394 | 3.0857 | 3.0857 | 2019-12-16 06:00 | 1.3794 | 2.2606 | 3.7108 | 3.7108 | 3.7108 | 3.7108
2021-10-18 18:00 | 2.2938 | 2.7913 | 2.7311 | 2.9376 | 2.7827 | 2.9892 | 1.5375 | 2.6366 | 3.2534 | 3.2534 | 3.6647 | 3.6647 | 2019-12-16 07:00 | 1.7757 | 2.91 | 4.7769 | 4.7769 | 4.7769 | 4.7769
2021-10-18 19:00 | 2.3063 | 2.8065 | 2.746 | 2.9536 | 2.7979 | 3.0055 | 1.5204 | 2.6072 | 3.2172 | 3.2172 | 3.6238 | 3.6238 | 2019-12-16 08:00 | 2.3015 | 3.7718 | 6.1915 | 6.1915 | 6.1915 | 6.1915
2021-10-18 20:00 | 2.3006 | 2.7996 | 2.7392 | 2.9462 | 2.791 | 2.998 | 1.4775 | 2.5337 | 3.1265 | 3.1265 | 3.5216 | 3.5216 | 2019-12-16 09:00 | 2.332 | 3.8218 | 6.2735 | 6.2735 | 6.2735 | 6.2735
2021-10-18 21:00 | 2.1748 | 2.6466 | 2.5895 | 2.7852 | 2.6384 | 2.8341 | 1.3889 | 2.3818 | 2.939 | 2.939 | 3.3105 | 3.3105 | 2019-12-16 10:00 | 2.4692 | 4.0466 | 6.6425 | 6.6425 | 6.6425 | 6.6425
2021-10-18 22:00 | 1.9376 | 2.3579 | 2.307 | 2.4814 | 2.3506 | 2.525 | 1.2317 | 2.1122 | 2.6064 | 2.6064 | 2.9358 | 2.9358 | 2019-12-16 11:00 | 2.4768 | 4.0591 | 6.663 | 6.663 | 6.663 | 6.663
2021-10-18 23:00 | 1.7233 | 2.0971 | 2.0518 | 2.2069 | 2.0906 | 2.2457 | 1.0603 | 1.8182 | 2.2435 | 2.2435 | 2.5271 | 2.5271 | 2019-12-16 12:00 | 2.4997 | 4.0965 | 6.7245 | 6.7245 | 6.7245 | 6.7245
2021-10-19 | 1.6503 | 2.0083 | 1.965 | 2.1135 | 2.0021 | 2.1506 | 0.97168 | 1.6663 | 2.0561 | 2.0561 | 2.316 | 2.316 | 2019-12-16 13:00 | 2.5302 | 4.1465 | 6.8065 | 6.8065 | 6.8065 | 6.8065
2021-10-19 01:00 | 1.5004 | 1.8258 | 1.7864 | 1.9215 | 1.8202 | 1.9552 | 0.8888 | 1.5241 | 1.8807 | 1.8807 | 2.1184 | 2.1184 | 2019-12-16 14:00 | 2.7588 | 4.5212 | 7.4216 | 7.4216 | 7.4216 | 7.4216
2021-10-19 02:00 | 1.5032 | 1.8293 | 1.7898 | 1.9251 | 1.8237 | 1.9589 | 0.80592 | 1.382 | 1.7053 | 1.7053 | 1.9209 | 1.9209 | 2019-12-16 15:00 | 2.454 | 4.0216 | 6.6015 | 6.6015 | 6.6015 | 6.6015
2021-10-19 03:00 | 1.489 | 1.8119 | 1.7728 | 1.9068 | 1.8063 | 1.9403 | 0.79735 | 1.3673 | 1.6872 | 1.6872 | 1.9004 | 1.9004 | 2019-12-16 16:00 | 2.4463 | 4.0091 | 6.581 | 6.581 | 6.581 | 6.581
2021-10-19 04:00 | 1.529 | 1.8606 | 1.8205 | 1.9581 | 1.8549 | 1.9925 | 0.73441 | 1.2594 | 1.554 | 1.554 | 1.7504 | 1.7504 | 2019-12-16 17:00 | 2.3244 | 3.8093 | 6.253 | 6.253 | 6.253 | 6.253
2021-10-19 05:00 | 1.5947 | 1.9406 | 1.8987 | 2.0422 | 1.9346 | 2.0781 | 0.80546 | 1.3812 | 1.7044 | 1.7044 | 1.9198 | 1.9198 | 2019-12-16 18:00 | 2.0119 | 3.2972 | 5.4124 | 5.4124 | 5.4124 | 5.4124
2021-10-19 06:00 | 1.9898 | 2.4214 | 2.3691 | 2.5482 | 2.4139 | 2.593 | 1.0231 | 1.7545 | 2.1649 | 2.1649 | 2.4386 | 2.4386 | 2019-12-16 19:00 | 1.8748 | 3.0724 | 5.0434 | 5.0434 | 5.0434 | 5.0434
2021-10-19 07:00 | 2.2577 | 2.7474 | 2.6882 | 2.8913 | 2.739 | 2.9421 | 1.117 | 1.9154 | 2.3635 | 2.3635 | 2.6623 | 2.6623 | 2019-12-16 20:00 | 1.73 | 2.8351 | 4.6538 | 4.6538 | 4.6538 | 4.6538
2021-10-19 08:00 | 2.3406 | 2.8483 | 2.7868 | 2.9975 | 2.8395 | 3.0501 | 1.2289 | 2.1073 | 2.6003 | 2.6003 | 2.929 | 2.929 | 2019-12-16 21:00 | 1.7223 | 2.8226 | 4.6333 | 4.6333 | 4.6333 | 4.6333
2021-10-19 09:00 | 2.1777 | 2.65 | 2.5929 | 2.7889 | 2.6419 | 2.8379 | 1.2603 | 2.1613 | 2.6669 | 2.6669 | 3.0039 | 3.0039 | 2019-12-16 22:00 | 1.5242 | 2.4979 | 4.1003 | 4.1003 | 4.1003 | 4.1003
2021-10-19 10:00 | 2.1406 | 2.6048 | 2.5486 | 2.7413 | 2.5968 | 2.7895 | 1.2918 | 2.2152 | 2.7334 | 2.7334 | 3.0789 | 3.0789 | 2019-12-16 23:00 | 1.3565 | 2.2231 | 3.6493 | 3.6493 | 3.6493 | 3.6493
2021-10-19 11:00 | 2.2692 | 2.7613 | 2.7018 | 2.906 | 2.7528 | 2.957 | 1.2975 | 2.225 | 2.7455 | 2.7455 | 3.0925 | 3.0925 | 2019-12-17 | 1.2879 | 2.1107 | 3.4648 | 3.4648 | 3.4648 | 3.4648
2021-10-19 12:00 | 2.1577 | 2.6257 | 2.5691 | 2.7632 | 2.6176 | 2.8118 | 1.3632 | 2.3377 | 2.8846 | 2.8846 | 3.2491 | 3.2491 | 2019-12-17 01:00 | 1.2879 | 2.1107 | 3.4648 | 3.4648 | 3.4648 | 3.4648
2021-10-19 13:00 | 1.9805 | 2.4101 | 2.3581 | 2.5363 | 2.4026 | 2.5809 | 1.3518 | 2.3181 | 2.8604 | 2.8604 | 3.2219 | 3.2219 | 2019-12-17 02:00 | 1.227 | 2.0108 | 3.3007 | 3.3007 | 3.3007 | 3.3007
2021-10-19 14:00 | 1.629 | 1.9823 | 1.9396 | 2.0862 | 1.9762 | 2.1228 | 1.2232 | 2.0975 | 2.5882 | 2.5882 | 2.9154 | 2.9154 | 2019-12-17 03:00 | 1.2117 | 1.9858 | 3.2597 | 3.2597 | 3.2597 | 3.2597
2021-10-19 15:00 | 1.8633 | 2.2675 | 2.2186 | 2.3863 | 2.2605 | 2.4282 | 1.1717 | 2.0093 | 2.4794 | 2.4794 | 2.7928 | 2.7928 | 2019-12-17 04:00 | 1.227 | 2.0108 | 3.3007 | 3.3007 | 3.3007 | 3.3007
2021-10-19 16:00 | 2.0577 | 2.504 | 2.45 | 2.6352 | 2.4963 | 2.6814 | 1.3918 | 2.3867 | 2.945 | 2.945 | 3.3173 | 3.3173 | 2019-12-17 05:00 | 1.2956 | 2.1232 | 3.4853 | 3.4853 | 3.4853 | 3.4853
2021-10-19 17:00 | 2.192 | 2.6674 | 2.6099 | 2.8072 | 2.6592 | 2.8565 | 1.5404 | 2.6415 | 3.2595 | 3.2595 | 3.6715 | 3.6715 | 2019-12-17 06:00 | 1.4327 | 2.348 | 3.8543 | 3.8543 | 3.8543 | 3.8543
2021-10-19 18:00 | 2.5035 | 3.0465 | 2.9808 | 3.2061 | 3.0371 | 3.2624 | 1.5718 | 2.6954 | 3.326 | 3.326 | 3.7464 | 3.7464 | 2019-12-17 07:00 | 1.8214 | 2.985 | 4.8999 | 4.8999 | 4.8999 | 4.8999
2021-10-19 19:00 | 2.5264 | 3.0743 | 3.008 | 3.2354 | 3.0649 | 3.2922 | 1.6404 | 2.8131 | 3.4712 | 3.4712 | 3.9099 | 3.9099 | 2019-12-17 08:00 | 1.8824 | 3.0849 | 5.0639 | 5.0639 | 5.0639 | 5.0639
2021-10-19 20:00 | 2.4635 | 2.9978 | 2.9331 | 3.1549 | 2.9886 | 3.2103 | 1.6776 | 2.8768 | 3.5498 | 3.5498 | 3.9984 | 3.9984 | 2019-12-17 09:00 | 2.1034 | 3.4471 | 5.6584 | 5.6584 | 5.6584 | 5.6584
2021-10-19 21:00 | 2.3663 | 2.8796 | 2.8175 | 3.0304 | 2.8707 | 3.0837 | 1.569 | 2.6905 | 3.32 | 3.32 | 3.7396 | 3.7396 | 2019-12-17 10:00 | 2.1644 | 3.547 | 5.8224 | 5.8224 | 5.8224 | 5.8224
2021-10-19 22:00 | 2.1234 | 2.584 | 2.5282 | 2.7193 | 2.576 | 2.7671 | 1.3946 | 2.3916 | 2.9511 | 2.9511 | 3.3241 | 3.3241 | 2019-12-17 11:00 | 2.3015 | 3.7718 | 6.1915 | 6.1915 | 6.1915 | 6.1915
2021-10-19 23:00 | 1.9148 | 2.3301 | 2.2798 | 2.4522 | 2.3229 | 2.4952 | 1.146 | 1.9652 | 2.425 | 2.425 | 2.7315 | 2.7315 | 2019-12-17 12:00 | 2.3473 | 3.8467 | 6.3145 | 6.3145 | 6.3145 | 6.3145
2021-10-20 | 1.7465 | 2.1253 | 2.0795 | 2.2367 | 2.1188 | 2.276 | 1.0317 | 1.7692 | 2.1831 | 2.1831 | 2.459 | 2.459 | 2019-12-17 13:00 | 2.5149 | 4.1215 | 6.7655 | 6.7655 | 6.7655 | 6.7655
2021-10-20 01:00 | 1.6404 | 1.9962 | 1.9532 | 2.1008 | 1.9901 | 2.1377 | 0.87787 | 1.5054 | 1.8576 | 1.8576 | 2.0924 | 2.0924 | 2019-12-17 14:00 | 2.454 | 4.0216 | 6.6015 | 6.6015 | 6.6015 | 6.6015
2021-10-20 02:00 | 1.5433 | 1.878 | 1.8375 | 1.9764 | 1.8722 | 2.0111 | 0.85736 | 1.4702 | 1.8142 | 1.8142 | 2.0435 | 2.0435 | 2019-12-17 15:00 | 2.4159 | 3.9591 | 6.499 | 6.499 | 6.499 | 6.499
2021-10-20 03:00 | 1.5518 | 1.8884 | 1.8477 | 1.9873 | 1.8826 | 2.0223 | 0.7774 | 1.3331 | 1.645 | 1.645 | 1.8529 | 1.8529 | 2019-12-17 16:00 | 2.4997 | 4.0965 | 6.7245 | 6.7245 | 6.7245 | 6.7245
2021-10-20 04:00 | 1.549 | 1.8849 | 1.8443 | 1.9837 | 1.8791 | 2.0185 | 0.80584 | 1.3819 | 1.7052 | 1.7052 | 1.9207 | 1.9207 | 2019-12-17 17:00 | 2.393 | 3.9217 | 6.4375 | 6.4375 | 6.4375 | 6.4375
2021-10-20 05:00 | 1.7681 | 2.1516 | 2.1052 | 2.2644 | 2.145 | 2.3041 | 0.85992 | 1.4746 | 1.8196 | 1.8196 | 2.0496 | 2.0496 | 2019-12-17 18:00 | 2.1263 | 3.4845 | 5.7199 | 5.7199 | 5.7199 | 5.7199
2021-10-20 06:00 | 2.3092 | 2.81 | 2.7494 | 2.9572 | 2.8014 | 3.0092 | 0.98279 | 1.6853 | 2.0796 | 2.0796 | 2.3424 | 2.3424 | 2019-12-17 19:00 | 1.7833 | 2.9225 | 4.7974 | 4.7974 | 4.7974 | 4.7974
2021-10-20 07:00 | 2.5321 | 3.0813 | 3.0148 | 3.2427 | 3.0718 | 3.2997 | 1.2203 | 2.0926 | 2.5822 | 2.5822 | 2.9086 | 2.9086 | 2019-12-17 20:00 | 2.0119 | 3.2972 | 5.4124 | 5.4124 | 5.4124 | 5.4124
2021-10-20 08:00 | 2.7007 | 3.2865 | 3.2156 | 3.4586 | 3.2763 | 3.5194 | 1.3603 | 2.3328 | 2.8785 | 2.8785 | 3.2423 | 3.2423 | 2019-12-17 21:00 | 1.9053 | 3.1224 | 5.1254 | 5.1254 | 5.1254 | 5.1254
2021-10-20 09:00 | 2.6435 | 3.2169 | 3.1475 | 3.3854 | 3.207 | 3.4449 | 1.3746 | 2.3573 | 2.9088 | 2.9088 | 3.2764 | 3.2764 | 2019-12-17 22:00 | 1.6461 | 2.6977 | 4.4283 | 4.4283 | 4.4283 | 4.4283
2021-10-20 10:00 | 2.5835 | 3.1439 | 3.0761 | 3.3086 | 3.1342 | 3.3667 | 1.4518 | 2.4896 | 3.072 | 3.072 | 3.4603 | 3.4603 | 2019-12-17 23:00 | 1.4785 | 2.4229 | 3.9773 | 3.9773 | 3.9773 | 3.9773
2021-10-20 11:00 | 2.6521 | 3.2273 | 3.1577 | 3.3964 | 3.2174 | 3.4561 | 1.4804 | 2.5386 | 3.1325 | 3.1325 | 3.5284 | 3.5284 | 2019-12-18 | 1.2879 | 2.1107 | 3.4648 | 3.4648 | 3.4648 | 3.4648
2021-10-20 12:00 | 2.595 | 3.1578 | 3.0897 | 3.3232 | 3.1481 | 3.3816 | 1.4547 | 2.4945 | 3.0781 | 3.0781 | 3.4671 | 3.4671 | 2019-12-18 01:00 | 1.3413 | 2.1981 | 3.6083 | 3.6083 | 3.6083 | 3.6083
2021-10-20 13:00 | 2.5235 | 3.0708 | 3.0046 | 3.2317 | 3.0614 | 3.2885 | 1.5547 | 2.666 | 3.2897 | 3.2897 | 3.7055 | 3.7055 | 2019-12-18 02:00 | 1.2346 | 2.0233 | 3.3212 | 3.3212 | 3.3212 | 3.3212
2021-10-20 14:00 | 2.1863 | 2.6605 | 2.6031 | 2.7998 | 2.6523 | 2.849 | 1.3461 | 2.3083 | 2.8483 | 2.8483 | 3.2083 | 3.2083 | 2019-12-18 03:00 | 1.2956 | 2.1232 | 3.4853 | 3.4853 | 3.4853 | 3.4853
2021-10-20 15:00 | 2.1863 | 2.6605 | 2.6031 | 2.7998 | 2.6523 | 2.849 | 1.3089 | 2.2446 | 2.7697 | 2.7697 | 3.1197 | 3.1197 | 2019-12-18 04:00 | 1.3184 | 2.1607 | 3.5468 | 3.5468 | 3.5468 | 3.5468
2021-10-20 16:00 | 2.0662 | 2.5144 | 2.4602 | 2.6461 | 2.5067 | 2.6926 | 1.246 | 2.1367 | 2.6366 | 2.6366 | 2.9699 | 2.9699 | 2019-12-18 05:00 | 1.3337 | 2.1856 | 3.5878 | 3.5878 | 3.5878 | 3.5878
2021-10-20 17:00 | 2.192 | 2.6674 | 2.6099 | 2.8072 | 2.6592 | 2.8565 | 1.3403 | 2.2985 | 2.8362 | 2.8362 | 3.1947 | 3.1947 | 2019-12-18 06:00 | 1.4251 | 2.3355 | 3.8338 | 3.8338 | 3.8338 | 3.8338
2021-10-20 18:00 | 2.6207 | 3.1891 | 3.1203 | 3.3562 | 3.1793 | 3.4151 | 1.4661 | 2.5141 | 3.1023 | 3.1023 | 3.4944 | 3.4944 | 2019-12-18 07:00 | 1.6766 | 2.7477 | 4.5103 | 4.5103 | 4.5103 | 4.5103
2021-10-20 19:00 | 2.6635 | 3.2413 | 3.1713 | 3.4111 | 3.2313 | 3.471 | 1.5575 | 2.6709 | 3.2958 | 3.2958 | 3.7123 | 3.7123 | 2019-12-18 08:00 | 2.0653 | 3.3846 | 5.5559 | 5.5559 | 5.5559 | 5.5559
2021-10-20 20:00 | 2.5178 | 3.0639 | 2.9978 | 3.2244 | 3.0545 | 3.2811 | 1.6576 | 2.8425 | 3.5074 | 3.5074 | 3.9507 | 3.9507 | 2019-12-18 09:00 | 2.2025 | 3.6094 | 5.9249 | 5.9249 | 5.9249 | 5.9249
2021-10-20 21:00 | 2.3692 | 2.8831 | 2.8209 | 3.0341 | 2.8742 | 3.0874 | 1.5861 | 2.7199 | 3.3563 | 3.3563 | 3.7805 | 3.7805 | 2019-12-18 10:00 | 2.2787 | 3.7343 | 6.13 | 6.13 | 6.13 | 6.13
2021-10-20 22:00 | 2.1406 | 2.6048 | 2.5486 | 2.7413 | 2.5968 | 2.7895 | 1.3175 | 2.2593 | 2.7878 | 2.7878 | 3.1402 | 3.1402 | 2019-12-18 11:00 | 2.4616 | 4.0341 | 6.622 | 6.622 | 6.622 | 6.622
2021-10-20 23:00 | 1.8605 | 2.264 | 2.2152 | 2.3826 | 2.257 | 2.4245 | 1.086 | 1.8624 | 2.2981 | 2.2981 | 2.5885 | 2.5885 | 2019-12-18 12:00 | 2.4921 | 4.084 | 6.704 | 6.704 | 6.704 | 6.704
2021-10-21 | 1.6779 | 2.0418 | 1.9978 | 2.1488 | 2.0355 | 2.1865 | 1.0117 | 1.7349 | 2.1407 | 2.1407 | 2.4113 | 2.4113 | 2019-12-18 13:00 | 2.5226 | 4.134 | 6.786 | 6.786 | 6.786 | 6.786
2021-10-21 01:00 | 1.5718 | 1.9128 | 1.8715 | 2.013 | 1.9069 | 2.0483 | 0.881 | 1.5108 | 1.8642 | 1.8642 | 2.0998 | 2.0998 | 2019-12-18 14:00 | 2.5759 | 4.2214 | 6.9295 | 6.9295 | 6.9295 | 6.9295
2021-10-21 02:00 | 1.5204 | 1.8502 | 1.8102 | 1.9471 | 1.8445 | 1.9813 | 0.7802 | 1.3379 | 1.6509 | 1.6509 | 1.8596 | 1.8596 | 2019-12-18 15:00 | 2.5607 | 4.1964 | 6.8885 | 6.8885 | 6.8885 | 6.8885
2021-10-21 03:00 | 1.5375 | 1.871 | 1.8307 | 1.969 | 1.8653 | 2.0036 | 0.76277 | 1.308 | 1.614 | 1.614 | 1.818 | 1.818 | 2019-12-18 16:00 | 2.5454 | 4.1715 | 6.8475 | 6.8475 | 6.8475 | 6.8475
2021-10-21 04:00 | 1.5433 | 1.878 | 1.8375 | 1.9764 | 1.8722 | 2.0111 | 0.76305 | 1.3085 | 1.6146 | 1.6146 | 1.8187 | 1.8187 | 2019-12-18 17:00 | 2.4845 | 4.0716 | 6.6835 | 6.6835 | 6.6835 | 6.6835
2021-10-21 05:00 | 1.669 | 2.031 | 1.9872 | 2.1374 | 2.0247 | 2.175 | 0.8202 | 1.4065 | 1.7356 | 1.7356 | 1.9549 | 1.9549 | 2019-12-18 18:00 | 2.2253 | 3.6469 | 5.9865 | 5.9865 | 5.9865 | 5.9865
2021-10-21 06:00 | 2.0691 | 2.5179 | 2.4636 | 2.6498 | 2.5101 | 2.6963 | 0.94193 | 1.6153 | 1.9931 | 1.9931 | 2.245 | 2.245 | 2019-12-18 19:00 | 2.1567 | 3.5345 | 5.8019 | 5.8019 | 5.8019 | 5.8019
2021-10-21 07:00 | 2.4263 | 2.9526 | 2.8889 | 3.1073 | 2.9435 | 3.1619 | 1.1454 | 1.9641 | 2.4236 | 2.4236 | 2.73 | 2.73 | 2019-12-18 20:00 | 2.1415 | 3.5095 | 5.7609 | 5.7609 | 5.7609 | 5.7609
2021-10-21 08:00 | 2.4806 | 3.0187 | 2.9536 | 3.1768 | 3.0094 | 3.2326 | 1.2432 | 2.1318 | 2.6306 | 2.6306 | 2.9631 | 2.9631 | 2019-12-18 21:00 | 2.0882 | 3.4221 | 5.6174 | 5.6174 | 5.6174 | 5.6174
2021-10-21 09:00 | 2.4578 | 2.9909 | 2.9263 | 3.1475 | 2.9816 | 3.2028 | 1.3375 | 2.2936 | 2.8301 | 2.8301 | 3.1878 | 3.1878 | 2019-12-18 22:00 | 1.8748 | 3.0724 | 5.0434 | 5.0434 | 5.0434 | 5.0434
2021-10-21 10:00 | 2.4006 | 2.9213 | 2.8583 | 3.0743 | 2.9123 | 3.1284 | 1.3432 | 2.3034 | 2.8422 | 2.8422 | 3.2015 | 3.2015 | 2019-12-18 23:00 | 1.6233 | 2.6602 | 4.3668 | 4.3668 | 4.3668 | 4.3668
2021-10-21 11:00 | 2.5121 | 3.0569 | 2.991 | 3.2171 | 3.0475 | 3.2736 | 1.3461 | 2.3083 | 2.8483 | 2.8483 | 3.2083 | 3.2083 | 2019-12-19 | 1.5547 | 2.5478 | 4.1823 | 4.1823 | 4.1823 | 4.1823
2021-10-21 12:00 | 2.3749 | 2.89 | 2.8277 | 3.0414 | 2.8811 | 3.0948 | 1.3089 | 2.2446 | 2.7697 | 2.7697 | 3.1197 | 3.1197 | 2019-12-19 01:00 | 1.4023 | 2.2981 | 3.7723 | 3.7723 | 3.7723 | 3.7723
2021-10-21 13:00 | 2.3177 | 2.8205 | 2.7596 | 2.9682 | 2.8118 | 3.0204 | 1.3432 | 2.3034 | 2.8422 | 2.8422 | 3.2015 | 3.2015 | 2019-12-19 02:00 | 1.4023 | 2.2981 | 3.7723 | 3.7723 | 3.7723 | 3.7723
2021-10-21 14:00 | 2.2949 | 2.7926 | 2.7324 | 2.9389 | 2.784 | 2.9906 | 1.2775 | 2.1907 | 2.7031 | 2.7031 | 3.0448 | 3.0448 | 2019-12-19 03:00 | 1.3642 | 2.2356 | 3.6698 | 3.6698 | 3.6698 | 3.6698
2021-10-21 15:00 | 2.0777 | 2.5283 | 2.4738 | 2.6608 | 2.5205 | 2.7075 | 1.2317 | 2.1122 | 2.6064 | 2.6064 | 2.9358 | 2.9358 | 2019-12-19 04:00 | 1.3642 | 2.2356 | 3.6698 | 3.6698 | 3.6698 | 3.6698
2021-10-21 16:00 | 1.9576 | 2.3823 | 2.3309 | 2.5071 | 2.3749 | 2.5511 | 1.2689 | 2.176 | 2.685 | 2.685 | 3.0244 | 3.0244 | 2019-12-19 05:00 | 1.4404 | 2.3605 | 3.8748 | 3.8748 | 3.8748 | 3.8748
2021-10-21 17:00 | 2.1291 | 2.5909 | 2.535 | 2.7266 | 2.5829 | 2.7746 | 1.3689 | 2.3475 | 2.8967 | 2.8967 | 3.2628 | 3.2628 | 2019-12-19 06:00 | 1.5775 | 2.5853 | 4.2438 | 4.2438 | 4.2438 | 4.2438
2021-10-21 18:00 | 2.4121 | 2.9352 | 2.8719 | 3.089 | 2.9262 | 3.1433 | 1.4347 | 2.4602 | 3.0357 | 3.0357 | 3.4194 | 3.4194 | 2019-12-19 07:00 | 2.0119 | 3.2972 | 5.4124 | 5.4124 | 5.4124 | 5.4124
2021-10-21 19:00 | 2.4406 | 2.97 | 2.9059 | 3.1256 | 2.9608 | 3.1805 | 1.5747 | 2.7003 | 3.3321 | 3.3321 | 3.7532 | 3.7532 | 2019-12-19 08:00 | 2.393 | 3.9217 | 6.4375 | 6.4375 | 6.4375 | 6.4375
2021-10-21 20:00 | 2.316 | 2.8183 | 2.7575 | 2.9659 | 2.8096 | 3.018 | 1.529 | 2.6219 | 3.2353 | 3.2353 | 3.6442 | 3.6442 | 2019-12-19 09:00 | 2.4082 | 3.9467 | 6.4785 | 6.4785 | 6.4785 | 6.4785
2021-10-21 21:00 | 2.2226 | 2.7047 | 2.6464 | 2.8464 | 2.6964 | 2.8964 | 1.5004 | 2.5729 | 3.1748 | 3.1748 | 3.5761 | 3.5761 | 2019-12-19 10:00 | 2.6445 | 4.3338 | 7.114 | 7.114 | 7.114 | 7.114
2021-10-21 22:00 | 2.0177 | 2.4553 | 2.4023 | 2.5839 | 2.4477 | 2.6293 | 1.2263 | 2.1029 | 2.5949 | 2.5949 | 2.9229 | 2.9229 | 2019-12-19 11:00 | 2.6445 | 4.3338 | 7.114 | 7.114 | 7.114 | 7.114
2021-10-21 23:00 | 1.809 | 2.2014 | 2.1539 | 2.3167 | 2.1946 | 2.3574 | 1.0174 | 1.7447 | 2.1528 | 2.1528 | 2.4249 | 2.4249 | 2019-12-19 12:00 | 2.553 | 4.184 | 6.868 | 6.868 | 6.868 | 6.868
2021-10-22 | 1.6519 | 2.0101 | 1.9668 | 2.1154 | 2.0039 | 2.1526 | 0.96882 | 1.6614 | 2.05 | 2.05 | 2.3091 | 2.3091 | 2019-12-19 13:00 | 2.4997 | 4.0965 | 6.7245 | 6.7245 | 6.7245 | 6.7245
2021-10-22 01:00 | 1.5148 | 1.8434 | 1.8036 | 1.9399 | 1.8377 | 1.974 | 0.86022 | 1.4751 | 1.8202 | 1.8202 | 2.0503 | 2.0503 | 2019-12-19 14:00 | 2.6445 | 4.3338 | 7.114 | 7.114 | 7.114 | 7.114
2021-10-22 02:00 | 1.4289 | 1.7389 | 1.7014 | 1.83 | 1.7335 | 1.8621 | 0.78591 | 1.3477 | 1.663 | 1.663 | 1.8732 | 1.8732 | 2019-12-19 15:00 | 2.675 | 4.3838 | 7.196 | 7.196 | 7.196 | 7.196
2021-10-22 03:00 | 1.4437 | 1.7569 | 1.719 | 1.8489 | 1.7515 | 1.8814 | 0.77448 | 1.3281 | 1.6388 | 1.6388 | 1.8459 | 1.8459 | 2019-12-19 16:00 | 2.7436 | 4.4962 | 7.3806 | 7.3806 | 7.3806 | 7.3806
2021-10-22 04:00 | 1.4461 | 1.7597 | 1.7218 | 1.8519 | 1.7543 | 1.8845 | 0.73161 | 1.2546 | 1.5481 | 1.5481 | 1.7438 | 1.7438 | 2019-12-19 17:00 | 2.5911 | 4.2464 | 6.9705 | 6.9705 | 6.9705 | 6.9705
2021-10-22 05:00 | 1.6004 | 1.9475 | 1.9055 | 2.0496 | 1.9415 | 2.0856 | 0.7802 | 1.3379 | 1.6509 | 1.6509 | 1.8596 | 1.8596 | 2019-12-19 18:00 | 2.3778 | 3.8967 | 6.3965 | 6.3965 | 6.3965 | 6.3965
2021-10-22 06:00 | 1.8776 | 2.2849 | 2.2356 | 2.4046 | 2.2778 | 2.4468 | 0.88022 | 1.5094 | 1.8626 | 1.8626 | 2.098 | 2.098 | 2019-12-19 19:00 | 2.1034 | 3.4471 | 5.6584 | 5.6584 | 5.6584 | 5.6584
2021-10-22 07:00 | 2.2267 | 2.7096 | 2.6512 | 2.8516 | 2.7013 | 2.9017 | 1.1003 | 1.8868 | 2.3282 | 2.3282 | 2.6225 | 2.6225 | 2019-12-19 20:00 | 1.9434 | 3.1848 | 5.2279 | 5.2279 | 5.2279 | 5.2279
2021-10-22 08:00 | 2.4092 | 2.9317 | 2.8685 | 3.0853 | 2.9227 | 3.1395 | 1.246 | 2.1367 | 2.6366 | 2.6366 | 2.9699 | 2.9699 | 2019-12-19 21:00 | 1.9434 | 3.1848 | 5.2279 | 5.2279 | 5.2279 | 5.2279
2021-10-22 09:00 | 2.1406 | 2.6048 | 2.5486 | 2.7413 | 2.5968 | 2.7895 | 1.186 | 2.0338 | 2.5096 | 2.5096 | 2.8268 | 2.8268 | 2019-12-19 22:00 | 1.6614 | 2.7227 | 4.4693 | 4.4693 | 4.4693 | 4.4693
2021-10-22 10:00 | 1.9977 | 2.4309 | 2.3785 | 2.5583 | 2.4235 | 2.6032 | 1.1746 | 2.0142 | 2.4854 | 2.4854 | 2.7996 | 2.7996 | 2019-12-19 23:00 | 1.4785 | 2.4229 | 3.9773 | 3.9773 | 3.9773 | 3.9773
2021-10-22 11:00 | 1.9805 | 2.4101 | 2.3581 | 2.5363 | 2.4026 | 2.5809 | 1.2003 | 2.0583 | 2.5399 | 2.5399 | 2.8609 | 2.8609 | 2019-12-20 | 1.3642 | 2.2356 | 3.6698 | 3.6698 | 3.6698 | 3.6698
2021-10-22 12:00 | 2.1034 | 2.5596 | 2.5044 | 2.6937 | 2.5517 | 2.741 | 1.2175 | 2.0877 | 2.5761 | 2.5761 | 2.9018 | 2.9018 | 2019-12-20 01:00 | 1.3108 | 2.1482 | 3.5263 | 3.5263 | 3.5263 | 3.5263
2021-10-22 13:00 | 1.9434 | 2.3649 | 2.3139 | 2.4888 | 2.3576 | 2.5325 | 1.2003 | 2.0583 | 2.5399 | 2.5399 | 2.8609 | 2.8609 | 2019-12-20 02:00 | 1.2651 | 2.0732 | 3.4033 | 3.4033 | 3.4033 | 3.4033
2021-10-22 14:00 | 1.829 | 2.2258 | 2.1777 | 2.3424 | 2.2189 | 2.3835 | 1.1774 | 2.0191 | 2.4915 | 2.4915 | 2.8064 | 2.8064 | 2019-12-20 03:00 | 1.2575 | 2.0608 | 3.3828 | 3.3828 | 3.3828 | 3.3828
2021-10-22 15:00 | 1.7862 | 2.1736 | 2.1267 | 2.2875 | 2.1669 | 2.3276 | 1.166 | 1.9995 | 2.4673 | 2.4673 | 2.7791 | 2.7791 | 2019-12-20 04:00 | 1.2575 | 2.0608 | 3.3828 | 3.3828 | 3.3828 | 3.3828
2021-10-22 16:00 | 1.8262 | 2.2223 | 2.1743 | 2.3387 | 2.2154 | 2.3798 | 1.3029 | 2.2342 | 2.7569 | 2.7569 | 3.1053 | 3.1053 | 2019-12-20 05:00 | 1.2575 | 2.0608 | 3.3828 | 3.3828 | 3.3828 | 3.3828
2021-10-22 17:00 | 1.9805 | 2.4101 | 2.3581 | 2.5363 | 2.4026 | 2.5809 | 1.3432 | 2.3034 | 2.8422 | 2.8422 | 3.2015 | 3.2015 | 2019-12-20 06:00 | 1.3565 | 2.2231 | 3.6493 | 3.6493 | 3.6493 | 3.6493
2021-10-22 18:00 | 2.1548 | 2.6222 | 2.5657 | 2.7596 | 2.6141 | 2.8081 | 1.379 | 2.3647 | 2.9179 | 2.9179 | 3.2867 | 3.2867 | 2019-12-20 07:00 | 1.7681 | 2.8975 | 4.7564 | 4.7564 | 4.7564 | 4.7564
2021-10-22 19:00 | 2.1005 | 2.5561 | 2.501 | 2.69 | 2.5483 | 2.7373 | 1.4286 | 2.4498 | 3.0229 | 3.0229 | 3.405 | 3.405 | 2019-12-20 08:00 | 2.1339 | 3.497 | 5.7404 | 5.7404 | 5.7404 | 5.7404
2021-10-22 20:00 | 2.0805 | 2.5318 | 2.4772 | 2.6644 | 2.524 | 2.7112 | 1.4461 | 2.4798 | 3.0599 | 3.0599 | 3.4467 | 3.4467 | 2019-12-20 09:00 | 2.1949 | 3.597 | 5.9044 | 5.9044 | 5.9044 | 5.9044
2021-10-22 21:00 | 2.0034 | 2.4379 | 2.3853 | 2.5656 | 2.4304 | 2.6107 | 1.3861 | 2.3769 | 2.9329 | 2.9329 | 3.3036 | 3.3036 | 2019-12-20 10:00 | 2.1567 | 3.5345 | 5.8019 | 5.8019 | 5.8019 | 5.8019
2021-10-22 22:00 | 1.8208 | 2.2157 | 2.1679 | 2.3318 | 2.2089 | 2.3727 | 1.2317 | 2.1122 | 2.6064 | 2.6064 | 2.9358 | 2.9358 | 2019-12-20 11:00 | 2.3701 | 3.8842 | 6.376 | 6.376 | 6.376 | 6.376
2021-10-22 23:00 | 1.6577 | 2.0172 | 1.9737 | 2.1229 | 2.011 | 2.1602 | 0.9974 | 1.7104 | 2.1105 | 2.1105 | 2.3773 | 2.3773 | 2019-12-20 12:00 | 2.5378 | 4.159 | 6.827 | 6.827 | 6.827 | 6.827
2021-10-23 | 1.5775 | 1.9197 | 1.8783 | 2.0203 | 1.9138 | 2.0558 | 0.9431 | 1.6173 | 1.9956 | 1.9956 | 2.2478 | 2.2478 | 2019-12-20 13:00 | 2.5378 | 4.159 | 6.827 | 6.827 | 6.827 | 6.827
2021-10-23 01:00 | 1.4404 | 1.7528 | 1.715 | 1.8446 | 1.7474 | 1.877 | 0.8546 | 1.4655 | 1.8083 | 1.8083 | 2.0369 | 2.0369 | 2019-12-20 14:00 | 2.6597 | 4.3588 | 7.155 | 7.155 | 7.155 | 7.155
2021-10-23 02:00 | 1.3461 | 1.638 | 1.6027 | 1.7238 | 1.633 | 1.7541 | 0.75162 | 1.2889 | 1.5904 | 1.5904 | 1.7915 | 1.7915 | 2019-12-20 15:00 | 2.6445 | 4.3338 | 7.114 | 7.114 | 7.114 | 7.114
2021-10-23 03:00 | 1.3346 | 1.6241 | 1.5891 | 1.7092 | 1.6191 | 1.7392 | 0.72304 | 1.2399 | 1.53 | 1.53 | 1.7233 | 1.7233 | 2019-12-20 16:00 | 2.614 | 4.2839 | 7.032 | 7.032 | 7.032 | 7.032
2021-10-23 04:00 | 1.3539 | 1.6475 | 1.612 | 1.7338 | 1.6425 | 1.7643 | 0.72018 | 1.235 | 1.5239 | 1.5239 | 1.7165 | 1.7165 | 2019-12-20 17:00 | 2.5073 | 4.109 | 6.745 | 6.745 | 6.745 | 6.745
2021-10-23 05:00 | 1.4289 | 1.7389 | 1.7014 | 1.83 | 1.7335 | 1.8621 | 0.71447 | 1.2252 | 1.5118 | 1.5118 | 1.7029 | 1.7029 | 2019-12-20 18:00 | 2.2482 | 3.6844 | 6.048 | 6.048 | 6.048 | 6.048
2021-10-23 06:00 | 1.5547 | 1.8919 | 1.8511 | 1.991 | 1.8861 | 2.026 | 0.75448 | 1.2938 | 1.5965 | 1.5965 | 1.7983 | 1.7983 | 2019-12-20 19:00 | 2.0729 | 3.3971 | 5.5764 | 5.5764 | 5.5764 | 5.5764
2021-10-23 07:00 | 1.7147 | 2.0866 | 2.0416 | 2.196 | 2.0802 | 2.2345 | 0.92023 | 1.5781 | 1.9472 | 1.9472 | 2.1933 | 2.1933 | 2019-12-20 20:00 | 2.0272 | 3.3222 | 5.4534 | 5.4534 | 5.4534 | 5.4534
2021-10-23 08:00 | 1.7347 | 2.111 | 2.0655 | 2.2216 | 2.1045 | 2.2606 | 0.99972 | 1.7144 | 2.1154 | 2.1154 | 2.3828 | 2.3828 | 2019-12-20 21:00 | 1.8671 | 3.0599 | 5.0229 | 5.0229 | 5.0229 | 5.0229
2021-10-23 09:00 | 1.6804 | 2.0449 | 2.0008 | 2.152 | 2.0386 | 2.1898 | 1.1346 | 1.9456 | 2.4008 | 2.4008 | 2.7042 | 2.7042 | 2019-12-20 22:00 | 1.7071 | 2.7976 | 4.5923 | 4.5923 | 4.5923 | 4.5923
2021-10-23 10:00 | 1.7147 | 2.0866 | 2.0416 | 2.196 | 2.0802 | 2.2345 | 1.3146 | 2.2544 | 2.7818 | 2.7818 | 3.1333 | 3.1333 | 2019-12-20 23:00 | 1.6309 | 2.6727 | 4.3873 | 4.3873 | 4.3873 | 4.3873
2021-10-23 11:00 | 1.6861 | 2.0519 | 2.0076 | 2.1594 | 2.0455 | 2.1973 | 1.3375 | 2.2936 | 2.8301 | 2.8301 | 3.1878 | 3.1878 | 2019-12-21 | 1.4556 | 2.3855 | 3.9158 | 3.9158 | 3.9158 | 3.9158
2021-10-23 12:00 | 1.7147 | 2.0866 | 2.0416 | 2.196 | 2.0802 | 2.2345 | 1.3946 | 2.3915 | 2.9509 | 2.9509 | 3.3239 | 3.3239 | 2019-12-21 01:00 | 1.448 | 2.373 | 3.8953 | 3.8953 | 3.8953 | 3.8953
2021-10-23 13:00 | 1.6804 | 2.0449 | 2.0008 | 2.152 | 2.0386 | 2.1898 | 1.3946 | 2.3916 | 2.9511 | 2.9511 | 3.3241 | 3.3241 | 2019-12-21 02:00 | 1.3718 | 2.2481 | 3.6903 | 3.6903 | 3.6903 | 3.6903
2021-10-23 14:00 | 1.6804 | 2.0449 | 2.0008 | 2.152 | 2.0386 | 2.1898 | 1.3089 | 2.2446 | 2.7697 | 2.7697 | 3.1197 | 3.1197 | 2019-12-21 03:00 | 1.3413 | 2.1981 | 3.6083 | 3.6083 | 3.6083 | 3.6083
2021-10-23 15:00 | 1.6033 | 1.951 | 1.9089 | 2.0532 | 1.945 | 2.0893 | 1.306 | 2.2397 | 2.7636 | 2.7636 | 3.1129 | 3.1129 | 2019-12-21 04:00 | 1.4099 | 2.3105 | 3.7928 | 3.7928 | 3.7928 | 3.7928
2021-10-23 16:00 | 1.6633 | 2.024 | 1.9804 | 2.1301 | 2.0178 | 2.1675 | 1.3003 | 2.2299 | 2.7515 | 2.7515 | 3.0993 | 3.0993 | 2019-12-21 05:00 | 1.387 | 2.2731 | 3.7313 | 3.7313 | 3.7313 | 3.7313
2021-10-23 17:00 | 1.689 | 2.0553 | 2.011 | 2.163 | 2.049 | 2.201 | 1.2689 | 2.176 | 2.685 | 2.685 | 3.0244 | 3.0244 | 2019-12-21 06:00 | 1.5013 | 2.4604 | 4.0388 | 4.0388 | 4.0388 | 4.0388
2021-10-23 18:00 | 1.8805 | 2.2884 | 2.239 | 2.4082 | 2.2813 | 2.4505 | 1.3032 | 2.2348 | 2.7576 | 2.7576 | 3.1061 | 3.1061 | 2019-12-21 07:00 | 1.8214 | 2.985 | 4.8999 | 4.8999 | 4.8999 | 4.8999
2021-10-23 19:00 | 1.9262 | 2.344 | 2.2934 | 2.4668 | 2.3368 | 2.5101 | 1.3432 | 2.3034 | 2.8422 | 2.8422 | 3.2015 | 3.2015 | 2019-12-21 08:00 | 1.8367 | 3.0099 | 4.9409 | 4.9409 | 4.9409 | 4.9409
2021-10-23 20:00 | 1.9033 | 2.3162 | 2.2662 | 2.4375 | 2.309 | 2.4803 | 1.3518 | 2.3181 | 2.8604 | 2.8604 | 3.2219 | 3.2219 | 2019-12-21 09:00 | 2.1263 | 3.4845 | 5.7199 | 5.7199 | 5.7199 | 5.7199
2021-10-23 21:00 | 1.7776 | 2.1632 | 2.1165 | 2.2765 | 2.1565 | 2.3165 | 1.3318 | 2.2838 | 2.818 | 2.818 | 3.1742 | 3.1742 | 2019-12-21 10:00 | 2.1415 | 3.5095 | 5.7609 | 5.7609 | 5.7609 | 5.7609
2021-10-23 22:00 | 1.7262 | 2.1006 | 2.0552 | 2.2106 | 2.0941 | 2.2494 | 1.2032 | 2.0632 | 2.5459 | 2.5459 | 2.8677 | 2.8677 | 2019-12-21 11:00 | 2.2025 | 3.6094 | 5.9249 | 5.9249 | 5.9249 | 5.9249
2021-10-23 23:00 | 1.6147 | 1.9649 | 1.9225 | 2.0679 | 1.9589 | 2.1042 | 0.98597 | 1.6908 | 2.0863 | 2.0863 | 2.35 | 2.35 | 2019-12-21 12:00 | 2.4082 | 3.9467 | 6.4785 | 6.4785 | 6.4785 | 6.4785
2021-10-24 | 1.5263 | 1.8574 | 1.8173 | 1.9547 | 1.8517 | 1.989 | 0.96596 | 1.6565 | 2.044 | 2.044 | 2.3023 | 2.3023 | 2019-12-21 13:00 | 2.4921 | 4.084 | 6.704 | 6.704 | 6.704 | 6.704
2021-10-24 01:00 | 1.4175 | 1.725 | 1.6878 | 1.8153 | 1.7196 | 1.8472 | 0.82322 | 1.4117 | 1.7419 | 1.7419 | 1.9621 | 1.9621 | 2019-12-21 14:00 | 2.5226 | 4.134 | 6.786 | 6.786 | 6.786 | 6.786
2021-10-24 02:00 | 1.3632 | 1.6589 | 1.6231 | 1.7458 | 1.6538 | 1.7765 | 0.75448 | 1.2938 | 1.5965 | 1.5965 | 1.7983 | 1.7983 | 2019-12-21 15:00 | 2.4845 | 4.0716 | 6.6835 | 6.6835 | 6.6835 | 6.6835
2021-10-24 03:00 | 1.3775 | 1.6763 | 1.6401 | 1.7641 | 1.6711 | 1.7951 | 0.76305 | 1.3085 | 1.6146 | 1.6146 | 1.8187 | 1.8187 | 2019-12-21 16:00 | 2.454 | 4.0216 | 6.6015 | 6.6015 | 6.6015 | 6.6015
2021-10-24 04:00 | 1.3572 | 1.6516 | 1.616 | 1.7381 | 1.6465 | 1.7687 | 0.75803 | 1.2999 | 1.604 | 1.604 | 1.8067 | 1.8067 | 2019-12-21 17:00 | 2.3244 | 3.8093 | 6.253 | 6.253 | 6.253 | 6.253
2021-10-24 05:00 | 1.3661 | 1.6624 | 1.6265 | 1.7494 | 1.6572 | 1.7802 | 0.73733 | 1.2644 | 1.5602 | 1.5602 | 1.7574 | 1.7574 | 2019-12-21 18:00 | 2.0501 | 3.3597 | 5.5149 | 5.5149 | 5.5149 | 5.5149
2021-10-24 06:00 | 1.5004 | 1.8258 | 1.7864 | 1.9215 | 1.8202 | 1.9552 | 0.75448 | 1.2938 | 1.5965 | 1.5965 | 1.7983 | 1.7983 | 2019-12-21 19:00 | 1.9662 | 3.2223 | 5.2894 | 5.2894 | 5.2894 | 5.2894
2021-10-24 07:00 | 1.6204 | 1.9719 | 1.9293 | 2.0752 | 1.9658 | 2.1116 | 0.82592 | 1.4163 | 1.7477 | 1.7477 | 1.9686 | 1.9686 | 2019-12-21 20:00 | 1.9662 | 3.2223 | 5.2894 | 5.2894 | 5.2894 | 5.2894
2021-10-24 08:00 | 1.6147 | 1.9649 | 1.9225 | 2.0679 | 1.9589 | 2.1042 | 0.93058 | 1.5958 | 1.9691 | 1.9691 | 2.218 | 2.218 | 2019-12-21 21:00 | 1.8214 | 2.985 | 4.8999 | 4.8999 | 4.8999 | 4.8999
2021-10-24 09:00 | 1.6318 | 1.9858 | 1.943 | 2.0898 | 1.9797 | 2.1265 | 1.1174 | 1.9162 | 2.3645 | 2.3645 | 2.6633 | 2.6633 | 2019-12-21 22:00 | 1.6385 | 2.6852 | 4.4078 | 4.4078 | 4.4078 | 4.4078
2021-10-24 10:00 | 1.5804 | 1.9232 | 1.8817 | 2.0239 | 1.9173 | 2.0595 | 1.2146 | 2.0828 | 2.5701 | 2.5701 | 2.8949 | 2.8949 | 2019-12-21 23:00 | 1.5394 | 2.5229 | 4.1413 | 4.1413 | 4.1413 | 4.1413
2021-10-24 11:00 | 1.5061 | 1.8328 | 1.7932 | 1.9288 | 1.8271 | 1.9627 | 1.3003 | 2.2299 | 2.7515 | 2.7515 | 3.0993 | 3.0993 | 2019-12-22 | 1.3794 | 2.2606 | 3.7108 | 3.7108 | 3.7108 | 3.7108
2021-10-24 12:00 | 1.7404 | 2.1179 | 2.0723 | 2.2289 | 2.1114 | 2.2681 | 1.2925 | 2.2164 | 2.7349 | 2.7349 | 3.0805 | 3.0805 | 2019-12-22 01:00 | 1.3565 | 2.2231 | 3.6493 | 3.6493 | 3.6493 | 3.6493
2021-10-24 13:00 | 1.7776 | 2.1632 | 2.1165 | 2.2765 | 2.1565 | 2.3165 | 1.3003 | 2.2299 | 2.7515 | 2.7515 | 3.0993 | 3.0993 | 2019-12-22 02:00 | 1.3413 | 2.1981 | 3.6083 | 3.6083 | 3.6083 | 3.6083
2021-10-24 14:00 | 1.6176 | 1.9684 | 1.9259 | 2.0715 | 1.9623 | 2.1079 | 1.2232 | 2.0975 | 2.5882 | 2.5882 | 2.9154 | 2.9154 | 2019-12-22 03:00 | 1.2956 | 2.1232 | 3.4853 | 3.4853 | 3.4853 | 3.4853
2021-10-24 15:00 | 1.5547 | 1.8919 | 1.8511 | 1.991 | 1.8861 | 2.026 | 1.206 | 2.0681 | 2.552 | 2.552 | 2.8745 | 2.8745 | 2019-12-22 04:00 | 1.2803 | 2.0982 | 3.4443 | 3.4443 | 3.4443 | 3.4443
2021-10-24 16:00 | 1.5261 | 1.8571 | 1.8171 | 1.9544 | 1.8514 | 1.9887 | 1.1632 | 1.9946 | 2.4612 | 2.4612 | 2.7723 | 2.7723 | 2019-12-22 05:00 | 1.3718 | 2.2481 | 3.6903 | 3.6903 | 3.6903 | 3.6903
2021-10-24 17:00 | 1.7519 | 2.1319 | 2.0859 | 2.2435 | 2.1253 | 2.283 | 1.2375 | 2.122 | 2.6185 | 2.6185 | 2.9494 | 2.9494 | 2019-12-22 06:00 | 1.4709 | 2.4105 | 3.9568 | 3.9568 | 3.9568 | 3.9568
2021-10-24 18:00 | 1.9548 | 2.3788 | 2.3275 | 2.5034 | 2.3714 | 2.5474 | 1.3861 | 2.3769 | 2.9329 | 2.9329 | 3.3036 | 3.3036 | 2019-12-22 07:00 | 1.6004 | 2.6228 | 4.3053 | 4.3053 | 4.3053 | 4.3053
2021-10-24 19:00 | 2.0863 | 2.5388 | 2.484 | 2.6718 | 2.5309 | 2.7187 | 1.4175 | 2.4308 | 2.9995 | 2.9995 | 3.3786 | 3.3786 | 2019-12-22 08:00 | 1.8214 | 2.985 | 4.8999 | 4.8999 | 4.8999 | 4.8999
2021-10-24 20:00 | 2.0891 | 2.5422 | 2.4874 | 2.6754 | 2.5344 | 2.7224 | 1.4404 | 2.47 | 3.0478 | 3.0478 | 3.4331 | 3.4331 | 2019-12-22 09:00 | 1.8519 | 3.0349 | 4.9819 | 4.9819 | 4.9819 | 4.9819
2021-10-24 21:00 | 1.9119 | 2.3266 | 2.2764 | 2.4485 | 2.3194 | 2.4915 | 1.3546 | 2.323 | 2.8664 | 2.8664 | 3.2287 | 3.2287 | 2019-12-22 10:00 | 1.8748 | 3.0724 | 5.0434 | 5.0434 | 5.0434 | 5.0434
2021-10-24 22:00 | 1.7947 | 2.184 | 2.1369 | 2.2984 | 2.1773 | 2.3388 | 1.1403 | 1.9554 | 2.4129 | 2.4129 | 2.7178 | 2.7178 | 2019-12-22 11:00 | 1.9738 | 3.2348 | 5.3099 | 5.3099 | 5.3099 | 5.3099
2021-10-24 23:00 | 1.609 | 1.958 | 1.9157 | 2.0605 | 1.9519 | 2.0967 | 1.046 | 1.7937 | 2.2133 | 2.2133 | 2.4931 | 2.4931 | 2019-12-22 12:00 | 1.9891 | 3.2597 | 5.3509 | 5.3509 | 5.3509 | 5.3509
2021-10-25 | 1.5861 | 1.9301 | 1.8885 | 2.0313 | 1.9242 | 2.0669 | 0.88022 | 1.5094 | 1.8626 | 1.8626 | 2.098 | 2.098 | 2019-12-22 13:00 | 1.9738 | 3.2348 | 5.3099 | 5.3099 | 5.3099 | 5.3099
2021-10-25 01:00 | 1.4261 | 1.7354 | 1.698 | 1.8263 | 1.73 | 1.8584 | 0.74135 | 1.2713 | 1.5687 | 1.5687 | 1.767 | 1.767 | 2019-12-22 14:00 | 1.9129 | 3.1348 | 5.1459 | 5.1459 | 5.1459 | 5.1459
2021-10-25 02:00 | 1.4032 | 1.7076 | 1.6707 | 1.797 | 1.7023 | 1.8286 | 0.72024 | 1.2351 | 1.524 | 1.524 | 1.7167 | 1.7167 | 2019-12-22 15:00 | 2.0348 | 3.3347 | 5.4739 | 5.4739 | 5.4739 | 5.4739
2021-10-25 03:00 | 1.3632 | 1.6589 | 1.6231 | 1.7458 | 1.6538 | 1.7765 | 0.70018 | 1.2007 | 1.4816 | 1.4816 | 1.6688 | 1.6688 | 2019-12-22 16:00 | 1.9815 | 3.2472 | 5.3304 | 5.3304 | 5.3304 | 5.3304
2021-10-25 04:00 | 1.3975 | 1.7006 | 1.6639 | 1.7897 | 1.6954 | 1.8211 | 0.70304 | 1.2056 | 1.4876 | 1.4876 | 1.6757 | 1.6757 | 2019-12-22 17:00 | 1.89 | 3.0974 | 5.0844 | 5.0844 | 5.0844 | 5.0844
2021-10-25 05:00 | 1.5347 | 1.8675 | 1.8273 | 1.9654 | 1.8618 | 1.9999 | 0.76019 | 1.3036 | 1.6086 | 1.6086 | 1.8119 | 1.8119 | 2019-12-22 18:00 | 1.6995 | 2.7851 | 4.5718 | 4.5718 | 4.5718 | 4.5718
2021-10-25 06:00 | 2.0577 | 2.504 | 2.45 | 2.6352 | 2.4963 | 2.6814 | 0.87451 | 1.4996 | 1.8505 | 1.8505 | 2.0844 | 2.0844 | 2019-12-22 19:00 | 1.6157 | 2.6478 | 4.3463 | 4.3463 | 4.3463 | 4.3463
2021-10-25 07:00 | 2.3206 | 2.8239 | 2.763 | 2.9719 | 2.8152 | 3.0241 | 1.0288 | 1.7643 | 2.177 | 2.177 | 2.4522 | 2.4522 | 2019-12-22 20:00 | 1.5928 | 2.6103 | 4.2848 | 4.2848 | 4.2848 | 4.2848
2021-10-25 08:00 | 2.4035 | 2.9248 | 2.8617 | 3.078 | 2.9158 | 3.1321 | 1.1089 | 1.9015 | 2.3464 | 2.3464 | 2.6429 | 2.6429 | 2019-12-22 21:00 | 1.5928 | 2.6103 | 4.2848 | 4.2848 | 4.2848 | 4.2848
2021-10-25 09:00 | 2.2577 | 2.7474 | 2.6882 | 2.8913 | 2.739 | 2.9421 | 1.1174 | 1.9162 | 2.3645 | 2.3645 | 2.6633 | 2.6633 | 2019-12-22 22:00 | 1.4404 | 2.3605 | 3.8748 | 3.8748 | 3.8748 | 3.8748
2021-10-25 10:00 | 2.072 | 2.5214 | 2.467 | 2.6535 | 2.5136 | 2.7001 | 1.1946 | 2.0485 | 2.5278 | 2.5278 | 2.8473 | 2.8473 | 2019-12-22 23:00 | 1.2879 | 2.1107 | 3.4648 | 3.4648 | 3.4648 | 3.4648
2021-10-25 11:00 | 2.1291 | 2.5909 | 2.535 | 2.7266 | 2.5829 | 2.7746 | 1.2317 | 2.1122 | 2.6064 | 2.6064 | 2.9358 | 2.9358 | 2019-12-23 | 1.2041 | 1.9733 | 3.2392 | 3.2392 | 3.2392 | 3.2392
2021-10-25 12:00 | 1.9719 | 2.3996 | 2.3479 | 2.5254 | 2.3922 | 2.5697 | 1.2432 | 2.1318 | 2.6306 | 2.6306 | 2.9631 | 2.9631 | 2019-12-23 01:00 | 1.1355 | 1.8609 | 3.0547 | 3.0547 | 3.0547 | 3.0547
2021-10-25 13:00 | 2.0777 | 2.5283 | 2.4738 | 2.6608 | 2.5205 | 2.7075 | 1.2632 | 2.1662 | 2.6729 | 2.6729 | 3.0107 | 3.0107 | 2019-12-23 02:00 | 1.1203 | 1.8359 | 3.0137 | 3.0137 | 3.0137 | 3.0137
2021-10-25 14:00 | 1.9348 | 2.3544 | 2.3036 | 2.4778 | 2.3472 | 2.5213 | 1.2117 | 2.0779 | 2.5641 | 2.5641 | 2.8881 | 2.8881 | 2019-12-23 03:00 | 1.2041 | 1.9733 | 3.2392 | 3.2392 | 3.2392 | 3.2392
2021-10-25 15:00 | 1.9891 | 2.4205 | 2.3683 | 2.5473 | 2.4131 | 2.5921 | 1.1117 | 1.9064 | 2.3524 | 2.3524 | 2.6497 | 2.6497 | 2019-12-23 04:00 | 1.1813 | 1.9359 | 3.1777 | 3.1777 | 3.1777 | 3.1777
2021-10-25 16:00 | 1.8433 | 2.2431 | 2.1948 | 2.3607 | 2.2362 | 2.4021 | 1.1746 | 2.0142 | 2.4854 | 2.4854 | 2.7996 | 2.7996 | 2019-12-23 05:00 | 1.1813 | 1.9359 | 3.1777 | 3.1777 | 3.1777 | 3.1777
2021-10-25 17:00 | 2.1606 | 2.6292 | 2.5725 | 2.7669 | 2.6211 | 2.8155 | 1.2632 | 2.1662 | 2.6729 | 2.6729 | 3.0107 | 3.0107 | 2019-12-23 06:00 | 1.2651 | 2.0732 | 3.4033 | 3.4033 | 3.4033 | 3.4033
2021-10-25 18:00 | 2.4121 | 2.9352 | 2.8719 | 3.089 | 2.9262 | 3.1433 | 1.4032 | 2.4063 | 2.9692 | 2.9692 | 3.3445 | 3.3445 | 2019-12-23 07:00 | 1.7605 | 2.8851 | 4.7359 | 4.7359 | 4.7359 | 4.7359
2021-10-25 19:00 | 2.5378 | 3.0882 | 3.0216 | 3.25 | 3.0787 | 3.3071 | 1.5232 | 2.6121 | 3.2232 | 3.2232 | 3.6306 | 3.6306 | 2019-12-23 08:00 | 1.9434 | 3.1848 | 5.2279 | 5.2279 | 5.2279 | 5.2279
2021-10-25 20:00 | 2.4235 | 2.9491 | 2.8855 | 3.1036 | 2.94 | 3.1582 | 1.5204 | 2.6072 | 3.2172 | 3.2172 | 3.6238 | 3.6238 | 2019-12-23 09:00 | 1.9586 | 3.2098 | 5.2689 | 5.2689 | 5.2689 | 5.2689
2021-10-25 21:00 | 2.2206 | 2.7022 | 2.6439 | 2.8438 | 2.6939 | 2.8937 | 1.4661 | 2.5141 | 3.1023 | 3.1023 | 3.4944 | 3.4944 | 2019-12-23 10:00 | 2.1491 | 3.522 | 5.7814 | 5.7814 | 5.7814 | 5.7814
2021-10-25 22:00 | 1.9748 | 2.4031 | 2.3513 | 2.529 | 2.3957 | 2.5734 | 1.2527 | 2.1483 | 2.6508 | 2.6508 | 2.9859 | 2.9859 | 2019-12-23 11:00 | 2.172 | 3.5595 | 5.8429 | 5.8429 | 5.8429 | 5.8429
2021-10-25 23:00 | 1.6861 | 2.0519 | 2.0076 | 2.1594 | 2.0455 | 2.1973 | 1.0746 | 1.8427 | 2.2738 | 2.2738 | 2.5612 | 2.5612 | 2019-12-23 12:00 | 2.2482 | 3.6844 | 6.048 | 6.048 | 6.048 | 6.048
2021-10-26 | 1.649 | 2.0067 | 1.9634 | 2.1118 | 2.0005 | 2.1489 | 0.96596 | 1.6565 | 2.044 | 2.044 | 2.3023 | 2.3023 | 2019-12-23 13:00 | 2.2406 | 3.6719 | 6.0275 | 6.0275 | 6.0275 | 6.0275
2021-10-26 01:00 | 1.5004 | 1.8258 | 1.7864 | 1.9215 | 1.8202 | 1.9552 | 0.86022 | 1.4751 | 1.8202 | 1.8202 | 2.0503 | 2.0503 | 2019-12-23 14:00 | 2.4463 | 4.0091 | 6.581 | 6.581 | 6.581 | 6.581
2021-10-26 02:00 | 1.5032 | 1.8293 | 1.7898 | 1.9251 | 1.8237 | 1.9589 | 0.78325 | 1.3432 | 1.6574 | 1.6574 | 1.8669 | 1.8669 | 2019-12-23 15:00 | 2.5149 | 4.1215 | 6.7655 | 6.7655 | 6.7655 | 6.7655
2021-10-26 03:00 | 1.4575 | 1.7736 | 1.7354 | 1.8666 | 1.7682 | 1.8994 | 0.74019 | 1.2693 | 1.5662 | 1.5662 | 1.7642 | 1.7642 | 2019-12-23 16:00 | 2.5835 | 4.2339 | 6.95 | 6.95 | 6.95 | 6.95
2021-10-26 04:00 | 1.509 | 1.8362 | 1.7966 | 1.9324 | 1.8306 | 1.9664 | 0.70952 | 1.2167 | 1.5014 | 1.5014 | 1.6911 | 1.6911 | 2019-12-23 17:00 | 2.4845 | 4.0716 | 6.6835 | 6.6835 | 6.6835 | 6.6835
2021-10-26 05:00 | 1.7209 | 2.0941 | 2.049 | 2.2038 | 2.0877 | 2.2426 | 0.84307 | 1.4457 | 1.7839 | 1.7839 | 2.0094 | 2.0094 | 2019-12-23 18:00 | 2.0653 | 3.3846 | 5.5559 | 5.5559 | 5.5559 | 5.5559
2021-10-26 06:00 | 2.092 | 2.5457 | 2.4908 | 2.6791 | 2.5379 | 2.7261 | 0.87737 | 1.5045 | 1.8565 | 1.8565 | 2.0912 | 2.0912 | 2019-12-23 19:00 | 1.9967 | 3.2722 | 5.3714 | 5.3714 | 5.3714 | 5.3714
2021-10-26 07:00 | 2.3692 | 2.8831 | 2.8209 | 3.0341 | 2.8742 | 3.0874 | 1.1689 | 2.0044 | 2.4733 | 2.4733 | 2.786 | 2.786 | 2019-12-23 20:00 | 1.9129 | 3.1348 | 5.1459 | 5.1459 | 5.1459 | 5.1459
2021-10-26 08:00 | 2.4463 | 2.9769 | 2.9127 | 3.1329 | 2.9678 | 3.1879 | 1.1856 | 2.0331 | 2.5087 | 2.5087 | 2.8258 | 2.8258 | 2019-12-23 21:00 | 1.9281 | 3.1598 | 5.1869 | 5.1869 | 5.1869 | 5.1869
2021-10-26 09:00 | 2.2149 | 2.6953 | 2.6371 | 2.8364 | 2.6869 | 2.8863 | 1.2003 | 2.0583 | 2.5399 | 2.5399 | 2.8609 | 2.8609 | 2019-12-23 22:00 | 1.7605 | 2.8851 | 4.7359 | 4.7359 | 4.7359 | 4.7359
2021-10-26 10:00 | 1.9262 | 2.344 | 2.2934 | 2.4668 | 2.3368 | 2.5101 | 1.2003 | 2.0583 | 2.5399 | 2.5399 | 2.8609 | 2.8609 | 2019-12-23 23:00 | 1.6538 | 2.7102 | 4.4488 | 4.4488 | 4.4488 | 4.4488
2021-10-26 11:00 | 1.9119 | 2.3266 | 2.2764 | 2.4485 | 2.3194 | 2.4915 | 1.2117 | 2.0779 | 2.5641 | 2.5641 | 2.8881 | 2.8881 | 2019-12-24 | 1.4861 | 2.4354 | 3.9978 | 3.9978 | 3.9978 | 3.9978
2021-10-26 12:00 | 1.8033 | 2.1945 | 2.1471 | 2.3094 | 2.1877 | 2.35 | 1.1603 | 1.9897 | 2.4552 | 2.4552 | 2.7655 | 2.7655 | 2019-12-24 01:00 | 1.4632 | 2.398 | 3.9363 | 3.9363 | 3.9363 | 3.9363
2021-10-26 13:00 | 1.7347 | 2.111 | 2.0655 | 2.2216 | 2.1045 | 2.2606 | 1.1546 | 1.9799 | 2.4431 | 2.4431 | 2.7519 | 2.7519 | 2019-12-24 02:00 | 1.448 | 2.373 | 3.8953 | 3.8953 | 3.8953 | 3.8953
2021-10-26 14:00 | 1.6261 | 1.9788 | 1.9361 | 2.0825 | 1.9727 | 2.1191 | 1.146 | 1.9652 | 2.425 | 2.425 | 2.7315 | 2.7315 | 2019-12-24 03:00 | 1.4251 | 2.3355 | 3.8338 | 3.8338 | 3.8338 | 3.8338
2021-10-26 15:00 | 1.6919 | 2.0588 | 2.0144 | 2.1667 | 2.0525 | 2.2047 | 1.0346 | 1.7741 | 2.1891 | 2.1891 | 2.4658 | 2.4658 | 2019-12-24 04:00 | 1.4709 | 2.4105 | 3.9568 | 3.9568 | 3.9568 | 3.9568
2021-10-26 16:00 | 1.689 | 2.0553 | 2.011 | 2.163 | 2.049 | 2.201 | 1.2117 | 2.0779 | 2.5641 | 2.5641 | 2.8881 | 2.8881 | 2019-12-24 05:00 | 1.4861 | 2.4354 | 3.9978 | 3.9978 | 3.9978 | 3.9978
2021-10-26 17:00 | 2.1463 | 2.6118 | 2.5554 | 2.7486 | 2.6037 | 2.7969 | 1.3175 | 2.2593 | 2.7878 | 2.7878 | 3.1402 | 3.1402 | 2019-12-24 06:00 | 1.5318 | 2.5104 | 4.1208 | 4.1208 | 4.1208 | 4.1208
2021-10-26 18:00 | 2.292 | 2.7892 | 2.729 | 2.9353 | 2.7806 | 2.9868 | 1.4575 | 2.4994 | 3.0841 | 3.0841 | 3.4739 | 3.4739 | 2019-12-24 07:00 | 1.951 | 3.1973 | 5.2484 | 5.2484 | 5.2484 | 5.2484
2021-10-26 19:00 | 2.2406 | 2.7266 | 2.6677 | 2.8694 | 2.7181 | 2.9198 | 1.5375 | 2.6366 | 3.2534 | 3.2534 | 3.6647 | 3.6647 | 2019-12-24 08:00 | 2.1872 | 3.5845 | 5.8839 | 5.8839 | 5.8839 | 5.8839
2021-10-26 20:00 | 2.2406 | 2.7266 | 2.6677 | 2.8694 | 2.7181 | 2.9198 | 1.549 | 2.6562 | 3.2776 | 3.2776 | 3.6919 | 3.6919 | 2019-12-24 09:00 | 2.233 | 3.6594 | 6.007 | 6.007 | 6.007 | 6.007
2021-10-26 21:00 | 2.0891 | 2.5422 | 2.4874 | 2.6754 | 2.5344 | 2.7224 | 1.4547 | 2.4945 | 3.0781 | 3.0781 | 3.4671 | 3.4671 | 2019-12-24 10:00 | 2.3854 | 3.9092 | 6.417 | 6.417 | 6.417 | 6.417
2021-10-26 22:00 | 1.8719 | 2.2779 | 2.2288 | 2.3973 | 2.2709 | 2.4394 | 1.209 | 2.0733 | 2.5583 | 2.5583 | 2.8816 | 2.8816 | 2019-12-24 11:00 | 2.4921 | 4.084 | 6.704 | 6.704 | 6.704 | 6.704
2021-10-26 23:00 | 1.6777 | 2.0415 | 1.9975 | 2.1485 | 2.0353 | 2.1862 | 1.0431 | 1.7888 | 2.2073 | 2.2073 | 2.4862 | 2.4862 | 2019-12-24 12:00 | 2.4768 | 4.0591 | 6.663 | 6.663 | 6.663 | 6.663
2021-10-27 | 1.6299 | 1.9834 | 1.9406 | 2.0873 | 1.9773 | 2.1239 | 0.95453 | 1.6369 | 2.0198 | 2.0198 | 2.2751 | 2.2751 | 2019-12-24 13:00 | 2.4845 | 4.0716 | 6.6835 | 6.6835 | 6.6835 | 6.6835
2021-10-27 01:00 | 1.4947 | 1.8189 | 1.7796 | 1.9141 | 1.8133 | 1.9478 | 0.78591 | 1.3477 | 1.663 | 1.663 | 1.8732 | 1.8732 | 2019-12-24 14:00 | 2.5226 | 4.134 | 6.786 | 6.786 | 6.786 | 6.786
2021-10-27 02:00 | 1.4289 | 1.7389 | 1.7014 | 1.83 | 1.7335 | 1.8621 | 0.77737 | 1.3331 | 1.6449 | 1.6449 | 1.8528 | 1.8528 | 2019-12-24 15:00 | 2.4463 | 4.0091 | 6.581 | 6.581 | 6.581 | 6.581
2021-10-27 03:00 | 1.3889 | 1.6902 | 1.6537 | 1.7787 | 1.685 | 1.81 | 0.73733 | 1.2644 | 1.5602 | 1.5602 | 1.7574 | 1.7574 | 2019-12-24 16:00 | 2.4159 | 3.9591 | 6.499 | 6.499 | 6.499 | 6.499
2021-10-27 04:00 | 1.4461 | 1.7597 | 1.7218 | 1.8519 | 1.7543 | 1.8845 | 0.73447 | 1.2595 | 1.5542 | 1.5542 | 1.7506 | 1.7506 | 2019-12-24 17:00 | 2.332 | 3.8218 | 6.2735 | 6.2735 | 6.2735 | 6.2735
2021-10-27 05:00 | 1.6033 | 1.951 | 1.9089 | 2.0532 | 1.945 | 2.0893 | 0.79449 | 1.3624 | 1.6811 | 1.6811 | 1.8936 | 1.8936 | 2019-12-24 18:00 | 2.0272 | 3.3222 | 5.4534 | 5.4534 | 5.4534 | 5.4534
2021-10-27 06:00 | 1.9856 | 2.4163 | 2.3642 | 2.5429 | 2.4089 | 2.5876 | 0.82021 | 1.4065 | 1.7356 | 1.7356 | 1.9549 | 1.9549 | 2019-12-24 19:00 | 1.9357 | 3.1723 | 5.2074 | 5.2074 | 5.2074 | 5.2074
2021-10-27 07:00 | 2.2977 | 2.7961 | 2.7358 | 2.9426 | 2.7875 | 2.9943 | 1.0717 | 1.8378 | 2.2677 | 2.2677 | 2.5544 | 2.5544 | 2019-12-24 20:00 | 1.8671 | 3.0599 | 5.0229 | 5.0229 | 5.0229 | 5.0229
2021-10-27 08:00 | 2.3835 | 2.9004 | 2.8379 | 3.0524 | 2.8915 | 3.106 | 1.1431 | 1.9603 | 2.4189 | 2.4189 | 2.7246 | 2.7246 | 2019-12-24 21:00 | 1.7071 | 2.7976 | 4.5923 | 4.5923 | 4.5923 | 4.5923
2021-10-27 09:00 | 2.1606 | 2.6292 | 2.5725 | 2.7669 | 2.6211 | 2.8155 | 1.1746 | 2.0142 | 2.4854 | 2.4854 | 2.7996 | 2.7996 | 2019-12-24 22:00 | 1.6309 | 2.6727 | 4.3873 | 4.3873 | 4.3873 | 4.3873
2021-10-27 10:00 | 1.8891 | 2.2988 | 2.2492 | 2.4192 | 2.2917 | 2.4617 | 1.1574 | 1.9848 | 2.4492 | 2.4492 | 2.7587 | 2.7587 | 2019-12-24 23:00 | 1.5166 | 2.4854 | 4.0798 | 4.0798 | 4.0798 | 4.0798
2021-10-27 11:00 | 1.8891 | 2.2988 | 2.2492 | 2.4192 | 2.2917 | 2.4617 | 1.2032 | 2.0632 | 2.5459 | 2.5459 | 2.8677 | 2.8677 | 2019-12-25 | 1.3946 | 2.2856 | 3.7518 | 3.7518 | 3.7518 | 3.7518
2021-10-27 12:00 | 1.9319 | 2.351 | 2.3002 | 2.4741 | 2.3437 | 2.5176 | 1.1803 | 2.024 | 2.4975 | 2.4975 | 2.8132 | 2.8132 | 2019-12-25 01:00 | 1.3642 | 2.2356 | 3.6698 | 3.6698 | 3.6698 | 3.6698
2021-10-27 13:00 | 1.7833 | 2.1701 | 2.1233 | 2.2838 | 2.1634 | 2.3239 | 1.1632 | 1.9946 | 2.4612 | 2.4612 | 2.7723 | 2.7723 | 2019-12-25 02:00 | 1.3642 | 2.2356 | 3.6698 | 3.6698 | 3.6698 | 3.6698
2021-10-27 14:00 | 1.8176 | 2.2118 | 2.1641 | 2.3277 | 2.205 | 2.3686 | 1.1489 | 1.9701 | 2.431 | 2.431 | 2.7383 | 2.7383 | 2019-12-25 03:00 | 1.2956 | 2.1232 | 3.4853 | 3.4853 | 3.4853 | 3.4853
2021-10-27 15:00 | 1.709 | 2.0797 | 2.0348 | 2.1886 | 2.0733 | 2.2271 | 1.106 | 1.8966 | 2.3403 | 2.3403 | 2.6361 | 2.6361 | 2019-12-25 04:00 | 1.3337 | 2.1856 | 3.5878 | 3.5878 | 3.5878 | 3.5878
2021-10-27 16:00 | 1.8205 | 2.2153 | 2.1675 | 2.3314 | 2.2085 | 2.3723 | 1.1803 | 2.024 | 2.4975 | 2.4975 | 2.8132 | 2.8132 | 2019-12-25 05:00 | 1.3337 | 2.1856 | 3.5878 | 3.5878 | 3.5878 | 3.5878
2021-10-27 17:00 | 2.0623 | 2.5096 | 2.4555 | 2.6411 | 2.5019 | 2.6875 | 1.3175 | 2.2593 | 2.7878 | 2.7878 | 3.1402 | 3.1402 | 2019-12-25 06:00 | 1.3794 | 2.2606 | 3.7108 | 3.7108 | 3.7108 | 3.7108
2021-10-27 18:00 | 2.252 | 2.7405 | 2.6813 | 2.884 | 2.732 | 2.9347 | 1.4032 | 2.4063 | 2.9692 | 2.9692 | 3.3445 | 3.3445 | 2019-12-25 07:00 | 1.4937 | 2.4479 | 4.0183 | 4.0183 | 4.0183 | 4.0183
2021-10-27 19:00 | 2.2053 | 2.6836 | 2.6257 | 2.8242 | 2.6754 | 2.8738 | 1.5004 | 2.5729 | 3.1748 | 3.1748 | 3.5761 | 3.5761 | 2019-12-25 08:00 | 1.5394 | 2.5229 | 4.1413 | 4.1413 | 4.1413 | 4.1413
2021-10-27 20:00 | 2.112 | 2.5701 | 2.5146 | 2.7047 | 2.5621 | 2.7522 | 1.4747 | 2.5288 | 3.1204 | 3.1204 | 3.5148 | 3.5148 | 2019-12-25 09:00 | 1.608 | 2.6353 | 4.3258 | 4.3258 | 4.3258 | 4.3258
2021-10-27 21:00 | 1.998 | 2.4314 | 2.3789 | 2.5588 | 2.4239 | 2.6037 | 1.3632 | 2.3377 | 2.8846 | 2.8846 | 3.2491 | 3.2491 | 2019-12-25 10:00 | 1.6233 | 2.6602 | 4.3668 | 4.3668 | 4.3668 | 4.3668
2021-10-27 22:00 | 1.8144 | 2.208 | 2.1603 | 2.3236 | 2.2012 | 2.3645 | 1.2003 | 2.0583 | 2.5399 | 2.5399 | 2.8609 | 2.8609 | 2019-12-25 11:00 | 1.669 | 2.7352 | 4.4898 | 4.4898 | 4.4898 | 4.4898
2021-10-27 23:00 | 1.5826 | 1.9258 | 1.8843 | 2.0267 | 1.9199 | 2.0623 | 1.0574 | 1.8133 | 2.2375 | 2.2375 | 2.5203 | 2.5203 | 2019-12-25 12:00 | 1.7147 | 2.8101 | 4.6128 | 4.6128 | 4.6128 | 4.6128
2021-10-28 | 1.5444 | 1.8794 | 1.8388 | 1.9778 | 1.8736 | 2.0126 | 0.91738 | 1.5732 | 1.9412 | 1.9412 | 2.1865 | 2.1865 | 2019-12-25 13:00 | 1.7605 | 2.8851 | 4.7359 | 4.7359 | 4.7359 | 4.7359
2021-10-28 01:00 | 1.3888 | 1.69 | 1.6535 | 1.7785 | 1.6848 | 1.8098 | 0.75734 | 1.2987 | 1.6025 | 1.6025 | 1.8051 | 1.8051 | 2019-12-25 14:00 | 1.7681 | 2.8975 | 4.7564 | 4.7564 | 4.7564 | 4.7564
2021-10-28 02:00 | 1.3744 | 1.6726 | 1.6365 | 1.7602 | 1.6674 | 1.7911 | 0.69448 | 1.1909 | 1.4695 | 1.4695 | 1.6553 | 1.6553 | 2019-12-25 15:00 | 1.7605 | 2.8851 | 4.7359 | 4.7359 | 4.7359 | 4.7359
2021-10-28 03:00 | 1.4347 | 1.7458 | 1.7082 | 1.8373 | 1.7404 | 1.8696 | 0.70875 | 1.2154 | 1.4997 | 1.4997 | 1.6893 | 1.6893 | 2019-12-25 16:00 | 1.7528 | 2.8726 | 4.7154 | 4.7154 | 4.7154 | 4.7154
2021-10-28 04:00 | 1.4004 | 1.7041 | 1.6673 | 1.7934 | 1.6988 | 1.8249 | 0.70528 | 1.2094 | 1.4924 | 1.4924 | 1.681 | 1.681 | 2019-12-25 17:00 | 1.7528 | 2.8726 | 4.7154 | 4.7154 | 4.7154 | 4.7154
2021-10-28 05:00 | 1.489 | 1.8119 | 1.7728 | 1.9068 | 1.8063 | 1.9403 | 0.76019 | 1.3036 | 1.6086 | 1.6086 | 1.8119 | 1.8119 | 2019-12-25 18:00 | 1.7223 | 2.8226 | 4.6333 | 4.6333 | 4.6333 | 4.6333
2021-10-28 06:00 | 1.809 | 2.2014 | 2.1539 | 2.3167 | 2.1946 | 2.3574 | 0.82021 | 1.4065 | 1.7356 | 1.7356 | 1.9549 | 1.9549 | 2019-12-25 19:00 | 1.6919 | 2.7726 | 4.5513 | 4.5513 | 4.5513 | 4.5513
2021-10-28 07:00 | 2.1548 | 2.6222 | 2.5657 | 2.7596 | 2.6141 | 2.8081 | 1.0145 | 1.7398 | 2.1468 | 2.1468 | 2.4181 | 2.4181 | 2019-12-25 20:00 | 1.7605 | 2.8851 | 4.7359 | 4.7359 | 4.7359 | 4.7359
2021-10-28 08:00 | 2.2091 | 2.6883 | 2.6303 | 2.8291 | 2.68 | 2.8788 | 1.0831 | 1.8574 | 2.2919 | 2.2919 | 2.5816 | 2.5816 | 2019-12-25 21:00 | 1.7833 | 2.9225 | 4.7974 | 4.7974 | 4.7974 | 4.7974
2021-10-28 09:00 | 2.1234 | 2.584 | 2.5282 | 2.7193 | 2.576 | 2.7671 | 1.1546 | 1.9799 | 2.4431 | 2.4431 | 2.7519 | 2.7519 | 2019-12-25 22:00 | 1.8214 | 2.985 | 4.8999 | 4.8999 | 4.8999 | 4.8999
2021-10-28 10:00 | 2.032 | 2.4727 | 2.4193 | 2.6022 | 2.4651 | 2.6479 | 1.2489 | 2.1416 | 2.6427 | 2.6427 | 2.9767 | 2.9767 | 2019-12-25 23:00 | 1.7986 | 2.9475 | 4.8384 | 4.8384 | 4.8384 | 4.8384
2021-10-28 11:00 | 2.2091 | 2.6883 | 2.6303 | 2.8291 | 2.68 | 2.8788 | 1.2746 | 2.1858 | 2.6971 | 2.6971 | 3.038 | 3.038 | 2019-12-26 | 1.6309 | 2.6727 | 4.3873 | 4.3873 | 4.3873 | 4.3873
2021-10-28 12:00 | 2.0462 | 2.4901 | 2.4364 | 2.6205 | 2.4824 | 2.6666 | 1.2375 | 2.122 | 2.6185 | 2.6185 | 2.9494 | 2.9494 | 2019-12-26 01:00 | 1.5775 | 2.5853 | 4.2438 | 4.2438 | 4.2438 | 4.2438
2021-10-28 13:00 | 1.9834 | 2.4136 | 2.3615 | 2.54 | 2.4061 | 2.5846 | 1.2975 | 2.225 | 2.7455 | 2.7455 | 3.0925 | 3.0925 | 2019-12-26 02:00 | 1.5623 | 2.5603 | 4.2028 | 4.2028 | 4.2028 | 4.2028
2021-10-28 14:00 | 2.0605 | 2.5075 | 2.4534 | 2.6388 | 2.4997 | 2.6852 | 1.1803 | 2.024 | 2.4975 | 2.4975 | 2.8132 | 2.8132 | 2019-12-26 03:00 | 1.5013 | 2.4604 | 4.0388 | 4.0388 | 4.0388 | 4.0388
2021-10-28 15:00 | 2.1377 | 2.6014 | 2.5452 | 2.7376 | 2.5933 | 2.7857 | 1.2203 | 2.0926 | 2.5822 | 2.5822 | 2.9086 | 2.9086 | 2019-12-26 04:00 | 1.5318 | 2.5104 | 4.1208 | 4.1208 | 4.1208 | 4.1208
2021-10-28 16:00 | 2.0948 | 2.5492 | 2.4942 | 2.6827 | 2.5413 | 2.7299 | 1.3289 | 2.2789 | 2.812 | 2.812 | 3.1674 | 3.1674 | 2019-12-26 05:00 | 1.5623 | 2.5603 | 4.2028 | 4.2028 | 4.2028 | 4.2028
2021-10-28 17:00 | 2.2006 | 2.6779 | 2.6201 | 2.8181 | 2.6696 | 2.8677 | 1.3318 | 2.2838 | 2.818 | 2.818 | 3.1742 | 3.1742 | 2019-12-26 06:00 | 1.6004 | 2.6228 | 4.3053 | 4.3053 | 4.3053 | 4.3053
2021-10-28 18:00 | 2.3463 | 2.8552 | 2.7936 | 3.0048 | 2.8464 | 3.0576 | 1.4289 | 2.4504 | 3.0236 | 3.0236 | 3.4058 | 3.4058 | 2019-12-26 07:00 | 2.0043 | 3.2847 | 5.3919 | 5.3919 | 5.3919 | 5.3919
2021-10-28 19:00 | 2.2349 | 2.7196 | 2.6609 | 2.8621 | 2.7112 | 2.9124 | 1.3918 | 2.3867 | 2.945 | 2.945 | 3.3173 | 3.3173 | 2019-12-26 08:00 | 2.1644 | 3.547 | 5.8224 | 5.8224 | 5.8224 | 5.8224
2021-10-28 20:00 | 2.1348 | 2.5979 | 2.5418 | 2.734 | 2.5899 | 2.782 | 1.3918 | 2.3867 | 2.945 | 2.945 | 3.3173 | 3.3173 | 2019-12-26 09:00 | 2.3244 | 3.8093 | 6.253 | 6.253 | 6.253 | 6.253
2021-10-28 21:00 | 1.9948 | 2.4275 | 2.3751 | 2.5546 | 2.42 | 2.5995 | 1.2718 | 2.1809 | 2.691 | 2.691 | 3.0312 | 3.0312 | 2019-12-26 10:00 | 2.332 | 3.8218 | 6.2735 | 6.2735 | 6.2735 | 6.2735
2021-10-28 22:00 | 1.8119 | 2.2049 | 2.1573 | 2.3204 | 2.1981 | 2.3612 | 1.1546 | 1.9799 | 2.4431 | 2.4431 | 2.7519 | 2.7519 | 2019-12-26 11:00 | 2.4235 | 3.9716 | 6.5195 | 6.5195 | 6.5195 | 6.5195
2021-10-28 23:00 | 1.6233 | 1.9754 | 1.9327 | 2.0788 | 1.9693 | 2.1154 | 1.0117 | 1.7349 | 2.1407 | 2.1407 | 2.4113 | 2.4113 | 2019-12-26 12:00 | 2.3092 | 3.7843 | 6.212 | 6.212 | 6.212 | 6.212
2021-10-29 | 1.5834 | 1.9268 | 1.8852 | 2.0277 | 1.9209 | 2.0634 | 0.88905 | 1.5246 | 1.8813 | 1.8813 | 2.119 | 2.119 | 2019-12-26 13:00 | 2.393 | 3.9217 | 6.4375 | 6.4375 | 6.4375 | 6.4375
2021-10-29 01:00 | 1.3835 | 1.6836 | 1.6473 | 1.7718 | 1.6784 | 1.8029 | 0.84879 | 1.4555 | 1.796 | 1.796 | 2.0231 | 2.0231 | 2019-12-26 14:00 | 2.332 | 3.8218 | 6.2735 | 6.2735 | 6.2735 | 6.2735
2021-10-29 02:00 | 1.3661 | 1.6624 | 1.6265 | 1.7494 | 1.6572 | 1.7802 | 0.7202 | 1.235 | 1.5239 | 1.5239 | 1.7166 | 1.7166 | 2019-12-26 15:00 | 2.5454 | 4.1715 | 6.8475 | 6.8475 | 6.8475 | 6.8475
2021-10-29 03:00 | 1.3546 | 1.6484 | 1.6129 | 1.7348 | 1.6434 | 1.7653 | 0.71447 | 1.2252 | 1.5118 | 1.5118 | 1.7029 | 1.7029 | 2019-12-26 16:00 | 2.5911 | 4.2464 | 6.9705 | 6.9705 | 6.9705 | 6.9705
2021-10-29 04:00 | 1.3518 | 1.645 | 1.6095 | 1.7311 | 1.6399 | 1.7616 | 0.70018 | 1.2007 | 1.4816 | 1.4816 | 1.6688 | 1.6688 | 2019-12-26 17:00 | 2.5149 | 4.1215 | 6.7655 | 6.7655 | 6.7655 | 6.7655
2021-10-29 05:00 | 1.511 | 1.8387 | 1.799 | 1.935 | 1.833 | 1.969 | 0.77414 | 1.3275 | 1.6381 | 1.6381 | 1.8451 | 1.8451 | 2019-12-26 18:00 | 2.2406 | 3.6719 | 6.0275 | 6.0275 | 6.0275 | 6.0275
2021-10-29 06:00 | 1.7776 | 2.1632 | 2.1165 | 2.2765 | 2.1565 | 2.3165 | 0.81164 | 1.3918 | 1.7174 | 1.7174 | 1.9345 | 1.9345 | 2019-12-26 19:00 | 2.1186 | 3.4721 | 5.6994 | 5.6994 | 5.6994 | 5.6994
2021-10-29 07:00 | 2.0661 | 2.5142 | 2.46 | 2.6459 | 2.5064 | 2.6924 | 1.0003 | 1.7153 | 2.1166 | 2.1166 | 2.3841 | 2.3841 | 2019-12-26 20:00 | 2.0043 | 3.2847 | 5.3919 | 5.3919 | 5.3919 | 5.3919
2021-10-29 08:00 | 2.1748 | 2.6466 | 2.5895 | 2.7852 | 2.6384 | 2.8341 | 1.2117 | 2.0779 | 2.5641 | 2.5641 | 2.8881 | 2.8881 | 2019-12-26 21:00 | 1.8824 | 3.0849 | 5.0639 | 5.0639 | 5.0639 | 5.0639
2021-10-29 09:00 | 2.1863 | 2.6605 | 2.6031 | 2.7998 | 2.6523 | 2.849 | 1.2145 | 2.0827 | 2.5699 | 2.5699 | 2.8947 | 2.8947 | 2019-12-26 22:00 | 1.6842 | 2.7602 | 4.5308 | 4.5308 | 4.5308 | 4.5308
2021-10-29 10:00 | 2.0548 | 2.5005 | 2.4466 | 2.6315 | 2.4928 | 2.6777 | 1.2517 | 2.1466 | 2.6487 | 2.6487 | 2.9835 | 2.9835 | 2019-12-26 23:00 | 1.6004 | 2.6228 | 4.3053 | 4.3053 | 4.3053 | 4.3053
2021-10-29 11:00 | 1.9777 | 2.4066 | 2.3547 | 2.5327 | 2.3992 | 2.5772 | 1.2889 | 2.2103 | 2.7273 | 2.7273 | 3.072 | 3.072 | 2019-12-27 | 1.5166 | 2.4854 | 4.0798 | 4.0798 | 4.0798 | 4.0798
2021-10-29 12:00 | 1.8119 | 2.2049 | 2.1573 | 2.3204 | 2.1981 | 2.3612 | 1.2432 | 2.1318 | 2.6306 | 2.6306 | 2.9631 | 2.9631 | 2019-12-27 01:00 | 1.5166 | 2.4854 | 4.0798 | 4.0798 | 4.0798 | 4.0798
2021-10-29 13:00 | 1.7376 | 2.1145 | 2.0689 | 2.2252 | 2.108 | 2.2643 | 1.1746 | 2.0142 | 2.4854 | 2.4854 | 2.7996 | 2.7996 | 2019-12-27 02:00 | 1.448 | 2.373 | 3.8953 | 3.8953 | 3.8953 | 3.8953
2021-10-29 14:00 | 1.8605 | 2.264 | 2.2152 | 2.3826 | 2.257 | 2.4245 | 1.2003 | 2.0583 | 2.5399 | 2.5399 | 2.8609 | 2.8609 | 2019-12-27 03:00 | 1.4404 | 2.3605 | 3.8748 | 3.8748 | 3.8748 | 3.8748
2021-10-29 15:00 | 1.9033 | 2.3162 | 2.2662 | 2.4375 | 2.309 | 2.4803 | 1.2003 | 2.0583 | 2.5399 | 2.5399 | 2.8609 | 2.8609 | 2019-12-27 04:00 | 1.4175 | 2.323 | 3.8133 | 3.8133 | 3.8133 | 3.8133
2021-10-29 16:00 | 1.8233 | 2.2188 | 2.1709 | 2.335 | 2.212 | 2.3761 | 1.2775 | 2.1907 | 2.7031 | 2.7031 | 3.0448 | 3.0448 | 2019-12-27 05:00 | 1.509 | 2.4729 | 4.0593 | 4.0593 | 4.0593 | 4.0593
2021-10-29 17:00 | 2.0094 | 2.4452 | 2.3924 | 2.5733 | 2.4377 | 2.6185 | 1.4175 | 2.4308 | 2.9995 | 2.9995 | 3.3786 | 3.3786 | 2019-12-27 06:00 | 1.6385 | 2.6852 | 4.4078 | 4.4078 | 4.4078 | 4.4078
2021-10-29 18:00 | 2.1491 | 2.6153 | 2.5588 | 2.7523 | 2.6072 | 2.8006 | 1.5232 | 2.6121 | 3.2232 | 3.2232 | 3.6306 | 3.6306 | 2019-12-27 07:00 | 1.829 | 2.9975 | 4.9204 | 4.9204 | 4.9204 | 4.9204
2021-10-29 19:00 | 2.0863 | 2.5388 | 2.484 | 2.6718 | 2.5309 | 2.7187 | 1.6233 | 2.7837 | 3.4349 | 3.4349 | 3.869 | 3.869 | 2019-12-27 08:00 | 2.0577 | 3.3721 | 5.5354 | 5.5354 | 5.5354 | 5.5354
2021-10-29 20:00 | 2.0834 | 2.5353 | 2.4806 | 2.6681 | 2.5275 | 2.715 | 1.6061 | 2.7543 | 3.3986 | 3.3986 | 3.8281 | 3.8281 | 2019-12-27 09:00 | 2.233 | 3.6594 | 6.007 | 6.007 | 6.007 | 6.007
2021-10-29 21:00 | 2.0148 | 2.4518 | 2.3989 | 2.5803 | 2.4443 | 2.6256 | 1.529 | 2.6219 | 3.2353 | 3.2353 | 3.6442 | 3.6442 | 2019-12-27 10:00 | 2.393 | 3.9217 | 6.4375 | 6.4375 | 6.4375 | 6.4375
2021-10-29 22:00 | 1.8267 | 2.223 | 2.175 | 2.3394 | 2.2161 | 2.3805 | 1.2832 | 2.2005 | 2.7152 | 2.7152 | 3.0584 | 3.0584 | 2019-12-27 11:00 | 2.5378 | 4.159 | 6.827 | 6.827 | 6.827 | 6.827
2021-10-29 23:00 | 1.6804 | 2.0449 | 2.0008 | 2.152 | 2.0386 | 2.1898 | 1.146 | 1.9652 | 2.425 | 2.425 | 2.7315 | 2.7315 | 2019-12-27 12:00 | 2.6674 | 4.3713 | 7.1755 | 7.1755 | 7.1755 | 7.1755
2021-10-30 | 1.6405 | 1.9964 | 1.9533 | 2.1009 | 1.9902 | 2.1379 | 1.0088 | 1.73 | 2.1347 | 2.1347 | 2.4045 | 2.4045 | 2019-12-27 13:00 | 2.7588 | 4.5212 | 7.4216 | 7.4216 | 7.4216 | 7.4216
2021-10-30 01:00 | 1.4387 | 1.7507 | 1.713 | 1.8425 | 1.7453 | 1.8748 | 0.8774 | 1.5046 | 1.8566 | 1.8566 | 2.0912 | 2.0912 | 2019-12-27 14:00 | 2.6902 | 4.4088 | 7.237 | 7.237 | 7.237 | 7.237
2021-10-30 02:00 | 1.4318 | 1.7423 | 1.7048 | 1.8336 | 1.737 | 1.8658 | 0.84879 | 1.4555 | 1.796 | 1.796 | 2.0231 | 2.0231 | 2019-12-27 15:00 | 2.8198 | 4.6211 | 7.5856 | 7.5856 | 7.5856 | 7.5856
2021-10-30 03:00 | 1.4347 | 1.7458 | 1.7082 | 1.8373 | 1.7404 | 1.8696 | 0.77736 | 1.3331 | 1.6449 | 1.6449 | 1.8528 | 1.8528 | 2019-12-27 16:00 | 2.7131 | 4.4462 | 7.2986 | 7.2986 | 7.2986 | 7.2986
2021-10-30 04:00 | 1.4261 | 1.7354 | 1.698 | 1.8263 | 1.73 | 1.8584 | 0.75461 | 1.294 | 1.5968 | 1.5968 | 1.7986 | 1.7986 | 2019-12-27 17:00 | 2.5302 | 4.1465 | 6.8065 | 6.8065 | 6.8065 | 6.8065
2021-10-30 05:00 | 1.5118 | 1.8397 | 1.8 | 1.9361 | 1.8341 | 1.9701 | 0.7259 | 1.2448 | 1.536 | 1.536 | 1.7301 | 1.7301 | 2019-12-27 18:00 | 2.1491 | 3.522 | 5.7814 | 5.7814 | 5.7814 | 5.7814
2021-10-30 06:00 | 1.6404 | 1.9962 | 1.9532 | 2.1008 | 1.9901 | 2.1377 | 0.78591 | 1.3477 | 1.663 | 1.663 | 1.8732 | 1.8732 | 2019-12-27 19:00 | 2.0729 | 3.3971 | 5.5764 | 5.5764 | 5.5764 | 5.5764
2021-10-30 07:00 | 1.7462 | 2.1249 | 2.0791 | 2.2362 | 2.1184 | 2.2755 | 0.92023 | 1.5781 | 1.9472 | 1.9472 | 2.1933 | 2.1933 | 2019-12-27 20:00 | 2.111 | 3.4596 | 5.6789 | 5.6789 | 5.6789 | 5.6789
2021-10-30 08:00 | 1.7862 | 2.1736 | 2.1267 | 2.2875 | 2.1669 | 2.3276 | 1.026 | 1.7594 | 2.171 | 2.171 | 2.4454 | 2.4454 | 2019-12-27 21:00 | 2.1186 | 3.4721 | 5.6994 | 5.6994 | 5.6994 | 5.6994
2021-10-30 09:00 | 1.7033 | 2.0727 | 2.028 | 2.1813 | 2.0663 | 2.2196 | 1.146 | 1.9652 | 2.425 | 2.425 | 2.7315 | 2.7315 | 2019-12-27 22:00 | 1.9586 | 3.2098 | 5.2689 | 5.2689 | 5.2689 | 5.2689
2021-10-30 10:00 | 1.6661 | 2.0275 | 1.9838 | 2.1337 | 2.0213 | 2.1712 | 1.2918 | 2.2152 | 2.7334 | 2.7334 | 3.0789 | 3.0789 | 2019-12-27 23:00 | 1.8214 | 2.985 | 4.8999 | 4.8999 | 4.8999 | 4.8999
2021-10-30 11:00 | 1.609 | 1.958 | 1.9157 | 2.0605 | 1.9519 | 2.0967 | 1.2803 | 2.1956 | 2.7092 | 2.7092 | 3.0516 | 3.0516 | 2019-12-28 | 1.6766 | 2.7477 | 4.5103 | 4.5103 | 4.5103 | 4.5103
2021-10-30 12:00 | 1.5661 | 1.9058 | 1.8647 | 2.0056 | 1.8999 | 2.0409 | 1.266 | 2.1711 | 2.679 | 2.679 | 3.0176 | 3.0176 | 2019-12-28 01:00 | 1.6233 | 2.6602 | 4.3668 | 4.3668 | 4.3668 | 4.3668
2021-10-30 13:00 | 1.7576 | 2.1388 | 2.0927 | 2.2509 | 2.1322 | 2.2904 | 1.4118 | 2.421 | 2.9874 | 2.9874 | 3.3649 | 3.3649 | 2019-12-28 02:00 | 1.6309 | 2.6727 | 4.3873 | 4.3873 | 4.3873 | 4.3873
2021-10-30 14:00 | 1.7404 | 2.1179 | 2.0723 | 2.2289 | 2.1114 | 2.2681 | 1.3175 | 2.2593 | 2.7878 | 2.7878 | 3.1402 | 3.1402 | 2019-12-28 03:00 | 1.5623 | 2.5603 | 4.2028 | 4.2028 | 4.2028 | 4.2028
2021-10-30 15:00 | 1.5118 | 1.8397 | 1.8 | 1.9361 | 1.8341 | 1.9701 | 1.246 | 2.1367 | 2.6366 | 2.6366 | 2.9699 | 2.9699 | 2019-12-28 04:00 | 1.669 | 2.7352 | 4.4898 | 4.4898 | 4.4898 | 4.4898
2021-10-30 16:00 | 1.5661 | 1.9058 | 1.8647 | 2.0056 | 1.8999 | 2.0409 | 1.286 | 2.2054 | 2.7213 | 2.7213 | 3.0652 | 3.0652 | 2019-12-28 05:00 | 1.5852 | 2.5978 | 4.2643 | 4.2643 | 4.2643 | 4.2643
2021-10-30 17:00 | 1.8484 | 2.2493 | 2.2008 | 2.3672 | 2.2424 | 2.4087 | 1.4261 | 2.4455 | 3.0176 | 3.0176 | 3.399 | 3.399 | 2019-12-28 06:00 | 1.7681 | 2.8975 | 4.7564 | 4.7564 | 4.7564 | 4.7564
2021-10-30 18:00 | 1.8948 | 2.3057 | 2.256 | 2.4265 | 2.2986 | 2.4692 | 1.4318 | 2.4553 | 3.0297 | 3.0297 | 3.4126 | 3.4126 | 2019-12-28 07:00 | 2.0196 | 3.3097 | 5.4329 | 5.4329 | 5.4329 | 5.4329
2021-10-30 19:00 | 1.9634 | 2.3892 | 2.3377 | 2.5144 | 2.3818 | 2.5585 | 1.4747 | 2.5288 | 3.1204 | 3.1204 | 3.5148 | 3.5148 | 2019-12-28 08:00 | 2.172 | 3.5595 | 5.8429 | 5.8429 | 5.8429 | 5.8429
2021-10-30 20:00 | 2.0262 | 2.4657 | 2.4125 | 2.5949 | 2.4581 | 2.6405 | 1.5318 | 2.6268 | 3.2414 | 3.2414 | 3.651 | 3.651 | 2019-12-28 09:00 | 2.3092 | 3.7843 | 6.212 | 6.212 | 6.212 | 6.212
2021-10-30 21:00 | 1.9376 | 2.3579 | 2.307 | 2.4814 | 2.3506 | 2.525 | 1.5461 | 2.6513 | 3.2716 | 3.2716 | 3.6851 | 3.6851 | 2019-12-28 10:00 | 2.5073 | 4.109 | 6.745 | 6.745 | 6.745 | 6.745
2021-10-30 22:00 | 1.8633 | 2.2675 | 2.2186 | 2.3863 | 2.2605 | 2.4282 | 1.2432 | 2.1318 | 2.6306 | 2.6306 | 2.9631 | 2.9631 | 2019-12-28 11:00 | 2.5683 | 4.2089 | 6.909 | 6.909 | 6.909 | 6.909
2021-10-30 23:00 | 1.749 | 2.1284 | 2.0825 | 2.2399 | 2.1218 | 2.2792 | 1.1093 | 1.9023 | 2.3474 | 2.3474 | 2.6441 | 2.6441 | 2019-12-28 12:00 | 2.6521 | 4.3463 | 7.1345 | 7.1345 | 7.1345 | 7.1345
2021-10-31 | 1.7147 | 2.0866 | 2.0416 | 2.196 | 2.0802 | 2.2345 | 1.0688 | 1.8329 | 2.2617 | 2.2617 | 2.5475 | 2.5475 | 2019-12-28 13:00 | 2.6826 | 4.3963 | 7.2165 | 7.2165 | 7.2165 | 7.2165
2021-10-31 01:00 | 1.5919 | 1.9372 | 1.8954 | 2.0387 | 1.9312 | 2.0745 | 0.94596 | 1.6222 | 2.0017 | 2.0017 | 2.2546 | 2.2546 | 2019-12-28 14:00 | 2.7207 | 4.4587 | 7.3191 | 7.3191 | 7.3191 | 7.3191
2021-10-31 02:00 | 1.5139 | 1.8423 | 1.8026 | 1.9388 | 1.8366 | 1.9729 | 0.87171 | 1.4948 | 1.8445 | 1.8445 | 2.0777 | 2.0777 | 2019-12-28 15:00 | 2.8426 | 4.6586 | 7.6471 | 7.6471 | 7.6471 | 7.6471
2021-10-31 03:00 | 1.5147 | 1.8432 | 1.8034 | 1.9398 | 1.8375 | 1.9738 | 0.90309 | 1.5487 | 1.9109 | 1.9109 | 2.1525 | 2.1525 | 2019-12-28 16:00 | 2.7817 | 4.5586 | 7.4831 | 7.4831 | 7.4831 | 7.4831
2021-10-31 04:00 | 1.4632 | 1.7806 | 1.7422 | 1.8739 | 1.7751 | 1.9068 | 0.77748 | 1.3333 | 1.6452 | 1.6452 | 1.8531 | 1.8531 | 2019-12-28 17:00 | 2.6292 | 4.3088 | 7.073 | 7.073 | 7.073 | 7.073
2021-10-31 05:00 | 1.5453 | 1.8805 | 1.84 | 1.979 | 1.8747 | 2.0138 | 0.77734 | 1.333 | 1.6449 | 1.6449 | 1.8528 | 1.8528 | 2019-12-28 18:00 | 2.2406 | 3.6719 | 6.0275 | 6.0275 | 6.0275 | 6.0275
2021-10-31 06:00 | 1.669 | 2.031 | 1.9872 | 2.1374 | 2.0247 | 2.175 | 0.82307 | 1.4114 | 1.7416 | 1.7416 | 1.9617 | 1.9617 | 2019-12-28 19:00 | 2.1491 | 3.522 | 5.7814 | 5.7814 | 5.7814 | 5.7814
2021-10-31 07:00 | 1.7947 | 2.184 | 2.1369 | 2.2984 | 2.1773 | 2.3388 | 0.86879 | 1.4898 | 1.8384 | 1.8384 | 2.0707 | 2.0707 | 2019-12-28 20:00 | 2.1186 | 3.4721 | 5.6994 | 5.6994 | 5.6994 | 5.6994
2021-10-31 08:00 | 1.8376 | 2.2362 | 2.188 | 2.3533 | 2.2293 | 2.3947 | 0.99378 | 1.7042 | 2.1028 | 2.1028 | 2.3686 | 2.3686 | 2019-12-28 21:00 | 2.1339 | 3.497 | 5.7404 | 5.7404 | 5.7404 | 5.7404
2021-10-31 09:00 | 1.7404 | 2.1179 | 2.0723 | 2.2289 | 2.1114 | 2.2681 | 1.2403 | 2.1269 | 2.6245 | 2.6245 | 2.9562 | 2.9562 | 2019-12-28 22:00 | 1.8824 | 3.0849 | 5.0639 | 5.0639 | 5.0639 | 5.0639
2021-10-31 10:00 | 1.6261 | 1.9788 | 1.9361 | 2.0825 | 1.9727 | 2.1191 | 1.3032 | 2.2348 | 2.7576 | 2.7576 | 3.1061 | 3.1061 | 2019-12-28 23:00 | 1.7833 | 2.9225 | 4.7974 | 4.7974 | 4.7974 | 4.7974
2021-10-31 11:00 | 1.5547 | 1.8919 | 1.8511 | 1.991 | 1.8861 | 2.026 | 1.3318 | 2.2838 | 2.818 | 2.818 | 3.1742 | 3.1742 | 2019-12-29 | 1.6538 | 2.7102 | 4.4488 | 4.4488 | 4.4488 | 4.4488
2021-10-31 12:00 | 1.4432 | 1.7563 | 1.7184 | 1.8483 | 1.7508 | 1.8807 | 1.3232 | 2.2691 | 2.7999 | 2.7999 | 3.1538 | 3.1538 | 2019-12-29 01:00 | 1.5852 | 2.5978 | 4.2643 | 4.2643 | 4.2643 | 4.2643
2021-10-31 13:00 | 1.3403 | 1.6311 | 1.5959 | 1.7165 | 1.626 | 1.7467 | 1.3375 | 2.2936 | 2.8301 | 2.8301 | 3.1878 | 3.1878 | 2019-12-29 02:00 | 1.5471 | 2.5353 | 4.1618 | 4.1618 | 4.1618 | 4.1618
2021-10-31 14:00 | 1.2975 | 1.5789 | 1.5448 | 1.6616 | 1.574 | 1.6908 | 1.3232 | 2.2691 | 2.7999 | 2.7999 | 3.1538 | 3.1538 | 2019-12-29 03:00 | 1.6385 | 2.6852 | 4.4078 | 4.4078 | 4.4078 | 4.4078
2021-10-31 15:00 | 1.3593 | 1.6541 | 1.6184 | 1.7407 | 1.649 | 1.7713 | 1.2489 | 2.1416 | 2.6427 | 2.6427 | 2.9767 | 2.9767 | 2019-12-29 04:00 | 1.5623 | 2.5603 | 4.2028 | 4.2028 | 4.2028 | 4.2028
2021-10-31 16:00 | 1.4575 | 1.7736 | 1.7354 | 1.8666 | 1.7682 | 1.8994 | 1.3918 | 2.3867 | 2.945 | 2.945 | 3.3173 | 3.3173 | 2019-12-29 05:00 | 1.6766 | 2.7477 | 4.5103 | 4.5103 | 4.5103 | 4.5103
2021-10-31 17:00 | 1.7233 | 2.0971 | 2.0518 | 2.2069 | 2.0906 | 2.2457 | 1.3603 | 2.3328 | 2.8785 | 2.8785 | 3.2423 | 3.2423 | 2019-12-29 06:00 | 1.7986 | 2.9475 | 4.8384 | 4.8384 | 4.8384 | 4.8384
2021-10-31 18:00 | 1.9262 | 2.344 | 2.2934 | 2.4668 | 2.3368 | 2.5101 | 1.5118 | 2.5925 | 3.199 | 3.199 | 3.6034 | 3.6034 | 2019-12-29 07:00 | 1.9357 | 3.1723 | 5.2074 | 5.2074 | 5.2074 | 5.2074
2021-10-31 19:00 | 2.0234 | 2.4622 | 2.4091 | 2.5912 | 2.4547 | 2.6368 | 1.5347 | 2.6317 | 3.2474 | 3.2474 | 3.6578 | 3.6578 | 2019-12-29 08:00 | 2.1034 | 3.4471 | 5.6584 | 5.6584 | 5.6584 | 5.6584
2021-10-31 20:00 | 2.1348 | 2.5979 | 2.5418 | 2.734 | 2.5899 | 2.782 | 1.4747 | 2.5288 | 3.1204 | 3.1204 | 3.5148 | 3.5148 | 2019-12-29 09:00 | 2.3015 | 3.7718 | 6.1915 | 6.1915 | 6.1915 | 6.1915
2021-10-31 21:00 | 1.9834 | 2.4136 | 2.3615 | 2.54 | 2.4061 | 2.5846 | 1.4747 | 2.5288 | 3.1204 | 3.1204 | 3.5148 | 3.5148 | 2019-12-29 10:00 | 2.3778 | 3.8967 | 6.3965 | 6.3965 | 6.3965 | 6.3965
2021-10-31 22:00 | 1.8605 | 2.264 | 2.2152 | 2.3826 | 2.257 | 2.4245 | 1.2946 | 2.2201 | 2.7394 | 2.7394 | 3.0857 | 3.0857 | 2019-12-29 11:00 | 2.4768 | 4.0591 | 6.663 | 6.663 | 6.663 | 6.663
2021-10-31 23:00 | 1.6804 | 2.0449 | 2.0008 | 2.152 | 2.0386 | 2.1898 | 1.072 | 1.8383 | 2.2683 | 2.2683 | 2.555 | 2.555 | 2019-12-29 12:00 | 2.614 | 4.2839 | 7.032 | 7.032 | 7.032 | 7.032
2021-11-01 | 1.5833 | 1.9267 | 1.8851 | 2.0276 | 1.9207 | 2.0632 | 0.93741 | 1.6075 | 1.9836 | 1.9836 | 2.2343 | 2.2343 | 2019-12-29 13:00 | 2.6597 | 4.3588 | 7.155 | 7.155 | 7.155 | 7.155
2021-11-01 01:00 | 1.4689 | 1.7876 | 1.749 | 1.8812 | 1.7821 | 1.9143 | 0.83751 | 1.4362 | 1.7722 | 1.7722 | 1.9962 | 1.9962 | 2019-12-29 14:00 | 2.6216 | 4.2964 | 7.0525 | 7.0525 | 7.0525 | 7.0525
2021-11-01 02:00 | 1.4318 | 1.7423 | 1.7048 | 1.8336 | 1.737 | 1.8658 | 0.75162 | 1.2889 | 1.5904 | 1.5904 | 1.7915 | 1.7915 | 2019-12-29 15:00 | 2.6064 | 4.2714 | 7.0115 | 7.0115 | 7.0115 | 7.0115
2021-11-01 03:00 | 1.4175 | 1.725 | 1.6878 | 1.8153 | 1.7196 | 1.8472 | 0.75162 | 1.2889 | 1.5904 | 1.5904 | 1.7915 | 1.7915 | 2019-12-29 16:00 | 2.5759 | 4.2214 | 6.9295 | 6.9295 | 6.9295 | 6.9295
2021-11-01 04:00 | 1.4602 | 1.777 | 1.7386 | 1.8701 | 1.7715 | 1.9029 | 0.76877 | 1.3183 | 1.6267 | 1.6267 | 1.8323 | 1.8323 | 2019-12-29 17:00 | 2.4768 | 4.0591 | 6.663 | 6.663 | 6.663 | 6.663
2021-11-01 05:00 | 1.5604 | 1.8988 | 1.8579 | 1.9983 | 1.893 | 2.0334 | 0.77162 | 1.3232 | 1.6328 | 1.6328 | 1.8391 | 1.8391 | 2019-12-29 18:00 | 2.2863 | 3.7468 | 6.1505 | 6.1505 | 6.1505 | 6.1505
2021-11-01 06:00 | 2.0538 | 2.4993 | 2.4454 | 2.6302 | 2.4916 | 2.6764 | 0.90595 | 1.5536 | 1.917 | 1.917 | 2.1593 | 2.1593 | 2019-12-29 19:00 | 2.1491 | 3.522 | 5.7814 | 5.7814 | 5.7814 | 5.7814
2021-11-01 07:00 | 2.3377 | 2.8448 | 2.7834 | 2.9938 | 2.836 | 3.0464 | 1.1203 | 1.9211 | 2.3705 | 2.3705 | 2.6702 | 2.6702 | 2019-12-29 20:00 | 2.111 | 3.4596 | 5.6789 | 5.6789 | 5.6789 | 5.6789
2021-11-01 08:00 | 2.3292 | 2.8344 | 2.7732 | 2.9828 | 2.8256 | 3.0353 | 1.1289 | 1.9358 | 2.3887 | 2.3887 | 2.6906 | 2.6906 | 2019-12-29 21:00 | 2.111 | 3.4596 | 5.6789 | 5.6789 | 5.6789 | 5.6789
2021-11-01 09:00 | 2.2091 | 2.6883 | 2.6303 | 2.8291 | 2.68 | 2.8788 | 1.1118 | 1.9066 | 2.3526 | 2.3526 | 2.6499 | 2.6499 | 2019-12-29 22:00 | 2.0501 | 3.3597 | 5.5149 | 5.5149 | 5.5149 | 5.5149
2021-11-01 10:00 | 2.0034 | 2.4379 | 2.3853 | 2.5656 | 2.4304 | 2.6107 | 1.1146 | 1.9113 | 2.3584 | 2.3584 | 2.6565 | 2.6565 | 2019-12-29 23:00 | 1.7986 | 2.9475 | 4.8384 | 4.8384 | 4.8384 | 4.8384
2021-11-01 11:00 | 1.9805 | 2.4101 | 2.3581 | 2.5363 | 2.4026 | 2.5809 | 1.1746 | 2.0142 | 2.4854 | 2.4854 | 2.7996 | 2.7996 | 2019-12-30 | 1.669 | 2.7352 | 4.4898 | 4.4898 | 4.4898 | 4.4898
2021-11-01 12:00 | 1.8576 | 2.2605 | 2.2118 | 2.379 | 2.2536 | 2.4208 | 1.1746 | 2.0142 | 2.4854 | 2.4854 | 2.7996 | 2.7996 | 2019-12-30 01:00 | 1.6461 | 2.6977 | 4.4283 | 4.4283 | 4.4283 | 4.4283
2021-11-01 13:00 | 1.7633 | 2.1458 | 2.0995 | 2.2582 | 2.1392 | 2.2979 | 1.2346 | 2.1171 | 2.6124 | 2.6124 | 2.9426 | 2.9426 | 2019-12-30 02:00 | 1.5547 | 2.5478 | 4.1823 | 4.1823 | 4.1823 | 4.1823
2021-11-01 14:00 | 1.709 | 2.0797 | 2.0348 | 2.1886 | 2.0733 | 2.2271 | 1.1403 | 1.9554 | 2.4129 | 2.4129 | 2.7178 | 2.7178 | 2019-12-30 03:00 | 1.5547 | 2.5478 | 4.1823 | 4.1823 | 4.1823 | 4.1823
2021-11-01 15:00 | 1.7776 | 2.1632 | 2.1165 | 2.2765 | 2.1565 | 2.3165 | 1.1603 | 1.9897 | 2.4552 | 2.4552 | 2.7655 | 2.7655 | 2019-12-30 04:00 | 1.6461 | 2.6977 | 4.4283 | 4.4283 | 4.4283 | 4.4283
2021-11-01 16:00 | 1.9234 | 2.3405 | 2.29 | 2.4631 | 2.3333 | 2.5064 | 1.2746 | 2.1858 | 2.6971 | 2.6971 | 3.038 | 3.038 | 2019-12-30 05:00 | 1.6461 | 2.6977 | 4.4283 | 4.4283 | 4.4283 | 4.4283
2021-11-01 17:00 | 2.072 | 2.5214 | 2.467 | 2.6535 | 2.5136 | 2.7001 | 1.286 | 2.2054 | 2.7213 | 2.7213 | 3.0652 | 3.0652 | 2019-12-30 06:00 | 1.9662 | 3.2223 | 5.2894 | 5.2894 | 5.2894 | 5.2894
2021-11-01 18:00 | 2.3349 | 2.8413 | 2.78 | 2.9902 | 2.8326 | 3.0427 | 1.4527 | 2.4912 | 3.0739 | 3.0739 | 3.4625 | 3.4625 | 2019-12-30 07:00 | 1.9738 | 3.2348 | 5.3099 | 5.3099 | 5.3099 | 5.3099
2021-11-01 19:00 | 2.2606 | 2.7509 | 2.6916 | 2.895 | 2.7424 | 2.9459 | 1.5747 | 2.7003 | 3.3321 | 3.3321 | 3.7532 | 3.7532 | 2019-12-30 08:00 | 2.2482 | 3.6844 | 6.048 | 6.048 | 6.048 | 6.048
2021-11-01 20:00 | 2.2149 | 2.6953 | 2.6371 | 2.8364 | 2.6869 | 2.8863 | 1.5633 | 2.6807 | 3.3079 | 3.3079 | 3.726 | 3.726 | 2019-12-30 09:00 | 2.3701 | 3.8842 | 6.376 | 6.376 | 6.376 | 6.376
2021-11-01 21:00 | 2.1063 | 2.5631 | 2.5078 | 2.6974 | 2.5552 | 2.7448 | 1.4318 | 2.4553 | 3.0297 | 3.0297 | 3.4126 | 3.4126 | 2019-12-30 10:00 | 2.6445 | 4.3338 | 7.114 | 7.114 | 7.114 | 7.114
2021-11-01 22:00 | 1.8176 | 2.2118 | 2.1641 | 2.3277 | 2.205 | 2.3686 | 1.2403 | 2.1269 | 2.6245 | 2.6245 | 2.9562 | 2.9562 | 2019-12-30 11:00 | 2.774 | 4.5461 | 7.4626 | 7.4626 | 7.4626 | 7.4626
2021-11-01 23:00 | 1.6719 | 2.0345 | 1.9906 | 2.1411 | 2.0282 | 2.1787 | 1.0591 | 1.8162 | 2.2411 | 2.2411 | 2.5243 | 2.5243 | 2019-12-30 12:00 | 2.8122 | 4.6086 | 7.5651 | 7.5651 | 7.5651 | 7.5651
2021-11-02 | 1.5604 | 1.8988 | 1.8579 | 1.9983 | 1.893 | 2.0334 | 0.89001 | 1.5262 | 1.8833 | 1.8833 | 2.1213 | 2.1213 | 2019-12-30 13:00 | 2.8884 | 4.7335 | 7.7701 | 7.7701 | 7.7701 | 7.7701
2021-11-02 01:00 | 1.4289 | 1.7389 | 1.7014 | 1.83 | 1.7335 | 1.8621 | 0.84307 | 1.4457 | 1.7839 | 1.7839 | 2.0094 | 2.0094 | 2019-12-30 14:00 | 2.8198 | 4.6211 | 7.5856 | 7.5856 | 7.5856 | 7.5856
2021-11-02 02:00 | 1.3775 | 1.6763 | 1.6401 | 1.7641 | 1.6711 | 1.7951 | 0.76591 | 1.3134 | 1.6207 | 1.6207 | 1.8255 | 1.8255 | 2019-12-30 15:00 | 2.7131 | 4.4462 | 7.2986 | 7.2986 | 7.2986 | 7.2986
2021-11-02 03:00 | 1.4118 | 1.718 | 1.6809 | 1.808 | 1.7127 | 1.8398 | 0.7406 | 1.27 | 1.5671 | 1.5671 | 1.7652 | 1.7652 | 2019-12-30 16:00 | 2.5911 | 4.2464 | 6.9705 | 6.9705 | 6.9705 | 6.9705
2021-11-02 04:00 | 1.4489 | 1.7632 | 1.7252 | 1.8556 | 1.7578 | 1.8882 | 0.7116 | 1.2203 | 1.5058 | 1.5058 | 1.6961 | 1.6961 | 2019-12-30 17:00 | 2.553 | 4.184 | 6.868 | 6.868 | 6.868 | 6.868
2021-11-02 05:00 | 1.5175 | 1.8467 | 1.8068 | 1.9434 | 1.841 | 1.9776 | 0.77162 | 1.3232 | 1.6328 | 1.6328 | 1.8391 | 1.8391 | 2019-12-30 18:00 | 2.1491 | 3.522 | 5.7814 | 5.7814 | 5.7814 | 5.7814
2021-11-02 06:00 | 1.9859 | 2.4167 | 2.3645 | 2.5433 | 2.4092 | 2.5879 | 0.88308 | 1.5143 | 1.8686 | 1.8686 | 2.1048 | 2.1048 | 2019-12-30 19:00 | 2.0196 | 3.3097 | 5.4329 | 5.4329 | 5.4329 | 5.4329
2021-11-02 07:00 | 2.212 | 2.6918 | 2.6337 | 2.8328 | 2.6835 | 2.8826 | 1.0917 | 1.8721 | 2.3101 | 2.3101 | 2.602 | 2.602 | 2019-12-30 20:00 | 1.9891 | 3.2597 | 5.3509 | 5.3509 | 5.3509 | 5.3509
2021-11-02 08:00 | 2.3349 | 2.8413 | 2.78 | 2.9902 | 2.8326 | 3.0427 | 1.2117 | 2.0779 | 2.5641 | 2.5641 | 2.8881 | 2.8881 | 2019-12-30 21:00 | 1.9891 | 3.2597 | 5.3509 | 5.3509 | 5.3509 | 5.3509
2021-11-02 09:00 | 2.0548 | 2.5005 | 2.4466 | 2.6315 | 2.4928 | 2.6777 | 1.1231 | 1.926 | 2.3766 | 2.3766 | 2.677 | 2.677 | 2019-12-30 22:00 | 1.7376 | 2.8476 | 4.6744 | 4.6744 | 4.6744 | 4.6744
2021-11-02 10:00 | 2.0377 | 2.4796 | 2.4261 | 2.6095 | 2.472 | 2.6554 | 1.266 | 2.1711 | 2.679 | 2.679 | 3.0176 | 3.0176 | 2019-12-30 23:00 | 1.7071 | 2.7976 | 4.5923 | 4.5923 | 4.5923 | 4.5923
2021-11-02 11:00 | 2.0145 | 2.4514 | 2.3986 | 2.5799 | 2.4439 | 2.6252 | 1.2603 | 2.1613 | 2.6669 | 2.6669 | 3.0039 | 3.0039 | 2019-12-31 | 1.5699 | 2.5728 | 4.2233 | 4.2233 | 4.2233 | 4.2233
2021-11-02 12:00 | 2.1063 | 2.5631 | 2.5078 | 2.6974 | 2.5552 | 2.7448 | 1.2432 | 2.1318 | 2.6306 | 2.6306 | 2.9631 | 2.9631 | 2019-12-31 01:00 | 1.4785 | 2.4229 | 3.9773 | 3.9773 | 3.9773 | 3.9773
2021-11-02 13:00 | 1.9805 | 2.4101 | 2.3581 | 2.5363 | 2.4026 | 2.5809 | 1.3175 | 2.2593 | 2.7878 | 2.7878 | 3.1402 | 3.1402 | 2019-12-31 02:00 | 1.448 | 2.373 | 3.8953 | 3.8953 | 3.8953 | 3.8953
2021-11-02 14:00 | 1.9262 | 2.344 | 2.2934 | 2.4668 | 2.3368 | 2.5101 | 1.2117 | 2.0779 | 2.5641 | 2.5641 | 2.8881 | 2.8881 | 2019-12-31 03:00 | 1.4404 | 2.3605 | 3.8748 | 3.8748 | 3.8748 | 3.8748
2021-11-02 15:00 | 2.0091 | 2.4449 | 2.3921 | 2.5729 | 2.4373 | 2.6181 | 1.1746 | 2.0142 | 2.4854 | 2.4854 | 2.7996 | 2.7996 | 2019-12-31 04:00 | 1.4861 | 2.4354 | 3.9978 | 3.9978 | 3.9978 | 3.9978
2021-11-02 16:00 | 1.8833 | 2.2918 | 2.2424 | 2.4119 | 2.2848 | 2.4543 | 1.3203 | 2.2642 | 2.7939 | 2.7939 | 3.147 | 3.147 | 2019-12-31 05:00 | 1.509 | 2.4729 | 4.0593 | 4.0593 | 4.0593 | 4.0593
2021-11-02 17:00 | 2.0863 | 2.5388 | 2.484 | 2.6718 | 2.5309 | 2.7187 | 1.4347 | 2.4602 | 3.0357 | 3.0357 | 3.4194 | 3.4194 | 2019-12-31 06:00 | 1.608 | 2.6353 | 4.3258 | 4.3258 | 4.3258 | 4.3258
2021-11-02 18:00 | 2.4178 | 2.9422 | 2.8787 | 3.0963 | 2.9331 | 3.1507 | 1.5173 | 2.6019 | 3.2106 | 3.2106 | 3.6164 | 3.6164 | 2019-12-31 07:00 | 1.7909 | 2.935 | 4.8179 | 4.8179 | 4.8179 | 4.8179
2021-11-02 19:00 | 2.2663 | 2.7579 | 2.6984 | 2.9023 | 2.7494 | 2.9533 | 1.589 | 2.7248 | 3.3623 | 3.3623 | 3.7873 | 3.7873 | 2019-12-31 08:00 | 1.9891 | 3.2597 | 5.3509 | 5.3509 | 5.3509 | 5.3509
2021-11-02 20:00 | 2.1057 | 2.5624 | 2.5071 | 2.6967 | 2.5545 | 2.744 | 1.5004 | 2.5729 | 3.1748 | 3.1748 | 3.5761 | 3.5761 | 2019-12-31 09:00 | 2.0805 | 3.4096 | 5.5969 | 5.5969 | 5.5969 | 5.5969
2021-11-02 21:00 | 2.0491 | 2.4935 | 2.4398 | 2.6242 | 2.4859 | 2.6703 | 1.4175 | 2.4308 | 2.9995 | 2.9995 | 3.3786 | 3.3786 | 2019-12-31 10:00 | 2.1949 | 3.597 | 5.9044 | 5.9044 | 5.9044 | 5.9044
2021-11-02 22:00 | 1.7976 | 2.1875 | 2.1403 | 2.3021 | 2.1808 | 2.3425 | 1.209 | 2.0733 | 2.5583 | 2.5583 | 2.8817 | 2.8817 | 2019-12-31 11:00 | 2.5607 | 4.1964 | 6.8885 | 6.8885 | 6.8885 | 6.8885
2021-11-02 23:00 | 1.5747 | 1.9162 | 1.8749 | 2.0166 | 1.9103 | 2.0521 | 1.0295 | 1.7654 | 2.1784 | 2.1784 | 2.4537 | 2.4537 | 2019-12-31 12:00 | 2.614 | 4.2839 | 7.032 | 7.032 | 7.032 | 7.032
2021-11-03 | 1.5204 | 1.8502 | 1.8102 | 1.9471 | 1.8445 | 1.9813 | 0.86658 | 1.486 | 1.8337 | 1.8337 | 2.0655 | 2.0655 | 2019-12-31 13:00 | 2.6369 | 4.3213 | 7.0935 | 7.0935 | 7.0935 | 7.0935
2021-11-03 01:00 | 1.3861 | 1.6867 | 1.6503 | 1.7751 | 1.6815 | 1.8063 | 0.77734 | 1.333 | 1.6449 | 1.6449 | 1.8528 | 1.8528 | 2019-12-31 14:00 | 2.6292 | 4.3088 | 7.073 | 7.073 | 7.073 | 7.073
2021-11-03 02:00 | 1.3718 | 1.6693 | 1.6333 | 1.7568 | 1.6642 | 1.7876 | 0.76764 | 1.3164 | 1.6243 | 1.6243 | 1.8296 | 1.8296 | 2019-12-31 15:00 | 2.6674 | 4.3713 | 7.1755 | 7.1755 | 7.1755 | 7.1755
2021-11-03 03:00 | 1.3689 | 1.6658 | 1.6299 | 1.7531 | 1.6607 | 1.7839 | 0.70875 | 1.2154 | 1.4997 | 1.4997 | 1.6893 | 1.6893 | 2019-12-31 16:00 | 2.5607 | 4.1964 | 6.8885 | 6.8885 | 6.8885 | 6.8885
2021-11-03 04:00 | 1.3546 | 1.6484 | 1.6129 | 1.7348 | 1.6434 | 1.7653 | 0.70018 | 1.2007 | 1.4816 | 1.4816 | 1.6688 | 1.6688 | 2019-12-31 17:00 | 2.4006 | 3.9342 | 6.458 | 6.458 | 6.458 | 6.458
2021-11-03 05:00 | 1.4878 | 1.8105 | 1.7715 | 1.9054 | 1.8049 | 1.9388 | 0.76591 | 1.3134 | 1.6207 | 1.6207 | 1.8255 | 1.8255 | 2019-12-31 18:00 | 2.1567 | 3.5345 | 5.8019 | 5.8019 | 5.8019 | 5.8019
2021-11-03 06:00 | 1.9491 | 2.3718 | 2.3207 | 2.4961 | 2.3645 | 2.5399 | 0.9088 | 1.5585 | 1.923 | 1.923 | 2.1661 | 2.1661 | 2019-12-31 19:00 | 1.9967 | 3.2722 | 5.3714 | 5.3714 | 5.3714 | 5.3714
2021-11-03 07:00 | 2.2149 | 2.6953 | 2.6371 | 2.8364 | 2.6869 | 2.8863 | 1.0517 | 1.8035 | 2.2254 | 2.2254 | 2.5067 | 2.5067 | 2019-12-31 20:00 | 1.8443 | 3.0224 | 4.9614 | 4.9614 | 4.9614 | 4.9614
2021-11-03 08:00 | 2.2149 | 2.6953 | 2.6371 | 2.8364 | 2.6869 | 2.8863 | 1.106 | 1.8966 | 2.3403 | 2.3403 | 2.6361 | 2.6361 | 2019-12-31 21:00 | 1.7452 | 2.8601 | 4.6949 | 4.6949 | 4.6949 | 4.6949
2021-11-03 09:00 | 1.9262 | 2.344 | 2.2934 | 2.4668 | 2.3368 | 2.5101 | 1.1574 | 1.9848 | 2.4492 | 2.4492 | 2.7587 | 2.7587 | 2019-12-31 22:00 | 1.6004 | 2.6228 | 4.3053 | 4.3053 | 4.3053 | 4.3053
2021-11-03 10:00 | 1.8948 | 2.3057 | 2.256 | 2.4265 | 2.2986 | 2.4692 | 1.1203 | 1.9211 | 2.3705 | 2.3705 | 2.6702 | 2.6702 | 2019-12-31 23:00 | 1.5318 | 2.5104 | 4.1208 | 4.1208 | 4.1208 | 4.1208
2021-11-03 11:00 | 1.8801 | 2.2879 | 2.2386 | 2.4078 | 2.2809 | 2.4501 | 1.1431 | 1.9603 | 2.4189 | 2.4189 | 2.7246 | 2.7246 | 2020-01-01 | 1.5318 | 2.5104 | 4.1208 | 4.1208 | 4.1208 | 4.1208
2021-11-03 12:00 | 1.9205 | 2.337 | 2.2866 | 2.4595 | 2.3298 | 2.5027 | 1.1746 | 2.0142 | 2.4854 | 2.4854 | 2.7996 | 2.7996 | 2020-01-01 01:00 | 1.4861 | 2.4354 | 3.9978 | 3.9978 | 3.9978 | 3.9978
2021-11-03 13:00 | 1.9862 | 2.417 | 2.3649 | 2.5437 | 2.4096 | 2.5883 | 1.2317 | 2.1122 | 2.6064 | 2.6064 | 2.9358 | 2.9358 | 2020-01-01 02:00 | 1.4251 | 2.3355 | 3.8338 | 3.8338 | 3.8338 | 3.8338
2021-11-03 14:00 | 1.9977 | 2.4309 | 2.3785 | 2.5583 | 2.4235 | 2.6032 | 1.206 | 2.0681 | 2.552 | 2.552 | 2.8745 | 2.8745 | 2020-01-01 03:00 | 1.4251 | 2.3355 | 3.8338 | 3.8338 | 3.8338 | 3.8338
2021-11-03 15:00 | 1.9777 | 2.4066 | 2.3547 | 2.5327 | 2.3992 | 2.5772 | 1.2089 | 2.073 | 2.558 | 2.558 | 2.8813 | 2.8813 | 2020-01-01 04:00 | 1.4556 | 2.3855 | 3.9158 | 3.9158 | 3.9158 | 3.9158
2021-11-03 16:00 | 1.9805 | 2.4101 | 2.3581 | 2.5363 | 2.4026 | 2.5809 | 1.2689 | 2.176 | 2.685 | 2.685 | 3.0244 | 3.0244 | 2020-01-01 05:00 | 1.5013 | 2.4604 | 4.0388 | 4.0388 | 4.0388 | 4.0388
2021-11-03 17:00 | 2.1234 | 2.584 | 2.5282 | 2.7193 | 2.576 | 2.7671 | 1.3546 | 2.323 | 2.8664 | 2.8664 | 3.2287 | 3.2287 | 2020-01-01 06:00 | 1.6004 | 2.6228 | 4.3053 | 4.3053 | 4.3053 | 4.3053
2021-11-03 18:00 | 2.3492 | 2.8587 | 2.797 | 3.0085 | 2.8499 | 3.0613 | 1.4489 | 2.4847 | 3.066 | 3.066 | 3.4535 | 3.4535 | 2020-01-01 07:00 | 1.7833 | 2.9225 | 4.7974 | 4.7974 | 4.7974 | 4.7974
2021-11-03 19:00 | 2.1748 | 2.6466 | 2.5895 | 2.7852 | 2.6384 | 2.8341 | 1.5375 | 2.6366 | 3.2534 | 3.2534 | 3.6647 | 3.6647 | 2020-01-01 08:00 | 1.9662 | 3.2223 | 5.2894 | 5.2894 | 5.2894 | 5.2894
2021-11-03 20:00 | 2.1348 | 2.5979 | 2.5418 | 2.734 | 2.5899 | 2.782 | 1.549 | 2.6562 | 3.2776 | 3.2776 | 3.6919 | 3.6919 | 2020-01-01 09:00 | 2.0577 | 3.3721 | 5.5354 | 5.5354 | 5.5354 | 5.5354
2021-11-03 21:00 | 1.9662 | 2.3927 | 2.3411 | 2.518 | 2.3853 | 2.5623 | 1.4718 | 2.5239 | 3.1144 | 3.1144 | 3.508 | 3.508 | 2020-01-01 10:00 | 2.1872 | 3.5845 | 5.8839 | 5.8839 | 5.8839 | 5.8839
2021-11-03 22:00 | 1.7147 | 2.0866 | 2.0416 | 2.196 | 2.0802 | 2.2345 | 1.2209 | 2.0937 | 2.5835 | 2.5835 | 2.9101 | 2.9101 | 2020-01-01 11:00 | 2.1796 | 3.572 | 5.8634 | 5.8634 | 5.8634 | 5.8634
2021-11-03 23:00 | 1.5433 | 1.878 | 1.8375 | 1.9764 | 1.8722 | 2.0111 | 1.0317 | 1.7692 | 2.1831 | 2.1831 | 2.459 | 2.459 | 2020-01-01 12:00 | 2.3244 | 3.8093 | 6.253 | 6.253 | 6.253 | 6.253
2021-11-04 | 1.489 | 1.8119 | 1.7728 | 1.9068 | 1.8063 | 1.9403 | 0.89737 | 1.5388 | 1.8988 | 1.8988 | 2.1388 | 2.1388 | 2020-01-01 13:00 | 2.3397 | 3.8343 | 6.294 | 6.294 | 6.294 | 6.294
2021-11-04 01:00 | 1.3804 | 1.6797 | 1.6435 | 1.7677 | 1.6746 | 1.7988 | 0.81164 | 1.3918 | 1.7174 | 1.7174 | 1.9345 | 1.9345 | 2020-01-01 14:00 | 2.2939 | 3.7593 | 6.171 | 6.171 | 6.171 | 6.171
2021-11-04 02:00 | 1.3318 | 1.6206 | 1.5857 | 1.7055 | 1.6156 | 1.7355 | 0.73161 | 1.2546 | 1.5481 | 1.5481 | 1.7438 | 1.7438 | 2020-01-01 15:00 | 2.3625 | 3.8717 | 6.3555 | 6.3555 | 6.3555 | 6.3555
2021-11-04 03:00 | 1.3375 | 1.6276 | 1.5925 | 1.7128 | 1.6226 | 1.7429 | 0.68303 | 1.1713 | 1.4453 | 1.4453 | 1.628 | 1.628 | 2020-01-01 16:00 | 2.2863 | 3.7468 | 6.1505 | 6.1505 | 6.1505 | 6.1505
2021-11-04 04:00 | 1.2803 | 1.558 | 1.5244 | 1.6396 | 1.5532 | 1.6685 | 0.69732 | 1.1958 | 1.4755 | 1.4755 | 1.662 | 1.662 | 2020-01-01 17:00 | 2.2711 | 3.7218 | 6.1095 | 6.1095 | 6.1095 | 6.1095
2021-11-04 05:00 | 1.4861 | 1.8084 | 1.7694 | 1.9032 | 1.8029 | 1.9366 | 0.76877 | 1.3183 | 1.6267 | 1.6267 | 1.8323 | 1.8323 | 2020-01-01 18:00 | 2.0729 | 3.3971 | 5.5764 | 5.5764 | 5.5764 | 5.5764
2021-11-04 06:00 | 1.7062 | 2.0762 | 2.0314 | 2.185 | 2.0698 | 2.2234 | 0.81047 | 1.3898 | 1.715 | 1.715 | 1.9317 | 1.9317 | 2020-01-01 19:00 | 1.9281 | 3.1598 | 5.1869 | 5.1869 | 5.1869 | 5.1869
2021-11-04 07:00 | 2.0834 | 2.5353 | 2.4806 | 2.6681 | 2.5275 | 2.715 | 1.1517 | 1.975 | 2.4371 | 2.4371 | 2.7451 | 2.7451 | 2020-01-01 20:00 | 1.89 | 3.0974 | 5.0844 | 5.0844 | 5.0844 | 5.0844
2021-11-04 08:00 | 2.1891 | 2.664 | 2.6065 | 2.8035 | 2.6557 | 2.8528 | 1.2117 | 2.0779 | 2.5641 | 2.5641 | 2.8881 | 2.8881 | 2020-01-01 21:00 | 1.8138 | 2.9725 | 4.8794 | 4.8794 | 4.8794 | 4.8794
2021-11-04 09:00 | 2.2091 | 2.6883 | 2.6303 | 2.8291 | 2.68 | 2.8788 | 1.2085 | 2.0723 | 2.5571 | 2.5571 | 2.8803 | 2.8803 | 2020-01-01 22:00 | 1.7223 | 2.8226 | 4.6333 | 4.6333 | 4.6333 | 4.6333
2021-11-04 10:00 | 2.292 | 2.7892 | 2.729 | 2.9353 | 2.7806 | 2.9868 | 1.3346 | 2.2887 | 2.8241 | 2.8241 | 3.181 | 3.181 | 2020-01-01 23:00 | 1.6233 | 2.6602 | 4.3668 | 4.3668 | 4.3668 | 4.3668
2021-11-04 11:00 | 2.2463 | 2.7335 | 2.6745 | 2.8767 | 2.7251 | 2.9272 | 1.3746 | 2.3573 | 2.9088 | 2.9088 | 3.2764 | 3.2764 | 2020-01-02 | 1.4632 | 2.398 | 3.9363 | 3.9363 | 3.9363 | 3.9363
2021-11-04 12:00 | 2.2434 | 2.73 | 2.6711 | 2.873 | 2.7216 | 2.9235 | 1.3632 | 2.3377 | 2.8846 | 2.8846 | 3.2491 | 3.2491 | 2020-01-02 01:00 | 1.5623 | 2.5603 | 4.2028 | 4.2028 | 4.2028 | 4.2028
2021-11-04 13:00 | 2.1577 | 2.6257 | 2.5691 | 2.7632 | 2.6176 | 2.8118 | 1.3432 | 2.3034 | 2.8422 | 2.8422 | 3.2015 | 3.2015 | 2020-01-02 02:00 | 1.4251 | 2.3355 | 3.8338 | 3.8338 | 3.8338 | 3.8338
2021-11-04 14:00 | 2.1777 | 2.65 | 2.5929 | 2.7889 | 2.6419 | 2.8379 | 1.3203 | 2.2642 | 2.7939 | 2.7939 | 3.147 | 3.147 | 2020-01-02 03:00 | 1.448 | 2.373 | 3.8953 | 3.8953 | 3.8953 | 3.8953
2021-11-04 15:00 | 2.0548 | 2.5005 | 2.4466 | 2.6315 | 2.4928 | 2.6777 | 1.2403 | 2.1269 | 2.6245 | 2.6245 | 2.9562 | 2.9562 | 2020-01-02 04:00 | 1.4327 | 2.348 | 3.8543 | 3.8543 | 3.8543 | 3.8543
2021-11-04 16:00 | 2.1777 | 2.65 | 2.5929 | 2.7889 | 2.6419 | 2.8379 | 1.3756 | 2.359 | 2.9109 | 2.9109 | 3.2788 | 3.2788 | 2020-01-02 05:00 | 1.509 | 2.4729 | 4.0593 | 4.0593 | 4.0593 | 4.0593
2021-11-04 17:00 | 2.3357 | 2.8423 | 2.7809 | 2.9912 | 2.8335 | 3.0437 | 1.529 | 2.6219 | 3.2353 | 3.2353 | 3.6442 | 3.6442 | 2020-01-02 06:00 | 1.6309 | 2.6727 | 4.3873 | 4.3873 | 4.3873 | 4.3873
2021-11-04 18:00 | 2.5035 | 3.0465 | 2.9808 | 3.2061 | 3.0371 | 3.2624 | 1.6347 | 2.8033 | 3.4591 | 3.4591 | 3.8963 | 3.8963 | 2020-01-02 07:00 | 1.9967 | 3.2722 | 5.3714 | 5.3714 | 5.3714 | 5.3714
2021-11-04 19:00 | 2.4149 | 2.9387 | 2.8753 | 3.0926 | 2.9296 | 3.147 | 1.5604 | 2.6758 | 3.3018 | 3.3018 | 3.7192 | 3.7192 | 2020-01-02 08:00 | 2.1644 | 3.547 | 5.8224 | 5.8224 | 5.8224 | 5.8224
2021-11-04 20:00 | 2.3406 | 2.8483 | 2.7868 | 2.9975 | 2.8395 | 3.0501 | 1.5261 | 2.617 | 3.2293 | 3.2293 | 3.6374 | 3.6374 | 2020-01-02 09:00 | 2.172 | 3.5595 | 5.8429 | 5.8429 | 5.8429 | 5.8429
2021-11-04 21:00 | 2.2107 | 2.6902 | 2.6321 | 2.8311 | 2.6819 | 2.8808 | 1.4413 | 2.4716 | 3.0498 | 3.0498 | 3.4353 | 3.4353 | 2020-01-02 10:00 | 2.2253 | 3.6469 | 5.9865 | 5.9865 | 5.9865 | 5.9865
2021-11-04 22:00 | 1.8486 | 2.2495 | 2.201 | 2.3673 | 2.2426 | 2.4089 | 1.214 | 2.0817 | 2.5687 | 2.5687 | 2.8934 | 2.8934 | 2020-01-02 11:00 | 2.3625 | 3.8717 | 6.3555 | 6.3555 | 6.3555 | 6.3555
2021-11-04 23:00 | 1.7204 | 2.0936 | 2.0484 | 2.2033 | 2.0871 | 2.242 | 1.0529 | 1.8055 | 2.2279 | 2.2279 | 2.5095 | 2.5095 | 2020-01-02 12:00 | 2.3473 | 3.8467 | 6.3145 | 6.3145 | 6.3145 | 6.3145
2021-11-05 | 1.6033 | 1.951 | 1.9089 | 2.0532 | 1.945 | 2.0893 | 0.98025 | 1.681 | 2.0742 | 2.0742 | 2.3364 | 2.3364 | 2020-01-02 13:00 | 2.4082 | 3.9467 | 6.4785 | 6.4785 | 6.4785 | 6.4785
2021-11-05 01:00 | 1.4604 | 1.7771 | 1.7388 | 1.8702 | 1.7716 | 1.9031 | 0.8002 | 1.3722 | 1.6932 | 1.6932 | 1.9073 | 1.9073 | 2020-01-02 14:00 | 2.4463 | 4.0091 | 6.581 | 6.581 | 6.581 | 6.581
2021-11-05 02:00 | 1.3861 | 1.6867 | 1.6503 | 1.7751 | 1.6815 | 1.8063 | 0.76591 | 1.3134 | 1.6207 | 1.6207 | 1.8255 | 1.8255 | 2020-01-02 15:00 | 2.3397 | 3.8343 | 6.294 | 6.294 | 6.294 | 6.294
2021-11-05 03:00 | 1.3573 | 1.6517 | 1.6161 | 1.7382 | 1.6466 | 1.7688 | 0.74305 | 1.2742 | 1.5723 | 1.5723 | 1.771 | 1.771 | 2020-01-02 16:00 | 2.3625 | 3.8717 | 6.3555 | 6.3555 | 6.3555 | 6.3555
2021-11-05 04:00 | 1.3746 | 1.6728 | 1.6367 | 1.7604 | 1.6676 | 1.7914 | 0.73733 | 1.2644 | 1.5602 | 1.5602 | 1.7574 | 1.7574 | 2020-01-02 17:00 | 2.111 | 3.4596 | 5.6789 | 5.6789 | 5.6789 | 5.6789
2021-11-05 05:00 | 1.5276 | 1.859 | 1.8189 | 1.9564 | 1.8533 | 1.9907 | 0.76305 | 1.3085 | 1.6146 | 1.6146 | 1.8187 | 1.8187 | 2020-01-02 18:00 | 2.1796 | 3.572 | 5.8634 | 5.8634 | 5.8634 | 5.8634
2021-11-05 06:00 | 1.8462 | 2.2466 | 2.1982 | 2.3643 | 2.2397 | 2.4059 | 0.88308 | 1.5143 | 1.8686 | 1.8686 | 2.1048 | 2.1048 | 2020-01-02 19:00 | 1.8443 | 3.0224 | 4.9614 | 4.9614 | 4.9614 | 4.9614
2021-11-05 07:00 | 2.2206 | 2.7022 | 2.6439 | 2.8438 | 2.6939 | 2.8937 | 1.0517 | 1.8035 | 2.2254 | 2.2254 | 2.5067 | 2.5067 | 2020-01-02 20:00 | 1.7223 | 2.8226 | 4.6333 | 4.6333 | 4.6333 | 4.6333
2021-11-05 08:00 | 2.4063 | 2.9283 | 2.8651 | 3.0817 | 2.9192 | 3.1358 | 1.1142 | 1.9107 | 2.3577 | 2.3577 | 2.6557 | 2.6557 | 2020-01-02 21:00 | 1.7223 | 2.8226 | 4.6333 | 4.6333 | 4.6333 | 4.6333
2021-11-05 09:00 | 2.372 | 2.8865 | 2.8243 | 3.0377 | 2.8776 | 3.0911 | 1.266 | 2.1711 | 2.679 | 2.679 | 3.0176 | 3.0176 | 2020-01-02 22:00 | 1.7223 | 2.8226 | 4.6333 | 4.6333 | 4.6333 | 4.6333
2021-11-05 10:00 | 2.2406 | 2.7266 | 2.6677 | 2.8694 | 2.7181 | 2.9198 | 1.3289 | 2.2789 | 2.812 | 2.812 | 3.1674 | 3.1674 | 2020-01-02 23:00 | 1.6309 | 2.6727 | 4.3873 | 4.3873 | 4.3873 | 4.3873
2021-11-05 11:00 | 2.3406 | 2.8483 | 2.7868 | 2.9975 | 2.8395 | 3.0501 | 1.3746 | 2.3573 | 2.9088 | 2.9088 | 3.2764 | 3.2764 | 2020-01-03 | 1.4709 | 2.4105 | 3.9568 | 3.9568 | 3.9568 | 3.9568
2021-11-05 12:00 | 2.2806 | 2.7752 | 2.7154 | 2.9206 | 2.7667 | 2.9719 | 1.4004 | 2.4014 | 2.9632 | 2.9632 | 3.3377 | 3.3377 | 2020-01-03 01:00 | 1.4556 | 2.3855 | 3.9158 | 3.9158 | 3.9158 | 3.9158
2021-11-05 13:00 | 2.252 | 2.7405 | 2.6813 | 2.884 | 2.732 | 2.9347 | 1.4004 | 2.4014 | 2.9632 | 2.9632 | 3.3377 | 3.3377 | 2020-01-03 02:00 | 1.448 | 2.373 | 3.8953 | 3.8953 | 3.8953 | 3.8953
2021-11-05 14:00 | 2.152 | 2.6187 | 2.5623 | 2.7559 | 2.6107 | 2.8043 | 1.3146 | 2.2544 | 2.7818 | 2.7818 | 3.1333 | 3.1333 | 2020-01-03 03:00 | 1.4175 | 2.323 | 3.8133 | 3.8133 | 3.8133 | 3.8133
2021-11-05 15:00 | 2.0064 | 2.4416 | 2.3889 | 2.5695 | 2.4341 | 2.6146 | 1.2317 | 2.1122 | 2.6064 | 2.6064 | 2.9358 | 2.9358 | 2020-01-03 04:00 | 1.4099 | 2.3105 | 3.7928 | 3.7928 | 3.7928 | 3.7928
2021-11-05 16:00 | 2.1577 | 2.6257 | 2.5691 | 2.7632 | 2.6176 | 2.8118 | 1.3403 | 2.2985 | 2.8362 | 2.8362 | 3.1947 | 3.1947 | 2020-01-03 05:00 | 1.4861 | 2.4354 | 3.9978 | 3.9978 | 3.9978 | 3.9978
2021-11-05 17:00 | 2.2149 | 2.6953 | 2.6371 | 2.8364 | 2.6869 | 2.8863 | 1.4747 | 2.5288 | 3.1204 | 3.1204 | 3.5148 | 3.5148 | 2020-01-03 06:00 | 1.6385 | 2.6852 | 4.4078 | 4.4078 | 4.4078 | 4.4078
2021-11-05 18:00 | 2.3035 | 2.8031 | 2.7426 | 2.9499 | 2.7944 | 3.0017 | 1.5804 | 2.7101 | 3.3442 | 3.3442 | 3.7668 | 3.7668 | 2020-01-03 07:00 | 1.7528 | 2.8726 | 4.7154 | 4.7154 | 4.7154 | 4.7154
2021-11-05 19:00 | 2.2857 | 2.7815 | 2.7215 | 2.9272 | 2.7729 | 2.9786 | 1.6633 | 2.8523 | 3.5195 | 3.5195 | 3.9644 | 3.9644 | 2020-01-03 08:00 | 2.0348 | 3.3347 | 5.4739 | 5.4739 | 5.4739 | 5.4739
2021-11-05 20:00 | 2.1834 | 2.657 | 2.5997 | 2.7962 | 2.6488 | 2.8453 | 1.6318 | 2.7984 | 3.453 | 3.453 | 3.8894 | 3.8894 | 2020-01-03 09:00 | 2.172 | 3.5595 | 5.8429 | 5.8429 | 5.8429 | 5.8429
2021-11-05 21:00 | 2.0462 | 2.4901 | 2.4364 | 2.6205 | 2.4824 | 2.6666 | 1.6033 | 2.7494 | 3.3925 | 3.3925 | 3.8213 | 3.8213 | 2020-01-03 10:00 | 2.4692 | 4.0466 | 6.6425 | 6.6425 | 6.6425 | 6.6425
2021-11-05 22:00 | 1.8977 | 2.3094 | 2.2595 | 2.4303 | 2.3022 | 2.473 | 1.3175 | 2.2593 | 2.7878 | 2.7878 | 3.1402 | 3.1402 | 2020-01-03 11:00 | 2.3473 | 3.8467 | 6.3145 | 6.3145 | 6.3145 | 6.3145
2021-11-05 23:00 | 1.6947 | 2.0623 | 2.0178 | 2.1703 | 2.0559 | 2.2085 | 1.1346 | 1.9456 | 2.4008 | 2.4008 | 2.7042 | 2.7042 | 2020-01-03 12:00 | 2.4159 | 3.9591 | 6.499 | 6.499 | 6.499 | 6.499
2021-11-06 | 1.5661 | 1.9058 | 1.8647 | 2.0056 | 1.8999 | 2.0409 | 0.99454 | 1.7055 | 2.1045 | 2.1045 | 2.3704 | 2.3704 | 2020-01-03 13:00 | 2.4311 | 3.9841 | 6.54 | 6.54 | 6.54 | 6.54
2021-11-06 01:00 | 1.4437 | 1.7568 | 1.7189 | 1.8488 | 1.7514 | 1.8813 | 0.87165 | 1.4947 | 1.8444 | 1.8444 | 2.0775 | 2.0775 | 2020-01-03 14:00 | 2.4768 | 4.0591 | 6.663 | 6.663 | 6.663 | 6.663
2021-11-06 02:00 | 1.3975 | 1.7006 | 1.6639 | 1.7897 | 1.6954 | 1.8211 | 0.86022 | 1.4751 | 1.8202 | 1.8202 | 2.0503 | 2.0503 | 2020-01-03 15:00 | 2.4921 | 4.084 | 6.704 | 6.704 | 6.704 | 6.704
2021-11-06 03:00 | 1.3746 | 1.6728 | 1.6367 | 1.7604 | 1.6676 | 1.7914 | 0.76305 | 1.3085 | 1.6146 | 1.6146 | 1.8187 | 1.8187 | 2020-01-03 16:00 | 2.5226 | 4.134 | 6.786 | 6.786 | 6.786 | 6.786
2021-11-06 04:00 | 1.4118 | 1.718 | 1.6809 | 1.808 | 1.7127 | 1.8398 | 0.72304 | 1.2399 | 1.53 | 1.53 | 1.7233 | 1.7233 | 2020-01-03 17:00 | 2.4616 | 4.0341 | 6.622 | 6.622 | 6.622 | 6.622
2021-11-06 05:00 | 1.4167 | 1.7239 | 1.6867 | 1.8142 | 1.7186 | 1.8461 | 0.76305 | 1.3085 | 1.6146 | 1.6146 | 1.8187 | 1.8187 | 2020-01-03 18:00 | 2.1567 | 3.5345 | 5.8019 | 5.8019 | 5.8019 | 5.8019
2021-11-06 06:00 | 1.529 | 1.8606 | 1.8205 | 1.9581 | 1.8549 | 1.9925 | 0.79735 | 1.3673 | 1.6872 | 1.6872 | 1.9004 | 1.9004 | 2020-01-03 19:00 | 1.9662 | 3.2223 | 5.2894 | 5.2894 | 5.2894 | 5.2894
2021-11-06 07:00 | 1.689 | 2.0553 | 2.011 | 2.163 | 2.049 | 2.201 | 0.97043 | 1.6641 | 2.0534 | 2.0534 | 2.313 | 2.313 | 2020-01-03 20:00 | 1.8748 | 3.0724 | 5.0434 | 5.0434 | 5.0434 | 5.0434
2021-11-06 08:00 | 1.7433 | 2.1214 | 2.0757 | 2.2326 | 2.1149 | 2.2718 | 1.0346 | 1.7741 | 2.1891 | 2.1891 | 2.4658 | 2.4658 | 2020-01-03 21:00 | 1.7986 | 2.9475 | 4.8384 | 4.8384 | 4.8384 | 4.8384
2021-11-06 09:00 | 1.7747 | 2.1597 | 2.1131 | 2.2728 | 2.153 | 2.3127 | 1.2117 | 2.0779 | 2.5641 | 2.5641 | 2.8881 | 2.8881 | 2020-01-03 22:00 | 1.7986 | 2.9475 | 4.8384 | 4.8384 | 4.8384 | 4.8384
2021-11-06 10:00 | 1.8776 | 2.2849 | 2.2356 | 2.4046 | 2.2778 | 2.4468 | 1.4175 | 2.4308 | 2.9995 | 2.9995 | 3.3786 | 3.3786 | 2020-01-03 23:00 | 1.7071 | 2.7976 | 4.5923 | 4.5923 | 4.5923 | 4.5923
2021-11-06 11:00 | 1.9462 | 2.3683 | 2.3173 | 2.4924 | 2.361 | 2.5362 | 1.3975 | 2.3965 | 2.9571 | 2.9571 | 3.3309 | 3.3309 | 2020-01-04 | 1.6004 | 2.6228 | 4.3053 | 4.3053 | 4.3053 | 4.3053
2021-11-06 12:00 | 1.709 | 2.0797 | 2.0348 | 2.1886 | 2.0733 | 2.2271 | 1.3775 | 2.3622 | 2.9148 | 2.9148 | 3.2832 | 3.2832 | 2020-01-04 01:00 | 1.5699 | 2.5728 | 4.2233 | 4.2233 | 4.2233 | 4.2233
2021-11-06 13:00 | 1.629 | 1.9823 | 1.9396 | 2.0862 | 1.9762 | 2.1228 | 1.3918 | 2.3867 | 2.945 | 2.945 | 3.3173 | 3.3173 | 2020-01-04 02:00 | 1.5318 | 2.5104 | 4.1208 | 4.1208 | 4.1208 | 4.1208
2021-11-06 14:00 | 1.7176 | 2.0901 | 2.045 | 2.1996 | 2.0837 | 2.2383 | 1.3632 | 2.3377 | 2.8846 | 2.8846 | 3.2491 | 3.2491 | 2020-01-04 03:00 | 1.5471 | 2.5353 | 4.1618 | 4.1618 | 4.1618 | 4.1618
2021-11-06 15:00 | 1.6318 | 1.9858 | 1.943 | 2.0898 | 1.9797 | 2.1265 | 1.3089 | 2.2446 | 2.7697 | 2.7697 | 3.1197 | 3.1197 | 2020-01-04 04:00 | 1.6157 | 2.6478 | 4.3463 | 4.3463 | 4.3463 | 4.3463
2021-11-06 16:00 | 1.6016 | 1.949 | 1.907 | 2.0511 | 1.943 | 2.0871 | 1.3289 | 2.2789 | 2.812 | 2.812 | 3.1674 | 3.1674 | 2020-01-04 05:00 | 1.6004 | 2.6228 | 4.3053 | 4.3053 | 4.3053 | 4.3053
2021-11-06 17:00 | 1.7262 | 2.1006 | 2.0552 | 2.2106 | 2.0941 | 2.2494 | 1.3546 | 2.323 | 2.8664 | 2.8664 | 3.2287 | 3.2287 | 2020-01-04 06:00 | 1.7986 | 2.9475 | 4.8384 | 4.8384 | 4.8384 | 4.8384
2021-11-06 18:00 | 1.8891 | 2.2988 | 2.2492 | 2.4192 | 2.2917 | 2.4617 | 1.489 | 2.5533 | 3.1506 | 3.1506 | 3.5489 | 3.5489 | 2020-01-04 07:00 | 1.9891 | 3.2597 | 5.3509 | 5.3509 | 5.3509 | 5.3509
2021-11-06 19:00 | 1.9119 | 2.3266 | 2.2764 | 2.4485 | 2.3194 | 2.4915 | 1.4661 | 2.5141 | 3.1023 | 3.1023 | 3.4944 | 3.4944 | 2020-01-04 08:00 | 2.1491 | 3.522 | 5.7814 | 5.7814 | 5.7814 | 5.7814
2021-11-06 20:00 | 1.9205 | 2.337 | 2.2866 | 2.4595 | 2.3298 | 2.5027 | 1.4318 | 2.4553 | 3.0297 | 3.0297 | 3.4126 | 3.4126 | 2020-01-04 09:00 | 2.3092 | 3.7843 | 6.212 | 6.212 | 6.212 | 6.212
2021-11-06 21:00 | 1.8062 | 2.1979 | 2.1505 | 2.3131 | 2.1912 | 2.3537 | 1.3832 | 2.372 | 2.9269 | 2.9269 | 3.2968 | 3.2968 | 2020-01-04 10:00 | 2.4845 | 4.0716 | 6.6835 | 6.6835 | 6.6835 | 6.6835
2021-11-06 22:00 | 1.6919 | 2.0588 | 2.0144 | 2.1667 | 2.0525 | 2.2047 | 1.2803 | 2.1956 | 2.7092 | 2.7092 | 3.0516 | 3.0516 | 2020-01-04 11:00 | 2.332 | 3.8218 | 6.2735 | 6.2735 | 6.2735 | 6.2735
2021-11-06 23:00 | 1.6261 | 1.9788 | 1.9361 | 2.0825 | 1.9727 | 2.1191 | 1.0553 | 1.8096 | 2.233 | 2.233 | 2.5152 | 2.5152 | 2020-01-04 12:00 | 2.5073 | 4.109 | 6.745 | 6.745 | 6.745 | 6.745
2021-11-07 | 1.5547 | 1.8919 | 1.8511 | 1.991 | 1.8861 | 2.026 | 1.0145 | 1.7398 | 2.1468 | 2.1468 | 2.4181 | 2.4181 | 2020-01-04 13:00 | 2.6674 | 4.3713 | 7.1755 | 7.1755 | 7.1755 | 7.1755
2021-11-07 01:00 | 1.4518 | 1.7667 | 1.7286 | 1.8592 | 1.7612 | 1.8919 | 0.869 | 1.4902 | 1.8388 | 1.8388 | 2.0712 | 2.0712 | 2020-01-04 14:00 | 2.614 | 4.2839 | 7.032 | 7.032 | 7.032 | 7.032
2021-11-07 02:00 | 1.3804 | 1.6797 | 1.6435 | 1.7677 | 1.6746 | 1.7988 | 0.77452 | 1.3282 | 1.6389 | 1.6389 | 1.846 | 1.846 | 2020-01-04 15:00 | 2.6978 | 4.4213 | 7.2576 | 7.2576 | 7.2576 | 7.2576
2021-11-07 03:00 | 1.3686 | 1.6654 | 1.6295 | 1.7527 | 1.6603 | 1.7835 | 0.75958 | 1.3026 | 1.6073 | 1.6073 | 1.8104 | 1.8104 | 2020-01-04 16:00 | 2.7207 | 4.4587 | 7.3191 | 7.3191 | 7.3191 | 7.3191
2021-11-07 04:00 | 1.3346 | 1.6241 | 1.5891 | 1.7092 | 1.6191 | 1.7392 | 0.76019 | 1.3036 | 1.6086 | 1.6086 | 1.8119 | 1.8119 | 2020-01-04 17:00 | 2.4997 | 4.0965 | 6.7245 | 6.7245 | 6.7245 | 6.7245
2021-11-07 05:00 | 1.3461 | 1.638 | 1.6027 | 1.7238 | 1.633 | 1.7541 | 0.68814 | 1.18 | 1.4561 | 1.4561 | 1.6401 | 1.6401 | 2020-01-04 18:00 | 2.2787 | 3.7343 | 6.13 | 6.13 | 6.13 | 6.13
2021-11-07 06:00 | 1.3775 | 1.6763 | 1.6401 | 1.7641 | 1.6711 | 1.7951 | 0.73161 | 1.2546 | 1.5481 | 1.5481 | 1.7438 | 1.7438 | 2020-01-04 19:00 | 2.5607 | 4.1964 | 6.8885 | 6.8885 | 6.8885 | 6.8885
2021-11-07 07:00 | 1.5404 | 1.8745 | 1.8341 | 1.9727 | 1.8687 | 2.0074 | 0.86879 | 1.4898 | 1.8384 | 1.8384 | 2.0707 | 2.0707 | 2020-01-04 20:00 | 2.1339 | 3.497 | 5.7404 | 5.7404 | 5.7404 | 5.7404
2021-11-07 08:00 | 1.5804 | 1.9232 | 1.8817 | 2.0239 | 1.9173 | 2.0595 | 1.0059 | 1.725 | 2.1285 | 2.1285 | 2.3975 | 2.3975 | 2020-01-04 21:00 | 2.0501 | 3.3597 | 5.5149 | 5.5149 | 5.5149 | 5.5149
2021-11-07 09:00 | 1.6118 | 1.9614 | 1.9191 | 2.0642 | 1.9554 | 2.1005 | 1.2117 | 2.0779 | 2.5641 | 2.5641 | 2.8881 | 2.8881 | 2020-01-04 22:00 | 1.8595 | 3.0474 | 5.0024 | 5.0024 | 5.0024 | 5.0024
2021-11-07 10:00 | 1.6861 | 2.0519 | 2.0076 | 2.1594 | 2.0455 | 2.1973 | 1.3689 | 2.3475 | 2.8967 | 2.8967 | 3.2628 | 3.2628 | 2020-01-04 23:00 | 1.7452 | 2.8601 | 4.6949 | 4.6949 | 4.6949 | 4.6949
2021-11-07 11:00 | 1.7605 | 2.1423 | 2.0961 | 2.2545 | 2.1357 | 2.2941 | 1.3689 | 2.3475 | 2.8967 | 2.8967 | 3.2628 | 3.2628 | 2020-01-05 | 1.5547 | 2.5478 | 4.1823 | 4.1823 | 4.1823 | 4.1823
2021-11-07 12:00 | 1.709 | 2.0797 | 2.0348 | 2.1886 | 2.0733 | 2.2271 | 1.4004 | 2.4014 | 2.9632 | 2.9632 | 3.3377 | 3.3377 | 2020-01-05 01:00 | 1.5013 | 2.4604 | 4.0388 | 4.0388 | 4.0388 | 4.0388
2021-11-07 13:00 | 1.6118 | 1.9614 | 1.9191 | 2.0642 | 1.9554 | 2.1005 | 1.4032 | 2.4063 | 2.9692 | 2.9692 | 3.3445 | 3.3445 | 2020-01-05 02:00 | 1.5013 | 2.4604 | 4.0388 | 4.0388 | 4.0388 | 4.0388
2021-11-07 14:00 | 1.6318 | 1.9858 | 1.943 | 2.0898 | 1.9797 | 2.1265 | 1.4461 | 2.4798 | 3.0599 | 3.0599 | 3.4467 | 3.4467 | 2020-01-05 03:00 | 1.4861 | 2.4354 | 3.9978 | 3.9978 | 3.9978 | 3.9978
2021-11-07 15:00 | 1.549 | 1.8849 | 1.8443 | 1.9837 | 1.8791 | 2.0185 | 1.3689 | 2.3475 | 2.8967 | 2.8967 | 3.2628 | 3.2628 | 2020-01-05 04:00 | 1.5242 | 2.4979 | 4.1003 | 4.1003 | 4.1003 | 4.1003
2021-11-07 16:00 | 1.7033 | 2.0727 | 2.028 | 2.1813 | 2.0663 | 2.2196 | 1.3689 | 2.3475 | 2.8967 | 2.8967 | 3.2628 | 3.2628 | 2020-01-05 05:00 | 1.5242 | 2.4979 | 4.1003 | 4.1003 | 4.1003 | 4.1003
2021-11-07 17:00 | 1.7547 | 2.1353 | 2.0893 | 2.2472 | 2.1288 | 2.2867 | 1.4289 | 2.4504 | 3.0236 | 3.0236 | 3.4058 | 3.4058 | 2020-01-05 06:00 | 1.4937 | 2.4479 | 4.0183 | 4.0183 | 4.0183 | 4.0183
2021-11-07 18:00 | 1.9348 | 2.3544 | 2.3036 | 2.4778 | 2.3472 | 2.5213 | 1.4489 | 2.4847 | 3.066 | 3.066 | 3.4535 | 3.4535 | 2020-01-05 07:00 | 1.829 | 2.9975 | 4.9204 | 4.9204 | 4.9204 | 4.9204
2021-11-07 19:00 | 2.0119 | 2.4483 | 2.3955 | 2.5766 | 2.4408 | 2.6219 | 1.4918 | 2.5582 | 3.1567 | 3.1567 | 3.5557 | 3.5557 | 2020-01-05 08:00 | 1.8824 | 3.0849 | 5.0639 | 5.0639 | 5.0639 | 5.0639
2021-11-07 20:00 | 1.9977 | 2.4309 | 2.3785 | 2.5583 | 2.4235 | 2.6032 | 1.5061 | 2.5827 | 3.1869 | 3.1869 | 3.5897 | 3.5897 | 2020-01-05 09:00 | 1.7605 | 2.8851 | 4.7359 | 4.7359 | 4.7359 | 4.7359
2021-11-07 21:00 | 1.8976 | 2.3092 | 2.2594 | 2.4302 | 2.3021 | 2.4729 | 1.4032 | 2.4063 | 2.9692 | 2.9692 | 3.3445 | 3.3445 | 2020-01-05 10:00 | 1.7986 | 2.9475 | 4.8384 | 4.8384 | 4.8384 | 4.8384
2021-11-07 22:00 | 1.7433 | 2.1214 | 2.0757 | 2.2326 | 2.1149 | 2.2718 | 1.2975 | 2.225 | 2.7455 | 2.7455 | 3.0925 | 3.0925 | 2020-01-05 11:00 | 1.829 | 2.9975 | 4.9204 | 4.9204 | 4.9204 | 4.9204
2021-11-07 23:00 | 1.5918 | 1.9371 | 1.8953 | 2.0386 | 1.9311 | 2.0744 | 1.0546 | 1.8084 | 2.2315 | 2.2315 | 2.5135 | 2.5135 | 2020-01-05 12:00 | 1.8671 | 3.0599 | 5.0229 | 5.0229 | 5.0229 | 5.0229
2021-11-08 | 1.4732 | 1.7927 | 1.754 | 1.8866 | 1.7872 | 1.9197 | 0.95739 | 1.6418 | 2.0258 | 2.0258 | 2.2819 | 2.2819 | 2020-01-05 13:00 | 1.8367 | 3.0099 | 4.9409 | 4.9409 | 4.9409 | 4.9409
2021-11-08 01:00 | 1.3746 | 1.6728 | 1.6367 | 1.7604 | 1.6676 | 1.7914 | 0.88594 | 1.5192 | 1.8747 | 1.8747 | 2.1116 | 2.1116 | 2020-01-05 14:00 | 1.8671 | 3.0599 | 5.0229 | 5.0229 | 5.0229 | 5.0229
2021-11-08 02:00 | 1.3346 | 1.6241 | 1.5891 | 1.7092 | 1.6191 | 1.7392 | 0.75734 | 1.2987 | 1.6025 | 1.6025 | 1.8051 | 1.8051 | 2020-01-05 15:00 | 1.8138 | 2.9725 | 4.8794 | 4.8794 | 4.8794 | 4.8794
2021-11-08 03:00 | 1.3489 | 1.6415 | 1.6061 | 1.7275 | 1.6364 | 1.7578 | 0.65617 | 1.1252 | 1.3885 | 1.3885 | 1.5639 | 1.5639 | 2020-01-05 16:00 | 1.7833 | 2.9225 | 4.7974 | 4.7974 | 4.7974 | 4.7974
2021-11-08 04:00 | 1.3461 | 1.638 | 1.6027 | 1.7238 | 1.633 | 1.7541 | 0.67446 | 1.1566 | 1.4272 | 1.4272 | 1.6075 | 1.6075 | 2020-01-05 17:00 | 1.6842 | 2.7602 | 4.5308 | 4.5308 | 4.5308 | 4.5308
2021-11-08 05:00 | 1.4828 | 1.8044 | 1.7655 | 1.899 | 1.7989 | 1.9323 | 0.75448 | 1.2938 | 1.5965 | 1.5965 | 1.7983 | 1.7983 | 2020-01-05 18:00 | 1.6233 | 2.6602 | 4.3668 | 4.3668 | 4.3668 | 4.3668
2021-11-08 06:00 | 1.7882 | 2.1761 | 2.1291 | 2.2901 | 2.1694 | 2.3303 | 0.78306 | 1.3428 | 1.657 | 1.657 | 1.8664 | 1.8664 | 2020-01-05 19:00 | 1.6233 | 2.6602 | 4.3668 | 4.3668 | 4.3668 | 4.3668
2021-11-08 07:00 | 2.0034 | 2.4379 | 2.3853 | 2.5656 | 2.4304 | 2.6107 | 1.0088 | 1.73 | 2.1347 | 2.1347 | 2.4045 | 2.4045 | 2020-01-05 20:00 | 1.6233 | 2.6602 | 4.3668 | 4.3668 | 4.3668 | 4.3668
2021-11-08 08:00 | 2.1634 | 2.6327 | 2.5759 | 2.7706 | 2.6245 | 2.8192 | 1.086 | 1.8623 | 2.298 | 2.298 | 2.5884 | 2.5884 | 2020-01-05 21:00 | 1.608 | 2.6353 | 4.3258 | 4.3258 | 4.3258 | 4.3258
2021-11-08 09:00 | 1.9691 | 2.3962 | 2.3445 | 2.5217 | 2.3888 | 2.566 | 1.1431 | 1.9603 | 2.4189 | 2.4189 | 2.7246 | 2.7246 | 2020-01-05 22:00 | 1.4099 | 2.3105 | 3.7928 | 3.7928 | 3.7928 | 3.7928
2021-11-08 10:00 | 2.0691 | 2.5179 | 2.4636 | 2.6498 | 2.5101 | 2.6963 | 1.1403 | 1.9554 | 2.4129 | 2.4129 | 2.7178 | 2.7178 | 2020-01-05 23:00 | 1.4023 | 2.2981 | 3.7723 | 3.7723 | 3.7723 | 3.7723
2021-11-08 11:00 | 2.0291 | 2.4692 | 2.4159 | 2.5986 | 2.4616 | 2.6442 | 1.2432 | 2.1318 | 2.6306 | 2.6306 | 2.9631 | 2.9631 | 2020-01-06 | 1.3032 | 2.1357 | 3.5058 | 3.5058 | 3.5058 | 3.5058
2021-11-08 12:00 | 2.1634 | 2.6327 | 2.5759 | 2.7706 | 2.6245 | 2.8192 | 1.2032 | 2.0632 | 2.5459 | 2.5459 | 2.8677 | 2.8677 | 2020-01-06 01:00 | 1.2194 | 1.9983 | 3.2802 | 3.2802 | 3.2802 | 3.2802
2021-11-08 13:00 | 2.112 | 2.5701 | 2.5146 | 2.7047 | 2.5621 | 2.7522 | 1.286 | 2.2054 | 2.7213 | 2.7213 | 3.0652 | 3.0652 | 2020-01-06 02:00 | 1.2346 | 2.0233 | 3.3212 | 3.3212 | 3.3212 | 3.3212
2021-11-08 14:00 | 2.0577 | 2.504 | 2.45 | 2.6352 | 2.4963 | 2.6814 | 1.1689 | 2.0044 | 2.4733 | 2.4733 | 2.786 | 2.786 | 2020-01-06 03:00 | 1.1736 | 1.9234 | 3.1572 | 3.1572 | 3.1572 | 3.1572
2021-11-08 15:00 | 2.0491 | 2.4935 | 2.4398 | 2.6242 | 2.4859 | 2.6703 | 1.1317 | 1.9407 | 2.3947 | 2.3947 | 2.6974 | 2.6974 | 2020-01-06 04:00 | 1.2651 | 2.0732 | 3.4033 | 3.4033 | 3.4033 | 3.4033
2021-11-08 16:00 | 2.0234 | 2.4622 | 2.4091 | 2.5912 | 2.4547 | 2.6368 | 1.1999 | 2.0576 | 2.5389 | 2.5389 | 2.8598 | 2.8598 | 2020-01-06 05:00 | 1.4556 | 2.3855 | 3.9158 | 3.9158 | 3.9158 | 3.9158
2021-11-08 17:00 | 2.1748 | 2.6466 | 2.5895 | 2.7852 | 2.6384 | 2.8341 | 1.4787 | 2.5357 | 3.1289 | 3.1289 | 3.5243 | 3.5243 | 2020-01-06 06:00 | 1.5166 | 2.4854 | 4.0798 | 4.0798 | 4.0798 | 4.0798
2021-11-08 18:00 | 2.372 | 2.8865 | 2.8243 | 3.0377 | 2.8776 | 3.0911 | 1.4832 | 2.5435 | 3.1385 | 3.1385 | 3.5352 | 3.5352 | 2020-01-06 07:00 | 1.8367 | 3.0099 | 4.9409 | 4.9409 | 4.9409 | 4.9409
2021-11-08 19:00 | 2.212 | 2.6918 | 2.6337 | 2.8328 | 2.6835 | 2.8826 | 1.489 | 2.5533 | 3.1506 | 3.1506 | 3.5489 | 3.5489 | 2020-01-06 08:00 | 2.0119 | 3.2972 | 5.4124 | 5.4124 | 5.4124 | 5.4124
2021-11-08 20:00 | 2.2663 | 2.7579 | 2.6984 | 2.9023 | 2.7494 | 2.9533 | 1.4347 | 2.4602 | 3.0357 | 3.0357 | 3.4194 | 3.4194 | 2020-01-06 09:00 | 1.9662 | 3.2223 | 5.2894 | 5.2894 | 5.2894 | 5.2894
2021-11-08 21:00 | 2.112 | 2.5701 | 2.5146 | 2.7047 | 2.5621 | 2.7522 | 1.3946 | 2.3916 | 2.9511 | 2.9511 | 3.3241 | 3.3241 | 2020-01-06 10:00 | 2.1186 | 3.4721 | 5.6994 | 5.6994 | 5.6994 | 5.6994
2021-11-08 22:00 | 1.9348 | 2.3544 | 2.3036 | 2.4778 | 2.3472 | 2.5213 | 1.1917 | 2.0436 | 2.5217 | 2.5217 | 2.8404 | 2.8404 | 2020-01-06 11:00 | 2.233 | 3.6594 | 6.007 | 6.007 | 6.007 | 6.007
2021-11-08 23:00 | 1.5833 | 1.9267 | 1.8851 | 2.0276 | 1.9207 | 2.0632 | 0.98256 | 1.6849 | 2.0791 | 2.0791 | 2.3419 | 2.3419 | 2020-01-06 12:00 | 2.233 | 3.6594 | 6.007 | 6.007 | 6.007 | 6.007
2021-11-09 | 1.4947 | 1.8189 | 1.7796 | 1.9141 | 1.8133 | 1.9478 | 0.88594 | 1.5192 | 1.8747 | 1.8747 | 2.1116 | 2.1116 | 2020-01-06 13:00 | 2.2025 | 3.6094 | 5.9249 | 5.9249 | 5.9249 | 5.9249
2021-11-09 01:00 | 1.3918 | 1.6937 | 1.6571 | 1.7824 | 1.6884 | 1.8137 | 0.76315 | 1.3087 | 1.6148 | 1.6148 | 1.8189 | 1.8189 | 2020-01-06 14:00 | 2.1949 | 3.597 | 5.9044 | 5.9044 | 5.9044 | 5.9044
2021-11-09 02:00 | 1.3546 | 1.6484 | 1.6129 | 1.7348 | 1.6434 | 1.7653 | 0.72876 | 1.2497 | 1.5421 | 1.5421 | 1.737 | 1.737 | 2020-01-06 15:00 | 2.2025 | 3.6094 | 5.9249 | 5.9249 | 5.9249 | 5.9249
2021-11-09 03:00 | 1.366 | 1.6623 | 1.6264 | 1.7494 | 1.6572 | 1.7801 | 0.68017 | 1.1664 | 1.4393 | 1.4393 | 1.6212 | 1.6212 | 2020-01-06 16:00 | 2.4387 | 3.9966 | 6.5605 | 6.5605 | 6.5605 | 6.5605
2021-11-09 04:00 | 1.3661 | 1.6624 | 1.6265 | 1.7494 | 1.6572 | 1.7802 | 0.70589 | 1.2105 | 1.4937 | 1.4937 | 1.6825 | 1.6825 | 2020-01-06 17:00 | 2.2634 | 3.7094 | 6.089 | 6.089 | 6.089 | 6.089
2021-11-09 05:00 | 1.4746 | 1.7944 | 1.7557 | 1.8884 | 1.7889 | 1.9216 | 0.69446 | 1.1909 | 1.4695 | 1.4695 | 1.6552 | 1.6552 | 2020-01-06 18:00 | 2.0196 | 3.3097 | 5.4329 | 5.4329 | 5.4329 | 5.4329
2021-11-09 06:00 | 1.8345 | 2.2324 | 2.1842 | 2.3493 | 2.2255 | 2.3906 | 0.77448 | 1.3281 | 1.6388 | 1.6388 | 1.8459 | 1.8459 | 2020-01-06 19:00 | 1.89 | 3.0974 | 5.0844 | 5.0844 | 5.0844 | 5.0844
2021-11-09 07:00 | 2.1091 | 2.5666 | 2.5112 | 2.701 | 2.5587 | 2.7485 | 1.1089 | 1.9015 | 2.3464 | 2.3464 | 2.6429 | 2.6429 | 2020-01-06 20:00 | 1.9434 | 3.1848 | 5.2279 | 5.2279 | 5.2279 | 5.2279
2021-11-09 08:00 | 2.0634 | 2.5109 | 2.4568 | 2.6425 | 2.5032 | 2.6889 | 1.0717 | 1.8378 | 2.2677 | 2.2677 | 2.5544 | 2.5544 | 2020-01-06 21:00 | 1.8595 | 3.0474 | 5.0024 | 5.0024 | 5.0024 | 5.0024
2021-11-09 09:00 | 2.1063 | 2.5631 | 2.5078 | 2.6974 | 2.5552 | 2.7448 | 1.0974 | 1.8819 | 2.3222 | 2.3222 | 2.6157 | 2.6157 | 2020-01-06 22:00 | 1.7528 | 2.8726 | 4.7154 | 4.7154 | 4.7154 | 4.7154
2021-11-09 10:00 | 1.8805 | 2.2884 | 2.239 | 2.4082 | 2.2813 | 2.4505 | 1.2089 | 2.073 | 2.558 | 2.558 | 2.8813 | 2.8813 | 2020-01-06 23:00 | 1.6233 | 2.6602 | 4.3668 | 4.3668 | 4.3668 | 4.3668
2021-11-09 11:00 | 1.9348 | 2.3544 | 2.3036 | 2.4778 | 2.3472 | 2.5213 | 1.2117 | 2.0779 | 2.5641 | 2.5641 | 2.8881 | 2.8881 | 2020-01-07 | 1.5547 | 2.5478 | 4.1823 | 4.1823 | 4.1823 | 4.1823
2021-11-09 12:00 | 1.9719 | 2.3996 | 2.3479 | 2.5254 | 2.3922 | 2.5697 | 1.1403 | 1.9554 | 2.4129 | 2.4129 | 2.7178 | 2.7178 | 2020-01-07 01:00 | 1.4937 | 2.4479 | 4.0183 | 4.0183 | 4.0183 | 4.0183
2021-11-09 13:00 | 1.8748 | 2.2814 | 2.2322 | 2.4009 | 2.2744 | 2.4431 | 1.1546 | 1.9799 | 2.4431 | 2.4431 | 2.7519 | 2.7519 | 2020-01-07 02:00 | 1.4861 | 2.4354 | 3.9978 | 3.9978 | 3.9978 | 3.9978
2021-11-09 14:00 | 1.7862 | 2.1736 | 2.1267 | 2.2875 | 2.1669 | 2.3276 | 1.1374 | 1.9505 | 2.4068 | 2.4068 | 2.711 | 2.711 | 2020-01-07 03:00 | 1.509 | 2.4729 | 4.0593 | 4.0593 | 4.0593 | 4.0593
2021-11-09 15:00 | 1.8348 | 2.2327 | 2.1845 | 2.3497 | 2.2258 | 2.391 | 1.0631 | 1.8231 | 2.2496 | 2.2496 | 2.5339 | 2.5339 | 2020-01-07 04:00 | 1.5166 | 2.4854 | 4.0798 | 4.0798 | 4.0798 | 4.0798
2021-11-09 16:00 | 1.8405 | 2.2397 | 2.1914 | 2.357 | 2.2328 | 2.3984 | 1.2603 | 2.1613 | 2.6669 | 2.6669 | 3.0039 | 3.0039 | 2020-01-07 05:00 | 1.5242 | 2.4979 | 4.1003 | 4.1003 | 4.1003 | 4.1003
2021-11-09 17:00 | 2.1548 | 2.6222 | 2.5657 | 2.7596 | 2.6141 | 2.8081 | 1.3775 | 2.3622 | 2.9148 | 2.9148 | 3.2832 | 3.2832 | 2020-01-07 06:00 | 1.6842 | 2.7602 | 4.5308 | 4.5308 | 4.5308 | 4.5308
2021-11-09 18:00 | 2.3806 | 2.897 | 2.8345 | 3.0487 | 2.888 | 3.1023 | 1.3918 | 2.3867 | 2.945 | 2.945 | 3.3173 | 3.3173 | 2020-01-07 07:00 | 2.1263 | 3.4845 | 5.7199 | 5.7199 | 5.7199 | 5.7199
2021-11-09 19:00 | 2.1863 | 2.6605 | 2.6031 | 2.7998 | 2.6523 | 2.849 | 1.7862 | 3.063 | 3.7796 | 3.7796 | 4.2573 | 4.2573 | 2020-01-07 08:00 | 2.5607 | 4.1964 | 6.8885 | 6.8885 | 6.8885 | 6.8885
2021-11-09 20:00 | 2.0805 | 2.5318 | 2.4772 | 2.6644 | 2.524 | 2.7112 | 1.4489 | 2.4847 | 3.066 | 3.066 | 3.4535 | 3.4535 | 2020-01-07 09:00 | 2.5378 | 4.159 | 6.827 | 6.827 | 6.827 | 6.827
2021-11-09 21:00 | 2.0348 | 2.4762 | 2.4227 | 2.6059 | 2.4685 | 2.6517 | 1.4118 | 2.421 | 2.9874 | 2.9874 | 3.3649 | 3.3649 | 2020-01-07 10:00 | 2.7131 | 4.4462 | 7.2986 | 7.2986 | 7.2986 | 7.2986
2021-11-09 22:00 | 1.7662 | 2.1492 | 2.1029 | 2.2618 | 2.1426 | 2.3016 | 1.2787 | 2.1928 | 2.7058 | 2.7058 | 3.0477 | 3.0477 | 2020-01-07 11:00 | 2.8274 | 4.6336 | 7.6061 | 7.6061 | 7.6061 | 7.6061
2021-11-09 23:00 | 1.542 | 1.8765 | 1.836 | 1.9748 | 1.8707 | 2.0095 | 1.0403 | 1.7839 | 2.2012 | 2.2012 | 2.4794 | 2.4794 | 2020-01-07 12:00 | 2.8731 | 4.7085 | 7.7291 | 7.7291 | 7.7291 | 7.7291
2021-11-10 | 1.489 | 1.8119 | 1.7728 | 1.9068 | 1.8063 | 1.9403 | 0.89172 | 1.5292 | 1.8869 | 1.8869 | 2.1254 | 2.1254 | 2020-01-07 13:00 | 1.5318 | 2.5104 | 4.1208 | 4.1208 | 4.1208 | 4.1208
2021-11-10 01:00 | 1.3746 | 1.6728 | 1.6367 | 1.7604 | 1.6676 | 1.7914 | 0.72026 | 1.2351 | 1.5241 | 1.5241 | 1.7167 | 1.7167 | 2020-01-07 14:00 | 1.3032 | 2.1357 | 3.5058 | 3.5058 | 3.5058 | 3.5058
2021-11-10 02:00 | 1.3003 | 1.5824 | 1.5482 | 1.6653 | 1.5775 | 1.6945 | 0.70589 | 1.2105 | 1.4937 | 1.4937 | 1.6825 | 1.6825 | 2020-01-07 15:00 | 1.3489 | 2.2106 | 3.6288 | 3.6288 | 3.6288 | 3.6288
2021-11-10 03:00 | 1.3575 | 1.6519 | 1.6163 | 1.7385 | 1.6468 | 1.769 | 0.70018 | 1.2007 | 1.4816 | 1.4816 | 1.6688 | 1.6688 | 2020-01-07 16:00 | 1.3108 | 2.1482 | 3.5263 | 3.5263 | 3.5263 | 3.5263
2021-11-10 04:00 | 1.2918 | 1.5719 | 1.538 | 1.6543 | 1.5671 | 1.6834 | 0.68631 | 1.1769 | 1.4522 | 1.4522 | 1.6358 | 1.6358 | 2020-01-07 17:00 | 1.2346 | 2.0233 | 3.3212 | 3.3212 | 3.3212 | 3.3212
2021-11-10 05:00 | 1.4853 | 1.8074 | 1.7684 | 1.9021 | 1.8019 | 1.9355 | 0.70018 | 1.2007 | 1.4816 | 1.4816 | 1.6688 | 1.6688 | 2020-01-07 18:00 | 1.2041 | 1.9733 | 3.2392 | 3.2392 | 3.2392 | 3.2392
2021-11-10 06:00 | 1.7404 | 2.1179 | 2.0723 | 2.2289 | 2.1114 | 2.2681 | 0.80592 | 1.382 | 1.7053 | 1.7053 | 1.9209 | 1.9209 | 2020-01-07 19:00 | 1.2422 | 2.0358 | 3.3417 | 3.3417 | 3.3417 | 3.3417
2021-11-10 07:00 | 2.0863 | 2.5388 | 2.484 | 2.6718 | 2.5309 | 2.7187 | 0.95453 | 1.6369 | 2.0198 | 2.0198 | 2.2751 | 2.2751 | 2020-01-07 20:00 | 1.1279 | 1.8484 | 3.0342 | 3.0342 | 3.0342 | 3.0342
2021-11-10 08:00 | 2.172 | 2.6431 | 2.5861 | 2.7815 | 2.6349 | 2.8304 | 1.0974 | 1.8819 | 2.3222 | 2.3222 | 2.6157 | 2.6157 | 2020-01-07 21:00 | 1.1279 | 1.8484 | 3.0342 | 3.0342 | 3.0342 | 3.0342
2021-11-10 09:00 | 2.1577 | 2.6257 | 2.5691 | 2.7632 | 2.6176 | 2.8118 | 1.1374 | 1.9505 | 2.4068 | 2.4068 | 2.711 | 2.711 | 2020-01-07 22:00 | 1.7519 | 2.871 | 4.7128 | 4.7128 | 4.7128 | 4.7128
2021-11-10 10:00 | 2.232 | 2.7161 | 2.6575 | 2.8584 | 2.7077 | 2.9086 | 1.1886 | 2.0383 | 2.5151 | 2.5151 | 2.833 | 2.833 | 2020-01-07 23:00 | 1.5671 | 2.5681 | 4.2156 | 4.2156 | 4.2156 | 4.2156
2021-11-10 11:00 | 2.172 | 2.6431 | 2.5861 | 2.7815 | 2.6349 | 2.8304 | 1.2718 | 2.1809 | 2.691 | 2.691 | 3.0312 | 3.0312 | 2020-01-08 | 1.4175 | 2.323 | 3.8133 | 3.8133 | 3.8133 | 3.8133
2021-11-10 12:00 | 2.1748 | 2.6466 | 2.5895 | 2.7852 | 2.6384 | 2.8341 | 1.206 | 2.0681 | 2.552 | 2.552 | 2.8745 | 2.8745 | 2020-01-08 01:00 | 1.3746 | 2.2528 | 3.698 | 3.698 | 3.698 | 3.698
2021-11-10 13:00 | 2.2949 | 2.7926 | 2.7324 | 2.9389 | 2.784 | 2.9906 | 1.2575 | 2.1564 | 2.6608 | 2.6608 | 2.9971 | 2.9971 | 2020-01-08 02:00 | 1.3489 | 2.2106 | 3.6288 | 3.6288 | 3.6288 | 3.6288
2021-11-10 14:00 | 2.0548 | 2.5005 | 2.4466 | 2.6315 | 2.4928 | 2.6777 | 1.1974 | 2.0534 | 2.5338 | 2.5338 | 2.8541 | 2.8541 | 2020-01-08 03:00 | 1.3518 | 2.2153 | 3.6365 | 3.6365 | 3.6365 | 3.6365
2021-11-10 15:00 | 2.0491 | 2.4935 | 2.4398 | 2.6242 | 2.4859 | 2.6703 | 1.1917 | 2.0436 | 2.5217 | 2.5217 | 2.8404 | 2.8404 | 2020-01-08 04:00 | 1.3804 | 2.2621 | 3.7133 | 3.7133 | 3.7133 | 3.7133
2021-11-10 16:00 | 2.0834 | 2.5353 | 2.4806 | 2.6681 | 2.5275 | 2.715 | 1.2689 | 2.176 | 2.685 | 2.685 | 3.0244 | 3.0244 | 2020-01-08 05:00 | 1.4594 | 2.3917 | 3.926 | 3.926 | 3.926 | 3.926
2021-11-10 17:00 | 2.2349 | 2.7196 | 2.6609 | 2.8621 | 2.7112 | 2.9124 | 1.4461 | 2.4798 | 3.0599 | 3.0599 | 3.4467 | 3.4467 | 2020-01-08 06:00 | 1.6109 | 2.6399 | 4.3335 | 4.3335 | 4.3335 | 4.3335
2021-11-10 18:00 | 2.3263 | 2.8309 | 2.7698 | 2.9792 | 2.8222 | 3.0315 | 1.4261 | 2.4455 | 3.0176 | 3.0176 | 3.399 | 3.399 | 2020-01-08 07:00 | 1.9453 | 3.1879 | 5.233 | 5.233 | 5.233 | 5.233
2021-11-10 19:00 | 2.2206 | 2.7022 | 2.6439 | 2.8438 | 2.6939 | 2.8937 | 1.4375 | 2.4651 | 3.0418 | 3.0418 | 3.4262 | 3.4262 | 2020-01-08 08:00 | 2.273 | 3.725 | 6.1146 | 6.1146 | 6.1146 | 6.1146
2021-11-10 20:00 | 2.1348 | 2.5979 | 2.5418 | 2.734 | 2.5899 | 2.782 | 1.4318 | 2.4553 | 3.0297 | 3.0297 | 3.4126 | 3.4126 | 2020-01-08 09:00 | 2.4768 | 4.0591 | 6.663 | 6.663 | 6.663 | 6.663
2021-11-10 21:00 | 2.1148 | 2.5735 | 2.518 | 2.7083 | 2.5656 | 2.7559 | 1.4318 | 2.4553 | 3.0297 | 3.0297 | 3.4126 | 3.4126 | 2020-01-08 10:00 | 2.5349 | 4.1543 | 6.8193 | 6.8193 | 6.8193 | 6.8193
2021-11-10 22:00 | 1.849 | 2.2501 | 2.2016 | 2.368 | 2.2432 | 2.4096 | 1.2549 | 2.1519 | 2.6553 | 2.6553 | 2.9909 | 2.9909 | 2020-01-08 11:00 | 2.5168 | 4.1246 | 6.7706 | 6.7706 | 6.7706 | 6.7706
2021-11-10 23:00 | 1.6147 | 1.9649 | 1.9225 | 2.0679 | 1.9589 | 2.1042 | 1.046 | 1.7937 | 2.2133 | 2.2133 | 2.4931 | 2.4931 | 2020-01-08 12:00 | 2.5549 | 4.1871 | 6.8731 | 6.8731 | 6.8731 | 6.8731
2021-11-11 | 1.5378 | 1.8713 | 1.8309 | 1.9693 | 1.8655 | 2.0039 | 0.88169 | 1.512 | 1.8657 | 1.8657 | 2.1015 | 2.1015 | 2020-01-08 13:00 | 2.5997 | 4.2605 | 6.9936 | 6.9936 | 6.9936 | 6.9936
2021-11-11 01:00 | 1.4146 | 1.7215 | 1.6843 | 1.8117 | 1.7162 | 1.8435 | 0.79454 | 1.3625 | 1.6812 | 1.6812 | 1.8937 | 1.8937 | 2020-01-08 14:00 | 2.5711 | 4.2136 | 6.9167 | 6.9167 | 6.9167 | 6.9167
2021-11-11 02:00 | 1.3975 | 1.7006 | 1.6639 | 1.7897 | 1.6954 | 1.8211 | 0.77162 | 1.3232 | 1.6328 | 1.6328 | 1.8391 | 1.8391 | 2020-01-08 15:00 | 2.553 | 4.184 | 6.868 | 6.868 | 6.868 | 6.868
2021-11-11 03:00 | 1.3403 | 1.6311 | 1.5959 | 1.7165 | 1.626 | 1.7467 | 0.71161 | 1.2203 | 1.5058 | 1.5058 | 1.6961 | 1.6961 | 2020-01-08 16:00 | 2.573 | 4.2167 | 6.9218 | 6.9218 | 6.9218 | 6.9218
2021-11-11 04:00 | 1.3575 | 1.6519 | 1.6163 | 1.7385 | 1.6468 | 1.769 | 0.69716 | 1.1955 | 1.4752 | 1.4752 | 1.6616 | 1.6616 | 2020-01-08 17:00 | 2.3339 | 3.8249 | 6.2786 | 6.2786 | 6.2786 | 6.2786
2021-11-11 05:00 | 1.4739 | 1.7935 | 1.7548 | 1.8875 | 1.788 | 1.9206 | 0.70304 | 1.2056 | 1.4876 | 1.4876 | 1.6757 | 1.6757 | 2020-01-08 18:00 | 2.1053 | 3.4502 | 5.6636 | 5.6636 | 5.6636 | 5.6636
2021-11-11 06:00 | 1.7976 | 2.1875 | 2.1403 | 2.3021 | 2.1808 | 2.3425 | 0.84879 | 1.4555 | 1.796 | 1.796 | 2.0231 | 2.0231 | 2020-01-08 19:00 | 1.85 | 3.0318 | 4.9767 | 4.9767 | 4.9767 | 4.9767
2021-11-11 07:00 | 2.1463 | 2.6118 | 2.5554 | 2.7486 | 2.6037 | 2.7969 | 0.99454 | 1.7055 | 2.1045 | 2.1045 | 2.3704 | 2.3704 | 2020-01-08 20:00 | 1.7738 | 2.9069 | 4.7717 | 4.7717 | 4.7717 | 4.7717
2021-11-11 08:00 | 2.1634 | 2.6327 | 2.5759 | 2.7706 | 2.6245 | 2.8192 | 0.99168 | 1.7006 | 2.0984 | 2.0984 | 2.3636 | 2.3636 | 2020-01-08 21:00 | 1.7824 | 2.921 | 4.7948 | 4.7948 | 4.7948 | 4.7948
2021-11-11 09:00 | 2.0405 | 2.4831 | 2.4295 | 2.6132 | 2.4755 | 2.6591 | 1.0517 | 1.8035 | 2.2254 | 2.2254 | 2.5067 | 2.5067 | 2020-01-08 22:00 | 1.6576 | 2.7164 | 4.4591 | 4.4591 | 4.4591 | 4.4591
2021-11-11 10:00 | 2.0282 | 2.4681 | 2.4149 | 2.5974 | 2.4605 | 2.6431 | 1.1517 | 1.975 | 2.4371 | 2.4371 | 2.7451 | 2.7451 | 2020-01-08 23:00 | 1.5547 | 2.5478 | 4.1823 | 4.1823 | 4.1823 | 4.1823
2021-11-11 11:00 | 2.0948 | 2.5492 | 2.4942 | 2.6827 | 2.5413 | 2.7299 | 1.1632 | 1.9946 | 2.4612 | 2.4612 | 2.7723 | 2.7723 | 2020-01-09 | 1.4061 | 2.3043 | 3.7825 | 3.7825 | 3.7825 | 3.7825
2021-11-11 12:00 | 1.9719 | 2.3996 | 2.3479 | 2.5254 | 2.3922 | 2.5697 | 1.2146 | 2.0828 | 2.5701 | 2.5701 | 2.8949 | 2.8949 | 2020-01-09 01:00 | 1.3499 | 2.2122 | 3.6313 | 3.6313 | 3.6313 | 3.6313
2021-11-11 13:00 | 1.9376 | 2.3579 | 2.307 | 2.4814 | 2.3506 | 2.525 | 1.1889 | 2.0387 | 2.5157 | 2.5157 | 2.8336 | 2.8336 | 2020-01-09 02:00 | 1.3727 | 2.2497 | 3.6928 | 3.6928 | 3.6928 | 3.6928
2021-11-11 14:00 | 1.8233 | 2.2188 | 2.1709 | 2.335 | 2.212 | 2.3761 | 1.1574 | 1.9848 | 2.4492 | 2.4492 | 2.7587 | 2.7587 | 2020-01-09 03:00 | 1.2918 | 2.117 | 3.475 | 3.475 | 3.475 | 3.475
2021-11-11 15:00 | 2.032 | 2.4727 | 2.4193 | 2.6022 | 2.4651 | 2.6479 | 1.1374 | 1.9504 | 2.4067 | 2.4067 | 2.7109 | 2.7109 | 2020-01-09 04:00 | 1.348 | 2.2091 | 3.6262 | 3.6262 | 3.6262 | 3.6262
2021-11-11 16:00 | 2.0434 | 2.4866 | 2.4329 | 2.6169 | 2.4789 | 2.6628 | 1.3575 | 2.3279 | 2.8725 | 2.8725 | 3.2355 | 3.2355 | 2020-01-09 05:00 | 1.4832 | 2.4308 | 3.9901 | 3.9901 | 3.9901 | 3.9901
2021-11-11 17:00 | 2.1005 | 2.5561 | 2.501 | 2.69 | 2.5483 | 2.7373 | 1.4404 | 2.47 | 3.0478 | 3.0478 | 3.4331 | 3.4331 | 2020-01-09 06:00 | 1.5756 | 2.5822 | 4.2387 | 4.2387 | 4.2387 | 4.2387
2021-11-11 18:00 | 2.2806 | 2.7752 | 2.7154 | 2.9206 | 2.7667 | 2.9719 | 1.489 | 2.5533 | 3.1506 | 3.1506 | 3.5489 | 3.5489 | 2020-01-09 07:00 | 1.9491 | 3.1942 | 5.2433 | 5.2433 | 5.2433 | 5.2433
2021-11-11 19:00 | 2.2206 | 2.7022 | 2.6439 | 2.8438 | 2.6939 | 2.8937 | 1.5315 | 2.6262 | 3.2406 | 3.2406 | 3.6502 | 3.6502 | 2020-01-09 08:00 | 2.2387 | 3.6688 | 6.0223 | 6.0223 | 6.0223 | 6.0223
2021-11-11 20:00 | 2.2263 | 2.7092 | 2.6507 | 2.8511 | 2.7008 | 2.9012 | 1.5575 | 2.6709 | 3.2958 | 3.2958 | 3.7123 | 3.7123 | 2020-01-09 09:00 | 2.2949 | 3.7609 | 6.1735 | 6.1735 | 6.1735 | 6.1735
2021-11-11 21:00 | 2.0748 | 2.5248 | 2.4704 | 2.6571 | 2.5171 | 2.7038 | 1.4832 | 2.5435 | 3.1385 | 3.1385 | 3.5352 | 3.5352 | 2020-01-09 10:00 | 2.3501 | 3.8514 | 6.3222 | 6.3222 | 6.3222 | 6.3222
2021-11-11 22:00 | 1.9041 | 2.3171 | 2.2671 | 2.4385 | 2.31 | 2.4813 | 1.266 | 2.1711 | 2.679 | 2.679 | 3.0176 | 3.0176 | 2020-01-09 11:00 | 2.4187 | 3.9638 | 6.5067 | 6.5067 | 6.5067 | 6.5067
2021-11-11 23:00 | 1.6804 | 2.0449 | 2.0008 | 2.152 | 2.0386 | 2.1898 | 1.1003 | 1.8868 | 2.3282 | 2.3282 | 2.6225 | 2.6225 | 2020-01-09 12:00 | 2.131 | 3.4924 | 5.7327 | 5.7327 | 5.7327 | 5.7327
2021-11-12 | 1.6061 | 1.9545 | 1.9123 | 2.0569 | 1.9485 | 2.093 | 1.0288 | 1.7643 | 2.177 | 2.177 | 2.4522 | 2.4522 | 2020-01-09 13:00 | 2.2225 | 3.6422 | 5.9788 | 5.9788 | 5.9788 | 5.9788
2021-11-12 01:00 | 1.4379 | 1.7497 | 1.712 | 1.8414 | 1.7443 | 1.8737 | 0.83813 | 1.4373 | 1.7735 | 1.7735 | 1.9976 | 1.9976 | 2020-01-09 14:00 | 2.1644 | 3.547 | 5.8224 | 5.8224 | 5.8224 | 5.8224
2021-11-12 02:00 | 1.4204 | 1.7284 | 1.6912 | 1.819 | 1.7231 | 1.8509 | 0.74019 | 1.2693 | 1.5662 | 1.5662 | 1.7642 | 1.7642 | 2020-01-09 15:00 | 2.1529 | 3.5283 | 5.7917 | 5.7917 | 5.7917 | 5.7917
2021-11-12 03:00 | 1.4061 | 1.711 | 1.6741 | 1.8007 | 1.7058 | 1.8323 | 0.70017 | 1.2007 | 1.4816 | 1.4816 | 1.6688 | 1.6688 | 2020-01-09 16:00 | 2.1501 | 3.5236 | 5.784 | 5.784 | 5.784 | 5.784
2021-11-12 04:00 | 1.3918 | 1.6937 | 1.6571 | 1.7824 | 1.6884 | 1.8137 | 0.74712 | 1.2812 | 1.5809 | 1.5809 | 1.7807 | 1.7807 | 2020-01-09 17:00 | 2.0405 | 3.344 | 5.4893 | 5.4893 | 5.4893 | 5.4893
2021-11-12 05:00 | 1.5976 | 1.9441 | 1.9021 | 2.0459 | 1.9381 | 2.0818 | 0.76877 | 1.3183 | 1.6267 | 1.6267 | 1.8323 | 1.8323 | 2020-01-09 18:00 | 1.8605 | 3.049 | 5.0049 | 5.0049 | 5.0049 | 5.0049
2021-11-12 06:00 | 1.9462 | 2.3683 | 2.3173 | 2.4924 | 2.361 | 2.5362 | 0.88866 | 1.5239 | 1.8804 | 1.8804 | 2.1181 | 2.1181 | 2020-01-09 19:00 | 1.6795 | 2.7524 | 4.518 | 4.518 | 4.518 | 4.518
2021-11-12 07:00 | 2.4549 | 2.9874 | 2.9229 | 3.1439 | 2.9782 | 3.1991 | 1.0946 | 1.877 | 2.3161 | 2.3161 | 2.6089 | 2.6089 | 2020-01-09 20:00 | 1.6976 | 2.782 | 4.5667 | 4.5667 | 4.5667 | 4.5667
2021-11-12 08:00 | 2.6264 | 3.196 | 3.1271 | 3.3635 | 3.1862 | 3.4226 | 1.1089 | 1.9015 | 2.3464 | 2.3464 | 2.6429 | 2.6429 | 2020-01-09 21:00 | 1.67 | 2.7367 | 4.4924 | 4.4924 | 4.4924 | 4.4924
2021-11-12 09:00 | 2.6207 | 3.1891 | 3.1203 | 3.3562 | 3.1793 | 3.4151 | 1.2546 | 2.1515 | 2.6548 | 2.6548 | 2.9903 | 2.9903 | 2020-01-09 22:00 | 1.609 | 2.6368 | 4.3284 | 4.3284 | 4.3284 | 4.3284
2021-11-12 10:00 | 2.5407 | 3.0917 | 3.025 | 3.2537 | 3.0822 | 3.3108 | 1.3432 | 2.3034 | 2.8422 | 2.8422 | 3.2015 | 3.2015 | 2020-01-09 23:00 | 1.4842 | 2.4323 | 3.9927 | 3.9927 | 3.9927 | 3.9927
2021-11-12 11:00 | 2.4778 | 3.0152 | 2.9502 | 3.1732 | 3.0059 | 3.2289 | 1.3661 | 2.3426 | 2.8906 | 2.8906 | 3.256 | 3.256 | 2020-01-10 | 1.3718 | 2.2481 | 3.6903 | 3.6903 | 3.6903 | 3.6903
2021-11-12 12:00 | 2.4635 | 2.9978 | 2.9331 | 3.1549 | 2.9886 | 3.2103 | 1.3718 | 2.3524 | 2.9027 | 2.9027 | 3.2696 | 3.2696 | 2020-01-10 01:00 | 1.3565 | 2.2231 | 3.6493 | 3.6493 | 3.6493 | 3.6493
2021-11-12 13:00 | 2.3863 | 2.9039 | 2.8413 | 3.056 | 2.895 | 3.1097 | 1.3689 | 2.3475 | 2.8967 | 2.8967 | 3.2628 | 3.2628 | 2020-01-10 02:00 | 1.3299 | 2.1794 | 3.5775 | 3.5775 | 3.5775 | 3.5775
2021-11-12 14:00 | 2.2091 | 2.6883 | 2.6303 | 2.8291 | 2.68 | 2.8788 | 1.3255 | 2.273 | 2.8048 | 2.8048 | 3.1593 | 3.1593 | 2020-01-10 03:00 | 1.327 | 2.1747 | 3.5698 | 3.5698 | 3.5698 | 3.5698
2021-11-12 15:00 | 2.152 | 2.6187 | 2.5623 | 2.7559 | 2.6107 | 2.8043 | 1.3261 | 2.274 | 2.8059 | 2.8059 | 3.1606 | 3.1606 | 2020-01-10 04:00 | 1.387 | 2.2731 | 3.7313 | 3.7313 | 3.7313 | 3.7313
2021-11-12 16:00 | 2.2263 | 2.7092 | 2.6507 | 2.8511 | 2.7008 | 2.9012 | 1.4118 | 2.421 | 2.9874 | 2.9874 | 3.3649 | 3.3649 | 2020-01-10 05:00 | 1.4832 | 2.4308 | 3.9901 | 3.9901 | 3.9901 | 3.9901
2021-11-12 17:00 | 2.1377 | 2.6014 | 2.5452 | 2.7376 | 2.5933 | 2.7857 | 1.4575 | 2.4994 | 3.0841 | 3.0841 | 3.4739 | 3.4739 | 2020-01-10 06:00 | 1.7871 | 2.9288 | 4.8076 | 4.8076 | 4.8076 | 4.8076
2021-11-12 18:00 | 2.2777 | 2.7718 | 2.712 | 2.917 | 2.7632 | 2.9682 | 1.5976 | 2.7395 | 3.3804 | 3.3804 | 3.8077 | 3.8077 | 2020-01-10 07:00 | 1.99 | 3.2613 | 5.3535 | 5.3535 | 5.3535 | 5.3535
2021-11-12 19:00 | 2.192 | 2.6674 | 2.6099 | 2.8072 | 2.6592 | 2.8565 | 1.6275 | 2.7909 | 3.4437 | 3.4437 | 3.879 | 3.879 | 2020-01-10 08:00 | 2.4683 | 4.045 | 6.6399 | 6.6399 | 6.6399 | 6.6399
2021-11-12 20:00 | 2.2034 | 2.6813 | 2.6235 | 2.8218 | 2.6731 | 2.8714 | 1.6919 | 2.9013 | 3.58 | 3.58 | 4.0325 | 4.0325 | 2020-01-10 09:00 | 2.5121 | 4.1168 | 6.7578 | 6.7578 | 6.7578 | 6.7578
2021-11-12 21:00 | 2.2091 | 2.6883 | 2.6303 | 2.8291 | 2.68 | 2.8788 | 1.6004 | 2.7445 | 3.3865 | 3.3865 | 3.8145 | 3.8145 | 2020-01-10 10:00 | 2.6092 | 4.2761 | 7.0192 | 7.0192 | 7.0192 | 7.0192
2021-11-12 22:00 | 1.9576 | 2.3823 | 2.3309 | 2.5071 | 2.3749 | 2.5511 | 1.4318 | 2.4553 | 3.0297 | 3.0297 | 3.4126 | 3.4126 | 2020-01-10 11:00 | 2.796 | 4.5821 | 7.5215 | 7.5215 | 7.5215 | 7.5215
2021-11-12 23:00 | 1.8119 | 2.2049 | 2.1573 | 2.3204 | 2.1981 | 2.3612 | 1.1922 | 2.0444 | 2.5226 | 2.5226 | 2.8415 | 2.8415 | 2020-01-10 12:00 | 2.8807 | 4.721 | 7.7496 | 7.7496 | 7.7496 | 7.7496
2021-11-13 | 1.6528 | 2.0113 | 1.9679 | 2.1166 | 2.0051 | 2.1538 | 1.0005 | 1.7158 | 2.1171 | 2.1171 | 2.3847 | 2.3847 | 2020-01-10 13:00 | 2.7874 | 4.568 | 7.4984 | 7.4984 | 7.4984 | 7.4984
2021-11-13 01:00 | 1.5461 | 1.8815 | 1.8409 | 1.98 | 1.8757 | 2.0148 | 0.92023 | 1.5781 | 1.9472 | 1.9472 | 2.1933 | 2.1933 | 2020-01-10 14:00 | 2.8579 | 4.6835 | 7.6881 | 7.6881 | 7.6881 | 7.6881
2021-11-13 02:00 | 1.4775 | 1.798 | 1.7592 | 1.8922 | 1.7925 | 1.9254 | 0.82878 | 1.4212 | 1.7537 | 1.7537 | 1.9754 | 1.9754 | 2020-01-10 15:00 | 2.9703 | 4.8678 | 7.9905 | 7.9905 | 7.9905 | 7.9905
2021-11-13 03:00 | 1.4632 | 1.7806 | 1.7422 | 1.8739 | 1.7751 | 1.9068 | 0.81735 | 1.4016 | 1.7295 | 1.7295 | 1.9481 | 1.9481 | 2020-01-10 16:00 | 2.9512 | 4.8365 | 7.9392 | 7.9392 | 7.9392 | 7.9392
2021-11-13 04:00 | 1.4547 | 1.7702 | 1.732 | 1.8629 | 1.7647 | 1.8956 | 0.83736 | 1.4359 | 1.7719 | 1.7719 | 1.9958 | 1.9958 | 2020-01-10 17:00 | 2.7502 | 4.5071 | 7.3985 | 7.3985 | 7.3985 | 7.3985
2021-11-13 05:00 | 1.5289 | 1.8606 | 1.8204 | 1.958 | 1.8548 | 1.9924 | 0.78877 | 1.3526 | 1.6691 | 1.6691 | 1.88 | 1.88 | 2020-01-10 18:00 | 2.4273 | 3.9779 | 6.5297 | 6.5297 | 6.5297 | 6.5297
2021-11-13 06:00 | 1.709 | 2.0797 | 2.0348 | 2.1886 | 2.0733 | 2.2271 | 0.86022 | 1.4751 | 1.8202 | 1.8202 | 2.0503 | 2.0503 | 2020-01-10 19:00 | 2.0901 | 3.4252 | 5.6225 | 5.6225 | 5.6225 | 5.6225
2021-11-13 07:00 | 2.0577 | 2.504 | 2.45 | 2.6352 | 2.4963 | 2.6814 | 0.99423 | 1.7049 | 2.1038 | 2.1038 | 2.3697 | 2.3697 | 2020-01-10 20:00 | 2.0634 | 3.3815 | 5.5508 | 5.5508 | 5.5508 | 5.5508
2021-11-13 08:00 | 2.1348 | 2.5979 | 2.5418 | 2.734 | 2.5899 | 2.782 | 1.1774 | 2.0191 | 2.4915 | 2.4915 | 2.8064 | 2.8064 | 2020-01-10 21:00 | 1.9033 | 3.1192 | 5.1203 | 5.1203 | 5.1203 | 5.1203
2021-11-13 09:00 | 2.1863 | 2.6605 | 2.6031 | 2.7998 | 2.6523 | 2.849 | 1.3403 | 2.2985 | 2.8362 | 2.8362 | 3.1947 | 3.1947 | 2020-01-10 22:00 | 1.7843 | 2.9241 | 4.7999 | 4.7999 | 4.7999 | 4.7999
2021-11-13 10:00 | 2.1377 | 2.6014 | 2.5452 | 2.7376 | 2.5933 | 2.7857 | 1.4861 | 2.5484 | 3.1446 | 3.1446 | 3.542 | 3.542 | 2020-01-10 23:00 | 1.6814 | 2.7555 | 4.5232 | 4.5232 | 4.5232 | 4.5232
2021-11-13 11:00 | 2.0634 | 2.5109 | 2.4568 | 2.6425 | 2.5032 | 2.6889 | 1.5718 | 2.6954 | 3.326 | 3.326 | 3.7464 | 3.7464 | 2020-01-11 | 1.549 | 2.5385 | 4.1669 | 4.1669 | 4.1669 | 4.1669
2021-11-13 12:00 | 2.0577 | 2.504 | 2.45 | 2.6352 | 2.4963 | 2.6814 | 1.5433 | 2.6464 | 3.2655 | 3.2655 | 3.6783 | 3.6783 | 2020-01-11 01:00 | 1.468 | 2.4058 | 3.9491 | 3.9491 | 3.9491 | 3.9491
2021-11-13 13:00 | 2.0548 | 2.5005 | 2.4466 | 2.6315 | 2.4928 | 2.6777 | 1.5661 | 2.6856 | 3.3139 | 3.3139 | 3.7328 | 3.7328 | 2020-01-11 02:00 | 1.4556 | 2.3855 | 3.9158 | 3.9158 | 3.9158 | 3.9158
2021-11-13 14:00 | 1.9777 | 2.4066 | 2.3547 | 2.5327 | 2.3992 | 2.5772 | 1.5175 | 2.6023 | 3.2111 | 3.2111 | 3.617 | 3.617 | 2020-01-11 03:00 | 1.4385 | 2.3574 | 3.8697 | 3.8697 | 3.8697 | 3.8697
2021-11-13 15:00 | 1.9795 | 2.4089 | 2.3569 | 2.5351 | 2.4014 | 2.5796 | 1.5204 | 2.6072 | 3.2172 | 3.2172 | 3.6238 | 3.6238 | 2020-01-11 04:00 | 1.5585 | 2.5541 | 4.1926 | 4.1926 | 4.1926 | 4.1926
2021-11-13 16:00 | 2.1491 | 2.6153 | 2.5588 | 2.7523 | 2.6072 | 2.8006 | 1.5604 | 2.6758 | 3.3018 | 3.3018 | 3.7192 | 3.7192 | 2020-01-11 05:00 | 1.5652 | 2.565 | 4.2105 | 4.2105 | 4.2105 | 4.2105
2021-11-13 17:00 | 2.3863 | 2.9039 | 2.8413 | 3.056 | 2.895 | 3.1097 | 1.7404 | 2.9846 | 3.6828 | 3.6828 | 4.1483 | 4.1483 | 2020-01-11 06:00 | 1.5537 | 2.5463 | 4.1798 | 4.1798 | 4.1798 | 4.1798
2021-11-13 18:00 | 2.3263 | 2.8309 | 2.7698 | 2.9792 | 2.8222 | 3.0315 | 1.6976 | 2.9111 | 3.5921 | 3.5921 | 4.0461 | 4.0461 | 2020-01-11 07:00 | 1.8862 | 3.0911 | 5.0741 | 5.0741 | 5.0741 | 5.0741
2021-11-13 19:00 | 2.3492 | 2.8587 | 2.797 | 3.0085 | 2.8499 | 3.0613 | 1.6776 | 2.8768 | 3.5498 | 3.5498 | 3.9984 | 3.9984 | 2020-01-11 08:00 | 1.9043 | 3.1208 | 5.1228 | 5.1228 | 5.1228 | 5.1228
2021-11-13 20:00 | 2.2034 | 2.6813 | 2.6235 | 2.8218 | 2.6731 | 2.8714 | 1.6776 | 2.8768 | 3.5498 | 3.5498 | 3.9984 | 3.9984 | 2020-01-11 09:00 | 1.9958 | 3.2707 | 5.3688 | 5.3688 | 5.3688 | 5.3688
2021-11-13 21:00 | 2.2006 | 2.6779 | 2.6201 | 2.8181 | 2.6696 | 2.8677 | 1.6004 | 2.7445 | 3.3865 | 3.3865 | 3.8145 | 3.8145 | 2020-01-11 10:00 | 2.1034 | 3.4471 | 5.6584 | 5.6584 | 5.6584 | 5.6584
2021-11-13 22:00 | 2.0148 | 2.4518 | 2.3989 | 2.5803 | 2.4443 | 2.6256 | 1.4804 | 2.5386 | 3.1325 | 3.1325 | 3.5284 | 3.5284 | 2020-01-11 11:00 | 2.0901 | 3.4252 | 5.6226 | 5.6226 | 5.6226 | 5.6226
2021-11-13 23:00 | 1.8862 | 2.2953 | 2.2458 | 2.4156 | 2.2882 | 2.458 | 1.2175 | 2.0877 | 2.5761 | 2.5761 | 2.9018 | 2.9018 | 2020-01-11 12:00 | 2.1472 | 3.5189 | 5.7763 | 5.7763 | 5.7763 | 5.7763
2021-11-14 | 1.7976 | 2.1875 | 2.1403 | 2.3021 | 2.1808 | 2.3425 | 1.1117 | 1.9064 | 2.3524 | 2.3524 | 2.6497 | 2.6497 | 2020-01-11 13:00 | 2.2568 | 3.6984 | 6.071 | 6.071 | 6.071 | 6.071
2021-11-14 01:00 | 1.6265 | 1.9793 | 1.9366 | 2.083 | 1.9732 | 2.1196 | 0.9772 | 1.6757 | 2.0678 | 2.0678 | 2.3291 | 2.3291 | 2020-01-11 14:00 | 2.4197 | 3.9654 | 6.5092 | 6.5092 | 6.5092 | 6.5092
2021-11-14 02:00 | 1.5261 | 1.8571 | 1.8171 | 1.9544 | 1.8514 | 1.9887 | 0.95453 | 1.6369 | 2.0198 | 2.0198 | 2.2751 | 2.2751 | 2020-01-11 15:00 | 2.4349 | 3.9904 | 6.5502 | 6.5502 | 6.5502 | 6.5502
2021-11-14 03:00 | 1.5747 | 1.9162 | 1.8749 | 2.0166 | 1.9103 | 2.0521 | 0.88022 | 1.5094 | 1.8626 | 1.8626 | 2.098 | 2.098 | 2020-01-11 16:00 | 2.2453 | 3.6797 | 6.0403 | 6.0403 | 6.0403 | 6.0403
2021-11-14 04:00 | 1.5747 | 1.9162 | 1.8749 | 2.0166 | 1.9103 | 2.0521 | 0.84879 | 1.4555 | 1.796 | 1.796 | 2.0231 | 2.0231 | 2020-01-11 17:00 | 2.0796 | 3.408 | 5.5944 | 5.5944 | 5.5944 | 5.5944
2021-11-14 05:00 | 1.5804 | 1.9232 | 1.8817 | 2.0239 | 1.9173 | 2.0595 | 0.84021 | 1.4408 | 1.7779 | 1.7779 | 2.0026 | 2.0026 | 2020-01-11 18:00 | 1.9719 | 3.2316 | 5.3048 | 5.3048 | 5.3048 | 5.3048
2021-11-14 06:00 | 1.689 | 2.0553 | 2.011 | 2.163 | 2.049 | 2.201 | 0.8545 | 1.4653 | 1.8081 | 1.8081 | 2.0367 | 2.0367 | 2020-01-11 19:00 | 1.6804 | 2.7539 | 4.5206 | 4.5206 | 4.5206 | 4.5206
2021-11-14 07:00 | 1.8805 | 2.2884 | 2.239 | 2.4082 | 2.2813 | 2.4505 | 0.95453 | 1.6369 | 2.0198 | 2.0198 | 2.2751 | 2.2751 | 2020-01-11 20:00 | 1.6433 | 2.693 | 4.4206 | 4.4206 | 4.4206 | 4.4206
2021-11-14 08:00 | 1.9319 | 2.351 | 2.3002 | 2.4741 | 2.3437 | 2.5176 | 1.0803 | 1.8525 | 2.2859 | 2.2859 | 2.5748 | 2.5748 | 2020-01-11 21:00 | 1.6195 | 2.654 | 4.3566 | 4.3566 | 4.3566 | 4.3566
2021-11-14 09:00 | 1.9948 | 2.4275 | 2.3751 | 2.5546 | 2.42 | 2.5995 | 1.3518 | 2.3181 | 2.8604 | 2.8604 | 3.2219 | 3.2219 | 2020-01-11 22:00 | 1.508 | 2.4713 | 4.0567 | 4.0567 | 4.0567 | 4.0567
2021-11-14 10:00 | 2.1806 | 2.6535 | 2.5963 | 2.7925 | 2.6453 | 2.8416 | 1.5575 | 2.6709 | 3.2958 | 3.2958 | 3.7123 | 3.7123 | 2020-01-11 23:00 | 1.468 | 2.4058 | 3.9491 | 3.9491 | 3.9491 | 3.9491
2021-11-14 11:00 | 2.2234 | 2.7057 | 2.6473 | 2.8474 | 2.6973 | 2.8975 | 1.6204 | 2.7788 | 3.4288 | 3.4288 | 3.8622 | 3.8622 | 2020-01-12 | 1.4137 | 2.3168 | 3.803 | 3.803 | 3.803 | 3.803
2021-11-14 12:00 | 2.0634 | 2.5109 | 2.4568 | 2.6425 | 2.5032 | 2.6889 | 1.5947 | 2.7346 | 3.3744 | 3.3744 | 3.8009 | 3.8009 | 2020-01-12 01:00 | 1.3203 | 2.1638 | 3.5519 | 3.5519 | 3.5519 | 3.5519
2021-11-14 13:00 | 2.0548 | 2.5005 | 2.4466 | 2.6315 | 2.4928 | 2.6777 | 1.6661 | 2.8572 | 3.5256 | 3.5256 | 3.9712 | 3.9712 | 2020-01-12 02:00 | 1.3203 | 2.1638 | 3.5519 | 3.5519 | 3.5519 | 3.5519
2021-11-14 14:00 | 2.2892 | 2.7857 | 2.7256 | 2.9316 | 2.7771 | 2.9831 | 1.7062 | 2.9258 | 3.6102 | 3.6102 | 4.0665 | 4.0665 | 2020-01-12 03:00 | 1.3108 | 2.1482 | 3.5263 | 3.5263 | 3.5263 | 3.5263
2021-11-14 15:00 | 2.4549 | 2.9874 | 2.9229 | 3.1439 | 2.9782 | 3.1991 | 1.7147 | 2.9405 | 3.6284 | 3.6284 | 4.087 | 4.087 | 2020-01-12 04:00 | 1.3813 | 2.2637 | 3.7159 | 3.7159 | 3.7159 | 3.7159
2021-11-14 16:00 | 2.2492 | 2.737 | 2.6779 | 2.8804 | 2.7286 | 2.931 | 1.6404 | 2.8131 | 3.4712 | 3.4712 | 3.9099 | 3.9099 | 2020-01-12 05:00 | 1.3975 | 2.2902 | 3.7595 | 3.7595 | 3.7595 | 3.7595
2021-11-14 17:00 | 2.6521 | 3.2273 | 3.1577 | 3.3964 | 3.2174 | 3.4561 | 1.8337 | 3.1446 | 3.8802 | 3.8802 | 4.3706 | 4.3706 | 2020-01-12 06:00 | 1.7614 | 2.8866 | 4.7384 | 4.7384 | 4.7384 | 4.7384
2021-11-14 18:00 | 2.7436 | 3.3386 | 3.2666 | 3.5135 | 3.3283 | 3.5753 | 1.8405 | 3.1561 | 3.8945 | 3.8945 | 4.3867 | 4.3867 | 2020-01-12 07:00 | 2.1044 | 3.4486 | 5.661 | 5.661 | 5.661 | 5.661
2021-11-14 19:00 | 2.7493 | 3.3456 | 3.2734 | 3.5209 | 3.3353 | 3.5827 | 1.8862 | 3.2345 | 3.9912 | 3.9912 | 4.4957 | 4.4957 | 2020-01-12 08:00 | 1.87 | 3.0646 | 5.0306 | 5.0306 | 5.0306 | 5.0306
2021-11-14 20:00 | 2.8122 | 3.4221 | 3.3483 | 3.6014 | 3.4116 | 3.6646 | 1.8833 | 3.2296 | 3.9852 | 3.9852 | 4.4889 | 4.4889 | 2020-01-12 09:00 | 1.9434 | 3.1848 | 5.2279 | 5.2279 | 5.2279 | 5.2279
2021-11-14 21:00 | 2.5121 | 3.0569 | 2.991 | 3.2171 | 3.0475 | 3.2736 | 1.8119 | 3.1071 | 3.834 | 3.834 | 4.3186 | 4.3186 | 2020-01-12 10:00 | 1.9376 | 3.1754 | 5.2125 | 5.2125 | 5.2125 | 5.2125
2021-11-14 22:00 | 2.3189 | 2.8219 | 2.761 | 2.9698 | 2.8132 | 3.0219 | 1.5833 | 2.715 | 3.3502 | 3.3502 | 3.7736 | 3.7736 | 2020-01-12 11:00 | 2.0015 | 3.28 | 5.3842 | 5.3842 | 5.3842 | 5.3842
2021-11-14 23:00 | 1.9948 | 2.4275 | 2.3751 | 2.5546 | 2.42 | 2.5995 | 1.3003 | 2.2299 | 2.7515 | 2.7515 | 3.0993 | 3.0993 | 2020-01-12 12:00 | 2.0053 | 3.2863 | 5.3945 | 5.3945 | 5.3945 | 5.3945
2021-11-15 | 1.8862 | 2.2953 | 2.2458 | 2.4156 | 2.2882 | 2.458 | 1.1317 | 1.9407 | 2.3947 | 2.3947 | 2.6974 | 2.6974 | 2020-01-12 13:00 | 1.9186 | 3.1442 | 5.1613 | 5.1613 | 5.1613 | 5.1613
2021-11-15 01:00 | 1.7319 | 2.1075 | 2.0621 | 2.2179 | 2.101 | 2.2569 | 0.96882 | 1.6614 | 2.05 | 2.05 | 2.3091 | 2.3091 | 2020-01-12 14:00 | 1.8995 | 3.113 | 5.11 | 5.11 | 5.11 | 5.11
2021-11-15 02:00 | 1.6517 | 2.01 | 1.9666 | 2.1153 | 2.0038 | 2.1524 | 0.9431 | 1.6173 | 1.9956 | 1.9956 | 2.2478 | 2.2478 | 2020-01-12 15:00 | 1.9596 | 3.2113 | 5.2715 | 5.2715 | 5.2715 | 5.2715
2021-11-15 03:00 | 1.6519 | 2.0101 | 1.9668 | 2.1154 | 2.0039 | 2.1526 | 0.89166 | 1.529 | 1.8868 | 1.8868 | 2.1252 | 2.1252 | 2020-01-12 16:00 | 1.9367 | 3.1739 | 5.21 | 5.21 | 5.21 | 5.21
2021-11-15 04:00 | 1.689 | 2.0553 | 2.011 | 2.163 | 2.049 | 2.201 | 0.90595 | 1.5536 | 1.917 | 1.917 | 2.1593 | 2.1593 | 2020-01-12 17:00 | 1.8329 | 3.0037 | 4.9306 | 4.9306 | 4.9306 | 4.9306
2021-11-15 05:00 | 1.8233 | 2.2188 | 2.1709 | 2.335 | 2.212 | 2.3761 | 0.90309 | 1.5487 | 1.9109 | 1.9109 | 2.1525 | 2.1525 | 2020-01-12 18:00 | 1.6461 | 2.6977 | 4.4283 | 4.4283 | 4.4283 | 4.4283
2021-11-15 06:00 | 2.6978 | 3.283 | 3.2122 | 3.455 | 3.2729 | 3.5157 | 1.1109 | 1.905 | 2.3506 | 2.3506 | 2.6477 | 2.6477 | 2020-01-12 19:00 | 1.5642 | 2.5635 | 4.2079 | 4.2079 | 4.2079 | 4.2079
2021-11-15 07:00 | 3.1803 | 3.8702 | 3.7867 | 4.0729 | 3.8582 | 4.1445 | 1.3832 | 2.372 | 2.9269 | 2.9269 | 3.2968 | 3.2968 | 2020-01-12 20:00 | 1.5833 | 2.5947 | 4.2592 | 4.2592 | 4.2592 | 4.2592
2021-11-15 08:00 | 3.3009 | 4.0168 | 3.9301 | 4.2272 | 4.0044 | 4.3015 | 1.5004 | 2.5729 | 3.1748 | 3.1748 | 3.5761 | 3.5761 | 2020-01-12 21:00 | 1.529 | 2.5057 | 4.1131 | 4.1131 | 4.1131 | 4.1131
2021-11-15 09:00 | 3.2608 | 3.9681 | 3.8825 | 4.176 | 3.9559 | 4.2494 | 1.5518 | 2.6611 | 3.2837 | 3.2837 | 3.6987 | 3.6987 | 2020-01-12 22:00 | 1.4975 | 2.4542 | 4.0286 | 4.0286 | 4.0286 | 4.0286
2021-11-15 10:00 | 3.0522 | 3.7142 | 3.6341 | 3.9088 | 3.7028 | 3.9775 | 1.5118 | 2.5925 | 3.199 | 3.199 | 3.6034 | 3.6034 | 2020-01-12 23:00 | 1.4356 | 2.3527 | 3.862 | 3.862 | 3.862 | 3.862
2021-11-15 11:00 | 3.1094 | 3.7838 | 3.7022 | 3.982 | 3.7721 | 4.052 | 1.6347 | 2.8033 | 3.4591 | 3.4591 | 3.8963 | 3.8963 | 2020-01-13 | 1.3575 | 2.2247 | 3.6518 | 3.6518 | 3.6518 | 3.6518
2021-11-15 12:00 | 3.0837 | 3.7525 | 3.6715 | 3.9491 | 3.7409 | 4.0185 | 1.6261 | 2.7886 | 3.4409 | 3.4409 | 3.8758 | 3.8758 | 2020-01-13 01:00 | 1.2403 | 2.0326 | 3.3366 | 3.3366 | 3.3366 | 3.3366
2021-11-15 13:00 | 2.955 | 3.596 | 3.5184 | 3.7844 | 3.5849 | 3.8509 | 1.5747 | 2.7003 | 3.3321 | 3.3321 | 3.7532 | 3.7532 | 2020-01-13 02:00 | 1.1489 | 1.8828 | 3.0906 | 3.0906 | 3.0906 | 3.0906
2021-11-15 14:00 | 2.9722 | 3.6169 | 3.5388 | 3.8063 | 3.6057 | 3.8732 | 1.5861 | 2.7199 | 3.3563 | 3.3563 | 3.7805 | 3.7805 | 2020-01-13 03:00 | 1.1165 | 1.8297 | 3.0035 | 3.0035 | 3.0035 | 3.0035
2021-11-15 15:00 | 2.8064 | 3.4151 | 3.3415 | 3.5941 | 3.4046 | 3.6572 | 1.4333 | 2.4579 | 3.0329 | 3.0329 | 3.4162 | 3.4162 | 2020-01-13 04:00 | 1.1765 | 1.9281 | 3.1649 | 3.1649 | 3.1649 | 3.1649
2021-11-15 16:00 | 2.755 | 3.3525 | 3.2802 | 3.5282 | 3.3422 | 3.5902 | 1.5861 | 2.7199 | 3.3563 | 3.3563 | 3.7805 | 3.7805 | 2020-01-13 05:00 | 1.3184 | 2.1607 | 3.5468 | 3.5468 | 3.5468 | 3.5468
2021-11-15 17:00 | 3.0122 | 3.6655 | 3.5865 | 3.8576 | 3.6542 | 3.9253 | 1.7547 | 3.0091 | 3.713 | 3.713 | 4.1823 | 4.1823 | 2020-01-13 06:00 | 1.4204 | 2.3277 | 3.821 | 3.821 | 3.821 | 3.821
2021-11-15 18:00 | 3.1494 | 3.8325 | 3.7498 | 4.0332 | 3.8207 | 4.1041 | 1.8862 | 3.2345 | 3.9912 | 3.9912 | 4.4957 | 4.4957 | 2020-01-13 07:00 | 2.091 | 3.4268 | 5.6251 | 5.6251 | 5.6251 | 5.6251
2021-11-15 19:00 | 3.1179 | 3.7942 | 3.7124 | 3.993 | 3.7825 | 4.0631 | 1.8776 | 3.2198 | 3.9731 | 3.9731 | 4.4752 | 4.4752 | 2020-01-13 08:00 | 2.1063 | 3.4518 | 5.6661 | 5.6661 | 5.6661 | 5.6661
2021-11-15 20:00 | 3.0751 | 3.7421 | 3.6613 | 3.9381 | 3.7305 | 4.0073 | 2.0062 | 3.4404 | 4.2452 | 4.2452 | 4.7818 | 4.7818 | 2020-01-13 09:00 | 2.1148 | 3.4658 | 5.6892 | 5.6892 | 5.6892 | 5.6892
2021-11-15 21:00 | 2.835 | 3.4499 | 3.3755 | 3.6307 | 3.4393 | 3.6944 | 1.8691 | 3.2051 | 3.9549 | 3.9549 | 4.4548 | 4.4548 | 2020-01-13 10:00 | 2.3692 | 3.8826 | 6.3734 | 6.3734 | 6.3734 | 6.3734
2021-11-15 22:00 | 2.4149 | 2.9387 | 2.8753 | 3.0926 | 2.9296 | 3.147 | 1.5691 | 2.6907 | 3.3202 | 3.3202 | 3.7399 | 3.7399 | 2020-01-13 11:00 | 2.5026 | 4.1012 | 6.7322 | 6.7322 | 6.7322 | 6.7322
2021-11-15 23:00 | 2.0091 | 2.4449 | 2.3921 | 2.5729 | 2.4373 | 2.6181 | 1.3146 | 2.2544 | 2.7818 | 2.7818 | 3.1333 | 3.1333 | 2020-01-13 12:00 | 2.6264 | 4.3042 | 7.0653 | 7.0653 | 7.0653 | 7.0653
2021-11-16 | 1.8262 | 2.2223 | 2.1743 | 2.3387 | 2.2154 | 2.3798 | 1.1174 | 1.9162 | 2.3645 | 2.3645 | 2.6633 | 2.6633 | 2020-01-13 13:00 | 2.7255 | 4.4665 | 7.3319 | 7.3319 | 7.3319 | 7.3319
2021-11-16 01:00 | 1.7012 | 2.0702 | 2.0256 | 2.1787 | 2.0638 | 2.2169 | 0.9631 | 1.6516 | 2.0379 | 2.0379 | 2.2955 | 2.2955 | 2020-01-13 14:00 | 2.6369 | 4.3213 | 7.0935 | 7.0935 | 7.0935 | 7.0935
2021-11-16 02:00 | 1.6947 | 2.0623 | 2.0178 | 2.1703 | 2.0559 | 2.2085 | 0.90023 | 1.5438 | 1.9049 | 1.9049 | 2.1457 | 2.1457 | 2020-01-13 15:00 | 2.7712 | 4.5415 | 7.4549 | 7.4549 | 7.4549 | 7.4549
2021-11-16 03:00 | 1.6318 | 1.9858 | 1.943 | 2.0898 | 1.9797 | 2.1265 | 0.91452 | 1.5683 | 1.9351 | 1.9351 | 2.1797 | 2.1797 | 2020-01-13 16:00 | 2.7188 | 4.4556 | 7.3139 | 7.3139 | 7.3139 | 7.3139
2021-11-16 04:00 | 1.6947 | 2.0623 | 2.0178 | 2.1703 | 2.0559 | 2.2085 | 0.87169 | 1.4948 | 1.8445 | 1.8445 | 2.0776 | 2.0776 | 2020-01-13 17:00 | 2.6521 | 4.3463 | 7.1345 | 7.1345 | 7.1345 | 7.1345
2021-11-16 05:00 | 1.8486 | 2.2496 | 2.2011 | 2.3674 | 2.2427 | 2.409 | 0.9631 | 1.6516 | 2.0379 | 2.0379 | 2.2955 | 2.2955 | 2020-01-13 18:00 | 2.0386 | 3.3409 | 5.4842 | 5.4842 | 5.4842 | 5.4842
2021-11-16 06:00 | 2.7636 | 3.363 | 3.2904 | 3.5392 | 3.3526 | 3.6013 | 1.0772 | 1.8472 | 2.2794 | 2.2794 | 2.5675 | 2.5675 | 2020-01-13 19:00 | 1.7995 | 2.9491 | 4.8409 | 4.8409 | 4.8409 | 4.8409
2021-11-16 07:00 | 3.0694 | 3.7351 | 3.6545 | 3.9308 | 3.7236 | 3.9998 | 1.2517 | 2.1466 | 2.6487 | 2.6487 | 2.9835 | 2.9835 | 2020-01-13 20:00 | 1.7833 | 2.9225 | 4.7974 | 4.7974 | 4.7974 | 4.7974
2021-11-16 08:00 | 3.0036 | 3.6551 | 3.5763 | 3.8466 | 3.6438 | 3.9142 | 1.3689 | 2.3475 | 2.8967 | 2.8967 | 3.2628 | 3.2628 | 2020-01-13 21:00 | 1.6881 | 2.7664 | 4.5411 | 4.5411 | 4.5411 | 4.5411
2021-11-16 09:00 | 2.7178 | 3.3073 | 3.236 | 3.4806 | 3.2971 | 3.5417 | 1.3775 | 2.3622 | 2.9148 | 2.9148 | 3.2832 | 3.2832 | 2020-01-13 22:00 | 1.6014 | 2.6243 | 4.3079 | 4.3079 | 4.3079 | 4.3079
2021-11-16 10:00 | 2.4521 | 2.9839 | 2.9195 | 3.1402 | 2.9747 | 3.1954 | 1.2946 | 2.2201 | 2.7394 | 2.7394 | 3.0857 | 3.0857 | 2020-01-13 23:00 | 1.4928 | 2.4464 | 4.0157 | 4.0157 | 4.0157 | 4.0157
2021-11-16 11:00 | 2.2892 | 2.7857 | 2.7256 | 2.9316 | 2.7771 | 2.9831 | 1.3175 | 2.2593 | 2.7878 | 2.7878 | 3.1402 | 3.1402 | 2020-01-14 | 1.388 | 2.2746 | 3.7338 | 3.7338 | 3.7338 | 3.7338
2021-11-16 12:00 | 2.2663 | 2.7579 | 2.6984 | 2.9023 | 2.7494 | 2.9533 | 1.3261 | 2.274 | 2.8059 | 2.8059 | 3.1606 | 3.1606 | 2020-01-14 01:00 | 1.3575 | 2.2247 | 3.6518 | 3.6518 | 3.6518 | 3.6518
2021-11-16 13:00 | 2.1377 | 2.6014 | 2.5452 | 2.7376 | 2.5933 | 2.7857 | 1.3375 | 2.2936 | 2.8301 | 2.8301 | 3.1878 | 3.1878 | 2020-01-14 02:00 | 1.2851 | 2.106 | 3.4571 | 3.4571 | 3.4571 | 3.4571
2021-11-16 14:00 | 2.1205 | 2.5805 | 2.5248 | 2.7157 | 2.5725 | 2.7634 | 1.2117 | 2.0779 | 2.5641 | 2.5641 | 2.8881 | 2.8881 | 2020-01-14 03:00 | 1.2946 | 2.1216 | 3.4827 | 3.4827 | 3.4827 | 3.4827
2021-11-16 15:00 | 2.2291 | 2.7126 | 2.6541 | 2.8547 | 2.7043 | 2.9049 | 1.2517 | 2.1466 | 2.6487 | 2.6487 | 2.9835 | 2.9835 | 2020-01-14 04:00 | 1.307 | 2.1419 | 3.516 | 3.516 | 3.516 | 3.516
2021-11-16 16:00 | 2.1463 | 2.6118 | 2.5554 | 2.7486 | 2.6037 | 2.7969 | 1.4477 | 2.4826 | 3.0634 | 3.0634 | 3.4506 | 3.4506 | 2020-01-14 05:00 | 1.427 | 2.3386 | 3.8389 | 3.8389 | 3.8389 | 3.8389
2021-11-16 17:00 | 2.5121 | 3.0569 | 2.991 | 3.2171 | 3.0475 | 3.2736 | 1.6004 | 2.7445 | 3.3865 | 3.3865 | 3.8145 | 3.8145 | 2020-01-14 06:00 | 1.6499 | 2.704 | 4.4386 | 4.4386 | 4.4386 | 4.4386
2021-11-16 18:00 | 2.7696 | 3.3703 | 3.2976 | 3.5469 | 3.3599 | 3.6092 | 1.7062 | 2.9258 | 3.6102 | 3.6102 | 4.0665 | 4.0665 | 2020-01-14 07:00 | 2.1129 | 3.4627 | 5.6841 | 5.6841 | 5.6841 | 5.6841
2021-11-16 19:00 | 2.775 | 3.3769 | 3.304 | 3.5538 | 3.3665 | 3.6162 | 1.7691 | 3.0336 | 3.7433 | 3.7433 | 4.2165 | 4.2165 | 2020-01-14 08:00 | 2.293 | 3.7578 | 6.1684 | 6.1684 | 6.1684 | 6.1684
2021-11-16 20:00 | 2.6178 | 3.1856 | 3.1169 | 3.3525 | 3.1758 | 3.4114 | 1.8262 | 3.1316 | 3.8642 | 3.8642 | 4.3526 | 4.3526 | 2020-01-14 09:00 | 2.5492 | 4.1777 | 6.8578 | 6.8578 | 6.8578 | 6.8578
2021-11-16 21:00 | 2.4806 | 3.0187 | 2.9536 | 3.1768 | 3.0094 | 3.2326 | 1.7319 | 2.9699 | 3.6647 | 3.6647 | 4.1278 | 4.1278 | 2020-01-14 10:00 | 2.8388 | 4.6523 | 7.6368 | 7.6368 | 7.6368 | 7.6368
2021-11-16 22:00 | 2.1991 | 2.6761 | 2.6184 | 2.8163 | 2.6678 | 2.8658 | 1.5242 | 2.6137 | 3.2252 | 3.2252 | 3.6328 | 3.6328 | 2020-01-14 11:00 | 2.8264 | 4.632 | 7.6035 | 7.6035 | 7.6035 | 7.6035
2021-11-16 23:00 | 1.9463 | 2.3685 | 2.3174 | 2.4925 | 2.3612 | 2.5363 | 1.246 | 2.1367 | 2.6366 | 2.6366 | 2.9699 | 2.9699 | 2020-01-14 12:00 | 2.9941 | 4.9068 | 8.0546 | 8.0546 | 8.0546 | 8.0546
2021-11-17 | 1.7719 | 2.1562 | 2.1097 | 2.2692 | 2.1496 | 2.309 | 1.1174 | 1.9162 | 2.3645 | 2.3645 | 2.6633 | 2.6633 | 2020-01-14 13:00 | 3.037 | 4.977 | 8.1699 | 8.1699 | 8.1699 | 8.1699
2021-11-17 01:00 | 1.6362 | 1.9911 | 1.9482 | 2.0955 | 1.985 | 2.1323 | 0.9431 | 1.6173 | 1.9956 | 1.9956 | 2.2478 | 2.2478 | 2020-01-14 14:00 | 2.9846 | 4.8912 | 8.0289 | 8.0289 | 8.0289 | 8.0289
2021-11-17 02:00 | 1.5347 | 1.8675 | 1.8273 | 1.9654 | 1.8618 | 1.9999 | 0.86908 | 1.4903 | 1.839 | 1.839 | 2.0714 | 2.0714 | 2020-01-14 15:00 | 2.9998 | 4.9161 | 8.0699 | 8.0699 | 8.0699 | 8.0699
2021-11-17 03:00 | 1.569 | 1.9093 | 1.8681 | 2.0093 | 1.9034 | 2.0446 | 0.80592 | 1.382 | 1.7053 | 1.7053 | 1.9209 | 1.9209 | 2020-01-14 16:00 | 2.8731 | 4.7085 | 7.7291 | 7.7291 | 7.7291 | 7.7291
2021-11-17 04:00 | 1.5404 | 1.8745 | 1.8341 | 1.9727 | 1.8687 | 2.0074 | 0.86879 | 1.4898 | 1.8384 | 1.8384 | 2.0707 | 2.0707 | 2020-01-14 17:00 | 2.7521 | 4.5102 | 7.4036 | 7.4036 | 7.4036 | 7.4036
2021-11-17 05:00 | 1.7206 | 2.0938 | 2.0487 | 2.2035 | 2.0874 | 2.2422 | 0.9631 | 1.6516 | 2.0379 | 2.0379 | 2.2955 | 2.2955 | 2020-01-14 18:00 | 2.211 | 3.6235 | 5.948 | 5.948 | 5.948 | 5.948
2021-11-17 06:00 | 2.4663 | 3.0013 | 2.9366 | 3.1585 | 2.992 | 3.214 | 1.0097 | 1.7314 | 2.1364 | 2.1364 | 2.4065 | 2.4065 | 2020-01-14 19:00 | 2.0786 | 3.4065 | 5.5918 | 5.5918 | 5.5918 | 5.5918
2021-11-17 07:00 | 2.9122 | 3.5438 | 3.4674 | 3.7295 | 3.5329 | 3.795 | 1.2317 | 2.1122 | 2.6064 | 2.6064 | 2.9358 | 2.9358 | 2020-01-14 20:00 | 1.8938 | 3.1036 | 5.0946 | 5.0946 | 5.0946 | 5.0946
2021-11-17 08:00 | 2.9051 | 3.5353 | 3.459 | 3.7205 | 3.5244 | 3.7858 | 1.3146 | 2.2544 | 2.7818 | 2.7818 | 3.1333 | 3.1333 | 2020-01-14 21:00 | 1.8519 | 3.0349 | 4.9819 | 4.9819 | 4.9819 | 4.9819
2021-11-17 09:00 | 2.5778 | 3.1369 | 3.0693 | 3.3013 | 3.1273 | 3.3593 | 1.2726 | 2.1823 | 2.6929 | 2.6929 | 3.0332 | 3.0332 | 2020-01-14 22:00 | 1.6395 | 2.6868 | 4.4104 | 4.4104 | 4.4104 | 4.4104
2021-11-17 10:00 | 2.4749 | 3.0117 | 2.9468 | 3.1695 | 3.0024 | 3.2252 | 1.2746 | 2.1858 | 2.6971 | 2.6971 | 3.038 | 3.038 | 2020-01-14 23:00 | 1.5137 | 2.4807 | 4.0721 | 4.0721 | 4.0721 | 4.0721
2021-11-17 11:00 | 2.3435 | 2.8518 | 2.7902 | 3.0011 | 2.843 | 3.0539 | 1.3146 | 2.2544 | 2.7818 | 2.7818 | 3.1333 | 3.1333 | 2020-01-15 | 1.4166 | 2.3215 | 3.8107 | 3.8107 | 3.8107 | 3.8107
2021-11-17 12:00 | 2.1148 | 2.5735 | 2.518 | 2.7083 | 2.5656 | 2.7559 | 1.3461 | 2.3083 | 2.8483 | 2.8483 | 3.2083 | 3.2083 | 2020-01-15 01:00 | 1.4118 | 2.3137 | 3.7979 | 3.7979 | 3.7979 | 3.7979
2021-11-17 13:00 | 2.0777 | 2.5283 | 2.4738 | 2.6608 | 2.5205 | 2.7075 | 1.2746 | 2.1858 | 2.6971 | 2.6971 | 3.038 | 3.038 | 2020-01-15 02:00 | 1.3318 | 2.1825 | 3.5826 | 3.5826 | 3.5826 | 3.5826
2021-11-17 14:00 | 2.0148 | 2.4518 | 2.3989 | 2.5803 | 2.4443 | 2.6256 | 1.306 | 2.2397 | 2.7636 | 2.7636 | 3.1129 | 3.1129 | 2020-01-15 03:00 | 1.3765 | 2.2559 | 3.7031 | 3.7031 | 3.7031 | 3.7031
2021-11-17 15:00 | 1.7976 | 2.1875 | 2.1403 | 2.3021 | 2.1808 | 2.3425 | 1.1546 | 1.9799 | 2.4431 | 2.4431 | 2.7519 | 2.7519 | 2020-01-15 04:00 | 1.3718 | 2.2481 | 3.6903 | 3.6903 | 3.6903 | 3.6903
2021-11-17 16:00 | 1.8348 | 2.2327 | 2.1845 | 2.3497 | 2.2258 | 2.391 | 1.263 | 2.1658 | 2.6725 | 2.6725 | 3.0103 | 3.0103 | 2020-01-15 05:00 | 1.4204 | 2.3277 | 3.821 | 3.821 | 3.821 | 3.821
2021-11-17 17:00 | 2.2406 | 2.7266 | 2.6677 | 2.8694 | 2.7181 | 2.9198 | 1.4061 | 2.4112 | 2.9753 | 2.9753 | 3.3513 | 3.3513 | 2020-01-15 06:00 | 1.5909 | 2.6072 | 4.2797 | 4.2797 | 4.2797 | 4.2797
2021-11-17 18:00 | 2.392 | 2.9109 | 2.8481 | 3.0634 | 2.9019 | 3.1172 | 1.5375 | 2.6366 | 3.2534 | 3.2534 | 3.6647 | 3.6647 | 2020-01-15 07:00 | 2.2387 | 3.6688 | 6.0223 | 6.0223 | 6.0223 | 6.0223
2021-11-17 19:00 | 2.2464 | 2.7337 | 2.6747 | 2.8769 | 2.7253 | 2.9274 | 1.6347 | 2.8033 | 3.4591 | 3.4591 | 3.8963 | 3.8963 | 2020-01-15 08:00 | 2.7731 | 4.5446 | 7.46 | 7.46 | 7.46 | 7.46
2021-11-17 20:00 | 2.3149 | 2.817 | 2.7562 | 2.9645 | 2.8083 | 3.0166 | 1.6576 | 2.8425 | 3.5074 | 3.5074 | 3.9507 | 3.9507 | 2020-01-15 09:00 | 2.6588 | 4.3572 | 7.1525 | 7.1525 | 7.1525 | 7.1525
2021-11-17 21:00 | 2.2577 | 2.7474 | 2.6882 | 2.8913 | 2.739 | 2.9421 | 1.5518 | 2.6611 | 3.2837 | 3.2837 | 3.6987 | 3.6987 | 2020-01-15 10:00 | 2.876 | 4.7132 | 7.7368 | 7.7368 | 7.7368 | 7.7368
2021-11-17 22:00 | 1.9891 | 2.4205 | 2.3683 | 2.5473 | 2.4131 | 2.5921 | 1.3491 | 2.3135 | 2.8547 | 2.8547 | 3.2155 | 3.2155 | 2020-01-15 11:00 | 3.0027 | 4.9208 | 8.0776 | 8.0776 | 8.0776 | 8.0776
2021-11-17 23:00 | 1.7147 | 2.0866 | 2.0416 | 2.196 | 2.0802 | 2.2345 | 1.1489 | 1.9701 | 2.431 | 2.431 | 2.7383 | 2.7383 | 2020-01-15 12:00 | 2.9693 | 4.8662 | 7.9879 | 7.9879 | 7.9879 | 7.9879
2021-11-18 | 1.6118 | 1.9614 | 1.9191 | 2.0642 | 1.9554 | 2.1005 | 1.0031 | 1.7202 | 2.1226 | 2.1226 | 2.3909 | 2.3909 | 2020-01-15 13:00 | 2.9674 | 4.8631 | 7.9828 | 7.9828 | 7.9828 | 7.9828
2021-11-18 01:00 | 1.5032 | 1.8293 | 1.7898 | 1.9251 | 1.8237 | 1.9589 | 0.8752 | 1.5008 | 1.8519 | 1.8519 | 2.086 | 2.086 | 2020-01-15 14:00 | 3.0408 | 4.9833 | 8.1801 | 8.1801 | 8.1801 | 8.1801
2021-11-18 02:00 | 1.4804 | 1.8015 | 1.7626 | 1.8958 | 1.7959 | 1.9292 | 0.77453 | 1.3282 | 1.6389 | 1.6389 | 1.846 | 1.846 | 2020-01-15 15:00 | 3.0751 | 5.0395 | 8.2724 | 8.2724 | 8.2724 | 8.2724
2021-11-18 03:00 | 1.5032 | 1.8293 | 1.7898 | 1.9251 | 1.8237 | 1.9589 | 0.76591 | 1.3134 | 1.6207 | 1.6207 | 1.8255 | 1.8255 | 2020-01-15 16:00 | 2.9674 | 4.8631 | 7.9828 | 7.9828 | 7.9828 | 7.9828
2021-11-18 04:00 | 1.4975 | 1.8223 | 1.783 | 1.9178 | 1.8167 | 1.9515 | 0.76306 | 1.3085 | 1.6146 | 1.6146 | 1.8187 | 1.8187 | 2020-01-15 17:00 | 2.8017 | 4.5914 | 7.5369 | 7.5369 | 7.5369 | 7.5369
2021-11-18 05:00 | 1.6473 | 2.0046 | 1.9614 | 2.1096 | 1.9985 | 2.1467 | 0.80013 | 1.3721 | 1.6931 | 1.6931 | 1.9071 | 1.9071 | 2020-01-15 18:00 | 2.2387 | 3.6688 | 6.0223 | 6.0223 | 6.0223 | 6.0223
2021-11-18 06:00 | 2.3635 | 2.8761 | 2.8141 | 3.0268 | 2.8672 | 3.0799 | 0.86594 | 1.4849 | 1.8323 | 1.8323 | 2.0639 | 2.0639 | 2020-01-15 19:00 | 2.0739 | 3.3987 | 5.579 | 5.579 | 5.579 | 5.579
2021-11-18 07:00 | 2.4378 | 2.9665 | 2.9025 | 3.1219 | 2.9574 | 3.1768 | 1.126 | 1.9309 | 2.3826 | 2.3826 | 2.6838 | 2.6838 | 2020-01-15 20:00 | 2.0348 | 3.3347 | 5.4739 | 5.4739 | 5.4739 | 5.4739
2021-11-18 08:00 | 2.4235 | 2.9491 | 2.8855 | 3.1036 | 2.94 | 3.1582 | 1.1974 | 2.0534 | 2.5338 | 2.5338 | 2.8541 | 2.8541 | 2020-01-15 21:00 | 2.03 | 3.3269 | 5.4611 | 5.4611 | 5.4611 | 5.4611
2021-11-18 09:00 | 2.2806 | 2.7752 | 2.7154 | 2.9206 | 2.7667 | 2.9719 | 1.1689 | 2.0044 | 2.4733 | 2.4733 | 2.786 | 2.786 | 2020-01-15 22:00 | 1.8233 | 2.9881 | 4.905 | 4.905 | 4.905 | 4.905
2021-11-18 10:00 | 1.9634 | 2.3892 | 2.3377 | 2.5144 | 2.3818 | 2.5585 | 1.206 | 2.0681 | 2.552 | 2.552 | 2.8745 | 2.8745 | 2020-01-15 23:00 | 1.7366 | 2.846 | 4.6718 | 4.6718 | 4.6718 | 4.6718
2021-11-18 11:00 | 1.9805 | 2.4101 | 2.3581 | 2.5363 | 2.4026 | 2.5809 | 1.2289 | 2.1073 | 2.6003 | 2.6003 | 2.929 | 2.929 | 2020-01-16 | 1.5785 | 2.5869 | 4.2464 | 4.2464 | 4.2464 | 4.2464
2021-11-18 12:00 | 1.8662 | 2.271 | 2.222 | 2.3899 | 2.264 | 2.4319 | 1.1974 | 2.0534 | 2.5338 | 2.5338 | 2.8541 | 2.8541 | 2020-01-16 01:00 | 1.5299 | 2.5072 | 4.1157 | 4.1157 | 4.1157 | 4.1157
2021-11-18 13:00 | 1.8833 | 2.2918 | 2.2424 | 2.4119 | 2.2848 | 2.4543 | 1.2146 | 2.0828 | 2.5701 | 2.5701 | 2.8949 | 2.8949 | 2020-01-16 02:00 | 1.4937 | 2.4479 | 4.0183 | 4.0183 | 4.0183 | 4.0183
2021-11-18 14:00 | 1.7403 | 2.1178 | 2.0721 | 2.2288 | 2.1113 | 2.2679 | 1.1889 | 2.0387 | 2.5157 | 2.5157 | 2.8336 | 2.8336 | 2020-01-16 03:00 | 1.4766 | 2.4198 | 3.9722 | 3.9722 | 3.9722 | 3.9722
2021-11-18 15:00 | 1.8691 | 2.2744 | 2.2254 | 2.3936 | 2.2674 | 2.4356 | 1.1431 | 1.9603 | 2.4189 | 2.4189 | 2.7246 | 2.7246 | 2020-01-16 04:00 | 1.5242 | 2.4979 | 4.1003 | 4.1003 | 4.1003 | 4.1003
2021-11-18 16:00 | 1.8862 | 2.2953 | 2.2458 | 2.4156 | 2.2882 | 2.458 | 1.2489 | 2.1416 | 2.6427 | 2.6427 | 2.9767 | 2.9767 | 2020-01-16 05:00 | 1.5909 | 2.6072 | 4.2797 | 4.2797 | 4.2797 | 4.2797
2021-11-18 17:00 | 2.0377 | 2.4796 | 2.4261 | 2.6095 | 2.472 | 2.6554 | 1.3603 | 2.3328 | 2.8785 | 2.8785 | 3.2423 | 3.2423 | 2020-01-16 06:00 | 1.7195 | 2.8179 | 4.6257 | 4.6257 | 4.6257 | 4.6257
2021-11-18 18:00 | 2.2234 | 2.7057 | 2.6473 | 2.8474 | 2.6973 | 2.8975 | 1.4432 | 2.4749 | 3.0539 | 3.0539 | 3.4399 | 3.4399 | 2020-01-16 07:00 | 2.5569 | 4.1902 | 6.8783 | 6.8783 | 6.8783 | 6.8783
2021-11-18 19:00 | 2.2349 | 2.7196 | 2.6609 | 2.8621 | 2.7112 | 2.9124 | 1.589 | 2.7248 | 3.3623 | 3.3623 | 3.7873 | 3.7873 | 2020-01-16 08:00 | 2.7617 | 4.5259 | 7.4293 | 7.4293 | 7.4293 | 7.4293
2021-11-18 20:00 | 2.2091 | 2.6883 | 2.6303 | 2.8291 | 2.68 | 2.8788 | 1.5547 | 2.666 | 3.2897 | 3.2897 | 3.7055 | 3.7055 | 2020-01-16 09:00 | 2.8846 | 4.7272 | 7.7598 | 7.7598 | 7.7598 | 7.7598
2021-11-18 21:00 | 2.0851 | 2.5374 | 2.4826 | 2.6703 | 2.5295 | 2.7172 | 1.5518 | 2.6611 | 3.2837 | 3.2837 | 3.6987 | 3.6987 | 2020-01-16 10:00 | 2.9827 | 4.888 | 8.0238 | 8.0238 | 8.0238 | 8.0238
2021-11-18 22:00 | 1.8833 | 2.2918 | 2.2424 | 2.4119 | 2.2848 | 2.4543 | 1.3261 | 2.274 | 2.8059 | 2.8059 | 3.1606 | 3.1606 | 2020-01-16 11:00 | 2.9912 | 4.9021 | 8.0469 | 8.0469 | 8.0469 | 8.0469
2021-11-18 23:00 | 1.6776 | 2.0414 | 1.9974 | 2.1484 | 2.0351 | 2.1861 | 1.1746 | 2.0142 | 2.4854 | 2.4854 | 2.7996 | 2.7996 | 2020-01-16 12:00 | 3.0665 | 5.0254 | 8.2493 | 8.2493 | 8.2493 | 8.2493
2021-11-19 | 1.5264 | 1.8575 | 1.8174 | 1.9548 | 1.8517 | 1.9891 | 0.99676 | 1.7093 | 2.1092 | 2.1092 | 2.3757 | 2.3757 | 2020-01-16 13:00 | 3.0341 | 4.9724 | 8.1622 | 8.1622 | 8.1622 | 8.1622
2021-11-19 01:00 | 1.4604 | 1.7771 | 1.7388 | 1.8702 | 1.7716 | 1.9031 | 0.85472 | 1.4657 | 1.8086 | 1.8086 | 2.0372 | 2.0372 | 2020-01-16 14:00 | 2.9874 | 4.8959 | 8.0366 | 8.0366 | 8.0366 | 8.0366
2021-11-19 02:00 | 1.4004 | 1.7041 | 1.6673 | 1.7934 | 1.6988 | 1.8249 | 0.8002 | 1.3722 | 1.6932 | 1.6932 | 1.9073 | 1.9073 | 2020-01-16 15:00 | 2.9312 | 4.8037 | 7.8854 | 7.8854 | 7.8854 | 7.8854
2021-11-19 03:00 | 1.3461 | 1.638 | 1.6027 | 1.7238 | 1.633 | 1.7541 | 0.82307 | 1.4114 | 1.7416 | 1.7416 | 1.9617 | 1.9617 | 2020-01-16 16:00 | 2.8607 | 4.6882 | 7.6958 | 7.6958 | 7.6958 | 7.6958
2021-11-19 04:00 | 1.3375 | 1.6276 | 1.5925 | 1.7128 | 1.6226 | 1.7429 | 0.74876 | 1.284 | 1.5844 | 1.5844 | 1.7846 | 1.7846 | 2020-01-16 17:00 | 2.7521 | 4.5102 | 7.4036 | 7.4036 | 7.4036 | 7.4036
2021-11-19 05:00 | 1.5243 | 1.8549 | 1.8149 | 1.9521 | 1.8492 | 1.9864 | 0.8002 | 1.3722 | 1.6932 | 1.6932 | 1.9073 | 1.9073 | 2020-01-16 18:00 | 2.1082 | 3.4549 | 5.6712 | 5.6712 | 5.6712 | 5.6712
2021-11-19 06:00 | 1.7937 | 2.1827 | 2.1356 | 2.2971 | 2.176 | 2.3374 | 0.94024 | 1.6124 | 1.9896 | 1.9896 | 2.241 | 2.241 | 2020-01-16 19:00 | 1.8348 | 3.0068 | 4.9357 | 4.9357 | 4.9357 | 4.9357
2021-11-19 07:00 | 2.1291 | 2.5909 | 2.535 | 2.7266 | 2.5829 | 2.7746 | 1.2032 | 2.0632 | 2.5459 | 2.5459 | 2.8677 | 2.8677 | 2020-01-16 20:00 | 1.8338 | 3.0053 | 4.9332 | 4.9332 | 4.9332 | 4.9332
2021-11-19 08:00 | 2.2349 | 2.7196 | 2.6609 | 2.8621 | 2.7112 | 2.9124 | 1.2175 | 2.0877 | 2.5761 | 2.5761 | 2.9018 | 2.9018 | 2020-01-16 21:00 | 1.8433 | 3.0209 | 4.9588 | 4.9588 | 4.9588 | 4.9588
2021-11-19 09:00 | 2.1949 | 2.6709 | 2.6133 | 2.8108 | 2.6627 | 2.8602 | 1.186 | 2.0338 | 2.5096 | 2.5096 | 2.8268 | 2.8268 | 2020-01-16 22:00 | 1.7328 | 2.8398 | 4.6615 | 4.6615 | 4.6615 | 4.6615
2021-11-19 10:00 | 2.1434 | 2.6083 | 2.552 | 2.7449 | 2.6003 | 2.7932 | 1.146 | 1.9652 | 2.425 | 2.425 | 2.7315 | 2.7315 | 2020-01-16 23:00 | 1.5556 | 2.5494 | 4.1849 | 4.1849 | 4.1849 | 4.1849
2021-11-19 11:00 | 1.9519 | 2.3753 | 2.3241 | 2.4997 | 2.368 | 2.5437 | 1.2003 | 2.0583 | 2.5399 | 2.5399 | 2.8609 | 2.8609 | 2020-01-17 | 1.4966 | 2.4526 | 4.026 | 4.026 | 4.026 | 4.026
2021-11-19 12:00 | 2.152 | 2.6187 | 2.5623 | 2.7559 | 2.6107 | 2.8043 | 1.2456 | 2.136 | 2.6357 | 2.6357 | 2.9688 | 2.9688 | 2020-01-17 01:00 | 1.4023 | 2.2981 | 3.7723 | 3.7723 | 3.7723 | 3.7723
2021-11-19 13:00 | 2.0834 | 2.5353 | 2.4806 | 2.6681 | 2.5275 | 2.715 | 1.266 | 2.1711 | 2.679 | 2.679 | 3.0176 | 3.0176 | 2020-01-17 02:00 | 1.3765 | 2.2559 | 3.7031 | 3.7031 | 3.7031 | 3.7031
2021-11-19 14:00 | 2.1148 | 2.5735 | 2.518 | 2.7083 | 2.5656 | 2.7559 | 1.2889 | 2.2103 | 2.7273 | 2.7273 | 3.072 | 3.072 | 2020-01-17 03:00 | 1.3937 | 2.284 | 3.7492 | 3.7492 | 3.7492 | 3.7492
2021-11-19 15:00 | 2.0491 | 2.4935 | 2.4398 | 2.6242 | 2.4859 | 2.6703 | 1.2317 | 2.1122 | 2.6064 | 2.6064 | 2.9358 | 2.9358 | 2020-01-17 04:00 | 1.4032 | 2.2996 | 3.7748 | 3.7748 | 3.7748 | 3.7748
2021-11-19 16:00 | 1.9948 | 2.4275 | 2.3751 | 2.5546 | 2.42 | 2.5995 | 1.3518 | 2.3181 | 2.8604 | 2.8604 | 3.2219 | 3.2219 | 2020-01-17 05:00 | 1.4766 | 2.4198 | 3.9722 | 3.9722 | 3.9722 | 3.9722
2021-11-19 17:00 | 2.0948 | 2.5492 | 2.4942 | 2.6827 | 2.5413 | 2.7299 | 1.4146 | 2.4259 | 2.9934 | 2.9934 | 3.3718 | 3.3718 | 2020-01-17 06:00 | 1.7652 | 2.8929 | 4.7487 | 4.7487 | 4.7487 | 4.7487
2021-11-19 18:00 | 2.2177 | 2.6987 | 2.6405 | 2.8401 | 2.6904 | 2.89 | 1.5518 | 2.6611 | 3.2837 | 3.2837 | 3.6987 | 3.6987 | 2020-01-17 07:00 | 2.3254 | 3.8108 | 6.2555 | 6.2555 | 6.2555 | 6.2555
2021-11-19 19:00 | 2.0567 | 2.5028 | 2.4488 | 2.634 | 2.4951 | 2.6802 | 1.6147 | 2.769 | 3.4167 | 3.4167 | 3.8486 | 3.8486 | 2020-01-17 08:00 | 2.6197 | 4.2932 | 7.0474 | 7.0474 | 7.0474 | 7.0474
2021-11-19 20:00 | 2.072 | 2.5214 | 2.467 | 2.6535 | 2.5136 | 2.7001 | 1.6318 | 2.7984 | 3.453 | 3.453 | 3.8894 | 3.8894 | 2020-01-17 09:00 | 2.5892 | 4.2433 | 6.9654 | 6.9654 | 6.9654 | 6.9654
2021-11-19 21:00 | 1.8919 | 2.3023 | 2.2526 | 2.4229 | 2.2952 | 2.4654 | 1.549 | 2.6562 | 3.2776 | 3.2776 | 3.6919 | 3.6919 | 2020-01-17 10:00 | 2.6874 | 4.4041 | 7.2294 | 7.2294 | 7.2294 | 7.2294
2021-11-19 22:00 | 1.8033 | 2.1945 | 2.1471 | 2.3094 | 2.1877 | 2.35 | 1.3489 | 2.3132 | 2.8543 | 2.8543 | 3.2151 | 3.2151 | 2020-01-17 11:00 | 2.8855 | 4.7288 | 7.7624 | 7.7624 | 7.7624 | 7.7624
2021-11-19 23:00 | 1.6404 | 1.9962 | 1.9532 | 2.1008 | 1.9901 | 2.1377 | 1.0901 | 1.8693 | 2.3066 | 2.3066 | 2.5982 | 2.5982 | 2020-01-17 12:00 | 2.7455 | 4.4993 | 7.3857 | 7.3857 | 7.3857 | 7.3857
2021-11-20 | 1.5045 | 1.8309 | 1.7914 | 1.9268 | 1.8252 | 1.9606 | 0.96571 | 1.656 | 2.0435 | 2.0435 | 2.3017 | 2.3017 | 2020-01-17 13:00 | 2.7617 | 4.5259 | 7.4293 | 7.4293 | 7.4293 | 7.4293
2021-11-20 01:00 | 1.4432 | 1.7563 | 1.7184 | 1.8483 | 1.7508 | 1.8807 | 0.8002 | 1.3722 | 1.6932 | 1.6932 | 1.9073 | 1.9073 | 2020-01-17 14:00 | 2.7455 | 4.4993 | 7.3857 | 7.3857 | 7.3857 | 7.3857
2021-11-20 02:00 | 1.4089 | 1.7145 | 1.6775 | 1.8043 | 1.7092 | 1.836 | 0.78877 | 1.3526 | 1.6691 | 1.6691 | 1.88 | 1.88 | 2020-01-17 15:00 | 2.6864 | 4.4025 | 7.2268 | 7.2268 | 7.2268 | 7.2268
2021-11-20 03:00 | 1.3889 | 1.6902 | 1.6537 | 1.7787 | 1.685 | 1.81 | 0.74305 | 1.2742 | 1.5723 | 1.5723 | 1.771 | 1.771 | 2020-01-17 16:00 | 2.7159 | 4.4509 | 7.3062 | 7.3062 | 7.3062 | 7.3062
2021-11-20 04:00 | 1.3318 | 1.6206 | 1.5857 | 1.7055 | 1.6156 | 1.7355 | 0.73447 | 1.2595 | 1.5542 | 1.5542 | 1.7506 | 1.7506 | 2020-01-17 17:00 | 2.2434 | 3.6766 | 6.0351 | 6.0351 | 6.0351 | 6.0351
2021-11-20 05:00 | 1.3804 | 1.6797 | 1.6435 | 1.7677 | 1.6746 | 1.7988 | 0.7459 | 1.2791 | 1.5783 | 1.5783 | 1.7778 | 1.7778 | 2020-01-17 18:00 | 2.0234 | 3.3159 | 5.4432 | 5.4432 | 5.4432 | 5.4432
2021-11-20 06:00 | 1.5747 | 1.9162 | 1.8749 | 2.0166 | 1.9103 | 2.0521 | 0.72304 | 1.2399 | 1.53 | 1.53 | 1.7233 | 1.7233 | 2020-01-17 19:00 | 1.7347 | 2.8429 | 4.6667 | 4.6667 | 4.6667 | 4.6667
2021-11-20 07:00 | 1.7871 | 2.1747 | 2.1278 | 2.2886 | 2.168 | 2.3289 | 0.96882 | 1.6614 | 2.05 | 2.05 | 2.3091 | 2.3091 | 2020-01-17 20:00 | 1.6919 | 2.7726 | 4.5513 | 4.5513 | 4.5513 | 4.5513
2021-11-20 08:00 | 1.9348 | 2.3544 | 2.3036 | 2.4778 | 2.3472 | 2.5213 | 1.026 | 1.7594 | 2.171 | 2.171 | 2.4454 | 2.4454 | 2020-01-17 21:00 | 1.668 | 2.7336 | 4.4873 | 4.4873 | 4.4873 | 4.4873
2021-11-20 09:00 | 1.9634 | 2.3892 | 2.3377 | 2.5144 | 2.3818 | 2.5585 | 1.2775 | 2.1907 | 2.7031 | 2.7031 | 3.0448 | 3.0448 | 2020-01-17 22:00 | 1.6061 | 2.6321 | 4.3207 | 4.3207 | 4.3207 | 4.3207
2021-11-20 10:00 | 2.0434 | 2.4866 | 2.4329 | 2.6169 | 2.4789 | 2.6628 | 1.3775 | 2.3622 | 2.9148 | 2.9148 | 3.2832 | 3.2832 | 2020-01-17 23:00 | 1.4794 | 2.4245 | 3.9799 | 3.9799 | 3.9799 | 3.9799
2021-11-20 11:00 | 2.1234 | 2.584 | 2.5282 | 2.7193 | 2.576 | 2.7671 | 1.4689 | 2.519 | 3.1083 | 3.1083 | 3.5012 | 3.5012 | 2020-01-18 | 1.408 | 2.3074 | 3.7877 | 3.7877 | 3.7877 | 3.7877
2021-11-20 12:00 | 2.1005 | 2.5561 | 2.501 | 2.69 | 2.5483 | 2.7373 | 1.5175 | 2.6023 | 3.2111 | 3.2111 | 3.617 | 3.617 | 2020-01-18 01:00 | 1.3832 | 2.2668 | 3.721 | 3.721 | 3.721 | 3.721
2021-11-20 13:00 | 2.1291 | 2.5909 | 2.535 | 2.7266 | 2.5829 | 2.7746 | 1.5461 | 2.6513 | 3.2716 | 3.2716 | 3.6851 | 3.6851 | 2020-01-18 02:00 | 1.3632 | 2.234 | 3.6672 | 3.6672 | 3.6672 | 3.6672
2021-11-20 14:00 | 1.9376 | 2.3579 | 2.307 | 2.4814 | 2.3506 | 2.525 | 1.5004 | 2.5729 | 3.1748 | 3.1748 | 3.5761 | 3.5761 | 2020-01-18 03:00 | 1.3299 | 2.1794 | 3.5775 | 3.5775 | 3.5775 | 3.5775
2021-11-20 15:00 | 1.8519 | 2.2536 | 2.205 | 2.3716 | 2.2466 | 2.4133 | 1.489 | 2.5533 | 3.1506 | 3.1506 | 3.5489 | 3.5489 | 2020-01-18 04:00 | 1.3432 | 2.2013 | 3.6134 | 3.6134 | 3.6134 | 3.6134
2021-11-20 16:00 | 1.8289 | 2.2256 | 2.1776 | 2.3422 | 2.2187 | 2.3833 | 1.4118 | 2.421 | 2.9874 | 2.9874 | 3.3649 | 3.3649 | 2020-01-18 05:00 | 1.3861 | 2.2715 | 3.7287 | 3.7287 | 3.7287 | 3.7287
2021-11-20 17:00 | 2.0462 | 2.4901 | 2.4364 | 2.6205 | 2.4824 | 2.6666 | 1.5766 | 2.7037 | 3.3362 | 3.3362 | 3.7579 | 3.7579 | 2020-01-18 06:00 | 1.5871 | 2.6009 | 4.2694 | 4.2694 | 4.2694 | 4.2694
2021-11-20 18:00 | 2.0377 | 2.4796 | 2.4261 | 2.6095 | 2.472 | 2.6554 | 1.5775 | 2.7052 | 3.3381 | 3.3381 | 3.76 | 3.76 | 2020-01-18 07:00 | 1.7328 | 2.8398 | 4.6615 | 4.6615 | 4.6615 | 4.6615
2021-11-20 19:00 | 2.0577 | 2.504 | 2.45 | 2.6352 | 2.4963 | 2.6814 | 1.529 | 2.6219 | 3.2353 | 3.2353 | 3.6442 | 3.6442 | 2020-01-18 08:00 | 2.2034 | 3.611 | 5.9275 | 5.9275 | 5.9275 | 5.9275
2021-11-20 20:00 | 1.9862 | 2.417 | 2.3649 | 2.5437 | 2.4096 | 2.5883 | 1.4575 | 2.4994 | 3.0841 | 3.0841 | 3.4739 | 3.4739 | 2020-01-18 09:00 | 2.2653 | 3.7125 | 6.0941 | 6.0941 | 6.0941 | 6.0941
2021-11-20 21:00 | 1.8833 | 2.2918 | 2.2424 | 2.4119 | 2.2848 | 2.4543 | 1.5004 | 2.5729 | 3.1748 | 3.1748 | 3.5761 | 3.5761 | 2020-01-18 10:00 | 2.0186 | 3.3081 | 5.4303 | 5.4303 | 5.4303 | 5.4303
2021-11-20 22:00 | 1.7776 | 2.1632 | 2.1165 | 2.2765 | 2.1565 | 2.3165 | 1.3462 | 2.3085 | 2.8486 | 2.8486 | 3.2086 | 3.2086 | 2020-01-18 11:00 | 2.3492 | 3.8499 | 6.3196 | 6.3196 | 6.3196 | 6.3196
2021-11-20 23:00 | 1.669 | 2.031 | 1.9872 | 2.1374 | 2.0247 | 2.175 | 1.0831 | 1.8574 | 2.2919 | 2.2919 | 2.5816 | 2.5816 | 2020-01-18 12:00 | 2.3425 | 3.8389 | 6.3017 | 6.3017 | 6.3017 | 6.3017
2021-11-21 | 1.6776 | 2.0414 | 1.9974 | 2.1484 | 2.0351 | 2.1861 | 1.0603 | 1.8182 | 2.2435 | 2.2435 | 2.5271 | 2.5271 | 2020-01-18 13:00 | 2.4902 | 4.0809 | 6.6989 | 6.6989 | 6.6989 | 6.6989
2021-11-21 01:00 | 1.4804 | 1.8015 | 1.7626 | 1.8958 | 1.7959 | 1.9292 | 0.9088 | 1.5585 | 1.923 | 1.923 | 2.1661 | 2.1661 | 2020-01-18 14:00 | 2.4321 | 3.9857 | 6.5426 | 6.5426 | 6.5426 | 6.5426
2021-11-21 02:00 | 1.4568 | 1.7728 | 1.7346 | 1.8657 | 1.7673 | 1.8984 | 0.82592 | 1.4163 | 1.7477 | 1.7477 | 1.9686 | 1.9686 | 2020-01-18 15:00 | 2.5283 | 4.1434 | 6.8014 | 6.8014 | 6.8014 | 6.8014
2021-11-21 03:00 | 1.4604 | 1.7771 | 1.7388 | 1.8702 | 1.7716 | 1.9031 | 0.78877 | 1.3526 | 1.6691 | 1.6691 | 1.88 | 1.88 | 2020-01-18 16:00 | 2.3416 | 3.8374 | 6.2991 | 6.2991 | 6.2991 | 6.2991
2021-11-21 04:00 | 1.4775 | 1.798 | 1.7592 | 1.8922 | 1.7925 | 1.9254 | 0.78306 | 1.3428 | 1.657 | 1.657 | 1.8664 | 1.8664 | 2020-01-18 17:00 | 1.9005 | 3.1145 | 5.1126 | 5.1126 | 5.1126 | 5.1126
2021-11-21 05:00 | 1.4461 | 1.7597 | 1.7218 | 1.8519 | 1.7543 | 1.8845 | 0.71522 | 1.2265 | 1.5134 | 1.5134 | 1.7047 | 1.7047 | 2020-01-18 18:00 | 1.8052 | 2.9584 | 4.8563 | 4.8563 | 4.8563 | 4.8563
2021-11-21 06:00 | 1.5311 | 1.8631 | 1.823 | 1.9607 | 1.8574 | 1.9952 | 0.78185 | 1.3407 | 1.6544 | 1.6544 | 1.8635 | 1.8635 | 2020-01-18 19:00 | 1.6652 | 2.7289 | 4.4796 | 4.4796 | 4.4796 | 4.4796
2021-11-21 07:00 | 1.7262 | 2.1006 | 2.0552 | 2.2106 | 2.0941 | 2.2494 | 0.88822 | 1.5232 | 1.8795 | 1.8795 | 2.117 | 2.117 | 2020-01-18 20:00 | 1.5566 | 2.551 | 4.1874 | 4.1874 | 4.1874 | 4.1874
2021-11-21 08:00 | 1.8548 | 2.2571 | 2.2084 | 2.3753 | 2.2501 | 2.417 | 1.1231 | 1.926 | 2.3766 | 2.3766 | 2.677 | 2.677 | 2020-01-18 21:00 | 1.5947 | 2.6134 | 4.2899 | 4.2899 | 4.2899 | 4.2899
2021-11-21 09:00 | 1.8376 | 2.2362 | 2.188 | 2.3533 | 2.2293 | 2.3947 | 1.3375 | 2.2936 | 2.8301 | 2.8301 | 3.1878 | 3.1878 | 2020-01-18 22:00 | 1.5642 | 2.5635 | 4.2079 | 4.2079 | 4.2079 | 4.2079
2021-11-21 10:00 | 1.9634 | 2.3892 | 2.3377 | 2.5144 | 2.3818 | 2.5585 | 1.509 | 2.5876 | 3.193 | 3.193 | 3.5965 | 3.5965 | 2020-01-18 23:00 | 1.487 | 2.437 | 4.0004 | 4.0004 | 4.0004 | 4.0004
2021-11-21 11:00 | 1.9691 | 2.3962 | 2.3445 | 2.5217 | 2.3888 | 2.566 | 1.4861 | 2.5484 | 3.1446 | 3.1446 | 3.542 | 3.542 | 2020-01-19 | 1.3565 | 2.2231 | 3.6493 | 3.6493 | 3.6493 | 3.6493
2021-11-21 12:00 | 1.9862 | 2.417 | 2.3649 | 2.5437 | 2.4096 | 2.5883 | 1.5318 | 2.6268 | 3.2414 | 3.2414 | 3.651 | 3.651 | 2020-01-19 01:00 | 1.3546 | 2.22 | 3.6441 | 3.6441 | 3.6441 | 3.6441
2021-11-21 13:00 | 1.9005 | 2.3127 | 2.2628 | 2.4339 | 2.3056 | 2.4766 | 1.4947 | 2.5631 | 3.1627 | 3.1627 | 3.5625 | 3.5625 | 2020-01-19 02:00 | 1.2889 | 2.1123 | 3.4673 | 3.4673 | 3.4673 | 3.4673
2021-11-21 14:00 | 1.8784 | 2.2858 | 2.2365 | 2.4056 | 2.2788 | 2.4479 | 1.5032 | 2.5778 | 3.1809 | 3.1809 | 3.5829 | 3.5829 | 2020-01-19 03:00 | 1.2746 | 2.0889 | 3.4289 | 3.4289 | 3.4289 | 3.4289
2021-11-21 15:00 | 1.8605 | 2.264 | 2.2152 | 2.3826 | 2.257 | 2.4245 | 1.4318 | 2.4553 | 3.0297 | 3.0297 | 3.4126 | 3.4126 | 2020-01-19 04:00 | 1.3384 | 2.1935 | 3.6006 | 3.6006 | 3.6006 | 3.6006
2021-11-21 16:00 | 1.9091 | 2.3231 | 2.273 | 2.4448 | 2.316 | 2.4878 | 1.4689 | 2.519 | 3.1083 | 3.1083 | 3.5012 | 3.5012 | 2020-01-19 05:00 | 1.4737 | 2.4151 | 3.9645 | 3.9645 | 3.9645 | 3.9645
2021-11-21 17:00 | 2.1091 | 2.5666 | 2.5112 | 2.701 | 2.5587 | 2.7485 | 1.5147 | 2.5974 | 3.2051 | 3.2051 | 3.6102 | 3.6102 | 2020-01-19 06:00 | 1.4909 | 2.4432 | 4.0106 | 4.0106 | 4.0106 | 4.0106
2021-11-21 18:00 | 2.2234 | 2.7057 | 2.6473 | 2.8474 | 2.6973 | 2.8975 | 1.6633 | 2.8523 | 3.5195 | 3.5195 | 3.9644 | 3.9644 | 2020-01-19 07:00 | 1.7938 | 2.9397 | 4.8256 | 4.8256 | 4.8256 | 4.8256
2021-11-21 19:00 | 2.2406 | 2.7266 | 2.6677 | 2.8694 | 2.7181 | 2.9198 | 1.6519 | 2.8327 | 3.4953 | 3.4953 | 3.9371 | 3.9371 | 2020-01-19 08:00 | 2.2634 | 3.7094 | 6.089 | 6.089 | 6.089 | 6.089
2021-11-21 20:00 | 2.3406 | 2.8483 | 2.7868 | 2.9975 | 2.8395 | 3.0501 | 1.5976 | 2.7395 | 3.3804 | 3.3804 | 3.8077 | 3.8077 | 2020-01-19 09:00 | 2.1225 | 3.4783 | 5.7097 | 5.7097 | 5.7097 | 5.7097
2021-11-21 21:00 | 2.172 | 2.6431 | 2.5861 | 2.7815 | 2.6349 | 2.8304 | 1.5061 | 2.5827 | 3.1869 | 3.1869 | 3.5897 | 3.5897 | 2020-01-19 10:00 | 2.2539 | 3.6937 | 6.0633 | 6.0633 | 6.0633 | 6.0633
2021-11-21 22:00 | 1.9205 | 2.337 | 2.2866 | 2.4595 | 2.3298 | 2.5027 | 1.3289 | 2.2789 | 2.812 | 2.812 | 3.1674 | 3.1674 | 2020-01-19 11:00 | 2.5092 | 4.1121 | 6.7501 | 6.7501 | 6.7501 | 6.7501
2021-11-21 23:00 | 1.6947 | 2.0623 | 2.0178 | 2.1703 | 2.0559 | 2.2085 | 1.0889 | 1.8673 | 2.3042 | 2.3042 | 2.5954 | 2.5954 | 2020-01-19 12:00 | 2.5302 | 4.1465 | 6.8065 | 6.8065 | 6.8065 | 6.8065
2021-11-22 | 1.6261 | 1.9788 | 1.9361 | 2.0825 | 1.9727 | 2.1191 | 0.97453 | 1.6712 | 2.0621 | 2.0621 | 2.3228 | 2.3228 | 2020-01-19 13:00 | 2.6007 | 4.262 | 6.9962 | 6.9962 | 6.9962 | 6.9962
2021-11-22 01:00 | 1.5175 | 1.8467 | 1.8068 | 1.9434 | 1.841 | 1.9776 | 0.86022 | 1.4751 | 1.8202 | 1.8202 | 2.0503 | 2.0503 | 2020-01-19 14:00 | 2.5302 | 4.1465 | 6.8065 | 6.8065 | 6.8065 | 6.8065
2021-11-22 02:00 | 1.4718 | 1.791 | 1.7524 | 1.8849 | 1.7855 | 1.918 | 0.76878 | 1.3183 | 1.6268 | 1.6268 | 1.8324 | 1.8324 | 2020-01-19 15:00 | 2.5054 | 4.1059 | 6.7399 | 6.7399 | 6.7399 | 6.7399
2021-11-22 03:00 | 1.4632 | 1.7806 | 1.7422 | 1.8739 | 1.7751 | 1.9068 | 0.78306 | 1.3428 | 1.657 | 1.657 | 1.8664 | 1.8664 | 2020-01-19 16:00 | 2.554 | 4.1855 | 6.8706 | 6.8706 | 6.8706 | 6.8706
2021-11-22 04:00 | 1.4975 | 1.8223 | 1.783 | 1.9178 | 1.8167 | 1.9515 | 0.73733 | 1.2644 | 1.5602 | 1.5602 | 1.7574 | 1.7574 | 2020-01-19 17:00 | 2.0205 | 3.3113 | 5.4355 | 5.4355 | 5.4355 | 5.4355
2021-11-22 05:00 | 1.6346 | 1.9892 | 1.9462 | 2.0934 | 1.983 | 2.1301 | 0.76305 | 1.3085 | 1.6146 | 1.6146 | 1.8187 | 1.8187 | 2020-01-19 18:00 | 1.8186 | 2.9803 | 4.8922 | 4.8922 | 4.8922 | 4.8922
2021-11-22 06:00 | 2.1863 | 2.6605 | 2.6031 | 2.7998 | 2.6523 | 2.849 | 0.9088 | 1.5585 | 1.923 | 1.923 | 2.1661 | 2.1661 | 2020-01-19 19:00 | 1.7338 | 2.8413 | 4.6641 | 4.6641 | 4.6641 | 4.6641
2021-11-22 07:00 | 2.4406 | 2.97 | 2.9059 | 3.1256 | 2.9608 | 3.1805 | 1.126 | 1.9309 | 2.3826 | 2.3826 | 2.6838 | 2.6838 | 2020-01-19 20:00 | 1.7062 | 2.7961 | 4.5898 | 4.5898 | 4.5898 | 4.5898
2021-11-22 08:00 | 2.5178 | 3.0639 | 2.9978 | 3.2244 | 3.0545 | 3.2811 | 1.2832 | 2.2005 | 2.7152 | 2.7152 | 3.0584 | 3.0584 | 2020-01-19 21:00 | 1.7528 | 2.8726 | 4.7154 | 4.7154 | 4.7154 | 4.7154
2021-11-22 09:00 | 2.4721 | 3.0082 | 2.9434 | 3.1658 | 2.999 | 3.2215 | 1.2346 | 2.1171 | 2.6124 | 2.6124 | 2.9426 | 2.9426 | 2020-01-19 22:00 | 1.6109 | 2.6399 | 4.3335 | 4.3335 | 4.3335 | 4.3335
2021-11-22 10:00 | 2.332 | 2.8378 | 2.7766 | 2.9865 | 2.8291 | 3.039 | 1.243 | 2.1316 | 2.6302 | 2.6302 | 2.9627 | 2.9627 | 2020-01-19 23:00 | 1.5537 | 2.5463 | 4.1798 | 4.1798 | 4.1798 | 4.1798
2021-11-22 11:00 | 2.3292 | 2.8344 | 2.7732 | 2.9828 | 2.8256 | 3.0353 | 1.2918 | 2.2152 | 2.7334 | 2.7334 | 3.0789 | 3.0789 | 2020-01-20 | 1.4442 | 2.3667 | 3.885 | 3.885 | 3.885 | 3.885
2021-11-22 12:00 | 2.4006 | 2.9213 | 2.8583 | 3.0743 | 2.9123 | 3.1284 | 1.4261 | 2.4455 | 3.0176 | 3.0176 | 3.399 | 3.399 | 2020-01-20 01:00 | 1.4023 | 2.2981 | 3.7723 | 3.7723 | 3.7723 | 3.7723
2021-11-22 13:00 | 2.2977 | 2.7961 | 2.7358 | 2.9426 | 2.7875 | 2.9943 | 1.3632 | 2.3377 | 2.8846 | 2.8846 | 3.2491 | 3.2491 | 2020-01-20 02:00 | 1.4004 | 2.2949 | 3.7672 | 3.7672 | 3.7672 | 3.7672
2021-11-22 14:00 | 2.1205 | 2.5805 | 2.5248 | 2.7157 | 2.5725 | 2.7634 | 1.2803 | 2.1956 | 2.7092 | 2.7092 | 3.0516 | 3.0516 | 2020-01-20 03:00 | 1.3842 | 2.2684 | 3.7236 | 3.7236 | 3.7236 | 3.7236
2021-11-22 15:00 | 2.0262 | 2.4657 | 2.4125 | 2.5949 | 2.4581 | 2.6405 | 1.2746 | 2.1858 | 2.6971 | 2.6971 | 3.038 | 3.038 | 2020-01-20 04:00 | 1.4204 | 2.3277 | 3.821 | 3.821 | 3.821 | 3.821
2021-11-22 16:00 | 2.0148 | 2.4518 | 2.3989 | 2.5803 | 2.4443 | 2.6256 | 1.2718 | 2.1809 | 2.691 | 2.691 | 3.0312 | 3.0312 | 2020-01-20 05:00 | 1.5271 | 2.5026 | 4.108 | 4.108 | 4.108 | 4.108
2021-11-22 17:00 | 2.2349 | 2.7196 | 2.6609 | 2.8621 | 2.7112 | 2.9124 | 1.4689 | 2.519 | 3.1083 | 3.1083 | 3.5012 | 3.5012 | 2020-01-20 06:00 | 1.9586 | 3.2098 | 5.2689 | 5.2689 | 5.2689 | 5.2689
2021-11-22 18:00 | 2.4063 | 2.9283 | 2.8651 | 3.0817 | 2.9192 | 3.1358 | 1.5061 | 2.5827 | 3.1869 | 3.1869 | 3.5897 | 3.5897 | 2020-01-20 07:00 | 2.5711 | 4.2136 | 6.9167 | 6.9167 | 6.9167 | 6.9167
2021-11-22 19:00 | 2.3549 | 2.8657 | 2.8038 | 3.0158 | 2.8568 | 3.0688 | 1.549 | 2.6562 | 3.2776 | 3.2776 | 3.6919 | 3.6919 | 2020-01-20 08:00 | 2.7617 | 4.5259 | 7.4293 | 7.4293 | 7.4293 | 7.4293
2021-11-22 20:00 | 2.4606 | 2.9943 | 2.9297 | 3.1512 | 2.9851 | 3.2066 | 1.6061 | 2.7543 | 3.3986 | 3.3986 | 3.8281 | 3.8281 | 2020-01-20 09:00 | 2.7598 | 4.5227 | 7.4241 | 7.4241 | 7.4241 | 7.4241
2021-11-22 21:00 | 2.3835 | 2.9004 | 2.8379 | 3.0524 | 2.8915 | 3.106 | 1.489 | 2.5533 | 3.1506 | 3.1506 | 3.5489 | 3.5489 | 2020-01-20 10:00 | 2.8398 | 4.6539 | 7.6394 | 7.6394 | 7.6394 | 7.6394
2021-11-22 22:00 | 2.0751 | 2.5251 | 2.4707 | 2.6574 | 2.5174 | 2.7041 | 1.3689 | 2.3475 | 2.8967 | 2.8967 | 3.2628 | 3.2628 | 2020-01-20 11:00 | 2.9598 | 4.8506 | 7.9623 | 7.9623 | 7.9623 | 7.9623
2021-11-22 23:00 | 1.7864 | 2.1738 | 2.1269 | 2.2877 | 2.1671 | 2.3279 | 1.1689 | 2.0044 | 2.4733 | 2.4733 | 2.786 | 2.786 | 2020-01-20 12:00 | 2.9541 | 4.8412 | 7.9469 | 7.9469 | 7.9469 | 7.9469
2021-11-23 | 1.7376 | 2.1145 | 2.0689 | 2.2252 | 2.108 | 2.2643 | 1.0317 | 1.7692 | 2.1831 | 2.1831 | 2.459 | 2.459 | 2020-01-20 13:00 | 2.5273 | 4.1418 | 6.7988 | 6.7988 | 6.7988 | 6.7988
2021-11-23 01:00 | 1.5804 | 1.9232 | 1.8817 | 2.0239 | 1.9173 | 2.0595 | 0.82878 | 1.4212 | 1.7537 | 1.7537 | 1.9754 | 1.9754 | 2020-01-20 14:00 | 2.393 | 3.9217 | 6.4375 | 6.4375 | 6.4375 | 6.4375
2021-11-23 02:00 | 1.4404 | 1.7528 | 1.715 | 1.8446 | 1.7474 | 1.877 | 0.7802 | 1.3379 | 1.6509 | 1.6509 | 1.8596 | 1.8596 | 2020-01-20 15:00 | 2.7398 | 4.4899 | 7.3703 | 7.3703 | 7.3703 | 7.3703
2021-11-23 03:00 | 1.5004 | 1.8258 | 1.7864 | 1.9215 | 1.8202 | 1.9552 | 0.73161 | 1.2546 | 1.5481 | 1.5481 | 1.7438 | 1.7438 | 2020-01-20 16:00 | 2.4273 | 3.9779 | 6.5297 | 6.5297 | 6.5297 | 6.5297
2021-11-23 04:00 | 1.4575 | 1.7736 | 1.7354 | 1.8666 | 1.7682 | 1.8994 | 0.71733 | 1.2301 | 1.5179 | 1.5179 | 1.7097 | 1.7097 | 2020-01-20 17:00 | 2.5654 | 4.2043 | 6.9013 | 6.9013 | 6.9013 | 6.9013
2021-11-23 05:00 | 1.6093 | 1.9584 | 1.9161 | 2.061 | 1.9523 | 2.0972 | 0.76877 | 1.3183 | 1.6267 | 1.6267 | 1.8323 | 1.8323 | 2020-01-20 18:00 | 2.011 | 3.2956 | 5.4098 | 5.4098 | 5.4098 | 5.4098
2021-11-23 06:00 | 2.1063 | 2.5631 | 2.5078 | 2.6974 | 2.5552 | 2.7448 | 0.95121 | 1.6312 | 2.0128 | 2.0128 | 2.2672 | 2.2672 | 2020-01-20 19:00 | 1.6852 | 2.7617 | 4.5334 | 4.5334 | 4.5334 | 4.5334
2021-11-23 07:00 | 2.4178 | 2.9422 | 2.8787 | 3.0963 | 2.9331 | 3.1507 | 1.1089 | 1.9015 | 2.3464 | 2.3464 | 2.6429 | 2.6429 | 2020-01-20 20:00 | 1.6471 | 2.6993 | 4.4309 | 4.4309 | 4.4309 | 4.4309
2021-11-23 08:00 | 2.5607 | 3.1161 | 3.0488 | 3.2793 | 3.1065 | 3.3369 | 1.2117 | 2.0779 | 2.5641 | 2.5641 | 2.8881 | 2.8881 | 2020-01-20 21:00 | 1.5899 | 2.6056 | 4.2771 | 4.2771 | 4.2771 | 4.2771
2021-11-23 09:00 | 2.4406 | 2.97 | 2.9059 | 3.1256 | 2.9608 | 3.1805 | 1.2803 | 2.1956 | 2.7092 | 2.7092 | 3.0516 | 3.0516 | 2020-01-20 22:00 | 1.5566 | 2.551 | 4.1874 | 4.1874 | 4.1874 | 4.1874
2021-11-23 10:00 | 2.4263 | 2.9526 | 2.8889 | 3.1073 | 2.9435 | 3.1619 | 1.2918 | 2.2152 | 2.7334 | 2.7334 | 3.0789 | 3.0789 | 2020-01-20 23:00 | 1.4061 | 2.3043 | 3.7825 | 3.7825 | 3.7825 | 3.7825
2021-11-23 11:00 | 2.2863 | 2.7822 | 2.7222 | 2.9279 | 2.7736 | 2.9794 | 1.2975 | 2.225 | 2.7455 | 2.7455 | 3.0925 | 3.0925 | 2020-01-21 | 1.2908 | 2.1154 | 3.4724 | 3.4724 | 3.4724 | 3.4724
2021-11-23 12:00 | 2.2302 | 2.714 | 2.6554 | 2.8562 | 2.7056 | 2.9063 | 1.2117 | 2.0779 | 2.5641 | 2.5641 | 2.8881 | 2.8881 | 2020-01-21 01:00 | 1.2356 | 2.0248 | 3.3238 | 3.3238 | 3.3238 | 3.3238
2021-11-23 13:00 | 2.0805 | 2.5318 | 2.4772 | 2.6644 | 2.524 | 2.7112 | 1.2403 | 2.1269 | 2.6245 | 2.6245 | 2.9562 | 2.9562 | 2020-01-21 02:00 | 1.2032 | 1.9718 | 3.2367 | 3.2367 | 3.2367 | 3.2367
2021-11-23 14:00 | 2.0691 | 2.5179 | 2.4636 | 2.6498 | 2.5101 | 2.6963 | 1.2489 | 2.1416 | 2.6427 | 2.6427 | 2.9767 | 2.9767 | 2020-01-21 03:00 | 1.1832 | 1.939 | 3.1829 | 3.1829 | 3.1829 | 3.1829
2021-11-23 15:00 | 2.0405 | 2.4831 | 2.4295 | 2.6132 | 2.4755 | 2.6591 | 1.2003 | 2.0583 | 2.5399 | 2.5399 | 2.8609 | 2.8609 | 2020-01-21 04:00 | 1.2432 | 2.0373 | 3.3443 | 3.3443 | 3.3443 | 3.3443
2021-11-23 16:00 | 1.9605 | 2.3857 | 2.3343 | 2.5107 | 2.3784 | 2.5548 | 1.3003 | 2.2299 | 2.7515 | 2.7515 | 3.0993 | 3.0993 | 2020-01-21 05:00 | 1.3584 | 2.2262 | 3.6544 | 3.6544 | 3.6544 | 3.6544
2021-11-23 17:00 | 2.112 | 2.5701 | 2.5146 | 2.7047 | 2.5621 | 2.7522 | 1.4146 | 2.4259 | 2.9934 | 2.9934 | 3.3718 | 3.3718 | 2020-01-21 06:00 | 1.5337 | 2.5135 | 4.1259 | 4.1259 | 4.1259 | 4.1259
2021-11-23 18:00 | 2.4035 | 2.9248 | 2.8617 | 3.078 | 2.9158 | 3.1321 | 1.5061 | 2.5827 | 3.1869 | 3.1869 | 3.5897 | 3.5897 | 2020-01-21 07:00 | 2.2892 | 3.7515 | 6.1582 | 6.1582 | 6.1582 | 6.1582
2021-11-23 19:00 | 2.3177 | 2.8205 | 2.7596 | 2.9682 | 2.8118 | 3.0204 | 1.5947 | 2.7346 | 3.3744 | 3.3744 | 3.8009 | 3.8009 | 2020-01-21 08:00 | 2.4025 | 3.9373 | 6.4631 | 6.4631 | 6.4631 | 6.4631
2021-11-23 20:00 | 2.2263 | 2.7092 | 2.6507 | 2.8511 | 2.7008 | 2.9012 | 1.5804 | 2.7101 | 3.3442 | 3.3442 | 3.7668 | 3.7668 | 2020-01-21 09:00 | 2.5969 | 4.2558 | 6.9859 | 6.9859 | 6.9859 | 6.9859
2021-11-23 21:00 | 2.1148 | 2.5735 | 2.518 | 2.7083 | 2.5656 | 2.7559 | 1.5433 | 2.6464 | 3.2655 | 3.2655 | 3.6783 | 3.6783 | 2020-01-21 10:00 | 2.6521 | 4.3463 | 7.1345 | 7.1345 | 7.1345 | 7.1345
2021-11-23 22:00 | 1.9205 | 2.337 | 2.2866 | 2.4595 | 2.3298 | 2.5027 | 1.2674 | 2.1735 | 2.6819 | 2.6819 | 3.0209 | 3.0209 | 2020-01-21 11:00 | 2.7883 | 4.5696 | 7.501 | 7.501 | 7.501 | 7.501
2021-11-23 23:00 | 1.7347 | 2.111 | 2.0655 | 2.2216 | 2.1045 | 2.2606 | 1.126 | 1.9309 | 2.3826 | 2.3826 | 2.6838 | 2.6838 | 2020-01-21 12:00 | 2.9027 | 4.7569 | 7.8085 | 7.8085 | 7.8085 | 7.8085
2021-11-24 | 1.6318 | 1.9858 | 1.943 | 2.0898 | 1.9797 | 2.1265 | 0.98029 | 1.681 | 2.0743 | 2.0743 | 2.3365 | 2.3365 | 2020-01-21 13:00 | 2.8626 | 4.6913 | 7.7009 | 7.7009 | 7.7009 | 7.7009
2021-11-24 01:00 | 1.529 | 1.8606 | 1.8205 | 1.9581 | 1.8549 | 1.9925 | 0.83739 | 1.436 | 1.7719 | 1.7719 | 1.9959 | 1.9959 | 2020-01-21 14:00 | 2.8283 | 4.6351 | 7.6086 | 7.6086 | 7.6086 | 7.6086
2021-11-24 02:00 | 1.4318 | 1.7423 | 1.7048 | 1.8336 | 1.737 | 1.8658 | 0.75448 | 1.2938 | 1.5965 | 1.5965 | 1.7983 | 1.7983 | 2020-01-21 15:00 | 2.8045 | 4.5961 | 7.5446 | 7.5446 | 7.5446 | 7.5446
2021-11-24 03:00 | 1.4661 | 1.7841 | 1.7456 | 1.8775 | 1.7786 | 1.9105 | 0.71733 | 1.2301 | 1.5179 | 1.5179 | 1.7097 | 1.7097 | 2020-01-21 16:00 | 2.7674 | 4.5352 | 7.4446 | 7.4446 | 7.4446 | 7.4446
2021-11-24 04:00 | 1.443 | 1.7559 | 1.7181 | 1.8479 | 1.7505 | 1.8804 | 0.70875 | 1.2154 | 1.4997 | 1.4997 | 1.6893 | 1.6893 | 2020-01-21 17:00 | 2.6759 | 4.3853 | 7.1986 | 7.1986 | 7.1986 | 7.1986
2021-11-24 05:00 | 1.5918 | 1.9371 | 1.8953 | 2.0386 | 1.9311 | 2.0744 | 0.78591 | 1.3477 | 1.663 | 1.663 | 1.8732 | 1.8732 | 2020-01-21 18:00 | 2.0196 | 3.3097 | 5.4329 | 5.4329 | 5.4329 | 5.4329
2021-11-24 06:00 | 1.9033 | 2.3162 | 2.2662 | 2.4375 | 2.309 | 2.4803 | 0.87086 | 1.4934 | 1.8427 | 1.8427 | 2.0756 | 2.0756 | 2020-01-21 19:00 | 1.9281 | 3.1598 | 5.1869 | 5.1869 | 5.1869 | 5.1869
2021-11-24 07:00 | 2.1748 | 2.6466 | 2.5895 | 2.7852 | 2.6384 | 2.8341 | 1.0787 | 1.8497 | 2.2824 | 2.2824 | 2.5709 | 2.5709 | 2020-01-21 20:00 | 1.8119 | 2.9694 | 4.8742 | 4.8742 | 4.8742 | 4.8742
2021-11-24 08:00 | 2.2234 | 2.7057 | 2.6473 | 2.8474 | 2.6973 | 2.8975 | 1.1174 | 1.9162 | 2.3645 | 2.3645 | 2.6633 | 2.6633 | 2020-01-21 21:00 | 1.8052 | 2.9584 | 4.8563 | 4.8563 | 4.8563 | 4.8563
2021-11-24 09:00 | 2.1548 | 2.6222 | 2.5657 | 2.7596 | 2.6141 | 2.8081 | 1.1803 | 2.024 | 2.4975 | 2.4975 | 2.8132 | 2.8132 | 2020-01-21 22:00 | 1.6519 | 2.7071 | 4.4437 | 4.4437 | 4.4437 | 4.4437
2021-11-24 10:00 | 2.2406 | 2.7266 | 2.6677 | 2.8694 | 2.7181 | 2.9198 | 1.2803 | 2.1956 | 2.7092 | 2.7092 | 3.0516 | 3.0516 | 2020-01-21 23:00 | 1.4699 | 2.4089 | 3.9542 | 3.9542 | 3.9542 | 3.9542
2021-11-24 11:00 | 2.3949 | 2.9143 | 2.8515 | 3.067 | 2.9054 | 3.1209 | 1.3403 | 2.2985 | 2.8362 | 2.8362 | 3.1947 | 3.1947 | 2020-01-22 | 1.3594 | 2.2278 | 3.657 | 3.657 | 3.657 | 3.657
2021-11-24 12:00 | 2.2949 | 2.7926 | 2.7324 | 2.9389 | 2.784 | 2.9906 | 1.3632 | 2.3377 | 2.8846 | 2.8846 | 3.2491 | 3.2491 | 2020-01-22 01:00 | 1.2813 | 2.0998 | 3.4468 | 3.4468 | 3.4468 | 3.4468
2021-11-24 13:00 | 2.1748 | 2.6466 | 2.5895 | 2.7852 | 2.6384 | 2.8341 | 1.3346 | 2.2887 | 2.8241 | 2.8241 | 3.181 | 3.181 | 2020-01-22 02:00 | 1.2679 | 2.0779 | 3.4109 | 3.4109 | 3.4109 | 3.4109
2021-11-24 14:00 | 2.152 | 2.6187 | 2.5623 | 2.7559 | 2.6107 | 2.8043 | 1.3146 | 2.2544 | 2.7818 | 2.7818 | 3.1333 | 3.1333 | 2020-01-22 03:00 | 1.2422 | 2.0358 | 3.3417 | 3.3417 | 3.3417 | 3.3417
2021-11-24 15:00 | 2.0891 | 2.5422 | 2.4874 | 2.6754 | 2.5344 | 2.7224 | 1.2146 | 2.0828 | 2.5701 | 2.5701 | 2.8949 | 2.8949 | 2020-01-22 04:00 | 1.2727 | 2.0857 | 3.4238 | 3.4238 | 3.4238 | 3.4238
2021-11-24 16:00 | 2.0577 | 2.504 | 2.45 | 2.6352 | 2.4963 | 2.6814 | 1.2918 | 2.2152 | 2.7334 | 2.7334 | 3.0789 | 3.0789 | 2020-01-22 05:00 | 1.3289 | 2.1778 | 3.575 | 3.575 | 3.575 | 3.575
2021-11-24 17:00 | 2.2263 | 2.7092 | 2.6507 | 2.8511 | 2.7008 | 2.9012 | 1.3346 | 2.2887 | 2.8241 | 2.8241 | 3.181 | 3.181 | 2020-01-22 06:00 | 1.508 | 2.4713 | 4.0567 | 4.0567 | 4.0567 | 4.0567
2021-11-24 18:00 | 2.3635 | 2.8761 | 2.8141 | 3.0268 | 2.8672 | 3.0799 | 1.4575 | 2.4994 | 3.0841 | 3.0841 | 3.4739 | 3.4739 | 2020-01-22 07:00 | 2.2263 | 3.6485 | 5.989 | 5.989 | 5.989 | 5.989
2021-11-24 19:00 | 2.2312 | 2.7152 | 2.6566 | 2.8574 | 2.7068 | 2.9076 | 1.4575 | 2.4994 | 3.0841 | 3.0841 | 3.4739 | 3.4739 | 2020-01-22 08:00 | 2.5788 | 4.2261 | 6.9372 | 6.9372 | 6.9372 | 6.9372
2021-11-24 20:00 | 2.232 | 2.7161 | 2.6575 | 2.8584 | 2.7077 | 2.9086 | 1.5175 | 2.6023 | 3.2111 | 3.2111 | 3.617 | 3.617 | 2020-01-22 09:00 | 2.6769 | 4.3869 | 7.2012 | 7.2012 | 7.2012 | 7.2012
2021-11-24 21:00 | 2.1491 | 2.6153 | 2.5588 | 2.7523 | 2.6072 | 2.8006 | 1.3804 | 2.3671 | 2.9208 | 2.9208 | 3.29 | 3.29 | 2020-01-22 10:00 | 2.8093 | 4.6039 | 7.5574 | 7.5574 | 7.5574 | 7.5574
2021-11-24 22:00 | 1.8634 | 2.2675 | 2.2186 | 2.3863 | 2.2605 | 2.4282 | 1.2432 | 2.1318 | 2.6306 | 2.6306 | 2.9631 | 2.9631 | 2020-01-22 11:00 | 2.795 | 4.5805 | 7.5189 | 7.5189 | 7.5189 | 7.5189
2021-11-24 23:00 | 1.6833 | 2.0484 | 2.0042 | 2.1557 | 2.0421 | 2.1936 | 0.97754 | 1.6763 | 2.0685 | 2.0685 | 2.3299 | 2.3299 | 2020-01-22 12:00 | 2.9007 | 4.7538 | 7.8034 | 7.8034 | 7.8034 | 7.8034
2021-11-25 | 1.5976 | 1.9441 | 1.9021 | 2.0459 | 1.9381 | 2.0818 | 0.96891 | 1.6615 | 2.0502 | 2.0502 | 2.3094 | 2.3094 | 2020-01-22 13:00 | 2.7531 | 4.5118 | 7.4062 | 7.4062 | 7.4062 | 7.4062
2021-11-25 01:00 | 1.4775 | 1.798 | 1.7592 | 1.8922 | 1.7925 | 1.9254 | 0.85165 | 1.4604 | 1.8021 | 1.8021 | 2.0299 | 2.0299 | 2020-01-22 14:00 | 2.8769 | 4.7148 | 7.7393 | 7.7393 | 7.7393 | 7.7393
2021-11-25 02:00 | 1.4004 | 1.7041 | 1.6673 | 1.7934 | 1.6988 | 1.8249 | 0.76305 | 1.3085 | 1.6146 | 1.6146 | 1.8187 | 1.8187 | 2020-01-22 15:00 | 2.895 | 4.7444 | 7.788 | 7.788 | 7.788 | 7.788
2021-11-25 03:00 | 1.3804 | 1.6797 | 1.6435 | 1.7677 | 1.6746 | 1.7988 | 0.80306 | 1.3771 | 1.6993 | 1.6993 | 1.9141 | 1.9141 | 2020-01-22 16:00 | 2.9017 | 4.7553 | 7.806 | 7.806 | 7.806 | 7.806
2021-11-25 04:00 | 1.3461 | 1.638 | 1.6027 | 1.7238 | 1.633 | 1.7541 | 0.74305 | 1.2742 | 1.5723 | 1.5723 | 1.771 | 1.771 | 2020-01-22 17:00 | 2.7988 | 4.5867 | 7.5292 | 7.5292 | 7.5292 | 7.5292
2021-11-25 05:00 | 1.4907 | 1.8141 | 1.775 | 1.9091 | 1.8085 | 1.9427 | 0.80878 | 1.3869 | 1.7114 | 1.7114 | 1.9277 | 1.9277 | 2020-01-22 18:00 | 2.211 | 3.6235 | 5.948 | 5.948 | 5.948 | 5.948
2021-11-25 06:00 | 1.7976 | 2.1875 | 2.1403 | 2.3021 | 2.1808 | 2.3425 | 0.87737 | 1.5045 | 1.8565 | 1.8565 | 2.0912 | 2.0912 | 2020-01-22 19:00 | 2.0529 | 3.3643 | 5.5226 | 5.5226 | 5.5226 | 5.5226
2021-11-25 07:00 | 2.0605 | 2.5075 | 2.4534 | 2.6388 | 2.4997 | 2.6852 | 1.162 | 1.9927 | 2.4588 | 2.4588 | 2.7696 | 2.7696 | 2020-01-22 20:00 | 1.95 | 3.1957 | 5.2458 | 5.2458 | 5.2458 | 5.2458
2021-11-25 08:00 | 2.192 | 2.6674 | 2.6099 | 2.8072 | 2.6592 | 2.8565 | 1.1632 | 1.9946 | 2.4612 | 2.4612 | 2.7723 | 2.7723 | 2020-01-22 21:00 | 1.93 | 3.1629 | 5.192 | 5.192 | 5.192 | 5.192
2021-11-25 09:00 | 2.232 | 2.7161 | 2.6575 | 2.8584 | 2.7077 | 2.9086 | 1.1689 | 2.0044 | 2.4733 | 2.4733 | 2.786 | 2.786 | 2020-01-22 22:00 | 1.7042 | 2.7929 | 4.5847 | 4.5847 | 4.5847 | 4.5847
2021-11-25 10:00 | 2.3663 | 2.8796 | 2.8175 | 3.0304 | 2.8707 | 3.0837 | 1.2146 | 2.0828 | 2.5701 | 2.5701 | 2.8949 | 2.8949 | 2020-01-22 23:00 | 1.5347 | 2.5151 | 4.1285 | 4.1285 | 4.1285 | 4.1285
2021-11-25 11:00 | 2.4263 | 2.9526 | 2.8889 | 3.1073 | 2.9435 | 3.1619 | 1.2746 | 2.1858 | 2.6971 | 2.6971 | 3.038 | 3.038 | 2020-01-23 | 1.3442 | 2.2028 | 3.616 | 3.616 | 3.616 | 3.616
2021-11-25 12:00 | 2.3377 | 2.8448 | 2.7834 | 2.9938 | 2.836 | 3.0464 | 1.226 | 2.1024 | 2.5943 | 2.5943 | 2.9222 | 2.9222 | 2020-01-23 01:00 | 1.3299 | 2.1794 | 3.5775 | 3.5775 | 3.5775 | 3.5775
2021-11-25 13:00 | 2.252 | 2.7405 | 2.6813 | 2.884 | 2.732 | 2.9347 | 1.2832 | 2.2005 | 2.7152 | 2.7152 | 3.0584 | 3.0584 | 2020-01-23 02:00 | 1.2356 | 2.0248 | 3.3238 | 3.3238 | 3.3238 | 3.3238
2021-11-25 14:00 | 2.252 | 2.7405 | 2.6813 | 2.884 | 2.732 | 2.9347 | 1.306 | 2.2397 | 2.7636 | 2.7636 | 3.1129 | 3.1129 | 2020-01-23 03:00 | 1.2279 | 2.0124 | 3.3033 | 3.3033 | 3.3033 | 3.3033
2021-11-25 15:00 | 2.2025 | 2.6802 | 2.6224 | 2.8206 | 2.6719 | 2.8702 | 1.2667 | 2.1722 | 2.6803 | 2.6803 | 3.0191 | 3.0191 | 2020-01-23 04:00 | 1.3356 | 2.1888 | 3.5929 | 3.5929 | 3.5929 | 3.5929
2021-11-25 16:00 | 2.2291 | 2.7126 | 2.6541 | 2.8547 | 2.7043 | 2.9049 | 1.3975 | 2.3965 | 2.9571 | 2.9571 | 3.3309 | 3.3309 | 2020-01-23 05:00 | 1.4108 | 2.3121 | 3.7953 | 3.7953 | 3.7953 | 3.7953
2021-11-25 17:00 | 2.3714 | 2.8857 | 2.8235 | 3.0369 | 2.8768 | 3.0902 | 1.4918 | 2.5582 | 3.1567 | 3.1567 | 3.5557 | 3.5557 | 2020-01-23 06:00 | 1.8548 | 3.0396 | 4.9896 | 4.9896 | 4.9896 | 4.9896
2021-11-25 18:00 | 2.5178 | 3.0639 | 2.9978 | 3.2244 | 3.0545 | 3.2811 | 1.5518 | 2.6611 | 3.2837 | 3.2837 | 3.6987 | 3.6987 | 2020-01-23 07:00 | 2.3825 | 3.9045 | 6.4093 | 6.4093 | 6.4093 | 6.4093
2021-11-25 19:00 | 2.3215 | 2.8251 | 2.7641 | 2.9731 | 2.8164 | 3.0253 | 1.569 | 2.6905 | 3.32 | 3.32 | 3.7396 | 3.7396 | 2020-01-23 08:00 | 2.6712 | 4.3775 | 7.1858 | 7.1858 | 7.1858 | 7.1858
2021-11-25 20:00 | 2.2634 | 2.7544 | 2.695 | 2.8987 | 2.7459 | 2.9496 | 1.5661 | 2.6856 | 3.3139 | 3.3139 | 3.7328 | 3.7328 | 2020-01-23 09:00 | 2.8274 | 4.6336 | 7.6061 | 7.6061 | 7.6061 | 7.6061
2021-11-25 21:00 | 2.212 | 2.6918 | 2.6337 | 2.8328 | 2.6835 | 2.8826 | 1.4432 | 2.4749 | 3.0539 | 3.0539 | 3.4399 | 3.4399 | 2020-01-23 10:00 | 2.8722 | 4.707 | 7.7265 | 7.7265 | 7.7265 | 7.7265
2021-11-25 22:00 | 1.8863 | 2.2954 | 2.2459 | 2.4156 | 2.2883 | 2.4581 | 1.2746 | 2.1858 | 2.6971 | 2.6971 | 3.038 | 3.038 | 2020-01-23 11:00 | 2.9893 | 4.899 | 8.0417 | 8.0417 | 8.0417 | 8.0417
2021-11-25 23:00 | 1.6919 | 2.0588 | 2.0144 | 2.1667 | 2.0525 | 2.2047 | 1.0832 | 1.8575 | 2.2921 | 2.2921 | 2.5818 | 2.5818 | 2020-01-23 12:00 | 3.0255 | 4.9583 | 8.1391 | 8.1391 | 8.1391 | 8.1391
2021-11-26 | 1.629 | 1.9823 | 1.9396 | 2.0862 | 1.9762 | 2.1228 | 0.94596 | 1.6222 | 2.0017 | 2.0017 | 2.2546 | 2.2546 | 2020-01-23 13:00 | 2.9227 | 4.7897 | 7.8623 | 7.8623 | 7.8623 | 7.8623
2021-11-26 01:00 | 1.4118 | 1.718 | 1.6809 | 1.808 | 1.7127 | 1.8398 | 1.1946 | 2.0485 | 2.5278 | 2.5278 | 2.8473 | 2.8473 | 2020-01-23 14:00 | 2.7693 | 4.5383 | 7.4498 | 7.4498 | 7.4498 | 7.4498
2021-11-26 02:00 | 1.3832 | 1.6832 | 1.6469 | 1.7714 | 1.678 | 1.8025 | 0.7661 | 1.3137 | 1.6211 | 1.6211 | 1.826 | 1.826 | 2020-01-23 15:00 | 2.7998 | 4.5883 | 7.5318 | 7.5318 | 7.5318 | 7.5318
2021-11-26 03:00 | 1.3489 | 1.6415 | 1.6061 | 1.7275 | 1.6364 | 1.7578 | 0.72548 | 1.2441 | 1.5351 | 1.5351 | 1.7292 | 1.7292 | 2020-01-23 16:00 | 2.8236 | 4.6273 | 7.5958 | 7.5958 | 7.5958 | 7.5958
2021-11-26 04:00 | 1.3775 | 1.6763 | 1.6401 | 1.7641 | 1.6711 | 1.7951 | 0.69446 | 1.1909 | 1.4695 | 1.4695 | 1.6552 | 1.6552 | 2020-01-23 17:00 | 2.7188 | 4.4556 | 7.3139 | 7.3139 | 7.3139 | 7.3139
2021-11-26 05:00 | 1.5544 | 1.8916 | 1.8508 | 1.9907 | 1.8857 | 2.0256 | 0.74305 | 1.2742 | 1.5723 | 1.5723 | 1.771 | 1.771 | 2020-01-23 18:00 | 2.3044 | 3.7765 | 6.1992 | 6.1992 | 6.1992 | 6.1992
2021-11-26 06:00 | 1.8605 | 2.264 | 2.2152 | 2.3826 | 2.257 | 2.4245 | 0.96588 | 1.6563 | 2.0438 | 2.0438 | 2.3021 | 2.3021 | 2020-01-23 19:00 | 1.9996 | 3.2769 | 5.3791 | 5.3791 | 5.3791 | 5.3791
2021-11-26 07:00 | 2.4149 | 2.9387 | 2.8753 | 3.0926 | 2.9296 | 3.147 | 1.2974 | 2.2249 | 2.7454 | 2.7454 | 3.0924 | 3.0924 | 2020-01-23 20:00 | 1.8386 | 3.0131 | 4.946 | 4.946 | 4.946 | 4.946
2021-11-26 08:00 | 2.4035 | 2.9248 | 2.8617 | 3.078 | 2.9158 | 3.1321 | 1.3603 | 2.3328 | 2.8785 | 2.8785 | 3.2423 | 3.2423 | 2020-01-23 21:00 | 1.7643 | 2.8913 | 4.7461 | 4.7461 | 4.7461 | 4.7461
2021-11-26 09:00 | 2.5035 | 3.0465 | 2.9808 | 3.2061 | 3.0371 | 3.2624 | 1.3889 | 2.3818 | 2.939 | 2.939 | 3.3105 | 3.3105 | 2020-01-23 22:00 | 1.6157 | 2.6478 | 4.3463 | 4.3463 | 4.3463 | 4.3463
2021-11-26 10:00 | 2.4606 | 2.9943 | 2.9297 | 3.1512 | 2.9851 | 3.2066 | 1.529 | 2.6219 | 3.2353 | 3.2353 | 3.6442 | 3.6442 | 2020-01-23 23:00 | 1.5337 | 2.5135 | 4.1259 | 4.1259 | 4.1259 | 4.1259
2021-11-26 11:00 | 2.5407 | 3.0917 | 3.025 | 3.2537 | 3.0822 | 3.3108 | 1.489 | 2.5533 | 3.1506 | 3.1506 | 3.5489 | 3.5489 | 2020-01-24 | 1.468 | 2.4058 | 3.9491 | 3.9491 | 3.9491 | 3.9491
2021-11-26 12:00 | 2.5092 | 3.0535 | 2.9876 | 3.2134 | 3.0441 | 3.2699 | 1.5204 | 2.6072 | 3.2172 | 3.2172 | 3.6238 | 3.6238 | 2020-01-24 01:00 | 1.4489 | 2.3745 | 3.8979 | 3.8979 | 3.8979 | 3.8979
2021-11-26 13:00 | 2.3892 | 2.9074 | 2.8447 | 3.0597 | 2.8984 | 3.1135 | 1.509 | 2.5876 | 3.193 | 3.193 | 3.5965 | 3.5965 | 2020-01-24 02:00 | 1.3356 | 2.1888 | 3.5929 | 3.5929 | 3.5929 | 3.5929
2021-11-26 14:00 | 2.3578 | 2.8691 | 2.8072 | 3.0194 | 2.8603 | 3.0725 | 1.5175 | 2.6023 | 3.2111 | 3.2111 | 3.617 | 3.617 | 2020-01-24 03:00 | 1.4013 | 2.2965 | 3.7697 | 3.7697 | 3.7697 | 3.7697
2021-11-26 15:00 | 2.2349 | 2.7196 | 2.6609 | 2.8621 | 2.7112 | 2.9124 | 1.4861 | 2.5484 | 3.1446 | 3.1446 | 3.542 | 3.542 | 2020-01-24 04:00 | 1.4604 | 2.3933 | 3.9286 | 3.9286 | 3.9286 | 3.9286
2021-11-26 16:00 | 2.1091 | 2.5666 | 2.5112 | 2.701 | 2.5587 | 2.7485 | 1.4775 | 2.5337 | 3.1265 | 3.1265 | 3.5216 | 3.5216 | 2020-01-24 05:00 | 1.5032 | 2.4635 | 4.0439 | 4.0439 | 4.0439 | 4.0439
2021-11-26 17:00 | 2.3806 | 2.897 | 2.8345 | 3.0487 | 2.888 | 3.1023 | 1.6461 | 2.8229 | 3.4832 | 3.4832 | 3.9235 | 3.9235 | 2020-01-24 06:00 | 1.5604 | 2.5572 | 4.1977 | 4.1977 | 4.1977 | 4.1977
2021-11-26 18:00 | 2.4406 | 2.97 | 2.9059 | 3.1256 | 2.9608 | 3.1805 | 1.8008 | 3.0881 | 3.8105 | 3.8105 | 4.2921 | 4.2921 | 2020-01-24 07:00 | 2.3368 | 3.8296 | 6.2863 | 6.2863 | 6.2863 | 6.2863
2021-11-26 19:00 | 2.3377 | 2.8448 | 2.7834 | 2.9938 | 2.836 | 3.0464 | 1.8662 | 3.2002 | 3.9489 | 3.9489 | 4.448 | 4.448 | 2020-01-24 08:00 | 2.5121 | 4.1168 | 6.7578 | 6.7578 | 6.7578 | 6.7578
2021-11-26 20:00 | 2.3235 | 2.8274 | 2.7664 | 2.9755 | 2.8187 | 3.0278 | 1.8805 | 3.2247 | 3.9791 | 3.9791 | 4.4821 | 4.4821 | 2020-01-24 09:00 | 2.6493 | 4.3416 | 7.1269 | 7.1269 | 7.1269 | 7.1269
2021-11-26 21:00 | 2.1548 | 2.6222 | 2.5657 | 2.7596 | 2.6141 | 2.8081 | 1.7376 | 2.9797 | 3.6768 | 3.6768 | 4.1415 | 4.1415 | 2020-01-24 10:00 | 2.7788 | 4.554 | 7.4754 | 7.4754 | 7.4754 | 7.4754
2021-11-26 22:00 | 2.0177 | 2.4553 | 2.4023 | 2.5839 | 2.4477 | 2.6293 | 1.4698 | 2.5205 | 3.1102 | 3.1102 | 3.5032 | 3.5032 | 2020-01-24 11:00 | 2.7788 | 4.554 | 7.4754 | 7.4754 | 7.4754 | 7.4754
2021-11-26 23:00 | 1.8519 | 2.2536 | 2.205 | 2.3716 | 2.2466 | 2.4133 | 1.3302 | 2.281 | 2.8146 | 2.8146 | 3.1704 | 3.1704 | 2020-01-24 12:00 | 2.7645 | 4.5305 | 7.4369 | 7.4369 | 7.4369 | 7.4369
2021-11-27 | 1.7004 | 2.0693 | 2.0246 | 2.1777 | 2.0629 | 2.2159 | 1.0403 | 1.7839 | 2.2012 | 2.2012 | 2.4794 | 2.4794 | 2020-01-24 13:00 | 2.815 | 4.6133 | 7.5728 | 7.5728 | 7.5728 | 7.5728
2021-11-27 01:00 | 1.5804 | 1.9232 | 1.8817 | 2.0239 | 1.9173 | 2.0595 | 0.93552 | 1.6043 | 1.9796 | 1.9796 | 2.2298 | 2.2298 | 2020-01-24 14:00 | 2.7941 | 4.5789 | 7.5164 | 7.5164 | 7.5164 | 7.5164
2021-11-27 02:00 | 1.4947 | 1.8189 | 1.7796 | 1.9141 | 1.8133 | 1.9478 | 0.81076 | 1.3903 | 1.7156 | 1.7156 | 1.9324 | 1.9324 | 2020-01-24 15:00 | 2.8436 | 4.6601 | 7.6496 | 7.6496 | 7.6496 | 7.6496
2021-11-27 03:00 | 1.4575 | 1.7736 | 1.7354 | 1.8666 | 1.7682 | 1.8994 | 0.82096 | 1.4078 | 1.7372 | 1.7372 | 1.9567 | 1.9567 | 2020-01-24 16:00 | 2.8102 | 4.6055 | 7.5599 | 7.5599 | 7.5599 | 7.5599
2021-11-27 04:00 | 1.4604 | 1.7771 | 1.7388 | 1.8702 | 1.7716 | 1.9031 | 0.82307 | 1.4114 | 1.7416 | 1.7416 | 1.9617 | 1.9617 | 2020-01-24 17:00 | 2.3025 | 3.7734 | 6.194 | 6.194 | 6.194 | 6.194
2021-11-27 05:00 | 1.4975 | 1.8223 | 1.783 | 1.9178 | 1.8167 | 1.9515 | 0.77448 | 1.3281 | 1.6388 | 1.6388 | 1.8459 | 1.8459 | 2020-01-24 18:00 | 2.0234 | 3.3159 | 5.4432 | 5.4432 | 5.4432 | 5.4432
2021-11-27 06:00 | 1.6947 | 2.0623 | 2.0178 | 2.1703 | 2.0559 | 2.2085 | 0.80644 | 1.3829 | 1.7064 | 1.7064 | 1.9221 | 1.9221 | 2020-01-24 19:00 | 1.8367 | 3.0099 | 4.9409 | 4.9409 | 4.9409 | 4.9409
2021-11-27 07:00 | 1.8776 | 2.2849 | 2.2356 | 2.4046 | 2.2778 | 2.4468 | 1.1203 | 1.9211 | 2.3705 | 2.3705 | 2.6702 | 2.6702 | 2020-01-24 20:00 | 1.75 | 2.8679 | 4.7077 | 4.7077 | 4.7077 | 4.7077
2021-11-27 08:00 | 1.9834 | 2.4136 | 2.3615 | 2.54 | 2.4061 | 2.5846 | 1.2432 | 2.1318 | 2.6306 | 2.6306 | 2.9631 | 2.9631 | 2020-01-24 21:00 | 1.7595 | 2.8835 | 4.7333 | 4.7333 | 4.7333 | 4.7333
2021-11-27 09:00 | 2.1891 | 2.664 | 2.6065 | 2.8035 | 2.6557 | 2.8528 | 1.3718 | 2.3524 | 2.9027 | 2.9027 | 3.2696 | 3.2696 | 2020-01-24 22:00 | 1.6223 | 2.6587 | 4.3643 | 4.3643 | 4.3643 | 4.3643
2021-11-27 10:00 | 2.132 | 2.5944 | 2.5384 | 2.7303 | 2.5864 | 2.7783 | 1.5804 | 2.7101 | 3.3442 | 3.3442 | 3.7668 | 3.7668 | 2020-01-24 23:00 | 1.5261 | 2.501 | 4.1054 | 4.1054 | 4.1054 | 4.1054
2021-11-27 11:00 | 2.1691 | 2.6396 | 2.5827 | 2.7779 | 2.6315 | 2.8267 | 1.6376 | 2.8082 | 3.4651 | 3.4651 | 3.9031 | 3.9031 | 2020-01-25 | 1.6309 | 2.6727 | 4.3873 | 4.3873 | 4.3873 | 4.3873
2021-11-27 12:00 | 2.0977 | 2.5527 | 2.4976 | 2.6864 | 2.5448 | 2.7336 | 1.6576 | 2.8425 | 3.5074 | 3.5074 | 3.9507 | 3.9507 | 2020-01-25 01:00 | 1.3813 | 2.2637 | 3.7159 | 3.7159 | 3.7159 | 3.7159
2021-11-27 13:00 | 2.072 | 2.5214 | 2.467 | 2.6535 | 2.5136 | 2.7001 | 1.669 | 2.8621 | 3.5316 | 3.5316 | 3.978 | 3.978 | 2020-01-25 02:00 | 1.4127 | 2.3152 | 3.8005 | 3.8005 | 3.8005 | 3.8005
2021-11-27 14:00 | 2.0034 | 2.4379 | 2.3853 | 2.5656 | 2.4304 | 2.6107 | 1.6604 | 2.8474 | 3.5135 | 3.5135 | 3.9576 | 3.9576 | 2020-01-25 03:00 | 1.3089 | 2.1451 | 3.5211 | 3.5211 | 3.5211 | 3.5211
2021-11-27 15:00 | 1.9348 | 2.3544 | 2.3036 | 2.4778 | 2.3472 | 2.5213 | 1.6261 | 2.7886 | 3.4409 | 3.4409 | 3.8758 | 3.8758 | 2020-01-25 04:00 | 1.4042 | 2.3012 | 3.7774 | 3.7774 | 3.7774 | 3.7774
2021-11-27 16:00 | 1.8862 | 2.2953 | 2.2458 | 2.4156 | 2.2882 | 2.458 | 1.666 | 2.857 | 3.5254 | 3.5254 | 3.9709 | 3.9709 | 2020-01-25 05:00 | 1.4461 | 2.3699 | 3.8902 | 3.8902 | 3.8902 | 3.8902
2021-11-27 17:00 | 1.9834 | 2.4136 | 2.3615 | 2.54 | 2.4061 | 2.5846 | 1.6919 | 2.9013 | 3.58 | 3.58 | 4.0325 | 4.0325 | 2020-01-25 06:00 | 1.5699 | 2.5728 | 4.2233 | 4.2233 | 4.2233 | 4.2233
2021-11-27 18:00 | 2.2263 | 2.7092 | 2.6507 | 2.8511 | 2.7008 | 2.9012 | 1.8691 | 3.2051 | 3.9549 | 3.9549 | 4.4548 | 4.4548 | 2020-01-25 07:00 | 1.9815 | 3.2472 | 5.3304 | 5.3304 | 5.3304 | 5.3304
2021-11-27 19:00 | 2.2177 | 2.6987 | 2.6405 | 2.8401 | 2.6904 | 2.89 | 1.789 | 3.0679 | 3.7856 | 3.7856 | 4.2641 | 4.2641 | 2020-01-25 08:00 | 2.1291 | 3.4892 | 5.7276 | 5.7276 | 5.7276 | 5.7276
2021-11-27 20:00 | 2.1863 | 2.6605 | 2.6031 | 2.7998 | 2.6523 | 2.849 | 1.729 | 2.965 | 3.6586 | 3.6586 | 4.121 | 4.121 | 2020-01-25 09:00 | 2.1691 | 3.5548 | 5.8353 | 5.8353 | 5.8353 | 5.8353
2021-11-27 21:00 | 2.092 | 2.5457 | 2.4908 | 2.6791 | 2.5379 | 2.7261 | 1.7233 | 2.9552 | 3.6465 | 3.6465 | 4.1074 | 4.1074 | 2020-01-25 10:00 | 2.2215 | 3.6407 | 5.9762 | 5.9762 | 5.9762 | 5.9762
2021-11-27 22:00 | 1.9349 | 2.3546 | 2.3038 | 2.4779 | 2.3473 | 2.5214 | 1.4689 | 2.519 | 3.1083 | 3.1083 | 3.5012 | 3.5012 | 2020-01-25 11:00 | 2.2206 | 3.6391 | 5.9736 | 5.9736 | 5.9736 | 5.9736
2021-11-27 23:00 | 1.789 | 2.1771 | 2.1301 | 2.2911 | 2.1704 | 2.3314 | 1.2863 | 2.2058 | 2.7218 | 2.7218 | 3.0658 | 3.0658 | 2020-01-25 12:00 | 2.273 | 3.725 | 6.1146 | 6.1146 | 6.1146 | 6.1146
2021-11-28 | 1.7324 | 2.1082 | 2.0627 | 2.2187 | 2.1017 | 2.2576 | 1.0917 | 1.8721 | 2.3101 | 2.3101 | 2.602 | 2.602 | 2020-01-25 13:00 | 2.2301 | 3.6547 | 5.9993 | 5.9993 | 5.9993 | 5.9993
2021-11-28 01:00 | 1.6204 | 1.9719 | 1.9293 | 2.0752 | 1.9658 | 2.1116 | 0.88308 | 1.5143 | 1.8686 | 1.8686 | 2.1048 | 2.1048 | 2020-01-25 14:00 | 2.2492 | 3.6859 | 6.0505 | 6.0505 | 6.0505 | 6.0505
2021-11-28 02:00 | 1.5804 | 1.9232 | 1.8817 | 2.0239 | 1.9173 | 2.0595 | 0.88025 | 1.5095 | 1.8626 | 1.8626 | 2.098 | 2.098 | 2020-01-25 15:00 | 2.2044 | 3.6126 | 5.9301 | 5.9301 | 5.9301 | 5.9301
2021-11-28 03:00 | 1.5605 | 1.899 | 1.858 | 1.9985 | 1.8931 | 2.0336 | 0.83736 | 1.4359 | 1.7719 | 1.7719 | 1.9958 | 1.9958 | 2020-01-25 16:00 | 2.2149 | 3.6297 | 5.9583 | 5.9583 | 5.9583 | 5.9583
2021-11-28 04:00 | 1.4751 | 1.795 | 1.7563 | 1.8891 | 1.7895 | 1.9222 | 0.80295 | 1.3769 | 1.699 | 1.699 | 1.9138 | 1.9138 | 2020-01-25 17:00 | 2.1034 | 3.4471 | 5.6584 | 5.6584 | 5.6584 | 5.6584
2021-11-28 05:00 | 1.5032 | 1.8293 | 1.7898 | 1.9251 | 1.8237 | 1.9589 | 0.80306 | 1.3771 | 1.6993 | 1.6993 | 1.9141 | 1.9141 | 2020-01-25 18:00 | 1.9977 | 3.2738 | 5.374 | 5.374 | 5.374 | 5.374
2021-11-28 06:00 | 1.5747 | 1.9162 | 1.8749 | 2.0166 | 1.9103 | 2.0521 | 0.86875 | 1.4898 | 1.8383 | 1.8383 | 2.0706 | 2.0706 | 2020-01-25 19:00 | 1.7843 | 2.9241 | 4.7999 | 4.7999 | 4.7999 | 4.7999
2021-11-28 07:00 | 1.7976 | 2.1875 | 2.1403 | 2.3021 | 2.1808 | 2.3425 | 1.0517 | 1.8035 | 2.2254 | 2.2254 | 2.5067 | 2.5067 | 2020-01-25 20:00 | 1.8843 | 3.088 | 5.069 | 5.069 | 5.069 | 5.069
2021-11-28 08:00 | 1.8633 | 2.2675 | 2.2186 | 2.3863 | 2.2605 | 2.4282 | 1.285 | 2.2035 | 2.719 | 2.719 | 3.0627 | 3.0627 | 2020-01-25 21:00 | 1.7471 | 2.8632 | 4.7 | 4.7 | 4.7 | 4.7
2021-11-28 09:00 | 1.8485 | 2.2495 | 2.2009 | 2.3673 | 2.2425 | 2.4089 | 1.4089 | 2.4161 | 2.9813 | 2.9813 | 3.3581 | 3.3581 | 2020-01-25 22:00 | 1.7947 | 2.9413 | 4.8281 | 4.8281 | 4.8281 | 4.8281
2021-11-28 10:00 | 1.9033 | 2.3162 | 2.2662 | 2.4375 | 2.309 | 2.4803 | 1.5232 | 2.6121 | 3.2232 | 3.2232 | 3.6306 | 3.6306 | 2020-01-25 23:00 | 1.7262 | 2.8289 | 4.6436 | 4.6436 | 4.6436 | 4.6436
2021-11-28 11:00 | 1.8976 | 2.3092 | 2.2594 | 2.4302 | 2.3021 | 2.4729 | 1.5661 | 2.6856 | 3.3139 | 3.3139 | 3.7328 | 3.7328 | 2020-01-26 | 1.6357 | 2.6805 | 4.4001 | 4.4001 | 4.4001 | 4.4001
2021-11-28 12:00 | 1.6347 | 1.9893 | 1.9464 | 2.0935 | 1.9831 | 2.1303 | 1.6147 | 2.769 | 3.4167 | 3.4167 | 3.8486 | 3.8486 | 2020-01-26 01:00 | 1.5775 | 2.5853 | 4.2438 | 4.2438 | 4.2438 | 4.2438
2021-11-28 13:00 | 1.6919 | 2.0588 | 2.0144 | 2.1667 | 2.0525 | 2.2047 | 1.6747 | 2.8719 | 3.5437 | 3.5437 | 3.9916 | 3.9916 | 2020-01-26 02:00 | 1.4994 | 2.4573 | 4.0337 | 4.0337 | 4.0337 | 4.0337
2021-11-28 14:00 | 1.6747 | 2.038 | 1.994 | 2.1447 | 2.0317 | 2.1824 | 1.5718 | 2.6954 | 3.326 | 3.326 | 3.7464 | 3.7464 | 2020-01-26 03:00 | 1.4566 | 2.387 | 3.9184 | 3.9184 | 3.9184 | 3.9184
2021-11-28 15:00 | 1.609 | 1.958 | 1.9157 | 2.0605 | 1.9519 | 2.0967 | 1.5375 | 2.6366 | 3.2534 | 3.2534 | 3.6647 | 3.6647 | 2020-01-26 04:00 | 1.468 | 2.4058 | 3.9491 | 3.9491 | 3.9491 | 3.9491
2021-11-28 16:00 | 1.7262 | 2.1006 | 2.0552 | 2.2106 | 2.0941 | 2.2494 | 1.629 | 2.7935 | 3.447 | 3.447 | 3.8826 | 3.8826 | 2020-01-26 05:00 | 1.4842 | 2.4323 | 3.9927 | 3.9927 | 3.9927 | 3.9927
2021-11-28 17:00 | 1.806 | 2.1977 | 2.1503 | 2.3128 | 2.1909 | 2.3535 | 1.7262 | 2.9601 | 3.6526 | 3.6526 | 4.1142 | 4.1142 | 2020-01-26 06:00 | 1.6042 | 2.629 | 4.3156 | 4.3156 | 4.3156 | 4.3156
2021-11-28 18:00 | 2.1348 | 2.5979 | 2.5418 | 2.734 | 2.5899 | 2.782 | 1.7204 | 2.9503 | 3.6405 | 3.6405 | 4.1006 | 4.1006 | 2020-01-26 07:00 | 1.8519 | 3.0349 | 4.9819 | 4.9819 | 4.9819 | 4.9819
2021-11-28 19:00 | 2.1434 | 2.6083 | 2.552 | 2.7449 | 2.6003 | 2.7932 | 1.7262 | 2.9601 | 3.6526 | 3.6526 | 4.1142 | 4.1142 | 2020-01-26 08:00 | 2.152 | 3.5267 | 5.7891 | 5.7891 | 5.7891 | 5.7891
2021-11-28 20:00 | 2.1949 | 2.6709 | 2.6133 | 2.8108 | 2.6627 | 2.8602 | 1.7674 | 3.0308 | 3.7398 | 3.7398 | 4.2125 | 4.2125 | 2020-01-26 09:00 | 2.2415 | 3.6734 | 6.03 | 6.03 | 6.03 | 6.03
2021-11-28 21:00 | 2.1061 | 2.5629 | 2.5077 | 2.6972 | 2.555 | 2.7446 | 1.769 | 3.0336 | 3.7433 | 3.7433 | 4.2164 | 4.2164 | 2020-01-26 10:00 | 2.3168 | 3.7968 | 6.2325 | 6.2325 | 6.2325 | 6.2325
2021-11-28 22:00 | 1.8605 | 2.264 | 2.2152 | 2.3826 | 2.257 | 2.4245 | 1.3446 | 2.3058 | 2.8452 | 2.8452 | 3.2048 | 3.2048 | 2020-01-26 11:00 | 2.3663 | 3.878 | 6.3657 | 6.3657 | 6.3657 | 6.3657
2021-11-28 23:00 | 1.7033 | 2.0727 | 2.028 | 2.1813 | 2.0663 | 2.2196 | 1.146 | 1.9652 | 2.425 | 2.425 | 2.7315 | 2.7315 | 2020-01-26 12:00 | 2.3168 | 3.7968 | 6.2325 | 6.2325 | 6.2325 | 6.2325
2021-11-29 | 1.5976 | 1.9441 | 1.9022 | 2.046 | 1.9381 | 2.0819 | 0.97755 | 1.6763 | 2.0685 | 2.0685 | 2.33 | 2.33 | 2020-01-26 13:00 | 2.2996 | 3.7687 | 6.1863 | 6.1863 | 6.1863 | 6.1863
2021-11-29 01:00 | 1.5062 | 1.8329 | 1.7933 | 1.9289 | 1.8272 | 1.9628 | 0.83831 | 1.4376 | 1.7739 | 1.7739 | 1.9981 | 1.9981 | 2020-01-26 14:00 | 2.2958 | 3.7624 | 6.1761 | 6.1761 | 6.1761 | 6.1761
2021-11-29 02:00 | 1.4347 | 1.7458 | 1.7082 | 1.8373 | 1.7404 | 1.8696 | 0.80309 | 1.3772 | 1.6993 | 1.6993 | 1.9141 | 1.9141 | 2020-01-26 15:00 | 2.2625 | 3.7078 | 6.0864 | 6.0864 | 6.0864 | 6.0864
2021-11-29 03:00 | 1.4518 | 1.7667 | 1.7286 | 1.8592 | 1.7612 | 1.8919 | 0.72304 | 1.2399 | 1.53 | 1.53 | 1.7233 | 1.7233 | 2020-01-26 16:00 | 2.3006 | 3.7702 | 6.1889 | 6.1889 | 6.1889 | 6.1889
2021-11-29 04:00 | 1.4775 | 1.798 | 1.7592 | 1.8922 | 1.7925 | 1.9254 | 0.76008 | 1.3034 | 1.6083 | 1.6083 | 1.8116 | 1.8116 | 2020-01-26 17:00 | 2.2053 | 3.6141 | 5.9326 | 5.9326 | 5.9326 | 5.9326
2021-11-29 05:00 | 1.6003 | 1.9474 | 1.9054 | 2.0494 | 1.9414 | 2.0854 | 0.80878 | 1.3869 | 1.7114 | 1.7114 | 1.9277 | 1.9277 | 2020-01-26 18:00 | 1.9891 | 3.2597 | 5.3509 | 5.3509 | 5.3509 | 5.3509
2021-11-29 06:00 | 2.1788 | 2.6514 | 2.5942 | 2.7903 | 2.6432 | 2.8393 | 0.99383 | 1.7043 | 2.103 | 2.103 | 2.3688 | 2.3688 | 2020-01-26 19:00 | 1.9119 | 3.1333 | 5.1433 | 5.1433 | 5.1433 | 5.1433
2021-11-29 07:00 | 2.392 | 2.9109 | 2.8481 | 3.0634 | 2.9019 | 3.1172 | 1.2289 | 2.1073 | 2.6003 | 2.6003 | 2.929 | 2.929 | 2020-01-26 20:00 | 1.8805 | 3.0818 | 5.0588 | 5.0588 | 5.0588 | 5.0588
2021-11-29 08:00 | 2.4178 | 2.9422 | 2.8787 | 3.0963 | 2.9331 | 3.1507 | 1.2803 | 2.1956 | 2.7092 | 2.7092 | 3.0516 | 3.0516 | 2020-01-26 21:00 | 1.8757 | 3.074 | 5.0459 | 5.0459 | 5.0459 | 5.0459
2021-11-29 09:00 | 2.3377 | 2.8448 | 2.7834 | 2.9938 | 2.836 | 3.0464 | 1.306 | 2.2397 | 2.7636 | 2.7636 | 3.1129 | 3.1129 | 2020-01-26 22:00 | 1.7881 | 2.9303 | 4.8102 | 4.8102 | 4.8102 | 4.8102
2021-11-29 10:00 | 2.0405 | 2.4831 | 2.4295 | 2.6132 | 2.4755 | 2.6591 | 1.2918 | 2.2152 | 2.7334 | 2.7334 | 3.0789 | 3.0789 | 2020-01-26 23:00 | 1.6023 | 2.6259 | 4.3104 | 4.3104 | 4.3104 | 4.3104
2021-11-29 11:00 | 1.9205 | 2.337 | 2.2866 | 2.4595 | 2.3298 | 2.5027 | 1.3661 | 2.3426 | 2.8906 | 2.8906 | 3.256 | 3.256 | 2020-01-27 | 1.5299 | 2.5072 | 4.1157 | 4.1157 | 4.1157 | 4.1157
2021-11-29 12:00 | 1.8519 | 2.2536 | 2.205 | 2.3716 | 2.2466 | 2.4133 | 1.2889 | 2.2103 | 2.7273 | 2.7273 | 3.072 | 3.072 | 2020-01-27 01:00 | 1.3727 | 2.2497 | 3.6928 | 3.6928 | 3.6928 | 3.6928
2021-11-29 13:00 | 1.8662 | 2.271 | 2.222 | 2.3899 | 2.264 | 2.4319 | 1.3175 | 2.2593 | 2.7878 | 2.7878 | 3.1402 | 3.1402 | 2020-01-27 02:00 | 1.3175 | 2.1591 | 3.5442 | 3.5442 | 3.5442 | 3.5442
2021-11-29 14:00 | 1.7062 | 2.0762 | 2.0314 | 2.185 | 2.0698 | 2.2234 | 1.266 | 2.1711 | 2.679 | 2.679 | 3.0176 | 3.0176 | 2020-01-27 03:00 | 1.387 | 2.2731 | 3.7313 | 3.7313 | 3.7313 | 3.7313
2021-11-29 15:00 | 1.8633 | 2.2675 | 2.2186 | 2.3863 | 2.2605 | 2.4282 | 1.3575 | 2.3279 | 2.8725 | 2.8725 | 3.2355 | 3.2355 | 2020-01-27 04:00 | 1.3813 | 2.2637 | 3.7159 | 3.7159 | 3.7159 | 3.7159
2021-11-29 16:00 | 1.8605 | 2.264 | 2.2152 | 2.3826 | 2.257 | 2.4245 | 1.3861 | 2.3769 | 2.9329 | 2.9329 | 3.3036 | 3.3036 | 2020-01-27 05:00 | 1.4966 | 2.4526 | 4.026 | 4.026 | 4.026 | 4.026
2021-11-29 17:00 | 2.2234 | 2.7057 | 2.6473 | 2.8474 | 2.6973 | 2.8975 | 1.5775 | 2.7052 | 3.3381 | 3.3381 | 3.76 | 3.76 | 2020-01-27 06:00 | 1.6433 | 2.693 | 4.4206 | 4.4206 | 4.4206 | 4.4206
2021-11-29 18:00 | 2.332 | 2.8378 | 2.7766 | 2.9865 | 2.8291 | 3.039 | 1.6033 | 2.7494 | 3.3925 | 3.3925 | 3.8213 | 3.8213 | 2020-01-27 07:00 | 1.7833 | 2.9225 | 4.7974 | 4.7974 | 4.7974 | 4.7974
2021-11-29 19:00 | 2.1691 | 2.6396 | 2.5827 | 2.7779 | 2.6315 | 2.8267 | 1.5976 | 2.7395 | 3.3804 | 3.3804 | 3.8077 | 3.8077 | 2020-01-27 08:00 | 2.0472 | 3.355 | 5.5072 | 5.5072 | 5.5072 | 5.5072
2021-11-29 20:00 | 2.2434 | 2.73 | 2.6711 | 2.873 | 2.7216 | 2.9235 | 1.6347 | 2.8033 | 3.4591 | 3.4591 | 3.8963 | 3.8963 | 2020-01-27 09:00 | 2.0986 | 3.4393 | 5.6456 | 5.6456 | 5.6456 | 5.6456
2021-11-29 21:00 | 2.1263 | 2.5874 | 2.5316 | 2.723 | 2.5795 | 2.7708 | 1.6347 | 2.8033 | 3.4591 | 3.4591 | 3.8963 | 3.8963 | 2020-01-27 10:00 | 2.2901 | 3.7531 | 6.1607 | 6.1607 | 6.1607 | 6.1607
2021-11-29 22:00 | 1.9322 | 2.3513 | 2.3006 | 2.4745 | 2.3441 | 2.518 | 1.2521 | 2.1472 | 2.6495 | 2.6495 | 2.9844 | 2.9844 | 2020-01-27 11:00 | 2.6283 | 4.3073 | 7.0705 | 7.0705 | 7.0705 | 7.0705
2021-11-29 23:00 | 1.6549 | 2.0139 | 1.9704 | 2.1194 | 2.0077 | 2.1566 | 1.0836 | 1.8582 | 2.2929 | 2.2929 | 2.5827 | 2.5827 | 2020-01-27 12:00 | 2.5216 | 4.1324 | 6.7835 | 6.7835 | 6.7835 | 6.7835
2021-11-30 | 1.5547 | 1.8919 | 1.8511 | 1.991 | 1.8861 | 2.026 | 0.95167 | 1.632 | 2.0137 | 2.0137 | 2.2683 | 2.2683 | 2020-01-27 13:00 | 2.5473 | 4.1746 | 6.8526 | 6.8526 | 6.8526 | 6.8526
2021-11-30 01:00 | 1.4146 | 1.7215 | 1.6843 | 1.8117 | 1.7162 | 1.8435 | 0.81185 | 1.3922 | 1.7179 | 1.7179 | 1.935 | 1.935 | 2020-01-27 14:00 | 2.5864 | 4.2386 | 6.9577 | 6.9577 | 6.9577 | 6.9577
2021-11-30 02:00 | 1.4089 | 1.7145 | 1.6775 | 1.8043 | 1.7092 | 1.836 | 0.76877 | 1.3183 | 1.6267 | 1.6267 | 1.8323 | 1.8323 | 2020-01-27 15:00 | 2.553 | 4.184 | 6.868 | 6.868 | 6.868 | 6.868
2021-11-30 03:00 | 1.3546 | 1.6484 | 1.6129 | 1.7348 | 1.6434 | 1.7653 | 0.70875 | 1.2154 | 1.4997 | 1.4997 | 1.6893 | 1.6893 | 2020-01-27 16:00 | 2.715 | 4.4494 | 7.3037 | 7.3037 | 7.3037 | 7.3037
2021-11-30 04:00 | 1.3718 | 1.6693 | 1.6333 | 1.7568 | 1.6642 | 1.7876 | 0.69442 | 1.1908 | 1.4694 | 1.4694 | 1.6551 | 1.6551 | 2020-01-27 17:00 | 2.4835 | 4.07 | 6.6809 | 6.6809 | 6.6809 | 6.6809
2021-11-30 05:00 | 1.529 | 1.8606 | 1.8205 | 1.9581 | 1.8549 | 1.9925 | 0.70589 | 1.2105 | 1.4937 | 1.4937 | 1.6825 | 1.6825 | 2020-01-27 18:00 | 2.2663 | 3.714 | 6.0966 | 6.0966 | 6.0966 | 6.0966
2021-11-30 06:00 | 1.9091 | 2.3231 | 2.273 | 2.4448 | 2.316 | 2.4878 | 0.78591 | 1.3477 | 1.663 | 1.663 | 1.8732 | 1.8732 | 2020-01-27 19:00 | 2.0177 | 3.3066 | 5.4278 | 5.4278 | 5.4278 | 5.4278
2021-11-30 07:00 | 2.1291 | 2.5909 | 2.535 | 2.7266 | 2.5829 | 2.7746 | 1.1657 | 1.9989 | 2.4666 | 2.4666 | 2.7783 | 2.7783 | 2020-01-27 20:00 | 1.8614 | 3.0505 | 5.0075 | 5.0075 | 5.0075 | 5.0075
2021-11-30 08:00 | 2.2377 | 2.7231 | 2.6643 | 2.8657 | 2.7147 | 2.9161 | 1.2603 | 2.1613 | 2.6669 | 2.6669 | 3.0039 | 3.0039 | 2020-01-27 21:00 | 1.911 | 3.1317 | 5.1408 | 5.1408 | 5.1408 | 5.1408
2021-11-30 09:00 | 1.9634 | 2.3892 | 2.3377 | 2.5144 | 2.3818 | 2.5585 | 1.2689 | 2.176 | 2.685 | 2.685 | 3.0244 | 3.0244 | 2020-01-27 22:00 | 1.9624 | 3.216 | 5.2791 | 5.2791 | 5.2791 | 5.2791
2021-11-30 10:00 | 1.9119 | 2.3266 | 2.2764 | 2.4485 | 2.3194 | 2.4915 | 1.2489 | 2.1416 | 2.6427 | 2.6427 | 2.9767 | 2.9767 | 2020-01-27 23:00 | 1.6928 | 2.7742 | 4.5539 | 4.5539 | 4.5539 | 4.5539
2021-11-30 11:00 | 1.8548 | 2.2571 | 2.2084 | 2.3753 | 2.2501 | 2.417 | 1.2832 | 2.2005 | 2.7152 | 2.7152 | 3.0584 | 3.0584 | 2020-01-28 | 1.5985 | 2.6197 | 4.3002 | 4.3002 | 4.3002 | 4.3002
2021-11-30 12:00 | 2.0034 | 2.4379 | 2.3853 | 2.5656 | 2.4304 | 2.6107 | 1.2775 | 2.1907 | 2.7031 | 2.7031 | 3.0448 | 3.0448 | 2020-01-28 01:00 | 1.5547 | 2.5478 | 4.1823 | 4.1823 | 4.1823 | 4.1823
2021-11-30 13:00 | 2.1148 | 2.5735 | 2.518 | 2.7083 | 2.5656 | 2.7559 | 1.3661 | 2.3426 | 2.8906 | 2.8906 | 3.256 | 3.256 | 2020-01-28 02:00 | 1.5175 | 2.487 | 4.0824 | 4.0824 | 4.0824 | 4.0824
2021-11-30 14:00 | 2.1977 | 2.6744 | 2.6167 | 2.8145 | 2.6661 | 2.8639 | 1.3918 | 2.3867 | 2.945 | 2.945 | 3.3173 | 3.3173 | 2020-01-28 03:00 | 1.5156 | 2.4838 | 4.0772 | 4.0772 | 4.0772 | 4.0772
2021-11-30 15:00 | 1.9834 | 2.4136 | 2.3615 | 2.54 | 2.4061 | 2.5846 | 1.3003 | 2.2299 | 2.7515 | 2.7515 | 3.0993 | 3.0993 | 2020-01-28 04:00 | 1.5299 | 2.5072 | 4.1157 | 4.1157 | 4.1157 | 4.1157
2021-11-30 16:00 | 2.1263 | 2.5874 | 2.5316 | 2.723 | 2.5795 | 2.7708 | 1.3718 | 2.3524 | 2.9027 | 2.9027 | 3.2696 | 3.2696 | 2020-01-28 05:00 | 1.6499 | 2.704 | 4.4386 | 4.4386 | 4.4386 | 4.4386
2021-11-30 17:00 | 2.152 | 2.6187 | 2.5623 | 2.7559 | 2.6107 | 2.8043 | 1.5518 | 2.6611 | 3.2837 | 3.2837 | 3.6987 | 3.6987 | 2020-01-28 06:00 | 2.2815 | 3.739 | 6.1377 | 6.1377 | 6.1377 | 6.1377
2021-11-30 18:00 | 2.3692 | 2.8831 | 2.8209 | 3.0341 | 2.8742 | 3.0874 | 1.5718 | 2.6954 | 3.326 | 3.326 | 3.7464 | 3.7464 | 2020-01-28 07:00 | 2.7683 | 4.5368 | 7.4472 | 7.4472 | 7.4472 | 7.4472
2021-11-30 19:00 | 2.1416 | 2.6061 | 2.5499 | 2.7426 | 2.5981 | 2.7908 | 1.5918 | 2.7297 | 3.3683 | 3.3683 | 3.7941 | 3.7941 | 2020-01-28 08:00 | 3.1027 | 5.0848 | 8.3467 | 8.3467 | 8.3467 | 8.3467
2021-11-30 20:00 | 2.1434 | 2.6083 | 2.552 | 2.7449 | 2.6003 | 2.7932 | 1.6033 | 2.7494 | 3.3925 | 3.3925 | 3.8213 | 3.8213 | 2020-01-28 09:00 | 3.056 | 5.0083 | 8.2211 | 8.2211 | 8.2211 | 8.2211
2021-11-30 21:00 | 2.0062 | 2.4414 | 2.3887 | 2.5693 | 2.4339 | 2.6144 | 1.5375 | 2.6366 | 3.2534 | 3.2534 | 3.6647 | 3.6647 | 2020-01-28 10:00 | 3.1037 | 5.0863 | 8.3493 | 8.3493 | 8.3493 | 8.3493
2021-11-30 22:00 | 1.829 | 2.2258 | 2.1777 | 2.3424 | 2.2189 | 2.3835 | 1.3147 | 2.2545 | 2.7819 | 2.7819 | 3.1335 | 3.1335 | 2020-01-28 11:00 | 3.0151 | 4.9411 | 8.1109 | 8.1109 | 8.1109 | 8.1109
2021-11-30 23:00 | 1.6233 | 1.9754 | 1.9327 | 2.0788 | 1.9693 | 2.1154 | 1.0089 | 1.7302 | 2.1349 | 2.1349 | 2.4048 | 2.4048 | 2020-01-28 12:00 | 3.0541 | 5.0051 | 8.216 | 8.216 | 8.216 | 8.216
2021-12-01 | 1.5633 | 1.9023 | 1.8613 | 2.002 | 1.8965 | 2.0372 | 0.93452 | 1.6026 | 1.9775 | 1.9775 | 2.2274 | 2.2274 | 2020-01-28 13:00 | 2.8541 | 4.6773 | 7.6778 | 7.6778 | 7.6778 | 7.6778
2021-12-01 01:00 | 1.4347 | 1.7458 | 1.7082 | 1.8373 | 1.7404 | 1.8696 | 0.82307 | 1.4114 | 1.7416 | 1.7416 | 1.9617 | 1.9617 | 2020-01-28 14:00 | 2.7188 | 4.4556 | 7.3139 | 7.3139 | 7.3139 | 7.3139
2021-12-01 02:00 | 1.3461 | 1.638 | 1.6027 | 1.7238 | 1.633 | 1.7541 | 0.77162 | 1.3232 | 1.6328 | 1.6328 | 1.8391 | 1.8391 | 2020-01-28 15:00 | 2.6769 | 4.3869 | 7.2012 | 7.2012 | 7.2012 | 7.2012
2021-12-01 03:00 | 1.3661 | 1.6624 | 1.6265 | 1.7494 | 1.6572 | 1.7802 | 0.70596 | 1.2106 | 1.4938 | 1.4938 | 1.6826 | 1.6826 | 2020-01-28 16:00 | 2.6464 | 4.337 | 7.1192 | 7.1192 | 7.1192 | 7.1192
2021-12-01 04:00 | 1.3488 | 1.6414 | 1.606 | 1.7274 | 1.6363 | 1.7577 | 0.683 | 1.1712 | 1.4452 | 1.4452 | 1.6279 | 1.6279 | 2020-01-28 17:00 | 2.5883 | 4.2417 | 6.9628 | 6.9628 | 6.9628 | 6.9628
2021-12-01 05:00 | 1.471 | 1.7901 | 1.7515 | 1.8838 | 1.7845 | 1.9169 | 0.7459 | 1.2791 | 1.5783 | 1.5783 | 1.7778 | 1.7778 | 2020-01-28 18:00 | 2.3759 | 3.8936 | 6.3914 | 6.3914 | 6.3914 | 6.3914
2021-12-01 06:00 | 1.7547 | 2.1353 | 2.0893 | 2.2472 | 2.1288 | 2.2867 | 0.81735 | 1.4016 | 1.7295 | 1.7295 | 1.9481 | 1.9481 | 2020-01-28 19:00 | 2.0139 | 3.3003 | 5.4175 | 5.4175 | 5.4175 | 5.4175
2021-12-01 07:00 | 2.1463 | 2.6118 | 2.5554 | 2.7486 | 2.6037 | 2.7969 | 1.134 | 1.9446 | 2.3995 | 2.3995 | 2.7028 | 2.7028 | 2020-01-28 20:00 | 1.9996 | 3.2769 | 5.3791 | 5.3791 | 5.3791 | 5.3791
2021-12-01 08:00 | 2.1263 | 2.5874 | 2.5316 | 2.723 | 2.5795 | 2.7708 | 1.2089 | 2.073 | 2.558 | 2.558 | 2.8813 | 2.8813 | 2020-01-28 21:00 | 1.9729 | 3.2332 | 5.3073 | 5.3073 | 5.3073 | 5.3073
2021-12-01 09:00 | 2.1234 | 2.584 | 2.5282 | 2.7193 | 2.576 | 2.7671 | 1.2632 | 2.1662 | 2.6729 | 2.6729 | 3.0107 | 3.0107 | 2020-01-28 22:00 | 1.85 | 3.0318 | 4.9767 | 4.9767 | 4.9767 | 4.9767
2021-12-01 10:00 | 2.072 | 2.5214 | 2.467 | 2.6535 | 2.5136 | 2.7001 | 1.2889 | 2.2103 | 2.7273 | 2.7273 | 3.072 | 3.072 | 2020-01-28 23:00 | 1.7223 | 2.8226 | 4.6333 | 4.6333 | 4.6333 | 4.6333
2021-12-01 11:00 | 2.2863 | 2.7822 | 2.7222 | 2.9279 | 2.7736 | 2.9794 | 1.3632 | 2.3377 | 2.8846 | 2.8846 | 3.2491 | 3.2491 | 2020-01-29 | 1.5042 | 2.4651 | 4.0465 | 4.0465 | 4.0465 | 4.0465
2021-12-01 12:00 | 2.3292 | 2.8344 | 2.7732 | 2.9828 | 2.8256 | 3.0353 | 1.4004 | 2.4014 | 2.9632 | 2.9632 | 3.3377 | 3.3377 | 2020-01-29 01:00 | 1.4051 | 2.3027 | 3.78 | 3.78 | 3.78 | 3.78
2021-12-01 13:00 | 2.3492 | 2.8587 | 2.797 | 3.0085 | 2.8499 | 3.0613 | 1.3889 | 2.3818 | 2.939 | 2.939 | 3.3105 | 3.3105 | 2020-01-29 02:00 | 1.3889 | 2.2762 | 3.7364 | 3.7364 | 3.7364 | 3.7364
2021-12-01 14:00 | 2.2149 | 2.6953 | 2.6371 | 2.8364 | 2.6869 | 2.8863 | 1.3603 | 2.3328 | 2.8785 | 2.8785 | 3.2423 | 3.2423 | 2020-01-29 03:00 | 1.3842 | 2.2684 | 3.7236 | 3.7236 | 3.7236 | 3.7236
2021-12-01 15:00 | 2.0977 | 2.5527 | 2.4976 | 2.6864 | 2.5448 | 2.7336 | 1.3175 | 2.2593 | 2.7878 | 2.7878 | 3.1402 | 3.1402 | 2020-01-29 04:00 | 1.4499 | 2.3761 | 3.9004 | 3.9004 | 3.9004 | 3.9004
2021-12-01 16:00 | 2.1291 | 2.5909 | 2.535 | 2.7266 | 2.5829 | 2.7746 | 1.4061 | 2.4112 | 2.9753 | 2.9753 | 3.3513 | 3.3513 | 2020-01-29 05:00 | 1.5213 | 2.4932 | 4.0926 | 4.0926 | 4.0926 | 4.0926
2021-12-01 17:00 | 2.152 | 2.6187 | 2.5623 | 2.7559 | 2.6107 | 2.8043 | 1.559 | 2.6734 | 3.2988 | 3.2988 | 3.7158 | 3.7158 | 2020-01-29 06:00 | 1.7443 | 2.8585 | 4.6923 | 4.6923 | 4.6923 | 4.6923
2021-12-01 18:00 | 2.5006 | 3.043 | 2.9774 | 3.2024 | 3.0336 | 3.2587 | 1.5604 | 2.6758 | 3.3018 | 3.3018 | 3.7192 | 3.7192 | 2020-01-29 07:00 | 2.0682 | 3.3893 | 5.5636 | 5.5636 | 5.5636 | 5.5636
2021-12-01 19:00 | 2.2018 | 2.6794 | 2.6216 | 2.8198 | 2.6712 | 2.8693 | 1.5633 | 2.6807 | 3.3079 | 3.3079 | 3.726 | 3.726 | 2020-01-29 08:00 | 2.3901 | 3.917 | 6.4298 | 6.4298 | 6.4298 | 6.4298
2021-12-01 20:00 | 2.1949 | 2.6709 | 2.6133 | 2.8108 | 2.6627 | 2.8602 | 1.6033 | 2.7494 | 3.3925 | 3.3925 | 3.8213 | 3.8213 | 2020-01-29 09:00 | 2.4302 | 3.9826 | 6.5374 | 6.5374 | 6.5374 | 6.5374
2021-12-01 21:00 | 2.0748 | 2.5248 | 2.4704 | 2.6571 | 2.5171 | 2.7038 | 1.5633 | 2.6807 | 3.3079 | 3.3079 | 3.726 | 3.726 | 2020-01-29 10:00 | 2.5578 | 4.1918 | 6.8808 | 6.8808 | 6.8808 | 6.8808
2021-12-01 22:00 | 1.8966 | 2.3079 | 2.2581 | 2.4288 | 2.3008 | 2.4715 | 1.2462 | 2.137 | 2.637 | 2.637 | 2.9703 | 2.9703 | 2020-01-29 11:00 | 2.8207 | 4.6226 | 7.5881 | 7.5881 | 7.5881 | 7.5881
2021-12-01 23:00 | 1.6061 | 1.9545 | 1.9123 | 2.0569 | 1.9485 | 2.093 | 1.0203 | 1.7496 | 2.1589 | 2.1589 | 2.4317 | 2.4317 | 2020-01-29 12:00 | 3.0703 | 5.0317 | 8.2596 | 8.2596 | 8.2596 | 8.2596
2021-12-02 | 1.5518 | 1.8884 | 1.8477 | 1.9873 | 1.8826 | 2.0223 | 0.96596 | 1.6565 | 2.044 | 2.044 | 2.3023 | 2.3023 | 2020-01-29 13:00 | 2.8026 | 4.593 | 7.5394 | 7.5394 | 7.5394 | 7.5394
2021-12-02 01:00 | 1.4061 | 1.711 | 1.6741 | 1.8007 | 1.7058 | 1.8323 | 0.83164 | 1.4261 | 1.7598 | 1.7598 | 1.9822 | 1.9822 | 2020-01-29 14:00 | 2.8626 | 4.6913 | 7.7009 | 7.7009 | 7.7009 | 7.7009
2021-12-02 02:00 | 1.3918 | 1.6937 | 1.6571 | 1.7824 | 1.6884 | 1.8137 | 0.77448 | 1.3281 | 1.6388 | 1.6388 | 1.8459 | 1.8459 | 2020-01-29 15:00 | 2.8541 | 4.6773 | 7.6778 | 7.6778 | 7.6778 | 7.6778
2021-12-02 03:00 | 1.3546 | 1.6484 | 1.6129 | 1.7348 | 1.6434 | 1.7653 | 0.71721 | 1.2299 | 1.5176 | 1.5176 | 1.7094 | 1.7094 | 2020-01-29 16:00 | 2.8693 | 4.7023 | 7.7188 | 7.7188 | 7.7188 | 7.7188
2021-12-02 04:00 | 1.3718 | 1.6693 | 1.6333 | 1.7568 | 1.6642 | 1.7876 | 0.71733 | 1.2301 | 1.5179 | 1.5179 | 1.7097 | 1.7097 | 2020-01-29 17:00 | 2.7455 | 4.4993 | 7.3857 | 7.3857 | 7.3857 | 7.3857
2021-12-02 05:00 | 1.5147 | 1.8432 | 1.8034 | 1.9398 | 1.8375 | 1.9738 | 0.70875 | 1.2154 | 1.4997 | 1.4997 | 1.6893 | 1.6893 | 2020-01-29 18:00 | 2.6397 | 4.326 | 7.1012 | 7.1012 | 7.1012 | 7.1012
2021-12-02 06:00 | 1.8005 | 2.191 | 2.1437 | 2.3058 | 2.1842 | 2.3463 | 0.81735 | 1.4016 | 1.7295 | 1.7295 | 1.9481 | 1.9481 | 2020-01-29 19:00 | 2.3549 | 3.8592 | 6.335 | 6.335 | 6.335 | 6.335
2021-12-02 07:00 | 2.0291 | 2.4692 | 2.4159 | 2.5986 | 2.4616 | 2.6442 | 1.1089 | 1.9015 | 2.3464 | 2.3464 | 2.6429 | 2.6429 | 2020-01-29 20:00 | 2.3101 | 3.7859 | 6.2145 | 6.2145 | 6.2145 | 6.2145
2021-12-02 08:00 | 2.0491 | 2.4935 | 2.4398 | 2.6242 | 2.4859 | 2.6703 | 1.2546 | 2.1515 | 2.6548 | 2.6548 | 2.9903 | 2.9903 | 2020-01-29 21:00 | 2.1729 | 3.561 | 5.8455 | 5.8455 | 5.8455 | 5.8455
2021-12-02 09:00 | 2.0348 | 2.4762 | 2.4227 | 2.6059 | 2.4685 | 2.6517 | 1.1917 | 2.0436 | 2.5217 | 2.5217 | 2.8404 | 2.8404 | 2020-01-29 22:00 | 2.0281 | 3.3237 | 5.456 | 5.456 | 5.456 | 5.456
2021-12-02 10:00 | 2.0748 | 2.5248 | 2.4704 | 2.6571 | 2.5171 | 2.7038 | 1.306 | 2.2397 | 2.7636 | 2.7636 | 3.1129 | 3.1129 | 2020-01-29 23:00 | 1.8329 | 3.0037 | 4.9306 | 4.9306 | 4.9306 | 4.9306
2021-12-02 11:00 | 2.1234 | 2.584 | 2.5282 | 2.7193 | 2.576 | 2.7671 | 1.3403 | 2.2985 | 2.8362 | 2.8362 | 3.1947 | 3.1947 | 2020-01-30 | 1.5861 | 2.5994 | 4.2669 | 4.2669 | 4.2669 | 4.2669
2021-12-02 12:00 | 2.1177 | 2.577 | 2.5214 | 2.712 | 2.5691 | 2.7597 | 1.2975 | 2.225 | 2.7455 | 2.7455 | 3.0925 | 3.0925 | 2020-01-30 01:00 | 1.6547 | 2.7118 | 4.4514 | 4.4514 | 4.4514 | 4.4514
2021-12-02 13:00 | 2.052 | 2.4971 | 2.4432 | 2.6279 | 2.4894 | 2.6741 | 1.3746 | 2.3573 | 2.9088 | 2.9088 | 3.2764 | 3.2764 | 2020-01-30 02:00 | 1.5899 | 2.6056 | 4.2771 | 4.2771 | 4.2771 | 4.2771
2021-12-02 14:00 | 2.3492 | 2.8587 | 2.797 | 3.0085 | 2.8499 | 3.0613 | 1.3546 | 2.323 | 2.8664 | 2.8664 | 3.2287 | 3.2287 | 2020-01-30 03:00 | 1.6328 | 2.6759 | 4.3925 | 4.3925 | 4.3925 | 4.3925
2021-12-02 15:00 | 2.2349 | 2.7196 | 2.6609 | 2.8621 | 2.7112 | 2.9124 | 1.3575 | 2.3279 | 2.8725 | 2.8725 | 3.2355 | 3.2355 | 2020-01-30 04:00 | 1.5509 | 2.5416 | 4.1721 | 4.1721 | 4.1721 | 4.1721
2021-12-02 16:00 | 2.4406 | 2.97 | 2.9059 | 3.1256 | 2.9608 | 3.1805 | 1.5004 | 2.5729 | 3.1748 | 3.1748 | 3.5761 | 3.5761 | 2020-01-30 05:00 | 1.6747 | 2.7445 | 4.5052 | 4.5052 | 4.5052 | 4.5052
2021-12-02 17:00 | 2.2634 | 2.7544 | 2.695 | 2.8987 | 2.7459 | 2.9496 | 1.5661 | 2.6856 | 3.3139 | 3.3139 | 3.7328 | 3.7328 | 2020-01-30 06:00 | 1.9014 | 3.1161 | 5.1151 | 5.1151 | 5.1151 | 5.1151
2021-12-02 18:00 | 2.5121 | 3.0569 | 2.991 | 3.2171 | 3.0475 | 3.2736 | 1.7462 | 2.9944 | 3.6949 | 3.6949 | 4.1619 | 4.1619 | 2020-01-30 07:00 | 2.4825 | 4.0684 | 6.6784 | 6.6784 | 6.6784 | 6.6784
2021-12-02 19:00 | 2.3778 | 2.8935 | 2.8311 | 3.0451 | 2.8846 | 3.0986 | 1.6719 | 2.867 | 3.5377 | 3.5377 | 3.9848 | 3.9848 | 2020-01-30 08:00 | 2.4292 | 3.981 | 6.5349 | 6.5349 | 6.5349 | 6.5349
2021-12-02 20:00 | 2.2434 | 2.73 | 2.6711 | 2.873 | 2.7216 | 2.9235 | 1.6547 | 2.8376 | 3.5014 | 3.5014 | 3.9439 | 3.9439 | 2020-01-30 09:00 | 2.5778 | 4.2245 | 6.9347 | 6.9347 | 6.9347 | 6.9347
2021-12-02 21:00 | 2.1348 | 2.5979 | 2.5418 | 2.734 | 2.5899 | 2.782 | 1.5204 | 2.6072 | 3.2172 | 3.2172 | 3.6238 | 3.6238 | 2020-01-30 10:00 | 2.4959 | 4.0903 | 6.7143 | 6.7143 | 6.7143 | 6.7143
2021-12-02 22:00 | 1.8405 | 2.2397 | 2.1914 | 2.357 | 2.2328 | 2.3984 | 1.2689 | 2.176 | 2.685 | 2.685 | 3.0244 | 3.0244 | 2020-01-30 11:00 | 2.6454 | 4.3354 | 7.1166 | 7.1166 | 7.1166 | 7.1166
2021-12-02 23:00 | 1.7319 | 2.1075 | 2.0621 | 2.2179 | 2.101 | 2.2569 | 1.0946 | 1.877 | 2.3161 | 2.3161 | 2.6089 | 2.6089 | 2020-01-30 12:00 | 2.7845 | 4.5633 | 7.4908 | 7.4908 | 7.4908 | 7.4908
2021-12-03 | 1.5976 | 1.9442 | 1.9022 | 2.046 | 1.9382 | 2.082 | 0.94596 | 1.6222 | 2.0017 | 2.0017 | 2.2546 | 2.2546 | 2020-01-30 13:00 | 2.8083 | 4.6024 | 7.5548 | 7.5548 | 7.5548 | 7.5548
2021-12-03 01:00 | 1.4404 | 1.7528 | 1.715 | 1.8446 | 1.7474 | 1.877 | 0.78591 | 1.3477 | 1.663 | 1.663 | 1.8732 | 1.8732 | 2020-01-30 14:00 | 2.7731 | 4.5446 | 7.46 | 7.46 | 7.46 | 7.46
2021-12-03 02:00 | 1.3461 | 1.638 | 1.6027 | 1.7238 | 1.633 | 1.7541 | 0.7459 | 1.2791 | 1.5783 | 1.5783 | 1.7778 | 1.7778 | 2020-01-30 15:00 | 3.0789 | 5.0457 | 8.2826 | 8.2826 | 8.2826 | 8.2826
2021-12-03 03:00 | 1.3152 | 1.6005 | 1.5659 | 1.6843 | 1.5955 | 1.7139 | 0.70875 | 1.2154 | 1.4997 | 1.4997 | 1.6893 | 1.6893 | 2020-01-30 16:00 | 2.774 | 4.5461 | 7.4626 | 7.4626 | 7.4626 | 7.4626
2021-12-03 04:00 | 1.3346 | 1.6241 | 1.5891 | 1.7092 | 1.6191 | 1.7392 | 0.68908 | 1.1817 | 1.4581 | 1.4581 | 1.6424 | 1.6424 | 2020-01-30 17:00 | 2.654 | 4.3494 | 7.1397 | 7.1397 | 7.1397 | 7.1397
2021-12-03 05:00 | 1.4632 | 1.7806 | 1.7422 | 1.8739 | 1.7751 | 1.9068 | 0.75734 | 1.2987 | 1.6025 | 1.6025 | 1.8051 | 1.8051 | 2020-01-30 18:00 | 2.5026 | 4.1012 | 6.7322 | 6.7322 | 6.7322 | 6.7322
2021-12-03 06:00 | 1.7433 | 2.1214 | 2.0757 | 2.2326 | 2.1149 | 2.2718 | 0.79421 | 1.3619 | 1.6806 | 1.6806 | 1.893 | 1.893 | 2020-01-30 19:00 | 2.3549 | 3.8592 | 6.335 | 6.335 | 6.335 | 6.335
2021-12-03 07:00 | 2.1005 | 2.5561 | 2.501 | 2.69 | 2.5483 | 2.7373 | 1.2003 | 2.0583 | 2.5399 | 2.5399 | 2.8609 | 2.8609 | 2020-01-30 20:00 | 2.2911 | 3.7546 | 6.1633 | 6.1633 | 6.1633 | 6.1633
2021-12-03 08:00 | 2.2406 | 2.7266 | 2.6677 | 2.8694 | 2.7181 | 2.9198 | 1.3489 | 2.3132 | 2.8543 | 2.8543 | 3.2151 | 3.2151 | 2020-01-30 21:00 | 2.2625 | 3.7078 | 6.0864 | 6.0864 | 6.0864 | 6.0864
2021-12-03 09:00 | 2.2549 | 2.7439 | 2.6848 | 2.8877 | 2.7355 | 2.9384 | 1.2346 | 2.1171 | 2.6124 | 2.6124 | 2.9426 | 2.9426 | 2020-01-30 22:00 | 2.111 | 3.4596 | 5.6789 | 5.6789 | 5.6789 | 5.6789
2021-12-03 10:00 | 2.3177 | 2.8205 | 2.7596 | 2.9682 | 2.8118 | 3.0204 | 1.3146 | 2.2544 | 2.7818 | 2.7818 | 3.1333 | 3.1333 | 2020-01-30 23:00 | 1.9662 | 3.2223 | 5.2894 | 5.2894 | 5.2894 | 5.2894
2021-12-03 11:00 | 2.5521 | 3.1056 | 3.0386 | 3.2683 | 3.0961 | 3.3257 | 1.3804 | 2.3671 | 2.9208 | 2.9208 | 3.29 | 3.29 | 2020-01-31 | 1.7681 | 2.8975 | 4.7564 | 4.7564 | 4.7564 | 4.7564
2021-12-03 12:00 | 2.4611 | 2.9949 | 2.9303 | 3.1518 | 2.9856 | 3.2071 | 1.4232 | 2.4406 | 3.0116 | 3.0116 | 3.3922 | 3.3922 | 2020-01-31 01:00 | 1.7547 | 2.8757 | 4.7205 | 4.7205 | 4.7205 | 4.7205
2021-12-03 13:00 | 2.4778 | 3.0152 | 2.9502 | 3.1732 | 3.0059 | 3.2289 | 1.4461 | 2.4798 | 3.0599 | 3.0599 | 3.4467 | 3.4467 | 2020-01-31 02:00 | 1.7328 | 2.8398 | 4.6615 | 4.6615 | 4.6615 | 4.6615
2021-12-03 14:00 | 2.695 | 3.2795 | 3.2088 | 3.4513 | 3.2694 | 3.512 | 1.4689 | 2.519 | 3.1083 | 3.1083 | 3.5012 | 3.5012 | 2020-01-31 03:00 | 1.6861 | 2.7633 | 4.536 | 4.536 | 4.536 | 4.536
2021-12-03 15:00 | 2.6007 | 3.1647 | 3.0965 | 3.3305 | 3.155 | 3.3891 | 1.4004 | 2.4014 | 2.9632 | 2.9632 | 3.3377 | 3.3377 | 2020-01-31 04:00 | 1.809 | 2.9647 | 4.8666 | 4.8666 | 4.8666 | 4.8666
2021-12-03 16:00 | 2.5178 | 3.0639 | 2.9978 | 3.2244 | 3.0545 | 3.2811 | 1.5318 | 2.6268 | 3.2414 | 3.2414 | 3.651 | 3.651 | 2020-01-31 05:00 | 1.8281 | 2.9959 | 4.9178 | 4.9178 | 4.9178 | 4.9178
2021-12-03 17:00 | 2.5121 | 3.0569 | 2.991 | 3.2171 | 3.0475 | 3.2736 | 1.609 | 2.7592 | 3.4046 | 3.4046 | 3.8349 | 3.8349 | 2020-01-31 06:00 | 1.8386 | 3.0131 | 4.946 | 4.946 | 4.946 | 4.946
2021-12-03 18:00 | 2.4463 | 2.9769 | 2.9127 | 3.1329 | 2.9678 | 3.1879 | 1.7462 | 2.9944 | 3.6949 | 3.6949 | 4.1619 | 4.1619 | 2020-01-31 07:00 | 2.1815 | 3.5751 | 5.8686 | 5.8686 | 5.8686 | 5.8686
2021-12-03 19:00 | 2.1748 | 2.6466 | 2.5895 | 2.7852 | 2.6384 | 2.8341 | 1.6919 | 2.9013 | 3.58 | 3.58 | 4.0325 | 4.0325 | 2020-01-31 08:00 | 2.4625 | 4.0356 | 6.6246 | 6.6246 | 6.6246 | 6.6246
2021-12-03 20:00 | 2.0491 | 2.4935 | 2.4398 | 2.6242 | 2.4859 | 2.6703 | 1.7233 | 2.9552 | 3.6465 | 3.6465 | 4.1074 | 4.1074 | 2020-01-31 09:00 | 2.5902 | 4.2448 | 6.968 | 6.968 | 6.968 | 6.968
2021-12-03 21:00 | 1.9205 | 2.337 | 2.2866 | 2.4595 | 2.3298 | 2.5027 | 1.5747 | 2.7003 | 3.3321 | 3.3321 | 3.7532 | 3.7532 | 2020-01-31 10:00 | 2.7502 | 4.5071 | 7.3985 | 7.3985 | 7.3985 | 7.3985
2021-12-03 22:00 | 1.8176 | 2.2118 | 2.1641 | 2.3277 | 2.205 | 2.3686 | 1.3203 | 2.2642 | 2.7939 | 2.7939 | 3.147 | 3.147 | 2020-01-31 11:00 | 2.8607 | 4.6882 | 7.6958 | 7.6958 | 7.6958 | 7.6958
2021-12-03 23:00 | 1.669 | 2.031 | 1.9872 | 2.1374 | 2.0247 | 2.175 | 1.1489 | 1.9701 | 2.431 | 2.431 | 2.7383 | 2.7383 | 2020-01-31 12:00 | 2.9436 | 4.824 | 7.9187 | 7.9187 | 7.9187 | 7.9187
2021-12-04 | 1.6062 | 1.9546 | 1.9124 | 2.057 | 1.9486 | 2.0931 | 0.97338 | 1.6692 | 2.0597 | 2.0597 | 2.32 | 2.32 | 2020-01-31 13:00 | 2.9341 | 4.8084 | 7.8931 | 7.8931 | 7.8931 | 7.8931
2021-12-04 01:00 | 1.4289 | 1.7389 | 1.7014 | 1.83 | 1.7335 | 1.8621 | 0.82592 | 1.4163 | 1.7477 | 1.7477 | 1.9686 | 1.9686 | 2020-01-31 14:00 | 2.9693 | 4.8662 | 7.9879 | 7.9879 | 7.9879 | 7.9879
2021-12-04 02:00 | 1.3804 | 1.6797 | 1.6435 | 1.7677 | 1.6746 | 1.7988 | 0.80306 | 1.3771 | 1.6993 | 1.6993 | 1.9141 | 1.9141 | 2020-01-31 15:00 | 3.0513 | 5.0005 | 8.2083 | 8.2083 | 8.2083 | 8.2083
2021-12-04 03:00 | 1.3463 | 1.6383 | 1.603 | 1.7242 | 1.6333 | 1.7545 | 0.75734 | 1.2987 | 1.6025 | 1.6025 | 1.8051 | 1.8051 | 2020-01-31 16:00 | 3.1389 | 5.1441 | 8.4441 | 8.4441 | 8.4441 | 8.4441
2021-12-04 04:00 | 1.3318 | 1.6206 | 1.5857 | 1.7055 | 1.6156 | 1.7355 | 0.73161 | 1.2546 | 1.5481 | 1.5481 | 1.7438 | 1.7438 | 2020-01-31 17:00 | 3.0055 | 4.9255 | 8.0853 | 8.0853 | 8.0853 | 8.0853
2021-12-04 05:00 | 1.3665 | 1.6629 | 1.627 | 1.75 | 1.6578 | 1.7807 | 0.70555 | 1.2099 | 1.493 | 1.493 | 1.6817 | 1.6817 | 2020-01-31 18:00 | 2.7645 | 4.5305 | 7.4369 | 7.4369 | 7.4369 | 7.4369
2021-12-04 06:00 | 1.5032 | 1.8293 | 1.7898 | 1.9251 | 1.8237 | 1.9589 | 0.74019 | 1.2693 | 1.5662 | 1.5662 | 1.7642 | 1.7642 | 2020-01-31 19:00 | 2.4092 | 3.9482 | 6.4811 | 6.4811 | 6.4811 | 6.4811
2021-12-04 07:00 | 1.5827 | 1.9259 | 1.8844 | 2.0268 | 1.92 | 2.0624 | 0.97739 | 1.6761 | 2.0682 | 2.0682 | 2.3296 | 2.3296 | 2020-01-31 20:00 | 2.2615 | 3.7062 | 6.0838 | 6.0838 | 6.0838 | 6.0838
2021-12-04 08:00 | 1.6233 | 1.9754 | 1.9327 | 2.0788 | 1.9693 | 2.1154 | 1.126 | 1.9309 | 2.3826 | 2.3826 | 2.6838 | 2.6838 | 2020-01-31 21:00 | 2.1301 | 3.4908 | 5.7302 | 5.7302 | 5.7302 | 5.7302
2021-12-04 09:00 | 1.7147 | 2.0866 | 2.0416 | 2.196 | 2.0802 | 2.2345 | 1.2603 | 2.1613 | 2.6669 | 2.6669 | 3.0039 | 3.0039 | 2020-01-31 22:00 | 2.0386 | 3.3409 | 5.4842 | 5.4842 | 5.4842 | 5.4842
2021-12-04 10:00 | 1.5347 | 1.8675 | 1.8273 | 1.9654 | 1.8618 | 1.9999 | 1.4347 | 2.4602 | 3.0357 | 3.0357 | 3.4194 | 3.4194 | 2020-01-31 23:00 | 1.9691 | 3.227 | 5.2971 | 5.2971 | 5.2971 | 5.2971
2021-12-04 11:00 | 1.5232 | 1.8536 | 1.8137 | 1.9507 | 1.8479 | 1.985 | 1.4489 | 2.4847 | 3.066 | 3.066 | 3.4535 | 3.4535 | 2020-02-01 | 1.8872 | 3.0927 | 5.0767 | 5.0767 | 5.0767 | 5.0767
2021-12-04 12:00 | 1.5061 | 1.8328 | 1.7932 | 1.9288 | 1.8271 | 1.9627 | 1.4918 | 2.5582 | 3.1567 | 3.1567 | 3.5557 | 3.5557 | 2020-02-01 01:00 | 1.7166 | 2.8132 | 4.618 | 4.618 | 4.618 | 4.618
2021-12-04 13:00 | 1.669 | 2.031 | 1.9872 | 2.1374 | 2.0247 | 2.175 | 1.4489 | 2.4847 | 3.066 | 3.066 | 3.4535 | 3.4535 | 2020-02-01 02:00 | 1.6966 | 2.7805 | 4.5642 | 4.5642 | 4.5642 | 4.5642
2021-12-04 14:00 | 1.4604 | 1.7771 | 1.7388 | 1.8702 | 1.7716 | 1.9031 | 1.4232 | 2.4406 | 3.0116 | 3.0116 | 3.3922 | 3.3922 | 2020-02-01 03:00 | 1.749 | 2.8663 | 4.7051 | 4.7051 | 4.7051 | 4.7051
2021-12-04 15:00 | 1.7404 | 2.1179 | 2.0723 | 2.2289 | 2.1114 | 2.2681 | 1.5061 | 2.5827 | 3.1869 | 3.1869 | 3.5897 | 3.5897 | 2020-02-01 04:00 | 1.7214 | 2.821 | 4.6308 | 4.6308 | 4.6308 | 4.6308
2021-12-04 16:00 | 1.6776 | 2.0414 | 1.9974 | 2.1484 | 2.0351 | 2.1861 | 1.509 | 2.5876 | 3.193 | 3.193 | 3.5965 | 3.5965 | 2020-02-01 05:00 | 1.7547 | 2.8757 | 4.7205 | 4.7205 | 4.7205 | 4.7205
2021-12-04 17:00 | 1.7334 | 2.1093 | 2.0638 | 2.2198 | 2.1028 | 2.2588 | 1.609 | 2.7592 | 3.4046 | 3.4046 | 3.8349 | 3.8349 | 2020-02-01 06:00 | 2.0529 | 3.3643 | 5.5226 | 5.5226 | 5.5226 | 5.5226
2021-12-04 18:00 | 1.7919 | 2.1805 | 2.1335 | 2.2948 | 2.1738 | 2.3351 | 1.6261 | 2.7886 | 3.4409 | 3.4409 | 3.8758 | 3.8758 | 2020-02-01 07:00 | 2.1815 | 3.5751 | 5.8686 | 5.8686 | 5.8686 | 5.8686
2021-12-04 19:00 | 1.8319 | 2.2292 | 2.1811 | 2.346 | 2.2224 | 2.3872 | 1.5633 | 2.6807 | 3.3079 | 3.3079 | 3.726 | 3.726 | 2020-02-01 08:00 | 2.4806 | 4.0653 | 6.6733 | 6.6733 | 6.6733 | 6.6733
2021-12-04 20:00 | 1.8633 | 2.2675 | 2.2186 | 2.3863 | 2.2605 | 2.4282 | 1.5518 | 2.6611 | 3.2837 | 3.2837 | 3.6987 | 3.6987 | 2020-02-01 09:00 | 2.6645 | 4.3666 | 7.1679 | 7.1679 | 7.1679 | 7.1679
2021-12-04 21:00 | 1.7919 | 2.1805 | 2.1335 | 2.2948 | 2.1738 | 2.3351 | 1.4861 | 2.5484 | 3.1446 | 3.1446 | 3.542 | 3.542 | 2020-02-01 10:00 | 2.7674 | 4.5352 | 7.4446 | 7.4446 | 7.4446 | 7.4446
2021-12-04 22:00 | 1.6261 | 1.9788 | 1.9361 | 2.0825 | 1.9727 | 2.1191 | 1.3289 | 2.2789 | 2.812 | 2.812 | 3.1674 | 3.1674 | 2020-02-01 11:00 | 2.8903 | 4.7366 | 7.7752 | 7.7752 | 7.7752 | 7.7752
2021-12-04 23:00 | 1.6347 | 1.9893 | 1.9464 | 2.0935 | 1.9831 | 2.1303 | 1.0688 | 1.8329 | 2.2617 | 2.2617 | 2.5475 | 2.5475 | 2020-02-01 12:00 | 2.9493 | 4.8334 | 7.9341 | 7.9341 | 7.9341 | 7.9341
2021-12-05 | 1.5232 | 1.8536 | 1.8137 | 1.9507 | 1.8479 | 1.985 | 0.96689 | 1.6581 | 2.046 | 2.046 | 2.3045 | 2.3045 | 2020-02-01 13:00 | 3.0322 | 4.9692 | 8.1571 | 8.1571 | 8.1571 | 8.1571
2021-12-05 01:00 | 1.4604 | 1.7771 | 1.7388 | 1.8702 | 1.7716 | 1.9031 | 0.83183 | 1.4265 | 1.7602 | 1.7602 | 1.9826 | 1.9826 | 2020-02-01 14:00 | 3.037 | 4.977 | 8.1699 | 8.1699 | 8.1699 | 8.1699
2021-12-05 02:00 | 1.3861 | 1.6867 | 1.6503 | 1.7751 | 1.6815 | 1.8063 | 0.84307 | 1.4457 | 1.7839 | 1.7839 | 2.0094 | 2.0094 | 2020-02-01 15:00 | 3.0551 | 5.0067 | 8.2186 | 8.2186 | 8.2186 | 8.2186
2021-12-05 03:00 | 1.3661 | 1.6624 | 1.6265 | 1.7494 | 1.6572 | 1.7802 | 0.77462 | 1.3284 | 1.6391 | 1.6391 | 1.8463 | 1.8463 | 2020-02-01 16:00 | 2.9922 | 4.9037 | 8.0494 | 8.0494 | 8.0494 | 8.0494
2021-12-05 04:00 | 1.3346 | 1.6241 | 1.5891 | 1.7092 | 1.6191 | 1.7392 | 0.77448 | 1.3281 | 1.6388 | 1.6388 | 1.8459 | 1.8459 | 2020-02-01 17:00 | 2.9284 | 4.7991 | 7.8777 | 7.8777 | 7.8777 | 7.8777
2021-12-05 05:00 | 1.3432 | 1.6345 | 1.5993 | 1.7202 | 1.6295 | 1.7504 | 0.75448 | 1.2938 | 1.5965 | 1.5965 | 1.7983 | 1.7983 | 2020-02-01 18:00 | 2.6969 | 4.4197 | 7.255 | 7.255 | 7.255 | 7.255
2021-12-05 06:00 | 1.3688 | 1.6657 | 1.6298 | 1.753 | 1.6606 | 1.7838 | 0.71733 | 1.2301 | 1.5179 | 1.5179 | 1.7097 | 1.7097 | 2020-02-01 19:00 | 2.473 | 4.0528 | 6.6528 | 6.6528 | 6.6528 | 6.6528
2021-12-05 07:00 | 1.489 | 1.8119 | 1.7728 | 1.9068 | 1.8063 | 1.9403 | 0.99168 | 1.7006 | 2.0984 | 2.0984 | 2.3636 | 2.3636 | 2020-02-01 20:00 | 2.4044 | 3.9404 | 6.4682 | 6.4682 | 6.4682 | 6.4682
2021-12-05 08:00 | 1.6233 | 1.9754 | 1.9327 | 2.0788 | 1.9693 | 2.1154 | 1.1317 | 1.9407 | 2.3947 | 2.3947 | 2.6974 | 2.6974 | 2020-02-01 21:00 | 2.2625 | 3.7078 | 6.0864 | 6.0864 | 6.0864 | 6.0864
2021-12-05 09:00 | 1.6204 | 1.9719 | 1.9293 | 2.0752 | 1.9658 | 2.1116 | 1.3409 | 2.2995 | 2.8374 | 2.8374 | 3.196 | 3.196 | 2020-02-01 22:00 | 2.1996 | 3.6048 | 5.9173 | 5.9173 | 5.9173 | 5.9173
2021-12-05 10:00 | 1.7652 | 2.1481 | 2.1017 | 2.2606 | 2.1415 | 2.3003 | 1.5004 | 2.5729 | 3.1748 | 3.1748 | 3.5761 | 3.5761 | 2020-02-01 23:00 | 2.1196 | 3.4736 | 5.702 | 5.702 | 5.702 | 5.702
2021-12-05 11:00 | 1.8433 | 2.2431 | 2.1948 | 2.3607 | 2.2362 | 2.4021 | 1.5604 | 2.6758 | 3.3018 | 3.3018 | 3.7192 | 3.7192 | 2020-02-02 | 1.9005 | 3.1145 | 5.1126 | 5.1126 | 5.1126 | 5.1126
2021-12-05 12:00 | 1.8148 | 2.2084 | 2.1607 | 2.3241 | 2.2016 | 2.3649 | 1.5661 | 2.6856 | 3.3139 | 3.3139 | 3.7328 | 3.7328 | 2020-02-02 01:00 | 1.8471 | 3.0271 | 4.9691 | 4.9691 | 4.9691 | 4.9691
2021-12-05 13:00 | 1.6976 | 2.0658 | 2.0212 | 2.174 | 2.0594 | 2.2122 | 1.5433 | 2.6464 | 3.2655 | 3.2655 | 3.6783 | 3.6783 | 2020-02-02 02:00 | 1.8519 | 3.0349 | 4.9819 | 4.9819 | 4.9819 | 4.9819
2021-12-05 14:00 | 1.6376 | 1.9927 | 1.9498 | 2.0971 | 1.9866 | 2.134 | 1.5232 | 2.6121 | 3.2232 | 3.2232 | 3.6306 | 3.6306 | 2020-02-02 03:00 | 1.7871 | 2.9288 | 4.8076 | 4.8076 | 4.8076 | 4.8076
2021-12-05 15:00 | 1.5261 | 1.8571 | 1.8171 | 1.9544 | 1.8514 | 1.9887 | 1.4832 | 2.5435 | 3.1385 | 3.1385 | 3.5352 | 3.5352 | 2020-02-02 04:00 | 1.89 | 3.0974 | 5.0844 | 5.0844 | 5.0844 | 5.0844
2021-12-05 16:00 | 1.5804 | 1.9232 | 1.8817 | 2.0239 | 1.9173 | 2.0595 | 1.4432 | 2.4749 | 3.0539 | 3.0539 | 3.4399 | 3.4399 | 2020-02-02 05:00 | 1.9129 | 3.1348 | 5.1459 | 5.1459 | 5.1459 | 5.1459
2021-12-05 17:00 | 1.8633 | 2.2675 | 2.2186 | 2.3863 | 2.2605 | 2.4282 | 1.5976 | 2.7395 | 3.3804 | 3.3804 | 3.8077 | 3.8077 | 2020-02-02 06:00 | 2.1844 | 3.5798 | 5.8763 | 5.8763 | 5.8763 | 5.8763
2021-12-05 18:00 | 1.9234 | 2.3405 | 2.29 | 2.4631 | 2.3333 | 2.5064 | 1.6976 | 2.9111 | 3.5921 | 3.5921 | 4.0461 | 4.0461 | 2020-02-02 07:00 | 2.4349 | 3.9904 | 6.5502 | 6.5502 | 6.5502 | 6.5502
2021-12-05 19:00 | 1.9834 | 2.4136 | 2.3615 | 2.54 | 2.4061 | 2.5846 | 1.6661 | 2.8572 | 3.5256 | 3.5256 | 3.9712 | 3.9712 | 2020-02-02 08:00 | 2.5502 | 4.1793 | 6.8603 | 6.8603 | 6.8603 | 6.8603
2021-12-05 20:00 | 2.072 | 2.5214 | 2.467 | 2.6535 | 2.5136 | 2.7001 | 1.6919 | 2.9013 | 3.58 | 3.58 | 4.0325 | 4.0325 | 2020-02-02 09:00 | 2.755 | 4.5149 | 7.4113 | 7.4113 | 7.4113 | 7.4113
2021-12-05 21:00 | 1.9691 | 2.3962 | 2.3445 | 2.5217 | 2.3888 | 2.566 | 1.5747 | 2.7003 | 3.3321 | 3.3321 | 3.7532 | 3.7532 | 2020-02-02 10:00 | 2.8217 | 4.6242 | 7.5907 | 7.5907 | 7.5907 | 7.5907
2021-12-05 22:00 | 1.8605 | 2.264 | 2.2152 | 2.3826 | 2.257 | 2.4245 | 1.3057 | 2.2391 | 2.7629 | 2.7629 | 3.1122 | 3.1122 | 2020-02-02 11:00 | 2.8865 | 4.7304 | 7.765 | 7.765 | 7.765 | 7.765
2021-12-05 23:00 | 1.6347 | 1.9893 | 1.9464 | 2.0935 | 1.9831 | 2.1303 | 1.0803 | 1.8525 | 2.2859 | 2.2859 | 2.5748 | 2.5748 | 2020-02-02 12:00 | 2.8884 | 4.7335 | 7.7701 | 7.7701 | 7.7701 | 7.7701
2021-12-06 | 1.5812 | 1.9241 | 1.8826 | 2.0249 | 1.9182 | 2.0605 | 0.97453 | 1.6712 | 2.0621 | 2.0621 | 2.3228 | 2.3228 | 2020-02-02 13:00 | 2.9541 | 4.8412 | 7.9469 | 7.9469 | 7.9469 | 7.9469
2021-12-06 01:00 | 1.4518 | 1.7667 | 1.7286 | 1.8592 | 1.7612 | 1.8919 | 0.83462 | 1.4312 | 1.7661 | 1.7661 | 1.9893 | 1.9893 | 2020-02-02 14:00 | 2.8884 | 4.7335 | 7.7701 | 7.7701 | 7.7701 | 7.7701
2021-12-06 02:00 | 1.4261 | 1.7354 | 1.698 | 1.8263 | 1.73 | 1.8584 | 0.84879 | 1.4555 | 1.796 | 1.796 | 2.0231 | 2.0231 | 2020-02-02 15:00 | 2.9103 | 4.7694 | 7.829 | 7.829 | 7.829 | 7.829
2021-12-06 03:00 | 1.4004 | 1.7041 | 1.6673 | 1.7934 | 1.6988 | 1.8249 | 0.76591 | 1.3134 | 1.6207 | 1.6207 | 1.8255 | 1.8255 | 2020-02-02 16:00 | 2.8198 | 4.6211 | 7.5856 | 7.5856 | 7.5856 | 7.5856
2021-12-06 04:00 | 1.3746 | 1.6728 | 1.6367 | 1.7604 | 1.6676 | 1.7914 | 0.76305 | 1.3085 | 1.6146 | 1.6146 | 1.8187 | 1.8187 | 2020-02-02 17:00 | 2.6845 | 4.3994 | 7.2217 | 7.2217 | 7.2217 | 7.2217
2021-12-06 05:00 | 1.5728 | 1.9139 | 1.8726 | 2.0142 | 1.908 | 2.0496 | 0.78306 | 1.3428 | 1.657 | 1.657 | 1.8664 | 1.8664 | 2020-02-02 18:00 | 2.2644 | 3.7109 | 6.0915 | 6.0915 | 6.0915 | 6.0915
2021-12-06 06:00 | 1.8833 | 2.2918 | 2.2424 | 2.4119 | 2.2848 | 2.4543 | 0.84879 | 1.4555 | 1.796 | 1.796 | 2.0231 | 2.0231 | 2020-02-02 19:00 | 2.0253 | 3.3191 | 5.4483 | 5.4483 | 5.4483 | 5.4483
2021-12-06 07:00 | 2.1748 | 2.6466 | 2.5895 | 2.7852 | 2.6384 | 2.8341 | 1.1632 | 1.9946 | 2.4612 | 2.4612 | 2.7723 | 2.7723 | 2020-02-02 20:00 | 1.9958 | 3.2707 | 5.3688 | 5.3688 | 5.3688 | 5.3688
2021-12-06 08:00 | 2.292 | 2.7892 | 2.729 | 2.9353 | 2.7806 | 2.9868 | 1.3032 | 2.2348 | 2.7576 | 2.7576 | 3.1061 | 3.1061 | 2020-02-02 21:00 | 1.9834 | 3.2504 | 5.3355 | 5.3355 | 5.3355 | 5.3355
2021-12-06 09:00 | 2.1634 | 2.6327 | 2.5759 | 2.7706 | 2.6245 | 2.8192 | 1.2784 | 2.1922 | 2.705 | 2.705 | 3.0469 | 3.0469 | 2020-02-02 22:00 | 1.8224 | 2.9865 | 4.9024 | 4.9024 | 4.9024 | 4.9024
2021-12-06 10:00 | 2.0577 | 2.504 | 2.45 | 2.6352 | 2.4963 | 2.6814 | 1.3375 | 2.2936 | 2.8301 | 2.8301 | 3.1878 | 3.1878 | 2020-02-02 23:00 | 1.729 | 2.8335 | 4.6513 | 4.6513 | 4.6513 | 4.6513
2021-12-06 11:00 | 2.1291 | 2.5909 | 2.535 | 2.7266 | 2.5829 | 2.7746 | 1.3489 | 2.3132 | 2.8543 | 2.8543 | 3.2151 | 3.2151 | 2020-02-03 | 1.5671 | 2.5681 | 4.2156 | 4.2156 | 4.2156 | 4.2156
2021-12-06 12:00 | 1.9519 | 2.3753 | 2.3241 | 2.4997 | 2.368 | 2.5437 | 1.3603 | 2.3328 | 2.8785 | 2.8785 | 3.2423 | 3.2423 | 2020-02-03 01:00 | 1.4709 | 2.4105 | 3.9568 | 3.9568 | 3.9568 | 3.9568
2021-12-06 13:00 | 2.1606 | 2.6292 | 2.5725 | 2.7669 | 2.6211 | 2.8155 | 1.4032 | 2.4063 | 2.9692 | 2.9692 | 3.3445 | 3.3445 | 2020-02-03 02:00 | 1.4528 | 2.3808 | 3.9081 | 3.9081 | 3.9081 | 3.9081
2021-12-06 14:00 | 2.0691 | 2.5179 | 2.4636 | 2.6498 | 2.5101 | 2.6963 | 1.3804 | 2.3671 | 2.9208 | 2.9208 | 3.29 | 3.29 | 2020-02-03 03:00 | 1.3461 | 2.2059 | 3.6211 | 3.6211 | 3.6211 | 3.6211
2021-12-06 15:00 | 2.0959 | 2.5505 | 2.4955 | 2.6841 | 2.5426 | 2.7313 | 1.3346 | 2.2887 | 2.8241 | 2.8241 | 3.181 | 3.181 | 2020-02-03 04:00 | 1.3927 | 2.2824 | 3.7467 | 3.7467 | 3.7467 | 3.7467
2021-12-06 16:00 | 2.1406 | 2.6048 | 2.5486 | 2.7413 | 2.5968 | 2.7895 | 1.4061 | 2.4112 | 2.9753 | 2.9753 | 3.3513 | 3.3513 | 2020-02-03 05:00 | 1.4642 | 2.3995 | 3.9389 | 3.9389 | 3.9389 | 3.9389
2021-12-06 17:00 | 2.1177 | 2.577 | 2.5214 | 2.712 | 2.5691 | 2.7597 | 1.4918 | 2.5582 | 3.1567 | 3.1567 | 3.5557 | 3.5557 | 2020-02-03 06:00 | 1.8767 | 3.0755 | 5.0485 | 5.0485 | 5.0485 | 5.0485
2021-12-06 18:00 | 2.252 | 2.7405 | 2.6813 | 2.884 | 2.732 | 2.9347 | 1.5518 | 2.6611 | 3.2837 | 3.2837 | 3.6987 | 3.6987 | 2020-02-03 07:00 | 2.2168 | 3.6329 | 5.9634 | 5.9634 | 5.9634 | 5.9634
2021-12-06 19:00 | 2.1691 | 2.6396 | 2.5827 | 2.7779 | 2.6315 | 2.8267 | 1.569 | 2.6905 | 3.32 | 3.32 | 3.7396 | 3.7396 | 2020-02-03 08:00 | 2.3149 | 3.7937 | 6.2273 | 6.2273 | 6.2273 | 6.2273
2021-12-06 20:00 | 2.2777 | 2.7718 | 2.712 | 2.917 | 2.7632 | 2.9682 | 1.6061 | 2.7543 | 3.3986 | 3.3986 | 3.8281 | 3.8281 | 2020-02-03 09:00 | 2.4321 | 3.9857 | 6.5426 | 6.5426 | 6.5426 | 6.5426
2021-12-06 21:00 | 2.1548 | 2.6222 | 2.5657 | 2.7596 | 2.6141 | 2.8081 | 1.5775 | 2.7052 | 3.3381 | 3.3381 | 3.76 | 3.76 | 2020-02-03 10:00 | 2.4063 | 3.9435 | 6.4734 | 6.4734 | 6.4734 | 6.4734
2021-12-06 22:00 | 1.95 | 2.373 | 2.3218 | 2.4973 | 2.3657 | 2.5412 | 1.2432 | 2.1318 | 2.6306 | 2.6306 | 2.9631 | 2.9631 | 2020-02-03 11:00 | 2.5064 | 4.1075 | 6.7424 | 6.7424 | 6.7424 | 6.7424
2021-12-06 23:00 | 1.6433 | 1.9997 | 1.9566 | 2.1045 | 1.9935 | 2.1414 | 1.0574 | 1.8133 | 2.2375 | 2.2375 | 2.5203 | 2.5203 | 2020-02-03 12:00 | 2.4968 | 4.0918 | 6.7168 | 6.7168 | 6.7168 | 6.7168
2021-12-07 | 1.5775 | 1.9197 | 1.8783 | 2.0203 | 1.9138 | 2.0558 | 0.95458 | 1.6369 | 2.0199 | 2.0199 | 2.2752 | 2.2752 | 2020-02-03 13:00 | 2.4254 | 3.9748 | 6.5246 | 6.5246 | 6.5246 | 6.5246
2021-12-07 01:00 | 1.4432 | 1.7563 | 1.7184 | 1.8483 | 1.7508 | 1.8807 | 0.83164 | 1.4261 | 1.7598 | 1.7598 | 1.9822 | 1.9822 | 2020-02-03 14:00 | 2.4892 | 4.0794 | 6.6963 | 6.6963 | 6.6963 | 6.6963
2021-12-07 02:00 | 1.3975 | 1.7006 | 1.6639 | 1.7897 | 1.6954 | 1.8211 | 0.70589 | 1.2105 | 1.4937 | 1.4937 | 1.6825 | 1.6825 | 2020-02-03 15:00 | 2.4473 | 4.0107 | 6.5836 | 6.5836 | 6.5836 | 6.5836
2021-12-07 03:00 | 1.3346 | 1.6241 | 1.5891 | 1.7092 | 1.6191 | 1.7392 | 0.69771 | 1.1965 | 1.4764 | 1.4764 | 1.663 | 1.663 | 2020-02-03 16:00 | 2.4702 | 4.0481 | 6.6451 | 6.6451 | 6.6451 | 6.6451
2021-12-07 04:00 | 1.4061 | 1.711 | 1.6741 | 1.8007 | 1.7058 | 1.8323 | 0.71447 | 1.2252 | 1.5118 | 1.5118 | 1.7029 | 1.7029 | 2020-02-03 17:00 | 2.4187 | 3.9638 | 6.5067 | 6.5067 | 6.5067 | 6.5067
2021-12-07 05:00 | 1.5108 | 1.8385 | 1.7988 | 1.9348 | 1.8328 | 1.9688 | 0.70304 | 1.2056 | 1.4876 | 1.4876 | 1.6757 | 1.6757 | 2020-02-03 18:00 | 2.2291 | 3.6532 | 5.9967 | 5.9967 | 5.9967 | 5.9967
2021-12-07 06:00 | 1.8462 | 2.2466 | 2.1982 | 2.3643 | 2.2397 | 2.4059 | 0.94024 | 1.6124 | 1.9896 | 1.9896 | 2.241 | 2.241 | 2020-02-03 19:00 | 1.9634 | 3.2176 | 5.2817 | 5.2817 | 5.2817 | 5.2817
2021-12-07 07:00 | 2.1177 | 2.577 | 2.5214 | 2.712 | 2.5691 | 2.7597 | 1.1632 | 1.9946 | 2.4612 | 2.4612 | 2.7723 | 2.7723 | 2020-02-03 20:00 | 1.8586 | 3.0459 | 4.9998 | 4.9998 | 4.9998 | 4.9998
2021-12-07 08:00 | 2.1463 | 2.6118 | 2.5554 | 2.7486 | 2.6037 | 2.7969 | 1.22 | 2.0921 | 2.5815 | 2.5815 | 2.9078 | 2.9078 | 2020-02-03 21:00 | 1.8481 | 3.0287 | 4.9716 | 4.9716 | 4.9716 | 4.9716
2021-12-07 09:00 | 2.1748 | 2.6466 | 2.5895 | 2.7852 | 2.6384 | 2.8341 | 1.3089 | 2.2446 | 2.7697 | 2.7697 | 3.1197 | 3.1197 | 2020-02-03 22:00 | 1.7166 | 2.8132 | 4.618 | 4.618 | 4.618 | 4.618
2021-12-07 10:00 | 2.1005 | 2.5561 | 2.501 | 2.69 | 2.5483 | 2.7373 | 1.3318 | 2.2838 | 2.818 | 2.818 | 3.1742 | 3.1742 | 2020-02-03 23:00 | 1.5928 | 2.6103 | 4.2848 | 4.2848 | 4.2848 | 4.2848
2021-12-07 11:00 | 2.0234 | 2.4622 | 2.4091 | 2.5912 | 2.4547 | 2.6368 | 1.3518 | 2.3181 | 2.8604 | 2.8604 | 3.2219 | 3.2219 | 2020-02-04 | 1.4156 | 2.3199 | 3.8082 | 3.8082 | 3.8082 | 3.8082
2021-12-07 12:00 | 2.1691 | 2.6396 | 2.5827 | 2.7779 | 2.6315 | 2.8267 | 1.3403 | 2.2985 | 2.8362 | 2.8362 | 3.1947 | 3.1947 | 2020-02-04 01:00 | 1.4004 | 2.2949 | 3.7672 | 3.7672 | 3.7672 | 3.7672
2021-12-07 13:00 | 2.1691 | 2.6396 | 2.5827 | 2.7779 | 2.6315 | 2.8267 | 1.3203 | 2.2642 | 2.7939 | 2.7939 | 3.147 | 3.147 | 2020-02-04 02:00 | 1.2975 | 2.1263 | 3.4904 | 3.4904 | 3.4904 | 3.4904
2021-12-07 14:00 | 2.2634 | 2.7544 | 2.695 | 2.8987 | 2.7459 | 2.9496 | 1.3375 | 2.2936 | 2.8301 | 2.8301 | 3.1878 | 3.1878 | 2020-02-04 03:00 | 1.2879 | 2.1107 | 3.4648 | 3.4648 | 3.4648 | 3.4648
2021-12-07 15:00 | 2.1949 | 2.6709 | 2.6133 | 2.8108 | 2.6627 | 2.8602 | 1.3175 | 2.2593 | 2.7878 | 2.7878 | 3.1402 | 3.1402 | 2020-02-04 04:00 | 1.2841 | 2.1045 | 3.4545 | 3.4545 | 3.4545 | 3.4545
2021-12-07 16:00 | 2.0034 | 2.4379 | 2.3853 | 2.5656 | 2.4304 | 2.6107 | 1.4141 | 2.425 | 2.9923 | 2.9923 | 3.3705 | 3.3705 | 2020-02-04 05:00 | 1.4137 | 2.3168 | 3.803 | 3.803 | 3.803 | 3.803
2021-12-07 17:00 | 2.1663 | 2.6361 | 2.5793 | 2.7742 | 2.628 | 2.823 | 1.5147 | 2.5974 | 3.2051 | 3.2051 | 3.6102 | 3.6102 | 2020-02-04 06:00 | 1.5709 | 2.5744 | 4.2259 | 4.2259 | 4.2259 | 4.2259
2021-12-07 18:00 | 2.3063 | 2.8065 | 2.746 | 2.9536 | 2.7979 | 3.0055 | 1.6061 | 2.7543 | 3.3986 | 3.3986 | 3.8281 | 3.8281 | 2020-02-04 07:00 | 1.8148 | 2.974 | 4.8819 | 4.8819 | 4.8819 | 4.8819
2021-12-07 19:00 | 2.1949 | 2.6709 | 2.6133 | 2.8108 | 2.6627 | 2.8602 | 1.6004 | 2.7445 | 3.3865 | 3.3865 | 3.8145 | 3.8145 | 2020-02-04 08:00 | 2.2539 | 3.6937 | 6.0633 | 6.0633 | 6.0633 | 6.0633
2021-12-07 20:00 | 2.0748 | 2.5248 | 2.4704 | 2.6571 | 2.5171 | 2.7038 | 1.6261 | 2.7886 | 3.4409 | 3.4409 | 3.8758 | 3.8758 | 2020-02-04 09:00 | 2.1024 | 3.4455 | 5.6559 | 5.6559 | 5.6559 | 5.6559
2021-12-07 21:00 | 1.9576 | 2.3823 | 2.3309 | 2.5071 | 2.3749 | 2.5511 | 1.5861 | 2.7199 | 3.3563 | 3.3563 | 3.7805 | 3.7805 | 2020-02-04 10:00 | 2.1796 | 3.572 | 5.8634 | 5.8634 | 5.8634 | 5.8634
2021-12-07 22:00 | 1.8448 | 2.2449 | 2.1965 | 2.3625 | 2.238 | 2.404 | 1.3704 | 2.35 | 2.8997 | 2.8997 | 3.2662 | 3.2662 | 2020-02-04 11:00 | 2.2149 | 3.6297 | 5.9583 | 5.9583 | 5.9583 | 5.9583
2021-12-07 23:00 | 1.6204 | 1.9719 | 1.9293 | 2.0752 | 1.9658 | 2.1116 | 1.0088 | 1.73 | 2.1347 | 2.1347 | 2.4045 | 2.4045 | 2020-02-04 12:00 | 2.2472 | 3.6828 | 6.0454 | 6.0454 | 6.0454 | 6.0454
2021-12-08 | 1.4749 | 1.7948 | 1.7561 | 1.8888 | 1.7892 | 1.922 | 0.92309 | 1.583 | 1.9533 | 1.9533 | 2.2002 | 2.2002 | 2020-02-04 13:00 | 2.2396 | 3.6703 | 6.0249 | 6.0249 | 6.0249 | 6.0249
2021-12-08 01:00 | 1.3775 | 1.6763 | 1.6401 | 1.7641 | 1.6711 | 1.7951 | 0.81164 | 1.3918 | 1.7174 | 1.7174 | 1.9345 | 1.9345 | 2020-02-04 14:00 | 2.2749 | 3.7281 | 6.1197 | 6.1197 | 6.1197 | 6.1197
2021-12-08 02:00 | 1.3003 | 1.5824 | 1.5482 | 1.6653 | 1.5775 | 1.6945 | 0.73447 | 1.2595 | 1.5542 | 1.5542 | 1.7506 | 1.7506 | 2020-02-04 15:00 | 2.3406 | 3.8358 | 6.2965 | 6.2965 | 6.2965 | 6.2965
2021-12-08 03:00 | 1.3003 | 1.5824 | 1.5482 | 1.6653 | 1.5775 | 1.6945 | 0.68875 | 1.1811 | 1.4574 | 1.4574 | 1.6416 | 1.6416 | 2020-02-04 16:00 | 2.233 | 3.6594 | 6.007 | 6.007 | 6.007 | 6.007
2021-12-08 04:00 | 1.2889 | 1.5685 | 1.5346 | 1.6506 | 1.5636 | 1.6796 | 0.65799 | 1.1284 | 1.3923 | 1.3923 | 1.5683 | 1.5683 | 2020-02-04 17:00 | 2.1939 | 3.5954 | 5.9019 | 5.9019 | 5.9019 | 5.9019
2021-12-08 05:00 | 1.3784 | 1.6774 | 1.6412 | 1.7653 | 1.6722 | 1.7963 | 0.73733 | 1.2644 | 1.5602 | 1.5602 | 1.7574 | 1.7574 | 2020-02-04 18:00 | 2.0453 | 3.3518 | 5.5021 | 5.5021 | 5.5021 | 5.5021
2021-12-08 06:00 | 1.7976 | 2.1875 | 2.1403 | 2.3021 | 2.1808 | 2.3425 | 0.86022 | 1.4751 | 1.8202 | 1.8202 | 2.0503 | 2.0503 | 2020-02-04 19:00 | 1.9529 | 3.2004 | 5.2535 | 5.2535 | 5.2535 | 5.2535
2021-12-08 07:00 | 2.1777 | 2.65 | 2.5929 | 2.7889 | 2.6419 | 2.8379 | 1.2003 | 2.0583 | 2.5399 | 2.5399 | 2.8609 | 2.8609 | 2020-02-04 20:00 | 1.8776 | 3.0771 | 5.0511 | 5.0511 | 5.0511 | 5.0511
2021-12-08 08:00 | 2.2634 | 2.7544 | 2.695 | 2.8987 | 2.7459 | 2.9496 | 1.3175 | 2.2593 | 2.7878 | 2.7878 | 3.1402 | 3.1402 | 2020-02-04 21:00 | 1.7719 | 2.9038 | 4.7666 | 4.7666 | 4.7666 | 4.7666
2021-12-08 09:00 | 2.2606 | 2.7509 | 2.6916 | 2.895 | 2.7424 | 2.9459 | 1.2946 | 2.2201 | 2.7394 | 2.7394 | 3.0857 | 3.0857 | 2020-02-04 22:00 | 1.5795 | 2.5884 | 4.2489 | 4.2489 | 4.2489 | 4.2489
2021-12-08 10:00 | 2.2206 | 2.7022 | 2.6439 | 2.8438 | 2.6939 | 2.8937 | 1.3261 | 2.274 | 2.8059 | 2.8059 | 3.1606 | 3.1606 | 2020-02-04 23:00 | 1.5185 | 2.4885 | 4.0849 | 4.0849 | 4.0849 | 4.0849
2021-12-08 11:00 | 2.1548 | 2.6222 | 2.5657 | 2.7596 | 2.6141 | 2.8081 | 1.3403 | 2.2985 | 2.8362 | 2.8362 | 3.1947 | 3.1947 | 2020-02-05 | 1.3689 | 2.2434 | 3.6826 | 3.6826 | 3.6826 | 3.6826
2021-12-08 12:00 | 2.3978 | 2.9178 | 2.8549 | 3.0707 | 2.9088 | 3.1246 | 1.4118 | 2.421 | 2.9874 | 2.9874 | 3.3649 | 3.3649 | 2020-02-05 01:00 | 1.2813 | 2.0998 | 3.4468 | 3.4468 | 3.4468 | 3.4468
2021-12-08 13:00 | 2.1434 | 2.6083 | 2.552 | 2.7449 | 2.6003 | 2.7932 | 1.3775 | 2.3622 | 2.9148 | 2.9148 | 3.2832 | 3.2832 | 2020-02-05 02:00 | 1.3165 | 2.1575 | 3.5416 | 3.5416 | 3.5416 | 3.5416
2021-12-08 14:00 | 2.1406 | 2.6048 | 2.5486 | 2.7413 | 2.5968 | 2.7895 | 1.3661 | 2.3426 | 2.8906 | 2.8906 | 3.256 | 3.256 | 2020-02-05 03:00 | 1.2775 | 2.0935 | 3.4366 | 3.4366 | 3.4366 | 3.4366
2021-12-08 15:00 | 2.0242 | 2.4633 | 2.4102 | 2.5923 | 2.4557 | 2.6379 | 1.3518 | 2.3181 | 2.8604 | 2.8604 | 3.2219 | 3.2219 | 2020-02-05 04:00 | 1.2927 | 2.1185 | 3.4776 | 3.4776 | 3.4776 | 3.4776
2021-12-08 16:00 | 2.1034 | 2.5596 | 2.5044 | 2.6937 | 2.5517 | 2.741 | 1.3089 | 2.2446 | 2.7697 | 2.7697 | 3.1197 | 3.1197 | 2020-02-05 05:00 | 1.3632 | 2.234 | 3.6672 | 3.6672 | 3.6672 | 3.6672
2021-12-08 17:00 | 2.1377 | 2.6014 | 2.5452 | 2.7376 | 2.5933 | 2.7857 | 1.4373 | 2.4647 | 3.0413 | 3.0413 | 3.4257 | 3.4257 | 2020-02-05 06:00 | 1.5156 | 2.4838 | 4.0772 | 4.0772 | 4.0772 | 4.0772
2021-12-08 18:00 | 2.2577 | 2.7474 | 2.6882 | 2.8913 | 2.739 | 2.9421 | 1.6233 | 2.7837 | 3.4349 | 3.4349 | 3.869 | 3.869 | 2020-02-05 07:00 | 1.8586 | 3.0459 | 4.9998 | 4.9998 | 4.9998 | 4.9998
2021-12-08 19:00 | 2.1222 | 2.5825 | 2.5268 | 2.7178 | 2.5745 | 2.7655 | 1.5804 | 2.7101 | 3.3442 | 3.3442 | 3.7668 | 3.7668 | 2020-02-05 08:00 | 2.1044 | 3.4486 | 5.661 | 5.661 | 5.661 | 5.661
2021-12-08 20:00 | 2.1406 | 2.6048 | 2.5486 | 2.7413 | 2.5968 | 2.7895 | 1.6233 | 2.7837 | 3.4349 | 3.4349 | 3.869 | 3.869 | 2020-02-05 09:00 | 2.2025 | 3.6094 | 5.9249 | 5.9249 | 5.9249 | 5.9249
2021-12-08 21:00 | 2.0662 | 2.5144 | 2.4602 | 2.6461 | 2.5067 | 2.6926 | 1.5804 | 2.7101 | 3.3442 | 3.3442 | 3.7668 | 3.7668 | 2020-02-05 10:00 | 2.0872 | 3.4205 | 5.6149 | 5.6149 | 5.6149 | 5.6149
2021-12-08 22:00 | 1.867 | 2.2719 | 2.2229 | 2.391 | 2.2649 | 2.433 | 1.3097 | 2.2459 | 2.7714 | 2.7714 | 3.1216 | 3.1216 | 2020-02-05 11:00 | 2.1548 | 3.5314 | 5.7968 | 5.7968 | 5.7968 | 5.7968
2021-12-08 23:00 | 1.6404 | 1.9962 | 1.9532 | 2.1008 | 1.9901 | 2.1377 | 1.1089 | 1.9015 | 2.3464 | 2.3464 | 2.6429 | 2.6429 | 2020-02-05 12:00 | 2.1977 | 3.6016 | 5.9121 | 5.9121 | 5.9121 | 5.9121
2021-12-09 | 1.5375 | 1.871 | 1.8307 | 1.969 | 1.8653 | 2.0036 | 0.98071 | 1.6818 | 2.0752 | 2.0752 | 2.3375 | 2.3375 | 2020-02-05 13:00 | 2.3149 | 3.7937 | 6.2273 | 6.2273 | 6.2273 | 6.2273
2021-12-09 01:00 | 1.4547 | 1.7702 | 1.732 | 1.8629 | 1.7647 | 1.8956 | 0.76762 | 1.3163 | 1.6243 | 1.6243 | 1.8296 | 1.8296 | 2020-02-05 14:00 | 2.392 | 3.9201 | 6.4349 | 6.4349 | 6.4349 | 6.4349
2021-12-09 02:00 | 1.3489 | 1.6415 | 1.6061 | 1.7275 | 1.6364 | 1.7578 | 0.76305 | 1.3085 | 1.6146 | 1.6146 | 1.8187 | 1.8187 | 2020-02-05 15:00 | 2.3759 | 3.8936 | 6.3914 | 6.3914 | 6.3914 | 6.3914
2021-12-09 03:00 | 1.3432 | 1.6345 | 1.5993 | 1.7202 | 1.6295 | 1.7504 | 0.70875 | 1.2154 | 1.4997 | 1.4997 | 1.6893 | 1.6893 | 2020-02-05 16:00 | 2.2587 | 3.7016 | 6.0761 | 6.0761 | 6.0761 | 6.0761
2021-12-09 04:00 | 1.3775 | 1.6763 | 1.6401 | 1.7641 | 1.6711 | 1.7951 | 0.70945 | 1.2166 | 1.5012 | 1.5012 | 1.6909 | 1.6909 | 2020-02-05 17:00 | 2.3092 | 3.7843 | 6.212 | 6.212 | 6.212 | 6.212
2021-12-09 05:00 | 1.5059 | 1.8326 | 1.793 | 1.9286 | 1.8269 | 1.9624 | 0.74305 | 1.2742 | 1.5723 | 1.5723 | 1.771 | 1.771 | 2020-02-05 18:00 | 1.9777 | 3.241 | 5.3202 | 5.3202 | 5.3202 | 5.3202
2021-12-09 06:00 | 1.8891 | 2.2988 | 2.2492 | 2.4192 | 2.2917 | 2.4617 | 0.84593 | 1.4506 | 1.79 | 1.79 | 2.0162 | 2.0162 | 2020-02-05 19:00 | 1.8957 | 3.1067 | 5.0998 | 5.0998 | 5.0998 | 5.0998
2021-12-09 07:00 | 2.232 | 2.7161 | 2.6575 | 2.8584 | 2.7077 | 2.9086 | 1.2117 | 2.0779 | 2.5641 | 2.5641 | 2.8881 | 2.8881 | 2020-02-05 20:00 | 1.8576 | 3.0443 | 4.9973 | 4.9973 | 4.9973 | 4.9973
2021-12-09 08:00 | 2.352 | 2.8622 | 2.8004 | 3.0121 | 2.8534 | 3.065 | 1.2803 | 2.1956 | 2.7092 | 2.7092 | 3.0516 | 3.0516 | 2020-02-05 21:00 | 1.7471 | 2.8632 | 4.7 | 4.7 | 4.7 | 4.7
2021-12-09 09:00 | 2.2892 | 2.7857 | 2.7256 | 2.9316 | 2.7771 | 2.9831 | 1.3261 | 2.274 | 2.8059 | 2.8059 | 3.1606 | 3.1606 | 2020-02-05 22:00 | 1.5709 | 2.5744 | 4.2259 | 4.2259 | 4.2259 | 4.2259
2021-12-09 10:00 | 2.1577 | 2.6257 | 2.5691 | 2.7632 | 2.6176 | 2.8118 | 1.4004 | 2.4014 | 2.9632 | 2.9632 | 3.3377 | 3.3377 | 2020-02-05 23:00 | 1.5213 | 2.4932 | 4.0926 | 4.0926 | 4.0926 | 4.0926
2021-12-09 11:00 | 2.032 | 2.4727 | 2.4193 | 2.6022 | 2.4651 | 2.6479 | 1.3461 | 2.3083 | 2.8483 | 2.8483 | 3.2083 | 3.2083 | 2020-02-06 | 1.3575 | 2.2247 | 3.6518 | 3.6518 | 3.6518 | 3.6518
2021-12-09 12:00 | 2.2549 | 2.7439 | 2.6848 | 2.8877 | 2.7355 | 2.9384 | 1.4204 | 2.4357 | 3.0055 | 3.0055 | 3.3854 | 3.3854 | 2020-02-06 01:00 | 1.3137 | 2.1529 | 3.534 | 3.534 | 3.534 | 3.534
2021-12-09 13:00 | 2.1663 | 2.6361 | 2.5793 | 2.7742 | 2.628 | 2.823 | 1.3939 | 2.3903 | 2.9495 | 2.9495 | 3.3223 | 3.3223 | 2020-02-06 02:00 | 1.2641 | 2.0717 | 3.4007 | 3.4007 | 3.4007 | 3.4007
2021-12-09 14:00 | 1.8519 | 2.2536 | 2.205 | 2.3716 | 2.2466 | 2.4133 | 1.3118 | 2.2495 | 2.7757 | 2.7757 | 3.1265 | 3.1265 | 2020-02-06 03:00 | 1.2937 | 2.1201 | 3.4801 | 3.4801 | 3.4801 | 3.4801
2021-12-09 15:00 | 2.1949 | 2.6709 | 2.6133 | 2.8108 | 2.6627 | 2.8602 | 1.3603 | 2.3328 | 2.8785 | 2.8785 | 3.2423 | 3.2423 | 2020-02-06 04:00 | 1.308 | 2.1435 | 3.5186 | 3.5186 | 3.5186 | 3.5186
2021-12-09 16:00 | 2.232 | 2.7161 | 2.6575 | 2.8584 | 2.7077 | 2.9086 | 1.4432 | 2.4749 | 3.0539 | 3.0539 | 3.4399 | 3.4399 | 2020-02-06 05:00 | 1.3413 | 2.1981 | 3.6083 | 3.6083 | 3.6083 | 3.6083
2021-12-09 17:00 | 2.2688 | 2.7609 | 2.7014 | 2.9056 | 2.7524 | 2.9566 | 1.609 | 2.7592 | 3.4046 | 3.4046 | 3.8349 | 3.8349 | 2020-02-06 06:00 | 1.5071 | 2.4698 | 4.0542 | 4.0542 | 4.0542 | 4.0542
2021-12-09 18:00 | 2.4235 | 2.9491 | 2.8855 | 3.1036 | 2.94 | 3.1582 | 1.6376 | 2.8082 | 3.4651 | 3.4651 | 3.9031 | 3.9031 | 2020-02-06 07:00 | 1.9719 | 3.2316 | 5.3048 | 5.3048 | 5.3048 | 5.3048
2021-12-09 19:00 | 2.2898 | 2.7864 | 2.7263 | 2.9324 | 2.7778 | 2.9839 | 1.709 | 2.9307 | 3.6163 | 3.6163 | 4.0734 | 4.0734 | 2020-02-06 08:00 | 2.2225 | 3.6422 | 5.9788 | 5.9788 | 5.9788 | 5.9788
2021-12-09 20:00 | 2.2091 | 2.6883 | 2.6303 | 2.8291 | 2.68 | 2.8788 | 1.6833 | 2.8866 | 3.5619 | 3.5619 | 4.0121 | 4.0121 | 2020-02-06 09:00 | 2.1625 | 3.5439 | 5.8173 | 5.8173 | 5.8173 | 5.8173
2021-12-09 21:00 | 2.092 | 2.5457 | 2.4908 | 2.6791 | 2.5379 | 2.7261 | 1.6318 | 2.7984 | 3.453 | 3.453 | 3.8894 | 3.8894 | 2020-02-06 10:00 | 2.2644 | 3.7109 | 6.0915 | 6.0915 | 6.0915 | 6.0915
2021-12-09 22:00 | 1.8862 | 2.2953 | 2.2458 | 2.4156 | 2.2882 | 2.458 | 1.3375 | 2.2936 | 2.8301 | 2.8301 | 3.1878 | 3.1878 | 2020-02-06 11:00 | 2.2358 | 3.6641 | 6.0146 | 6.0146 | 6.0146 | 6.0146
2021-12-09 23:00 | 1.7176 | 2.0901 | 2.045 | 2.1996 | 2.0837 | 2.2383 | 1.0804 | 1.8527 | 2.2861 | 2.2861 | 2.5751 | 2.5751 | 2020-02-06 12:00 | 2.3225 | 3.8061 | 6.2478 | 6.2478 | 6.2478 | 6.2478
2021-12-10 | 1.661 | 2.0213 | 1.9777 | 2.1272 | 2.0151 | 2.1646 | 0.95453 | 1.6369 | 2.0198 | 2.0198 | 2.2751 | 2.2751 | 2020-02-06 13:00 | 2.2682 | 3.7172 | 6.1018 | 6.1018 | 6.1018 | 6.1018
2021-12-10 01:00 | 1.498 | 1.8229 | 1.7836 | 1.9184 | 1.8173 | 1.9521 | 0.78885 | 1.3527 | 1.6692 | 1.6692 | 1.8802 | 1.8802 | 2020-02-06 14:00 | 2.293 | 3.7578 | 6.1684 | 6.1684 | 6.1684 | 6.1684
2021-12-10 02:00 | 1.4347 | 1.7458 | 1.7082 | 1.8373 | 1.7404 | 1.8696 | 0.8002 | 1.3722 | 1.6932 | 1.6932 | 1.9073 | 1.9073 | 2020-02-06 15:00 | 2.3168 | 3.7968 | 6.2325 | 6.2325 | 6.2325 | 6.2325
2021-12-10 03:00 | 1.3861 | 1.6867 | 1.6503 | 1.7751 | 1.6815 | 1.8063 | 0.67736 | 1.1616 | 1.4333 | 1.4333 | 1.6145 | 1.6145 | 2020-02-06 16:00 | 2.3406 | 3.8358 | 6.2965 | 6.2965 | 6.2965 | 6.2965
2021-12-10 04:00 | 1.4518 | 1.7667 | 1.7286 | 1.8592 | 1.7612 | 1.8919 | 0.68017 | 1.1664 | 1.4393 | 1.4393 | 1.6212 | 1.6212 | 2020-02-06 17:00 | 2.2263 | 3.6485 | 5.989 | 5.989 | 5.989 | 5.989
2021-12-10 05:00 | 1.5631 | 1.9021 | 1.8611 | 2.0017 | 1.8962 | 2.0369 | 0.74019 | 1.2693 | 1.5662 | 1.5662 | 1.7642 | 1.7642 | 2020-02-06 18:00 | 2.0996 | 3.4408 | 5.6482 | 5.6482 | 5.6482 | 5.6482
2021-12-10 06:00 | 1.9719 | 2.3996 | 2.3479 | 2.5254 | 2.3922 | 2.5697 | 0.93452 | 1.6026 | 1.9775 | 1.9775 | 2.2274 | 2.2274 | 2020-02-06 19:00 | 1.8538 | 3.038 | 4.987 | 4.987 | 4.987 | 4.987
2021-12-10 07:00 | 2.4206 | 2.9456 | 2.8821 | 3.1 | 2.9366 | 3.1544 | 1.2889 | 2.2103 | 2.7273 | 2.7273 | 3.072 | 3.072 | 2020-02-06 20:00 | 1.8262 | 2.9928 | 4.9127 | 4.9127 | 4.9127 | 4.9127
2021-12-10 08:00 | 2.5778 | 3.1369 | 3.0693 | 3.3013 | 3.1273 | 3.3593 | 1.3518 | 2.3181 | 2.8604 | 2.8604 | 3.2219 | 3.2219 | 2020-02-06 21:00 | 1.8014 | 2.9522 | 4.8461 | 4.8461 | 4.8461 | 4.8461
2021-12-10 09:00 | 2.5721 | 3.13 | 3.0625 | 3.2939 | 3.1203 | 3.3518 | 1.3632 | 2.3377 | 2.8846 | 2.8846 | 3.2491 | 3.2491 | 2020-02-06 22:00 | 1.6976 | 2.782 | 4.5667 | 4.5667 | 4.5667 | 4.5667
2021-12-10 10:00 | 2.7321 | 3.3247 | 3.253 | 3.4989 | 3.3145 | 3.5604 | 1.5404 | 2.6415 | 3.2595 | 3.2595 | 3.6715 | 3.6715 | 2020-02-06 23:00 | 1.6204 | 2.6556 | 4.3591 | 4.3591 | 4.3591 | 4.3591
2021-12-10 11:00 | 2.6864 | 3.2691 | 3.1986 | 3.4403 | 3.259 | 3.5008 | 1.5461 | 2.6513 | 3.2716 | 3.2716 | 3.6851 | 3.6851 | 2020-02-07 | 1.4337 | 2.3496 | 3.8569 | 3.8569 | 3.8569 | 3.8569
2021-12-10 12:00 | 2.6693 | 3.2482 | 3.1781 | 3.4184 | 3.2382 | 3.4784 | 1.6061 | 2.7543 | 3.3986 | 3.3986 | 3.8281 | 3.8281 | 2020-02-07 01:00 | 1.4051 | 2.3027 | 3.78 | 3.78 | 3.78 | 3.78
2021-12-10 13:00 | 2.635 | 3.2065 | 3.1373 | 3.3745 | 3.1966 | 3.4337 | 1.6118 | 2.7641 | 3.4107 | 3.4107 | 3.8418 | 3.8418 | 2020-02-07 02:00 | 1.3661 | 2.2387 | 3.6749 | 3.6749 | 3.6749 | 3.6749
2021-12-10 14:00 | 2.4864 | 3.0256 | 2.9604 | 3.1841 | 3.0163 | 3.2401 | 1.5518 | 2.6611 | 3.2837 | 3.2837 | 3.6987 | 3.6987 | 2020-02-07 03:00 | 1.3489 | 2.2106 | 3.6288 | 3.6288 | 3.6288 | 3.6288
2021-12-10 15:00 | 2.312 | 2.8135 | 2.7528 | 2.9609 | 2.8048 | 3.0129 | 1.509 | 2.5876 | 3.193 | 3.193 | 3.5965 | 3.5965 | 2020-02-07 04:00 | 1.3537 | 2.2184 | 3.6416 | 3.6416 | 3.6416 | 3.6416
2021-12-10 16:00 | 2.3492 | 2.8587 | 2.797 | 3.0085 | 2.8499 | 3.0613 | 1.521 | 2.6082 | 3.2184 | 3.2184 | 3.6252 | 3.6252 | 2020-02-07 05:00 | 1.4699 | 2.4089 | 3.9542 | 3.9542 | 3.9542 | 3.9542
2021-12-10 17:00 | 2.4063 | 2.9283 | 2.8651 | 3.0817 | 2.9192 | 3.1358 | 1.6804 | 2.8817 | 3.5558 | 3.5558 | 4.0052 | 4.0052 | 2020-02-07 06:00 | 1.5918 | 2.6087 | 4.2823 | 4.2823 | 4.2823 | 4.2823
2021-12-10 18:00 | 2.3692 | 2.8831 | 2.8209 | 3.0341 | 2.8742 | 3.0874 | 1.7462 | 2.9944 | 3.6949 | 3.6949 | 4.1619 | 4.1619 | 2020-02-07 07:00 | 2.0348 | 3.3347 | 5.4739 | 5.4739 | 5.4739 | 5.4739
2021-12-10 19:00 | 2.2918 | 2.7889 | 2.7287 | 2.935 | 2.7803 | 2.9865 | 1.7633 | 3.0238 | 3.7312 | 3.7312 | 4.2028 | 4.2028 | 2020-02-07 08:00 | 2.1987 | 3.6032 | 5.9147 | 5.9147 | 5.9147 | 5.9147
2021-12-10 20:00 | 2.2434 | 2.73 | 2.6711 | 2.873 | 2.7216 | 2.9235 | 1.8319 | 3.1414 | 3.8763 | 3.8763 | 4.3663 | 4.3663 | 2020-02-07 09:00 | 2.1968 | 3.6001 | 5.9096 | 5.9096 | 5.9096 | 5.9096
2021-12-10 21:00 | 2.1977 | 2.6744 | 2.6167 | 2.8145 | 2.6661 | 2.8639 | 1.6547 | 2.8376 | 3.5014 | 3.5014 | 3.9439 | 3.9439 | 2020-02-07 10:00 | 2.2406 | 3.6719 | 6.0275 | 6.0275 | 6.0275 | 6.0275
2021-12-10 22:00 | 2.0121 | 2.4485 | 2.3957 | 2.5768 | 2.441 | 2.622 | 1.4347 | 2.4602 | 3.0357 | 3.0357 | 3.4194 | 3.4194 | 2020-02-07 11:00 | 2.3006 | 3.7702 | 6.1889 | 6.1889 | 6.1889 | 6.1889
2021-12-10 23:00 | 1.7919 | 2.1805 | 2.1335 | 2.2948 | 2.1738 | 2.3351 | 1.2317 | 2.1122 | 2.6064 | 2.6064 | 2.9358 | 2.9358 | 2020-02-07 12:00 | 2.3225 | 3.8061 | 6.2478 | 6.2478 | 6.2478 | 6.2478
2021-12-11 | 1.7605 | 2.1423 | 2.0961 | 2.2545 | 2.1357 | 2.2941 | 1.0231 | 1.7545 | 2.1649 | 2.1649 | 2.4386 | 2.4386 | 2020-02-07 13:00 | 2.2644 | 3.7109 | 6.0915 | 6.0915 | 6.0915 | 6.0915
2021-12-11 01:00 | 1.6604 | 2.0206 | 1.977 | 2.1264 | 2.0143 | 2.1638 | 0.89737 | 1.5388 | 1.8988 | 1.8988 | 2.1388 | 2.1388 | 2020-02-07 14:00 | 2.2558 | 3.6969 | 6.0685 | 6.0685 | 6.0685 | 6.0685
2021-12-11 02:00 | 1.5261 | 1.8571 | 1.8171 | 1.9544 | 1.8514 | 1.9887 | 0.83417 | 1.4305 | 1.7651 | 1.7651 | 1.9882 | 1.9882 | 2020-02-07 15:00 | 2.2501 | 3.6875 | 6.0531 | 6.0531 | 6.0531 | 6.0531
2021-12-11 03:00 | 1.5004 | 1.8258 | 1.7864 | 1.9215 | 1.8202 | 1.9552 | 0.8345 | 1.431 | 1.7658 | 1.7658 | 1.989 | 1.989 | 2020-02-07 16:00 | 2.2139 | 3.6282 | 5.9557 | 5.9557 | 5.9557 | 5.9557
2021-12-11 04:00 | 1.4689 | 1.7876 | 1.749 | 1.8812 | 1.7821 | 1.9143 | 0.80592 | 1.382 | 1.7053 | 1.7053 | 1.9209 | 1.9209 | 2020-02-07 17:00 | 2.1539 | 3.5298 | 5.7943 | 5.7943 | 5.7943 | 5.7943
2021-12-11 05:00 | 1.5416 | 1.876 | 1.8355 | 1.9743 | 1.8702 | 2.009 | 0.8002 | 1.3722 | 1.6932 | 1.6932 | 1.9073 | 1.9073 | 2020-02-07 18:00 | 1.9662 | 3.2223 | 5.2894 | 5.2894 | 5.2894 | 5.2894
2021-12-11 06:00 | 1.6747 | 2.038 | 1.994 | 2.1447 | 2.0317 | 2.1824 | 0.8345 | 1.431 | 1.7658 | 1.7658 | 1.989 | 1.989 | 2020-02-07 19:00 | 1.7404 | 2.8523 | 4.682 | 4.682 | 4.682 | 4.682
2021-12-11 07:00 | 1.7605 | 2.1423 | 2.0961 | 2.2545 | 2.1357 | 2.2941 | 1.0288 | 1.7643 | 2.177 | 2.177 | 2.4522 | 2.4522 | 2020-02-07 20:00 | 1.7071 | 2.7976 | 4.5923 | 4.5923 | 4.5923 | 4.5923
2021-12-11 08:00 | 1.8919 | 2.3023 | 2.2526 | 2.4229 | 2.2952 | 2.4654 | 1.2977 | 2.2253 | 2.7459 | 2.7459 | 3.0929 | 3.0929 | 2020-02-07 21:00 | 1.6061 | 2.6321 | 4.3207 | 4.3207 | 4.3207 | 4.3207
2021-12-11 09:00 | 1.8719 | 2.2779 | 2.2288 | 2.3973 | 2.2709 | 2.4394 | 1.3575 | 2.3279 | 2.8725 | 2.8725 | 3.2355 | 3.2355 | 2020-02-07 22:00 | 1.5918 | 2.6087 | 4.2823 | 4.2823 | 4.2823 | 4.2823
2021-12-11 10:00 | 1.7976 | 2.1875 | 2.1403 | 2.3021 | 2.1808 | 2.3425 | 1.4661 | 2.5141 | 3.1023 | 3.1023 | 3.4944 | 3.4944 | 2020-02-07 23:00 | 1.5804 | 2.59 | 4.2515 | 4.2515 | 4.2515 | 4.2515
2021-12-11 11:00 | 1.8405 | 2.2397 | 2.1914 | 2.357 | 2.2328 | 2.3984 | 1.5547 | 2.666 | 3.2897 | 3.2897 | 3.7055 | 3.7055 | 2020-02-08 | 1.4185 | 2.3246 | 3.8158 | 3.8158 | 3.8158 | 3.8158
2021-12-11 12:00 | 1.6833 | 2.0484 | 2.0042 | 2.1557 | 2.0421 | 2.1936 | 1.5118 | 2.5925 | 3.199 | 3.199 | 3.6034 | 3.6034 | 2020-02-08 01:00 | 1.3946 | 2.2856 | 3.7518 | 3.7518 | 3.7518 | 3.7518
2021-12-11 13:00 | 1.5833 | 1.9267 | 1.8851 | 2.0276 | 1.9207 | 2.0632 | 1.4918 | 2.5582 | 3.1567 | 3.1567 | 3.5557 | 3.5557 | 2020-02-08 02:00 | 1.3642 | 2.2356 | 3.6698 | 3.6698 | 3.6698 | 3.6698
2021-12-11 14:00 | 1.589 | 1.9336 | 1.8919 | 2.0349 | 1.9277 | 2.0707 | 1.4347 | 2.4602 | 3.0357 | 3.0357 | 3.4194 | 3.4194 | 2020-02-08 03:00 | 1.3327 | 2.1841 | 3.5852 | 3.5852 | 3.5852 | 3.5852
2021-12-11 15:00 | 1.589 | 1.9336 | 1.8919 | 2.0349 | 1.9277 | 2.0707 | 1.4661 | 2.5141 | 3.1023 | 3.1023 | 3.4944 | 3.4944 | 2020-02-08 04:00 | 1.4632 | 2.398 | 3.9363 | 3.9363 | 3.9363 | 3.9363
2021-12-11 16:00 | 1.5775 | 1.9197 | 1.8783 | 2.0203 | 1.9138 | 2.0558 | 1.4404 | 2.47 | 3.0478 | 3.0478 | 3.4331 | 3.4331 | 2020-02-08 05:00 | 1.4632 | 2.398 | 3.9363 | 3.9363 | 3.9363 | 3.9363
2021-12-11 17:00 | 1.6233 | 1.9754 | 1.9327 | 2.0788 | 1.9693 | 2.1154 | 1.5518 | 2.6611 | 3.2837 | 3.2837 | 3.6987 | 3.6987 | 2020-02-08 06:00 | 1.427 | 2.3386 | 3.8389 | 3.8389 | 3.8389 | 3.8389
2021-12-11 18:00 | 1.7033 | 2.0727 | 2.028 | 2.1813 | 2.0663 | 2.2196 | 1.5518 | 2.6611 | 3.2837 | 3.2837 | 3.6987 | 3.6987 | 2020-02-08 07:00 | 1.7366 | 2.846 | 4.6718 | 4.6718 | 4.6718 | 4.6718
2021-12-11 19:00 | 1.7662 | 2.1492 | 2.1029 | 2.2618 | 2.1426 | 2.3016 | 1.5622 | 2.6789 | 3.3056 | 3.3056 | 3.7234 | 3.7234 | 2020-02-08 08:00 | 1.8519 | 3.0349 | 4.9819 | 4.9819 | 4.9819 | 4.9819
2021-12-11 20:00 | 1.9119 | 2.3266 | 2.2764 | 2.4485 | 2.3194 | 2.4915 | 1.5833 | 2.715 | 3.3502 | 3.3502 | 3.7736 | 3.7736 | 2020-02-08 09:00 | 1.8805 | 3.0818 | 5.0588 | 5.0588 | 5.0588 | 5.0588
2021-12-11 21:00 | 1.8976 | 2.3092 | 2.2594 | 2.4302 | 2.3021 | 2.4729 | 1.5518 | 2.6611 | 3.2837 | 3.2837 | 3.6987 | 3.6987 | 2020-02-08 10:00 | 1.8757 | 3.074 | 5.0459 | 5.0459 | 5.0459 | 5.0459
2021-12-11 22:00 | 1.7332 | 2.1092 | 2.0637 | 2.2197 | 2.1027 | 2.2587 | 1.3918 | 2.3867 | 2.945 | 2.945 | 3.3173 | 3.3173 | 2020-02-08 11:00 | 1.9014 | 3.1161 | 5.1151 | 5.1151 | 5.1151 | 5.1151
2021-12-11 23:00 | 1.7747 | 2.1597 | 2.1131 | 2.2728 | 2.153 | 2.3127 | 1.135 | 1.9463 | 2.4016 | 2.4016 | 2.7051 | 2.7051 | 2020-02-08 12:00 | 1.9634 | 3.2176 | 5.2817 | 5.2817 | 5.2817 | 5.2817
2021-12-12 | 1.6661 | 2.0275 | 1.9838 | 2.1337 | 2.0213 | 2.1712 | 0.9974 | 1.7104 | 2.1105 | 2.1105 | 2.3773 | 2.3773 | 2020-02-08 13:00 | 1.9634 | 3.2176 | 5.2817 | 5.2817 | 5.2817 | 5.2817
2021-12-12 01:00 | 1.5318 | 1.8641 | 1.8239 | 1.9617 | 1.8583 | 1.9962 | 0.85486 | 1.466 | 1.8089 | 1.8089 | 2.0375 | 2.0375 | 2020-02-08 14:00 | 2.0043 | 3.2847 | 5.3919 | 5.3919 | 5.3919 | 5.3919
2021-12-12 02:00 | 1.4496 | 1.7641 | 1.726 | 1.8565 | 1.7586 | 1.8891 | 0.81449 | 1.3967 | 1.7235 | 1.7235 | 1.9413 | 1.9413 | 2020-02-08 15:00 | 2.0262 | 3.3206 | 5.4508 | 5.4508 | 5.4508 | 5.4508
2021-12-12 03:00 | 1.4347 | 1.7458 | 1.7082 | 1.8373 | 1.7404 | 1.8696 | 0.79449 | 1.3624 | 1.6811 | 1.6811 | 1.8936 | 1.8936 | 2020-02-08 16:00 | 1.931 | 3.1645 | 5.1946 | 5.1946 | 5.1946 | 5.1946
2021-12-12 04:00 | 1.4146 | 1.7215 | 1.6843 | 1.8117 | 1.7162 | 1.8435 | 0.78306 | 1.3428 | 1.657 | 1.657 | 1.8664 | 1.8664 | 2020-02-08 17:00 | 1.8633 | 3.0537 | 5.0126 | 5.0126 | 5.0126 | 5.0126
2021-12-12 05:00 | 1.3917 | 1.6936 | 1.657 | 1.7823 | 1.6883 | 1.8136 | 0.77734 | 1.333 | 1.6449 | 1.6449 | 1.8528 | 1.8528 | 2020-02-08 18:00 | 1.749 | 2.8663 | 4.7051 | 4.7051 | 4.7051 | 4.7051
2021-12-12 06:00 | 1.5256 | 1.8564 | 1.8164 | 1.9537 | 1.8507 | 1.988 | 0.79449 | 1.3624 | 1.6811 | 1.6811 | 1.8936 | 1.8936 | 2020-02-08 19:00 | 1.7223 | 2.8226 | 4.6333 | 4.6333 | 4.6333 | 4.6333
2021-12-12 07:00 | 1.5976 | 1.9441 | 1.9021 | 2.0459 | 1.9381 | 2.0818 | 0.91166 | 1.5634 | 1.9291 | 1.9291 | 2.1729 | 2.1729 | 2020-02-08 20:00 | 1.7509 | 2.8694 | 4.7102 | 4.7102 | 4.7102 | 4.7102
2021-12-12 08:00 | 1.6519 | 2.0101 | 1.9668 | 2.1154 | 2.0039 | 2.1526 | 1.0999 | 1.8862 | 2.3275 | 2.3275 | 2.6216 | 2.6216 | 2020-02-08 21:00 | 1.648 | 2.7008 | 4.4335 | 4.4335 | 4.4335 | 4.4335
2021-12-12 09:00 | 1.6176 | 1.9684 | 1.9259 | 2.0715 | 1.9623 | 2.1079 | 1.2346 | 2.1171 | 2.6124 | 2.6124 | 2.9426 | 2.9426 | 2020-02-08 22:00 | 1.5537 | 2.5463 | 4.1798 | 4.1798 | 4.1798 | 4.1798
2021-12-12 10:00 | 1.4461 | 1.7597 | 1.7218 | 1.8519 | 1.7543 | 1.8845 | 1.4061 | 2.4112 | 2.9753 | 2.9753 | 3.3513 | 3.3513 | 2020-02-08 23:00 | 1.5756 | 2.5822 | 4.2387 | 4.2387 | 4.2387 | 4.2387
2021-12-12 11:00 | 1.4804 | 1.8015 | 1.7626 | 1.8958 | 1.7959 | 1.9292 | 1.4347 | 2.4602 | 3.0357 | 3.0357 | 3.4194 | 3.4194 | 2020-02-09 | 1.4804 | 2.4261 | 3.9824 | 3.9824 | 3.9824 | 3.9824
2021-12-12 12:00 | 1.3718 | 1.6693 | 1.6333 | 1.7568 | 1.6642 | 1.7876 | 1.4604 | 2.5043 | 3.0902 | 3.0902 | 3.4807 | 3.4807 | 2020-02-09 01:00 | 1.4327 | 2.348 | 3.8543 | 3.8543 | 3.8543 | 3.8543
2021-12-12 13:00 | 1.4089 | 1.7145 | 1.6775 | 1.8043 | 1.7092 | 1.836 | 1.4261 | 2.4455 | 3.0176 | 3.0176 | 3.399 | 3.399 | 2020-02-09 02:00 | 1.3241 | 2.17 | 3.5621 | 3.5621 | 3.5621 | 3.5621
2021-12-12 14:00 | 1.2403 | 1.5093 | 1.4768 | 1.5884 | 1.5047 | 1.6163 | 1.4718 | 2.5239 | 3.1144 | 3.1144 | 3.508 | 3.508 | 2020-02-09 03:00 | 1.3565 | 2.2231 | 3.6493 | 3.6493 | 3.6493 | 3.6493
2021-12-12 15:00 | 1.5347 | 1.8675 | 1.8273 | 1.9654 | 1.8618 | 1.9999 | 1.4575 | 2.4994 | 3.0841 | 3.0841 | 3.4739 | 3.4739 | 2020-02-09 04:00 | 1.3661 | 2.2387 | 3.6749 | 3.6749 | 3.6749 | 3.6749
2021-12-12 16:00 | 1.5604 | 1.8988 | 1.8579 | 1.9983 | 1.893 | 2.0334 | 1.4573 | 2.499 | 3.0836 | 3.0836 | 3.4733 | 3.4733 | 2020-02-09 05:00 | 1.4156 | 2.3199 | 3.8082 | 3.8082 | 3.8082 | 3.8082
2021-12-12 17:00 | 1.8719 | 2.2779 | 2.2288 | 2.3973 | 2.2709 | 2.4394 | 1.5265 | 2.6177 | 3.2301 | 3.2301 | 3.6384 | 3.6384 | 2020-02-09 06:00 | 1.4146 | 2.3183 | 3.8056 | 3.8056 | 3.8056 | 3.8056
2021-12-12 18:00 | 2.0091 | 2.4449 | 2.3921 | 2.5729 | 2.4373 | 2.6181 | 1.5775 | 2.7052 | 3.3381 | 3.3381 | 3.76 | 3.76 | 2020-02-09 07:00 | 1.7433 | 2.857 | 4.6897 | 4.6897 | 4.6897 | 4.6897
2021-12-12 19:00 | 1.9919 | 2.424 | 2.3717 | 2.551 | 2.4165 | 2.5958 | 1.5747 | 2.7003 | 3.3321 | 3.3321 | 3.7532 | 3.7532 | 2020-02-09 08:00 | 1.8443 | 3.0224 | 4.9614 | 4.9614 | 4.9614 | 4.9614
2021-12-12 20:00 | 1.9576 | 2.3823 | 2.3309 | 2.5071 | 2.3749 | 2.5511 | 1.5661 | 2.6856 | 3.3139 | 3.3139 | 3.7328 | 3.7328 | 2020-02-09 09:00 | 1.8757 | 3.074 | 5.0459 | 5.0459 | 5.0459 | 5.0459
2021-12-12 21:00 | 1.9548 | 2.3788 | 2.3275 | 2.5034 | 2.3714 | 2.5474 | 1.569 | 2.6905 | 3.32 | 3.32 | 3.7396 | 3.7396 | 2020-02-09 10:00 | 1.8872 | 3.0927 | 5.0767 | 5.0767 | 5.0767 | 5.0767
2021-12-12 22:00 | 1.8205 | 2.2153 | 2.1675 | 2.3314 | 2.2085 | 2.3723 | 1.295 | 2.2207 | 2.7403 | 2.7403 | 3.0866 | 3.0866 | 2020-02-09 11:00 | 1.8986 | 3.1114 | 5.1074 | 5.1074 | 5.1074 | 5.1074
2021-12-12 23:00 | 1.6661 | 2.0275 | 1.9838 | 2.1337 | 2.0213 | 2.1712 | 1.0288 | 1.7643 | 2.177 | 2.177 | 2.4522 | 2.4522 | 2020-02-09 12:00 | 1.8872 | 3.0927 | 5.0767 | 5.0767 | 5.0767 | 5.0767
2021-12-13 | 1.5575 | 1.8954 | 1.8545 | 1.9947 | 1.8895 | 2.0297 | 0.95182 | 1.6322 | 2.0141 | 2.0141 | 2.2686 | 2.2686 | 2020-02-09 13:00 | 1.8872 | 3.0927 | 5.0767 | 5.0767 | 5.0767 | 5.0767
2021-12-13 01:00 | 1.4547 | 1.7702 | 1.732 | 1.8629 | 1.7647 | 1.8956 | 0.80603 | 1.3822 | 1.7056 | 1.7056 | 1.9211 | 1.9211 | 2020-02-09 14:00 | 1.8414 | 3.0178 | 4.9537 | 4.9537 | 4.9537 | 4.9537
2021-12-13 02:00 | 1.3812 | 1.6808 | 1.6445 | 1.7688 | 1.6756 | 1.7999 | 0.72619 | 1.2453 | 1.5366 | 1.5366 | 1.7308 | 1.7308 | 2020-02-09 15:00 | 1.8605 | 3.049 | 5.0049 | 5.0049 | 5.0049 | 5.0049
2021-12-13 03:00 | 1.3775 | 1.6763 | 1.6401 | 1.7641 | 1.6711 | 1.7951 | 0.67731 | 1.1615 | 1.4332 | 1.4332 | 1.6144 | 1.6144 | 2020-02-09 16:00 | 1.8271 | 2.9943 | 4.9152 | 4.9152 | 4.9152 | 4.9152
2021-12-13 04:00 | 1.4175 | 1.725 | 1.6878 | 1.8153 | 1.7196 | 1.8472 | 0.6716 | 1.1517 | 1.4211 | 1.4211 | 1.6007 | 1.6007 | 2020-02-09 17:00 | 1.8481 | 3.0287 | 4.9716 | 4.9716 | 4.9716 | 4.9716
2021-12-13 05:00 | 1.4648 | 1.7826 | 1.7441 | 1.8759 | 1.7771 | 1.9089 | 0.70875 | 1.2154 | 1.4997 | 1.4997 | 1.6893 | 1.6893 | 2020-02-09 18:00 | 1.6061 | 2.6321 | 4.3207 | 4.3207 | 4.3207 | 4.3207
2021-12-13 06:00 | 1.9205 | 2.337 | 2.2866 | 2.4595 | 2.3298 | 2.5027 | 0.84806 | 1.4543 | 1.7945 | 1.7945 | 2.0213 | 2.0213 | 2020-02-09 19:00 | 1.6071 | 2.6337 | 4.3233 | 4.3233 | 4.3233 | 4.3233
2021-12-13 07:00 | 2.1263 | 2.5874 | 2.5316 | 2.723 | 2.5795 | 2.7708 | 1.1803 | 2.024 | 2.4975 | 2.4975 | 2.8132 | 2.8132 | 2020-02-09 20:00 | 1.6338 | 2.6774 | 4.395 | 4.395 | 4.395 | 4.395
2021-12-13 08:00 | 2.2949 | 2.7926 | 2.7324 | 2.9389 | 2.784 | 2.9906 | 1.2918 | 2.2152 | 2.7334 | 2.7334 | 3.0789 | 3.0789 | 2020-02-09 21:00 | 1.629 | 2.6696 | 4.3822 | 4.3822 | 4.3822 | 4.3822
2021-12-13 09:00 | 2.1205 | 2.5805 | 2.5248 | 2.7157 | 2.5725 | 2.7634 | 1.1974 | 2.0534 | 2.5338 | 2.5338 | 2.8541 | 2.8541 | 2020-02-09 22:00 | 1.5509 | 2.5416 | 4.1721 | 4.1721 | 4.1721 | 4.1721
2021-12-13 10:00 | 2.0462 | 2.4901 | 2.4364 | 2.6205 | 2.4824 | 2.6666 | 1.2317 | 2.1122 | 2.6064 | 2.6064 | 2.9358 | 2.9358 | 2020-02-09 23:00 | 1.4461 | 2.3699 | 3.8902 | 3.8902 | 3.8902 | 3.8902
2021-12-13 11:00 | 1.8205 | 2.2153 | 2.1675 | 2.3314 | 2.2085 | 2.3723 | 1.2375 | 2.122 | 2.6185 | 2.6185 | 2.9494 | 2.9494 | 2020-02-10 | 1.3765 | 2.2559 | 3.7031 | 3.7031 | 3.7031 | 3.7031
2021-12-13 12:00 | 1.8405 | 2.2397 | 2.1914 | 2.357 | 2.2328 | 2.3984 | 1.1832 | 2.0289 | 2.5036 | 2.5036 | 2.82 | 2.82 | 2020-02-10 01:00 | 1.348 | 2.2091 | 3.6262 | 3.6262 | 3.6262 | 3.6262
2021-12-13 13:00 | 1.7833 | 2.1701 | 2.1233 | 2.2838 | 2.1634 | 2.3239 | 1.2032 | 2.0632 | 2.5459 | 2.5459 | 2.8677 | 2.8677 | 2020-02-10 02:00 | 1.3384 | 2.1935 | 3.6006 | 3.6006 | 3.6006 | 3.6006
2021-12-13 14:00 | 1.9119 | 2.3266 | 2.2764 | 2.4485 | 2.3194 | 2.4915 | 1.2432 | 2.1318 | 2.6306 | 2.6306 | 2.9631 | 2.9631 | 2020-02-10 03:00 | 1.3184 | 2.1607 | 3.5468 | 3.5468 | 3.5468 | 3.5468
2021-12-13 15:00 | 2.0805 | 2.5318 | 2.4772 | 2.6644 | 2.524 | 2.7112 | 1.2317 | 2.1122 | 2.6064 | 2.6064 | 2.9358 | 2.9358 | 2020-02-10 04:00 | 1.3642 | 2.2356 | 3.6698 | 3.6698 | 3.6698 | 3.6698
2021-12-13 16:00 | 1.9634 | 2.3892 | 2.3377 | 2.5144 | 2.3818 | 2.5585 | 1.3003 | 2.2299 | 2.7515 | 2.7515 | 3.0993 | 3.0993 | 2020-02-10 05:00 | 1.4185 | 2.3246 | 3.8158 | 3.8158 | 3.8158 | 3.8158
2021-12-13 17:00 | 2.1977 | 2.6744 | 2.6167 | 2.8145 | 2.6661 | 2.8639 | 1.4718 | 2.5239 | 3.1144 | 3.1144 | 3.508 | 3.508 | 2020-02-10 06:00 | 1.5995 | 2.6212 | 4.3028 | 4.3028 | 4.3028 | 4.3028
2021-12-13 18:00 | 2.3578 | 2.8691 | 2.8072 | 3.0194 | 2.8603 | 3.0725 | 1.5861 | 2.7199 | 3.3563 | 3.3563 | 3.7805 | 3.7805 | 2020-02-10 07:00 | 1.97 | 3.2285 | 5.2996 | 5.2996 | 5.2996 | 5.2996
2021-12-13 19:00 | 2.3035 | 2.8032 | 2.7427 | 2.95 | 2.7945 | 3.0018 | 1.5976 | 2.7395 | 3.3804 | 3.3804 | 3.8077 | 3.8077 | 2020-02-10 08:00 | 2.1891 | 3.5876 | 5.8891 | 5.8891 | 5.8891 | 5.8891
2021-12-13 20:00 | 2.2034 | 2.6813 | 2.6235 | 2.8218 | 2.6731 | 2.8714 | 1.649 | 2.8278 | 3.4893 | 3.4893 | 3.9303 | 3.9303 | 2020-02-10 09:00 | 2.1872 | 3.5845 | 5.8839 | 5.8839 | 5.8839 | 5.8839
2021-12-13 21:00 | 2.1005 | 2.5561 | 2.501 | 2.69 | 2.5483 | 2.7373 | 1.5976 | 2.7395 | 3.3804 | 3.3804 | 3.8077 | 3.8077 | 2020-02-10 10:00 | 2.2882 | 3.7499 | 6.1556 | 6.1556 | 6.1556 | 6.1556
2021-12-13 22:00 | 1.8462 | 2.2466 | 2.1982 | 2.3643 | 2.2397 | 2.4059 | 1.2861 | 2.2055 | 2.7214 | 2.7214 | 3.0654 | 3.0654 | 2020-02-10 11:00 | 2.3825 | 3.9045 | 6.4093 | 6.4093 | 6.4093 | 6.4093
2021-12-13 23:00 | 1.6833 | 2.0484 | 2.0042 | 2.1557 | 2.0421 | 2.1936 | 1.0688 | 1.8329 | 2.2617 | 2.2617 | 2.5475 | 2.5475 | 2020-02-10 12:00 | 2.3844 | 3.9076 | 6.4144 | 6.4144 | 6.4144 | 6.4144
2021-12-14 | 1.5433 | 1.878 | 1.8375 | 1.9764 | 1.8722 | 2.0111 | 0.8717 | 1.4948 | 1.8445 | 1.8445 | 2.0777 | 2.0777 | 2020-02-10 13:00 | 2.5111 | 4.1153 | 6.7553 | 6.7553 | 6.7553 | 6.7553
2021-12-14 01:00 | 1.4318 | 1.7423 | 1.7048 | 1.8336 | 1.737 | 1.8658 | 0.76591 | 1.3134 | 1.6207 | 1.6207 | 1.8255 | 1.8255 | 2020-02-10 14:00 | 2.4006 | 3.9342 | 6.458 | 6.458 | 6.458 | 6.458
2021-12-14 02:00 | 1.3804 | 1.6797 | 1.6435 | 1.7677 | 1.6746 | 1.7988 | 0.74876 | 1.284 | 1.5844 | 1.5844 | 1.7846 | 1.7846 | 2020-02-10 15:00 | 2.4425 | 4.0029 | 6.5707 | 6.5707 | 6.5707 | 6.5707
2021-12-14 03:00 | 1.3718 | 1.6693 | 1.6333 | 1.7568 | 1.6642 | 1.7876 | 0.7259 | 1.2448 | 1.536 | 1.536 | 1.7301 | 1.7301 | 2020-02-10 16:00 | 2.3806 | 3.9014 | 6.4042 | 6.4042 | 6.4042 | 6.4042
2021-12-14 04:00 | 1.3489 | 1.6415 | 1.6061 | 1.7275 | 1.6364 | 1.7578 | 0.66017 | 1.1321 | 1.3969 | 1.3969 | 1.5735 | 1.5735 | 2020-02-10 17:00 | 2.2301 | 3.6547 | 5.9993 | 5.9993 | 5.9993 | 5.9993
2021-12-14 05:00 | 1.4625 | 1.7797 | 1.7413 | 1.873 | 1.7743 | 1.9059 | 0.67446 | 1.1566 | 1.4272 | 1.4272 | 1.6075 | 1.6075 | 2020-02-10 18:00 | 2.1139 | 3.4643 | 5.6866 | 5.6866 | 5.6866 | 5.6866
2021-12-14 06:00 | 1.7833 | 2.1701 | 2.1233 | 2.2838 | 2.1634 | 2.3239 | 0.81141 | 1.3914 | 1.717 | 1.717 | 1.934 | 1.934 | 2020-02-10 19:00 | 1.9872 | 3.2566 | 5.3458 | 5.3458 | 5.3458 | 5.3458
2021-12-14 07:00 | 1.9948 | 2.4275 | 2.3751 | 2.5546 | 2.42 | 2.5995 | 1.0603 | 1.8182 | 2.2435 | 2.2435 | 2.5271 | 2.5271 | 2020-02-10 20:00 | 1.9014 | 3.1161 | 5.1151 | 5.1151 | 5.1151 | 5.1151
2021-12-14 08:00 | 2.0577 | 2.504 | 2.45 | 2.6352 | 2.4963 | 2.6814 | 1.186 | 2.0338 | 2.5096 | 2.5096 | 2.8268 | 2.8268 | 2020-02-10 21:00 | 1.829 | 2.9975 | 4.9204 | 4.9204 | 4.9204 | 4.9204
2021-12-14 09:00 | 1.9605 | 2.3857 | 2.3343 | 2.5107 | 2.3784 | 2.5548 | 1.166 | 1.9995 | 2.4673 | 2.4673 | 2.7791 | 2.7791 | 2020-02-10 22:00 | 1.7157 | 2.8117 | 4.6154 | 4.6154 | 4.6154 | 4.6154
2021-12-14 10:00 | 2.0891 | 2.5422 | 2.4874 | 2.6754 | 2.5344 | 2.7224 | 1.2632 | 2.1662 | 2.6729 | 2.6729 | 3.0107 | 3.0107 | 2020-02-10 23:00 | 1.6976 | 2.782 | 4.5667 | 4.5667 | 4.5667 | 4.5667
2021-12-14 11:00 | 2.1034 | 2.5596 | 2.5044 | 2.6937 | 2.5517 | 2.741 | 1.286 | 2.2054 | 2.7213 | 2.7213 | 3.0652 | 3.0652 | 2020-02-11 | 1.5109 | 2.476 | 4.0644 | 4.0644 | 4.0644 | 4.0644
2021-12-14 12:00 | 2.0891 | 2.5422 | 2.4874 | 2.6754 | 2.5344 | 2.7224 | 1.3089 | 2.2446 | 2.7697 | 2.7697 | 3.1198 | 3.1198 | 2020-02-11 01:00 | 1.5347 | 2.5151 | 4.1285 | 4.1285 | 4.1285 | 4.1285
2021-12-14 13:00 | 2.1005 | 2.5561 | 2.501 | 2.69 | 2.5483 | 2.7373 | 1.3575 | 2.3279 | 2.8725 | 2.8725 | 3.2355 | 3.2355 | 2020-02-11 02:00 | 1.447 | 2.3714 | 3.8927 | 3.8927 | 3.8927 | 3.8927
2021-12-14 14:00 | 2.2749 | 2.7683 | 2.7086 | 2.9133 | 2.7598 | 2.9645 | 1.3661 | 2.3426 | 2.8906 | 2.8906 | 3.256 | 3.256 | 2020-02-11 03:00 | 1.3985 | 2.2918 | 3.762 | 3.762 | 3.762 | 3.762
2021-12-14 15:00 | 2.1463 | 2.6118 | 2.5554 | 2.7486 | 2.6037 | 2.7969 | 1.2718 | 2.1809 | 2.691 | 2.691 | 3.0312 | 3.0312 | 2020-02-11 04:00 | 1.488 | 2.4386 | 4.0029 | 4.0029 | 4.0029 | 4.0029
2021-12-14 16:00 | 2.2091 | 2.6883 | 2.6303 | 2.8291 | 2.68 | 2.8788 | 1.4689 | 2.519 | 3.1083 | 3.1083 | 3.5012 | 3.5012 | 2020-02-11 05:00 | 1.5213 | 2.4932 | 4.0926 | 4.0926 | 4.0926 | 4.0926
2021-12-14 17:00 | 2.312 | 2.8135 | 2.7528 | 2.9609 | 2.8048 | 3.0129 | 1.549 | 2.6562 | 3.2776 | 3.2776 | 3.6919 | 3.6919 | 2020-02-11 06:00 | 1.6347 | 2.679 | 4.3976 | 4.3976 | 4.3976 | 4.3976
2021-12-14 18:00 | 2.3578 | 2.8691 | 2.8072 | 3.0194 | 2.8603 | 3.0725 | 1.5747 | 2.7003 | 3.3321 | 3.3321 | 3.7532 | 3.7532 | 2020-02-11 07:00 | 2.1482 | 3.5205 | 5.7789 | 5.7789 | 5.7789 | 5.7789
2021-12-14 19:00 | 2.2334 | 2.7178 | 2.6591 | 2.8601 | 2.7094 | 2.9104 | 1.6433 | 2.818 | 3.4772 | 3.4772 | 3.9167 | 3.9167 | 2020-02-11 08:00 | 2.253 | 3.6922 | 6.0608 | 6.0608 | 6.0608 | 6.0608
2021-12-14 20:00 | 2.0377 | 2.4796 | 2.4261 | 2.6095 | 2.472 | 2.6554 | 1.5976 | 2.7395 | 3.3804 | 3.3804 | 3.8077 | 3.8077 | 2020-02-11 09:00 | 2.3511 | 3.853 | 6.3247 | 6.3247 | 6.3247 | 6.3247
2021-12-14 21:00 | 2.0062 | 2.4414 | 2.3887 | 2.5693 | 2.4339 | 2.6144 | 1.5118 | 2.5925 | 3.199 | 3.199 | 3.6034 | 3.6034 | 2020-02-11 10:00 | 2.4016 | 3.9357 | 6.4606 | 6.4606 | 6.4606 | 6.4606
2021-12-14 22:00 | 1.8833 | 2.2918 | 2.2424 | 2.4119 | 2.2848 | 2.4543 | 1.1746 | 2.0142 | 2.4854 | 2.4854 | 2.7996 | 2.7996 | 2020-02-11 11:00 | 2.4873 | 4.0762 | 6.6912 | 6.6912 | 6.6912 | 6.6912
2021-12-14 23:00 | 1.6204 | 1.9719 | 1.9293 | 2.0752 | 1.9658 | 2.1116 | 1.0141 | 1.7391 | 2.1459 | 2.1459 | 2.4171 | 2.4171 | 2020-02-11 12:00 | 2.4654 | 4.0403 | 6.6323 | 6.6323 | 6.6323 | 6.6323
2021-12-15 | 1.5038 | 1.8299 | 1.7904 | 1.9258 | 1.8243 | 1.9596 | 0.92074 | 1.5789 | 1.9483 | 1.9483 | 2.1946 | 2.1946 | 2020-02-11 13:00 | 2.4168 | 3.9607 | 6.5016 | 6.5016 | 6.5016 | 6.5016
2021-12-15 01:00 | 1.4518 | 1.7667 | 1.7286 | 1.8592 | 1.7612 | 1.8919 | 0.8002 | 1.3722 | 1.6932 | 1.6932 | 1.9073 | 1.9073 | 2020-02-11 14:00 | 2.4063 | 3.9435 | 6.4734 | 6.4734 | 6.4734 | 6.4734
2021-12-15 02:00 | 1.3123 | 1.5969 | 1.5625 | 1.6806 | 1.592 | 1.7101 | 0.71733 | 1.2301 | 1.5179 | 1.5179 | 1.7097 | 1.7097 | 2020-02-11 15:00 | 2.4673 | 4.0434 | 6.6374 | 6.6374 | 6.6374 | 6.6374
2021-12-15 03:00 | 1.3289 | 1.6171 | 1.5823 | 1.7019 | 1.6122 | 1.7318 | 0.71161 | 1.2203 | 1.5058 | 1.5058 | 1.6961 | 1.6961 | 2020-02-11 16:00 | 2.4206 | 3.967 | 6.5118 | 6.5118 | 6.5118 | 6.5118
2021-12-15 04:00 | 1.2918 | 1.5719 | 1.538 | 1.6543 | 1.5671 | 1.6834 | 0.67494 | 1.1574 | 1.4282 | 1.4282 | 1.6087 | 1.6087 | 2020-02-11 17:00 | 2.4321 | 3.9857 | 6.5426 | 6.5426 | 6.5426 | 6.5426
2021-12-15 05:00 | 1.4508 | 1.7655 | 1.7274 | 1.858 | 1.7601 | 1.8907 | 0.70875 | 1.2154 | 1.4997 | 1.4997 | 1.6893 | 1.6893 | 2020-02-11 18:00 | 2.2568 | 3.6984 | 6.071 | 6.071 | 6.071 | 6.071
2021-12-15 06:00 | 1.7662 | 2.1492 | 2.1029 | 2.2618 | 2.1426 | 2.3016 | 0.79064 | 1.3558 | 1.673 | 1.673 | 1.8844 | 1.8844 | 2020-02-11 19:00 | 2.0672 | 3.3878 | 5.561 | 5.561 | 5.561 | 5.561
2021-12-15 07:00 | 2.0091 | 2.4449 | 2.3921 | 2.5729 | 2.4373 | 2.6181 | 1.1354 | 1.947 | 2.4025 | 2.4025 | 2.7061 | 2.7061 | 2020-02-11 20:00 | 1.99 | 3.2613 | 5.3535 | 5.3535 | 5.3535 | 5.3535
2021-12-15 08:00 | 2.1063 | 2.5631 | 2.5078 | 2.6974 | 2.5552 | 2.7448 | 1.2403 | 2.1269 | 2.6245 | 2.6245 | 2.9562 | 2.9562 | 2020-02-11 21:00 | 1.83 | 2.999 | 4.9229 | 4.9229 | 4.9229 | 4.9229
2021-12-15 09:00 | 2.2463 | 2.7335 | 2.6745 | 2.8767 | 2.7251 | 2.9272 | 1.1946 | 2.0485 | 2.5278 | 2.5278 | 2.8473 | 2.8473 | 2020-02-11 22:00 | 1.7881 | 2.9303 | 4.8102 | 4.8102 | 4.8102 | 4.8102
2021-12-15 10:00 | 2.2577 | 2.7474 | 2.6882 | 2.8913 | 2.739 | 2.9421 | 1.3775 | 2.3622 | 2.9148 | 2.9148 | 3.2832 | 3.2832 | 2020-02-11 23:00 | 1.668 | 2.7336 | 4.4873 | 4.4873 | 4.4873 | 4.4873
2021-12-15 11:00 | 2.232 | 2.7161 | 2.6575 | 2.8584 | 2.7077 | 2.9086 | 1.3489 | 2.3132 | 2.8543 | 2.8543 | 3.2151 | 3.2151 | 2020-02-12 | 1.5471 | 2.5353 | 4.1618 | 4.1618 | 4.1618 | 4.1618
2021-12-15 12:00 | 2.252 | 2.7405 | 2.6813 | 2.884 | 2.732 | 2.9347 | 1.3461 | 2.3083 | 2.8483 | 2.8483 | 3.2083 | 3.2083 | 2020-02-12 01:00 | 1.5204 | 2.4916 | 4.0901 | 4.0901 | 4.0901 | 4.0901
2021-12-15 13:00 | 2.2349 | 2.7196 | 2.6609 | 2.8621 | 2.7112 | 2.9124 | 1.4432 | 2.4749 | 3.0539 | 3.0539 | 3.4399 | 3.4399 | 2020-02-12 02:00 | 1.4585 | 2.3902 | 3.9235 | 3.9235 | 3.9235 | 3.9235
2021-12-15 14:00 | 2.4663 | 3.0013 | 2.9366 | 3.1585 | 2.992 | 3.214 | 1.4004 | 2.4014 | 2.9632 | 2.9632 | 3.3377 | 3.3377 | 2020-02-12 03:00 | 1.4318 | 2.3464 | 3.8517 | 3.8517 | 3.8517 | 3.8517
2021-12-15 15:00 | 2.5035 | 3.0465 | 2.9808 | 3.2061 | 3.0371 | 3.2624 | 1.4289 | 2.4504 | 3.0236 | 3.0236 | 3.4058 | 3.4058 | 2020-02-12 04:00 | 1.4508 | 2.3777 | 3.903 | 3.903 | 3.903 | 3.903
2021-12-15 16:00 | 2.372 | 2.8865 | 2.8243 | 3.0377 | 2.8776 | 3.0911 | 1.4947 | 2.5631 | 3.1627 | 3.1627 | 3.5625 | 3.5625 | 2020-02-12 05:00 | 1.5575 | 2.5525 | 4.19 | 4.19 | 4.19 | 4.19
2021-12-15 17:00 | 2.4035 | 2.9248 | 2.8617 | 3.078 | 2.9158 | 3.1321 | 1.5718 | 2.6954 | 3.326 | 3.326 | 3.7464 | 3.7464 | 2020-02-12 06:00 | 1.7805 | 2.9178 | 4.7897 | 4.7897 | 4.7897 | 4.7897
2021-12-15 18:00 | 2.3377 | 2.8448 | 2.7834 | 2.9938 | 2.836 | 3.0464 | 1.5918 | 2.7297 | 3.3683 | 3.3683 | 3.7941 | 3.7941 | 2020-02-12 07:00 | 2.0367 | 3.3378 | 5.479 | 5.479 | 5.479 | 5.479
2021-12-15 19:00 | 2.1923 | 2.6678 | 2.6103 | 2.8076 | 2.6596 | 2.8569 | 1.5404 | 2.6415 | 3.2595 | 3.2595 | 3.6715 | 3.6715 | 2020-02-12 08:00 | 2.3978 | 3.9295 | 6.4503 | 6.4503 | 6.4503 | 6.4503
2021-12-15 20:00 | 2.1291 | 2.5909 | 2.535 | 2.7266 | 2.5829 | 2.7746 | 1.509 | 2.5876 | 3.193 | 3.193 | 3.5965 | 3.5965 | 2020-02-12 09:00 | 2.3806 | 3.9014 | 6.4042 | 6.4042 | 6.4042 | 6.4042
2021-12-15 21:00 | 2.0577 | 2.504 | 2.45 | 2.6352 | 2.4963 | 2.6814 | 1.5433 | 2.6464 | 3.2655 | 3.2655 | 3.6783 | 3.6783 | 2020-02-12 10:00 | 2.533 | 4.1512 | 6.8142 | 6.8142 | 6.8142 | 6.8142
2021-12-15 22:00 | 1.8691 | 2.2744 | 2.2254 | 2.3936 | 2.2674 | 2.4356 | 1.1917 | 2.0436 | 2.5217 | 2.5217 | 2.8404 | 2.8404 | 2020-02-12 11:00 | 2.5254 | 4.1387 | 6.7937 | 6.7937 | 6.7937 | 6.7937
2021-12-15 23:00 | 1.7234 | 2.0972 | 2.052 | 2.2071 | 2.0908 | 2.2459 | 1.026 | 1.7594 | 2.171 | 2.171 | 2.4454 | 2.4454 | 2020-02-12 12:00 | 2.5959 | 4.2542 | 6.9833 | 6.9833 | 6.9833 | 6.9833
2021-12-16 | 1.6147 | 1.9649 | 1.9225 | 2.0679 | 1.9589 | 2.1042 | 0.89451 | 1.5339 | 1.8928 | 1.8928 | 2.132 | 2.132 | 2020-02-12 13:00 | 2.5988 | 4.2589 | 6.991 | 6.991 | 6.991 | 6.991
2021-12-16 01:00 | 1.4318 | 1.7423 | 1.7048 | 1.8336 | 1.737 | 1.8658 | 0.77734 | 1.333 | 1.6449 | 1.6449 | 1.8528 | 1.8528 | 2020-02-12 14:00 | 2.5378 | 4.159 | 6.827 | 6.827 | 6.827 | 6.827
2021-12-16 02:00 | 1.3261 | 1.6137 | 1.5789 | 1.6982 | 1.6087 | 1.7281 | 0.70021 | 1.2008 | 1.4817 | 1.4817 | 1.6689 | 1.6689 | 2020-02-12 15:00 | 2.594 | 4.2511 | 6.9782 | 6.9782 | 6.9782 | 6.9782
2021-12-16 03:00 | 1.3489 | 1.6415 | 1.6061 | 1.7275 | 1.6364 | 1.7578 | 0.74019 | 1.2693 | 1.5662 | 1.5662 | 1.7642 | 1.7642 | 2020-02-12 16:00 | 2.6083 | 4.2745 | 7.0167 | 7.0167 | 7.0167 | 7.0167
2021-12-16 04:00 | 1.3404 | 1.6311 | 1.5959 | 1.7166 | 1.6261 | 1.7467 | 0.67443 | 1.1565 | 1.4271 | 1.4271 | 1.6075 | 1.6075 | 2020-02-12 17:00 | 2.5311 | 4.148 | 6.8091 | 6.8091 | 6.8091 | 6.8091
2021-12-16 05:00 | 1.4947 | 1.8189 | 1.7796 | 1.9141 | 1.8133 | 1.9478 | 0.70589 | 1.2105 | 1.4937 | 1.4937 | 1.6825 | 1.6825 | 2020-02-12 18:00 | 2.3673 | 3.8795 | 6.3683 | 6.3683 | 6.3683 | 6.3683
2021-12-16 06:00 | 1.6976 | 2.0658 | 2.0212 | 2.174 | 2.0594 | 2.2122 | 0.79449 | 1.3624 | 1.6811 | 1.6811 | 1.8936 | 1.8936 | 2020-02-12 19:00 | 2.1901 | 3.5891 | 5.8916 | 5.8916 | 5.8916 | 5.8916
2021-12-16 07:00 | 2.0291 | 2.4692 | 2.4159 | 2.5986 | 2.4616 | 2.6442 | 1.1317 | 1.9407 | 2.3947 | 2.3947 | 2.6974 | 2.6974 | 2020-02-12 20:00 | 2.0939 | 3.4315 | 5.6328 | 5.6328 | 5.6328 | 5.6328
2021-12-16 08:00 | 2.1148 | 2.5735 | 2.518 | 2.7083 | 2.5656 | 2.7559 | 1.2375 | 2.122 | 2.6185 | 2.6185 | 2.9494 | 2.9494 | 2020-02-12 21:00 | 2.0796 | 3.408 | 5.5944 | 5.5944 | 5.5944 | 5.5944
2021-12-16 09:00 | 2.0863 | 2.5388 | 2.484 | 2.6718 | 2.5309 | 2.7187 | 1.2117 | 2.0779 | 2.5641 | 2.5641 | 2.8881 | 2.8881 | 2020-02-12 22:00 | 1.8586 | 3.0459 | 4.9998 | 4.9998 | 4.9998 | 4.9998
2021-12-16 10:00 | 2.1406 | 2.6048 | 2.5486 | 2.7413 | 2.5968 | 2.7895 | 1.3689 | 2.3475 | 2.8967 | 2.8967 | 3.2628 | 3.2628 | 2020-02-12 23:00 | 1.7805 | 2.9178 | 4.7897 | 4.7897 | 4.7897 | 4.7897
2021-12-16 11:00 | 2.0977 | 2.5527 | 2.4976 | 2.6864 | 2.5448 | 2.7336 | 1.3689 | 2.3475 | 2.8967 | 2.8967 | 3.2628 | 3.2628 | 2020-02-13 | 1.6233 | 2.6602 | 4.3668 | 4.3668 | 4.3668 | 4.3668
2021-12-16 12:00 | 2.2492 | 2.737 | 2.6779 | 2.8804 | 2.7286 | 2.931 | 1.3575 | 2.3279 | 2.8725 | 2.8725 | 3.2355 | 3.2355 | 2020-02-13 01:00 | 1.569 | 2.5713 | 4.2208 | 4.2208 | 4.2208 | 4.2208
2021-12-16 13:00 | 2.1863 | 2.6605 | 2.6031 | 2.7998 | 2.6523 | 2.849 | 1.4489 | 2.4847 | 3.066 | 3.066 | 3.4535 | 3.4535 | 2020-02-13 02:00 | 1.5252 | 2.4994 | 4.1029 | 4.1029 | 4.1029 | 4.1029
2021-12-16 14:00 | 2.2749 | 2.7683 | 2.7086 | 2.9133 | 2.7598 | 2.9645 | 1.4061 | 2.4112 | 2.9753 | 2.9753 | 3.3513 | 3.3513 | 2020-02-13 03:00 | 1.5956 | 2.615 | 4.2925 | 4.2925 | 4.2925 | 4.2925
2021-12-16 15:00 | 2.2892 | 2.7857 | 2.7256 | 2.9316 | 2.7771 | 2.9831 | 1.3232 | 2.2691 | 2.7999 | 2.7999 | 3.1538 | 3.1538 | 2020-02-13 04:00 | 1.5814 | 2.5916 | 4.2541 | 4.2541 | 4.2541 | 4.2541
2021-12-16 16:00 | 2.2149 | 2.6953 | 2.6371 | 2.8364 | 2.6869 | 2.8863 | 1.3461 | 2.3083 | 2.8483 | 2.8483 | 3.2083 | 3.2083 | 2020-02-13 05:00 | 1.6795 | 2.7524 | 4.518 | 4.518 | 4.518 | 4.518
2021-12-16 17:00 | 2.3949 | 2.9143 | 2.8515 | 3.067 | 2.9054 | 3.1209 | 1.5461 | 2.6513 | 3.2716 | 3.2716 | 3.6851 | 3.6851 | 2020-02-13 06:00 | 1.8071 | 2.9616 | 4.8614 | 4.8614 | 4.8614 | 4.8614
2021-12-16 18:00 | 2.3549 | 2.8657 | 2.8038 | 3.0158 | 2.8568 | 3.0688 | 1.589 | 2.7248 | 3.3623 | 3.3623 | 3.7873 | 3.7873 | 2020-02-13 07:00 | 2.3416 | 3.8374 | 6.2991 | 6.2991 | 6.2991 | 6.2991
2021-12-16 19:00 | 2.2007 | 2.6781 | 2.6203 | 2.8184 | 2.6698 | 2.8679 | 1.549 | 2.6562 | 3.2776 | 3.2776 | 3.6919 | 3.6919 | 2020-02-13 08:00 | 2.4483 | 4.0122 | 6.5861 | 6.5861 | 6.5861 | 6.5861
2021-12-16 20:00 | 2.0863 | 2.5388 | 2.484 | 2.6718 | 2.5309 | 2.7187 | 1.5829 | 2.7144 | 3.3494 | 3.3494 | 3.7728 | 3.7728 | 2020-02-13 09:00 | 2.7807 | 4.5571 | 7.4805 | 7.4805 | 7.4805 | 7.4805
2021-12-16 21:00 | 2.0177 | 2.4553 | 2.4023 | 2.5839 | 2.4477 | 2.6293 | 1.5947 | 2.7346 | 3.3744 | 3.3744 | 3.8009 | 3.8009 | 2020-02-13 10:00 | 2.6159 | 4.287 | 7.0372 | 7.0372 | 7.0372 | 7.0372
2021-12-16 22:00 | 1.7895 | 2.1777 | 2.1307 | 2.2918 | 2.171 | 2.332 | 1.2271 | 2.1043 | 2.5965 | 2.5965 | 2.9247 | 2.9247 | 2020-02-13 11:00 | 2.6712 | 4.3775 | 7.1858 | 7.1858 | 7.1858 | 7.1858
2021-12-16 23:00 | 1.6233 | 1.9754 | 1.9327 | 2.0788 | 1.9693 | 2.1154 | 1.0546 | 1.8084 | 2.2315 | 2.2315 | 2.5135 | 2.5135 | 2020-02-13 12:00 | 2.6045 | 4.2683 | 7.0064 | 7.0064 | 7.0064 | 7.0064
2021-12-17 | 1.5518 | 1.8884 | 1.8477 | 1.9873 | 1.8826 | 2.0223 | 0.93167 | 1.5977 | 1.9714 | 1.9714 | 2.2206 | 2.2206 | 2020-02-13 13:00 | 2.7074 | 4.4369 | 7.2832 | 7.2832 | 7.2832 | 7.2832
2021-12-17 01:00 | 1.3774 | 1.6761 | 1.64 | 1.7639 | 1.6709 | 1.7949 | 0.87165 | 1.4947 | 1.8444 | 1.8444 | 2.0775 | 2.0775 | 2020-02-13 14:00 | 2.6845 | 4.3994 | 7.2217 | 7.2217 | 7.2217 | 7.2217
2021-12-17 02:00 | 1.3146 | 1.5998 | 1.5653 | 1.6836 | 1.5948 | 1.7131 | 0.72876 | 1.2497 | 1.5421 | 1.5421 | 1.737 | 1.737 | 2020-02-13 15:00 | 2.6664 | 4.3697 | 7.173 | 7.173 | 7.173 | 7.173
2021-12-17 03:00 | 1.3175 | 1.6032 | 1.5687 | 1.6872 | 1.5983 | 1.7169 | 0.69422 | 1.1905 | 1.469 | 1.469 | 1.6546 | 1.6546 | 2020-02-13 16:00 | 2.6521 | 4.3463 | 7.1345 | 7.1345 | 7.1345 | 7.1345
2021-12-17 04:00 | 1.3175 | 1.6032 | 1.5687 | 1.6872 | 1.5983 | 1.7169 | 0.69446 | 1.1909 | 1.4695 | 1.4695 | 1.6552 | 1.6552 | 2020-02-13 17:00 | 2.534 | 4.1527 | 6.8168 | 6.8168 | 6.8168 | 6.8168
2021-12-17 05:00 | 1.5204 | 1.8502 | 1.8102 | 1.9471 | 1.8445 | 1.9813 | 0.66588 | 1.1419 | 1.409 | 1.409 | 1.5871 | 1.5871 | 2020-02-13 18:00 | 2.4159 | 3.9591 | 6.499 | 6.499 | 6.499 | 6.499
2021-12-17 06:00 | 1.7805 | 2.1666 | 2.1199 | 2.2801 | 2.16 | 2.3202 | 0.82592 | 1.4163 | 1.7477 | 1.7477 | 1.9686 | 1.9686 | 2020-02-13 19:00 | 2.3263 | 3.8124 | 6.2581 | 6.2581 | 6.2581 | 6.2581
2021-12-17 07:00 | 1.9634 | 2.3892 | 2.3377 | 2.5144 | 2.3818 | 2.5585 | 1.1774 | 2.0191 | 2.4915 | 2.4915 | 2.8064 | 2.8064 | 2020-02-13 20:00 | 2.2653 | 3.7125 | 6.0941 | 6.0941 | 6.0941 | 6.0941
2021-12-17 08:00 | 2.0491 | 2.4935 | 2.4398 | 2.6242 | 2.4859 | 2.6703 | 1.2432 | 2.1318 | 2.6306 | 2.6306 | 2.9631 | 2.9631 | 2020-02-13 21:00 | 2.0739 | 3.3987 | 5.579 | 5.579 | 5.579 | 5.579
2021-12-17 09:00 | 2.0034 | 2.4379 | 2.3853 | 2.5656 | 2.4304 | 2.6107 | 1.2203 | 2.0926 | 2.5822 | 2.5822 | 2.9086 | 2.9086 | 2020-02-13 22:00 | 1.9234 | 3.152 | 5.1741 | 5.1741 | 5.1741 | 5.1741
2021-12-17 10:00 | 1.9091 | 2.3231 | 2.273 | 2.4448 | 2.316 | 2.4878 | 1.3003 | 2.2299 | 2.7515 | 2.7515 | 3.0993 | 3.0993 | 2020-02-13 23:00 | 1.8176 | 2.9787 | 4.8896 | 4.8896 | 4.8896 | 4.8896
2021-12-17 11:00 | 1.9262 | 2.344 | 2.2934 | 2.4668 | 2.3368 | 2.5101 | 1.266 | 2.1711 | 2.679 | 2.679 | 3.0176 | 3.0176 | 2020-02-14 | 1.6795 | 2.7524 | 4.518 | 4.518 | 4.518 | 4.518
2021-12-17 12:00 | 1.8748 | 2.2814 | 2.2322 | 2.4009 | 2.2744 | 2.4431 | 1.306 | 2.2397 | 2.7636 | 2.7636 | 3.1129 | 3.1129 | 2020-02-14 01:00 | 1.6052 | 2.6306 | 4.3181 | 4.3181 | 4.3181 | 4.3181
2021-12-17 13:00 | 1.8381 | 2.2367 | 2.1885 | 2.3539 | 2.2299 | 2.3953 | 1.3032 | 2.2348 | 2.7576 | 2.7576 | 3.1061 | 3.1061 | 2020-02-14 02:00 | 1.5471 | 2.5353 | 4.1618 | 4.1618 | 4.1618 | 4.1618
2021-12-17 14:00 | 1.8976 | 2.3092 | 2.2594 | 2.4302 | 2.3021 | 2.4729 | 1.2689 | 2.176 | 2.685 | 2.685 | 3.0244 | 3.0244 | 2020-02-14 03:00 | 1.5328 | 2.5119 | 4.1234 | 4.1234 | 4.1234 | 4.1234
2021-12-17 15:00 | 1.9462 | 2.3683 | 2.3173 | 2.4924 | 2.361 | 2.5362 | 1.3232 | 2.2691 | 2.7999 | 2.7999 | 3.1538 | 3.1538 | 2020-02-14 04:00 | 1.5413 | 2.526 | 4.1464 | 4.1464 | 4.1464 | 4.1464
2021-12-17 16:00 | 2.006 | 2.4411 | 2.3885 | 2.569 | 2.4336 | 2.6142 | 1.4947 | 2.5631 | 3.1627 | 3.1627 | 3.5625 | 3.5625 | 2020-02-14 05:00 | 1.628 | 2.668 | 4.3796 | 4.3796 | 4.3796 | 4.3796
2021-12-17 17:00 | 2.2634 | 2.7544 | 2.695 | 2.8987 | 2.7459 | 2.9496 | 1.6412 | 2.8143 | 3.4727 | 3.4727 | 3.9117 | 3.9117 | 2020-02-14 06:00 | 1.9338 | 3.1692 | 5.2023 | 5.2023 | 5.2023 | 5.2023
2021-12-17 18:00 | 2.3377 | 2.8448 | 2.7834 | 2.9938 | 2.836 | 3.0464 | 1.7404 | 2.9846 | 3.6828 | 3.6828 | 4.1483 | 4.1483 | 2020-02-14 07:00 | 2.0834 | 3.4143 | 5.6046 | 5.6046 | 5.6046 | 5.6046
2021-12-17 19:00 | 2.2589 | 2.7489 | 2.6896 | 2.8929 | 2.7404 | 2.9437 | 1.7719 | 3.0385 | 3.7493 | 3.7493 | 4.2232 | 4.2232 | 2020-02-14 08:00 | 2.4368 | 3.9935 | 6.5554 | 6.5554 | 6.5554 | 6.5554
2021-12-17 20:00 | 1.9719 | 2.3996 | 2.3479 | 2.5254 | 2.3922 | 2.5697 | 1.7347 | 2.9748 | 3.6707 | 3.6707 | 4.1347 | 4.1347 | 2020-02-14 09:00 | 2.4749 | 4.0559 | 6.6579 | 6.6579 | 6.6579 | 6.6579
2021-12-17 21:00 | 1.9748 | 2.4031 | 2.3513 | 2.529 | 2.3957 | 2.5734 | 1.6519 | 2.8327 | 3.4953 | 3.4953 | 3.9371 | 3.9371 | 2020-02-14 10:00 | 2.4187 | 3.9638 | 6.5067 | 6.5067 | 6.5067 | 6.5067
2021-12-17 22:00 | 1.8433 | 2.2431 | 2.1948 | 2.3607 | 2.2362 | 2.4021 | 1.4832 | 2.5435 | 3.1385 | 3.1385 | 3.5352 | 3.5352 | 2020-02-14 11:00 | 2.4625 | 4.0356 | 6.6246 | 6.6246 | 6.6246 | 6.6246
2021-12-17 23:00 | 1.6776 | 2.0414 | 1.9974 | 2.1484 | 2.0351 | 2.1861 | 1.192 | 2.0441 | 2.5223 | 2.5223 | 2.8411 | 2.8411 | 2020-02-14 12:00 | 2.4483 | 4.0122 | 6.5861 | 6.5861 | 6.5861 | 6.5861
2021-12-18 | 1.6204 | 1.9719 | 1.9293 | 2.0752 | 1.9658 | 2.1116 | 0.97453 | 1.6712 | 2.0621 | 2.0621 | 2.3228 | 2.3228 | 2020-02-14 13:00 | 2.4711 | 4.0497 | 6.6476 | 6.6476 | 6.6476 | 6.6476
2021-12-18 01:00 | 1.489 | 1.8119 | 1.7728 | 1.9068 | 1.8063 | 1.9403 | 0.85736 | 1.4702 | 1.8142 | 1.8142 | 2.0435 | 2.0435 | 2020-02-14 14:00 | 2.7293 | 4.4728 | 7.3421 | 7.3421 | 7.3421 | 7.3421
2021-12-18 02:00 | 1.3585 | 1.6532 | 1.6175 | 1.7398 | 1.6481 | 1.7704 | 0.79449 | 1.3624 | 1.6811 | 1.6811 | 1.8936 | 1.8936 | 2020-02-14 15:00 | 2.6483 | 4.3401 | 7.1243 | 7.1243 | 7.1243 | 7.1243
2021-12-18 03:00 | 1.3661 | 1.6624 | 1.6265 | 1.7494 | 1.6572 | 1.7802 | 0.74305 | 1.2742 | 1.5723 | 1.5723 | 1.771 | 1.771 | 2020-02-14 16:00 | 2.6226 | 4.2979 | 7.0551 | 7.0551 | 7.0551 | 7.0551
2021-12-18 04:00 | 1.3118 | 1.5963 | 1.5618 | 1.6799 | 1.5914 | 1.7094 | 0.75043 | 1.2869 | 1.5879 | 1.5879 | 1.7886 | 1.7886 | 2020-02-14 17:00 | 2.5197 | 4.1293 | 6.7783 | 6.7783 | 6.7783 | 6.7783
2021-12-18 05:00 | 1.3739 | 1.6719 | 1.6358 | 1.7595 | 1.6667 | 1.7904 | 0.75162 | 1.2889 | 1.5904 | 1.5904 | 1.7915 | 1.7915 | 2020-02-14 18:00 | 2.2682 | 3.7172 | 6.1018 | 6.1018 | 6.1018 | 6.1018
2021-12-18 06:00 | 1.5004 | 1.8258 | 1.7864 | 1.9215 | 1.8202 | 1.9552 | 0.71447 | 1.2252 | 1.5118 | 1.5118 | 1.7029 | 1.7029 | 2020-02-14 19:00 | 2.0462 | 3.3534 | 5.5047 | 5.5047 | 5.5047 | 5.5047
2021-12-18 07:00 | 1.5918 | 1.9371 | 1.8953 | 2.0386 | 1.9311 | 2.0744 | 0.99454 | 1.7055 | 2.1045 | 2.1045 | 2.3704 | 2.3704 | 2020-02-14 20:00 | 2.0748 | 3.4002 | 5.5815 | 5.5815 | 5.5815 | 5.5815
2021-12-18 08:00 | 1.7462 | 2.1249 | 2.0791 | 2.2362 | 2.1184 | 2.2755 | 1.1431 | 1.9603 | 2.4189 | 2.4189 | 2.7246 | 2.7246 | 2020-02-14 21:00 | 1.9281 | 3.1598 | 5.1869 | 5.1869 | 5.1869 | 5.1869
2021-12-18 09:00 | 1.7605 | 2.1423 | 2.0961 | 2.2545 | 2.1357 | 2.2941 | 1.3461 | 2.3083 | 2.8483 | 2.8483 | 3.2083 | 3.2083 | 2020-02-14 22:00 | 1.8748 | 3.0724 | 5.0434 | 5.0434 | 5.0434 | 5.0434
2021-12-18 10:00 | 1.7633 | 2.1458 | 2.0995 | 2.2582 | 2.1392 | 2.2979 | 1.4775 | 2.5337 | 3.1265 | 3.1265 | 3.5216 | 3.5216 | 2020-02-14 23:00 | 1.7957 | 2.9428 | 4.8307 | 4.8307 | 4.8307 | 4.8307
2021-12-18 11:00 | 1.9662 | 2.3927 | 2.3411 | 2.518 | 2.3853 | 2.5623 | 1.5833 | 2.715 | 3.3502 | 3.3502 | 3.7736 | 3.7736 | 2020-02-15 | 1.6633 | 2.7258 | 4.4745 | 4.4745 | 4.4745 | 4.4745
2021-12-18 12:00 | 1.9748 | 2.4031 | 2.3513 | 2.529 | 2.3957 | 2.5734 | 1.6376 | 2.8082 | 3.4651 | 3.4651 | 3.9031 | 3.9031 | 2020-02-15 01:00 | 1.5871 | 2.6009 | 4.2694 | 4.2694 | 4.2694 | 4.2694
2021-12-18 13:00 | 1.9948 | 2.4275 | 2.3751 | 2.5546 | 2.42 | 2.5995 | 1.6519 | 2.8327 | 3.4953 | 3.4953 | 3.9371 | 3.9371 | 2020-02-15 02:00 | 1.5309 | 2.5088 | 4.1182 | 4.1182 | 4.1182 | 4.1182
2021-12-18 14:00 | 1.9348 | 2.3544 | 2.3036 | 2.4778 | 2.3472 | 2.5213 | 1.6061 | 2.7543 | 3.3986 | 3.3986 | 3.8281 | 3.8281 | 2020-02-15 03:00 | 1.5213 | 2.4932 | 4.0926 | 4.0926 | 4.0926 | 4.0926
2021-12-18 15:00 | 1.9634 | 2.3892 | 2.3377 | 2.5144 | 2.3818 | 2.5585 | 1.6376 | 2.8082 | 3.4651 | 3.4651 | 3.9031 | 3.9031 | 2020-02-15 04:00 | 1.4623 | 2.3964 | 3.9337 | 3.9337 | 3.9337 | 3.9337
2021-12-18 16:00 | 2.1005 | 2.5561 | 2.501 | 2.69 | 2.5483 | 2.7373 | 1.7708 | 3.0367 | 3.7471 | 3.7471 | 4.2207 | 4.2207 | 2020-02-15 05:00 | 1.5937 | 2.6118 | 4.2874 | 4.2874 | 4.2874 | 4.2874
2021-12-18 17:00 | 2.1434 | 2.6083 | 2.552 | 2.7449 | 2.6003 | 2.7932 | 1.7776 | 3.0483 | 3.7614 | 3.7614 | 4.2368 | 4.2368 | 2020-02-15 06:00 | 1.6033 | 2.6275 | 4.313 | 4.313 | 4.313 | 4.313
2021-12-18 18:00 | 2.1034 | 2.5596 | 2.5044 | 2.6937 | 2.5517 | 2.741 | 1.8433 | 3.161 | 3.9005 | 3.9005 | 4.3935 | 4.3935 | 2020-02-15 07:00 | 1.9977 | 3.2738 | 5.374 | 5.374 | 5.374 | 5.374
2021-12-18 19:00 | 2.0262 | 2.4657 | 2.4125 | 2.5949 | 2.4581 | 2.6405 | 1.6747 | 2.8719 | 3.5437 | 3.5437 | 3.9916 | 3.9916 | 2020-02-15 08:00 | 2.0015 | 3.28 | 5.3842 | 5.3842 | 5.3842 | 5.3842
2021-12-18 20:00 | 1.8862 | 2.2953 | 2.2458 | 2.4156 | 2.2882 | 2.458 | 1.5918 | 2.7297 | 3.3683 | 3.3683 | 3.7941 | 3.7941 | 2020-02-15 09:00 | 2.0682 | 3.3893 | 5.5636 | 5.5636 | 5.5636 | 5.5636
2021-12-18 21:00 | 1.8319 | 2.2292 | 2.1811 | 2.346 | 2.2224 | 2.3872 | 1.5804 | 2.7101 | 3.3442 | 3.3442 | 3.7668 | 3.7668 | 2020-02-15 10:00 | 2.2434 | 3.6766 | 6.0351 | 6.0351 | 6.0351 | 6.0351
2021-12-18 22:00 | 1.8148 | 2.2084 | 2.1607 | 2.3241 | 2.2016 | 2.3649 | 1.2918 | 2.2152 | 2.7334 | 2.7334 | 3.0789 | 3.0789 | 2020-02-15 11:00 | 2.3501 | 3.8514 | 6.3222 | 6.3222 | 6.3222 | 6.3222
2021-12-18 23:00 | 1.669 | 2.031 | 1.9872 | 2.1374 | 2.0247 | 2.175 | 1.1117 | 1.9064 | 2.3524 | 2.3524 | 2.6497 | 2.6497 | 2020-02-15 12:00 | 2.3739 | 3.8905 | 6.3862 | 6.3862 | 6.3862 | 6.3862
2021-12-19 | 1.589 | 1.9336 | 1.8919 | 2.0349 | 1.9277 | 2.0707 | 0.96651 | 1.6574 | 2.0451 | 2.0451 | 2.3036 | 2.3036 | 2020-02-15 13:00 | 2.4282 | 3.9794 | 6.5323 | 6.5323 | 6.5323 | 6.5323
2021-12-19 01:00 | 1.4247 | 1.7337 | 1.6963 | 1.8245 | 1.7283 | 1.8566 | 0.85741 | 1.4703 | 1.8143 | 1.8143 | 2.0436 | 2.0436 | 2020-02-15 14:00 | 2.4568 | 4.0263 | 6.6092 | 6.6092 | 6.6092 | 6.6092
2021-12-19 02:00 | 1.3775 | 1.6763 | 1.6401 | 1.7641 | 1.6711 | 1.7951 | 0.75162 | 1.2889 | 1.5904 | 1.5904 | 1.7915 | 1.7915 | 2020-02-15 15:00 | 2.2501 | 3.6875 | 6.0531 | 6.0531 | 6.0531 | 6.0531
2021-12-19 03:00 | 1.3775 | 1.6763 | 1.6401 | 1.7641 | 1.6711 | 1.7951 | 0.73179 | 1.2549 | 1.5485 | 1.5485 | 1.7442 | 1.7442 | 2020-02-15 16:00 | 2.1672 | 3.5517 | 5.8301 | 5.8301 | 5.8301 | 5.8301
2021-12-19 04:00 | 1.303 | 1.5856 | 1.5514 | 1.6687 | 1.5807 | 1.698 | 0.69446 | 1.1909 | 1.4695 | 1.4695 | 1.6552 | 1.6552 | 2020-02-15 17:00 | 2.1396 | 3.5064 | 5.7558 | 5.7558 | 5.7558 | 5.7558
2021-12-19 05:00 | 1.3118 | 1.5963 | 1.5618 | 1.6799 | 1.5914 | 1.7094 | 0.70018 | 1.2007 | 1.4816 | 1.4816 | 1.6688 | 1.6688 | 2020-02-15 18:00 | 2.0672 | 3.3878 | 5.561 | 5.561 | 5.561 | 5.561
2021-12-19 06:00 | 1.3746 | 1.6728 | 1.6367 | 1.7604 | 1.6676 | 1.7914 | 0.72018 | 1.235 | 1.5239 | 1.5239 | 1.7165 | 1.7165 | 2020-02-15 19:00 | 1.9815 | 3.2472 | 5.3304 | 5.3304 | 5.3304 | 5.3304
2021-12-19 07:00 | 1.5175 | 1.8467 | 1.8068 | 1.9434 | 1.841 | 1.9776 | 0.93452 | 1.6026 | 1.9775 | 1.9775 | 2.2274 | 2.2274 | 2020-02-15 20:00 | 1.91 | 3.1302 | 5.1382 | 5.1382 | 5.1382 | 5.1382
2021-12-19 08:00 | 1.5861 | 1.9301 | 1.8885 | 2.0313 | 1.9242 | 2.0669 | 1.2603 | 2.1613 | 2.6669 | 2.6669 | 3.0039 | 3.0039 | 2020-02-15 21:00 | 1.7747 | 2.9085 | 4.7743 | 4.7743 | 4.7743 | 4.7743
2021-12-19 09:00 | 1.7319 | 2.1075 | 2.0621 | 2.2179 | 2.101 | 2.2569 | 1.3146 | 2.2544 | 2.7818 | 2.7818 | 3.1333 | 3.1333 | 2020-02-15 22:00 | 1.9291 | 3.1614 | 5.1895 | 5.1895 | 5.1895 | 5.1895
2021-12-19 10:00 | 1.8833 | 2.2918 | 2.2424 | 2.4119 | 2.2848 | 2.4543 | 1.4575 | 2.4994 | 3.0841 | 3.0841 | 3.4739 | 3.4739 | 2020-02-15 23:00 | 1.769 | 2.8991 | 4.7589 | 4.7589 | 4.7589 | 4.7589
2021-12-19 11:00 | 1.8976 | 2.3092 | 2.2594 | 2.4302 | 2.3021 | 2.4729 | 1.5604 | 2.6758 | 3.3018 | 3.3018 | 3.7192 | 3.7192 | 2020-02-16 | 1.6338 | 2.6774 | 4.395 | 4.395 | 4.395 | 4.395
2021-12-19 12:00 | 1.8462 | 2.2466 | 2.1982 | 2.3643 | 2.2397 | 2.4059 | 1.5833 | 2.715 | 3.3502 | 3.3502 | 3.7736 | 3.7736 | 2020-02-16 01:00 | 1.5795 | 2.5884 | 4.2489 | 4.2489 | 4.2489 | 4.2489
2021-12-19 13:00 | 1.7404 | 2.1179 | 2.0723 | 2.2289 | 2.1114 | 2.2681 | 1.6061 | 2.7543 | 3.3986 | 3.3986 | 3.8281 | 3.8281 | 2020-02-16 02:00 | 1.4947 | 2.4495 | 4.0209 | 4.0209 | 4.0209 | 4.0209
2021-12-19 14:00 | 1.7662 | 2.1492 | 2.1029 | 2.2618 | 2.1426 | 2.3016 | 1.5433 | 2.6464 | 3.2655 | 3.2655 | 3.6783 | 3.6783 | 2020-02-16 03:00 | 1.5023 | 2.462 | 4.0414 | 4.0414 | 4.0414 | 4.0414
2021-12-19 15:00 | 1.7862 | 2.1736 | 2.1267 | 2.2875 | 2.1669 | 2.3276 | 1.509 | 2.5876 | 3.193 | 3.193 | 3.5965 | 3.5965 | 2020-02-16 04:00 | 1.5375 | 2.5197 | 4.1362 | 4.1362 | 4.1362 | 4.1362
2021-12-19 16:00 | 1.7833 | 2.1701 | 2.1233 | 2.2838 | 2.1634 | 2.3239 | 1.4689 | 2.519 | 3.1083 | 3.1083 | 3.5012 | 3.5012 | 2020-02-16 05:00 | 1.5518 | 2.5432 | 4.1746 | 4.1746 | 4.1746 | 4.1746
2021-12-19 17:00 | 1.8576 | 2.2605 | 2.2118 | 2.379 | 2.2536 | 2.4208 | 1.5633 | 2.6807 | 3.3079 | 3.3079 | 3.726 | 3.726 | 2020-02-16 06:00 | 1.5823 | 2.5931 | 4.2566 | 4.2566 | 4.2566 | 4.2566
2021-12-19 18:00 | 1.8919 | 2.3023 | 2.2526 | 2.4229 | 2.2952 | 2.4654 | 1.5947 | 2.7346 | 3.3744 | 3.3744 | 3.8009 | 3.8009 | 2020-02-16 07:00 | 1.8576 | 3.0443 | 4.9973 | 4.9973 | 4.9973 | 4.9973
2021-12-19 19:00 | 1.8891 | 2.2988 | 2.2492 | 2.4192 | 2.2917 | 2.4617 | 1.5147 | 2.5974 | 3.2051 | 3.2051 | 3.6102 | 3.6102 | 2020-02-16 08:00 | 1.9395 | 3.1786 | 5.2176 | 5.2176 | 5.2176 | 5.2176
2021-12-19 20:00 | 1.8976 | 2.3092 | 2.2594 | 2.4302 | 2.3021 | 2.4729 | 1.4832 | 2.5435 | 3.1385 | 3.1385 | 3.5352 | 3.5352 | 2020-02-16 09:00 | 2.0186 | 3.3081 | 5.4303 | 5.4303 | 5.4303 | 5.4303
2021-12-19 21:00 | 1.8205 | 2.2153 | 2.1675 | 2.3314 | 2.2085 | 2.3723 | 1.4147 | 2.4261 | 2.9936 | 2.9936 | 3.372 | 3.372 | 2020-02-16 10:00 | 2.1501 | 3.5236 | 5.784 | 5.784 | 5.784 | 5.784
2021-12-19 22:00 | 1.729 | 2.104 | 2.0586 | 2.2143 | 2.0976 | 2.2532 | 1.206 | 2.0681 | 2.552 | 2.552 | 2.8745 | 2.8745 | 2020-02-16 11:00 | 2.112 | 3.4611 | 5.6815 | 5.6815 | 5.6815 | 5.6815
2021-12-19 23:00 | 1.6018 | 1.9492 | 1.9071 | 2.0513 | 1.9432 | 2.0873 | 0.98649 | 1.6917 | 2.0874 | 2.0874 | 2.3512 | 2.3512 | 2020-02-16 12:00 | 2.172 | 3.5595 | 5.8429 | 5.8429 | 5.8429 | 5.8429
2021-12-20 | 1.529 | 1.8606 | 1.8205 | 1.9581 | 1.8549 | 1.9925 | 0.87737 | 1.5045 | 1.8565 | 1.8565 | 2.0912 | 2.0912 | 2020-02-16 13:00 | 2.2006 | 3.6063 | 5.9198 | 5.9198 | 5.9198 | 5.9198
2021-12-20 01:00 | 1.3918 | 1.6937 | 1.6571 | 1.7824 | 1.6884 | 1.8137 | 0.74878 | 1.284 | 1.5844 | 1.5844 | 1.7847 | 1.7847 | 2020-02-16 14:00 | 2.2263 | 3.6485 | 5.989 | 5.989 | 5.989 | 5.989
2021-12-20 02:00 | 1.3346 | 1.6241 | 1.5891 | 1.7092 | 1.6191 | 1.7392 | 0.70875 | 1.2154 | 1.4997 | 1.4997 | 1.6893 | 1.6893 | 2020-02-16 15:00 | 2.1834 | 3.5782 | 5.8737 | 5.8737 | 5.8737 | 5.8737
2021-12-20 03:00 | 1.3403 | 1.6311 | 1.5959 | 1.7165 | 1.626 | 1.7467 | 0.68906 | 1.1816 | 1.4581 | 1.4581 | 1.6424 | 1.6424 | 2020-02-16 16:00 | 2.1672 | 3.5517 | 5.8301 | 5.8301 | 5.8301 | 5.8301
2021-12-20 04:00 | 1.3118 | 1.5963 | 1.5618 | 1.6799 | 1.5914 | 1.7094 | 0.65436 | 1.1221 | 1.3846 | 1.3846 | 1.5597 | 1.5597 | 2020-02-16 17:00 | 2.1005 | 3.4424 | 5.6507 | 5.6507 | 5.6507 | 5.6507
2021-12-20 05:00 | 1.4267 | 1.7361 | 1.6987 | 1.8271 | 1.7308 | 1.8592 | 0.6916 | 1.186 | 1.4634 | 1.4634 | 1.6484 | 1.6484 | 2020-02-16 18:00 | 1.9824 | 3.2488 | 5.333 | 5.333 | 5.333 | 5.333
2021-12-20 06:00 | 1.749 | 2.1284 | 2.0825 | 2.2399 | 2.1218 | 2.2792 | 0.78306 | 1.3428 | 1.657 | 1.657 | 1.8664 | 1.8664 | 2020-02-16 19:00 | 1.8814 | 3.0833 | 5.0613 | 5.0613 | 5.0613 | 5.0613
2021-12-20 07:00 | 1.829 | 2.2258 | 2.1777 | 2.3424 | 2.2189 | 2.3835 | 1.0388 | 1.7814 | 2.1981 | 2.1981 | 2.4759 | 2.4759 | 2020-02-16 20:00 | 1.8738 | 3.0708 | 5.0408 | 5.0408 | 5.0408 | 5.0408
2021-12-20 08:00 | 1.9691 | 2.3962 | 2.3445 | 2.5217 | 2.3888 | 2.566 | 1.1603 | 1.9897 | 2.4552 | 2.4552 | 2.7655 | 2.7655 | 2020-02-16 21:00 | 1.85 | 3.0318 | 4.9767 | 4.9767 | 4.9767 | 4.9767
2021-12-20 09:00 | 1.8748 | 2.2814 | 2.2322 | 2.4009 | 2.2744 | 2.4431 | 1.1317 | 1.9407 | 2.3947 | 2.3947 | 2.6974 | 2.6974 | 2020-02-16 22:00 | 1.7128 | 2.807 | 4.6077 | 4.6077 | 4.6077 | 4.6077
2021-12-20 10:00 | 1.8348 | 2.2327 | 2.1845 | 2.3497 | 2.2258 | 2.391 | 1.204 | 2.0647 | 2.5477 | 2.5477 | 2.8697 | 2.8697 | 2020-02-16 23:00 | 1.6604 | 2.7211 | 4.4668 | 4.4668 | 4.4668 | 4.4668
2021-12-20 11:00 | 1.8119 | 2.2049 | 2.1573 | 2.3204 | 2.1981 | 2.3612 | 1.2517 | 2.1466 | 2.6487 | 2.6487 | 2.9835 | 2.9835 | 2020-02-17 | 1.5966 | 2.6165 | 4.2951 | 4.2951 | 4.2951 | 4.2951
2021-12-20 12:00 | 1.7776 | 2.1632 | 2.1165 | 2.2765 | 2.1565 | 2.3165 | 1.2546 | 2.1515 | 2.6548 | 2.6548 | 2.9903 | 2.9903 | 2020-02-17 01:00 | 1.5118 | 2.4776 | 4.067 | 4.067 | 4.067 | 4.067
2021-12-20 13:00 | 1.8176 | 2.2118 | 2.1641 | 2.3277 | 2.205 | 2.3686 | 1.306 | 2.2397 | 2.7636 | 2.7636 | 3.1129 | 3.1129 | 2020-02-17 02:00 | 1.4575 | 2.3886 | 3.9209 | 3.9209 | 3.9209 | 3.9209
2021-12-20 14:00 | 1.7976 | 2.1875 | 2.1403 | 2.3021 | 2.1808 | 2.3425 | 1.2832 | 2.2005 | 2.7152 | 2.7152 | 3.0584 | 3.0584 | 2020-02-17 03:00 | 1.4737 | 2.4151 | 3.9645 | 3.9645 | 3.9645 | 3.9645
2021-12-20 15:00 | 1.7662 | 2.1492 | 2.1029 | 2.2618 | 2.1426 | 2.3016 | 1.2546 | 2.1515 | 2.6548 | 2.6548 | 2.9903 | 2.9903 | 2020-02-17 04:00 | 1.5023 | 2.462 | 4.0414 | 4.0414 | 4.0414 | 4.0414
2021-12-20 16:00 | 1.9491 | 2.3718 | 2.3207 | 2.4961 | 2.3645 | 2.5399 | 1.3546 | 2.323 | 2.8664 | 2.8664 | 3.2287 | 3.2287 | 2020-02-17 05:00 | 1.6376 | 2.6837 | 4.4053 | 4.4053 | 4.4053 | 4.4053
2021-12-20 17:00 | 2.192 | 2.6674 | 2.6099 | 2.8072 | 2.6592 | 2.8565 | 1.5147 | 2.5974 | 3.2051 | 3.2051 | 3.6102 | 3.6102 | 2020-02-17 06:00 | 1.6604 | 2.7211 | 4.4668 | 4.4668 | 4.4668 | 4.4668
2021-12-20 18:00 | 2.2863 | 2.7822 | 2.7222 | 2.9279 | 2.7736 | 2.9794 | 1.629 | 2.7935 | 3.447 | 3.447 | 3.8826 | 3.8826 | 2020-02-17 07:00 | 2.1205 | 3.4752 | 5.7046 | 5.7046 | 5.7046 | 5.7046
2021-12-20 19:00 | 2.2091 | 2.6883 | 2.6303 | 2.8291 | 2.68 | 2.8788 | 1.6318 | 2.7984 | 3.453 | 3.453 | 3.8894 | 3.8894 | 2020-02-17 08:00 | 2.2692 | 3.7187 | 6.1043 | 6.1043 | 6.1043 | 6.1043
2021-12-20 20:00 | 1.9977 | 2.4309 | 2.3785 | 2.5583 | 2.4235 | 2.6032 | 1.5918 | 2.7297 | 3.3683 | 3.3683 | 3.7941 | 3.7941 | 2020-02-17 09:00 | 2.2854 | 3.7453 | 6.1479 | 6.1479 | 6.1479 | 6.1479
2021-12-20 21:00 | 2.0091 | 2.4449 | 2.3921 | 2.5729 | 2.4373 | 2.6181 | 1.5261 | 2.617 | 3.2293 | 3.2293 | 3.6374 | 3.6374 | 2020-02-17 10:00 | 2.3759 | 3.8936 | 6.3914 | 6.3914 | 6.3914 | 6.3914
2021-12-20 22:00 | 1.7747 | 2.1597 | 2.1131 | 2.2728 | 2.153 | 2.3127 | 1.2432 | 2.1318 | 2.6306 | 2.6306 | 2.9631 | 2.9631 | 2020-02-17 11:00 | 2.4311 | 3.9841 | 6.54 | 6.54 | 6.54 | 6.54
2021-12-20 23:00 | 1.5855 | 1.9294 | 1.8878 | 2.0305 | 1.9235 | 2.0662 | 1.0117 | 1.7349 | 2.1407 | 2.1407 | 2.4113 | 2.4113 | 2020-02-17 12:00 | 2.5549 | 4.1871 | 6.8731 | 6.8731 | 6.8731 | 6.8731
2021-12-21 | 1.5347 | 1.8675 | 1.8273 | 1.9654 | 1.8618 | 1.9999 | 0.88022 | 1.5094 | 1.8626 | 1.8626 | 2.098 | 2.098 | 2020-02-17 13:00 | 2.5654 | 4.2043 | 6.9013 | 6.9013 | 6.9013 | 6.9013
2021-12-21 01:00 | 1.3804 | 1.6797 | 1.6435 | 1.7677 | 1.6746 | 1.7988 | 0.75514 | 1.2949 | 1.5979 | 1.5979 | 1.7998 | 1.7998 | 2020-02-17 14:00 | 2.6092 | 4.2761 | 7.0192 | 7.0192 | 7.0192 | 7.0192
2021-12-21 02:00 | 1.3203 | 1.6067 | 1.5721 | 1.6909 | 1.6018 | 1.7206 | 0.6916 | 1.186 | 1.4634 | 1.4634 | 1.6484 | 1.6484 | 2020-02-17 15:00 | 2.6016 | 4.2636 | 6.9987 | 6.9987 | 6.9987 | 6.9987
2021-12-21 03:00 | 1.306 | 1.5893 | 1.555 | 1.6726 | 1.5844 | 1.702 | 0.68025 | 1.1665 | 1.4394 | 1.4394 | 1.6214 | 1.6214 | 2020-02-17 16:00 | 2.6045 | 4.2683 | 7.0064 | 7.0064 | 7.0064 | 7.0064
2021-12-21 04:00 | 1.2918 | 1.5719 | 1.538 | 1.6543 | 1.5671 | 1.6834 | 0.64596 | 1.1077 | 1.3669 | 1.3669 | 1.5396 | 1.5396 | 2020-02-17 17:00 | 2.5797 | 4.2277 | 6.9398 | 6.9398 | 6.9398 | 6.9398
2021-12-21 05:00 | 1.3918 | 1.6937 | 1.6571 | 1.7824 | 1.6884 | 1.8137 | 0.66802 | 1.1455 | 1.4135 | 1.4135 | 1.5922 | 1.5922 | 2020-02-17 18:00 | 2.4711 | 4.0497 | 6.6476 | 6.6476 | 6.6476 | 6.6476
2021-12-21 06:00 | 1.7319 | 2.1075 | 2.0621 | 2.2179 | 2.101 | 2.2569 | 0.79449 | 1.3624 | 1.6811 | 1.6811 | 1.8936 | 1.8936 | 2020-02-17 19:00 | 2.1434 | 3.5126 | 5.7661 | 5.7661 | 5.7661 | 5.7661
2021-12-21 07:00 | 1.8548 | 2.2571 | 2.2084 | 2.3753 | 2.2501 | 2.417 | 0.9974 | 1.7104 | 2.1105 | 2.1105 | 2.3773 | 2.3773 | 2020-02-17 20:00 | 2.0481 | 3.3565 | 5.5098 | 5.5098 | 5.5098 | 5.5098
2021-12-21 08:00 | 1.9434 | 2.3649 | 2.3139 | 2.4888 | 2.3576 | 2.5325 | 1.1403 | 1.9554 | 2.4129 | 2.4129 | 2.7178 | 2.7178 | 2020-02-17 21:00 | 1.9872 | 3.2566 | 5.3458 | 5.3458 | 5.3458 | 5.3458
2021-12-21 09:00 | 1.769 | 2.1527 | 2.1063 | 2.2655 | 2.1461 | 2.3053 | 1.1517 | 1.975 | 2.4371 | 2.4371 | 2.7451 | 2.7451 | 2020-02-17 22:00 | 1.8833 | 3.0864 | 5.0664 | 5.0664 | 5.0664 | 5.0664
2021-12-21 10:00 | 1.7805 | 2.1666 | 2.1199 | 2.2801 | 2.16 | 2.3202 | 1.2203 | 2.0926 | 2.5822 | 2.5822 | 2.9086 | 2.9086 | 2020-02-17 23:00 | 1.7128 | 2.807 | 4.6077 | 4.6077 | 4.6077 | 4.6077
2021-12-21 11:00 | 1.809 | 2.2014 | 2.1539 | 2.3167 | 2.1946 | 2.3574 | 1.3146 | 2.2544 | 2.7818 | 2.7818 | 3.1333 | 3.1333 | 2020-02-18 | 1.6071 | 2.6337 | 4.3233 | 4.3233 | 4.3233 | 4.3233
2021-12-21 12:00 | 1.9319 | 2.351 | 2.3002 | 2.4741 | 2.3437 | 2.5176 | 1.2889 | 2.2103 | 2.7273 | 2.7273 | 3.072 | 3.072 | 2020-02-18 01:00 | 1.5366 | 2.5182 | 4.1336 | 4.1336 | 4.1336 | 4.1336
2021-12-21 13:00 | 1.7919 | 2.1805 | 2.1335 | 2.2948 | 2.1738 | 2.3351 | 1.3689 | 2.3475 | 2.8967 | 2.8967 | 3.2628 | 3.2628 | 2020-02-18 02:00 | 1.5261 | 2.501 | 4.1054 | 4.1054 | 4.1054 | 4.1054
2021-12-21 14:00 | 1.809 | 2.2014 | 2.1539 | 2.3167 | 2.1946 | 2.3574 | 1.4347 | 2.4602 | 3.0357 | 3.0357 | 3.4194 | 3.4194 | 2020-02-18 03:00 | 1.5318 | 2.5104 | 4.1208 | 4.1208 | 4.1208 | 4.1208
2021-12-21 15:00 | 1.8662 | 2.271 | 2.222 | 2.3899 | 2.264 | 2.4319 | 1.3575 | 2.3279 | 2.8725 | 2.8725 | 3.2355 | 3.2355 | 2020-02-18 04:00 | 1.5271 | 2.5026 | 4.108 | 4.108 | 4.108 | 4.108
2021-12-21 16:00 | 2.0389 | 2.4811 | 2.4276 | 2.6111 | 2.4735 | 2.657 | 1.4375 | 2.4651 | 3.0418 | 3.0418 | 3.4262 | 3.4262 | 2020-02-18 05:00 | 1.6804 | 2.7539 | 4.5206 | 4.5206 | 4.5206 | 4.5206
2021-12-21 17:00 | 2.312 | 2.8135 | 2.7528 | 2.9609 | 2.8048 | 3.0129 | 1.5404 | 2.6415 | 3.2595 | 3.2595 | 3.6715 | 3.6715 | 2020-02-18 06:00 | 1.8214 | 2.985 | 4.8999 | 4.8999 | 4.8999 | 4.8999
2021-12-21 18:00 | 2.352 | 2.8622 | 2.8004 | 3.0121 | 2.8534 | 3.065 | 1.7033 | 2.9209 | 3.6042 | 3.6042 | 4.0597 | 4.0597 | 2020-02-18 07:00 | 2.2291 | 3.6532 | 5.9967 | 5.9967 | 5.9967 | 5.9967
2021-12-21 19:00 | 2.3092 | 2.81 | 2.7494 | 2.9572 | 2.8014 | 3.0092 | 1.6461 | 2.8229 | 3.4832 | 3.4832 | 3.9235 | 3.9235 | 2020-02-18 08:00 | 2.5111 | 4.1153 | 6.7553 | 6.7553 | 6.7553 | 6.7553
2021-12-21 20:00 | 2.0691 | 2.5179 | 2.4636 | 2.6498 | 2.5101 | 2.6963 | 1.5918 | 2.7297 | 3.3683 | 3.3683 | 3.7941 | 3.7941 | 2020-02-18 09:00 | 2.6369 | 4.3213 | 7.0935 | 7.0935 | 7.0935 | 7.0935
2021-12-21 21:00 | 2.0415 | 2.4843 | 2.4307 | 2.6145 | 2.4767 | 2.6604 | 1.5175 | 2.6023 | 3.2111 | 3.2111 | 3.617 | 3.617 | 2020-02-18 10:00 | 2.6674 | 4.3713 | 7.1755 | 7.1755 | 7.1755 | 7.1755
2021-12-21 22:00 | 1.8455 | 2.2457 | 2.1973 | 2.3634 | 2.2388 | 2.4049 | 1.2437 | 2.1328 | 2.6318 | 2.6318 | 2.9644 | 2.9644 | 2020-02-18 11:00 | 2.6111 | 4.2792 | 7.0243 | 7.0243 | 7.0243 | 7.0243
2021-12-21 23:00 | 1.5918 | 1.9371 | 1.8953 | 2.0386 | 1.9311 | 2.0744 | 1.1403 | 1.9554 | 2.4129 | 2.4129 | 2.7178 | 2.7178 | 2020-02-18 12:00 | 2.775 | 4.5477 | 7.4651 | 7.4651 | 7.4651 | 7.4651
2021-12-22 | 1.5204 | 1.8502 | 1.8103 | 1.9471 | 1.8445 | 1.9813 | 0.89786 | 1.5397 | 1.8999 | 1.8999 | 2.14 | 2.14 | 2020-02-18 13:00 | 2.8655 | 4.696 | 7.7086 | 7.7086 | 7.7086 | 7.7086
2021-12-22 01:00 | 1.3461 | 1.638 | 1.6027 | 1.7238 | 1.633 | 1.7541 | 0.81735 | 1.4016 | 1.7295 | 1.7295 | 1.9481 | 1.9481 | 2020-02-18 14:00 | 2.8998 | 4.7522 | 7.8008 | 7.8008 | 7.8008 | 7.8008
2021-12-22 02:00 | 1.3603 | 1.6554 | 1.6197 | 1.7421 | 1.6503 | 1.7727 | 0.76591 | 1.3134 | 1.6207 | 1.6207 | 1.8255 | 1.8255 | 2020-02-18 15:00 | 2.8188 | 4.6195 | 7.583 | 7.583 | 7.583 | 7.583
2021-12-22 03:00 | 1.3203 | 1.6067 | 1.5721 | 1.6909 | 1.6018 | 1.7206 | 0.7259 | 1.2448 | 1.536 | 1.536 | 1.7301 | 1.7301 | 2020-02-18 16:00 | 2.8655 | 4.696 | 7.7086 | 7.7086 | 7.7086 | 7.7086
2021-12-22 04:00 | 1.3175 | 1.6032 | 1.5687 | 1.6872 | 1.5983 | 1.7169 | 0.70875 | 1.2154 | 1.4997 | 1.4997 | 1.6893 | 1.6893 | 2020-02-18 17:00 | 2.6683 | 4.3729 | 7.1781 | 7.1781 | 7.1781 | 7.1781
2021-12-22 05:00 | 1.3907 | 1.6923 | 1.6558 | 1.781 | 1.6871 | 1.8123 | 0.70304 | 1.2056 | 1.4876 | 1.4876 | 1.6757 | 1.6757 | 2020-02-18 18:00 | 2.5368 | 4.1574 | 6.8245 | 6.8245 | 6.8245 | 6.8245
2021-12-22 06:00 | 1.5994 | 1.9463 | 1.9043 | 2.0482 | 1.9403 | 2.0842 | 0.7372 | 1.2642 | 1.5599 | 1.5599 | 1.7571 | 1.7571 | 2020-02-18 19:00 | 2.252 | 3.6906 | 6.0582 | 6.0582 | 6.0582 | 6.0582
2021-12-22 07:00 | 1.8376 | 2.2362 | 2.188 | 2.3533 | 2.2293 | 2.3947 | 1.1045 | 1.8941 | 2.3372 | 2.3372 | 2.6326 | 2.6326 | 2020-02-18 20:00 | 2.1291 | 3.4892 | 5.7276 | 5.7276 | 5.7276 | 5.7276
2021-12-22 08:00 | 1.9805 | 2.4101 | 2.3581 | 2.5363 | 2.4026 | 2.5809 | 1.2232 | 2.0975 | 2.5882 | 2.5882 | 2.9154 | 2.9154 | 2020-02-18 21:00 | 2.1139 | 3.4643 | 5.6866 | 5.6866 | 5.6866 | 5.6866
2021-12-22 09:00 | 2.0348 | 2.4762 | 2.4227 | 2.6059 | 2.4685 | 2.6517 | 1.2289 | 2.1073 | 2.6003 | 2.6003 | 2.929 | 2.929 | 2020-02-18 22:00 | 1.8805 | 3.0818 | 5.0588 | 5.0588 | 5.0588 | 5.0588
2021-12-22 10:00 | 2.0462 | 2.4901 | 2.4364 | 2.6205 | 2.4824 | 2.6666 | 1.2773 | 2.1904 | 2.7028 | 2.7028 | 3.0444 | 3.0444 | 2020-02-18 23:00 | 1.6814 | 2.7555 | 4.5232 | 4.5232 | 4.5232 | 4.5232
2021-12-22 11:00 | 2.0405 | 2.4831 | 2.4295 | 2.6132 | 2.4755 | 2.6591 | 1.3689 | 2.3475 | 2.8967 | 2.8967 | 3.2628 | 3.2628 | 2020-02-19 | 1.4985 | 2.4557 | 4.0311 | 4.0311 | 4.0311 | 4.0311
2021-12-22 12:00 | 2.0805 | 2.5318 | 2.4772 | 2.6644 | 2.524 | 2.7112 | 1.3975 | 2.3965 | 2.9571 | 2.9571 | 3.3309 | 3.3309 | 2020-02-19 01:00 | 1.4185 | 2.3246 | 3.8158 | 3.8158 | 3.8158 | 3.8158
2021-12-22 13:00 | 2.0863 | 2.5388 | 2.484 | 2.6718 | 2.5309 | 2.7187 | 1.4318 | 2.4553 | 3.0297 | 3.0297 | 3.4126 | 3.4126 | 2020-02-19 02:00 | 1.4242 | 2.334 | 3.8312 | 3.8312 | 3.8312 | 3.8312
2021-12-22 14:00 | 2.2091 | 2.6883 | 2.6303 | 2.8291 | 2.68 | 2.8788 | 1.5032 | 2.5778 | 3.1809 | 3.1809 | 3.5829 | 3.5829 | 2020-02-19 03:00 | 1.3651 | 2.2372 | 3.6723 | 3.6723 | 3.6723 | 3.6723
2021-12-22 15:00 | 2.1891 | 2.664 | 2.6065 | 2.8035 | 2.6557 | 2.8528 | 1.3804 | 2.3671 | 2.9208 | 2.9208 | 3.29 | 3.29 | 2020-02-19 04:00 | 1.3965 | 2.2887 | 3.7569 | 3.7569 | 3.7569 | 3.7569
2021-12-22 16:00 | 2.3063 | 2.8065 | 2.746 | 2.9536 | 2.7979 | 3.0055 | 1.4947 | 2.5631 | 3.1627 | 3.1627 | 3.5625 | 3.5625 | 2020-02-19 05:00 | 1.4528 | 2.3808 | 3.9081 | 3.9081 | 3.9081 | 3.9081
2021-12-22 17:00 | 2.6007 | 3.1647 | 3.0965 | 3.3305 | 3.155 | 3.3891 | 1.6233 | 2.7837 | 3.4349 | 3.4349 | 3.869 | 3.869 | 2020-02-19 06:00 | 1.6137 | 2.6446 | 4.3412 | 4.3412 | 4.3412 | 4.3412
2021-12-22 18:00 | 2.5892 | 3.1508 | 3.0829 | 3.3159 | 3.1411 | 3.3742 | 1.649 | 2.8278 | 3.4893 | 3.4893 | 3.9303 | 3.9303 | 2020-02-19 07:00 | 1.9719 | 3.2316 | 5.3048 | 5.3048 | 5.3048 | 5.3048
2021-12-22 19:00 | 2.4669 | 3.002 | 2.9372 | 3.1592 | 2.9927 | 3.2147 | 1.6519 | 2.8327 | 3.4953 | 3.4953 | 3.9371 | 3.9371 | 2020-02-19 08:00 | 2.0739 | 3.3987 | 5.579 | 5.579 | 5.579 | 5.579
2021-12-22 20:00 | 2.0434 | 2.4866 | 2.4329 | 2.6169 | 2.4789 | 2.6628 | 1.5375 | 2.6366 | 3.2534 | 3.2534 | 3.6647 | 3.6647 | 2020-02-19 09:00 | 2.1615 | 3.5423 | 5.8148 | 5.8148 | 5.8148 | 5.8148
2021-12-22 21:00 | 1.9339 | 2.3534 | 2.3026 | 2.4767 | 2.3462 | 2.5202 | 1.4804 | 2.5386 | 3.1325 | 3.1325 | 3.5284 | 3.5284 | 2020-02-19 10:00 | 2.1358 | 3.5002 | 5.7456 | 5.7456 | 5.7456 | 5.7456
2021-12-22 22:00 | 1.8462 | 2.2466 | 2.1982 | 2.3643 | 2.2397 | 2.4059 | 1.2375 | 2.122 | 2.6185 | 2.6185 | 2.9494 | 2.9494 | 2020-02-19 11:00 | 2.1672 | 3.5517 | 5.8301 | 5.8301 | 5.8301 | 5.8301
2021-12-22 23:00 | 1.6147 | 1.9649 | 1.9225 | 2.0679 | 1.9589 | 2.1042 | 1.1146 | 1.9113 | 2.3584 | 2.3584 | 2.6565 | 2.6565 | 2020-02-19 12:00 | 2.2834 | 3.7421 | 6.1428 | 6.1428 | 6.1428 | 6.1428
2021-12-23 | 1.4863 | 1.8087 | 1.7696 | 1.9034 | 1.8031 | 1.9368 | 0.93578 | 1.6047 | 1.9801 | 1.9801 | 2.2304 | 2.2304 | 2020-02-19 13:00 | 2.2472 | 3.6828 | 6.0454 | 6.0454 | 6.0454 | 6.0454
2021-12-23 01:00 | 1.3918 | 1.6937 | 1.6571 | 1.7824 | 1.6884 | 1.8137 | 0.81735 | 1.4016 | 1.7295 | 1.7295 | 1.9481 | 1.9481 | 2020-02-19 14:00 | 2.1463 | 3.5173 | 5.7737 | 5.7737 | 5.7737 | 5.7737
2021-12-23 02:00 | 1.3604 | 1.6555 | 1.6198 | 1.7423 | 1.6504 | 1.7729 | 0.7802 | 1.3379 | 1.6509 | 1.6509 | 1.8596 | 1.8596 | 2020-02-19 15:00 | 2.1882 | 3.586 | 5.8865 | 5.8865 | 5.8865 | 5.8865
2021-12-23 03:00 | 1.2803 | 1.558 | 1.5244 | 1.6396 | 1.5532 | 1.6685 | 0.70018 | 1.2007 | 1.4816 | 1.4816 | 1.6688 | 1.6688 | 2020-02-19 16:00 | 2.1377 | 3.5033 | 5.7507 | 5.7507 | 5.7507 | 5.7507
2021-12-23 04:00 | 1.2718 | 1.5476 | 1.5142 | 1.6287 | 1.5428 | 1.6573 | 0.66874 | 1.1468 | 1.4151 | 1.4151 | 1.5939 | 1.5939 | 2020-02-19 17:00 | 2.0196 | 3.3097 | 5.4329 | 5.4329 | 5.4329 | 5.4329
2021-12-23 05:00 | 1.3888 | 1.69 | 1.6536 | 1.7785 | 1.6848 | 1.8098 | 0.66874 | 1.1468 | 1.4151 | 1.4151 | 1.5939 | 1.5939 | 2020-02-19 18:00 | 1.9777 | 3.241 | 5.3202 | 5.3202 | 5.3202 | 5.3202
2021-12-23 06:00 | 1.5633 | 1.9023 | 1.8613 | 2.002 | 1.8965 | 2.0372 | 0.72016 | 1.235 | 1.5239 | 1.5239 | 1.7165 | 1.7165 | 2020-02-19 19:00 | 1.7643 | 2.8913 | 4.7461 | 4.7461 | 4.7461 | 4.7461
2021-12-23 07:00 | 1.7605 | 2.1423 | 2.0961 | 2.2545 | 2.1357 | 2.2941 | 1.0628 | 1.8225 | 2.2489 | 2.2489 | 2.5331 | 2.5331 | 2020-02-19 20:00 | 1.7233 | 2.8242 | 4.6359 | 4.6359 | 4.6359 | 4.6359
2021-12-23 08:00 | 1.9005 | 2.3127 | 2.2628 | 2.4339 | 2.3056 | 2.4766 | 1.1832 | 2.0289 | 2.5036 | 2.5036 | 2.82 | 2.82 | 2020-02-19 21:00 | 1.6919 | 2.7726 | 4.5513 | 4.5513 | 4.5513 | 4.5513
2021-12-23 09:00 | 1.8976 | 2.3092 | 2.2594 | 2.4302 | 2.3021 | 2.4729 | 1.1889 | 2.0387 | 2.5157 | 2.5157 | 2.8336 | 2.8336 | 2020-02-19 22:00 | 1.608 | 2.6353 | 4.3258 | 4.3258 | 4.3258 | 4.3258
2021-12-23 10:00 | 1.8976 | 2.3092 | 2.2594 | 2.4302 | 2.3021 | 2.4729 | 1.2746 | 2.1858 | 2.6971 | 2.6971 | 3.038 | 3.038 | 2020-02-19 23:00 | 1.4813 | 2.4276 | 3.985 | 3.985 | 3.985 | 3.985
2021-12-23 11:00 | 2.1463 | 2.6118 | 2.5554 | 2.7486 | 2.6037 | 2.7969 | 1.3603 | 2.3328 | 2.8785 | 2.8785 | 3.2423 | 3.2423 | 2020-02-20 | 1.3708 | 2.2465 | 3.6877 | 3.6877 | 3.6877 | 3.6877
2021-12-23 12:00 | 2.0605 | 2.5075 | 2.4534 | 2.6388 | 2.4997 | 2.6852 | 1.3804 | 2.3671 | 2.9208 | 2.9208 | 3.29 | 3.29 | 2020-02-20 01:00 | 1.3318 | 2.1825 | 3.5826 | 3.5826 | 3.5826 | 3.5826
2021-12-23 13:00 | 2.1205 | 2.5805 | 2.5248 | 2.7157 | 2.5725 | 2.7634 | 1.4832 | 2.5435 | 3.1385 | 3.1385 | 3.5352 | 3.5352 | 2020-02-20 02:00 | 1.2918 | 2.117 | 3.475 | 3.475 | 3.475 | 3.475
2021-12-23 14:00 | 2.1891 | 2.664 | 2.6065 | 2.8035 | 2.6557 | 2.8528 | 1.5575 | 2.6709 | 3.2958 | 3.2958 | 3.7123 | 3.7123 | 2020-02-20 03:00 | 1.468 | 2.4058 | 3.9491 | 3.9491 | 3.9491 | 3.9491
2021-12-23 15:00 | 2.2291 | 2.7126 | 2.6541 | 2.8547 | 2.7043 | 2.9049 | 1.4146 | 2.4259 | 2.9934 | 2.9934 | 3.3718 | 3.3718 | 2020-02-20 04:00 | 1.307 | 2.1419 | 3.516 | 3.516 | 3.516 | 3.516
2021-12-23 16:00 | 2.2006 | 2.6779 | 2.6201 | 2.8181 | 2.6696 | 2.8677 | 1.4518 | 2.4896 | 3.072 | 3.072 | 3.4603 | 3.4603 | 2020-02-20 05:00 | 1.3899 | 2.2778 | 3.739 | 3.739 | 3.739 | 3.739
2021-12-23 17:00 | 2.4121 | 2.9352 | 2.8719 | 3.089 | 2.9262 | 3.1433 | 1.529 | 2.6219 | 3.2353 | 3.2353 | 3.6442 | 3.6442 | 2020-02-20 06:00 | 1.5471 | 2.5353 | 4.1618 | 4.1618 | 4.1618 | 4.1618
2021-12-23 18:00 | 2.4349 | 2.963 | 2.8991 | 3.1183 | 2.9539 | 3.173 | 1.6404 | 2.8131 | 3.4712 | 3.4712 | 3.9099 | 3.9099 | 2020-02-20 07:00 | 1.8852 | 3.0896 | 5.0716 | 5.0716 | 5.0716 | 5.0716
2021-12-23 19:00 | 2.4035 | 2.9248 | 2.8617 | 3.078 | 2.9158 | 3.1321 | 1.6433 | 2.818 | 3.4772 | 3.4772 | 3.9167 | 3.9167 | 2020-02-20 08:00 | 2.1425 | 3.5111 | 5.7635 | 5.7635 | 5.7635 | 5.7635
2021-12-23 20:00 | 2.052 | 2.497 | 2.4432 | 2.6278 | 2.4893 | 2.674 | 1.5947 | 2.7346 | 3.3744 | 3.3744 | 3.8009 | 3.8009 | 2020-02-20 09:00 | 2.1701 | 3.5564 | 5.8378 | 5.8378 | 5.8378 | 5.8378
2021-12-23 21:00 | 1.9376 | 2.3579 | 2.307 | 2.4814 | 2.3506 | 2.525 | 1.5261 | 2.617 | 3.2293 | 3.2293 | 3.6374 | 3.6374 | 2020-02-20 10:00 | 2.1015 | 3.444 | 5.6533 | 5.6533 | 5.6533 | 5.6533
2021-12-23 22:00 | 1.8034 | 2.1946 | 2.1473 | 2.3096 | 2.1878 | 2.3501 | 1.1917 | 2.0436 | 2.5217 | 2.5217 | 2.8404 | 2.8404 | 2020-02-20 11:00 | 2.2225 | 3.6422 | 5.9788 | 5.9788 | 5.9788 | 5.9788
2021-12-23 23:00 | 1.5661 | 1.9058 | 1.8647 | 2.0056 | 1.8999 | 2.0409 | 1.0517 | 1.8035 | 2.2254 | 2.2254 | 2.5067 | 2.5067 | 2020-02-20 12:00 | 2.3054 | 3.778 | 6.2017 | 6.2017 | 6.2017 | 6.2017
2021-12-24 | 1.4489 | 1.7632 | 1.7252 | 1.8556 | 1.7578 | 1.8882 | 0.92386 | 1.5843 | 1.9549 | 1.9549 | 2.202 | 2.202 | 2020-02-20 13:00 | 2.2634 | 3.7094 | 6.089 | 6.089 | 6.089 | 6.089
2021-12-24 01:00 | 1.3661 | 1.6624 | 1.6265 | 1.7494 | 1.6572 | 1.7802 | 0.76603 | 1.3136 | 1.6209 | 1.6209 | 1.8258 | 1.8258 | 2020-02-20 14:00 | 2.2815 | 3.739 | 6.1377 | 6.1377 | 6.1377 | 6.1377
2021-12-24 02:00 | 1.3142 | 1.5993 | 1.5648 | 1.6831 | 1.5944 | 1.7127 | 0.72876 | 1.2497 | 1.5421 | 1.5421 | 1.737 | 1.737 | 2020-02-20 15:00 | 2.333 | 3.8233 | 6.276 | 6.276 | 6.276 | 6.276
2021-12-24 03:00 | 1.3289 | 1.6171 | 1.5823 | 1.7019 | 1.6122 | 1.7318 | 0.72018 | 1.235 | 1.5239 | 1.5239 | 1.7165 | 1.7165 | 2020-02-20 16:00 | 2.273 | 3.725 | 6.1146 | 6.1146 | 6.1146 | 6.1146
2021-12-24 04:00 | 1.2946 | 1.5754 | 1.5414 | 1.6579 | 1.5706 | 1.6871 | 0.68875 | 1.1811 | 1.4574 | 1.4574 | 1.6416 | 1.6416 | 2020-02-20 17:00 | 2.1958 | 3.5985 | 5.907 | 5.907 | 5.907 | 5.907
2021-12-24 05:00 | 1.4089 | 1.7145 | 1.6775 | 1.8043 | 1.7092 | 1.836 | 0.70875 | 1.2154 | 1.4997 | 1.4997 | 1.6893 | 1.6893 | 2020-02-20 18:00 | 2.0691 | 3.3909 | 5.5662 | 5.5662 | 5.5662 | 5.5662
2021-12-24 06:00 | 1.4347 | 1.7458 | 1.7082 | 1.8373 | 1.7404 | 1.8696 | 0.72876 | 1.2497 | 1.5421 | 1.5421 | 1.737 | 1.737 | 2020-02-20 19:00 | 1.9243 | 3.1536 | 5.1766 | 5.1766 | 5.1766 | 5.1766
2021-12-24 07:00 | 1.7033 | 2.0727 | 2.028 | 2.1813 | 2.0663 | 2.2196 | 1.0746 | 1.8427 | 2.2738 | 2.2738 | 2.5612 | 2.5612 | 2020-02-20 20:00 | 1.8367 | 3.0099 | 4.9409 | 4.9409 | 4.9409 | 4.9409
2021-12-24 08:00 | 1.8176 | 2.2118 | 2.1641 | 2.3277 | 2.205 | 2.3686 | 1.126 | 1.9309 | 2.3826 | 2.3826 | 2.6838 | 2.6838 | 2020-02-20 21:00 | 1.7214 | 2.821 | 4.6308 | 4.6308 | 4.6308 | 4.6308
2021-12-24 09:00 | 1.8005 | 2.191 | 2.1437 | 2.3058 | 2.1842 | 2.3463 | 1.1974 | 2.0534 | 2.5338 | 2.5338 | 2.8541 | 2.8541 | 2020-02-20 22:00 | 1.5995 | 2.6212 | 4.3028 | 4.3028 | 4.3028 | 4.3028
2021-12-24 10:00 | 1.9227 | 2.3397 | 2.2892 | 2.4622 | 2.3325 | 2.5055 | 1.2746 | 2.1858 | 2.6971 | 2.6971 | 3.038 | 3.038 | 2020-02-20 23:00 | 1.4585 | 2.3902 | 3.9235 | 3.9235 | 3.9235 | 3.9235
2021-12-24 11:00 | 1.9291 | 2.3475 | 2.2968 | 2.4705 | 2.3402 | 2.5139 | 1.3461 | 2.3083 | 2.8483 | 2.8483 | 3.2083 | 3.2083 | 2020-02-21 | 1.3232 | 2.1685 | 3.5596 | 3.5596 | 3.5596 | 3.5596
2021-12-24 12:00 | 1.7464 | 2.1252 | 2.0794 | 2.2366 | 2.1187 | 2.2759 | 1.2775 | 2.1907 | 2.7031 | 2.7031 | 3.0448 | 3.0448 | 2020-02-21 01:00 | 1.3375 | 2.1919 | 3.598 | 3.598 | 3.598 | 3.598
2021-12-24 13:00 | 1.7233 | 2.0971 | 2.0518 | 2.2069 | 2.0906 | 2.2457 | 1.3603 | 2.3328 | 2.8785 | 2.8785 | 3.2423 | 3.2423 | 2020-02-21 02:00 | 1.2937 | 2.1201 | 3.4801 | 3.4801 | 3.4801 | 3.4801
2021-12-24 14:00 | 1.609 | 1.958 | 1.9157 | 2.0605 | 1.9519 | 2.0967 | 1.3232 | 2.2691 | 2.7999 | 2.7999 | 3.1538 | 3.1538 | 2020-02-21 03:00 | 1.3994 | 2.2934 | 3.7646 | 3.7646 | 3.7646 | 3.7646
2021-12-24 15:00 | 1.7719 | 2.1562 | 2.1097 | 2.2692 | 2.1496 | 2.309 | 1.3318 | 2.2838 | 2.818 | 2.818 | 3.1742 | 3.1742 | 2020-02-21 04:00 | 1.4004 | 2.2949 | 3.7672 | 3.7672 | 3.7672 | 3.7672
2021-12-24 16:00 | 1.9977 | 2.4309 | 2.3785 | 2.5583 | 2.4235 | 2.6032 | 1.3804 | 2.3671 | 2.9208 | 2.9208 | 3.29 | 3.29 | 2020-02-21 05:00 | 1.387 | 2.2731 | 3.7313 | 3.7313 | 3.7313 | 3.7313
2021-12-24 17:00 | 2.0891 | 2.5422 | 2.4874 | 2.6754 | 2.5344 | 2.7224 | 1.3575 | 2.3279 | 2.8725 | 2.8725 | 3.2355 | 3.2355 | 2020-02-21 06:00 | 1.7766 | 2.9116 | 4.7794 | 4.7794 | 4.7794 | 4.7794
2021-12-24 18:00 | 2.1663 | 2.6361 | 2.5793 | 2.7742 | 2.628 | 2.823 | 1.4318 | 2.4553 | 3.0297 | 3.0297 | 3.4126 | 3.4126 | 2020-02-21 07:00 | 2.0243 | 3.3175 | 5.4457 | 5.4457 | 5.4457 | 5.4457
2021-12-24 19:00 | 2.0391 | 2.4814 | 2.4279 | 2.6114 | 2.4738 | 2.6573 | 1.3889 | 2.3818 | 2.939 | 2.939 | 3.3105 | 3.3105 | 2020-02-21 08:00 | 2.1215 | 3.4767 | 5.7071 | 5.7071 | 5.7071 | 5.7071
2021-12-24 20:00 | 1.8948 | 2.3057 | 2.256 | 2.4265 | 2.2986 | 2.4692 | 1.3832 | 2.372 | 2.9269 | 2.9269 | 3.2968 | 3.2968 | 2020-02-21 09:00 | 2.1015 | 3.444 | 5.6533 | 5.6533 | 5.6533 | 5.6533
2021-12-24 21:00 | 1.8033 | 2.1945 | 2.1471 | 2.3094 | 2.1877 | 2.35 | 1.3403 | 2.2985 | 2.8362 | 2.8362 | 3.1947 | 3.1947 | 2020-02-21 10:00 | 2.171 | 3.5579 | 5.8404 | 5.8404 | 5.8404 | 5.8404
2021-12-24 22:00 | 1.7119 | 2.0832 | 2.0382 | 2.1923 | 2.0767 | 2.2308 | 1.1203 | 1.9211 | 2.3705 | 2.3705 | 2.6702 | 2.6702 | 2020-02-21 11:00 | 2.1587 | 3.5376 | 5.8071 | 5.8071 | 5.8071 | 5.8071
2021-12-24 23:00 | 1.5591 | 1.8973 | 1.8564 | 1.9967 | 1.8914 | 2.0318 | 1.0603 | 1.8183 | 2.2437 | 2.2437 | 2.5272 | 2.5272 | 2020-02-21 12:00 | 2.1787 | 3.5704 | 5.8609 | 5.8609 | 5.8609 | 5.8609
2021-12-25 | 1.5061 | 1.8328 | 1.7932 | 1.9288 | 1.8271 | 1.9627 | 0.89451 | 1.5339 | 1.8928 | 1.8928 | 2.132 | 2.132 | 2020-02-21 13:00 | 2.273 | 3.725 | 6.1146 | 6.1146 | 6.1146 | 6.1146
2021-12-25 01:00 | 1.3262 | 1.6138 | 1.579 | 1.6984 | 1.6089 | 1.7282 | 0.80306 | 1.3771 | 1.6993 | 1.6993 | 1.9141 | 1.9141 | 2020-02-21 14:00 | 2.2806 | 3.7375 | 6.1351 | 6.1351 | 6.1351 | 6.1351
2021-12-25 02:00 | 1.2489 | 1.5198 | 1.487 | 1.5994 | 1.5151 | 1.6275 | 0.78591 | 1.3477 | 1.663 | 1.663 | 1.8732 | 1.8732 | 2020-02-21 15:00 | 2.3177 | 3.7983 | 6.235 | 6.235 | 6.235 | 6.235
2021-12-25 03:00 | 1.226 | 1.492 | 1.4598 | 1.5701 | 1.4874 | 1.5977 | 0.72876 | 1.2497 | 1.5421 | 1.5421 | 1.737 | 1.737 | 2020-02-21 16:00 | 2.3806 | 3.9014 | 6.4042 | 6.4042 | 6.4042 | 6.4042
2021-12-25 04:00 | 1.2575 | 1.5302 | 1.4972 | 1.6104 | 1.5255 | 1.6387 | 0.70304 | 1.2056 | 1.4876 | 1.4876 | 1.6757 | 1.6757 | 2020-02-21 17:00 | 2.3149 | 3.7937 | 6.2273 | 6.2273 | 6.2273 | 6.2273
2021-12-25 05:00 | 1.2603 | 1.5337 | 1.5006 | 1.614 | 1.529 | 1.6424 | 0.66303 | 1.137 | 1.403 | 1.403 | 1.5803 | 1.5803 | 2020-02-21 18:00 | 2.1339 | 3.497 | 5.7404 | 5.7404 | 5.7404 | 5.7404
2021-12-25 06:00 | 1.274 | 1.5503 | 1.5168 | 1.6315 | 1.5455 | 1.6602 | 0.6916 | 1.186 | 1.4634 | 1.4634 | 1.6484 | 1.6484 | 2020-02-21 19:00 | 1.8481 | 3.0287 | 4.9716 | 4.9716 | 4.9716 | 4.9716
2021-12-25 07:00 | 1.3832 | 1.6832 | 1.6469 | 1.7714 | 1.678 | 1.8025 | 0.78757 | 1.3506 | 1.6665 | 1.6665 | 1.8772 | 1.8772 | 2020-02-21 20:00 | 1.8433 | 3.0209 | 4.9588 | 4.9588 | 4.9588 | 4.9588
2021-12-25 08:00 | 1.4518 | 1.7667 | 1.7286 | 1.8592 | 1.7612 | 1.8919 | 0.82592 | 1.4163 | 1.7477 | 1.7477 | 1.9686 | 1.9686 | 2020-02-21 21:00 | 1.7357 | 2.8445 | 4.6692 | 4.6692 | 4.6692 | 4.6692
2021-12-25 09:00 | 1.5542 | 1.8912 | 1.8504 | 1.9903 | 1.8854 | 2.0253 | 0.92881 | 1.5928 | 1.9654 | 1.9654 | 2.2138 | 2.2138 | 2020-02-21 22:00 | 1.6299 | 2.6712 | 4.3848 | 4.3848 | 4.3848 | 4.3848
2021-12-25 10:00 | 1.7233 | 2.0971 | 2.0518 | 2.2069 | 2.0906 | 2.2457 | 0.95739 | 1.6418 | 2.0258 | 2.0258 | 2.2819 | 2.2819 | 2020-02-21 23:00 | 1.5804 | 2.59 | 4.2515 | 4.2515 | 4.2515 | 4.2515
2021-12-25 11:00 | 1.7662 | 2.1492 | 2.1029 | 2.2618 | 2.1426 | 2.3016 | 1.0174 | 1.7447 | 2.1528 | 2.1528 | 2.4249 | 2.4249 | 2020-02-22 | 1.4632 | 2.398 | 3.9363 | 3.9363 | 3.9363 | 3.9363
2021-12-25 12:00 | 1.7376 | 2.1145 | 2.0689 | 2.2252 | 2.108 | 2.2643 | 0.99718 | 1.71 | 2.1101 | 2.1101 | 2.3767 | 2.3767 | 2020-02-22 01:00 | 1.4556 | 2.3855 | 3.9158 | 3.9158 | 3.9158 | 3.9158
2021-12-25 13:00 | 1.7605 | 2.1423 | 2.0961 | 2.2545 | 2.1357 | 2.2941 | 1.0746 | 1.8427 | 2.2738 | 2.2738 | 2.5612 | 2.5612 | 2020-02-22 02:00 | 1.3918 | 2.2809 | 3.7441 | 3.7441 | 3.7441 | 3.7441
2021-12-25 14:00 | 1.7519 | 2.1319 | 2.0859 | 2.2435 | 2.1253 | 2.283 | 0.97453 | 1.6712 | 2.0621 | 2.0621 | 2.3228 | 2.3228 | 2020-02-22 03:00 | 1.3746 | 2.2528 | 3.698 | 3.698 | 3.698 | 3.698
2021-12-25 15:00 | 1.8405 | 2.2397 | 2.1914 | 2.357 | 2.2328 | 2.3984 | 0.98025 | 1.681 | 2.0742 | 2.0742 | 2.3364 | 2.3364 | 2020-02-22 04:00 | 1.3632 | 2.234 | 3.6672 | 3.6672 | 3.6672 | 3.6672
2021-12-25 16:00 | 1.7719 | 2.1562 | 2.1097 | 2.2692 | 2.1496 | 2.309 | 0.97739 | 1.6761 | 2.0682 | 2.0682 | 2.3296 | 2.3296 | 2020-02-22 05:00 | 1.3861 | 2.2715 | 3.7287 | 3.7287 | 3.7287 | 3.7287
2021-12-25 17:00 | 1.6833 | 2.0484 | 2.0042 | 2.1557 | 2.0421 | 2.1936 | 0.99168 | 1.7006 | 2.0984 | 2.0984 | 2.3636 | 2.3636 | 2020-02-22 06:00 | 1.368 | 2.2418 | 3.68 | 3.68 | 3.68 | 3.68
2021-12-25 18:00 | 1.6804 | 2.0449 | 2.0008 | 2.152 | 2.0386 | 2.1898 | 1.0088 | 1.73 | 2.1347 | 2.1347 | 2.4045 | 2.4045 | 2020-02-22 07:00 | 1.7023 | 2.7898 | 4.5795 | 4.5795 | 4.5795 | 4.5795
2021-12-25 19:00 | 1.6604 | 2.0206 | 1.977 | 2.1264 | 2.0143 | 2.1638 | 1.026 | 1.7594 | 2.171 | 2.171 | 2.4454 | 2.4454 | 2020-02-22 08:00 | 1.8586 | 3.0459 | 4.9998 | 4.9998 | 4.9998 | 4.9998
2021-12-25 20:00 | 1.669 | 2.031 | 1.9872 | 2.1374 | 2.0247 | 2.175 | 1.0488 | 1.7986 | 2.2194 | 2.2194 | 2.4999 | 2.4999 | 2020-02-22 09:00 | 1.8919 | 3.1005 | 5.0895 | 5.0895 | 5.0895 | 5.0895
2021-12-25 21:00 | 1.7262 | 2.1006 | 2.0552 | 2.2106 | 2.0941 | 2.2494 | 1.0346 | 1.7741 | 2.1891 | 2.1891 | 2.4658 | 2.4658 | 2020-02-22 10:00 | 1.8767 | 3.0755 | 5.0485 | 5.0485 | 5.0485 | 5.0485
2021-12-25 22:00 | 1.5918 | 1.9371 | 1.8953 | 2.0386 | 1.9311 | 2.0744 | 0.94881 | 1.6271 | 2.0077 | 2.0077 | 2.2615 | 2.2615 | 2020-02-22 11:00 | 1.971 | 3.2301 | 5.3022 | 5.3022 | 5.3022 | 5.3022
2021-12-25 23:00 | 1.5612 | 1.8998 | 1.8588 | 1.9994 | 1.894 | 2.0345 | 0.93167 | 1.5977 | 1.9714 | 1.9714 | 2.2206 | 2.2206 | 2020-02-22 12:00 | 1.9777 | 3.241 | 5.3202 | 5.3202 | 5.3202 | 5.3202
2021-12-26 | 1.4432 | 1.7563 | 1.7184 | 1.8483 | 1.7508 | 1.8807 | 0.84322 | 1.446 | 1.7843 | 1.7843 | 2.0098 | 2.0098 | 2020-02-22 13:00 | 1.99 | 3.2613 | 5.3535 | 5.3535 | 5.3535 | 5.3535
2021-12-26 01:00 | 1.3176 | 1.6034 | 1.5688 | 1.6874 | 1.5984 | 1.717 | 0.75448 | 1.2938 | 1.5965 | 1.5965 | 1.7983 | 1.7983 | 2020-02-22 14:00 | 2.0243 | 3.3175 | 5.4457 | 5.4457 | 5.4457 | 5.4457
2021-12-26 02:00 | 1.2715 | 1.5473 | 1.5139 | 1.6284 | 1.5425 | 1.657 | 0.74876 | 1.284 | 1.5844 | 1.5844 | 1.7846 | 1.7846 | 2020-02-22 15:00 | 1.9891 | 3.2597 | 5.3509 | 5.3509 | 5.3509 | 5.3509
2021-12-26 03:00 | 1.2918 | 1.5719 | 1.538 | 1.6543 | 1.5671 | 1.6834 | 0.66013 | 1.132 | 1.3968 | 1.3968 | 1.5734 | 1.5734 | 2020-02-22 16:00 | 2.0539 | 3.3659 | 5.5252 | 5.5252 | 5.5252 | 5.5252
2021-12-26 04:00 | 1.2517 | 1.5232 | 1.4904 | 1.603 | 1.5186 | 1.6312 | 0.66017 | 1.1321 | 1.3969 | 1.3969 | 1.5735 | 1.5735 | 2020-02-22 17:00 | 1.9443 | 3.1864 | 5.2305 | 5.2305 | 5.2305 | 5.2305
2021-12-26 05:00 | 1.2117 | 1.4746 | 1.4428 | 1.5518 | 1.47 | 1.5791 | 0.66017 | 1.1321 | 1.3969 | 1.3969 | 1.5735 | 1.5735 | 2020-02-22 18:00 | 1.8033 | 2.9553 | 4.8512 | 4.8512 | 4.8512 | 4.8512
2021-12-26 06:00 | 1.2199 | 1.4845 | 1.4525 | 1.5623 | 1.4799 | 1.5897 | 0.71161 | 1.2203 | 1.5058 | 1.5058 | 1.6961 | 1.6961 | 2020-02-22 19:00 | 1.6795 | 2.7524 | 4.518 | 4.518 | 4.518 | 4.518
2021-12-26 07:00 | 1.2375 | 1.5059 | 1.4734 | 1.5847 | 1.5012 | 1.6126 | 0.97739 | 1.6761 | 2.0682 | 2.0682 | 2.3296 | 2.3296 | 2020-02-22 20:00 | 1.7357 | 2.8445 | 4.6692 | 4.6692 | 4.6692 | 4.6692
2021-12-26 08:00 | 1.3414 | 1.6323 | 1.5971 | 1.7178 | 1.6273 | 1.748 | 1.0946 | 1.877 | 2.3161 | 2.3161 | 2.6089 | 2.6089 | 2020-02-22 21:00 | 1.6623 | 2.7243 | 4.4719 | 4.4719 | 4.4719 | 4.4719
2021-12-26 09:00 | 1.3889 | 1.6902 | 1.6537 | 1.7787 | 1.685 | 1.81 | 1.2375 | 2.122 | 2.6185 | 2.6185 | 2.9494 | 2.9494 | 2020-02-22 22:00 | 1.6014 | 2.6243 | 4.3079 | 4.3079 | 4.3079 | 4.3079
2021-12-26 10:00 | 1.4832 | 1.8049 | 1.766 | 1.8995 | 1.7994 | 1.9329 | 1.3118 | 2.2495 | 2.7757 | 2.7757 | 3.1265 | 3.1265 | 2020-02-22 23:00 | 1.5594 | 2.5556 | 4.1951 | 4.1951 | 4.1951 | 4.1951
2021-12-26 11:00 | 1.489 | 1.8119 | 1.7728 | 1.9068 | 1.8063 | 1.9403 | 1.4204 | 2.4357 | 3.0055 | 3.0055 | 3.3854 | 3.3854 | 2020-02-23 | 1.4366 | 2.3543 | 3.8645 | 3.8645 | 3.8645 | 3.8645
2021-12-26 12:00 | 1.4718 | 1.791 | 1.7524 | 1.8849 | 1.7855 | 1.918 | 1.4575 | 2.4994 | 3.0841 | 3.0841 | 3.4739 | 3.4739 | 2020-02-23 01:00 | 1.3889 | 2.2762 | 3.7364 | 3.7364 | 3.7364 | 3.7364
2021-12-26 13:00 | 1.3689 | 1.6658 | 1.6299 | 1.7531 | 1.6607 | 1.7839 | 1.4175 | 2.4308 | 2.9995 | 2.9995 | 3.3786 | 3.3786 | 2020-02-23 02:00 | 1.3413 | 2.1981 | 3.6083 | 3.6083 | 3.6083 | 3.6083
2021-12-26 14:00 | 1.5947 | 1.9406 | 1.8987 | 2.0422 | 1.9346 | 2.0781 | 1.3775 | 2.3622 | 2.9148 | 2.9148 | 3.2832 | 3.2832 | 2020-02-23 03:00 | 1.3651 | 2.2372 | 3.6723 | 3.6723 | 3.6723 | 3.6723
2021-12-26 15:00 | 1.6547 | 2.0136 | 1.9702 | 2.1191 | 2.0074 | 2.1563 | 1.3918 | 2.3867 | 2.945 | 2.945 | 3.3173 | 3.3173 | 2020-02-23 04:00 | 1.3403 | 2.1966 | 3.6057 | 3.6057 | 3.6057 | 3.6057
2021-12-26 16:00 | 1.5412 | 1.8755 | 1.8351 | 1.9738 | 1.8698 | 2.0085 | 1.3603 | 2.3328 | 2.8785 | 2.8785 | 3.2423 | 3.2423 | 2020-02-23 05:00 | 1.3746 | 2.2528 | 3.698 | 3.698 | 3.698 | 3.698
2021-12-26 17:00 | 1.5518 | 1.8884 | 1.8477 | 1.9873 | 1.8826 | 2.0223 | 1.4604 | 2.5043 | 3.0902 | 3.0902 | 3.4807 | 3.4807 | 2020-02-23 06:00 | 1.467 | 2.4042 | 3.9465 | 3.9465 | 3.9465 | 3.9465
2021-12-26 18:00 | 1.6376 | 1.9927 | 1.9498 | 2.0971 | 1.9866 | 2.134 | 1.4347 | 2.4602 | 3.0357 | 3.0357 | 3.4194 | 3.4194 | 2020-02-23 07:00 | 1.6795 | 2.7524 | 4.518 | 4.518 | 4.518 | 4.518
2021-12-26 19:00 | 1.5775 | 1.9197 | 1.8783 | 2.0203 | 1.9138 | 2.0558 | 1.4175 | 2.4308 | 2.9995 | 2.9995 | 3.3786 | 3.3786 | 2020-02-23 08:00 | 1.8471 | 3.0271 | 4.9691 | 4.9691 | 4.9691 | 4.9691
2021-12-26 20:00 | 1.587 | 1.9312 | 1.8896 | 2.0324 | 1.9253 | 2.0681 | 1.4261 | 2.4455 | 3.0176 | 3.0176 | 3.399 | 3.399 | 2020-02-23 09:00 | 1.9005 | 3.1145 | 5.1126 | 5.1126 | 5.1126 | 5.1126
2021-12-26 21:00 | 1.589 | 1.9336 | 1.8919 | 2.0349 | 1.9277 | 2.0707 | 1.3232 | 2.2691 | 2.7999 | 2.7999 | 3.1538 | 3.1538 | 2020-02-23 10:00 | 1.9167 | 3.1411 | 5.1561 | 5.1561 | 5.1561 | 5.1561
2021-12-26 22:00 | 1.474 | 1.7937 | 1.755 | 1.8876 | 1.7881 | 1.9208 | 1.1231 | 1.926 | 2.3766 | 2.3766 | 2.677 | 2.677 | 2020-02-23 11:00 | 2.132 | 3.4939 | 5.7353 | 5.7353 | 5.7353 | 5.7353
2021-12-26 23:00 | 1.4575 | 1.7736 | 1.7354 | 1.8666 | 1.7682 | 1.8994 | 0.93202 | 1.5983 | 1.9722 | 1.9722 | 2.2214 | 2.2214 | 2020-02-23 12:00 | 2.0462 | 3.3534 | 5.5047 | 5.5047 | 5.5047 | 5.5047
2021-12-27 | 1.3721 | 1.6697 | 1.6336 | 1.7571 | 1.6645 | 1.788 | 0.81782 | 1.4024 | 1.7305 | 1.7305 | 1.9492 | 1.9492 | 2020-02-23 13:00 | 2.1234 | 3.4799 | 5.7122 | 5.7122 | 5.7122 | 5.7122
2021-12-27 01:00 | 1.2975 | 1.579 | 1.5449 | 1.6617 | 1.5741 | 1.6909 | 0.76034 | 1.3039 | 1.6089 | 1.6089 | 1.8122 | 1.8122 | 2020-02-23 14:00 | 2.0434 | 3.3487 | 5.497 | 5.497 | 5.497 | 5.497
2021-12-27 02:00 | 1.2775 | 1.5545 | 1.521 | 1.636 | 1.5498 | 1.6647 | 0.73733 | 1.2644 | 1.5602 | 1.5602 | 1.7574 | 1.7574 | 2020-02-23 15:00 | 2.0853 | 3.4174 | 5.6097 | 5.6097 | 5.6097 | 5.6097
2021-12-27 03:00 | 1.2262 | 1.4922 | 1.46 | 1.5703 | 1.4876 | 1.5979 | 0.70875 | 1.2154 | 1.4997 | 1.4997 | 1.6893 | 1.6893 | 2020-02-23 16:00 | 2.0615 | 3.3784 | 5.5457 | 5.5457 | 5.5457 | 5.5457
2021-12-27 04:00 | 1.246 | 1.5163 | 1.4836 | 1.5957 | 1.5116 | 1.6238 | 0.68174 | 1.1691 | 1.4426 | 1.4426 | 1.6249 | 1.6249 | 2020-02-23 17:00 | 1.9891 | 3.2597 | 5.3509 | 5.3509 | 5.3509 | 5.3509
2021-12-27 05:00 | 1.2346 | 1.5024 | 1.47 | 1.5811 | 1.4978 | 1.6089 | 0.64302 | 1.1027 | 1.3606 | 1.3606 | 1.5326 | 1.5326 | 2020-02-23 18:00 | 1.9272 | 3.1583 | 5.1843 | 5.1843 | 5.1843 | 5.1843
2021-12-27 06:00 | 1.246 | 1.5163 | 1.4836 | 1.5957 | 1.5116 | 1.6238 | 0.62873 | 1.0782 | 1.3304 | 1.3304 | 1.4986 | 1.4986 | 2020-02-23 19:00 | 1.8138 | 2.9725 | 4.8794 | 4.8794 | 4.8794 | 4.8794
2021-12-27 07:00 | 1.3338 | 1.6231 | 1.5881 | 1.7081 | 1.6181 | 1.7381 | 0.91906 | 1.576 | 1.9447 | 1.9447 | 2.1905 | 2.1905 | 2020-02-23 20:00 | 1.7452 | 2.8601 | 4.6949 | 4.6949 | 4.6949 | 4.6949
2021-12-27 08:00 | 1.4432 | 1.7563 | 1.7184 | 1.8483 | 1.7508 | 1.8807 | 1.0288 | 1.7643 | 2.177 | 2.177 | 2.4522 | 2.4522 | 2020-02-23 21:00 | 1.7004 | 2.7867 | 4.5744 | 4.5744 | 4.5744 | 4.5744
2021-12-27 09:00 | 1.5433 | 1.878 | 1.8375 | 1.9764 | 1.8722 | 2.0111 | 1.2232 | 2.0975 | 2.5882 | 2.5882 | 2.9154 | 2.9154 | 2020-02-23 22:00 | 1.6099 | 2.6384 | 4.331 | 4.331 | 4.331 | 4.331
2021-12-27 10:00 | 1.5947 | 1.9406 | 1.8987 | 2.0422 | 1.9346 | 2.0781 | 1.2718 | 2.1809 | 2.691 | 2.691 | 3.0312 | 3.0312 | 2020-02-23 23:00 | 1.5394 | 2.5229 | 4.1413 | 4.1413 | 4.1413 | 4.1413
2021-12-27 11:00 | 1.5105 | 1.8381 | 1.7985 | 1.9344 | 1.8325 | 1.9684 | 1.2432 | 2.1318 | 2.6306 | 2.6306 | 2.9631 | 2.9631 | 2020-02-24 | 1.4375 | 2.3558 | 3.8671 | 3.8671 | 3.8671 | 3.8671
2021-12-27 12:00 | 1.6033 | 1.951 | 1.9089 | 2.0532 | 1.945 | 2.0893 | 1.3232 | 2.2691 | 2.7999 | 2.7999 | 3.1538 | 3.1538 | 2020-02-24 01:00 | 1.3842 | 2.2684 | 3.7236 | 3.7236 | 3.7236 | 3.7236
2021-12-27 13:00 | 1.4001 | 1.7038 | 1.667 | 1.793 | 1.6985 | 1.8245 | 1.3175 | 2.2593 | 2.7878 | 2.7878 | 3.1402 | 3.1402 | 2020-02-24 02:00 | 1.3546 | 2.22 | 3.6441 | 3.6441 | 3.6441 | 3.6441
2021-12-27 14:00 | 1.3918 | 1.6937 | 1.6571 | 1.7824 | 1.6884 | 1.8137 | 1.2951 | 2.2209 | 2.7404 | 2.7404 | 3.0868 | 3.0868 | 2020-02-24 03:00 | 1.3832 | 2.2668 | 3.721 | 3.721 | 3.721 | 3.721
2021-12-27 15:00 | 1.4232 | 1.7319 | 1.6946 | 1.8226 | 1.7266 | 1.8547 | 1.2889 | 2.2103 | 2.7273 | 2.7273 | 3.072 | 3.072 | 2020-02-24 04:00 | 1.408 | 2.3074 | 3.7877 | 3.7877 | 3.7877 | 3.7877
2021-12-27 16:00 | 1.4375 | 1.7493 | 1.7116 | 1.8409 | 1.7439 | 1.8733 | 1.3032 | 2.2348 | 2.7576 | 2.7576 | 3.1061 | 3.1061 | 2020-02-24 05:00 | 1.4985 | 2.4557 | 4.0311 | 4.0311 | 4.0311 | 4.0311
2021-12-27 17:00 | 1.509 | 1.8362 | 1.7966 | 1.9324 | 1.8306 | 1.9664 | 1.3632 | 2.3377 | 2.8846 | 2.8846 | 3.2491 | 3.2491 | 2020-02-24 06:00 | 1.6004 | 2.6228 | 4.3053 | 4.3053 | 4.3053 | 4.3053
2021-12-27 18:00 | 1.6147 | 1.9649 | 1.9225 | 2.0679 | 1.9589 | 2.1042 | 1.4518 | 2.4896 | 3.072 | 3.072 | 3.4603 | 3.4603 | 2020-02-24 07:00 | 2.0148 | 3.3019 | 5.4201 | 5.4201 | 5.4201 | 5.4201
2021-12-27 19:00 | 1.629 | 1.9823 | 1.9396 | 2.0862 | 1.9762 | 2.1228 | 1.4347 | 2.4602 | 3.0357 | 3.0357 | 3.4194 | 3.4194 | 2020-02-24 08:00 | 2.2492 | 3.6859 | 6.0505 | 6.0505 | 6.0505 | 6.0505
2021-12-27 20:00 | 1.629 | 1.9823 | 1.9396 | 2.0862 | 1.9762 | 2.1228 | 1.3603 | 2.3328 | 2.8785 | 2.8785 | 3.2423 | 3.2423 | 2020-02-24 09:00 | 2.2854 | 3.7453 | 6.1479 | 6.1479 | 6.1479 | 6.1479
2021-12-27 21:00 | 1.629 | 1.9823 | 1.9396 | 2.0862 | 1.9762 | 2.1228 | 1.2375 | 2.122 | 2.6185 | 2.6185 | 2.9494 | 2.9494 | 2020-02-24 10:00 | 2.3568 | 3.8624 | 6.3401 | 6.3401 | 6.3401 | 6.3401
2021-12-27 22:00 | 1.5747 | 1.9162 | 1.8749 | 2.0166 | 1.9103 | 2.0521 | 1.1093 | 1.9022 | 2.3473 | 2.3473 | 2.6439 | 2.6439 | 2020-02-24 11:00 | 2.5673 | 4.2074 | 6.9065 | 6.9065 | 6.9065 | 6.9065
2021-12-27 23:00 | 1.5232 | 1.8536 | 1.8137 | 1.9507 | 1.8479 | 1.985 | 1.0231 | 1.7545 | 2.1649 | 2.1649 | 2.4386 | 2.4386 | 2020-02-24 12:00 | 2.5006 | 4.0981 | 6.7271 | 6.7271 | 6.7271 | 6.7271
2021-12-28 | 1.4175 | 1.725 | 1.6878 | 1.8153 | 1.7196 | 1.8472 | 0.90988 | 1.5603 | 1.9253 | 1.9253 | 2.1687 | 2.1687 | 2020-02-24 13:00 | 2.5921 | 4.248 | 6.9731 | 6.9731 | 6.9731 | 6.9731
2021-12-28 01:00 | 1.3483 | 1.6407 | 1.6053 | 1.7267 | 1.6357 | 1.757 | 0.76891 | 1.3186 | 1.627 | 1.627 | 1.8327 | 1.8327 | 2020-02-24 14:00 | 2.6388 | 4.3245 | 7.0987 | 7.0987 | 7.0987 | 7.0987
2021-12-28 02:00 | 1.2803 | 1.558 | 1.5244 | 1.6396 | 1.5532 | 1.6685 | 0.71733 | 1.2301 | 1.5179 | 1.5179 | 1.7097 | 1.7097 | 2020-02-24 15:00 | 2.5445 | 4.1699 | 6.845 | 6.845 | 6.845 | 6.845
2021-12-28 03:00 | 1.2517 | 1.5232 | 1.4904 | 1.603 | 1.5186 | 1.6312 | 0.6916 | 1.186 | 1.4634 | 1.4634 | 1.6484 | 1.6484 | 2020-02-24 16:00 | 2.5006 | 4.0981 | 6.7271 | 6.7271 | 6.7271 | 6.7271
2021-12-28 04:00 | 1.2632 | 1.5372 | 1.504 | 1.6177 | 1.5324 | 1.6461 | 0.68268 | 1.1707 | 1.4446 | 1.4446 | 1.6271 | 1.6271 | 2020-02-24 17:00 | 2.4025 | 3.9373 | 6.4631 | 6.4631 | 6.4631 | 6.4631
2021-12-28 05:00 | 1.2603 | 1.5337 | 1.5006 | 1.614 | 1.529 | 1.6424 | 0.68303 | 1.1713 | 1.4453 | 1.4453 | 1.628 | 1.628 | 2020-02-24 18:00 | 2.2587 | 3.7016 | 6.0761 | 6.0761 | 6.0761 | 6.0761
2021-12-28 06:00 | 1.3118 | 1.5963 | 1.5618 | 1.6799 | 1.5914 | 1.7094 | 0.68303 | 1.1713 | 1.4453 | 1.4453 | 1.628 | 1.628 | 2020-02-24 19:00 | 1.9824 | 3.2488 | 5.333 | 5.333 | 5.333 | 5.333
2021-12-28 07:00 | 1.3661 | 1.6624 | 1.6265 | 1.7494 | 1.6572 | 1.7802 | 0.8345 | 1.431 | 1.7658 | 1.7658 | 1.989 | 1.989 | 2020-02-24 20:00 | 1.9214 | 3.1489 | 5.169 | 5.169 | 5.169 | 5.169
2021-12-28 08:00 | 1.4118 | 1.718 | 1.6809 | 1.808 | 1.7127 | 1.8398 | 1.0203 | 1.7496 | 2.1589 | 2.1589 | 2.4317 | 2.4317 | 2020-02-24 21:00 | 1.8214 | 2.985 | 4.8999 | 4.8999 | 4.8999 | 4.8999
2021-12-28 09:00 | 1.3775 | 1.6763 | 1.6401 | 1.7641 | 1.6711 | 1.7951 | 1.046 | 1.7937 | 2.2133 | 2.2133 | 2.4931 | 2.4931 | 2020-02-24 22:00 | 1.7347 | 2.8429 | 4.6667 | 4.6667 | 4.6667 | 4.6667
2021-12-28 10:00 | 1.3832 | 1.6832 | 1.6469 | 1.7714 | 1.678 | 1.8025 | 1.1946 | 2.0485 | 2.5278 | 2.5278 | 2.8473 | 2.8473 | 2020-02-24 23:00 | 1.6157 | 2.6478 | 4.3463 | 4.3463 | 4.3463 | 4.3463
2021-12-28 11:00 | 1.3775 | 1.6763 | 1.6401 | 1.7641 | 1.6711 | 1.7951 | 1.3432 | 2.3034 | 2.8422 | 2.8422 | 3.2015 | 3.2015 | 2020-02-25 | 1.4299 | 2.3433 | 3.8466 | 3.8466 | 3.8466 | 3.8466
2021-12-28 12:00 | 1.3489 | 1.6415 | 1.6061 | 1.7275 | 1.6364 | 1.7578 | 1.266 | 2.1711 | 2.679 | 2.679 | 3.0176 | 3.0176 | 2020-02-25 01:00 | 1.3994 | 2.2934 | 3.7646 | 3.7646 | 3.7646 | 3.7646
2021-12-28 13:00 | 1.166 | 1.4189 | 1.3883 | 1.4933 | 1.4145 | 1.5195 | 1.2975 | 2.225 | 2.7455 | 2.7455 | 3.0925 | 3.0925 | 2020-02-25 02:00 | 1.3508 | 2.2137 | 3.6339 | 3.6339 | 3.6339 | 3.6339
2021-12-28 14:00 | 1.2689 | 1.5441 | 1.5108 | 1.625 | 1.5394 | 1.6536 | 1.2489 | 2.1416 | 2.6427 | 2.6427 | 2.9767 | 2.9767 | 2020-02-25 03:00 | 1.3356 | 2.1888 | 3.5929 | 3.5929 | 3.5929 | 3.5929
2021-12-28 15:00 | 1.2718 | 1.5476 | 1.5142 | 1.6287 | 1.5428 | 1.6573 | 1.2432 | 2.1318 | 2.6306 | 2.6306 | 2.9631 | 2.9631 | 2020-02-25 04:00 | 1.3661 | 2.2387 | 3.6749 | 3.6749 | 3.6749 | 3.6749
2021-12-28 16:00 | 1.226 | 1.492 | 1.4598 | 1.5701 | 1.4874 | 1.5977 | 1.266 | 2.1711 | 2.679 | 2.679 | 3.0176 | 3.0176 | 2020-02-25 05:00 | 1.5099 | 2.4745 | 4.0619 | 4.0619 | 4.0619 | 4.0619
2021-12-28 17:00 | 1.3946 | 1.6971 | 1.6605 | 1.786 | 1.6919 | 1.8174 | 1.3661 | 2.3426 | 2.8906 | 2.8906 | 3.256 | 3.256 | 2020-02-25 06:00 | 1.6366 | 2.6821 | 4.4027 | 4.4027 | 4.4027 | 4.4027
2021-12-28 18:00 | 1.6004 | 1.9475 | 1.9055 | 2.0496 | 1.9415 | 2.0856 | 1.4347 | 2.4602 | 3.0357 | 3.0357 | 3.4194 | 3.4194 | 2020-02-25 07:00 | 2.0005 | 3.2785 | 5.3817 | 5.3817 | 5.3817 | 5.3817
2021-12-28 19:00 | 1.5575 | 1.8954 | 1.8545 | 1.9947 | 1.8895 | 2.0297 | 1.4775 | 2.5337 | 3.1265 | 3.1265 | 3.5216 | 3.5216 | 2020-02-25 08:00 | 2.3682 | 3.8811 | 6.3709 | 6.3709 | 6.3709 | 6.3709
2021-12-28 20:00 | 1.6318 | 1.9858 | 1.943 | 2.0898 | 1.9797 | 2.1265 | 1.4689 | 2.519 | 3.1083 | 3.1083 | 3.5012 | 3.5012 | 2020-02-25 09:00 | 2.3063 | 3.7796 | 6.2043 | 6.2043 | 6.2043 | 6.2043
2021-12-28 21:00 | 1.629 | 1.9823 | 1.9396 | 2.0862 | 1.9762 | 2.1228 | 1.3975 | 2.3965 | 2.9571 | 2.9571 | 3.3309 | 3.3309 | 2020-02-25 10:00 | 2.493 | 4.0856 | 6.7066 | 6.7066 | 6.7066 | 6.7066
2021-12-28 22:00 | 1.509 | 1.8362 | 1.7966 | 1.9324 | 1.8306 | 1.9664 | 1.1517 | 1.975 | 2.4371 | 2.4371 | 2.7451 | 2.7451 | 2020-02-25 11:00 | 2.5407 | 4.1637 | 6.8347 | 6.8347 | 6.8347 | 6.8347
2021-12-28 23:00 | 1.4232 | 1.7319 | 1.6946 | 1.8226 | 1.7266 | 1.8547 | 0.93167 | 1.5977 | 1.9714 | 1.9714 | 2.2206 | 2.2206 | 2020-02-25 12:00 | 2.5378 | 4.159 | 6.827 | 6.827 | 6.827 | 6.827
2021-12-29 | 1.4204 | 1.7284 | 1.6912 | 1.819 | 1.7231 | 1.8509 | 0.87451 | 1.4996 | 1.8505 | 1.8505 | 2.0844 | 2.0844 | 2020-02-25 13:00 | 2.593 | 4.2495 | 6.9757 | 6.9757 | 6.9757 | 6.9757
2021-12-29 01:00 | 1.3032 | 1.5859 | 1.5517 | 1.669 | 1.581 | 1.6983 | 0.7802 | 1.3379 | 1.6509 | 1.6509 | 1.8596 | 1.8596 | 2020-02-25 14:00 | 2.6597 | 4.3588 | 7.155 | 7.155 | 7.155 | 7.155
2021-12-29 02:00 | 1.2403 | 1.5093 | 1.4768 | 1.5884 | 1.5047 | 1.6163 | 0.73733 | 1.2644 | 1.5602 | 1.5602 | 1.7574 | 1.7574 | 2020-02-25 15:00 | 2.7293 | 4.4728 | 7.3421 | 7.3421 | 7.3421 | 7.3421
2021-12-29 03:00 | 1.2403 | 1.5093 | 1.4768 | 1.5884 | 1.5047 | 1.6163 | 0.67446 | 1.1566 | 1.4272 | 1.4272 | 1.6076 | 1.6076 | 2020-02-25 16:00 | 2.6588 | 4.3572 | 7.1525 | 7.1525 | 7.1525 | 7.1525
2021-12-29 04:00 | 1.2261 | 1.4921 | 1.4599 | 1.5702 | 1.4875 | 1.5978 | 0.64874 | 1.1125 | 1.3727 | 1.3727 | 1.5462 | 1.5462 | 2020-02-25 17:00 | 2.5016 | 4.0997 | 6.7296 | 6.7296 | 6.7296 | 6.7296
2021-12-29 05:00 | 1.246 | 1.5163 | 1.4836 | 1.5957 | 1.5116 | 1.6238 | 0.64302 | 1.1027 | 1.3606 | 1.3606 | 1.5326 | 1.5326 | 2020-02-25 18:00 | 2.3149 | 3.7937 | 6.2273 | 6.2273 | 6.2273 | 6.2273
2021-12-29 06:00 | 1.306 | 1.5893 | 1.555 | 1.6726 | 1.5844 | 1.702 | 0.65445 | 1.1223 | 1.3848 | 1.3848 | 1.5599 | 1.5599 | 2020-02-25 19:00 | 2.0729 | 3.3971 | 5.5764 | 5.5764 | 5.5764 | 5.5764
2021-12-29 07:00 | 1.4089 | 1.7145 | 1.6775 | 1.8043 | 1.7092 | 1.836 | 0.91452 | 1.5683 | 1.9351 | 1.9351 | 2.1797 | 2.1797 | 2020-02-25 20:00 | 2.0272 | 3.3222 | 5.4534 | 5.4534 | 5.4534 | 5.4534
2021-12-29 08:00 | 1.3632 | 1.6589 | 1.6231 | 1.7458 | 1.6538 | 1.7765 | 1.0288 | 1.7643 | 2.177 | 2.177 | 2.4522 | 2.4522 | 2020-02-25 21:00 | 2.0491 | 3.3581 | 5.5124 | 5.5124 | 5.5124 | 5.5124
2021-12-29 09:00 | 1.3718 | 1.6693 | 1.6333 | 1.7568 | 1.6642 | 1.7876 | 1.1003 | 1.8868 | 2.3282 | 2.3282 | 2.6225 | 2.6225 | 2020-02-25 22:00 | 1.83 | 2.999 | 4.9229 | 4.9229 | 4.9229 | 4.9229
2021-12-29 10:00 | 1.3003 | 1.5824 | 1.5482 | 1.6653 | 1.5775 | 1.6945 | 1.2115 | 2.0775 | 2.5636 | 2.5636 | 2.8876 | 2.8876 | 2020-02-25 23:00 | 1.6985 | 2.7836 | 4.5693 | 4.5693 | 4.5693 | 4.5693
2021-12-29 11:00 | 1.2489 | 1.5198 | 1.487 | 1.5994 | 1.5151 | 1.6275 | 1.2546 | 2.1515 | 2.6548 | 2.6548 | 2.9903 | 2.9903 | 2020-02-26 | 1.5899 | 2.6056 | 4.2771 | 4.2771 | 4.2771 | 4.2771
2021-12-29 12:00 | 1.1717 | 1.4259 | 1.3951 | 1.5006 | 1.4215 | 1.5269 | 1.2489 | 2.1416 | 2.6427 | 2.6427 | 2.9767 | 2.9767 | 2020-02-26 01:00 | 1.528 | 2.5041 | 4.1106 | 4.1106 | 4.1106 | 4.1106
2021-12-29 13:00 | 1.1717 | 1.4259 | 1.3951 | 1.5006 | 1.4215 | 1.5269 | 1.2546 | 2.1515 | 2.6548 | 2.6548 | 2.9903 | 2.9903 | 2020-02-26 02:00 | 1.488 | 2.4386 | 4.0029 | 4.0029 | 4.0029 | 4.0029
2021-12-29 14:00 | 1.1632 | 1.4154 | 1.3849 | 1.4896 | 1.4111 | 1.5158 | 1.2632 | 2.1662 | 2.6729 | 2.6729 | 3.0107 | 3.0107 | 2020-02-26 03:00 | 1.4651 | 2.4011 | 3.9414 | 3.9414 | 3.9414 | 3.9414
2021-12-29 15:00 | 1.186 | 1.4433 | 1.4121 | 1.5189 | 1.4388 | 1.5456 | 1.2232 | 2.0975 | 2.5882 | 2.5882 | 2.9154 | 2.9154 | 2020-02-26 04:00 | 1.5099 | 2.4745 | 4.0619 | 4.0619 | 4.0619 | 4.0619
2021-12-29 16:00 | 1.3889 | 1.6902 | 1.6537 | 1.7787 | 1.685 | 1.81 | 1.2857 | 2.2048 | 2.7206 | 2.7206 | 3.0645 | 3.0645 | 2020-02-26 05:00 | 1.588 | 2.6025 | 4.272 | 4.272 | 4.272 | 4.272
2021-12-29 17:00 | 1.6434 | 1.9999 | 1.9567 | 2.1046 | 1.9937 | 2.1416 | 1.4347 | 2.4602 | 3.0357 | 3.0357 | 3.4194 | 3.4194 | 2020-02-26 06:00 | 1.7328 | 2.8398 | 4.6615 | 4.6615 | 4.6615 | 4.6615
2021-12-29 18:00 | 1.8119 | 2.2049 | 2.1573 | 2.3204 | 2.1981 | 2.3612 | 1.4918 | 2.5582 | 3.1567 | 3.1567 | 3.5557 | 3.5557 | 2020-02-26 07:00 | 2.1615 | 3.5423 | 5.8148 | 5.8148 | 5.8148 | 5.8148
2021-12-29 19:00 | 1.7981 | 2.1881 | 2.1409 | 2.3027 | 2.1814 | 2.3432 | 1.4193 | 2.4338 | 3.0032 | 3.0032 | 3.3828 | 3.3828 | 2020-02-26 08:00 | 2.434 | 3.9888 | 6.5477 | 6.5477 | 6.5477 | 6.5477
2021-12-29 20:00 | 1.629 | 1.9823 | 1.9396 | 2.0862 | 1.9762 | 2.1228 | 1.4575 | 2.4994 | 3.0841 | 3.0841 | 3.4739 | 3.4739 | 2020-02-26 09:00 | 2.4559 | 4.0247 | 6.6066 | 6.6066 | 6.6066 | 6.6066
2021-12-29 21:00 | 1.6147 | 1.9649 | 1.9225 | 2.0679 | 1.9589 | 2.1042 | 1.4089 | 2.4161 | 2.9813 | 2.9813 | 3.3581 | 3.3581 | 2020-02-26 10:00 | 2.6083 | 4.2745 | 7.0167 | 7.0167 | 7.0167 | 7.0167
2021-12-29 22:00 | 1.549 | 1.885 | 1.8444 | 1.9838 | 1.8792 | 2.0186 | 1.1832 | 2.0289 | 2.5036 | 2.5036 | 2.82 | 2.82 | 2020-02-26 11:00 | 2.6397 | 4.326 | 7.1012 | 7.1012 | 7.1012 | 7.1012
2021-12-29 23:00 | 1.5062 | 1.8328 | 1.7933 | 1.9289 | 1.8272 | 1.9628 | 0.9974 | 1.7104 | 2.1105 | 2.1105 | 2.3773 | 2.3773 | 2020-02-26 12:00 | 2.6826 | 4.3963 | 7.2165 | 7.2165 | 7.2165 | 7.2165
2021-12-30 | 1.3975 | 1.7006 | 1.6639 | 1.7897 | 1.6954 | 1.8211 | 0.92309 | 1.583 | 1.9533 | 1.9533 | 2.2002 | 2.2002 | 2020-02-26 13:00 | 2.4873 | 4.0762 | 6.6912 | 6.6912 | 6.6912 | 6.6912
2021-12-30 01:00 | 1.306 | 1.5893 | 1.555 | 1.6726 | 1.5844 | 1.702 | 0.77448 | 1.3281 | 1.6388 | 1.6388 | 1.8459 | 1.8459 | 2020-02-26 14:00 | 2.5988 | 4.2589 | 6.991 | 6.991 | 6.991 | 6.991
2021-12-30 02:00 | 1.2575 | 1.5302 | 1.4972 | 1.6104 | 1.5255 | 1.6387 | 0.72876 | 1.2497 | 1.5421 | 1.5421 | 1.737 | 1.737 | 2020-02-26 15:00 | 2.4959 | 4.0903 | 6.7143 | 6.7143 | 6.7143 | 6.7143
2021-12-30 03:00 | 1.2375 | 1.5059 | 1.4734 | 1.5847 | 1.5012 | 1.6126 | 0.70291 | 1.2054 | 1.4874 | 1.4874 | 1.6754 | 1.6754 | 2020-02-26 16:00 | 2.4368 | 3.9935 | 6.5554 | 6.5554 | 6.5554 | 6.5554
2021-12-30 04:00 | 1.246 | 1.5163 | 1.4836 | 1.5957 | 1.5116 | 1.6238 | 0.70304 | 1.2056 | 1.4876 | 1.4876 | 1.6757 | 1.6757 | 2020-02-26 17:00 | 2.3416 | 3.8374 | 6.2991 | 6.2991 | 6.2991 | 6.2991
2021-12-30 05:00 | 1.2489 | 1.5198 | 1.487 | 1.5994 | 1.5151 | 1.6275 | 0.70875 | 1.2154 | 1.4997 | 1.4997 | 1.6893 | 1.6893 | 2020-02-26 18:00 | 2.2387 | 3.6688 | 6.0223 | 6.0223 | 6.0223 | 6.0223
2021-12-30 06:00 | 1.246 | 1.5163 | 1.4836 | 1.5957 | 1.5116 | 1.6238 | 0.7335 | 1.2578 | 1.5521 | 1.5521 | 1.7483 | 1.7483 | 2020-02-26 19:00 | 2.0215 | 3.3128 | 5.438 | 5.438 | 5.438 | 5.438
2021-12-30 07:00 | 1.3975 | 1.7006 | 1.6639 | 1.7897 | 1.6954 | 1.8211 | 0.92727 | 1.5901 | 1.9621 | 1.9621 | 2.2101 | 2.2101 | 2020-02-26 20:00 | 2.0596 | 3.3753 | 5.5405 | 5.5405 | 5.5405 | 5.5405
2021-12-30 08:00 | 1.4232 | 1.7319 | 1.6946 | 1.8226 | 1.7266 | 1.8547 | 0.99447 | 1.7054 | 2.1043 | 2.1043 | 2.3703 | 2.3703 | 2020-02-26 21:00 | 1.9576 | 3.2082 | 5.2663 | 5.2663 | 5.2663 | 5.2663
2021-12-30 09:00 | 1.4204 | 1.7284 | 1.6912 | 1.819 | 1.7231 | 1.8509 | 1.0714 | 1.8373 | 2.2672 | 2.2672 | 2.5537 | 2.5537 | 2020-02-26 22:00 | 1.7328 | 2.8398 | 4.6615 | 4.6615 | 4.6615 | 4.6615
2021-12-30 10:00 | 1.3689 | 1.6658 | 1.6299 | 1.7531 | 1.6607 | 1.7839 | 1.204 | 2.0647 | 2.5478 | 2.5478 | 2.8698 | 2.8698 | 2020-02-26 23:00 | 1.6585 | 2.718 | 4.4616 | 4.4616 | 4.4616 | 4.4616
2021-12-30 11:00 | 1.3346 | 1.6241 | 1.5891 | 1.7092 | 1.6191 | 1.7392 | 1.2632 | 2.1662 | 2.6729 | 2.6729 | 3.0107 | 3.0107 | 2020-02-27 | 1.5099 | 2.4745 | 4.0619 | 4.0619 | 4.0619 | 4.0619
2021-12-30 12:00 | 1.3661 | 1.6624 | 1.6265 | 1.7494 | 1.6572 | 1.7802 | 1.2575 | 2.1564 | 2.6608 | 2.6608 | 2.9971 | 2.9971 | 2020-02-27 01:00 | 1.4966 | 2.4526 | 4.026 | 4.026 | 4.026 | 4.026
2021-12-30 13:00 | 1.2832 | 1.5615 | 1.5278 | 1.6433 | 1.5567 | 1.6722 | 1.3003 | 2.2299 | 2.7515 | 2.7515 | 3.0993 | 3.0993 | 2020-02-27 02:00 | 1.4175 | 2.323 | 3.8133 | 3.8133 | 3.8133 | 3.8133
2021-12-30 14:00 | 1.3203 | 1.6067 | 1.5721 | 1.6909 | 1.6018 | 1.7206 | 1.2946 | 2.2201 | 2.7394 | 2.7394 | 3.0857 | 3.0857 | 2020-02-27 03:00 | 1.4575 | 2.3886 | 3.9209 | 3.9209 | 3.9209 | 3.9209
2021-12-30 15:00 | 1.509 | 1.8362 | 1.7966 | 1.9324 | 1.8306 | 1.9664 | 1.2918 | 2.2152 | 2.7334 | 2.7334 | 3.0789 | 3.0789 | 2020-02-27 04:00 | 1.4318 | 2.3464 | 3.8517 | 3.8517 | 3.8517 | 3.8517
2021-12-30 16:00 | 1.5747 | 1.9162 | 1.8749 | 2.0166 | 1.9103 | 2.0521 | 1.3101 | 2.2465 | 2.7721 | 2.7721 | 3.1225 | 3.1225 | 2020-02-27 05:00 | 1.4928 | 2.4464 | 4.0157 | 4.0157 | 4.0157 | 4.0157
2021-12-30 17:00 | 1.8433 | 2.2431 | 2.1948 | 2.3607 | 2.2362 | 2.4021 | 1.4461 | 2.4798 | 3.0599 | 3.0599 | 3.4467 | 3.4467 | 2020-02-27 06:00 | 1.649 | 2.7024 | 4.436 | 4.436 | 4.436 | 4.436
2021-12-30 18:00 | 1.9793 | 2.4086 | 2.3567 | 2.5348 | 2.4012 | 2.5793 | 1.4547 | 2.4945 | 3.0781 | 3.0781 | 3.4671 | 3.4671 | 2020-02-27 07:00 | 1.9586 | 3.2098 | 5.2689 | 5.2689 | 5.2689 | 5.2689
2021-12-30 19:00 | 1.9805 | 2.4101 | 2.3581 | 2.5363 | 2.4026 | 2.5809 | 1.4375 | 2.4651 | 3.0418 | 3.0418 | 3.4262 | 3.4262 | 2020-02-27 08:00 | 2.1891 | 3.5876 | 5.8891 | 5.8891 | 5.8891 | 5.8891
2021-12-30 20:00 | 1.6633 | 2.024 | 1.9804 | 2.1301 | 2.0178 | 2.1675 | 1.4146 | 2.4259 | 2.9934 | 2.9934 | 3.3718 | 3.3718 | 2020-02-27 09:00 | 2.2511 | 3.6891 | 6.0556 | 6.0556 | 6.0556 | 6.0556
2021-12-30 21:00 | 1.6404 | 1.9962 | 1.9532 | 2.1008 | 1.9901 | 2.1377 | 1.4032 | 2.4063 | 2.9692 | 2.9692 | 3.3445 | 3.3445 | 2020-02-27 10:00 | 2.2234 | 3.6438 | 5.9813 | 5.9813 | 5.9813 | 5.9813
2021-12-30 22:00 | 1.5718 | 1.9128 | 1.8715 | 2.013 | 1.9069 | 2.0483 | 1.1803 | 2.0241 | 2.4976 | 2.4976 | 2.8133 | 2.8133 | 2020-02-27 11:00 | 2.2158 | 3.6313 | 5.9608 | 5.9608 | 5.9608 | 5.9608
2021-12-30 23:00 | 1.5033 | 1.8293 | 1.7899 | 1.9252 | 1.8237 | 1.959 | 1.0117 | 1.7349 | 2.1407 | 2.1407 | 2.4113 | 2.4113 | 2020-02-27 12:00 | 2.2777 | 3.7328 | 6.1274 | 6.1274 | 6.1274 | 6.1274
2021-12-31 | 1.4432 | 1.7563 | 1.7184 | 1.8483 | 1.7509 | 1.8807 | 0.92023 | 1.5781 | 1.9472 | 1.9472 | 2.1933 | 2.1933 | 2020-02-27 13:00 | 2.3263 | 3.8124 | 6.2581 | 6.2581 | 6.2581 | 6.2581
2021-12-31 01:00 | 1.3261 | 1.6137 | 1.5789 | 1.6982 | 1.6087 | 1.728 | 0.77734 | 1.333 | 1.6449 | 1.6449 | 1.8528 | 1.8528 | 2020-02-27 14:00 | 2.2663 | 3.714 | 6.0966 | 6.0966 | 6.0966 | 6.0966
2021-12-31 02:00 | 1.2575 | 1.5302 | 1.4972 | 1.6104 | 1.5255 | 1.6387 | 0.69446 | 1.1909 | 1.4695 | 1.4695 | 1.6552 | 1.6552 | 2020-02-27 15:00 | 2.3492 | 3.8499 | 6.3196 | 6.3196 | 6.3196 | 6.3196
2021-12-31 03:00 | 1.2462 | 1.5165 | 1.4838 | 1.5959 | 1.5118 | 1.624 | 0.6916 | 1.186 | 1.4634 | 1.4634 | 1.6484 | 1.6484 | 2020-02-27 16:00 | 2.3597 | 3.867 | 6.3478 | 6.3478 | 6.3478 | 6.3478
2021-12-31 04:00 | 1.2032 | 1.4641 | 1.4326 | 1.5408 | 1.4596 | 1.5679 | 0.61162 | 1.0488 | 1.2942 | 1.2942 | 1.4578 | 1.4578 | 2020-02-27 17:00 | 2.253 | 3.6922 | 6.0608 | 6.0608 | 6.0608 | 6.0608
2021-12-31 05:00 | 1.2002 | 1.4606 | 1.4291 | 1.5371 | 1.4561 | 1.5641 | 0.62587 | 1.0733 | 1.3244 | 1.3244 | 1.4917 | 1.4917 | 2020-02-27 18:00 | 2.0967 | 3.4362 | 5.6405 | 5.6405 | 5.6405 | 5.6405
2021-12-31 06:00 | 1.2403 | 1.5093 | 1.4767 | 1.5884 | 1.5046 | 1.6163 | 0.66008 | 1.1319 | 1.3967 | 1.3967 | 1.5733 | 1.5733 | 2020-02-27 19:00 | 1.9538 | 3.202 | 5.2561 | 5.2561 | 5.2561 | 5.2561
2021-12-31 07:00 | 1.3775 | 1.6763 | 1.6401 | 1.7641 | 1.6711 | 1.7951 | 0.92309 | 1.583 | 1.9533 | 1.9533 | 2.2002 | 2.2002 | 2020-02-27 20:00 | 1.8986 | 3.1114 | 5.1074 | 5.1074 | 5.1074 | 5.1074
2021-12-31 08:00 | 1.4318 | 1.7423 | 1.7048 | 1.8336 | 1.737 | 1.8658 | 1.0403 | 1.7839 | 2.2012 | 2.2012 | 2.4794 | 2.4794 | 2020-02-27 21:00 | 1.8271 | 2.9943 | 4.9152 | 4.9152 | 4.9152 | 4.9152
2021-12-31 09:00 | 1.5175 | 1.8467 | 1.8068 | 1.9434 | 1.841 | 1.9776 | 1.1146 | 1.9113 | 2.3584 | 2.3584 | 2.6565 | 2.6565 | 2020-02-27 22:00 | 1.6357 | 2.6805 | 4.4001 | 4.4001 | 4.4001 | 4.4001
2021-12-31 10:00 | 1.4575 | 1.7736 | 1.7354 | 1.8666 | 1.7682 | 1.8994 | 1.2175 | 2.0877 | 2.5761 | 2.5761 | 2.9018 | 2.9018 | 2020-02-27 23:00 | 1.5385 | 2.5213 | 4.1387 | 4.1387 | 4.1387 | 4.1387
2021-12-31 11:00 | 1.4604 | 1.7771 | 1.7388 | 1.8702 | 1.7716 | 1.9031 | 1.3032 | 2.2348 | 2.7576 | 2.7576 | 3.1061 | 3.1061 | 2020-02-28 | 1.3899 | 2.2778 | 3.739 | 3.739 | 3.739 | 3.739
2021-12-31 12:00 | 1.5232 | 1.8536 | 1.8137 | 1.9507 | 1.8479 | 1.985 | 1.3546 | 2.323 | 2.8664 | 2.8664 | 3.2287 | 3.2287 | 2020-02-28 01:00 | 1.3365 | 2.1903 | 3.5955 | 3.5955 | 3.5955 | 3.5955
2021-12-31 13:00 | 1.7074 | 2.0778 | 2.033 | 2.1866 | 2.0714 | 2.225 | 1.4175 | 2.4308 | 2.9995 | 2.9995 | 3.3786 | 3.3786 | 2020-02-28 02:00 | 1.3108 | 2.1482 | 3.5263 | 3.5263 | 3.5263 | 3.5263
2021-12-31 14:00 | 1.8062 | 2.1979 | 2.1505 | 2.3131 | 2.1912 | 2.3537 | 1.4261 | 2.4455 | 3.0176 | 3.0176 | 3.399 | 3.399 | 2020-02-28 03:00 | 1.2908 | 2.1154 | 3.4724 | 3.4724 | 3.4724 | 3.4724
2021-12-31 15:00 | 1.8148 | 2.2084 | 2.1607 | 2.3241 | 2.2016 | 2.3649 | 1.4375 | 2.4651 | 3.0418 | 3.0418 | 3.4262 | 3.4262 | 2020-02-28 04:00 | 1.3051 | 2.1388 | 3.5109 | 3.5109 | 3.5109 | 3.5109
2021-12-31 16:00 | 1.8748 | 2.2814 | 2.2322 | 2.4009 | 2.2744 | 2.4431 | 1.4174 | 2.4306 | 2.9992 | 2.9992 | 3.3783 | 3.3783 | 2020-02-28 05:00 | 1.3584 | 2.2262 | 3.6544 | 3.6544 | 3.6544 | 3.6544
2021-12-31 17:00 | 2.0891 | 2.5422 | 2.4874 | 2.6754 | 2.5344 | 2.7224 | 1.6661 | 2.8572 | 3.5256 | 3.5256 | 3.9712 | 3.9712 | 2020-02-28 06:00 | 1.4489 | 2.3745 | 3.8979 | 3.8979 | 3.8979 | 3.8979
2021-12-31 18:00 | 2.0748 | 2.5248 | 2.4704 | 2.6571 | 2.5171 | 2.7038 | 1.613 | 2.766 | 3.4131 | 3.4131 | 3.8445 | 3.8445 | 2020-02-28 07:00 | 1.8662 | 3.0583 | 5.0203 | 5.0203 | 5.0203 | 5.0203
2021-12-31 19:00 | 2.1091 | 2.5666 | 2.5112 | 2.701 | 2.5587 | 2.7485 | 1.529 | 2.6219 | 3.2353 | 3.2353 | 3.6442 | 3.6442 | 2020-02-28 08:00 | 2.2034 | 3.611 | 5.9275 | 5.9275 | 5.9275 | 5.9275
2021-12-31 20:00 | 1.7776 | 2.1632 | 2.1165 | 2.2765 | 2.1565 | 2.3165 | 1.4547 | 2.4945 | 3.0781 | 3.0781 | 3.4671 | 3.4671 | 2020-02-28 09:00 | 2.1625 | 3.5439 | 5.8173 | 5.8173 | 5.8173 | 5.8173
2021-12-31 21:00 | 1.6804 | 2.0449 | 2.0008 | 2.152 | 2.0386 | 2.1898 | 1.3461 | 2.3084 | 2.8484 | 2.8484 | 3.2084 | 3.2084 | 2020-02-28 10:00 | 2.131 | 3.4924 | 5.7327 | 5.7327 | 5.7327 | 5.7327
2021-12-31 22:00 | 1.6804 | 2.0449 | 2.0008 | 2.152 | 2.0386 | 2.1898 | 1.1917 | 2.0436 | 2.5217 | 2.5217 | 2.8404 | 2.8404 | 2020-02-28 11:00 | 2.1644 | 3.547 | 5.8224 | 5.8224 | 5.8224 | 5.8224
2021-12-31 23:00 | 1.5461 | 1.8815 | 1.8409 | 1.98 | 1.8757 | 2.0148 | 0.98532 | 1.6897 | 2.0849 | 2.0849 | 2.3485 | 2.3485 | 2020-02-28 12:00 | 2.1825 | 3.5767 | 5.8711 | 5.8711 | 5.8711 | 5.8711
2022-01-01 | 1.4747 | 1.7945 | 1.7558 | 1.8885 | 1.789 | 1.9217 | 0.90309 | 1.5487 | 1.9109 | 1.9109 | 2.1525 | 2.1525 | 2020-02-28 13:00 | 2.2587 | 3.7016 | 6.0761 | 6.0761 | 6.0761 | 6.0761

## Daily Load - Winter
| Wolseley | [11 empty] | Quick | [11 empty] | Bowen
| Average Winter Day Load (MW/MVA) | [5 empty] | Peak Winter Day Load (MW/MVA) | [5 empty] | Average Winter Day Load (MW/MVA) | [5 empty] | Peak Winter Day Load (MW/MVA) | [5 empty] | Average Winter Day Load (MW/MVA) | [5 empty] | Peak Winter Day Load (MW/MVA)
Time | 2021 | 2025 | 2026 | 2027 | 2028 | 2029 | 2021 | 2025 | 2026 | 2027 | 2028 | 2029 | 2021 | 2025 | 2026 | 2027 | 2028 | 2029 | 2021 | 2025 | 2026 | 2027 | 2028 | 2029 | 2019 | 2025 | 2026 | 2027 | 2028 | 2029 | 2019 | 2025 | 2026 | 2027 | 2028 | 2029
0:00 | 1.9504 | 2.4153 | 2.4537 | 2.6186 | 2.5526 | 2.7175 | 2.4692 | 3.0577 | 3.1064 | 3.3152 | 3.2317 | 3.4404 | 1.2717 | 1.9263 | 2.2934 | 2.2934 | 2.5381 | 2.5381 | 1.6919 | 2.5628 | 3.0512 | 3.0512 | 3.3768 | 3.3768 | 1.4242 | 2.444 | 4.1307 | 4.1307 | 4.1307 | 4.1307 | 1.5623 | 2.6809 | 4.5312 | 4.5312 | 4.5312 | 4.5312
1:00 | 1.8207 | 2.2546 | 2.2906 | 2.4445 | 2.3829 | 2.5368 | 2.2549 | 2.7923 | 2.8368 | 3.0274 | 2.9511 | 3.1417 | 1.1236 | 1.7021 | 2.0264 | 2.0264 | 2.2426 | 2.2426 | 1.4175 | 2.1472 | 2.5564 | 2.5564 | 2.8292 | 2.8292 | 1.361 | 2.3355 | 3.9473 | 3.9473 | 3.9473 | 3.9473 | 1.5394 | 2.6417 | 4.4649 | 4.4649 | 4.4649 | 4.4649
2:00 | 1.7687 | 2.1903 | 2.2252 | 2.3747 | 2.3149 | 2.4644 | 2.2377 | 2.7711 | 2.8152 | 3.0044 | 2.9287 | 3.1179 | 1.0487 | 1.5886 | 1.8914 | 1.8914 | 2.0932 | 2.0932 | 1.3203 | 2.0001 | 2.3812 | 2.3812 | 2.6353 | 2.6353 | 1.3277 | 2.2783 | 3.8507 | 3.8507 | 3.8507 | 3.8507 | 1.5394 | 2.6417 | 4.4649 | 4.4649 | 4.4649 | 4.4649
3:00 | 1.7664 | 2.1875 | 2.2223 | 2.3716 | 2.3119 | 2.4612 | 2.212 | 2.7392 | 2.7828 | 2.9698 | 2.895 | 3.082 | 1.0231 | 1.5498 | 1.8451 | 1.8451 | 2.042 | 2.042 | 1.2632 | 1.9135 | 2.2781 | 2.2781 | 2.5212 | 2.5212 | 1.3262 | 2.2757 | 3.8464 | 3.8464 | 3.8464 | 3.8464 | 1.5166 | 2.6025 | 4.3986 | 4.3986 | 4.3986 | 4.3986
4:00 | 1.8396 | 2.278 | 2.3143 | 2.4698 | 2.4076 | 2.5631 | 2.3287 | 2.8837 | 2.9297 | 3.1265 | 3.0478 | 3.2446 | 1.0391 | 1.5741 | 1.8741 | 1.8741 | 2.074 | 2.074 | 1.2432 | 1.8832 | 2.242 | 2.242 | 2.4812 | 2.4812 | 1.3784 | 2.3654 | 3.9979 | 3.9979 | 3.9979 | 3.9979 | 1.608 | 2.7594 | 4.6638 | 4.6638 | 4.6638 | 4.6638
5:00 | 2.1119 | 2.6153 | 2.6569 | 2.8354 | 2.764 | 2.9426 | 2.8236 | 3.4966 | 3.5523 | 3.7909 | 3.6955 | 3.9342 | 1.1267 | 1.7067 | 2.0319 | 2.0319 | 2.2487 | 2.2487 | 1.3089 | 1.9827 | 2.3606 | 2.3606 | 2.6124 | 2.6124 | 1.5468 | 2.6543 | 4.4862 | 4.4862 | 4.4862 | 4.4862 | 1.6614 | 2.8509 | 4.8186 | 4.8186 | 4.8186 | 4.8186
6:00 | 2.7046 | 3.3493 | 3.4026 | 3.6312 | 3.5398 | 3.7684 | 4.2125 | 5.2165 | 5.2996 | 5.6557 | 5.5133 | 5.8694 | 1.3457 | 2.0385 | 2.4269 | 2.4269 | 2.6858 | 2.6858 | 1.4632 | 2.2165 | 2.6389 | 2.6389 | 2.9205 | 2.9205 | 1.727 | 2.9636 | 5.0089 | 5.0089 | 5.0089 | 5.0089 | 1.7986 | 3.0863 | 5.2164 | 5.2164 | 5.2164 | 5.2164
7:00 | 3.083 | 3.8178 | 3.8786 | 4.1392 | 4.035 | 4.2956 | 5.0499 | 6.2535 | 6.3531 | 6.78 | 6.6092 | 7.0361 | 1.6424 | 2.4879 | 2.962 | 2.962 | 3.2781 | 3.2781 | 1.6461 | 2.4936 | 2.9687 | 2.9687 | 3.2855 | 3.2855 | 1.914 | 3.2845 | 5.5514 | 5.5514 | 5.5514 | 5.5514 | 1.8748 | 3.2171 | 5.4375 | 5.4375 | 5.4375 | 5.4375
8:00 | 3.141 | 3.8896 | 3.9515 | 4.2171 | 4.1108 | 4.3764 | 5.0699 | 6.2782 | 6.3782 | 6.8068 | 6.6354 | 7.064 | 1.7167 | 2.6005 | 3.0961 | 3.0961 | 3.4264 | 3.4264 | 2.1005 | 3.1819 | 3.7882 | 3.7882 | 4.1925 | 4.1925 | 2.0795 | 3.5684 | 6.0311 | 6.0311 | 6.0311 | 6.0311 | 2.111 | 3.6225 | 6.1227 | 6.1227 | 6.1227 | 6.1227
9:00 | 3.0181 | 3.7374 | 3.797 | 4.0521 | 3.9501 | 4.2052 | 4.8527 | 6.0093 | 6.105 | 6.5152 | 6.3511 | 6.7613 | 1.7037 | 2.5807 | 3.0725 | 3.0725 | 3.4003 | 3.4003 | 2.1863 | 3.3118 | 3.9429 | 3.9429 | 4.3636 | 4.3636 | 2.0749 | 3.5606 | 6.0179 | 6.0179 | 6.0179 | 6.0179 | 2.1796 | 3.7402 | 6.3216 | 6.3216 | 6.3216 | 6.3216
10:00 | 2.8947 | 3.5847 | 3.6418 | 3.8865 | 3.7886 | 4.0333 | 4.5097 | 5.5846 | 5.6735 | 6.0548 | 5.9023 | 6.2835 | 1.7336 | 2.6261 | 3.1265 | 3.1265 | 3.4601 | 3.4601 | 2.5035 | 3.7923 | 4.515 | 4.515 | 4.9967 | 4.9967 | 2.0683 | 3.5492 | 5.9987 | 5.9987 | 5.9987 | 5.9987 | 2.2253 | 3.8187 | 6.4542 | 6.4542 | 6.4542 | 6.4542
11:00 | 2.7245 | 3.3739 | 3.4276 | 3.658 | 3.5658 | 3.7961 | 4.0782 | 5.0502 | 5.1306 | 5.4754 | 5.3375 | 5.6822 | 1.7363 | 2.6302 | 3.1314 | 3.1314 | 3.4656 | 3.4656 | 2.5664 | 3.8876 | 4.6284 | 4.6284 | 5.1222 | 5.1222 | 2.0932 | 3.5919 | 6.071 | 6.071 | 6.071 | 6.071 | 2.3015 | 3.9495 | 6.6753 | 6.6753 | 6.6753 | 6.6753
12:00 | 2.6166 | 3.2403 | 3.2919 | 3.5131 | 3.4246 | 3.6458 | 3.8181 | 4.7281 | 4.8035 | 5.1262 | 4.9971 | 5.3199 | 1.7216 | 2.608 | 3.1049 | 3.1049 | 3.4362 | 3.4362 | 2.4463 | 3.7057 | 4.4119 | 4.4119 | 4.8826 | 4.8826 | 2.0997 | 3.603 | 6.0897 | 6.0897 | 6.0897 | 6.0897 | 2.4006 | 4.1195 | 6.9626 | 6.9626 | 6.9626 | 6.9626
13:00 | 2.5334 | 3.1372 | 3.1871 | 3.4013 | 3.3156 | 3.5298 | 3.4323 | 4.2504 | 4.3181 | 4.6082 | 4.4922 | 4.7823 | 1.7068 | 2.5854 | 3.0781 | 3.0781 | 3.4065 | 3.4065 | 2.4549 | 3.7187 | 4.4273 | 4.4273 | 4.8998 | 4.8998 | 2.0835 | 3.5752 | 6.0427 | 6.0427 | 6.0427 | 6.0427 | 2.6597 | 4.5641 | 7.7141 | 7.7141 | 7.7141 | 7.7141
14:00 | 2.4973 | 3.0926 | 3.1418 | 3.3529 | 3.2685 | 3.4796 | 3.6524 | 4.5229 | 4.5949 | 4.9037 | 4.7802 | 5.0889 | 1.6808 | 2.5461 | 3.0312 | 3.0312 | 3.3547 | 3.3547 | 2.5149 | 3.8096 | 4.5356 | 4.5356 | 5.0195 | 5.0195 | 2.0858 | 3.5792 | 6.0495 | 6.0495 | 6.0495 | 6.0495 | 2.5835 | 4.4333 | 7.4931 | 7.4931 | 7.4931 | 7.4931
15:00 | 2.5276 | 3.1301 | 3.1799 | 3.3936 | 3.3081 | 3.5218 | 3.6924 | 4.5724 | 4.6453 | 4.9574 | 4.8325 | 5.1447 | 1.6789 | 2.5432 | 3.0278 | 3.0278 | 3.3509 | 3.3509 | 2.5149 | 3.8096 | 4.5356 | 4.5356 | 5.0195 | 5.0195 | 2.078 | 3.5658 | 6.0268 | 6.0268 | 6.0268 | 6.0268 | 2.3397 | 4.0149 | 6.7858 | 6.7858 | 6.7858 | 6.7858
16:00 | 2.7636 | 3.4222 | 3.4767 | 3.7103 | 3.6169 | 3.8505 | 3.9804 | 4.929 | 5.0075 | 5.344 | 5.2094 | 5.5459 | 1.8414 | 2.7893 | 3.3208 | 3.3208 | 3.6752 | 3.6752 | 2.7093 | 4.104 | 4.8861 | 4.8861 | 5.4074 | 5.4074 | 2.0943 | 3.5938 | 6.0741 | 6.0741 | 6.0741 | 6.0741 | 2.3092 | 3.9625 | 6.6974 | 6.6974 | 6.6974 | 6.6974
17:00 | 3.2246 | 3.9931 | 4.0567 | 4.3293 | 4.2203 | 4.4929 | 4.5783 | 5.6695 | 5.7598 | 6.1469 | 5.992 | 6.3791 | 2.0945 | 3.1727 | 3.7773 | 3.7773 | 4.1804 | 4.1804 | 2.9383 | 4.4509 | 5.299 | 5.299 | 5.8645 | 5.8645 | 2.0915 | 3.5891 | 6.0661 | 6.0661 | 6.0661 | 6.0661 | 2.111 | 3.6225 | 6.1227 | 6.1227 | 6.1227 | 6.1227
18:00 | 3.3669 | 4.1693 | 4.2357 | 4.5203 | 4.4065 | 4.6911 | 4.6669 | 5.7792 | 5.8713 | 6.2658 | 6.108 | 6.5025 | 2.2489 | 3.4066 | 4.0558 | 4.0558 | 4.4885 | 4.4885 | 3.1179 | 4.7231 | 5.6231 | 5.6231 | 6.2231 | 6.2231 | 2.0467 | 3.5122 | 5.9362 | 5.9362 | 5.9362 | 5.9362 | 2.0729 | 3.5571 | 6.0121 | 6.0121 | 6.0121 | 6.0121
19:00 | 3.2388 | 4.0107 | 4.0746 | 4.3484 | 4.2389 | 4.5127 | 4.4812 | 5.5492 | 5.6376 | 6.0164 | 5.8649 | 6.2437 | 2.251 | 3.4098 | 4.0595 | 4.0595 | 4.4927 | 4.4927 | 3.0408 | 4.6062 | 5.4839 | 5.4839 | 6.0691 | 6.0691 | 1.9582 | 3.3603 | 5.6794 | 5.6794 | 5.6794 | 5.6794 | 1.89 | 3.2433 | 5.4817 | 5.4817 | 5.4817 | 5.4817
20:00 | 2.9986 | 3.7133 | 3.7725 | 4.0259 | 3.9245 | 4.178 | 4.3668 | 5.4076 | 5.4938 | 5.8629 | 5.7153 | 6.0844 | 2.1549 | 3.2643 | 3.8863 | 3.8863 | 4.301 | 4.301 | 2.8722 | 4.3508 | 5.1798 | 5.1798 | 5.7325 | 5.7325 | 1.8559 | 3.1848 | 5.3829 | 5.3829 | 5.3829 | 5.3829 | 1.8824 | 3.2302 | 5.4596 | 5.4596 | 5.4596 | 5.4596
21:00 | 2.7487 | 3.4038 | 3.458 | 3.6903 | 3.5974 | 3.8298 | 3.769 | 4.6673 | 4.7416 | 5.0602 | 4.9328 | 5.2514 | 2.0163 | 3.0543 | 3.6363 | 3.6363 | 4.0243 | 4.0243 | 2.6721 | 4.0477 | 4.8191 | 4.8191 | 5.3333 | 5.3333 | 1.7678 | 3.0336 | 5.1273 | 5.1273 | 5.1273 | 5.1273 | 1.7452 | 2.9948 | 5.0617 | 5.0617 | 5.0617 | 5.0617
22:00 | 2.4403 | 3.0219 | 3.0701 | 3.2764 | 3.1938 | 3.4001 | 3.2798 | 4.0616 | 4.1262 | 4.4035 | 4.2926 | 4.5699 | 1.7817 | 2.699 | 3.2133 | 3.2133 | 3.5562 | 3.5562 | 2.272 | 3.4417 | 4.0975 | 4.0975 | 4.5347 | 4.5347 | 1.6756 | 2.8753 | 4.8597 | 4.8597 | 4.8597 | 4.8597 | 1.6538 | 2.8379 | 4.7965 | 4.7965 | 4.7965 | 4.7965
23:00 | 2.2316 | 2.7635 | 2.8075 | 2.9961 | 2.9207 | 3.1093 | 2.8713 | 3.5556 | 3.6122 | 3.855 | 3.7579 | 4.0006 | 1.5151 | 2.295 | 2.7323 | 2.7323 | 3.0239 | 3.0239 | 2.0005 | 3.0304 | 3.6078 | 3.6078 | 3.9928 | 3.9928 | 1.5314 | 2.6278 | 4.4415 | 4.4415 | 4.4415 | 4.4415 | 1.5699 | 2.694 | 4.5533 | 4.5533 | 4.5533 | 4.5533

## Daily Load - Summer
| Wolseley | [11 empty] | Quick | [11 empty] | Bowen
| Average Summer Day Load (MW/MVA) | [5 empty] | Peak Summer Day Load (MW/MVA) | [5 empty] | Average Summer Day Load (MW/MVA) | [5 empty] | Peak Summer Day Load (MW/MVA) | [5 empty] | Average Summer Day Load (MW/MVA) | [5 empty] | Peak Summer Day Load (MW/MVA)
Time | 2021 | 2025 | 2026 | 2027 | 2028 | 2029 | 2021 | 2025 | 2026 | 2027 | 2028 | 2029 | 2021 | 2025 | 2026 | 2027 | 2028 | 2029 | 2021 | 2025 | 2026 | 2027 | 2028 | 2029 | 2019 | 2025 | 2026 | 2027 | 2028 | 2029 | 2019 | 2025 | 2026 | 2027 | 2028 | 2029
0:00 | 1.5266 | 1.8577 | 1.8176 | 1.955 | 1.852 | 1.9894 | 1.6061 | 1.9545 | 1.9123 | 2.0569 | 1.9485 | 2.093 | 0.97224 | 1.6672 | 2.0573 | 2.0573 | 2.3173 | 2.3173 | 1.1804 | 2.0243 | 2.4978 | 2.4978 | 2.8135 | 2.8135 | 1.4408 | 2.3613 | 3.8761 | 3.8761 | 3.8761 | 3.8761 | 1.7681 | 2.8975 | 4.7564 | 4.7564 | 4.7564 | 4.7564
1:00 | 1.3958 | 1.6986 | 1.6619 | 1.7875 | 1.6933 | 1.8189 | 1.4604 | 1.7771 | 1.7388 | 1.8702 | 1.7716 | 1.9031 | 0.8458 | 1.4504 | 1.7897 | 1.7897 | 2.0159 | 2.0159 | 1.0147 | 1.74 | 2.1471 | 2.1471 | 2.4185 | 2.4185 | 1.3884 | 2.2753 | 3.735 | 3.735 | 3.735 | 3.735 | 1.7547 | 2.8757 | 4.7205 | 4.7205 | 4.7205 | 4.7205
2:00 | 1.3388 | 1.6292 | 1.5941 | 1.7146 | 1.6242 | 1.7447 | 1.3804 | 1.6797 | 1.6435 | 1.7677 | 1.6746 | 1.7988 | 0.78713 | 1.3498 | 1.6656 | 1.6656 | 1.8761 | 1.8761 | 0.9632 | 1.6517 | 2.0381 | 2.0381 | 2.2958 | 2.2958 | 1.3501 | 2.2125 | 3.6318 | 3.6318 | 3.6318 | 3.6318 | 1.7328 | 2.8398 | 4.6615 | 4.6615 | 4.6615 | 4.6615
3:00 | 1.326 | 1.6135 | 1.5787 | 1.6981 | 1.6086 | 1.7279 | 1.3832 | 1.6832 | 1.6469 | 1.7714 | 1.678 | 1.8025 | 0.75445 | 1.2938 | 1.5964 | 1.5964 | 1.7982 | 1.7982 | 0.91166 | 1.5634 | 1.9291 | 1.9291 | 2.1729 | 2.1729 | 1.3399 | 2.1959 | 3.6046 | 3.6046 | 3.6046 | 3.6046 | 1.6861 | 2.7633 | 4.536 | 4.536 | 4.536 | 4.536
4:00 | 1.3282 | 1.6163 | 1.5814 | 1.7009 | 1.6113 | 1.7308 | 1.3257 | 1.6132 | 1.5784 | 1.6978 | 1.6083 | 1.7276 | 0.7454 | 1.2782 | 1.5773 | 1.5773 | 1.7766 | 1.7766 | 0.88308 | 1.5143 | 1.8686 | 1.8686 | 2.1048 | 2.1048 | 1.3754 | 2.2539 | 3.6999 | 3.6999 | 3.6999 | 3.6999 | 1.809 | 2.9647 | 4.8666 | 4.8666 | 4.8666 | 4.8666
5:00 | 1.4429 | 1.7559 | 1.718 | 1.8479 | 1.7505 | 1.8804 | 1.7822 | 2.1688 | 2.122 | 2.2824 | 2.1621 | 2.3225 | 0.78044 | 1.3383 | 1.6514 | 1.6514 | 1.8602 | 1.8602 | 0.92023 | 1.5781 | 1.9472 | 1.9472 | 2.1933 | 2.1933 | 1.4583 | 2.3899 | 3.9231 | 3.9231 | 3.9231 | 3.9231 | 1.8281 | 2.9959 | 4.9178 | 4.9178 | 4.9178 | 4.9178
6:00 | 1.6892 | 2.0556 | 2.0113 | 2.1633 | 2.0493 | 2.2013 | 1.9095 | 2.3237 | 2.2736 | 2.4454 | 2.3165 | 2.4884 | 0.9023 | 1.5473 | 1.9093 | 1.9093 | 2.1506 | 2.1506 | 0.98311 | 1.6859 | 2.0803 | 2.0803 | 2.3432 | 2.3432 | 1.6056 | 2.6312 | 4.3192 | 4.3192 | 4.3192 | 4.3192 | 1.8386 | 3.0131 | 4.946 | 4.946 | 4.946 | 4.946
7:00 | 1.9257 | 2.3433 | 2.2928 | 2.4661 | 2.3361 | 2.5094 | 2.2624 | 2.7531 | 2.6937 | 2.8973 | 2.7446 | 2.9482 | 1.1135 | 1.9095 | 2.3562 | 2.3562 | 2.654 | 2.654 | 1.2489 | 2.1416 | 2.6427 | 2.6427 | 2.9767 | 2.9767 | 1.9049 | 3.1217 | 5.1244 | 5.1244 | 5.1244 | 5.1244 | 2.1815 | 3.5751 | 5.8686 | 5.8686 | 5.8686 | 5.8686
8:00 | 2.0374 | 2.4793 | 2.4258 | 2.6092 | 2.4717 | 2.655 | 2.5492 | 3.1021 | 3.0352 | 3.2647 | 3.0926 | 3.322 | 1.2292 | 2.1079 | 2.601 | 2.601 | 2.9298 | 2.9298 | 1.3375 | 2.2936 | 2.8301 | 2.8301 | 3.1878 | 3.1878 | 2.1075 | 3.4538 | 5.6695 | 5.6695 | 5.6695 | 5.6695 | 2.4625 | 4.0356 | 6.6246 | 6.6246 | 6.6246 | 6.6246
9:00 | 2.0289 | 2.4689 | 2.4157 | 2.5983 | 2.4613 | 2.6439 | 2.9036 | 3.5334 | 3.4572 | 3.7185 | 3.5225 | 3.7838 | 1.2791 | 2.1935 | 2.7066 | 2.7066 | 3.0487 | 3.0487 | 1.5118 | 2.5925 | 3.199 | 3.199 | 3.6034 | 3.6034 | 2.1734 | 3.5617 | 5.8466 | 5.8466 | 5.8466 | 5.8466 | 2.5902 | 4.2448 | 6.968 | 6.968 | 6.968 | 6.968
10:00 | 2.0153 | 2.4524 | 2.3995 | 2.5808 | 2.4448 | 2.6262 | 2.9979 | 3.6482 | 3.5695 | 3.8393 | 3.6369 | 3.9067 | 1.3745 | 2.357 | 2.9085 | 2.9085 | 3.2761 | 3.2761 | 1.6947 | 2.9062 | 3.586 | 3.586 | 4.0393 | 4.0393 | 2.2356 | 3.6637 | 6.014 | 6.014 | 6.014 | 6.014 | 2.7502 | 4.5071 | 7.3985 | 7.3985 | 7.3985 | 7.3985
11:00 | 2.0205 | 2.4588 | 2.4057 | 2.5876 | 2.4512 | 2.633 | 3.1151 | 3.7907 | 3.709 | 3.9893 | 3.7791 | 4.0594 | 1.3979 | 2.3972 | 2.958 | 2.958 | 3.3319 | 3.3319 | 1.7662 | 3.0287 | 3.7372 | 3.7372 | 4.2096 | 4.2096 | 2.2955 | 3.7619 | 6.1753 | 6.1753 | 6.1753 | 6.1753 | 2.8607 | 4.6882 | 7.6958 | 7.6958 | 7.6958 | 7.6958
12:00 | 2.0003 | 2.4342 | 2.3817 | 2.5617 | 2.4267 | 2.6067 | 3.2837 | 3.9959 | 3.9097 | 4.2053 | 3.9836 | 4.2791 | 1.4037 | 2.4071 | 2.9702 | 2.9702 | 3.3456 | 3.3456 | 1.769 | 3.0336 | 3.7433 | 3.7433 | 4.2164 | 4.2164 | 2.3258 | 3.8116 | 6.2568 | 6.2568 | 6.2568 | 6.2568 | 2.9436 | 4.824 | 7.9187 | 7.9187 | 7.9187 | 7.9187
13:00 | 1.98 | 2.4095 | 2.3575 | 2.5357 | 2.4021 | 2.5803 | 3.6009 | 4.382 | 4.2874 | 4.6115 | 4.3685 | 4.6925 | 1.4226 | 2.4396 | 3.0103 | 3.0103 | 3.3908 | 3.3908 | 1.9119 | 3.2786 | 4.0456 | 4.0456 | 4.557 | 4.557 | 2.3288 | 3.8165 | 6.2649 | 6.2649 | 6.2649 | 6.2649 | 2.9341 | 4.8084 | 7.8931 | 7.8931 | 7.8931 | 7.8931
14:00 | 1.9685 | 2.3955 | 2.3438 | 2.521 | 2.3881 | 2.5653 | 3.6895 | 4.4898 | 4.3929 | 4.725 | 4.4759 | 4.808 | 1.3972 | 2.3961 | 2.9566 | 2.9566 | 3.3303 | 3.3303 | 1.9262 | 3.3031 | 4.0759 | 4.0759 | 4.591 | 4.591 | 2.3368 | 3.8296 | 6.2863 | 6.2863 | 6.2863 | 6.2863 | 2.9693 | 4.8662 | 7.9879 | 7.9879 | 7.9879 | 7.9879
15:00 | 1.9603 | 2.3855 | 2.334 | 2.5104 | 2.3781 | 2.5546 | 3.8096 | 4.6358 | 4.5358 | 4.8787 | 4.6216 | 4.9644 | 1.3577 | 2.3282 | 2.8729 | 2.8729 | 3.236 | 3.236 | 1.8862 | 3.2345 | 3.9912 | 3.9912 | 4.4957 | 4.4957 | 2.3336 | 3.8244 | 6.2778 | 6.2778 | 6.2778 | 6.2778 | 3.0513 | 5.0005 | 8.2083 | 8.2083 | 8.2083 | 8.2083
16:00 | 1.9825 | 2.4125 | 2.3605 | 2.5389 | 2.4051 | 2.5835 | 3.8038 | 4.6289 | 4.529 | 4.8714 | 4.6146 | 4.957 | 1.4079 | 2.4144 | 2.9792 | 2.9792 | 3.3557 | 3.3557 | 1.9434 | 3.3325 | 4.1122 | 4.1122 | 4.6319 | 4.6319 | 2.3155 | 3.7947 | 6.229 | 6.229 | 6.229 | 6.229 | 3.1389 | 5.1441 | 8.4441 | 8.4441 | 8.4441 | 8.4441
17:00 | 2.1102 | 2.5679 | 2.5125 | 2.7024 | 2.56 | 2.7499 | 3.7981 | 4.6219 | 4.5222 | 4.8641 | 4.6077 | 4.9495 | 1.5106 | 2.5904 | 3.1964 | 3.1964 | 3.6004 | 3.6004 | 2.1834 | 3.7442 | 4.6201 | 4.6201 | 5.2041 | 5.2041 | 2.2133 | 3.6271 | 5.954 | 5.954 | 5.954 | 5.954 | 3.0055 | 4.9255 | 8.0853 | 8.0853 | 8.0853 | 8.0853
18:00 | 2.2382 | 2.7237 | 2.665 | 2.8664 | 2.7153 | 2.9168 | 3.7553 | 4.5698 | 4.4712 | 4.8092 | 4.5557 | 4.8936 | 1.5782 | 2.7064 | 3.3395 | 3.3395 | 3.7616 | 3.7616 | 2.2177 | 3.803 | 4.6927 | 4.6927 | 5.2858 | 5.2858 | 2.0237 | 3.3165 | 5.444 | 5.444 | 5.444 | 5.444 | 2.7645 | 4.5305 | 7.4369 | 7.4369 | 7.4369 | 7.4369
19:00 | 2.1881 | 2.6627 | 2.6052 | 2.8022 | 2.6545 | 2.8514 | 3.5612 | 4.3336 | 4.2401 | 4.5606 | 4.3202 | 4.6407 | 1.6049 | 2.7522 | 3.3961 | 3.3961 | 3.8253 | 3.8253 | 2.2434 | 3.8471 | 4.7471 | 4.7471 | 5.3471 | 5.3471 | 1.9067 | 3.1248 | 5.1294 | 5.1294 | 5.1294 | 5.1294 | 2.4092 | 3.9482 | 6.4811 | 6.4811 | 6.4811 | 6.4811
20:00 | 2.0815 | 2.533 | 2.4783 | 2.6657 | 2.5252 | 2.7125 | 2.9865 | 3.6342 | 3.5558 | 3.8246 | 3.623 | 3.8918 | 1.5763 | 2.703 | 3.3354 | 3.3354 | 3.757 | 3.757 | 2.0691 | 3.5482 | 4.3782 | 4.3782 | 4.9316 | 4.9316 | 1.8521 | 3.0352 | 4.9824 | 4.9824 | 4.9824 | 4.9824 | 2.2615 | 3.7062 | 6.0838 | 6.0838 | 6.0838 | 6.0838
21:00 | 1.9723 | 2.4 | 2.3483 | 2.5258 | 2.3926 | 2.5701 | 2.7693 | 3.3699 | 3.2972 | 3.5465 | 3.3596 | 3.6088 | 1.504 | 2.5791 | 3.1825 | 3.1825 | 3.5847 | 3.5847 | 1.9033 | 3.2639 | 4.0275 | 4.0275 | 4.5365 | 4.5365 | 1.7765 | 2.9114 | 4.7791 | 4.7791 | 4.7791 | 4.7791 | 2.1301 | 3.4908 | 5.7302 | 5.7302 | 5.7302 | 5.7302
22:00 | 1.7925 | 2.1813 | 2.1343 | 2.2956 | 2.1746 | 2.3359 | 2.2263 | 2.7092 | 2.6507 | 2.8511 | 2.7008 | 2.9012 | 1.3123 | 2.2505 | 2.7769 | 2.7769 | 3.1279 | 3.1279 | 1.8719 | 3.21 | 3.961 | 3.961 | 4.4616 | 4.4616 | 1.6586 | 2.7182 | 4.4619 | 4.4619 | 4.4619 | 4.4619 | 2.0386 | 3.3409 | 5.4842 | 5.4842 | 5.4842 | 5.4842
23:00 | 1.6168 | 1.9675 | 1.925 | 2.0705 | 1.9614 | 2.1069 | 1.9491 | 2.3718 | 2.3207 | 2.4961 | 2.3645 | 2.5399 | 1.1106 | 1.9046 | 2.3501 | 2.3501 | 2.6471 | 2.6471 | 1.5105 | 2.5902 | 3.1961 | 3.1961 | 3.6001 | 3.6001 | 1.5506 | 2.5411 | 4.1713 | 4.1713 | 4.1713 | 4.1713 | 1.9691 | 3.227 | 5.2971 | 5.2971 | 5.2971 | 5.2971

## Feeder Loadings
Feeder | Summer |  | Winter |  | 2025 |  | 2026 |  | 2027 |  | 2028 |  | 2029 |  | 2030 |  | 2031 |  | 2032
| Firm | Thermal | Firm | Thermal | Summer | Winter | Summer | Winter | Summer | Winter | Summer | Winter | Summer | Winter | Summer | Winter | Summer | Winter | Summer | Winter
Wolseley | 4.4466 | 5.916 | 5.0191 | 6.6794 | 4.6358 | 6.2782 | 4.5358 | 6.3782 | 4.8787 | 6.8068 | 4.6216 | 6.6354 | 4.9644 | 7.064 | 5.3073 | 7.4925 | 5.6501 | 7.9211 | 5.993 | 8.3497
Quick | 3.5878 | 4.771 | 4.3702 | 5.8206 | 3.8471 | 4.7231 | 4.7471 | 5.6231 | 4.7471 | 5.6231 | 5.3471 | 6.2231 | 5.3471 | 6.2231 | 5.3471 | 6.2231 | 5.3471 | 6.2231 | 5.3471 | 6.2231
Bowen | 5.5153 | 7.3473 | 6.1641 | 8.2061 | 5.1441 | 4.5641 | 8.4441 | 7.7141 | 8.4441 | 7.7141 | 8.4441 | 7.7141 | 8.4441 | 7.7141 | 8.4441 | 7.7141 | 8.4441 | 7.7141 | 8.4441 | 7.7141
Above Firm
Above Thermal
Units: MVA/MW

## Methodology
Tab | Description
Annual Load | Hourly historical demand of relevant feeders and their hourly forecasts. These forecasts preserve relative percentage of seasonal peak demand in any given hour across a year, and scale the peak demand itself based on addition of point loads as described in the business case
Daily Load | Average Summer / Winter Day load: Calculated by averaging the demand at the same hour throughtout the year. Peak Summer / Winter Day load: The daily load profile on the day when the peak summer/winter demand occurs.
Feeder Loadings | Forecast peak seasonal loadings of relevant feeders in winter and summer.