## Annual Load
| Peak Demand | 6.7256 | 2022-06-14 18:00 |  | Winter | Peak Demand | 4.6869 | 2022-06-07 18:00 |  | Winter | Peak Demand | 7.6401 | 2022-06-07 18:00 |  | Winter
| Anthony Rolfe |  |  |  |  | Nona |  |  |  |  | Hamer
Timestamp | Historical Load (MVA/MW) |  |  |  |  | Historical Load (MVA/MW) |  |  |  |  | Historical Load (MVA/MW)
| 2021 | 2026 | 2027 | 2028 | 2029 | 2021 | 2026 | 2027 | 2028 | 2029 | 2021 | 2026 | 2027 | 2028 | 2029
2021-08-01 | 2.534 | 2.7899 | 2.8244 | 2.8667 | 2.9159 | 2.0216 | 2.4373 | 2.4642 | 2.5009 | 2.0216 | 2.6674 | 3.012 | 3.0362 | 3.0683 | 3.2533
2021-08-01 01:00 | 2.3816 | 2.6166 | 2.6462 | 2.6825 | 2.7247 | 1.829 | 2.2029 | 2.226 | 2.2575 | 1.829 | 2.7055 | 3.0475 | 3.0683 | 3.0959 | 3.2776
2021-08-01 02:00 | 2.2863 | 2.5022 | 2.5256 | 2.5543 | 2.5878 | 1.5666 | 1.884 | 1.9023 | 1.9273 | 1.5666 | 2.0767 | 2.3403 | 2.3567 | 2.3786 | 2.5188
2021-08-01 03:00 | 2.2101 | 2.4085 | 2.4259 | 2.4472 | 2.472 | 1.5074 | 1.8055 | 1.8191 | 1.8376 | 1.5074 | 2.0767 | 2.3319 | 2.3441 | 2.3603 | 2.4939
2021-08-01 04:00 | 2.2291 | 2.4189 | 2.4311 | 2.4461 | 2.4636 | 1.5433 | 1.8406 | 1.8501 | 1.8632 | 1.5433 | 2.896 | 3.2352 | 3.2438 | 3.2552 | 3.428
2021-08-01 05:00 | 2.3435 | 2.5377 | 2.5479 | 2.5605 | 2.5751 | 1.7313 | 2.0598 | 2.0678 | 2.0787 | 1.7313 | 2.6483 | 2.9571 | 2.9643 | 2.9738 | 3.1308
2021-08-01 06:00 | 2.5721 | 2.7867 | 2.7986 | 2.8132 | 2.8303 | 1.9624 | 2.3353 | 2.3446 | 2.3573 | 1.9624 | 3.2961 | 3.6794 | 3.6877 | 3.6988 | 3.8933
2021-08-01 07:00 | 2.7055 | 2.939 | 2.9556 | 2.9759 | 2.9996 | 2.2228 | 2.6494 | 2.6624 | 2.68 | 2.2228 | 3.1056 | 3.4741 | 3.4857 | 3.5011 | 3.6903
2021-08-01 08:00 | 2.8281 | 3.0842 | 3.1076 | 3.1362 | 3.1696 | 2.5149 | 3.0043 | 3.0226 | 3.0475 | 2.5149 | 4.1725 | 4.6692 | 4.6856 | 4.7074 | 4.9628
2021-08-01 09:00 | 2.9531 | 3.2327 | 3.2634 | 3.301 | 3.3447 | 2.4959 | 2.9921 | 3.0161 | 3.0487 | 2.4959 | 4.1916 | 4.7004 | 4.7219 | 4.7505 | 5.0151
2021-08-01 10:00 | 2.9913 | 3.2846 | 3.3209 | 3.3653 | 3.417 | 2.6102 | 3.1351 | 3.1634 | 3.202 | 2.6102 | 3.7915 | 4.2636 | 4.289 | 4.3227 | 4.5715
2021-08-01 11:00 | 2.8579 | 3.1457 | 3.1842 | 3.2313 | 3.2862 | 2.4959 | 3.0032 | 3.0333 | 3.0742 | 2.4959 | 3.639 | 4.0973 | 4.1242 | 4.1601 | 4.403
2021-08-01 12:00 | 3.0103 | 3.3084 | 3.3463 | 3.3928 | 3.4469 | 2.4768 | 2.98 | 3.0096 | 3.05 | 2.4768 | 4.001 | 4.4988 | 4.5254 | 4.5607 | 4.8229
2021-08-01 13:00 | 3.1318 | 3.4339 | 3.4693 | 3.5127 | 3.5632 | 2.6674 | 3.2014 | 3.229 | 3.2667 | 2.6674 | 4.6107 | 5.1728 | 5.1976 | 5.2305 | 5.5234
2021-08-01 14:00 | 3.1627 | 3.4617 | 3.4944 | 3.5343 | 3.5809 | 2.5911 | 3.1075 | 3.1329 | 3.1677 | 2.5911 | 4.4392 | 4.9784 | 5.0013 | 5.0316 | 5.312
2021-08-01 15:00 | 3.0103 | 3.2944 | 3.3252 | 3.3629 | 3.4069 | 2.3244 | 2.7898 | 2.8138 | 2.8466 | 2.3244 | 3.2008 | 3.5997 | 3.6212 | 3.6499 | 3.8602
2021-08-01 16:00 | 3.5628 | 3.8871 | 3.9175 | 3.9547 | 3.998 | 3.0675 | 3.6669 | 3.6906 | 3.723 | 3.0675 | 5.0108 | 5.6104 | 5.6317 | 5.66 | 5.9692
2021-08-01 17:00 | 4.0582 | 4.4229 | 4.455 | 4.4944 | 4.5404 | 3.5819 | 4.2772 | 4.3023 | 4.3366 | 3.5819 | 5.3919 | 6.0364 | 6.0589 | 6.0889 | 6.4211
2021-08-01 18:00 | 4.1154 | 4.4916 | 4.5276 | 4.5716 | 4.6228 | 3.7724 | 4.5076 | 4.5357 | 4.5739 | 3.7724 | 5.7348 | 6.4227 | 6.4479 | 6.4813 | 6.8366
2021-08-01 19:00 | 4.2868 | 4.6856 | 4.7265 | 4.7766 | 4.835 | 3.6962 | 4.4247 | 4.4566 | 4.5002 | 3.6962 | 6.0397 | 6.7684 | 6.797 | 6.8351 | 7.2127
2021-08-01 20:00 | 4.1916 | 4.5929 | 4.6388 | 4.6949 | 4.7604 | 3.6771 | 4.4092 | 4.445 | 4.4938 | 3.6771 | 5.8491 | 6.5635 | 6.5956 | 6.6383 | 7.0109
2021-08-01 21:00 | 4.0102 | 4.3997 | 4.4464 | 4.5036 | 4.5702 | 3.4759 | 4.1727 | 4.2091 | 4.2588 | 3.4759 | 5.3347 | 5.993 | 6.0257 | 6.0692 | 6.4144
2021-08-01 22:00 | 3.62 | 3.9745 | 4.0182 | 4.0716 | 4.1339 | 2.9603 | 3.5593 | 3.5933 | 3.6398 | 2.9603 | 4.6107 | 5.1842 | 5.2148 | 5.2554 | 5.5575
2021-08-01 23:00 | 3.2389 | 3.5567 | 3.5961 | 3.6442 | 3.7003 | 2.5721 | 3.0945 | 3.1252 | 3.1671 | 2.5721 | 4.3059 | 4.8395 | 4.867 | 4.9037 | 5.1842
2021-08-02 | 3.0103 | 3.3016 | 3.3362 | 3.3784 | 3.4276 | 2.1302 | 2.5656 | 2.5926 | 2.6293 | 2.1302 | 3.277 | 3.6895 | 3.7137 | 3.7458 | 3.9644
2021-08-02 01:00 | 2.7055 | 2.9646 | 2.9942 | 3.0304 | 3.0727 | 1.928 | 2.3198 | 2.3429 | 2.3745 | 1.928 | 2.8198 | 3.1746 | 3.1953 | 3.2229 | 3.4109
2021-08-02 02:00 | 2.5911 | 2.8297 | 2.8531 | 2.8818 | 2.9153 | 1.7949 | 2.1537 | 2.172 | 2.197 | 1.7949 | 2.6864 | 3.0178 | 3.0342 | 3.0561 | 3.2298
2021-08-02 03:00 | 2.5911 | 2.8179 | 2.8353 | 2.8566 | 2.8814 | 1.7338 | 2.073 | 2.0865 | 2.1051 | 1.7338 | 3.1818 | 3.5599 | 3.5721 | 3.5883 | 3.7826
2021-08-02 04:00 | 2.6483 | 2.8692 | 2.8814 | 2.8965 | 2.914 | 1.8225 | 2.1704 | 2.18 | 2.193 | 1.8225 | 3.0675 | 3.4257 | 3.4343 | 3.4457 | 3.628
2021-08-02 05:00 | 3.0484 | 3.2951 | 3.3053 | 3.3178 | 3.3324 | 2.3406 | 2.7797 | 2.7876 | 2.7985 | 2.3406 | 4.363 | 4.8626 | 4.8698 | 4.8793 | 5.1306
2021-08-02 06:00 | 3.833 | 4.1413 | 4.1532 | 4.1678 | 4.1849 | 3.0294 | 3.5957 | 3.605 | 3.6177 | 3.0294 | 4.8965 | 5.4578 | 5.4662 | 5.4773 | 5.7598
2021-08-02 07:00 | 4.6488 | 5.0269 | 5.0435 | 5.0638 | 5.0874 | 3.5247 | 4.1875 | 4.2005 | 4.2181 | 3.5247 | 5.3347 | 5.9512 | 5.9628 | 5.9783 | 6.29
2021-08-02 08:00 | 4.6107 | 4.9993 | 5.0227 | 5.0513 | 5.0847 | 3.3991 | 4.0488 | 4.067 | 4.0919 | 3.3991 | 4.9537 | 5.5372 | 5.5536 | 5.5754 | 5.8738
2021-08-02 09:00 | 4.5345 | 4.9317 | 4.9623 | 4.9999 | 5.0437 | 2.9531 | 3.5323 | 3.5563 | 3.5889 | 2.9531 | 4.0963 | 4.5946 | 4.6161 | 4.6446 | 4.904
2021-08-02 10:00 | 4.2514 | 4.6385 | 4.6747 | 4.7191 | 4.7709 | 2.6674 | 3.2027 | 3.2309 | 3.2696 | 2.6674 | 3.2961 | 3.7131 | 3.7385 | 3.7723 | 3.9938
2021-08-02 11:00 | 3.3533 | 3.6779 | 3.7164 | 3.7635 | 3.8184 | 1.7043 | 2.0681 | 2.0981 | 2.1391 | 1.7043 | 1.6385 | 1.8742 | 1.9011 | 1.937 | 2.0699
2021-08-02 12:00 | 2.8198 | 3.1037 | 3.1416 | 3.1881 | 3.2422 | 1.3527 | 1.652 | 1.6816 | 1.722 | 1.3527 | 0.81926 | 0.96303 | 0.98962 | 1.0249 | 1.1122
2021-08-02 13:00 | 2.553 | 2.8121 | 2.8475 | 2.8909 | 2.9414 | 1.2384 | 1.5133 | 1.541 | 1.5787 | 1.2384 | 0.74305 | 0.87481 | 0.89961 | 0.93257 | 1.0128
2021-08-02 14:00 | 2.6864 | 2.95 | 2.9826 | 3.0226 | 3.0692 | 1.5052 | 1.8245 | 1.85 | 1.8847 | 1.5052 | 1.086 | 1.2521 | 1.2749 | 1.3053 | 1.4014
2021-08-02 15:00 | 2.7433 | 3.0075 | 3.0383 | 3.076 | 3.12 | 1.7447 | 2.1049 | 2.1289 | 2.1618 | 1.7447 | 1.9243 | 2.1811 | 2.2027 | 2.2314 | 2.3715
2021-08-02 16:00 | 3.3723 | 3.6824 | 3.7128 | 3.75 | 3.7933 | 2.5834 | 3.0951 | 3.1188 | 3.1511 | 2.5834 | 3.8105 | 4.2766 | 4.2978 | 4.3261 | 4.5694
2021-08-02 17:00 | 4.1587 | 4.5308 | 4.563 | 4.6024 | 4.6483 | 3.4485 | 4.1197 | 4.1448 | 4.179 | 3.4485 | 5.0299 | 5.6341 | 5.6566 | 5.6866 | 5.9989
2021-08-02 18:00 | 4.363 | 4.7577 | 4.7937 | 4.8377 | 4.8889 | 3.7152 | 4.4401 | 4.4682 | 4.5064 | 3.7152 | 5.7729 | 6.465 | 6.4902 | 6.5237 | 6.881
2021-08-02 19:00 | 4.2723 | 4.67 | 4.7109 | 4.761 | 4.8194 | 3.6962 | 4.4247 | 4.4566 | 4.5002 | 3.6962 | 5.5062 | 6.1755 | 6.2042 | 6.2423 | 6.5905
2021-08-02 20:00 | 4.0963 | 4.4906 | 4.5365 | 4.5926 | 4.658 | 3.591 | 4.3075 | 4.3433 | 4.3921 | 3.591 | 5.0695 | 5.6971 | 5.7292 | 5.7719 | 6.1016
2021-08-02 21:00 | 3.7724 | 4.1443 | 4.1909 | 4.2481 | 4.3147 | 3.254 | 3.9106 | 3.947 | 3.9967 | 3.254 | 4.6869 | 5.2731 | 5.3058 | 5.3493 | 5.6589
2021-08-02 22:00 | 3.4485 | 3.7903 | 3.834 | 3.8874 | 3.9497 | 2.8389 | 3.4159 | 3.4499 | 3.4964 | 2.8389 | 4.0963 | 4.6126 | 4.6432 | 4.6838 | 4.9576
2021-08-02 23:00 | 2.9722 | 3.2702 | 3.3095 | 3.3576 | 3.4138 | 2.3625 | 2.8469 | 2.8776 | 2.9195 | 2.3625 | 3.6009 | 4.0561 | 4.0837 | 4.1203 | 4.362
2021-08-03 | 2.7055 | 2.9741 | 3.0087 | 3.0509 | 3.1001 | 1.9094 | 2.3047 | 2.3317 | 2.3684 | 1.9094 | 2.7245 | 3.0755 | 3.0997 | 3.1318 | 3.32
2021-08-03 01:00 | 2.4197 | 2.6575 | 2.6872 | 2.7234 | 2.7657 | 1.7338 | 2.0903 | 2.1134 | 2.145 | 1.7338 | 2.3244 | 2.6241 | 2.6448 | 2.6724 | 2.8332
2021-08-03 02:00 | 2.3435 | 2.5636 | 2.587 | 2.6157 | 2.6492 | 1.5814 | 1.9015 | 1.9198 | 1.9448 | 1.5814 | 2.4197 | 2.7214 | 2.7378 | 2.7597 | 2.9188
2021-08-03 03:00 | 2.2877 | 2.4919 | 2.5093 | 2.5306 | 2.5555 | 1.5814 | 1.8929 | 1.9065 | 1.925 | 1.5814 | 2.0767 | 2.3319 | 2.3441 | 2.3603 | 2.4939
2021-08-03 04:00 | 2.3816 | 2.5826 | 2.5949 | 2.6099 | 2.6274 | 1.6957 | 2.0206 | 2.0302 | 2.0433 | 1.6957 | 2.191 | 2.4518 | 2.4604 | 2.4718 | 2.6059
2021-08-03 05:00 | 2.8388 | 3.0699 | 3.0801 | 3.0927 | 3.1073 | 1.9964 | 2.3731 | 2.381 | 2.3919 | 1.9964 | 2.9913 | 3.3382 | 3.3454 | 3.3549 | 3.5308
2021-08-03 06:00 | 3.6009 | 3.892 | 3.9039 | 3.9185 | 3.9356 | 2.7817 | 3.3031 | 3.3124 | 3.3251 | 2.7817 | 4.725 | 5.2673 | 5.2756 | 5.2867 | 5.5598
2021-08-03 07:00 | 4.1535 | 4.4947 | 4.5113 | 4.5316 | 4.5552 | 3.0675 | 3.6473 | 3.6603 | 3.6779 | 3.0675 | 4.6298 | 5.1679 | 5.1795 | 5.1949 | 5.4679
2021-08-03 08:00 | 4.0772 | 4.4262 | 4.4496 | 4.4782 | 4.5116 | 2.9961 | 3.5727 | 3.591 | 3.6159 | 2.9961 | 4.4964 | 5.0291 | 5.0455 | 5.0673 | 5.3405
2021-08-03 09:00 | 3.8677 | 4.2152 | 4.2459 | 4.2835 | 4.3273 | 2.4959 | 2.9921 | 3.0161 | 3.0487 | 2.4959 | 3.277 | 3.6842 | 3.7057 | 3.7342 | 3.9485
2021-08-03 10:00 | 3.6771 | 4.0215 | 4.0578 | 4.1022 | 4.1539 | 2.2673 | 2.73 | 2.7583 | 2.7969 | 2.2673 | 3.3914 | 3.819 | 3.8444 | 3.8781 | 4.1049
2021-08-03 11:00 | 3.4295 | 3.7597 | 3.7982 | 3.8453 | 3.9003 | 2.1148 | 2.5531 | 2.5831 | 2.6241 | 2.1148 | 2.8579 | 3.2292 | 3.2562 | 3.292 | 3.4919
2021-08-03 12:00 | 3.4485 | 3.7792 | 3.8171 | 3.8636 | 3.9177 | 1.7909 | 2.1697 | 2.1993 | 2.2397 | 1.7909 | 2.0958 | 2.3816 | 2.4082 | 2.4435 | 2.6009
2021-08-03 13:00 | 3.1627 | 3.4671 | 3.5025 | 3.5459 | 3.5964 | 1.7719 | 2.1436 | 2.1712 | 2.2089 | 1.7719 | 2.5721 | 2.9073 | 2.9322 | 2.9651 | 3.1459
2021-08-03 14:00 | 3.277 | 3.5846 | 3.6172 | 3.6571 | 3.7037 | 1.9434 | 2.3422 | 2.3677 | 2.4024 | 1.9434 | 2.9913 | 3.3693 | 3.3922 | 3.4226 | 3.6233
2021-08-03 15:00 | 3.2199 | 3.5196 | 3.5504 | 3.5881 | 3.632 | 2.1394 | 2.5712 | 2.5953 | 2.6281 | 2.1394 | 2.553 | 2.8798 | 2.9014 | 2.9301 | 3.1047
2021-08-03 16:00 | 3.9439 | 4.2965 | 4.3269 | 4.364 | 4.4074 | 2.8198 | 3.3743 | 3.398 | 3.4304 | 2.8198 | 5.2585 | 5.8857 | 5.9069 | 5.9352 | 6.2581
2021-08-03 17:00 | 4.5301 | 4.9298 | 4.962 | 5.0014 | 5.0473 | 3.8486 | 4.5923 | 4.6174 | 4.6517 | 3.8486 | 6.0206 | 6.7351 | 6.7576 | 6.7876 | 7.1543
2021-08-03 18:00 | 4.8775 | 5.3104 | 5.3463 | 5.3903 | 5.4416 | 4.2868 | 5.1154 | 5.1434 | 5.1817 | 4.2868 | 6.3064 | 7.0579 | 7.083 | 7.1165 | 7.5032
2021-08-03 19:00 | 4.6298 | 5.0541 | 5.095 | 5.1451 | 5.2035 | 4.2297 | 5.0549 | 5.0868 | 5.1304 | 4.2297 | 6.535 | 7.3188 | 7.3475 | 7.3856 | 7.7904
2021-08-03 20:00 | 4.5782 | 5.0083 | 5.0542 | 5.1103 | 5.1757 | 4.0582 | 4.8594 | 4.8951 | 4.944 | 4.0582 | 6.4779 | 7.2622 | 7.2943 | 7.337 | 7.7441
2021-08-03 21:00 | 4.3059 | 4.7174 | 4.7641 | 4.8212 | 4.8879 | 3.7534 | 4.5004 | 4.5369 | 4.5866 | 3.7534 | 5.6396 | 6.3317 | 6.3645 | 6.4079 | 6.7699
2021-08-03 22:00 | 3.7877 | 4.1547 | 4.1984 | 4.2518 | 4.3141 | 3.1303 | 3.76 | 3.7941 | 3.8406 | 3.1303 | 4.7631 | 5.3536 | 5.3842 | 5.4248 | 5.7353
2021-08-03 23:00 | 3.277 | 3.5977 | 3.637 | 3.6851 | 3.7413 | 2.6067 | 3.1353 | 3.166 | 3.2079 | 2.6067 | 4.0582 | 4.5642 | 4.5918 | 4.6284 | 4.8953
2021-08-04 | 2.8267 | 3.1044 | 3.1389 | 3.1812 | 3.2304 | 2.1569 | 2.5972 | 2.6241 | 2.6608 | 2.1569 | 3.5819 | 4.0282 | 4.0524 | 4.0845 | 4.3199
2021-08-04 01:00 | 2.6483 | 2.9032 | 2.9328 | 2.969 | 3.0113 | 1.9053 | 2.2929 | 2.316 | 2.3475 | 1.9053 | 2.7245 | 3.0687 | 3.0895 | 3.117 | 3.2998
2021-08-04 02:00 | 2.5911 | 2.8297 | 2.8531 | 2.8818 | 2.9153 | 1.7909 | 2.1491 | 2.1674 | 2.1923 | 1.7909 | 2.7626 | 3.1025 | 3.1189 | 3.1408 | 3.3187
2021-08-04 03:00 | 2.6308 | 2.8605 | 2.8779 | 2.8992 | 2.9241 | 1.7819 | 2.1298 | 2.1434 | 2.162 | 1.7819 | 2.553 | 2.8612 | 2.8734 | 2.8896 | 3.0494
2021-08-04 04:00 | 2.7436 | 2.9715 | 2.9838 | 2.9988 | 3.0163 | 1.926 | 2.2927 | 2.3023 | 2.3154 | 1.926 | 2.7626 | 3.087 | 3.0956 | 3.107 | 3.2725
2021-08-04 05:00 | 3.2389 | 3.4998 | 3.51 | 3.5225 | 3.5371 | 2.4408 | 2.898 | 2.906 | 2.9169 | 2.4408 | 3.8296 | 4.2698 | 4.277 | 4.2865 | 4.5084
2021-08-04 06:00 | 4.0391 | 4.3628 | 4.3747 | 4.3893 | 4.4064 | 3.1035 | 3.6833 | 3.6926 | 3.7053 | 3.1035 | 5.3157 | 5.9236 | 5.932 | 5.9431 | 6.2486
2021-08-04 07:00 | 4.5345 | 4.9041 | 4.9207 | 4.9409 | 4.9646 | 3.4295 | 4.075 | 4.0879 | 4.1056 | 3.4295 | 5.2395 | 5.8454 | 5.857 | 5.8724 | 6.1789
2021-08-04 08:00 | 4.3059 | 4.6718 | 4.6952 | 4.7238 | 4.7572 | 3.2956 | 3.9265 | 3.9448 | 3.9697 | 3.2956 | 4.5031 | 5.0365 | 5.0529 | 5.0747 | 5.3483
2021-08-04 09:00 | 3.8105 | 4.1538 | 4.1845 | 4.2221 | 4.2658 | 2.2482 | 2.6995 | 2.7235 | 2.7561 | 2.2482 | 2.8579 | 3.2184 | 3.2399 | 3.2684 | 3.4597
2021-08-04 10:00 | 3.7152 | 4.0624 | 4.0987 | 4.1431 | 4.1948 | 1.9624 | 2.3699 | 2.3982 | 2.4368 | 1.9624 | 2.6483 | 2.9932 | 3.0186 | 3.0524 | 3.2384
2021-08-04 11:00 | 3.4104 | 3.7393 | 3.7778 | 3.8249 | 3.8798 | 1.8672 | 2.2605 | 2.2905 | 2.3315 | 1.8672 | 2.0386 | 2.3188 | 2.3458 | 2.3816 | 2.5365
2021-08-04 12:00 | 2.915 | 3.206 | 3.244 | 3.2904 | 3.3446 | 1.7147 | 2.0797 | 2.1093 | 2.1497 | 1.7147 | 1.3527 | 1.5559 | 1.5824 | 1.6178 | 1.7344
2021-08-04 13:00 | 2.9722 | 3.2625 | 3.2979 | 3.3412 | 3.3917 | 1.81 | 2.1886 | 2.2162 | 2.2539 | 1.81 | 1.6576 | 1.8911 | 1.9159 | 1.9488 | 2.0794
2021-08-04 14:00 | 3.4676 | 3.7892 | 3.8219 | 3.8618 | 3.9084 | 1.9815 | 2.3872 | 2.4127 | 2.4474 | 1.9815 | 2.2482 | 2.5436 | 2.5665 | 2.5968 | 2.7568
2021-08-04 15:00 | 3.2839 | 3.5883 | 3.6191 | 3.6568 | 3.7008 | 2.2381 | 2.6878 | 2.7118 | 2.7446 | 2.2381 | 2.7436 | 3.0915 | 3.1131 | 3.1418 | 3.3269
2021-08-04 16:00 | 4.1344 | 4.5012 | 4.5316 | 4.5687 | 4.6121 | 2.9722 | 3.5544 | 3.5781 | 3.6104 | 2.9722 | 4.7631 | 5.3352 | 5.3564 | 5.3847 | 5.6804
2021-08-04 17:00 | 4.516 | 4.9148 | 4.9469 | 4.9863 | 5.0322 | 3.9821 | 4.75 | 4.7751 | 4.8094 | 3.9821 | 7.1447 | 7.9842 | 8.0068 | 8.0367 | 8.4653
2021-08-04 18:00 | 4.7441 | 5.1671 | 5.2031 | 5.247 | 5.2983 | 4.2868 | 5.1154 | 5.1434 | 5.1817 | 4.2868 | 7.0304 | 7.8624 | 7.8876 | 7.921 | 8.3475
2021-08-04 19:00 | 4.7441 | 5.1769 | 5.2178 | 5.2679 | 5.3263 | 4.2487 | 5.0774 | 5.1093 | 5.1529 | 4.2487 | 6.5541 | 7.34 | 7.3687 | 7.4068 | 7.8126
2021-08-04 20:00 | 4.4964 | 4.9204 | 4.9663 | 5.0224 | 5.0879 | 4.0772 | 4.8819 | 4.9177 | 4.9665 | 4.0772 | 5.8872 | 6.6058 | 6.638 | 6.6806 | 7.0553
2021-08-04 21:00 | 4.2678 | 4.6764 | 4.7231 | 4.7803 | 4.8469 | 3.6581 | 4.3879 | 4.4243 | 4.474 | 3.6581 | 5.1442 | 5.7813 | 5.814 | 5.8574 | 6.1922
2021-08-04 22:00 | 3.7357 | 4.0989 | 4.1425 | 4.1959 | 4.2582 | 3.1704 | 3.8075 | 3.8415 | 3.888 | 3.1704 | 4.4392 | 4.9937 | 5.0243 | 5.0649 | 5.3575
2021-08-04 23:00 | 3.2961 | 3.6181 | 3.6575 | 3.7056 | 3.7617 | 2.5999 | 3.1273 | 3.158 | 3.1999 | 2.5999 | 3.4485 | 3.8867 | 3.9143 | 3.9509 | 4.1843
2021-08-05 | 2.8388 | 3.1174 | 3.1519 | 3.1942 | 3.2434 | 2.172 | 2.615 | 2.6419 | 2.6786 | 2.172 | 2.9913 | 3.3719 | 3.3961 | 3.4282 | 3.6311
2021-08-05 01:00 | 2.553 | 2.8008 | 2.8304 | 2.8667 | 2.909 | 1.8334 | 2.208 | 2.2311 | 2.2626 | 1.8334 | 2.553 | 2.8782 | 2.8989 | 2.9265 | 3.0998
2021-08-05 02:00 | 2.4197 | 2.6455 | 2.6689 | 2.6976 | 2.7311 | 1.7528 | 2.1041 | 2.1224 | 2.1473 | 1.7528 | 2.4578 | 2.7637 | 2.7802 | 2.802 | 2.9632
2021-08-05 03:00 | 2.4387 | 2.6541 | 2.6715 | 2.6928 | 2.7177 | 1.7338 | 2.073 | 2.0865 | 2.1051 | 1.7338 | 2.4006 | 2.6918 | 2.704 | 2.7203 | 2.8716
2021-08-05 04:00 | 2.6293 | 2.8487 | 2.861 | 2.876 | 2.8935 | 1.8118 | 2.1579 | 2.1674 | 2.1805 | 1.8118 | 2.5911 | 2.8964 | 2.905 | 2.9164 | 3.0725
2021-08-05 05:00 | 3.0103 | 3.2541 | 3.2644 | 3.2769 | 3.2915 | 2.2225 | 2.6401 | 2.6481 | 2.659 | 2.2225 | 3.2961 | 3.677 | 3.6842 | 3.6937 | 3.8863
2021-08-05 06:00 | 3.7915 | 4.0967 | 4.1086 | 4.1232 | 4.1403 | 2.9341 | 3.4832 | 3.4925 | 3.5052 | 2.9341 | 4.6298 | 5.1614 | 5.1698 | 5.1809 | 5.4487
2021-08-05 07:00 | 4.4011 | 4.7608 | 4.7774 | 4.7977 | 4.8213 | 3.2961 | 3.9174 | 3.9304 | 3.948 | 3.2961 | 4.6107 | 5.1467 | 5.1583 | 5.1737 | 5.4457
2021-08-05 08:00 | 4.0973 | 4.4477 | 4.4711 | 4.4997 | 4.5331 | 3.0733 | 3.6639 | 3.6821 | 3.707 | 3.0733 | 4.3086 | 4.8204 | 4.8368 | 4.8586 | 5.1215
2021-08-05 09:00 | 3.3342 | 3.6421 | 3.6728 | 3.7103 | 3.7541 | 1.9858 | 2.3895 | 2.4134 | 2.4461 | 1.9858 | 2.2863 | 2.5832 | 2.6047 | 2.6333 | 2.7931
2021-08-05 10:00 | 2.8769 | 3.1618 | 3.1981 | 3.2425 | 3.2942 | 1.6004 | 1.9422 | 1.9705 | 2.0091 | 1.6004 | 1.2384 | 1.4265 | 1.4519 | 1.4857 | 1.5941
2021-08-05 11:00 | 2.7245 | 3.0024 | 3.0409 | 3.088 | 3.1429 | 1.3908 | 1.6978 | 1.7278 | 1.7688 | 1.3908 | 1.1432 | 1.3237 | 1.3507 | 1.3865 | 1.4922
2021-08-05 12:00 | 2.4387 | 2.6943 | 2.7323 | 2.7787 | 2.8329 | 1.1813 | 1.4494 | 1.479 | 1.5195 | 1.1813 | 0.66684 | 0.79366 | 0.82024 | 0.85557 | 0.93447
2021-08-05 13:00 | 2.3244 | 2.5665 | 2.6019 | 2.6452 | 2.6958 | 1.1241 | 1.3783 | 1.4059 | 1.4436 | 1.1241 | 0.62873 | 0.74778 | 0.77258 | 0.80554 | 0.87951
2021-08-05 14:00 | 2.4006 | 2.643 | 2.6756 | 2.7156 | 2.7621 | 1.3594 | 1.6524 | 1.6778 | 1.7126 | 1.3594 | 0.80261 | 0.93717 | 0.96003 | 0.99042 | 1.0709
2021-08-05 15:00 | 2.6483 | 2.9055 | 2.9363 | 2.974 | 3.018 | 1.7549 | 2.1169 | 2.141 | 2.1738 | 1.7549 | 1.7147 | 1.9482 | 1.9698 | 1.9985 | 2.127
2021-08-05 16:00 | 3.3518 | 3.6604 | 3.6908 | 3.7279 | 3.7713 | 2.5502 | 3.0559 | 3.0795 | 3.1119 | 2.5502 | 3.6771 | 4.1284 | 4.1496 | 4.1779 | 4.4138
2021-08-05 17:00 | 3.9629 | 4.3205 | 4.3527 | 4.3921 | 4.438 | 3.4212 | 4.0874 | 4.1125 | 4.1467 | 3.4212 | 6.516 | 7.2855 | 7.3081 | 7.338 | 7.7321
2021-08-05 18:00 | 4.3249 | 4.7168 | 4.7527 | 4.7967 | 4.848 | 3.7724 | 4.5076 | 4.5357 | 4.5739 | 3.7724 | 5.8872 | 6.5921 | 6.6172 | 6.6507 | 7.0143
2021-08-05 19:00 | 4.3249 | 4.7266 | 4.7675 | 4.8175 | 4.8759 | 3.7152 | 4.4472 | 4.4791 | 4.5227 | 3.7152 | 6.4017 | 7.1706 | 7.1993 | 7.2374 | 7.6349
2021-08-05 20:00 | 4.1916 | 4.5929 | 4.6388 | 4.6949 | 4.7604 | 3.5438 | 4.2517 | 4.2874 | 4.3363 | 3.5438 | 6.535 | 7.3257 | 7.3578 | 7.4005 | 7.8108
2021-08-05 21:00 | 3.7915 | 4.1647 | 4.2114 | 4.2686 | 4.3352 | 3.3244 | 3.9937 | 4.0301 | 4.0799 | 3.3244 | 5.9444 | 6.6705 | 6.7032 | 6.7467 | 7.1254
2021-08-05 22:00 | 3.4772 | 3.8212 | 3.8648 | 3.9183 | 3.9806 | 2.915 | 3.5058 | 3.5398 | 3.5863 | 2.915 | 5.2395 | 5.8829 | 5.9135 | 5.9541 | 6.2907
2021-08-05 23:00 | 3.0865 | 3.393 | 3.4323 | 3.4804 | 3.5366 | 2.4312 | 2.928 | 2.9587 | 3.0006 | 2.4312 | 3.4295 | 3.8656 | 3.8931 | 3.9297 | 4.1621
2021-08-06 | 2.6864 | 2.9537 | 2.9882 | 3.0304 | 3.0797 | 1.9622 | 2.3671 | 2.3941 | 2.4308 | 1.9622 | 2.7245 | 3.0755 | 3.0997 | 3.1318 | 3.32
2021-08-06 01:00 | 2.4387 | 2.678 | 2.7076 | 2.7439 | 2.7861 | 1.7813 | 2.1465 | 2.1696 | 2.2011 | 1.7813 | 2.8198 | 3.1746 | 3.1953 | 3.2229 | 3.4109
2021-08-06 02:00 | 2.3816 | 2.6045 | 2.628 | 2.6567 | 2.6901 | 1.6845 | 2.0234 | 2.0416 | 2.0666 | 1.6845 | 2.4006 | 2.7002 | 2.7167 | 2.7385 | 2.8966
2021-08-06 03:00 | 2.4197 | 2.6336 | 2.651 | 2.6724 | 2.6972 | 1.7002 | 2.0333 | 2.0469 | 2.0654 | 1.7002 | 2.2673 | 2.5436 | 2.5558 | 2.572 | 2.7161
2021-08-06 04:00 | 2.5911 | 2.8078 | 2.82 | 2.835 | 2.8525 | 1.7859 | 2.1272 | 2.1368 | 2.1498 | 1.7859 | 2.6483 | 2.9599 | 2.9685 | 2.98 | 3.1392
2021-08-06 05:00 | 2.9531 | 3.1927 | 3.203 | 3.2155 | 3.2301 | 2.3593 | 2.8018 | 2.8097 | 2.8206 | 2.3593 | 3.277 | 3.6558 | 3.663 | 3.6725 | 3.8641
2021-08-06 06:00 | 3.5987 | 3.8896 | 3.9016 | 3.9162 | 3.9332 | 2.853 | 3.3874 | 3.3967 | 3.4094 | 2.853 | 4.8012 | 5.352 | 5.3603 | 5.3714 | 5.6487
2021-08-06 07:00 | 4.2297 | 4.5766 | 4.5931 | 4.6134 | 4.6371 | 3.2008 | 3.8049 | 3.8178 | 3.8355 | 3.2008 | 4.7441 | 5.2949 | 5.3065 | 5.3219 | 5.6012
2021-08-06 08:00 | 4.0582 | 4.4057 | 4.4291 | 4.4577 | 4.4911 | 2.9763 | 3.5494 | 3.5676 | 3.5925 | 2.9763 | 4.0772 | 4.5633 | 4.5797 | 4.6015 | 4.8517
2021-08-06 09:00 | 3.1818 | 3.4784 | 3.509 | 3.5466 | 3.5904 | 1.9815 | 2.3844 | 2.4084 | 2.441 | 1.9815 | 1.8481 | 2.0963 | 2.1177 | 2.1463 | 2.282
2021-08-06 10:00 | 2.5721 | 2.8343 | 2.8706 | 2.915 | 2.9667 | 1.4283 | 1.7389 | 1.7672 | 1.8058 | 1.4283 | 1.0288 | 1.1936 | 1.219 | 1.2528 | 1.3497
2021-08-06 11:00 | 2.3435 | 2.593 | 2.6315 | 2.6786 | 2.7335 | 1.2003 | 1.4727 | 1.5027 | 1.5437 | 1.2003 | 0.68589 | 0.81557 | 0.84254 | 0.87836 | 0.95891
2021-08-06 12:00 | 2.0844 | 2.3137 | 2.3516 | 2.3981 | 2.4522 | 1.0479 | 1.2919 | 1.3215 | 1.3619 | 1.0479 | 0.80021 | 0.94186 | 0.96845 | 1.0038 | 1.09
2021-08-06 13:00 | 2.0958 | 2.3209 | 2.3563 | 2.3996 | 2.4501 | 1.0669 | 1.3108 | 1.3384 | 1.3761 | 1.0669 | 0.74305 | 0.87481 | 0.89961 | 0.93257 | 1.0128
2021-08-06 14:00 | 2.172 | 2.3973 | 2.43 | 2.4699 | 2.5165 | 1.1622 | 1.4194 | 1.4448 | 1.4796 | 1.1622 | 0.81926 | 0.95567 | 0.97854 | 1.0089 | 1.0903
2021-08-06 15:00 | 2.4387 | 2.6803 | 2.7111 | 2.7488 | 2.7928 | 1.6344 | 1.9746 | 1.9986 | 2.0314 | 1.6344 | 1.467 | 1.673 | 1.6946 | 1.7232 | 1.8382
2021-08-06 16:00 | 2.9341 | 3.2117 | 3.242 | 3.2792 | 3.3225 | 2.2249 | 2.6716 | 2.6952 | 2.7276 | 2.2249 | 2.6293 | 2.9639 | 2.9852 | 3.0134 | 3.1918
2021-08-06 17:00 | 3.5819 | 3.9112 | 3.9433 | 3.9827 | 4.0286 | 3.2199 | 3.8496 | 3.8747 | 3.9089 | 3.2199 | 4.2678 | 4.7872 | 4.8098 | 4.8397 | 5.1101
2021-08-06 18:00 | 3.8677 | 4.2255 | 4.2615 | 4.3055 | 4.3567 | 3.5728 | 4.2718 | 4.2998 | 4.3381 | 3.5728 | 5.2013 | 5.8299 | 5.855 | 5.8885 | 6.2144
2021-08-06 19:00 | 3.7915 | 4.1534 | 4.1943 | 4.2444 | 4.3028 | 3.5819 | 4.2897 | 4.3216 | 4.3651 | 3.5819 | 5.2966 | 5.9426 | 5.9713 | 6.0094 | 6.3461
2021-08-06 20:00 | 3.8105 | 4.1836 | 4.2294 | 4.2855 | 4.351 | 3.3914 | 4.0716 | 4.1074 | 4.1562 | 3.3914 | 6.0778 | 6.8175 | 6.8497 | 6.8924 | 7.2775
2021-08-06 21:00 | 3.8105 | 4.1852 | 4.2319 | 4.289 | 4.3557 | 3.3914 | 4.0728 | 4.1092 | 4.1589 | 3.3914 | 5.5062 | 6.1835 | 6.2162 | 6.2597 | 6.6144
2021-08-06 22:00 | 3.5819 | 3.9336 | 3.9773 | 4.0307 | 4.093 | 2.9854 | 3.5889 | 3.6229 | 3.6694 | 2.9854 | 4.363 | 4.909 | 4.9396 | 4.9802 | 5.2686
2021-08-06 23:00 | 3.2961 | 3.6181 | 3.6575 | 3.7056 | 3.7617 | 2.6416 | 3.1766 | 3.2073 | 3.2492 | 2.6416 | 3.5438 | 3.9926 | 4.0201 | 4.0568 | 4.2954
2021-08-07 | 2.896 | 3.1788 | 3.2133 | 3.2556 | 3.3048 | 2.1612 | 2.6022 | 2.6291 | 2.6659 | 2.1612 | 3.1627 | 3.5625 | 3.5866 | 3.6188 | 3.831
2021-08-07 01:00 | 2.553 | 2.8008 | 2.8304 | 2.8667 | 2.909 | 1.9624 | 2.3604 | 2.3835 | 2.4151 | 1.9624 | 2.915 | 3.2804 | 3.3012 | 3.3288 | 3.522
2021-08-07 02:00 | 2.534 | 2.7683 | 2.7917 | 2.8204 | 2.8539 | 1.8285 | 2.1934 | 2.2117 | 2.2367 | 1.8285 | 2.7817 | 3.1237 | 3.1401 | 3.1619 | 3.3409
2021-08-07 03:00 | 2.534 | 2.7565 | 2.7739 | 2.7952 | 2.82 | 1.7909 | 2.1405 | 2.1541 | 2.1726 | 1.7909 | 2.553 | 2.8612 | 2.8734 | 2.8896 | 3.0494
2021-08-07 04:00 | 2.6293 | 2.8487 | 2.861 | 2.876 | 2.8935 | 1.9075 | 2.2709 | 2.2805 | 2.2935 | 1.9075 | 2.9913 | 3.341 | 3.3496 | 3.3611 | 3.5391
2021-08-07 05:00 | 2.8388 | 3.0699 | 3.0801 | 3.0927 | 3.1073 | 2.2603 | 2.6847 | 2.6927 | 2.7036 | 2.2603 | 3.5247 | 3.9311 | 3.9382 | 3.9478 | 4.1529
2021-08-07 06:00 | 3.0294 | 3.2779 | 3.2899 | 3.3045 | 3.3215 | 2.4197 | 2.8755 | 2.8848 | 2.8975 | 2.4197 | 3.639 | 4.0605 | 4.0688 | 4.0799 | 4.2933
2021-08-07 07:00 | 3.4866 | 3.7783 | 3.7949 | 3.8151 | 3.8388 | 2.7817 | 3.3097 | 3.3227 | 3.3403 | 2.7817 | 4.0582 | 4.5327 | 4.5443 | 4.5597 | 4.8013
2021-08-07 08:00 | 3.3151 | 3.6074 | 3.6308 | 3.6594 | 3.6928 | 2.7817 | 3.3194 | 3.3377 | 3.3626 | 2.7817 | 4.0963 | 4.5845 | 4.6009 | 4.6227 | 4.8739
2021-08-07 09:00 | 3.0294 | 3.3146 | 3.3453 | 3.3828 | 3.4266 | 2.5009 | 2.998 | 3.0219 | 3.0546 | 2.5009 | 3.0229 | 3.4017 | 3.4232 | 3.4518 | 3.6521
2021-08-07 10:00 | 2.6674 | 2.9366 | 2.9729 | 3.0173 | 3.0691 | 1.9169 | 2.316 | 2.3443 | 2.383 | 1.9169 | 2.1148 | 2.4004 | 2.4258 | 2.4596 | 2.6162
2021-08-07 11:00 | 2.3054 | 2.5521 | 2.5906 | 2.6377 | 2.6926 | 1.5814 | 1.9229 | 1.9529 | 1.9939 | 1.5814 | 1.2251 | 1.4148 | 1.4418 | 1.4776 | 1.5878
2021-08-07 12:00 | 2.0196 | 2.244 | 2.2819 | 2.3284 | 2.3825 | 1.3718 | 1.6745 | 1.7041 | 1.7445 | 1.3718 | 0.91452 | 1.0689 | 1.0955 | 1.1308 | 1.2233
2021-08-07 13:00 | 1.8862 | 2.0957 | 2.1311 | 2.1744 | 2.225 | 1.3718 | 1.6709 | 1.6985 | 1.7362 | 1.3718 | 0.95263 | 1.1077 | 1.1325 | 1.1655 | 1.2572
2021-08-07 14:00 | 1.9243 | 2.1313 | 2.1639 | 2.2038 | 2.2504 | 1.467 | 1.7795 | 1.805 | 1.8397 | 1.467 | 1.3908 | 1.5908 | 1.6137 | 1.6441 | 1.7569
2021-08-07 15:00 | 2.4006 | 2.6394 | 2.6702 | 2.7079 | 2.7519 | 1.886 | 2.2719 | 2.2959 | 2.3287 | 1.886 | 2.2863 | 2.5834 | 2.605 | 2.6336 | 2.7936
2021-08-07 16:00 | 3.0675 | 3.3549 | 3.3853 | 3.4225 | 3.4658 | 2.5859 | 3.098 | 3.1217 | 3.154 | 2.5859 | 3.6581 | 4.1072 | 4.1285 | 4.1567 | 4.3916
2021-08-07 17:00 | 3.8296 | 4.1772 | 4.2094 | 4.2488 | 4.2947 | 3.4498 | 4.1212 | 4.1463 | 4.1805 | 3.4498 | 5.5062 | 6.1634 | 6.1859 | 6.2159 | 6.5544
2021-08-07 18:00 | 3.9439 | 4.3074 | 4.3434 | 4.3873 | 4.4386 | 3.6009 | 4.3051 | 4.3331 | 4.3714 | 3.6009 | 5.5443 | 6.211 | 6.2361 | 6.2696 | 6.6144
2021-08-07 19:00 | 4.0201 | 4.399 | 4.44 | 4.49 | 4.5484 | 3.5247 | 4.2221 | 4.254 | 4.2976 | 3.5247 | 5.2585 | 5.9003 | 5.929 | 5.967 | 6.3017
2021-08-07 20:00 | 3.9248 | 4.3064 | 4.3522 | 4.4084 | 4.4738 | 3.4485 | 4.1391 | 4.1749 | 4.2237 | 3.4485 | 6.0016 | 6.7329 | 6.765 | 6.8077 | 7.1887
2021-08-07 21:00 | 3.7915 | 4.1647 | 4.2114 | 4.2686 | 4.3352 | 3.3342 | 4.0053 | 4.0417 | 4.0914 | 3.3342 | 5.6396 | 6.3317 | 6.3645 | 6.4079 | 6.7699
2021-08-07 22:00 | 3.4295 | 3.7699 | 3.8135 | 3.8669 | 3.9292 | 3.0233 | 3.6337 | 3.6677 | 3.7142 | 3.0233 | 4.5536 | 5.1207 | 5.1513 | 5.1919 | 5.4908
2021-08-07 23:00 | 3.2389 | 3.5567 | 3.5961 | 3.6442 | 3.7003 | 2.6456 | 3.1814 | 3.212 | 3.2539 | 2.6456 | 3.9629 | 4.4584 | 4.4859 | 4.5226 | 4.7842
2021-08-08 | 2.9531 | 3.2402 | 3.2747 | 3.317 | 3.3662 | 2.2936 | 2.7587 | 2.7856 | 2.8223 | 2.2936 | 2.9795 | 3.3588 | 3.383 | 3.4151 | 3.6173
2021-08-08 01:00 | 2.6674 | 2.9236 | 2.9532 | 2.9895 | 3.0318 | 2.0386 | 2.4505 | 2.4736 | 2.5051 | 2.0386 | 3.0675 | 3.4498 | 3.4706 | 3.4981 | 3.6997
2021-08-08 02:00 | 2.5911 | 2.8297 | 2.8531 | 2.8818 | 2.9153 | 1.8862 | 2.2616 | 2.2799 | 2.3049 | 1.8862 | 2.4768 | 2.7849 | 2.8013 | 2.8232 | 2.9854
2021-08-08 03:00 | 2.553 | 2.7769 | 2.7943 | 2.8156 | 2.8405 | 1.829 | 2.1855 | 2.1991 | 2.2176 | 1.829 | 2.5721 | 2.8824 | 2.8946 | 2.9108 | 3.0716
2021-08-08 04:00 | 2.5721 | 2.7873 | 2.7996 | 2.8146 | 2.8321 | 1.8862 | 2.2457 | 2.2553 | 2.2684 | 1.8862 | 2.8579 | 3.1928 | 3.2014 | 3.2128 | 3.3836
2021-08-08 05:00 | 2.7055 | 2.9266 | 2.9369 | 2.9494 | 2.964 | 2.088 | 2.4813 | 2.4892 | 2.5001 | 2.088 | 2.896 | 3.2324 | 3.2395 | 3.2491 | 3.4197
2021-08-08 06:00 | 2.915 | 3.1551 | 3.1671 | 3.1817 | 3.1987 | 2.3625 | 2.8079 | 2.8173 | 2.83 | 2.3625 | 3.277 | 3.6582 | 3.6665 | 3.6777 | 3.8711
2021-08-08 07:00 | 3.0484 | 3.3075 | 3.3241 | 3.3444 | 3.368 | 2.6102 | 3.1071 | 3.1201 | 3.1377 | 2.6102 | 3.7534 | 4.1939 | 4.2055 | 4.221 | 4.4458
2021-08-08 08:00 | 3.1818 | 3.4641 | 3.4875 | 3.5162 | 3.5496 | 2.8579 | 3.4094 | 3.4277 | 3.4526 | 2.8579 | 4.725 | 5.2832 | 5.2996 | 5.3213 | 5.6071
2021-08-08 09:00 | 3.1818 | 3.4784 | 3.509 | 3.5466 | 3.5904 | 2.7245 | 3.2622 | 3.2862 | 3.3188 | 2.7245 | 4.8203 | 5.3991 | 5.4206 | 5.4492 | 5.7483
2021-08-08 10:00 | 3.1437 | 3.4484 | 3.4846 | 3.529 | 3.5808 | 2.6674 | 3.2027 | 3.2309 | 3.2696 | 2.6674 | 3.9629 | 4.4541 | 4.4795 | 4.5133 | 4.7715
2021-08-08 11:00 | 3.3151 | 3.6369 | 3.6754 | 3.7225 | 3.7774 | 2.7245 | 3.2733 | 3.3034 | 3.3443 | 2.7245 | 4.2106 | 4.7324 | 4.7594 | 4.7952 | 5.0695
2021-08-08 12:00 | 3.3342 | 3.6564 | 3.6943 | 3.7407 | 3.7949 | 2.915 | 3.4977 | 3.5273 | 3.5677 | 2.915 | 4.3821 | 4.9222 | 4.9488 | 4.9842 | 5.2673
2021-08-08 13:00 | 3.1719 | 3.477 | 3.5124 | 3.5557 | 3.6063 | 2.8388 | 3.404 | 3.4316 | 3.4693 | 2.8388 | 4.4392 | 4.9822 | 5.007 | 5.04 | 5.3234
2021-08-08 14:00 | 3.0675 | 3.3594 | 3.392 | 3.432 | 3.4786 | 2.7055 | 3.2425 | 3.268 | 3.3027 | 2.7055 | 3.5819 | 4.0256 | 4.0485 | 4.0789 | 4.3121
2021-08-08 15:00 | 3.1627 | 3.4581 | 3.489 | 3.5267 | 3.5706 | 2.6483 | 3.1724 | 3.1964 | 3.2292 | 2.6483 | 4.4202 | 4.9547 | 4.9763 | 5.0049 | 5.2822
2021-08-08 16:00 | 3.5355 | 3.8578 | 3.8882 | 3.9253 | 3.9687 | 3.0587 | 3.6566 | 3.6803 | 3.7126 | 3.0587 | 4.5345 | 5.0811 | 5.1024 | 5.1307 | 5.4137
2021-08-08 17:00 | 4.2345 | 4.6123 | 4.6444 | 4.6838 | 4.7297 | 3.8242 | 4.5635 | 4.5886 | 4.6228 | 3.8242 | 5.6967 | 6.3751 | 6.3977 | 6.4276 | 6.7766
2021-08-08 18:00 | 4.4392 | 4.8396 | 4.8755 | 4.9195 | 4.9708 | 4.0582 | 4.8453 | 4.8733 | 4.9116 | 4.0582 | 5.9635 | 6.6768 | 6.7019 | 6.7354 | 7.1032
2021-08-08 19:00 | 4.363 | 4.7675 | 4.8084 | 4.8585 | 4.9169 | 3.9793 | 4.7591 | 4.791 | 4.8346 | 3.9793 | 5.8682 | 6.5778 | 6.6065 | 6.6446 | 7.0127
2021-08-08 20:00 | 4.1154 | 4.5111 | 4.5569 | 4.6131 | 4.6785 | 3.7799 | 4.5306 | 4.5664 | 4.6152 | 3.7799 | 5.3919 | 6.0553 | 6.0875 | 6.1302 | 6.4776
2021-08-08 21:00 | 3.9058 | 4.2875 | 4.3342 | 4.3914 | 4.458 | 3.5057 | 4.2078 | 4.2443 | 4.294 | 3.5057 | 4.9727 | 5.5907 | 5.6234 | 5.6669 | 5.9922
2021-08-08 22:00 | 3.2863 | 3.616 | 3.6597 | 3.7131 | 3.7754 | 2.8819 | 3.4666 | 3.5006 | 3.5471 | 2.8819 | 4.001 | 4.5067 | 4.5373 | 4.5779 | 4.8465
2021-08-08 23:00 | 3.0294 | 3.3316 | 3.3709 | 3.419 | 3.4752 | 2.3625 | 2.8469 | 2.8776 | 2.9195 | 2.3625 | 4.0772 | 4.5854 | 4.613 | 4.6496 | 4.9175
2021-08-09 | 2.7245 | 2.9946 | 3.0291 | 3.0714 | 3.1206 | 1.9624 | 2.3674 | 2.3943 | 2.431 | 1.9624 | 2.7436 | 3.0967 | 3.1208 | 3.153 | 3.3422
2021-08-09 01:00 | 2.5149 | 2.7599 | 2.7895 | 2.8257 | 2.868 | 1.7909 | 2.1579 | 2.181 | 2.2125 | 1.7909 | 2.3435 | 2.6453 | 2.666 | 2.6936 | 2.8554
2021-08-09 02:00 | 2.4006 | 2.625 | 2.6484 | 2.6771 | 2.7106 | 1.6195 | 1.9465 | 1.9648 | 1.9898 | 1.6195 | 2.2673 | 2.552 | 2.5684 | 2.5903 | 2.741
2021-08-09 03:00 | 2.4006 | 2.6132 | 2.6306 | 2.6519 | 2.6767 | 1.6385 | 1.9604 | 1.974 | 1.9925 | 1.6385 | 2.3625 | 2.6495 | 2.6617 | 2.6779 | 2.8272
2021-08-09 04:00 | 2.553 | 2.7668 | 2.7791 | 2.7941 | 2.8116 | 1.7823 | 2.123 | 2.1325 | 2.1456 | 1.7823 | 2.3625 | 2.6424 | 2.651 | 2.6624 | 2.8059
2021-08-09 05:00 | 2.8579 | 3.0904 | 3.1006 | 3.1131 | 3.1277 | 2.2203 | 2.6375 | 2.6454 | 2.6563 | 2.2203 | 3.5628 | 3.9734 | 3.9806 | 3.9901 | 4.1973
2021-08-09 06:00 | 3.6771 | 3.9739 | 3.9858 | 4.0004 | 4.0175 | 2.8358 | 3.367 | 3.3764 | 3.3891 | 2.8358 | 4.6298 | 5.1614 | 5.1698 | 5.1809 | 5.4487
2021-08-09 07:00 | 4.3059 | 4.6584 | 4.675 | 4.6953 | 4.719 | 3.1627 | 3.7599 | 3.7728 | 3.7905 | 3.1627 | 4.9918 | 5.5701 | 5.5817 | 5.5972 | 5.89
2021-08-09 08:00 | 4.2106 | 4.5694 | 4.5928 | 4.6215 | 4.6549 | 3.0294 | 3.612 | 3.6303 | 3.6552 | 3.0294 | 4.4774 | 5.0079 | 5.0243 | 5.0461 | 5.3183
2021-08-09 09:00 | 3.7534 | 4.0924 | 4.1231 | 4.1607 | 4.2044 | 2.4387 | 2.9246 | 2.9485 | 2.9812 | 2.4387 | 3.0675 | 3.4513 | 3.4728 | 3.5013 | 3.7041
2021-08-09 10:00 | 3.1627 | 3.4688 | 3.5051 | 3.5495 | 3.6012 | 1.5623 | 1.8972 | 1.9255 | 1.9641 | 1.5623 | 1.467 | 1.6806 | 1.706 | 1.7397 | 1.8607
2021-08-09 11:00 | 2.7245 | 3.0024 | 3.0409 | 3.088 | 3.1429 | 1.3527 | 1.6528 | 1.6828 | 1.7238 | 1.3527 | 1.0669 | 1.239 | 1.266 | 1.3018 | 1.4033
2021-08-09 12:00 | 2.915 | 3.206 | 3.244 | 3.2904 | 3.3446 | 1.4861 | 1.8096 | 1.8392 | 1.8796 | 1.4861 | 1.829 | 2.0852 | 2.1117 | 2.1471 | 2.2899
2021-08-09 13:00 | 2.4197 | 2.6689 | 2.7043 | 2.7476 | 2.7981 | 1.3393 | 1.6325 | 1.6601 | 1.6978 | 1.3393 | 1.3527 | 1.5523 | 1.5771 | 1.6101 | 1.7239
2021-08-09 14:00 | 2.7626 | 3.0319 | 3.0645 | 3.1045 | 3.1511 | 1.5052 | 1.8245 | 1.85 | 1.8847 | 1.5052 | 1.3908 | 1.5908 | 1.6137 | 1.6441 | 1.7569
2021-08-09 15:00 | 2.4959 | 2.7417 | 2.7725 | 2.8102 | 2.8542 | 1.5242 | 1.8444 | 1.8685 | 1.9013 | 1.5242 | 1.9053 | 2.1599 | 2.1815 | 2.2102 | 2.3492
2021-08-09 16:00 | 2.9341 | 3.2117 | 3.242 | 3.2792 | 3.3225 | 2.1417 | 2.5733 | 2.597 | 2.6293 | 2.1417 | 2.7436 | 3.0909 | 3.1122 | 3.1405 | 3.3251
2021-08-09 17:00 | 3.4295 | 3.7474 | 3.7796 | 3.819 | 3.8649 | 2.9645 | 3.5479 | 3.573 | 3.6073 | 2.9645 | 4.3375 | 4.8647 | 4.8873 | 4.9172 | 5.1915
2021-08-09 18:00 | 3.8105 | 4.1641 | 4.2001 | 4.2441 | 4.2953 | 3.277 | 3.9224 | 3.9505 | 3.9887 | 3.277 | 5.0489 | 5.6605 | 5.6857 | 5.7191 | 6.0367
2021-08-09 19:00 | 3.7724 | 4.133 | 4.1739 | 4.2239 | 4.2823 | 3.2389 | 3.8845 | 3.9164 | 3.96 | 3.2389 | 5.43 | 6.0908 | 6.1195 | 6.1576 | 6.5017
2021-08-09 20:00 | 3.6962 | 4.0607 | 4.1066 | 4.1627 | 4.2282 | 3.2008 | 3.8465 | 3.8823 | 3.9311 | 3.2008 | 6.3636 | 7.1351 | 7.1673 | 7.21 | 7.6108
2021-08-09 21:00 | 3.6009 | 3.96 | 4.0067 | 4.0639 | 4.1305 | 3.0636 | 3.6856 | 3.722 | 3.7717 | 3.0636 | 4.2297 | 4.765 | 4.7977 | 4.8412 | 5.1257
2021-08-09 22:00 | 3.2389 | 3.5652 | 3.6088 | 3.6622 | 3.7245 | 2.6861 | 3.2353 | 3.2694 | 3.3158 | 2.6861 | 3.639 | 4.1044 | 4.135 | 4.1757 | 4.4243
2021-08-09 23:00 | 2.8007 | 3.0859 | 3.1253 | 3.1734 | 3.2296 | 2.2219 | 2.6808 | 2.7115 | 2.7533 | 2.2219 | 3.277 | 3.6962 | 3.7237 | 3.7604 | 3.9843
2021-08-10 | 2.3819 | 2.6265 | 2.661 | 2.7032 | 2.7525 | 1.8862 | 2.2773 | 2.3043 | 2.341 | 1.8862 | 2.5149 | 2.8426 | 2.8668 | 2.8989 | 3.0756
2021-08-10 01:00 | 2.2673 | 2.4938 | 2.5234 | 2.5597 | 2.6019 | 1.6766 | 2.0228 | 2.0459 | 2.0774 | 1.6766 | 2.191 | 2.4759 | 2.4966 | 2.5242 | 2.6776
2021-08-10 02:00 | 2.2482 | 2.4612 | 2.4847 | 2.5134 | 2.5468 | 1.6004 | 1.924 | 1.9423 | 1.9673 | 1.6004 | 2.191 | 2.4673 | 2.4838 | 2.5056 | 2.6521
2021-08-10 03:00 | 2.3054 | 2.5108 | 2.5282 | 2.5495 | 2.5744 | 1.6004 | 1.9154 | 1.929 | 1.9475 | 1.6004 | 2.553 | 2.8612 | 2.8734 | 2.8896 | 3.0494
2021-08-10 04:00 | 2.4959 | 2.7054 | 2.7177 | 2.7327 | 2.7502 | 1.7338 | 2.0656 | 2.0752 | 2.0883 | 1.7338 | 2.7817 | 3.1082 | 3.1167 | 3.1282 | 3.2947
2021-08-10 05:00 | 2.8188 | 3.0484 | 3.0586 | 3.0711 | 3.0857 | 2.1448 | 2.5483 | 2.5563 | 2.5672 | 2.1448 | 3.2389 | 3.6135 | 3.6206 | 3.6302 | 3.8196
2021-08-10 06:00 | 3.6581 | 3.9534 | 3.9653 | 3.98 | 3.997 | 2.8714 | 3.4092 | 3.4185 | 3.4312 | 2.8714 | 4.725 | 5.2673 | 5.2756 | 5.2867 | 5.5598
2021-08-10 07:00 | 4.1154 | 4.4538 | 4.4703 | 4.4906 | 4.5143 | 3.1056 | 3.6924 | 3.7053 | 3.7229 | 3.1056 | 5.1632 | 5.7607 | 5.7723 | 5.7877 | 6.09
2021-08-10 08:00 | 3.7534 | 4.0782 | 4.1016 | 4.1302 | 4.1636 | 2.7166 | 3.2426 | 3.2608 | 3.2857 | 2.7166 | 3.674 | 4.1152 | 4.1316 | 4.1533 | 4.3814
2021-08-10 09:00 | 3.0865 | 3.376 | 3.4067 | 3.4442 | 3.488 | 1.9434 | 2.3394 | 2.3633 | 2.396 | 1.9434 | 2.0577 | 2.3291 | 2.3506 | 2.3792 | 2.5265
2021-08-10 10:00 | 2.534 | 2.7934 | 2.8296 | 2.874 | 2.9258 | 1.3908 | 1.6946 | 1.7229 | 1.7615 | 1.3908 | 0.97168 | 1.1301 | 1.1555 | 1.1892 | 1.283
2021-08-10 11:00 | 2.3625 | 2.6135 | 2.652 | 2.6991 | 2.754 | 1.1762 | 1.4443 | 1.4743 | 1.5153 | 1.1762 | 0.89547 | 1.0485 | 1.0754 | 1.1113 | 1.2033
2021-08-10 12:00 | 2.0958 | 2.3259 | 2.3638 | 2.4103 | 2.4644 | 1.0206 | 1.2596 | 1.2892 | 1.3296 | 1.0206 | 0.81926 | 0.96303 | 0.98962 | 1.0249 | 1.1122
2021-08-10 13:00 | 2.3625 | 2.6074 | 2.6428 | 2.6862 | 2.7367 | 1.3337 | 1.6259 | 1.6535 | 1.6912 | 1.3337 | 1.0288 | 1.1924 | 1.2172 | 1.2502 | 1.3461
2021-08-10 14:00 | 2.6293 | 2.8886 | 2.9212 | 2.9612 | 3.0078 | 1.6004 | 1.9371 | 1.9625 | 1.9973 | 1.6004 | 1.448 | 1.6544 | 1.6772 | 1.7076 | 1.8235
2021-08-10 15:00 | 2.7245 | 2.9874 | 3.0182 | 3.0559 | 3.0998 | 1.6385 | 1.9795 | 2.0035 | 2.0363 | 1.6385 | 1.829 | 2.0753 | 2.0968 | 2.1255 | 2.2604
2021-08-10 16:00 | 2.8579 | 3.1298 | 3.1601 | 3.1973 | 3.2407 | 2.0464 | 2.4606 | 2.4843 | 2.5167 | 2.0464 | 2.915 | 3.2815 | 3.3027 | 3.331 | 3.5251
2021-08-10 17:00 | 3.4485 | 3.7679 | 3.8 | 3.8394 | 3.8853 | 2.9089 | 3.4822 | 3.5073 | 3.5416 | 2.9089 | 4.2678 | 4.7872 | 4.8098 | 4.8397 | 5.1101
2021-08-10 18:00 | 3.62 | 3.9594 | 3.9954 | 4.0394 | 4.0906 | 3.2389 | 3.8774 | 3.9055 | 3.9437 | 3.2389 | 4.4774 | 5.0253 | 5.0505 | 5.0839 | 5.3701
2021-08-10 19:00 | 3.6771 | 4.0306 | 4.0715 | 4.1216 | 4.18 | 3.3533 | 4.0196 | 4.0515 | 4.0951 | 3.3533 | 4.9346 | 5.5404 | 5.569 | 5.6071 | 5.9239
2021-08-10 20:00 | 3.6581 | 4.0198 | 4.0657 | 4.1218 | 4.1872 | 3.1246 | 3.7565 | 3.7923 | 3.8411 | 3.1246 | 4.8203 | 5.4202 | 5.4523 | 5.495 | 5.811
2021-08-10 21:00 | 3.3723 | 3.7144 | 3.7611 | 3.8182 | 3.8849 | 3.0103 | 3.6226 | 3.659 | 3.7088 | 3.0103 | 4.3249 | 4.8709 | 4.9036 | 4.947 | 5.2368
2021-08-10 22:00 | 3.1627 | 3.4833 | 3.5269 | 3.5804 | 3.6427 | 2.5911 | 3.1231 | 3.1572 | 3.2037 | 2.5911 | 3.4485 | 3.8927 | 3.9233 | 3.9639 | 4.2021
2021-08-10 23:00 | 2.7174 | 2.9964 | 3.0358 | 3.0839 | 3.14 | 2.191 | 2.6443 | 2.675 | 2.7169 | 2.191 | 3.4866 | 3.9291 | 3.9566 | 3.9933 | 4.2287
2021-08-11 | 2.4006 | 2.6466 | 2.6811 | 2.7234 | 2.7726 | 1.8481 | 2.2323 | 2.2592 | 2.296 | 1.8481 | 2.3816 | 2.6944 | 2.7186 | 2.7507 | 2.92
2021-08-11 01:00 | 2.3244 | 2.5552 | 2.5848 | 2.6211 | 2.6633 | 1.6503 | 1.9917 | 2.0148 | 2.0463 | 1.6503 | 2.2101 | 2.4971 | 2.5178 | 2.5454 | 2.6998
2021-08-11 02:00 | 2.172 | 2.3794 | 2.4028 | 2.4315 | 2.465 | 1.4975 | 1.8024 | 1.8207 | 1.8456 | 1.4975 | 2.3054 | 2.5944 | 2.6108 | 2.6326 | 2.7855
2021-08-11 03:00 | 2.2482 | 2.4494 | 2.4668 | 2.4881 | 2.513 | 1.5242 | 1.8254 | 1.839 | 1.8575 | 1.5242 | 2.191 | 2.459 | 2.4711 | 2.4874 | 2.6272
2021-08-11 04:00 | 2.3816 | 2.5826 | 2.5949 | 2.6099 | 2.6274 | 1.5988 | 1.9062 | 1.9158 | 1.9288 | 1.5988 | 2.3625 | 2.6424 | 2.651 | 2.6624 | 2.8059
2021-08-11 05:00 | 2.7047 | 2.9258 | 2.9361 | 2.9486 | 2.9632 | 2.1339 | 2.5354 | 2.5434 | 2.5543 | 2.1339 | 3.5438 | 3.9522 | 3.9594 | 3.9689 | 4.1751
2021-08-11 06:00 | 3.4531 | 3.7332 | 3.7451 | 3.7597 | 3.7767 | 2.7245 | 3.2356 | 3.2449 | 3.2576 | 2.7245 | 4.1129 | 4.587 | 4.5954 | 4.6065 | 4.8459
2021-08-11 07:00 | 3.8677 | 4.1877 | 4.2042 | 4.2245 | 4.2482 | 2.7245 | 3.2422 | 3.2551 | 3.2728 | 2.7245 | 4.2487 | 4.7444 | 4.756 | 4.7715 | 5.0235
2021-08-11 08:00 | 3.4413 | 3.743 | 3.7664 | 3.795 | 3.8284 | 2.3625 | 2.8242 | 2.8425 | 2.8674 | 2.3625 | 3.3533 | 3.7588 | 3.7752 | 3.7969 | 4.0073
2021-08-11 09:00 | 2.6293 | 2.8848 | 2.9154 | 2.953 | 2.9968 | 1.5336 | 1.8553 | 1.8792 | 1.9119 | 1.5336 | 1.5242 | 1.7363 | 1.7578 | 1.7864 | 1.9043
2021-08-11 10:00 | 2.3625 | 2.6091 | 2.6454 | 2.6898 | 2.7415 | 1.2575 | 1.5371 | 1.5654 | 1.604 | 1.2575 | 1.2956 | 1.49 | 1.5154 | 1.5492 | 1.6608
2021-08-11 11:00 | 2.3816 | 2.634 | 2.6724 | 2.7195 | 2.7745 | 1.1821 | 1.4512 | 1.4812 | 1.5222 | 1.1821 | 0.81926 | 0.96378 | 0.99074 | 1.0266 | 1.1144
2021-08-11 12:00 | 2.2101 | 2.4487 | 2.4866 | 2.5331 | 2.5872 | 1.2575 | 1.5395 | 1.5691 | 1.6095 | 1.2575 | 1.0669 | 1.2383 | 1.2649 | 1.3002 | 1.4011
2021-08-11 13:00 | 2.4197 | 2.6689 | 2.7043 | 2.7476 | 2.7981 | 1.448 | 1.7609 | 1.7885 | 1.8262 | 1.448 | 1.7528 | 1.9969 | 2.0217 | 2.0547 | 2.1905
2021-08-11 14:00 | 2.191 | 2.4178 | 2.4505 | 2.4904 | 2.537 | 1.3527 | 1.6445 | 1.6699 | 1.7047 | 1.3527 | 1.3146 | 1.5061 | 1.529 | 1.5594 | 1.668
2021-08-11 15:00 | 2.4387 | 2.6803 | 2.7111 | 2.7488 | 2.7928 | 1.467 | 1.7769 | 1.8009 | 1.8337 | 1.467 | 1.9815 | 2.2446 | 2.2662 | 2.2949 | 2.4381
2021-08-11 16:00 | 2.6293 | 2.8842 | 2.9145 | 2.9517 | 2.995 | 1.9422 | 2.3376 | 2.3613 | 2.3936 | 1.9422 | 2.6293 | 2.9639 | 2.9852 | 3.0134 | 3.1918
2021-08-11 17:00 | 3.1056 | 3.3994 | 3.4316 | 3.471 | 3.5169 | 2.5508 | 3.0591 | 3.0842 | 3.1185 | 2.5508 | 3.6759 | 4.1295 | 4.152 | 4.182 | 4.4198
2021-08-11 18:00 | 3.258 | 3.5705 | 3.6065 | 3.6505 | 3.7017 | 2.8769 | 3.4498 | 3.4778 | 3.5161 | 2.8769 | 4.0963 | 4.6019 | 4.627 | 4.6605 | 4.9257
2021-08-11 19:00 | 3.3533 | 3.6826 | 3.7235 | 3.7736 | 3.832 | 2.7817 | 3.3443 | 3.3762 | 3.4198 | 2.7817 | 4.4202 | 4.9687 | 4.9974 | 5.0355 | 5.324
2021-08-11 20:00 | 3.2199 | 3.549 | 3.5949 | 3.651 | 3.7165 | 2.7245 | 3.2838 | 3.3196 | 3.3684 | 2.7245 | 4.5155 | 5.0814 | 5.1136 | 5.1562 | 5.4555
2021-08-11 21:00 | 3.0103 | 3.3255 | 3.3722 | 3.4293 | 3.496 | 2.6199 | 3.1615 | 3.1979 | 3.2476 | 2.6199 | 3.5819 | 4.0451 | 4.0778 | 4.1213 | 4.3702
2021-08-11 22:00 | 2.6864 | 2.9716 | 3.0152 | 3.0686 | 3.1309 | 2.3093 | 2.7902 | 2.8242 | 2.8707 | 2.3093 | 3.2389 | 3.6598 | 3.6904 | 3.731 | 3.9577
2021-08-11 23:00 | 2.5149 | 2.7789 | 2.8182 | 2.8664 | 2.9225 | 1.9624 | 2.3742 | 2.4049 | 2.4468 | 1.9624 | 2.8007 | 3.1669 | 3.1944 | 3.231 | 3.4288
2021-08-12 | 2.191 | 2.4215 | 2.456 | 2.4982 | 2.5475 | 1.6237 | 1.9672 | 1.9941 | 2.0309 | 1.6237 | 2.2101 | 2.5038 | 2.528 | 2.5601 | 2.7201
2021-08-12 01:00 | 2.172 | 2.3914 | 2.4211 | 2.4573 | 2.4996 | 1.5623 | 1.8878 | 1.9109 | 1.9424 | 1.5623 | 1.9243 | 2.1795 | 2.2002 | 2.2278 | 2.3666
2021-08-12 02:00 | 2.191 | 2.3998 | 2.4233 | 2.452 | 2.4854 | 1.4099 | 1.6989 | 1.7172 | 1.7422 | 1.4099 | 2.0577 | 2.3191 | 2.3356 | 2.3574 | 2.4966
2021-08-12 03:00 | 2.1339 | 2.3266 | 2.344 | 2.3653 | 2.3902 | 1.4099 | 1.6903 | 1.7039 | 1.7225 | 1.4099 | 2.1529 | 2.4166 | 2.4288 | 2.445 | 2.5827
2021-08-12 04:00 | 2.2863 | 2.4803 | 2.4925 | 2.5075 | 2.525 | 1.5887 | 1.8942 | 1.9038 | 1.9169 | 1.5887 | 2.191 | 2.4518 | 2.4604 | 2.4718 | 2.6059
2021-08-12 05:00 | 2.6095 | 2.8235 | 2.8338 | 2.8463 | 2.8609 | 1.997 | 2.3737 | 2.3816 | 2.3925 | 1.997 | 3.0675 | 3.4229 | 3.4301 | 3.4396 | 3.6196
2021-08-12 06:00 | 3.4485 | 3.7283 | 3.7402 | 3.7548 | 3.7718 | 2.5721 | 3.0555 | 3.0648 | 3.0776 | 2.5721 | 3.9639 | 4.4215 | 4.4299 | 4.441 | 4.6722
2021-08-12 07:00 | 3.7152 | 4.0239 | 4.0405 | 4.0608 | 4.0844 | 2.6864 | 3.1972 | 3.2101 | 3.2278 | 2.6864 | 4.344 | 4.8503 | 4.8619 | 4.8773 | 5.1346
2021-08-12 08:00 | 3.5819 | 3.894 | 3.9174 | 3.946 | 3.9794 | 2.3054 | 2.7567 | 2.775 | 2.7999 | 2.3054 | 3.1196 | 3.4991 | 3.5155 | 3.5373 | 3.7348
2021-08-12 09:00 | 2.8687 | 3.142 | 3.1727 | 3.2103 | 3.254 | 1.6059 | 1.9408 | 1.9647 | 1.9974 | 1.6059 | 1.5242 | 1.7363 | 1.7578 | 1.7864 | 1.9043
2021-08-12 10:00 | 2.4768 | 2.732 | 2.7682 | 2.8126 | 2.8644 | 1.2003 | 1.4696 | 1.4978 | 1.5365 | 1.2003 | 0.91452 | 1.0666 | 1.092 | 1.1257 | 1.2164
2021-08-12 11:00 | 2.2471 | 2.4895 | 2.528 | 2.5751 | 2.63 | 0.99073 | 1.2251 | 1.2551 | 1.2961 | 0.99073 | 0.7621 | 0.90026 | 0.92722 | 0.96305 | 1.0478
2021-08-12 12:00 | 1.9053 | 2.1212 | 2.1591 | 2.2056 | 2.2597 | 0.87642 | 1.0893 | 1.1189 | 1.1593 | 0.87642 | 0.93358 | 1.0901 | 1.1167 | 1.152 | 1.2455
2021-08-12 13:00 | 1.9434 | 2.1571 | 2.1925 | 2.2359 | 2.2864 | 0.85737 | 1.0632 | 1.0908 | 1.1285 | 0.85737 | 1.0098 | 1.1712 | 1.196 | 1.229 | 1.3239
2021-08-12 14:00 | 2.1529 | 2.3769 | 2.4095 | 2.4495 | 2.496 | 1.086 | 1.3294 | 1.3548 | 1.3896 | 1.086 | 0.83831 | 0.97684 | 0.99971 | 1.0301 | 1.1125
2021-08-12 15:00 | 2.3244 | 2.5575 | 2.5883 | 2.626 | 2.67 | 1.4578 | 1.766 | 1.79 | 1.8228 | 1.4578 | 1.5814 | 1.8 | 1.8216 | 1.8503 | 1.9715
2021-08-12 16:00 | 2.9341 | 3.2117 | 3.242 | 3.2792 | 3.3225 | 2.2304 | 2.6781 | 2.7018 | 2.7341 | 2.2304 | 2.7055 | 3.0486 | 3.0698 | 3.0981 | 3.2806
2021-08-12 17:00 | 3.5431 | 3.8695 | 3.9017 | 3.941 | 3.987 | 3.1818 | 3.8046 | 3.8297 | 3.8639 | 3.1818 | 4.4729 | 5.0152 | 5.0377 | 5.0677 | 5.3494
2021-08-12 18:00 | 3.9248 | 4.287 | 4.3229 | 4.3669 | 4.4182 | 3.5438 | 4.2376 | 4.2656 | 4.3039 | 3.5438 | 5.3919 | 6.0416 | 6.0668 | 6.1002 | 6.4366
2021-08-12 19:00 | 3.9248 | 4.2967 | 4.3376 | 4.3877 | 4.4461 | 3.5438 | 4.2446 | 4.2766 | 4.3201 | 3.5438 | 5.7158 | 6.4084 | 6.4371 | 6.4752 | 6.8349
2021-08-12 20:00 | 3.9058 | 4.2859 | 4.3318 | 4.3879 | 4.4533 | 3.2199 | 3.869 | 3.9048 | 3.9536 | 3.2199 | 6.0968 | 6.8387 | 6.8708 | 6.9135 | 7.2998
2021-08-12 21:00 | 3.7152 | 4.0828 | 4.1295 | 4.1867 | 4.2533 | 3.277 | 3.9377 | 3.9742 | 4.0239 | 3.277 | 4.5536 | 5.1249 | 5.1576 | 5.2011 | 5.5034
2021-08-12 22:00 | 3.3652 | 3.7009 | 3.7445 | 3.7979 | 3.8602 | 2.8383 | 3.4151 | 3.4492 | 3.4956 | 2.8383 | 4.6679 | 5.2477 | 5.2783 | 5.319 | 5.6242
2021-08-12 23:00 | 2.9531 | 3.2497 | 3.289 | 3.3372 | 3.3933 | 2.3856 | 2.8742 | 2.9048 | 2.9467 | 2.3856 | 3.9058 | 4.3949 | 4.4224 | 4.459 | 4.7175
2021-08-13 | 2.6295 | 2.8926 | 2.9271 | 2.9693 | 3.0186 | 2.0395 | 2.4584 | 2.4854 | 2.5221 | 2.0395 | 3.1437 | 3.5413 | 3.5655 | 3.5976 | 3.8088
2021-08-13 01:00 | 2.4959 | 2.7394 | 2.769 | 2.8053 | 2.8475 | 1.8672 | 2.2479 | 2.271 | 2.3025 | 1.8672 | 2.6674 | 3.0052 | 3.0259 | 3.0535 | 3.2331
2021-08-13 02:00 | 2.3816 | 2.6045 | 2.628 | 2.6567 | 2.6901 | 1.7528 | 2.1041 | 2.1224 | 2.1473 | 1.7528 | 2.4197 | 2.7214 | 2.7378 | 2.7597 | 2.9188
2021-08-13 03:00 | 2.4578 | 2.6746 | 2.692 | 2.7133 | 2.7381 | 1.7719 | 2.118 | 2.1316 | 2.1501 | 1.7719 | 2.8198 | 3.1576 | 3.1698 | 3.186 | 3.3604
2021-08-13 04:00 | 2.5747 | 2.7902 | 2.8024 | 2.8174 | 2.8349 | 1.7909 | 2.1332 | 2.1427 | 2.1558 | 1.7909 | 2.7245 | 3.0446 | 3.0532 | 3.0646 | 3.2281
2021-08-13 05:00 | 2.7817 | 3.0085 | 3.0187 | 3.0313 | 3.0459 | 2.1657 | 2.573 | 2.581 | 2.5919 | 2.1657 | 3.277 | 3.6558 | 3.663 | 3.6725 | 3.8641
2021-08-13 06:00 | 3.2961 | 3.5645 | 3.5764 | 3.591 | 3.6081 | 2.5149 | 2.988 | 2.9973 | 3.01 | 2.5149 | 4.6488 | 5.1826 | 5.1909 | 5.2021 | 5.4709
2021-08-13 07:00 | 3.9439 | 4.2695 | 4.2861 | 4.3064 | 4.3301 | 3.0675 | 3.6473 | 3.6603 | 3.6779 | 3.0675 | 4.706 | 5.2525 | 5.2642 | 5.2796 | 5.5568
2021-08-13 08:00 | 4.0772 | 4.4262 | 4.4496 | 4.4782 | 4.5116 | 3.2008 | 3.8146 | 3.8328 | 3.8578 | 3.2008 | 4.6488 | 5.1985 | 5.2149 | 5.2367 | 5.5183
2021-08-13 09:00 | 4.0582 | 4.4199 | 4.4506 | 4.4882 | 4.5319 | 3.2008 | 3.8249 | 3.8489 | 3.8815 | 3.2008 | 4.7631 | 5.3356 | 5.3571 | 5.3857 | 5.6817
2021-08-13 10:00 | 3.0865 | 3.387 | 3.4232 | 3.4676 | 3.5194 | 2.4387 | 2.9326 | 2.9609 | 2.9995 | 2.4387 | 2.8769 | 3.2473 | 3.2727 | 3.3065 | 3.505
2021-08-13 11:00 | 2.678 | 2.9524 | 2.9909 | 3.038 | 3.0929 | 1.9243 | 2.328 | 2.358 | 2.399 | 1.9243 | 1.6957 | 1.9377 | 1.9647 | 2.0005 | 2.1366
2021-08-13 12:00 | 2.3054 | 2.551 | 2.589 | 2.6354 | 2.6896 | 1.6195 | 1.9671 | 1.9967 | 2.0371 | 1.6195 | 1.2956 | 1.4923 | 1.5189 | 1.5543 | 1.6677
2021-08-13 13:00 | 2.0767 | 2.3004 | 2.3358 | 2.3791 | 2.4297 | 1.4861 | 1.8059 | 1.8336 | 1.8713 | 1.4861 | 1.105 | 1.2771 | 1.3019 | 1.3348 | 1.435
2021-08-13 14:00 | 2.0767 | 2.295 | 2.3276 | 2.3676 | 2.4142 | 1.4735 | 1.7871 | 1.8126 | 1.8474 | 1.4735 | 1.2384 | 1.4215 | 1.4443 | 1.4747 | 1.5791
2021-08-13 15:00 | 2.3435 | 2.578 | 2.6088 | 2.6465 | 2.6905 | 1.6914 | 2.0419 | 2.0659 | 2.0987 | 1.6914 | 2.3435 | 2.6469 | 2.6685 | 2.6972 | 2.8603
2021-08-13 16:00 | 2.8007 | 3.0684 | 3.0987 | 3.1359 | 3.1792 | 2.1749 | 2.6125 | 2.6362 | 2.6685 | 2.1749 | 2.8769 | 3.2391 | 3.2604 | 3.2887 | 3.4806
2021-08-13 17:00 | 3.6009 | 3.9316 | 3.9638 | 4.0032 | 4.0491 | 3.0251 | 3.6195 | 3.6446 | 3.6788 | 3.0251 | 4.4668 | 5.0084 | 5.031 | 5.0609 | 5.3423
2021-08-13 18:00 | 3.7343 | 4.0823 | 4.1182 | 4.1622 | 4.2135 | 3.3723 | 4.035 | 4.063 | 4.1013 | 3.3723 | 6.0016 | 6.7191 | 6.7443 | 6.7777 | 7.1477
2021-08-13 19:00 | 3.7152 | 4.0715 | 4.1125 | 4.1625 | 4.2209 | 3.3533 | 4.0196 | 4.0515 | 4.0951 | 3.3533 | 5.2585 | 5.9003 | 5.929 | 5.967 | 6.3017
2021-08-13 20:00 | 3.6771 | 4.0403 | 4.0861 | 4.1423 | 4.2077 | 3.1707 | 3.8109 | 3.8467 | 3.8955 | 3.1707 | 5.2013 | 5.8436 | 5.8758 | 5.9184 | 6.2554
2021-08-13 21:00 | 3.4295 | 3.7758 | 3.8225 | 3.8796 | 3.9463 | 3.0675 | 3.6902 | 3.7266 | 3.7763 | 3.0675 | 5.0489 | 5.6754 | 5.7081 | 5.7516 | 6.0811
2021-08-13 22:00 | 3.277 | 3.6061 | 3.6498 | 3.7032 | 3.7655 | 2.8049 | 3.3756 | 3.4097 | 3.4561 | 2.8049 | 4.001 | 4.5067 | 4.5373 | 4.5779 | 4.8465
2021-08-13 23:00 | 2.896 | 3.1883 | 3.2276 | 3.2758 | 3.3319 | 2.3323 | 2.8112 | 2.8419 | 2.8838 | 2.3323 | 3.5247 | 3.9714 | 3.999 | 4.0356 | 4.2732
2021-08-14 | 2.7626 | 3.0356 | 3.0701 | 3.1123 | 3.1615 | 2.1309 | 2.5664 | 2.5933 | 2.6301 | 2.1309 | 3.1056 | 3.4989 | 3.5231 | 3.5552 | 3.7644
2021-08-14 01:00 | 2.4959 | 2.7394 | 2.769 | 2.8053 | 2.8475 | 1.8862 | 2.2704 | 2.2935 | 2.325 | 1.8862 | 2.553 | 2.8782 | 2.8989 | 2.9265 | 3.0998
2021-08-14 02:00 | 2.4387 | 2.6659 | 2.6894 | 2.7181 | 2.7515 | 1.7576 | 2.1097 | 2.1279 | 2.1529 | 1.7576 | 2.9531 | 3.3142 | 3.3306 | 3.3525 | 3.5409
2021-08-14 03:00 | 2.4959 | 2.7155 | 2.7329 | 2.7542 | 2.7791 | 1.762 | 2.1063 | 2.1199 | 2.1384 | 1.762 | 2.5911 | 2.9036 | 2.9158 | 2.932 | 3.0938
2021-08-14 04:00 | 2.553 | 2.7668 | 2.7791 | 2.7941 | 2.8116 | 1.8016 | 2.1458 | 2.1554 | 2.1684 | 1.8016 | 2.6674 | 2.9811 | 2.9897 | 3.0011 | 3.1614
2021-08-14 05:00 | 2.7099 | 2.9314 | 2.9416 | 2.9541 | 2.9687 | 2.0637 | 2.4526 | 2.4606 | 2.4714 | 2.0637 | 3.0211 | 3.3714 | 3.3786 | 3.3881 | 3.5655
2021-08-14 06:00 | 2.8803 | 3.1178 | 3.1297 | 3.1444 | 3.1614 | 2.3244 | 2.7629 | 2.7722 | 2.7849 | 2.3244 | 3.9629 | 4.4204 | 4.4287 | 4.4399 | 4.671
2021-08-14 07:00 | 3.0484 | 3.3075 | 3.3241 | 3.3444 | 3.368 | 2.4578 | 2.9271 | 2.94 | 2.9577 | 2.4578 | 4.0201 | 4.4903 | 4.502 | 4.5174 | 4.7568
2021-08-14 08:00 | 3.0865 | 3.3618 | 3.3852 | 3.4138 | 3.4472 | 2.553 | 3.0493 | 3.0676 | 3.0925 | 2.553 | 3.7857 | 4.2393 | 4.2557 | 4.2775 | 4.5116
2021-08-14 09:00 | 2.8573 | 3.1298 | 3.1605 | 3.198 | 3.2418 | 2.3435 | 2.8121 | 2.836 | 2.8687 | 2.3435 | 3.5438 | 3.9806 | 4.0021 | 4.0306 | 4.2596
2021-08-14 10:00 | 2.4578 | 2.7115 | 2.7477 | 2.7921 | 2.8439 | 1.8957 | 2.291 | 2.3193 | 2.3579 | 1.8957 | 2.2673 | 2.5698 | 2.5952 | 2.629 | 2.794
2021-08-14 11:00 | 2.0767 | 2.3064 | 2.3449 | 2.392 | 2.447 | 1.81 | 2.193 | 2.223 | 2.264 | 1.81 | 1.5242 | 1.7472 | 1.7741 | 1.8099 | 1.9366
2021-08-14 12:00 | 1.9434 | 2.1621 | 2.2001 | 2.2465 | 2.3007 | 1.5242 | 1.8546 | 1.8842 | 1.9246 | 1.5242 | 1.2194 | 1.4077 | 1.4342 | 1.4696 | 1.5788
2021-08-14 13:00 | 1.8862 | 2.0957 | 2.1311 | 2.1744 | 2.225 | 1.3908 | 1.6934 | 1.721 | 1.7587 | 1.3908 | 1.1622 | 1.3406 | 1.3654 | 1.3984 | 1.5017
2021-08-14 14:00 | 1.9243 | 2.1313 | 2.1639 | 2.2038 | 2.2504 | 1.4742 | 1.788 | 1.8135 | 1.8482 | 1.4742 | 1.2956 | 1.485 | 1.5078 | 1.5382 | 1.6458
2021-08-14 15:00 | 2.2291 | 2.4552 | 2.486 | 2.5237 | 2.5676 | 1.6794 | 2.0277 | 2.0518 | 2.0846 | 1.6794 | 2.1148 | 2.3928 | 2.4144 | 2.4431 | 2.5937
2021-08-14 16:00 | 2.7245 | 2.9865 | 3.0169 | 3.054 | 3.0974 | 2.3234 | 2.788 | 2.8117 | 2.844 | 2.3234 | 3.2961 | 3.7049 | 3.7262 | 3.7545 | 3.9695
2021-08-14 17:00 | 3.5624 | 3.8903 | 3.9224 | 3.9618 | 4.0077 | 3.258 | 3.8946 | 3.9197 | 3.954 | 3.258 | 4.8584 | 5.4435 | 5.4661 | 5.496 | 5.7989
2021-08-14 18:00 | 3.7534 | 4.1027 | 4.1387 | 4.1826 | 4.2339 | 3.3723 | 4.035 | 4.063 | 4.1013 | 3.3723 | 5.2204 | 5.851 | 5.8762 | 5.9097 | 6.2367
2021-08-14 19:00 | 3.6962 | 4.0511 | 4.092 | 4.1421 | 4.2005 | 3.3151 | 3.9745 | 4.0065 | 4.05 | 3.3151 | 5.6396 | 6.3237 | 6.3524 | 6.3905 | 6.7461
2021-08-14 20:00 | 3.639 | 3.9993 | 4.0452 | 4.1013 | 4.1668 | 3.277 | 3.9366 | 3.9723 | 4.0212 | 3.277 | 5.2013 | 5.8436 | 5.8758 | 5.9184 | 6.2554
2021-08-14 21:00 | 3.639 | 4.001 | 4.0477 | 4.1048 | 4.1714 | 3.1246 | 3.7577 | 3.7941 | 3.8438 | 3.1246 | 4.8965 | 5.506 | 5.5387 | 5.5822 | 5.9034
2021-08-14 22:00 | 3.3342 | 3.6675 | 3.7112 | 3.7646 | 3.8269 | 2.7863 | 3.3537 | 3.3878 | 3.4343 | 2.7863 | 4.8393 | 5.4383 | 5.4689 | 5.5095 | 5.8241
2021-08-14 23:00 | 3.1056 | 3.4134 | 3.4528 | 3.5009 | 3.5571 | 2.4588 | 2.9606 | 2.9913 | 3.0332 | 2.4588 | 3.7152 | 4.1831 | 4.2107 | 4.2473 | 4.4953
2021-08-15 | 2.7256 | 2.9957 | 3.0303 | 3.0725 | 3.1217 | 2.0717 | 2.4965 | 2.5234 | 2.5601 | 2.0717 | 2.7626 | 3.1178 | 3.142 | 3.1741 | 3.3644
2021-08-15 01:00 | 2.6674 | 2.9236 | 2.9532 | 2.9895 | 3.0318 | 1.8837 | 2.2674 | 2.2905 | 2.3221 | 1.8837 | 2.5149 | 2.8358 | 2.8566 | 2.8841 | 3.0554
2021-08-15 02:00 | 2.4197 | 2.6455 | 2.6689 | 2.6976 | 2.7311 | 1.7719 | 2.1266 | 2.1449 | 2.1698 | 1.7719 | 2.4578 | 2.7637 | 2.7802 | 2.802 | 2.9632
2021-08-15 03:00 | 2.4578 | 2.6746 | 2.692 | 2.7133 | 2.7381 | 1.7528 | 2.0955 | 2.1091 | 2.1276 | 1.7528 | 2.534 | 2.8401 | 2.8523 | 2.8685 | 3.0271
2021-08-15 04:00 | 2.5911 | 2.8078 | 2.82 | 2.835 | 2.8525 | 1.81 | 2.1557 | 2.1652 | 2.1783 | 1.81 | 2.5721 | 2.8753 | 2.8838 | 2.8953 | 3.0503
2021-08-15 05:00 | 2.6864 | 2.9062 | 2.9164 | 2.9289 | 2.9435 | 1.9426 | 2.3094 | 2.3174 | 2.3283 | 1.9426 | 2.896 | 3.2324 | 3.2395 | 3.2491 | 3.4197
2021-08-15 06:00 | 2.8007 | 3.0323 | 3.0442 | 3.0588 | 3.0759 | 2.1826 | 2.5954 | 2.6047 | 2.6174 | 2.1826 | 3.5628 | 3.9758 | 3.9841 | 3.9952 | 4.2044
2021-08-15 07:00 | 2.8198 | 3.0619 | 3.0784 | 3.0987 | 3.1224 | 2.4197 | 2.8821 | 2.895 | 2.9127 | 2.4197 | 3.7534 | 4.1939 | 4.2055 | 4.221 | 4.4458
2021-08-15 08:00 | 2.8007 | 3.0547 | 3.0781 | 3.1068 | 3.1402 | 2.4959 | 2.9818 | 3 | 3.025 | 2.4959 | 3.5819 | 4.0128 | 4.0292 | 4.051 | 4.274
2021-08-15 09:00 | 2.5721 | 2.8234 | 2.854 | 2.8916 | 2.9354 | 2.2335 | 2.6821 | 2.7061 | 2.7387 | 2.2335 | 3.0103 | 3.3878 | 3.4093 | 3.4378 | 3.6374
2021-08-15 10:00 | 2.5721 | 2.8343 | 2.8706 | 2.915 | 2.9667 | 2.0657 | 2.4918 | 2.5201 | 2.5587 | 2.0657 | 2.2863 | 2.591 | 2.6164 | 2.6501 | 2.8162
2021-08-15 11:00 | 2.1339 | 2.3679 | 2.4063 | 2.4534 | 2.5084 | 1.7719 | 2.1479 | 2.178 | 2.219 | 1.7719 | 1.6957 | 1.9377 | 1.9647 | 2.0005 | 2.1366
2021-08-15 12:00 | 1.9815 | 2.2031 | 2.241 | 2.2874 | 2.3416 | 1.5433 | 1.8771 | 1.9067 | 1.9471 | 1.5433 | 1.1813 | 1.3653 | 1.3919 | 1.4272 | 1.5344
2021-08-15 13:00 | 1.7338 | 1.932 | 1.9674 | 2.0107 | 2.0612 | 1.4099 | 1.7159 | 1.7435 | 1.7812 | 1.4099 | 1.1241 | 1.2983 | 1.3231 | 1.356 | 1.4572
2021-08-15 14:00 | 2.3054 | 2.5406 | 2.5733 | 2.6132 | 2.6598 | 1.6576 | 2.0046 | 2.03 | 2.0648 | 1.6576 | 1.2765 | 1.4638 | 1.4867 | 1.5171 | 1.6236
2021-08-15 15:00 | 2.4959 | 2.7417 | 2.7725 | 2.8102 | 2.8542 | 2.0386 | 2.4521 | 2.4762 | 2.509 | 2.0386 | 2.4578 | 2.7739 | 2.7955 | 2.8242 | 2.9936
2021-08-15 16:00 | 2.9722 | 3.2526 | 3.283 | 3.3201 | 3.3635 | 2.4959 | 2.9917 | 3.0154 | 3.0477 | 2.4959 | 3.9629 | 4.4459 | 4.4672 | 4.4955 | 4.7471
2021-08-15 17:00 | 3.6581 | 3.993 | 4.0252 | 4.0646 | 4.1105 | 3.3338 | 3.9842 | 4.0093 | 4.0436 | 3.3338 | 5.3919 | 6.0364 | 6.0589 | 6.0889 | 6.4211
2021-08-15 18:00 | 3.8867 | 4.246 | 4.2819 | 4.3259 | 4.3772 | 3.5628 | 4.2601 | 4.2881 | 4.3264 | 3.5628 | 6.0016 | 6.7191 | 6.7443 | 6.7777 | 7.1477
2021-08-15 19:00 | 3.8486 | 4.2148 | 4.2557 | 4.3058 | 4.3642 | 3.5057 | 4.1996 | 4.2315 | 4.2751 | 3.5057 | 4.9918 | 5.6039 | 5.6325 | 5.6706 | 5.9906
2021-08-15 20:00 | 3.7152 | 4.0812 | 4.1271 | 4.1832 | 4.2487 | 3.258 | 3.914 | 3.9498 | 3.9987 | 3.258 | 4.7441 | 5.3355 | 5.3676 | 5.4103 | 5.7222
2021-08-15 21:00 | 3.5628 | 3.9191 | 3.9658 | 4.0229 | 4.0896 | 3.0103 | 3.6226 | 3.659 | 3.7088 | 3.0103 | 4.5917 | 5.1673 | 5.2 | 5.2434 | 5.5478
2021-08-15 22:00 | 3.1658 | 3.4866 | 3.5303 | 3.5837 | 3.646 | 2.7308 | 3.2881 | 3.3222 | 3.3687 | 2.7308 | 3.7152 | 4.1891 | 4.2197 | 4.2603 | 4.5132
2021-08-15 23:00 | 2.8198 | 3.1064 | 3.1457 | 3.1939 | 3.25 | 2.3097 | 2.7846 | 2.8152 | 2.8571 | 2.3097 | 2.915 | 3.2939 | 3.3215 | 3.3581 | 3.5621
2021-08-16 | 2.5149 | 2.7695 | 2.804 | 2.8462 | 2.8954 | 1.9333 | 2.333 | 2.3599 | 2.3967 | 1.9333 | 2.4959 | 2.8214 | 2.8456 | 2.8777 | 3.0533
2021-08-16 01:00 | 2.4197 | 2.6575 | 2.6872 | 2.7234 | 2.7657 | 1.6957 | 2.0453 | 2.0684 | 2.1 | 1.6957 | 2.3244 | 2.6241 | 2.6448 | 2.6724 | 2.8332
2021-08-16 02:00 | 2.3435 | 2.5636 | 2.587 | 2.6157 | 2.6492 | 1.6195 | 1.9465 | 1.9648 | 1.9898 | 1.6195 | 2.0386 | 2.2979 | 2.3144 | 2.3362 | 2.4744
2021-08-16 03:00 | 2.4197 | 2.6336 | 2.651 | 2.6724 | 2.6972 | 1.5814 | 1.8929 | 1.9065 | 1.925 | 1.5814 | 2.1529 | 2.4166 | 2.4288 | 2.445 | 2.5827
2021-08-16 04:00 | 2.4197 | 2.6236 | 2.6358 | 2.6508 | 2.6683 | 1.6852 | 2.0083 | 2.0179 | 2.0309 | 1.6852 | 2.3435 | 2.6212 | 2.6298 | 2.6412 | 2.7837
2021-08-16 05:00 | 2.6403 | 2.8566 | 2.8668 | 2.8793 | 2.8939 | 1.9788 | 2.3523 | 2.3602 | 2.3711 | 1.9788 | 3.1246 | 3.4864 | 3.4936 | 3.5031 | 3.6863
2021-08-16 06:00 | 3.0294 | 3.2779 | 3.2899 | 3.3045 | 3.3215 | 2.3054 | 2.7404 | 2.7497 | 2.7624 | 2.3054 | 3.9629 | 4.4204 | 4.4287 | 4.4399 | 4.671
2021-08-16 07:00 | 3.4676 | 3.7578 | 3.7744 | 3.7947 | 3.8183 | 2.5721 | 3.0621 | 3.0751 | 3.0927 | 2.5721 | 3.982 | 4.448 | 4.4596 | 4.475 | 4.7124
2021-08-16 08:00 | 3.3914 | 3.6893 | 3.7127 | 3.7413 | 3.7747 | 2.5149 | 3.0043 | 3.0226 | 3.0475 | 2.5149 | 3.5438 | 3.9705 | 3.9869 | 4.0087 | 4.2295
2021-08-16 09:00 | 3.0675 | 3.3556 | 3.3862 | 3.4238 | 3.4676 | 2.2125 | 2.6573 | 2.6813 | 2.7139 | 2.2125 | 2.7055 | 3.049 | 3.0705 | 3.0991 | 3.2819
2021-08-16 10:00 | 2.7055 | 2.9776 | 3.0138 | 3.0582 | 3.11 | 1.9032 | 2.3 | 2.3282 | 2.3669 | 1.9032 | 1.9053 | 2.1675 | 2.1929 | 2.2267 | 2.3718
2021-08-16 11:00 | 2.4006 | 2.6544 | 2.6929 | 2.74 | 2.7949 | 1.6088 | 1.9553 | 1.9853 | 2.0263 | 1.6088 | 1.2956 | 1.4931 | 1.52 | 1.5559 | 1.6699
2021-08-16 12:00 | 2.2482 | 2.4896 | 2.5276 | 2.574 | 2.6282 | 1.5814 | 1.9221 | 1.9517 | 1.9921 | 1.5814 | 1.2956 | 1.4923 | 1.5189 | 1.5543 | 1.6677
2021-08-16 13:00 | 2.4387 | 2.6893 | 2.7247 | 2.768 | 2.8186 | 1.4861 | 1.8059 | 1.8336 | 1.8713 | 1.4861 | 1.086 | 1.2559 | 1.2807 | 1.3137 | 1.4128
2021-08-16 14:00 | 2.4959 | 2.7453 | 2.778 | 2.8179 | 2.8645 | 1.9434 | 2.3422 | 2.3677 | 2.4024 | 1.9434 | 1.5052 | 1.7179 | 1.7407 | 1.7711 | 1.8902
2021-08-16 15:00 | 2.896 | 3.1716 | 3.2024 | 3.2401 | 3.2841 | 2.191 | 2.6322 | 2.6562 | 2.689 | 2.191 | 2.5149 | 2.8375 | 2.859 | 2.8877 | 3.0603
2021-08-16 16:00 | 3.3914 | 3.7029 | 3.7333 | 3.7704 | 3.8138 | 2.9284 | 3.5026 | 3.5263 | 3.5586 | 2.9284 | 4.6488 | 5.2081 | 5.2294 | 5.2577 | 5.547
2021-08-16 17:00 | 4.0963 | 4.4638 | 4.496 | 4.5354 | 4.5813 | 3.7343 | 4.4573 | 4.4824 | 4.5166 | 3.7343 | 6.1349 | 6.8621 | 6.8846 | 6.9146 | 7.2877
2021-08-16 18:00 | 4.2678 | 4.6554 | 4.6913 | 4.7353 | 4.7866 | 3.8486 | 4.5977 | 4.6257 | 4.664 | 3.8486 | 6.1921 | 6.9308 | 6.956 | 6.9894 | 7.3699
2021-08-16 19:00 | 4.0582 | 4.44 | 4.4809 | 4.531 | 4.5894 | 3.7152 | 4.4472 | 4.4791 | 4.5227 | 3.7152 | 6.2492 | 7.0012 | 7.0299 | 7.068 | 7.4571
2021-08-16 20:00 | 3.9439 | 4.3268 | 4.3727 | 4.4288 | 4.4943 | 3.6009 | 4.3192 | 4.355 | 4.4038 | 3.6009 | 5.6586 | 6.3518 | 6.3839 | 6.4266 | 6.7887
2021-08-16 21:00 | 3.6188 | 3.9792 | 4.0259 | 4.0831 | 4.1497 | 3.277 | 3.9377 | 3.9742 | 4.0239 | 3.277 | 5.2966 | 5.9506 | 5.9834 | 6.0268 | 6.37
2021-08-16 22:00 | 3.1917 | 3.5144 | 3.558 | 3.6115 | 3.6738 | 2.865 | 3.4467 | 3.4807 | 3.5272 | 2.865 | 4.1916 | 4.7184 | 4.749 | 4.7896 | 5.0687
2021-08-16 23:00 | 2.915 | 3.2087 | 3.2481 | 3.2962 | 3.3524 | 2.3194 | 2.796 | 2.8266 | 2.8685 | 2.3194 | 3.2389 | 3.6538 | 3.6814 | 3.718 | 3.9399
2021-08-17 | 2.5547 | 2.8122 | 2.8467 | 2.889 | 2.9382 | 2.0577 | 2.4799 | 2.5068 | 2.5436 | 2.0577 | 3.4104 | 3.8377 | 3.8619 | 3.894 | 4.1199
2021-08-17 01:00 | 2.3435 | 2.5757 | 2.6053 | 2.6415 | 2.6838 | 1.7719 | 2.1353 | 2.1584 | 2.19 | 1.7719 | 2.3435 | 2.6453 | 2.666 | 2.6936 | 2.8554
2021-08-17 02:00 | 2.3435 | 2.5636 | 2.587 | 2.6157 | 2.6492 | 1.6576 | 1.9915 | 2.0098 | 2.0348 | 1.6576 | 2.2673 | 2.552 | 2.5684 | 2.5903 | 2.741
2021-08-17 03:00 | 2.3244 | 2.5313 | 2.5487 | 2.57 | 2.5949 | 1.6004 | 1.9154 | 1.929 | 1.9475 | 1.6004 | 2.4006 | 2.6918 | 2.704 | 2.7203 | 2.8716
2021-08-17 04:00 | 2.4006 | 2.6031 | 2.6154 | 2.6304 | 2.6479 | 1.6957 | 2.0206 | 2.0302 | 2.0433 | 1.6957 | 2.6293 | 2.9388 | 2.9474 | 2.9588 | 3.117
2021-08-17 05:00 | 2.7055 | 2.9266 | 2.9369 | 2.9494 | 2.964 | 1.9505 | 2.3188 | 2.3267 | 2.3376 | 1.9505 | 3.1246 | 3.4864 | 3.4936 | 3.5031 | 3.6863
2021-08-17 06:00 | 3.0103 | 3.2575 | 3.2694 | 3.284 | 3.301 | 2.4732 | 2.9387 | 2.948 | 2.9608 | 2.4732 | 4.2868 | 4.7803 | 4.7887 | 4.7998 | 5.0487
2021-08-17 07:00 | 3.4676 | 3.7578 | 3.7744 | 3.7947 | 3.8183 | 2.6864 | 3.1972 | 3.2101 | 3.2278 | 2.6864 | 4.2297 | 4.7232 | 4.7349 | 4.7503 | 5.0013
2021-08-17 08:00 | 3.4295 | 3.7302 | 3.7536 | 3.7823 | 3.8156 | 2.6565 | 3.1716 | 3.1898 | 3.2147 | 2.6565 | 3.7534 | 4.2034 | 4.2198 | 4.2416 | 4.4739
2021-08-17 09:00 | 2.896 | 3.1713 | 3.202 | 3.2396 | 3.2833 | 2.3244 | 2.7896 | 2.8135 | 2.8462 | 2.3244 | 2.8595 | 3.2202 | 3.2417 | 3.2702 | 3.4616
2021-08-17 10:00 | 2.5721 | 2.8343 | 2.8706 | 2.915 | 2.9667 | 1.7719 | 2.1448 | 2.1731 | 2.2117 | 1.7719 | 2.0577 | 2.3369 | 2.3623 | 2.3961 | 2.5496
2021-08-17 11:00 | 2.2101 | 2.4497 | 2.4882 | 2.5353 | 2.5902 | 1.5814 | 1.9229 | 1.9529 | 1.9939 | 1.5814 | 1.0669 | 1.239 | 1.266 | 1.3018 | 1.4033
2021-08-17 12:00 | 2.0958 | 2.3259 | 2.3638 | 2.4103 | 2.4644 | 1.5052 | 1.8321 | 1.8617 | 1.9021 | 1.5052 | 1.0288 | 1.1959 | 1.2225 | 1.2578 | 1.3566
2021-08-17 13:00 | 2.2482 | 2.4846 | 2.52 | 2.5634 | 2.6139 | 1.5433 | 1.8735 | 1.9011 | 1.9388 | 1.5433 | 0.78115 | 0.91716 | 0.94196 | 0.97491 | 1.0573
2021-08-17 14:00 | 1.9624 | 2.1722 | 2.2048 | 2.2448 | 2.2914 | 1.5184 | 1.8401 | 1.8656 | 1.9003 | 1.5184 | 1.2384 | 1.4215 | 1.4443 | 1.4747 | 1.5791
2021-08-17 15:00 | 2.2482 | 2.4756 | 2.5064 | 2.5441 | 2.5881 | 1.6957 | 2.047 | 2.071 | 2.1038 | 1.6957 | 2.0577 | 2.3293 | 2.3509 | 2.3796 | 2.527
2021-08-17 16:00 | 2.8061 | 3.0741 | 3.1045 | 3.1417 | 3.185 | 2.2609 | 2.7141 | 2.7378 | 2.7701 | 2.2609 | 2.8769 | 3.2391 | 3.2604 | 3.2887 | 3.4806
2021-08-17 17:00 | 3.5291 | 3.8544 | 3.8866 | 3.926 | 3.9719 | 3.2687 | 3.9073 | 3.9324 | 3.9666 | 3.2687 | 4.5917 | 5.1471 | 5.1697 | 5.1996 | 5.4879
2021-08-17 18:00 | 3.7915 | 4.1437 | 4.1796 | 4.2236 | 4.2749 | 3.3723 | 4.035 | 4.063 | 4.1013 | 3.3723 | 4.9346 | 5.5335 | 5.5586 | 5.5921 | 5.9034
2021-08-17 19:00 | 3.7534 | 4.1125 | 4.1534 | 4.2035 | 4.2619 | 3.5057 | 4.1996 | 4.2315 | 4.2751 | 3.5057 | 6.2111 | 6.9589 | 6.9876 | 7.0257 | 7.4127
2021-08-17 20:00 | 3.6962 | 4.0607 | 4.1066 | 4.1627 | 4.2282 | 3.3342 | 4.0041 | 4.0398 | 4.0887 | 3.3342 | 5.0299 | 5.6531 | 5.6852 | 5.7279 | 6.0555
2021-08-17 21:00 | 3.5628 | 3.9191 | 3.9658 | 4.0229 | 4.0896 | 3.1638 | 3.8039 | 3.8404 | 3.8901 | 3.1638 | 4.725 | 5.3155 | 5.3482 | 5.3917 | 5.7034
2021-08-17 22:00 | 3.258 | 3.5856 | 3.6293 | 3.6827 | 3.745 | 2.8198 | 3.3932 | 3.4273 | 3.4738 | 2.8198 | 3.9248 | 4.422 | 4.4526 | 4.4932 | 4.7576
2021-08-17 23:00 | 3.0103 | 3.3111 | 3.3504 | 3.3986 | 3.4547 | 2.3625 | 2.8469 | 2.8776 | 2.9195 | 2.3625 | 3.2008 | 3.6115 | 3.639 | 3.6757 | 3.8954
2021-08-18 | 2.5911 | 2.8513 | 2.8858 | 2.9281 | 2.9773 | 2.0811 | 2.5076 | 2.5345 | 2.5713 | 2.0811 | 2.8007 | 3.1602 | 3.1844 | 3.2165 | 3.4089
2021-08-18 01:00 | 2.5149 | 2.7599 | 2.7895 | 2.8257 | 2.868 | 1.8672 | 2.2479 | 2.271 | 2.3025 | 1.8672 | 2.4768 | 2.7935 | 2.8142 | 2.8418 | 3.0109
2021-08-18 02:00 | 2.4578 | 2.6864 | 2.7098 | 2.7385 | 2.772 | 1.7528 | 2.1041 | 2.1224 | 2.1473 | 1.7528 | 2.7626 | 3.1025 | 3.1189 | 3.1408 | 3.3187
2021-08-18 03:00 | 2.4387 | 2.6541 | 2.6715 | 2.6928 | 2.7177 | 1.7719 | 2.118 | 2.1316 | 2.1501 | 1.7719 | 2.7436 | 3.0729 | 3.0851 | 3.1014 | 3.2716
2021-08-18 04:00 | 2.4959 | 2.7054 | 2.7177 | 2.7327 | 2.7502 | 1.8711 | 2.2279 | 2.2374 | 2.2505 | 1.8711 | 2.7626 | 3.087 | 3.0956 | 3.107 | 3.2725
2021-08-18 05:00 | 2.8565 | 3.0889 | 3.0991 | 3.1116 | 3.1262 | 2.172 | 2.5804 | 2.5884 | 2.5993 | 2.172 | 3.2961 | 3.677 | 3.6842 | 3.6937 | 3.8863
2021-08-18 06:00 | 3.2008 | 3.4622 | 3.4741 | 3.4887 | 3.5057 | 2.6483 | 3.1456 | 3.1549 | 3.1676 | 2.6483 | 4.4202 | 4.9285 | 4.9369 | 4.948 | 5.2043
2021-08-18 07:00 | 3.6962 | 4.0034 | 4.02 | 4.0403 | 4.064 | 2.896 | 3.4448 | 3.4577 | 3.4754 | 2.896 | 4.4202 | 4.935 | 4.9466 | 4.962 | 5.2235
2021-08-18 08:00 | 3.6581 | 3.9758 | 3.9992 | 4.0279 | 4.0613 | 2.896 | 3.4545 | 3.4727 | 3.4976 | 2.896 | 4.2487 | 4.7539 | 4.7703 | 4.792 | 5.0517
2021-08-18 09:00 | 3.258 | 3.5602 | 3.5909 | 3.6285 | 3.6722 | 2.6143 | 3.1321 | 3.156 | 3.1887 | 2.6143 | 3.7343 | 4.1923 | 4.2138 | 4.2424 | 4.4818
2021-08-18 10:00 | 2.6674 | 2.9366 | 2.9729 | 3.0173 | 3.0691 | 2.1339 | 2.5724 | 2.6007 | 2.6394 | 2.1339 | 2.3625 | 2.6757 | 2.7011 | 2.7348 | 2.9051
2021-08-18 11:00 | 2.2603 | 2.5037 | 2.5422 | 2.5893 | 2.6442 | 1.7119 | 2.0771 | 2.1071 | 2.1481 | 1.7119 | 1.2765 | 1.4719 | 1.4989 | 1.5347 | 1.6477
2021-08-18 12:00 | 2.0386 | 2.2645 | 2.3024 | 2.3488 | 2.403 | 1.5242 | 1.8546 | 1.8842 | 1.9246 | 1.5242 | 1.086 | 1.2594 | 1.286 | 1.3214 | 1.4233
2021-08-18 13:00 | 2.0386 | 2.2595 | 2.2949 | 2.3382 | 2.3887 | 1.467 | 1.7834 | 1.8111 | 1.8487 | 1.467 | 0.95263 | 1.1077 | 1.1325 | 1.1655 | 1.2572
2021-08-18 14:00 | 2.0958 | 2.3155 | 2.3481 | 2.3881 | 2.4346 | 1.4435 | 1.7517 | 1.7772 | 1.812 | 1.4435 | 1.448 | 1.6544 | 1.6772 | 1.7076 | 1.8235
2021-08-18 15:00 | 2.2101 | 2.4347 | 2.4655 | 2.5032 | 2.5472 | 1.7147 | 2.0695 | 2.0935 | 2.1263 | 1.7147 | 1.7719 | 2.0117 | 2.0333 | 2.062 | 2.1937
2021-08-18 16:00 | 2.7817 | 3.0479 | 3.0783 | 3.1154 | 3.1588 | 2.3029 | 2.7637 | 2.7874 | 2.8197 | 2.3029 | 3.3723 | 3.7896 | 3.8109 | 3.8391 | 4.0583
2021-08-18 17:00 | 3.5617 | 3.8895 | 3.9217 | 3.961 | 4.007 | 3.1627 | 3.7821 | 3.8071 | 3.8414 | 3.1627 | 5.5824 | 6.2481 | 6.2706 | 6.3006 | 6.6433
2021-08-18 18:00 | 3.9058 | 4.2665 | 4.3024 | 4.3464 | 4.3977 | 3.5057 | 4.1925 | 4.2206 | 4.2588 | 3.5057 | 5.1823 | 5.8087 | 5.8339 | 5.8673 | 6.1922
2021-08-18 19:00 | 3.8486 | 4.2148 | 4.2557 | 4.3058 | 4.3642 | 3.3914 | 4.0646 | 4.0965 | 4.1401 | 3.3914 | 4.9537 | 5.5615 | 5.5902 | 5.6283 | 5.9462
2021-08-18 20:00 | 3.6962 | 4.0607 | 4.1066 | 4.1627 | 4.2282 | 3.277 | 3.9366 | 3.9723 | 4.0212 | 3.277 | 5.2204 | 5.8648 | 5.8969 | 5.9396 | 6.2777
2021-08-18 21:00 | 3.5438 | 3.8986 | 3.9453 | 4.0025 | 4.0691 | 3.1056 | 3.7352 | 3.7716 | 3.8213 | 3.1056 | 4.7441 | 5.3366 | 5.3694 | 5.4128 | 5.7256
2021-08-18 22:00 | 3.1469 | 3.4663 | 3.51 | 3.5634 | 3.6257 | 2.7954 | 3.3644 | 3.3985 | 3.4449 | 2.7954 | 3.8867 | 4.3797 | 4.4103 | 4.4509 | 4.7131
2021-08-18 23:00 | 2.8388 | 3.1269 | 3.1662 | 3.2144 | 3.2705 | 2.3813 | 2.8691 | 2.8998 | 2.9417 | 2.3813 | 3.2008 | 3.6115 | 3.639 | 3.6757 | 3.8954
2021-08-19 | 2.553 | 2.8104 | 2.8449 | 2.8871 | 2.9364 | 1.986 | 2.3952 | 2.4221 | 2.4589 | 1.986 | 3.3151 | 3.7318 | 3.756 | 3.7881 | 4.0088
2021-08-19 01:00 | 2.4197 | 2.6575 | 2.6872 | 2.7234 | 2.7657 | 1.814 | 2.1851 | 2.2082 | 2.2398 | 1.814 | 2.3816 | 2.6876 | 2.7084 | 2.7359 | 2.8998
2021-08-19 02:00 | 2.3625 | 2.5841 | 2.6075 | 2.6362 | 2.6697 | 1.7231 | 2.0689 | 2.0872 | 2.1122 | 1.7231 | 2.4006 | 2.7002 | 2.7167 | 2.7385 | 2.8966
2021-08-19 03:00 | 2.4006 | 2.6132 | 2.6306 | 2.6519 | 2.6767 | 1.7197 | 2.0563 | 2.0699 | 2.0884 | 1.7197 | 2.5911 | 2.9036 | 2.9158 | 2.932 | 3.0938
2021-08-19 04:00 | 2.451 | 2.6572 | 2.6694 | 2.6844 | 2.7019 | 1.8621 | 2.2172 | 2.2268 | 2.2398 | 1.8621 | 2.8388 | 3.1717 | 3.1803 | 3.1917 | 3.3614
2021-08-19 05:00 | 2.7055 | 2.9266 | 2.9369 | 2.9494 | 2.964 | 2.1485 | 2.5527 | 2.5607 | 2.5716 | 2.1485 | 3.2961 | 3.677 | 3.6842 | 3.6937 | 3.8863
2021-08-19 06:00 | 3.1056 | 3.3598 | 3.3717 | 3.3864 | 3.4034 | 2.6102 | 3.1005 | 3.1099 | 3.1226 | 2.6102 | 4.1916 | 4.6745 | 4.6828 | 4.6939 | 4.9376
2021-08-19 07:00 | 3.5438 | 3.8397 | 3.8563 | 3.8766 | 3.9002 | 2.9531 | 3.5123 | 3.5252 | 3.5429 | 2.9531 | 4.8393 | 5.4007 | 5.4124 | 5.4278 | 5.7123
2021-08-19 08:00 | 3.6962 | 4.0168 | 4.0402 | 4.0688 | 4.1022 | 3.0294 | 3.612 | 3.6303 | 3.6552 | 3.0294 | 4.8203 | 5.389 | 5.4054 | 5.4272 | 5.7182
2021-08-19 09:00 | 3.639 | 3.9696 | 4.0003 | 4.0378 | 4.0816 | 2.8198 | 3.3748 | 3.3987 | 3.4314 | 2.8198 | 5.0489 | 5.6532 | 5.6747 | 5.7032 | 6.0149
2021-08-19 10:00 | 2.896 | 3.1823 | 3.2185 | 3.2629 | 3.3147 | 2.4197 | 2.9101 | 2.9383 | 2.977 | 2.4197 | 2.8769 | 3.2473 | 3.2727 | 3.3065 | 3.505
2021-08-19 11:00 | 2.2482 | 2.4907 | 2.5292 | 2.5763 | 2.6312 | 1.823 | 2.2083 | 2.2383 | 2.2793 | 1.823 | 1.5433 | 1.7683 | 1.7953 | 1.8311 | 1.9588
2021-08-19 12:00 | 2.0005 | 2.2235 | 2.2615 | 2.3079 | 2.3621 | 1.5814 | 1.9221 | 1.9517 | 1.9921 | 1.5814 | 1.5242 | 1.7464 | 1.773 | 1.8083 | 1.9344
2021-08-19 13:00 | 2.2101 | 2.4437 | 2.4791 | 2.5224 | 2.5729 | 1.7338 | 2.0985 | 2.1262 | 2.1639 | 1.7338 | 1.9434 | 2.2087 | 2.2335 | 2.2664 | 2.4127
2021-08-19 14:00 | 2.4959 | 2.7453 | 2.778 | 2.8179 | 2.8645 | 1.9053 | 2.2972 | 2.3226 | 2.3574 | 1.9053 | 1.9815 | 2.2472 | 2.27 | 2.3004 | 2.4457
2021-08-19 15:00 | 2.3435 | 2.578 | 2.6088 | 2.6465 | 2.6905 | 1.7719 | 2.137 | 2.1611 | 2.1939 | 1.7719 | 2.1529 | 2.4352 | 2.4568 | 2.4854 | 2.6381
2021-08-19 16:00 | 2.7436 | 3.007 | 3.0373 | 3.0745 | 3.1178 | 2.275 | 2.7307 | 2.7544 | 2.7867 | 2.275 | 3.4676 | 3.8955 | 3.9167 | 3.945 | 4.1694
2021-08-19 17:00 | 3.277 | 3.5836 | 3.6158 | 3.6552 | 3.7011 | 3.0741 | 3.6774 | 3.7025 | 3.7367 | 3.0741 | 4.5726 | 5.126 | 5.1485 | 5.1785 | 5.4657
2021-08-19 18:00 | 3.7534 | 4.1027 | 4.1387 | 4.1826 | 4.2339 | 3.3151 | 3.9675 | 3.9955 | 4.0338 | 3.3151 | 4.9727 | 5.5758 | 5.601 | 5.6344 | 5.9478
2021-08-19 19:00 | 3.7534 | 4.1125 | 4.1534 | 4.2035 | 4.2619 | 3.2389 | 3.8845 | 3.9164 | 3.96 | 3.2389 | 5.792 | 6.4931 | 6.5218 | 6.5599 | 6.9238
2021-08-19 20:00 | 3.62 | 3.9789 | 4.0247 | 4.0809 | 4.1463 | 3.2008 | 3.8465 | 3.8823 | 3.9311 | 3.2008 | 5.6586 | 6.3518 | 6.3839 | 6.4266 | 6.7887
2021-08-19 21:00 | 3.4676 | 3.8167 | 3.8634 | 3.9206 | 3.9872 | 2.9531 | 3.5551 | 3.5915 | 3.6412 | 2.9531 | 5.5252 | 6.2047 | 6.2374 | 6.2809 | 6.6366
2021-08-19 22:00 | 3.2008 | 3.5242 | 3.5679 | 3.6213 | 3.6836 | 2.5817 | 3.112 | 3.146 | 3.1925 | 2.5817 | 4.3059 | 4.8455 | 4.876 | 4.9167 | 5.202
2021-08-19 23:00 | 2.8198 | 3.1064 | 3.1457 | 3.1939 | 3.25 | 2.2069 | 2.6631 | 2.6938 | 2.7357 | 2.2069 | 3.7534 | 4.2255 | 4.253 | 4.2897 | 4.5398
2021-08-20 | 2.553 | 2.8104 | 2.8449 | 2.8871 | 2.9364 | 1.9305 | 2.3296 | 2.3565 | 2.3933 | 1.9305 | 2.6102 | 2.9485 | 2.9726 | 3.0048 | 3.1867
2021-08-20 01:00 | 2.3625 | 2.5961 | 2.6257 | 2.662 | 2.7043 | 1.7039 | 2.0551 | 2.0782 | 2.1097 | 1.7039 | 2.3816 | 2.6876 | 2.7084 | 2.7359 | 2.8998
2021-08-20 02:00 | 2.2482 | 2.4612 | 2.4847 | 2.5134 | 2.5468 | 1.6195 | 1.9465 | 1.9648 | 1.9898 | 1.6195 | 2.6674 | 2.9966 | 3.0131 | 3.0349 | 3.2076
2021-08-20 03:00 | 2.2673 | 2.4699 | 2.4873 | 2.5086 | 2.5334 | 1.5623 | 1.8704 | 1.884 | 1.9025 | 1.5623 | 2.4197 | 2.713 | 2.7252 | 2.7414 | 2.8938
2021-08-20 04:00 | 2.4197 | 2.6236 | 2.6358 | 2.6508 | 2.6683 | 1.6673 | 1.9872 | 1.9967 | 2.0098 | 1.6673 | 2.8198 | 3.1505 | 3.1591 | 3.1705 | 3.3392
2021-08-20 05:00 | 2.5911 | 2.8038 | 2.814 | 2.8266 | 2.8412 | 2.0076 | 2.3863 | 2.3943 | 2.4052 | 2.0076 | 3.1818 | 3.55 | 3.5571 | 3.5667 | 3.753
2021-08-20 06:00 | 3.0098 | 3.2569 | 3.2689 | 3.2835 | 3.3005 | 2.4578 | 2.9205 | 2.9298 | 2.9425 | 2.4578 | 3.8296 | 4.2722 | 4.2805 | 4.2917 | 4.5155
2021-08-20 07:00 | 3.2961 | 3.5736 | 3.5902 | 3.6105 | 3.6341 | 2.6483 | 3.1522 | 3.1651 | 3.1828 | 2.6483 | 4.0772 | 4.5539 | 4.5655 | 4.5809 | 4.8235
2021-08-20 08:00 | 3.2389 | 3.5255 | 3.5489 | 3.5776 | 3.611 | 2.7055 | 3.2294 | 3.2476 | 3.2726 | 2.7055 | 4.1916 | 4.6903 | 4.7067 | 4.7285 | 4.985
2021-08-20 09:00 | 2.9531 | 3.2327 | 3.2634 | 3.301 | 3.3447 | 2.2987 | 2.7591 | 2.7831 | 2.8157 | 2.2987 | 2.7817 | 3.1337 | 3.1552 | 3.1837 | 3.3708
2021-08-20 10:00 | 2.4006 | 2.6501 | 2.6863 | 2.7307 | 2.7825 | 1.6324 | 1.9801 | 2.0084 | 2.047 | 1.6324 | 1.5623 | 1.7864 | 1.8118 | 1.8456 | 1.9718
2021-08-20 11:00 | 1.9624 | 2.1836 | 2.2221 | 2.2692 | 2.3241 | 1.3908 | 1.6978 | 1.7278 | 1.7688 | 1.3908 | 0.93358 | 1.0908 | 1.1178 | 1.1536 | 1.2478
2021-08-20 12:00 | 1.8481 | 2.0598 | 2.0977 | 2.1442 | 2.1983 | 1.4099 | 1.7195 | 1.7491 | 1.7895 | 1.4099 | 0.91452 | 1.0689 | 1.0955 | 1.1308 | 1.2233
2021-08-20 13:00 | 2.1148 | 2.3413 | 2.3767 | 2.4201 | 2.4706 | 1.6004 | 1.941 | 1.9686 | 2.0063 | 1.6004 | 1.3337 | 1.5312 | 1.556 | 1.5889 | 1.7016
2021-08-20 14:00 | 2.0018 | 2.2145 | 2.2472 | 2.2871 | 2.3337 | 1.6766 | 2.0271 | 2.0526 | 2.0873 | 1.6766 | 1.7909 | 2.0355 | 2.0583 | 2.0887 | 2.2235
2021-08-20 15:00 | 2.2673 | 2.4961 | 2.5269 | 2.5646 | 2.6086 | 1.829 | 2.2046 | 2.2286 | 2.2614 | 1.829 | 2.2673 | 2.5622 | 2.5838 | 2.6125 | 2.7714
2021-08-20 16:00 | 2.6483 | 2.9046 | 2.935 | 2.9722 | 3.0155 | 2.2362 | 2.6849 | 2.7086 | 2.741 | 2.2362 | 3.1627 | 3.5567 | 3.578 | 3.6062 | 3.8139
2021-08-20 17:00 | 3.258 | 3.5632 | 3.5954 | 3.6347 | 3.6807 | 3.0294 | 3.6245 | 3.6496 | 3.6839 | 3.0294 | 4.3059 | 4.8296 | 4.8521 | 4.882 | 5.1546
2021-08-20 18:00 | 3.3533 | 3.6729 | 3.7088 | 3.7528 | 3.8041 | 2.9722 | 3.5623 | 3.5903 | 3.6286 | 2.9722 | 4.8584 | 5.4488 | 5.4739 | 5.5074 | 5.8145
2021-08-20 19:00 | 3.3533 | 3.6826 | 3.7235 | 3.7736 | 3.832 | 3.0484 | 3.6594 | 3.6913 | 3.7349 | 3.0484 | 4.6298 | 5.2016 | 5.2303 | 5.2684 | 5.5684
2021-08-20 20:00 | 3.3151 | 3.6514 | 3.6972 | 3.7534 | 3.8188 | 2.915 | 3.5089 | 3.5447 | 3.5935 | 2.915 | 4.5917 | 5.1661 | 5.1982 | 5.2409 | 5.5444
2021-08-20 21:00 | 3.1437 | 3.4688 | 3.5155 | 3.5726 | 3.6392 | 2.669 | 3.2194 | 3.2558 | 3.3055 | 2.669 | 4.344 | 4.892 | 4.9247 | 4.9682 | 5.259
2021-08-20 22:00 | 2.9341 | 3.2377 | 3.2813 | 3.3347 | 3.397 | 2.3816 | 2.8755 | 2.9096 | 2.9561 | 2.3816 | 3.4676 | 3.9139 | 3.9445 | 3.9851 | 4.2243
2021-08-20 23:00 | 2.8007 | 3.0859 | 3.1253 | 3.1734 | 3.2296 | 2.1148 | 2.5543 | 2.585 | 2.6269 | 2.1148 | 3.1246 | 3.5268 | 3.5544 | 3.591 | 3.8065
2021-08-21 | 2.4578 | 2.708 | 2.7426 | 2.7848 | 2.834 | 1.8525 | 2.2376 | 2.2645 | 2.3012 | 1.8525 | 2.7055 | 3.0543 | 3.0785 | 3.1106 | 3.2978
2021-08-21 01:00 | 2.172 | 2.3914 | 2.4211 | 2.4573 | 2.4996 | 1.6195 | 1.9553 | 1.9784 | 2.0099 | 1.6195 | 2.3244 | 2.6241 | 2.6448 | 2.6724 | 2.8332
2021-08-21 02:00 | 2.172 | 2.3794 | 2.4028 | 2.4315 | 2.465 | 1.467 | 1.7664 | 1.7847 | 1.8097 | 1.467 | 2.0005 | 2.2556 | 2.272 | 2.2939 | 2.4299
2021-08-21 03:00 | 2.1148 | 2.3061 | 2.3235 | 2.3448 | 2.3697 | 1.467 | 1.7579 | 1.7714 | 1.79 | 1.467 | 1.9434 | 2.1837 | 2.1959 | 2.2121 | 2.3383
2021-08-21 04:00 | 2.0577 | 2.2346 | 2.2469 | 2.2619 | 2.2794 | 1.4289 | 1.7055 | 1.7151 | 1.7281 | 1.4289 | 2.2291 | 2.4942 | 2.5027 | 2.5142 | 2.6504
2021-08-21 05:00 | 2.1516 | 2.3316 | 2.3418 | 2.3543 | 2.3689 | 1.5834 | 1.8851 | 1.8931 | 1.904 | 1.5834 | 2.1529 | 2.4067 | 2.4138 | 2.4233 | 2.5531
2021-08-21 06:00 | 2.2101 | 2.3978 | 2.4097 | 2.4243 | 2.4413 | 1.829 | 2.1777 | 2.187 | 2.1997 | 1.829 | 2.7245 | 3.0442 | 3.0525 | 3.0637 | 3.2267
2021-08-21 07:00 | 2.2673 | 2.4683 | 2.4848 | 2.5051 | 2.5288 | 1.7909 | 2.1393 | 2.1522 | 2.1699 | 1.7909 | 2.7436 | 3.0718 | 3.0834 | 3.0988 | 3.2681
2021-08-21 08:00 | 2.3435 | 2.5635 | 2.5869 | 2.6155 | 2.6489 | 1.9624 | 2.3516 | 2.3698 | 2.3947 | 1.9624 | 2.553 | 2.8695 | 2.8859 | 2.9077 | 3.0741
2021-08-21 09:00 | 2.1148 | 2.3321 | 2.3628 | 2.4003 | 2.4441 | 1.6385 | 1.9793 | 2.0032 | 2.0359 | 1.6385 | 1.81 | 2.0539 | 2.0754 | 2.104 | 2.2376
2021-08-21 10:00 | 2.1529 | 2.384 | 2.4202 | 2.4646 | 2.5164 | 1.5814 | 1.9197 | 1.948 | 1.9866 | 1.5814 | 1.7338 | 1.977 | 2.0024 | 2.0361 | 2.1718
2021-08-21 11:00 | 2.0577 | 2.286 | 2.3245 | 2.3716 | 2.4265 | 1.7147 | 2.0804 | 2.1104 | 2.1514 | 1.7147 | 2.0767 | 2.3611 | 2.3881 | 2.4239 | 2.5809
2021-08-21 12:00 | 1.829 | 2.0393 | 2.0772 | 2.1237 | 2.1778 | 1.7475 | 2.1183 | 2.1479 | 2.1883 | 1.7475 | 2.4197 | 2.7415 | 2.7681 | 2.8034 | 2.9787
2021-08-21 13:00 | 2.2291 | 2.4642 | 2.4996 | 2.5429 | 2.5934 | 1.9434 | 2.3461 | 2.3737 | 2.4114 | 1.9434 | 2.8388 | 3.2038 | 3.2286 | 3.2615 | 3.457
2021-08-21 14:00 | 2.191 | 2.4178 | 2.4505 | 2.4904 | 2.537 | 1.9243 | 2.3197 | 2.3452 | 2.3799 | 1.9243 | 2.9531 | 3.327 | 3.3498 | 3.3802 | 3.5789
2021-08-21 15:00 | 2.0577 | 2.2709 | 2.3017 | 2.3395 | 2.3834 | 1.7338 | 2.092 | 2.116 | 2.1488 | 1.7338 | 2.3054 | 2.6046 | 2.6261 | 2.6548 | 2.8158
2021-08-21 16:00 | 2.3625 | 2.5976 | 2.628 | 2.6651 | 2.7085 | 1.9392 | 2.3341 | 2.3578 | 2.3901 | 1.9392 | 2.9341 | 3.3026 | 3.3239 | 3.3522 | 3.5473
2021-08-21 17:00 | 2.8408 | 3.115 | 3.1472 | 3.1866 | 3.2325 | 2.6715 | 3.2018 | 3.2269 | 3.2611 | 2.6715 | 3.982 | 4.4696 | 4.4922 | 4.5221 | 4.7768
2021-08-21 18:00 | 3.1056 | 3.4068 | 3.4427 | 3.4867 | 3.538 | 2.9341 | 3.5173 | 3.5453 | 3.5836 | 2.9341 | 4.0201 | 4.5172 | 4.5424 | 4.5758 | 4.8368
2021-08-21 19:00 | 3.1056 | 3.4165 | 3.4575 | 3.5075 | 3.5659 | 2.8388 | 3.4118 | 3.4438 | 3.4873 | 2.8388 | 4.0391 | 4.5453 | 4.5739 | 4.612 | 4.8796
2021-08-21 20:00 | 3.0484 | 3.3648 | 3.4107 | 3.4668 | 3.5322 | 2.6864 | 3.2388 | 3.2746 | 3.3234 | 2.6864 | 4.2487 | 4.785 | 4.8171 | 4.8598 | 5.1444
2021-08-21 21:00 | 3.0103 | 3.3255 | 3.3722 | 3.4293 | 3.496 | 2.5911 | 3.1275 | 3.1639 | 3.2136 | 2.5911 | 4.001 | 4.5109 | 4.5436 | 4.5871 | 4.859
2021-08-21 22:00 | 2.896 | 3.1967 | 3.2404 | 3.2938 | 3.3561 | 2.3716 | 2.8637 | 2.8978 | 2.9443 | 2.3716 | 3.6771 | 4.1468 | 4.1774 | 4.218 | 4.4687
2021-08-21 23:00 | 2.5721 | 2.8403 | 2.8796 | 2.9278 | 2.9839 | 2.0614 | 2.4912 | 2.5219 | 2.5638 | 2.0614 | 2.9722 | 3.3574 | 3.385 | 3.4216 | 3.6288
2021-08-22 | 2.4006 | 2.6466 | 2.6811 | 2.7234 | 2.7726 | 1.7528 | 2.1198 | 2.1467 | 2.1835 | 1.7528 | 2.5721 | 2.9061 | 2.9303 | 2.9624 | 3.1422
2021-08-22 01:00 | 2.2291 | 2.4528 | 2.4825 | 2.5187 | 2.561 | 1.6195 | 1.9553 | 1.9784 | 2.0099 | 1.6195 | 2.3244 | 2.6241 | 2.6448 | 2.6724 | 2.8332
2021-08-22 02:00 | 2.1339 | 2.3384 | 2.3619 | 2.3906 | 2.424 | 1.5018 | 1.8074 | 1.8257 | 1.8507 | 1.5018 | 2.2673 | 2.552 | 2.5684 | 2.5903 | 2.741
2021-08-22 03:00 | 2.1339 | 2.3266 | 2.344 | 2.3653 | 2.3902 | 1.448 | 1.7353 | 1.7489 | 1.7675 | 1.448 | 2.0386 | 2.2896 | 2.3018 | 2.318 | 2.4494
2021-08-22 04:00 | 2.1339 | 2.3165 | 2.3288 | 2.3438 | 2.3613 | 1.5052 | 1.7956 | 1.8051 | 1.8182 | 1.5052 | 2.3244 | 2.6 | 2.6086 | 2.62 | 2.7615
2021-08-22 05:00 | 2.2482 | 2.4354 | 2.4456 | 2.4581 | 2.4727 | 1.6491 | 1.9627 | 1.9707 | 1.9816 | 1.6491 | 2.8007 | 3.1265 | 3.1337 | 3.1432 | 3.3086
2021-08-22 06:00 | 2.4768 | 2.6843 | 2.6963 | 2.7109 | 2.7279 | 1.9053 | 2.2678 | 2.2771 | 2.2898 | 1.9053 | 2.8198 | 3.15 | 3.1584 | 3.1695 | 3.3378
2021-08-22 07:00 | 2.4006 | 2.6115 | 2.6281 | 2.6484 | 2.6721 | 1.8862 | 2.2519 | 2.2648 | 2.2824 | 1.8862 | 2.8198 | 3.1565 | 3.1681 | 3.1835 | 3.357
2021-08-22 08:00 | 2.2101 | 2.4202 | 2.4436 | 2.4722 | 2.5056 | 1.7719 | 2.1265 | 2.1448 | 2.1697 | 1.7719 | 2.5721 | 2.8907 | 2.9071 | 2.9289 | 3.0963
2021-08-22 09:00 | 1.8862 | 2.0865 | 2.1171 | 2.1547 | 2.1985 | 1.6048 | 1.9394 | 1.9634 | 1.996 | 1.6048 | 2.0005 | 2.2656 | 2.2871 | 2.3157 | 2.4598
2021-08-22 10:00 | 1.6766 | 1.8723 | 1.9085 | 1.9529 | 2.0047 | 1.2099 | 1.4809 | 1.5092 | 1.5478 | 1.2099 | 1.4099 | 1.617 | 1.6424 | 1.6762 | 1.7941
2021-08-22 11:00 | 1.4851 | 1.6708 | 1.7093 | 1.7564 | 1.8113 | 1.1622 | 1.4277 | 1.4577 | 1.4987 | 1.1622 | 0.7621 | 0.90026 | 0.92722 | 0.96305 | 1.0478
2021-08-22 12:00 | 1.4861 | 1.6709 | 1.7088 | 1.7552 | 1.8094 | 1.086 | 1.3369 | 1.3665 | 1.4069 | 1.086 | 0.87642 | 1.0265 | 1.0531 | 1.0885 | 1.1789
2021-08-22 13:00 | 1.448 | 1.6249 | 1.6603 | 1.7037 | 1.7542 | 1.1432 | 1.4008 | 1.4284 | 1.4661 | 1.1432 | 0.91452 | 1.0654 | 1.0902 | 1.1231 | 1.2128
2021-08-22 14:00 | 1.6385 | 1.8242 | 1.8569 | 1.8968 | 1.9434 | 1.2384 | 1.5094 | 1.5349 | 1.5696 | 1.2384 | 0.95263 | 1.1039 | 1.1267 | 1.1571 | 1.2458
2021-08-22 15:00 | 2.0005 | 2.2095 | 2.2403 | 2.278 | 2.322 | 1.6385 | 1.9795 | 2.0035 | 2.0363 | 1.6385 | 1.9053 | 2.1599 | 2.1815 | 2.2102 | 2.3492
2021-08-22 16:00 | 2.3244 | 2.5567 | 2.587 | 2.6242 | 2.6675 | 1.8805 | 2.2647 | 2.2884 | 2.3207 | 1.8805 | 2.2482 | 2.5404 | 2.5617 | 2.59 | 2.7474
2021-08-22 17:00 | 2.7055 | 2.9696 | 3.0018 | 3.0411 | 3.0871 | 2.3786 | 2.8557 | 2.8808 | 2.9151 | 2.3786 | 3.6771 | 4.1309 | 4.1534 | 4.1834 | 4.4213
2021-08-22 18:00 | 3.0484 | 3.3454 | 3.3813 | 3.4253 | 3.4766 | 2.5911 | 3.1122 | 3.1402 | 3.1785 | 2.5911 | 3.8105 | 4.2843 | 4.3095 | 4.3429 | 4.5924
2021-08-22 19:00 | 3.0103 | 3.3142 | 3.3551 | 3.4052 | 3.4636 | 2.4959 | 3.0067 | 3.0386 | 3.0822 | 2.4959 | 3.5438 | 3.9948 | 4.0235 | 4.0615 | 4.3019
2021-08-22 20:00 | 2.8579 | 3.1601 | 3.206 | 3.2621 | 3.3275 | 2.4959 | 3.0137 | 3.0495 | 3.0983 | 2.4959 | 3.5438 | 4.0016 | 4.0338 | 4.0765 | 4.3223
2021-08-22 21:00 | 2.6689 | 2.9587 | 3.0054 | 3.0625 | 3.1292 | 2.3244 | 2.8123 | 2.8488 | 2.8985 | 2.3244 | 3.7534 | 4.2357 | 4.2684 | 4.3119 | 4.5702
2021-08-22 22:00 | 2.4959 | 2.7669 | 2.8105 | 2.8639 | 2.9262 | 2.1148 | 2.5604 | 2.5945 | 2.641 | 2.1148 | 3.3533 | 3.7869 | 3.8174 | 3.8581 | 4.091
2021-08-22 23:00 | 2.3625 | 2.6151 | 2.6545 | 2.7026 | 2.7588 | 1.8006 | 2.1831 | 2.2137 | 2.2556 | 1.8006 | 2.9341 | 3.3151 | 3.3426 | 3.3793 | 3.5843
2021-08-23 | 2.1316 | 2.3576 | 2.3921 | 2.4343 | 2.4836 | 1.5552 | 1.8863 | 1.9132 | 1.9499 | 1.5552 | 2.0958 | 2.3768 | 2.401 | 2.4331 | 2.5867
2021-08-23 01:00 | 1.9815 | 2.1867 | 2.2164 | 2.2526 | 2.2949 | 1.4099 | 1.7077 | 1.7308 | 1.7623 | 1.4099 | 2.1529 | 2.4335 | 2.4543 | 2.4819 | 2.6332
2021-08-23 02:00 | 1.9434 | 2.1337 | 2.1572 | 2.1859 | 2.2193 | 1.3337 | 1.6089 | 1.6272 | 1.6521 | 1.3337 | 1.81 | 2.0439 | 2.0603 | 2.0821 | 2.2077
2021-08-23 03:00 | 2.0005 | 2.1833 | 2.2007 | 2.222 | 2.2469 | 1.2956 | 1.5553 | 1.5689 | 1.5874 | 1.2956 | 1.81 | 2.0355 | 2.0477 | 2.0639 | 2.1828
2021-08-23 04:00 | 1.9434 | 2.1118 | 2.1241 | 2.1391 | 2.1566 | 1.3151 | 1.571 | 1.5806 | 1.5937 | 1.3151 | 1.6766 | 1.8802 | 1.8888 | 1.9002 | 2.006
2021-08-23 05:00 | 2.0386 | 2.2102 | 2.2204 | 2.233 | 2.2476 | 1.5338 | 1.8265 | 1.8344 | 1.8453 | 1.5338 | 2.2673 | 2.5337 | 2.5409 | 2.5504 | 2.6864
2021-08-23 06:00 | 2.2673 | 2.4592 | 2.4711 | 2.4857 | 2.5028 | 1.7147 | 2.0427 | 2.052 | 2.0647 | 1.7147 | 2.4959 | 2.7901 | 2.7985 | 2.8096 | 2.9601
2021-08-23 07:00 | 2.3816 | 2.5911 | 2.6077 | 2.6279 | 2.6516 | 1.7909 | 2.1393 | 2.1522 | 2.1699 | 1.7909 | 2.553 | 2.8601 | 2.8717 | 2.8871 | 3.0459
2021-08-23 08:00 | 2.3303 | 2.5493 | 2.5727 | 2.6013 | 2.6347 | 1.6957 | 2.0365 | 2.0547 | 2.0796 | 1.6957 | 2.4387 | 2.7425 | 2.7589 | 2.7807 | 2.9408
2021-08-23 09:00 | 2.2101 | 2.4344 | 2.4651 | 2.5027 | 2.5464 | 1.6766 | 2.0243 | 2.0482 | 2.0809 | 1.6766 | 1.6957 | 1.9269 | 1.9484 | 1.9769 | 2.1043
2021-08-23 10:00 | 1.5544 | 1.7409 | 1.7772 | 1.8216 | 1.8733 | 1.105 | 1.357 | 1.3853 | 1.4239 | 1.105 | 0.80021 | 0.93953 | 0.96494 | 0.9987 | 1.0831
2021-08-23 11:00 | 1.6954 | 1.8968 | 1.9353 | 1.9824 | 2.0373 | 1.3527 | 1.6528 | 1.6828 | 1.7238 | 1.3527 | 0.87642 | 1.0273 | 1.0543 | 1.0901 | 1.1811
2021-08-23 12:00 | 2.0196 | 2.244 | 2.2819 | 2.3284 | 2.3825 | 1.5814 | 1.9221 | 1.9517 | 1.9921 | 1.5814 | 1.3527 | 1.5559 | 1.5824 | 1.6178 | 1.7344
2021-08-23 13:00 | 2.0577 | 2.2799 | 2.3153 | 2.3587 | 2.4092 | 1.5814 | 1.9185 | 1.9461 | 1.9838 | 1.5814 | 1.7338 | 1.9758 | 2.0006 | 2.0335 | 2.1682
2021-08-23 14:00 | 2.3244 | 2.5611 | 2.5937 | 2.6337 | 2.6803 | 1.8862 | 2.2747 | 2.3001 | 2.3349 | 1.8862 | 2.3625 | 2.6706 | 2.6935 | 2.7239 | 2.8901
2021-08-23 15:00 | 2.4112 | 2.6507 | 2.6815 | 2.7192 | 2.7632 | 1.9515 | 2.3493 | 2.3733 | 2.4061 | 1.9515 | 2.534 | 2.8586 | 2.8802 | 2.9089 | 3.0825
2021-08-23 16:00 | 2.553 | 2.8023 | 2.8326 | 2.8698 | 2.9131 | 2.2482 | 2.6991 | 2.7228 | 2.7551 | 2.2482 | 3.4295 | 3.8531 | 3.8744 | 3.9027 | 4.125
2021-08-23 17:00 | 2.998 | 3.2839 | 3.316 | 3.3554 | 3.4013 | 2.6575 | 3.1852 | 3.2103 | 3.2446 | 2.6575 | 3.8296 | 4.3002 | 4.3228 | 4.3527 | 4.5991
2021-08-23 18:00 | 3.2008 | 3.5091 | 3.5451 | 3.589 | 3.6403 | 2.8388 | 3.4048 | 3.4328 | 3.4711 | 2.8388 | 4.8584 | 5.4488 | 5.4739 | 5.5074 | 5.8145
2021-08-23 19:00 | 3.3151 | 3.6417 | 3.6826 | 3.7327 | 3.7911 | 2.8769 | 3.4569 | 3.4888 | 3.5324 | 2.8769 | 4.4964 | 5.0534 | 5.0821 | 5.1202 | 5.4129
2021-08-23 20:00 | 3.2199 | 3.549 | 3.5949 | 3.651 | 3.7165 | 2.7715 | 3.3394 | 3.3751 | 3.424 | 2.7715 | 4.5536 | 5.1238 | 5.1559 | 5.1986 | 5.5
2021-08-23 21:00 | 2.9531 | 3.2641 | 3.3108 | 3.3679 | 3.4346 | 2.6881 | 3.242 | 3.2785 | 3.3282 | 2.6881 | 4.2297 | 4.765 | 4.7977 | 4.8412 | 5.1257
2021-08-23 22:00 | 2.6293 | 2.9102 | 2.9538 | 3.0072 | 3.0695 | 2.2554 | 2.7266 | 2.7606 | 2.8071 | 2.2554 | 3.9058 | 4.4008 | 4.4314 | 4.4721 | 4.7354
2021-08-23 23:00 | 2.4387 | 2.697 | 2.7364 | 2.7845 | 2.8406 | 1.9434 | 2.3517 | 2.3824 | 2.4243 | 1.9434 | 3.2961 | 3.7174 | 3.7449 | 3.7815 | 4.0065
2021-08-24 | 2.2291 | 2.4624 | 2.4969 | 2.5392 | 2.5884 | 1.6195 | 1.9622 | 1.9892 | 2.0259 | 1.6195 | 2.4578 | 2.7791 | 2.8033 | 2.8354 | 3.0089
2021-08-24 01:00 | 2.1148 | 2.33 | 2.3596 | 2.3959 | 2.4382 | 1.5052 | 1.8202 | 1.8433 | 1.8749 | 1.5052 | 2.0196 | 2.2853 | 2.3061 | 2.3337 | 2.4777
2021-08-24 02:00 | 2.1529 | 2.3589 | 2.3823 | 2.411 | 2.4445 | 1.4558 | 1.7532 | 1.7715 | 1.7965 | 1.4558 | 1.9624 | 2.2133 | 2.2297 | 2.2515 | 2.3855
2021-08-24 03:00 | 2.1522 | 2.3463 | 2.3637 | 2.385 | 2.4098 | 1.4251 | 1.7083 | 1.7218 | 1.7404 | 1.4251 | 2.0767 | 2.3319 | 2.3441 | 2.3603 | 2.4939
2021-08-24 04:00 | 2.2291 | 2.4189 | 2.4311 | 2.4461 | 2.4636 | 1.5201 | 1.8132 | 1.8228 | 1.8359 | 1.5201 | 2.2673 | 2.5365 | 2.5451 | 2.5565 | 2.6948
2021-08-24 05:00 | 2.4006 | 2.5991 | 2.6094 | 2.6219 | 2.6365 | 1.7359 | 2.0652 | 2.0732 | 2.0841 | 1.7359 | 2.5721 | 2.8724 | 2.8796 | 2.8891 | 3.0419
2021-08-24 06:00 | 2.7817 | 3.0118 | 3.0238 | 3.0384 | 3.0554 | 2.1148 | 2.5153 | 2.5247 | 2.5374 | 2.1148 | 3.6771 | 4.1028 | 4.1112 | 4.1223 | 4.3377
2021-08-24 07:00 | 3.3971 | 3.6821 | 3.6987 | 3.719 | 3.7427 | 2.6154 | 3.1133 | 3.1262 | 3.1439 | 2.6154 | 4.8393 | 5.4007 | 5.4124 | 5.4278 | 5.7123
2021-08-24 08:00 | 3.8296 | 4.1601 | 4.1835 | 4.2121 | 4.2455 | 3.1789 | 3.7887 | 3.8069 | 3.8318 | 3.1789 | 5.2013 | 5.8125 | 5.8289 | 5.8507 | 6.1626
2021-08-24 09:00 | 4.001 | 4.3585 | 4.3892 | 4.4268 | 4.4705 | 3.2961 | 3.9375 | 3.9614 | 3.9941 | 3.2961 | 5.5443 | 6.2037 | 6.2252 | 6.2537 | 6.5927
2021-08-24 10:00 | 3.9439 | 4.3081 | 4.3443 | 4.3887 | 4.4405 | 3.2396 | 3.8787 | 3.907 | 3.9456 | 3.2396 | 5.5443 | 6.2114 | 6.2368 | 6.2706 | 6.6158
2021-08-24 11:00 | 3.8486 | 4.2101 | 4.2485 | 4.2957 | 4.3506 | 3.3151 | 3.9711 | 4.0011 | 4.0421 | 3.3151 | 6.0206 | 6.7438 | 6.7708 | 6.8066 | 7.1804
2021-08-24 12:00 | 4.0582 | 4.4342 | 4.4721 | 4.5186 | 4.5727 | 3.3342 | 3.9928 | 4.0224 | 4.0628 | 3.3342 | 5.811 | 6.5102 | 6.5368 | 6.5721 | 6.9338
2021-08-24 13:00 | 3.9022 | 4.2616 | 4.297 | 4.3403 | 4.3908 | 3.215 | 3.8484 | 3.876 | 3.9137 | 3.215 | 5.7729 | 6.4643 | 6.4891 | 6.522 | 6.8788
2021-08-24 14:00 | 3.7724 | 4.1167 | 4.1494 | 4.1893 | 4.2359 | 3.0103 | 3.6026 | 3.6281 | 3.6629 | 3.0103 | 5.6586 | 6.3334 | 6.3563 | 6.3867 | 6.7341
2021-08-24 15:00 | 3.7915 | 4.1336 | 4.1644 | 4.2021 | 4.2461 | 3.2199 | 3.8476 | 3.8717 | 3.9045 | 3.2199 | 4.9918 | 5.5899 | 5.6114 | 5.6401 | 5.9488
2021-08-24 16:00 | 4.0201 | 4.3784 | 4.4088 | 4.4459 | 4.4893 | 3.4469 | 4.1152 | 4.1389 | 4.1712 | 3.4469 | 6.3064 | 7.0501 | 7.0714 | 7.0997 | 7.4802
2021-08-24 17:00 | 4.3249 | 4.7094 | 4.7416 | 4.781 | 4.8269 | 3.9027 | 4.6563 | 4.6814 | 4.7156 | 3.9027 | 7.4496 | 8.323 | 8.3455 | 8.3755 | 8.8208
2021-08-24 18:00 | 4.4392 | 4.8396 | 4.8755 | 4.9195 | 4.9708 | 3.9248 | 4.6877 | 4.7157 | 4.754 | 3.9248 | 6.3445 | 7.1002 | 7.1254 | 7.1588 | 7.5476
2021-08-24 19:00 | 4.2297 | 4.6242 | 4.6651 | 4.7152 | 4.7736 | 3.8105 | 4.5597 | 4.5917 | 4.6352 | 3.8105 | 6.9923 | 7.827 | 7.8556 | 7.8937 | 8.3237
2021-08-24 20:00 | 4.001 | 4.3883 | 4.4341 | 4.4902 | 4.5557 | 3.5818 | 4.2966 | 4.3323 | 4.3812 | 3.5818 | 6.1349 | 6.8811 | 6.9132 | 6.9559 | 7.3442
2021-08-24 21:00 | 3.8296 | 4.2057 | 4.2523 | 4.3095 | 4.3761 | 3.4485 | 4.1403 | 4.1767 | 4.2264 | 3.4485 | 5.4109 | 6.0777 | 6.1104 | 6.1539 | 6.5033
2021-08-24 22:00 | 3.5628 | 3.9131 | 3.9568 | 4.0102 | 4.0725 | 2.9764 | 3.5783 | 3.6123 | 3.6588 | 2.9764 | 4.3249 | 4.8666 | 4.8972 | 4.9379 | 5.2242
2021-08-24 23:00 | 2.9722 | 3.2702 | 3.3095 | 3.3576 | 3.4138 | 2.4656 | 2.9686 | 2.9993 | 3.0412 | 2.4656 | 4.363 | 4.903 | 4.9306 | 4.9672 | 5.2508
2021-08-25 | 2.7436 | 3.0151 | 3.0496 | 3.0918 | 3.1411 | 2.0242 | 2.4404 | 2.4673 | 2.5041 | 2.0242 | 3.4485 | 3.88 | 3.9042 | 3.9363 | 4.1643
2021-08-25 01:00 | 2.534 | 2.7803 | 2.81 | 2.8462 | 2.8885 | 1.8672 | 2.2479 | 2.271 | 2.3025 | 1.8672 | 2.5911 | 2.9205 | 2.9413 | 2.9688 | 3.1442
2021-08-25 02:00 | 2.4006 | 2.625 | 2.6484 | 2.6771 | 2.7106 | 1.7719 | 2.1266 | 2.1449 | 2.1698 | 1.7719 | 2.4578 | 2.7637 | 2.7802 | 2.802 | 2.9632
2021-08-25 03:00 | 2.3435 | 2.5518 | 2.5692 | 2.5905 | 2.6153 | 1.7338 | 2.073 | 2.0865 | 2.1051 | 1.7338 | 2.8388 | 3.1788 | 3.191 | 3.2072 | 3.3827
2021-08-25 04:00 | 2.4006 | 2.6031 | 2.6154 | 2.6304 | 2.6479 | 1.7338 | 2.0656 | 2.0752 | 2.0883 | 1.7338 | 2.7245 | 3.0446 | 3.0532 | 3.0646 | 3.2281
2021-08-25 05:00 | 2.6293 | 2.8447 | 2.855 | 2.8675 | 2.8821 | 2.0112 | 2.3904 | 2.3984 | 2.4093 | 2.0112 | 3.1056 | 3.4653 | 3.4724 | 3.482 | 3.6641
2021-08-25 06:00 | 2.9722 | 3.2165 | 3.2285 | 3.2431 | 3.2601 | 2.3604 | 2.8055 | 2.8148 | 2.8275 | 2.3604 | 3.7152 | 4.1451 | 4.1535 | 4.1646 | 4.3821
2021-08-25 07:00 | 3.6009 | 3.9011 | 3.9177 | 3.938 | 3.9616 | 2.8257 | 3.3617 | 3.3747 | 3.3923 | 2.8257 | 4.7822 | 5.3372 | 5.3488 | 5.3643 | 5.6456
2021-08-25 08:00 | 3.8105 | 4.1396 | 4.163 | 4.1916 | 4.225 | 2.896 | 3.4545 | 3.4727 | 3.4976 | 2.896 | 4.9156 | 5.4949 | 5.5113 | 5.5331 | 5.8293
2021-08-25 09:00 | 3.7915 | 4.1334 | 4.164 | 4.2016 | 4.2454 | 2.7055 | 3.2397 | 3.2637 | 3.2963 | 2.7055 | 4.2487 | 4.764 | 4.7854 | 4.814 | 5.0817
2021-08-25 10:00 | 3.4295 | 3.7554 | 3.7917 | 3.8361 | 3.8878 | 2.6102 | 3.1351 | 3.1634 | 3.202 | 2.6102 | 3.7724 | 4.2424 | 4.2678 | 4.3016 | 4.5493
2021-08-25 11:00 | 3.2961 | 3.6165 | 3.6549 | 3.7021 | 3.757 | 2.5911 | 3.1158 | 3.1458 | 3.1868 | 2.5911 | 3.5819 | 4.0338 | 4.0607 | 4.0965 | 4.3363
2021-08-25 12:00 | 3.0294 | 3.3288 | 3.3668 | 3.4132 | 3.4674 | 2.2291 | 2.6874 | 2.717 | 2.7574 | 2.2291 | 2.8007 | 3.1649 | 3.1915 | 3.2269 | 3.4231
2021-08-25 13:00 | 3.0484 | 3.3443 | 3.3797 | 3.4231 | 3.4736 | 2.2482 | 2.7063 | 2.7339 | 2.7716 | 2.2482 | 3.5057 | 3.9448 | 3.9696 | 4.0025 | 4.2347
2021-08-25 14:00 | 2.8388 | 3.1138 | 3.1464 | 3.1863 | 3.2329 | 2.191 | 2.6348 | 2.6603 | 2.695 | 2.191 | 2.6483 | 2.9882 | 3.0111 | 3.0415 | 3.2234
2021-08-25 15:00 | 2.9913 | 3.2739 | 3.3047 | 3.3424 | 3.3864 | 2.3054 | 2.7672 | 2.7913 | 2.8241 | 2.3054 | 3.4295 | 3.8537 | 3.8753 | 3.904 | 4.1268
2021-08-25 16:00 | 3.258 | 3.5596 | 3.59 | 3.6272 | 3.6705 | 2.7295 | 3.2677 | 3.2914 | 3.3237 | 2.7295 | 4.4392 | 4.9752 | 4.9965 | 5.0248 | 5.3026
2021-08-25 17:00 | 3.6932 | 4.0307 | 4.0629 | 4.1023 | 4.1482 | 3.258 | 3.8946 | 3.9197 | 3.954 | 3.258 | 5.087 | 5.6976 | 5.7202 | 5.7501 | 6.0656
2021-08-25 18:00 | 3.9058 | 4.2665 | 4.3024 | 4.3464 | 4.3977 | 3.4295 | 4.1025 | 4.1305 | 4.1688 | 3.4295 | 6.2683 | 7.0155 | 7.0407 | 7.0741 | 7.4587
2021-08-25 19:00 | 3.9248 | 4.2967 | 4.3376 | 4.3877 | 4.4461 | 3.4295 | 4.1096 | 4.1415 | 4.1851 | 3.4295 | 5.3347 | 5.985 | 6.0136 | 6.0517 | 6.3906
2021-08-25 20:00 | 3.7705 | 4.1406 | 4.1864 | 4.2426 | 4.308 | 3.2389 | 3.8915 | 3.9273 | 3.9761 | 3.2389 | 5.2966 | 5.9495 | 5.9816 | 6.0243 | 6.3665
2021-08-25 21:00 | 3.5819 | 3.9396 | 3.9863 | 4.0434 | 4.11 | 3.0817 | 3.707 | 3.7434 | 3.7931 | 3.0817 | 4.6869 | 5.2731 | 5.3058 | 5.3493 | 5.6589
2021-08-25 22:00 | 3.277 | 3.6061 | 3.6498 | 3.7032 | 3.7655 | 2.6518 | 3.1948 | 3.2288 | 3.2753 | 2.6518 | 3.9058 | 4.4008 | 4.4314 | 4.4721 | 4.7354
2021-08-25 23:00 | 2.9063 | 3.1993 | 3.2386 | 3.2868 | 3.3429 | 2.3114 | 2.7865 | 2.8172 | 2.8591 | 2.3114 | 3.2008 | 3.6115 | 3.639 | 3.6757 | 3.8954
2021-08-26 | 2.6864 | 2.9537 | 2.9882 | 3.0304 | 3.0797 | 1.9267 | 2.3252 | 2.3521 | 2.3888 | 1.9267 | 3.0103 | 3.3931 | 3.4173 | 3.4494 | 3.6533
2021-08-26 01:00 | 2.4006 | 2.6371 | 2.6667 | 2.7029 | 2.7452 | 1.7349 | 2.0916 | 2.1147 | 2.1462 | 1.7349 | 2.8198 | 3.1746 | 3.1953 | 3.2229 | 3.4109
2021-08-26 02:00 | 2.3435 | 2.5636 | 2.587 | 2.6157 | 2.6492 | 1.6385 | 1.969 | 1.9873 | 2.0123 | 1.6385 | 2.4006 | 2.7002 | 2.7167 | 2.7385 | 2.8966
2021-08-26 03:00 | 2.3625 | 2.5722 | 2.5896 | 2.6109 | 2.6358 | 1.6385 | 1.9604 | 1.974 | 1.9925 | 1.6385 | 2.5911 | 2.9036 | 2.9158 | 2.932 | 3.0938
2021-08-26 04:00 | 2.4479 | 2.6539 | 2.6661 | 2.6812 | 2.6987 | 1.8251 | 2.1736 | 2.1831 | 2.1962 | 1.8251 | 2.915 | 3.2564 | 3.2649 | 3.2764 | 3.4503
2021-08-26 05:00 | 2.6601 | 2.8779 | 2.8882 | 2.9007 | 2.9153 | 2.0451 | 2.4305 | 2.4385 | 2.4494 | 2.0451 | 3.3151 | 3.6982 | 3.7053 | 3.7149 | 3.9085
2021-08-26 06:00 | 3.1133 | 3.3681 | 3.38 | 3.3946 | 3.4117 | 2.4959 | 2.9655 | 2.9748 | 2.9875 | 2.4959 | 4.001 | 4.4627 | 4.4711 | 4.4822 | 4.7154
2021-08-26 07:00 | 3.258 | 3.5326 | 3.5492 | 3.5695 | 3.5932 | 2.5911 | 3.0846 | 3.0976 | 3.1152 | 2.5911 | 4.0772 | 4.5539 | 4.5655 | 4.5809 | 4.8235
2021-08-26 08:00 | 3.2008 | 3.4846 | 3.508 | 3.5366 | 3.57 | 2.5025 | 2.9896 | 3.0079 | 3.0328 | 2.5025 | 4.0772 | 4.5633 | 4.5797 | 4.6015 | 4.8517
2021-08-26 09:00 | 2.8007 | 3.069 | 3.0997 | 3.1372 | 3.181 | 2.172 | 2.6095 | 2.6334 | 2.6661 | 2.172 | 2.7326 | 3.0792 | 3.1007 | 3.1292 | 3.3136
2021-08-26 10:00 | 2.3054 | 2.5477 | 2.584 | 2.6284 | 2.6801 | 1.7909 | 2.1673 | 2.1956 | 2.2342 | 1.7909 | 1.9434 | 2.2099 | 2.2353 | 2.269 | 2.4162
2021-08-26 11:00 | 2.2482 | 2.4907 | 2.5292 | 2.5763 | 2.6312 | 1.5623 | 1.9004 | 1.9304 | 1.9714 | 1.5623 | 1.6385 | 1.8742 | 1.9011 | 1.937 | 2.0699
2021-08-26 12:00 | 2.3412 | 2.5896 | 2.6275 | 2.674 | 2.7281 | 1.9434 | 2.3498 | 2.3794 | 2.4198 | 1.9434 | 1.5623 | 1.7888 | 1.8153 | 1.8507 | 1.9788
2021-08-26 13:00 | 2.6483 | 2.9145 | 2.9499 | 2.9932 | 3.0437 | 2.0767 | 2.5037 | 2.5313 | 2.569 | 2.0767 | 2.1148 | 2.3992 | 2.424 | 2.457 | 2.6126
2021-08-26 14:00 | 2.8769 | 3.1547 | 3.1873 | 3.2273 | 3.2739 | 2.172 | 2.6123 | 2.6378 | 2.6725 | 2.172 | 2.6864 | 3.0306 | 3.0534 | 3.0838 | 3.2678
2021-08-26 15:00 | 3.0865 | 3.3763 | 3.4071 | 3.4448 | 3.4887 | 2.5911 | 3.1049 | 3.1289 | 3.1617 | 2.5911 | 3.6962 | 4.1501 | 4.1717 | 4.2004 | 4.4379
2021-08-26 16:00 | 3.2424 | 3.5429 | 3.5733 | 3.6104 | 3.6538 | 2.7626 | 3.3068 | 3.3305 | 3.3628 | 2.7626 | 4.1916 | 4.7 | 4.7213 | 4.7495 | 5.0138
2021-08-26 17:00 | 3.5247 | 3.8497 | 3.8819 | 3.9213 | 3.9672 | 3.2089 | 3.8366 | 3.8617 | 3.896 | 3.2089 | 5.6015 | 6.2693 | 6.2918 | 6.3218 | 6.6655
2021-08-26 18:00 | 3.8486 | 4.2051 | 4.241 | 4.285 | 4.3363 | 3.277 | 3.9224 | 3.9505 | 3.9887 | 3.277 | 5.0299 | 5.6393 | 5.6645 | 5.6979 | 6.0145
2021-08-26 19:00 | 3.7343 | 4.092 | 4.1329 | 4.183 | 4.2414 | 3.277 | 3.9295 | 3.9614 | 4.005 | 3.277 | 4.8012 | 5.3922 | 5.4208 | 5.4589 | 5.7684
2021-08-26 20:00 | 3.7343 | 4.1017 | 4.1475 | 4.2037 | 4.2691 | 3.1246 | 3.7565 | 3.7923 | 3.8411 | 3.1246 | 5.6015 | 6.2882 | 6.3204 | 6.3631 | 6.722
2021-08-26 21:00 | 3.4676 | 3.8167 | 3.8634 | 3.9206 | 3.9872 | 2.896 | 3.4876 | 3.524 | 3.5737 | 2.896 | 4.6107 | 5.1884 | 5.2212 | 5.2646 | 5.5701
2021-08-26 22:00 | 2.9913 | 3.2991 | 3.3427 | 3.3961 | 3.4584 | 2.566 | 3.0934 | 3.1275 | 3.1739 | 2.566 | 3.5247 | 3.9774 | 4.008 | 4.0486 | 4.291
2021-08-26 23:00 | 2.7055 | 2.9836 | 3.0229 | 3.0711 | 3.1272 | 2.0577 | 2.4868 | 2.5175 | 2.5593 | 2.0577 | 2.8769 | 3.2516 | 3.2791 | 3.3157 | 3.5177
2021-08-27 | 2.3846 | 2.6294 | 2.6639 | 2.7061 | 2.7554 | 1.7338 | 2.0973 | 2.1242 | 2.1609 | 1.7338 | 2.4197 | 2.7367 | 2.7609 | 2.793 | 2.9645
2021-08-27 01:00 | 2.1529 | 2.371 | 2.4006 | 2.4368 | 2.4791 | 1.6099 | 1.944 | 1.9671 | 1.9987 | 1.6099 | 2.5149 | 2.8358 | 2.8566 | 2.8841 | 3.0554
2021-08-27 02:00 | 2.1339 | 2.3384 | 2.3619 | 2.3906 | 2.424 | 1.4827 | 1.7849 | 1.8032 | 1.8281 | 1.4827 | 1.9815 | 2.2344 | 2.2509 | 2.2727 | 2.4077
2021-08-27 03:00 | 2.1148 | 2.3061 | 2.3235 | 2.3448 | 2.3697 | 1.4548 | 1.7434 | 1.7569 | 1.7755 | 1.4548 | 1.9053 | 2.1414 | 2.1536 | 2.1698 | 2.2939
2021-08-27 04:00 | 2.191 | 2.3779 | 2.3902 | 2.4052 | 2.4227 | 1.5623 | 1.8631 | 1.8726 | 1.8857 | 1.5623 | 2.2482 | 2.5153 | 2.5239 | 2.5353 | 2.6726
2021-08-27 05:00 | 2.3853 | 2.5826 | 2.5929 | 2.6054 | 2.62 | 1.7462 | 2.0775 | 2.0854 | 2.0963 | 1.7462 | 2.553 | 2.8513 | 2.8584 | 2.868 | 3.0197
2021-08-27 06:00 | 2.6293 | 2.8481 | 2.86 | 2.8746 | 2.8917 | 2.0813 | 2.4758 | 2.4851 | 2.4978 | 2.0813 | 3.1818 | 3.5523 | 3.5607 | 3.5718 | 3.76
2021-08-27 07:00 | 3.0865 | 3.3484 | 3.365 | 3.3853 | 3.409 | 2.2863 | 2.7245 | 2.7374 | 2.7551 | 2.2863 | 3.4866 | 3.8975 | 3.9091 | 3.9246 | 4.1347
2021-08-27 08:00 | 3.1437 | 3.4232 | 3.4466 | 3.4752 | 3.5086 | 2.553 | 3.0493 | 3.0676 | 3.0925 | 2.553 | 4.2868 | 4.7962 | 4.8126 | 4.8344 | 5.0961
2021-08-27 09:00 | 3.1056 | 3.3965 | 3.4272 | 3.4647 | 3.5085 | 2.4578 | 2.9471 | 2.9711 | 3.0037 | 2.4578 | 3.3151 | 3.7265 | 3.748 | 3.7766 | 3.993
2021-08-27 10:00 | 2.7245 | 2.9981 | 3.0343 | 3.0787 | 3.1305 | 2.1148 | 2.5499 | 2.5782 | 2.6168 | 2.1148 | 2.6483 | 2.9932 | 3.0186 | 3.0524 | 3.2384
2021-08-27 11:00 | 2.7245 | 3.0024 | 3.0409 | 3.088 | 3.1429 | 1.8734 | 2.2678 | 2.2978 | 2.3388 | 1.8734 | 2.3244 | 2.6364 | 2.6633 | 2.6992 | 2.8698
2021-08-27 12:00 | 3.1056 | 3.4107 | 3.4487 | 3.4951 | 3.5493 | 2.4006 | 2.8899 | 2.9195 | 2.96 | 2.4006 | 3.3914 | 3.8213 | 3.8479 | 3.8832 | 4.1119
2021-08-27 13:00 | 3.1818 | 3.4876 | 3.523 | 3.5663 | 3.6169 | 2.4197 | 2.9088 | 2.9364 | 2.9741 | 2.4197 | 3.5247 | 3.966 | 3.9908 | 4.0237 | 4.2569
2021-08-27 14:00 | 3.277 | 3.5846 | 3.6172 | 3.6571 | 3.7037 | 2.3625 | 2.8374 | 2.8628 | 2.8976 | 2.3625 | 3.8677 | 4.3432 | 4.3661 | 4.3965 | 4.6454
2021-08-27 15:00 | 3.277 | 3.581 | 3.6118 | 3.6495 | 3.6934 | 2.6674 | 3.1949 | 3.2189 | 3.2517 | 2.6674 | 4.4392 | 4.9759 | 4.9974 | 5.0261 | 5.3044
2021-08-27 16:00 | 3.3342 | 3.6415 | 3.6719 | 3.709 | 3.7524 | 2.8884 | 3.4554 | 3.4791 | 3.5114 | 2.8884 | 5.1632 | 5.7798 | 5.8011 | 5.8293 | 6.147
2021-08-27 17:00 | 3.6581 | 3.993 | 4.0252 | 4.0646 | 4.1105 | 3.3151 | 3.9621 | 3.9872 | 4.0215 | 3.3151 | 5.2585 | 5.8882 | 5.9107 | 5.9407 | 6.2656
2021-08-27 18:00 | 3.8105 | 4.1641 | 4.2001 | 4.2441 | 4.2953 | 3.4295 | 4.1025 | 4.1305 | 4.1688 | 3.4295 | 5.6015 | 6.2745 | 6.2997 | 6.3331 | 6.681
2021-08-27 19:00 | 3.8296 | 4.1944 | 4.2353 | 4.2854 | 4.3438 | 3.3533 | 4.0196 | 4.0515 | 4.0951 | 3.3533 | 5.0299 | 5.6462 | 5.6749 | 5.713 | 6.035
2021-08-27 20:00 | 3.5438 | 3.897 | 3.9429 | 3.999 | 4.0644 | 3.1056 | 3.734 | 3.7698 | 3.8186 | 3.1056 | 4.8584 | 5.4625 | 5.4947 | 5.5373 | 5.8555
2021-08-27 21:00 | 3.4676 | 3.8167 | 3.8634 | 3.9206 | 3.9872 | 2.9658 | 3.57 | 3.6064 | 3.6562 | 2.9658 | 5.5443 | 6.2259 | 6.2586 | 6.3021 | 6.6588
2021-08-27 22:00 | 3.3342 | 3.6675 | 3.7112 | 3.7646 | 3.8269 | 2.7245 | 3.2807 | 3.3147 | 3.3612 | 2.7245 | 4.1154 | 4.6337 | 4.6643 | 4.705 | 4.9798
2021-08-27 23:00 | 2.896 | 3.1883 | 3.2276 | 3.2758 | 3.3319 | 2.3244 | 2.8019 | 2.8326 | 2.8745 | 2.3244 | 3.7152 | 4.1831 | 4.2107 | 4.2473 | 4.4953
2021-08-28 | 2.5721 | 2.8309 | 2.8654 | 2.9076 | 2.9569 | 1.9206 | 2.318 | 2.3449 | 2.3817 | 1.9206 | 2.7626 | 3.1178 | 3.142 | 3.1741 | 3.3644
2021-08-28 01:00 | 2.4006 | 2.6371 | 2.6667 | 2.7029 | 2.7452 | 1.705 | 2.0563 | 2.0794 | 2.111 | 1.705 | 2.3054 | 2.6029 | 2.6237 | 2.6512 | 2.8109
2021-08-28 02:00 | 2.2291 | 2.4408 | 2.4642 | 2.4929 | 2.5264 | 1.6195 | 1.9465 | 1.9648 | 1.9898 | 1.6195 | 2.2101 | 2.4885 | 2.5049 | 2.5268 | 2.6744
2021-08-28 03:00 | 2.172 | 2.3675 | 2.3849 | 2.4063 | 2.4311 | 1.5433 | 1.8479 | 1.8615 | 1.88 | 1.5433 | 2.0767 | 2.3319 | 2.3441 | 2.3603 | 2.4939
2021-08-28 04:00 | 2.172 | 2.3575 | 2.3697 | 2.3847 | 2.4022 | 1.5242 | 1.8181 | 1.8276 | 1.8407 | 1.5242 | 2.553 | 2.8541 | 2.8627 | 2.8741 | 3.0281
2021-08-28 05:00 | 2.2673 | 2.4558 | 2.4661 | 2.4786 | 2.4932 | 1.6958 | 2.0179 | 2.0259 | 2.0368 | 1.6958 | 2.4006 | 2.6819 | 2.6891 | 2.6986 | 2.842
2021-08-28 06:00 | 2.3244 | 2.5206 | 2.5325 | 2.5471 | 2.5642 | 1.9053 | 2.2678 | 2.2771 | 2.2898 | 1.9053 | 2.8007 | 3.1289 | 3.1372 | 3.1483 | 3.3156
2021-08-28 07:00 | 2.553 | 2.7753 | 2.7919 | 2.8122 | 2.8358 | 2.0196 | 2.4094 | 2.4223 | 2.44 | 2.0196 | 3.1056 | 3.4741 | 3.4857 | 3.5011 | 3.6903
2021-08-28 08:00 | 2.6293 | 2.8705 | 2.8939 | 2.9226 | 2.956 | 2.1148 | 2.5316 | 2.5499 | 2.5748 | 2.1148 | 3.62 | 4.0552 | 4.0716 | 4.0934 | 4.3184
2021-08-28 09:00 | 2.3625 | 2.5982 | 2.6289 | 2.6664 | 2.7102 | 1.9053 | 2.2944 | 2.3183 | 2.351 | 1.9053 | 2.3435 | 2.6467 | 2.6682 | 2.6968 | 2.8598
2021-08-28 10:00 | 2.172 | 2.4045 | 2.4407 | 2.4851 | 2.5369 | 1.6576 | 2.0097 | 2.038 | 2.0767 | 1.6576 | 2.1148 | 2.4004 | 2.4258 | 2.4596 | 2.6162
2021-08-28 11:00 | 2.4197 | 2.6749 | 2.7134 | 2.7605 | 2.8154 | 1.7848 | 2.1632 | 2.1933 | 2.2342 | 1.7848 | 1.8672 | 2.1283 | 2.1552 | 2.191 | 2.3365
2021-08-28 12:00 | 2.3816 | 2.6329 | 2.6708 | 2.7173 | 2.7714 | 2.0196 | 2.4398 | 2.4694 | 2.5098 | 2.0196 | 2.5721 | 2.9109 | 2.9375 | 2.9728 | 3.1564
2021-08-28 13:00 | 2.3244 | 2.5665 | 2.6019 | 2.6452 | 2.6958 | 1.9243 | 2.3236 | 2.3512 | 2.3889 | 1.9243 | 2.4578 | 2.7803 | 2.8051 | 2.8381 | 3.0126
2021-08-28 14:00 | 2.5911 | 2.8477 | 2.8803 | 2.9202 | 2.9668 | 2.1529 | 2.5898 | 2.6152 | 2.65 | 2.1529 | 2.9913 | 3.3693 | 3.3922 | 3.4226 | 3.6233
2021-08-28 15:00 | 2.5721 | 2.8236 | 2.8544 | 2.8921 | 2.9361 | 2.2673 | 2.7222 | 2.7463 | 2.7791 | 2.2673 | 3.62 | 4.0654 | 4.087 | 4.1157 | 4.349
2021-08-28 16:00 | 2.8769 | 3.1503 | 3.1806 | 3.2178 | 3.2611 | 2.4246 | 2.9075 | 2.9312 | 2.9635 | 2.4246 | 4.1535 | 4.6577 | 4.6789 | 4.7072 | 4.9693
2021-08-28 17:00 | 3.2961 | 3.6041 | 3.6363 | 3.6757 | 3.7216 | 3.1246 | 3.737 | 3.7621 | 3.7964 | 3.1246 | 4.4583 | 4.9989 | 5.0215 | 5.0514 | 5.3323
2021-08-28 18:00 | 3.6771 | 4.0209 | 4.0568 | 4.1008 | 4.1521 | 3.258 | 3.8999 | 3.928 | 3.9662 | 3.258 | 4.9346 | 5.5335 | 5.5586 | 5.5921 | 5.9034
2021-08-28 19:00 | 3.5819 | 3.9283 | 3.9692 | 4.0193 | 4.0777 | 3.258 | 3.907 | 3.9389 | 3.9825 | 3.258 | 5.0299 | 5.6462 | 5.6749 | 5.713 | 6.035
2021-08-28 20:00 | 3.5441 | 3.8973 | 3.9431 | 3.9993 | 4.0647 | 3.0865 | 3.7115 | 3.7472 | 3.7961 | 3.0865 | 5.43 | 6.0977 | 6.1298 | 6.1725 | 6.5221
2021-08-28 21:00 | 3.4485 | 3.7963 | 3.843 | 3.9001 | 3.9668 | 2.8834 | 3.4728 | 3.5092 | 3.5589 | 2.8834 | 4.5345 | 5.1037 | 5.1365 | 5.1799 | 5.4812
2021-08-28 22:00 | 3.2199 | 3.5447 | 3.5883 | 3.6418 | 3.7041 | 2.7384 | 3.2971 | 3.3312 | 3.3776 | 2.7384 | 5.0299 | 5.65 | 5.6806 | 5.7212 | 6.0463
2021-08-28 23:00 | 2.915 | 3.2087 | 3.2481 | 3.2962 | 3.3524 | 2.3308 | 2.8094 | 2.8401 | 2.882 | 2.3308 | 3.3342 | 3.7597 | 3.7873 | 3.8239 | 4.051
2021-08-29 | 2.6483 | 2.9127 | 2.9472 | 2.9895 | 3.0387 | 2.0103 | 2.4239 | 2.4509 | 2.4876 | 2.0103 | 2.8276 | 3.19 | 3.2142 | 3.2463 | 3.4402
2021-08-29 01:00 | 2.4578 | 2.6985 | 2.7281 | 2.7643 | 2.8066 | 1.829 | 2.2029 | 2.226 | 2.2575 | 1.829 | 2.5721 | 2.8993 | 2.9201 | 2.9477 | 3.122
2021-08-29 02:00 | 2.2673 | 2.4817 | 2.5052 | 2.5339 | 2.5673 | 1.6957 | 2.0365 | 2.0548 | 2.0798 | 1.6957 | 2.4768 | 2.7849 | 2.8013 | 2.8232 | 2.9854
2021-08-29 03:00 | 2.3054 | 2.5108 | 2.5282 | 2.5495 | 2.5744 | 1.6385 | 1.9604 | 1.974 | 1.9925 | 1.6385 | 2.3435 | 2.6283 | 2.6405 | 2.6567 | 2.8049
2021-08-29 04:00 | 2.3244 | 2.5212 | 2.5335 | 2.5485 | 2.566 | 1.5814 | 1.8856 | 1.8951 | 1.9082 | 1.5814 | 2.1529 | 2.4095 | 2.4181 | 2.4295 | 2.5615
2021-08-29 05:00 | 2.3244 | 2.5172 | 2.5275 | 2.54 | 2.5546 | 1.6909 | 2.0121 | 2.0201 | 2.031 | 1.6909 | 2.6293 | 2.936 | 2.9431 | 2.9527 | 3.1086
2021-08-29 06:00 | 2.4006 | 2.6025 | 2.6144 | 2.629 | 2.646 | 1.97 | 2.3443 | 2.3536 | 2.3663 | 1.97 | 2.9722 | 3.3194 | 3.3278 | 3.3389 | 3.5156
2021-08-29 07:00 | 2.7055 | 2.939 | 2.9556 | 2.9759 | 2.9996 | 2.2482 | 2.6795 | 2.6924 | 2.7101 | 2.2482 | 3.5057 | 3.9187 | 3.9303 | 3.9457 | 4.1569
2021-08-29 08:00 | 2.7245 | 2.9729 | 2.9963 | 3.0249 | 3.0583 | 2.3646 | 2.8266 | 2.8449 | 2.8698 | 2.3646 | 4.1154 | 4.6057 | 4.6221 | 4.6438 | 4.8961
2021-08-29 09:00 | 3.0294 | 3.3146 | 3.3453 | 3.3828 | 3.4266 | 2.6102 | 3.1272 | 3.1511 | 3.1838 | 2.6102 | 4.706 | 5.2721 | 5.2936 | 5.3221 | 5.615
2021-08-29 10:00 | 2.9341 | 3.2232 | 3.2595 | 3.3039 | 3.3556 | 2.5149 | 3.0226 | 3.0509 | 3.0895 | 2.5149 | 3.7534 | 4.2212 | 4.2466 | 4.2804 | 4.5271
2021-08-29 11:00 | 3.0103 | 3.3094 | 3.3479 | 3.395 | 3.4499 | 2.6674 | 3.2058 | 3.2358 | 3.2768 | 2.6674 | 4.4583 | 5.0077 | 5.0346 | 5.0705 | 5.3584
2021-08-29 12:00 | 3.3342 | 3.6564 | 3.6943 | 3.7407 | 3.7949 | 2.9726 | 3.5657 | 3.5953 | 3.6357 | 2.9726 | 4.9727 | 5.5786 | 5.6052 | 5.6405 | 5.9561
2021-08-29 13:00 | 3.5438 | 3.8765 | 3.9119 | 3.9553 | 4.0058 | 3.1437 | 3.7641 | 3.7917 | 3.8294 | 3.1437 | 5.4109 | 6.062 | 6.0868 | 6.1198 | 6.4566
2021-08-29 14:00 | 3.5819 | 3.9121 | 3.9447 | 3.9846 | 4.0312 | 3.1818 | 3.8052 | 3.8307 | 3.8654 | 3.1818 | 5.8682 | 6.5663 | 6.5892 | 6.6196 | 6.9785
2021-08-29 15:00 | 3.0865 | 3.3763 | 3.4071 | 3.4448 | 3.4887 | 2.8007 | 3.3525 | 3.3765 | 3.4093 | 2.8007 | 4.5726 | 5.1241 | 5.1456 | 5.1743 | 5.46
2021-08-29 16:00 | 3.5819 | 3.9076 | 3.938 | 3.9751 | 4.0185 | 3.3364 | 3.9846 | 4.0083 | 4.0406 | 3.3364 | 6.2683 | 7.0078 | 7.0291 | 7.0573 | 7.4357
2021-08-29 17:00 | 3.8783 | 4.2296 | 4.2618 | 4.3011 | 4.3471 | 3.5628 | 4.2547 | 4.2798 | 4.3141 | 3.5628 | 5.8872 | 6.5869 | 6.6094 | 6.6393 | 6.9988
2021-08-29 18:00 | 4.0201 | 4.3893 | 4.4252 | 4.4692 | 4.5205 | 3.7152 | 4.4401 | 4.4682 | 4.5064 | 3.7152 | 6.2492 | 6.9943 | 7.0195 | 7.053 | 7.4365
2021-08-29 19:00 | 4.0201 | 4.399 | 4.44 | 4.49 | 4.5484 | 3.535 | 4.2343 | 4.2662 | 4.3098 | 3.535 | 5.6396 | 6.3237 | 6.3524 | 6.3905 | 6.7461
2021-08-29 20:00 | 3.8486 | 4.2245 | 4.2704 | 4.3265 | 4.3919 | 3.3914 | 4.0716 | 4.1074 | 4.1562 | 3.3914 | 5.1632 | 5.8013 | 5.8334 | 5.8761 | 6.211
2021-08-29 21:00 | 3.62 | 3.9805 | 4.0272 | 4.0843 | 4.151 | 3.2389 | 3.8927 | 3.9291 | 3.9789 | 3.2389 | 5.0299 | 5.6542 | 5.6869 | 5.7304 | 6.0589
2021-08-29 22:00 | 3.4104 | 3.7494 | 3.793 | 3.8465 | 3.9088 | 2.8123 | 3.3844 | 3.4185 | 3.465 | 2.8123 | 4.0963 | 4.6126 | 4.6432 | 4.6838 | 4.9576
2021-08-29 23:00 | 2.9722 | 3.2702 | 3.3095 | 3.3576 | 3.4138 | 2.3668 | 2.8519 | 2.8826 | 2.9245 | 2.3668 | 3.4485 | 3.8867 | 3.9143 | 3.9509 | 4.1843
2021-08-30 | 2.6483 | 2.9127 | 2.9472 | 2.9895 | 3.0387 | 1.9434 | 2.3449 | 2.3718 | 2.4085 | 1.9434 | 2.6326 | 2.9734 | 2.9976 | 3.0297 | 3.2128
2021-08-30 01:00 | 2.4768 | 2.7189 | 2.7486 | 2.7848 | 2.8271 | 1.7719 | 2.1353 | 2.1584 | 2.19 | 1.7719 | 2.4578 | 2.7723 | 2.793 | 2.8206 | 2.9887
2021-08-30 02:00 | 2.3244 | 2.5431 | 2.5666 | 2.5953 | 2.6287 | 1.6951 | 2.0359 | 2.0541 | 2.0791 | 1.6951 | 2.2482 | 2.5308 | 2.5473 | 2.5691 | 2.7188
2021-08-30 03:00 | 2.3816 | 2.5927 | 2.6101 | 2.6314 | 2.6563 | 1.6195 | 1.9379 | 1.9515 | 1.97 | 1.6195 | 2.4197 | 2.713 | 2.7252 | 2.7414 | 2.8938
2021-08-30 04:00 | 2.4387 | 2.644 | 2.6563 | 2.6713 | 2.6888 | 1.7551 | 2.0908 | 2.1004 | 2.1135 | 1.7551 | 2.534 | 2.8329 | 2.8415 | 2.8529 | 3.0059
2021-08-30 05:00 | 2.6102 | 2.8243 | 2.8345 | 2.847 | 2.8616 | 1.9743 | 2.3469 | 2.3548 | 2.3657 | 1.9743 | 3.7915 | 4.2275 | 4.2346 | 4.2442 | 4.464
2021-08-30 06:00 | 3.0333 | 3.2822 | 3.2941 | 3.3087 | 3.3257 | 2.4197 | 2.8755 | 2.8848 | 2.8975 | 2.4197 | 3.982 | 4.4416 | 4.4499 | 4.461 | 4.6932
2021-08-30 07:00 | 3.5438 | 3.8397 | 3.8563 | 3.8766 | 3.9002 | 2.8769 | 3.4223 | 3.4352 | 3.4528 | 2.8769 | 4.5345 | 5.062 | 5.0736 | 5.089 | 5.3568
2021-08-30 08:00 | 4.0201 | 4.3648 | 4.3882 | 4.4168 | 4.4502 | 3.1627 | 3.7696 | 3.7878 | 3.8127 | 3.1627 | 5.4109 | 6.0454 | 6.0618 | 6.0835 | 6.4071
2021-08-30 09:00 | 3.9058 | 4.2562 | 4.2869 | 4.3244 | 4.3682 | 3.277 | 3.915 | 3.9389 | 3.9716 | 3.277 | 4.8393 | 5.4203 | 5.4418 | 5.4703 | 5.7705
2021-08-30 10:00 | 3.2961 | 3.6121 | 3.6484 | 3.6928 | 3.7445 | 2.6534 | 3.1862 | 3.2145 | 3.2531 | 2.6534 | 3.5628 | 4.0095 | 4.0349 | 4.0687 | 4.3049
2021-08-30 11:00 | 2.7055 | 2.9819 | 3.0204 | 3.0675 | 3.1224 | 2.172 | 2.6206 | 2.6506 | 2.6916 | 2.172 | 2.3816 | 2.6999 | 2.7269 | 2.7627 | 2.9365
2021-08-30 12:00 | 2.3625 | 2.6124 | 2.6504 | 2.6968 | 2.751 | 1.829 | 2.2147 | 2.2443 | 2.2847 | 1.829 | 1.9053 | 2.1699 | 2.1964 | 2.2318 | 2.3787
2021-08-30 13:00 | 2.553 | 2.8121 | 2.8475 | 2.8909 | 2.9414 | 1.8404 | 2.2245 | 2.2521 | 2.2898 | 1.8404 | 1.9624 | 2.2298 | 2.2546 | 2.2876 | 2.4349
2021-08-30 14:00 | 2.5428 | 2.7957 | 2.8284 | 2.8683 | 2.9149 | 1.9434 | 2.3422 | 2.3677 | 2.4024 | 1.9434 | 2.6102 | 2.9459 | 2.9687 | 2.9991 | 3.1789
2021-08-30 15:00 | 2.6483 | 2.9055 | 2.9363 | 2.974 | 3.018 | 2.0577 | 2.4746 | 2.4987 | 2.5315 | 2.0577 | 2.9341 | 3.3032 | 3.3248 | 3.3535 | 3.5491
2021-08-30 16:00 | 3.0103 | 3.2935 | 3.3239 | 3.3611 | 3.4044 | 2.5216 | 3.0221 | 3.0458 | 3.0781 | 2.5216 | 3.6771 | 4.1284 | 4.1496 | 4.1779 | 4.4138
2021-08-30 17:00 | 3.7106 | 4.0495 | 4.0817 | 4.121 | 4.167 | 3.3533 | 4.0071 | 4.0322 | 4.0665 | 3.3533 | 6.2683 | 7.0103 | 7.0328 | 7.0628 | 7.4432
2021-08-30 18:00 | 3.8677 | 4.2255 | 4.2615 | 4.3055 | 4.3567 | 3.4676 | 4.1475 | 4.1756 | 4.2138 | 3.4676 | 5.2585 | 5.8934 | 5.9186 | 5.952 | 6.2811
2021-08-30 19:00 | 3.9248 | 4.2967 | 4.3376 | 4.3877 | 4.4461 | 3.4676 | 4.1546 | 4.1865 | 4.2301 | 3.4676 | 5.0489 | 5.6674 | 5.6961 | 5.7342 | 6.0573
2021-08-30 20:00 | 3.6771 | 4.0403 | 4.0861 | 4.1423 | 4.2077 | 3.3151 | 3.9816 | 4.0173 | 4.0662 | 3.3151 | 5.9444 | 6.6693 | 6.7015 | 6.7442 | 7.122
2021-08-30 21:00 | 3.6009 | 3.96 | 4.0067 | 4.0639 | 4.1305 | 3.1627 | 3.8027 | 3.8391 | 3.8888 | 3.1627 | 4.6298 | 5.2096 | 5.2423 | 5.2858 | 5.5923
2021-08-30 22:00 | 3.1246 | 3.4424 | 3.486 | 3.5394 | 3.6017 | 2.7436 | 3.3032 | 3.3372 | 3.3837 | 2.7436 | 3.8105 | 4.295 | 4.3256 | 4.3662 | 4.6243
2021-08-30 23:00 | 2.7626 | 3.045 | 3.0843 | 3.1325 | 3.1886 | 2.301 | 2.7742 | 2.8049 | 2.8468 | 2.301 | 3.2961 | 3.7174 | 3.7449 | 3.7815 | 4.0065
2021-08-31 | 2.6674 | 2.9332 | 2.9677 | 3.01 | 3.0592 | 1.971 | 2.3775 | 2.4044 | 2.4412 | 1.971 | 2.7817 | 3.139 | 3.1632 | 3.1953 | 3.3866
2021-08-31 01:00 | 2.4387 | 2.678 | 2.7076 | 2.7439 | 2.7861 | 1.7797 | 2.1446 | 2.1677 | 2.1992 | 1.7797 | 2.3625 | 2.6664 | 2.6872 | 2.7148 | 2.8776
2021-08-31 02:00 | 2.2863 | 2.5022 | 2.5256 | 2.5543 | 2.5878 | 1.6957 | 2.0365 | 2.0548 | 2.0798 | 1.6957 | 2.3625 | 2.6579 | 2.6743 | 2.6961 | 2.8521
2021-08-31 03:00 | 2.3625 | 2.5722 | 2.5896 | 2.6109 | 2.6358 | 1.6576 | 1.9829 | 1.9965 | 2.0151 | 1.6576 | 2.5721 | 2.8824 | 2.8946 | 2.9108 | 3.0716
2021-08-31 04:00 | 2.4006 | 2.6031 | 2.6154 | 2.6304 | 2.6479 | 1.7314 | 2.0629 | 2.0724 | 2.0855 | 1.7314 | 2.5149 | 2.8117 | 2.8203 | 2.8317 | 2.9836
2021-08-31 05:00 | 2.7436 | 2.9676 | 2.9778 | 2.9903 | 3.0049 | 2.0399 | 2.4244 | 2.4324 | 2.4433 | 2.0399 | 3.639 | 4.0581 | 4.0653 | 4.0748 | 4.2862
2021-08-31 06:00 | 2.9469 | 3.1894 | 3.2013 | 3.2159 | 3.233 | 2.4006 | 2.853 | 2.8623 | 2.875 | 2.4006 | 3.9439 | 4.3992 | 4.4076 | 4.4187 | 4.6488
2021-08-31 07:00 | 3.3723 | 3.6555 | 3.672 | 3.6923 | 3.716 | 2.6293 | 3.1297 | 3.1426 | 3.1602 | 2.6293 | 4.0391 | 4.5115 | 4.5231 | 4.5386 | 4.7791
2021-08-31 08:00 | 3.258 | 3.546 | 3.5694 | 3.598 | 3.6314 | 2.5696 | 3.0688 | 3.0871 | 3.112 | 2.5696 | 3.6009 | 4.034 | 4.0504 | 4.0722 | 4.2962
2021-08-31 09:00 | 3.0103 | 3.2941 | 3.3248 | 3.3624 | 3.4061 | 2.1226 | 2.5512 | 2.5751 | 2.6077 | 2.1226 | 2.8007 | 3.1549 | 3.1764 | 3.2049 | 3.393
2021-08-31 10:00 | 2.191 | 2.4249 | 2.4612 | 2.5056 | 2.5573 | 1.6576 | 2.0097 | 2.038 | 2.0767 | 1.6576 | 1.81 | 2.0617 | 2.0871 | 2.1208 | 2.2607
2021-08-31 11:00 | 1.9243 | 2.1427 | 2.1812 | 2.2283 | 2.2832 | 1.4289 | 1.7428 | 1.7728 | 1.8138 | 1.4289 | 0.83831 | 0.98495 | 1.0119 | 1.0477 | 1.1367
2021-08-31 12:00 | 1.81 | 2.0188 | 2.0568 | 2.1032 | 2.1574 | 1.2909 | 1.579 | 1.6086 | 1.649 | 1.2909 | 0.81926 | 0.96303 | 0.98962 | 1.0249 | 1.1122
2021-08-31 13:00 | 2.2673 | 2.5051 | 2.5405 | 2.5838 | 2.6344 | 1.7719 | 2.1436 | 2.1712 | 2.2089 | 1.7719 | 1.6385 | 1.8699 | 1.8947 | 1.9277 | 2.0571
2021-08-31 14:00 | 2.4959 | 2.7453 | 2.778 | 2.8179 | 2.8645 | 1.8556 | 2.2385 | 2.264 | 2.2987 | 1.8556 | 1.8499 | 2.101 | 2.1239 | 2.1543 | 2.2923
2021-08-31 15:00 | 2.5911 | 2.8441 | 2.8749 | 2.9126 | 2.9565 | 1.8672 | 2.2496 | 2.2736 | 2.3064 | 1.8672 | 2.0196 | 2.287 | 2.3086 | 2.3372 | 2.4826
2021-08-31 16:00 | 2.553 | 2.8023 | 2.8326 | 2.8698 | 2.9131 | 2.1182 | 2.5455 | 2.5692 | 2.6015 | 2.1182 | 2.5911 | 2.9215 | 2.9428 | 2.9711 | 3.1473
2021-08-31 17:00 | 3.2253 | 3.528 | 3.5602 | 3.5996 | 3.6455 | 2.7557 | 3.3013 | 3.3264 | 3.3606 | 2.7557 | 4.1154 | 4.6178 | 4.6404 | 4.6703 | 4.9324
2021-08-31 18:00 | 3.4676 | 3.7957 | 3.8316 | 3.8756 | 3.9269 | 3.1818 | 3.8099 | 3.8379 | 3.8762 | 3.1818 | 4.6869 | 5.2582 | 5.2834 | 5.3168 | 5.6145
2021-08-31 19:00 | 3.4801 | 3.8189 | 3.8598 | 3.9099 | 3.9683 | 3.0865 | 3.7045 | 3.7364 | 3.7799 | 3.0865 | 4.7631 | 5.3498 | 5.3785 | 5.4166 | 5.724
2021-08-31 20:00 | 3.4866 | 3.8356 | 3.8814 | 3.9376 | 4.003 | 2.9341 | 3.5314 | 3.5672 | 3.616 | 2.9341 | 4.4964 | 5.0603 | 5.0924 | 5.1351 | 5.4333
2021-08-31 21:00 | 3.2961 | 3.6325 | 3.6792 | 3.7364 | 3.803 | 2.8007 | 3.375 | 3.4115 | 3.4612 | 2.8007 | 4.5726 | 5.1461 | 5.1788 | 5.2223 | 5.5256
2021-08-31 22:00 | 3.0103 | 3.3195 | 3.3632 | 3.4166 | 3.4789 | 2.5086 | 3.0257 | 3.0597 | 3.1062 | 2.5086 | 3.4485 | 3.8927 | 3.9233 | 3.9639 | 4.2021
2021-08-31 23:00 | 2.7055 | 2.9836 | 3.0229 | 3.0711 | 3.1272 | 2.0032 | 2.4225 | 2.4532 | 2.495 | 2.0032 | 3.2199 | 3.6327 | 3.6602 | 3.6968 | 3.9176
2021-09-01 | 2.3816 | 2.6262 | 2.6607 | 2.7029 | 2.7522 | 1.7719 | 2.1423 | 2.1692 | 2.206 | 1.7719 | 2.3054 | 2.6097 | 2.6339 | 2.666 | 2.8312
2021-09-01 01:00 | 2.191 | 2.4119 | 2.4415 | 2.4778 | 2.52 | 1.5814 | 1.9103 | 1.9334 | 1.9649 | 1.5814 | 2.1148 | 2.3912 | 2.4119 | 2.4395 | 2.5887
2021-09-01 02:00 | 2.1529 | 2.3589 | 2.3823 | 2.411 | 2.4445 | 1.4099 | 1.6989 | 1.7172 | 1.7422 | 1.4099 | 1.9815 | 2.2344 | 2.2509 | 2.2727 | 2.4077
2021-09-01 03:00 | 2.0196 | 2.2038 | 2.2212 | 2.2425 | 2.2674 | 1.4099 | 1.6903 | 1.7039 | 1.7225 | 1.4099 | 2.0005 | 2.2472 | 2.2594 | 2.2756 | 2.405
2021-09-01 04:00 | 2.1339 | 2.3165 | 2.3288 | 2.3438 | 2.3613 | 1.5052 | 1.7956 | 1.8051 | 1.8182 | 1.5052 | 1.9942 | 2.2331 | 2.2416 | 2.2531 | 2.3763
2021-09-01 05:00 | 2.3244 | 2.5172 | 2.5275 | 2.54 | 2.5546 | 1.7207 | 2.0473 | 2.0553 | 2.0662 | 1.7207 | 2.6674 | 2.9783 | 2.9855 | 2.995 | 3.153
2021-09-01 06:00 | 2.5144 | 2.7247 | 2.7366 | 2.7512 | 2.7682 | 2.0756 | 2.469 | 2.4783 | 2.491 | 2.0756 | 3.2199 | 3.5947 | 3.603 | 3.6141 | 3.8044
2021-09-01 07:00 | 2.8198 | 3.0619 | 3.0784 | 3.0987 | 3.1224 | 2.1148 | 2.5219 | 2.5349 | 2.5525 | 2.1148 | 3.1246 | 3.4952 | 3.5069 | 3.5223 | 3.7125
2021-09-01 08:00 | 2.7245 | 2.9729 | 2.9963 | 3.0249 | 3.0583 | 2.1148 | 2.5316 | 2.5499 | 2.5748 | 2.1148 | 3.1818 | 3.5682 | 3.5846 | 3.6064 | 3.8074
2021-09-01 09:00 | 2.7241 | 2.9866 | 3.0173 | 3.0549 | 3.0986 | 2.0767 | 2.497 | 2.5209 | 2.5536 | 2.0767 | 1.9434 | 2.2021 | 2.2236 | 2.2522 | 2.3931
2021-09-01 10:00 | 1.8481 | 2.0565 | 2.0927 | 2.1371 | 2.1889 | 1.3337 | 1.6271 | 1.6554 | 1.694 | 1.3337 | 0.91452 | 1.0666 | 1.092 | 1.1257 | 1.2164
2021-09-01 11:00 | 1.6004 | 1.7947 | 1.8332 | 1.8803 | 1.9352 | 1.1432 | 1.4052 | 1.4352 | 1.4762 | 1.1432 | 0.78115 | 0.92143 | 0.9484 | 0.98422 | 1.07
2021-09-01 12:00 | 1.5623 | 1.7527 | 1.7907 | 1.8371 | 1.8913 | 1.086 | 1.3369 | 1.3665 | 1.4069 | 1.086 | 0.85737 | 1.0054 | 1.032 | 1.0673 | 1.1567
2021-09-01 13:00 | 1.5433 | 1.7273 | 1.7627 | 1.806 | 1.8565 | 1.0288 | 1.2658 | 1.2934 | 1.3311 | 1.0288 | 0.80021 | 0.93833 | 0.96313 | 0.99609 | 1.0795
2021-09-01 14:00 | 1.6957 | 1.8856 | 1.9183 | 1.9582 | 2.0048 | 1.105 | 1.3519 | 1.3773 | 1.4121 | 1.105 | 0.80021 | 0.9345 | 0.95736 | 0.98775 | 1.0681
2021-09-01 15:00 | 1.9815 | 2.1891 | 2.2199 | 2.2576 | 2.3015 | 1.1813 | 1.4393 | 1.4633 | 1.4961 | 1.1813 | 1.1241 | 1.2919 | 1.3135 | 1.3421 | 1.4382
2021-09-01 16:00 | 2.2101 | 2.4338 | 2.4642 | 2.5014 | 2.5447 | 1.5953 | 1.9278 | 1.9515 | 1.9839 | 1.5953 | 1.8481 | 2.0958 | 2.1171 | 2.1454 | 2.2808
2021-09-01 17:00 | 2.553 | 2.8058 | 2.838 | 2.8774 | 2.9233 | 2.1603 | 2.5979 | 2.623 | 2.6572 | 2.1603 | 2.6905 | 3.0344 | 3.057 | 3.0869 | 3.2706
2021-09-01 18:00 | 2.7626 | 3.0383 | 3.0743 | 3.1183 | 3.1695 | 2.4197 | 2.9096 | 2.9376 | 2.9759 | 2.4197 | 3.2389 | 3.6491 | 3.6743 | 3.7077 | 3.9258
2021-09-01 19:00 | 2.7817 | 3.0686 | 3.1095 | 3.1596 | 3.218 | 2.3625 | 2.8492 | 2.8811 | 2.9246 | 2.3625 | 3.5628 | 4.016 | 4.0446 | 4.0827 | 4.3241
2021-09-01 20:00 | 2.915 | 3.2215 | 3.2674 | 3.3235 | 3.389 | 2.2863 | 2.7661 | 2.8019 | 2.8508 | 2.2863 | 3.9058 | 4.4039 | 4.436 | 4.4787 | 4.7445
2021-09-01 21:00 | 2.6102 | 2.8956 | 2.9423 | 2.9995 | 3.0661 | 2.2863 | 2.7673 | 2.8037 | 2.8535 | 2.2863 | 3.639 | 4.1087 | 4.1414 | 4.1848 | 4.4369
2021-09-01 22:00 | 2.4768 | 2.7464 | 2.7901 | 2.8435 | 2.9058 | 2.0225 | 2.4514 | 2.4854 | 2.5319 | 2.0225 | 2.7436 | 3.1093 | 3.1399 | 3.1806 | 3.38
2021-09-01 23:00 | 2.2863 | 2.5333 | 2.5726 | 2.6208 | 2.6769 | 1.738 | 2.1091 | 2.1398 | 2.1817 | 1.738 | 2.2863 | 2.5952 | 2.6228 | 2.6594 | 2.8289
2021-09-02 | 2.2673 | 2.5034 | 2.5379 | 2.5801 | 2.6294 | 1.5623 | 1.8947 | 1.9216 | 1.9584 | 1.5623 | 2.1148 | 2.398 | 2.4222 | 2.4543 | 2.609
2021-09-02 01:00 | 2.0005 | 2.2072 | 2.2368 | 2.2731 | 2.3154 | 1.3908 | 1.6852 | 1.7083 | 1.7398 | 1.3908 | 1.7719 | 2.0101 | 2.0308 | 2.0584 | 2.1888
2021-09-02 02:00 | 2.0196 | 2.2156 | 2.2391 | 2.2678 | 2.3012 | 1.3527 | 1.6314 | 1.6497 | 1.6747 | 1.3527 | 1.7719 | 2.0015 | 2.018 | 2.0398 | 2.1633
2021-09-02 03:00 | 2.0386 | 2.2243 | 2.2417 | 2.263 | 2.2878 | 1.3275 | 1.593 | 1.6065 | 1.6251 | 1.3275 | 2.1148 | 2.3743 | 2.3865 | 2.4027 | 2.5383
2021-09-02 04:00 | 2.172 | 2.3575 | 2.3697 | 2.3847 | 2.4022 | 1.4586 | 1.7405 | 1.7501 | 1.7631 | 1.4586 | 2.0005 | 2.2401 | 2.2487 | 2.2601 | 2.3837
2021-09-02 05:00 | 2.4003 | 2.5988 | 2.609 | 2.6215 | 2.6362 | 1.7605 | 2.0943 | 2.1023 | 2.1132 | 1.7605 | 2.8007 | 3.1265 | 3.1337 | 3.1432 | 3.3086
2021-09-02 06:00 | 2.6102 | 2.8276 | 2.8396 | 2.8542 | 2.8712 | 2.0577 | 2.4478 | 2.4571 | 2.4698 | 2.0577 | 3.1437 | 3.51 | 3.5183 | 3.5294 | 3.7156
2021-09-02 07:00 | 2.7436 | 2.98 | 2.9966 | 3.0169 | 3.0405 | 2.0767 | 2.4769 | 2.4899 | 2.5075 | 2.0767 | 3.3723 | 3.7705 | 3.7821 | 3.7975 | 4.0014
2021-09-02 08:00 | 2.6293 | 2.8705 | 2.8939 | 2.9226 | 2.956 | 1.908 | 2.2873 | 2.3055 | 2.3304 | 1.908 | 2.8388 | 3.1871 | 3.2035 | 3.2253 | 3.4074
2021-09-02 09:00 | 2.2482 | 2.4754 | 2.5061 | 2.5436 | 2.5874 | 1.5762 | 1.9057 | 1.9296 | 1.9623 | 1.5762 | 1.6195 | 1.8422 | 1.8637 | 1.8922 | 2.0154
2021-09-02 10:00 | 1.829 | 2.036 | 2.0723 | 2.1167 | 2.1684 | 1.2575 | 1.5371 | 1.5654 | 1.604 | 1.2575 | 0.95263 | 1.1089 | 1.1343 | 1.1681 | 1.2608
2021-09-02 11:00 | 1.5814 | 1.7743 | 1.8127 | 1.8598 | 1.9148 | 1.0288 | 1.2701 | 1.3002 | 1.3411 | 1.0288 | 0.85737 | 1.0061 | 1.0331 | 1.0689 | 1.1589
2021-09-02 12:00 | 1.5052 | 1.6913 | 1.7293 | 1.7757 | 1.8299 | 1.0098 | 1.2469 | 1.2765 | 1.3169 | 1.0098 | 0.97168 | 1.1324 | 1.159 | 1.1943 | 1.29
2021-09-02 13:00 | 1.7338 | 1.932 | 1.9674 | 2.0107 | 2.0612 | 1.0098 | 1.2433 | 1.2709 | 1.3086 | 1.0098 | 1.105 | 1.2771 | 1.3019 | 1.3348 | 1.435
2021-09-02 14:00 | 2.0005 | 2.2131 | 2.2458 | 2.2857 | 2.3323 | 0.94811 | 1.1665 | 1.1919 | 1.2267 | 0.94811 | 1.086 | 1.2521 | 1.2749 | 1.3053 | 1.4014
2021-09-02 15:00 | 1.7719 | 1.9639 | 1.9947 | 2.0324 | 2.0764 | 1.209 | 1.4721 | 1.4961 | 1.5289 | 1.209 | 1.0288 | 1.186 | 1.2076 | 1.2363 | 1.3271
2021-09-02 16:00 | 2.0386 | 2.2496 | 2.28 | 2.3171 | 2.3605 | 1.5416 | 1.8644 | 1.8881 | 1.9204 | 1.5416 | 1.8862 | 2.1382 | 2.1594 | 2.1877 | 2.3252
2021-09-02 17:00 | 2.4489 | 2.6939 | 2.7261 | 2.7655 | 2.8114 | 2.0577 | 2.4766 | 2.5017 | 2.536 | 2.0577 | 3.2389 | 3.6439 | 3.6664 | 3.6964 | 3.9103
2021-09-02 18:00 | 2.6864 | 2.9565 | 2.9924 | 3.0364 | 3.0877 | 2.2291 | 2.6845 | 2.7125 | 2.7508 | 2.2291 | 3.1818 | 3.5856 | 3.6108 | 3.6442 | 3.8591
2021-09-02 19:00 | 2.6864 | 2.9662 | 3.0071 | 3.0572 | 3.1156 | 2.2291 | 2.6916 | 2.7235 | 2.7671 | 2.2291 | 3.2961 | 3.7195 | 3.7482 | 3.7863 | 4.0131
2021-09-02 20:00 | 2.6864 | 2.9759 | 3.0217 | 3.0779 | 3.1433 | 2.1339 | 2.5861 | 2.6219 | 2.6707 | 2.1339 | 3.3723 | 3.8111 | 3.8432 | 3.8859 | 4.1223
2021-09-02 21:00 | 2.4387 | 2.7114 | 2.7581 | 2.8153 | 2.8819 | 1.988 | 2.415 | 2.4514 | 2.5011 | 1.988 | 3.1246 | 3.537 | 3.5697 | 3.6132 | 3.8369
2021-09-02 22:00 | 2.2692 | 2.5234 | 2.567 | 2.6204 | 2.6827 | 1.81 | 2.2003 | 2.2344 | 2.2808 | 1.81 | 2.8579 | 3.2364 | 3.267 | 3.3076 | 3.5133
2021-09-02 23:00 | 2.0958 | 2.3286 | 2.3679 | 2.4161 | 2.4722 | 1.586 | 1.9295 | 1.9602 | 2.0021 | 1.586 | 2.5149 | 2.8493 | 2.8768 | 2.9135 | 3.0955
2021-09-03 | 1.9434 | 2.1554 | 2.1899 | 2.2321 | 2.2814 | 1.3718 | 1.6696 | 1.6965 | 1.7333 | 1.3718 | 1.8862 | 2.1439 | 2.1681 | 2.2002 | 2.3423
2021-09-03 01:00 | 1.8862 | 2.0844 | 2.114 | 2.1503 | 2.1925 | 1.279 | 1.5531 | 1.5762 | 1.6077 | 1.279 | 1.6195 | 1.8407 | 1.8615 | 1.889 | 2.011
2021-09-03 02:00 | 1.8481 | 2.0314 | 2.0548 | 2.0835 | 2.117 | 1.1813 | 1.4288 | 1.4471 | 1.4721 | 1.1813 | 1.7147 | 1.938 | 1.9544 | 1.9763 | 2.0966
2021-09-03 03:00 | 1.7909 | 1.9582 | 1.9756 | 1.9969 | 2.0217 | 1.1813 | 1.4202 | 1.4338 | 1.4524 | 1.1813 | 1.6766 | 1.8873 | 1.8995 | 1.9157 | 2.0273
2021-09-03 04:00 | 1.7999 | 1.9577 | 1.97 | 1.985 | 2.0025 | 1.2194 | 1.4579 | 1.4675 | 1.4806 | 1.2194 | 1.7338 | 1.9437 | 1.9523 | 1.9637 | 2.0726
2021-09-03 05:00 | 1.9967 | 2.1652 | 2.1754 | 2.188 | 2.2026 | 1.4861 | 1.7702 | 1.7781 | 1.789 | 1.4861 | 2.4959 | 2.7878 | 2.7949 | 2.8045 | 2.953
2021-09-03 06:00 | 2.1529 | 2.3364 | 2.3483 | 2.3629 | 2.3799 | 1.6576 | 1.9752 | 1.9845 | 1.9972 | 1.6576 | 2.5149 | 2.8113 | 2.8197 | 2.8308 | 2.9823
2021-09-03 07:00 | 2.191 | 2.3864 | 2.403 | 2.4233 | 2.4469 | 1.6576 | 1.9818 | 1.9947 | 2.0123 | 1.6576 | 2.4959 | 2.7966 | 2.8082 | 2.8236 | 2.9793
2021-09-03 08:00 | 2.0386 | 2.236 | 2.2594 | 2.288 | 2.3214 | 1.5242 | 1.8339 | 1.8521 | 1.8771 | 1.5242 | 1.9624 | 2.2132 | 2.2296 | 2.2514 | 2.3853
2021-09-03 09:00 | 1.8862 | 2.0865 | 2.1171 | 2.1547 | 2.1985 | 1.4289 | 1.7317 | 1.7556 | 1.7883 | 1.4289 | 1.6957 | 1.9269 | 1.9484 | 1.9769 | 2.1043
2021-09-03 10:00 | 2.0386 | 2.2612 | 2.2974 | 2.3418 | 2.3936 | 1.3908 | 1.6946 | 1.7229 | 1.7615 | 1.3908 | 1.5242 | 1.7441 | 1.7695 | 1.8032 | 1.9274
2021-09-03 11:00 | 1.6385 | 1.8357 | 1.8741 | 1.9212 | 1.9762 | 1.2765 | 1.5627 | 1.5928 | 1.6337 | 1.2765 | 1.2194 | 1.4084 | 1.4354 | 1.4712 | 1.5811
2021-09-03 12:00 | 1.8481 | 2.0598 | 2.0977 | 2.1442 | 2.1983 | 1.2956 | 1.5845 | 1.6141 | 1.6545 | 1.2956 | 1.2956 | 1.4923 | 1.5189 | 1.5543 | 1.6677
2021-09-03 13:00 | 1.9053 | 2.1162 | 2.1516 | 2.1949 | 2.2454 | 1.2575 | 1.5359 | 1.5635 | 1.6012 | 1.2575 | 1.2765 | 1.4676 | 1.4924 | 1.5254 | 1.635
2021-09-03 14:00 | 1.7719 | 1.9675 | 2.0001 | 2.0401 | 2.0867 | 1.3146 | 1.5994 | 1.6249 | 1.6597 | 1.3146 | 1.448 | 1.6544 | 1.6772 | 1.7076 | 1.8235
2021-09-03 15:00 | 1.829 | 2.0253 | 2.0561 | 2.0938 | 2.1378 | 1.3146 | 1.5968 | 1.6209 | 1.6537 | 1.3146 | 1.5433 | 1.7577 | 1.7793 | 1.8079 | 1.9271
2021-09-03 16:00 | 2.0767 | 2.2906 | 2.3209 | 2.3581 | 2.4014 | 1.4641 | 1.7728 | 1.7964 | 1.8288 | 1.4641 | 1.8862 | 2.1382 | 2.1594 | 2.1877 | 2.3252
2021-09-03 17:00 | 2.4197 | 2.6625 | 2.6947 | 2.7341 | 2.78 | 2.0111 | 2.4216 | 2.4467 | 2.4809 | 2.0111 | 2.896 | 3.2628 | 3.2853 | 3.3153 | 3.5103
2021-09-03 18:00 | 2.6102 | 2.8746 | 2.9105 | 2.9545 | 3.0058 | 2.1529 | 2.5945 | 2.6225 | 2.6608 | 2.1529 | 2.9531 | 3.3315 | 3.3567 | 3.3902 | 3.5925
2021-09-03 19:00 | 2.4899 | 2.7551 | 2.796 | 2.8461 | 2.9045 | 2.2101 | 2.6691 | 2.701 | 2.7446 | 2.2101 | 3.2961 | 3.7195 | 3.7482 | 3.7863 | 4.0131
2021-09-03 20:00 | 2.4959 | 2.7712 | 2.8171 | 2.8732 | 2.9386 | 2.1148 | 2.5636 | 2.5993 | 2.6482 | 2.1148 | 2.915 | 3.303 | 3.3351 | 3.3778 | 3.5891
2021-09-03 21:00 | 2.4006 | 2.6705 | 2.7172 | 2.7743 | 2.841 | 1.9624 | 2.3847 | 2.4211 | 2.4708 | 1.9624 | 3.0103 | 3.41 | 3.4427 | 3.4861 | 3.7036
2021-09-03 22:00 | 2.2673 | 2.5212 | 2.5649 | 2.6183 | 2.6806 | 1.726 | 2.101 | 2.1351 | 2.1816 | 1.726 | 3.0103 | 3.4058 | 3.4363 | 3.477 | 3.691
2021-09-03 23:00 | 2.1339 | 2.3695 | 2.4089 | 2.457 | 2.5131 | 1.6004 | 1.9466 | 1.9773 | 2.0192 | 1.6004 | 2.4006 | 2.7223 | 2.7498 | 2.7864 | 2.9622
2021-09-04 | 1.9564 | 2.1693 | 2.2039 | 2.2461 | 2.2953 | 1.3671 | 1.6641 | 1.691 | 1.7277 | 1.3671 | 2.172 | 2.4615 | 2.4857 | 2.5178 | 2.6756
2021-09-04 01:00 | 1.8862 | 2.0844 | 2.114 | 2.1503 | 2.1925 | 1.2503 | 1.5192 | 1.5423 | 1.5738 | 1.2503 | 1.7147 | 1.9466 | 1.9673 | 1.9949 | 2.1221
2021-09-04 02:00 | 1.7719 | 1.9495 | 1.973 | 2.0017 | 2.0351 | 1.1622 | 1.4063 | 1.4246 | 1.4496 | 1.1622 | 1.6385 | 1.8533 | 1.8698 | 1.8916 | 2.0078
2021-09-04 03:00 | 1.7528 | 1.9172 | 1.9346 | 1.9559 | 1.9808 | 1.1241 | 1.3527 | 1.3663 | 1.3848 | 1.1241 | 1.6766 | 1.8873 | 1.8995 | 1.9157 | 2.0273
2021-09-04 04:00 | 1.6766 | 1.8253 | 1.8375 | 1.8525 | 1.87 | 1.1241 | 1.3454 | 1.355 | 1.368 | 1.1241 | 1.6195 | 1.8166 | 1.8252 | 1.8366 | 1.9393
2021-09-04 05:00 | 1.7528 | 1.9032 | 1.9134 | 1.9259 | 1.9405 | 1.2039 | 1.4368 | 1.4447 | 1.4556 | 1.2039 | 2.172 | 2.4278 | 2.435 | 2.4445 | 2.5753
2021-09-04 06:00 | 1.7719 | 1.927 | 1.9389 | 1.9535 | 1.9706 | 1.2956 | 1.5475 | 1.5568 | 1.5695 | 1.2956 | 1.8481 | 2.0703 | 2.0786 | 2.0897 | 2.2046
2021-09-04 07:00 | 2.0386 | 2.2226 | 2.2392 | 2.2595 | 2.2832 | 1.5242 | 1.8242 | 1.8371 | 1.8548 | 1.5242 | 2.172 | 2.4366 | 2.4482 | 2.4637 | 2.6015
2021-09-04 08:00 | 2.2153 | 2.4258 | 2.4491 | 2.4778 | 2.5112 | 1.81 | 2.1715 | 2.1898 | 2.2147 | 1.81 | 2.8579 | 3.2083 | 3.2247 | 3.2465 | 3.4296
2021-09-04 09:00 | 2.4578 | 2.7005 | 2.7312 | 2.7688 | 2.8125 | 1.9243 | 2.3169 | 2.3408 | 2.3735 | 1.9243 | 3.3533 | 3.7689 | 3.7904 | 3.8189 | 4.0374
2021-09-04 10:00 | 2.5373 | 2.797 | 2.8332 | 2.8776 | 2.9294 | 2.1529 | 2.595 | 2.6232 | 2.6619 | 2.1529 | 3.5247 | 3.9672 | 3.9926 | 4.0263 | 4.2605
2021-09-04 11:00 | 2.6864 | 2.9615 | 2.9999 | 3.047 | 3.102 | 2.2292 | 2.6882 | 2.7182 | 2.7592 | 2.2292 | 3.7724 | 4.2455 | 4.2724 | 4.3083 | 4.5585
2021-09-04 12:00 | 2.7245 | 3.0013 | 3.0393 | 3.0857 | 3.1399 | 2.3816 | 2.8674 | 2.897 | 2.9374 | 2.3816 | 4.1154 | 4.6258 | 4.6524 | 4.6877 | 4.9562
2021-09-04 13:00 | 2.7626 | 3.0373 | 3.0727 | 3.116 | 3.1665 | 2.4387 | 2.9313 | 2.959 | 2.9966 | 2.4387 | 3.6771 | 4.1353 | 4.1601 | 4.1931 | 4.4346
2021-09-04 14:00 | 2.7055 | 2.9705 | 3.0031 | 3.0431 | 3.0896 | 2.4768 | 2.9724 | 2.9979 | 3.0326 | 2.4768 | 4.0772 | 4.5761 | 4.599 | 4.6294 | 4.8898
2021-09-04 15:00 | 2.6864 | 2.9464 | 2.9772 | 3.0149 | 3.0589 | 2.4006 | 2.8798 | 2.9038 | 2.9366 | 2.4006 | 4.2487 | 4.7641 | 4.7857 | 4.8144 | 5.0823
2021-09-04 16:00 | 2.8388 | 3.1093 | 3.1397 | 3.1768 | 3.2202 | 2.5911 | 3.1042 | 3.1279 | 3.1603 | 2.5911 | 4.6107 | 5.1658 | 5.1871 | 5.2153 | 5.5026
2021-09-04 17:00 | 3.0675 | 3.3585 | 3.3907 | 3.43 | 3.476 | 2.7436 | 3.2869 | 3.312 | 3.3462 | 2.7436 | 5.1061 | 5.7188 | 5.7413 | 5.7713 | 6.0878
2021-09-04 18:00 | 3.1818 | 3.4887 | 3.5246 | 3.5686 | 3.6199 | 2.896 | 3.4723 | 3.5003 | 3.5386 | 2.896 | 4.2487 | 4.7712 | 4.7964 | 4.8299 | 5.1034
2021-09-04 19:00 | 3.1784 | 3.4948 | 3.5357 | 3.5858 | 3.6442 | 2.7245 | 3.2768 | 3.3087 | 3.3523 | 2.7245 | 4.0963 | 4.6088 | 4.6374 | 4.6755 | 4.9463
2021-09-04 20:00 | 2.8181 | 3.1173 | 3.1632 | 3.2193 | 3.2848 | 2.5149 | 3.0362 | 3.072 | 3.1208 | 2.5149 | 4.1344 | 4.658 | 4.6901 | 4.7328 | 5.0111
2021-09-04 21:00 | 2.7055 | 2.998 | 3.0447 | 3.1018 | 3.1685 | 2.3324 | 2.8218 | 2.8582 | 2.9079 | 2.3324 | 3.5628 | 4.024 | 4.0567 | 4.1001 | 4.348
2021-09-04 22:00 | 2.553 | 2.8283 | 2.8719 | 2.9254 | 2.9877 | 2.1544 | 2.6072 | 2.6413 | 2.6877 | 2.1544 | 3.7724 | 4.2526 | 4.2832 | 4.3239 | 4.5798
2021-09-04 23:00 | 2.3625 | 2.6151 | 2.6545 | 2.7026 | 2.7588 | 1.8146 | 2.1996 | 2.2303 | 2.2722 | 1.8146 | 2.8388 | 3.2092 | 3.2368 | 3.2734 | 3.4732
2021-09-05 | 2.0935 | 2.3167 | 2.3512 | 2.3935 | 2.4427 | 1.5718 | 1.9059 | 1.9328 | 1.9696 | 1.5718 | 2.2482 | 2.5462 | 2.5704 | 2.6025 | 2.7645
2021-09-05 01:00 | 2.0386 | 2.2482 | 2.2778 | 2.314 | 2.3563 | 1.4313 | 1.733 | 1.7561 | 1.7877 | 1.4313 | 2.3816 | 2.6876 | 2.7084 | 2.7359 | 2.8998
2021-09-05 02:00 | 1.9243 | 2.1133 | 2.1367 | 2.1654 | 2.1989 | 1.3318 | 1.6067 | 1.625 | 1.65 | 1.3318 | 1.81 | 2.0439 | 2.0603 | 2.0821 | 2.2077
2021-09-05 03:00 | 1.9048 | 2.0805 | 2.0979 | 2.1192 | 2.1441 | 1.2956 | 1.5553 | 1.5689 | 1.5874 | 1.2956 | 1.8862 | 2.1202 | 2.1324 | 2.1486 | 2.2717
2021-09-05 04:00 | 1.9815 | 2.1528 | 2.165 | 2.18 | 2.1975 | 1.3337 | 1.593 | 1.6025 | 1.6156 | 1.3337 | 1.9053 | 2.1342 | 2.1428 | 2.1542 | 2.2726
2021-09-05 05:00 | 2.1529 | 2.333 | 2.3433 | 2.3558 | 2.3704 | 1.467 | 1.7477 | 1.7556 | 1.7665 | 1.467 | 2.191 | 2.449 | 2.4562 | 2.4657 | 2.5975
2021-09-05 06:00 | 2.1529 | 2.3364 | 2.3483 | 2.3629 | 2.3799 | 1.6385 | 1.9526 | 1.962 | 1.9747 | 1.6385 | 2.6102 | 2.9172 | 2.9255 | 2.9366 | 3.0934
2021-09-05 07:00 | 2.3054 | 2.5092 | 2.5258 | 2.5461 | 2.5697 | 1.81 | 2.1618 | 2.1748 | 2.1924 | 1.81 | 2.9531 | 3.3047 | 3.3163 | 3.3317 | 3.5125
2021-09-05 08:00 | 2.2863 | 2.5021 | 2.5255 | 2.5541 | 2.5875 | 2.0407 | 2.4441 | 2.4624 | 2.4873 | 2.0407 | 2.9531 | 3.3142 | 3.3305 | 3.3523 | 3.5407
2021-09-05 09:00 | 2.3816 | 2.6187 | 2.6493 | 2.6869 | 2.7307 | 2.0577 | 2.4745 | 2.4984 | 2.5311 | 2.0577 | 2.9722 | 3.3454 | 3.3669 | 3.3955 | 3.593
2021-09-05 10:00 | 2.191 | 2.4249 | 2.4612 | 2.5056 | 2.5573 | 1.7909 | 2.1673 | 2.1956 | 2.2342 | 1.7909 | 2.4197 | 2.7392 | 2.7646 | 2.7983 | 2.9717
2021-09-05 11:00 | 2.7436 | 3.0229 | 3.0613 | 3.1084 | 3.1634 | 2.5901 | 3.1146 | 3.1446 | 3.1856 | 2.5901 | 4.4392 | 4.9865 | 5.0135 | 5.0493 | 5.3362
2021-09-05 12:00 | 2.9341 | 3.2265 | 3.2644 | 3.3109 | 3.3651 | 2.6674 | 3.2051 | 3.2347 | 3.2751 | 2.6674 | 4.001 | 4.4988 | 4.5254 | 4.5607 | 4.8229
2021-09-05 13:00 | 2.9913 | 3.2829 | 3.3183 | 3.3616 | 3.4122 | 2.6864 | 3.2239 | 3.2516 | 3.2893 | 2.6864 | 5.2013 | 5.8291 | 5.8539 | 5.8869 | 6.2122
2021-09-05 14:00 | 3.0294 | 3.3185 | 3.3511 | 3.391 | 3.4376 | 2.7817 | 3.3326 | 3.358 | 3.3928 | 2.7817 | 4.8393 | 5.423 | 5.4459 | 5.4763 | 5.7786
2021-09-05 15:00 | 2.915 | 3.1921 | 3.2229 | 3.2606 | 3.3045 | 2.6182 | 3.1368 | 3.1609 | 3.1937 | 2.6182 | 4.8203 | 5.3993 | 5.4209 | 5.4496 | 5.7488
2021-09-05 16:00 | 3.0294 | 3.314 | 3.3444 | 3.3815 | 3.4249 | 2.553 | 3.0592 | 3.0829 | 3.1152 | 2.553 | 3.7724 | 4.2342 | 4.2555 | 4.2838 | 4.5249
2021-09-05 17:00 | 3.5057 | 3.8293 | 3.8614 | 3.9008 | 3.9468 | 3.1247 | 3.7371 | 3.7622 | 3.7965 | 3.1247 | 4.7074 | 5.2758 | 5.2983 | 5.3283 | 5.6229
2021-09-05 18:00 | 3.9439 | 4.3074 | 4.3434 | 4.3873 | 4.4386 | 3.4866 | 4.17 | 4.1981 | 4.2363 | 3.4866 | 5.3919 | 6.0416 | 6.0668 | 6.1002 | 6.4366
2021-09-05 19:00 | 3.8486 | 4.2148 | 4.2557 | 4.3058 | 4.3642 | 3.3533 | 4.0196 | 4.0515 | 4.0951 | 3.3533 | 5.5252 | 6.1967 | 6.2254 | 6.2635 | 6.6128
2021-09-05 20:00 | 3.6962 | 4.0607 | 4.1066 | 4.1627 | 4.2282 | 3.1818 | 3.824 | 3.8598 | 3.9086 | 3.1818 | 5.6205 | 6.3094 | 6.3415 | 6.3842 | 6.7443
2021-09-05 21:00 | 3.4932 | 3.8443 | 3.891 | 3.9481 | 4.0148 | 2.915 | 3.5101 | 3.5465 | 3.5962 | 2.915 | 4.3182 | 4.8634 | 4.8961 | 4.9396 | 5.229
2021-09-05 22:00 | 3.1078 | 3.4243 | 3.4679 | 3.5214 | 3.5837 | 2.6232 | 3.161 | 3.195 | 3.2415 | 2.6232 | 4.1344 | 4.6549 | 4.6855 | 4.7261 | 5.002
2021-09-05 23:00 | 2.8949 | 3.1871 | 3.2264 | 3.2746 | 3.3307 | 2.1124 | 2.5514 | 2.5821 | 2.624 | 2.1124 | 3.639 | 4.0985 | 4.126 | 4.1626 | 4.4065
2021-09-06 | 2.5149 | 2.7695 | 2.804 | 2.8462 | 2.8954 | 1.8862 | 2.2773 | 2.3043 | 2.341 | 1.8862 | 2.7817 | 3.139 | 3.1632 | 3.1953 | 3.3866
2021-09-06 01:00 | 2.3054 | 2.5347 | 2.5643 | 2.6006 | 2.6429 | 1.6923 | 2.0414 | 2.0645 | 2.096 | 1.6923 | 2.553 | 2.8782 | 2.8989 | 2.9265 | 3.0998
2021-09-06 02:00 | 2.2101 | 2.4203 | 2.4437 | 2.4724 | 2.5059 | 1.5814 | 1.9015 | 1.9198 | 1.9448 | 1.5814 | 2.4387 | 2.7426 | 2.759 | 2.7808 | 2.941
2021-09-06 03:00 | 2.2673 | 2.4699 | 2.4873 | 2.5086 | 2.5334 | 1.5433 | 1.8479 | 1.8615 | 1.88 | 1.5433 | 2.3625 | 2.6495 | 2.6617 | 2.6779 | 2.8272
2021-09-06 04:00 | 2.2863 | 2.4803 | 2.4925 | 2.5075 | 2.525 | 1.6338 | 1.9476 | 1.9571 | 1.9702 | 1.6338 | 2.4768 | 2.7694 | 2.778 | 2.7894 | 2.9392
2021-09-06 05:00 | 2.4573 | 2.66 | 2.6702 | 2.6828 | 2.6974 | 1.9125 | 2.2738 | 2.2818 | 2.2927 | 1.9125 | 2.6674 | 2.9783 | 2.9855 | 2.995 | 3.153
2021-09-06 06:00 | 2.7436 | 2.9709 | 2.9828 | 2.9974 | 3.0145 | 2.2291 | 2.6504 | 2.6597 | 2.6724 | 2.2291 | 3.4485 | 3.8487 | 3.8571 | 3.8682 | 4.0711
2021-09-06 07:00 | 2.9531 | 3.2051 | 3.2217 | 3.242 | 3.2657 | 2.2101 | 2.6345 | 2.6474 | 2.6651 | 2.2101 | 3.3342 | 3.7281 | 3.7398 | 3.7552 | 3.9569
2021-09-06 08:00 | 2.7817 | 3.0343 | 3.0577 | 3.0863 | 3.1197 | 2.1148 | 2.5316 | 2.5499 | 2.5748 | 2.1148 | 2.8769 | 3.2295 | 3.2459 | 3.2676 | 3.4518
2021-09-06 09:00 | 2.4006 | 2.6391 | 2.6698 | 2.7074 | 2.7511 | 1.7338 | 2.0918 | 2.1158 | 2.1484 | 1.7338 | 1.7528 | 1.9904 | 2.0119 | 2.0404 | 2.1709
2021-09-06 10:00 | 2.0958 | 2.3226 | 2.3588 | 2.4032 | 2.455 | 1.3527 | 1.6496 | 1.6779 | 1.7165 | 1.3527 | 1.1432 | 1.3206 | 1.346 | 1.3798 | 1.483
2021-09-06 11:00 | 1.7338 | 1.938 | 1.9765 | 2.0236 | 2.0785 | 1.2003 | 1.4727 | 1.5027 | 1.5437 | 1.2003 | 0.80021 | 0.94261 | 0.96957 | 1.0054 | 1.0922
2021-09-06 12:00 | 1.7909 | 1.9984 | 2.0363 | 2.0828 | 2.1369 | 1.2194 | 1.4945 | 1.5241 | 1.5645 | 1.2194 | 0.66684 | 0.79366 | 0.82024 | 0.85557 | 0.93447
2021-09-06 13:00 | 1.6004 | 1.7887 | 1.8241 | 1.8674 | 1.9179 | 1.086 | 1.3333 | 1.3609 | 1.3986 | 1.086 | 0.81926 | 0.9595 | 0.9843 | 1.0173 | 1.1017
2021-09-06 14:00 | 1.81 | 2.0084 | 2.0411 | 2.081 | 2.1276 | 1.2003 | 1.4644 | 1.4899 | 1.5246 | 1.2003 | 0.78115 | 0.91333 | 0.93619 | 0.96657 | 1.0459
2021-09-06 15:00 | 2.0572 | 2.2704 | 2.3013 | 2.339 | 2.3829 | 1.3312 | 1.6164 | 1.6404 | 1.6733 | 1.3312 | 1.2575 | 1.4401 | 1.4617 | 1.4903 | 1.5938
2021-09-06 16:00 | 2.553 | 2.8023 | 2.8326 | 2.8698 | 2.9131 | 1.9202 | 2.3116 | 2.3353 | 2.3676 | 1.9202 | 2.553 | 2.8792 | 2.9005 | 2.9287 | 3.1029
2021-09-06 17:00 | 3.1246 | 3.4199 | 3.4521 | 3.4915 | 3.5374 | 2.7904 | 3.3422 | 3.3673 | 3.4016 | 2.7904 | 3.742 | 4.2029 | 4.2255 | 4.2554 | 4.497
2021-09-06 18:00 | 3.6962 | 4.0413 | 4.0773 | 4.1212 | 4.1725 | 3.0707 | 3.6787 | 3.7068 | 3.745 | 3.0707 | 4.4202 | 4.9618 | 4.987 | 5.0204 | 5.3034
2021-09-06 19:00 | 3.6808 | 4.0345 | 4.0754 | 4.1255 | 4.1839 | 3.1056 | 3.727 | 3.7589 | 3.8024 | 3.1056 | 4.9537 | 5.5615 | 5.5902 | 5.6283 | 5.9462
2021-09-06 20:00 | 3.5819 | 3.9379 | 3.9838 | 4.0399 | 4.1054 | 3.0763 | 3.6994 | 3.7352 | 3.784 | 3.0763 | 4.6679 | 5.2508 | 5.2829 | 5.3256 | 5.6333
2021-09-06 21:00 | 3.4104 | 3.7553 | 3.802 | 3.8592 | 3.9258 | 2.7837 | 3.355 | 3.3914 | 3.4411 | 2.7837 | 4.2297 | 4.765 | 4.7977 | 4.8412 | 5.1257
2021-09-06 22:00 | 3.1571 | 3.4772 | 3.5209 | 3.5743 | 3.6366 | 2.5038 | 3.0199 | 3.054 | 3.1005 | 2.5038 | 3.8677 | 4.3585 | 4.3891 | 4.4297 | 4.6909
2021-09-06 23:00 | 2.7055 | 2.9836 | 3.0229 | 3.0711 | 3.1272 | 2.105 | 2.5427 | 2.5733 | 2.6152 | 2.105 | 3.1056 | 3.5056 | 3.5332 | 3.5698 | 3.7843
2021-09-07 | 2.4578 | 2.708 | 2.7426 | 2.7848 | 2.834 | 1.8481 | 2.2323 | 2.2592 | 2.296 | 1.8481 | 2.6293 | 2.9696 | 2.9938 | 3.0259 | 3.2089
2021-09-07 01:00 | 2.3625 | 2.5961 | 2.6257 | 2.662 | 2.7043 | 1.7147 | 2.0678 | 2.0909 | 2.1225 | 1.7147 | 2.4006 | 2.7088 | 2.7295 | 2.7571 | 2.922
2021-09-07 02:00 | 2.2291 | 2.4408 | 2.4642 | 2.4929 | 2.5264 | 1.6004 | 1.924 | 1.9423 | 1.9673 | 1.6004 | 2.4768 | 2.7849 | 2.8013 | 2.8232 | 2.9854
2021-09-07 03:00 | 2.2291 | 2.4289 | 2.4464 | 2.4677 | 2.4925 | 1.5814 | 1.8929 | 1.9065 | 1.925 | 1.5814 | 2.4578 | 2.7554 | 2.7676 | 2.7838 | 2.9383
2021-09-07 04:00 | 2.3435 | 2.5417 | 2.5539 | 2.5689 | 2.5864 | 1.6385 | 1.9531 | 1.9627 | 1.9757 | 1.6385 | 2.6864 | 3.0023 | 3.0109 | 3.0223 | 3.1836
2021-09-07 05:00 | 2.455 | 2.6576 | 2.6678 | 2.6803 | 2.6949 | 2.0147 | 2.3946 | 2.4026 | 2.4135 | 2.0147 | 3.2389 | 3.6135 | 3.6206 | 3.6302 | 3.8196
2021-09-07 06:00 | 2.7626 | 2.9914 | 3.0033 | 3.0179 | 3.0349 | 2.2291 | 2.6504 | 2.6597 | 2.6724 | 2.2291 | 3.62 | 4.0393 | 4.0476 | 4.0588 | 4.271
2021-09-07 07:00 | 2.9722 | 3.2256 | 3.2422 | 3.2625 | 3.2861 | 2.2863 | 2.7245 | 2.7374 | 2.7551 | 2.2863 | 3.4226 | 3.8264 | 3.838 | 3.8535 | 4.0601
2021-09-07 08:00 | 2.8579 | 3.1161 | 3.1395 | 3.1682 | 3.2016 | 2.1148 | 2.5316 | 2.5499 | 2.5748 | 2.1148 | 3.0103 | 3.3777 | 3.3941 | 3.4158 | 3.6074
2021-09-07 09:00 | 2.5721 | 2.8234 | 2.854 | 2.8916 | 2.9354 | 1.8481 | 2.2269 | 2.2508 | 2.2835 | 1.8481 | 1.9434 | 2.2021 | 2.2236 | 2.2522 | 2.3931
2021-09-07 10:00 | 2.1037 | 2.3311 | 2.3674 | 2.4117 | 2.4635 | 1.5575 | 1.8915 | 1.9198 | 1.9584 | 1.5575 | 1.5433 | 1.7652 | 1.7907 | 1.8244 | 1.9496
2021-09-07 11:00 | 2.2101 | 2.4497 | 2.4882 | 2.5353 | 2.5902 | 1.6385 | 1.9904 | 2.0204 | 2.0614 | 1.6385 | 1.6004 | 1.8318 | 1.8588 | 1.8946 | 2.0255
2021-09-07 12:00 | 1.7338 | 1.937 | 1.9749 | 2.0213 | 2.0755 | 1.1622 | 1.4269 | 1.4565 | 1.4969 | 1.1622 | 0.74305 | 0.87834 | 0.90493 | 0.94026 | 1.0233
2021-09-07 13:00 | 1.6195 | 1.8092 | 1.8446 | 1.8879 | 1.9384 | 1.1432 | 1.4008 | 1.4284 | 1.4661 | 1.1432 | 0.68589 | 0.8113 | 0.8361 | 0.86905 | 0.94617
2021-09-07 14:00 | 1.6957 | 1.8856 | 1.9183 | 1.9582 | 2.0048 | 1.1098 | 1.3575 | 1.383 | 1.4177 | 1.1098 | 0.83831 | 0.97684 | 0.99971 | 1.0301 | 1.1125
2021-09-07 15:00 | 2.1339 | 2.3528 | 2.3836 | 2.4213 | 2.4653 | 1.4121 | 1.712 | 1.736 | 1.7688 | 1.4121 | 1.4861 | 1.6942 | 1.7157 | 1.7444 | 1.8604
2021-09-07 16:00 | 2.5329 | 2.7806 | 2.811 | 2.8482 | 2.8915 | 1.937 | 2.3315 | 2.3552 | 2.3875 | 1.937 | 2.7436 | 3.0909 | 3.1122 | 3.1405 | 3.3251
2021-09-07 17:00 | 2.9982 | 3.2841 | 3.3163 | 3.3557 | 3.4016 | 2.7741 | 3.323 | 3.3481 | 3.3823 | 2.7741 | 4.2678 | 4.7872 | 4.8098 | 4.8397 | 5.1101
2021-09-07 18:00 | 3.3723 | 3.6934 | 3.7293 | 3.7733 | 3.8246 | 3.1246 | 3.7424 | 3.7704 | 3.8087 | 3.1246 | 5.087 | 5.7028 | 5.728 | 5.7615 | 6.0811
2021-09-07 19:00 | 3.5057 | 3.8464 | 3.8873 | 3.9374 | 3.9958 | 3.0675 | 3.6819 | 3.7139 | 3.7574 | 3.0675 | 4.8012 | 5.3922 | 5.4208 | 5.4589 | 5.7684
2021-09-07 20:00 | 3.4295 | 3.7742 | 3.82 | 3.8762 | 3.9416 | 2.896 | 3.4864 | 3.5222 | 3.571 | 2.896 | 4.363 | 4.912 | 4.9442 | 4.9869 | 5.2778
2021-09-07 21:00 | 3.2961 | 3.6325 | 3.6792 | 3.7364 | 3.803 | 2.7817 | 3.3525 | 3.389 | 3.4387 | 2.7817 | 4.2106 | 4.7438 | 4.7765 | 4.82 | 5.1034
2021-09-07 22:00 | 2.9843 | 3.2916 | 3.3353 | 3.3887 | 3.451 | 2.4073 | 2.906 | 2.94 | 2.9865 | 2.4073 | 3.3342 | 3.7657 | 3.7963 | 3.8369 | 4.0688
2021-09-07 23:00 | 2.7055 | 2.9836 | 3.0229 | 3.0711 | 3.1272 | 2.0135 | 2.4346 | 2.4652 | 2.5071 | 2.0135 | 2.8388 | 3.2092 | 3.2368 | 3.2734 | 3.4732
2021-09-08 | 2.4768 | 2.7285 | 2.763 | 2.8053 | 2.8545 | 1.7338 | 2.0973 | 2.1242 | 2.1609 | 1.7338 | 2.534 | 2.8638 | 2.8879 | 2.9201 | 3.0978
2021-09-08 01:00 | 2.191 | 2.4119 | 2.4415 | 2.4778 | 2.52 | 1.5623 | 1.8878 | 1.9109 | 1.9424 | 1.5623 | 2.191 | 2.4759 | 2.4966 | 2.5242 | 2.6776
2021-09-08 02:00 | 2.2291 | 2.4408 | 2.4642 | 2.4929 | 2.5264 | 1.492 | 1.796 | 1.8143 | 1.8392 | 1.492 | 2.3054 | 2.5944 | 2.6108 | 2.6326 | 2.7855
2021-09-08 03:00 | 2.172 | 2.3675 | 2.3849 | 2.4063 | 2.4311 | 1.5052 | 1.8029 | 1.8165 | 1.835 | 1.5052 | 2.2101 | 2.4801 | 2.4923 | 2.5085 | 2.6494
2021-09-08 04:00 | 2.2482 | 2.4393 | 2.4516 | 2.4666 | 2.4841 | 1.5814 | 1.8856 | 1.8951 | 1.9082 | 1.5814 | 2.2482 | 2.5153 | 2.5239 | 2.5353 | 2.6726
2021-09-08 05:00 | 2.4387 | 2.6401 | 2.6503 | 2.6628 | 2.6774 | 1.8647 | 2.2175 | 2.2254 | 2.2363 | 1.8647 | 2.8769 | 3.2112 | 3.2184 | 3.2279 | 3.3974
2021-09-08 06:00 | 2.7436 | 2.9709 | 2.9828 | 2.9974 | 3.0145 | 2.2101 | 2.6279 | 2.6372 | 2.6499 | 2.2101 | 3.3914 | 3.7852 | 3.7936 | 3.8047 | 4.0044
2021-09-08 07:00 | 3.2896 | 3.5666 | 3.5832 | 3.6035 | 3.6271 | 2.6293 | 3.1297 | 3.1426 | 3.1602 | 2.6293 | 3.8296 | 4.2786 | 4.2902 | 4.3057 | 4.5346
2021-09-08 08:00 | 3.5628 | 3.8735 | 3.8969 | 3.9255 | 3.9589 | 2.8769 | 3.432 | 3.4502 | 3.4751 | 2.8769 | 5.2395 | 5.8548 | 5.8712 | 5.893 | 6.2071
2021-09-08 09:00 | 3.62 | 3.9492 | 3.9798 | 4.0174 | 4.0612 | 2.8769 | 3.4423 | 3.4662 | 3.4989 | 2.8769 | 4.1344 | 4.6369 | 4.6584 | 4.687 | 4.9484
2021-09-08 10:00 | 3.2008 | 3.5098 | 3.546 | 3.5904 | 3.6422 | 2.6102 | 3.1351 | 3.1634 | 3.202 | 2.6102 | 4.1535 | 4.6658 | 4.6913 | 4.725 | 4.9937
2021-09-08 11:00 | 2.9531 | 3.248 | 3.2865 | 3.3336 | 3.3885 | 2.3012 | 2.7732 | 2.8032 | 2.8442 | 2.3012 | 3.1818 | 3.5891 | 3.6161 | 3.6519 | 3.8697
2021-09-08 12:00 | 2.0577 | 2.2849 | 2.3229 | 2.3693 | 2.4235 | 1.6385 | 1.9896 | 2.0192 | 2.0596 | 1.6385 | 1.105 | 1.2806 | 1.3072 | 1.3425 | 1.4455
2021-09-08 13:00 | 1.6766 | 1.8706 | 1.906 | 1.9493 | 1.9998 | 1.1622 | 1.4233 | 1.4509 | 1.4886 | 1.1622 | 0.74305 | 0.87481 | 0.89961 | 0.93257 | 1.0128
2021-09-08 14:00 | 1.6766 | 1.8652 | 1.8978 | 1.9377 | 1.9843 | 1.2003 | 1.4644 | 1.4899 | 1.5246 | 1.2003 | 0.78115 | 0.91333 | 0.93619 | 0.96657 | 1.0459
2021-09-08 15:00 | 1.9815 | 2.1891 | 2.2199 | 2.2576 | 2.3015 | 1.4289 | 1.7319 | 1.7559 | 1.7887 | 1.4289 | 1.3063 | 1.4943 | 1.5159 | 1.5446 | 1.6507
2021-09-08 16:00 | 2.398 | 2.6357 | 2.6661 | 2.7033 | 2.7466 | 1.9525 | 2.3498 | 2.3735 | 2.4058 | 1.9525 | 2.5149 | 2.8368 | 2.8581 | 2.8864 | 3.0584
2021-09-08 17:00 | 3.0473 | 3.3368 | 3.369 | 3.4084 | 3.4543 | 2.6232 | 3.1447 | 3.1698 | 3.2041 | 2.6232 | 3.8867 | 4.3638 | 4.3863 | 4.4163 | 4.6657
2021-09-08 18:00 | 3.4295 | 3.7548 | 3.7907 | 3.8347 | 3.886 | 3.0103 | 3.6073 | 3.6354 | 3.6736 | 3.0103 | 4.5536 | 5.11 | 5.1352 | 5.1686 | 5.459
2021-09-08 19:00 | 3.4676 | 3.8054 | 3.8464 | 3.8964 | 3.9548 | 2.9531 | 3.5469 | 3.5788 | 3.6224 | 2.9531 | 4.4011 | 4.9475 | 4.9762 | 5.0143 | 5.3018
2021-09-08 20:00 | 3.2389 | 3.5695 | 3.6153 | 3.6715 | 3.7369 | 2.896 | 3.4864 | 3.5222 | 3.571 | 2.896 | 4.1535 | 4.6792 | 4.7113 | 4.754 | 5.0334
2021-09-08 21:00 | 3.0484 | 3.3664 | 3.4131 | 3.4703 | 3.5369 | 2.6734 | 3.2246 | 3.261 | 3.3108 | 2.6734 | 4.1154 | 4.638 | 4.6707 | 4.7141 | 4.9924
2021-09-08 22:00 | 2.9722 | 3.2786 | 3.3222 | 3.3757 | 3.438 | 2.3996 | 2.8969 | 2.9309 | 2.9774 | 2.3996 | 3.4485 | 3.8927 | 3.9233 | 3.9639 | 4.2021
2021-09-08 23:00 | 2.6102 | 2.8812 | 2.9206 | 2.9687 | 3.0249 | 1.9815 | 2.3967 | 2.4274 | 2.4693 | 1.9815 | 3.0103 | 3.3998 | 3.4273 | 3.4639 | 3.6732
2021-09-09 | 2.3816 | 2.6262 | 2.6607 | 2.7029 | 2.7522 | 1.7527 | 2.1196 | 2.1465 | 2.1832 | 1.7527 | 2.3244 | 2.6309 | 2.6551 | 2.6872 | 2.8534
2021-09-09 01:00 | 2.2673 | 2.4938 | 2.5234 | 2.5597 | 2.6019 | 1.5433 | 1.8652 | 1.8884 | 1.9199 | 1.5433 | 2.1148 | 2.3912 | 2.4119 | 2.4395 | 2.5887
2021-09-09 02:00 | 2.2291 | 2.4408 | 2.4642 | 2.4929 | 2.5264 | 1.467 | 1.7664 | 1.7847 | 1.8097 | 1.467 | 2.0958 | 2.3615 | 2.3779 | 2.3997 | 2.541
2021-09-09 03:00 | 2.0959 | 2.2857 | 2.3032 | 2.3245 | 2.3493 | 1.467 | 1.7579 | 1.7714 | 1.79 | 1.467 | 2.3244 | 2.6072 | 2.6194 | 2.6356 | 2.7827
2021-09-09 04:00 | 2.1763 | 2.3621 | 2.3743 | 2.3893 | 2.4068 | 1.5484 | 1.8466 | 1.8562 | 1.8693 | 1.5484 | 2.3244 | 2.6 | 2.6086 | 2.62 | 2.7615
2021-09-09 05:00 | 2.5911 | 2.8038 | 2.814 | 2.8266 | 2.8412 | 1.8606 | 2.2126 | 2.2206 | 2.2315 | 1.8606 | 3.1437 | 3.5076 | 3.5148 | 3.5243 | 3.7085
2021-09-09 06:00 | 2.7245 | 2.9504 | 2.9624 | 2.977 | 2.994 | 2.1529 | 2.5604 | 2.5697 | 2.5824 | 2.1529 | 3.3914 | 3.7852 | 3.7936 | 3.8047 | 4.0044
2021-09-09 07:00 | 2.896 | 3.1437 | 3.1603 | 3.1806 | 3.2043 | 2.2101 | 2.6345 | 2.6474 | 2.6651 | 2.2101 | 3.3723 | 3.7705 | 3.7821 | 3.7975 | 4.0014
2021-09-09 08:00 | 2.7245 | 2.9729 | 2.9963 | 3.0249 | 3.0583 | 2.0506 | 2.4557 | 2.474 | 2.4989 | 2.0506 | 2.8579 | 3.2083 | 3.2247 | 3.2465 | 3.4296
2021-09-09 09:00 | 2.4959 | 2.7415 | 2.7722 | 2.8097 | 2.8535 | 1.6385 | 1.9793 | 2.0032 | 2.0359 | 1.6385 | 1.7528 | 1.9904 | 2.0119 | 2.0404 | 2.1709
2021-09-09 10:00 | 2.2107 | 2.446 | 2.4823 | 2.5267 | 2.5784 | 1.4099 | 1.7171 | 1.7454 | 1.7841 | 1.4099 | 1.2194 | 1.4053 | 1.4307 | 1.4645 | 1.5719
2021-09-09 11:00 | 1.9243 | 2.1427 | 2.1812 | 2.2283 | 2.2832 | 1.4289 | 1.7428 | 1.7728 | 1.8138 | 1.4289 | 0.99073 | 1.1543 | 1.1813 | 1.2171 | 1.3144
2021-09-09 12:00 | 2.0577 | 2.2849 | 2.3229 | 2.3693 | 2.4235 | 1.5623 | 1.8996 | 1.9292 | 1.9696 | 1.5623 | 1.3527 | 1.5559 | 1.5824 | 1.6178 | 1.7344
2021-09-09 13:00 | 1.81 | 2.0138 | 2.0492 | 2.0926 | 2.1431 | 1.4099 | 1.7159 | 1.7435 | 1.7812 | 1.4099 | 0.99073 | 1.1501 | 1.1749 | 1.2078 | 1.3017
2021-09-09 14:00 | 1.6004 | 1.7833 | 1.8159 | 1.8559 | 1.9024 | 1.0288 | 1.2618 | 1.2873 | 1.322 | 1.0288 | 0.87642 | 1.0192 | 1.0421 | 1.0724 | 1.1569
2021-09-09 15:00 | 1.8672 | 2.0663 | 2.0971 | 2.1348 | 2.1787 | 1.2956 | 1.5743 | 1.5984 | 1.6312 | 1.2956 | 1.086 | 1.2495 | 1.2711 | 1.2998 | 1.3938
2021-09-09 16:00 | 2.191 | 2.4134 | 2.4437 | 2.4809 | 2.5242 | 1.6424 | 1.9834 | 2.0071 | 2.0394 | 1.6424 | 1.7528 | 1.99 | 2.0112 | 2.0395 | 2.1697
2021-09-09 17:00 | 2.7436 | 3.0105 | 3.0427 | 3.0821 | 3.128 | 2.3869 | 2.8655 | 2.8906 | 2.9249 | 2.3869 | 3.4866 | 3.9191 | 3.9417 | 3.9716 | 4.1991
2021-09-09 18:00 | 3.0484 | 3.3454 | 3.3813 | 3.4253 | 3.4766 | 2.7436 | 3.2922 | 3.3203 | 3.3585 | 2.7436 | 3.8867 | 4.369 | 4.3942 | 4.4276 | 4.6813
2021-09-09 19:00 | 3.258 | 3.5803 | 3.6212 | 3.6713 | 3.7297 | 2.7245 | 3.2768 | 3.3087 | 3.3523 | 2.7245 | 4.0582 | 4.5664 | 4.5951 | 4.6332 | 4.9018
2021-09-09 20:00 | 3.1394 | 3.4626 | 3.5084 | 3.5646 | 3.63 | 2.534 | 3.0587 | 3.0945 | 3.1434 | 2.534 | 3.7343 | 4.2134 | 4.2455 | 4.2882 | 4.5445
2021-09-09 21:00 | 2.8579 | 3.1617 | 3.2084 | 3.2656 | 3.3322 | 2.4959 | 3.0149 | 3.0513 | 3.1011 | 2.4959 | 3.3914 | 3.8334 | 3.8661 | 3.9096 | 4.148
2021-09-09 22:00 | 2.6293 | 2.9102 | 2.9538 | 3.0072 | 3.0695 | 2.1529 | 2.6055 | 2.6395 | 2.686 | 2.1529 | 3.1437 | 3.554 | 3.5845 | 3.6252 | 3.8466
2021-09-09 23:00 | 2.2863 | 2.5333 | 2.5726 | 2.6208 | 2.6769 | 1.8481 | 2.2392 | 2.2699 | 2.3118 | 1.8481 | 2.4387 | 2.7646 | 2.7922 | 2.8288 | 3.0066
2021-09-10 | 2.1339 | 2.3601 | 2.3946 | 2.4368 | 2.4861 | 1.5528 | 1.8834 | 1.9103 | 1.9471 | 1.5528 | 2.1339 | 2.4192 | 2.4433 | 2.4755 | 2.6312
2021-09-10 01:00 | 2.0005 | 2.2072 | 2.2368 | 2.2731 | 2.3154 | 1.4289 | 1.7302 | 1.7533 | 1.7848 | 1.4289 | 1.829 | 2.0736 | 2.0944 | 2.1219 | 2.2555
2021-09-10 02:00 | 1.9401 | 2.1303 | 2.1537 | 2.1824 | 2.2159 | 1.3302 | 1.6048 | 1.623 | 1.648 | 1.3302 | 1.9053 | 2.1497 | 2.1662 | 2.188 | 2.3188
2021-09-10 03:00 | 1.9815 | 2.1629 | 2.1803 | 2.2016 | 2.2264 | 1.3146 | 1.5778 | 1.5914 | 1.6099 | 1.3146 | 1.81 | 2.0355 | 2.0477 | 2.0639 | 2.1828
2021-09-10 04:00 | 2.0011 | 2.1739 | 2.1861 | 2.2012 | 2.2186 | 1.3384 | 1.5986 | 1.6082 | 1.6212 | 1.3384 | 1.8862 | 2.1131 | 2.1216 | 2.1331 | 2.2504
2021-09-10 05:00 | 2.2101 | 2.3944 | 2.4047 | 2.4172 | 2.4318 | 1.6957 | 2.0177 | 2.0257 | 2.0366 | 1.6957 | 2.3244 | 2.5972 | 2.6044 | 2.6139 | 2.7531
2021-09-10 06:00 | 2.3816 | 2.582 | 2.5939 | 2.6085 | 2.6256 | 1.7909 | 2.1327 | 2.142 | 2.1547 | 1.7909 | 2.8198 | 3.15 | 3.1584 | 3.1695 | 3.3378
2021-09-10 07:00 | 2.553 | 2.7753 | 2.7919 | 2.8122 | 2.8358 | 1.7909 | 2.1393 | 2.1522 | 2.1699 | 1.7909 | 2.6102 | 2.9236 | 2.9352 | 2.9506 | 3.1126
2021-09-10 08:00 | 2.3244 | 2.543 | 2.5664 | 2.5951 | 2.6284 | 1.7158 | 2.0602 | 2.0785 | 2.1034 | 1.7158 | 2.2673 | 2.5519 | 2.5683 | 2.5901 | 2.7408
2021-09-10 09:00 | 2.1339 | 2.3526 | 2.3832 | 2.4208 | 2.4646 | 1.3146 | 1.5967 | 1.6206 | 1.6533 | 1.3146 | 1.2575 | 1.4399 | 1.4614 | 1.49 | 1.5932
2021-09-10 10:00 | 1.829 | 2.036 | 2.0723 | 2.1167 | 2.1684 | 1.2003 | 1.4696 | 1.4978 | 1.5365 | 1.2003 | 0.91452 | 1.0666 | 1.092 | 1.1257 | 1.2164
2021-09-10 11:00 | 2.1339 | 2.3679 | 2.4063 | 2.4534 | 2.5084 | 1.5623 | 1.9004 | 1.9304 | 1.9714 | 1.5623 | 1.6004 | 1.8318 | 1.8588 | 1.8946 | 2.0255
2021-09-10 12:00 | 2.2863 | 2.5306 | 2.5685 | 2.6149 | 2.6691 | 1.6766 | 2.0346 | 2.0642 | 2.1047 | 1.6766 | 1.829 | 2.0852 | 2.1117 | 2.1471 | 2.2899
2021-09-10 13:00 | 1.9434 | 2.1571 | 2.1925 | 2.2359 | 2.2864 | 1.3146 | 1.6034 | 1.631 | 1.6687 | 1.3146 | 1.3146 | 1.51 | 1.5348 | 1.5677 | 1.6794
2021-09-10 14:00 | 1.9243 | 2.1313 | 2.1639 | 2.2038 | 2.2504 | 1.3146 | 1.5994 | 1.6249 | 1.6597 | 1.3146 | 1.105 | 1.2733 | 1.2961 | 1.3265 | 1.4236
2021-09-10 15:00 | 2.0196 | 2.23 | 2.2608 | 2.2985 | 2.3425 | 1.3146 | 1.5968 | 1.6209 | 1.6537 | 1.3146 | 1.3337 | 1.5248 | 1.5464 | 1.575 | 1.6826
2021-09-10 16:00 | 2.2101 | 2.4338 | 2.4642 | 2.5014 | 2.5447 | 1.6195 | 1.9563 | 1.98 | 2.0124 | 1.6195 | 1.9053 | 2.1593 | 2.1806 | 2.2089 | 2.3474
2021-09-10 17:00 | 2.4959 | 2.7444 | 2.7766 | 2.816 | 2.8619 | 2.1067 | 2.5345 | 2.5596 | 2.5939 | 2.1067 | 2.9341 | 3.3052 | 3.3277 | 3.3576 | 3.5548
2021-09-10 18:00 | 2.8007 | 3.0793 | 3.1152 | 3.1592 | 3.2105 | 2.4147 | 2.9037 | 2.9318 | 2.97 | 2.4147 | 3.277 | 3.6915 | 3.7166 | 3.7501 | 3.9702
2021-09-10 19:00 | 2.8198 | 3.1095 | 3.1504 | 3.2005 | 3.2589 | 2.4197 | 2.9167 | 2.9486 | 2.9922 | 2.4197 | 3.258 | 3.6772 | 3.7059 | 3.744 | 3.9686
2021-09-10 20:00 | 2.7436 | 3.0373 | 3.0832 | 3.1393 | 3.2047 | 2.3625 | 2.8562 | 2.8919 | 2.9408 | 2.3625 | 3.2389 | 3.6629 | 3.695 | 3.7377 | 3.9668
2021-09-10 21:00 | 2.6102 | 2.8956 | 2.9423 | 2.9995 | 3.0661 | 2.2101 | 2.6773 | 2.7137 | 2.7634 | 2.2101 | 3.1246 | 3.537 | 3.5697 | 3.6132 | 3.8369
2021-09-10 22:00 | 2.4578 | 2.7259 | 2.7696 | 2.823 | 2.8853 | 2.0285 | 2.4584 | 2.4924 | 2.5389 | 2.0285 | 2.7245 | 3.0882 | 3.1187 | 3.1594 | 3.3577
2021-09-10 23:00 | 2.2661 | 2.5116 | 2.5509 | 2.5991 | 2.6552 | 1.7528 | 2.1267 | 2.1573 | 2.1992 | 1.7528 | 2.6483 | 2.9975 | 3.0251 | 3.0617 | 3.251
2021-09-11 | 2.1148 | 2.3396 | 2.3741 | 2.4163 | 2.4656 | 1.4829 | 1.8009 | 1.8278 | 1.8646 | 1.4829 | 2.191 | 2.4827 | 2.5068 | 2.539 | 2.6978
2021-09-11 01:00 | 1.9815 | 2.1867 | 2.2164 | 2.2526 | 2.2949 | 1.3337 | 1.6177 | 1.6408 | 1.6723 | 1.3337 | 1.8481 | 2.0948 | 2.1155 | 2.1431 | 2.2777
2021-09-11 02:00 | 1.9815 | 2.1747 | 2.1981 | 2.2268 | 2.2603 | 1.2765 | 1.5414 | 1.5597 | 1.5846 | 1.2765 | 1.7147 | 1.938 | 1.9544 | 1.9763 | 2.0966
2021-09-11 03:00 | 1.9624 | 2.1424 | 2.1598 | 2.1811 | 2.2059 | 1.2384 | 1.4878 | 1.5013 | 1.5199 | 1.2384 | 1.6385 | 1.845 | 1.8572 | 1.8734 | 1.9828
2021-09-11 04:00 | 1.9815 | 2.1528 | 2.165 | 2.18 | 2.1975 | 1.2194 | 1.4579 | 1.4675 | 1.4806 | 1.2194 | 1.81 | 2.0284 | 2.037 | 2.0484 | 2.1615
2021-09-11 05:00 | 2.0577 | 2.2307 | 2.2409 | 2.2534 | 2.268 | 1.448 | 1.7251 | 1.7331 | 1.744 | 1.448 | 1.8862 | 2.1102 | 2.1174 | 2.1269 | 2.242
2021-09-11 06:00 | 2.0386 | 2.2135 | 2.2255 | 2.2401 | 2.2571 | 1.5433 | 1.8401 | 1.8494 | 1.8621 | 1.5433 | 2.4197 | 2.7054 | 2.7138 | 2.7249 | 2.8712
2021-09-11 07:00 | 1.9815 | 2.1612 | 2.1778 | 2.1981 | 2.2218 | 1.448 | 1.7342 | 1.7471 | 1.7648 | 1.448 | 1.9434 | 2.1826 | 2.1942 | 2.2096 | 2.3349
2021-09-11 08:00 | 1.6957 | 1.8675 | 1.8909 | 1.9196 | 1.953 | 1.2765 | 1.5413 | 1.5595 | 1.5845 | 1.2765 | 1.4099 | 1.5992 | 1.6156 | 1.6374 | 1.7409
2021-09-11 09:00 | 1.4861 | 1.6566 | 1.6873 | 1.7248 | 1.7686 | 1.086 | 1.3266 | 1.3505 | 1.3832 | 1.086 | 0.91452 | 1.0588 | 1.0803 | 1.1089 | 1.1933
2021-09-11 10:00 | 1.3337 | 1.5038 | 1.5401 | 1.5845 | 1.6362 | 0.93358 | 1.1544 | 1.1827 | 1.2214 | 0.93358 | 0.724 | 0.85484 | 0.88025 | 0.91401 | 0.99418
2021-09-11 11:00 | 1.2575 | 1.4263 | 1.4648 | 1.5119 | 1.5668 | 0.93358 | 1.1576 | 1.1876 | 1.2286 | 0.93358 | 0.78115 | 0.92143 | 0.9484 | 0.98422 | 1.07
2021-09-11 12:00 | 1.2384 | 1.4048 | 1.4427 | 1.4892 | 1.5433 | 0.89547 | 1.1118 | 1.1414 | 1.1818 | 0.89547 | 0.91452 | 1.0689 | 1.0955 | 1.1308 | 1.2233
2021-09-11 13:00 | 1.2765 | 1.4407 | 1.4761 | 1.5194 | 1.57 | 0.86232 | 1.069 | 1.0967 | 1.1344 | 0.86232 | 0.81926 | 0.9595 | 0.9843 | 1.0173 | 1.1017
2021-09-11 14:00 | 1.448 | 1.6195 | 1.6522 | 1.6921 | 1.7387 | 0.95263 | 1.1718 | 1.1973 | 1.232 | 0.95263 | 0.91452 | 1.0615 | 1.0844 | 1.1148 | 1.2014
2021-09-11 15:00 | 1.7719 | 1.9639 | 1.9947 | 2.0324 | 2.0764 | 1.2066 | 1.4692 | 1.4933 | 1.5261 | 1.2066 | 1.0288 | 1.186 | 1.2076 | 1.2363 | 1.3271
2021-09-11 16:00 | 1.9815 | 2.1882 | 2.2186 | 2.2557 | 2.2991 | 1.5242 | 1.8438 | 1.8675 | 1.8998 | 1.5242 | 2.0386 | 2.3075 | 2.3288 | 2.3571 | 2.503
2021-09-11 17:00 | 2.4578 | 2.7035 | 2.7357 | 2.775 | 2.821 | 2.0196 | 2.4316 | 2.4567 | 2.4909 | 2.0196 | 3.0484 | 3.4322 | 3.4547 | 3.4847 | 3.6881
2021-09-11 18:00 | 2.6102 | 2.8746 | 2.9105 | 2.9545 | 3.0058 | 2.2785 | 2.7428 | 2.7708 | 2.8091 | 2.2785 | 3.2008 | 3.6068 | 3.632 | 3.6654 | 3.8814
2021-09-11 19:00 | 2.534 | 2.8025 | 2.8434 | 2.8935 | 2.9519 | 2.2863 | 2.7591 | 2.791 | 2.8346 | 2.2863 | 2.9341 | 3.3173 | 3.3459 | 3.384 | 3.5909
2021-09-11 20:00 | 2.553 | 2.8326 | 2.8785 | 2.9346 | 3 | 2.0958 | 2.5411 | 2.5768 | 2.6257 | 2.0958 | 3.0484 | 3.4512 | 3.4833 | 3.526 | 3.7446
2021-09-11 21:00 | 2.4006 | 2.6705 | 2.7172 | 2.7743 | 2.841 | 1.984 | 2.4102 | 2.4466 | 2.4963 | 1.984 | 3.277 | 3.7064 | 3.7391 | 3.7826 | 4.0147
2021-09-11 22:00 | 2.3625 | 2.6236 | 2.6672 | 2.7207 | 2.783 | 1.8458 | 2.2426 | 2.2767 | 2.3232 | 1.8458 | 2.4578 | 2.7918 | 2.8223 | 2.863 | 3.0467
2021-09-11 23:00 | 2.0958 | 2.3286 | 2.3679 | 2.4161 | 2.4722 | 1.6048 | 1.9518 | 1.9825 | 2.0244 | 1.6048 | 2.2291 | 2.5317 | 2.5593 | 2.5959 | 2.7622
2021-09-12 | 1.9815 | 2.1963 | 2.2308 | 2.2731 | 2.3223 | 1.4099 | 1.7146 | 1.7416 | 1.7783 | 1.4099 | 2.0005 | 2.2709 | 2.2951 | 2.3272 | 2.4756
2021-09-12 01:00 | 1.9815 | 2.1867 | 2.2164 | 2.2526 | 2.2949 | 1.3146 | 1.5952 | 1.6183 | 1.6498 | 1.3146 | 1.7719 | 2.0101 | 2.0308 | 2.0584 | 2.1888
2021-09-12 02:00 | 1.9624 | 2.1542 | 2.1776 | 2.2063 | 2.2398 | 1.1908 | 1.4401 | 1.4583 | 1.4833 | 1.1908 | 1.6195 | 1.8322 | 1.8486 | 1.8704 | 1.9855
2021-09-12 03:00 | 1.8481 | 2.0196 | 2.037 | 2.0583 | 2.0831 | 1.1216 | 1.3497 | 1.3633 | 1.3818 | 1.1216 | 1.467 | 1.6544 | 1.6666 | 1.6828 | 1.7828
2021-09-12 04:00 | 1.8481 | 2.0095 | 2.0218 | 2.0368 | 2.0543 | 1.1622 | 1.3904 | 1.4 | 1.413 | 1.1622 | 1.5814 | 1.7743 | 1.7829 | 1.7943 | 1.8949
2021-09-12 05:00 | 1.9243 | 2.0874 | 2.0976 | 2.1102 | 2.1248 | 1.2575 | 1.5001 | 1.508 | 1.5189 | 1.2575 | 1.6957 | 1.8985 | 1.9057 | 1.9152 | 2.0198
2021-09-12 06:00 | 1.829 | 1.9884 | 2.0003 | 2.0149 | 2.032 | 1.3527 | 1.615 | 1.6243 | 1.637 | 1.3527 | 1.9243 | 2.155 | 2.1633 | 2.1744 | 2.2935
2021-09-12 07:00 | 1.6957 | 1.8542 | 1.8708 | 1.8911 | 1.9147 | 1.277 | 1.5321 | 1.5451 | 1.5627 | 1.277 | 1.4861 | 1.6744 | 1.686 | 1.7015 | 1.8016
2021-09-12 08:00 | 1.7909 | 1.9699 | 1.9933 | 2.0219 | 2.0553 | 1.3527 | 1.6313 | 1.6496 | 1.6745 | 1.3527 | 1.5052 | 1.7051 | 1.7215 | 1.7432 | 1.852
2021-09-12 09:00 | 1.3146 | 1.4724 | 1.5031 | 1.5406 | 1.5844 | 0.99547 | 1.2196 | 1.2435 | 1.2762 | 0.99547 | 0.80021 | 0.93178 | 0.95327 | 0.98183 | 1.06
2021-09-12 10:00 | 1.1813 | 1.3401 | 1.3763 | 1.4207 | 1.4725 | 1.0288 | 1.267 | 1.2953 | 1.3339 | 1.0288 | 0.89547 | 1.0454 | 1.0708 | 1.1046 | 1.1942
2021-09-12 11:00 | 1.3146 | 1.4877 | 1.5262 | 1.5733 | 1.6282 | 1.1813 | 1.4502 | 1.4802 | 1.5212 | 1.1813 | 0.89547 | 1.0485 | 1.0754 | 1.1113 | 1.2033
2021-09-12 12:00 | 1.5814 | 1.7732 | 1.8111 | 1.8576 | 1.9118 | 1.2003 | 1.472 | 1.5015 | 1.542 | 1.2003 | 1.105 | 1.2806 | 1.3072 | 1.3425 | 1.4455
2021-09-12 13:00 | 1.6766 | 1.8706 | 1.906 | 1.9493 | 1.9998 | 1.3337 | 1.6259 | 1.6535 | 1.6912 | 1.3337 | 1.3146 | 1.51 | 1.5348 | 1.5677 | 1.6794
2021-09-12 14:00 | 1.9624 | 2.1722 | 2.2048 | 2.2448 | 2.2914 | 1.5359 | 1.8608 | 1.8863 | 1.921 | 1.5359 | 1.8672 | 2.1201 | 2.143 | 2.1734 | 2.3124
2021-09-12 15:00 | 2.3125 | 2.5447 | 2.5755 | 2.6132 | 2.6571 | 1.9243 | 2.3171 | 2.3411 | 2.3739 | 1.9243 | 2.8007 | 3.155 | 3.1766 | 3.2053 | 3.3936
2021-09-12 16:00 | 2.534 | 2.7818 | 2.8122 | 2.8493 | 2.8927 | 2.1625 | 2.5978 | 2.6215 | 2.6539 | 2.1625 | 3.3342 | 3.7473 | 3.7685 | 3.7968 | 4.0139
2021-09-12 17:00 | 2.8769 | 3.1538 | 3.186 | 3.2254 | 3.2713 | 2.5721 | 3.0843 | 3.1094 | 3.1437 | 2.5721 | 4.2487 | 4.766 | 4.7886 | 4.8185 | 5.0879
2021-09-12 18:00 | 3.1818 | 3.4887 | 3.5246 | 3.5686 | 3.6199 | 2.8198 | 3.3823 | 3.4103 | 3.4486 | 2.8198 | 3.9439 | 4.4325 | 4.4577 | 4.4911 | 4.7479
2021-09-12 19:00 | 3.1056 | 3.4165 | 3.4575 | 3.5075 | 3.5659 | 2.896 | 3.4794 | 3.5113 | 3.5549 | 2.896 | 3.8677 | 4.3547 | 4.3834 | 4.4215 | 4.6796
2021-09-12 20:00 | 3.0675 | 3.3853 | 3.4311 | 3.4873 | 3.5527 | 2.6483 | 3.1938 | 3.2296 | 3.2784 | 2.6483 | 3.7343 | 4.2134 | 4.2455 | 4.2882 | 4.5445
2021-09-12 21:00 | 2.8769 | 3.1822 | 3.2289 | 3.286 | 3.3527 | 2.4959 | 3.0149 | 3.0513 | 3.1011 | 2.4959 | 3.5057 | 3.9604 | 3.9932 | 4.0366 | 4.2813
2021-09-12 22:00 | 2.7436 | 3.033 | 3.0766 | 3.13 | 3.1923 | 2.1853 | 2.6436 | 2.6777 | 2.7242 | 2.1853 | 3.1437 | 3.554 | 3.5845 | 3.6252 | 3.8466
2021-09-12 23:00 | 2.6102 | 2.8812 | 2.9206 | 2.9687 | 3.0249 | 1.9053 | 2.3067 | 2.3374 | 2.3793 | 1.9053 | 2.8388 | 3.2092 | 3.2368 | 3.2734 | 3.4732
2021-09-13 | 2.251 | 2.4859 | 2.5205 | 2.5627 | 2.6119 | 1.7147 | 2.0748 | 2.1017 | 2.1384 | 1.7147 | 2.3625 | 2.6732 | 2.6974 | 2.7295 | 2.8978
2021-09-13 01:00 | 2.172 | 2.3914 | 2.4211 | 2.4573 | 2.4996 | 1.5757 | 1.9036 | 1.9267 | 1.9582 | 1.5757 | 2.4387 | 2.7511 | 2.7719 | 2.7994 | 2.9665
2021-09-13 02:00 | 2.1339 | 2.3384 | 2.3619 | 2.3906 | 2.424 | 1.4289 | 1.7214 | 1.7397 | 1.7647 | 1.4289 | 2.0958 | 2.3615 | 2.3779 | 2.3997 | 2.541
2021-09-13 03:00 | 2.172 | 2.3675 | 2.3849 | 2.4063 | 2.4311 | 1.3908 | 1.6678 | 1.6814 | 1.6999 | 1.3908 | 1.9243 | 2.1625 | 2.1747 | 2.1909 | 2.3161
2021-09-13 04:00 | 2.1608 | 2.3454 | 2.3577 | 2.3727 | 2.3902 | 1.4861 | 1.773 | 1.7826 | 1.7957 | 1.4861 | 2.1339 | 2.3883 | 2.3969 | 2.4083 | 2.5393
2021-09-13 05:00 | 2.3816 | 2.5787 | 2.5889 | 2.6014 | 2.616 | 1.7897 | 2.1288 | 2.1367 | 2.1476 | 1.7897 | 2.6483 | 2.9571 | 2.9643 | 2.9738 | 3.1308
2021-09-13 06:00 | 2.6293 | 2.8481 | 2.86 | 2.8746 | 2.8917 | 2.0767 | 2.4703 | 2.4796 | 2.4923 | 2.0767 | 3.3533 | 3.7429 | 3.7512 | 3.7623 | 3.96
2021-09-13 07:00 | 3.0103 | 3.2666 | 3.2831 | 3.3034 | 3.3271 | 2.2101 | 2.6345 | 2.6474 | 2.6651 | 2.2101 | 3.4295 | 3.834 | 3.8456 | 3.861 | 4.068
2021-09-13 08:00 | 3.3533 | 3.6483 | 3.6717 | 3.7004 | 3.7338 | 2.6864 | 3.2069 | 3.2251 | 3.25 | 2.6864 | 4.6488 | 5.1985 | 5.2149 | 5.2367 | 5.5183
2021-09-13 09:00 | 3.62 | 3.9492 | 3.9798 | 4.0174 | 4.0612 | 2.9341 | 3.5098 | 3.5338 | 3.5664 | 2.9341 | 4.725 | 5.2933 | 5.3148 | 5.3433 | 5.6372
2021-09-13 10:00 | 3.5057 | 3.8373 | 3.8735 | 3.9179 | 3.9697 | 2.7817 | 3.3377 | 3.366 | 3.4046 | 2.7817 | 4.6869 | 5.2587 | 5.2841 | 5.3178 | 5.6159
2021-09-13 11:00 | 3.1849 | 3.497 | 3.5355 | 3.5826 | 3.6376 | 2.4458 | 2.944 | 2.9741 | 3.015 | 2.4458 | 3.1627 | 3.568 | 3.5949 | 3.6308 | 3.8475
2021-09-13 12:00 | 2.2482 | 2.4896 | 2.5276 | 2.574 | 2.6282 | 1.9158 | 2.3172 | 2.3468 | 2.3872 | 1.9158 | 1.3337 | 1.5347 | 1.5613 | 1.5966 | 1.7122
2021-09-13 13:00 | 2.896 | 3.1806 | 3.216 | 3.2593 | 3.3098 | 2.0767 | 2.5037 | 2.5313 | 2.569 | 2.0767 | 3.258 | 3.6696 | 3.6944 | 3.7273 | 3.9458
2021-09-13 14:00 | 2.9531 | 3.2366 | 3.2692 | 3.3092 | 3.3557 | 2.191 | 2.6348 | 2.6603 | 2.695 | 2.191 | 3.5247 | 3.9621 | 3.985 | 4.0154 | 4.2455
2021-09-13 15:00 | 2.7055 | 2.9669 | 2.9977 | 3.0354 | 3.0794 | 2.0577 | 2.4746 | 2.4987 | 2.5315 | 2.0577 | 2.7817 | 3.1339 | 3.1555 | 3.1841 | 3.3713
2021-09-13 16:00 | 2.8579 | 3.1298 | 3.1601 | 3.1973 | 3.2407 | 2.3244 | 2.7891 | 2.8128 | 2.8452 | 2.3244 | 3.277 | 3.6837 | 3.705 | 3.7333 | 3.9472
2021-09-13 17:00 | 3.4295 | 3.7474 | 3.7796 | 3.819 | 3.8649 | 3.0823 | 3.687 | 3.7121 | 3.7464 | 3.0823 | 4.6298 | 5.1895 | 5.212 | 5.242 | 5.5323
2021-09-13 18:00 | 3.8867 | 4.246 | 4.2819 | 4.3259 | 4.3772 | 3.4104 | 4.08 | 4.108 | 4.1463 | 3.4104 | 5.0299 | 5.6393 | 5.6645 | 5.6979 | 6.0145
2021-09-13 19:00 | 3.8105 | 4.1739 | 4.2148 | 4.2649 | 4.3233 | 3.3723 | 4.0421 | 4.074 | 4.1176 | 3.3723 | 4.8393 | 5.4345 | 5.4632 | 5.5013 | 5.8128
2021-09-13 20:00 | 3.5438 | 3.897 | 3.9429 | 3.999 | 4.0644 | 3.0865 | 3.7115 | 3.7472 | 3.7961 | 3.0865 | 4.5536 | 5.1238 | 5.1559 | 5.1986 | 5.5
2021-09-13 21:00 | 3.4104 | 3.7553 | 3.802 | 3.8592 | 3.9258 | 2.915 | 3.5101 | 3.5465 | 3.5962 | 2.915 | 4.8203 | 5.4213 | 5.454 | 5.4975 | 5.8145
2021-09-13 22:00 | 2.9722 | 3.2786 | 3.3222 | 3.3757 | 3.438 | 2.4696 | 2.9795 | 3.0136 | 3.0601 | 2.4696 | 3.9248 | 4.422 | 4.4526 | 4.4932 | 4.7576
2021-09-13 23:00 | 2.5149 | 2.7789 | 2.8182 | 2.8664 | 2.9225 | 2.0386 | 2.4643 | 2.4949 | 2.5368 | 2.0386 | 3.0865 | 3.4845 | 3.512 | 3.5486 | 3.7621
2021-09-14 | 2.4387 | 2.6876 | 2.7221 | 2.7643 | 2.8136 | 1.7714 | 2.1417 | 2.1687 | 2.2054 | 1.7714 | 2.3816 | 2.6944 | 2.7186 | 2.7507 | 2.92
2021-09-14 01:00 | 2.2291 | 2.4528 | 2.4825 | 2.5187 | 2.561 | 1.6202 | 1.9562 | 1.9793 | 2.0108 | 1.6202 | 2.172 | 2.4547 | 2.4755 | 2.503 | 2.6554
2021-09-14 02:00 | 2.2291 | 2.4408 | 2.4642 | 2.4929 | 2.5264 | 1.5623 | 1.879 | 1.8973 | 1.9222 | 1.5623 | 2.0386 | 2.2979 | 2.3144 | 2.3362 | 2.4744
2021-09-14 03:00 | 2.2291 | 2.4289 | 2.4464 | 2.4677 | 2.4925 | 1.5052 | 1.8029 | 1.8165 | 1.835 | 1.5052 | 2.6483 | 2.9671 | 2.9793 | 2.9955 | 3.1605
2021-09-14 04:00 | 2.3054 | 2.5007 | 2.513 | 2.528 | 2.5455 | 1.6195 | 1.9306 | 1.9402 | 1.9532 | 1.6195 | 2.4197 | 2.7059 | 2.7145 | 2.7259 | 2.8725
2021-09-14 05:00 | 2.4387 | 2.6401 | 2.6503 | 2.6628 | 2.6774 | 1.9339 | 2.2992 | 2.3072 | 2.3181 | 1.9339 | 2.8579 | 3.19 | 3.1972 | 3.2067 | 3.3752
2021-09-14 06:00 | 2.7055 | 2.93 | 2.9419 | 2.9565 | 2.9735 | 2.0958 | 2.4928 | 2.5021 | 2.5149 | 2.0958 | 3.5247 | 3.9334 | 3.9418 | 3.9529 | 4.1599
2021-09-14 07:00 | 2.8007 | 3.0414 | 3.058 | 3.0783 | 3.1019 | 2.0958 | 2.4994 | 2.5124 | 2.53 | 2.0958 | 3.1437 | 3.5164 | 3.528 | 3.5435 | 3.7347
2021-09-14 08:00 | 2.6674 | 2.9115 | 2.9349 | 2.9635 | 2.9969 | 1.9624 | 2.3516 | 2.3698 | 2.3947 | 1.9624 | 2.7245 | 3.0601 | 3.0765 | 3.0983 | 3.2741
2021-09-14 09:00 | 2.5911 | 2.8438 | 2.8745 | 2.912 | 2.9558 | 1.7528 | 2.1143 | 2.1383 | 2.1709 | 1.7528 | 2.1529 | 2.435 | 2.4565 | 2.4851 | 2.6376
2021-09-14 10:00 | 2.534 | 2.7934 | 2.8296 | 2.874 | 2.9258 | 1.7719 | 2.1448 | 2.1731 | 2.2117 | 1.7719 | 1.9054 | 2.1677 | 2.1931 | 2.2269 | 2.372
2021-09-14 11:00 | 2.5149 | 2.7772 | 2.8157 | 2.8628 | 2.9177 | 1.6576 | 2.0129 | 2.0429 | 2.0839 | 1.6576 | 1.7147 | 1.9589 | 1.9858 | 2.0217 | 2.1588
2021-09-14 12:00 | 2.4387 | 2.6943 | 2.7323 | 2.7787 | 2.8329 | 1.6576 | 2.0121 | 2.0417 | 2.0821 | 1.6576 | 1.448 | 1.6617 | 1.6883 | 1.7236 | 1.8455
2021-09-14 13:00 | 2.3625 | 2.6074 | 2.6428 | 2.6862 | 2.7367 | 1.4099 | 1.7159 | 1.7435 | 1.7812 | 1.4099 | 1.4099 | 1.6158 | 1.6406 | 1.6736 | 1.7905
2021-09-14 14:00 | 2.2101 | 2.4383 | 2.4709 | 2.5109 | 2.5574 | 1.5242 | 1.847 | 1.8725 | 1.9072 | 1.5242 | 1.2765 | 1.4638 | 1.4867 | 1.5171 | 1.6236
2021-09-14 15:00 | 2.2482 | 2.4756 | 2.5064 | 2.5441 | 2.5881 | 1.6576 | 2.002 | 2.026 | 2.0588 | 1.6576 | 1.9815 | 2.2446 | 2.2662 | 2.2949 | 2.4381
2021-09-14 16:00 | 2.6864 | 2.9456 | 2.9759 | 3.0131 | 3.0564 | 1.9272 | 2.3199 | 2.3436 | 2.3759 | 1.9272 | 2.534 | 2.858 | 2.8793 | 2.9076 | 3.0807
2021-09-14 17:00 | 3.2389 | 3.5427 | 3.5749 | 3.6143 | 3.6602 | 2.6597 | 3.1878 | 3.2129 | 3.2472 | 2.6597 | 3.8571 | 4.3308 | 4.3533 | 4.3833 | 4.6311
2021-09-14 18:00 | 3.4866 | 3.8162 | 3.8521 | 3.8961 | 3.9474 | 2.915 | 3.4948 | 3.5228 | 3.5611 | 2.915 | 4.344 | 4.8771 | 4.9023 | 4.9357 | 5.2145
2021-09-14 19:00 | 3.3914 | 3.7236 | 3.7645 | 3.8146 | 3.873 | 2.896 | 3.4794 | 3.5113 | 3.5549 | 2.896 | 4.5536 | 5.1169 | 5.1456 | 5.1837 | 5.4795
2021-09-14 20:00 | 3.4104 | 3.7537 | 3.7996 | 3.8557 | 3.9211 | 2.8198 | 3.3964 | 3.4321 | 3.481 | 2.8198 | 4.5536 | 5.1238 | 5.1559 | 5.1986 | 5.5
2021-09-14 21:00 | 3.2389 | 3.5711 | 3.6178 | 3.675 | 3.7416 | 2.7245 | 3.285 | 3.3214 | 3.3712 | 2.7245 | 4.5536 | 5.1249 | 5.1576 | 5.2011 | 5.5034
2021-09-14 22:00 | 3.0103 | 3.3195 | 3.3632 | 3.4166 | 3.4789 | 2.3529 | 2.8416 | 2.8757 | 2.9222 | 2.3529 | 3.6009 | 4.0621 | 4.0927 | 4.1333 | 4.3799
2021-09-14 23:00 | 2.6102 | 2.8812 | 2.9206 | 2.9687 | 3.0249 | 2.0386 | 2.4643 | 2.4949 | 2.5368 | 2.0386 | 3.0294 | 3.4209 | 3.4485 | 3.4851 | 3.6954
2021-09-15 | 2.3435 | 2.5852 | 2.6197 | 2.662 | 2.7112 | 1.7167 | 2.0771 | 2.104 | 2.1408 | 1.7167 | 2.4197 | 2.7367 | 2.7609 | 2.793 | 2.9645
2021-09-15 01:00 | 2.3244 | 2.5552 | 2.5848 | 2.6211 | 2.6633 | 1.5439 | 1.866 | 1.8891 | 1.9206 | 1.5439 | 2.3816 | 2.6876 | 2.7084 | 2.7359 | 2.8998
2021-09-15 02:00 | 2.191 | 2.3998 | 2.4233 | 2.452 | 2.4854 | 1.5052 | 1.8115 | 1.8297 | 1.8547 | 1.5052 | 2.0196 | 2.2768 | 2.2932 | 2.315 | 2.4522
2021-09-15 03:00 | 2.1529 | 2.3471 | 2.3645 | 2.3858 | 2.4106 | 1.5163 | 1.8161 | 1.8297 | 1.8482 | 1.5163 | 2.172 | 2.4378 | 2.45 | 2.4662 | 2.605
2021-09-15 04:00 | 2.3435 | 2.5417 | 2.5539 | 2.5689 | 2.5864 | 1.6197 | 1.9309 | 1.9405 | 1.9535 | 1.6197 | 2.3435 | 2.6212 | 2.6298 | 2.6412 | 2.7837
2021-09-15 05:00 | 2.534 | 2.7424 | 2.7526 | 2.7652 | 2.7798 | 1.9211 | 2.284 | 2.292 | 2.3029 | 1.9211 | 2.8769 | 3.2112 | 3.2184 | 3.2279 | 3.3974
2021-09-15 06:00 | 2.7436 | 2.9709 | 2.9828 | 2.9974 | 3.0145 | 2.0958 | 2.4928 | 2.5021 | 2.5149 | 2.0958 | 3.3151 | 3.7005 | 3.7089 | 3.72 | 3.9155
2021-09-15 07:00 | 2.8388 | 3.0823 | 3.0989 | 3.1192 | 3.1429 | 2.3435 | 2.792 | 2.805 | 2.8226 | 2.3435 | 3.3151 | 3.707 | 3.7186 | 3.734 | 3.9347
2021-09-15 08:00 | 2.6864 | 2.9319 | 2.9553 | 2.984 | 3.0174 | 2.0196 | 2.4191 | 2.4374 | 2.4623 | 2.0196 | 2.915 | 3.2718 | 3.2882 | 3.31 | 3.4963
2021-09-15 09:00 | 2.4959 | 2.7415 | 2.7722 | 2.8097 | 2.8535 | 1.7147 | 2.0693 | 2.0933 | 2.1259 | 1.7147 | 2.2482 | 2.5409 | 2.5624 | 2.5909 | 2.7487
2021-09-15 10:00 | 1.9434 | 2.1588 | 2.1951 | 2.2395 | 2.2912 | 1.448 | 1.7622 | 1.7904 | 1.8291 | 1.448 | 1.5052 | 1.7229 | 1.7483 | 1.7821 | 1.9052
2021-09-15 11:00 | 1.7909 | 1.9994 | 2.0379 | 2.085 | 2.1399 | 1.3337 | 1.6303 | 1.6603 | 1.7013 | 1.3337 | 1.3718 | 1.5778 | 1.6047 | 1.6406 | 1.7588
2021-09-15 12:00 | 2.2291 | 2.4691 | 2.5071 | 2.5535 | 2.6077 | 1.3527 | 1.652 | 1.6816 | 1.722 | 1.3527 | 0.87642 | 1.0265 | 1.0531 | 1.0885 | 1.1789
2021-09-15 13:00 | 2.2101 | 2.4437 | 2.4791 | 2.5224 | 2.5729 | 1.5623 | 1.896 | 1.9236 | 1.9613 | 1.5623 | 1.086 | 1.2559 | 1.2807 | 1.3137 | 1.4128
2021-09-15 14:00 | 2.3435 | 2.5816 | 2.6142 | 2.6542 | 2.7007 | 1.2575 | 1.5319 | 1.5574 | 1.5921 | 1.2575 | 1.1813 | 1.3579 | 1.3808 | 1.4112 | 1.5125
2021-09-15 15:00 | 2.1458 | 2.3656 | 2.3964 | 2.4341 | 2.4781 | 1.4289 | 1.7319 | 1.7559 | 1.7887 | 1.4289 | 1.448 | 1.6518 | 1.6734 | 1.7021 | 1.816
2021-09-15 16:00 | 2.4959 | 2.7409 | 2.7712 | 2.8084 | 2.8517 | 1.7909 | 2.1589 | 2.1826 | 2.2149 | 1.7909 | 2.534 | 2.858 | 2.8793 | 2.9076 | 3.0807
2021-09-15 17:00 | 3.0957 | 3.3888 | 3.421 | 3.4604 | 3.5063 | 2.5366 | 3.0424 | 3.0675 | 3.1018 | 2.5366 | 3.7915 | 4.2579 | 4.2804 | 4.3104 | 4.5546
2021-09-15 18:00 | 3.3621 | 3.6824 | 3.7183 | 3.7623 | 3.8136 | 2.8911 | 3.4665 | 3.4946 | 3.5328 | 2.8911 | 4.0772 | 4.5807 | 4.6059 | 4.6393 | 4.9035
2021-09-15 19:00 | 3.4866 | 3.8259 | 3.8668 | 3.9169 | 3.9753 | 2.9341 | 3.5244 | 3.5563 | 3.5999 | 2.9341 | 5.0108 | 5.625 | 5.6537 | 5.6918 | 6.0128
2021-09-15 20:00 | 3.3342 | 3.6718 | 3.7177 | 3.7738 | 3.8393 | 2.8579 | 3.4414 | 3.4772 | 3.526 | 2.8579 | 4.2297 | 4.7638 | 4.796 | 4.8387 | 5.1222
2021-09-15 21:00 | 3.2199 | 3.5507 | 3.5973 | 3.6545 | 3.7211 | 2.6293 | 3.1725 | 3.2089 | 3.2586 | 2.6293 | 4.8203 | 5.4213 | 5.454 | 5.4975 | 5.8145
2021-09-15 22:00 | 2.9531 | 3.2581 | 3.3018 | 3.3552 | 3.4175 | 2.3625 | 2.853 | 2.8871 | 2.9336 | 2.3625 | 3.4104 | 3.8504 | 3.8809 | 3.9216 | 4.1577
2021-09-15 23:00 | 2.6102 | 2.8812 | 2.9206 | 2.9687 | 3.0249 | 1.9434 | 2.3517 | 2.3824 | 2.4243 | 1.9434 | 2.6674 | 3.0187 | 3.0462 | 3.0828 | 3.2733
2021-09-16 | 2.3816 | 2.6262 | 2.6607 | 2.7029 | 2.7522 | 1.679 | 2.0326 | 2.0595 | 2.0963 | 1.679 | 2.2673 | 2.5674 | 2.5915 | 2.6237 | 2.7867
2021-09-16 01:00 | 2.1148 | 2.33 | 2.3596 | 2.3959 | 2.4382 | 1.4657 | 1.7737 | 1.7968 | 1.8283 | 1.4657 | 2.0386 | 2.3065 | 2.3273 | 2.3548 | 2.4999
2021-09-16 02:00 | 2.0958 | 2.2975 | 2.3209 | 2.3496 | 2.3831 | 1.3908 | 1.6764 | 1.6947 | 1.7197 | 1.3908 | 1.8481 | 2.0862 | 2.1027 | 2.1245 | 2.2522
2021-09-16 03:00 | 2.0386 | 2.2243 | 2.2417 | 2.263 | 2.2878 | 1.3527 | 1.6228 | 1.6364 | 1.6549 | 1.3527 | 1.7719 | 1.9932 | 2.0054 | 2.0216 | 2.1384
2021-09-16 04:00 | 2.0577 | 2.2346 | 2.2469 | 2.2619 | 2.2794 | 1.4221 | 1.6974 | 1.707 | 1.72 | 1.4221 | 1.8672 | 2.0919 | 2.1005 | 2.1119 | 2.2282
2021-09-16 05:00 | 2.2482 | 2.4354 | 2.4456 | 2.4581 | 2.4727 | 1.7181 | 2.0442 | 2.0522 | 2.0631 | 1.7181 | 2.2863 | 2.5549 | 2.562 | 2.5716 | 2.7086
2021-09-16 06:00 | 2.4578 | 2.6639 | 2.6758 | 2.6904 | 2.7074 | 1.81 | 2.1552 | 2.1645 | 2.1772 | 1.81 | 2.7055 | 3.023 | 3.0314 | 3.0425 | 3.2045
2021-09-16 07:00 | 2.4197 | 2.632 | 2.6486 | 2.6689 | 2.6925 | 1.81 | 2.1618 | 2.1748 | 2.1924 | 1.81 | 2.5149 | 2.8177 | 2.8293 | 2.8448 | 3.0015
2021-09-16 08:00 | 2.3054 | 2.5225 | 2.5459 | 2.5746 | 2.608 | 1.6576 | 1.9915 | 2.0097 | 2.0346 | 1.6576 | 1.7528 | 1.9803 | 1.9967 | 2.0185 | 2.1409
2021-09-16 09:00 | 2.0958 | 2.3116 | 2.3423 | 2.3799 | 2.4236 | 1.3718 | 1.6642 | 1.6881 | 1.7208 | 1.3718 | 2.0005 | 2.2656 | 2.2871 | 2.3157 | 2.4598
2021-09-16 10:00 | 2.2673 | 2.5068 | 2.5431 | 2.5874 | 2.6392 | 1.3617 | 1.6602 | 1.6885 | 1.7271 | 1.3617 | 1.6195 | 1.8499 | 1.8753 | 1.9091 | 2.0385
2021-09-16 11:00 | 2.2482 | 2.4907 | 2.5292 | 2.5763 | 2.6312 | 1.6004 | 1.9454 | 1.9754 | 2.0164 | 1.6004 | 1.2956 | 1.4931 | 1.52 | 1.5559 | 1.6699
2021-09-16 12:00 | 2.1148 | 2.3463 | 2.3843 | 2.4307 | 2.4849 | 1.5052 | 1.8321 | 1.8617 | 1.9021 | 1.5052 | 1.3527 | 1.5559 | 1.5824 | 1.6178 | 1.7344
2021-09-16 13:00 | 1.9434 | 2.1571 | 2.1925 | 2.2359 | 2.2864 | 1.4099 | 1.7159 | 1.7435 | 1.7812 | 1.4099 | 1.0212 | 1.184 | 1.2088 | 1.2417 | 1.3373
2021-09-16 14:00 | 2.1339 | 2.3564 | 2.389 | 2.429 | 2.4756 | 1.5433 | 1.8695 | 1.895 | 1.9298 | 1.5433 | 1.3527 | 1.5485 | 1.5714 | 1.6017 | 1.7124
2021-09-16 15:00 | 2.1339 | 2.3528 | 2.3836 | 2.4213 | 2.4653 | 1.5433 | 1.8669 | 1.891 | 1.9238 | 1.5433 | 1.1432 | 1.3131 | 1.3346 | 1.3633 | 1.4604
2021-09-16 16:00 | 2.2863 | 2.5157 | 2.5461 | 2.5832 | 2.6266 | 1.6385 | 1.9788 | 2.0025 | 2.0349 | 1.6385 | 1.7909 | 2.0323 | 2.0536 | 2.0818 | 2.2141
2021-09-16 17:00 | 2.7626 | 3.031 | 3.0632 | 3.1025 | 3.1485 | 2.2769 | 2.7356 | 2.7607 | 2.7949 | 2.2769 | 3.072 | 3.4584 | 3.481 | 3.5109 | 3.7156
2021-09-16 18:00 | 3.2008 | 3.5091 | 3.5451 | 3.589 | 3.6403 | 2.6483 | 3.1797 | 3.2077 | 3.246 | 2.6483 | 4.2106 | 4.7289 | 4.7541 | 4.7875 | 5.059
2021-09-16 19:00 | 3.2199 | 3.5394 | 3.5803 | 3.6303 | 3.6887 | 2.7626 | 3.3218 | 3.3537 | 3.3973 | 2.7626 | 3.8486 | 4.3335 | 4.3622 | 4.4003 | 4.6574
2021-09-16 20:00 | 3.1437 | 3.4671 | 3.513 | 3.5691 | 3.6346 | 2.6302 | 3.1724 | 3.2082 | 3.257 | 2.6302 | 4.0963 | 4.6156 | 4.6478 | 4.6905 | 4.9667
2021-09-16 21:00 | 3.0103 | 3.3255 | 3.3722 | 3.4293 | 3.496 | 2.534 | 3.0599 | 3.0964 | 3.1461 | 2.534 | 3.5819 | 4.0451 | 4.0778 | 4.1213 | 4.3702
2021-09-16 22:00 | 2.7817 | 3.0739 | 3.1176 | 3.171 | 3.2333 | 2.2851 | 2.7616 | 2.7956 | 2.8421 | 2.2851 | 3.4676 | 3.9139 | 3.9445 | 3.9851 | 4.2243
2021-09-16 23:00 | 2.4959 | 2.7584 | 2.7978 | 2.8459 | 2.902 | 1.8931 | 2.2924 | 2.3231 | 2.365 | 1.8931 | 2.5911 | 2.934 | 2.9615 | 2.9982 | 3.1844
2021-09-17 | 2.2863 | 2.5238 | 2.5583 | 2.6006 | 2.6498 | 1.6069 | 1.9474 | 1.9743 | 2.0111 | 1.6069 | 2.1529 | 2.4403 | 2.4645 | 2.4966 | 2.6534
2021-09-17 01:00 | 2.0577 | 2.2686 | 2.2982 | 2.3345 | 2.3768 | 1.4766 | 1.7865 | 1.8096 | 1.8411 | 1.4766 | 1.9815 | 2.243 | 2.2637 | 2.2913 | 2.4332
2021-09-17 02:00 | 2.0005 | 2.1951 | 2.2186 | 2.2473 | 2.2808 | 1.3718 | 1.6539 | 1.6722 | 1.6972 | 1.3718 | 1.8481 | 2.0862 | 2.1027 | 2.1245 | 2.2522
2021-09-17 03:00 | 1.9434 | 2.1219 | 2.1393 | 2.1606 | 2.1855 | 1.2956 | 1.5553 | 1.5689 | 1.5874 | 1.2956 | 1.7338 | 1.9508 | 1.963 | 1.9792 | 2.0939
2021-09-17 04:00 | 2.0767 | 2.2551 | 2.2674 | 2.2824 | 2.2999 | 1.3971 | 1.6679 | 1.6775 | 1.6905 | 1.3971 | 1.8481 | 2.0707 | 2.0793 | 2.0907 | 2.206
2021-09-17 05:00 | 2.2673 | 2.4558 | 2.4661 | 2.4786 | 2.4932 | 1.6867 | 2.0071 | 2.0151 | 2.026 | 1.6867 | 2.6102 | 2.9148 | 2.922 | 2.9315 | 3.0864
2021-09-17 06:00 | 2.3625 | 2.5615 | 2.5735 | 2.5881 | 2.6051 | 1.9053 | 2.2678 | 2.2771 | 2.2898 | 1.9053 | 2.6483 | 2.9595 | 2.9679 | 2.979 | 3.1378
2021-09-17 07:00 | 2.3625 | 2.5706 | 2.5872 | 2.6075 | 2.6311 | 1.7909 | 2.1393 | 2.1522 | 2.1699 | 1.7909 | 2.6674 | 2.9871 | 2.9987 | 3.0142 | 3.1792
2021-09-17 08:00 | 2.1339 | 2.3383 | 2.3617 | 2.3904 | 2.4238 | 1.5814 | 1.9014 | 1.9197 | 1.9446 | 1.5814 | 1.7719 | 2.0015 | 2.0179 | 2.0396 | 2.1631
2021-09-17 09:00 | 1.9624 | 2.1684 | 2.199 | 2.2366 | 2.2804 | 1.3146 | 1.5967 | 1.6206 | 1.6533 | 1.3146 | 1.0669 | 1.2282 | 1.2497 | 1.2782 | 1.371
2021-09-17 10:00 | 1.6957 | 1.8927 | 1.929 | 1.9734 | 2.0251 | 1.012 | 1.2471 | 1.2754 | 1.314 | 1.012 | 0.91452 | 1.0666 | 1.092 | 1.1257 | 1.2164
2021-09-17 11:00 | 1.448 | 1.631 | 1.6695 | 1.7166 | 1.7715 | 0.95263 | 1.1801 | 1.2101 | 1.2511 | 0.95263 | 0.97168 | 1.1332 | 1.1601 | 1.1959 | 1.2922
2021-09-17 12:00 | 1.3214 | 1.4939 | 1.5318 | 1.5783 | 1.6324 | 0.83831 | 1.0443 | 1.0739 | 1.1143 | 0.83831 | 1.0288 | 1.1959 | 1.2225 | 1.2578 | 1.3566
2021-09-17 13:00 | 1.3337 | 1.5021 | 1.5375 | 1.5808 | 1.6314 | 0.93358 | 1.1532 | 1.1808 | 1.2185 | 0.93358 | 0.95263 | 1.1077 | 1.1325 | 1.1655 | 1.2572
2021-09-17 14:00 | 2.1661 | 2.391 | 2.4236 | 2.4636 | 2.5101 | 1.4289 | 1.7345 | 1.76 | 1.7947 | 1.4289 | 1.4099 | 1.612 | 1.6349 | 1.6653 | 1.7791
2021-09-17 15:00 | 2.2101 | 2.4347 | 2.4655 | 2.5032 | 2.5472 | 1.4289 | 1.7319 | 1.7559 | 1.7887 | 1.4289 | 1.6957 | 1.9271 | 1.9486 | 1.9773 | 2.1048
2021-09-17 16:00 | 2.3244 | 2.5567 | 2.587 | 2.6242 | 2.6675 | 1.7252 | 2.0813 | 2.105 | 2.1373 | 1.7252 | 2.172 | 2.4557 | 2.477 | 2.5053 | 2.6585
2021-09-17 17:00 | 2.6483 | 2.9082 | 2.9403 | 2.9797 | 3.0256 | 2.2482 | 2.7017 | 2.7268 | 2.761 | 2.2482 | 3.3723 | 3.7921 | 3.8147 | 3.8446 | 4.0658
2021-09-17 18:00 | 2.915 | 3.2021 | 3.238 | 3.282 | 3.3333 | 2.3816 | 2.8646 | 2.8926 | 2.9309 | 2.3816 | 3.4104 | 3.8397 | 3.8648 | 3.8983 | 4.1258
2021-09-17 19:00 | 2.7817 | 3.0686 | 3.1095 | 3.1596 | 3.218 | 2.3435 | 2.8266 | 2.8586 | 2.9021 | 2.3435 | 3.1818 | 3.5925 | 3.6212 | 3.6593 | 3.8797
2021-09-17 20:00 | 2.6492 | 2.9359 | 2.9818 | 3.0379 | 3.1034 | 2.2482 | 2.7211 | 2.7569 | 2.8057 | 2.2482 | 3.7724 | 4.2557 | 4.2878 | 4.3305 | 4.589
2021-09-17 21:00 | 2.5979 | 2.8824 | 2.9291 | 2.9862 | 3.0529 | 2.1148 | 2.5648 | 2.6012 | 2.6509 | 2.1148 | 2.915 | 3.3041 | 3.3368 | 3.3803 | 3.5925
2021-09-17 22:00 | 2.4387 | 2.7055 | 2.7491 | 2.8025 | 2.8648 | 1.9129 | 2.3219 | 2.3559 | 2.4024 | 1.9129 | 2.5911 | 2.94 | 2.9705 | 3.0112 | 3.2022
2021-09-17 23:00 | 2.1529 | 2.39 | 2.4293 | 2.4775 | 2.5336 | 1.6991 | 2.0632 | 2.0939 | 2.1358 | 1.6991 | 2.8769 | 3.2516 | 3.2791 | 3.3157 | 3.5177
2021-09-18 | 1.9624 | 2.1759 | 2.2104 | 2.2526 | 2.3018 | 1.5052 | 1.8272 | 1.8541 | 1.8909 | 1.5052 | 2.0005 | 2.2709 | 2.2951 | 2.3272 | 2.4756
2021-09-18 01:00 | 1.8862 | 2.0844 | 2.114 | 2.1503 | 2.1925 | 1.3337 | 1.6177 | 1.6408 | 1.6723 | 1.3337 | 1.9053 | 2.1583 | 2.1791 | 2.2066 | 2.3443
2021-09-18 02:00 | 1.7719 | 1.9495 | 1.973 | 2.0017 | 2.0351 | 1.2384 | 1.4963 | 1.5146 | 1.5396 | 1.2384 | 1.5052 | 1.7051 | 1.7216 | 1.7434 | 1.8522
2021-09-18 03:00 | 1.7528 | 1.9172 | 1.9346 | 1.9559 | 1.9808 | 1.1813 | 1.4202 | 1.4338 | 1.4524 | 1.1813 | 1.5052 | 1.6968 | 1.7089 | 1.7252 | 1.8273
2021-09-18 04:00 | 1.7338 | 1.8867 | 1.8989 | 1.9139 | 1.9314 | 1.2003 | 1.4354 | 1.445 | 1.458 | 1.2003 | 1.467 | 1.6473 | 1.6559 | 1.6673 | 1.7616
2021-09-18 05:00 | 1.8481 | 2.0055 | 2.0158 | 2.0283 | 2.0429 | 1.3337 | 1.5901 | 1.5981 | 1.609 | 1.3337 | 1.9053 | 2.1314 | 2.1386 | 2.1481 | 2.2642
2021-09-18 06:00 | 1.8672 | 2.0293 | 2.0413 | 2.0559 | 2.0729 | 1.448 | 1.7276 | 1.7369 | 1.7496 | 1.448 | 1.9243 | 2.155 | 2.1633 | 2.1744 | 2.2935
2021-09-18 07:00 | 2.2101 | 2.4069 | 2.4234 | 2.4437 | 2.4674 | 1.6075 | 1.9226 | 1.9356 | 1.9532 | 1.6075 | 2.3054 | 2.5848 | 2.5965 | 2.6119 | 2.7571
2021-09-18 08:00 | 2.2482 | 2.4611 | 2.4845 | 2.5132 | 2.5466 | 1.81 | 2.1715 | 2.1898 | 2.2147 | 1.81 | 3.2008 | 3.5894 | 3.6058 | 3.6276 | 3.8296
2021-09-18 09:00 | 2.5149 | 2.762 | 2.7926 | 2.8302 | 2.874 | 1.9243 | 2.3169 | 2.3408 | 2.3735 | 1.9243 | 2.8388 | 3.1972 | 3.2187 | 3.2473 | 3.4375
2021-09-18 10:00 | 2.3625 | 2.6091 | 2.6454 | 2.6898 | 2.7415 | 1.9053 | 2.3023 | 2.3306 | 2.3693 | 1.9053 | 2.5911 | 2.9297 | 2.9551 | 2.9889 | 3.1717
2021-09-18 11:00 | 2.4006 | 2.6544 | 2.6929 | 2.74 | 2.7949 | 2.0386 | 2.4631 | 2.4931 | 2.5341 | 2.0386 | 2.7055 | 3.0598 | 3.0868 | 3.1226 | 3.3142
2021-09-18 12:00 | 2.3054 | 2.551 | 2.589 | 2.6354 | 2.6896 | 1.9243 | 2.3272 | 2.3568 | 2.3973 | 1.9243 | 2.3244 | 2.6356 | 2.6622 | 2.6976 | 2.8676
2021-09-18 13:00 | 2.191 | 2.4232 | 2.4586 | 2.502 | 2.5525 | 1.7338 | 2.0985 | 2.1262 | 2.1639 | 1.7338 | 2.0577 | 2.3357 | 2.3605 | 2.3935 | 2.546
2021-09-18 14:00 | 1.81 | 2.0084 | 2.0411 | 2.081 | 2.1276 | 1.6195 | 1.9596 | 1.985 | 2.0198 | 1.6195 | 1.9624 | 2.226 | 2.2489 | 2.2793 | 2.4235
2021-09-18 15:00 | 2.0577 | 2.2709 | 2.3017 | 2.3395 | 2.3834 | 1.5715 | 1.9003 | 1.9243 | 1.9571 | 1.5715 | 1.9243 | 2.1811 | 2.2027 | 2.2314 | 2.3715
2021-09-18 16:00 | 2.2291 | 2.4543 | 2.4847 | 2.5218 | 2.5652 | 1.8189 | 2.1919 | 2.2156 | 2.2479 | 1.8189 | 2.4006 | 2.7098 | 2.7311 | 2.7594 | 2.9251
2021-09-18 17:00 | 2.9913 | 3.2766 | 3.3088 | 3.3482 | 3.3941 | 2.4768 | 2.9718 | 2.9969 | 3.0311 | 2.4768 | 3.6962 | 4.152 | 4.1746 | 4.2045 | 4.4435
2021-09-18 18:00 | 3.2008 | 3.5091 | 3.5451 | 3.589 | 3.6403 | 2.8198 | 3.3823 | 3.4103 | 3.4486 | 2.8198 | 4.8012 | 5.3852 | 5.4104 | 5.4439 | 5.7478
2021-09-18 19:00 | 3.2199 | 3.5394 | 3.5803 | 3.6303 | 3.6887 | 2.9341 | 3.5244 | 3.5563 | 3.5999 | 2.9341 | 3.9629 | 4.4606 | 4.4892 | 4.5273 | 4.7907
2021-09-18 20:00 | 3.2008 | 3.5286 | 3.5744 | 3.6305 | 3.696 | 2.7436 | 3.3063 | 3.3421 | 3.3909 | 2.7436 | 4.4583 | 5.0179 | 5.05 | 5.0927 | 5.3889
2021-09-18 21:00 | 2.9341 | 3.2436 | 3.2903 | 3.3475 | 3.4141 | 2.5268 | 3.0514 | 3.0878 | 3.1375 | 2.5268 | 3.5378 | 3.9961 | 4.0288 | 4.0723 | 4.3188
2021-09-18 22:00 | 2.8388 | 3.1353 | 3.179 | 3.2324 | 3.2947 | 2.315 | 2.7969 | 2.8309 | 2.8774 | 2.315 | 3.6009 | 4.0621 | 4.0927 | 4.1333 | 4.3799
2021-09-18 23:00 | 2.6483 | 2.9222 | 2.9615 | 3.0097 | 3.0658 | 1.9638 | 2.3759 | 2.4066 | 2.4485 | 1.9638 | 3.2199 | 3.6327 | 3.6602 | 3.6968 | 3.9176
2021-09-19 | 2.4006 | 2.6466 | 2.6811 | 2.7234 | 2.7726 | 1.7991 | 2.1745 | 2.2014 | 2.2381 | 1.7991 | 2.915 | 3.2872 | 3.3114 | 3.3435 | 3.5422
2021-09-19 01:00 | 2.2673 | 2.4938 | 2.5234 | 2.5597 | 2.6019 | 1.6004 | 1.9328 | 1.9559 | 1.9874 | 1.6004 | 2.172 | 2.4547 | 2.4755 | 2.503 | 2.6554
2021-09-19 02:00 | 2.172 | 2.3794 | 2.4028 | 2.4315 | 2.465 | 1.448 | 1.7439 | 1.7622 | 1.7872 | 1.448 | 1.9434 | 2.1921 | 2.2085 | 2.2303 | 2.3633
2021-09-19 03:00 | 2.1339 | 2.3266 | 2.344 | 2.3653 | 2.3902 | 1.3908 | 1.6678 | 1.6814 | 1.6999 | 1.3908 | 1.9434 | 2.1837 | 2.1959 | 2.2121 | 2.3383
2021-09-19 04:00 | 2.1529 | 2.337 | 2.3493 | 2.3643 | 2.3818 | 1.448 | 1.728 | 1.7376 | 1.7506 | 1.448 | 2.1148 | 2.3671 | 2.3757 | 2.3871 | 2.517
2021-09-19 05:00 | 2.172 | 2.3535 | 2.3637 | 2.3762 | 2.3909 | 1.5814 | 1.8827 | 1.8907 | 1.9016 | 1.5814 | 2.2482 | 2.5125 | 2.5197 | 2.5292 | 2.6642
2021-09-19 06:00 | 2.3054 | 2.5001 | 2.512 | 2.5267 | 2.5437 | 1.7528 | 2.0877 | 2.097 | 2.1097 | 1.7528 | 3.1246 | 3.4888 | 3.4972 | 3.5083 | 3.6933
2021-09-19 07:00 | 2.1148 | 2.3045 | 2.3211 | 2.3414 | 2.365 | 1.5985 | 1.9119 | 1.9249 | 1.9425 | 1.5985 | 2.3435 | 2.6272 | 2.6388 | 2.6542 | 2.8015
2021-09-19 08:00 | 1.8672 | 2.0518 | 2.0752 | 2.1038 | 2.1372 | 1.3908 | 1.6763 | 1.6946 | 1.7195 | 1.3908 | 1.6957 | 1.9168 | 1.9332 | 1.955 | 2.0742
2021-09-19 09:00 | 1.9815 | 2.1888 | 2.2195 | 2.257 | 2.3008 | 1.5242 | 1.8442 | 1.8682 | 1.9008 | 1.5242 | 1.6385 | 1.8634 | 1.8848 | 1.9134 | 2.0376
2021-09-19 10:00 | 1.8481 | 2.0565 | 2.0927 | 2.1371 | 2.1889 | 1.4289 | 1.7397 | 1.7679 | 1.8066 | 1.4289 | 1.4289 | 1.6382 | 1.6636 | 1.6974 | 1.8163
2021-09-19 11:00 | 2.0386 | 2.2655 | 2.304 | 2.3511 | 2.406 | 1.6576 | 2.0129 | 2.0429 | 2.0839 | 1.6576 | 1.7147 | 1.9589 | 1.9858 | 2.0217 | 2.1588
2021-09-19 12:00 | 2.0767 | 2.3054 | 2.3433 | 2.3898 | 2.4439 | 1.6766 | 2.0346 | 2.0642 | 2.1047 | 1.6766 | 2.172 | 2.4663 | 2.4928 | 2.5282 | 2.6898
2021-09-19 13:00 | 2.0005 | 2.2185 | 2.2539 | 2.2973 | 2.3478 | 1.6576 | 2.0085 | 2.0361 | 2.0738 | 1.6576 | 2.191 | 2.4839 | 2.5087 | 2.5417 | 2.7015
2021-09-19 14:00 | 1.8862 | 2.0903 | 2.123 | 2.1629 | 2.2095 | 1.4099 | 1.712 | 1.7374 | 1.7722 | 1.4099 | 1.9815 | 2.2472 | 2.27 | 2.3004 | 2.4457
2021-09-19 15:00 | 1.829 | 2.0253 | 2.0561 | 2.0938 | 2.1378 | 1.5814 | 1.912 | 1.936 | 1.9688 | 1.5814 | 1.5814 | 1.8 | 1.8216 | 1.8503 | 1.9715
2021-09-19 16:00 | 2.3054 | 2.5362 | 2.5665 | 2.6037 | 2.647 | 1.9815 | 2.384 | 2.4077 | 2.44 | 1.9815 | 2.6102 | 2.9427 | 2.964 | 2.9923 | 3.1695
2021-09-19 17:00 | 3.0103 | 3.2971 | 3.3293 | 3.3686 | 3.4146 | 2.5911 | 3.1068 | 3.1319 | 3.1662 | 2.5911 | 3.7343 | 4.1944 | 4.2169 | 4.2469 | 4.488
2021-09-19 18:00 | 3.277 | 3.591 | 3.6269 | 3.6709 | 3.7222 | 2.9341 | 3.5173 | 3.5453 | 3.5836 | 2.9341 | 4.2487 | 4.7712 | 4.7964 | 4.8299 | 5.1034
2021-09-19 19:00 | 3.3342 | 3.6622 | 3.7031 | 3.7532 | 3.8116 | 2.9531 | 3.5469 | 3.5788 | 3.6224 | 2.9531 | 4.5917 | 5.1593 | 5.1879 | 5.226 | 5.524
2021-09-19 20:00 | 3.1649 | 3.4899 | 3.5358 | 3.5919 | 3.6573 | 2.7626 | 3.3288 | 3.3646 | 3.4134 | 2.7626 | 4.8775 | 5.4837 | 5.5158 | 5.5585 | 5.8777
2021-09-19 21:00 | 3.0294 | 3.346 | 3.3927 | 3.4498 | 3.5164 | 2.5526 | 3.082 | 3.1184 | 3.1681 | 2.5526 | 3.639 | 4.1087 | 4.1414 | 4.1848 | 4.4369
2021-09-19 22:00 | 2.7414 | 3.0307 | 3.0743 | 3.1277 | 3.19 | 2.2006 | 2.6618 | 2.6959 | 2.7423 | 2.2006 | 3.1246 | 3.5328 | 3.5634 | 3.604 | 3.8244
2021-09-19 23:00 | 2.4768 | 2.738 | 2.7773 | 2.8254 | 2.8816 | 1.9434 | 2.3517 | 2.3824 | 2.4243 | 1.9434 | 3.0294 | 3.4209 | 3.4485 | 3.4851 | 3.6954
2021-09-20 | 2.2673 | 2.5034 | 2.5379 | 2.5801 | 2.6294 | 1.6437 | 1.9909 | 2.0178 | 2.0545 | 1.6437 | 2.3816 | 2.6944 | 2.7186 | 2.7507 | 2.92
2021-09-20 01:00 | 2.1529 | 2.371 | 2.4006 | 2.4368 | 2.4791 | 1.4547 | 1.7606 | 1.7837 | 1.8152 | 1.4547 | 2.0767 | 2.3489 | 2.3696 | 2.3972 | 2.5443
2021-09-20 02:00 | 2.0958 | 2.2975 | 2.3209 | 2.3496 | 2.3831 | 1.4289 | 1.7214 | 1.7397 | 1.7647 | 1.4289 | 1.829 | 2.0651 | 2.0815 | 2.1033 | 2.23
2021-09-20 03:00 | 2.0196 | 2.2038 | 2.2212 | 2.2425 | 2.2674 | 1.3337 | 1.6003 | 1.6139 | 1.6324 | 1.3337 | 1.7719 | 1.9932 | 2.0054 | 2.0216 | 2.1384
2021-09-20 04:00 | 2.0577 | 2.2346 | 2.2469 | 2.2619 | 2.2794 | 1.3908 | 1.6605 | 1.6701 | 1.6831 | 1.3908 | 2.0005 | 2.2401 | 2.2487 | 2.2601 | 2.3837
2021-09-20 05:00 | 2.3054 | 2.4968 | 2.507 | 2.5195 | 2.5341 | 1.6385 | 1.9502 | 1.9582 | 1.9691 | 1.6385 | 2.5149 | 2.8089 | 2.8161 | 2.8256 | 2.9753
2021-09-20 06:00 | 2.4578 | 2.6639 | 2.6758 | 2.6904 | 2.7074 | 1.8672 | 2.2227 | 2.232 | 2.2448 | 1.8672 | 2.8007 | 3.1289 | 3.1372 | 3.1483 | 3.3156
2021-09-20 07:00 | 2.4387 | 2.6525 | 2.6691 | 2.6894 | 2.713 | 1.7091 | 2.0426 | 2.0556 | 2.0732 | 1.7091 | 2.4578 | 2.7542 | 2.7658 | 2.7813 | 2.9348
2021-09-20 08:00 | 2.191 | 2.3997 | 2.4231 | 2.4518 | 2.4852 | 1.5511 | 1.8657 | 1.884 | 1.9089 | 1.5511 | 1.81 | 2.0438 | 2.0602 | 2.082 | 2.2075
2021-09-20 09:00 | 1.9434 | 2.1479 | 2.1786 | 2.2161 | 2.2599 | 1.3906 | 1.6864 | 1.7103 | 1.743 | 1.3906 | 1.0098 | 1.1647 | 1.1862 | 1.2147 | 1.3044
2021-09-20 10:00 | 2.0005 | 2.2202 | 2.2565 | 2.3009 | 2.3526 | 1.467 | 1.7847 | 1.813 | 1.8516 | 1.467 | 1.7528 | 1.9981 | 2.0235 | 2.0573 | 2.194
2021-09-20 11:00 | 1.7463 | 1.9514 | 1.9899 | 2.037 | 2.0919 | 1.3094 | 1.6016 | 1.6316 | 1.6726 | 1.3094 | 0.99073 | 1.1543 | 1.1813 | 1.2171 | 1.3144
2021-09-20 12:00 | 2.3816 | 2.6329 | 2.6708 | 2.7173 | 2.7714 | 1.9053 | 2.3047 | 2.3343 | 2.3748 | 1.9053 | 2.3054 | 2.6145 | 2.6411 | 2.6764 | 2.8454
2021-09-20 13:00 | 2.5149 | 2.7712 | 2.8066 | 2.8499 | 2.9004 | 1.937 | 2.3387 | 2.3663 | 2.404 | 1.937 | 2.3816 | 2.6956 | 2.7204 | 2.7534 | 2.9237
2021-09-20 14:00 | 2.9531 | 3.2366 | 3.2692 | 3.3092 | 3.3557 | 2.4428 | 2.9322 | 2.9577 | 2.9924 | 2.4428 | 3.8296 | 4.3009 | 4.3238 | 4.3541 | 4.601
2021-09-20 15:00 | 3.1246 | 3.4172 | 3.448 | 3.4857 | 3.5297 | 2.553 | 3.0599 | 3.0839 | 3.1167 | 2.553 | 4.1154 | 4.6159 | 4.6375 | 4.6662 | 4.9267
2021-09-20 16:00 | 3.3723 | 3.6824 | 3.7128 | 3.75 | 3.7933 | 2.6864 | 3.2168 | 3.2405 | 3.2728 | 2.6864 | 4.0582 | 4.5518 | 4.5731 | 4.6013 | 4.8582
2021-09-20 17:00 | 3.5819 | 3.9112 | 3.9433 | 3.9827 | 4.0286 | 3.2149 | 3.8437 | 3.8688 | 3.9031 | 3.2149 | 5.1251 | 5.74 | 5.7625 | 5.7925 | 6.11
2021-09-20 18:00 | 3.8677 | 4.2255 | 4.2615 | 4.3055 | 4.3567 | 3.5247 | 4.215 | 4.2431 | 4.2813 | 3.5247 | 5.9253 | 6.6344 | 6.6596 | 6.693 | 7.0588
2021-09-20 19:00 | 3.8677 | 4.2353 | 4.2762 | 4.3263 | 4.3847 | 3.5438 | 4.2446 | 4.2766 | 4.3201 | 3.5438 | 5.8682 | 6.5778 | 6.6065 | 6.6446 | 7.0127
2021-09-20 20:00 | 3.7152 | 4.0812 | 4.1271 | 4.1832 | 4.2487 | 3.2961 | 3.9591 | 3.9948 | 4.0437 | 3.2961 | 4.9727 | 5.5896 | 5.6217 | 5.6644 | 5.9888
2021-09-20 21:00 | 3.4295 | 3.7758 | 3.8225 | 3.8796 | 3.9463 | 2.967 | 3.5715 | 3.6079 | 3.6576 | 2.967 | 5.1061 | 5.7389 | 5.7716 | 5.8151 | 6.1478
2021-09-20 22:00 | 3.1818 | 3.5038 | 3.5474 | 3.6008 | 3.6631 | 2.6008 | 3.1345 | 3.1685 | 3.215 | 2.6008 | 4.5726 | 5.1419 | 5.1725 | 5.2131 | 5.5131
2021-09-20 23:00 | 2.7245 | 3.0041 | 3.0434 | 3.0915 | 3.1477 | 2.1432 | 2.5878 | 2.6184 | 2.6603 | 2.1432 | 3.2199 | 3.6327 | 3.6602 | 3.6968 | 3.9176
2021-09-21 | 2.4959 | 2.749 | 2.7835 | 2.8257 | 2.875 | 1.7719 | 2.1423 | 2.1692 | 2.206 | 1.7719 | 2.6293 | 2.9696 | 2.9938 | 3.0259 | 3.2089
2021-09-21 01:00 | 2.2482 | 2.4733 | 2.5029 | 2.5392 | 2.5815 | 1.6656 | 2.0097 | 2.0328 | 2.0644 | 1.6656 | 2.4768 | 2.7935 | 2.8142 | 2.8418 | 3.0109
2021-09-21 02:00 | 2.2482 | 2.4612 | 2.4847 | 2.5134 | 2.5468 | 1.6004 | 1.924 | 1.9423 | 1.9673 | 1.6004 | 2.2673 | 2.552 | 2.5684 | 2.5903 | 2.741
2021-09-21 03:00 | 2.3054 | 2.5108 | 2.5282 | 2.5495 | 2.5744 | 1.5623 | 1.8704 | 1.884 | 1.9025 | 1.5623 | 2.2482 | 2.5225 | 2.5347 | 2.5509 | 2.6938
2021-09-21 04:00 | 2.2863 | 2.4803 | 2.4925 | 2.5075 | 2.525 | 1.6385 | 1.9531 | 1.9627 | 1.9757 | 1.6385 | 2.4197 | 2.7059 | 2.7145 | 2.7259 | 2.8725
2021-09-21 05:00 | 2.5911 | 2.8038 | 2.814 | 2.8266 | 2.8412 | 1.9815 | 2.3554 | 2.3633 | 2.3742 | 1.9815 | 3.0294 | 3.3806 | 3.3877 | 3.3973 | 3.5752
2021-09-21 06:00 | 2.7245 | 2.9504 | 2.9624 | 2.977 | 2.994 | 2.172 | 2.5829 | 2.5922 | 2.6049 | 2.172 | 3.3723 | 3.764 | 3.7724 | 3.7835 | 3.9822
2021-09-21 07:00 | 2.8388 | 3.0823 | 3.0989 | 3.1192 | 3.1429 | 2.172 | 2.5895 | 2.6024 | 2.6201 | 2.172 | 3.8867 | 4.3421 | 4.3537 | 4.3692 | 4.6013
2021-09-21 08:00 | 2.6293 | 2.8705 | 2.8939 | 2.9226 | 2.956 | 2.0577 | 2.4641 | 2.4824 | 2.5073 | 2.0577 | 2.4768 | 2.7848 | 2.8012 | 2.823 | 2.9852
2021-09-21 09:00 | 2.6293 | 2.8848 | 2.9154 | 2.953 | 2.9968 | 1.9624 | 2.3619 | 2.3859 | 2.4185 | 1.9624 | 2.6102 | 2.9431 | 2.9646 | 2.9932 | 3.1708
2021-09-21 10:00 | 2.915 | 3.2027 | 3.239 | 3.2834 | 3.3352 | 2.172 | 2.6175 | 2.6457 | 2.6844 | 2.172 | 2.553 | 2.8874 | 2.9128 | 2.9465 | 3.1273
2021-09-21 11:00 | 2.4959 | 2.7568 | 2.7952 | 2.8424 | 2.8973 | 1.9434 | 2.3505 | 2.3805 | 2.4215 | 1.9434 | 1.81 | 2.0647 | 2.0917 | 2.1275 | 2.2699
2021-09-21 12:00 | 2.4578 | 2.7148 | 2.7527 | 2.7992 | 2.8533 | 1.9434 | 2.3498 | 2.3794 | 2.4198 | 1.9434 | 2.0005 | 2.2757 | 2.3023 | 2.3376 | 2.4898
2021-09-21 13:00 | 2.4197 | 2.6689 | 2.7043 | 2.7476 | 2.7981 | 1.7909 | 2.1661 | 2.1937 | 2.2314 | 1.7909 | 1.7719 | 2.0181 | 2.0429 | 2.0759 | 2.2127
2021-09-21 14:00 | 2.2291 | 2.4588 | 2.4914 | 2.5313 | 2.5779 | 1.7528 | 2.1171 | 2.1426 | 2.1773 | 1.7528 | 1.105 | 1.2733 | 1.2961 | 1.3265 | 1.4236
2021-09-21 15:00 | 2.6483 | 2.9055 | 2.9363 | 2.974 | 3.018 | 1.9053 | 2.2946 | 2.3186 | 2.3514 | 1.9053 | 2.7817 | 3.1339 | 3.1555 | 3.1841 | 3.3713
2021-09-21 16:00 | 2.7055 | 2.966 | 2.9964 | 3.0336 | 3.0769 | 2.0577 | 2.474 | 2.4977 | 2.53 | 2.0577 | 2.6695 | 3.0086 | 3.0299 | 3.0581 | 3.2387
2021-09-21 17:00 | 3.2389 | 3.5427 | 3.5749 | 3.6143 | 3.6602 | 2.7346 | 3.2763 | 3.3014 | 3.3357 | 2.7346 | 4.1916 | 4.7025 | 4.7251 | 4.755 | 5.0213
2021-09-21 18:00 | 3.62 | 3.9594 | 3.9954 | 4.0394 | 4.0906 | 3.1627 | 3.7874 | 3.8154 | 3.8537 | 3.1627 | 4.725 | 5.3006 | 5.3257 | 5.3592 | 5.6589
2021-09-21 19:00 | 3.5628 | 3.9078 | 3.9487 | 3.9988 | 4.0572 | 3.2389 | 3.8845 | 3.9164 | 3.96 | 3.2389 | 5.6015 | 6.2814 | 6.3101 | 6.3481 | 6.7016
2021-09-21 20:00 | 3.5819 | 3.9379 | 3.9838 | 4.0399 | 4.1054 | 3.1246 | 3.7565 | 3.7923 | 3.8411 | 3.1246 | 4.4774 | 5.0391 | 5.0712 | 5.1139 | 5.4111
2021-09-21 21:00 | 3.5057 | 3.8577 | 3.9044 | 3.9615 | 4.0282 | 2.8769 | 3.4651 | 3.5015 | 3.5512 | 2.8769 | 4.6679 | 5.252 | 5.2847 | 5.3281 | 5.6367
2021-09-21 22:00 | 3.2389 | 3.5652 | 3.6088 | 3.6622 | 3.7245 | 2.6359 | 3.176 | 3.2101 | 3.2566 | 2.6359 | 3.6771 | 4.1468 | 4.1774 | 4.218 | 4.4687
2021-09-21 23:00 | 2.7817 | 3.0655 | 3.1048 | 3.1529 | 3.2091 | 2.2101 | 2.6668 | 2.6975 | 2.7394 | 2.2101 | 3.0484 | 3.4421 | 3.4697 | 3.5063 | 3.7177
2021-09-22 | 2.4959 | 2.749 | 2.7835 | 2.8257 | 2.875 | 1.8445 | 2.2281 | 2.255 | 2.2917 | 1.8445 | 2.553 | 2.8849 | 2.9091 | 2.9412 | 3.12
2021-09-22 01:00 | 2.4197 | 2.6575 | 2.6872 | 2.7234 | 2.7657 | 1.6679 | 2.0125 | 2.0356 | 2.0671 | 1.6679 | 2.3244 | 2.6241 | 2.6448 | 2.6724 | 2.8332
2021-09-22 02:00 | 2.3244 | 2.5431 | 2.5666 | 2.5953 | 2.6287 | 1.5513 | 1.8659 | 1.8842 | 1.9092 | 1.5513 | 2.172 | 2.4462 | 2.4626 | 2.4844 | 2.6299
2021-09-22 03:00 | 2.2673 | 2.4699 | 2.4873 | 2.5086 | 2.5334 | 1.6147 | 1.9323 | 1.9458 | 1.9644 | 1.6147 | 2.6864 | 3.0094 | 3.0216 | 3.0378 | 3.2049
2021-09-22 04:00 | 2.3435 | 2.5417 | 2.5539 | 2.5689 | 2.5864 | 1.6957 | 2.0206 | 2.0302 | 2.0433 | 1.6957 | 2.3625 | 2.6424 | 2.651 | 2.6624 | 2.8059
2021-09-22 05:00 | 2.6293 | 2.8447 | 2.855 | 2.8675 | 2.8821 | 2.06 | 2.4482 | 2.4562 | 2.4671 | 2.06 | 3.1246 | 3.4864 | 3.4936 | 3.5031 | 3.6863
2021-09-22 06:00 | 2.7055 | 2.93 | 2.9419 | 2.9565 | 2.9735 | 2.2101 | 2.6279 | 2.6372 | 2.6499 | 2.2101 | 3.3151 | 3.7005 | 3.7089 | 3.72 | 3.9155
2021-09-22 07:00 | 2.7245 | 2.9595 | 2.9761 | 2.9964 | 3.0201 | 2.2863 | 2.7245 | 2.7374 | 2.7551 | 2.2863 | 3.4104 | 3.8128 | 3.8244 | 3.8399 | 4.0458
2021-09-22 08:00 | 2.7055 | 2.9524 | 2.9758 | 3.0044 | 3.0378 | 2.0577 | 2.4641 | 2.4824 | 2.5073 | 2.0577 | 2.7817 | 3.1236 | 3.14 | 3.1618 | 3.3407
2021-09-22 09:00 | 2.2313 | 2.4572 | 2.4879 | 2.5255 | 2.5692 | 1.5814 | 1.9118 | 1.9357 | 1.9684 | 1.5814 | 1.5052 | 1.7152 | 1.7366 | 1.7652 | 1.8821
2021-09-22 10:00 | 1.7909 | 1.9951 | 2.0313 | 2.0757 | 2.1275 | 1.2575 | 1.5371 | 1.5654 | 1.604 | 1.2575 | 0.7621 | 0.89718 | 0.92259 | 0.95635 | 1.0386
2021-09-22 11:00 | 1.6195 | 1.8152 | 1.8537 | 1.9008 | 1.9557 | 1.0827 | 1.3337 | 1.3638 | 1.4047 | 1.0827 | 0.7621 | 0.90026 | 0.92722 | 0.96305 | 1.0478
2021-09-22 12:00 | 1.5623 | 1.7527 | 1.7907 | 1.8371 | 1.8913 | 1.0479 | 1.2919 | 1.3215 | 1.3619 | 1.0479 | 0.74305 | 0.87834 | 0.90493 | 0.94026 | 1.0233
2021-09-22 13:00 | 1.4861 | 1.6659 | 1.7013 | 1.7446 | 1.7951 | 0.97168 | 1.1982 | 1.2258 | 1.2635 | 0.97168 | 0.85737 | 1.0018 | 1.0266 | 1.0596 | 1.1461
2021-09-22 14:00 | 1.6576 | 1.8447 | 1.8773 | 1.9173 | 1.9638 | 1.0479 | 1.2843 | 1.3098 | 1.3446 | 1.0479 | 0.74305 | 0.87098 | 0.89385 | 0.92423 | 1.0014
2021-09-22 15:00 | 1.7719 | 1.9639 | 1.9947 | 2.0324 | 2.0764 | 1.2705 | 1.5447 | 1.5687 | 1.6015 | 1.2705 | 1.105 | 1.2707 | 1.2923 | 1.321 | 1.416
2021-09-22 16:00 | 2.2863 | 2.5157 | 2.5461 | 2.5832 | 2.6266 | 1.7182 | 2.073 | 2.0967 | 2.129 | 1.7182 | 1.8862 | 2.1382 | 2.1594 | 2.1877 | 2.3252
2021-09-22 17:00 | 2.796 | 3.0669 | 3.0991 | 3.1384 | 3.1844 | 2.3625 | 2.8367 | 2.8618 | 2.8961 | 2.3625 | 3.9439 | 4.4273 | 4.4498 | 4.4798 | 4.7324
2021-09-22 18:00 | 3.3533 | 3.6729 | 3.7088 | 3.7528 | 3.8041 | 2.8439 | 3.4108 | 3.4388 | 3.477 | 2.8439 | 4.2106 | 4.7289 | 4.7541 | 4.7875 | 5.059
2021-09-22 19:00 | 3.3151 | 3.6417 | 3.6826 | 3.7327 | 3.7911 | 2.8579 | 3.4344 | 3.4663 | 3.5098 | 2.8579 | 4.0391 | 4.5453 | 4.5739 | 4.612 | 4.8796
2021-09-22 20:00 | 3.0865 | 3.4057 | 3.4516 | 3.5077 | 3.5732 | 2.6293 | 3.1713 | 3.2071 | 3.2559 | 2.6293 | 3.9248 | 4.4251 | 4.4572 | 4.4999 | 4.7667
2021-09-22 21:00 | 2.9547 | 3.2658 | 3.3125 | 3.3696 | 3.4362 | 2.5911 | 3.1275 | 3.1639 | 3.2136 | 2.5911 | 3.5628 | 4.024 | 4.0567 | 4.1001 | 4.348
2021-09-22 22:00 | 2.7436 | 3.033 | 3.0766 | 3.13 | 3.1923 | 2.2107 | 2.6737 | 2.7077 | 2.7542 | 2.2107 | 3.1246 | 3.5328 | 3.5634 | 3.604 | 3.8244
2021-09-22 23:00 | 2.4959 | 2.7584 | 2.7978 | 2.8459 | 2.902 | 1.9675 | 2.3802 | 2.4109 | 2.4528 | 1.9675 | 2.6864 | 3.0398 | 3.0674 | 3.104 | 3.2955
2021-09-23 | 2.3244 | 2.5648 | 2.5993 | 2.6415 | 2.6908 | 1.6363 | 1.9821 | 2.009 | 2.0458 | 1.6363 | 2.2482 | 2.5462 | 2.5704 | 2.6025 | 2.7645
2021-09-23 01:00 | 2.0958 | 2.3096 | 2.3392 | 2.3754 | 2.4177 | 1.5242 | 1.8427 | 1.8658 | 1.8974 | 1.5242 | 2.2673 | 2.5606 | 2.5813 | 2.6089 | 2.7665
2021-09-23 02:00 | 2.0577 | 2.2565 | 2.28 | 2.3087 | 2.3422 | 1.4251 | 1.7169 | 1.7352 | 1.7601 | 1.4251 | 1.7909 | 2.0227 | 2.0391 | 2.061 | 2.1855
2021-09-23 03:00 | 2.0196 | 2.2038 | 2.2212 | 2.2425 | 2.2674 | 1.3527 | 1.6228 | 1.6364 | 1.6549 | 1.3527 | 1.9434 | 2.1837 | 2.1959 | 2.2121 | 2.3383
2021-09-23 04:00 | 2.0958 | 2.2756 | 2.2878 | 2.3029 | 2.3204 | 1.4165 | 1.6908 | 1.7004 | 1.7135 | 1.4165 | 2.0577 | 2.3036 | 2.3122 | 2.3236 | 2.4504
2021-09-23 05:00 | 2.172 | 2.3535 | 2.3637 | 2.3762 | 2.3909 | 1.6663 | 1.9831 | 1.9911 | 2.002 | 1.6663 | 2.5721 | 2.8724 | 2.8796 | 2.8891 | 3.0419
2021-09-23 06:00 | 2.3982 | 2.5999 | 2.6118 | 2.6264 | 2.6435 | 2.0005 | 2.3803 | 2.3896 | 2.4023 | 2.0005 | 3.1246 | 3.4888 | 3.4972 | 3.5083 | 3.6933
2021-09-23 07:00 | 2.8579 | 3.1028 | 3.1194 | 3.1397 | 3.1633 | 2.1586 | 2.5737 | 2.5866 | 2.6043 | 2.1586 | 3.5247 | 3.9399 | 3.9515 | 3.9669 | 4.1791
2021-09-23 08:00 | 2.896 | 3.1571 | 3.1805 | 3.2091 | 3.2425 | 2.2726 | 2.718 | 2.7363 | 2.7612 | 2.2726 | 3.3151 | 3.7164 | 3.7328 | 3.7546 | 3.9629
2021-09-23 09:00 | 3.0103 | 3.2941 | 3.3248 | 3.3624 | 3.4061 | 2.2863 | 2.7446 | 2.7685 | 2.8012 | 2.2863 | 3.0865 | 3.4724 | 3.4939 | 3.5225 | 3.7263
2021-09-23 10:00 | 2.7817 | 3.0595 | 3.0957 | 3.1401 | 3.1919 | 2.0577 | 2.4824 | 2.5107 | 2.5493 | 2.0577 | 2.7055 | 3.0568 | 3.0822 | 3.1159 | 3.305
2021-09-23 11:00 | 1.9434 | 2.1632 | 2.2016 | 2.2488 | 2.3037 | 1.3915 | 1.6986 | 1.7286 | 1.7696 | 1.3915 | 1.0288 | 1.1967 | 1.2236 | 1.2595 | 1.3589
2021-09-23 12:00 | 1.4289 | 1.6095 | 1.6474 | 1.6938 | 1.748 | 0.95263 | 1.1793 | 1.2089 | 1.2494 | 0.95263 | 0.7621 | 0.89952 | 0.9261 | 0.96143 | 1.0456
2021-09-23 13:00 | 1.3527 | 1.5226 | 1.558 | 1.6013 | 1.6518 | 0.91452 | 1.1307 | 1.1583 | 1.196 | 0.91452 | 1.0288 | 1.1924 | 1.2172 | 1.2502 | 1.3461
2021-09-23 14:00 | 1.448 | 1.6195 | 1.6522 | 1.6921 | 1.7387 | 0.97168 | 1.1943 | 1.2198 | 1.2545 | 0.97168 | 0.7621 | 0.89215 | 0.91502 | 0.9454 | 1.0236
2021-09-23 15:00 | 1.7719 | 1.9639 | 1.9947 | 2.0324 | 2.0764 | 1.1102 | 1.3553 | 1.3794 | 1.4122 | 1.1102 | 1.1622 | 1.3342 | 1.3558 | 1.3845 | 1.4827
2021-09-23 16:00 | 2.0751 | 2.2888 | 2.3192 | 2.3563 | 2.3997 | 1.5855 | 1.9162 | 1.9399 | 1.9722 | 1.5855 | 2.0005 | 2.2652 | 2.2865 | 2.3147 | 2.4585
2021-09-23 17:00 | 2.5496 | 2.8021 | 2.8343 | 2.8736 | 2.9196 | 2.181 | 2.6223 | 2.6474 | 2.6816 | 2.181 | 3.258 | 3.6651 | 3.6876 | 3.7176 | 3.9325
2021-09-23 18:00 | 2.9341 | 3.2226 | 3.2585 | 3.3025 | 3.3538 | 2.6483 | 3.1797 | 3.2077 | 3.246 | 2.6483 | 3.5438 | 3.9879 | 4.0131 | 4.0465 | 4.2813
2021-09-23 19:00 | 2.915 | 3.2118 | 3.2528 | 3.3028 | 3.3612 | 2.553 | 3.0742 | 3.1061 | 3.1497 | 2.553 | 3.5247 | 3.9736 | 4.0023 | 4.0404 | 4.2797
2021-09-23 20:00 | 2.8769 | 3.1806 | 3.2264 | 3.2826 | 3.348 | 2.4959 | 3.0137 | 3.0495 | 3.0983 | 2.4959 | 3.4676 | 3.9169 | 3.9491 | 3.9918 | 4.2334
2021-09-23 21:00 | 2.7626 | 3.0594 | 3.1061 | 3.1632 | 3.2299 | 2.4387 | 2.9474 | 2.9838 | 3.0335 | 2.4387 | 3.2199 | 3.6429 | 3.6756 | 3.719 | 3.948
2021-09-23 22:00 | 2.5721 | 2.8488 | 2.8924 | 2.9458 | 3.0081 | 2.1284 | 2.5764 | 2.6105 | 2.6569 | 2.1284 | 3.4676 | 3.9139 | 3.9445 | 3.9851 | 4.2243
2021-09-23 23:00 | 2.3816 | 2.6356 | 2.675 | 2.7231 | 2.7792 | 1.7338 | 2.1041 | 2.1348 | 2.1767 | 1.7338 | 2.5721 | 2.9128 | 2.9404 | 2.977 | 3.1622
2021-09-24 | 2.0846 | 2.3071 | 2.3416 | 2.3838 | 2.4331 | 1.6004 | 1.9397 | 1.9666 | 2.0034 | 1.6004 | 1.9701 | 2.2372 | 2.2613 | 2.2935 | 2.4402
2021-09-24 01:00 | 1.9624 | 2.1663 | 2.1959 | 2.2321 | 2.2744 | 1.3933 | 1.6882 | 1.7113 | 1.7428 | 1.3933 | 2.0386 | 2.3065 | 2.3273 | 2.3548 | 2.4999
2021-09-24 02:00 | 1.8304 | 2.0123 | 2.0358 | 2.0645 | 2.0979 | 1.2956 | 1.5639 | 1.5822 | 1.6071 | 1.2956 | 1.7147 | 1.938 | 1.9544 | 1.9763 | 2.0966
2021-09-24 03:00 | 1.8481 | 2.0196 | 2.037 | 2.0583 | 2.0831 | 1.2582 | 1.5112 | 1.5247 | 1.5433 | 1.2582 | 2.0196 | 2.2684 | 2.2806 | 2.2968 | 2.4272
2021-09-24 04:00 | 1.9434 | 2.1118 | 2.1241 | 2.1391 | 2.1566 | 1.3527 | 1.6155 | 1.6251 | 1.6381 | 1.3527 | 1.6957 | 1.9013 | 1.9099 | 1.9213 | 2.0282
2021-09-24 05:00 | 2.054 | 2.2268 | 2.237 | 2.2495 | 2.2641 | 1.609 | 1.9154 | 1.9234 | 1.9343 | 1.609 | 2.0577 | 2.3008 | 2.308 | 2.3175 | 2.442
2021-09-24 06:00 | 2.1339 | 2.3159 | 2.3278 | 2.3424 | 2.3595 | 1.6957 | 2.0202 | 2.0295 | 2.0422 | 1.6957 | 2.2101 | 2.4725 | 2.4809 | 2.492 | 2.6268
2021-09-24 07:00 | 2.0196 | 2.2022 | 2.2187 | 2.239 | 2.2627 | 1.5814 | 1.8917 | 1.9047 | 1.9223 | 1.5814 | 1.9815 | 2.2249 | 2.2365 | 2.252 | 2.3793
2021-09-24 08:00 | 1.9243 | 2.1132 | 2.1366 | 2.1652 | 2.1986 | 1.3525 | 1.6311 | 1.6493 | 1.6743 | 1.3525 | 1.3337 | 1.5145 | 1.5309 | 1.5527 | 1.652
2021-09-24 09:00 | 1.6957 | 1.8818 | 1.9125 | 1.95 | 1.9938 | 1.086 | 1.3266 | 1.3505 | 1.3832 | 1.086 | 0.68589 | 0.80474 | 0.82624 | 0.85479 | 0.92665
2021-09-24 10:00 | 2.0386 | 2.2612 | 2.2974 | 2.3418 | 2.3936 | 1.2384 | 1.5146 | 1.5429 | 1.5815 | 1.2384 | 1.105 | 1.2783 | 1.3037 | 1.3375 | 1.4386
2021-09-24 11:00 | 1.6576 | 1.8561 | 1.8946 | 1.9417 | 1.9966 | 1.2003 | 1.4727 | 1.5027 | 1.5437 | 1.2003 | 0.99073 | 1.1543 | 1.1813 | 1.2171 | 1.3144
2021-09-24 12:00 | 1.6195 | 1.8141 | 1.8521 | 1.8985 | 1.9527 | 1.3527 | 1.652 | 1.6816 | 1.722 | 1.3527 | 0.95263 | 1.1112 | 1.1378 | 1.1732 | 1.2678
2021-09-24 13:00 | 1.9624 | 2.1776 | 2.213 | 2.2563 | 2.3068 | 1.3908 | 1.6934 | 1.721 | 1.7587 | 1.3908 | 1.467 | 1.6794 | 1.7042 | 1.7371 | 1.8572
2021-09-24 14:00 | 2.0005 | 2.2131 | 2.2458 | 2.2857 | 2.3323 | 1.2956 | 1.5769 | 1.6024 | 1.6372 | 1.2956 | 1.3908 | 1.5908 | 1.6137 | 1.6441 | 1.7569
2021-09-24 15:00 | 2.3816 | 2.6189 | 2.6497 | 2.6874 | 2.7314 | 1.6385 | 1.9795 | 2.0035 | 2.0363 | 1.6385 | 2.0386 | 2.3082 | 2.3297 | 2.3584 | 2.5048
2021-09-24 16:00 | 2.1339 | 2.352 | 2.3823 | 2.4195 | 2.4628 | 1.6385 | 1.9788 | 2.0025 | 2.0349 | 1.6385 | 2.1339 | 2.4134 | 2.4347 | 2.4629 | 2.6141
2021-09-24 17:00 | 2.4768 | 2.7239 | 2.7561 | 2.7955 | 2.8414 | 2.1148 | 2.5441 | 2.5692 | 2.6035 | 2.1148 | 3.0484 | 3.4322 | 3.4547 | 3.4847 | 3.6881
2021-09-24 18:00 | 2.915 | 3.2021 | 3.238 | 3.282 | 3.3333 | 2.3625 | 2.8421 | 2.8701 | 2.9084 | 2.3625 | 3.4104 | 3.8397 | 3.8648 | 3.8983 | 4.1258
2021-09-24 19:00 | 2.8388 | 3.13 | 3.1709 | 3.221 | 3.2794 | 2.3816 | 2.8717 | 2.9036 | 2.9472 | 2.3816 | 3.2008 | 3.6137 | 3.6424 | 3.6804 | 3.902
2021-09-24 20:00 | 2.7626 | 3.0578 | 3.1036 | 3.1598 | 3.2252 | 2.3101 | 2.7943 | 2.83 | 2.8789 | 2.3101 | 3.2389 | 3.6629 | 3.695 | 3.7377 | 3.9668
2021-09-24 21:00 | 2.7055 | 2.998 | 3.0447 | 3.1018 | 3.1685 | 2.2291 | 2.6998 | 2.7362 | 2.7859 | 2.2291 | 3.3151 | 3.7487 | 3.7814 | 3.8249 | 4.0591
2021-09-24 22:00 | 2.6483 | 2.9306 | 2.9743 | 3.0277 | 3.09 | 1.9662 | 2.3848 | 2.4189 | 2.4654 | 1.9662 | 2.6674 | 3.0246 | 3.0552 | 3.0959 | 3.2911
2021-09-24 23:00 | 2.3816 | 2.6356 | 2.675 | 2.7231 | 2.7792 | 1.7719 | 2.1492 | 2.1798 | 2.2217 | 1.7719 | 2.4959 | 2.8281 | 2.8557 | 2.8923 | 3.0733
2021-09-25 | 2.1739 | 2.403 | 2.4375 | 2.4798 | 2.529 | 1.5174 | 1.8416 | 1.8686 | 1.9053 | 1.5174 | 1.9624 | 2.2286 | 2.2528 | 2.2849 | 2.4312
2021-09-25 01:00 | 2.0196 | 2.2277 | 2.2573 | 2.2936 | 2.3358 | 1.4099 | 1.7077 | 1.7308 | 1.7623 | 1.4099 | 1.9624 | 2.2218 | 2.2426 | 2.2701 | 2.411
2021-09-25 02:00 | 2.0196 | 2.2156 | 2.2391 | 2.2678 | 2.3012 | 1.2695 | 1.5331 | 1.5514 | 1.5764 | 1.2695 | 1.6957 | 1.9168 | 1.9333 | 1.9551 | 2.0744
2021-09-25 03:00 | 1.9243 | 2.1014 | 2.1189 | 2.1402 | 2.165 | 1.2384 | 1.4878 | 1.5013 | 1.5199 | 1.2384 | 1.6004 | 1.8026 | 1.8148 | 1.831 | 1.9384
2021-09-25 04:00 | 1.9815 | 2.1528 | 2.165 | 2.18 | 2.1975 | 1.2575 | 1.503 | 1.5125 | 1.5256 | 1.2575 | 1.5623 | 1.7531 | 1.7617 | 1.7731 | 1.8727
2021-09-25 05:00 | 2.0577 | 2.2307 | 2.2409 | 2.2534 | 2.268 | 1.3908 | 1.6576 | 1.6656 | 1.6765 | 1.3908 | 1.7719 | 1.9832 | 1.9904 | 1.9999 | 2.1087
2021-09-25 06:00 | 1.9434 | 2.1112 | 2.1231 | 2.1377 | 2.1548 | 1.4099 | 1.6826 | 1.6919 | 1.7046 | 1.4099 | 1.8862 | 2.1126 | 2.121 | 2.1321 | 2.2491
2021-09-25 07:00 | 1.8862 | 2.0589 | 2.0755 | 2.0958 | 2.1194 | 1.3908 | 1.6666 | 1.6796 | 1.6972 | 1.3908 | 1.6576 | 1.865 | 1.8766 | 1.892 | 2.0016
2021-09-25 08:00 | 1.6766 | 1.8471 | 1.8705 | 1.8991 | 1.9325 | 1.191 | 1.4403 | 1.4585 | 1.4835 | 1.191 | 1.2003 | 1.3663 | 1.3827 | 1.4045 | 1.4965
2021-09-25 09:00 | 1.4099 | 1.5748 | 1.6054 | 1.643 | 1.6868 | 1.0479 | 1.2815 | 1.3055 | 1.3381 | 1.0479 | 0.7621 | 0.88943 | 0.91092 | 0.93948 | 1.0155
2021-09-25 10:00 | 1.416 | 1.5922 | 1.6285 | 1.6729 | 1.7246 | 0.91452 | 1.1319 | 1.1602 | 1.1988 | 0.91452 | 0.80021 | 0.93953 | 0.96494 | 0.9987 | 1.0831
2021-09-25 11:00 | 1.467 | 1.6514 | 1.6899 | 1.737 | 1.792 | 0.91452 | 1.1351 | 1.1651 | 1.2061 | 0.91452 | 0.93358 | 1.0908 | 1.1178 | 1.1536 | 1.2478
2021-09-25 12:00 | 1.2384 | 1.4048 | 1.4427 | 1.4892 | 1.5433 | 0.89547 | 1.1118 | 1.1414 | 1.1818 | 0.89547 | 0.80021 | 0.94186 | 0.96845 | 1.0038 | 1.09
2021-09-25 13:00 | 1.2194 | 1.3793 | 1.4147 | 1.458 | 1.5086 | 0.89547 | 1.1082 | 1.1358 | 1.1735 | 0.89547 | 0.74305 | 0.87481 | 0.89961 | 0.93257 | 1.0128
2021-09-25 14:00 | 1.5242 | 1.7014 | 1.734 | 1.774 | 1.8206 | 1.0098 | 1.2393 | 1.2648 | 1.2995 | 1.0098 | 0.83831 | 0.97684 | 0.99971 | 1.0301 | 1.1125
2021-09-25 15:00 | 2.184 | 2.4066 | 2.4374 | 2.4751 | 2.5191 | 1.6683 | 2.0147 | 2.0387 | 2.0715 | 1.6683 | 1.8862 | 2.1388 | 2.1604 | 2.189 | 2.327
2021-09-25 16:00 | 2.3435 | 2.5771 | 2.6075 | 2.6447 | 2.688 | 1.8481 | 2.2264 | 2.2501 | 2.2825 | 1.8481 | 2.2673 | 2.5616 | 2.5829 | 2.6112 | 2.7696
2021-09-25 17:00 | 2.7626 | 3.031 | 3.0632 | 3.1025 | 3.1485 | 2.4098 | 2.8925 | 2.9176 | 2.9519 | 2.4098 | 3.2286 | 3.6325 | 3.655 | 3.685 | 3.8983
2021-09-25 18:00 | 3.2008 | 3.5091 | 3.5451 | 3.589 | 3.6403 | 2.7626 | 3.3147 | 3.3428 | 3.381 | 2.7626 | 3.7724 | 4.2419 | 4.2671 | 4.3006 | 4.548
2021-09-25 19:00 | 3.1627 | 3.4779 | 3.5189 | 3.5689 | 3.6273 | 2.7626 | 3.3218 | 3.3537 | 3.3973 | 2.7626 | 4.4964 | 5.0534 | 5.0821 | 5.1202 | 5.4129
2021-09-25 20:00 | 3.1056 | 3.4262 | 3.4721 | 3.5282 | 3.5936 | 2.6277 | 3.1695 | 3.2052 | 3.2541 | 2.6277 | 4.0582 | 4.5733 | 4.6054 | 4.6481 | 4.9223
2021-09-25 21:00 | 2.9531 | 3.2641 | 3.3108 | 3.3679 | 3.4346 | 2.4197 | 2.9249 | 2.9613 | 3.011 | 2.4197 | 3.5819 | 4.0451 | 4.0778 | 4.1213 | 4.3702
2021-09-25 22:00 | 2.8007 | 3.0944 | 3.138 | 3.1915 | 3.2537 | 2.153 | 2.6055 | 2.6395 | 2.686 | 2.153 | 3.4104 | 3.8504 | 3.8809 | 3.9216 | 4.1577
2021-09-25 23:00 | 2.5149 | 2.7789 | 2.8182 | 2.8664 | 2.9225 | 2.0396 | 2.4655 | 2.4962 | 2.538 | 2.0396 | 2.915 | 3.2939 | 3.3215 | 3.3581 | 3.5621
2021-09-26 | 2.2699 | 2.5062 | 2.5407 | 2.5829 | 2.6322 | 1.6766 | 2.0298 | 2.0567 | 2.0934 | 1.6766 | 2.4768 | 2.8003 | 2.8244 | 2.8566 | 3.0311
2021-09-26 01:00 | 2.1529 | 2.371 | 2.4006 | 2.4368 | 2.4791 | 1.4769 | 1.7868 | 1.8099 | 1.8415 | 1.4769 | 1.9815 | 2.243 | 2.2637 | 2.2913 | 2.4332
2021-09-26 02:00 | 2.1148 | 2.318 | 2.3414 | 2.3701 | 2.4036 | 1.3527 | 1.6314 | 1.6497 | 1.6747 | 1.3527 | 1.8481 | 2.0862 | 2.1027 | 2.1245 | 2.2522
2021-09-26 03:00 | 2.0005 | 2.1833 | 2.2007 | 2.222 | 2.2469 | 1.3527 | 1.6228 | 1.6364 | 1.6549 | 1.3527 | 1.7909 | 2.0143 | 2.0265 | 2.0427 | 2.1606
2021-09-26 04:00 | 2.0958 | 2.2756 | 2.2878 | 2.3029 | 2.3204 | 1.3337 | 1.593 | 1.6025 | 1.6156 | 1.3337 | 1.81 | 2.0284 | 2.037 | 2.0484 | 2.1615
2021-09-26 05:00 | 2.1529 | 2.333 | 2.3433 | 2.3558 | 2.3704 | 1.448 | 1.7251 | 1.7331 | 1.744 | 1.448 | 2.0577 | 2.3008 | 2.308 | 2.3175 | 2.442
2021-09-26 06:00 | 2.0958 | 2.275 | 2.2869 | 2.3015 | 2.3185 | 1.5242 | 1.8176 | 1.8269 | 1.8396 | 1.5242 | 1.9815 | 2.2185 | 2.2268 | 2.2379 | 2.3602
2021-09-26 07:00 | 1.8481 | 2.0179 | 2.0345 | 2.0548 | 2.0785 | 1.448 | 1.7342 | 1.7471 | 1.7648 | 1.448 | 1.9053 | 2.1402 | 2.1518 | 2.1673 | 2.2905
2021-09-26 08:00 | 1.7338 | 1.9085 | 1.9319 | 1.9605 | 1.9939 | 1.3685 | 1.65 | 1.6682 | 1.6931 | 1.3685 | 1.5242 | 1.7262 | 1.7426 | 1.7644 | 1.8742
2021-09-26 09:00 | 1.7909 | 1.9841 | 2.0148 | 2.0524 | 2.0961 | 1.4289 | 1.7317 | 1.7556 | 1.7883 | 1.4289 | 1.6957 | 1.9269 | 1.9484 | 1.9769 | 2.1043
2021-09-26 10:00 | 1.4861 | 1.6676 | 1.7038 | 1.7482 | 1.8 | 1.1622 | 1.4245 | 1.4528 | 1.4915 | 1.1622 | 1.6766 | 1.9135 | 1.9389 | 1.9726 | 2.1052
2021-09-26 11:00 | 2.0386 | 2.2655 | 2.304 | 2.3511 | 2.406 | 1.5242 | 1.8553 | 1.8854 | 1.9263 | 1.5242 | 1.4861 | 1.7048 | 1.7318 | 1.7676 | 1.8921
2021-09-26 12:00 | 2.0767 | 2.3054 | 2.3433 | 2.3898 | 2.4439 | 1.5052 | 1.8321 | 1.8617 | 1.9021 | 1.5052 | 1.1813 | 1.3653 | 1.3919 | 1.4272 | 1.5344
2021-09-26 13:00 | 2.0577 | 2.2799 | 2.3153 | 2.3587 | 2.4092 | 1.4861 | 1.8059 | 1.8336 | 1.8713 | 1.4861 | 1.1813 | 1.3618 | 1.3866 | 1.4195 | 1.5239
2021-09-26 14:00 | 1.6957 | 1.8856 | 1.9183 | 1.9582 | 2.0048 | 1.1622 | 1.4194 | 1.4448 | 1.4796 | 1.1622 | 0.74305 | 0.87098 | 0.89385 | 0.92423 | 1.0014
2021-09-26 15:00 | 1.9243 | 2.1277 | 2.1585 | 2.1962 | 2.2401 | 1.3403 | 1.6272 | 1.6512 | 1.684 | 1.3403 | 1.0669 | 1.2284 | 1.2499 | 1.2786 | 1.3716
2021-09-26 16:00 | 2.3816 | 2.6181 | 2.6484 | 2.6856 | 2.7289 | 1.865 | 2.2464 | 2.2701 | 2.3024 | 1.865 | 2.1339 | 2.4134 | 2.4347 | 2.4629 | 2.6141
2021-09-26 17:00 | 2.9341 | 3.2152 | 3.2474 | 3.2868 | 3.3327 | 2.5205 | 3.0234 | 3.0485 | 3.0827 | 2.5205 | 3.6962 | 4.152 | 4.1746 | 4.2045 | 4.4435
2021-09-26 18:00 | 3.5057 | 3.8366 | 3.8726 | 3.9165 | 3.9678 | 2.9722 | 3.5623 | 3.5903 | 3.6286 | 2.9722 | 5.0489 | 5.6605 | 5.6857 | 5.7191 | 6.0367
2021-09-26 19:00 | 3.4866 | 3.8259 | 3.8668 | 3.9169 | 3.9753 | 2.9531 | 3.5469 | 3.5788 | 3.6224 | 2.9531 | 4.3059 | 4.8417 | 4.8703 | 4.9084 | 5.1907
2021-09-26 20:00 | 3.258 | 3.59 | 3.6358 | 3.6919 | 3.7574 | 2.8769 | 3.4639 | 3.4997 | 3.5485 | 2.8769 | 4.6679 | 5.2508 | 5.2829 | 5.3256 | 5.6333
2021-09-26 21:00 | 3.2199 | 3.5507 | 3.5973 | 3.6545 | 3.7211 | 2.6578 | 3.2062 | 3.2426 | 3.2924 | 2.6578 | 4.2487 | 4.7862 | 4.8189 | 4.8623 | 5.1479
2021-09-26 22:00 | 3.0484 | 3.3605 | 3.4041 | 3.4575 | 3.5198 | 2.3816 | 2.8755 | 2.9096 | 2.9561 | 2.3816 | 3.9248 | 4.422 | 4.4526 | 4.4932 | 4.7576
2021-09-26 23:00 | 2.6674 | 2.9427 | 2.982 | 3.0301 | 3.0863 | 2.0132 | 2.4343 | 2.465 | 2.5069 | 2.0132 | 2.7626 | 3.1245 | 3.1521 | 3.1887 | 3.3844
2021-09-27 | 2.4768 | 2.7285 | 2.763 | 2.8053 | 2.8545 | 1.6766 | 2.0298 | 2.0567 | 2.0934 | 1.6766 | 2.6674 | 3.012 | 3.0362 | 3.0683 | 3.2533
2021-09-27 01:00 | 2.2673 | 2.4938 | 2.5234 | 2.5597 | 2.6019 | 1.5414 | 1.863 | 1.8861 | 1.9177 | 1.5414 | 2.3054 | 2.6029 | 2.6237 | 2.6512 | 2.8109
2021-09-27 02:00 | 2.2291 | 2.4408 | 2.4642 | 2.4929 | 2.5264 | 1.4763 | 1.7774 | 1.7957 | 1.8206 | 1.4763 | 2.0196 | 2.2768 | 2.2932 | 2.315 | 2.4522
2021-09-27 03:00 | 2.172 | 2.3675 | 2.3849 | 2.4063 | 2.4311 | 1.448 | 1.7354 | 1.7489 | 1.7675 | 1.448 | 2.3435 | 2.6283 | 2.6405 | 2.6567 | 2.8049
2021-09-27 04:00 | 2.191 | 2.3779 | 2.3902 | 2.4052 | 2.4227 | 1.5492 | 1.8476 | 1.8571 | 1.8702 | 1.5492 | 2.5721 | 2.8753 | 2.8838 | 2.8953 | 3.0503
2021-09-27 05:00 | 2.3237 | 2.5165 | 2.5267 | 2.5392 | 2.5538 | 1.7552 | 2.088 | 2.096 | 2.1069 | 1.7552 | 2.6864 | 2.9995 | 3.0066 | 3.0162 | 3.1752
2021-09-27 06:00 | 2.534 | 2.7457 | 2.7577 | 2.7723 | 2.7893 | 1.9624 | 2.3353 | 2.3446 | 2.3573 | 1.9624 | 2.915 | 3.2559 | 3.2643 | 3.2754 | 3.4489
2021-09-27 07:00 | 2.6102 | 2.8367 | 2.8533 | 2.8736 | 2.8972 | 1.7909 | 2.1393 | 2.1522 | 2.1699 | 1.7909 | 2.6483 | 2.9659 | 2.9776 | 2.993 | 3.157
2021-09-27 08:00 | 2.3435 | 2.5635 | 2.5869 | 2.6155 | 2.6489 | 1.6406 | 1.9714 | 1.9896 | 2.0145 | 1.6406 | 1.7909 | 2.0226 | 2.039 | 2.0608 | 2.1853
2021-09-27 09:00 | 1.9434 | 2.1479 | 2.1786 | 2.2161 | 2.2599 | 1.2815 | 1.5576 | 1.5815 | 1.6142 | 1.2815 | 1.2765 | 1.4611 | 1.4826 | 1.5111 | 1.6155
2021-09-27 10:00 | 1.9624 | 2.1793 | 2.2156 | 2.2599 | 2.3117 | 1.3527 | 1.6496 | 1.6779 | 1.7165 | 1.3527 | 1.2003 | 1.3841 | 1.4096 | 1.4433 | 1.5497
2021-09-27 11:00 | 2.1529 | 2.3883 | 2.4268 | 2.4739 | 2.5288 | 1.4289 | 1.7428 | 1.7728 | 1.8138 | 1.4289 | 1.6195 | 1.853 | 1.88 | 1.9158 | 2.0477
2021-09-27 12:00 | 2.191 | 2.4282 | 2.4662 | 2.5126 | 2.5668 | 1.5623 | 1.8996 | 1.9292 | 1.9696 | 1.5623 | 1.6385 | 1.8734 | 1.9 | 1.9354 | 2.0677
2021-09-27 13:00 | 2.172 | 2.4028 | 2.4382 | 2.4815 | 2.532 | 1.5242 | 1.851 | 1.8786 | 1.9163 | 1.5242 | 1.5623 | 1.7852 | 1.81 | 1.843 | 1.9683
2021-09-27 14:00 | 2.172 | 2.3973 | 2.43 | 2.4699 | 2.5165 | 1.5052 | 1.8245 | 1.85 | 1.8847 | 1.5052 | 1.6195 | 1.8449 | 1.8678 | 1.8982 | 2.0235
2021-09-27 15:00 | 1.9434 | 2.1481 | 2.1789 | 2.2166 | 2.2606 | 1.3146 | 1.5968 | 1.6209 | 1.6537 | 1.3146 | 1.2384 | 1.4189 | 1.4405 | 1.4692 | 1.5715
2021-09-27 16:00 | 2.1339 | 2.352 | 2.3823 | 2.4195 | 2.4628 | 1.6004 | 1.9338 | 1.9575 | 1.9899 | 1.6004 | 2.172 | 2.4557 | 2.477 | 2.5053 | 2.6585
2021-09-27 17:00 | 2.6483 | 2.9082 | 2.9403 | 2.9797 | 3.0256 | 2.1529 | 2.5891 | 2.6142 | 2.6485 | 2.1529 | 3.0865 | 3.4745 | 3.4971 | 3.527 | 3.7325
2021-09-27 18:00 | 3.0675 | 3.3658 | 3.4018 | 3.4458 | 3.497 | 2.4959 | 2.9996 | 3.0277 | 3.0659 | 2.4959 | 3.6009 | 4.0514 | 4.0766 | 4.11 | 4.348
2021-09-27 19:00 | 3.1056 | 3.4165 | 3.4575 | 3.5075 | 3.5659 | 2.4959 | 3.0067 | 3.0386 | 3.0822 | 2.4959 | 3.7534 | 4.2277 | 4.2563 | 4.2944 | 4.5463
2021-09-27 20:00 | 3.0484 | 3.3648 | 3.4107 | 3.4668 | 3.5322 | 2.4006 | 2.9012 | 2.937 | 2.9858 | 2.4006 | 3.8867 | 4.3827 | 4.4149 | 4.4576 | 4.7223
2021-09-27 21:00 | 2.915 | 3.2231 | 3.2698 | 3.327 | 3.3936 | 2.2512 | 2.7259 | 2.7623 | 2.812 | 2.2512 | 3.4676 | 3.9181 | 3.9508 | 3.9943 | 4.2369
2021-09-27 22:00 | 2.5721 | 2.8488 | 2.8924 | 2.9458 | 3.0081 | 2.0288 | 2.4588 | 2.4928 | 2.5393 | 2.0288 | 2.9913 | 3.3846 | 3.4152 | 3.4558 | 3.6688
2021-09-27 23:00 | 2.3244 | 2.5742 | 2.6135 | 2.6617 | 2.7178 | 1.7253 | 2.0941 | 2.1248 | 2.1667 | 1.7253 | 2.4578 | 2.7858 | 2.8133 | 2.8499 | 3.0289
2021-09-28 | 2.1148 | 2.3396 | 2.3741 | 2.4163 | 2.4656 | 1.5154 | 1.8394 | 1.8663 | 1.903 | 1.5154 | 2.0386 | 2.3133 | 2.3375 | 2.3696 | 2.5201
2021-09-28 01:00 | 2.0767 | 2.2891 | 2.3187 | 2.355 | 2.3972 | 1.3908 | 1.6852 | 1.7083 | 1.7398 | 1.3908 | 1.8481 | 2.0948 | 2.1155 | 2.1431 | 2.2777
2021-09-28 02:00 | 1.9815 | 2.1747 | 2.1981 | 2.2268 | 2.2603 | 1.2858 | 1.5523 | 1.5706 | 1.5956 | 1.2858 | 1.7338 | 1.9592 | 1.9756 | 1.9975 | 2.1189
2021-09-28 03:00 | 2.0196 | 2.2038 | 2.2212 | 2.2425 | 2.2674 | 1.2575 | 1.5103 | 1.5238 | 1.5424 | 1.2575 | 1.8862 | 2.1202 | 2.1324 | 2.1486 | 2.2717
2021-09-28 04:00 | 2.0577 | 2.2346 | 2.2469 | 2.2619 | 2.2794 | 1.3614 | 1.6257 | 1.6353 | 1.6483 | 1.3614 | 2.0005 | 2.2401 | 2.2487 | 2.2601 | 2.3837
2021-09-28 05:00 | 2.1529 | 2.333 | 2.3433 | 2.3558 | 2.3704 | 1.5864 | 1.8887 | 1.8966 | 1.9075 | 1.5864 | 2.3244 | 2.5972 | 2.6044 | 2.6139 | 2.7531
2021-09-28 06:00 | 2.3244 | 2.5206 | 2.5325 | 2.5471 | 2.5642 | 1.81 | 2.1552 | 2.1645 | 2.1772 | 1.81 | 2.6102 | 2.9172 | 2.9255 | 2.9366 | 3.0934
2021-09-28 07:00 | 2.7055 | 2.939 | 2.9556 | 2.9759 | 2.9996 | 1.829 | 2.1843 | 2.1973 | 2.2149 | 1.829 | 3.5247 | 3.9399 | 3.9515 | 3.9669 | 4.1791
2021-09-28 08:00 | 2.1762 | 2.3838 | 2.4072 | 2.4358 | 2.4692 | 1.7161 | 2.0606 | 2.0788 | 2.1038 | 1.7161 | 2.5911 | 2.9119 | 2.9283 | 2.9501 | 3.1185
2021-09-28 09:00 | 2.4197 | 2.6596 | 2.6903 | 2.7278 | 2.7716 | 1.6766 | 2.0243 | 2.0482 | 2.0809 | 1.6766 | 1.9815 | 2.2445 | 2.2659 | 2.2945 | 2.4376
2021-09-28 10:00 | 2.191 | 2.4249 | 2.4612 | 2.5056 | 2.5573 | 1.6385 | 1.9872 | 2.0155 | 2.0541 | 1.6385 | 1.6195 | 1.8499 | 1.8753 | 1.9091 | 2.0385
2021-09-28 11:00 | 2.0767 | 2.3064 | 2.3449 | 2.392 | 2.447 | 1.5242 | 1.8553 | 1.8854 | 1.9263 | 1.5242 | 1.5242 | 1.7472 | 1.7741 | 1.8099 | 1.9366
2021-09-28 12:00 | 1.8672 | 2.0802 | 2.1182 | 2.1646 | 2.2188 | 1.2384 | 1.517 | 1.5466 | 1.587 | 1.2384 | 0.80021 | 0.94186 | 0.96845 | 1.0038 | 1.09
2021-09-28 13:00 | 1.6576 | 1.8501 | 1.8855 | 1.9288 | 1.9793 | 1.1432 | 1.4008 | 1.4284 | 1.4661 | 1.1432 | 0.85737 | 1.0018 | 1.0266 | 1.0596 | 1.1461
2021-09-28 14:00 | 1.9624 | 2.1722 | 2.2048 | 2.2448 | 2.2914 | 1.3527 | 1.6445 | 1.6699 | 1.7047 | 1.3527 | 0.93358 | 1.0827 | 1.1056 | 1.136 | 1.2236
2021-09-28 15:00 | 1.9624 | 2.1686 | 2.1994 | 2.2371 | 2.2811 | 1.2564 | 1.528 | 1.552 | 1.5848 | 1.2564 | 1.4099 | 1.6095 | 1.631 | 1.6597 | 1.7715
2021-09-28 16:00 | 2.0767 | 2.2906 | 2.3209 | 2.3581 | 2.4014 | 1.4861 | 1.7988 | 1.8225 | 1.8548 | 1.4861 | 1.6957 | 1.9264 | 1.9477 | 1.976 | 2.103
2021-09-28 17:00 | 2.453 | 2.6984 | 2.7306 | 2.7699 | 2.8159 | 1.9624 | 2.3641 | 2.3892 | 2.4234 | 1.9624 | 3.1056 | 3.4957 | 3.5182 | 3.5482 | 3.7547
2021-09-28 18:00 | 2.7817 | 3.0588 | 3.0947 | 3.1387 | 3.19 | 2.2482 | 2.707 | 2.735 | 2.7733 | 2.2482 | 3.0865 | 3.4797 | 3.5049 | 3.5384 | 3.7481
2021-09-28 19:00 | 2.8007 | 3.089 | 3.1299 | 3.18 | 3.2384 | 2.2673 | 2.7366 | 2.7685 | 2.8121 | 2.2673 | 3.277 | 3.6984 | 3.727 | 3.7651 | 3.9908
2021-09-28 20:00 | 2.6864 | 2.9759 | 3.0217 | 3.0779 | 3.1433 | 2.0958 | 2.5411 | 2.5768 | 2.6257 | 2.0958 | 3.3914 | 3.8323 | 3.8644 | 3.9071 | 4.1446
2021-09-28 21:00 | 2.5721 | 2.8547 | 2.9014 | 2.9585 | 3.0252 | 2.0005 | 2.4297 | 2.4661 | 2.5159 | 2.0005 | 3.0294 | 3.4311 | 3.4639 | 3.5073 | 3.7258
2021-09-28 22:00 | 2.3435 | 2.6031 | 2.6468 | 2.7002 | 2.7625 | 1.8534 | 2.2516 | 2.2856 | 2.3321 | 1.8534 | 3.0294 | 3.4269 | 3.4575 | 3.4981 | 3.7133
2021-09-28 23:00 | 2.1529 | 2.39 | 2.4293 | 2.4775 | 2.5336 | 1.5433 | 1.8791 | 1.9097 | 1.9516 | 1.5433 | 2.4006 | 2.7223 | 2.7498 | 2.7864 | 2.9622
2021-09-29 | 1.9719 | 2.1861 | 2.2206 | 2.2628 | 2.3121 | 1.3372 | 1.6287 | 1.6557 | 1.6924 | 1.3372 | 1.81 | 2.0592 | 2.0834 | 2.1155 | 2.2534
2021-09-29 01:00 | 1.7719 | 1.9616 | 1.9912 | 2.0275 | 2.0697 | 1.2432 | 1.5107 | 1.5338 | 1.5654 | 1.2432 | 1.5242 | 1.7349 | 1.7556 | 1.7832 | 1.8999
2021-09-29 02:00 | 1.7528 | 1.929 | 1.9525 | 1.9812 | 2.0147 | 1.1432 | 1.3838 | 1.4021 | 1.4271 | 1.1432 | 1.4861 | 1.684 | 1.7004 | 1.7222 | 1.83
2021-09-29 03:00 | 1.7147 | 1.8763 | 1.8937 | 1.915 | 1.9398 | 1.1432 | 1.3752 | 1.3888 | 1.4073 | 1.1432 | 1.4289 | 1.6121 | 1.6243 | 1.6405 | 1.7384
2021-09-29 04:00 | 1.7147 | 1.8662 | 1.8785 | 1.8935 | 1.911 | 1.1813 | 1.4129 | 1.4225 | 1.4355 | 1.1813 | 1.5242 | 1.7108 | 1.7194 | 1.7308 | 1.8282
2021-09-29 05:00 | 1.8481 | 2.0055 | 2.0158 | 2.0283 | 2.0429 | 1.3146 | 1.5676 | 1.5756 | 1.5865 | 1.3146 | 1.7719 | 1.9832 | 1.9904 | 1.9999 | 2.1087
2021-09-29 06:00 | 2.005 | 2.1774 | 2.1893 | 2.2039 | 2.221 | 1.5242 | 1.8176 | 1.8269 | 1.8396 | 1.5242 | 2.0005 | 2.2396 | 2.248 | 2.2591 | 2.3824
2021-09-29 07:00 | 2.3054 | 2.5092 | 2.5258 | 2.5461 | 2.5697 | 1.6744 | 2.0016 | 2.0145 | 2.0322 | 1.6744 | 2.3816 | 2.6695 | 2.6811 | 2.6966 | 2.846
2021-09-29 08:00 | 2.5282 | 2.762 | 2.7854 | 2.814 | 2.8474 | 1.9243 | 2.3066 | 2.3248 | 2.3497 | 1.9243 | 2.5721 | 2.8907 | 2.9071 | 2.9289 | 3.0963
2021-09-29 09:00 | 2.6674 | 2.9257 | 2.9564 | 2.9939 | 3.0377 | 1.9624 | 2.3619 | 2.3859 | 2.4185 | 1.9624 | 2.896 | 3.2607 | 3.2822 | 3.3108 | 3.5041
2021-09-29 10:00 | 2.7817 | 3.0595 | 3.0957 | 3.1401 | 3.1919 | 2.2083 | 2.6604 | 2.6887 | 2.7273 | 2.2083 | 3.0675 | 3.459 | 3.4844 | 3.5182 | 3.7272
2021-09-29 11:00 | 2.896 | 3.1866 | 3.2251 | 3.2722 | 3.3271 | 2.2863 | 2.7557 | 2.7857 | 2.8267 | 2.2863 | 3.2389 | 3.6527 | 3.6796 | 3.7154 | 3.9363
2021-09-29 12:00 | 2.915 | 3.206 | 3.244 | 3.2904 | 3.3446 | 2.3244 | 2.7999 | 2.8295 | 2.8699 | 2.3244 | 3.7343 | 4.2024 | 4.229 | 4.2643 | 4.5118
2021-09-29 13:00 | 2.8198 | 3.0987 | 3.1341 | 3.1774 | 3.228 | 2.2863 | 2.7513 | 2.7789 | 2.8166 | 2.2863 | 3.5057 | 3.9448 | 3.9696 | 4.0025 | 4.2347
2021-09-29 14:00 | 2.6102 | 2.8681 | 2.9008 | 2.9407 | 2.9873 | 2.0767 | 2.4998 | 2.5252 | 2.56 | 2.0767 | 2.6674 | 3.0094 | 3.0322 | 3.0626 | 3.2456
2021-09-29 15:00 | 2.7245 | 2.9874 | 3.0182 | 3.0559 | 3.0998 | 2.1148 | 2.5422 | 2.5662 | 2.599 | 2.1148 | 2.7245 | 3.0704 | 3.0919 | 3.1206 | 3.3047
2021-09-29 16:00 | 2.8579 | 3.1298 | 3.1601 | 3.1973 | 3.2407 | 2.1928 | 2.6336 | 2.6573 | 2.6897 | 2.1928 | 2.9465 | 3.3164 | 3.3376 | 3.3659 | 3.5617
2021-09-29 17:00 | 2.9332 | 3.2143 | 3.2464 | 3.2858 | 3.3317 | 2.534 | 3.0393 | 3.0644 | 3.0987 | 2.534 | 3.8867 | 4.3638 | 4.3863 | 4.4163 | 4.6657
2021-09-29 18:00 | 3.0904 | 3.3905 | 3.4265 | 3.4704 | 3.5217 | 2.6864 | 3.2247 | 3.2527 | 3.291 | 2.6864 | 4.2678 | 4.7924 | 4.8176 | 4.8511 | 5.1257
2021-09-29 19:00 | 3.1056 | 3.4165 | 3.4575 | 3.5075 | 3.5659 | 2.6864 | 3.2318 | 3.2637 | 3.3073 | 2.6864 | 3.9058 | 4.3971 | 4.4257 | 4.4638 | 4.7241
2021-09-29 20:00 | 2.896 | 3.201 | 3.2469 | 3.303 | 3.3685 | 2.4959 | 3.0137 | 3.0495 | 3.0983 | 2.4959 | 3.7152 | 4.1922 | 4.2243 | 4.267 | 4.5223
2021-09-29 21:00 | 2.6674 | 2.9571 | 3.0037 | 3.0609 | 3.1275 | 2.2641 | 2.7411 | 2.7775 | 2.8273 | 2.2641 | 3.3723 | 3.8122 | 3.845 | 3.8884 | 4.1258
2021-09-29 22:00 | 2.4152 | 2.6802 | 2.7239 | 2.7773 | 2.8396 | 1.9799 | 2.4011 | 2.4351 | 2.4816 | 1.9799 | 3.3914 | 3.8292 | 3.8598 | 3.9004 | 4.1354
2021-09-29 23:00 | 2.172 | 2.4105 | 2.4498 | 2.4979 | 2.5541 | 1.7383 | 2.1095 | 2.1402 | 2.1821 | 1.7383 | 2.3816 | 2.7011 | 2.7286 | 2.7653 | 2.94
2021-09-30 | 1.902 | 2.111 | 2.1455 | 2.1877 | 2.237 | 1.448 | 1.7597 | 1.7866 | 1.8233 | 1.448 | 2.0386 | 2.3133 | 2.3375 | 2.3696 | 2.5201
2021-09-30 01:00 | 1.8862 | 2.0844 | 2.114 | 2.1503 | 2.1925 | 1.3003 | 1.5783 | 1.6014 | 1.6329 | 1.3003 | 1.6004 | 1.8195 | 1.8403 | 1.8679 | 1.9888
2021-09-30 02:00 | 1.7331 | 1.9079 | 1.9313 | 1.96 | 1.9935 | 1.2228 | 1.4779 | 1.4962 | 1.5212 | 1.2228 | 1.5623 | 1.7686 | 1.7851 | 1.8069 | 1.9189
2021-09-30 03:00 | 1.7522 | 1.9166 | 1.934 | 1.9553 | 1.9802 | 1.1813 | 1.4202 | 1.4338 | 1.4524 | 1.1813 | 1.467 | 1.6544 | 1.6666 | 1.6828 | 1.7828
2021-09-30 04:00 | 1.7909 | 1.9481 | 1.9603 | 1.9753 | 1.9928 | 1.2171 | 1.4552 | 1.4648 | 1.4778 | 1.2171 | 1.7147 | 1.9225 | 1.9311 | 1.9425 | 2.0504
2021-09-30 05:00 | 1.9265 | 2.0897 | 2.0999 | 2.1125 | 2.1271 | 1.3639 | 1.6258 | 1.6338 | 1.6447 | 1.3639 | 1.8481 | 2.0679 | 2.0751 | 2.0846 | 2.1976
2021-09-30 06:00 | 2.1339 | 2.3159 | 2.3278 | 2.3424 | 2.3595 | 1.6385 | 1.9526 | 1.962 | 1.9747 | 1.6385 | 2.191 | 2.4514 | 2.4597 | 2.4708 | 2.6046
2021-09-30 07:00 | 2.3816 | 2.5911 | 2.6077 | 2.6279 | 2.6516 | 1.7528 | 2.0943 | 2.1072 | 2.1249 | 1.7528 | 2.553 | 2.8601 | 2.8717 | 2.8871 | 3.0459
2021-09-30 08:00 | 2.3625 | 2.584 | 2.6074 | 2.636 | 2.6694 | 1.7462 | 2.0962 | 2.1144 | 2.1394 | 1.7462 | 2.6674 | 2.9966 | 3.013 | 3.0347 | 3.2074
2021-09-30 09:00 | 2.4768 | 2.721 | 2.7517 | 2.7892 | 2.833 | 1.8481 | 2.2269 | 2.2508 | 2.2835 | 1.8481 | 2.8579 | 3.2184 | 3.2399 | 3.2684 | 3.4597
2021-09-30 10:00 | 2.6674 | 2.9366 | 2.9729 | 3.0173 | 3.0691 | 2.0767 | 2.5049 | 2.5332 | 2.5718 | 2.0767 | 2.5911 | 2.9297 | 2.9551 | 2.9889 | 3.1717
2021-09-30 11:00 | 2.1415 | 2.3761 | 2.4146 | 2.4617 | 2.5166 | 1.7147 | 2.0804 | 2.1104 | 2.1514 | 1.7147 | 1.7528 | 2.0012 | 2.0282 | 2.064 | 2.2032
2021-09-30 12:00 | 2.3625 | 2.6124 | 2.6504 | 2.6968 | 2.751 | 1.6576 | 2.0121 | 2.0417 | 2.0821 | 1.6576 | 1.6385 | 1.8734 | 1.9 | 1.9354 | 2.0677
2021-09-30 13:00 | 2.0005 | 2.2185 | 2.2539 | 2.2973 | 2.3478 | 1.467 | 1.7834 | 1.8111 | 1.8487 | 1.467 | 1.5052 | 1.7217 | 1.7465 | 1.7795 | 1.9016
2021-09-30 14:00 | 2.0958 | 2.3155 | 2.3481 | 2.3881 | 2.4346 | 1.5242 | 1.847 | 1.8725 | 1.9072 | 1.5242 | 1.6576 | 1.8872 | 1.9101 | 1.9405 | 2.068
2021-09-30 15:00 | 2.3143 | 2.5467 | 2.5775 | 2.6152 | 2.6591 | 1.7372 | 2.0961 | 2.1201 | 2.1529 | 1.7372 | 2.096 | 2.3719 | 2.3935 | 2.4222 | 2.5717
2021-09-30 16:00 | 2.3435 | 2.5771 | 2.6075 | 2.6447 | 2.688 | 1.7528 | 2.1139 | 2.1376 | 2.1699 | 1.7528 | 2.3054 | 2.604 | 2.6252 | 2.6535 | 2.814
2021-09-30 17:00 | 2.5277 | 2.7786 | 2.8107 | 2.8501 | 2.896 | 2.172 | 2.6116 | 2.6367 | 2.671 | 2.172 | 2.8388 | 3.1993 | 3.2218 | 3.2518 | 3.4437
2021-09-30 18:00 | 2.9722 | 3.2635 | 3.2994 | 3.3434 | 3.3947 | 2.553 | 3.0671 | 3.0952 | 3.1334 | 2.553 | 3.4485 | 3.882 | 3.9072 | 3.9406 | 4.1702
2021-09-30 19:00 | 2.9341 | 3.2323 | 3.2732 | 3.3233 | 3.3817 | 2.534 | 3.0517 | 3.0836 | 3.1272 | 2.534 | 3.5819 | 4.0371 | 4.0658 | 4.1039 | 4.3463
2021-09-30 20:00 | 2.8388 | 3.1396 | 3.1855 | 3.2416 | 3.3071 | 2.3244 | 2.8112 | 2.8469 | 2.8958 | 2.3244 | 3.9439 | 4.4463 | 4.4784 | 4.5211 | 4.7889
2021-09-30 21:00 | 2.7245 | 3.0185 | 3.0651 | 3.1223 | 3.1889 | 2.2863 | 2.7673 | 2.8037 | 2.8535 | 2.2863 | 3.1627 | 3.5793 | 3.6121 | 3.6555 | 3.8814
2021-09-30 22:00 | 2.4959 | 2.7669 | 2.8105 | 2.8639 | 2.9262 | 1.983 | 2.4047 | 2.4387 | 2.4852 | 1.983 | 2.8579 | 3.2364 | 3.267 | 3.3076 | 3.5133
2021-09-30 23:00 | 2.3244 | 2.5742 | 2.6135 | 2.6617 | 2.7178 | 1.6766 | 2.0366 | 2.0673 | 2.1092 | 1.6766 | 2.4768 | 2.8069 | 2.8345 | 2.8711 | 3.0511
2021-10-01 | 2.1148 | 2.3396 | 2.3741 | 2.4163 | 2.4656 | 1.4861 | 1.8047 | 1.8316 | 1.8683 | 1.4861 | 2.0005 | 2.2709 | 2.2951 | 2.3272 | 2.4756
2021-10-01 01:00 | 1.9243 | 2.1253 | 2.155 | 2.1912 | 2.2335 | 1.3908 | 1.6852 | 1.7083 | 1.7398 | 1.3908 | 1.81 | 2.0524 | 2.0732 | 2.1008 | 2.2332
2021-10-01 02:00 | 1.829 | 2.0109 | 2.0344 | 2.0631 | 2.0965 | 1.2575 | 1.5189 | 1.5371 | 1.5621 | 1.2575 | 1.7147 | 1.938 | 1.9544 | 1.9763 | 2.0966
2021-10-01 03:00 | 1.8672 | 2.04 | 2.0574 | 2.0788 | 2.1036 | 1.2003 | 1.4427 | 1.4563 | 1.4749 | 1.2003 | 1.6766 | 1.8873 | 1.8995 | 1.9157 | 2.0273
2021-10-01 04:00 | 1.8862 | 2.0504 | 2.0627 | 2.0777 | 2.0952 | 1.2379 | 1.4798 | 1.4894 | 1.5024 | 1.2379 | 1.829 | 2.0495 | 2.0581 | 2.0695 | 2.1837
2021-10-01 05:00 | 1.9624 | 2.1283 | 2.1386 | 2.1511 | 2.1657 | 1.3718 | 1.6351 | 1.6431 | 1.654 | 1.3718 | 1.8672 | 2.0891 | 2.0962 | 2.1058 | 2.2198
2021-10-01 06:00 | 2.0005 | 2.1726 | 2.1845 | 2.1992 | 2.2162 | 1.5242 | 1.8176 | 1.8269 | 1.8396 | 1.5242 | 2.2291 | 2.4937 | 2.5021 | 2.5132 | 2.649
2021-10-01 07:00 | 2.0767 | 2.2636 | 2.2802 | 2.3004 | 2.3241 | 1.3527 | 1.6216 | 1.6346 | 1.6522 | 1.3527 | 1.6385 | 1.8438 | 1.8554 | 1.8709 | 1.9794
2021-10-01 08:00 | 1.9624 | 2.1541 | 2.1775 | 2.2061 | 2.2395 | 1.3337 | 1.6088 | 1.6271 | 1.652 | 1.3337 | 1.4099 | 1.5992 | 1.6156 | 1.6374 | 1.7409
2021-10-01 09:00 | 1.6025 | 1.7817 | 1.8124 | 1.8499 | 1.8937 | 0.96327 | 1.1816 | 1.2055 | 1.2382 | 0.96327 | 0.87642 | 1.0165 | 1.038 | 1.0665 | 1.1488
2021-10-01 10:00 | 1.5623 | 1.7494 | 1.7857 | 1.8301 | 1.8819 | 0.93358 | 1.1544 | 1.1827 | 1.2214 | 0.93358 | 0.91452 | 1.0666 | 1.092 | 1.1257 | 1.2164
2021-10-01 11:00 | 1.7338 | 1.938 | 1.9765 | 2.0236 | 2.0785 | 1.1622 | 1.4277 | 1.4577 | 1.4987 | 1.1622 | 1.2575 | 1.4507 | 1.4777 | 1.5135 | 1.6255
2021-10-01 12:00 | 2.4387 | 2.6943 | 2.7323 | 2.7787 | 2.8329 | 1.8672 | 2.2597 | 2.2893 | 2.3297 | 1.8672 | 2.1339 | 2.4239 | 2.4505 | 2.4858 | 2.6454
2021-10-01 13:00 | 2.4768 | 2.7303 | 2.7657 | 2.809 | 2.8595 | 1.83 | 2.2122 | 2.2398 | 2.2775 | 1.83 | 2.2291 | 2.5262 | 2.551 | 2.584 | 2.746
2021-10-01 14:00 | 2.3054 | 2.5406 | 2.5733 | 2.6132 | 2.6598 | 1.7528 | 2.1171 | 2.1426 | 2.1773 | 1.7528 | 2.915 | 3.2846 | 3.3075 | 3.3379 | 3.5344
2021-10-01 15:00 | 2.1148 | 2.3324 | 2.3632 | 2.4009 | 2.4448 | 1.5623 | 1.8894 | 1.9135 | 1.9463 | 1.5623 | 1.9434 | 2.2023 | 2.2239 | 2.2525 | 2.3937
2021-10-01 16:00 | 2.191 | 2.4134 | 2.4437 | 2.4809 | 2.5242 | 1.5814 | 1.9113 | 1.935 | 1.9673 | 1.5814 | 2.1339 | 2.4134 | 2.4347 | 2.4629 | 2.6141
2021-10-01 17:00 | 2.534 | 2.7854 | 2.8175 | 2.8569 | 2.9028 | 2.086 | 2.51 | 2.5351 | 2.5694 | 2.086 | 3.2961 | 3.7074 | 3.73 | 3.7599 | 3.9769
2021-10-01 18:00 | 2.8007 | 3.0793 | 3.1152 | 3.1592 | 3.2105 | 2.4197 | 2.9096 | 2.9376 | 2.9759 | 2.4197 | 3.7915 | 4.2631 | 4.2883 | 4.3217 | 4.5702
2021-10-01 19:00 | 2.8007 | 3.089 | 3.1299 | 3.18 | 3.2384 | 2.3435 | 2.8266 | 2.8586 | 2.9021 | 2.3435 | 3.6581 | 4.1218 | 4.1505 | 4.1886 | 4.4352
2021-10-01 20:00 | 2.7626 | 3.0578 | 3.1036 | 3.1598 | 3.2252 | 2.3625 | 2.8562 | 2.8919 | 2.9408 | 2.3625 | 3.258 | 3.6841 | 3.7162 | 3.7589 | 3.989
2021-10-01 21:00 | 2.5966 | 2.881 | 2.9277 | 2.9848 | 3.0515 | 2.191 | 2.6548 | 2.6912 | 2.7409 | 2.191 | 3.2008 | 3.6217 | 3.6544 | 3.6979 | 3.9258
2021-10-01 22:00 | 2.4387 | 2.7055 | 2.7491 | 2.8025 | 2.8648 | 1.9446 | 2.3593 | 2.3933 | 2.4398 | 1.9446 | 2.6102 | 2.9611 | 2.9917 | 3.0323 | 3.2244
2021-10-01 23:00 | 2.2863 | 2.5333 | 2.5726 | 2.6208 | 2.6769 | 1.738 | 2.1091 | 2.1398 | 2.1817 | 1.738 | 2.2291 | 2.5317 | 2.5593 | 2.5959 | 2.7622
2021-10-02 | 2.2673 | 2.5034 | 2.5379 | 2.5801 | 2.6294 | 1.5623 | 1.8947 | 1.9216 | 1.9584 | 1.5623 | 1.9053 | 2.1651 | 2.1893 | 2.2214 | 2.3645
2021-10-02 01:00 | 2.0005 | 2.2072 | 2.2368 | 2.2731 | 2.3154 | 1.3908 | 1.6852 | 1.7083 | 1.7398 | 1.3908 | 1.7338 | 1.9678 | 1.9885 | 2.0161 | 2.1444
2021-10-02 02:00 | 2.0196 | 2.2156 | 2.2391 | 2.2678 | 2.3012 | 1.3527 | 1.6314 | 1.6497 | 1.6747 | 1.3527 | 1.5433 | 1.7475 | 1.7639 | 1.7857 | 1.8967
2021-10-02 03:00 | 2.0386 | 2.2243 | 2.2417 | 2.263 | 2.2878 | 1.3275 | 1.593 | 1.6065 | 1.6251 | 1.3275 | 1.6957 | 1.9085 | 1.9207 | 1.9369 | 2.0495
2021-10-02 04:00 | 2.172 | 2.3575 | 2.3697 | 2.3847 | 2.4022 | 1.4586 | 1.7405 | 1.7501 | 1.7631 | 1.4586 | 1.5242 | 1.7108 | 1.7194 | 1.7308 | 1.8282
2021-10-02 05:00 | 2.4003 | 2.5988 | 2.609 | 2.6215 | 2.6362 | 1.7605 | 2.0943 | 2.1023 | 2.1132 | 1.7605 | 1.6195 | 1.8138 | 1.821 | 1.8305 | 1.9309
2021-10-02 06:00 | 2.6102 | 2.8276 | 2.8396 | 2.8542 | 2.8712 | 2.0577 | 2.4478 | 2.4571 | 2.4698 | 2.0577 | 1.6385 | 1.8374 | 1.8457 | 1.8568 | 1.9602
2021-10-02 07:00 | 2.7436 | 2.98 | 2.9966 | 3.0169 | 3.0405 | 2.0767 | 2.4769 | 2.4899 | 2.5075 | 2.0767 | 1.6004 | 1.8015 | 1.8131 | 1.8285 | 1.9349
2021-10-02 08:00 | 2.6293 | 2.8705 | 2.8939 | 2.9226 | 2.956 | 1.908 | 2.2873 | 2.3055 | 2.3304 | 1.908 | 1.6957 | 1.9168 | 1.9332 | 1.955 | 2.0742
2021-10-02 09:00 | 2.2482 | 2.4754 | 2.5061 | 2.5436 | 2.5874 | 1.5762 | 1.9057 | 1.9296 | 1.9623 | 1.5762 | 2.0577 | 2.3291 | 2.3506 | 2.3792 | 2.5265
2021-10-02 10:00 | 1.829 | 2.036 | 2.0723 | 2.1167 | 2.1684 | 1.2575 | 1.5371 | 1.5654 | 1.604 | 1.2575 | 1.3527 | 1.5535 | 1.5789 | 1.6127 | 1.7274
2021-10-02 11:00 | 1.5814 | 1.7743 | 1.8127 | 1.8598 | 1.9148 | 1.0288 | 1.2701 | 1.3002 | 1.3411 | 1.0288 | 1.2384 | 1.4296 | 1.4565 | 1.4924 | 1.6033
2021-10-02 12:00 | 1.5052 | 1.6913 | 1.7293 | 1.7757 | 1.8299 | 1.0098 | 1.2469 | 1.2765 | 1.3169 | 1.0098 | 1.2575 | 1.45 | 1.4766 | 1.5119 | 1.6233
2021-10-02 13:00 | 1.7338 | 1.932 | 1.9674 | 2.0107 | 2.0612 | 1.0098 | 1.2433 | 1.2709 | 1.3086 | 1.0098 | 1.3908 | 1.5947 | 1.6195 | 1.6524 | 1.7683
2021-10-02 14:00 | 2.0005 | 2.2131 | 2.2458 | 2.2857 | 2.3323 | 0.94811 | 1.1665 | 1.1919 | 1.2267 | 0.94811 | 1.6385 | 1.8661 | 1.8889 | 1.9193 | 2.0457
2021-10-02 15:00 | 1.7719 | 1.9639 | 1.9947 | 2.0324 | 2.0764 | 1.209 | 1.4721 | 1.4961 | 1.5289 | 1.209 | 1.9815 | 2.2446 | 2.2662 | 2.2949 | 2.4381
2021-10-02 16:00 | 2.0386 | 2.2496 | 2.28 | 2.3171 | 2.3605 | 1.5416 | 1.8644 | 1.8881 | 1.9204 | 1.5416 | 3.258 | 3.6626 | 3.6838 | 3.7121 | 3.925
2021-10-02 17:00 | 2.4489 | 2.6939 | 2.7261 | 2.7655 | 2.8114 | 2.0577 | 2.4766 | 2.5017 | 2.536 | 2.0577 | 3.2199 | 3.6227 | 3.6453 | 3.6752 | 3.8881
2021-10-02 18:00 | 2.6864 | 2.9565 | 2.9924 | 3.0364 | 3.0877 | 2.2291 | 2.6845 | 2.7125 | 2.7508 | 2.2291 | 3.0294 | 3.4162 | 3.4414 | 3.4749 | 3.6814
2021-10-02 19:00 | 2.6864 | 2.9662 | 3.0071 | 3.0572 | 3.1156 | 2.2291 | 2.6916 | 2.7235 | 2.7671 | 2.2291 | 3.0865 | 3.4867 | 3.5153 | 3.5534 | 3.7686
2021-10-02 20:00 | 2.6864 | 2.9759 | 3.0217 | 3.0779 | 3.1433 | 2.1339 | 2.5861 | 2.6219 | 2.6707 | 2.1339 | 2.8388 | 3.2183 | 3.2504 | 3.2931 | 3.5002
2021-10-02 21:00 | 2.4387 | 2.7114 | 2.7581 | 2.8153 | 2.8819 | 1.988 | 2.415 | 2.4514 | 2.5011 | 1.988 | 2.5721 | 2.923 | 2.9557 | 2.9992 | 3.1926
2021-10-02 22:00 | 2.2692 | 2.5234 | 2.567 | 2.6204 | 2.6827 | 1.81 | 2.2003 | 2.2344 | 2.2808 | 1.81 | 2.2673 | 2.58 | 2.6106 | 2.6512 | 2.8245
2021-10-02 23:00 | 2.0958 | 2.3286 | 2.3679 | 2.4161 | 2.4722 | 1.586 | 1.9295 | 1.9602 | 2.0021 | 1.586 | 1.8481 | 2.1083 | 2.1358 | 2.1724 | 2.3178
2021-10-03 | 1.9434 | 2.1554 | 2.1899 | 2.2321 | 2.2814 | 1.3718 | 1.6696 | 1.6965 | 1.7333 | 1.3718 | 1.7338 | 1.9745 | 1.9987 | 2.0308 | 2.1646
2021-10-03 01:00 | 1.8862 | 2.0844 | 2.114 | 2.1503 | 2.1925 | 1.279 | 1.5531 | 1.5762 | 1.6077 | 1.279 | 1.6576 | 1.8831 | 1.9038 | 1.9314 | 2.0555
2021-10-03 03:00 | 1.8481 | 2.0314 | 2.0548 | 2.0835 | 2.117 | 1.1813 | 1.4288 | 1.4471 | 1.4721 | 1.1813 | 2.0958 | 2.3615 | 2.3779 | 2.3997 | 2.541
2021-10-03 04:00 | 1.7909 | 1.9582 | 1.9756 | 1.9969 | 2.0217 | 1.1813 | 1.4202 | 1.4338 | 1.4524 | 1.1813 | 1.81 | 2.0355 | 2.0477 | 2.0639 | 2.1828
2021-10-03 05:00 | 1.7999 | 1.9577 | 1.97 | 1.985 | 2.0025 | 1.2194 | 1.4579 | 1.4675 | 1.4806 | 1.2194 | 1.6385 | 1.8378 | 1.8464 | 1.8578 | 1.9615
2021-10-03 06:00 | 1.9967 | 2.1652 | 2.1754 | 2.188 | 2.2026 | 1.4861 | 1.7702 | 1.7781 | 1.789 | 1.4861 | 1.81 | 2.0256 | 2.0327 | 2.0422 | 2.1531
2021-10-03 07:00 | 2.1529 | 2.3364 | 2.3483 | 2.3629 | 2.3799 | 1.6576 | 1.9752 | 1.9845 | 1.9972 | 1.6576 | 1.8481 | 2.0703 | 2.0786 | 2.0897 | 2.2046
2021-10-03 08:00 | 2.191 | 2.3864 | 2.403 | 2.4233 | 2.4469 | 1.6576 | 1.9818 | 1.9947 | 2.0123 | 1.6576 | 1.7338 | 1.9497 | 1.9613 | 1.9767 | 2.0905
2021-10-03 09:00 | 2.0386 | 2.236 | 2.2594 | 2.288 | 2.3214 | 1.5242 | 1.8339 | 1.8521 | 1.8771 | 1.5242 | 1.3718 | 1.5569 | 1.5732 | 1.595 | 1.6965
2021-10-03 10:00 | 1.8862 | 2.0865 | 2.1171 | 2.1547 | 2.1985 | 1.4289 | 1.7317 | 1.7556 | 1.7883 | 1.4289 | 1.1813 | 1.3552 | 1.3767 | 1.4053 | 1.5044
2021-10-03 11:00 | 2.0386 | 2.2612 | 2.2974 | 2.3418 | 2.3936 | 1.3908 | 1.6946 | 1.7229 | 1.7615 | 1.3908 | 1.1241 | 1.2995 | 1.3249 | 1.3586 | 1.4608
2021-10-03 12:00 | 1.6385 | 1.8357 | 1.8741 | 1.9212 | 1.9762 | 1.2765 | 1.5627 | 1.5928 | 1.6337 | 1.2765 | 1.3146 | 1.5143 | 1.5412 | 1.577 | 1.6922
2021-10-03 13:00 | 1.8481 | 2.0598 | 2.0977 | 2.1442 | 2.1983 | 1.2956 | 1.5845 | 1.6141 | 1.6545 | 1.2956 | 1.1813 | 1.3653 | 1.3919 | 1.4272 | 1.5344
2021-10-03 14:00 | 1.9053 | 2.1162 | 2.1516 | 2.1949 | 2.2454 | 1.2575 | 1.5359 | 1.5635 | 1.6012 | 1.2575 | 1.5814 | 1.8064 | 1.8312 | 1.8641 | 1.9905
2021-10-03 15:00 | 1.7719 | 1.9675 | 2.0001 | 2.0401 | 2.0867 | 1.3146 | 1.5994 | 1.6249 | 1.6597 | 1.3146 | 1.7528 | 1.9931 | 2.016 | 2.0464 | 2.1791
2021-10-03 16:00 | 1.829 | 2.0253 | 2.0561 | 2.0938 | 2.1378 | 1.3146 | 1.5968 | 1.6209 | 1.6537 | 1.3146 | 2.4006 | 2.7104 | 2.732 | 2.7607 | 2.9269
2021-10-03 17:00 | 2.0767 | 2.2906 | 2.3209 | 2.3581 | 2.4014 | 1.4641 | 1.7728 | 1.7964 | 1.8288 | 1.4641 | 2.4006 | 2.7098 | 2.7311 | 2.7594 | 2.9251
2021-10-03 18:00 | 2.4197 | 2.6625 | 2.6947 | 2.7341 | 2.78 | 2.0111 | 2.4216 | 2.4467 | 2.4809 | 2.0111 | 2.7055 | 3.0511 | 3.0736 | 3.1036 | 3.2881
2021-10-03 19:00 | 2.6102 | 2.8746 | 2.9105 | 2.9545 | 3.0058 | 2.1529 | 2.5945 | 2.6225 | 2.6608 | 2.1529 | 2.9531 | 3.3315 | 3.3567 | 3.3902 | 3.5925
2021-10-03 20:00 | 2.4899 | 2.7551 | 2.796 | 2.8461 | 2.9045 | 2.2101 | 2.6691 | 2.701 | 2.7446 | 2.2101 | 2.915 | 3.2961 | 3.3248 | 3.3629 | 3.5687
2021-10-03 21:00 | 2.4959 | 2.7712 | 2.8171 | 2.8732 | 2.9386 | 2.1148 | 2.5636 | 2.5993 | 2.6482 | 2.1148 | 2.9722 | 3.3665 | 3.3986 | 3.4413 | 3.6557
2021-10-03 22:00 | 2.4006 | 2.6705 | 2.7172 | 2.7743 | 2.841 | 1.9624 | 2.3847 | 2.4211 | 2.4708 | 1.9624 | 2.6864 | 3.05 | 3.0828 | 3.1262 | 3.3259
2021-10-03 23:00 | 2.2673 | 2.5212 | 2.5649 | 2.6183 | 2.6806 | 1.726 | 2.101 | 2.1351 | 2.1816 | 1.726 | 2.7245 | 3.0882 | 3.1187 | 3.1594 | 3.3577
2021-10-04 | 2.1339 | 2.3695 | 2.4089 | 2.457 | 2.5131 | 1.6004 | 1.9466 | 1.9773 | 2.0192 | 1.6004 | 1.9434 | 2.2141 | 2.2417 | 2.2783 | 2.4289
2021-10-04 01:00 | 1.9564 | 2.1693 | 2.2039 | 2.2461 | 2.2953 | 1.3671 | 1.6641 | 1.691 | 1.7277 | 1.3671 | 1.7338 | 1.9745 | 1.9987 | 2.0308 | 2.1646
2021-10-04 02:00 | 1.8862 | 2.0844 | 2.114 | 2.1503 | 2.1925 | 1.2503 | 1.5192 | 1.5423 | 1.5738 | 1.2503 | 1.6766 | 1.9042 | 1.925 | 1.9526 | 2.0777
2021-10-04 03:00 | 1.7719 | 1.9495 | 1.973 | 2.0017 | 2.0351 | 1.1622 | 1.4063 | 1.4246 | 1.4496 | 1.1622 | 1.6385 | 1.8533 | 1.8698 | 1.8916 | 2.0078
2021-10-04 04:00 | 1.7528 | 1.9172 | 1.9346 | 1.9559 | 1.9808 | 1.1241 | 1.3527 | 1.3663 | 1.3848 | 1.1241 | 1.5623 | 1.7603 | 1.7725 | 1.7887 | 1.8939
2021-10-04 05:00 | 1.6766 | 1.8253 | 1.8375 | 1.8525 | 1.87 | 1.1241 | 1.3454 | 1.355 | 1.368 | 1.1241 | 1.5433 | 1.732 | 1.7405 | 1.752 | 1.8504
2021-10-04 06:00 | 1.7528 | 1.9032 | 1.9134 | 1.9259 | 1.9405 | 1.2039 | 1.4368 | 1.4447 | 1.4556 | 1.2039 | 1.6195 | 1.8138 | 1.821 | 1.8305 | 1.9309
2021-10-04 07:00 | 1.7719 | 1.927 | 1.9389 | 1.9535 | 1.9706 | 1.2956 | 1.5475 | 1.5568 | 1.5695 | 1.2956 | 1.7338 | 1.9432 | 1.9516 | 1.9627 | 2.0713
2021-10-04 08:00 | 2.0386 | 2.2226 | 2.2392 | 2.2595 | 2.2832 | 1.5242 | 1.8242 | 1.8371 | 1.8548 | 1.5242 | 1.7338 | 1.9497 | 1.9613 | 1.9767 | 2.0905
2021-10-04 09:00 | 2.2153 | 2.4258 | 2.4491 | 2.4778 | 2.5112 | 1.81 | 2.1715 | 2.1898 | 2.2147 | 1.81 | 0.89547 | 1.0275 | 1.0439 | 1.0657 | 1.141
2021-10-04 10:00 | 2.4578 | 2.7005 | 2.7312 | 2.7688 | 2.8125 | 1.9243 | 2.3169 | 2.3408 | 2.3735 | 1.9243 | 1.2384 | 1.4187 | 1.4402 | 1.4688 | 1.571
2021-10-04 11:00 | 2.5373 | 2.797 | 2.8332 | 2.8776 | 2.9294 | 2.1529 | 2.595 | 2.6232 | 2.6619 | 2.1529 | 0.99073 | 1.1513 | 1.1767 | 1.2104 | 1.3053
2021-10-04 12:00 | 2.6864 | 2.9615 | 2.9999 | 3.047 | 3.102 | 2.2292 | 2.6882 | 2.7182 | 2.7592 | 2.2292 | 0.95263 | 1.112 | 1.1389 | 1.1748 | 1.27
2021-10-04 13:00 | 2.7245 | 3.0013 | 3.0393 | 3.0857 | 3.1399 | 2.3816 | 2.8674 | 2.897 | 2.9374 | 2.3816 | 1.0479 | 1.2171 | 1.2437 | 1.279 | 1.3789
2021-10-04 14:00 | 2.7626 | 3.0373 | 3.0727 | 3.116 | 3.1665 | 2.4387 | 2.9313 | 2.959 | 2.9966 | 2.4387 | 1.086 | 1.2559 | 1.2807 | 1.3137 | 1.4128
2021-10-04 15:00 | 2.7055 | 2.9705 | 3.0031 | 3.0431 | 3.0896 | 2.4768 | 2.9724 | 2.9979 | 3.0326 | 2.4768 | 1.5242 | 1.739 | 1.7619 | 1.7923 | 1.9124
2021-10-04 16:00 | 2.6864 | 2.9464 | 2.9772 | 3.0149 | 3.0589 | 2.4006 | 2.8798 | 2.9038 | 2.9366 | 2.4006 | 1.448 | 1.6518 | 1.6734 | 1.7021 | 1.816
2021-10-04 17:00 | 2.8388 | 3.1093 | 3.1397 | 3.1768 | 3.2202 | 2.5911 | 3.1042 | 3.1279 | 3.1603 | 2.5911 | 2.3625 | 2.6675 | 2.6887 | 2.717 | 2.8807
2021-10-04 18:00 | 3.0675 | 3.3585 | 3.3907 | 3.43 | 3.476 | 2.7436 | 3.2869 | 3.312 | 3.3462 | 2.7436 | 3.3723 | 3.7921 | 3.8147 | 3.8446 | 4.0658
2021-10-04 19:00 | 3.1818 | 3.4887 | 3.5246 | 3.5686 | 3.6199 | 2.896 | 3.4723 | 3.5003 | 3.5386 | 2.896 | 4.1344 | 4.6442 | 4.6694 | 4.7028 | 4.9701
2021-10-04 20:00 | 3.1784 | 3.4948 | 3.5357 | 3.5858 | 3.6442 | 2.7245 | 3.2768 | 3.3087 | 3.3523 | 2.7245 | 3.9058 | 4.3971 | 4.4257 | 4.4638 | 4.7241
2021-10-04 21:00 | 2.8181 | 3.1173 | 3.1632 | 3.2193 | 3.2848 | 2.5149 | 3.0362 | 3.072 | 3.1208 | 2.5149 | 3.3151 | 3.7476 | 3.7797 | 3.8224 | 4.0557
2021-10-04 22:00 | 2.7055 | 2.998 | 3.0447 | 3.1018 | 3.1685 | 2.3324 | 2.8218 | 2.8582 | 2.9079 | 2.3324 | 3.0103 | 3.41 | 3.4427 | 3.4861 | 3.7036
2021-10-04 23:00 | 2.553 | 2.8283 | 2.8719 | 2.9254 | 2.9877 | 2.1544 | 2.6072 | 2.6413 | 2.6877 | 2.1544 | 2.7626 | 3.1305 | 3.1611 | 3.2017 | 3.4022
2021-10-05 | 2.3625 | 2.6151 | 2.6545 | 2.7026 | 2.7588 | 1.8146 | 2.1996 | 2.2303 | 2.2722 | 1.8146 | 2.0196 | 2.2988 | 2.3264 | 2.363 | 2.5178
2021-10-05 01:00 | 2.0935 | 2.3167 | 2.3512 | 2.3935 | 2.4427 | 1.5718 | 1.9059 | 1.9328 | 1.9696 | 1.5718 | 1.8481 | 2.1016 | 2.1257 | 2.1579 | 2.2979
2021-10-05 02:00 | 2.0386 | 2.2482 | 2.2778 | 2.314 | 2.3563 | 1.4313 | 1.733 | 1.7561 | 1.7877 | 1.4313 | 1.8862 | 2.1371 | 2.1579 | 2.1855 | 2.3221
2021-10-05 03:00 | 1.9243 | 2.1133 | 2.1367 | 2.1654 | 2.1989 | 1.3318 | 1.6067 | 1.625 | 1.65 | 1.3318 | 1.81 | 2.0439 | 2.0603 | 2.0821 | 2.2077
2021-10-05 04:00 | 1.9048 | 2.0805 | 2.0979 | 2.1192 | 2.1441 | 1.2956 | 1.5553 | 1.5689 | 1.5874 | 1.2956 | 1.7147 | 1.9296 | 1.9418 | 1.958 | 2.0717
2021-10-05 05:00 | 1.9815 | 2.1528 | 2.165 | 2.18 | 2.1975 | 1.3337 | 1.593 | 1.6025 | 1.6156 | 1.3337 | 2.2291 | 2.4942 | 2.5027 | 2.5142 | 2.6504
2021-10-05 06:00 | 2.1529 | 2.333 | 2.3433 | 2.3558 | 2.3704 | 1.467 | 1.7477 | 1.7556 | 1.7665 | 1.467 | 2.4387 | 2.7242 | 2.7314 | 2.7409 | 2.8864
2021-10-05 07:00 | 2.1529 | 2.3364 | 2.3483 | 2.3629 | 2.3799 | 1.6385 | 1.9526 | 1.962 | 1.9747 | 1.6385 | 2.896 | 3.2347 | 3.2431 | 3.2542 | 3.4267
2021-10-05 08:00 | 2.3054 | 2.5092 | 2.5258 | 2.5461 | 2.5697 | 1.81 | 2.1618 | 2.1748 | 2.1924 | 1.81 | 3.1627 | 3.5376 | 3.5492 | 3.5646 | 3.757
2021-10-05 09:00 | 2.2863 | 2.5021 | 2.5255 | 2.5541 | 2.5875 | 2.0407 | 2.4441 | 2.4624 | 2.4873 | 2.0407 | 2.4768 | 2.7848 | 2.8012 | 2.823 | 2.9852
2021-10-05 10:00 | 2.3816 | 2.6187 | 2.6493 | 2.6869 | 2.7307 | 2.0577 | 2.4745 | 2.4984 | 2.5311 | 2.0577 | 2.553 | 2.8796 | 2.9011 | 2.9297 | 3.1042
2021-10-05 11:00 | 2.191 | 2.4249 | 2.4612 | 2.5056 | 2.5573 | 1.7909 | 2.1673 | 2.1956 | 2.2342 | 1.7909 | 1.6957 | 1.9346 | 1.96 | 1.9938 | 2.1274
2021-10-05 12:00 | 2.7436 | 3.0229 | 3.0613 | 3.1084 | 3.1634 | 2.5901 | 3.1146 | 3.1446 | 3.1856 | 2.5901 | 1.1432 | 1.3237 | 1.3507 | 1.3865 | 1.4922
2021-10-05 13:00 | 2.9341 | 3.2265 | 3.2644 | 3.3109 | 3.3651 | 2.6674 | 3.2051 | 3.2347 | 3.2751 | 2.6674 | 1.4099 | 1.6194 | 1.646 | 1.6813 | 1.801
2021-10-05 14:00 | 2.9913 | 3.2829 | 3.3183 | 3.3616 | 3.4122 | 2.6864 | 3.2239 | 3.2516 | 3.2893 | 2.6864 | 1.5814 | 1.8064 | 1.8312 | 1.8641 | 1.9905
2021-10-05 15:00 | 3.0294 | 3.3185 | 3.3511 | 3.391 | 3.4376 | 2.7817 | 3.3326 | 3.358 | 3.3928 | 2.7817 | 1.8481 | 2.099 | 2.1218 | 2.1522 | 2.2901
2021-10-05 16:00 | 2.915 | 3.1921 | 3.2229 | 3.2606 | 3.3045 | 2.6182 | 3.1368 | 3.1609 | 3.1937 | 2.6182 | 2.3625 | 2.6681 | 2.6897 | 2.7183 | 2.8825
2021-10-05 17:00 | 3.0294 | 3.314 | 3.3444 | 3.3815 | 3.4249 | 2.553 | 3.0592 | 3.0829 | 3.1152 | 2.553 | 4.001 | 4.4883 | 4.5096 | 4.5378 | 4.7916
2021-10-05 18:00 | 3.5057 | 3.8293 | 3.8614 | 3.9008 | 3.9468 | 3.1247 | 3.7371 | 3.7622 | 3.7965 | 3.1247 | 4.5917 | 5.1471 | 5.1697 | 5.1996 | 5.4879
2021-10-05 19:00 | 3.9439 | 4.3074 | 4.3434 | 4.3873 | 4.4386 | 3.4866 | 4.17 | 4.1981 | 4.2363 | 3.4866 | 4.3821 | 4.9195 | 4.9446 | 4.9781 | 5.259
2021-10-05 20:00 | 3.8486 | 4.2148 | 4.2557 | 4.3058 | 4.3642 | 3.3533 | 4.0196 | 4.0515 | 4.0951 | 3.3533 | 4.8012 | 5.3922 | 5.4208 | 5.4589 | 5.7684
2021-10-05 21:00 | 3.6962 | 4.0607 | 4.1066 | 4.1627 | 4.2282 | 3.1818 | 3.824 | 3.8598 | 3.9086 | 3.1818 | 3.7724 | 4.2557 | 4.2878 | 4.3305 | 4.589
2021-10-05 22:00 | 3.4932 | 3.8443 | 3.891 | 3.9481 | 4.0148 | 2.915 | 3.5101 | 3.5465 | 3.5962 | 2.915 | 3.1437 | 3.5582 | 3.5909 | 3.6344 | 3.8591
2021-10-05 23:00 | 3.1078 | 3.4243 | 3.4679 | 3.5214 | 3.5837 | 2.6232 | 3.161 | 3.195 | 3.2415 | 2.6232 | 2.6483 | 3.0035 | 3.0341 | 3.0747 | 3.2689
2021-10-06 | 2.8949 | 3.1871 | 3.2264 | 3.2746 | 3.3307 | 2.1124 | 2.5514 | 2.5821 | 2.624 | 2.1124 | 2.4006 | 2.7223 | 2.7498 | 2.7864 | 2.9622
2021-10-06 01:00 | 2.5149 | 2.7695 | 2.804 | 2.8462 | 2.8954 | 1.8862 | 2.2773 | 2.3043 | 2.341 | 1.8862 | 2.0958 | 2.3768 | 2.401 | 2.4331 | 2.5867
2021-10-06 02:00 | 2.3054 | 2.5347 | 2.5643 | 2.6006 | 2.6429 | 1.6923 | 2.0414 | 2.0645 | 2.096 | 1.6923 | 1.8862 | 2.1371 | 2.1579 | 2.1855 | 2.3221
2021-10-06 03:00 | 2.2101 | 2.4203 | 2.4437 | 2.4724 | 2.5059 | 1.5814 | 1.9015 | 1.9198 | 1.9448 | 1.5814 | 1.9624 | 2.2133 | 2.2297 | 2.2515 | 2.3855
2021-10-06 04:00 | 2.2673 | 2.4699 | 2.4873 | 2.5086 | 2.5334 | 1.5433 | 1.8479 | 1.8615 | 1.88 | 1.5433 | 1.8481 | 2.0779 | 2.09 | 2.1063 | 2.2272
2021-10-06 05:00 | 2.2863 | 2.4803 | 2.4925 | 2.5075 | 2.525 | 1.6338 | 1.9476 | 1.9571 | 1.9702 | 1.6338 | 2.2863 | 2.5577 | 2.5663 | 2.5777 | 2.717
2021-10-06 06:00 | 2.4573 | 2.66 | 2.6702 | 2.6828 | 2.6974 | 1.9125 | 2.2738 | 2.2818 | 2.2927 | 1.9125 | 2.915 | 3.2535 | 3.2607 | 3.2702 | 3.4419
2021-10-06 07:00 | 2.7436 | 2.9709 | 2.9828 | 2.9974 | 3.0145 | 2.2291 | 2.6504 | 2.6597 | 2.6724 | 2.2291 | 2.8769 | 3.2136 | 3.2219 | 3.233 | 3.4045
2021-10-06 08:00 | 2.9531 | 3.2051 | 3.2217 | 3.242 | 3.2657 | 2.2101 | 2.6345 | 2.6474 | 2.6651 | 2.2101 | 2.6483 | 2.9659 | 2.9776 | 2.993 | 3.157
2021-10-06 09:00 | 2.7817 | 3.0343 | 3.0577 | 3.0863 | 3.1197 | 2.1148 | 2.5316 | 2.5499 | 2.5748 | 2.1148 | 1.5052 | 1.7051 | 1.7215 | 1.7432 | 1.852
2021-10-06 10:00 | 2.4006 | 2.6391 | 2.6698 | 2.7074 | 2.7511 | 1.7338 | 2.0918 | 2.1158 | 2.1484 | 1.7338 | 0.83831 | 0.97412 | 0.99561 | 1.0242 | 1.1044
2021-10-06 11:00 | 2.0958 | 2.3226 | 2.3588 | 2.4032 | 2.455 | 1.3527 | 1.6496 | 1.6779 | 1.7165 | 1.3527 | 0.97168 | 1.1301 | 1.1555 | 1.1892 | 1.283
2021-10-06 12:00 | 1.7338 | 1.938 | 1.9765 | 2.0236 | 2.0785 | 1.2003 | 1.4727 | 1.5027 | 1.5437 | 1.2003 | 0.95263 | 1.112 | 1.1389 | 1.1748 | 1.27
2021-10-06 13:00 | 1.7909 | 1.9984 | 2.0363 | 2.0828 | 2.1369 | 1.2194 | 1.4945 | 1.5241 | 1.5645 | 1.2194 | 1.0479 | 1.2171 | 1.2437 | 1.279 | 1.3789
2021-10-06 14:00 | 1.6004 | 1.7887 | 1.8241 | 1.8674 | 1.9179 | 1.086 | 1.3333 | 1.3609 | 1.3986 | 1.086 | 1.0479 | 1.2136 | 1.2384 | 1.2713 | 1.3683
2021-10-06 15:00 | 1.81 | 2.0084 | 2.0411 | 2.081 | 2.1276 | 1.2003 | 1.4644 | 1.4899 | 1.5246 | 1.2003 | 0.93358 | 1.0827 | 1.1056 | 1.136 | 1.2236
2021-10-06 16:00 | 2.0572 | 2.2704 | 2.3013 | 2.339 | 2.3829 | 1.3312 | 1.6164 | 1.6404 | 1.6733 | 1.3312 | 0.95263 | 1.1013 | 1.1229 | 1.1516 | 1.2383
2021-10-06 17:00 | 2.553 | 2.8023 | 2.8326 | 2.8698 | 2.9131 | 1.9202 | 2.3116 | 2.3353 | 2.3676 | 1.9202 | 1.8862 | 2.1382 | 2.1594 | 2.1877 | 2.3252
2021-10-06 18:00 | 3.1246 | 3.4199 | 3.4521 | 3.4915 | 3.5374 | 2.7904 | 3.3422 | 3.3673 | 3.4016 | 2.7904 | 2.6864 | 3.0299 | 3.0525 | 3.0824 | 3.2659
2021-10-06 19:00 | 3.6962 | 4.0413 | 4.0773 | 4.1212 | 4.1725 | 3.0707 | 3.6787 | 3.7068 | 3.745 | 3.0707 | 3.3151 | 3.7338 | 3.759 | 3.7924 | 4.0147
2021-10-06 20:00 | 3.6808 | 4.0345 | 4.0754 | 4.1255 | 4.1839 | 3.1056 | 3.727 | 3.7589 | 3.8024 | 3.1056 | 3.2008 | 3.6137 | 3.6424 | 3.6804 | 3.902
2021-10-06 21:00 | 3.5819 | 3.9379 | 3.9838 | 4.0399 | 4.1054 | 3.0763 | 3.6994 | 3.7352 | 3.784 | 3.0763 | 2.9913 | 3.3876 | 3.4198 | 3.4625 | 3.678
2021-10-06 22:00 | 3.4104 | 3.7553 | 3.802 | 3.8592 | 3.9258 | 2.7837 | 3.355 | 3.3914 | 3.4411 | 2.7837 | 2.7436 | 3.1136 | 3.1463 | 3.1897 | 3.3925
2021-10-06 23:00 | 3.1571 | 3.4772 | 3.5209 | 3.5743 | 3.6366 | 2.5038 | 3.0199 | 3.054 | 3.1005 | 2.5038 | 2.3816 | 2.7071 | 2.7376 | 2.7783 | 2.9578
2021-10-07 | 2.7055 | 2.9836 | 3.0229 | 3.0711 | 3.1272 | 2.105 | 2.5427 | 2.5733 | 2.6152 | 2.105 | 2.0196 | 2.2988 | 2.3264 | 2.363 | 2.5178
2021-10-07 01:00 | 2.4578 | 2.708 | 2.7426 | 2.7848 | 2.834 | 1.8481 | 2.2323 | 2.2592 | 2.296 | 1.8481 | 1.7338 | 1.9745 | 1.9987 | 2.0308 | 2.1646
2021-10-07 02:00 | 2.3625 | 2.5961 | 2.6257 | 2.662 | 2.7043 | 1.7147 | 2.0678 | 2.0909 | 2.1225 | 1.7147 | 1.9434 | 2.2006 | 2.2214 | 2.249 | 2.3888
2021-10-07 03:00 | 2.2291 | 2.4408 | 2.4642 | 2.4929 | 2.5264 | 1.6004 | 1.924 | 1.9423 | 1.9673 | 1.6004 | 1.6004 | 1.811 | 1.8274 | 1.8492 | 1.9633
2021-10-07 04:00 | 2.2291 | 2.4289 | 2.4464 | 2.4677 | 2.4925 | 1.5814 | 1.8929 | 1.9065 | 1.925 | 1.5814 | 1.5623 | 1.7603 | 1.7725 | 1.7887 | 1.8939
2021-10-07 05:00 | 2.3435 | 2.5417 | 2.5539 | 2.5689 | 2.5864 | 1.6385 | 1.9531 | 1.9627 | 1.9757 | 1.6385 | 1.9053 | 2.1342 | 2.1428 | 2.1542 | 2.2726
2021-10-07 06:00 | 2.455 | 2.6576 | 2.6678 | 2.6803 | 2.6949 | 2.0147 | 2.3946 | 2.4026 | 2.4135 | 2.0147 | 2.7055 | 3.0207 | 3.0278 | 3.0373 | 3.1975
2021-10-07 07:00 | 2.7626 | 2.9914 | 3.0033 | 3.0179 | 3.0349 | 2.2291 | 2.6504 | 2.6597 | 2.6724 | 2.2291 | 2.4768 | 2.7689 | 2.7773 | 2.7884 | 2.9379
2021-10-07 08:00 | 2.9722 | 3.2256 | 3.2422 | 3.2625 | 3.2861 | 2.2863 | 2.7245 | 2.7374 | 2.7551 | 2.2863 | 1.9815 | 2.2249 | 2.2365 | 2.252 | 2.3793
2021-10-07 09:00 | 2.8579 | 3.1161 | 3.1395 | 3.1682 | 3.2016 | 2.1148 | 2.5316 | 2.5499 | 2.5748 | 2.1148 | 1.3146 | 1.4933 | 1.5097 | 1.5315 | 1.6298
2021-10-07 10:00 | 2.5721 | 2.8234 | 2.854 | 2.8916 | 2.9354 | 1.8481 | 2.2269 | 2.2508 | 2.2835 | 1.8481 | 0.87642 | 1.0165 | 1.038 | 1.0665 | 1.1488
2021-10-07 11:00 | 2.1037 | 2.3311 | 2.3674 | 2.4117 | 2.4635 | 1.5575 | 1.8915 | 1.9198 | 1.9584 | 1.5575 | 0.93358 | 1.0877 | 1.1131 | 1.1469 | 1.2386
2021-10-07 12:00 | 2.2101 | 2.4497 | 2.4882 | 2.5353 | 2.5902 | 1.6385 | 1.9904 | 2.0204 | 2.0614 | 1.6385 | 1.0288 | 1.1967 | 1.2236 | 1.2595 | 1.3589
2021-10-07 13:00 | 1.7338 | 1.937 | 1.9749 | 2.0213 | 2.0755 | 1.1622 | 1.4269 | 1.4565 | 1.4969 | 1.1622 | 1.2194 | 1.4077 | 1.4342 | 1.4696 | 1.5788
2021-10-07 14:00 | 1.6195 | 1.8092 | 1.8446 | 1.8879 | 1.9384 | 1.1432 | 1.4008 | 1.4284 | 1.4661 | 1.1432 | 1.2384 | 1.4253 | 1.4501 | 1.483 | 1.5905
2021-10-07 15:00 | 1.6957 | 1.8856 | 1.9183 | 1.9582 | 2.0048 | 1.1098 | 1.3575 | 1.383 | 1.4177 | 1.1098 | 1.0288 | 1.1886 | 1.2114 | 1.2418 | 1.3347
2021-10-07 16:00 | 2.1339 | 2.3528 | 2.3836 | 2.4213 | 2.4653 | 1.4121 | 1.712 | 1.736 | 1.7688 | 1.4121 | 0.93358 | 1.0802 | 1.1017 | 1.1304 | 1.216
2021-10-07 17:00 | 2.5329 | 2.7806 | 2.811 | 2.8482 | 2.8915 | 1.937 | 2.3315 | 2.3552 | 2.3875 | 1.937 | 1.9434 | 2.2017 | 2.223 | 2.2512 | 2.3919
2021-10-07 18:00 | 2.9982 | 3.2841 | 3.3163 | 3.3557 | 3.4016 | 2.7741 | 3.323 | 3.3481 | 3.3823 | 2.7741 | 2.6102 | 2.9452 | 2.9678 | 2.9977 | 3.177
2021-10-07 19:00 | 3.3723 | 3.6934 | 3.7293 | 3.7733 | 3.8246 | 3.1246 | 3.7424 | 3.7704 | 3.8087 | 3.1246 | 3.0294 | 3.4162 | 3.4414 | 3.4749 | 3.6814
2021-10-07 20:00 | 3.5057 | 3.8464 | 3.8873 | 3.9374 | 3.9958 | 3.0675 | 3.6819 | 3.7139 | 3.7574 | 3.0675 | 3.2389 | 3.656 | 3.6847 | 3.7228 | 3.9464
2021-10-07 21:00 | 3.4295 | 3.7742 | 3.82 | 3.8762 | 3.9416 | 2.896 | 3.4864 | 3.5222 | 3.571 | 2.896 | 3.258 | 3.6841 | 3.7162 | 3.7589 | 3.989
2021-10-07 22:00 | 3.2961 | 3.6325 | 3.6792 | 3.7364 | 3.803 | 2.7817 | 3.3525 | 3.389 | 3.4387 | 2.7817 | 2.9722 | 3.3676 | 3.4003 | 3.4438 | 3.6592
2021-10-07 23:00 | 2.9843 | 3.2916 | 3.3353 | 3.3887 | 3.451 | 2.4073 | 2.906 | 2.94 | 2.9865 | 2.4073 | 2.2101 | 2.5165 | 2.5471 | 2.5877 | 2.7578
2021-10-08 | 2.7055 | 2.9836 | 3.0229 | 3.0711 | 3.1272 | 2.0135 | 2.4346 | 2.4652 | 2.5071 | 2.0135 | 1.9243 | 2.1929 | 2.2205 | 2.2571 | 2.4067
2021-10-08 01:00 | 2.4768 | 2.7285 | 2.763 | 2.8053 | 2.8545 | 1.7338 | 2.0973 | 2.1242 | 2.1609 | 1.7338 | 1.7528 | 1.9957 | 2.0199 | 2.052 | 2.1868
2021-10-08 02:00 | 2.191 | 2.4119 | 2.4415 | 2.4778 | 2.52 | 1.5623 | 1.8878 | 1.9109 | 1.9424 | 1.5623 | 1.6576 | 1.8831 | 1.9038 | 1.9314 | 2.0555
2021-10-08 03:00 | 2.2291 | 2.4408 | 2.4642 | 2.4929 | 2.5264 | 1.492 | 1.796 | 1.8143 | 1.8392 | 1.492 | 1.6385 | 1.8533 | 1.8698 | 1.8916 | 2.0078
2021-10-08 04:00 | 2.172 | 2.3675 | 2.3849 | 2.4063 | 2.4311 | 1.5052 | 1.8029 | 1.8165 | 1.835 | 1.5052 | 1.9243 | 2.1625 | 2.1747 | 2.1909 | 2.3161
2021-10-08 05:00 | 2.2482 | 2.4393 | 2.4516 | 2.4666 | 2.4841 | 1.5814 | 1.8856 | 1.8951 | 1.9082 | 1.5814 | 2.0767 | 2.3248 | 2.3334 | 2.3448 | 2.4726
2021-10-08 06:00 | 2.4387 | 2.6401 | 2.6503 | 2.6628 | 2.6774 | 1.8647 | 2.2175 | 2.2254 | 2.2363 | 1.8647 | 2.5911 | 2.8936 | 2.9008 | 2.9103 | 3.0641
2021-10-08 07:00 | 2.7436 | 2.9709 | 2.9828 | 2.9974 | 3.0145 | 2.2101 | 2.6279 | 2.6372 | 2.6499 | 2.2101 | 2.7626 | 3.0865 | 3.0949 | 3.106 | 3.2712
2021-10-08 08:00 | 3.2896 | 3.5666 | 3.5832 | 3.6035 | 3.6271 | 2.6293 | 3.1297 | 3.1426 | 3.1602 | 2.6293 | 2.172 | 2.4366 | 2.4482 | 2.4637 | 2.6015
2021-10-08 09:00 | 3.5628 | 3.8735 | 3.8969 | 3.9255 | 3.9589 | 2.8769 | 3.432 | 3.4502 | 3.4751 | 2.8769 | 1.4289 | 1.6204 | 1.6368 | 1.6585 | 1.7631
2021-10-08 10:00 | 3.62 | 3.9492 | 3.9798 | 4.0174 | 4.0612 | 2.8769 | 3.4423 | 3.4662 | 3.4989 | 2.8769 | 0.74305 | 0.86826 | 0.88975 | 0.91831 | 0.99331
2021-10-08 11:00 | 3.2008 | 3.5098 | 3.546 | 3.5904 | 3.6422 | 2.6102 | 3.1351 | 3.1634 | 3.202 | 2.6102 | 1.0479 | 1.2148 | 1.2402 | 1.2739 | 1.3719
2021-10-08 12:00 | 2.9531 | 3.248 | 3.2865 | 3.3336 | 3.3885 | 2.3012 | 2.7732 | 2.8032 | 2.8442 | 2.3012 | 1.0288 | 1.1967 | 1.2236 | 1.2595 | 1.3589
2021-10-08 13:00 | 2.0577 | 2.2849 | 2.3229 | 2.3693 | 2.4235 | 1.6385 | 1.9896 | 2.0192 | 2.0596 | 1.6385 | 1.1432 | 1.323 | 1.3495 | 1.3849 | 1.49
2021-10-08 14:00 | 1.6766 | 1.8706 | 1.906 | 1.9493 | 1.9998 | 1.1622 | 1.4233 | 1.4509 | 1.4886 | 1.1622 | 1.2384 | 1.4253 | 1.4501 | 1.483 | 1.5905
2021-10-08 15:00 | 1.6766 | 1.8652 | 1.8978 | 1.9377 | 1.9843 | 1.2003 | 1.4644 | 1.4899 | 1.5246 | 1.2003 | 1.1241 | 1.2944 | 1.3173 | 1.3477 | 1.4458
2021-10-08 16:00 | 1.9815 | 2.1891 | 2.2199 | 2.2576 | 2.3015 | 1.4289 | 1.7319 | 1.7559 | 1.7887 | 1.4289 | 0.93358 | 1.0802 | 1.1017 | 1.1304 | 1.216
2021-10-08 17:00 | 2.398 | 2.6357 | 2.6661 | 2.7033 | 2.7466 | 1.9525 | 2.3498 | 2.3735 | 2.4058 | 1.9525 | 1.8481 | 2.0958 | 2.1171 | 2.1454 | 2.2808
2021-10-08 18:00 | 3.0473 | 3.3368 | 3.369 | 3.4084 | 3.4543 | 2.6232 | 3.1447 | 3.1698 | 3.2041 | 2.6232 | 2.6102 | 2.9452 | 2.9678 | 2.9977 | 3.177
2021-10-08 19:00 | 3.4295 | 3.7548 | 3.7907 | 3.8347 | 3.886 | 3.0103 | 3.6073 | 3.6354 | 3.6736 | 3.0103 | 2.7055 | 3.0563 | 3.0815 | 3.1149 | 3.3037
2021-10-08 20:00 | 3.4676 | 3.8054 | 3.8464 | 3.8964 | 3.9548 | 2.9531 | 3.5469 | 3.5788 | 3.6224 | 2.9531 | 2.7436 | 3.1056 | 3.1342 | 3.1723 | 3.3687
2021-10-08 21:00 | 3.2389 | 3.5695 | 3.6153 | 3.6715 | 3.7369 | 2.896 | 3.4864 | 3.5222 | 3.571 | 2.896 | 2.7626 | 3.1336 | 3.1657 | 3.2084 | 3.4113
2021-10-08 22:00 | 3.0484 | 3.3664 | 3.4131 | 3.4703 | 3.5369 | 2.6734 | 3.2246 | 3.261 | 3.3108 | 2.6734 | 2.4578 | 2.796 | 2.8287 | 2.8722 | 3.0592
2021-10-08 23:00 | 2.9722 | 3.2786 | 3.3222 | 3.3757 | 3.438 | 2.3996 | 2.8969 | 2.9309 | 2.9774 | 2.3996 | 2.2863 | 2.6012 | 2.6318 | 2.6724 | 2.8467
2021-10-09 | 2.6102 | 2.8812 | 2.9206 | 2.9687 | 3.0249 | 1.9815 | 2.3967 | 2.4274 | 2.4693 | 1.9815 | 1.9434 | 2.2141 | 2.2417 | 2.2783 | 2.4289
2021-10-09 01:00 | 2.3816 | 2.6262 | 2.6607 | 2.7029 | 2.7522 | 1.7527 | 2.1196 | 2.1465 | 2.1832 | 1.7527 | 2.0196 | 2.2921 | 2.3163 | 2.3484 | 2.4979
2021-10-09 02:00 | 2.2673 | 2.4938 | 2.5234 | 2.5597 | 2.6019 | 1.5433 | 1.8652 | 1.8884 | 1.9199 | 1.5433 | 1.9624 | 2.2218 | 2.2426 | 2.2701 | 2.411
2021-10-09 03:00 | 2.2291 | 2.4408 | 2.4642 | 2.4929 | 2.5264 | 1.467 | 1.7664 | 1.7847 | 1.8097 | 1.467 | 1.7719 | 2.0015 | 2.018 | 2.0398 | 2.1633
2021-10-09 04:00 | 2.0959 | 2.2857 | 2.3032 | 2.3245 | 2.3493 | 1.467 | 1.7579 | 1.7714 | 1.79 | 1.467 | 1.6004 | 1.8026 | 1.8148 | 1.831 | 1.9384
2021-10-09 05:00 | 2.1763 | 2.3621 | 2.3743 | 2.3893 | 2.4068 | 1.5484 | 1.8466 | 1.8562 | 1.8693 | 1.5484 | 1.7147 | 1.9225 | 1.9311 | 1.9425 | 2.0504
2021-10-09 06:00 | 2.5911 | 2.8038 | 2.814 | 2.8266 | 2.8412 | 1.8606 | 2.2126 | 2.2206 | 2.2315 | 1.8606 | 1.9815 | 2.2161 | 2.2233 | 2.2328 | 2.3531
2021-10-09 07:00 | 2.7245 | 2.9504 | 2.9624 | 2.977 | 2.994 | 2.1529 | 2.5604 | 2.5697 | 2.5824 | 2.1529 | 2.0005 | 2.2396 | 2.248 | 2.2591 | 2.3824
2021-10-09 08:00 | 2.896 | 3.1437 | 3.1603 | 3.1806 | 3.2043 | 2.2101 | 2.6345 | 2.6474 | 2.6651 | 2.2101 | 1.5433 | 1.7379 | 1.7496 | 1.765 | 1.8683
2021-10-09 09:00 | 2.7245 | 2.9729 | 2.9963 | 3.0249 | 3.0583 | 2.0506 | 2.4557 | 2.474 | 2.4989 | 2.0506 | 1.1813 | 1.3451 | 1.3615 | 1.3833 | 1.4743
2021-10-09 10:00 | 2.4959 | 2.7415 | 2.7722 | 2.8097 | 2.8535 | 1.6385 | 1.9793 | 2.0032 | 2.0359 | 1.6385 | 1.3337 | 1.5246 | 1.5461 | 1.5746 | 1.6821
2021-10-09 11:00 | 2.2107 | 2.446 | 2.4823 | 2.5267 | 2.5784 | 1.4099 | 1.7171 | 1.7454 | 1.7841 | 1.4099 | 1.2384 | 1.4265 | 1.4519 | 1.4857 | 1.5941
2021-10-09 12:00 | 1.9243 | 2.1427 | 2.1812 | 2.2283 | 2.2832 | 1.4289 | 1.7428 | 1.7728 | 1.8138 | 1.4289 | 0.89547 | 1.0485 | 1.0754 | 1.1113 | 1.2033
2021-10-09 13:00 | 2.0577 | 2.2849 | 2.3229 | 2.3693 | 2.4235 | 1.5623 | 1.8996 | 1.9292 | 1.9696 | 1.5623 | 0.97168 | 1.1324 | 1.159 | 1.1943 | 1.29
2021-10-09 14:00 | 1.81 | 2.0138 | 2.0492 | 2.0926 | 2.1431 | 1.4099 | 1.7159 | 1.7435 | 1.7812 | 1.4099 | 1.0479 | 1.2136 | 1.2384 | 1.2713 | 1.3683
2021-10-09 15:00 | 1.6004 | 1.7833 | 1.8159 | 1.8559 | 1.9024 | 1.0288 | 1.2618 | 1.2873 | 1.322 | 1.0288 | 0.97168 | 1.125 | 1.1479 | 1.1783 | 1.268
2021-10-09 16:00 | 1.8672 | 2.0663 | 2.0971 | 2.1348 | 2.1787 | 1.2956 | 1.5743 | 1.5984 | 1.6312 | 1.2956 | 0.85737 | 0.99547 | 1.0171 | 1.0457 | 1.1272
2021-10-09 17:00 | 2.191 | 2.4134 | 2.4437 | 2.4809 | 2.5242 | 1.6424 | 1.9834 | 2.0071 | 2.0394 | 1.6424 | 1.81 | 2.0535 | 2.0747 | 2.103 | 2.2363
2021-10-09 18:00 | 2.7436 | 3.0105 | 3.0427 | 3.0821 | 3.128 | 2.3869 | 2.8655 | 2.8906 | 2.9249 | 2.3869 | 2.3625 | 2.67 | 2.6925 | 2.7225 | 2.8882
2021-10-09 19:00 | 3.0484 | 3.3454 | 3.3813 | 3.4253 | 3.4766 | 2.7436 | 3.2922 | 3.3203 | 3.3585 | 2.7436 | 2.4578 | 2.7811 | 2.8062 | 2.8397 | 3.0148
2021-10-09 20:00 | 3.258 | 3.5803 | 3.6212 | 3.6713 | 3.7297 | 2.7245 | 3.2768 | 3.3087 | 3.3523 | 2.7245 | 2.5721 | 2.915 | 2.9437 | 2.9818 | 3.1687
2021-10-09 21:00 | 3.1394 | 3.4626 | 3.5084 | 3.5646 | 3.63 | 2.534 | 3.0587 | 3.0945 | 3.1434 | 2.534 | 2.4387 | 2.7736 | 2.8058 | 2.8485 | 3.0336
2021-10-09 22:00 | 2.8579 | 3.1617 | 3.2084 | 3.2656 | 3.3322 | 2.4959 | 3.0149 | 3.0513 | 3.1011 | 2.4959 | 2.6102 | 2.9654 | 2.9981 | 3.0415 | 3.237
2021-10-09 23:00 | 2.6293 | 2.9102 | 2.9538 | 3.0072 | 3.0695 | 2.1529 | 2.6055 | 2.6395 | 2.686 | 2.1529 | 2.0386 | 2.326 | 2.3565 | 2.3972 | 2.5578
2021-10-10 | 2.2863 | 2.5333 | 2.5726 | 2.6208 | 2.6769 | 1.8481 | 2.2392 | 2.2699 | 2.3118 | 1.8481 | 1.7147 | 1.9601 | 1.9876 | 2.0242 | 2.1623
2021-10-10 01:00 | 2.1339 | 2.3601 | 2.3946 | 2.4368 | 2.4861 | 1.5528 | 1.8834 | 1.9103 | 1.9471 | 1.5528 | 1.6385 | 1.8687 | 1.8928 | 1.925 | 2.0535
2021-10-10 02:00 | 2.0005 | 2.2072 | 2.2368 | 2.2731 | 2.3154 | 1.4289 | 1.7302 | 1.7533 | 1.7848 | 1.4289 | 1.7719 | 2.0101 | 2.0308 | 2.0584 | 2.1888
2021-10-10 03:00 | 1.9401 | 2.1303 | 2.1537 | 2.1824 | 2.2159 | 1.3302 | 1.6048 | 1.623 | 1.648 | 1.3302 | 1.3527 | 1.5357 | 1.5522 | 1.574 | 1.6745
2021-10-10 04:00 | 1.9815 | 2.1629 | 2.1803 | 2.2016 | 2.2264 | 1.3146 | 1.5778 | 1.5914 | 1.6099 | 1.3146 | 1.3718 | 1.5485 | 1.5607 | 1.5769 | 1.6717
2021-10-10 05:00 | 2.0011 | 2.1739 | 2.1861 | 2.2012 | 2.2186 | 1.3384 | 1.5986 | 1.6082 | 1.6212 | 1.3384 | 1.3908 | 1.5626 | 1.5712 | 1.5826 | 1.6727
2021-10-10 06:00 | 2.2101 | 2.3944 | 2.4047 | 2.4172 | 2.4318 | 1.6957 | 2.0177 | 2.0257 | 2.0366 | 1.6957 | 1.6195 | 1.8138 | 1.821 | 1.8305 | 1.9309
2021-10-10 07:00 | 2.3816 | 2.582 | 2.5939 | 2.6085 | 2.6256 | 1.7909 | 2.1327 | 2.142 | 2.1547 | 1.7909 | 1.9243 | 2.155 | 2.1633 | 2.1744 | 2.2935
2021-10-10 08:00 | 2.553 | 2.7753 | 2.7919 | 2.8122 | 2.8358 | 1.7909 | 2.1393 | 2.1522 | 2.1699 | 1.7909 | 1.9815 | 2.2249 | 2.2365 | 2.252 | 2.3793
2021-10-10 09:00 | 2.3244 | 2.543 | 2.5664 | 2.5951 | 2.6284 | 1.7158 | 2.0602 | 2.0785 | 2.1034 | 1.7158 | 1.7338 | 1.9591 | 1.9755 | 1.9973 | 2.1187
2021-10-10 10:00 | 2.1339 | 2.3526 | 2.3832 | 2.4208 | 2.4646 | 1.3146 | 1.5967 | 1.6206 | 1.6533 | 1.3146 | 1.2575 | 1.4399 | 1.4614 | 1.49 | 1.5932
2021-10-10 11:00 | 1.829 | 2.036 | 2.0723 | 2.1167 | 2.1684 | 1.2003 | 1.4696 | 1.4978 | 1.5365 | 1.2003 | 1.2384 | 1.4265 | 1.4519 | 1.4857 | 1.5941
2021-10-10 12:00 | 2.1339 | 2.3679 | 2.4063 | 2.4534 | 2.5084 | 1.5623 | 1.9004 | 1.9304 | 1.9714 | 1.5623 | 1.3908 | 1.5989 | 1.6259 | 1.6617 | 1.781
2021-10-10 13:00 | 2.2863 | 2.5306 | 2.5685 | 2.6149 | 2.6691 | 1.6766 | 2.0346 | 2.0642 | 2.1047 | 1.6766 | 1.5623 | 1.7888 | 1.8153 | 1.8507 | 1.9788
2021-10-10 14:00 | 1.9434 | 2.1571 | 2.1925 | 2.2359 | 2.2864 | 1.3146 | 1.6034 | 1.631 | 1.6687 | 1.3146 | 1.6766 | 1.9123 | 1.9371 | 1.97 | 2.1016
2021-10-10 15:00 | 1.9243 | 2.1313 | 2.1639 | 2.2038 | 2.2504 | 1.3146 | 1.5994 | 1.6249 | 1.6597 | 1.3146 | 1.8672 | 2.1201 | 2.143 | 2.1734 | 2.3124
2021-10-10 16:00 | 2.0196 | 2.23 | 2.2608 | 2.2985 | 2.3425 | 1.3146 | 1.5968 | 1.6209 | 1.6537 | 1.3146 | 2.4006 | 2.7104 | 2.732 | 2.7607 | 2.9269
2021-10-10 17:00 | 2.2101 | 2.4338 | 2.4642 | 2.5014 | 2.5447 | 1.6195 | 1.9563 | 1.98 | 2.0124 | 1.6195 | 2.6864 | 3.0274 | 3.0487 | 3.0769 | 3.2584
2021-10-10 18:00 | 2.4959 | 2.7444 | 2.7766 | 2.816 | 2.8619 | 2.1067 | 2.5345 | 2.5596 | 2.5939 | 2.1067 | 2.915 | 3.284 | 3.3065 | 3.3365 | 3.5325
2021-10-10 19:00 | 2.8007 | 3.0793 | 3.1152 | 3.1592 | 3.2105 | 2.4147 | 2.9037 | 2.9318 | 2.97 | 2.4147 | 2.8388 | 3.2045 | 3.2297 | 3.2631 | 3.4592
2021-10-10 20:00 | 2.8198 | 3.1095 | 3.1504 | 3.2005 | 3.2589 | 2.4197 | 2.9167 | 2.9486 | 2.9922 | 2.4197 | 2.7817 | 3.1479 | 3.1766 | 3.2147 | 3.4131
2021-10-10 21:00 | 2.7436 | 3.0373 | 3.0832 | 3.1393 | 3.2047 | 2.3625 | 2.8562 | 2.8919 | 2.9408 | 2.3625 | 3.1056 | 3.5147 | 3.5468 | 3.5895 | 3.8113
2021-10-10 22:00 | 2.6102 | 2.8956 | 2.9423 | 2.9995 | 3.0661 | 2.2101 | 2.6773 | 2.7137 | 2.7634 | 2.2101 | 2.3625 | 2.6901 | 2.7228 | 2.7663 | 2.9481
2021-10-10 23:00 | 2.4578 | 2.7259 | 2.7696 | 2.823 | 2.8853 | 2.0285 | 2.4584 | 2.4924 | 2.5389 | 2.0285 | 1.9053 | 2.1778 | 2.2083 | 2.249 | 2.4023
2021-10-11 | 2.2661 | 2.5116 | 2.5509 | 2.5991 | 2.6552 | 1.7528 | 2.1267 | 2.1573 | 2.1992 | 1.7528 | 1.6957 | 1.9389 | 1.9664 | 2.0031 | 2.1401
2021-10-11 01:00 | 2.1148 | 2.3396 | 2.3741 | 2.4163 | 2.4656 | 1.4829 | 1.8009 | 1.8278 | 1.8646 | 1.4829 | 1.6004 | 1.8263 | 1.8505 | 1.8826 | 2.009
2021-10-11 02:00 | 1.9815 | 2.1867 | 2.2164 | 2.2526 | 2.2949 | 1.3337 | 1.6177 | 1.6408 | 1.6723 | 1.3337 | 1.4289 | 1.629 | 1.6497 | 1.6773 | 1.7888
2021-10-11 03:00 | 1.9815 | 2.1747 | 2.1981 | 2.2268 | 2.2603 | 1.2765 | 1.5414 | 1.5597 | 1.5846 | 1.2765 | 1.6385 | 1.8533 | 1.8698 | 1.8916 | 2.0078
2021-10-11 04:00 | 1.9624 | 2.1424 | 2.1598 | 2.1811 | 2.2059 | 1.2384 | 1.4878 | 1.5013 | 1.5199 | 1.2384 | 1.6195 | 1.8238 | 1.836 | 1.8522 | 1.9606
2021-10-11 05:00 | 1.9815 | 2.1528 | 2.165 | 2.18 | 2.1975 | 1.2194 | 1.4579 | 1.4675 | 1.4806 | 1.2194 | 1.9053 | 2.1342 | 2.1428 | 2.1542 | 2.2726
2021-10-11 06:00 | 2.0577 | 2.2307 | 2.2409 | 2.2534 | 2.268 | 1.448 | 1.7251 | 1.7331 | 1.744 | 1.448 | 2.5911 | 2.8936 | 2.9008 | 2.9103 | 3.0641
2021-10-11 07:00 | 2.0386 | 2.2135 | 2.2255 | 2.2401 | 2.2571 | 1.5433 | 1.8401 | 1.8494 | 1.8621 | 1.5433 | 2.4387 | 2.7266 | 2.735 | 2.7461 | 2.8934
2021-10-11 08:00 | 1.9815 | 2.1612 | 2.1778 | 2.1981 | 2.2218 | 1.448 | 1.7342 | 1.7471 | 1.7648 | 1.448 | 2.191 | 2.4578 | 2.4694 | 2.4849 | 2.6238
2021-10-11 09:00 | 1.6957 | 1.8675 | 1.8909 | 1.9196 | 1.953 | 1.2765 | 1.5413 | 1.5595 | 1.5845 | 1.2765 | 1.7147 | 1.938 | 1.9543 | 1.9761 | 2.0964
2021-10-11 10:00 | 1.4861 | 1.6566 | 1.6873 | 1.7248 | 1.7686 | 1.086 | 1.3266 | 1.3505 | 1.3832 | 1.086 | 1.3908 | 1.5881 | 1.6096 | 1.6382 | 1.7488
2021-10-11 11:00 | 1.3337 | 1.5038 | 1.5401 | 1.5845 | 1.6362 | 0.93358 | 1.1544 | 1.1827 | 1.2214 | 0.93358 | 0.85737 | 1.003 | 1.0285 | 1.0622 | 1.1497
2021-10-11 12:00 | 1.2575 | 1.4263 | 1.4648 | 1.5119 | 1.5668 | 0.93358 | 1.1576 | 1.1876 | 1.2286 | 0.93358 | 0.85737 | 1.0061 | 1.0331 | 1.0689 | 1.1589
2021-10-11 13:00 | 1.2384 | 1.4048 | 1.4427 | 1.4892 | 1.5433 | 0.89547 | 1.1118 | 1.1414 | 1.1818 | 0.89547 | 1.105 | 1.2806 | 1.3072 | 1.3425 | 1.4455
2021-10-11 14:00 | 1.2765 | 1.4407 | 1.4761 | 1.5194 | 1.57 | 0.86232 | 1.069 | 1.0967 | 1.1344 | 0.86232 | 1.2194 | 1.4041 | 1.4289 | 1.4619 | 1.5683
2021-10-11 15:00 | 1.448 | 1.6195 | 1.6522 | 1.6921 | 1.7387 | 0.95263 | 1.1718 | 1.1973 | 1.232 | 0.95263 | 0.95263 | 1.1039 | 1.1267 | 1.1571 | 1.2458
2021-10-11 16:00 | 1.7719 | 1.9639 | 1.9947 | 2.0324 | 2.0764 | 1.2066 | 1.4692 | 1.4933 | 1.5261 | 1.2066 | 1.7338 | 1.9694 | 1.991 | 2.0197 | 2.1493
2021-10-11 17:00 | 1.9815 | 2.1882 | 2.2186 | 2.2557 | 2.2991 | 1.5242 | 1.8438 | 1.8675 | 1.8998 | 1.5242 | 2.032 | 2.3001 | 2.3214 | 2.3497 | 2.4952
2021-10-11 18:00 | 2.4578 | 2.7035 | 2.7357 | 2.775 | 2.821 | 2.0196 | 2.4316 | 2.4567 | 2.4909 | 2.0196 | 3.4866 | 3.9191 | 3.9417 | 3.9716 | 4.1991
2021-10-11 19:00 | 2.6102 | 2.8746 | 2.9105 | 2.9545 | 3.0058 | 2.2785 | 2.7428 | 2.7708 | 2.8091 | 2.2785 | 3.6771 | 4.1361 | 4.1613 | 4.1947 | 4.4369
2021-10-11 20:00 | 2.534 | 2.8025 | 2.8434 | 2.8935 | 2.9519 | 2.2863 | 2.7591 | 2.791 | 2.8346 | 2.2863 | 3.8296 | 4.3124 | 4.341 | 4.3791 | 4.6352
2021-10-11 21:00 | 2.553 | 2.8326 | 2.8785 | 2.9346 | 3 | 2.0958 | 2.5411 | 2.5768 | 2.6257 | 2.0958 | 3.277 | 3.7052 | 3.7374 | 3.78 | 4.0112
2021-10-11 22:00 | 2.4006 | 2.6705 | 2.7172 | 2.7743 | 2.841 | 1.984 | 2.4102 | 2.4466 | 2.4963 | 1.984 | 2.7289 | 3.0973 | 3.13 | 3.1735 | 3.3755
2021-10-11 23:00 | 2.3625 | 2.6236 | 2.6672 | 2.7207 | 2.783 | 1.8458 | 2.2426 | 2.2767 | 2.3232 | 1.8458 | 2.7055 | 3.067 | 3.0976 | 3.1382 | 3.3355
2021-10-12 | 2.0958 | 2.3286 | 2.3679 | 2.4161 | 2.4722 | 1.6048 | 1.9518 | 1.9825 | 2.0244 | 1.6048 | 1.9243 | 2.1929 | 2.2205 | 2.2571 | 2.4067
2021-10-12 01:00 | 1.9815 | 2.1963 | 2.2308 | 2.2731 | 2.3223 | 1.4099 | 1.7146 | 1.7416 | 1.7783 | 1.4099 | 1.7719 | 2.0169 | 2.0411 | 2.0732 | 2.209
2021-10-12 02:00 | 1.9815 | 2.1867 | 2.2164 | 2.2526 | 2.2949 | 1.3146 | 1.5952 | 1.6183 | 1.6498 | 1.3146 | 1.6957 | 1.9254 | 1.9462 | 1.9737 | 2.0999
2021-10-12 03:00 | 1.9624 | 2.1542 | 2.1776 | 2.2063 | 2.2398 | 1.1908 | 1.4401 | 1.4583 | 1.4833 | 1.1908 | 1.6195 | 1.8322 | 1.8486 | 1.8704 | 1.9855
2021-10-12 04:00 | 1.8481 | 2.0196 | 2.037 | 2.0583 | 2.0831 | 1.1216 | 1.3497 | 1.3633 | 1.3818 | 1.1216 | 1.6195 | 1.8238 | 1.836 | 1.8522 | 1.9606
2021-10-12 05:00 | 1.8481 | 2.0095 | 2.0218 | 2.0368 | 2.0543 | 1.1622 | 1.3904 | 1.4 | 1.413 | 1.1622 | 2.2863 | 2.5577 | 2.5663 | 2.5777 | 2.717
2021-10-12 06:00 | 1.9243 | 2.0874 | 2.0976 | 2.1102 | 2.1248 | 1.2575 | 1.5001 | 1.508 | 1.5189 | 1.2575 | 2.4768 | 2.7666 | 2.7738 | 2.7833 | 2.9308
2021-10-12 07:00 | 1.829 | 1.9884 | 2.0003 | 2.0149 | 2.032 | 1.3527 | 1.615 | 1.6243 | 1.637 | 1.3527 | 2.4387 | 2.7266 | 2.735 | 2.7461 | 2.8934
2021-10-12 08:00 | 1.6957 | 1.8542 | 1.8708 | 1.8911 | 1.9147 | 1.277 | 1.5321 | 1.5451 | 1.5627 | 1.277 | 2.8198 | 3.1565 | 3.1681 | 3.1835 | 3.357
2021-10-12 09:00 | 1.7909 | 1.9699 | 1.9933 | 2.0219 | 2.0553 | 1.3527 | 1.6313 | 1.6496 | 1.6745 | 1.3527 | 3.2961 | 3.6953 | 3.7116 | 3.7334 | 3.9407
2021-10-12 10:00 | 1.3146 | 1.4724 | 1.5031 | 1.5406 | 1.5844 | 0.99547 | 1.2196 | 1.2435 | 1.2762 | 0.99547 | 2.915 | 3.2819 | 3.3034 | 3.3319 | 3.5263
2021-10-12 11:00 | 1.1813 | 1.3401 | 1.3763 | 1.4207 | 1.4725 | 1.0288 | 1.267 | 1.2953 | 1.3339 | 1.0288 | 2.7245 | 3.0779 | 3.1033 | 3.1371 | 3.3272
2021-10-12 12:00 | 1.3146 | 1.4877 | 1.5262 | 1.5733 | 1.6282 | 1.1813 | 1.4502 | 1.4802 | 1.5212 | 1.1813 | 2.4959 | 2.8269 | 2.8539 | 2.8897 | 3.0698
2021-10-12 13:00 | 1.5814 | 1.7732 | 1.8111 | 1.8576 | 1.9118 | 1.2003 | 1.472 | 1.5015 | 1.542 | 1.2003 | 2.3625 | 2.678 | 2.7046 | 2.7399 | 2.912
2021-10-12 14:00 | 1.6766 | 1.8706 | 1.906 | 1.9493 | 1.9998 | 1.3337 | 1.6259 | 1.6535 | 1.6912 | 1.3337 | 2.4768 | 2.8015 | 2.8263 | 2.8592 | 3.0348
2021-10-12 15:00 | 1.9624 | 2.1722 | 2.2048 | 2.2448 | 2.2914 | 1.5359 | 1.8608 | 1.8863 | 1.921 | 1.5359 | 2.1923 | 2.4815 | 2.5043 | 2.5347 | 2.6916
2021-10-12 16:00 | 2.3125 | 2.5447 | 2.5755 | 2.6132 | 2.6571 | 1.9243 | 2.3171 | 2.3411 | 2.3739 | 1.9243 | 2.9478 | 3.3184 | 3.34 | 3.3687 | 3.565
2021-10-12 17:00 | 2.534 | 2.7818 | 2.8122 | 2.8493 | 2.8927 | 2.1625 | 2.5978 | 2.6215 | 2.6539 | 2.1625 | 3.62 | 4.0648 | 4.0861 | 4.1144 | 4.3472
2021-10-12 18:00 | 2.8769 | 3.1538 | 3.186 | 3.2254 | 3.2713 | 2.5721 | 3.0843 | 3.1094 | 3.1437 | 2.5721 | 3.9629 | 4.4485 | 4.471 | 4.5009 | 4.7546
2021-10-12 19:00 | 3.1818 | 3.4887 | 3.5246 | 3.5686 | 3.6199 | 2.8198 | 3.3823 | 3.4103 | 3.4486 | 2.8198 | 4.344 | 4.8771 | 4.9023 | 4.9357 | 5.2145
2021-10-12 20:00 | 3.1056 | 3.4165 | 3.4575 | 3.5075 | 3.5659 | 2.896 | 3.4794 | 3.5113 | 3.5549 | 2.896 | 3.8677 | 4.3547 | 4.3834 | 4.4215 | 4.6796
2021-10-12 21:00 | 3.0675 | 3.3853 | 3.4311 | 3.4873 | 3.5527 | 2.6483 | 3.1938 | 3.2296 | 3.2784 | 2.6483 | 3.8105 | 4.298 | 4.3302 | 4.3729 | 4.6334
2021-10-12 22:00 | 2.8769 | 3.1822 | 3.2289 | 3.286 | 3.3527 | 2.4959 | 3.0149 | 3.0513 | 3.1011 | 2.4959 | 3.6009 | 4.0663 | 4.099 | 4.1425 | 4.3924
2021-10-12 23:00 | 2.7436 | 3.033 | 3.0766 | 3.13 | 3.1923 | 2.1853 | 2.6436 | 2.6777 | 2.7242 | 2.1853 | 2.3625 | 2.6859 | 2.7165 | 2.7571 | 2.9356
2021-10-13 | 2.6102 | 2.8812 | 2.9206 | 2.9687 | 3.0249 | 1.9053 | 2.3067 | 2.3374 | 2.3793 | 1.9053 | 2.191 | 2.4894 | 2.5169 | 2.5535 | 2.7178
2021-10-13 01:00 | 2.251 | 2.4859 | 2.5205 | 2.5627 | 2.6119 | 1.7147 | 2.0748 | 2.1017 | 2.1384 | 1.7147 | 1.7909 | 2.0381 | 2.0622 | 2.0944 | 2.2312
2021-10-13 02:00 | 2.172 | 2.3914 | 2.4211 | 2.4573 | 2.4996 | 1.5757 | 1.9036 | 1.9267 | 1.9582 | 1.5757 | 2.2673 | 2.5606 | 2.5813 | 2.6089 | 2.7665
2021-10-13 03:00 | 2.1339 | 2.3384 | 2.3619 | 2.3906 | 2.424 | 1.4289 | 1.7214 | 1.7397 | 1.7647 | 1.4289 | 1.6004 | 1.811 | 1.8274 | 1.8492 | 1.9633
2021-10-13 04:00 | 2.172 | 2.3675 | 2.3849 | 2.4063 | 2.4311 | 1.3908 | 1.6678 | 1.6814 | 1.6999 | 1.3908 | 1.6576 | 1.8661 | 1.8783 | 1.8945 | 2.005
2021-10-13 05:00 | 2.1608 | 2.3454 | 2.3577 | 2.3727 | 2.3902 | 1.4861 | 1.773 | 1.7826 | 1.7957 | 1.4861 | 1.7909 | 2.0072 | 2.0158 | 2.0272 | 2.1393
2021-10-13 06:00 | 2.3816 | 2.5787 | 2.5889 | 2.6014 | 2.616 | 1.7897 | 2.1288 | 2.1367 | 2.1476 | 1.7897 | 2.2863 | 2.5549 | 2.562 | 2.5716 | 2.7086
2021-10-13 07:00 | 2.6293 | 2.8481 | 2.86 | 2.8746 | 2.8917 | 2.0767 | 2.4703 | 2.4796 | 2.4923 | 2.0767 | 2.8769 | 3.2136 | 3.2219 | 3.233 | 3.4045
2021-10-13 08:00 | 3.0103 | 3.2666 | 3.2831 | 3.3034 | 3.3271 | 2.2101 | 2.6345 | 2.6474 | 2.6651 | 2.2101 | 2.4959 | 2.7966 | 2.8082 | 2.8236 | 2.9793
2021-10-13 09:00 | 3.3533 | 3.6483 | 3.6717 | 3.7004 | 3.7338 | 2.6864 | 3.2069 | 3.2251 | 3.25 | 2.6864 | 2.534 | 2.8484 | 2.8648 | 2.8865 | 3.0519
2021-10-13 10:00 | 3.62 | 3.9492 | 3.9798 | 4.0174 | 4.0612 | 2.9341 | 3.5098 | 3.5338 | 3.5664 | 2.9341 | 2.0196 | 2.2868 | 2.3083 | 2.3369 | 2.482
2021-10-13 11:00 | 3.5057 | 3.8373 | 3.8735 | 3.9179 | 3.9697 | 2.7817 | 3.3377 | 3.366 | 3.4046 | 2.7817 | 1.105 | 1.2783 | 1.3037 | 1.3375 | 1.4386
2021-10-13 12:00 | 3.1849 | 3.497 | 3.5355 | 3.5826 | 3.6376 | 2.4458 | 2.944 | 2.9741 | 3.015 | 2.4458 | 1.7528 | 2.0012 | 2.0282 | 2.064 | 2.2032
2021-10-13 13:00 | 2.2482 | 2.4896 | 2.5276 | 2.574 | 2.6282 | 1.9158 | 2.3172 | 2.3468 | 2.3872 | 1.9158 | 1.7719 | 2.0216 | 2.0482 | 2.0836 | 2.2232
2021-10-13 14:00 | 2.896 | 3.1806 | 3.216 | 3.2593 | 3.3098 | 2.0767 | 2.5037 | 2.5313 | 2.569 | 2.0767 | 1.6766 | 1.9123 | 1.9371 | 1.97 | 2.1016
2021-10-13 15:00 | 2.9531 | 3.2366 | 3.2692 | 3.3092 | 3.3557 | 2.191 | 2.6348 | 2.6603 | 2.695 | 2.191 | 1.7719 | 2.0143 | 2.0371 | 2.0675 | 2.2013
2021-10-13 16:00 | 2.7055 | 2.9669 | 2.9977 | 3.0354 | 3.0794 | 2.0577 | 2.4746 | 2.4987 | 2.5315 | 2.0577 | 2.6483 | 2.9857 | 3.0072 | 3.0359 | 3.2158
2021-10-13 17:00 | 2.8579 | 3.1298 | 3.1601 | 3.1973 | 3.2407 | 2.3244 | 2.7891 | 2.8128 | 2.8452 | 2.3244 | 3.3533 | 3.7684 | 3.7897 | 3.818 | 4.0361
2021-10-13 18:00 | 3.4295 | 3.7474 | 3.7796 | 3.819 | 3.8649 | 3.0823 | 3.687 | 3.7121 | 3.7464 | 3.0823 | 3.6581 | 4.1097 | 4.1322 | 4.1622 | 4.3991
2021-10-13 19:00 | 3.8867 | 4.246 | 4.2819 | 4.3259 | 4.3772 | 3.4104 | 4.08 | 4.108 | 4.1463 | 3.4104 | 3.982 | 4.4748 | 4.5 | 4.5335 | 4.7924
2021-10-13 20:00 | 3.8105 | 4.1739 | 4.2148 | 4.2649 | 4.3233 | 3.3723 | 4.0421 | 4.074 | 4.1176 | 3.3723 | 3.4866 | 3.9313 | 3.9599 | 3.998 | 4.2352
2021-10-13 21:00 | 3.5438 | 3.897 | 3.9429 | 3.999 | 4.0644 | 3.0865 | 3.7115 | 3.7472 | 3.7961 | 3.0865 | 4.1916 | 4.7215 | 4.7536 | 4.7963 | 5.0778
2021-10-13 22:00 | 3.4104 | 3.7553 | 3.802 | 3.8592 | 3.9258 | 2.915 | 3.5101 | 3.5465 | 3.5962 | 2.915 | 2.5379 | 2.885 | 2.9177 | 2.9612 | 3.1527
2021-10-13 23:00 | 2.9722 | 3.2786 | 3.3222 | 3.3757 | 3.438 | 2.4696 | 2.9795 | 3.0136 | 3.0601 | 2.4696 | 2.191 | 2.4953 | 2.5259 | 2.5666 | 2.7356
2021-10-14 | 2.5149 | 2.7789 | 2.8182 | 2.8664 | 2.9225 | 2.0386 | 2.4643 | 2.4949 | 2.5368 | 2.0386 | 1.829 | 2.0871 | 2.1146 | 2.1513 | 2.2956
2021-10-14 01:00 | 2.4387 | 2.6876 | 2.7221 | 2.7643 | 2.8136 | 1.7714 | 2.1417 | 2.1687 | 2.2054 | 1.7714 | 1.7338 | 1.9745 | 1.9987 | 2.0308 | 2.1646
2021-10-14 02:00 | 2.2291 | 2.4528 | 2.4825 | 2.5187 | 2.561 | 1.6202 | 1.9562 | 1.9793 | 2.0108 | 1.6202 | 1.6385 | 1.8619 | 1.8826 | 1.9102 | 2.0333
2021-10-14 03:00 | 2.2291 | 2.4408 | 2.4642 | 2.4929 | 2.5264 | 1.5623 | 1.879 | 1.8973 | 1.9222 | 1.5623 | 1.467 | 1.6628 | 1.6792 | 1.701 | 1.8078
2021-10-14 04:00 | 2.2291 | 2.4289 | 2.4464 | 2.4677 | 2.4925 | 1.5052 | 1.8029 | 1.8165 | 1.835 | 1.5052 | 1.7338 | 1.9508 | 1.963 | 1.9792 | 2.0939
2021-10-14 05:00 | 2.3054 | 2.5007 | 2.513 | 2.528 | 2.5455 | 1.6195 | 1.9306 | 1.9402 | 1.9532 | 1.6195 | 1.7719 | 1.986 | 1.9946 | 2.006 | 2.1171
2021-10-14 06:00 | 2.4387 | 2.6401 | 2.6503 | 2.6628 | 2.6774 | 1.9339 | 2.2992 | 2.3072 | 2.3181 | 1.9339 | 2.1339 | 2.3855 | 2.3927 | 2.4022 | 2.5309
2021-10-14 07:00 | 2.7055 | 2.93 | 2.9419 | 2.9565 | 2.9735 | 2.0958 | 2.4928 | 2.5021 | 2.5149 | 2.0958 | 2.9722 | 3.3194 | 3.3278 | 3.3389 | 3.5156
2021-10-14 08:00 | 2.8007 | 3.0414 | 3.058 | 3.0783 | 3.1019 | 2.0958 | 2.4994 | 2.5124 | 2.53 | 2.0958 | 2.9722 | 3.3259 | 3.3375 | 3.3529 | 3.5348
2021-10-14 09:00 | 2.6674 | 2.9115 | 2.9349 | 2.9635 | 2.9969 | 1.9624 | 2.3516 | 2.3698 | 2.3947 | 1.9624 | 2.8769 | 3.2295 | 3.2459 | 3.2676 | 3.4518
2021-10-14 10:00 | 2.5911 | 2.8438 | 2.8745 | 2.912 | 2.9558 | 1.7528 | 2.1143 | 2.1383 | 2.1709 | 1.7528 | 2.5721 | 2.9008 | 2.9223 | 2.9508 | 3.1264
2021-10-14 11:00 | 2.534 | 2.7934 | 2.8296 | 2.874 | 2.9258 | 1.7719 | 2.1448 | 2.1731 | 2.2117 | 1.7719 | 2.6293 | 2.9721 | 2.9975 | 3.0312 | 3.2161
2021-10-14 12:00 | 2.5149 | 2.7772 | 2.8157 | 2.8628 | 2.9177 | 1.6576 | 2.0129 | 2.0429 | 2.0839 | 1.6576 | 3.1056 | 3.5044 | 3.5314 | 3.5672 | 3.7808
2021-10-14 13:00 | 2.4387 | 2.6943 | 2.7323 | 2.7787 | 2.8329 | 1.6576 | 2.0121 | 2.0417 | 2.0821 | 1.6576 | 2.2673 | 2.5721 | 2.5987 | 2.634 | 2.8009
2021-10-14 14:00 | 2.3625 | 2.6074 | 2.6428 | 2.6862 | 2.7367 | 1.4099 | 1.7159 | 1.7435 | 1.7812 | 1.4099 | 2.0386 | 2.3145 | 2.3393 | 2.3723 | 2.5238
2021-10-14 15:00 | 2.2101 | 2.4383 | 2.4709 | 2.5109 | 2.5574 | 1.5242 | 1.847 | 1.8725 | 1.9072 | 1.5242 | 1.6576 | 1.8872 | 1.9101 | 1.9405 | 2.068
2021-10-14 16:00 | 2.2482 | 2.4756 | 2.5064 | 2.5441 | 2.5881 | 1.6576 | 2.002 | 2.026 | 2.0588 | 1.6576 | 2.191 | 2.4775 | 2.4991 | 2.5278 | 2.6825
2021-10-14 17:00 | 2.6864 | 2.9456 | 2.9759 | 3.0131 | 3.0564 | 1.9272 | 2.3199 | 2.3436 | 2.3759 | 1.9272 | 2.0577 | 2.3287 | 2.35 | 2.3783 | 2.5252
2021-10-14 18:00 | 3.2389 | 3.5427 | 3.5749 | 3.6143 | 3.6602 | 2.6597 | 3.1878 | 3.2129 | 3.2472 | 2.6597 | 2.7817 | 3.1358 | 3.1583 | 3.1883 | 3.377
2021-10-14 19:00 | 3.4866 | 3.8162 | 3.8521 | 3.8961 | 3.9474 | 2.915 | 3.4948 | 3.5228 | 3.5611 | 2.915 | 3.0103 | 3.3951 | 3.4202 | 3.4537 | 3.6592
2021-10-14 20:00 | 3.3914 | 3.7236 | 3.7645 | 3.8146 | 3.873 | 2.896 | 3.4794 | 3.5113 | 3.5549 | 2.896 | 3.3151 | 3.7407 | 3.7694 | 3.8075 | 4.0353
2021-10-14 21:00 | 3.4104 | 3.7537 | 3.7996 | 3.8557 | 3.9211 | 2.8198 | 3.3964 | 3.4321 | 3.481 | 2.8198 | 2.9913 | 3.3876 | 3.4198 | 3.4625 | 3.678
2021-10-14 22:00 | 3.2389 | 3.5711 | 3.6178 | 3.675 | 3.7416 | 2.7245 | 3.285 | 3.3214 | 3.3712 | 2.7245 | 2.6483 | 3.0077 | 3.0404 | 3.0839 | 3.2814
2021-10-14 23:00 | 3.0103 | 3.3195 | 3.3632 | 3.4166 | 3.4789 | 2.3529 | 2.8416 | 2.8757 | 2.9222 | 2.3529 | 2.191 | 2.4953 | 2.5259 | 2.5666 | 2.7356
2021-10-15 | 2.6102 | 2.8812 | 2.9206 | 2.9687 | 3.0249 | 2.0386 | 2.4643 | 2.4949 | 2.5368 | 2.0386 | 1.8672 | 2.1294 | 2.157 | 2.1936 | 2.34
2021-10-15 01:00 | 2.3435 | 2.5852 | 2.6197 | 2.662 | 2.7112 | 1.7167 | 2.0771 | 2.104 | 2.1408 | 1.7167 | 1.7528 | 1.9957 | 2.0199 | 2.052 | 2.1868
2021-10-15 02:00 | 2.3244 | 2.5552 | 2.5848 | 2.6211 | 2.6633 | 1.5439 | 1.866 | 1.8891 | 1.9206 | 1.5439 | 1.7528 | 1.9889 | 2.0097 | 2.0372 | 2.1666
2021-10-15 03:00 | 2.191 | 2.3998 | 2.4233 | 2.452 | 2.4854 | 1.5052 | 1.8115 | 1.8297 | 1.8547 | 1.5052 | 1.829 | 2.0651 | 2.0815 | 2.1033 | 2.23
2021-10-15 04:00 | 2.1529 | 2.3471 | 2.3645 | 2.3858 | 2.4106 | 1.5163 | 1.8161 | 1.8297 | 1.8482 | 1.5163 | 1.8862 | 2.1202 | 2.1324 | 2.1486 | 2.2717
2021-10-15 05:00 | 2.3435 | 2.5417 | 2.5539 | 2.5689 | 2.5864 | 1.6197 | 1.9309 | 1.9405 | 1.9535 | 1.6197 | 1.9815 | 2.2189 | 2.2275 | 2.2389 | 2.3615
2021-10-15 06:00 | 2.534 | 2.7424 | 2.7526 | 2.7652 | 2.7798 | 1.9211 | 2.284 | 2.292 | 2.3029 | 1.9211 | 2.7245 | 3.0418 | 3.049 | 3.0585 | 3.2197
2021-10-15 07:00 | 2.7436 | 2.9709 | 2.9828 | 2.9974 | 3.0145 | 2.0958 | 2.4928 | 2.5021 | 2.5149 | 2.0958 | 3.2008 | 3.5735 | 3.5819 | 3.593 | 3.7822
2021-10-15 08:00 | 2.8388 | 3.0823 | 3.0989 | 3.1192 | 3.1429 | 2.3435 | 2.792 | 2.805 | 2.8226 | 2.3435 | 3.7915 | 4.2363 | 4.2479 | 4.2633 | 4.4902
2021-10-15 09:00 | 2.6864 | 2.9319 | 2.9553 | 2.984 | 3.0174 | 2.0196 | 2.4191 | 2.4374 | 2.4623 | 2.0196 | 2.915 | 3.2718 | 3.2882 | 3.31 | 3.4963
2021-10-15 10:00 | 2.4959 | 2.7415 | 2.7722 | 2.8097 | 2.8535 | 1.7147 | 2.0693 | 2.0933 | 2.1259 | 1.7147 | 1.81 | 2.0539 | 2.0754 | 2.104 | 2.2376
2021-10-15 11:00 | 1.9434 | 2.1588 | 2.1951 | 2.2395 | 2.2912 | 1.448 | 1.7622 | 1.7904 | 1.8291 | 1.448 | 2.172 | 2.4639 | 2.4893 | 2.5231 | 2.6829
2021-10-15 12:00 | 1.7909 | 1.9994 | 2.0379 | 2.085 | 2.1399 | 1.3337 | 1.6303 | 1.6603 | 1.7013 | 1.3337 | 2.1339 | 2.4247 | 2.4516 | 2.4875 | 2.6476
2021-10-15 13:00 | 2.2291 | 2.4691 | 2.5071 | 2.5535 | 2.6077 | 1.3527 | 1.652 | 1.6816 | 1.722 | 1.3527 | 1.6004 | 1.8311 | 1.8577 | 1.893 | 2.0232
2021-10-15 14:00 | 2.2101 | 2.4437 | 2.4791 | 2.5224 | 2.5729 | 1.5623 | 1.896 | 1.9236 | 1.9613 | 1.5623 | 1.8672 | 2.124 | 2.1488 | 2.1817 | 2.3238
2021-10-15 15:00 | 2.3435 | 2.5816 | 2.6142 | 2.6542 | 2.7007 | 1.2575 | 1.5319 | 1.5574 | 1.5921 | 1.2575 | 1.448 | 1.6544 | 1.6772 | 1.7076 | 1.8235
2021-10-15 16:00 | 2.1458 | 2.3656 | 2.3964 | 2.4341 | 2.4781 | 1.4289 | 1.7319 | 1.7559 | 1.7887 | 1.4289 | 1.81 | 2.0541 | 2.0757 | 2.1043 | 2.2381
2021-10-15 17:00 | 2.4959 | 2.7409 | 2.7712 | 2.8084 | 2.8517 | 1.7909 | 2.1589 | 2.1826 | 2.2149 | 1.7909 | 3.0484 | 3.4297 | 3.4509 | 3.4792 | 3.6806
2021-10-15 18:00 | 3.0957 | 3.3888 | 3.421 | 3.4604 | 3.5063 | 2.5366 | 3.0424 | 3.0675 | 3.1018 | 2.5366 | 4.1344 | 4.639 | 4.6615 | 4.6915 | 4.9546
2021-10-15 19:00 | 3.3621 | 3.6824 | 3.7183 | 3.7623 | 3.8136 | 2.8911 | 3.4665 | 3.4946 | 3.5328 | 2.8911 | 4.001 | 4.496 | 4.5212 | 4.5546 | 4.8146
2021-10-15 20:00 | 3.4866 | 3.8259 | 3.8668 | 3.9169 | 3.9753 | 2.9341 | 3.5244 | 3.5563 | 3.5999 | 2.9341 | 3.6962 | 4.1642 | 4.1928 | 4.2309 | 4.4797
2021-10-15 21:00 | 3.3342 | 3.6718 | 3.7177 | 3.7738 | 3.8393 | 2.8579 | 3.4414 | 3.4772 | 3.526 | 2.8579 | 3.5438 | 4.0016 | 4.0338 | 4.0765 | 4.3223
2021-10-15 22:00 | 3.2199 | 3.5507 | 3.5973 | 3.6545 | 3.7211 | 2.6293 | 3.1725 | 3.2089 | 3.2586 | 2.6293 | 3.0103 | 3.41 | 3.4427 | 3.4861 | 3.7036
2021-10-15 23:00 | 2.9531 | 3.2581 | 3.3018 | 3.3552 | 3.4175 | 2.3625 | 2.853 | 2.8871 | 2.9336 | 2.3625 | 2.7436 | 3.1093 | 3.1399 | 3.1806 | 3.38
2021-10-16 | 2.6102 | 2.8812 | 2.9206 | 2.9687 | 3.0249 | 1.9434 | 2.3517 | 2.3824 | 2.4243 | 1.9434 | 2.4387 | 2.7646 | 2.7922 | 2.8288 | 3.0066
2021-10-16 01:00 | 2.3816 | 2.6262 | 2.6607 | 2.7029 | 2.7522 | 1.679 | 2.0326 | 2.0595 | 2.0963 | 1.679 | 2.0005 | 2.2709 | 2.2951 | 2.3272 | 2.4756
2021-10-16 02:00 | 2.1148 | 2.33 | 2.3596 | 2.3959 | 2.4382 | 1.4657 | 1.7737 | 1.7968 | 1.8283 | 1.4657 | 1.9434 | 2.2006 | 2.2214 | 2.249 | 2.3888
2021-10-16 03:00 | 2.0958 | 2.2975 | 2.3209 | 2.3496 | 2.3831 | 1.3908 | 1.6764 | 1.6947 | 1.7197 | 1.3908 | 1.9434 | 2.1921 | 2.2085 | 2.2303 | 2.3633
2021-10-16 04:00 | 2.0386 | 2.2243 | 2.2417 | 2.263 | 2.2878 | 1.3527 | 1.6228 | 1.6364 | 1.6549 | 1.3527 | 1.8672 | 2.099 | 2.1112 | 2.1274 | 2.2495
2021-10-16 05:00 | 2.0577 | 2.2346 | 2.2469 | 2.2619 | 2.2794 | 1.4221 | 1.6974 | 1.707 | 1.72 | 1.4221 | 1.9815 | 2.2189 | 2.2275 | 2.2389 | 2.3615
2021-10-16 06:00 | 2.2482 | 2.4354 | 2.4456 | 2.4581 | 2.4727 | 1.7181 | 2.0442 | 2.0522 | 2.0631 | 1.7181 | 2.3435 | 2.6184 | 2.6255 | 2.6351 | 2.7753
2021-10-16 07:00 | 2.4578 | 2.6639 | 2.6758 | 2.6904 | 2.7074 | 1.81 | 2.1552 | 2.1645 | 2.1772 | 1.81 | 2.3435 | 2.6207 | 2.6291 | 2.6402 | 2.7823
2021-10-16 08:00 | 2.4197 | 2.632 | 2.6486 | 2.6689 | 2.6925 | 1.81 | 2.1618 | 2.1748 | 2.1924 | 1.81 | 2.4197 | 2.7119 | 2.7235 | 2.7389 | 2.8904
2021-10-16 09:00 | 2.3054 | 2.5225 | 2.5459 | 2.5746 | 2.608 | 1.6576 | 1.9915 | 2.0097 | 2.0346 | 1.6576 | 2.534 | 2.8484 | 2.8648 | 2.8865 | 3.0519
2021-10-16 10:00 | 2.0958 | 2.3116 | 2.3423 | 2.3799 | 2.4236 | 1.3718 | 1.6642 | 1.6881 | 1.7208 | 1.3718 | 1.4861 | 1.694 | 1.7155 | 1.744 | 1.8599
2021-10-16 11:00 | 2.2673 | 2.5068 | 2.5431 | 2.5874 | 2.6392 | 1.3617 | 1.6602 | 1.6885 | 1.7271 | 1.3617 | 1.6385 | 1.8711 | 1.8965 | 1.9303 | 2.0607
2021-10-16 12:00 | 2.2482 | 2.4907 | 2.5292 | 2.5763 | 2.6312 | 1.6004 | 1.9454 | 1.9754 | 2.0164 | 1.6004 | 1.5814 | 1.8107 | 1.8376 | 1.8735 | 2.0032
2021-10-16 13:00 | 2.1148 | 2.3463 | 2.3843 | 2.4307 | 2.4849 | 1.5052 | 1.8321 | 1.8617 | 1.9021 | 1.5052 | 1.1241 | 1.3018 | 1.3284 | 1.3637 | 1.4677
2021-10-16 14:00 | 1.9434 | 2.1571 | 2.1925 | 2.2359 | 2.2864 | 1.4099 | 1.7159 | 1.7435 | 1.7812 | 1.4099 | 1.0288 | 1.1924 | 1.2172 | 1.2502 | 1.3461
2021-10-16 15:00 | 2.1339 | 2.3564 | 2.389 | 2.429 | 2.4756 | 1.5433 | 1.8695 | 1.895 | 1.9298 | 1.5433 | 1.7528 | 1.9931 | 2.016 | 2.0464 | 2.1791
2021-10-16 16:00 | 2.1339 | 2.3528 | 2.3836 | 2.4213 | 2.4653 | 1.5433 | 1.8669 | 1.891 | 1.9238 | 1.5433 | 1.9434 | 2.2023 | 2.2239 | 2.2525 | 2.3937
2021-10-16 17:00 | 2.2863 | 2.5157 | 2.5461 | 2.5832 | 2.6266 | 1.6385 | 1.9788 | 2.0025 | 2.0349 | 1.6385 | 2.3435 | 2.6463 | 2.6676 | 2.6958 | 2.8585
2021-10-16 18:00 | 2.7626 | 3.031 | 3.0632 | 3.1025 | 3.1485 | 2.2769 | 2.7356 | 2.7607 | 2.7949 | 2.2769 | 3.0356 | 3.418 | 3.4405 | 3.4705 | 3.6732
2021-10-16 19:00 | 3.2008 | 3.5091 | 3.5451 | 3.589 | 3.6403 | 2.6483 | 3.1797 | 3.2077 | 3.246 | 2.6483 | 3.7724 | 4.2419 | 4.2671 | 4.3006 | 4.548
2021-10-16 20:00 | 3.2199 | 3.5394 | 3.5803 | 3.6303 | 3.6887 | 2.7626 | 3.3218 | 3.3537 | 3.3973 | 2.7626 | 3.6009 | 4.0583 | 4.087 | 4.1251 | 4.3686
2021-10-16 21:00 | 3.1437 | 3.4671 | 3.513 | 3.5691 | 3.6346 | 2.6302 | 3.1724 | 3.2082 | 3.257 | 2.6302 | 3.3914 | 3.8323 | 3.8644 | 3.9071 | 4.1446
2021-10-16 22:00 | 3.0103 | 3.3255 | 3.3722 | 3.4293 | 3.496 | 2.534 | 3.0599 | 3.0964 | 3.1461 | 2.534 | 3.1056 | 3.5158 | 3.5485 | 3.592 | 3.8147
2021-10-16 23:00 | 2.7817 | 3.0739 | 3.1176 | 3.171 | 3.2333 | 2.2851 | 2.7616 | 2.7956 | 2.8421 | 2.2851 | 2.5911 | 2.94 | 2.9705 | 3.0112 | 3.2022
2021-10-17 | 2.4959 | 2.7584 | 2.7978 | 2.8459 | 2.902 | 1.8931 | 2.2924 | 2.3231 | 2.365 | 1.8931 | 2.3816 | 2.7011 | 2.7286 | 2.7653 | 2.94
2021-10-17 01:00 | 2.2863 | 2.5238 | 2.5583 | 2.6006 | 2.6498 | 1.6069 | 1.9474 | 1.9743 | 2.0111 | 1.6069 | 2.172 | 2.4615 | 2.4857 | 2.5178 | 2.6756
2021-10-17 02:00 | 2.0577 | 2.2686 | 2.2982 | 2.3345 | 2.3768 | 1.4766 | 1.7865 | 1.8096 | 1.8411 | 1.4766 | 1.7719 | 2.0101 | 2.0308 | 2.0584 | 2.1888
2021-10-17 03:00 | 2.0005 | 2.1951 | 2.2186 | 2.2473 | 2.2808 | 1.3718 | 1.6539 | 1.6722 | 1.6972 | 1.3718 | 1.9624 | 2.2133 | 2.2297 | 2.2515 | 2.3855
2021-10-17 04:00 | 1.9434 | 2.1219 | 2.1393 | 2.1606 | 2.1855 | 1.2956 | 1.5553 | 1.5689 | 1.5874 | 1.2956 | 1.7719 | 1.9932 | 2.0054 | 2.0216 | 2.1384
2021-10-17 05:00 | 2.0767 | 2.2551 | 2.2674 | 2.2824 | 2.2999 | 1.3971 | 1.6679 | 1.6775 | 1.6905 | 1.3971 | 1.8862 | 2.1131 | 2.1216 | 2.1331 | 2.2504
2021-10-17 06:00 | 2.2673 | 2.4558 | 2.4661 | 2.4786 | 2.4932 | 1.6867 | 2.0071 | 2.0151 | 2.026 | 1.6867 | 2.191 | 2.449 | 2.4562 | 2.4657 | 2.5975
2021-10-17 07:00 | 2.3625 | 2.5615 | 2.5735 | 2.5881 | 2.6051 | 1.9053 | 2.2678 | 2.2771 | 2.2898 | 1.9053 | 2.1529 | 2.409 | 2.4174 | 2.4285 | 2.5601
2021-10-17 08:00 | 2.3625 | 2.5706 | 2.5872 | 2.6075 | 2.6311 | 1.7909 | 2.1393 | 2.1522 | 2.1699 | 1.7909 | 1.829 | 2.0555 | 2.0671 | 2.0826 | 2.2016
2021-10-17 09:00 | 2.1339 | 2.3383 | 2.3617 | 2.3904 | 2.4238 | 1.5814 | 1.9014 | 1.9197 | 1.9446 | 1.5814 | 1.8481 | 2.0862 | 2.1026 | 2.1243 | 2.252
2021-10-17 10:00 | 1.9624 | 2.1684 | 2.199 | 2.2366 | 2.2804 | 1.3146 | 1.5967 | 1.6206 | 1.6533 | 1.3146 | 0.81926 | 0.95295 | 0.97444 | 1.003 | 1.0822
2021-10-17 11:00 | 1.6957 | 1.8927 | 1.929 | 1.9734 | 2.0251 | 1.012 | 1.2471 | 1.2754 | 1.314 | 1.012 | 0.93358 | 1.0877 | 1.1131 | 1.1469 | 1.2386
2021-10-17 12:00 | 1.448 | 1.631 | 1.6695 | 1.7166 | 1.7715 | 0.95263 | 1.1801 | 1.2101 | 1.2511 | 0.95263 | 0.97168 | 1.1332 | 1.1601 | 1.1959 | 1.2922
2021-10-17 13:00 | 1.3214 | 1.4939 | 1.5318 | 1.5783 | 1.6324 | 0.83831 | 1.0443 | 1.0739 | 1.1143 | 0.83831 | 0.99073 | 1.1536 | 1.1802 | 1.2155 | 1.3122
2021-10-17 14:00 | 1.3337 | 1.5021 | 1.5375 | 1.5808 | 1.6314 | 0.93358 | 1.1532 | 1.1808 | 1.2185 | 0.93358 | 1.2384 | 1.4253 | 1.4501 | 1.483 | 1.5905
2021-10-17 15:00 | 2.1661 | 2.391 | 2.4236 | 2.4636 | 2.5101 | 1.4289 | 1.7345 | 1.76 | 1.7947 | 1.4289 | 1.105 | 1.2733 | 1.2961 | 1.3265 | 1.4236
2021-10-17 16:00 | 2.2101 | 2.4347 | 2.4655 | 2.5032 | 2.5472 | 1.4289 | 1.7319 | 1.7559 | 1.7887 | 1.4289 | 0.95263 | 1.1013 | 1.1229 | 1.1516 | 1.2383
2021-10-17 17:00 | 2.3244 | 2.5567 | 2.587 | 2.6242 | 2.6675 | 1.7252 | 2.0813 | 2.105 | 2.1373 | 1.7252 | 1.8481 | 2.0958 | 2.1171 | 2.1454 | 2.2808
2021-10-17 18:00 | 2.6483 | 2.9082 | 2.9403 | 2.9797 | 3.0256 | 2.2482 | 2.7017 | 2.7268 | 2.761 | 2.2482 | 3.1437 | 3.538 | 3.5606 | 3.5905 | 3.7992
2021-10-17 19:00 | 2.915 | 3.2021 | 3.238 | 3.282 | 3.3333 | 2.3816 | 2.8646 | 2.8926 | 2.9309 | 2.3816 | 2.9913 | 3.3739 | 3.3991 | 3.4325 | 3.637
2021-10-17 20:00 | 2.7817 | 3.0686 | 3.1095 | 3.1596 | 3.218 | 2.3435 | 2.8266 | 2.8586 | 2.9021 | 2.3435 | 3.0865 | 3.4867 | 3.5153 | 3.5534 | 3.7686
2021-10-17 21:00 | 2.6492 | 2.9359 | 2.9818 | 3.0379 | 3.1034 | 2.2482 | 2.7211 | 2.7569 | 2.8057 | 2.2482 | 3.6009 | 4.0652 | 4.0973 | 4.14 | 4.389
2021-10-17 22:00 | 2.5979 | 2.8824 | 2.9291 | 2.9862 | 3.0529 | 2.1148 | 2.5648 | 2.6012 | 2.6509 | 2.1148 | 2.4959 | 2.8383 | 2.871 | 2.9145 | 3.1037
2021-10-17 23:00 | 2.4387 | 2.7055 | 2.7491 | 2.8025 | 2.8648 | 1.9129 | 2.3219 | 2.3559 | 2.4024 | 1.9129 | 2.1339 | 2.4318 | 2.4624 | 2.503 | 2.6689
2021-10-18 | 2.1529 | 2.39 | 2.4293 | 2.4775 | 2.5336 | 1.6991 | 2.0632 | 2.0939 | 2.1358 | 1.6991 | 1.8862 | 2.1506 | 2.1782 | 2.2148 | 2.3623
2021-10-18 01:00 | 1.9624 | 2.1759 | 2.2104 | 2.2526 | 2.3018 | 1.5052 | 1.8272 | 1.8541 | 1.8909 | 1.5052 | 1.9434 | 2.2074 | 2.2316 | 2.2637 | 2.409
2021-10-18 02:00 | 1.8862 | 2.0844 | 2.114 | 2.1503 | 2.1925 | 1.3337 | 1.6177 | 1.6408 | 1.6723 | 1.3337 | 1.5433 | 1.756 | 1.7768 | 1.8044 | 1.9222
2021-10-18 03:00 | 1.7719 | 1.9495 | 1.973 | 2.0017 | 2.0351 | 1.2384 | 1.4963 | 1.5146 | 1.5396 | 1.2384 | 1.6385 | 1.8533 | 1.8698 | 1.8916 | 2.0078
2021-10-18 04:00 | 1.7528 | 1.9172 | 1.9346 | 1.9559 | 1.9808 | 1.1813 | 1.4202 | 1.4338 | 1.4524 | 1.1813 | 1.7147 | 1.9296 | 1.9418 | 1.958 | 2.0717
2021-10-18 05:00 | 1.7338 | 1.8867 | 1.8989 | 1.9139 | 1.9314 | 1.2003 | 1.4354 | 1.445 | 1.458 | 1.2003 | 2.0767 | 2.3248 | 2.3334 | 2.3448 | 2.4726
2021-10-18 06:00 | 1.8481 | 2.0055 | 2.0158 | 2.0283 | 2.0429 | 1.3337 | 1.5901 | 1.5981 | 1.609 | 1.3337 | 2.8769 | 3.2112 | 3.2184 | 3.2279 | 3.3974
2021-10-18 07:00 | 1.8672 | 2.0293 | 2.0413 | 2.0559 | 2.0729 | 1.448 | 1.7276 | 1.7369 | 1.7496 | 1.448 | 2.5149 | 2.8113 | 2.8197 | 2.8308 | 2.9823
2021-10-18 08:00 | 2.2101 | 2.4069 | 2.4234 | 2.4437 | 2.4674 | 1.6075 | 1.9226 | 1.9356 | 1.9532 | 1.6075 | 2.0386 | 2.2884 | 2.3 | 2.3155 | 2.446
2021-10-18 09:00 | 2.2482 | 2.4611 | 2.4845 | 2.5132 | 2.5466 | 1.81 | 2.1715 | 2.1898 | 2.2147 | 1.81 | 1.0669 | 1.2181 | 1.2345 | 1.2563 | 1.341
2021-10-18 10:00 | 2.5149 | 2.762 | 2.7926 | 2.8302 | 2.874 | 1.9243 | 2.3169 | 2.3408 | 2.3735 | 1.9243 | 0.91452 | 1.0588 | 1.0803 | 1.1089 | 1.1933
2021-10-18 11:00 | 2.3625 | 2.6091 | 2.6454 | 2.6898 | 2.7415 | 1.9053 | 2.3023 | 2.3306 | 2.3693 | 1.9053 | 0.99073 | 1.1513 | 1.1767 | 1.2104 | 1.3053
2021-10-18 12:00 | 2.4006 | 2.6544 | 2.6929 | 2.74 | 2.7949 | 2.0386 | 2.4631 | 2.4931 | 2.5341 | 2.0386 | 1.2956 | 1.4931 | 1.52 | 1.5559 | 1.6699
2021-10-18 13:00 | 2.3054 | 2.551 | 2.589 | 2.6354 | 2.6896 | 1.9243 | 2.3272 | 2.3568 | 2.3973 | 1.9243 | 1.2384 | 1.4288 | 1.4554 | 1.4907 | 1.6011
2021-10-18 14:00 | 2.191 | 2.4232 | 2.4586 | 2.502 | 2.5525 | 1.7338 | 2.0985 | 2.1262 | 2.1639 | 1.7338 | 1.3527 | 1.5523 | 1.5771 | 1.6101 | 1.7239
2021-10-18 15:00 | 1.81 | 2.0084 | 2.0411 | 2.081 | 2.1276 | 1.6195 | 1.9596 | 1.985 | 2.0198 | 1.6195 | 1.2384 | 1.4215 | 1.4443 | 1.4747 | 1.5791
2021-10-18 16:00 | 2.0577 | 2.2709 | 2.3017 | 2.3395 | 2.3834 | 1.5715 | 1.9003 | 1.9243 | 1.9571 | 1.5715 | 1.2384 | 1.4189 | 1.4405 | 1.4692 | 1.5715
2021-10-18 17:00 | 2.2291 | 2.4543 | 2.4847 | 2.5218 | 2.5652 | 1.8189 | 2.1919 | 2.2156 | 2.2479 | 1.8189 | 2.3816 | 2.6886 | 2.7099 | 2.7382 | 2.9029
2021-10-18 18:00 | 2.9913 | 3.2766 | 3.3088 | 3.3482 | 3.3941 | 2.4768 | 2.9718 | 2.9969 | 3.0311 | 2.4768 | 2.7626 | 3.1146 | 3.1371 | 3.1671 | 3.3548
2021-10-18 19:00 | 3.2008 | 3.5091 | 3.5451 | 3.589 | 3.6403 | 2.8198 | 3.3823 | 3.4103 | 3.4486 | 2.8198 | 2.6674 | 3.014 | 3.0391 | 3.0726 | 3.2592
2021-10-18 20:00 | 3.2199 | 3.5394 | 3.5803 | 3.6303 | 3.6887 | 2.9341 | 3.5244 | 3.5563 | 3.5999 | 2.9341 | 2.8769 | 3.2538 | 3.2824 | 3.3205 | 3.5242
2021-10-18 21:00 | 3.2008 | 3.5286 | 3.5744 | 3.6305 | 3.696 | 2.7436 | 3.3063 | 3.3421 | 3.3909 | 2.7436 | 2.8198 | 3.1971 | 3.2292 | 3.2719 | 3.478
2021-10-18 22:00 | 2.9341 | 3.2436 | 3.2903 | 3.3475 | 3.4141 | 2.5268 | 3.0514 | 3.0878 | 3.1375 | 2.5268 | 2.4197 | 2.7536 | 2.7863 | 2.8298 | 3.0148
2021-10-18 23:00 | 2.8388 | 3.1353 | 3.179 | 3.2324 | 3.2947 | 2.315 | 2.7969 | 2.8309 | 2.8774 | 2.315 | 2.0005 | 2.2836 | 2.3142 | 2.3548 | 2.5134
2021-10-19 | 2.6483 | 2.9222 | 2.9615 | 3.0097 | 3.0658 | 1.9638 | 2.3759 | 2.4066 | 2.4485 | 1.9638 | 1.6004 | 1.833 | 1.8606 | 1.8972 | 2.029
2021-10-19 01:00 | 2.4006 | 2.6466 | 2.6811 | 2.7234 | 2.7726 | 1.7991 | 2.1745 | 2.2014 | 2.2381 | 1.7991 | 1.448 | 1.6569 | 1.6811 | 1.7133 | 1.8313
2021-10-19 02:00 | 2.2673 | 2.4938 | 2.5234 | 2.5597 | 2.6019 | 1.6004 | 1.9328 | 1.9559 | 1.9874 | 1.6004 | 1.467 | 1.6713 | 1.6921 | 1.7197 | 1.8333
2021-10-19 03:00 | 2.172 | 2.3794 | 2.4028 | 2.4315 | 2.465 | 1.448 | 1.7439 | 1.7622 | 1.7872 | 1.448 | 1.3337 | 1.5146 | 1.531 | 1.5528 | 1.6523
2021-10-19 04:00 | 2.1339 | 2.3266 | 2.344 | 2.3653 | 2.3902 | 1.3908 | 1.6678 | 1.6814 | 1.6999 | 1.3908 | 1.5433 | 1.7391 | 1.7513 | 1.7675 | 1.8717
2021-10-19 05:00 | 2.1529 | 2.337 | 2.3493 | 2.3643 | 2.3818 | 1.448 | 1.728 | 1.7376 | 1.7506 | 1.448 | 1.5623 | 1.7531 | 1.7617 | 1.7731 | 1.8727
2021-10-19 06:00 | 2.172 | 2.3535 | 2.3637 | 2.3762 | 2.3909 | 1.5814 | 1.8827 | 1.8907 | 1.9016 | 1.5814 | 1.7909 | 2.0044 | 2.0116 | 2.0211 | 2.1309
2021-10-19 07:00 | 2.3054 | 2.5001 | 2.512 | 2.5267 | 2.5437 | 1.7528 | 2.0877 | 2.097 | 2.1097 | 1.7528 | 2.1529 | 2.409 | 2.4174 | 2.4285 | 2.5601
2021-10-19 08:00 | 2.1148 | 2.3045 | 2.3211 | 2.3414 | 2.365 | 1.5985 | 1.9119 | 1.9249 | 1.9425 | 1.5985 | 1.7338 | 1.9497 | 1.9613 | 1.9767 | 2.0905
2021-10-19 09:00 | 1.8672 | 2.0518 | 2.0752 | 2.1038 | 2.1372 | 1.3908 | 1.6763 | 1.6946 | 1.7195 | 1.3908 | 1.0669 | 1.2181 | 1.2345 | 1.2563 | 1.341
2021-10-19 10:00 | 1.9815 | 2.1888 | 2.2195 | 2.257 | 2.3008 | 1.5242 | 1.8442 | 1.8682 | 1.9008 | 1.5242 | 1.3337 | 1.5246 | 1.5461 | 1.5746 | 1.6821
2021-10-19 11:00 | 1.8481 | 2.0565 | 2.0927 | 2.1371 | 2.1889 | 1.4289 | 1.7397 | 1.7679 | 1.8066 | 1.4289 | 1.4099 | 1.617 | 1.6424 | 1.6762 | 1.7941
2021-10-19 12:00 | 2.0386 | 2.2655 | 2.304 | 2.3511 | 2.406 | 1.6576 | 2.0129 | 2.0429 | 2.0839 | 1.6576 | 1.2194 | 1.4084 | 1.4354 | 1.4712 | 1.5811
2021-10-19 13:00 | 2.0767 | 2.3054 | 2.3433 | 2.3898 | 2.4439 | 1.6766 | 2.0346 | 2.0642 | 2.1047 | 1.6766 | 1.2575 | 1.45 | 1.4766 | 1.5119 | 1.6233
2021-10-19 14:00 | 2.0005 | 2.2185 | 2.2539 | 2.2973 | 2.3478 | 1.6576 | 2.0085 | 2.0361 | 2.0738 | 1.6576 | 1.3337 | 1.5312 | 1.556 | 1.5889 | 1.7016
2021-10-19 15:00 | 1.8862 | 2.0903 | 2.123 | 2.1629 | 2.2095 | 1.4099 | 1.712 | 1.7374 | 1.7722 | 1.4099 | 1.2194 | 1.4003 | 1.4232 | 1.4535 | 1.5569
2021-10-19 16:00 | 1.829 | 2.0253 | 2.0561 | 2.0938 | 2.1378 | 1.5814 | 1.912 | 1.936 | 1.9688 | 1.5814 | 1.4861 | 1.6942 | 1.7157 | 1.7444 | 1.8604
2021-10-19 17:00 | 2.3054 | 2.5362 | 2.5665 | 2.6037 | 2.647 | 1.9815 | 2.384 | 2.4077 | 2.44 | 1.9815 | 2.0577 | 2.3287 | 2.35 | 2.3783 | 2.5252
2021-10-19 18:00 | 3.0103 | 3.2971 | 3.3293 | 3.3686 | 3.4146 | 2.5911 | 3.1068 | 3.1319 | 3.1662 | 2.5911 | 2.553 | 2.8817 | 2.9042 | 2.9342 | 3.1104
2021-10-19 19:00 | 3.277 | 3.591 | 3.6269 | 3.6709 | 3.7222 | 2.9341 | 3.5173 | 3.5453 | 3.5836 | 2.9341 | 3.277 | 3.6915 | 3.7166 | 3.7501 | 3.9702
2021-10-19 20:00 | 3.3342 | 3.6622 | 3.7031 | 3.7532 | 3.8116 | 2.9531 | 3.5469 | 3.5788 | 3.6224 | 2.9531 | 2.9913 | 3.3808 | 3.4095 | 3.4475 | 3.6575
2021-10-19 21:00 | 3.1649 | 3.4899 | 3.5358 | 3.5919 | 3.6573 | 2.7626 | 3.3288 | 3.3646 | 3.4134 | 2.7626 | 2.9913 | 3.3876 | 3.4198 | 3.4625 | 3.678
2021-10-19 22:00 | 3.0294 | 3.346 | 3.3927 | 3.4498 | 3.5164 | 2.5526 | 3.082 | 3.1184 | 3.1681 | 2.5526 | 2.553 | 2.9018 | 2.9345 | 2.978 | 3.1703
2021-10-19 23:00 | 2.7414 | 3.0307 | 3.0743 | 3.1277 | 3.19 | 2.2006 | 2.6618 | 2.6959 | 2.7423 | 2.2006 | 2.2673 | 2.58 | 2.6106 | 2.6512 | 2.8245
2021-10-20 | 2.4768 | 2.738 | 2.7773 | 2.8254 | 2.8816 | 1.9434 | 2.3517 | 2.3824 | 2.4243 | 1.9434 | 2.2101 | 2.5105 | 2.5381 | 2.5747 | 2.74
2021-10-20 01:00 | 2.2673 | 2.5034 | 2.5379 | 2.5801 | 2.6294 | 1.6437 | 1.9909 | 2.0178 | 2.0545 | 1.6437 | 1.5433 | 1.7628 | 1.787 | 1.8191 | 1.9424
2021-10-20 02:00 | 2.1529 | 2.371 | 2.4006 | 2.4368 | 2.4791 | 1.4547 | 1.7606 | 1.7837 | 1.8152 | 1.4547 | 1.5814 | 1.7984 | 1.8191 | 1.8467 | 1.9666
2021-10-20 03:00 | 2.0958 | 2.2975 | 2.3209 | 2.3496 | 2.3831 | 1.4289 | 1.7214 | 1.7397 | 1.7647 | 1.4289 | 1.6576 | 1.8745 | 1.8909 | 1.9128 | 2.03
2021-10-20 04:00 | 2.0196 | 2.2038 | 2.2212 | 2.2425 | 2.2674 | 1.3337 | 1.6003 | 1.6139 | 1.6324 | 1.3337 | 1.6576 | 1.8661 | 1.8783 | 1.8945 | 2.005
2021-10-20 05:00 | 2.0577 | 2.2346 | 2.2469 | 2.2619 | 2.2794 | 1.3908 | 1.6605 | 1.6701 | 1.6831 | 1.3908 | 1.7719 | 1.986 | 1.9946 | 2.006 | 2.1171
2021-10-20 06:00 | 2.3054 | 2.4968 | 2.507 | 2.5195 | 2.5341 | 1.6385 | 1.9502 | 1.9582 | 1.9691 | 1.6385 | 2.191 | 2.449 | 2.4562 | 2.4657 | 2.5975
2021-10-20 07:00 | 2.4578 | 2.6639 | 2.6758 | 2.6904 | 2.7074 | 1.8672 | 2.2227 | 2.232 | 2.2448 | 1.8672 | 2.172 | 2.4302 | 2.4386 | 2.4497 | 2.5824
2021-10-20 08:00 | 2.4387 | 2.6525 | 2.6691 | 2.6894 | 2.713 | 1.7091 | 2.0426 | 2.0556 | 2.0732 | 1.7091 | 2.6102 | 2.9236 | 2.9352 | 2.9506 | 3.1126
2021-10-20 09:00 | 2.191 | 2.3997 | 2.4231 | 2.4518 | 2.4852 | 1.5511 | 1.8657 | 1.884 | 1.9089 | 1.5511 | 2.0005 | 2.2555 | 2.2719 | 2.2937 | 2.4297
2021-10-20 10:00 | 1.9434 | 2.1479 | 2.1786 | 2.2161 | 2.2599 | 1.3906 | 1.6864 | 1.7103 | 1.743 | 1.3906 | 1.5623 | 1.7787 | 1.8002 | 1.8287 | 1.9488
2021-10-20 11:00 | 2.0005 | 2.2202 | 2.2565 | 2.3009 | 2.3526 | 1.467 | 1.7847 | 1.813 | 1.8516 | 1.467 | 1.8672 | 2.1252 | 2.1506 | 2.1843 | 2.3274
2021-10-20 12:00 | 1.7463 | 1.9514 | 1.9899 | 2.037 | 2.0919 | 1.3094 | 1.6016 | 1.6316 | 1.6726 | 1.3094 | 2.4387 | 2.7634 | 2.7904 | 2.8262 | 3.0031
2021-10-20 13:00 | 2.3816 | 2.6329 | 2.6708 | 2.7173 | 2.7714 | 1.9053 | 2.3047 | 2.3343 | 2.3748 | 1.9053 | 1.5288 | 1.7515 | 1.7781 | 1.8134 | 1.9397
2021-10-20 14:00 | 2.5149 | 2.7712 | 2.8066 | 2.8499 | 2.9004 | 1.937 | 2.3387 | 2.3663 | 2.404 | 1.937 | 1.105 | 1.2771 | 1.3019 | 1.3348 | 1.435
2021-10-20 15:00 | 2.9531 | 3.2366 | 3.2692 | 3.3092 | 3.3557 | 2.4428 | 2.9322 | 2.9577 | 2.9924 | 2.4428 | 1.1432 | 1.3156 | 1.3385 | 1.3688 | 1.468
2021-10-20 16:00 | 3.1246 | 3.4172 | 3.448 | 3.4857 | 3.5297 | 2.553 | 3.0599 | 3.0839 | 3.1167 | 2.553 | 1.6957 | 1.9271 | 1.9486 | 1.9773 | 2.1048
2021-10-20 17:00 | 3.3723 | 3.6824 | 3.7128 | 3.75 | 3.7933 | 2.6864 | 3.2168 | 3.2405 | 3.2728 | 2.6864 | 2.3435 | 2.6463 | 2.6676 | 2.6958 | 2.8585
2021-10-20 18:00 | 3.5819 | 3.9112 | 3.9433 | 3.9827 | 4.0286 | 3.2149 | 3.8437 | 3.8688 | 3.9031 | 3.2149 | 3.1056 | 3.4957 | 3.5182 | 3.5482 | 3.7547
2021-10-20 19:00 | 3.8677 | 4.2255 | 4.2615 | 4.3055 | 4.3567 | 3.5247 | 4.215 | 4.2431 | 4.2813 | 3.5247 | 3.0484 | 3.4374 | 3.4626 | 3.496 | 3.7036
2021-10-20 20:00 | 3.8677 | 4.2353 | 4.2762 | 4.3263 | 4.3847 | 3.5438 | 4.2446 | 4.2766 | 4.3201 | 3.5438 | 3.258 | 3.6772 | 3.7059 | 3.744 | 3.9686
2021-10-20 21:00 | 3.7152 | 4.0812 | 4.1271 | 4.1832 | 4.2487 | 3.2961 | 3.9591 | 3.9948 | 4.0437 | 3.2961 | 2.7817 | 3.1547 | 3.1869 | 3.2296 | 3.4335
2021-10-20 22:00 | 3.4295 | 3.7758 | 3.8225 | 3.8796 | 3.9463 | 2.967 | 3.5715 | 3.6079 | 3.6576 | 2.967 | 2.4768 | 2.8171 | 2.8499 | 2.8933 | 3.0815
2021-10-20 23:00 | 3.1818 | 3.5038 | 3.5474 | 3.6008 | 3.6631 | 2.6008 | 3.1345 | 3.1685 | 3.215 | 2.6008 | 1.9624 | 2.2413 | 2.2719 | 2.3125 | 2.469
2021-10-21 | 2.7245 | 3.0041 | 3.0434 | 3.0915 | 3.1477 | 2.1432 | 2.5878 | 2.6184 | 2.6603 | 2.1432 | 1.9053 | 2.1718 | 2.1993 | 2.236 | 2.3845
2021-10-21 01:00 | 2.4959 | 2.749 | 2.7835 | 2.8257 | 2.875 | 1.7719 | 2.1423 | 2.1692 | 2.206 | 1.7719 | 1.4861 | 1.6993 | 1.7235 | 1.7556 | 1.8757
2021-10-21 02:00 | 2.2482 | 2.4733 | 2.5029 | 2.5392 | 2.5815 | 1.6656 | 2.0097 | 2.0328 | 2.0644 | 1.6656 | 1.5052 | 1.7137 | 1.7344 | 1.762 | 1.8777
2021-10-21 03:00 | 2.2482 | 2.4612 | 2.4847 | 2.5134 | 2.5468 | 1.6004 | 1.924 | 1.9423 | 1.9673 | 1.6004 | 1.4099 | 1.5993 | 1.6157 | 1.6375 | 1.7411
2021-10-21 04:00 | 2.3054 | 2.5108 | 2.5282 | 2.5495 | 2.5744 | 1.5623 | 1.8704 | 1.884 | 1.9025 | 1.5623 | 1.4289 | 1.6121 | 1.6243 | 1.6405 | 1.7384
2021-10-21 05:00 | 2.2863 | 2.4803 | 2.4925 | 2.5075 | 2.525 | 1.6385 | 1.9531 | 1.9627 | 1.9757 | 1.6385 | 1.622 | 1.8195 | 1.8281 | 1.8395 | 1.9423
2021-10-21 06:00 | 2.5911 | 2.8038 | 2.814 | 2.8266 | 2.8412 | 1.9815 | 2.3554 | 2.3633 | 2.3742 | 1.9815 | 1.9053 | 2.1314 | 2.1386 | 2.1481 | 2.2642
2021-10-21 07:00 | 2.7245 | 2.9504 | 2.9624 | 2.977 | 2.994 | 2.172 | 2.5829 | 2.5922 | 2.6049 | 2.172 | 1.9053 | 2.1338 | 2.1421 | 2.1533 | 2.2713
2021-10-21 08:00 | 2.8388 | 3.0823 | 3.0989 | 3.1192 | 3.1429 | 2.172 | 2.5895 | 2.6024 | 2.6201 | 2.172 | 1.81 | 2.0344 | 2.046 | 2.0614 | 2.1794
2021-10-21 09:00 | 2.6293 | 2.8705 | 2.8939 | 2.9226 | 2.956 | 2.0577 | 2.4641 | 2.4824 | 2.5073 | 2.0577 | 2.0005 | 2.2555 | 2.2719 | 2.2937 | 2.4297
2021-10-21 10:00 | 2.6293 | 2.8848 | 2.9154 | 2.953 | 2.9968 | 1.9624 | 2.3619 | 2.3859 | 2.4185 | 1.9624 | 2.191 | 2.4774 | 2.4988 | 2.5274 | 2.682
2021-10-21 11:00 | 2.915 | 3.2027 | 3.239 | 3.2834 | 3.3352 | 2.172 | 2.6175 | 2.6457 | 2.6844 | 2.172 | 1.3527 | 1.5535 | 1.5789 | 1.6127 | 1.7274
2021-10-21 12:00 | 2.4959 | 2.7568 | 2.7952 | 2.8424 | 2.8973 | 1.9434 | 2.3505 | 2.3805 | 2.4215 | 1.9434 | 1.0669 | 1.239 | 1.266 | 1.3018 | 1.4033
2021-10-21 13:00 | 2.4578 | 2.7148 | 2.7527 | 2.7992 | 2.8533 | 1.9434 | 2.3498 | 2.3794 | 2.4198 | 1.9434 | 1.9434 | 2.2122 | 2.2388 | 2.2741 | 2.4232
2021-10-21 14:00 | 2.4197 | 2.6689 | 2.7043 | 2.7476 | 2.7981 | 1.7909 | 2.1661 | 2.1937 | 2.2314 | 1.7909 | 1.467 | 1.6794 | 1.7042 | 1.7371 | 1.8572
2021-10-21 15:00 | 2.2291 | 2.4588 | 2.4914 | 2.5313 | 2.5779 | 1.7528 | 2.1171 | 2.1426 | 2.1773 | 1.7528 | 1.3527 | 1.5485 | 1.5714 | 1.6017 | 1.7124
2021-10-21 16:00 | 2.6483 | 2.9055 | 2.9363 | 2.974 | 3.018 | 1.9053 | 2.2946 | 2.3186 | 2.3514 | 1.9053 | 1.2575 | 1.4401 | 1.4617 | 1.4903 | 1.5938
2021-10-21 17:00 | 2.7055 | 2.966 | 2.9964 | 3.0336 | 3.0769 | 2.0577 | 2.474 | 2.4977 | 2.53 | 2.0577 | 1.9624 | 2.2229 | 2.2441 | 2.2724 | 2.4141
2021-10-21 18:00 | 3.2389 | 3.5427 | 3.5749 | 3.6143 | 3.6602 | 2.7346 | 3.2763 | 3.3014 | 3.3357 | 2.7346 | 2.3625 | 2.67 | 2.6925 | 2.7225 | 2.8882
2021-10-21 19:00 | 3.62 | 3.9594 | 3.9954 | 4.0394 | 4.0906 | 3.1627 | 3.7874 | 3.8154 | 3.8537 | 3.1627 | 2.8198 | 3.1833 | 3.2085 | 3.242 | 3.437
2021-10-21 20:00 | 3.5628 | 3.9078 | 3.9487 | 3.9988 | 4.0572 | 3.2389 | 3.8845 | 3.9164 | 3.96 | 3.2389 | 2.6102 | 2.9573 | 2.986 | 3.0241 | 3.2131
2021-10-21 21:00 | 3.5819 | 3.9379 | 3.9838 | 4.0399 | 4.1054 | 3.1246 | 3.7565 | 3.7923 | 3.8411 | 3.1246 | 2.6293 | 2.9854 | 3.0175 | 3.0602 | 3.2558
2021-10-21 22:00 | 3.5057 | 3.8577 | 3.9044 | 3.9615 | 4.0282 | 2.8769 | 3.4651 | 3.5015 | 3.5512 | 2.8769 | 2.4578 | 2.796 | 2.8287 | 2.8722 | 3.0592
2021-10-21 23:00 | 3.2389 | 3.5652 | 3.6088 | 3.6622 | 3.7245 | 2.6359 | 3.176 | 3.2101 | 3.2566 | 2.6359 | 1.829 | 2.0931 | 2.1237 | 2.1643 | 2.3134
2021-10-22 | 2.7817 | 3.0655 | 3.1048 | 3.1529 | 3.2091 | 2.2101 | 2.6668 | 2.6975 | 2.7394 | 2.2101 | 1.5433 | 1.7695 | 1.7971 | 1.8337 | 1.9623
2021-10-22 01:00 | 2.4959 | 2.749 | 2.7835 | 2.8257 | 2.875 | 1.8445 | 2.2281 | 2.255 | 2.2917 | 1.8445 | 1.3527 | 1.5511 | 1.5753 | 1.6074 | 1.7202
2021-10-22 02:00 | 2.4197 | 2.6575 | 2.6872 | 2.7234 | 2.7657 | 1.6679 | 2.0125 | 2.0356 | 2.0671 | 1.6679 | 1.3527 | 1.5443 | 1.5651 | 1.5926 | 1.7
2021-10-22 03:00 | 2.3244 | 2.5431 | 2.5666 | 2.5953 | 2.6287 | 1.5513 | 1.8659 | 1.8842 | 1.9092 | 1.5513 | 1.3146 | 1.4934 | 1.5098 | 1.5317 | 1.63
2021-10-22 04:00 | 2.2673 | 2.4699 | 2.4873 | 2.5086 | 2.5334 | 1.6147 | 1.9323 | 1.9458 | 1.9644 | 1.6147 | 1.2384 | 1.4003 | 1.4125 | 1.4287 | 1.5162
2021-10-22 05:00 | 2.3435 | 2.5417 | 2.5539 | 2.5689 | 2.5864 | 1.6957 | 2.0206 | 2.0302 | 2.0433 | 1.6957 | 1.3908 | 1.5626 | 1.5712 | 1.5826 | 1.6727
2021-10-22 06:00 | 2.6293 | 2.8447 | 2.855 | 2.8675 | 2.8821 | 2.06 | 2.4482 | 2.4562 | 2.4671 | 2.06 | 1.7338 | 1.9409 | 1.948 | 1.9576 | 2.0643
2021-10-22 07:00 | 2.7055 | 2.93 | 2.9419 | 2.9565 | 2.9735 | 2.2101 | 2.6279 | 2.6372 | 2.6499 | 2.2101 | 1.9815 | 2.2185 | 2.2268 | 2.2379 | 2.3602
2021-10-22 08:00 | 2.7245 | 2.9595 | 2.9761 | 2.9964 | 3.0201 | 2.2863 | 2.7245 | 2.7374 | 2.7551 | 2.2863 | 1.2575 | 1.4204 | 1.432 | 1.4474 | 1.535
2021-10-22 09:00 | 2.7055 | 2.9524 | 2.9758 | 3.0044 | 3.0378 | 2.0577 | 2.4641 | 2.4824 | 2.5073 | 2.0577 | 0.83831 | 0.96403 | 0.98042 | 1.0022 | 1.0743
2021-10-22 10:00 | 2.2313 | 2.4572 | 2.4879 | 2.5255 | 2.5692 | 1.5814 | 1.9118 | 1.9357 | 1.9684 | 1.5814 | 1.1241 | 1.2917 | 1.3132 | 1.3418 | 1.4377
2021-10-22 11:00 | 1.7909 | 1.9951 | 2.0313 | 2.0757 | 2.1275 | 1.2575 | 1.5371 | 1.5654 | 1.604 | 1.2575 | 1.105 | 1.2783 | 1.3037 | 1.3375 | 1.4386
2021-10-22 12:00 | 1.6195 | 1.8152 | 1.8537 | 1.9008 | 1.9557 | 1.0827 | 1.3337 | 1.3638 | 1.4047 | 1.0827 | 1.2956 | 1.4931 | 1.52 | 1.5559 | 1.6699
2021-10-22 13:00 | 1.5623 | 1.7527 | 1.7907 | 1.8371 | 1.8913 | 1.0479 | 1.2919 | 1.3215 | 1.3619 | 1.0479 | 1.4861 | 1.7041 | 1.7306 | 1.766 | 1.8899
2021-10-22 14:00 | 1.4861 | 1.6659 | 1.7013 | 1.7446 | 1.7951 | 0.97168 | 1.1982 | 1.2258 | 1.2635 | 0.97168 | 1.467 | 1.6794 | 1.7042 | 1.7371 | 1.8572
2021-10-22 15:00 | 1.6576 | 1.8447 | 1.8773 | 1.9173 | 1.9638 | 1.0479 | 1.2843 | 1.3098 | 1.3446 | 1.0479 | 1.1432 | 1.3156 | 1.3385 | 1.3688 | 1.468
2021-10-22 16:00 | 1.7719 | 1.9639 | 1.9947 | 2.0324 | 2.0764 | 1.2705 | 1.5447 | 1.5687 | 1.6015 | 1.2705 | 1.3105 | 1.4991 | 1.5206 | 1.5493 | 1.6557
2021-10-22 17:00 | 2.2863 | 2.5157 | 2.5461 | 2.5832 | 2.6266 | 1.7182 | 2.073 | 2.0967 | 2.129 | 1.7182 | 1.7147 | 1.9476 | 1.9689 | 1.9972 | 2.1252
2021-10-22 18:00 | 2.796 | 3.0669 | 3.0991 | 3.1384 | 3.1844 | 2.3625 | 2.8367 | 2.8618 | 2.8961 | 2.3625 | 2.0196 | 2.2889 | 2.3114 | 2.3414 | 2.4882
2021-10-22 19:00 | 3.3533 | 3.6729 | 3.7088 | 3.7528 | 3.8041 | 2.8439 | 3.4108 | 3.4388 | 3.477 | 2.8439 | 2.2482 | 2.5482 | 2.5733 | 2.6068 | 2.7704
2021-10-22 20:00 | 3.3151 | 3.6417 | 3.6826 | 3.7327 | 3.7911 | 2.8579 | 3.4344 | 3.4663 | 3.5098 | 2.8579 | 2.4006 | 2.7245 | 2.7531 | 2.7912 | 2.9687
2021-10-22 21:00 | 3.0865 | 3.4057 | 3.4516 | 3.5077 | 3.5732 | 2.6293 | 3.1713 | 3.2071 | 3.2559 | 2.6293 | 2.5721 | 2.9219 | 2.954 | 2.9967 | 3.1891
2021-10-22 22:00 | 2.9547 | 3.2658 | 3.3125 | 3.3696 | 3.4362 | 2.5911 | 3.1275 | 3.1639 | 3.2136 | 2.5911 | 2.2101 | 2.5207 | 2.5534 | 2.5969 | 2.7704
2021-10-22 23:00 | 2.7436 | 3.033 | 3.0766 | 3.13 | 3.1923 | 2.2107 | 2.6737 | 2.7077 | 2.7542 | 2.2107 | 1.8481 | 2.1142 | 2.1448 | 2.1855 | 2.3356
2021-10-23 | 2.4959 | 2.7584 | 2.7978 | 2.8459 | 2.902 | 1.9675 | 2.3802 | 2.4109 | 2.4528 | 1.9675 | 1.6385 | 1.8754 | 1.9029 | 1.9395 | 2.0734
2021-10-23 01:00 | 2.3244 | 2.5648 | 2.5993 | 2.6415 | 2.6908 | 1.6363 | 1.9821 | 2.009 | 2.0458 | 1.6363 | 1.5052 | 1.7205 | 1.7446 | 1.7768 | 1.8979
2021-10-23 02:00 | 2.0958 | 2.3096 | 2.3392 | 2.3754 | 2.4177 | 1.5242 | 1.8427 | 1.8658 | 1.8974 | 1.5242 | 1.2575 | 1.4384 | 1.4592 | 1.4868 | 1.5889
2021-10-23 03:00 | 2.0577 | 2.2565 | 2.28 | 2.3087 | 2.3422 | 1.4251 | 1.7169 | 1.7352 | 1.7601 | 1.4251 | 1.2194 | 1.3875 | 1.404 | 1.4258 | 1.5189
2021-10-23 04:00 | 2.0196 | 2.2038 | 2.2212 | 2.2425 | 2.2674 | 1.3527 | 1.6228 | 1.6364 | 1.6549 | 1.3527 | 1.2575 | 1.4215 | 1.4337 | 1.4499 | 1.5384
2021-10-23 05:00 | 2.0958 | 2.2756 | 2.2878 | 2.3029 | 2.3204 | 1.4165 | 1.6908 | 1.7004 | 1.7135 | 1.4165 | 1.3337 | 1.4991 | 1.5077 | 1.5191 | 1.606
2021-10-23 06:00 | 2.172 | 2.3535 | 2.3637 | 2.3762 | 2.3909 | 1.6663 | 1.9831 | 1.9911 | 2.002 | 1.6663 | 1.467 | 1.6445 | 1.6516 | 1.6611 | 1.7532
2021-10-23 07:00 | 2.3982 | 2.5999 | 2.6118 | 2.6264 | 2.6435 | 2.0005 | 2.3803 | 2.3896 | 2.4023 | 2.0005 | 1.2765 | 1.4351 | 1.4435 | 1.4546 | 1.538
2021-10-23 08:00 | 2.8579 | 3.1028 | 3.1194 | 3.1397 | 3.1633 | 2.1586 | 2.5737 | 2.5866 | 2.6043 | 2.1586 | 1.6385 | 1.8438 | 1.8554 | 1.8709 | 1.9794
2021-10-23 09:00 | 2.896 | 3.1571 | 3.1805 | 3.2091 | 3.2425 | 2.2726 | 2.718 | 2.7363 | 2.7612 | 2.2726 | 1.1241 | 1.2816 | 1.298 | 1.3198 | 1.4076
2021-10-23 10:00 | 3.0103 | 3.2941 | 3.3248 | 3.3624 | 3.4061 | 2.2863 | 2.7446 | 2.7685 | 2.8012 | 2.2863 | 0.93358 | 1.08 | 1.1015 | 1.13 | 1.2155
2021-10-23 11:00 | 2.7817 | 3.0595 | 3.0957 | 3.1401 | 3.1919 | 2.0577 | 2.4824 | 2.5107 | 2.5493 | 2.0577 | 1.1241 | 1.2995 | 1.3249 | 1.3586 | 1.4608
2021-10-23 12:00 | 1.9434 | 2.1632 | 2.2016 | 2.2488 | 2.3037 | 1.3915 | 1.6986 | 1.7286 | 1.7696 | 1.3915 | 1.1622 | 1.3449 | 1.3718 | 1.4077 | 1.5144
2021-10-23 13:00 | 1.4289 | 1.6095 | 1.6474 | 1.6938 | 1.748 | 0.95263 | 1.1793 | 1.2089 | 1.2494 | 0.95263 | 1.2765 | 1.4712 | 1.4978 | 1.5331 | 1.6455
2021-10-23 14:00 | 1.3527 | 1.5226 | 1.558 | 1.6013 | 1.6518 | 0.91452 | 1.1307 | 1.1583 | 1.196 | 0.91452 | 1.2956 | 1.4888 | 1.5136 | 1.5466 | 1.6572
2021-10-23 15:00 | 1.448 | 1.6195 | 1.6522 | 1.6921 | 1.7387 | 0.97168 | 1.1943 | 1.2198 | 1.2545 | 0.97168 | 1.2765 | 1.4638 | 1.4867 | 1.5171 | 1.6236
2021-10-23 16:00 | 1.7719 | 1.9639 | 1.9947 | 2.0324 | 2.0764 | 1.1102 | 1.3553 | 1.3794 | 1.4122 | 1.1102 | 1.3527 | 1.546 | 1.5675 | 1.5962 | 1.7049
2021-10-23 17:00 | 2.0751 | 2.2888 | 2.3192 | 2.3563 | 2.3997 | 1.5855 | 1.9162 | 1.9399 | 1.9722 | 1.5855 | 1.9815 | 2.244 | 2.2653 | 2.2936 | 2.4363
2021-10-23 18:00 | 2.5496 | 2.8021 | 2.8343 | 2.8736 | 2.9196 | 2.181 | 2.6223 | 2.6474 | 2.6816 | 2.181 | 2.0196 | 2.2889 | 2.3114 | 2.3414 | 2.4882
2021-10-23 19:00 | 2.9341 | 3.2226 | 3.2585 | 3.3025 | 3.3538 | 2.6483 | 3.1797 | 3.2077 | 3.246 | 2.6483 | 2.3054 | 2.6117 | 2.6369 | 2.6703 | 2.837
2021-10-23 20:00 | 2.915 | 3.2118 | 3.2528 | 3.3028 | 3.3612 | 2.553 | 3.0742 | 3.1061 | 3.1497 | 2.553 | 2.7055 | 3.0632 | 3.0919 | 3.13 | 3.3242
2021-10-23 21:00 | 2.8769 | 3.1806 | 3.2264 | 3.2826 | 3.348 | 2.4959 | 3.0137 | 3.0495 | 3.0983 | 2.4959 | 2.172 | 2.4772 | 2.5094 | 2.5521 | 2.7225
2021-10-23 22:00 | 2.7626 | 3.0594 | 3.1061 | 3.1632 | 3.2299 | 2.4387 | 2.9474 | 2.9838 | 3.0335 | 2.4387 | 2.2291 | 2.5419 | 2.5746 | 2.6181 | 2.7926
2021-10-23 23:00 | 2.5721 | 2.8488 | 2.8924 | 2.9458 | 3.0081 | 2.1284 | 2.5764 | 2.6105 | 2.6569 | 2.1284 | 1.7528 | 2.0084 | 2.039 | 2.0796 | 2.2245
2021-10-24 | 2.3816 | 2.6356 | 2.675 | 2.7231 | 2.7792 | 1.7338 | 2.1041 | 2.1348 | 2.1767 | 1.7338 | 1.6004 | 1.833 | 1.8606 | 1.8972 | 2.029
2021-10-24 01:00 | 2.0846 | 2.3071 | 2.3416 | 2.3838 | 2.4331 | 1.6004 | 1.9397 | 1.9666 | 2.0034 | 1.6004 | 1.5242 | 1.7416 | 1.7658 | 1.7979 | 1.9201
2021-10-24 02:00 | 1.9624 | 2.1663 | 2.1959 | 2.2321 | 2.2744 | 1.3933 | 1.6882 | 1.7113 | 1.7428 | 1.3933 | 1.3718 | 1.5655 | 1.5862 | 1.6138 | 1.7222
2021-10-24 03:00 | 1.8304 | 2.0123 | 2.0358 | 2.0645 | 2.0979 | 1.2956 | 1.5639 | 1.5822 | 1.6071 | 1.2956 | 1.2956 | 1.4722 | 1.4887 | 1.5105 | 1.6078
2021-10-24 04:00 | 1.8481 | 2.0196 | 2.037 | 2.0583 | 2.0831 | 1.2582 | 1.5112 | 1.5247 | 1.5433 | 1.2582 | 1.2956 | 1.4639 | 1.4761 | 1.4923 | 1.5829
2021-10-24 05:00 | 1.9434 | 2.1118 | 2.1241 | 2.1391 | 2.1566 | 1.3527 | 1.6155 | 1.6251 | 1.6381 | 1.3527 | 1.2765 | 1.4355 | 1.4441 | 1.4555 | 1.5394
2021-10-24 06:00 | 2.054 | 2.2268 | 2.237 | 2.2495 | 2.2641 | 1.609 | 1.9154 | 1.9234 | 1.9343 | 1.609 | 1.4099 | 1.5809 | 1.5881 | 1.5976 | 1.6865
2021-10-24 07:00 | 2.1339 | 2.3159 | 2.3278 | 2.3424 | 2.3595 | 1.6957 | 2.0202 | 2.0295 | 2.0422 | 1.6957 | 1.3146 | 1.4774 | 1.4858 | 1.4969 | 1.5825
2021-10-24 08:00 | 2.0196 | 2.2022 | 2.2187 | 2.239 | 2.2627 | 1.5814 | 1.8917 | 1.9047 | 1.9223 | 1.5814 | 0.91452 | 1.0393 | 1.0509 | 1.0663 | 1.135
2021-10-24 09:00 | 1.9243 | 2.1132 | 2.1366 | 2.1652 | 2.1986 | 1.3525 | 1.6311 | 1.6493 | 1.6743 | 1.3525 | 1.0479 | 1.1969 | 1.2133 | 1.2351 | 1.3188
2021-10-24 10:00 | 1.6957 | 1.8818 | 1.9125 | 1.95 | 1.9938 | 1.086 | 1.3266 | 1.3505 | 1.3832 | 1.086 | 0.89547 | 1.0376 | 1.0591 | 1.0877 | 1.1711
2021-10-24 11:00 | 2.0386 | 2.2612 | 2.2974 | 2.3418 | 2.3936 | 1.2384 | 1.5146 | 1.5429 | 1.5815 | 1.2384 | 1.1241 | 1.2995 | 1.3249 | 1.3586 | 1.4608
2021-10-24 12:00 | 1.6576 | 1.8561 | 1.8946 | 1.9417 | 1.9966 | 1.2003 | 1.4727 | 1.5027 | 1.5437 | 1.2003 | 1.4099 | 1.6201 | 1.6471 | 1.6829 | 1.8033
2021-10-24 13:00 | 1.6195 | 1.8141 | 1.8521 | 1.8985 | 1.9527 | 1.3527 | 1.652 | 1.6816 | 1.722 | 1.3527 | 1.1813 | 1.3653 | 1.3919 | 1.4272 | 1.5344
2021-10-24 14:00 | 1.9624 | 2.1776 | 2.213 | 2.2563 | 2.3068 | 1.3908 | 1.6934 | 1.721 | 1.7587 | 1.3908 | 1.3146 | 1.51 | 1.5348 | 1.5677 | 1.6794
2021-10-24 15:00 | 1.8672 | 2.0698 | 2.1025 | 2.1424 | 2.189 | 1.1622 | 1.4194 | 1.4448 | 1.4796 | 1.1622 | 1.8672 | 2.1201 | 2.143 | 2.1734 | 2.3124
2021-10-24 16:00 | 1.5052 | 1.6773 | 1.7081 | 1.7459 | 1.7898 | 1.0479 | 1.2817 | 1.3058 | 1.3386 | 1.0479 | 1.0098 | 1.1648 | 1.1864 | 1.2151 | 1.3049
2021-10-24 17:00 | 2.0196 | 2.2291 | 2.2595 | 2.2967 | 2.34 | 1.5538 | 1.8788 | 1.9025 | 1.9348 | 1.5538 | 1.5052 | 1.7147 | 1.736 | 1.7643 | 1.8808
2021-10-24 18:00 | 2.3435 | 2.5807 | 2.6128 | 2.6522 | 2.6981 | 1.8206 | 2.1965 | 2.2216 | 2.2558 | 1.8206 | 2.3435 | 2.6488 | 2.6714 | 2.7013 | 2.866
2021-10-24 19:00 | 2.7436 | 3.0179 | 3.0538 | 3.0978 | 3.1491 | 2.0195 | 2.4369 | 2.4649 | 2.5032 | 2.0195 | 2.5149 | 2.8446 | 2.8698 | 2.9032 | 3.0815
2021-10-24 20:00 | 2.7304 | 3.0135 | 3.0544 | 3.1045 | 3.1629 | 2.0196 | 2.444 | 2.4759 | 2.5195 | 2.0196 | 2.8198 | 3.1902 | 3.2189 | 3.257 | 3.4576
2021-10-24 21:00 | 2.534 | 2.8121 | 2.858 | 2.9141 | 2.9796 | 1.9434 | 2.361 | 2.3968 | 2.4456 | 1.9434 | 2.4197 | 2.7525 | 2.7846 | 2.8273 | 3.0114
2021-10-24 22:00 | 2.4387 | 2.7114 | 2.7581 | 2.8153 | 2.8819 | 1.6448 | 2.0095 | 2.046 | 2.0957 | 1.6448 | 2.172 | 2.4784 | 2.5111 | 2.5546 | 2.7259
2021-10-24 23:00 | 2.2101 | 2.4598 | 2.5035 | 2.5569 | 2.6192 | 1.4151 | 1.7338 | 1.7678 | 1.8143 | 1.4151 | 2.172 | 2.4742 | 2.5048 | 2.5454 | 2.7134
2021-10-25 | 2.0005 | 2.2262 | 2.2656 | 2.3137 | 2.3699 | 1.3146 | 1.609 | 1.6397 | 1.6815 | 1.3146 | 1.6957 | 1.9389 | 1.9664 | 2.0031 | 2.1401
2021-10-25 01:00 | 1.8672 | 2.0735 | 2.108 | 2.1503 | 2.1995 | 1.2003 | 1.4671 | 1.494 | 1.5307 | 1.2003 | 1.467 | 1.6781 | 1.7023 | 1.7344 | 1.8535
2021-10-25 02:00 | 1.8481 | 2.0435 | 2.0731 | 2.1093 | 2.1516 | 1.1488 | 1.3992 | 1.4223 | 1.4539 | 1.1488 | 1.4099 | 1.6078 | 1.6286 | 1.6561 | 1.7666
2021-10-25 03:00 | 1.81 | 1.9905 | 2.0139 | 2.0426 | 2.0761 | 1.1121 | 1.3471 | 1.3654 | 1.3904 | 1.1121 | 1.6766 | 1.8957 | 1.9121 | 1.9339 | 2.0522
2021-10-25 04:00 | 1.9434 | 2.1219 | 2.1393 | 2.1606 | 2.1855 | 1.1241 | 1.3527 | 1.3663 | 1.3848 | 1.1241 | 1.448 | 1.6332 | 1.6454 | 1.6616 | 1.7606
2021-10-25 05:00 | 2.0767 | 2.2551 | 2.2674 | 2.2824 | 2.2999 | 1.2927 | 1.5446 | 1.5542 | 1.5672 | 1.2927 | 1.7528 | 1.9649 | 1.9734 | 1.9849 | 2.0949
2021-10-25 06:00 | 2.1529 | 2.333 | 2.3433 | 2.3558 | 2.3704 | 1.4659 | 1.7463 | 1.7543 | 1.7652 | 1.4659 | 2.0196 | 2.2584 | 2.2656 | 2.2751 | 2.3976
2021-10-25 07:00 | 2.2673 | 2.4592 | 2.4711 | 2.4857 | 2.5028 | 1.5623 | 1.8626 | 1.8719 | 1.8846 | 1.5623 | 2.0577 | 2.3032 | 2.3115 | 2.3226 | 2.449
2021-10-25 08:00 | 2.1339 | 2.325 | 2.3416 | 2.3619 | 2.3855 | 1.4085 | 1.6875 | 1.7005 | 1.7181 | 1.4085 | 1.9243 | 2.1614 | 2.173 | 2.1884 | 2.3127
2021-10-25 09:00 | 2.0386 | 2.236 | 2.2594 | 2.288 | 2.3214 | 1.086 | 1.3162 | 1.3345 | 1.3594 | 1.086 | 0.7621 | 0.87934 | 0.89573 | 0.91752 | 0.98546
2021-10-25 10:00 | 2.0767 | 2.2912 | 2.3218 | 2.3594 | 2.4032 | 1.2194 | 1.4841 | 1.508 | 1.5407 | 1.2194 | 1.0479 | 1.207 | 1.2285 | 1.2571 | 1.3488
2021-10-25 11:00 | 2.2101 | 2.4454 | 2.4817 | 2.526 | 2.5778 | 1.105 | 1.357 | 1.3853 | 1.4239 | 1.105 | 1.086 | 1.2571 | 1.2825 | 1.3163 | 1.4164
2021-10-25 12:00 | 2.0173 | 2.2426 | 2.2811 | 2.3282 | 2.3831 | 0.93358 | 1.1576 | 1.1876 | 1.2286 | 0.93358 | 1.2575 | 1.4507 | 1.4777 | 1.5135 | 1.6255
2021-10-25 13:00 | 2.2863 | 2.5306 | 2.5685 | 2.6149 | 2.6691 | 1.2575 | 1.5395 | 1.5691 | 1.6095 | 1.2575 | 1.4099 | 1.6194 | 1.646 | 1.6813 | 1.801
2021-10-25 14:00 | 2.172 | 2.4028 | 2.4382 | 2.4815 | 2.532 | 1.2765 | 1.5584 | 1.586 | 1.6237 | 1.2765 | 1.0669 | 1.2347 | 1.2595 | 1.2925 | 1.3906
2021-10-25 15:00 | 1.9214 | 2.1282 | 2.1608 | 2.2007 | 2.2473 | 1.105 | 1.3519 | 1.3773 | 1.4121 | 1.105 | 1.0669 | 1.2309 | 1.2538 | 1.2842 | 1.3791
2021-10-25 16:00 | 1.9243 | 2.1277 | 2.1585 | 2.1962 | 2.2401 | 1.2575 | 1.5293 | 1.5533 | 1.5861 | 1.2575 | 0.99073 | 1.1437 | 1.1653 | 1.1939 | 1.2827
2021-10-25 17:00 | 2.2291 | 2.4543 | 2.4847 | 2.5218 | 2.5652 | 1.5814 | 1.9113 | 1.935 | 1.9673 | 1.5814 | 1.7909 | 2.0323 | 2.0536 | 2.0818 | 2.2141
2021-10-25 18:00 | 2.6102 | 2.8672 | 2.8994 | 2.9388 | 2.9847 | 1.9434 | 2.3415 | 2.3666 | 2.4009 | 1.9434 | 2.7055 | 3.0511 | 3.0736 | 3.1036 | 3.2881
2021-10-25 19:00 | 2.7245 | 2.9974 | 3.0333 | 3.0773 | 3.1286 | 2.0767 | 2.5045 | 2.5325 | 2.5707 | 2.0767 | 3.2199 | 3.6279 | 3.6531 | 3.6866 | 3.9036
2021-10-25 20:00 | 2.7245 | 3.0072 | 3.0481 | 3.0982 | 3.1566 | 2.0741 | 2.5084 | 2.5403 | 2.5839 | 2.0741 | 2.7055 | 3.0632 | 3.0919 | 3.13 | 3.3242
2021-10-25 21:00 | 2.553 | 2.8326 | 2.8785 | 2.9346 | 3 | 1.9243 | 2.3385 | 2.3743 | 2.4231 | 1.9243 | 2.6674 | 3.0277 | 3.0598 | 3.1025 | 3.3002
2021-10-25 22:00 | 2.4608 | 2.7352 | 2.7819 | 2.839 | 2.9057 | 1.6968 | 2.0709 | 2.1074 | 2.1571 | 1.6968 | 2.7436 | 3.1136 | 3.1463 | 3.1897 | 3.3925
2021-10-25 23:00 | 2.1529 | 2.3984 | 2.4421 | 2.4955 | 2.5578 | 1.3826 | 1.6954 | 1.7295 | 1.7759 | 1.3826 | 2.1339 | 2.4318 | 2.4624 | 2.503 | 2.6689
2021-10-26 | 1.8862 | 2.1034 | 2.1428 | 2.1909 | 2.247 | 1.2384 | 1.5189 | 1.5496 | 1.5915 | 1.2384 | 1.829 | 2.0871 | 2.1146 | 2.1513 | 2.2956
2021-10-26 01:00 | 1.8672 | 2.0735 | 2.108 | 2.1503 | 2.1995 | 1.154 | 1.4123 | 1.4392 | 1.476 | 1.154 | 1.5623 | 1.784 | 1.8082 | 1.8403 | 1.9646
2021-10-26 02:00 | 1.8937 | 2.0924 | 2.122 | 2.1583 | 2.2006 | 1.1432 | 1.3926 | 1.4157 | 1.4472 | 1.1432 | 1.448 | 1.6502 | 1.6709 | 1.6985 | 1.8111
2021-10-26 03:00 | 1.9053 | 2.0928 | 2.1162 | 2.1449 | 2.1784 | 1.1432 | 1.3838 | 1.4021 | 1.4271 | 1.1432 | 1.3718 | 1.5569 | 1.5733 | 1.5952 | 1.6967
2021-10-26 04:00 | 1.9624 | 2.1424 | 2.1598 | 2.1811 | 2.2059 | 1.1245 | 1.3532 | 1.3668 | 1.3853 | 1.1245 | 1.4099 | 1.5909 | 1.6031 | 1.6193 | 1.7162
2021-10-26 05:00 | 2.0386 | 2.2142 | 2.2264 | 2.2414 | 2.2589 | 1.3408 | 1.6014 | 1.6109 | 1.624 | 1.3408 | 1.7909 | 2.0072 | 2.0158 | 2.0272 | 2.1393
2021-10-26 06:00 | 2.2099 | 2.3942 | 2.4044 | 2.4169 | 2.4315 | 1.5332 | 1.8258 | 1.8338 | 1.8447 | 1.5332 | 2.1529 | 2.4067 | 2.4138 | 2.4233 | 2.5531
2021-10-26 07:00 | 2.2863 | 2.4796 | 2.4916 | 2.5062 | 2.5232 | 1.5814 | 1.8851 | 1.8944 | 1.9071 | 1.5814 | 2.2863 | 2.5572 | 2.5656 | 2.5767 | 2.7157
2021-10-26 08:00 | 2.2482 | 2.4478 | 2.4644 | 2.4847 | 2.5083 | 1.3946 | 1.6711 | 1.684 | 1.7017 | 1.3946 | 1.5433 | 1.7379 | 1.7496 | 1.765 | 1.8683
2021-10-26 09:00 | 1.9243 | 2.1132 | 2.1366 | 2.1652 | 2.1986 | 1.0878 | 1.3183 | 1.3365 | 1.3615 | 1.0878 | 0.81548 | 0.93866 | 0.95505 | 0.97683 | 1.0477
2021-10-26 10:00 | 1.5245 | 1.6978 | 1.7285 | 1.7661 | 1.8098 | 0.75758 | 0.93859 | 0.96252 | 0.99519 | 0.75758 | 1.086 | 1.2494 | 1.2709 | 1.2994 | 1.3933
2021-10-26 11:00 | 1.3718 | 1.5448 | 1.581 | 1.6254 | 1.6772 | 0.66684 | 0.83934 | 0.86763 | 0.90625 | 0.66684 | 1.2575 | 1.4477 | 1.4731 | 1.5068 | 1.6163
2021-10-26 12:00 | 1.4289 | 1.6105 | 1.649 | 1.6961 | 1.751 | 0.62873 | 0.79748 | 0.8275 | 0.86848 | 0.62873 | 1.5052 | 1.726 | 1.7529 | 1.7888 | 1.9144
2021-10-26 13:00 | 1.3527 | 1.5276 | 1.5655 | 1.612 | 1.6661 | 0.601 | 0.76395 | 0.79355 | 0.83396 | 0.601 | 1.6766 | 1.9158 | 1.9424 | 1.9777 | 2.1121
2021-10-26 14:00 | 1.3527 | 1.5226 | 1.558 | 1.6013 | 1.6518 | 0.66684 | 0.83811 | 0.86572 | 0.90342 | 0.66684 | 1.4289 | 1.637 | 1.6618 | 1.6948 | 1.8127
2021-10-26 15:00 | 1.3908 | 1.5581 | 1.5908 | 1.6307 | 1.6773 | 0.74305 | 0.92421 | 0.94967 | 0.98443 | 0.74305 | 1.2956 | 1.485 | 1.5078 | 1.5382 | 1.6458
2021-10-26 16:00 | 1.6766 | 1.8616 | 1.8924 | 1.9301 | 1.974 | 0.99775 | 1.2225 | 1.2465 | 1.2793 | 0.99775 | 0.93358 | 1.0802 | 1.1017 | 1.1304 | 1.216
2021-10-26 17:00 | 2.0577 | 2.2701 | 2.3005 | 2.3376 | 2.381 | 1.4289 | 1.7313 | 1.7549 | 1.7873 | 1.4289 | 1.467 | 1.6724 | 1.6936 | 1.7219 | 1.8364
2021-10-26 18:00 | 2.3816 | 2.6216 | 2.6538 | 2.6932 | 2.7391 | 1.7909 | 2.1615 | 2.1866 | 2.2208 | 1.7909 | 2.3625 | 2.67 | 2.6925 | 2.7225 | 2.8882
2021-10-26 19:00 | 2.553 | 2.8132 | 2.8491 | 2.8931 | 2.9444 | 1.9053 | 2.3019 | 2.3299 | 2.3682 | 1.9053 | 2.4578 | 2.7811 | 2.8062 | 2.8397 | 3.0148
2021-10-26 20:00 | 2.6102 | 2.8843 | 2.9253 | 2.9753 | 3.0337 | 1.9434 | 2.354 | 2.3859 | 2.4295 | 1.9434 | 2.553 | 2.8938 | 2.9225 | 2.9606 | 3.1465
2021-10-26 21:00 | 2.4578 | 2.7303 | 2.7761 | 2.8322 | 2.8977 | 1.8481 | 2.2485 | 2.2842 | 2.3331 | 1.8481 | 2.4768 | 2.816 | 2.8481 | 2.8908 | 3.078
2021-10-26 22:00 | 2.2121 | 2.468 | 2.5147 | 2.5718 | 2.6385 | 1.7242 | 2.1033 | 2.1398 | 2.1895 | 1.7242 | 2.4578 | 2.796 | 2.8287 | 2.8722 | 3.0592
2021-10-26 23:00 | 2.0196 | 2.2552 | 2.2988 | 2.3522 | 2.4145 | 1.4092 | 1.7268 | 1.7608 | 1.8073 | 1.4092 | 1.8862 | 2.1566 | 2.1872 | 2.2278 | 2.3801
2021-10-27 | 1.9053 | 2.1239 | 2.1632 | 2.2114 | 2.2675 | 1.2575 | 1.5414 | 1.5721 | 1.614 | 1.2575 | 1.6576 | 1.8965 | 1.9241 | 1.9607 | 2.0956
2021-10-27 01:00 | 1.7719 | 1.9712 | 2.0057 | 2.0479 | 2.0972 | 1.1432 | 1.3995 | 1.4265 | 1.4632 | 1.1432 | 1.448 | 1.6569 | 1.6811 | 1.7133 | 1.8313
2021-10-27 02:00 | 1.7719 | 1.9616 | 1.9912 | 2.0275 | 2.0697 | 1.105 | 1.3476 | 1.3707 | 1.4022 | 1.105 | 1.3908 | 1.5866 | 1.6074 | 1.635 | 1.7444
2021-10-27 03:00 | 1.7528 | 1.929 | 1.9525 | 1.9812 | 2.0147 | 1.086 | 1.3163 | 1.3346 | 1.3595 | 1.086 | 1.3337 | 1.5146 | 1.531 | 1.5528 | 1.6523
2021-10-27 04:00 | 1.7338 | 1.8968 | 1.9142 | 1.9355 | 1.9603 | 1.0789 | 1.2993 | 1.3129 | 1.3314 | 1.0789 | 1.3718 | 1.5485 | 1.5607 | 1.5769 | 1.6717
2021-10-27 05:00 | 1.8672 | 2.03 | 2.0422 | 2.0572 | 2.0747 | 1.3146 | 1.5705 | 1.58 | 1.5931 | 1.3146 | 1.829 | 2.0495 | 2.0581 | 2.0695 | 2.1837
2021-10-27 06:00 | 2.0237 | 2.1942 | 2.2044 | 2.2169 | 2.2315 | 1.4099 | 1.6801 | 1.6881 | 1.699 | 1.4099 | 1.9243 | 2.1526 | 2.1598 | 2.1693 | 2.2865
2021-10-27 07:00 | 2.1339 | 2.3159 | 2.3278 | 2.3424 | 2.3595 | 1.5623 | 1.8626 | 1.8719 | 1.8846 | 1.5623 | 2.4578 | 2.7478 | 2.7561 | 2.7672 | 2.9156
2021-10-27 08:00 | 2.0005 | 2.1817 | 2.1983 | 2.2186 | 2.2422 | 1.2897 | 1.5471 | 1.5601 | 1.5777 | 1.2897 | 1.3146 | 1.4839 | 1.4955 | 1.5109 | 1.6017
2021-10-27 09:00 | 1.6948 | 1.8666 | 1.89 | 1.9186 | 1.952 | 0.97168 | 1.1812 | 1.1994 | 1.2243 | 0.97168 | 0.97168 | 1.1122 | 1.1286 | 1.1504 | 1.2299
2021-10-27 10:00 | 1.4861 | 1.6566 | 1.6873 | 1.7248 | 1.7686 | 0.724 | 0.89892 | 0.92284 | 0.95551 | 0.724 | 1.2575 | 1.4399 | 1.4614 | 1.49 | 1.5932
2021-10-27 11:00 | 1.2765 | 1.4424 | 1.4787 | 1.5231 | 1.5748 | 0.59063 | 0.74931 | 0.77759 | 0.81622 | 0.59063 | 1.6004 | 1.8288 | 1.8542 | 1.8879 | 2.0163
2021-10-27 12:00 | 1.3337 | 1.5082 | 1.5466 | 1.5937 | 1.6487 | 0.60968 | 0.77497 | 0.80499 | 0.84597 | 0.60968 | 1.7909 | 2.0436 | 2.0705 | 2.1064 | 2.2476
2021-10-27 13:00 | 1.2461 | 1.413 | 1.4509 | 1.4974 | 1.5516 | 0.55252 | 0.70668 | 0.73628 | 0.77669 | 0.55252 | 1.9053 | 2.1699 | 2.1964 | 2.2318 | 2.3787
2021-10-27 14:00 | 1.2765 | 1.4407 | 1.4761 | 1.5194 | 1.57 | 0.57608 | 0.73089 | 0.7585 | 0.7962 | 0.57608 | 1.5052 | 1.7217 | 1.7465 | 1.7795 | 1.9016
2021-10-27 15:00 | 1.5222 | 1.6993 | 1.7319 | 1.7719 | 1.8185 | 0.6821 | 0.85221 | 0.87767 | 0.91243 | 0.6821 | 1.4289 | 1.6332 | 1.656 | 1.6864 | 1.8013
2021-10-27 16:00 | 1.6766 | 1.8616 | 1.8924 | 1.9301 | 1.974 | 1.0288 | 1.2592 | 1.2833 | 1.3161 | 1.0288 | 1.1432 | 1.3131 | 1.3346 | 1.3633 | 1.4604
2021-10-27 17:00 | 2.1529 | 2.3724 | 2.4028 | 2.44 | 2.4833 | 1.4099 | 1.7088 | 1.7324 | 1.7648 | 1.4099 | 1.467 | 1.6724 | 1.6936 | 1.7219 | 1.8364
2021-10-27 18:00 | 2.2673 | 2.4988 | 2.531 | 2.5703 | 2.6163 | 1.7338 | 2.094 | 2.1191 | 2.1533 | 1.7338 | 2.0958 | 2.3736 | 2.3961 | 2.4261 | 2.5771
2021-10-27 19:00 | 2.4768 | 2.7313 | 2.7672 | 2.8112 | 2.8625 | 1.9624 | 2.3694 | 2.3974 | 2.4357 | 1.9624 | 2.3054 | 2.6117 | 2.6369 | 2.6703 | 2.837
2021-10-27 20:00 | 2.3598 | 2.6154 | 2.6563 | 2.7064 | 2.7648 | 1.8672 | 2.2639 | 2.2959 | 2.3394 | 1.8672 | 2.8007 | 3.1691 | 3.1977 | 3.2358 | 3.4353
2021-10-27 21:00 | 2.3625 | 2.6279 | 2.6738 | 2.7299 | 2.7954 | 1.7909 | 2.1809 | 2.2167 | 2.2655 | 1.7909 | 2.2673 | 2.5831 | 2.6152 | 2.6579 | 2.8336
2021-10-27 22:00 | 2.2101 | 2.4658 | 2.5125 | 2.5696 | 2.6363 | 1.5623 | 1.912 | 1.9485 | 1.9982 | 1.5623 | 1.9624 | 2.2455 | 2.2782 | 2.3217 | 2.4815
2021-10-27 23:00 | 1.9434 | 2.1733 | 2.2169 | 2.2703 | 2.3326 | 1.3527 | 1.6601 | 1.6942 | 1.7406 | 1.3527 | 1.7719 | 2.0296 | 2.0601 | 2.1008 | 2.2468
2021-10-28 | 1.8862 | 2.1034 | 2.1428 | 2.1909 | 2.247 | 1.1919 | 1.464 | 1.4947 | 1.5366 | 1.1919 | 1.8672 | 2.1294 | 2.157 | 2.1936 | 2.34
2021-10-28 01:00 | 1.7719 | 1.9712 | 2.0057 | 2.0479 | 2.0972 | 1.0981 | 1.3463 | 1.3732 | 1.41 | 1.0981 | 1.3337 | 1.5299 | 1.5541 | 1.5862 | 1.698
2021-10-28 02:00 | 1.6385 | 1.8183 | 1.8479 | 1.8842 | 1.9264 | 1.0124 | 1.2382 | 1.2613 | 1.2928 | 1.0124 | 1.3908 | 1.5866 | 1.6074 | 1.635 | 1.7444
2021-10-28 03:00 | 1.6195 | 1.7858 | 1.8092 | 1.8379 | 1.8714 | 1.0098 | 1.2263 | 1.2445 | 1.2695 | 1.0098 | 1.448 | 1.6416 | 1.658 | 1.6799 | 1.7856
2021-10-28 04:00 | 1.6957 | 1.8558 | 1.8732 | 1.8945 | 1.9194 | 1.0479 | 1.2627 | 1.2763 | 1.2948 | 1.0479 | 1.3908 | 1.5697 | 1.5819 | 1.5981 | 1.694
2021-10-28 05:00 | 1.8862 | 2.0504 | 2.0627 | 2.0777 | 2.0952 | 1.2117 | 1.4489 | 1.4585 | 1.4715 | 1.2117 | 1.6004 | 1.7955 | 1.8041 | 1.8155 | 1.9171
2021-10-28 06:00 | 1.9053 | 2.0669 | 2.0772 | 2.0897 | 2.1043 | 1.2858 | 1.5335 | 1.5415 | 1.5524 | 1.2858 | 1.9053 | 2.1314 | 2.1386 | 2.1481 | 2.2642
2021-10-28 07:00 | 2.1148 | 2.2954 | 2.3074 | 2.322 | 2.339 | 1.5242 | 1.8176 | 1.8269 | 1.8396 | 1.5242 | 1.9243 | 2.155 | 2.1633 | 2.1744 | 2.2935
2021-10-28 08:00 | 2.2863 | 2.4887 | 2.5053 | 2.5256 | 2.5493 | 1.4289 | 1.7117 | 1.7246 | 1.7423 | 1.4289 | 1.6576 | 1.865 | 1.8766 | 1.892 | 2.0016
2021-10-28 09:00 | 2.2863 | 2.5021 | 2.5255 | 2.5541 | 2.5875 | 1.2956 | 1.5638 | 1.5821 | 1.607 | 1.2956 | 1.5242 | 1.7262 | 1.7426 | 1.7644 | 1.8742
2021-10-28 10:00 | 1.9815 | 2.1888 | 2.2195 | 2.257 | 2.3008 | 1.105 | 1.3491 | 1.373 | 1.4057 | 1.105 | 1.2384 | 1.4187 | 1.4402 | 1.4688 | 1.571
2021-10-28 11:00 | 2.0005 | 2.2202 | 2.2565 | 2.3009 | 2.3526 | 1.2194 | 1.4921 | 1.5204 | 1.559 | 1.2194 | 1.467 | 1.6806 | 1.706 | 1.7397 | 1.8607
2021-10-28 12:00 | 2.0577 | 2.286 | 2.3245 | 2.3716 | 2.4265 | 1.0761 | 1.326 | 1.356 | 1.397 | 1.0761 | 1.4861 | 1.7048 | 1.7318 | 1.7676 | 1.8921
2021-10-28 13:00 | 2.0196 | 2.244 | 2.2819 | 2.3284 | 2.3825 | 1.1241 | 1.3819 | 1.4115 | 1.4519 | 1.1241 | 1.6766 | 1.9158 | 1.9424 | 1.9777 | 2.1121
2021-10-28 14:00 | 2.0767 | 2.3004 | 2.3358 | 2.3791 | 2.4297 | 1.0669 | 1.3108 | 1.3384 | 1.3761 | 1.0669 | 1.5623 | 1.7852 | 1.81 | 1.843 | 1.9683
2021-10-28 15:00 | 2.1529 | 2.3769 | 2.4095 | 2.4495 | 2.496 | 1.1813 | 1.4419 | 1.4673 | 1.5021 | 1.1813 | 1.0479 | 1.2097 | 1.2326 | 1.263 | 1.3569
2021-10-28 16:00 | 2.2291 | 2.4552 | 2.486 | 2.5237 | 2.5676 | 1.4289 | 1.7319 | 1.7559 | 1.7887 | 1.4289 | 1.4861 | 1.6942 | 1.7157 | 1.7444 | 1.8604
2021-10-28 17:00 | 2.4353 | 2.6757 | 2.7061 | 2.7433 | 2.7866 | 1.7179 | 2.0727 | 2.0963 | 2.1287 | 1.7179 | 2.2101 | 2.4981 | 2.5194 | 2.5476 | 2.7029
2021-10-28 18:00 | 2.534 | 2.7854 | 2.8175 | 2.8569 | 2.9028 | 1.7912 | 2.1618 | 2.1869 | 2.2212 | 1.7912 | 2.2482 | 2.5429 | 2.5655 | 2.5954 | 2.7549
2021-10-28 19:00 | 2.553 | 2.8132 | 2.8491 | 2.8931 | 2.9444 | 1.829 | 2.2118 | 2.2399 | 2.2781 | 1.829 | 2.3054 | 2.6117 | 2.6369 | 2.6703 | 2.837
2021-10-28 20:00 | 2.4959 | 2.7615 | 2.8024 | 2.8525 | 2.9109 | 1.8481 | 2.2414 | 2.2734 | 2.3169 | 1.8481 | 3.0294 | 3.4231 | 3.4518 | 3.4899 | 3.702
2021-10-28 21:00 | 2.3435 | 2.6074 | 2.6533 | 2.7094 | 2.7749 | 1.6385 | 2.0009 | 2.0366 | 2.0855 | 1.6385 | 2.2863 | 2.6043 | 2.6364 | 2.6791 | 2.8558
2021-10-28 22:00 | 2.1339 | 2.3839 | 2.4306 | 2.4878 | 2.5544 | 1.5365 | 1.8816 | 1.918 | 1.9677 | 1.5365 | 2.2863 | 2.6054 | 2.6381 | 2.6816 | 2.8593
2021-10-28 23:00 | 1.9567 | 2.1876 | 2.2312 | 2.2847 | 2.347 | 1.2967 | 1.5939 | 1.6279 | 1.6744 | 1.2967 | 2.0005 | 2.2836 | 2.3142 | 2.3548 | 2.5134
2021-10-29 | 1.7719 | 1.9806 | 2.0199 | 2.0681 | 2.1242 | 1.1397 | 1.4023 | 1.433 | 1.4749 | 1.1397 | 1.5242 | 1.7483 | 1.7759 | 1.8125 | 1.9401
2021-10-29 01:00 | 1.7528 | 1.9507 | 1.9852 | 2.0274 | 2.0767 | 1.0375 | 1.2747 | 1.3016 | 1.3384 | 1.0375 | 1.2956 | 1.4876 | 1.5117 | 1.5439 | 1.6535
2021-10-29 02:00 | 1.6766 | 1.8592 | 1.8889 | 1.9251 | 1.9674 | 0.99073 | 1.2125 | 1.2356 | 1.2672 | 0.99073 | 1.2956 | 1.4808 | 1.5015 | 1.5291 | 1.6333
2021-10-29 03:00 | 1.6576 | 1.8267 | 1.8501 | 1.8788 | 1.9123 | 0.95263 | 1.1587 | 1.177 | 1.202 | 0.95263 | 1.3908 | 1.5781 | 1.5945 | 1.6163 | 1.7189
2021-10-29 04:00 | 1.6576 | 1.8149 | 1.8323 | 1.8536 | 1.8784 | 0.99519 | 1.2004 | 1.214 | 1.2325 | 0.99519 | 1.4289 | 1.6121 | 1.6243 | 1.6405 | 1.7384
2021-10-29 05:00 | 1.829 | 1.989 | 2.0013 | 2.0163 | 2.0338 | 1.086 | 1.3004 | 1.3099 | 1.323 | 1.086 | 1.3527 | 1.5202 | 1.5288 | 1.5402 | 1.6282
2021-10-29 06:00 | 1.9243 | 2.0874 | 2.0976 | 2.1102 | 2.1248 | 1.2384 | 1.4776 | 1.4855 | 1.4964 | 1.2384 | 1.5623 | 1.7503 | 1.7575 | 1.767 | 1.8643
2021-10-29 07:00 | 2.3244 | 2.5206 | 2.5325 | 2.5471 | 2.5642 | 1.448 | 1.7276 | 1.7369 | 1.7496 | 1.448 | 2.1339 | 2.3878 | 2.3962 | 2.4073 | 2.5379
2021-10-29 08:00 | 2.4387 | 2.6525 | 2.6691 | 2.6894 | 2.713 | 1.5814 | 1.8917 | 1.9047 | 1.9223 | 1.5814 | 2.1148 | 2.3731 | 2.3847 | 2.4002 | 2.5349
2021-10-29 09:00 | 2.4387 | 2.6658 | 2.6892 | 2.7179 | 2.7513 | 1.464 | 1.7628 | 1.781 | 1.8059 | 1.464 | 1.6766 | 1.8956 | 1.912 | 1.9338 | 2.052
2021-10-29 10:00 | 2.0767 | 2.2912 | 2.3218 | 2.3594 | 2.4032 | 1.1432 | 1.3941 | 1.418 | 1.4507 | 1.1432 | 1.2384 | 1.4187 | 1.4402 | 1.4688 | 1.571
2021-10-29 11:00 | 1.9624 | 2.1793 | 2.2156 | 2.2599 | 2.3117 | 1.0288 | 1.267 | 1.2953 | 1.3339 | 1.0288 | 1.3337 | 1.5324 | 1.5578 | 1.5915 | 1.7052
2021-10-29 12:00 | 1.4289 | 1.6105 | 1.649 | 1.6961 | 1.751 | 0.64779 | 0.81999 | 0.85 | 0.89099 | 0.64779 | 1.467 | 1.6836 | 1.7106 | 1.7464 | 1.8699
2021-10-29 13:00 | 1.5052 | 1.6913 | 1.7293 | 1.7757 | 1.8299 | 0.80021 | 0.99929 | 1.0289 | 1.0693 | 0.80021 | 1.448 | 1.6617 | 1.6883 | 1.7236 | 1.8455
2021-10-29 14:00 | 1.7719 | 1.9729 | 2.0083 | 2.0516 | 2.1022 | 1.1432 | 1.4008 | 1.4284 | 1.4661 | 1.1432 | 1.5052 | 1.7217 | 1.7465 | 1.7795 | 1.9016
2021-10-29 15:00 | 1.9815 | 2.1927 | 2.2253 | 2.2652 | 2.3118 | 0.93358 | 1.1493 | 1.1747 | 1.2095 | 0.93358 | 1.4861 | 1.6967 | 1.7196 | 1.7499 | 1.868
2021-10-29 16:00 | 2.0005 | 2.2095 | 2.2403 | 2.278 | 2.322 | 1.2194 | 1.4843 | 1.5083 | 1.5411 | 1.2194 | 1.0288 | 1.186 | 1.2076 | 1.2363 | 1.3271
2021-10-29 17:00 | 2.0577 | 2.2701 | 2.3005 | 2.3376 | 2.381 | 1.3718 | 1.6637 | 1.6874 | 1.7198 | 1.3718 | 1.4289 | 1.63 | 1.6513 | 1.6796 | 1.7919
2021-10-29 18:00 | 2.3054 | 2.5397 | 2.5719 | 2.6113 | 2.6572 | 1.6195 | 1.9589 | 1.984 | 2.0183 | 1.6195 | 1.9434 | 2.2042 | 2.2267 | 2.2567 | 2.3993
2021-10-29 19:00 | 2.3816 | 2.629 | 2.6649 | 2.7089 | 2.7602 | 1.8477 | 2.2339 | 2.262 | 2.3002 | 1.8477 | 2.2291 | 2.527 | 2.5522 | 2.5856 | 2.7482
2021-10-29 20:00 | 2.5149 | 2.782 | 2.8229 | 2.873 | 2.9314 | 1.8481 | 2.2414 | 2.2734 | 2.3169 | 1.8481 | 2.4959 | 2.8303 | 2.859 | 2.8971 | 3.0798
2021-10-29 21:00 | 2.4197 | 2.6893 | 2.7352 | 2.7913 | 2.8568 | 1.75 | 2.1326 | 2.1684 | 2.2172 | 1.75 | 2.172 | 2.4772 | 2.5094 | 2.5521 | 2.7225
2021-10-29 22:00 | 2.3054 | 2.5681 | 2.6148 | 2.672 | 2.7386 | 1.5814 | 1.9345 | 1.971 | 2.0207 | 1.5814 | 2.4578 | 2.796 | 2.8287 | 2.8722 | 3.0592
2021-10-29 23:00 | 2.191 | 2.4394 | 2.483 | 2.5364 | 2.5987 | 1.4289 | 1.7502 | 1.7842 | 1.8307 | 1.4289 | 1.7909 | 2.0507 | 2.0813 | 2.1219 | 2.269
2021-10-30 | 1.9923 | 2.2174 | 2.2568 | 2.3049 | 2.3611 | 1.3146 | 1.609 | 1.6397 | 1.6815 | 1.3146 | 1.81 | 2.0659 | 2.0935 | 2.1301 | 2.2734
2021-10-30 01:00 | 1.9053 | 2.1144 | 2.149 | 2.1912 | 2.2404 | 1.2384 | 1.5121 | 1.539 | 1.5757 | 1.2384 | 1.5814 | 1.8052 | 1.8293 | 1.8615 | 1.9868
2021-10-30 02:00 | 1.8437 | 2.0387 | 2.0684 | 2.1046 | 2.1469 | 1.105 | 1.3476 | 1.3707 | 1.4022 | 1.105 | 1.4099 | 1.6078 | 1.6286 | 1.6561 | 1.7666
2021-10-30 03:00 | 1.8862 | 2.0723 | 2.0958 | 2.1245 | 2.1579 | 1.1241 | 1.3613 | 1.3796 | 1.4046 | 1.1241 | 1.4861 | 1.684 | 1.7004 | 1.7222 | 1.83
2021-10-30 04:00 | 1.81 | 1.9786 | 1.996 | 2.0173 | 2.0422 | 1.1208 | 1.3488 | 1.3624 | 1.3809 | 1.1208 | 1.4861 | 1.6756 | 1.6878 | 1.704 | 1.8051
2021-10-30 05:00 | 1.8481 | 2.0095 | 2.0218 | 2.0368 | 2.0543 | 1.2194 | 1.4579 | 1.4675 | 1.4806 | 1.2194 | 1.6195 | 1.8166 | 1.8252 | 1.8366 | 1.9393
2021-10-30 06:00 | 1.8672 | 2.026 | 2.0362 | 2.0487 | 2.0633 | 1.2384 | 1.4776 | 1.4855 | 1.4964 | 1.2384 | 1.6004 | 1.7927 | 1.7998 | 1.8094 | 1.9087
2021-10-30 07:00 | 1.8862 | 2.0498 | 2.0617 | 2.0763 | 2.0934 | 1.2384 | 1.48 | 1.4893 | 1.502 | 1.2384 | 1.5052 | 1.6892 | 1.6975 | 1.7086 | 1.8047
2021-10-30 08:00 | 1.9243 | 2.0998 | 2.1164 | 2.1367 | 2.1604 | 1.2003 | 1.4416 | 1.4545 | 1.4722 | 1.2003 | 1.2956 | 1.4627 | 1.4743 | 1.4898 | 1.5794
2021-10-30 09:00 | 1.5052 | 1.6629 | 1.6862 | 1.7149 | 1.7483 | 1.0009 | 1.2157 | 1.2339 | 1.2589 | 1.0009 | 0.91452 | 1.0487 | 1.0651 | 1.0869 | 1.1632
2021-10-30 10:00 | 1.2384 | 1.3905 | 1.4212 | 1.4587 | 1.5025 | 1.0669 | 1.3041 | 1.328 | 1.3607 | 1.0669 | 1.1241 | 1.2917 | 1.3132 | 1.3418 | 1.4377
2021-10-30 11:00 | 1.3337 | 1.5038 | 1.5401 | 1.5845 | 1.6362 | 0.99611 | 1.2283 | 1.2566 | 1.2952 | 0.99611 | 1.2575 | 1.4477 | 1.4731 | 1.5068 | 1.6163
2021-10-30 12:00 | 1.2384 | 1.4058 | 1.4443 | 1.4914 | 1.5463 | 0.74305 | 0.93253 | 0.96254 | 1.0035 | 0.74305 | 1.3146 | 1.5143 | 1.5412 | 1.577 | 1.6922
2021-10-30 13:00 | 1.5433 | 1.7323 | 1.7702 | 1.8167 | 1.8708 | 0.99073 | 1.2244 | 1.254 | 1.2944 | 0.99073 | 1.2384 | 1.4288 | 1.4554 | 1.4907 | 1.6011
2021-10-30 14:00 | 1.7147 | 1.9115 | 1.9469 | 1.9902 | 2.0408 | 0.86572 | 1.0731 | 1.1007 | 1.1384 | 0.86572 | 1.467 | 1.6794 | 1.7042 | 1.7371 | 1.8572
2021-10-30 15:00 | 1.6385 | 1.8242 | 1.8569 | 1.8968 | 1.9434 | 0.89547 | 1.1043 | 1.1297 | 1.1645 | 0.89547 | 1.2003 | 1.3791 | 1.402 | 1.4324 | 1.5347
2021-10-30 16:00 | 1.5242 | 1.6978 | 1.7286 | 1.7663 | 1.8103 | 1.021 | 1.25 | 1.274 | 1.3068 | 1.021 | 0.87642 | 1.0166 | 1.0382 | 1.0669 | 1.1494
2021-10-30 17:00 | 1.9053 | 2.1063 | 2.1367 | 2.1739 | 2.2172 | 1.3612 | 1.6512 | 1.6749 | 1.7072 | 1.3612 | 1.5052 | 1.7147 | 1.736 | 1.7643 | 1.8808
2021-10-30 18:00 | 2.3344 | 2.571 | 2.6032 | 2.6425 | 2.6885 | 1.6766 | 2.0264 | 2.0515 | 2.0858 | 1.6766 | 2.7626 | 3.1146 | 3.1371 | 3.1671 | 3.3548
2021-10-30 19:00 | 2.534 | 2.7927 | 2.8286 | 2.8726 | 2.9239 | 1.8672 | 2.2569 | 2.2849 | 2.3232 | 1.8672 | 2.5721 | 2.9081 | 2.9333 | 2.9667 | 3.1481
2021-10-30 20:00 | 2.553 | 2.8229 | 2.8639 | 2.9139 | 2.9723 | 1.8862 | 2.2865 | 2.3184 | 2.3619 | 1.8862 | 2.7436 | 3.1056 | 3.1342 | 3.1723 | 3.3687
2021-10-30 21:00 | 2.4387 | 2.7098 | 2.7557 | 2.8118 | 2.8772 | 1.8079 | 2.201 | 2.2368 | 2.2856 | 1.8079 | 3.1056 | 3.5147 | 3.5468 | 3.5895 | 3.8113
2021-10-30 22:00 | 2.4006 | 2.6705 | 2.7172 | 2.7743 | 2.841 | 1.7528 | 2.1371 | 2.1735 | 2.2233 | 1.7528 | 2.4959 | 2.8383 | 2.871 | 2.9145 | 3.1037
2021-10-30 23:00 | 2.3054 | 2.5622 | 2.6058 | 2.6593 | 2.7216 | 1.5433 | 1.8852 | 1.9192 | 1.9657 | 1.5433 | 2.0958 | 2.3895 | 2.4201 | 2.4607 | 2.6245
2021-10-31 | 2.191 | 2.4309 | 2.4703 | 2.5184 | 2.5745 | 1.4076 | 1.7188 | 1.7495 | 1.7914 | 1.4076 | 1.7338 | 1.9812 | 2.0088 | 2.0454 | 2.1845
2021-10-31 01:00 | 2.0005 | 2.2168 | 2.2513 | 2.2935 | 2.3428 | 1.23 | 1.5022 | 1.5291 | 1.5658 | 1.23 | 1.6385 | 1.8687 | 1.8928 | 1.925 | 2.0535
2021-10-31 02:00 | 1.9815 | 2.1867 | 2.2164 | 2.2526 | 2.2949 | 1.1432 | 1.3926 | 1.4157 | 1.4472 | 1.1432 | 1.6957 | 1.9254 | 1.9462 | 1.9737 | 2.0999
2021-10-31 03:00 | 1.9243 | 2.1133 | 2.1367 | 2.1654 | 2.1989 | 1.1432 | 1.3838 | 1.4021 | 1.4271 | 1.1432 | 1.5433 | 1.7475 | 1.7639 | 1.7857 | 1.8967
2021-10-31 04:00 | 1.9243 | 2.1014 | 2.1189 | 2.1402 | 2.165 | 1.135 | 1.3656 | 1.3792 | 1.3977 | 1.135 | 1.5433 | 1.7391 | 1.7513 | 1.7675 | 1.8717
2021-10-31 05:00 | 1.9815 | 2.1528 | 2.165 | 2.18 | 2.1975 | 1.2575 | 1.503 | 1.5125 | 1.5256 | 1.2575 | 1.5433 | 1.732 | 1.7405 | 1.752 | 1.8504
2021-10-31 06:00 | 1.9243 | 2.0874 | 2.0976 | 2.1102 | 2.1248 | 1.2765 | 1.5226 | 1.5306 | 1.5415 | 1.2765 | 1.7909 | 2.0044 | 2.0116 | 2.0211 | 2.1309
2021-10-31 07:00 | 1.81 | 1.9679 | 1.9799 | 1.9945 | 2.0115 | 1.2387 | 1.4804 | 1.4897 | 1.5024 | 1.2387 | 1.5433 | 1.7315 | 1.7399 | 1.751 | 1.8491
2021-10-31 08:00 | 1.7338 | 1.8951 | 1.9117 | 1.932 | 1.9557 | 1.1813 | 1.4191 | 1.432 | 1.4496 | 1.1813 | 1.2194 | 1.378 | 1.3896 | 1.4051 | 1.4906
2021-10-31 09:00 | 1.3908 | 1.54 | 1.5634 | 1.5921 | 1.6255 | 1.0288 | 1.2487 | 1.2669 | 1.2919 | 1.0288 | 0.81926 | 0.94286 | 0.95925 | 0.98103 | 1.0521
2021-10-31 10:00 | 1.2575 | 1.411 | 1.4417 | 1.4792 | 1.523 | 0.89547 | 1.1015 | 1.1254 | 1.1581 | 0.89547 | 0.99073 | 1.1435 | 1.165 | 1.1935 | 1.2822
2021-10-31 11:00 | 1.0288 | 1.1763 | 1.2126 | 1.257 | 1.3087 | 0.7621 | 0.95188 | 0.98017 | 1.0188 | 0.7621 | 1.1241 | 1.2995 | 1.3249 | 1.3586 | 1.4608
2021-10-31 12:00 | 1.0479 | 1.2011 | 1.2396 | 1.2867 | 1.3416 | 0.68589 | 0.865 | 0.89502 | 0.936 | 0.68589 | 1.1241 | 1.3025 | 1.3295 | 1.3653 | 1.47
2021-10-31 13:00 | 0.99073 | 1.1387 | 1.1766 | 1.2231 | 1.2772 | 0.64779 | 0.81922 | 0.84882 | 0.88923 | 0.64779 | 1.2956 | 1.4923 | 1.5189 | 1.5543 | 1.6677
2021-10-31 14:00 | 1.0288 | 1.1746 | 1.21 | 1.2533 | 1.3039 | 0.64779 | 0.8156 | 0.84321 | 0.88091 | 0.64779 | 1.1813 | 1.3618 | 1.3866 | 1.4195 | 1.5239
2021-10-31 15:00 | 1.3146 | 1.4762 | 1.5089 | 1.5488 | 1.5954 | 0.76469 | 0.94978 | 0.97524 | 1.01 | 0.76469 | 1.105 | 1.2733 | 1.2961 | 1.3265 | 1.4236
2021-10-31 16:00 | 1.5814 | 1.7592 | 1.79 | 1.8277 | 1.8717 | 1.0453 | 1.2786 | 1.3027 | 1.3355 | 1.0453 | 0.91452 | 1.059 | 1.0806 | 1.1092 | 1.1938
2021-10-31 17:00 | 1.948 | 2.1523 | 2.1826 | 2.2198 | 2.2631 | 1.4812 | 1.793 | 1.8167 | 1.849 | 1.4812 | 1.448 | 1.6512 | 1.6725 | 1.7007 | 1.8141
2021-10-31 18:00 | 2.2482 | 2.4783 | 2.5105 | 2.5499 | 2.5958 | 1.7338 | 2.094 | 2.1191 | 2.1533 | 1.7338 | 2.0196 | 2.2889 | 2.3114 | 2.3414 | 2.4882
2021-10-31 19:00 | 2.4959 | 2.7518 | 2.7877 | 2.8317 | 2.883 | 1.8862 | 2.2794 | 2.3074 | 2.3457 | 1.8862 | 2.3625 | 2.6752 | 2.7004 | 2.7338 | 2.9037
2021-10-31 20:00 | 2.553 | 2.8229 | 2.8639 | 2.9139 | 2.9723 | 1.8752 | 2.2735 | 2.3054 | 2.349 | 1.8752 | 2.7245 | 3.0844 | 3.113 | 3.1511 | 3.3465
2021-10-31 21:00 | 2.4197 | 2.6893 | 2.7352 | 2.7913 | 2.8568 | 1.7936 | 2.1841 | 2.2199 | 2.2687 | 1.7936 | 2.5721 | 2.9219 | 2.954 | 2.9967 | 3.1891
2021-10-31 22:00 | 2.2863 | 2.5477 | 2.5944 | 2.6515 | 2.7181 | 1.6385 | 2.0021 | 2.0385 | 2.0882 | 1.6385 | 2.2101 | 2.5207 | 2.5534 | 2.5969 | 2.7704
2021-10-31 23:00 | 2.0386 | 2.2756 | 2.3193 | 2.3727 | 2.435 | 1.3964 | 1.7117 | 1.7458 | 1.7922 | 1.3964 | 1.8672 | 2.1354 | 2.166 | 2.2066 | 2.3579
2021-11-01 | 1.8862 | 2.1034 | 2.1428 | 2.1909 | 2.247 | 1.3146 | 1.609 | 1.6397 | 1.6815 | 1.3146 | 1.7909 | 2.0447 | 2.0723 | 2.1089 | 2.2512
2021-11-01 01:00 | 1.7528 | 1.9507 | 1.9852 | 2.0274 | 2.0767 | 1.1622 | 1.422 | 1.449 | 1.4857 | 1.1622 | 1.3527 | 1.5511 | 1.5753 | 1.6074 | 1.7202
2021-11-01 02:00 | 1.7338 | 1.9207 | 1.9503 | 1.9865 | 2.0288 | 1.0479 | 1.28 | 1.3031 | 1.3347 | 1.0479 | 1.2765 | 1.4596 | 1.4804 | 1.5079 | 1.6111
2021-11-01 03:00 | 1.7338 | 1.9086 | 1.932 | 1.9607 | 1.9942 | 1.0479 | 1.2713 | 1.2896 | 1.3145 | 1.0479 | 1.3146 | 1.4934 | 1.5098 | 1.5317 | 1.63
2021-11-01 04:00 | 1.7528 | 1.9172 | 1.9346 | 1.9559 | 1.9808 | 1.0737 | 1.2932 | 1.3067 | 1.3253 | 1.0737 | 1.467 | 1.6544 | 1.6666 | 1.6828 | 1.7828
2021-11-01 05:00 | 1.9624 | 2.1323 | 2.1446 | 2.1596 | 2.1771 | 1.2563 | 1.5016 | 1.5112 | 1.5242 | 1.2563 | 1.6004 | 1.7955 | 1.8041 | 1.8155 | 1.9171
2021-11-01 06:00 | 2.1792 | 2.3613 | 2.3715 | 2.384 | 2.3986 | 1.4827 | 1.7661 | 1.7741 | 1.785 | 1.4827 | 1.9053 | 2.1314 | 2.1386 | 2.1481 | 2.2642
2021-11-01 07:00 | 2.3625 | 2.5615 | 2.5735 | 2.5881 | 2.6051 | 1.6195 | 1.9301 | 1.9394 | 1.9522 | 1.6195 | 2.172 | 2.4302 | 2.4386 | 2.4497 | 2.5824
2021-11-01 08:00 | 2.2482 | 2.4478 | 2.4644 | 2.4847 | 2.5083 | 1.3412 | 1.608 | 1.621 | 1.6386 | 1.3412 | 1.7909 | 2.0132 | 2.0248 | 2.0402 | 2.1571
2021-11-01 09:00 | 1.8672 | 2.0518 | 2.0752 | 2.1038 | 2.1372 | 1.0098 | 1.2262 | 1.2444 | 1.2694 | 1.0098 | 1.1813 | 1.3451 | 1.3615 | 1.3833 | 1.4743
2021-11-01 10:00 | 1.9434 | 2.1479 | 2.1786 | 2.2161 | 2.2599 | 1.1813 | 1.4391 | 1.463 | 1.4957 | 1.1813 | 1.1622 | 1.3341 | 1.3555 | 1.3841 | 1.4821
2021-11-01 11:00 | 1.6766 | 1.8723 | 1.9085 | 1.9529 | 2.0047 | 0.7621 | 0.95188 | 0.98017 | 1.0188 | 0.7621 | 1.5242 | 1.7441 | 1.7695 | 1.8032 | 1.9274
2021-11-01 12:00 | 1.6957 | 1.8971 | 1.9356 | 1.9827 | 2.0376 | 0.80562 | 1.0064 | 1.0365 | 1.0774 | 0.80562 | 1.6766 | 1.9165 | 1.9435 | 1.9793 | 2.1143
2021-11-01 13:00 | 1.81 | 2.0188 | 2.0568 | 2.1032 | 2.1574 | 0.95263 | 1.1793 | 1.2089 | 1.2494 | 0.95263 | 1.6576 | 1.8946 | 1.9212 | 1.9565 | 2.0899
2021-11-01 14:00 | 1.448 | 1.6249 | 1.6603 | 1.7037 | 1.7542 | 0.724 | 0.90563 | 0.93324 | 0.97094 | 0.724 | 1.5433 | 1.764 | 1.7888 | 1.8218 | 1.946
2021-11-01 15:00 | 1.9624 | 2.1722 | 2.2048 | 2.2448 | 2.2914 | 1.0669 | 1.3068 | 1.3323 | 1.3671 | 1.0669 | 1.3337 | 1.5273 | 1.5502 | 1.5806 | 1.6902
2021-11-01 16:00 | 2.0958 | 2.3119 | 2.3427 | 2.3804 | 2.4244 | 1.2003 | 1.4618 | 1.4858 | 1.5186 | 1.2003 | 1.0669 | 1.2284 | 1.2499 | 1.2786 | 1.3716
2021-11-01 17:00 | 2.0767 | 2.2906 | 2.3209 | 2.3581 | 2.4014 | 1.3998 | 1.6968 | 1.7205 | 1.7529 | 1.3998 | 1.3527 | 1.5453 | 1.5666 | 1.5949 | 1.7031
2021-11-01 18:00 | 2.3625 | 2.6011 | 2.6333 | 2.6727 | 2.7186 | 1.7984 | 2.1703 | 2.1954 | 2.2297 | 1.7984 | 2.4959 | 2.8182 | 2.8407 | 2.8707 | 3.0437
2021-11-01 19:00 | 2.4768 | 2.7313 | 2.7672 | 2.8112 | 2.8625 | 1.829 | 2.2118 | 2.2399 | 2.2781 | 1.829 | 2.3054 | 2.6117 | 2.6369 | 2.6703 | 2.837
2021-11-01 20:00 | 2.4387 | 2.7001 | 2.741 | 2.7911 | 2.8495 | 1.8481 | 2.2414 | 2.2734 | 2.3169 | 1.8481 | 2.4959 | 2.8303 | 2.859 | 2.8971 | 3.0798
2021-11-01 21:00 | 2.3244 | 2.587 | 2.6328 | 2.689 | 2.7544 | 1.8481 | 2.2485 | 2.2842 | 2.3331 | 1.8481 | 2.3816 | 2.7101 | 2.7423 | 2.785 | 2.9669
2021-11-01 22:00 | 2.2291 | 2.4863 | 2.533 | 2.5901 | 2.6567 | 1.616 | 1.9754 | 2.0118 | 2.0616 | 1.616 | 1.9624 | 2.2455 | 2.2782 | 2.3217 | 2.4815
2021-11-01 23:00 | 2.002 | 2.2363 | 2.2799 | 2.3334 | 2.3957 | 1.3908 | 1.7051 | 1.7392 | 1.7857 | 1.3908 | 1.6576 | 1.9025 | 1.9331 | 1.9737 | 2.1134
2021-11-02 | 1.7909 | 2.0011 | 2.0404 | 2.0886 | 2.1447 | 1.184 | 1.4546 | 1.4853 | 1.5272 | 1.184 | 1.6957 | 1.9389 | 1.9664 | 2.0031 | 2.1401
2021-11-02 01:00 | 1.7147 | 1.9098 | 1.9443 | 1.9865 | 2.0358 | 1.0793 | 1.324 | 1.351 | 1.3877 | 1.0793 | 1.3718 | 1.5723 | 1.5964 | 1.6286 | 1.7424
2021-11-02 02:00 | 1.6576 | 1.8388 | 1.8684 | 1.9046 | 1.9469 | 1.0345 | 1.2643 | 1.2874 | 1.3189 | 1.0345 | 1.3527 | 1.5443 | 1.5651 | 1.5926 | 1.7
2021-11-02 03:00 | 1.6576 | 1.8267 | 1.8501 | 1.8788 | 1.9123 | 1.0069 | 1.2228 | 1.2411 | 1.2661 | 1.0069 | 1.2384 | 1.4087 | 1.4251 | 1.447 | 1.5412
2021-11-02 04:00 | 1.7519 | 1.9162 | 1.9336 | 1.9549 | 1.9798 | 1.0355 | 1.248 | 1.2616 | 1.2801 | 1.0355 | 1.3908 | 1.5697 | 1.5819 | 1.5981 | 1.694
2021-11-02 05:00 | 1.8241 | 1.9837 | 1.9959 | 2.0109 | 2.0284 | 1.214 | 1.4516 | 1.4611 | 1.4742 | 1.214 | 1.467 | 1.6473 | 1.6559 | 1.6673 | 1.7616
2021-11-02 06:00 | 1.9916 | 2.1597 | 2.1699 | 2.1824 | 2.197 | 1.3908 | 1.6576 | 1.6656 | 1.6765 | 1.3908 | 1.81 | 2.0256 | 2.0327 | 2.0422 | 2.1531
2021-11-02 07:00 | 2.1529 | 2.3364 | 2.3483 | 2.3629 | 2.3799 | 1.4861 | 1.7726 | 1.7819 | 1.7946 | 1.4861 | 1.6576 | 1.8585 | 1.8669 | 1.878 | 1.9824
2021-11-02 08:00 | 2.0577 | 2.2431 | 2.2597 | 2.28 | 2.3036 | 1.2575 | 1.5091 | 1.522 | 1.5397 | 1.2575 | 1.3337 | 1.5051 | 1.5167 | 1.5321 | 1.6239
2021-11-02 09:00 | 1.7254 | 1.8995 | 1.9229 | 1.9515 | 1.9849 | 0.95263 | 1.1587 | 1.1769 | 1.2018 | 0.95263 | 1.1622 | 1.324 | 1.3404 | 1.3621 | 1.4521
2021-11-02 10:00 | 1.3908 | 1.5543 | 1.585 | 1.6225 | 1.6663 | 0.70494 | 0.87641 | 0.90033 | 0.933 | 0.70494 | 1.2956 | 1.4823 | 1.5037 | 1.5323 | 1.6377
2021-11-02 11:00 | 1.3337 | 1.5038 | 1.5401 | 1.5845 | 1.6362 | 0.7621 | 0.95188 | 0.98017 | 1.0188 | 0.7621 | 1.7719 | 2.0193 | 2.0447 | 2.0785 | 2.2163
2021-11-02 12:00 | 2.0577 | 2.286 | 2.3245 | 2.3716 | 2.4265 | 0.87642 | 1.0901 | 1.1201 | 1.1611 | 0.87642 | 1.6576 | 1.8954 | 1.9223 | 1.9581 | 2.0921
2021-11-02 13:00 | 2.1529 | 2.3873 | 2.4252 | 2.4717 | 2.5258 | 1.1241 | 1.3819 | 1.4115 | 1.4519 | 1.1241 | 1.4099 | 1.6194 | 1.646 | 1.6813 | 1.801
2021-11-02 14:00 | 1.9229 | 2.1351 | 2.1705 | 2.2138 | 2.2644 | 1.0098 | 1.2433 | 1.2709 | 1.3086 | 1.0098 | 1.4861 | 1.7005 | 1.7253 | 1.7583 | 1.8794
2021-11-02 15:00 | 2.2291 | 2.4588 | 2.4914 | 2.5313 | 2.5779 | 1.1432 | 1.3969 | 1.4223 | 1.4571 | 1.1432 | 1.3908 | 1.5908 | 1.6137 | 1.6441 | 1.7569
2021-11-02 16:00 | 2.3244 | 2.5575 | 2.5883 | 2.626 | 2.67 | 1.3527 | 1.6419 | 1.6659 | 1.6987 | 1.3527 | 0.95263 | 1.1013 | 1.1229 | 1.1516 | 1.2383
2021-11-02 17:00 | 2.2673 | 2.4952 | 2.5256 | 2.5628 | 2.6061 | 1.4359 | 1.7395 | 1.7631 | 1.7955 | 1.4359 | 1.3527 | 1.5453 | 1.5666 | 1.5949 | 1.7031
2021-11-02 18:00 | 2.4197 | 2.6625 | 2.6947 | 2.7341 | 2.78 | 1.773 | 2.1403 | 2.1654 | 2.1997 | 1.773 | 2.3054 | 2.6065 | 2.629 | 2.659 | 2.8215
2021-11-02 19:00 | 2.4197 | 2.6699 | 2.7058 | 2.7498 | 2.8011 | 1.8481 | 2.2344 | 2.2624 | 2.3007 | 1.8481 | 2.896 | 3.268 | 3.2932 | 3.3266 | 3.5259
2021-11-02 20:00 | 2.4197 | 2.6797 | 2.7206 | 2.7707 | 2.829 | 1.829 | 2.2189 | 2.2508 | 2.2944 | 1.829 | 2.8007 | 3.1691 | 3.1977 | 3.2358 | 3.4353
2021-11-02 21:00 | 2.3054 | 2.5665 | 2.6124 | 2.6685 | 2.7339 | 1.7909 | 2.1809 | 2.2167 | 2.2655 | 1.7909 | 2.1529 | 2.4561 | 2.4882 | 2.5309 | 2.7003
2021-11-02 22:00 | 2.191 | 2.4453 | 2.492 | 2.5492 | 2.6158 | 1.6004 | 1.957 | 1.9935 | 2.0432 | 1.6004 | 1.9624 | 2.2455 | 2.2782 | 2.3217 | 2.4815
2021-11-02 23:00 | 1.9395 | 2.1691 | 2.2128 | 2.2662 | 2.3285 | 1.3768 | 1.6886 | 1.7226 | 1.7691 | 1.3768 | 1.7147 | 1.966 | 1.9966 | 2.0373 | 2.1801
2021-11-03 | 1.7909 | 2.0011 | 2.0404 | 2.0886 | 2.1447 | 1.1635 | 1.4304 | 1.4611 | 1.503 | 1.1635 | 1.6766 | 1.9177 | 1.9453 | 1.9819 | 2.1178
2021-11-03 01:00 | 1.6766 | 1.8688 | 1.9033 | 1.9456 | 1.9948 | 1.086 | 1.332 | 1.3589 | 1.3957 | 1.086 | 1.3337 | 1.5299 | 1.5541 | 1.5862 | 1.698
2021-11-03 02:00 | 1.6576 | 1.8388 | 1.8684 | 1.9046 | 1.9469 | 1.0098 | 1.235 | 1.2581 | 1.2897 | 1.0098 | 1.3146 | 1.502 | 1.5227 | 1.5503 | 1.6555
2021-11-03 03:00 | 1.6551 | 1.8241 | 1.8475 | 1.8762 | 1.9097 | 1.0098 | 1.2263 | 1.2445 | 1.2695 | 1.0098 | 1.3146 | 1.4934 | 1.5098 | 1.5317 | 1.63
2021-11-03 04:00 | 1.6576 | 1.8149 | 1.8323 | 1.8536 | 1.8784 | 1.0098 | 1.2177 | 1.2312 | 1.2498 | 1.0098 | 1.4861 | 1.6756 | 1.6878 | 1.704 | 1.8051
2021-11-03 05:00 | 1.81 | 1.9686 | 1.9808 | 1.9958 | 2.0133 | 1.1975 | 1.432 | 1.4416 | 1.4547 | 1.1975 | 1.5623 | 1.7531 | 1.7617 | 1.7731 | 1.8727
2021-11-03 06:00 | 1.7719 | 1.9236 | 1.9339 | 1.9464 | 1.961 | 1.2765 | 1.5226 | 1.5306 | 1.5415 | 1.2765 | 1.5433 | 1.7291 | 1.7363 | 1.7458 | 1.8421
2021-11-03 07:00 | 2.0196 | 2.1931 | 2.205 | 2.2196 | 2.2367 | 1.4099 | 1.6826 | 1.6919 | 1.7046 | 1.4099 | 1.4861 | 1.668 | 1.6764 | 1.6875 | 1.7824
2021-11-03 08:00 | 2.172 | 2.3659 | 2.3825 | 2.4028 | 2.4265 | 1.3146 | 1.5766 | 1.5895 | 1.6072 | 1.3146 | 1.467 | 1.6533 | 1.6649 | 1.6803 | 1.7794
2021-11-03 09:00 | 2.0386 | 2.236 | 2.2594 | 2.288 | 2.3214 | 1.1622 | 1.4062 | 1.4245 | 1.4494 | 1.1622 | 0.99073 | 1.1334 | 1.1498 | 1.1716 | 1.2521
2021-11-03 10:00 | 1.6766 | 1.8613 | 1.892 | 1.9295 | 1.9733 | 0.77538 | 0.95962 | 0.98354 | 1.0162 | 0.77538 | 1.3718 | 1.5669 | 1.5884 | 1.617 | 1.7266
2021-11-03 11:00 | 1.4099 | 1.5857 | 1.622 | 1.6663 | 1.7181 | 0.70494 | 0.88436 | 0.91264 | 0.95126 | 0.70494 | 1.4861 | 1.7017 | 1.7271 | 1.7609 | 1.883
2021-11-03 12:00 | 1.7528 | 1.9585 | 1.997 | 2.0441 | 2.099 | 0.87642 | 1.0901 | 1.1201 | 1.1611 | 0.87642 | 1.467 | 1.6836 | 1.7106 | 1.7464 | 1.8699
2021-11-03 13:00 | 1.7528 | 1.9574 | 1.9954 | 2.0418 | 2.096 | 0.83279 | 1.0378 | 1.0674 | 1.1078 | 0.83279 | 1.6766 | 1.9158 | 1.9424 | 1.9777 | 2.1121
2021-11-03 14:00 | 2.0386 | 2.2595 | 2.2949 | 2.3382 | 2.3887 | 1.1622 | 1.4233 | 1.4509 | 1.4886 | 1.1622 | 1.2194 | 1.4041 | 1.4289 | 1.4619 | 1.5683
2021-11-03 15:00 | 2.1529 | 2.3769 | 2.4095 | 2.4495 | 2.496 | 1.2384 | 1.5094 | 1.5349 | 1.5696 | 1.2384 | 0.95263 | 1.1039 | 1.1267 | 1.1571 | 1.2458
2021-11-03 16:00 | 2.2291 | 2.4552 | 2.486 | 2.5237 | 2.5676 | 1.3908 | 1.6869 | 1.7109 | 1.7437 | 1.3908 | 1.3908 | 1.5883 | 1.6099 | 1.6386 | 1.7493
2021-11-03 17:00 | 2.2654 | 2.4932 | 2.5236 | 2.5607 | 2.6041 | 1.6124 | 1.9481 | 1.9717 | 2.0041 | 1.6124 | 2.0767 | 2.3499 | 2.3712 | 2.3994 | 2.5474
2021-11-03 18:00 | 2.4578 | 2.7035 | 2.7357 | 2.775 | 2.821 | 1.7719 | 2.139 | 2.1641 | 2.1983 | 1.7719 | 2.2482 | 2.5429 | 2.5655 | 2.5954 | 2.7549
2021-11-03 19:00 | 2.534 | 2.7927 | 2.8286 | 2.8726 | 2.9239 | 1.8237 | 2.2056 | 2.2336 | 2.2718 | 1.8237 | 2.6293 | 2.9716 | 2.9968 | 3.0302 | 3.2148
2021-11-03 20:00 | 2.4959 | 2.7615 | 2.8024 | 2.8525 | 2.9109 | 1.8481 | 2.2414 | 2.2734 | 2.3169 | 1.8481 | 2.5911 | 2.9362 | 2.9648 | 3.0029 | 3.1909
2021-11-03 21:00 | 2.3816 | 2.6484 | 2.6942 | 2.7504 | 2.8158 | 1.7528 | 2.1359 | 2.1717 | 2.2205 | 1.7528 | 2.4768 | 2.816 | 2.8481 | 2.8908 | 3.078
2021-11-03 22:00 | 2.191 | 2.4453 | 2.492 | 2.5492 | 2.6158 | 1.5433 | 1.8895 | 1.9259 | 1.9757 | 1.5433 | 1.9434 | 2.2243 | 2.257 | 2.3005 | 2.4593
2021-11-03 23:00 | 2.0005 | 2.2347 | 2.2783 | 2.3318 | 2.394 | 1.3146 | 1.6151 | 1.6492 | 1.6956 | 1.3146 | 1.6957 | 1.9449 | 1.9754 | 2.0161 | 2.1579
2021-11-04 | 1.78 | 1.9893 | 2.0286 | 2.0768 | 2.1329 | 1.2003 | 1.4739 | 1.5046 | 1.5465 | 1.2003 | 1.4289 | 1.6425 | 1.67 | 1.7066 | 1.829
2021-11-04 01:00 | 1.7516 | 1.9493 | 1.9839 | 2.0261 | 2.0753 | 1.037 | 1.2741 | 1.301 | 1.3377 | 1.037 | 1.3908 | 1.5934 | 1.6176 | 1.6497 | 1.7646
2021-11-04 02:00 | 1.6205 | 1.7989 | 1.8285 | 1.8648 | 1.907 | 1.0098 | 1.235 | 1.2581 | 1.2897 | 1.0098 | 1.3146 | 1.502 | 1.5227 | 1.5503 | 1.6555
2021-11-04 03:00 | 1.6385 | 1.8062 | 1.8297 | 1.8584 | 1.8918 | 0.99073 | 1.2037 | 1.222 | 1.247 | 0.99073 | 1.2765 | 1.4511 | 1.4675 | 1.4893 | 1.5856
2021-11-04 04:00 | 1.6731 | 1.8315 | 1.8489 | 1.8703 | 1.8951 | 0.99073 | 1.1952 | 1.2087 | 1.2273 | 0.99073 | 1.2384 | 1.4003 | 1.4125 | 1.4287 | 1.5162
2021-11-04 05:00 | 1.7528 | 1.9071 | 1.9194 | 1.9344 | 1.9519 | 1.0669 | 1.2779 | 1.2874 | 1.3005 | 1.0669 | 1.3337 | 1.4991 | 1.5077 | 1.5191 | 1.606
2021-11-04 06:00 | 1.9409 | 2.1052 | 2.1155 | 2.128 | 2.1426 | 1.3146 | 1.5676 | 1.5756 | 1.5865 | 1.3146 | 1.5814 | 1.7715 | 1.7787 | 1.7882 | 1.8865
2021-11-04 07:00 | 2.3275 | 2.5239 | 2.5358 | 2.5505 | 2.5675 | 1.5814 | 1.8851 | 1.8944 | 1.9071 | 1.5814 | 1.9243 | 2.155 | 2.1633 | 2.1744 | 2.2935
2021-11-04 08:00 | 2.4145 | 2.6265 | 2.643 | 2.6633 | 2.687 | 1.5623 | 1.8692 | 1.8821 | 1.8998 | 1.5623 | 2.3244 | 2.606 | 2.6176 | 2.6331 | 2.7793
2021-11-04 09:00 | 2.4959 | 2.7272 | 2.7506 | 2.7793 | 2.8127 | 1.5814 | 1.9014 | 1.9197 | 1.9446 | 1.5814 | 2.1339 | 2.4037 | 2.4201 | 2.4419 | 2.5853
2021-11-04 10:00 | 2.5911 | 2.8438 | 2.8745 | 2.912 | 2.9558 | 1.5814 | 1.9118 | 1.9357 | 1.9684 | 1.5814 | 1.81 | 2.0539 | 2.0754 | 2.104 | 2.2376
2021-11-04 11:00 | 2.5149 | 2.7729 | 2.8092 | 2.8535 | 2.9053 | 1.5814 | 1.9197 | 1.948 | 1.9866 | 1.5814 | 1.8672 | 2.1252 | 2.1506 | 2.1843 | 2.3274
2021-11-04 12:00 | 2.553 | 2.8182 | 2.8567 | 2.9038 | 2.9587 | 1.5814 | 1.9229 | 1.9529 | 1.9939 | 1.5814 | 1.7528 | 2.0012 | 2.0282 | 2.064 | 2.2032
2021-11-04 13:00 | 2.534 | 2.7967 | 2.8346 | 2.881 | 2.9352 | 1.5814 | 1.9221 | 1.9517 | 1.9921 | 1.5814 | 1.7147 | 1.9581 | 1.9847 | 2.02 | 2.1565
2021-11-04 14:00 | 2.4959 | 2.7507 | 2.7861 | 2.8295 | 2.88 | 1.5623 | 1.896 | 1.9236 | 1.9613 | 1.5623 | 1.6957 | 1.9334 | 1.9582 | 1.9912 | 2.1238
2021-11-04 15:00 | 2.4387 | 2.6839 | 2.7166 | 2.7565 | 2.8031 | 1.5814 | 1.9146 | 1.94 | 1.9748 | 1.5814 | 1.8481 | 2.099 | 2.1218 | 2.1522 | 2.2901
2021-11-04 16:00 | 2.4387 | 2.6803 | 2.7111 | 2.7488 | 2.7928 | 1.6957 | 2.047 | 2.071 | 2.1038 | 1.6957 | 2.4197 | 2.7316 | 2.7532 | 2.7819 | 2.9492
2021-11-04 17:00 | 2.5721 | 2.8227 | 2.8531 | 2.8903 | 2.9336 | 1.9014 | 2.2894 | 2.3131 | 2.3454 | 1.9014 | 2.5016 | 2.822 | 2.8433 | 2.8716 | 3.0429
2021-11-04 18:00 | 2.6293 | 2.8877 | 2.9199 | 2.9593 | 3.0052 | 2.0632 | 2.4831 | 2.5082 | 2.5424 | 2.0632 | 2.7245 | 3.0723 | 3.0948 | 3.1248 | 3.3103
2021-11-04 19:00 | 2.6102 | 2.8746 | 2.9105 | 2.9545 | 3.0058 | 2.0958 | 2.527 | 2.555 | 2.5933 | 2.0958 | 3.5057 | 3.9455 | 3.9707 | 4.0042 | 4.2369
2021-11-04 20:00 | 2.6293 | 2.9048 | 2.9457 | 2.9958 | 3.0542 | 1.9434 | 2.354 | 2.3859 | 2.4295 | 1.9434 | 3.2199 | 3.6349 | 3.6635 | 3.7016 | 3.9242
2021-11-04 21:00 | 2.4006 | 2.6689 | 2.7147 | 2.7708 | 2.8363 | 1.8394 | 2.2382 | 2.274 | 2.3228 | 1.8394 | 2.5149 | 2.8583 | 2.8905 | 2.9332 | 3.1225
2021-11-04 22:00 | 2.3054 | 2.5681 | 2.6148 | 2.672 | 2.7386 | 1.5936 | 1.949 | 1.9854 | 2.0351 | 1.5936 | 2.0958 | 2.3937 | 2.4264 | 2.4699 | 2.6371
2021-11-04 23:00 | 2.0767 | 2.3166 | 2.3602 | 2.4136 | 2.4759 | 1.4289 | 1.7502 | 1.7842 | 1.8307 | 1.4289 | 1.81 | 2.0719 | 2.1025 | 2.1431 | 2.2912
2021-11-05 | 1.909 | 2.1279 | 2.1672 | 2.2153 | 2.2715 | 1.2474 | 1.5295 | 1.5602 | 1.6021 | 1.2474 | 1.5623 | 1.7907 | 1.8182 | 1.8549 | 1.9845
2021-11-05 01:00 | 1.7909 | 1.9916 | 2.0261 | 2.0684 | 2.1176 | 1.1047 | 1.3541 | 1.381 | 1.4178 | 1.1047 | 1.3908 | 1.5934 | 1.6176 | 1.6497 | 1.7646
2021-11-05 02:00 | 1.6957 | 1.8797 | 1.9093 | 1.9456 | 1.9879 | 1.0479 | 1.28 | 1.3031 | 1.3347 | 1.0479 | 1.2765 | 1.4596 | 1.4804 | 1.5079 | 1.6111
2021-11-05 03:00 | 1.6576 | 1.8267 | 1.8501 | 1.8788 | 1.9123 | 1.0479 | 1.2713 | 1.2896 | 1.3145 | 1.0479 | 1.2575 | 1.4299 | 1.4463 | 1.4681 | 1.5634
2021-11-05 04:00 | 1.6766 | 1.8353 | 1.8528 | 1.8741 | 1.8989 | 1.0479 | 1.2627 | 1.2763 | 1.2948 | 1.0479 | 1.448 | 1.6332 | 1.6454 | 1.6616 | 1.7606
2021-11-05 05:00 | 1.7719 | 1.9276 | 1.9399 | 1.9549 | 1.9724 | 1.1622 | 1.3904 | 1.4 | 1.413 | 1.1622 | 1.6766 | 1.8802 | 1.8888 | 1.9002 | 2.006
2021-11-05 06:00 | 2.0732 | 2.2474 | 2.2576 | 2.2702 | 2.2848 | 1.4099 | 1.6801 | 1.6881 | 1.699 | 1.4099 | 1.8862 | 2.1102 | 2.1174 | 2.1269 | 2.242
2021-11-05 07:00 | 2.3339 | 2.5308 | 2.5427 | 2.5573 | 2.5744 | 1.6957 | 2.0202 | 2.0295 | 2.0422 | 1.6957 | 1.9815 | 2.2185 | 2.2268 | 2.2379 | 2.3602
2021-11-05 08:00 | 2.3435 | 2.5501 | 2.5667 | 2.587 | 2.6107 | 1.6957 | 2.0268 | 2.0397 | 2.0574 | 1.6957 | 2.0958 | 2.3519 | 2.3636 | 2.379 | 2.5127
2021-11-05 09:00 | 2.4387 | 2.6658 | 2.6892 | 2.7179 | 2.7513 | 1.6957 | 2.0365 | 2.0547 | 2.0796 | 1.6957 | 1.6766 | 1.8956 | 1.912 | 1.9338 | 2.052
2021-11-05 10:00 | 2.3782 | 2.615 | 2.6457 | 2.6832 | 2.727 | 1.5052 | 1.8217 | 1.8457 | 1.8783 | 1.5052 | 1.3718 | 1.5669 | 1.5884 | 1.617 | 1.7266
2021-11-05 11:00 | 2.4768 | 2.732 | 2.7682 | 2.8126 | 2.8644 | 1.5052 | 1.8297 | 1.858 | 1.8966 | 1.5052 | 1.6957 | 1.9346 | 1.96 | 1.9938 | 2.1274
2021-11-05 12:00 | 2.4006 | 2.6544 | 2.6929 | 2.74 | 2.7949 | 1.6004 | 1.9454 | 1.9754 | 2.0164 | 1.6004 | 1.467 | 1.6836 | 1.7106 | 1.7464 | 1.8699
2021-11-05 13:00 | 2.5149 | 2.7762 | 2.8141 | 2.8606 | 2.9147 | 1.5242 | 1.8546 | 1.8842 | 1.9246 | 1.5242 | 1.2956 | 1.4923 | 1.5189 | 1.5543 | 1.6677
2021-11-05 14:00 | 2.1529 | 2.3823 | 2.4177 | 2.461 | 2.5115 | 1.2384 | 1.5133 | 1.541 | 1.5787 | 1.2384 | 0.91452 | 1.0654 | 1.0902 | 1.1231 | 1.2128
2021-11-05 15:00 | 2.3244 | 2.5611 | 2.5937 | 2.6337 | 2.6803 | 1.6004 | 1.9371 | 1.9625 | 1.9973 | 1.6004 | 1.6004 | 1.8237 | 1.8466 | 1.877 | 2.0013
2021-11-05 16:00 | 2.2863 | 2.5166 | 2.5474 | 2.5851 | 2.629 | 1.7385 | 2.0976 | 2.1216 | 2.1544 | 1.7385 | 2.0005 | 2.2658 | 2.2874 | 2.3161 | 2.4603
2021-11-05 17:00 | 2.2863 | 2.5157 | 2.5461 | 2.5832 | 2.6266 | 1.823 | 2.1968 | 2.2205 | 2.2528 | 1.823 | 1.9767 | 2.2387 | 2.26 | 2.2882 | 2.4307
2021-11-05 18:00 | 2.3816 | 2.6216 | 2.6538 | 2.6932 | 2.7391 | 1.8862 | 2.274 | 2.2991 | 2.3334 | 1.8862 | 2.4959 | 2.8182 | 2.8407 | 2.8707 | 3.0437
2021-11-05 19:00 | 2.3816 | 2.629 | 2.6649 | 2.7089 | 2.7602 | 1.9434 | 2.3469 | 2.3749 | 2.4132 | 1.9434 | 2.7055 | 3.0563 | 3.0815 | 3.1149 | 3.3037
2021-11-05 20:00 | 2.4197 | 2.6797 | 2.7206 | 2.7707 | 2.829 | 1.9035 | 2.3069 | 2.3388 | 2.3824 | 1.9035 | 2.4959 | 2.8303 | 2.859 | 2.8971 | 3.0798
2021-11-05 21:00 | 2.3625 | 2.6279 | 2.6738 | 2.7299 | 2.7954 | 1.829 | 2.226 | 2.2617 | 2.3106 | 1.829 | 2.6483 | 3.0065 | 3.0387 | 3.0814 | 3.278
2021-11-05 22:00 | 2.2482 | 2.5067 | 2.5534 | 2.6106 | 2.6772 | 1.6524 | 2.0184 | 2.0548 | 2.1046 | 1.6524 | 2.2291 | 2.5419 | 2.5746 | 2.6181 | 2.7926
2021-11-05 23:00 | 2.0196 | 2.2552 | 2.2988 | 2.3522 | 2.4145 | 1.448 | 1.7727 | 1.8067 | 1.8532 | 1.448 | 2.191 | 2.4953 | 2.5259 | 2.5666 | 2.7356
2021-11-06 | 1.8862 | 2.1034 | 2.1428 | 2.1909 | 2.247 | 1.2683 | 1.5542 | 1.5849 | 1.6268 | 1.2683 | 1.8481 | 2.1083 | 2.1358 | 2.1724 | 2.3178
2021-11-06 01:00 | 1.7909 | 1.9916 | 2.0261 | 2.0684 | 2.1176 | 1.1419 | 1.3981 | 1.425 | 1.4618 | 1.1419 | 1.5052 | 1.7205 | 1.7446 | 1.7768 | 1.8979
2021-11-06 02:00 | 1.6957 | 1.8797 | 1.9093 | 1.9456 | 1.9879 | 1.105 | 1.3476 | 1.3707 | 1.4022 | 1.105 | 1.4289 | 1.629 | 1.6497 | 1.6773 | 1.7888
2021-11-06 03:00 | 1.6576 | 1.8267 | 1.8501 | 1.8788 | 1.9123 | 1.0479 | 1.2713 | 1.2896 | 1.3145 | 1.0479 | 1.2765 | 1.4511 | 1.4675 | 1.4893 | 1.5856
2021-11-06 04:00 | 1.6385 | 1.7944 | 1.8118 | 1.8331 | 1.858 | 1.0288 | 1.2402 | 1.2538 | 1.2723 | 1.0288 | 1.2575 | 1.4215 | 1.4337 | 1.4499 | 1.5384
2021-11-06 05:00 | 1.6957 | 1.8457 | 1.858 | 1.873 | 1.8905 | 1.0644 | 1.2749 | 1.2844 | 1.2975 | 1.0644 | 1.4099 | 1.5838 | 1.5923 | 1.6038 | 1.6949
2021-11-06 06:00 | 1.6576 | 1.8008 | 1.8111 | 1.8236 | 1.8382 | 1.1813 | 1.41 | 1.418 | 1.4289 | 1.1813 | 1.3908 | 1.5598 | 1.5669 | 1.5765 | 1.6643
2021-11-06 07:00 | 1.7909 | 1.9474 | 1.9594 | 1.974 | 1.991 | 1.2003 | 1.435 | 1.4443 | 1.457 | 1.2003 | 1.467 | 1.6468 | 1.6552 | 1.6663 | 1.7602
2021-11-06 08:00 | 1.81 | 1.977 | 1.9936 | 2.0139 | 2.0375 | 1.2765 | 1.5316 | 1.5445 | 1.5622 | 1.2765 | 1.2765 | 1.4415 | 1.4531 | 1.4686 | 1.5572
2021-11-06 09:00 | 1.9675 | 2.1596 | 2.183 | 2.2116 | 2.245 | 1.3661 | 1.6471 | 1.6653 | 1.6902 | 1.3661 | 1.467 | 1.6627 | 1.6791 | 1.7009 | 1.8076
2021-11-06 10:00 | 2.0577 | 2.2707 | 2.3014 | 2.3389 | 2.3827 | 1.4099 | 1.7092 | 1.7331 | 1.7658 | 1.4099 | 1.5623 | 1.7787 | 1.8002 | 1.8287 | 1.9488
2021-11-06 11:00 | 1.9243 | 2.1384 | 2.1746 | 2.219 | 2.2708 | 1.3527 | 1.6496 | 1.6779 | 1.7165 | 1.3527 | 0.95263 | 1.1089 | 1.1343 | 1.1681 | 1.2608
2021-11-06 12:00 | 1.7528 | 1.9585 | 1.997 | 2.0441 | 2.099 | 1.2194 | 1.4952 | 1.5252 | 1.5662 | 1.2194 | 1.105 | 1.2814 | 1.3083 | 1.3442 | 1.4477
2021-11-06 13:00 | 1.8672 | 2.0802 | 2.1182 | 2.1646 | 2.2188 | 1.3337 | 1.6295 | 1.6591 | 1.6995 | 1.3337 | 1.1432 | 1.323 | 1.3495 | 1.3849 | 1.49
2021-11-06 14:00 | 1.7719 | 1.9729 | 2.0083 | 2.0516 | 2.1022 | 1.1432 | 1.4008 | 1.4284 | 1.4661 | 1.1432 | 1.0288 | 1.1924 | 1.2172 | 1.2502 | 1.3461
2021-11-06 15:00 | 1.6576 | 1.8447 | 1.8773 | 1.9173 | 1.9638 | 1.0098 | 1.2393 | 1.2648 | 1.2995 | 1.0098 | 1.2384 | 1.4215 | 1.4443 | 1.4747 | 1.5791
2021-11-06 16:00 | 1.7719 | 1.9639 | 1.9947 | 2.0324 | 2.0764 | 1.105 | 1.3493 | 1.3733 | 1.4061 | 1.105 | 1.2003 | 1.3766 | 1.3982 | 1.4268 | 1.5271
2021-11-06 17:00 | 2.0386 | 2.2496 | 2.28 | 2.3171 | 2.3605 | 1.4861 | 1.7988 | 1.8225 | 1.8548 | 1.4861 | 1.7909 | 2.0323 | 2.0536 | 2.0818 | 2.2141
2021-11-06 18:00 | 2.2268 | 2.4554 | 2.4875 | 2.5269 | 2.5728 | 1.6957 | 2.0489 | 2.074 | 2.1083 | 1.6957 | 2.0958 | 2.3736 | 2.3961 | 2.4261 | 2.5771
2021-11-06 19:00 | 2.3816 | 2.629 | 2.6649 | 2.7089 | 2.7602 | 1.7528 | 2.1218 | 2.1498 | 2.1881 | 1.7528 | 2.191 | 2.4846 | 2.5098 | 2.5433 | 2.7037
2021-11-06 20:00 | 2.4006 | 2.6592 | 2.7001 | 2.7502 | 2.8086 | 1.7338 | 2.1064 | 2.1383 | 2.1819 | 1.7338 | 2.3054 | 2.6186 | 2.6473 | 2.6853 | 2.8576
2021-11-06 21:00 | 2.2863 | 2.546 | 2.5919 | 2.648 | 2.7135 | 1.649 | 2.0132 | 2.049 | 2.0978 | 1.649 | 2.172 | 2.4772 | 2.5094 | 2.5521 | 2.7225
2021-11-06 22:00 | 2.172 | 2.4249 | 2.4715 | 2.5287 | 2.5953 | 1.5242 | 1.867 | 1.9034 | 1.9532 | 1.5242 | 2.1339 | 2.436 | 2.4688 | 2.5122 | 2.6815
2021-11-06 23:00 | 1.9434 | 2.1733 | 2.2169 | 2.2703 | 2.3326 | 1.3718 | 1.6826 | 1.7167 | 1.7632 | 1.3718 | 1.6766 | 1.9237 | 1.9543 | 1.9949 | 2.1357
2021-11-07 | 1.8672 | 2.083 | 2.1223 | 2.1704 | 2.2266 | 1.2675 | 1.5533 | 1.584 | 1.6259 | 1.2675 | 1.8481 | 2.1083 | 2.1358 | 2.1724 | 2.3178
2021-11-07 01:00 | 1.81 | 2.0121 | 2.0466 | 2.0888 | 2.1381 | 1.127 | 1.3805 | 1.4074 | 1.4441 | 1.127 | 1.6576 | 1.8898 | 1.914 | 1.9461 | 2.0757
2021-11-07 02:00 | 1.6957 | 1.8797 | 1.9093 | 1.9456 | 1.9879 | 1.0669 | 1.3026 | 1.3257 | 1.3572 | 1.0669 | 1.2384 | 1.4173 | 1.438 | 1.4656 | 1.5666
2021-11-07 03:00 | 1.6957 | 1.8676 | 1.8911 | 1.9198 | 1.9532 | 1.0045 | 1.22 | 1.2383 | 1.2633 | 1.0045 | 1.3337 | 1.5146 | 1.531 | 1.5528 | 1.6523
2021-11-07 04:00 | 1.6766 | 1.8353 | 1.8528 | 1.8741 | 1.8989 | 1.0098 | 1.2177 | 1.2312 | 1.2498 | 1.0098 | 1.2765 | 1.4427 | 1.4549 | 1.4711 | 1.5606
2021-11-07 05:00 | 1.7147 | 1.8662 | 1.8785 | 1.8935 | 1.911 | 1.0084 | 1.2087 | 1.2183 | 1.2313 | 1.0084 | 1.2575 | 1.4144 | 1.423 | 1.4344 | 1.5172
2021-11-07 06:00 | 1.7147 | 1.8622 | 1.8725 | 1.885 | 1.8996 | 1.0479 | 1.2525 | 1.2605 | 1.2714 | 1.0479 | 1.4289 | 1.6021 | 1.6093 | 1.6188 | 1.7087
2021-11-07 07:00 | 1.7147 | 1.8656 | 1.8775 | 1.8921 | 1.9092 | 1.1622 | 1.3899 | 1.3993 | 1.412 | 1.1622 | 1.3718 | 1.541 | 1.5493 | 1.5604 | 1.6491
2021-11-07 08:00 | 1.6029 | 1.7545 | 1.7711 | 1.7913 | 1.815 | 1.2003 | 1.4416 | 1.4545 | 1.4722 | 1.2003 | 1.4099 | 1.5897 | 1.6014 | 1.6168 | 1.7128
2021-11-07 09:00 | 1.448 | 1.6014 | 1.6248 | 1.6535 | 1.6869 | 1.105 | 1.3387 | 1.357 | 1.3819 | 1.105 | 0.95263 | 1.0911 | 1.1075 | 1.1292 | 1.2077
2021-11-07 10:00 | 1.5814 | 1.759 | 1.7896 | 1.8272 | 1.871 | 1.1241 | 1.3716 | 1.3955 | 1.4282 | 1.1241 | 1.1432 | 1.3129 | 1.3344 | 1.3629 | 1.4599
2021-11-07 11:00 | 1.5242 | 1.7085 | 1.7448 | 1.7892 | 1.8409 | 1.105 | 1.357 | 1.3853 | 1.4239 | 1.105 | 1.1622 | 1.3418 | 1.3672 | 1.401 | 1.5052
2021-11-07 12:00 | 1.4099 | 1.59 | 1.6285 | 1.6756 | 1.7305 | 0.87642 | 1.0901 | 1.1201 | 1.1611 | 0.87642 | 1.1432 | 1.3237 | 1.3507 | 1.3865 | 1.4922
2021-11-07 13:00 | 1.5433 | 1.7323 | 1.7702 | 1.8167 | 1.8708 | 0.87642 | 1.0893 | 1.1189 | 1.1593 | 0.87642 | 1.2003 | 1.3865 | 1.4131 | 1.4484 | 1.5566
2021-11-07 14:00 | 1.8481 | 2.0548 | 2.0902 | 2.1335 | 2.184 | 1.3146 | 1.6034 | 1.631 | 1.6687 | 1.3146 | 1.1432 | 1.3194 | 1.3442 | 1.3772 | 1.4794
2021-11-07 15:00 | 1.7909 | 1.988 | 2.0206 | 2.0606 | 2.1071 | 1.1813 | 1.4419 | 1.4673 | 1.5021 | 1.1813 | 1.0669 | 1.2309 | 1.2538 | 1.2842 | 1.3791
2021-11-07 16:00 | 2.0005 | 2.2095 | 2.2403 | 2.278 | 2.322 | 1.3337 | 1.6193 | 1.6434 | 1.6762 | 1.3337 | 1.467 | 1.673 | 1.6946 | 1.7232 | 1.8382
2021-11-07 17:00 | 2.2101 | 2.4338 | 2.4642 | 2.5014 | 2.5447 | 1.7338 | 2.0914 | 2.1151 | 2.1474 | 1.7338 | 1.9243 | 2.1805 | 2.2018 | 2.2301 | 2.3696
2021-11-07 18:00 | 2.3244 | 2.5602 | 2.5924 | 2.6318 | 2.6777 | 1.829 | 2.2065 | 2.2316 | 2.2659 | 1.829 | 2.3816 | 2.6912 | 2.7137 | 2.7437 | 2.9104
2021-11-07 19:00 | 2.467 | 2.7207 | 2.7566 | 2.8006 | 2.8519 | 1.9434 | 2.3469 | 2.3749 | 2.4132 | 1.9434 | 2.3816 | 2.6964 | 2.7215 | 2.755 | 2.9259
2021-11-07 20:00 | 2.553 | 2.8229 | 2.8639 | 2.9139 | 2.9723 | 1.9053 | 2.309 | 2.3409 | 2.3845 | 1.9053 | 2.3435 | 2.6609 | 2.6896 | 2.7277 | 2.9021
2021-11-07 21:00 | 2.4029 | 2.6714 | 2.7172 | 2.7733 | 2.8388 | 1.8481 | 2.2485 | 2.2842 | 2.3331 | 1.8481 | 2.3625 | 2.689 | 2.7211 | 2.7638 | 2.9447
2021-11-07 22:00 | 2.181 | 2.4346 | 2.4813 | 2.5384 | 2.6051 | 1.608 | 1.9661 | 2.0025 | 2.0522 | 1.608 | 2.0196 | 2.309 | 2.3417 | 2.3852 | 2.5482
2021-11-07 23:00 | 2.0386 | 2.2756 | 2.3193 | 2.3727 | 2.435 | 1.3579 | 1.6662 | 1.7003 | 1.7468 | 1.3579 | 1.8862 | 2.1566 | 2.1872 | 2.2278 | 2.3801
2021-11-08 | 1.8481 | 2.0625 | 2.1018 | 2.15 | 2.2061 | 1.1675 | 1.4352 | 1.4659 | 1.5078 | 1.1675 | 1.5623 | 1.7907 | 1.8182 | 1.8549 | 1.9845
2021-11-08 01:00 | 1.6962 | 1.8899 | 1.9244 | 1.9666 | 2.0159 | 1.0669 | 1.3095 | 1.3364 | 1.3732 | 1.0669 | 1.6957 | 1.9322 | 1.9564 | 1.9885 | 2.1201
2021-11-08 02:00 | 1.6576 | 1.8388 | 1.8684 | 1.9046 | 1.9469 | 0.98423 | 1.2048 | 1.2279 | 1.2595 | 0.98423 | 1.4861 | 1.6925 | 1.7133 | 1.7408 | 1.8555
2021-11-08 03:00 | 1.6385 | 1.8062 | 1.8297 | 1.8584 | 1.8918 | 0.97168 | 1.1812 | 1.1995 | 1.2245 | 0.97168 | 1.1813 | 1.3452 | 1.3616 | 1.3835 | 1.4745
2021-11-08 04:00 | 1.6195 | 1.7739 | 1.7913 | 1.8127 | 1.8375 | 0.96094 | 1.16 | 1.1735 | 1.1921 | 0.96094 | 1.2003 | 1.358 | 1.3702 | 1.3864 | 1.4718
2021-11-08 05:00 | 1.6766 | 1.8253 | 1.8375 | 1.8525 | 1.87 | 1.0669 | 1.2779 | 1.2874 | 1.3005 | 1.0669 | 1.4289 | 1.6049 | 1.6135 | 1.6249 | 1.7171
2021-11-08 06:00 | 1.8862 | 2.0465 | 2.0567 | 2.0692 | 2.0838 | 1.244 | 1.4841 | 1.4921 | 1.503 | 1.244 | 1.5242 | 1.708 | 1.7151 | 1.7247 | 1.8198
2021-11-08 07:00 | 2.2673 | 2.4592 | 2.4711 | 2.4857 | 2.5028 | 1.448 | 1.7276 | 1.7369 | 1.7496 | 1.448 | 1.7528 | 1.9644 | 1.9728 | 1.9839 | 2.0935
2021-11-08 08:00 | 2.2101 | 2.4069 | 2.4234 | 2.4437 | 2.4674 | 1.3908 | 1.6666 | 1.6796 | 1.6972 | 1.3908 | 1.6957 | 1.9073 | 1.9189 | 1.9344 | 2.046
2021-11-08 09:00 | 2.172 | 2.3793 | 2.4027 | 2.4313 | 2.4647 | 1.2575 | 1.5188 | 1.537 | 1.562 | 1.2575 | 1.1432 | 1.3028 | 1.3192 | 1.341 | 1.4299
2021-11-08 10:00 | 1.8862 | 2.0865 | 2.1171 | 2.1547 | 2.1985 | 1.0098 | 1.2365 | 1.2605 | 1.2931 | 1.0098 | 1.1622 | 1.3341 | 1.3555 | 1.3841 | 1.4821
2021-11-08 11:00 | 1.8862 | 2.0974 | 2.1337 | 2.1781 | 2.2298 | 0.89547 | 1.1094 | 1.1377 | 1.1763 | 0.89547 | 1.1432 | 1.3206 | 1.346 | 1.3798 | 1.483
2021-11-08 12:00 | 2.1148 | 2.3474 | 2.3859 | 2.433 | 2.4879 | 0.95652 | 1.1847 | 1.2147 | 1.2557 | 0.95652 | 1.5242 | 1.7472 | 1.7741 | 1.8099 | 1.9366
2021-11-08 13:00 | 2.2101 | 2.4487 | 2.4866 | 2.5331 | 2.5872 | 1.105 | 1.3594 | 1.389 | 1.4294 | 1.105 | 1.7147 | 1.9581 | 1.9847 | 2.02 | 2.1565
2021-11-08 14:00 | 1.9815 | 2.1981 | 2.2335 | 2.2768 | 2.3273 | 1.1241 | 1.3783 | 1.4059 | 1.4436 | 1.1241 | 1.5242 | 1.7429 | 1.7677 | 1.8006 | 1.9238
2021-11-08 15:00 | 1.6209 | 1.8053 | 1.8379 | 1.8779 | 1.9245 | 0.77856 | 0.96617 | 0.99162 | 1.0264 | 0.77856 | 1.3527 | 1.5485 | 1.5714 | 1.6017 | 1.7124
2021-11-08 16:00 | 1.9815 | 2.1891 | 2.2199 | 2.2576 | 2.3015 | 1.0479 | 1.2817 | 1.3058 | 1.3386 | 1.0479 | 0.91452 | 1.059 | 1.0806 | 1.1092 | 1.1938
2021-11-08 17:00 | 2.1339 | 2.352 | 2.3823 | 2.4195 | 2.4628 | 1.4793 | 1.7908 | 1.8144 | 1.8468 | 1.4793 | 1.3718 | 1.5665 | 1.5878 | 1.6161 | 1.7253
2021-11-08 18:00 | 2.3816 | 2.6216 | 2.6538 | 2.6932 | 2.7391 | 1.7528 | 2.1165 | 2.1416 | 2.1758 | 1.7528 | 2.4006 | 2.7123 | 2.7349 | 2.7648 | 2.9326
2021-11-08 19:00 | 2.4197 | 2.6699 | 2.7058 | 2.7498 | 2.8011 | 1.8481 | 2.2344 | 2.2624 | 2.3007 | 1.8481 | 2.2482 | 2.5482 | 2.5733 | 2.6068 | 2.7704
2021-11-08 20:00 | 2.534 | 2.8025 | 2.8434 | 2.8935 | 2.9519 | 1.8481 | 2.2414 | 2.2734 | 2.3169 | 1.8481 | 2.2291 | 2.5339 | 2.5626 | 2.6007 | 2.7688
2021-11-08 21:00 | 2.3315 | 2.5946 | 2.6405 | 2.6966 | 2.7621 | 1.7124 | 2.0881 | 2.1239 | 2.1727 | 1.7124 | 2.6483 | 3.0065 | 3.0387 | 3.0814 | 3.278
2021-11-08 22:00 | 2.172 | 2.4249 | 2.4715 | 2.5287 | 2.5953 | 1.5828 | 1.9362 | 1.9726 | 2.0224 | 1.5828 | 1.9815 | 2.2667 | 2.2994 | 2.3428 | 2.5038
2021-11-08 23:00 | 1.985 | 2.218 | 2.2616 | 2.3151 | 2.3774 | 1.3337 | 1.6376 | 1.6717 | 1.7181 | 1.3337 | 1.9243 | 2.1989 | 2.2295 | 2.2701 | 2.4245
2021-11-09 | 1.7909 | 2.0011 | 2.0404 | 2.0886 | 2.1447 | 1.1482 | 1.4124 | 1.4431 | 1.4849 | 1.1482 | 1.6004 | 1.833 | 1.8606 | 1.8972 | 2.029
2021-11-09 01:00 | 1.6385 | 1.8279 | 1.8624 | 1.9046 | 1.9539 | 1.0349 | 1.2717 | 1.2986 | 1.3353 | 1.0349 | 1.2384 | 1.4241 | 1.4482 | 1.4804 | 1.5869
2021-11-09 02:00 | 1.6385 | 1.8183 | 1.8479 | 1.8842 | 1.9264 | 0.97168 | 1.19 | 1.2131 | 1.2447 | 0.97168 | 1.1813 | 1.3538 | 1.3745 | 1.4021 | 1.5
2021-11-09 03:00 | 1.6195 | 1.7858 | 1.8092 | 1.8379 | 1.8714 | 0.97168 | 1.1812 | 1.1995 | 1.2245 | 0.97168 | 1.1622 | 1.324 | 1.3405 | 1.3623 | 1.4523
2021-11-09 04:00 | 1.6004 | 1.7535 | 1.7709 | 1.7922 | 1.817 | 0.97168 | 1.1727 | 1.1862 | 1.2048 | 0.97168 | 1.2956 | 1.4639 | 1.4761 | 1.4923 | 1.5829
2021-11-09 05:00 | 1.6195 | 1.7639 | 1.7761 | 1.7911 | 1.8086 | 1.0611 | 1.2709 | 1.2805 | 1.2935 | 1.0611 | 1.2765 | 1.4355 | 1.4441 | 1.4555 | 1.5394
2021-11-09 06:00 | 1.8291 | 1.9851 | 1.9953 | 2.0078 | 2.0224 | 1.2353 | 1.4739 | 1.4819 | 1.4928 | 1.2353 | 1.7909 | 2.0044 | 2.0116 | 2.0211 | 2.1309
2021-11-09 07:00 | 2.0958 | 2.275 | 2.2869 | 2.3015 | 2.3185 | 1.4861 | 1.7726 | 1.7819 | 1.7946 | 1.4861 | 1.6576 | 1.8585 | 1.8669 | 1.878 | 1.9824
2021-11-09 08:00 | 2.0958 | 2.284 | 2.3006 | 2.3209 | 2.3446 | 1.3112 | 1.5726 | 1.5855 | 1.6031 | 1.3112 | 1.4289 | 1.6109 | 1.6225 | 1.638 | 1.735
2021-11-09 09:00 | 2.0005 | 2.195 | 2.2184 | 2.2471 | 2.2805 | 0.88029 | 1.0732 | 1.0915 | 1.1164 | 0.88029 | 1.1813 | 1.3451 | 1.3615 | 1.3833 | 1.4743
2021-11-09 10:00 | 1.5052 | 1.6771 | 1.7078 | 1.7453 | 1.7891 | 0.63844 | 0.79784 | 0.82177 | 0.85444 | 0.63844 | 1.6957 | 1.9269 | 1.9484 | 1.9769 | 2.1043
2021-11-09 11:00 | 1.448 | 1.6266 | 1.6629 | 1.7073 | 1.759 | 0.60968 | 0.77182 | 0.8001 | 0.83872 | 0.60968 | 1.81 | 2.0617 | 2.0871 | 2.1208 | 2.2607
2021-11-09 12:00 | 1.4289 | 1.6105 | 1.649 | 1.6961 | 1.751 | 0.68589 | 0.865 | 0.89502 | 0.936 | 0.68589 | 1.9243 | 2.1918 | 2.2187 | 2.2546 | 2.4032
2021-11-09 13:00 | 1.3146 | 1.4866 | 1.5246 | 1.571 | 1.6252 | 0.49537 | 0.63916 | 0.66876 | 0.70917 | 0.49537 | 1.7528 | 2.0005 | 2.0271 | 2.0624 | 2.201
2021-11-09 14:00 | 1.2956 | 1.4612 | 1.4966 | 1.5399 | 1.5904 | 0.53347 | 0.68055 | 0.70817 | 0.74586 | 0.53347 | 1.6195 | 1.8487 | 1.8735 | 1.9065 | 2.0349
2021-11-09 15:00 | 1.5623 | 1.7423 | 1.775 | 1.8149 | 1.8615 | 0.74305 | 0.92421 | 0.94967 | 0.98443 | 0.74305 | 1.7147 | 1.9508 | 1.9736 | 2.004 | 2.1346
2021-11-09 16:00 | 1.829 | 2.0253 | 2.0561 | 2.0938 | 2.1378 | 1.0288 | 1.2592 | 1.2833 | 1.3161 | 1.0288 | 1.0288 | 1.186 | 1.2076 | 1.2363 | 1.3271
2021-11-09 17:00 | 2.2291 | 2.4543 | 2.4847 | 2.5218 | 2.5652 | 1.5006 | 1.816 | 1.8396 | 1.872 | 1.5006 | 1.5814 | 1.7994 | 1.8207 | 1.849 | 1.9697
2021-11-09 18:00 | 2.553 | 2.8058 | 2.838 | 2.8774 | 2.9233 | 1.7338 | 2.094 | 2.1191 | 2.1533 | 1.7338 | 2.0196 | 2.2889 | 2.3114 | 2.3414 | 2.4882
2021-11-09 19:00 | 2.4578 | 2.7108 | 2.7468 | 2.7908 | 2.842 | 1.8169 | 2.1975 | 2.2255 | 2.2638 | 1.8169 | 2.1529 | 2.4423 | 2.4675 | 2.5009 | 2.6593
2021-11-09 20:00 | 2.534 | 2.8025 | 2.8434 | 2.8935 | 2.9519 | 1.829 | 2.2189 | 2.2508 | 2.2944 | 1.829 | 2.4006 | 2.7245 | 2.7531 | 2.7912 | 2.9687
2021-11-09 21:00 | 2.4006 | 2.6689 | 2.7147 | 2.7708 | 2.8363 | 1.7407 | 2.1216 | 2.1573 | 2.2062 | 1.7407 | 2.3054 | 2.6254 | 2.6576 | 2.7003 | 2.878
2021-11-09 22:00 | 2.1529 | 2.4044 | 2.4511 | 2.5082 | 2.5749 | 1.5537 | 1.9018 | 1.9382 | 1.988 | 1.5537 | 2.2673 | 2.5843 | 2.617 | 2.6604 | 2.837
2021-11-09 23:00 | 2.0196 | 2.2552 | 2.2988 | 2.3522 | 2.4145 | 1.3131 | 1.6133 | 1.6473 | 1.6938 | 1.3131 | 1.6766 | 1.9237 | 1.9543 | 1.9949 | 2.1357
2021-11-10 | 1.81 | 2.0215 | 2.0609 | 2.109 | 2.1652 | 1.1432 | 1.4064 | 1.4371 | 1.479 | 1.1432 | 1.7719 | 2.0236 | 2.0511 | 2.0877 | 2.2289
2021-11-10 01:00 | 1.6385 | 1.8279 | 1.8624 | 1.9046 | 1.9539 | 1.0445 | 1.283 | 1.3099 | 1.3467 | 1.0445 | 1.2194 | 1.4029 | 1.4271 | 1.4592 | 1.5646
2021-11-10 02:00 | 1.6195 | 1.7978 | 1.8275 | 1.8637 | 1.906 | 0.97046 | 1.1886 | 1.2117 | 1.2432 | 0.97046 | 1.4289 | 1.629 | 1.6497 | 1.6773 | 1.7888
2021-11-10 03:00 | 1.5433 | 1.7039 | 1.7273 | 1.756 | 1.7895 | 0.97168 | 1.1812 | 1.1995 | 1.2245 | 0.97168 | 1.2384 | 1.4087 | 1.4251 | 1.447 | 1.5412
2021-11-10 04:00 | 1.6421 | 1.7982 | 1.8156 | 1.8369 | 1.8618 | 0.97168 | 1.1727 | 1.1862 | 1.2048 | 0.97168 | 1.2956 | 1.4639 | 1.4761 | 1.4923 | 1.5829
2021-11-10 05:00 | 1.6766 | 1.8253 | 1.8375 | 1.8525 | 1.87 | 1.0935 | 1.3092 | 1.3188 | 1.3318 | 1.0935 | 1.3146 | 1.4779 | 1.4865 | 1.4979 | 1.5838
2021-11-10 06:00 | 1.8251 | 1.9808 | 1.991 | 2.0035 | 2.0181 | 1.3527 | 1.6126 | 1.6206 | 1.6315 | 1.3527 | 1.5052 | 1.6868 | 1.694 | 1.7035 | 1.7976
2021-11-10 07:00 | 2.0767 | 2.2545 | 2.2664 | 2.281 | 2.2981 | 1.3908 | 1.66 | 1.6694 | 1.6821 | 1.3908 | 1.6766 | 1.8797 | 1.8881 | 1.8992 | 2.0046
2021-11-10 08:00 | 2.3054 | 2.5092 | 2.5258 | 2.5461 | 2.5697 | 1.4289 | 1.7117 | 1.7246 | 1.7423 | 1.4289 | 1.5242 | 1.7168 | 1.7284 | 1.7438 | 1.8461
2021-11-10 09:00 | 2.2863 | 2.5021 | 2.5255 | 2.5541 | 2.5875 | 1.3337 | 1.6088 | 1.6271 | 1.652 | 1.3337 | 1.448 | 1.6415 | 1.6579 | 1.6797 | 1.7854
2021-11-10 10:00 | 2.3816 | 2.6187 | 2.6493 | 2.6869 | 2.7307 | 1.3337 | 1.6192 | 1.6431 | 1.6758 | 1.3337 | 1.5242 | 1.7363 | 1.7578 | 1.7864 | 1.9043
2021-11-10 11:00 | 2.3816 | 2.6296 | 2.6659 | 2.7103 | 2.762 | 1.3337 | 1.6271 | 1.6554 | 1.694 | 1.3337 | 1.5433 | 1.7652 | 1.7907 | 1.8244 | 1.9496
2021-11-10 12:00 | 2.2482 | 2.4907 | 2.5292 | 2.5763 | 2.6312 | 1.2003 | 1.4727 | 1.5027 | 1.5437 | 1.2003 | 1.3718 | 1.5778 | 1.6047 | 1.6406 | 1.7588
2021-11-10 13:00 | 2.3625 | 2.6124 | 2.6504 | 2.6968 | 2.751 | 1.2194 | 1.4945 | 1.5241 | 1.5645 | 1.2194 | 1.0669 | 1.2383 | 1.2649 | 1.3002 | 1.4011
2021-11-10 14:00 | 2.2405 | 2.4764 | 2.5118 | 2.5551 | 2.6056 | 1.1432 | 1.4008 | 1.4284 | 1.4661 | 1.1432 | 1.0098 | 1.1712 | 1.196 | 1.229 | 1.3239
2021-11-10 15:00 | 2.3054 | 2.5406 | 2.5733 | 2.6132 | 2.6598 | 1.2765 | 1.5544 | 1.5799 | 1.6146 | 1.2765 | 1.2384 | 1.4215 | 1.4443 | 1.4747 | 1.5791
2021-11-10 16:00 | 2.0767 | 2.2914 | 2.3222 | 2.3599 | 2.4039 | 1.2575 | 1.5293 | 1.5533 | 1.5861 | 1.2575 | 1.3908 | 1.5883 | 1.6099 | 1.6386 | 1.7493
2021-11-10 17:00 | 2.2863 | 2.5157 | 2.5461 | 2.5832 | 2.6266 | 1.6957 | 2.0464 | 2.0701 | 2.1024 | 1.6957 | 1.9243 | 2.1805 | 2.2018 | 2.2301 | 2.3696
2021-11-10 18:00 | 2.2831 | 2.5158 | 2.548 | 2.5874 | 2.6333 | 1.7338 | 2.094 | 2.1191 | 2.1533 | 1.7338 | 2.3435 | 2.6488 | 2.6714 | 2.7013 | 2.866
2021-11-10 19:00 | 2.5149 | 2.7722 | 2.8082 | 2.8522 | 2.9034 | 1.829 | 2.2118 | 2.2399 | 2.2781 | 1.829 | 2.2863 | 2.5905 | 2.6157 | 2.6491 | 2.8148
2021-11-10 20:00 | 2.5149 | 2.782 | 2.8229 | 2.873 | 2.9314 | 1.9053 | 2.309 | 2.3409 | 2.3845 | 1.9053 | 2.7817 | 3.1479 | 3.1766 | 3.2147 | 3.4131
2021-11-10 21:00 | 2.3844 | 2.6514 | 2.6972 | 2.7534 | 2.8188 | 1.7888 | 2.1784 | 2.2142 | 2.2631 | 1.7888 | 2.3625 | 2.689 | 2.7211 | 2.7638 | 2.9447
2021-11-10 22:00 | 2.2482 | 2.5067 | 2.5534 | 2.6106 | 2.6772 | 1.6004 | 1.957 | 1.9935 | 2.0432 | 1.6004 | 2.2291 | 2.5419 | 2.5746 | 2.6181 | 2.7926
2021-11-10 23:00 | 2.0196 | 2.2552 | 2.2988 | 2.3522 | 2.4145 | 1.3313 | 1.6347 | 1.6688 | 1.7153 | 1.3313 | 1.7147 | 1.966 | 1.9966 | 2.0373 | 2.1801
2021-11-11 | 1.81 | 2.0215 | 2.0609 | 2.109 | 2.1652 | 1.1129 | 1.3707 | 1.4014 | 1.4433 | 1.1129 | 1.6576 | 1.8965 | 1.9241 | 1.9607 | 2.0956
2021-11-11 01:00 | 1.677 | 1.8692 | 1.9037 | 1.946 | 1.9952 | 1.0677 | 1.3104 | 1.3373 | 1.3741 | 1.0677 | 1.2765 | 1.4664 | 1.4906 | 1.5227 | 1.6313
2021-11-11 02:00 | 1.6385 | 1.8183 | 1.8479 | 1.8842 | 1.9264 | 1.0016 | 1.2254 | 1.2485 | 1.28 | 1.0016 | 1.2956 | 1.4808 | 1.5015 | 1.5291 | 1.6333
2021-11-11 03:00 | 1.6385 | 1.8062 | 1.8297 | 1.8584 | 1.8918 | 0.99073 | 1.2037 | 1.222 | 1.247 | 0.99073 | 1.3337 | 1.5146 | 1.531 | 1.5528 | 1.6523
2021-11-11 04:00 | 1.5996 | 1.7526 | 1.77 | 1.7913 | 1.8162 | 0.99073 | 1.1952 | 1.2087 | 1.2273 | 0.99073 | 1.2003 | 1.358 | 1.3702 | 1.3864 | 1.4718
2021-11-11 05:00 | 1.6957 | 1.8457 | 1.858 | 1.873 | 1.8905 | 1.1173 | 1.3374 | 1.3469 | 1.36 | 1.1173 | 1.4099 | 1.5838 | 1.5923 | 1.6038 | 1.6949
2021-11-11 06:00 | 1.81 | 1.9646 | 1.9748 | 1.9873 | 2.0019 | 1.2765 | 1.5226 | 1.5306 | 1.5415 | 1.2765 | 1.448 | 1.6233 | 1.6305 | 1.64 | 1.731
2021-11-11 07:00 | 1.9243 | 2.0907 | 2.1027 | 2.1173 | 2.1343 | 1.3527 | 1.615 | 1.6243 | 1.637 | 1.3527 | 1.5433 | 1.7315 | 1.7399 | 1.751 | 1.8491
2021-11-11 08:00 | 1.8481 | 2.0179 | 2.0345 | 2.0548 | 2.0785 | 1.2384 | 1.4866 | 1.4995 | 1.5172 | 1.2384 | 1.0669 | 1.2086 | 1.2203 | 1.2357 | 1.3128
2021-11-11 09:00 | 1.9815 | 2.1746 | 2.198 | 2.2266 | 2.26 | 1.086 | 1.3162 | 1.3345 | 1.3594 | 1.086 | 0.99073 | 1.1334 | 1.1498 | 1.1716 | 1.2521
2021-11-11 10:00 | 1.7909 | 1.9841 | 2.0148 | 2.0524 | 2.0961 | 0.87642 | 1.079 | 1.1029 | 1.1356 | 0.87642 | 1.3146 | 1.5034 | 1.5249 | 1.5535 | 1.6599
2021-11-11 11:00 | 1.81 | 2.0155 | 2.0518 | 2.0962 | 2.1479 | 0.87642 | 1.0869 | 1.1152 | 1.1538 | 0.87642 | 1.2575 | 1.4477 | 1.4731 | 1.5068 | 1.6163
2021-11-11 12:00 | 1.829 | 2.0404 | 2.0788 | 2.1259 | 2.1809 | 0.724 | 0.91002 | 0.94004 | 0.98102 | 0.724 | 1.5433 | 1.7683 | 1.7953 | 1.8311 | 1.9588
2021-11-11 13:00 | 1.7528 | 1.9574 | 1.9954 | 2.0418 | 2.096 | 0.68589 | 0.86424 | 0.89384 | 0.93425 | 0.68589 | 1.5814 | 1.8099 | 1.8365 | 1.8718 | 2.001
2021-11-11 14:00 | 1.7528 | 1.9524 | 1.9878 | 2.0312 | 2.0817 | 0.7621 | 0.95065 | 0.97826 | 1.016 | 0.7621 | 1.5623 | 1.7852 | 1.81 | 1.843 | 1.9683
2021-11-11 15:00 | 2.1148 | 2.3359 | 2.3686 | 2.4085 | 2.4551 | 1.105 | 1.3519 | 1.3773 | 1.4121 | 1.105 | 1.3527 | 1.5485 | 1.5714 | 1.6017 | 1.7124
2021-11-11 16:00 | 2.3625 | 2.5985 | 2.6293 | 2.667 | 2.7109 | 1.4761 | 1.7875 | 1.8116 | 1.8444 | 1.4761 | 1.4861 | 1.6942 | 1.7157 | 1.7444 | 1.8604
2021-11-11 17:00 | 2.3625 | 2.5976 | 2.628 | 2.6651 | 2.7085 | 1.829 | 2.2039 | 2.2276 | 2.2599 | 1.829 | 2.2482 | 2.5404 | 2.5617 | 2.59 | 2.7474
2021-11-11 18:00 | 2.4197 | 2.6625 | 2.6947 | 2.7341 | 2.78 | 1.9434 | 2.3415 | 2.3666 | 2.4009 | 1.9434 | 2.4387 | 2.7547 | 2.7772 | 2.8072 | 2.9771
2021-11-11 19:00 | 2.5149 | 2.7722 | 2.8082 | 2.8522 | 2.9034 | 1.9434 | 2.3469 | 2.3749 | 2.4132 | 1.9434 | 2.5911 | 2.9293 | 2.9544 | 2.9879 | 3.1703
2021-11-11 20:00 | 2.4578 | 2.7206 | 2.7615 | 2.8116 | 2.87 | 1.9815 | 2.399 | 2.4309 | 2.4745 | 1.9815 | 2.7626 | 3.1267 | 3.1554 | 3.1935 | 3.3909
2021-11-11 21:00 | 2.4006 | 2.6689 | 2.7147 | 2.7708 | 2.8363 | 1.8672 | 2.271 | 2.3067 | 2.3556 | 1.8672 | 2.4387 | 2.7736 | 2.8058 | 2.8485 | 3.0336
2021-11-11 22:00 | 2.1339 | 2.3839 | 2.4306 | 2.4878 | 2.5544 | 1.587 | 1.9412 | 1.9776 | 2.0273 | 1.587 | 2.0767 | 2.3725 | 2.4052 | 2.4487 | 2.6148
2021-11-11 23:00 | 2.0196 | 2.2552 | 2.2988 | 2.3522 | 2.4145 | 1.3826 | 1.6954 | 1.7294 | 1.7759 | 1.3826 | 1.7719 | 2.0296 | 2.0601 | 2.1008 | 2.2468
2021-11-12 | 1.7909 | 2.0011 | 2.0404 | 2.0886 | 2.1447 | 1.2677 | 1.5535 | 1.5842 | 1.6261 | 1.2677 | 1.6766 | 1.9177 | 1.9453 | 1.9819 | 2.1178
2021-11-12 01:00 | 1.7528 | 1.9507 | 1.9852 | 2.0274 | 2.0767 | 1.105 | 1.3545 | 1.3814 | 1.4182 | 1.105 | 1.3337 | 1.5299 | 1.5541 | 1.5862 | 1.698
2021-11-12 02:00 | 1.7341 | 1.921 | 1.9506 | 1.9869 | 2.0291 | 1.0404 | 1.2712 | 1.2943 | 1.3258 | 1.0404 | 1.3337 | 1.5231 | 1.5439 | 1.5715 | 1.6777
2021-11-12 03:00 | 1.6195 | 1.7858 | 1.8092 | 1.8379 | 1.8714 | 1.0669 | 1.2938 | 1.3121 | 1.337 | 1.0669 | 1.3527 | 1.5357 | 1.5522 | 1.574 | 1.6745
2021-11-12 04:00 | 1.6957 | 1.8558 | 1.8732 | 1.8945 | 1.9194 | 1.058 | 1.2746 | 1.2882 | 1.3067 | 1.058 | 1.4861 | 1.6756 | 1.6878 | 1.704 | 1.8051
2021-11-12 05:00 | 1.7528 | 1.9071 | 1.9194 | 1.9344 | 1.9519 | 1.1813 | 1.4129 | 1.4225 | 1.4355 | 1.1813 | 1.5242 | 1.7108 | 1.7194 | 1.7308 | 1.8282
2021-11-12 06:00 | 2.0767 | 2.2511 | 2.2614 | 2.2739 | 2.2885 | 1.5185 | 1.8085 | 1.8165 | 1.8274 | 1.5185 | 1.9053 | 2.1314 | 2.1386 | 2.1481 | 2.2642
2021-11-12 07:00 | 2.6293 | 2.8481 | 2.86 | 2.8746 | 2.8917 | 1.829 | 2.1777 | 2.187 | 2.1997 | 1.829 | 2.3435 | 2.6207 | 2.6291 | 2.6402 | 2.7823
2021-11-12 08:00 | 2.6293 | 2.8572 | 2.8738 | 2.894 | 2.9177 | 1.8672 | 2.2293 | 2.2423 | 2.2599 | 1.8672 | 2.553 | 2.8601 | 2.8717 | 2.8871 | 3.0459
2021-11-12 09:00 | 2.6293 | 2.8705 | 2.8939 | 2.9226 | 2.956 | 1.7909 | 2.149 | 2.1673 | 2.1922 | 1.7909 | 2.2863 | 2.5731 | 2.5895 | 2.6113 | 2.763
2021-11-12 10:00 | 2.6674 | 2.9257 | 2.9564 | 2.9939 | 3.0377 | 1.81 | 2.1819 | 2.2058 | 2.2385 | 1.81 | 2.3054 | 2.6044 | 2.6259 | 2.6544 | 2.8153
2021-11-12 11:00 | 2.553 | 2.8138 | 2.8501 | 2.8945 | 2.9462 | 1.7089 | 2.0703 | 2.0986 | 2.1372 | 1.7089 | 1.9053 | 2.1675 | 2.1929 | 2.2267 | 2.3718
2021-11-12 12:00 | 2.4959 | 2.7568 | 2.7952 | 2.8424 | 2.8973 | 1.6957 | 2.0579 | 2.0879 | 2.1289 | 1.6957 | 1.829 | 2.0859 | 2.1129 | 2.1487 | 2.2921
2021-11-12 13:00 | 2.2482 | 2.4896 | 2.5276 | 2.574 | 2.6282 | 1.4861 | 1.8096 | 1.8392 | 1.8796 | 1.4861 | 1.2194 | 1.4077 | 1.4342 | 1.4696 | 1.5788
2021-11-12 14:00 | 2.3816 | 2.6279 | 2.6633 | 2.7066 | 2.7572 | 1.4289 | 1.7384 | 1.766 | 1.8037 | 1.4289 | 1.3908 | 1.5947 | 1.6195 | 1.6524 | 1.7683
2021-11-12 15:00 | 2.3435 | 2.5816 | 2.6142 | 2.6542 | 2.7007 | 1.5623 | 1.892 | 1.9175 | 1.9523 | 1.5623 | 1.6957 | 1.9296 | 1.9525 | 1.9828 | 2.1124
2021-11-12 16:00 | 2.3435 | 2.578 | 2.6088 | 2.6465 | 2.6905 | 1.6592 | 2.0039 | 2.0279 | 2.0607 | 1.6592 | 2.1678 | 2.4517 | 2.4733 | 2.5019 | 2.6554
2021-11-12 17:00 | 2.3625 | 2.5976 | 2.628 | 2.6651 | 2.7085 | 1.7719 | 2.1364 | 2.1601 | 2.1924 | 1.7719 | 2.2673 | 2.5616 | 2.5829 | 2.6112 | 2.7696
2021-11-12 18:00 | 2.4959 | 2.7444 | 2.7766 | 2.816 | 2.8619 | 1.9053 | 2.2965 | 2.3216 | 2.3559 | 1.9053 | 2.6293 | 2.9664 | 2.9889 | 3.0189 | 3.1992
2021-11-12 19:00 | 2.4578 | 2.7108 | 2.7468 | 2.7908 | 2.842 | 2.0306 | 2.45 | 2.478 | 2.5163 | 2.0306 | 2.9531 | 3.3315 | 3.3567 | 3.3902 | 3.5925
2021-11-12 20:00 | 2.534 | 2.8025 | 2.8434 | 2.8935 | 2.9519 | 2.1529 | 2.6016 | 2.6335 | 2.6771 | 2.1529 | 3.0484 | 3.4443 | 3.473 | 3.5111 | 3.7242
2021-11-12 21:00 | 2.534 | 2.8121 | 2.858 | 2.9141 | 2.9796 | 2.0386 | 2.4735 | 2.5093 | 2.5582 | 2.0386 | 2.9341 | 3.3241 | 3.3563 | 3.3989 | 3.6113
2021-11-12 22:00 | 2.3487 | 2.6147 | 2.6614 | 2.7185 | 2.7852 | 1.8516 | 2.2537 | 2.2902 | 2.3399 | 1.8516 | 2.553 | 2.9018 | 2.9345 | 2.978 | 3.1703
2021-11-12 23:00 | 2.1529 | 2.3984 | 2.4421 | 2.4955 | 2.5578 | 1.6046 | 1.9577 | 1.9918 | 2.0382 | 1.6046 | 2.2291 | 2.5377 | 2.5683 | 2.6089 | 2.78
2021-11-13 | 2.0196 | 2.2467 | 2.286 | 2.3342 | 2.3903 | 1.467 | 1.789 | 1.8197 | 1.8616 | 1.467 | 1.8481 | 2.1083 | 2.1358 | 2.1724 | 2.3178
2021-11-13 01:00 | 1.9053 | 2.1144 | 2.149 | 2.1912 | 2.2404 | 1.2873 | 1.5699 | 1.5968 | 1.6335 | 1.2873 | 1.6195 | 1.8475 | 1.8717 | 1.9038 | 2.0312
2021-11-13 02:00 | 1.9053 | 2.1049 | 2.1345 | 2.1707 | 2.213 | 1.2575 | 1.5276 | 1.5507 | 1.5823 | 1.2575 | 1.5052 | 1.7137 | 1.7344 | 1.762 | 1.8777
2021-11-13 03:00 | 1.81 | 1.9905 | 2.0139 | 2.0426 | 2.0761 | 1.1622 | 1.4063 | 1.4246 | 1.4496 | 1.1622 | 1.5623 | 1.7686 | 1.7851 | 1.8069 | 1.9189
2021-11-13 04:00 | 1.829 | 1.9991 | 2.0165 | 2.0378 | 2.0627 | 1.1432 | 1.3752 | 1.3888 | 1.4073 | 1.1432 | 1.7338 | 1.9508 | 1.963 | 1.9792 | 2.0939
2021-11-13 05:00 | 1.8481 | 2.0095 | 2.0218 | 2.0368 | 2.0543 | 1.2736 | 1.522 | 1.5316 | 1.5446 | 1.2736 | 1.6385 | 1.8378 | 1.8464 | 1.8578 | 1.9615
2021-11-13 06:00 | 1.9434 | 2.1079 | 2.1181 | 2.1306 | 2.1452 | 1.3337 | 1.5901 | 1.5981 | 1.609 | 1.3337 | 1.7338 | 1.9409 | 1.948 | 1.9576 | 2.0643
2021-11-13 07:00 | 2.0942 | 2.2733 | 2.2852 | 2.2998 | 2.3169 | 1.5433 | 1.8401 | 1.8494 | 1.8621 | 1.5433 | 2.7055 | 3.023 | 3.0314 | 3.0425 | 3.2045
2021-11-13 08:00 | 2.3244 | 2.5297 | 2.5462 | 2.5665 | 2.5902 | 1.8093 | 2.161 | 2.1739 | 2.1916 | 1.8093 | 2.5911 | 2.9024 | 2.914 | 2.9295 | 3.0904
2021-11-13 09:00 | 2.4578 | 2.6863 | 2.7097 | 2.7383 | 2.7717 | 1.8672 | 2.239 | 2.2573 | 2.2822 | 1.8672 | 2.5149 | 2.8272 | 2.8436 | 2.8654 | 3.0297
2021-11-13 10:00 | 2.0958 | 2.3116 | 2.3423 | 2.3799 | 2.4236 | 1.6195 | 1.9568 | 1.9807 | 2.0134 | 1.6195 | 2.0196 | 2.2868 | 2.3083 | 2.3369 | 2.482
2021-11-13 11:00 | 2.0767 | 2.3021 | 2.3384 | 2.3828 | 2.4345 | 1.4861 | 1.8072 | 1.8355 | 1.8741 | 1.4861 | 1.7338 | 1.977 | 2.0024 | 2.0361 | 2.1718
2021-11-13 12:00 | 2.0958 | 2.3269 | 2.3654 | 2.4125 | 2.4674 | 1.3949 | 1.7026 | 1.7326 | 1.7736 | 1.3949 | 1.5433 | 1.7683 | 1.7953 | 1.8311 | 1.9588
2021-11-13 13:00 | 1.9053 | 2.1212 | 2.1591 | 2.2056 | 2.2597 | 1.3718 | 1.6745 | 1.7041 | 1.7445 | 1.3718 | 1.5052 | 1.7252 | 1.7518 | 1.7871 | 1.9121
2021-11-13 14:00 | 1.8481 | 2.0548 | 2.0902 | 2.1335 | 2.184 | 1.467 | 1.7834 | 1.8111 | 1.8487 | 1.467 | 2.0005 | 2.2722 | 2.297 | 2.3299 | 2.4793
2021-11-13 15:00 | 1.8862 | 2.0903 | 2.123 | 2.1629 | 2.2095 | 1.4861 | 1.802 | 1.8275 | 1.8622 | 1.4861 | 1.8481 | 2.099 | 2.1218 | 2.1522 | 2.2901
2021-11-13 16:00 | 2.1148 | 2.3324 | 2.3632 | 2.4009 | 2.4448 | 1.81 | 2.182 | 2.2061 | 2.2389 | 1.81 | 2.2101 | 2.4987 | 2.5203 | 2.549 | 2.7047
2021-11-13 17:00 | 2.4959 | 2.7409 | 2.7712 | 2.8084 | 2.8517 | 2.0767 | 2.4965 | 2.5202 | 2.5526 | 2.0767 | 3.0865 | 3.472 | 3.4933 | 3.5216 | 3.725
2021-11-13 18:00 | 2.4959 | 2.7444 | 2.7766 | 2.816 | 2.8619 | 2.172 | 2.6116 | 2.6367 | 2.671 | 2.172 | 3.3533 | 3.7709 | 3.7935 | 3.8234 | 4.0436
2021-11-13 19:00 | 2.6864 | 2.9565 | 2.9924 | 3.0364 | 3.0877 | 2.2863 | 2.752 | 2.7801 | 2.8183 | 2.2863 | 3.4485 | 3.882 | 3.9072 | 3.9406 | 4.1702
2021-11-13 20:00 | 2.7055 | 2.9867 | 3.0276 | 3.0777 | 3.1361 | 2.2482 | 2.7141 | 2.746 | 2.7896 | 2.2482 | 3.4866 | 3.9313 | 3.9599 | 3.998 | 4.2352
2021-11-13 21:00 | 2.5721 | 2.8531 | 2.8989 | 2.9551 | 3.0205 | 2.172 | 2.6311 | 2.6669 | 2.7157 | 2.172 | 3.3342 | 3.7687 | 3.8009 | 3.8436 | 4.0779
2021-11-13 22:00 | 2.553 | 2.8342 | 2.8809 | 2.9381 | 3.0047 | 1.9434 | 2.3622 | 2.3986 | 2.4483 | 1.9434 | 2.6674 | 3.0289 | 3.0616 | 3.105 | 3.3037
2021-11-13 23:00 | 2.3435 | 2.6031 | 2.6468 | 2.7002 | 2.7625 | 1.6867 | 2.0547 | 2.0887 | 2.1352 | 1.6867 | 2.2291 | 2.5377 | 2.5683 | 2.6089 | 2.78
2021-11-14 | 2.2482 | 2.4923 | 2.5317 | 2.5798 | 2.636 | 1.4963 | 1.8236 | 1.8543 | 1.8962 | 1.4963 | 2.0767 | 2.3623 | 2.3899 | 2.4265 | 2.5845
2021-11-14 01:00 | 2.0196 | 2.2373 | 2.2718 | 2.314 | 2.3633 | 1.3036 | 1.5891 | 1.616 | 1.6527 | 1.3036 | 1.8481 | 2.1016 | 2.1257 | 2.1579 | 2.2979
2021-11-14 02:00 | 2.0386 | 2.2482 | 2.2778 | 2.314 | 2.3563 | 1.2182 | 1.4813 | 1.5044 | 1.5359 | 1.2182 | 1.6004 | 1.8195 | 1.8403 | 1.8679 | 1.9888
2021-11-14 03:00 | 1.9815 | 2.1747 | 2.1981 | 2.2268 | 2.2603 | 1.2575 | 1.5189 | 1.5371 | 1.5621 | 1.2575 | 1.7147 | 1.938 | 1.9544 | 1.9763 | 2.0966
2021-11-14 04:00 | 1.9243 | 2.1014 | 2.1189 | 2.1402 | 2.165 | 1.2194 | 1.4653 | 1.4788 | 1.4974 | 1.2194 | 1.9815 | 2.2261 | 2.2383 | 2.2545 | 2.3828
2021-11-14 05:00 | 2.0577 | 2.2346 | 2.2469 | 2.2619 | 2.2794 | 1.2575 | 1.503 | 1.5125 | 1.5256 | 1.2575 | 1.6004 | 1.7955 | 1.8041 | 1.8155 | 1.9171
2021-11-14 06:00 | 1.9243 | 2.0874 | 2.0976 | 2.1102 | 2.1248 | 1.3337 | 1.5901 | 1.5981 | 1.609 | 1.3337 | 1.9053 | 2.1314 | 2.1386 | 2.1481 | 2.2642
2021-11-14 07:00 | 2.0767 | 2.2545 | 2.2664 | 2.281 | 2.2981 | 1.467 | 1.7501 | 1.7594 | 1.7721 | 1.467 | 2.0005 | 2.2396 | 2.248 | 2.2591 | 2.3824
2021-11-14 08:00 | 1.9624 | 2.1408 | 2.1573 | 2.1776 | 2.2013 | 1.2861 | 1.5429 | 1.5558 | 1.5735 | 1.2861 | 1.3908 | 1.5686 | 1.5802 | 1.5956 | 1.6905
2021-11-14 09:00 | 2.0386 | 2.236 | 2.2594 | 2.288 | 2.3214 | 1.6195 | 1.9464 | 1.9647 | 1.9896 | 1.6195 | 1.9053 | 2.1497 | 2.1661 | 2.1879 | 2.3186
2021-11-14 10:00 | 2.0767 | 2.2912 | 2.3218 | 2.3594 | 2.4032 | 1.5814 | 1.9118 | 1.9357 | 1.9684 | 1.5814 | 1.7909 | 2.0327 | 2.0542 | 2.0828 | 2.2154
2021-11-14 11:00 | 1.9624 | 2.1793 | 2.2156 | 2.2599 | 2.3117 | 1.4099 | 1.7171 | 1.7454 | 1.7841 | 1.4099 | 1.5433 | 1.7652 | 1.7907 | 1.8244 | 1.9496
2021-11-14 12:00 | 1.9815 | 2.2041 | 2.2426 | 2.2897 | 2.3446 | 1.4861 | 1.8103 | 1.8403 | 1.8813 | 1.4861 | 1.9053 | 2.1706 | 2.1976 | 2.2334 | 2.381
2021-11-14 13:00 | 2.2673 | 2.5101 | 2.548 | 2.5945 | 2.6486 | 1.8481 | 2.2372 | 2.2668 | 2.3072 | 1.8481 | 2.2101 | 2.5086 | 2.5352 | 2.5705 | 2.7343
2021-11-14 14:00 | 2.1488 | 2.3778 | 2.4132 | 2.4565 | 2.5071 | 1.6227 | 1.9673 | 1.9949 | 2.0326 | 1.6227 | 1.9053 | 2.1663 | 2.1911 | 2.2241 | 2.3682
2021-11-14 15:00 | 2.5149 | 2.7658 | 2.7984 | 2.8384 | 2.885 | 1.8862 | 2.2747 | 2.3001 | 2.3349 | 1.8862 | 2.553 | 2.8823 | 2.9052 | 2.9356 | 3.1123
2021-11-14 16:00 | 2.6864 | 2.9464 | 2.9772 | 3.0149 | 3.0589 | 2.2291 | 2.6772 | 2.7012 | 2.734 | 2.2291 | 3.1246 | 3.515 | 3.5366 | 3.5652 | 3.7713
2021-11-14 17:00 | 2.915 | 3.1912 | 3.2216 | 3.2587 | 3.3021 | 2.5721 | 3.0817 | 3.1054 | 3.1378 | 2.5721 | 4.4774 | 5.0176 | 5.0389 | 5.0671 | 5.3471
2021-11-14 18:00 | 2.9913 | 3.2766 | 3.3088 | 3.3482 | 3.3941 | 2.5721 | 3.0843 | 3.1094 | 3.1437 | 2.5721 | 4.0963 | 4.5967 | 4.6192 | 4.6492 | 4.9102
2021-11-14 19:00 | 3.1983 | 3.5064 | 3.5424 | 3.5863 | 3.6376 | 2.7824 | 3.338 | 3.3661 | 3.4043 | 2.7824 | 4.6298 | 5.1947 | 5.2199 | 5.2533 | 5.5478
2021-11-14 20:00 | 3.3533 | 3.6826 | 3.7235 | 3.7736 | 3.832 | 2.8579 | 3.4344 | 3.4663 | 3.5098 | 2.8579 | 4.6679 | 5.2439 | 5.2726 | 5.3107 | 5.6129
2021-11-14 21:00 | 3.2844 | 3.6183 | 3.6642 | 3.7203 | 3.7858 | 2.7436 | 3.3063 | 3.3421 | 3.3909 | 2.7436 | 3.6437 | 4.1127 | 4.1448 | 4.1875 | 4.4388
2021-11-14 22:00 | 2.9722 | 3.2846 | 3.3312 | 3.3884 | 3.455 | 2.3337 | 2.8233 | 2.8597 | 2.9094 | 2.3337 | 3.1627 | 3.5793 | 3.6121 | 3.6555 | 3.8814
2021-11-14 23:00 | 2.4768 | 2.7464 | 2.7901 | 2.8435 | 2.9058 | 1.8754 | 2.2776 | 2.3117 | 2.3581 | 1.8754 | 3.1818 | 3.5963 | 3.6269 | 3.6675 | 3.891
2021-11-15 | 2.2863 | 2.5333 | 2.5726 | 2.6208 | 2.6769 | 1.6255 | 1.9763 | 2.0069 | 2.0488 | 1.6255 | 2.172 | 2.4682 | 2.4957 | 2.5324 | 2.6956
2021-11-15 01:00 | 2.2101 | 2.442 | 2.4765 | 2.5187 | 2.5679 | 1.4861 | 1.8047 | 1.8316 | 1.8683 | 1.4861 | 2.0577 | 2.3345 | 2.3586 | 2.3908 | 2.5423
2021-11-15 02:00 | 2.1148 | 2.33 | 2.3596 | 2.3959 | 2.4382 | 1.4099 | 1.7077 | 1.7308 | 1.7623 | 1.4099 | 1.9434 | 2.2006 | 2.2214 | 2.249 | 2.3888
2021-11-15 03:00 | 2.1339 | 2.3384 | 2.3619 | 2.3906 | 2.424 | 1.3718 | 1.6539 | 1.6722 | 1.6972 | 1.3718 | 2.0386 | 2.2979 | 2.3144 | 2.3362 | 2.4744
2021-11-15 04:00 | 2.191 | 2.388 | 2.4054 | 2.4267 | 2.4516 | 1.4289 | 1.7128 | 1.7264 | 1.745 | 1.4289 | 1.9434 | 2.1837 | 2.1959 | 2.2121 | 2.3383
2021-11-15 05:00 | 2.3054 | 2.5007 | 2.513 | 2.528 | 2.5455 | 1.6026 | 1.9106 | 1.9202 | 1.9333 | 1.6026 | 2.4387 | 2.7271 | 2.7356 | 2.7471 | 2.8948
2021-11-15 06:00 | 2.6864 | 2.9062 | 2.9164 | 2.9289 | 2.9435 | 2.1095 | 2.5066 | 2.5146 | 2.5255 | 2.1095 | 3.0987 | 3.4576 | 3.4648 | 3.4743 | 3.6561
2021-11-15 07:00 | 3.4104 | 3.6873 | 3.6992 | 3.7139 | 3.7309 | 2.553 | 3.033 | 3.0423 | 3.055 | 2.553 | 3.639 | 4.0605 | 4.0688 | 4.0799 | 4.2933
2021-11-15 08:00 | 3.3723 | 3.6555 | 3.672 | 3.6923 | 3.716 | 2.4387 | 2.9046 | 2.9175 | 2.9352 | 2.4387 | 3.9248 | 4.3845 | 4.3961 | 4.4115 | 4.6457
2021-11-15 09:00 | 3.3914 | 3.6893 | 3.7127 | 3.7413 | 3.7747 | 2.4387 | 2.9143 | 2.9325 | 2.9574 | 2.4387 | 3.3533 | 3.7588 | 3.7752 | 3.7969 | 4.0073
2021-11-15 10:00 | 3.2389 | 3.5398 | 3.5704 | 3.608 | 3.6518 | 2.0958 | 2.5195 | 2.5434 | 2.5761 | 2.0958 | 3.0294 | 3.4089 | 3.4304 | 3.459 | 3.6597
2021-11-15 11:00 | 3.3914 | 3.7145 | 3.7507 | 3.7951 | 3.8469 | 2.1148 | 2.5499 | 2.5782 | 2.6168 | 2.1148 | 2.5721 | 2.9085 | 2.934 | 2.9677 | 3.1495
2021-11-15 12:00 | 3.2199 | 3.5346 | 3.5731 | 3.6202 | 3.6751 | 2.0767 | 2.5081 | 2.5381 | 2.5791 | 2.0767 | 2.0577 | 2.34 | 2.3669 | 2.4028 | 2.5587
2021-11-15 13:00 | 2.9341 | 3.2265 | 3.2644 | 3.3109 | 3.3651 | 1.829 | 2.2147 | 2.2443 | 2.2847 | 1.829 | 1.8672 | 2.1275 | 2.1541 | 2.1894 | 2.3343
2021-11-15 14:00 | 2.3816 | 2.6279 | 2.6633 | 2.7066 | 2.7572 | 1.4099 | 1.7159 | 1.7435 | 1.7812 | 1.4099 | 1.3718 | 1.5735 | 1.5983 | 1.6313 | 1.7461
2021-11-15 15:00 | 2.6102 | 2.8681 | 2.9008 | 2.9407 | 2.9873 | 1.448 | 1.757 | 1.7825 | 1.8172 | 1.448 | 1.4861 | 1.6967 | 1.7196 | 1.7499 | 1.868
2021-11-15 16:00 | 2.6293 | 2.885 | 2.9158 | 2.9535 | 2.9975 | 1.5438 | 1.8675 | 1.8916 | 1.9244 | 1.5438 | 2.0767 | 2.3505 | 2.3721 | 2.4008 | 2.5492
2021-11-15 17:00 | 2.9913 | 3.2731 | 3.3034 | 3.3406 | 3.3839 | 2.1339 | 2.5641 | 2.5877 | 2.6201 | 2.1339 | 3.3723 | 3.7896 | 3.8109 | 3.8391 | 4.0583
2021-11-15 18:00 | 3.1627 | 3.4608 | 3.493 | 3.5324 | 3.5783 | 2.4197 | 2.9042 | 2.9293 | 2.9636 | 2.4197 | 3.6962 | 4.152 | 4.1746 | 4.2045 | 4.4435
2021-11-15 19:00 | 3.3151 | 3.6319 | 3.6679 | 3.7119 | 3.7631 | 2.7436 | 3.2922 | 3.3203 | 3.3585 | 2.7436 | 4.344 | 4.8771 | 4.9023 | 4.9357 | 5.2145
2021-11-15 20:00 | 3.2961 | 3.6212 | 3.6621 | 3.7122 | 3.7706 | 2.8769 | 3.4569 | 3.4888 | 3.5324 | 2.8769 | 4.1154 | 4.63 | 4.6586 | 4.6967 | 4.9685
2021-11-15 21:00 | 3.1627 | 3.4876 | 3.5335 | 3.5896 | 3.6551 | 2.534 | 3.0587 | 3.0945 | 3.1434 | 2.534 | 4.0201 | 4.5309 | 4.5631 | 4.6058 | 4.8778
2021-11-15 22:00 | 2.9531 | 3.2641 | 3.3108 | 3.3679 | 3.4346 | 2.328 | 2.8166 | 2.853 | 2.9027 | 2.328 | 3.4485 | 3.8969 | 3.9296 | 3.9731 | 4.2147
2021-11-15 23:00 | 2.6483 | 2.9306 | 2.9743 | 3.0277 | 3.09 | 1.9243 | 2.3354 | 2.3694 | 2.4159 | 1.9243 | 2.5743 | 2.9213 | 2.9518 | 2.9925 | 3.1826
2021-11-16 | 2.3054 | 2.5537 | 2.5931 | 2.6412 | 2.6974 | 1.5488 | 1.8856 | 1.9162 | 1.9581 | 1.5488 | 2.0577 | 2.3412 | 2.3687 | 2.4053 | 2.5622
2021-11-16 01:00 | 2.172 | 2.401 | 2.4355 | 2.4778 | 2.527 | 1.4211 | 1.7279 | 1.7549 | 1.7916 | 1.4211 | 1.9624 | 2.2286 | 2.2528 | 2.2849 | 2.4312
2021-11-16 02:00 | 2.0577 | 2.2686 | 2.2982 | 2.3345 | 2.3768 | 1.3337 | 1.6177 | 1.6408 | 1.6723 | 1.3337 | 1.6957 | 1.9254 | 1.9462 | 1.9737 | 2.0999
2021-11-16 03:00 | 2.1529 | 2.3589 | 2.3823 | 2.411 | 2.4445 | 1.3346 | 1.61 | 1.6283 | 1.6533 | 1.3346 | 1.7147 | 1.938 | 1.9544 | 1.9763 | 2.0966
2021-11-16 04:00 | 2.2291 | 2.4289 | 2.4464 | 2.4677 | 2.4925 | 1.3718 | 1.6453 | 1.6589 | 1.6774 | 1.3718 | 1.7909 | 2.0143 | 2.0265 | 2.0427 | 2.1606
2021-11-16 05:00 | 2.2863 | 2.4803 | 2.4925 | 2.5075 | 2.525 | 1.633 | 1.9466 | 1.9561 | 1.9692 | 1.633 | 2.191 | 2.4518 | 2.4604 | 2.4718 | 2.6059
2021-11-16 06:00 | 2.553 | 2.7629 | 2.7731 | 2.7856 | 2.8002 | 2.0196 | 2.4004 | 2.4084 | 2.4193 | 2.0196 | 2.5911 | 2.8936 | 2.9008 | 2.9103 | 3.0641
2021-11-16 07:00 | 2.9341 | 3.1756 | 3.1875 | 3.2021 | 3.2192 | 2.2291 | 2.6504 | 2.6597 | 2.6724 | 2.2291 | 2.7817 | 3.1077 | 3.1161 | 3.1272 | 3.2934
2021-11-16 08:00 | 2.5911 | 2.8162 | 2.8328 | 2.8531 | 2.8768 | 2.1529 | 2.567 | 2.5799 | 2.5975 | 2.1529 | 2.2482 | 2.5213 | 2.5329 | 2.5484 | 2.6904
2021-11-16 09:00 | 2.2496 | 2.4626 | 2.486 | 2.5147 | 2.548 | 1.6004 | 1.9239 | 1.9422 | 1.9671 | 1.6004 | 0.7621 | 0.87934 | 0.89573 | 0.91752 | 0.98546
2021-11-16 10:00 | 1.829 | 2.0251 | 2.0557 | 2.0933 | 2.1371 | 1.1961 | 1.4567 | 1.4806 | 1.5133 | 1.1961 | 1.1813 | 1.3552 | 1.3767 | 1.4053 | 1.5044
2021-11-16 11:00 | 1.6766 | 1.8723 | 1.9085 | 1.9529 | 2.0047 | 1.6576 | 2.0097 | 2.038 | 2.0767 | 1.6576 | 1.2956 | 1.49 | 1.5154 | 1.5492 | 1.6608
2021-11-16 12:00 | 1.6004 | 1.7947 | 1.8332 | 1.8803 | 1.9352 | 0.68589 | 0.865 | 0.89502 | 0.936 | 0.68589 | 1.6385 | 1.8742 | 1.9011 | 1.937 | 2.0699
2021-11-16 13:00 | 1.5623 | 1.7527 | 1.7907 | 1.8371 | 1.8913 | 0.57158 | 0.72919 | 0.75879 | 0.7992 | 0.57158 | 1.6957 | 1.937 | 1.9635 | 1.9989 | 2.1343
2021-11-16 14:00 | 1.7528 | 1.9524 | 1.9878 | 2.0312 | 2.0817 | 0.66684 | 0.83811 | 0.86572 | 0.90342 | 0.66684 | 1.6385 | 1.8699 | 1.8947 | 1.9277 | 2.0571
2021-11-16 15:00 | 1.9721 | 2.1826 | 2.2152 | 2.2551 | 2.3017 | 1.0058 | 1.2346 | 1.2601 | 1.2948 | 1.0058 | 1.5433 | 1.7602 | 1.7831 | 1.8135 | 1.9346
2021-11-16 16:00 | 2.2101 | 2.4347 | 2.4655 | 2.5032 | 2.5472 | 1.2956 | 1.5743 | 1.5984 | 1.6312 | 1.2956 | 1.1432 | 1.3131 | 1.3346 | 1.3633 | 1.4604
2021-11-16 17:00 | 2.3435 | 2.5771 | 2.6075 | 2.6447 | 2.688 | 1.5623 | 1.8888 | 1.9125 | 1.9448 | 1.5623 | 1.8672 | 2.117 | 2.1383 | 2.1665 | 2.303
2021-11-16 18:00 | 2.4768 | 2.7239 | 2.7561 | 2.7955 | 2.8414 | 1.9256 | 2.3206 | 2.3457 | 2.3799 | 1.9256 | 2.7245 | 3.0723 | 3.0948 | 3.1248 | 3.3103
2021-11-16 19:00 | 2.6864 | 2.9565 | 2.9924 | 3.0364 | 3.0877 | 2.0516 | 2.4748 | 2.5028 | 2.5411 | 2.0516 | 2.7245 | 3.0775 | 3.1026 | 3.1361 | 3.3259
2021-11-16 20:00 | 2.8579 | 3.1504 | 3.1914 | 3.2414 | 3.2998 | 2.2101 | 2.6691 | 2.701 | 2.7446 | 2.2101 | 2.8769 | 3.2538 | 3.2824 | 3.3205 | 3.5242
2021-11-16 21:00 | 2.7436 | 3.0373 | 3.0832 | 3.1393 | 3.2047 | 2.1148 | 2.5636 | 2.5993 | 2.6482 | 2.1148 | 2.7055 | 3.0701 | 3.1022 | 3.1449 | 3.3447
2021-11-16 22:00 | 2.5911 | 2.8752 | 2.9219 | 2.979 | 3.0456 | 1.8862 | 2.2947 | 2.3311 | 2.3808 | 1.8862 | 2.915 | 3.3041 | 3.3368 | 3.3803 | 3.5925
2021-11-16 23:00 | 2.3816 | 2.6441 | 2.6877 | 2.7411 | 2.8034 | 1.6576 | 2.0202 | 2.0543 | 2.1008 | 1.6576 | 2.0958 | 2.3895 | 2.4201 | 2.4607 | 2.6245
2021-11-17 | 2.172 | 2.4105 | 2.4498 | 2.4979 | 2.5541 | 1.3256 | 1.6219 | 1.6526 | 1.6945 | 1.3256 | 1.9243 | 2.1929 | 2.2205 | 2.2571 | 2.4067
2021-11-17 01:00 | 1.9624 | 2.1759 | 2.2104 | 2.2526 | 2.3018 | 1.2575 | 1.5346 | 1.5615 | 1.5983 | 1.2575 | 1.5242 | 1.7416 | 1.7658 | 1.7979 | 1.9201
2021-11-17 02:00 | 2.0005 | 2.2072 | 2.2368 | 2.2731 | 2.3154 | 1.2003 | 1.4601 | 1.4832 | 1.5148 | 1.2003 | 1.5814 | 1.7984 | 1.8191 | 1.8467 | 1.9666
2021-11-17 03:00 | 1.9624 | 2.1542 | 2.1776 | 2.2063 | 2.2398 | 1.1813 | 1.4288 | 1.4471 | 1.4721 | 1.1813 | 1.4861 | 1.684 | 1.7004 | 1.7222 | 1.83
2021-11-17 04:00 | 1.9815 | 2.1629 | 2.1803 | 2.2016 | 2.2264 | 1.2166 | 1.462 | 1.4756 | 1.4941 | 1.2166 | 1.5814 | 1.7814 | 1.7936 | 1.8098 | 1.9162
2021-11-17 05:00 | 2.1339 | 2.3165 | 2.3288 | 2.3438 | 2.3613 | 1.4307 | 1.7076 | 1.7172 | 1.7302 | 1.4307 | 1.9815 | 2.2189 | 2.2275 | 2.2389 | 2.3615
2021-11-17 06:00 | 2.3625 | 2.5582 | 2.5684 | 2.5809 | 2.5955 | 1.6833 | 2.0031 | 2.0111 | 2.022 | 1.6833 | 2.2482 | 2.5125 | 2.5197 | 2.5292 | 2.6642
2021-11-17 07:00 | 2.6674 | 2.889 | 2.901 | 2.9156 | 2.9326 | 1.7719 | 2.1102 | 2.1195 | 2.1322 | 1.7719 | 2.2101 | 2.4725 | 2.4809 | 2.492 | 2.6268
2021-11-17 08:00 | 2.2863 | 2.4887 | 2.5053 | 2.5256 | 2.5493 | 1.5242 | 1.8242 | 1.8371 | 1.8548 | 1.5242 | 1.7338 | 1.9497 | 1.9613 | 1.9767 | 2.0905
2021-11-17 09:00 | 2.4006 | 2.6249 | 2.6483 | 2.6769 | 2.7103 | 1.1813 | 1.4288 | 1.447 | 1.4719 | 1.1813 | 0.89547 | 1.0275 | 1.0439 | 1.0657 | 1.141
2021-11-17 10:00 | 2.3244 | 2.5573 | 2.5879 | 2.6255 | 2.6693 | 1.086 | 1.3266 | 1.3505 | 1.3832 | 1.086 | 0.91452 | 1.0588 | 1.0803 | 1.1089 | 1.1933
2021-11-17 11:00 | 1.8672 | 2.0769 | 2.1132 | 2.1576 | 2.2094 | 0.81926 | 1.0194 | 1.0477 | 1.0863 | 0.81926 | 1.105 | 1.2783 | 1.3037 | 1.3375 | 1.4386
2021-11-17 12:00 | 1.9624 | 2.1836 | 2.2221 | 2.2692 | 2.3241 | 0.7621 | 0.95503 | 0.98505 | 1.026 | 0.7621 | 1.3527 | 1.5566 | 1.5836 | 1.6194 | 1.7366
2021-11-17 13:00 | 1.7528 | 1.9574 | 1.9954 | 2.0418 | 2.096 | 0.74305 | 0.93176 | 0.96136 | 1.0018 | 0.74305 | 1.1813 | 1.3653 | 1.3919 | 1.4272 | 1.5344
2021-11-17 14:00 | 1.6195 | 1.8092 | 1.8446 | 1.8879 | 1.9384 | 0.99073 | 1.2207 | 1.2484 | 1.2861 | 0.99073 | 1.5052 | 1.7217 | 1.7465 | 1.7795 | 1.9016
2021-11-17 15:00 | 1.9624 | 2.1722 | 2.2048 | 2.2448 | 2.2914 | 0.97168 | 1.1943 | 1.2198 | 1.2545 | 0.97168 | 1.3527 | 1.5485 | 1.5714 | 1.6017 | 1.7124
2021-11-17 16:00 | 1.7311 | 1.92 | 1.9508 | 1.9885 | 2.0325 | 0.97168 | 1.1917 | 1.2157 | 1.2485 | 0.97168 | 1.105 | 1.2707 | 1.2923 | 1.321 | 1.416
2021-11-17 17:00 | 1.9815 | 2.1882 | 2.2186 | 2.2557 | 2.2991 | 1.3674 | 1.6586 | 1.6822 | 1.7146 | 1.3674 | 1.2765 | 1.4607 | 1.4819 | 1.5102 | 1.6142
2021-11-17 18:00 | 2.4197 | 2.6625 | 2.6947 | 2.7341 | 2.78 | 1.7528 | 2.1165 | 2.1416 | 2.1758 | 1.7528 | 2.2291 | 2.5218 | 2.5443 | 2.5743 | 2.7326
2021-11-17 19:00 | 2.5721 | 2.8337 | 2.8696 | 2.9136 | 2.9649 | 1.8947 | 2.2894 | 2.3174 | 2.3557 | 1.8947 | 2.3816 | 2.6964 | 2.7215 | 2.755 | 2.9259
2021-11-17 20:00 | 2.6293 | 2.9048 | 2.9457 | 2.9958 | 3.0542 | 1.9624 | 2.3765 | 2.4084 | 2.452 | 1.9624 | 2.4578 | 2.788 | 2.8166 | 2.8547 | 3.0354
2021-11-17 21:00 | 2.4959 | 2.7712 | 2.8171 | 2.8732 | 2.9386 | 1.8241 | 2.2201 | 2.2559 | 2.3047 | 1.8241 | 2.4387 | 2.7736 | 2.8058 | 2.8485 | 3.0336
2021-11-17 22:00 | 2.2863 | 2.5477 | 2.5944 | 2.6515 | 2.7181 | 1.6866 | 2.0588 | 2.0952 | 2.145 | 1.6866 | 2.2101 | 2.5207 | 2.5534 | 2.5969 | 2.7704
2021-11-17 23:00 | 2.0767 | 2.3166 | 2.3602 | 2.4136 | 2.4759 | 1.4099 | 1.7276 | 1.7617 | 1.8082 | 1.4099 | 2.2291 | 2.5377 | 2.5683 | 2.6089 | 2.78
2021-11-18 | 1.8319 | 2.0451 | 2.0844 | 2.1326 | 2.1887 | 1.2508 | 1.5335 | 1.5642 | 1.6061 | 1.2508 | 1.5242 | 1.7483 | 1.7759 | 1.8125 | 1.9401
2021-11-18 01:00 | 1.81 | 2.0121 | 2.0466 | 2.0888 | 2.1381 | 1.1197 | 1.3718 | 1.3987 | 1.4355 | 1.1197 | 1.3527 | 1.5511 | 1.5753 | 1.6074 | 1.7202
2021-11-18 02:00 | 1.6576 | 1.8388 | 1.8684 | 1.9046 | 1.9469 | 1.086 | 1.3251 | 1.3482 | 1.3797 | 1.086 | 1.3908 | 1.5866 | 1.6074 | 1.635 | 1.7444
2021-11-18 03:00 | 1.7528 | 1.929 | 1.9525 | 1.9812 | 2.0147 | 1.0561 | 1.281 | 1.2992 | 1.3242 | 1.0561 | 1.5052 | 1.7051 | 1.7216 | 1.7434 | 1.8522
2021-11-18 04:00 | 1.7909 | 1.9582 | 1.9756 | 1.9969 | 2.0217 | 1.1432 | 1.3752 | 1.3888 | 1.4073 | 1.1432 | 1.5623 | 1.7603 | 1.7725 | 1.7887 | 1.8939
2021-11-18 05:00 | 1.8862 | 2.0504 | 2.0627 | 2.0777 | 2.0952 | 1.2395 | 1.4817 | 1.4913 | 1.5043 | 1.2395 | 1.5052 | 1.6896 | 1.6982 | 1.7096 | 1.806
2021-11-18 06:00 | 2.0675 | 2.2413 | 2.2515 | 2.264 | 2.2786 | 1.4861 | 1.7702 | 1.7781 | 1.789 | 1.4861 | 2.0577 | 2.3008 | 2.308 | 2.3175 | 2.442
2021-11-18 07:00 | 2.191 | 2.3773 | 2.3892 | 2.4038 | 2.4209 | 1.4861 | 1.7726 | 1.7819 | 1.7946 | 1.4861 | 1.8672 | 2.0914 | 2.0998 | 2.1109 | 2.2268
2021-11-18 08:00 | 1.9049 | 2.0789 | 2.0955 | 2.1158 | 2.1395 | 1.2575 | 1.5091 | 1.522 | 1.5397 | 1.2575 | 1.2956 | 1.4627 | 1.4743 | 1.4898 | 1.5794
2021-11-18 09:00 | 1.7338 | 1.9085 | 1.9319 | 1.9605 | 1.9939 | 0.97168 | 1.1812 | 1.1994 | 1.2243 | 0.97168 | 1.3146 | 1.4933 | 1.5097 | 1.5315 | 1.6298
2021-11-18 10:00 | 1.448 | 1.6157 | 1.6464 | 1.6839 | 1.7277 | 0.74305 | 0.92142 | 0.94535 | 0.97802 | 0.74305 | 1.6385 | 1.8634 | 1.8848 | 1.9134 | 2.0376
2021-11-18 11:00 | 1.7909 | 1.9951 | 2.0313 | 2.0757 | 2.1275 | 0.7621 | 0.95188 | 0.98017 | 1.0188 | 0.7621 | 1.6766 | 1.9135 | 1.9389 | 1.9726 | 2.1052
2021-11-18 12:00 | 1.6004 | 1.7947 | 1.8332 | 1.8803 | 1.9352 | 0.63958 | 0.8103 | 0.84031 | 0.8813 | 0.63958 | 1.8862 | 2.1494 | 2.1764 | 2.2122 | 2.3587
2021-11-18 13:00 | 1.5814 | 1.7732 | 1.8111 | 1.8576 | 1.9118 | 0.62873 | 0.79672 | 0.82631 | 0.86672 | 0.62873 | 2.1148 | 2.4027 | 2.4293 | 2.4647 | 2.6232
2021-11-18 14:00 | 1.829 | 2.0343 | 2.0697 | 2.113 | 2.1636 | 0.62269 | 0.78596 | 0.81357 | 0.85127 | 0.62269 | 1.7147 | 1.9546 | 1.9794 | 2.0124 | 2.146
2021-11-18 15:00 | 2.0196 | 2.2336 | 2.2662 | 2.3062 | 2.3528 | 0.99559 | 1.2226 | 1.248 | 1.2828 | 0.99559 | 1.7528 | 1.9931 | 2.016 | 2.0464 | 2.1791
2021-11-18 16:00 | 2.172 | 2.3938 | 2.4246 | 2.4623 | 2.5062 | 1.2765 | 1.5518 | 1.5759 | 1.6087 | 1.2765 | 1.1622 | 1.3342 | 1.3558 | 1.3845 | 1.4827
2021-11-18 17:00 | 2.172 | 2.3929 | 2.4233 | 2.4604 | 2.5038 | 2.1117 | 2.5378 | 2.5615 | 2.5938 | 2.1117 | 1.7909 | 2.0323 | 2.0536 | 2.0818 | 2.2141
2021-11-18 18:00 | 2.2863 | 2.5193 | 2.5514 | 2.5908 | 2.6367 | 2.3816 | 2.8592 | 2.8843 | 2.9186 | 2.3816 | 1.9434 | 2.2042 | 2.2267 | 2.2567 | 2.3993
2021-11-18 19:00 | 2.4197 | 2.6699 | 2.7058 | 2.7498 | 2.8011 | 2.6674 | 3.2022 | 3.2302 | 3.2685 | 2.6674 | 2.3244 | 2.6329 | 2.658 | 2.6915 | 2.8593
2021-11-18 20:00 | 2.4578 | 2.7206 | 2.7615 | 2.8116 | 2.87 | 2.6674 | 3.2093 | 3.2412 | 3.2848 | 2.6674 | 2.2673 | 2.5762 | 2.6049 | 2.643 | 2.8132
2021-11-18 21:00 | 2.3435 | 2.6074 | 2.6533 | 2.7094 | 2.7749 | 2.4387 | 2.9462 | 2.982 | 3.0308 | 2.4387 | 2.191 | 2.4984 | 2.5305 | 2.5732 | 2.7447
2021-11-18 22:00 | 2.2291 | 2.4863 | 2.533 | 2.5901 | 2.6567 | 2.285 | 2.7657 | 2.8022 | 2.8519 | 2.285 | 1.9434 | 2.2243 | 2.257 | 2.3005 | 2.4593
2021-11-18 23:00 | 2.0005 | 2.2347 | 2.2783 | 2.3318 | 2.394 | 2.0958 | 2.5379 | 2.572 | 2.6185 | 2.0958 | 1.6766 | 1.9237 | 1.9543 | 1.9949 | 2.1357
2021-11-19 | 1.9243 | 2.1444 | 2.1837 | 2.2318 | 2.288 | 1.7909 | 2.1717 | 2.2023 | 2.2442 | 1.7909 | 1.4289 | 1.6425 | 1.67 | 1.7066 | 1.829
2021-11-19 01:00 | 1.6957 | 1.8893 | 1.9238 | 1.966 | 2.0153 | 1.6645 | 2.0154 | 2.0423 | 2.0791 | 1.6645 | 1.2765 | 1.4664 | 1.4906 | 1.5227 | 1.6313
2021-11-19 02:00 | 1.6385 | 1.8183 | 1.8479 | 1.8842 | 1.9264 | 1.6004 | 1.9328 | 1.9559 | 1.9874 | 1.6004 | 1.2384 | 1.4173 | 1.438 | 1.4656 | 1.5666
2021-11-19 03:00 | 1.6385 | 1.8062 | 1.8297 | 1.8584 | 1.8918 | 1.5623 | 1.879 | 1.8973 | 1.9222 | 1.5623 | 1.2575 | 1.4299 | 1.4463 | 1.4681 | 1.5634
2021-11-19 04:00 | 1.6385 | 1.7944 | 1.8118 | 1.8331 | 1.858 | 1.626 | 1.9457 | 1.9593 | 1.9778 | 1.626 | 1.5242 | 1.7179 | 1.7301 | 1.7463 | 1.8495
2021-11-19 05:00 | 1.829 | 1.989 | 2.0013 | 2.0163 | 2.0338 | 1.8398 | 2.1909 | 2.2005 | 2.2136 | 1.8398 | 1.2956 | 1.4567 | 1.4653 | 1.4767 | 1.5616
2021-11-19 06:00 | 1.928 | 2.0913 | 2.1016 | 2.1141 | 2.1287 | 2.3625 | 2.8055 | 2.8135 | 2.8244 | 2.3625 | 1.6766 | 1.8773 | 1.8845 | 1.894 | 1.9976
2021-11-19 07:00 | 2.3435 | 2.541 | 2.553 | 2.5676 | 2.5846 | 2.7626 | 3.2806 | 3.2899 | 3.3026 | 2.7626 | 1.7909 | 2.0067 | 2.0151 | 2.0262 | 2.138
2021-11-19 08:00 | 2.2291 | 2.4273 | 2.4439 | 2.4642 | 2.4879 | 2.7626 | 3.2872 | 3.3001 | 3.3178 | 2.7626 | 1.6195 | 1.8226 | 1.8343 | 1.8497 | 1.9572
2021-11-19 09:00 | 2.1339 | 2.3383 | 2.3617 | 2.3904 | 2.4238 | 2.3625 | 2.8242 | 2.8425 | 2.8674 | 2.3625 | 0.95263 | 1.0911 | 1.1075 | 1.1292 | 1.2077
2021-11-19 10:00 | 2.0005 | 2.2093 | 2.24 | 2.2775 | 2.3213 | 2.4006 | 2.8796 | 2.9035 | 2.9362 | 2.4006 | 1.3718 | 1.5669 | 1.5884 | 1.617 | 1.7266
2021-11-19 11:00 | 1.5052 | 1.688 | 1.7243 | 1.7687 | 1.8204 | 1.6522 | 2.0034 | 2.0316 | 2.0703 | 1.6522 | 1.5242 | 1.7441 | 1.7695 | 1.8032 | 1.9274
2021-11-19 12:00 | 2.0767 | 2.3064 | 2.3449 | 2.392 | 2.447 | 1.1083 | 1.364 | 1.394 | 1.435 | 1.1083 | 1.448 | 1.6625 | 1.6894 | 1.7253 | 1.8477
2021-11-19 13:00 | 2.3625 | 2.6124 | 2.6504 | 2.6968 | 2.751 | 1.2956 | 1.5845 | 1.6141 | 1.6545 | 1.2956 | 1.2384 | 1.4288 | 1.4554 | 1.4907 | 1.6011
2021-11-19 14:00 | 2.2482 | 2.4846 | 2.52 | 2.5634 | 2.6139 | 1.2765 | 1.5584 | 1.586 | 1.6237 | 1.2765 | 1.086 | 1.2559 | 1.2807 | 1.3137 | 1.4128
2021-11-19 15:00 | 1.9624 | 2.1722 | 2.2048 | 2.2448 | 2.2914 | 1.2003 | 1.4644 | 1.4899 | 1.5246 | 1.2003 | 1.3908 | 1.5908 | 1.6137 | 1.6441 | 1.7569
2021-11-19 16:00 | 2.191 | 2.4142 | 2.445 | 2.4827 | 2.5267 | 1.3527 | 1.6419 | 1.6659 | 1.6987 | 1.3527 | 1.5623 | 1.7788 | 1.8004 | 1.8291 | 1.9493
2021-11-19 17:00 | 2.191 | 2.4134 | 2.4437 | 2.4809 | 2.5242 | 1.6195 | 1.9563 | 1.98 | 2.0124 | 1.6195 | 1.9434 | 2.2017 | 2.223 | 2.2512 | 2.3919
2021-11-19 18:00 | 2.2101 | 2.4374 | 2.4696 | 2.5089 | 2.5549 | 1.7147 | 2.0715 | 2.0966 | 2.1308 | 1.7147 | 2.5911 | 2.924 | 2.9466 | 2.9765 | 3.1548
2021-11-19 19:00 | 2.3244 | 2.5676 | 2.6035 | 2.6475 | 2.6988 | 1.7147 | 2.0768 | 2.1048 | 2.1431 | 1.7147 | 2.3625 | 2.6752 | 2.7004 | 2.7338 | 2.9037
2021-11-19 20:00 | 2.3054 | 2.5568 | 2.5978 | 2.6478 | 2.7062 | 1.7528 | 2.1289 | 2.1608 | 2.2044 | 1.7528 | 2.172 | 2.4704 | 2.4991 | 2.5371 | 2.7021
2021-11-19 21:00 | 2.2291 | 2.4846 | 2.5305 | 2.5866 | 2.6521 | 1.6875 | 2.0588 | 2.0945 | 2.1434 | 1.6875 | 2.3244 | 2.6466 | 2.6787 | 2.7214 | 2.9003
2021-11-19 22:00 | 2.172 | 2.4249 | 2.4715 | 2.5287 | 2.5953 | 1.5433 | 1.8895 | 1.9259 | 1.9757 | 1.5433 | 2.1148 | 2.4149 | 2.4476 | 2.4911 | 2.6593
2021-11-19 23:00 | 2.0005 | 2.2347 | 2.2783 | 2.3318 | 2.394 | 1.3991 | 1.7149 | 1.749 | 1.7954 | 1.3991 | 1.7909 | 2.0507 | 2.0813 | 2.1219 | 2.269
2021-11-20 | 1.9243 | 2.1444 | 2.1837 | 2.2318 | 2.288 | 1.2752 | 1.5623 | 1.593 | 1.6349 | 1.2752 | 1.6385 | 1.8754 | 1.9029 | 1.9395 | 2.0734
2021-11-20 01:00 | 1.7147 | 1.9098 | 1.9443 | 1.9865 | 2.0358 | 1.1045 | 1.3539 | 1.3808 | 1.4176 | 1.1045 | 1.3337 | 1.5299 | 1.5541 | 1.5862 | 1.698
2021-11-20 02:00 | 1.6766 | 1.8592 | 1.8889 | 1.9251 | 1.9674 | 1.0288 | 1.2575 | 1.2806 | 1.3122 | 1.0288 | 1.3146 | 1.502 | 1.5227 | 1.5503 | 1.6555
2021-11-20 03:00 | 1.621 | 1.7874 | 1.8108 | 1.8395 | 1.873 | 1.0098 | 1.2263 | 1.2445 | 1.2695 | 1.0098 | 1.2575 | 1.4299 | 1.4463 | 1.4681 | 1.5634
2021-11-20 04:00 | 1.6385 | 1.7944 | 1.8118 | 1.8331 | 1.858 | 1.0098 | 1.2177 | 1.2312 | 1.2498 | 1.0098 | 1.2003 | 1.358 | 1.3702 | 1.3864 | 1.4718
2021-11-20 05:00 | 1.6766 | 1.8253 | 1.8375 | 1.8525 | 1.87 | 1.0479 | 1.2554 | 1.2649 | 1.278 | 1.0479 | 1.4861 | 1.6684 | 1.677 | 1.6884 | 1.7838
2021-11-20 06:00 | 1.6766 | 1.8213 | 1.8315 | 1.8441 | 1.8587 | 1.105 | 1.32 | 1.328 | 1.3389 | 1.105 | 1.5052 | 1.6868 | 1.694 | 1.7035 | 1.7976
2021-11-20 07:00 | 1.7528 | 1.9065 | 1.9184 | 1.9331 | 1.9501 | 1.2682 | 1.5152 | 1.5245 | 1.5372 | 1.2682 | 1.6004 | 1.795 | 1.8034 | 1.8145 | 1.9158
2021-11-20 08:00 | 1.8862 | 2.0589 | 2.0755 | 2.0958 | 2.1194 | 1.3718 | 1.6441 | 1.6571 | 1.6747 | 1.3718 | 1.6195 | 1.8226 | 1.8343 | 1.8497 | 1.9572
2021-11-20 09:00 | 2.0577 | 2.2565 | 2.2798 | 2.3085 | 2.3419 | 1.448 | 1.7439 | 1.7621 | 1.787 | 1.448 | 1.9434 | 2.192 | 2.2084 | 2.2302 | 2.3631
2021-11-20 10:00 | 2.1148 | 2.3321 | 2.3628 | 2.4003 | 2.4441 | 1.448 | 1.7542 | 1.7781 | 1.8108 | 1.448 | 1.6004 | 1.821 | 1.8425 | 1.8711 | 1.9932
2021-11-20 11:00 | 2.1339 | 2.3635 | 2.3998 | 2.4442 | 2.4959 | 1.4861 | 1.8072 | 1.8355 | 1.8741 | 1.4861 | 1.8862 | 2.1463 | 2.1718 | 2.2055 | 2.3496
2021-11-20 12:00 | 2.1148 | 2.3474 | 2.3859 | 2.433 | 2.4879 | 1.5052 | 1.8328 | 1.8629 | 1.9038 | 1.5052 | 1.7719 | 2.0224 | 2.0494 | 2.0852 | 2.2254
2021-11-20 13:00 | 1.9815 | 2.2031 | 2.241 | 2.2874 | 2.3416 | 1.4861 | 1.8096 | 1.8392 | 1.8796 | 1.4861 | 1.7147 | 1.9581 | 1.9847 | 2.02 | 2.1565
2021-11-20 14:00 | 2.0386 | 2.2595 | 2.2949 | 2.3382 | 2.3887 | 1.5052 | 1.8285 | 1.8561 | 1.8938 | 1.5052 | 1.7528 | 1.9969 | 2.0217 | 2.0547 | 2.1905
2021-11-20 15:00 | 1.9434 | 2.1517 | 2.1844 | 2.2243 | 2.2709 | 1.3908 | 1.6895 | 1.7149 | 1.7497 | 1.3908 | 1.5623 | 1.7814 | 1.8043 | 1.8346 | 1.9569
2021-11-20 16:00 | 2.0767 | 2.2914 | 2.3222 | 2.3599 | 2.4039 | 1.5665 | 1.8944 | 1.9185 | 1.9513 | 1.5665 | 2.172 | 2.4564 | 2.4779 | 2.5066 | 2.6603
2021-11-20 17:00 | 2.3054 | 2.5362 | 2.5665 | 2.6037 | 2.647 | 1.7909 | 2.1589 | 2.1826 | 2.2149 | 1.7909 | 2.2482 | 2.5404 | 2.5617 | 2.59 | 2.7474
2021-11-20 18:00 | 2.3244 | 2.5602 | 2.5924 | 2.6318 | 2.6777 | 1.829 | 2.2065 | 2.2316 | 2.2659 | 1.829 | 2.5911 | 2.924 | 2.9466 | 2.9765 | 3.1548
2021-11-20 19:00 | 2.3816 | 2.629 | 2.6649 | 2.7089 | 2.7602 | 1.8356 | 2.2196 | 2.2476 | 2.2859 | 1.8356 | 2.896 | 3.268 | 3.2932 | 3.3266 | 3.5259
2021-11-20 20:00 | 2.3435 | 2.5978 | 2.6387 | 2.6888 | 2.7472 | 1.9053 | 2.309 | 2.3409 | 2.3845 | 1.9053 | 2.7436 | 3.1056 | 3.1342 | 3.1723 | 3.3687
2021-11-20 21:00 | 2.3054 | 2.5665 | 2.6124 | 2.6685 | 2.7339 | 1.7883 | 2.1779 | 2.2136 | 2.2625 | 1.7883 | 2.4197 | 2.7525 | 2.7846 | 2.8273 | 3.0114
2021-11-20 22:00 | 2.2147 | 2.4707 | 2.5174 | 2.5746 | 2.6412 | 1.6766 | 2.0471 | 2.0835 | 2.1332 | 1.6766 | 2.3054 | 2.6266 | 2.6593 | 2.7028 | 2.8815
2021-11-20 23:00 | 2.0958 | 2.337 | 2.3807 | 2.4341 | 2.4964 | 1.467 | 1.7952 | 1.8292 | 1.8757 | 1.467 | 2.2291 | 2.5377 | 2.5683 | 2.6089 | 2.78
2021-11-21 | 2.0005 | 2.2262 | 2.2656 | 2.3137 | 2.3699 | 1.3392 | 1.6381 | 1.6687 | 1.7106 | 1.3392 | 1.7147 | 1.9601 | 1.9876 | 2.0242 | 2.1623
2021-11-21 01:00 | 1.8672 | 2.0735 | 2.108 | 2.1503 | 2.1995 | 1.2194 | 1.4896 | 1.5165 | 1.5532 | 1.2194 | 1.7338 | 1.9745 | 1.9987 | 2.0308 | 2.1646
2021-11-21 02:00 | 1.7719 | 1.9616 | 1.9912 | 2.0275 | 2.0697 | 1.0814 | 1.3196 | 1.3427 | 1.3743 | 1.0814 | 1.4099 | 1.6078 | 1.6286 | 1.6561 | 1.7666
2021-11-21 03:00 | 1.7528 | 1.929 | 1.9525 | 1.9812 | 2.0147 | 1.086 | 1.3163 | 1.3346 | 1.3595 | 1.086 | 1.5433 | 1.7475 | 1.7639 | 1.7857 | 1.8967
2021-11-21 04:00 | 1.7338 | 1.8968 | 1.9142 | 1.9355 | 1.9603 | 1.0669 | 1.2852 | 1.2988 | 1.3173 | 1.0669 | 1.4289 | 1.6121 | 1.6243 | 1.6405 | 1.7384
2021-11-21 05:00 | 1.7147 | 1.8662 | 1.8785 | 1.8935 | 1.911 | 1.0669 | 1.2779 | 1.2874 | 1.3005 | 1.0669 | 1.3718 | 1.5414 | 1.55 | 1.5614 | 1.6505
2021-11-21 06:00 | 1.6766 | 1.8213 | 1.8315 | 1.8441 | 1.8587 | 1.1241 | 1.3425 | 1.3505 | 1.3614 | 1.1241 | 1.3908 | 1.5598 | 1.5669 | 1.5765 | 1.6643
2021-11-21 07:00 | 1.7577 | 1.9117 | 1.9236 | 1.9382 | 1.9553 | 1.2956 | 1.5475 | 1.5568 | 1.5695 | 1.2956 | 1.6576 | 1.8585 | 1.8669 | 1.878 | 1.9824
2021-11-21 08:00 | 1.8974 | 2.0709 | 2.0874 | 2.1077 | 2.1314 | 1.5242 | 1.8242 | 1.8371 | 1.8548 | 1.5242 | 1.8481 | 2.0767 | 2.0883 | 2.1038 | 2.2238
2021-11-21 09:00 | 2.0386 | 2.236 | 2.2594 | 2.288 | 2.3214 | 1.6385 | 1.9689 | 1.9872 | 2.0121 | 1.6385 | 1.9053 | 2.1497 | 2.1661 | 2.1879 | 2.3186
2021-11-21 10:00 | 1.7909 | 1.9841 | 2.0148 | 2.0524 | 2.0961 | 1.3697 | 1.6618 | 1.6857 | 1.7184 | 1.3697 | 1.5433 | 1.7575 | 1.779 | 1.8075 | 1.9265
2021-11-21 11:00 | 1.81 | 2.0155 | 2.0518 | 2.0962 | 2.1479 | 1.467 | 1.7847 | 1.813 | 1.8516 | 1.467 | 1.6576 | 1.8923 | 1.9177 | 1.9514 | 2.0829
2021-11-21 12:00 | 1.9053 | 2.1222 | 2.1607 | 2.2078 | 2.2627 | 1.4099 | 1.7203 | 1.7503 | 1.7913 | 1.4099 | 1.7528 | 2.0012 | 2.0282 | 2.064 | 2.2032
2021-11-21 13:00 | 1.81 | 2.0188 | 2.0568 | 2.1032 | 2.1574 | 1.4099 | 1.7195 | 1.7491 | 1.7895 | 1.4099 | 1.3908 | 1.5982 | 1.6248 | 1.6601 | 1.7788
2021-11-21 14:00 | 1.8862 | 2.0957 | 2.1311 | 2.1744 | 2.225 | 1.3908 | 1.6934 | 1.721 | 1.7587 | 1.3908 | 1.7338 | 1.9758 | 2.0006 | 2.0335 | 2.1682
2021-11-21 15:00 | 1.829 | 2.0289 | 2.0615 | 2.1015 | 2.1481 | 1.5242 | 1.847 | 1.8725 | 1.9072 | 1.5242 | 1.829 | 2.0778 | 2.1007 | 2.131 | 2.2679
2021-11-21 16:00 | 1.9815 | 2.1891 | 2.2199 | 2.2576 | 2.3015 | 1.5623 | 1.8894 | 1.9135 | 1.9463 | 1.5623 | 2.1529 | 2.4352 | 2.4568 | 2.4854 | 2.6381
2021-11-21 17:00 | 2.3054 | 2.5362 | 2.5665 | 2.6037 | 2.647 | 2.0196 | 2.429 | 2.4527 | 2.485 | 2.0196 | 2.6483 | 2.9851 | 3.0063 | 3.0346 | 3.214
2021-11-21 18:00 | 2.4197 | 2.6625 | 2.6947 | 2.7341 | 2.78 | 2.0577 | 2.4766 | 2.5017 | 2.536 | 2.0577 | 2.7436 | 3.0934 | 3.116 | 3.1459 | 3.3326
2021-11-21 19:00 | 2.534 | 2.7927 | 2.8286 | 2.8726 | 2.9239 | 2.0958 | 2.527 | 2.555 | 2.5933 | 2.0958 | 3.2008 | 3.6068 | 3.632 | 3.6654 | 3.8814
2021-11-21 20:00 | 2.6674 | 2.9458 | 2.9867 | 3.0367 | 3.0951 | 2.2101 | 2.6691 | 2.701 | 2.7446 | 2.2101 | 3.0865 | 3.4867 | 3.5153 | 3.5534 | 3.7686
2021-11-21 21:00 | 2.6293 | 2.9145 | 2.9603 | 3.0165 | 3.0819 | 2.0641 | 2.5037 | 2.5395 | 2.5883 | 2.0641 | 2.7626 | 3.1336 | 3.1657 | 3.2084 | 3.4113
2021-11-21 22:00 | 2.4578 | 2.7319 | 2.7786 | 2.8357 | 2.9024 | 1.7719 | 2.1596 | 2.196 | 2.2458 | 1.7719 | 2.3435 | 2.6689 | 2.7017 | 2.7451 | 2.9259
2021-11-21 23:00 | 2.2101 | 2.4598 | 2.5035 | 2.5569 | 2.6192 | 1.5084 | 1.8441 | 1.8781 | 1.9246 | 1.5084 | 2.2863 | 2.6012 | 2.6318 | 2.6724 | 2.8467
2021-11-22 | 1.9434 | 2.1648 | 2.2042 | 2.2523 | 2.3084 | 1.2882 | 1.5778 | 1.6084 | 1.6503 | 1.2882 | 1.7528 | 2.0024 | 2.03 | 2.0666 | 2.2067
2021-11-22 01:00 | 1.8672 | 2.0735 | 2.108 | 2.1503 | 2.1995 | 1.2062 | 1.474 | 1.5009 | 1.5377 | 1.2062 | 1.6385 | 1.8687 | 1.8928 | 1.925 | 2.0535
2021-11-22 02:00 | 1.8481 | 2.0435 | 2.0731 | 2.1093 | 2.1516 | 1.1622 | 1.4151 | 1.4382 | 1.4697 | 1.1622 | 1.4289 | 1.629 | 1.6497 | 1.6773 | 1.7888
2021-11-22 03:00 | 1.7338 | 1.9086 | 1.932 | 1.9607 | 1.9942 | 1.086 | 1.3163 | 1.3346 | 1.3595 | 1.086 | 1.4099 | 1.5993 | 1.6157 | 1.6375 | 1.7411
2021-11-22 04:00 | 1.7893 | 1.9564 | 1.9738 | 1.9951 | 2.0199 | 1.1622 | 1.3977 | 1.4113 | 1.4298 | 1.1622 | 1.6004 | 1.8026 | 1.8148 | 1.831 | 1.9384
2021-11-22 05:00 | 1.8862 | 2.0504 | 2.0627 | 2.0777 | 2.0952 | 1.3455 | 1.6069 | 1.6165 | 1.6295 | 1.3455 | 1.8672 | 2.0919 | 2.1005 | 2.1119 | 2.2282
2021-11-22 06:00 | 2.0958 | 2.2716 | 2.2818 | 2.2944 | 2.309 | 1.5433 | 1.8378 | 1.8457 | 1.8566 | 1.5433 | 2.0958 | 2.3431 | 2.3503 | 2.3598 | 2.4864
2021-11-22 07:00 | 2.3816 | 2.582 | 2.5939 | 2.6085 | 2.6256 | 1.7528 | 2.0877 | 2.097 | 2.1097 | 1.7528 | 2.1148 | 2.3667 | 2.375 | 2.3861 | 2.5157
2021-11-22 08:00 | 2.4197 | 2.632 | 2.6486 | 2.6689 | 2.6925 | 1.5433 | 1.8467 | 1.8596 | 1.8773 | 1.5433 | 1.829 | 2.0555 | 2.0671 | 2.0826 | 2.2016
2021-11-22 09:00 | 2.3054 | 2.5225 | 2.5459 | 2.5746 | 2.608 | 1.2956 | 1.5638 | 1.5821 | 1.607 | 1.2956 | 1.2194 | 1.3875 | 1.4039 | 1.4257 | 1.5187
2021-11-22 10:00 | 2.2291 | 2.4549 | 2.4856 | 2.5231 | 2.5669 | 1.2194 | 1.4841 | 1.508 | 1.5407 | 1.2194 | 1.2003 | 1.3764 | 1.3979 | 1.4264 | 1.5266
2021-11-22 11:00 | 2.0795 | 2.3051 | 2.3414 | 2.3858 | 2.4375 | 1.1836 | 1.4498 | 1.4781 | 1.5167 | 1.1836 | 1.0288 | 1.1936 | 1.219 | 1.2528 | 1.3497
2021-11-22 12:00 | 2.2291 | 2.4702 | 2.5087 | 2.5558 | 2.6107 | 1.2956 | 1.5853 | 1.6153 | 1.6563 | 1.2956 | 1.3146 | 1.5143 | 1.5412 | 1.577 | 1.6922
2021-11-22 13:00 | 2.0196 | 2.244 | 2.2819 | 2.3284 | 2.3825 | 1.0959 | 1.3486 | 1.3782 | 1.4186 | 1.0959 | 1.0669 | 1.2383 | 1.2649 | 1.3002 | 1.4011
2021-11-22 14:00 | 1.8862 | 2.0957 | 2.1311 | 2.1744 | 2.225 | 1.0288 | 1.2658 | 1.2934 | 1.3311 | 1.0288 | 1.2194 | 1.4041 | 1.4289 | 1.4619 | 1.5683
2021-11-22 15:00 | 1.9243 | 2.1313 | 2.1639 | 2.2038 | 2.2504 | 1.0669 | 1.3068 | 1.3323 | 1.3671 | 1.0669 | 1.2956 | 1.485 | 1.5078 | 1.5382 | 1.6458
2021-11-22 16:00 | 1.8672 | 2.0663 | 2.0971 | 2.1348 | 2.1787 | 1.2003 | 1.4618 | 1.4858 | 1.5186 | 1.2003 | 1.4099 | 1.6095 | 1.631 | 1.6597 | 1.7715
2021-11-22 17:00 | 2.2673 | 2.4952 | 2.5256 | 2.5628 | 2.6061 | 1.5623 | 1.8888 | 1.9125 | 1.9448 | 1.5623 | 1.7528 | 1.99 | 2.0112 | 2.0395 | 2.1697
2021-11-22 18:00 | 2.3244 | 2.5602 | 2.5924 | 2.6318 | 2.6777 | 1.6935 | 2.0463 | 2.0714 | 2.1057 | 1.6935 | 2.3816 | 2.6912 | 2.7137 | 2.7437 | 2.9104
2021-11-22 19:00 | 2.4959 | 2.7518 | 2.7877 | 2.8317 | 2.883 | 1.9062 | 2.303 | 2.3311 | 2.3693 | 1.9062 | 2.6102 | 2.9504 | 2.9756 | 3.0091 | 3.1926
2021-11-22 20:00 | 2.5721 | 2.8434 | 2.8843 | 2.9344 | 2.9928 | 2.0386 | 2.4665 | 2.4984 | 2.542 | 2.0386 | 3.2961 | 3.7195 | 3.7482 | 3.7863 | 4.0131
2021-11-22 21:00 | 2.5042 | 2.7802 | 2.826 | 2.8822 | 2.9476 | 1.9624 | 2.3835 | 2.4193 | 2.4681 | 1.9624 | 2.6864 | 3.0489 | 3.081 | 3.1237 | 3.3224
2021-11-22 22:00 | 2.2432 | 2.5013 | 2.548 | 2.6052 | 2.6718 | 1.7719 | 2.1596 | 2.196 | 2.2458 | 1.7719 | 2.4387 | 2.7748 | 2.8075 | 2.851 | 3.037
2021-11-22 23:00 | 2.0452 | 2.2826 | 2.3263 | 2.3797 | 2.442 | 1.369 | 1.6794 | 1.7134 | 1.7599 | 1.369 | 2.191 | 2.4953 | 2.5259 | 2.5666 | 2.7356
2021-11-23 | 1.8672 | 2.083 | 2.1223 | 2.1704 | 2.2266 | 1.2316 | 1.5109 | 1.5416 | 1.5835 | 1.2316 | 1.9243 | 2.1929 | 2.2205 | 2.2571 | 2.4067
2021-11-23 01:00 | 1.7909 | 1.9916 | 2.0261 | 2.0684 | 2.1176 | 1.1174 | 1.3691 | 1.396 | 1.4328 | 1.1174 | 1.6766 | 1.911 | 1.9352 | 1.9673 | 2.0979
2021-11-23 02:00 | 1.6957 | 1.8797 | 1.9093 | 1.9456 | 1.9879 | 1.0669 | 1.3026 | 1.3257 | 1.3572 | 1.0669 | 1.448 | 1.6502 | 1.6709 | 1.6985 | 1.8111
2021-11-23 03:00 | 1.6957 | 1.8676 | 1.8911 | 1.9198 | 1.9532 | 1.0479 | 1.2713 | 1.2896 | 1.3145 | 1.0479 | 1.2765 | 1.4511 | 1.4675 | 1.4893 | 1.5856
2021-11-23 04:00 | 1.81 | 1.9786 | 1.996 | 2.0173 | 2.0422 | 1.0669 | 1.2852 | 1.2988 | 1.3173 | 1.0669 | 1.4289 | 1.6121 | 1.6243 | 1.6405 | 1.7384
2021-11-23 05:00 | 1.829 | 1.989 | 2.0013 | 2.0163 | 2.0338 | 1.2177 | 1.4559 | 1.4655 | 1.4785 | 1.2177 | 1.5623 | 1.7531 | 1.7617 | 1.7731 | 1.8727
2021-11-23 06:00 | 2.0386 | 2.2102 | 2.2204 | 2.233 | 2.2476 | 1.3527 | 1.6126 | 1.6206 | 1.6315 | 1.3527 | 1.7147 | 1.9197 | 1.9269 | 1.9364 | 2.042
2021-11-23 07:00 | 2.2101 | 2.3978 | 2.4097 | 2.4243 | 2.4413 | 1.6004 | 1.9076 | 1.9169 | 1.9297 | 1.6004 | 1.9243 | 2.155 | 2.1633 | 2.1744 | 2.2935
2021-11-23 08:00 | 2.2673 | 2.4683 | 2.4848 | 2.5051 | 2.5288 | 1.4861 | 1.7792 | 1.7921 | 1.8098 | 1.4861 | 1.6766 | 1.8862 | 1.8978 | 1.9132 | 2.0238
2021-11-23 09:00 | 2.2863 | 2.5021 | 2.5255 | 2.5541 | 2.5875 | 1.448 | 1.7439 | 1.7621 | 1.787 | 1.448 | 1.2765 | 1.451 | 1.4674 | 1.4892 | 1.5854
2021-11-23 10:00 | 2.1529 | 2.373 | 2.4037 | 2.4413 | 2.485 | 1.2956 | 1.5742 | 1.5981 | 1.6307 | 1.2956 | 0.95263 | 1.1012 | 1.1226 | 1.1512 | 1.2377
2021-11-23 11:00 | 1.9434 | 2.1588 | 2.1951 | 2.2395 | 2.2912 | 1.086 | 1.3345 | 1.3628 | 1.4014 | 1.086 | 0.97168 | 1.1301 | 1.1555 | 1.1892 | 1.283
2021-11-23 12:00 | 1.8672 | 2.0813 | 2.1198 | 2.1669 | 2.2218 | 0.94342 | 1.1692 | 1.1993 | 1.2402 | 0.94342 | 1.3337 | 1.5354 | 1.5624 | 1.5982 | 1.7144
2021-11-23 13:00 | 1.7528 | 1.9574 | 1.9954 | 2.0418 | 2.096 | 0.7621 | 0.95427 | 0.98387 | 1.0243 | 0.7621 | 1.3527 | 1.5559 | 1.5824 | 1.6178 | 1.7344
2021-11-23 14:00 | 1.7528 | 1.9524 | 1.9878 | 2.0312 | 2.0817 | 0.7621 | 0.95065 | 0.97826 | 1.016 | 0.7621 | 1.3718 | 1.5735 | 1.5983 | 1.6313 | 1.7461
2021-11-23 15:00 | 1.8862 | 2.0903 | 2.123 | 2.1629 | 2.2095 | 1.0479 | 1.2843 | 1.3098 | 1.3446 | 1.0479 | 1.4099 | 1.612 | 1.6349 | 1.6653 | 1.7791
2021-11-23 16:00 | 1.9199 | 2.1229 | 2.1537 | 2.1914 | 2.2354 | 1.1543 | 1.4074 | 1.4314 | 1.4642 | 1.1543 | 1.0669 | 1.2284 | 1.2499 | 1.2786 | 1.3716
2021-11-23 17:00 | 2.172 | 2.3929 | 2.4233 | 2.4604 | 2.5038 | 1.5355 | 1.8572 | 1.8809 | 1.9132 | 1.5355 | 1.6004 | 1.8206 | 1.8419 | 1.8701 | 1.9919
2021-11-23 18:00 | 2.3396 | 2.5766 | 2.6087 | 2.6481 | 2.694 | 1.7338 | 2.094 | 2.1191 | 2.1533 | 1.7338 | 1.9992 | 2.2663 | 2.2888 | 2.3188 | 2.4645
2021-11-23 19:00 | 2.4578 | 2.7108 | 2.7468 | 2.7908 | 2.842 | 1.8672 | 2.2569 | 2.2849 | 2.3232 | 1.8672 | 2.4578 | 2.7811 | 2.8062 | 2.8397 | 3.0148
2021-11-23 20:00 | 2.4959 | 2.7615 | 2.8024 | 2.8525 | 2.9109 | 1.8672 | 2.2639 | 2.2959 | 2.3394 | 1.8672 | 2.4006 | 2.7245 | 2.7531 | 2.7912 | 2.9687
2021-11-23 21:00 | 2.4197 | 2.6893 | 2.7352 | 2.7913 | 2.8568 | 1.7195 | 2.0965 | 2.1323 | 2.1811 | 1.7195 | 2.2863 | 2.6043 | 2.6364 | 2.6791 | 2.8558
2021-11-23 22:00 | 2.172 | 2.4249 | 2.4715 | 2.5287 | 2.5953 | 1.5703 | 1.9214 | 1.9578 | 2.0076 | 1.5703 | 2.0958 | 2.3937 | 2.4264 | 2.4699 | 2.6371
2021-11-23 23:00 | 1.9572 | 2.1882 | 2.2318 | 2.2852 | 2.3475 | 1.3337 | 1.6376 | 1.6717 | 1.7181 | 1.3337 | 1.7338 | 1.9872 | 2.0178 | 2.0584 | 2.2023
2021-11-24 | 1.81 | 2.0215 | 2.0609 | 2.109 | 2.1652 | 1.2003 | 1.4739 | 1.5046 | 1.5465 | 1.2003 | 1.4099 | 1.6213 | 1.6489 | 1.6855 | 1.8068
2021-11-24 01:00 | 1.6957 | 1.8893 | 1.9238 | 1.966 | 2.0153 | 1.0711 | 1.3144 | 1.3413 | 1.3781 | 1.0711 | 1.3337 | 1.5299 | 1.5541 | 1.5862 | 1.698
2021-11-24 02:00 | 1.6195 | 1.7978 | 1.8275 | 1.8637 | 1.906 | 0.99073 | 1.2125 | 1.2356 | 1.2672 | 0.99073 | 1.3718 | 1.5655 | 1.5862 | 1.6138 | 1.7222
2021-11-24 03:00 | 1.6004 | 1.7653 | 1.7887 | 1.8174 | 1.8509 | 0.99073 | 1.2037 | 1.222 | 1.247 | 0.99073 | 1.2765 | 1.4511 | 1.4675 | 1.4893 | 1.5856
2021-11-24 04:00 | 1.6004 | 1.7535 | 1.7709 | 1.7922 | 1.817 | 0.98554 | 1.189 | 1.2026 | 1.2211 | 0.98554 | 1.2575 | 1.4215 | 1.4337 | 1.4499 | 1.5384
2021-11-24 05:00 | 1.7528 | 1.9071 | 1.9194 | 1.9344 | 1.9519 | 1.139 | 1.3629 | 1.3725 | 1.3856 | 1.139 | 1.2765 | 1.4355 | 1.4441 | 1.4555 | 1.5394
2021-11-24 06:00 | 1.8365 | 1.9931 | 2.0033 | 2.0159 | 2.0305 | 1.3093 | 1.5613 | 1.5693 | 1.5802 | 1.3093 | 1.6195 | 1.8138 | 1.821 | 1.8305 | 1.9309
2021-11-24 07:00 | 2.0196 | 2.1931 | 2.205 | 2.2196 | 2.2367 | 1.3908 | 1.66 | 1.6694 | 1.6821 | 1.3908 | 1.5433 | 1.7315 | 1.7399 | 1.751 | 1.8491
2021-11-24 08:00 | 2.0196 | 2.2022 | 2.2187 | 2.239 | 2.2627 | 1.2282 | 1.4745 | 1.4875 | 1.5051 | 1.2282 | 1.1467 | 1.2973 | 1.3089 | 1.3243 | 1.4058
2021-11-24 09:00 | 2.1508 | 2.3565 | 2.3799 | 2.4086 | 2.442 | 1.1379 | 1.3775 | 1.3958 | 1.4207 | 1.1379 | 0.93358 | 1.0699 | 1.0863 | 1.1081 | 1.1854
2021-11-24 10:00 | 2.3816 | 2.6187 | 2.6493 | 2.6869 | 2.7307 | 1.2888 | 1.5662 | 1.5901 | 1.6228 | 1.2888 | 1.3146 | 1.5034 | 1.5249 | 1.5535 | 1.6599
2021-11-24 11:00 | 2.3639 | 2.6107 | 2.6469 | 2.6913 | 2.7431 | 1.3146 | 1.6046 | 1.6329 | 1.6715 | 1.3146 | 1.6385 | 1.8711 | 1.8965 | 1.9303 | 2.0607
2021-11-24 12:00 | 2.4197 | 2.6749 | 2.7134 | 2.7605 | 2.8154 | 1.4099 | 1.7203 | 1.7503 | 1.7913 | 1.4099 | 1.4099 | 1.6201 | 1.6471 | 1.6829 | 1.8033
2021-11-24 13:00 | 2.2366 | 2.4771 | 2.5151 | 2.5615 | 2.6157 | 1.3012 | 1.5912 | 1.6208 | 1.6612 | 1.3012 | 1.2575 | 1.45 | 1.4766 | 1.5119 | 1.6233
2021-11-24 14:00 | 2.2101 | 2.4437 | 2.4791 | 2.5224 | 2.5729 | 1.2194 | 1.4908 | 1.5184 | 1.5561 | 1.2194 | 0.97168 | 1.1289 | 1.1537 | 1.1866 | 1.2795
2021-11-24 15:00 | 2.2863 | 2.5202 | 2.5528 | 2.5927 | 2.6393 | 1.2956 | 1.5769 | 1.6024 | 1.6372 | 1.2956 | 1.2384 | 1.4215 | 1.4443 | 1.4747 | 1.5791
2021-11-24 16:00 | 2.2291 | 2.4552 | 2.486 | 2.5237 | 2.5676 | 1.3216 | 1.6051 | 1.6291 | 1.662 | 1.3216 | 1.3337 | 1.5248 | 1.5464 | 1.575 | 1.6826
2021-11-24 17:00 | 2.2673 | 2.4952 | 2.5256 | 2.5628 | 2.6061 | 1.5296 | 1.8501 | 1.8738 | 1.9061 | 1.5296 | 1.7528 | 1.99 | 2.0112 | 2.0395 | 2.1697
2021-11-24 18:00 | 2.4006 | 2.6421 | 2.6742 | 2.7136 | 2.7595 | 1.7909 | 2.1615 | 2.1866 | 2.2208 | 1.7909 | 2.191 | 2.4794 | 2.502 | 2.5319 | 2.6882
2021-11-24 19:00 | 2.4164 | 2.6664 | 2.7023 | 2.7463 | 2.7976 | 1.8481 | 2.2344 | 2.2624 | 2.3007 | 1.8481 | 2.5721 | 2.9081 | 2.9333 | 2.9667 | 3.1481
2021-11-24 20:00 | 2.5149 | 2.782 | 2.8229 | 2.873 | 2.9314 | 1.8481 | 2.2414 | 2.2734 | 2.3169 | 1.8481 | 2.4768 | 2.8091 | 2.8378 | 2.8759 | 3.0576
2021-11-24 21:00 | 2.3435 | 2.6074 | 2.6533 | 2.7094 | 2.7749 | 1.7528 | 2.1359 | 2.1717 | 2.2205 | 1.7528 | 2.2291 | 2.5408 | 2.5729 | 2.6156 | 2.7892
2021-11-24 22:00 | 2.2482 | 2.5067 | 2.5534 | 2.6106 | 2.6772 | 1.5732 | 1.9249 | 1.9613 | 2.011 | 1.5732 | 2.4387 | 2.7748 | 2.8075 | 2.851 | 3.037
2021-11-24 23:00 | 2.0005 | 2.2347 | 2.2783 | 2.3318 | 2.394 | 1.3482 | 1.6548 | 1.6888 | 1.7353 | 1.3482 | 1.6576 | 1.9025 | 1.9331 | 1.9737 | 2.1134
2021-11-25 | 1.829 | 2.042 | 2.0814 | 2.1295 | 2.1856 | 1.1768 | 1.4461 | 1.4768 | 1.5187 | 1.1768 | 1.4289 | 1.6425 | 1.67 | 1.7066 | 1.829
2021-11-25 01:00 | 1.7528 | 1.9507 | 1.9852 | 2.0274 | 2.0767 | 1.0669 | 1.3095 | 1.3364 | 1.3732 | 1.0669 | 1.2384 | 1.4241 | 1.4482 | 1.4804 | 1.5869
2021-11-25 02:00 | 1.6576 | 1.8388 | 1.8684 | 1.9046 | 1.9469 | 1.0098 | 1.235 | 1.2581 | 1.2897 | 1.0098 | 1.3146 | 1.502 | 1.5227 | 1.5503 | 1.6555
2021-11-25 03:00 | 1.6766 | 1.8472 | 1.8706 | 1.8993 | 1.9328 | 0.96766 | 1.1765 | 1.1948 | 1.2197 | 0.96766 | 1.3527 | 1.5357 | 1.5522 | 1.574 | 1.6745
2021-11-25 04:00 | 1.6957 | 1.8558 | 1.8732 | 1.8945 | 1.9194 | 0.96297 | 1.1624 | 1.1759 | 1.1945 | 0.96297 | 1.2003 | 1.358 | 1.3702 | 1.3864 | 1.4718
2021-11-25 05:00 | 1.7528 | 1.9071 | 1.9194 | 1.9344 | 1.9519 | 1.093 | 1.3086 | 1.3182 | 1.3312 | 1.093 | 1.2384 | 1.3932 | 1.4018 | 1.4132 | 1.4949
2021-11-25 06:00 | 1.8873 | 2.0477 | 2.0579 | 2.0704 | 2.085 | 1.2384 | 1.4776 | 1.4855 | 1.4964 | 1.2384 | 1.4289 | 1.6021 | 1.6093 | 1.6188 | 1.7087
2021-11-25 07:00 | 2.0958 | 2.275 | 2.2869 | 2.3015 | 2.3185 | 1.2575 | 1.5025 | 1.5118 | 1.5245 | 1.2575 | 1.3718 | 1.541 | 1.5493 | 1.5604 | 1.6491
2021-11-25 08:00 | 2.0509 | 2.2358 | 2.2524 | 2.2727 | 2.2964 | 1.1813 | 1.4191 | 1.432 | 1.4496 | 1.1813 | 0.87642 | 0.99692 | 1.0085 | 1.024 | 1.0906
2021-11-25 09:00 | 2.172 | 2.3793 | 2.4027 | 2.4313 | 2.4647 | 1.105 | 1.3387 | 1.357 | 1.3819 | 1.105 | 1.086 | 1.2393 | 1.2557 | 1.2774 | 1.3632
2021-11-25 10:00 | 2.3054 | 2.5368 | 2.5675 | 2.605 | 2.6488 | 1.2384 | 1.5066 | 1.5306 | 1.5632 | 1.2384 | 1.1432 | 1.3129 | 1.3344 | 1.3629 | 1.4599
2021-11-25 11:00 | 2.3435 | 2.5887 | 2.6249 | 2.6693 | 2.7211 | 1.2575 | 1.5371 | 1.5654 | 1.604 | 1.2575 | 1.0479 | 1.2148 | 1.2402 | 1.2739 | 1.3719
2021-11-25 12:00 | 2.2101 | 2.4497 | 2.4882 | 2.5353 | 2.5902 | 1.1432 | 1.4052 | 1.4352 | 1.4762 | 1.1432 | 1.7909 | 2.0436 | 2.0705 | 2.1064 | 2.2476
2021-11-25 13:00 | 2.4711 | 2.729 | 2.767 | 2.8134 | 2.8676 | 1.3718 | 1.6745 | 1.7041 | 1.7445 | 1.3718 | 1.3718 | 1.577 | 1.6036 | 1.6389 | 1.7566
2021-11-25 14:00 | 2.4768 | 2.7303 | 2.7657 | 2.809 | 2.8595 | 1.3908 | 1.6934 | 1.721 | 1.7587 | 1.3908 | 1.3718 | 1.5735 | 1.5983 | 1.6313 | 1.7461
2021-11-25 15:00 | 2.7245 | 2.9909 | 3.0236 | 3.0635 | 3.1101 | 1.6385 | 1.9821 | 2.0075 | 2.0423 | 1.6385 | 1.8862 | 2.1413 | 2.1642 | 2.1946 | 2.3346
2021-11-25 16:00 | 2.5911 | 2.8441 | 2.8749 | 2.9126 | 2.9565 | 1.6766 | 2.0245 | 2.0485 | 2.0813 | 1.6766 | 1.9624 | 2.2235 | 2.245 | 2.2737 | 2.4159
2021-11-25 17:00 | 2.4818 | 2.7258 | 2.7561 | 2.7933 | 2.8366 | 1.6957 | 2.0464 | 2.0701 | 2.1024 | 1.6957 | 2.2291 | 2.5193 | 2.5405 | 2.5688 | 2.7252
2021-11-25 18:00 | 2.6102 | 2.8672 | 2.8994 | 2.9388 | 2.9847 | 1.9053 | 2.2965 | 2.3216 | 2.3559 | 1.9053 | 2.9531 | 3.3263 | 3.3489 | 3.3788 | 3.577
2021-11-25 19:00 | 2.5911 | 2.8541 | 2.8901 | 2.934 | 2.9853 | 1.9243 | 2.3244 | 2.3524 | 2.3907 | 1.9243 | 2.534 | 2.8657 | 2.8909 | 2.9244 | 3.1037
2021-11-25 20:00 | 2.6674 | 2.9458 | 2.9867 | 3.0367 | 3.0951 | 1.8672 | 2.2639 | 2.2959 | 2.3394 | 1.8672 | 2.6674 | 3.0209 | 3.0495 | 3.0876 | 3.2798
2021-11-25 21:00 | 2.4387 | 2.7098 | 2.7557 | 2.8118 | 2.8772 | 1.7147 | 2.0909 | 2.1267 | 2.1755 | 1.7147 | 2.3435 | 2.6678 | 2.6999 | 2.7426 | 2.9225
2021-11-25 22:00 | 2.2482 | 2.5067 | 2.5534 | 2.6106 | 2.6772 | 1.554 | 1.9023 | 1.9387 | 1.9884 | 1.554 | 1.9434 | 2.2243 | 2.257 | 2.3005 | 2.4593
2021-11-25 23:00 | 2.0577 | 2.2961 | 2.3397 | 2.3932 | 2.4555 | 1.3582 | 1.6666 | 1.7007 | 1.7471 | 1.3582 | 1.8672 | 2.1354 | 2.166 | 2.2066 | 2.3579
2021-11-26 | 1.9243 | 2.1444 | 2.1837 | 2.2318 | 2.288 | 1.1914 | 1.4634 | 1.494 | 1.5359 | 1.1914 | 1.829 | 2.0871 | 2.1146 | 2.1513 | 2.2956
2021-11-26 01:00 | 1.829 | 2.0326 | 2.0671 | 2.1093 | 2.1586 | 1.0943 | 1.3419 | 1.3688 | 1.4055 | 1.0943 | 1.3527 | 1.5511 | 1.5753 | 1.6074 | 1.7202
2021-11-26 02:00 | 1.7338 | 1.9207 | 1.9503 | 1.9865 | 2.0288 | 0.99073 | 1.2125 | 1.2356 | 1.2672 | 0.99073 | 1.4289 | 1.629 | 1.6497 | 1.6773 | 1.7888
2021-11-26 03:00 | 1.6957 | 1.8676 | 1.8911 | 1.9198 | 1.9532 | 0.97168 | 1.1812 | 1.1995 | 1.2245 | 0.97168 | 1.2765 | 1.4511 | 1.4675 | 1.4893 | 1.5856
2021-11-26 04:00 | 1.6766 | 1.8353 | 1.8528 | 1.8741 | 1.8989 | 0.99073 | 1.1952 | 1.2087 | 1.2273 | 0.99073 | 1.2575 | 1.4215 | 1.4337 | 1.4499 | 1.5384
2021-11-26 05:00 | 1.7909 | 1.9481 | 1.9603 | 1.9753 | 1.9928 | 1.086 | 1.3004 | 1.3099 | 1.323 | 1.086 | 1.3527 | 1.5202 | 1.5288 | 1.5402 | 1.6282
2021-11-26 06:00 | 2.0166 | 2.1866 | 2.1968 | 2.2093 | 2.2239 | 1.4861 | 1.7702 | 1.7781 | 1.789 | 1.4861 | 1.6957 | 1.8985 | 1.9057 | 1.9152 | 2.0198
2021-11-26 07:00 | 2.4387 | 2.6434 | 2.6553 | 2.6699 | 2.687 | 1.6195 | 1.9301 | 1.9394 | 1.9522 | 1.6195 | 2.1529 | 2.409 | 2.4174 | 2.4285 | 2.5601
2021-11-26 08:00 | 2.4768 | 2.6934 | 2.71 | 2.7303 | 2.754 | 1.6195 | 1.9367 | 1.9497 | 1.9673 | 1.6195 | 1.8672 | 2.0979 | 2.1095 | 2.1249 | 2.246
2021-11-26 09:00 | 2.5911 | 2.8296 | 2.853 | 2.8816 | 2.915 | 1.6385 | 1.9689 | 1.9872 | 2.0121 | 1.6385 | 2.1148 | 2.3826 | 2.399 | 2.4207 | 2.5631
2021-11-26 10:00 | 2.4959 | 2.7415 | 2.7722 | 2.8097 | 2.8535 | 1.5623 | 1.8893 | 1.9132 | 1.9459 | 1.5623 | 1.9243 | 2.1809 | 2.2024 | 2.231 | 2.3709
2021-11-26 11:00 | 2.534 | 2.7934 | 2.8296 | 2.874 | 2.9258 | 1.5623 | 1.8972 | 1.9255 | 1.9641 | 1.5623 | 1.6004 | 1.8288 | 1.8542 | 1.8879 | 2.0163
2021-11-26 12:00 | 2.6293 | 2.9001 | 2.9385 | 2.9856 | 3.0406 | 1.5623 | 1.9004 | 1.9304 | 1.9714 | 1.5623 | 1.6004 | 1.8318 | 1.8588 | 1.8946 | 2.0255
2021-11-26 13:00 | 2.4768 | 2.7352 | 2.7732 | 2.8196 | 2.8738 | 1.5623 | 1.8996 | 1.9292 | 1.9696 | 1.5623 | 1.5433 | 1.7676 | 1.7942 | 1.8295 | 1.9566
2021-11-26 14:00 | 2.3816 | 2.6279 | 2.6633 | 2.7066 | 2.7572 | 1.467 | 1.7834 | 1.8111 | 1.8487 | 1.467 | 1.467 | 1.6794 | 1.7042 | 1.7371 | 1.8572
2021-11-26 15:00 | 2.3816 | 2.6225 | 2.6551 | 2.6951 | 2.7417 | 1.448 | 1.757 | 1.7825 | 1.8172 | 1.448 | 1.4289 | 1.6332 | 1.656 | 1.6864 | 1.8013
2021-11-26 16:00 | 2.1603 | 2.3812 | 2.412 | 2.4497 | 2.4936 | 1.4539 | 1.7614 | 1.7855 | 1.8183 | 1.4539 | 1.6957 | 1.9271 | 1.9486 | 1.9773 | 2.1048
2021-11-26 17:00 | 2.534 | 2.7818 | 2.8122 | 2.8493 | 2.8927 | 1.9434 | 2.339 | 2.3627 | 2.395 | 1.9434 | 2.5911 | 2.9215 | 2.9428 | 2.9711 | 3.1473
2021-11-26 18:00 | 2.553 | 2.8058 | 2.838 | 2.8774 | 2.9233 | 2.0577 | 2.4766 | 2.5017 | 2.536 | 2.0577 | 2.9531 | 3.3263 | 3.3489 | 3.3788 | 3.577
2021-11-26 19:00 | 2.534 | 2.7927 | 2.8286 | 2.8726 | 2.9239 | 2.0958 | 2.527 | 2.555 | 2.5933 | 2.0958 | 3.1437 | 3.5433 | 3.5684 | 3.6019 | 3.8147
2021-11-26 20:00 | 2.6102 | 2.8843 | 2.9253 | 2.9753 | 3.0337 | 2.0958 | 2.534 | 2.566 | 2.6095 | 2.0958 | 3.0294 | 3.4231 | 3.4518 | 3.4899 | 3.702
2021-11-26 21:00 | 2.553 | 2.8326 | 2.8785 | 2.9346 | 3 | 2.0316 | 2.4653 | 2.501 | 2.5499 | 2.0316 | 2.9722 | 3.3665 | 3.3986 | 3.4413 | 3.6557
2021-11-26 22:00 | 2.4768 | 2.7524 | 2.799 | 2.8562 | 2.9228 | 1.9243 | 2.3397 | 2.3761 | 2.4258 | 1.9243 | 2.8198 | 3.1982 | 3.231 | 3.2744 | 3.4814
2021-11-26 23:00 | 2.2543 | 2.5074 | 2.551 | 2.6044 | 2.6667 | 1.7719 | 2.1553 | 2.1893 | 2.2358 | 1.7719 | 2.3625 | 2.6859 | 2.7165 | 2.7571 | 2.9356
2021-11-27 | 2.0196 | 2.2467 | 2.286 | 2.3342 | 2.3903 | 1.4657 | 1.7874 | 1.8181 | 1.86 | 1.4657 | 2.1148 | 2.4047 | 2.4322 | 2.4688 | 2.6289
2021-11-27 01:00 | 1.8862 | 2.094 | 2.1285 | 2.1707 | 2.22 | 1.2593 | 1.5367 | 1.5636 | 1.6004 | 1.2593 | 1.7528 | 1.9957 | 2.0199 | 2.052 | 2.1868
2021-11-27 02:00 | 1.7894 | 1.9804 | 2.01 | 2.0462 | 2.0885 | 1.2003 | 1.4601 | 1.4832 | 1.5148 | 1.2003 | 1.7338 | 1.9678 | 1.9885 | 2.0161 | 2.1444
2021-11-27 03:00 | 1.81 | 1.9905 | 2.0139 | 2.0426 | 2.0761 | 1.1177 | 1.3537 | 1.372 | 1.397 | 1.1177 | 1.4099 | 1.5993 | 1.6157 | 1.6375 | 1.7411
2021-11-27 04:00 | 1.8481 | 2.0196 | 2.037 | 2.0583 | 2.0831 | 1.1128 | 1.3393 | 1.3529 | 1.3715 | 1.1128 | 1.4289 | 1.6121 | 1.6243 | 1.6405 | 1.7384
2021-11-27 05:00 | 1.8862 | 2.0504 | 2.0627 | 2.0777 | 2.0952 | 1.1784 | 1.4095 | 1.4191 | 1.4321 | 1.1784 | 1.7528 | 1.9649 | 1.9734 | 1.9849 | 2.0949
2021-11-27 06:00 | 1.8862 | 2.0465 | 2.0567 | 2.0692 | 2.0838 | 1.2956 | 1.5451 | 1.5531 | 1.564 | 1.2956 | 1.6766 | 1.8773 | 1.8845 | 1.894 | 1.9976
2021-11-27 07:00 | 2.0386 | 2.2135 | 2.2255 | 2.2401 | 2.2571 | 1.4099 | 1.6826 | 1.6919 | 1.7046 | 1.4099 | 1.9053 | 2.1338 | 2.1421 | 2.1533 | 2.2713
2021-11-27 08:00 | 2.0386 | 2.2226 | 2.2392 | 2.2595 | 2.2832 | 1.6195 | 1.9367 | 1.9497 | 1.9673 | 1.6195 | 1.9053 | 2.1402 | 2.1518 | 2.1673 | 2.2905
2021-11-27 09:00 | 2.2482 | 2.4611 | 2.4845 | 2.5132 | 2.5466 | 1.7528 | 2.104 | 2.1222 | 2.1472 | 1.7528 | 2.1529 | 2.4249 | 2.4413 | 2.4631 | 2.6075
2021-11-27 10:00 | 2.1701 | 2.3914 | 2.4221 | 2.4596 | 2.5034 | 1.6385 | 1.9793 | 2.0032 | 2.0359 | 1.6385 | 2.3816 | 2.6891 | 2.7106 | 2.7391 | 2.9042
2021-11-27 11:00 | 2.2673 | 2.5068 | 2.5431 | 2.5874 | 2.6392 | 1.5052 | 1.8297 | 1.858 | 1.8966 | 1.5052 | 1.8481 | 2.104 | 2.1294 | 2.1632 | 2.3051
2021-11-27 12:00 | 2.2243 | 2.465 | 2.5034 | 2.5505 | 2.6055 | 1.466 | 1.7866 | 1.8166 | 1.8576 | 1.466 | 1.6766 | 1.9165 | 1.9435 | 1.9793 | 2.1143
2021-11-27 13:00 | 1.7528 | 1.9574 | 1.9954 | 2.0418 | 2.096 | 1.3718 | 1.6745 | 1.7041 | 1.7445 | 1.3718 | 1.2194 | 1.4077 | 1.4342 | 1.4696 | 1.5788
2021-11-27 14:00 | 1.6195 | 1.8092 | 1.8446 | 1.8879 | 1.9384 | 1.1241 | 1.3783 | 1.4059 | 1.4436 | 1.1241 | 0.81926 | 0.9595 | 0.9843 | 1.0173 | 1.1017
2021-11-27 15:00 | 1.9243 | 2.1313 | 2.1639 | 2.2038 | 2.2504 | 1.3245 | 1.6111 | 1.6365 | 1.6713 | 1.3245 | 2.0958 | 2.3742 | 2.3971 | 2.4275 | 2.579
2021-11-27 16:00 | 2.0386 | 2.2505 | 2.2813 | 2.319 | 2.3629 | 1.5433 | 1.8669 | 1.891 | 1.9238 | 1.5433 | 2.0005 | 2.2658 | 2.2874 | 2.3161 | 2.4603
2021-11-27 17:00 | 2.1529 | 2.3724 | 2.4028 | 2.44 | 2.4833 | 1.7856 | 2.1526 | 2.1762 | 2.2086 | 1.7856 | 2.4006 | 2.7098 | 2.7311 | 2.7594 | 2.9251
2021-11-27 18:00 | 2.6102 | 2.8672 | 2.8994 | 2.9388 | 2.9847 | 2.0196 | 2.4316 | 2.4567 | 2.4909 | 2.0196 | 2.8579 | 3.2205 | 3.243 | 3.273 | 3.4659
2021-11-27 19:00 | 2.5911 | 2.8541 | 2.8901 | 2.934 | 2.9853 | 2.0196 | 2.4369 | 2.465 | 2.5032 | 2.0196 | 3.2961 | 3.7126 | 3.7378 | 3.7713 | 3.9925
2021-11-27 20:00 | 2.5911 | 2.8639 | 2.9048 | 2.9549 | 3.0133 | 2.1148 | 2.5566 | 2.5885 | 2.632 | 2.1148 | 3.7152 | 4.1853 | 4.214 | 4.2521 | 4.5019
2021-11-27 21:00 | 2.5911 | 2.8735 | 2.9194 | 2.9755 | 3.041 | 2.0767 | 2.5186 | 2.5543 | 2.6032 | 2.0767 | 2.8579 | 3.2394 | 3.2716 | 3.3143 | 3.5224
2021-11-27 22:00 | 2.4578 | 2.7319 | 2.7786 | 2.8357 | 2.9024 | 1.8862 | 2.2947 | 2.3311 | 2.3808 | 1.8862 | 2.5721 | 2.923 | 2.9557 | 2.9992 | 3.1926
2021-11-27 23:00 | 2.2673 | 2.5212 | 2.5649 | 2.6183 | 2.6806 | 1.776 | 2.1601 | 2.1941 | 2.2406 | 1.776 | 2.2673 | 2.58 | 2.6106 | 2.6512 | 2.8245
2021-11-28 | 2.1148 | 2.3491 | 2.3884 | 2.4365 | 2.4927 | 1.4595 | 1.7801 | 1.8108 | 1.8527 | 1.4595 | 2.0196 | 2.2988 | 2.3264 | 2.363 | 2.5178
2021-11-28 01:00 | 1.9624 | 2.1759 | 2.2104 | 2.2526 | 2.3018 | 1.3169 | 1.6048 | 1.6317 | 1.6685 | 1.3169 | 1.6766 | 1.911 | 1.9352 | 1.9673 | 2.0979
2021-11-28 02:00 | 1.9815 | 2.1867 | 2.2164 | 2.2526 | 2.2949 | 1.1767 | 1.4322 | 1.4553 | 1.4869 | 1.1767 | 1.6385 | 1.8619 | 1.8826 | 1.9102 | 2.0333
2021-11-28 03:00 | 1.9216 | 2.1103 | 2.1338 | 2.1625 | 2.1959 | 1.1432 | 1.3838 | 1.4021 | 1.4271 | 1.1432 | 1.448 | 1.6416 | 1.658 | 1.6799 | 1.7856
2021-11-28 04:00 | 1.9624 | 2.1424 | 2.1598 | 2.1811 | 2.2059 | 1.1432 | 1.3752 | 1.3888 | 1.4073 | 1.1432 | 1.467 | 1.6544 | 1.6666 | 1.6828 | 1.7828
2021-11-28 05:00 | 1.9815 | 2.1528 | 2.165 | 2.18 | 2.1975 | 1.1813 | 1.4129 | 1.4225 | 1.4355 | 1.1813 | 1.5623 | 1.7531 | 1.7617 | 1.7731 | 1.8727
2021-11-28 06:00 | 1.9243 | 2.0874 | 2.0976 | 2.1102 | 2.1248 | 1.301 | 1.5515 | 1.5594 | 1.5703 | 1.301 | 1.7528 | 1.962 | 1.9692 | 1.9787 | 2.0865
2021-11-28 07:00 | 1.7719 | 1.927 | 1.9389 | 1.9535 | 1.9706 | 1.3146 | 1.57 | 1.5793 | 1.592 | 1.3146 | 1.4861 | 1.668 | 1.6764 | 1.6875 | 1.7824
2021-11-28 08:00 | 1.7909 | 1.9565 | 1.9731 | 1.9934 | 2.0171 | 1.3627 | 1.6334 | 1.6463 | 1.6639 | 1.3627 | 1.81 | 2.0344 | 2.046 | 2.0614 | 2.1794
2021-11-28 09:00 | 1.8481 | 2.0313 | 2.0547 | 2.0833 | 2.1167 | 1.448 | 1.7439 | 1.7621 | 1.787 | 1.448 | 1.6385 | 1.8533 | 1.8697 | 1.8914 | 2.0076
2021-11-28 10:00 | 1.829 | 2.0251 | 2.0557 | 2.0933 | 2.1371 | 1.448 | 1.7542 | 1.7781 | 1.8108 | 1.448 | 1.5433 | 1.7575 | 1.779 | 1.8075 | 1.9265
2021-11-28 11:00 | 1.9243 | 2.1384 | 2.1746 | 2.219 | 2.2708 | 1.4099 | 1.7171 | 1.7454 | 1.7841 | 1.4099 | 1.4099 | 1.617 | 1.6424 | 1.6762 | 1.7941
2021-11-28 12:00 | 1.7954 | 2.0042 | 2.0427 | 2.0898 | 2.1447 | 1.3968 | 1.7049 | 1.7349 | 1.7759 | 1.3968 | 1.3146 | 1.5143 | 1.5412 | 1.577 | 1.6922
2021-11-28 13:00 | 1.6766 | 1.8755 | 1.9135 | 1.9599 | 2.0141 | 1.3146 | 1.607 | 1.6366 | 1.677 | 1.3146 | 1.2575 | 1.45 | 1.4766 | 1.5119 | 1.6233
2021-11-28 14:00 | 1.6766 | 1.8706 | 1.906 | 1.9493 | 1.9998 | 1.2956 | 1.5809 | 1.6085 | 1.6462 | 1.2956 | 1.2575 | 1.4465 | 1.4713 | 1.5042 | 1.6128
2021-11-28 15:00 | 1.5433 | 1.7219 | 1.7545 | 1.7945 | 1.841 | 1.1529 | 1.4084 | 1.4338 | 1.4686 | 1.1529 | 1.2003 | 1.3791 | 1.402 | 1.4324 | 1.5347
2021-11-28 16:00 | 1.7338 | 1.923 | 1.9538 | 1.9915 | 2.0354 | 1.3146 | 1.5968 | 1.6209 | 1.6537 | 1.3146 | 1.1432 | 1.3131 | 1.3346 | 1.3633 | 1.4604
2021-11-28 17:00 | 1.8481 | 2.0449 | 2.0753 | 2.1125 | 2.1558 | 1.4801 | 1.7917 | 1.8153 | 1.8477 | 1.4801 | 1.6766 | 1.9053 | 1.9265 | 1.9548 | 2.0808
2021-11-28 18:00 | 2.3435 | 2.5807 | 2.6128 | 2.6522 | 2.6981 | 1.8672 | 2.2515 | 2.2766 | 2.3109 | 1.8672 | 2.191 | 2.4794 | 2.502 | 2.5319 | 2.6882
2021-11-28 19:00 | 2.4578 | 2.7108 | 2.7468 | 2.7908 | 2.842 | 2.0196 | 2.4369 | 2.465 | 2.5032 | 2.0196 | 2.7436 | 3.0986 | 3.1238 | 3.1573 | 3.3481
2021-11-28 20:00 | 2.6674 | 2.9458 | 2.9867 | 3.0367 | 3.0951 | 2.172 | 2.6241 | 2.656 | 2.6996 | 2.172 | 3.1246 | 3.529 | 3.5577 | 3.5958 | 3.8131
2021-11-28 21:00 | 2.6483 | 2.935 | 2.9808 | 3.0369 | 3.1024 | 2.0577 | 2.4961 | 2.5318 | 2.5807 | 2.0577 | 2.8198 | 3.1971 | 3.2292 | 3.2719 | 3.478
2021-11-28 22:00 | 2.4768 | 2.7524 | 2.799 | 2.8562 | 2.9228 | 1.8086 | 2.203 | 2.2395 | 2.2892 | 1.8086 | 2.4387 | 2.7748 | 2.8075 | 2.851 | 3.037
2021-11-28 23:00 | 2.191 | 2.4394 | 2.483 | 2.5364 | 2.5987 | 1.5051 | 1.8401 | 1.8741 | 1.9206 | 1.5051 | 2.1148 | 2.4107 | 2.4412 | 2.4819 | 2.6467
2021-11-29 | 1.9815 | 2.2058 | 2.2451 | 2.2932 | 2.3494 | 1.2956 | 1.5865 | 1.6171 | 1.659 | 1.2956 | 1.9243 | 2.1929 | 2.2205 | 2.2571 | 2.4067
2021-11-29 01:00 | 1.829 | 2.0326 | 2.0671 | 2.1093 | 2.1586 | 1.1534 | 1.4117 | 1.4386 | 1.4753 | 1.1534 | 1.5052 | 1.7205 | 1.7446 | 1.7768 | 1.8979
2021-11-29 02:00 | 1.7937 | 1.985 | 2.0147 | 2.0509 | 2.0932 | 1.086 | 1.3251 | 1.3482 | 1.3797 | 1.086 | 1.3718 | 1.5655 | 1.5862 | 1.6138 | 1.7222
2021-11-29 03:00 | 1.7909 | 1.97 | 1.9934 | 2.0221 | 2.0556 | 1.0777 | 1.3065 | 1.3248 | 1.3498 | 1.0777 | 1.4289 | 1.6204 | 1.6369 | 1.6587 | 1.7634
2021-11-29 04:00 | 1.846 | 2.0173 | 2.0347 | 2.056 | 2.0809 | 1.1539 | 1.3879 | 1.4015 | 1.42 | 1.1539 | 1.4861 | 1.6756 | 1.6878 | 1.704 | 1.8051
2021-11-29 05:00 | 1.9844 | 2.1559 | 2.1682 | 2.1832 | 2.2007 | 1.2899 | 1.5413 | 1.5508 | 1.5639 | 1.2899 | 1.6385 | 1.8378 | 1.8464 | 1.8578 | 1.9615
2021-11-29 06:00 | 2.1339 | 2.3126 | 2.3228 | 2.3353 | 2.3499 | 1.4418 | 1.7178 | 1.7258 | 1.7367 | 1.4418 | 1.9815 | 2.2161 | 2.2233 | 2.2328 | 2.3531
2021-11-29 07:00 | 2.3244 | 2.5206 | 2.5325 | 2.5471 | 2.5642 | 1.5623 | 1.8626 | 1.8719 | 1.8846 | 1.5623 | 2.1339 | 2.3878 | 2.3962 | 2.4073 | 2.5379
2021-11-29 08:00 | 2.0386 | 2.2226 | 2.2392 | 2.2595 | 2.2832 | 1.2983 | 1.5573 | 1.5702 | 1.5879 | 1.2983 | 1.3146 | 1.4839 | 1.4955 | 1.5109 | 1.6017
2021-11-29 09:00 | 1.8862 | 2.0722 | 2.0956 | 2.1243 | 2.1577 | 1.0228 | 1.2415 | 1.2598 | 1.2847 | 1.0228 | 0.97168 | 1.1122 | 1.1286 | 1.1504 | 1.2299
2021-11-29 10:00 | 1.3337 | 1.4929 | 1.5235 | 1.5611 | 1.6049 | 0.64779 | 0.80888 | 0.83281 | 0.86548 | 0.64779 | 1.4289 | 1.6305 | 1.652 | 1.6805 | 1.7932
2021-11-29 11:00 | 1.2765 | 1.4424 | 1.4787 | 1.5231 | 1.5748 | 0.53347 | 0.68178 | 0.71007 | 0.74869 | 0.53347 | 1.5242 | 1.7441 | 1.7695 | 1.8032 | 1.9274
2021-11-29 12:00 | 1.2765 | 1.4468 | 1.4852 | 1.5323 | 1.5873 | 0.51442 | 0.66243 | 0.69245 | 0.73343 | 0.51442 | 1.6957 | 1.9377 | 1.9647 | 2.0005 | 2.1366
2021-11-29 13:00 | 1.2575 | 1.4252 | 1.4632 | 1.5096 | 1.5638 | 0.51442 | 0.66167 | 0.69127 | 0.73168 | 0.51442 | 1.6195 | 1.8523 | 1.8789 | 1.9142 | 2.0455
2021-11-29 14:00 | 1.2765 | 1.4407 | 1.4761 | 1.5194 | 1.57 | 0.53347 | 0.68055 | 0.70817 | 0.74586 | 0.53347 | 1.9624 | 2.2298 | 2.2546 | 2.2876 | 2.4349
2021-11-29 15:00 | 1.6385 | 1.8242 | 1.8569 | 1.8968 | 1.9434 | 0.64779 | 0.81167 | 0.83713 | 0.87189 | 0.64779 | 1.9434 | 2.2048 | 2.2277 | 2.2581 | 2.4012
2021-11-29 16:00 | 2.0577 | 2.2709 | 2.3017 | 2.3395 | 2.3834 | 0.99073 | 1.2142 | 1.2382 | 1.271 | 0.99073 | 1.0669 | 1.2284 | 1.2499 | 1.2786 | 1.3716
2021-11-29 17:00 | 2.191 | 2.4134 | 2.4437 | 2.4809 | 2.5242 | 1.3718 | 1.6637 | 1.6874 | 1.7198 | 1.3718 | 1.1813 | 1.3548 | 1.3761 | 1.4043 | 1.5031
2021-11-29 18:00 | 2.4387 | 2.683 | 2.7152 | 2.7546 | 2.8005 | 1.7909 | 2.1615 | 2.1866 | 2.2208 | 1.7909 | 2.2101 | 2.5006 | 2.5231 | 2.5531 | 2.7104
2021-11-29 19:00 | 2.3816 | 2.629 | 2.6649 | 2.7089 | 2.7602 | 1.7909 | 2.1668 | 2.1949 | 2.2331 | 1.7909 | 2.3816 | 2.6964 | 2.7215 | 2.755 | 2.9259
2021-11-29 20:00 | 2.4578 | 2.7206 | 2.7615 | 2.8116 | 2.87 | 1.8672 | 2.2639 | 2.2959 | 2.3394 | 1.8672 | 2.4006 | 2.7245 | 2.7531 | 2.7912 | 2.9687
2021-11-29 21:00 | 2.389 | 2.6563 | 2.7022 | 2.7583 | 2.8238 | 1.7924 | 2.1827 | 2.2185 | 2.2673 | 1.7924 | 2.2291 | 2.5408 | 2.5729 | 2.6156 | 2.7892
2021-11-29 22:00 | 2.2863 | 2.5477 | 2.5944 | 2.6515 | 2.7181 | 1.5699 | 1.921 | 1.9575 | 2.0072 | 1.5699 | 2.172 | 2.4784 | 2.5111 | 2.5546 | 2.7259
2021-11-29 23:00 | 1.9101 | 2.1375 | 2.1812 | 2.2346 | 2.2969 | 1.3054 | 1.6042 | 1.6382 | 1.6847 | 1.3054 | 1.7909 | 2.0507 | 2.0813 | 2.1219 | 2.269
2021-11-30 | 1.7909 | 2.0011 | 2.0404 | 2.0886 | 2.1447 | 1.1364 | 1.3984 | 1.4291 | 1.471 | 1.1364 | 1.5623 | 1.7907 | 1.8182 | 1.8549 | 1.9845
2021-11-30 01:00 | 1.6766 | 1.8688 | 1.9033 | 1.9456 | 1.9948 | 1.076 | 1.3202 | 1.3471 | 1.3838 | 1.076 | 1.467 | 1.6781 | 1.7023 | 1.7344 | 1.8535
2021-11-30 02:00 | 1.6004 | 1.7774 | 1.807 | 1.8432 | 1.8855 | 0.99073 | 1.2125 | 1.2356 | 1.2672 | 0.99073 | 1.3718 | 1.5655 | 1.5862 | 1.6138 | 1.7222
2021-11-30 03:00 | 1.5814 | 1.7448 | 1.7683 | 1.797 | 1.8304 | 0.95774 | 1.1648 | 1.1831 | 1.208 | 0.95774 | 1.4289 | 1.6204 | 1.6369 | 1.6587 | 1.7634
2021-11-30 04:00 | 1.5814 | 1.733 | 1.7504 | 1.7717 | 1.7966 | 0.98098 | 1.1836 | 1.1972 | 1.2158 | 0.98098 | 1.3527 | 1.5274 | 1.5396 | 1.5558 | 1.6495
2021-11-30 05:00 | 1.6957 | 1.8457 | 1.858 | 1.873 | 1.8905 | 1.0663 | 1.2771 | 1.2866 | 1.2997 | 1.0663 | 1.3527 | 1.5202 | 1.5288 | 1.5402 | 1.6282
2021-11-30 06:00 | 1.7996 | 1.9534 | 1.9637 | 1.9762 | 1.9908 | 1.2575 | 1.5001 | 1.508 | 1.5189 | 1.2575 | 1.4289 | 1.6021 | 1.6093 | 1.6188 | 1.7087
2021-11-30 07:00 | 1.9434 | 2.1112 | 2.1231 | 2.1377 | 2.1548 | 1.3337 | 1.5925 | 1.6018 | 1.6145 | 1.3337 | 1.467 | 1.6468 | 1.6552 | 1.6663 | 1.7602
2021-11-30 08:00 | 1.81 | 1.977 | 1.9936 | 2.0139 | 2.0375 | 1.1432 | 1.374 | 1.387 | 1.4046 | 1.1432 | 0.99073 | 1.124 | 1.1356 | 1.151 | 1.2239
2021-11-30 09:00 | 1.5623 | 1.7243 | 1.7477 | 1.7763 | 1.8097 | 0.72968 | 0.89528 | 0.91353 | 0.93845 | 0.72968 | 1.1813 | 1.3451 | 1.3615 | 1.3833 | 1.4743
2021-11-30 10:00 | 1.4099 | 1.5748 | 1.6054 | 1.643 | 1.6868 | 0.55668 | 0.70125 | 0.72518 | 0.75785 | 0.55668 | 1.6195 | 1.8422 | 1.8637 | 1.8922 | 2.0154
2021-11-30 11:00 | 1.4099 | 1.5857 | 1.622 | 1.6663 | 1.7181 | 0.57158 | 0.7268 | 0.75509 | 0.79371 | 0.57158 | 1.6576 | 1.8923 | 1.9177 | 1.9514 | 2.0829
2021-11-30 12:00 | 2.2101 | 2.4497 | 2.4882 | 2.5353 | 2.5902 | 0.81926 | 1.0226 | 1.0526 | 1.0936 | 0.81926 | 1.5433 | 1.7683 | 1.7953 | 1.8311 | 1.9588
2021-11-30 13:00 | 2.191 | 2.4282 | 2.4662 | 2.5126 | 2.5668 | 0.97168 | 1.2019 | 1.2315 | 1.2719 | 0.97168 | 1.9434 | 2.2122 | 2.2388 | 2.2741 | 2.4232
2021-11-30 14:00 | 1.829 | 2.0343 | 2.0697 | 2.113 | 2.1636 | 0.92172 | 1.1392 | 1.1668 | 1.2045 | 0.92172 | 1.7338 | 1.9758 | 2.0006 | 2.0335 | 2.1682
2021-11-30 15:00 | 2.4113 | 2.6545 | 2.6871 | 2.727 | 2.7736 | 1.2296 | 1.499 | 1.5244 | 1.5592 | 1.2296 | 1.4861 | 1.6967 | 1.7196 | 1.7499 | 1.868
2021-11-30 16:00 | 2.4197 | 2.6599 | 2.6907 | 2.7284 | 2.7723 | 1.3146 | 1.5968 | 1.6209 | 1.6537 | 1.3146 | 1.3718 | 1.5671 | 1.5887 | 1.6174 | 1.7271
2021-11-30 17:00 | 2.3703 | 2.6059 | 2.6363 | 2.6735 | 2.7168 | 1.5519 | 1.8765 | 1.9002 | 1.9325 | 1.5519 | 1.829 | 2.0746 | 2.0959 | 2.1242 | 2.2585
2021-11-30 18:00 | 2.4578 | 2.7035 | 2.7357 | 2.775 | 2.821 | 1.7909 | 2.1615 | 2.1866 | 2.2208 | 1.7909 | 2.2291 | 2.5218 | 2.5443 | 2.5743 | 2.7326
2021-11-30 19:00 | 2.4551 | 2.708 | 2.7439 | 2.7879 | 2.8392 | 1.7909 | 2.1668 | 2.1949 | 2.2331 | 1.7909 | 2.172 | 2.4635 | 2.4886 | 2.5221 | 2.6815
2021-11-30 20:00 | 2.4578 | 2.7206 | 2.7615 | 2.8116 | 2.87 | 1.7719 | 2.1514 | 2.1833 | 2.2269 | 1.7719 | 2.2291 | 2.5339 | 2.5626 | 2.6007 | 2.7688
2021-11-30 21:00 | 2.4194 | 2.689 | 2.7349 | 2.791 | 2.8565 | 1.7338 | 2.1134 | 2.1492 | 2.198 | 1.7338 | 2.1529 | 2.4561 | 2.4882 | 2.5309 | 2.7003
2021-11-30 22:00 | 2.2291 | 2.4863 | 2.533 | 2.5901 | 2.6567 | 1.568 | 1.9188 | 1.9552 | 2.0049 | 1.568 | 2.0386 | 2.3302 | 2.3629 | 2.4064 | 2.5704
2021-11-30 23:00 | 1.9624 | 2.1937 | 2.2374 | 2.2908 | 2.3531 | 1.3264 | 1.629 | 1.6631 | 1.7096 | 1.3264 | 1.6766 | 1.9237 | 1.9543 | 1.9949 | 2.1357
2021-12-01 | 1.7744 | 1.9833 | 2.0227 | 2.0708 | 2.1269 | 1.1432 | 1.4064 | 1.4371 | 1.479 | 1.1432 | 1.5814 | 1.8118 | 1.8394 | 1.876 | 2.0067
2021-12-01 01:00 | 1.7147 | 1.9098 | 1.9443 | 1.9865 | 2.0358 | 1.0669 | 1.3095 | 1.3364 | 1.3732 | 1.0669 | 1.3908 | 1.5934 | 1.6176 | 1.6497 | 1.7646
2021-12-01 02:00 | 1.6385 | 1.8183 | 1.8479 | 1.8842 | 1.9264 | 0.97596 | 1.1951 | 1.2182 | 1.2497 | 0.97596 | 1.2575 | 1.4384 | 1.4592 | 1.4868 | 1.5889
2021-12-01 03:00 | 1.6004 | 1.7653 | 1.7887 | 1.8174 | 1.8509 | 0.93468 | 1.1375 | 1.1558 | 1.1808 | 0.93468 | 1.3718 | 1.5569 | 1.5733 | 1.5952 | 1.6967
2021-12-01 04:00 | 1.6118 | 1.7657 | 1.7831 | 1.8044 | 1.8293 | 0.97276 | 1.1739 | 1.1875 | 1.2061 | 0.97276 | 1.3337 | 1.5062 | 1.5184 | 1.5346 | 1.6273
2021-12-01 05:00 | 1.7147 | 1.8662 | 1.8785 | 1.8935 | 1.911 | 1.105 | 1.3229 | 1.3325 | 1.3455 | 1.105 | 1.3337 | 1.4991 | 1.5077 | 1.5191 | 1.606
2021-12-01 06:00 | 1.81 | 1.9646 | 1.9748 | 1.9873 | 2.0019 | 1.2194 | 1.4551 | 1.463 | 1.4739 | 1.2194 | 1.1622 | 1.3057 | 1.3129 | 1.3224 | 1.3977
2021-12-01 07:00 | 2.0958 | 2.275 | 2.2869 | 2.3015 | 2.3185 | 1.3527 | 1.615 | 1.6243 | 1.637 | 1.3527 | 1.1622 | 1.3081 | 1.3164 | 1.3275 | 1.4047
2021-12-01 08:00 | 1.8672 | 2.0384 | 2.055 | 2.0753 | 2.0989 | 1.105 | 1.329 | 1.342 | 1.3596 | 1.105 | 1.0479 | 1.1875 | 1.1991 | 1.2145 | 1.2906
2021-12-01 09:00 | 1.9624 | 2.1541 | 2.1775 | 2.2061 | 2.2395 | 1.0669 | 1.2937 | 1.312 | 1.3369 | 1.0669 | 1.0098 | 1.1546 | 1.171 | 1.1928 | 1.2743
2021-12-01 10:00 | 1.7719 | 1.9637 | 1.9943 | 2.0319 | 2.0757 | 0.78115 | 0.96644 | 0.99037 | 1.023 | 0.78115 | 1.2003 | 1.3764 | 1.3979 | 1.4264 | 1.5266
2021-12-01 11:00 | 1.467 | 1.6471 | 1.6834 | 1.7277 | 1.7795 | 0.53347 | 0.68178 | 0.71007 | 0.74869 | 0.53347 | 1.1622 | 1.3418 | 1.3672 | 1.401 | 1.5052
2021-12-01 12:00 | 2.1168 | 2.3495 | 2.388 | 2.4351 | 2.4901 | 1.2017 | 1.4743 | 1.5043 | 1.5453 | 1.2017 | 1.086 | 1.2602 | 1.2872 | 1.323 | 1.4255
2021-12-01 13:00 | 2.4959 | 2.7557 | 2.7937 | 2.8401 | 2.8943 | 1.3532 | 1.6526 | 1.6822 | 1.7226 | 1.3532 | 0.83831 | 0.98421 | 1.0108 | 1.0461 | 1.1344
2021-12-01 14:00 | 2.4645 | 2.717 | 2.7524 | 2.7958 | 2.8463 | 1.3718 | 1.6709 | 1.6985 | 1.7362 | 1.3718 | 0.93358 | 1.0865 | 1.1113 | 1.1443 | 1.235
2021-12-01 15:00 | 2.3244 | 2.5611 | 2.5937 | 2.6337 | 2.6803 | 1.0288 | 1.2618 | 1.2873 | 1.322 | 1.0288 | 0.95263 | 1.1039 | 1.1267 | 1.1571 | 1.2458
2021-12-01 16:00 | 2.4006 | 2.6394 | 2.6702 | 2.7079 | 2.7519 | 1.4206 | 1.7221 | 1.7461 | 1.7789 | 1.4206 | 1.2384 | 1.4189 | 1.4405 | 1.4692 | 1.5715
2021-12-01 17:00 | 2.4006 | 2.6385 | 2.6689 | 2.7061 | 2.7494 | 1.5242 | 1.8438 | 1.8675 | 1.8998 | 1.5242 | 1.6576 | 1.8841 | 1.9054 | 1.9336 | 2.0586
2021-12-01 18:00 | 2.3816 | 2.6216 | 2.6538 | 2.6932 | 2.7391 | 1.7528 | 2.1165 | 2.1416 | 2.1758 | 1.7528 | 1.9445 | 2.2054 | 2.228 | 2.2579 | 2.4006
2021-12-01 19:00 | 2.4006 | 2.6494 | 2.6854 | 2.7293 | 2.7806 | 1.7528 | 2.1218 | 2.1498 | 2.1881 | 1.7528 | 2.7436 | 3.0986 | 3.1238 | 3.1573 | 3.3481
2021-12-01 20:00 | 2.4768 | 2.7411 | 2.782 | 2.8321 | 2.8905 | 1.8481 | 2.2414 | 2.2734 | 2.3169 | 1.8481 | 2.7436 | 3.1056 | 3.1342 | 3.1723 | 3.3687
2021-12-01 21:00 | 2.4197 | 2.6893 | 2.7352 | 2.7913 | 2.8568 | 1.796 | 2.1869 | 2.2227 | 2.2715 | 1.796 | 2.4387 | 2.7736 | 2.8058 | 2.8485 | 3.0336
2021-12-01 22:00 | 2.1735 | 2.4265 | 2.4732 | 2.5303 | 2.5969 | 1.5623 | 1.912 | 1.9485 | 1.9982 | 1.5623 | 2.0767 | 2.3725 | 2.4052 | 2.4487 | 2.6148
2021-12-01 23:00 | 1.9656 | 2.1972 | 2.2408 | 2.2942 | 2.3565 | 1.3146 | 1.6151 | 1.6492 | 1.6956 | 1.3146 | 1.8481 | 2.1142 | 2.1448 | 2.1855 | 2.3356
2021-12-02 | 1.829 | 2.042 | 2.0814 | 2.1295 | 2.1856 | 1.1543 | 1.4196 | 1.4502 | 1.4921 | 1.1543 | 1.6385 | 1.8754 | 1.9029 | 1.9395 | 2.0734
2021-12-02 01:00 | 1.6385 | 1.8279 | 1.8624 | 1.9046 | 1.9539 | 1.0403 | 1.2781 | 1.305 | 1.3418 | 1.0403 | 1.3718 | 1.5723 | 1.5964 | 1.6286 | 1.7424
2021-12-02 02:00 | 1.6195 | 1.7978 | 1.8275 | 1.8637 | 1.906 | 0.97168 | 1.19 | 1.2131 | 1.2447 | 0.97168 | 1.3908 | 1.5866 | 1.6074 | 1.635 | 1.7444
2021-12-02 03:00 | 1.5623 | 1.7244 | 1.7478 | 1.7765 | 1.81 | 0.97168 | 1.1812 | 1.1995 | 1.2245 | 0.97168 | 1.4099 | 1.5993 | 1.6157 | 1.6375 | 1.7411
2021-12-02 04:00 | 1.5814 | 1.733 | 1.7504 | 1.7717 | 1.7966 | 0.95067 | 1.1478 | 1.1614 | 1.18 | 0.95067 | 1.3718 | 1.5485 | 1.5607 | 1.5769 | 1.6717
2021-12-02 05:00 | 1.6385 | 1.7843 | 1.7966 | 1.8116 | 1.8291 | 1.037 | 1.2425 | 1.252 | 1.2651 | 1.037 | 1.5052 | 1.6896 | 1.6982 | 1.7096 | 1.806
2021-12-02 06:00 | 1.7338 | 1.8827 | 1.8929 | 1.9055 | 1.9201 | 1.1722 | 1.3993 | 1.4073 | 1.4182 | 1.1722 | 1.6195 | 1.8138 | 1.821 | 1.8305 | 1.9309
2021-12-02 07:00 | 2.0958 | 2.275 | 2.2869 | 2.3015 | 2.3185 | 1.2575 | 1.5025 | 1.5118 | 1.5245 | 1.2575 | 1.7528 | 1.9644 | 1.9728 | 1.9839 | 2.0935
2021-12-02 08:00 | 1.7909 | 1.9565 | 1.9731 | 1.9934 | 2.0171 | 1.0479 | 1.2615 | 1.2744 | 1.2921 | 1.0479 | 1.1432 | 1.2933 | 1.3049 | 1.3204 | 1.4017
2021-12-02 09:00 | 1.6957 | 1.8675 | 1.8909 | 1.9196 | 1.953 | 0.7621 | 0.93358 | 0.95183 | 0.97675 | 0.7621 | 1.2956 | 1.4722 | 1.4886 | 1.5103 | 1.6076
2021-12-02 10:00 | 1.5623 | 1.7385 | 1.7692 | 1.8067 | 1.8505 | 0.64779 | 0.80888 | 0.83281 | 0.86548 | 0.64779 | 1.5052 | 1.7152 | 1.7366 | 1.7652 | 1.8821
2021-12-02 11:00 | 1.5052 | 1.688 | 1.7243 | 1.7687 | 1.8204 | 0.57158 | 0.7268 | 0.75509 | 0.79371 | 0.57158 | 1.2956 | 1.49 | 1.5154 | 1.5492 | 1.6608
2021-12-02 12:00 | 1.6195 | 1.8152 | 1.8537 | 1.9008 | 1.9557 | 0.55252 | 0.70745 | 0.73747 | 0.77845 | 0.55252 | 1.6766 | 1.9165 | 1.9435 | 1.9793 | 2.1143
2021-12-02 13:00 | 1.7147 | 1.9165 | 1.9544 | 2.0009 | 2.055 | 0.66684 | 0.84173 | 0.87133 | 0.91174 | 0.66684 | 0.91452 | 1.0689 | 1.0955 | 1.1308 | 1.2233
2021-12-02 14:00 | 2.172 | 2.4028 | 2.4382 | 2.4815 | 2.532 | 0.70494 | 0.88312 | 0.91074 | 0.94844 | 0.70494 | 0.99073 | 1.1501 | 1.1749 | 1.2078 | 1.3017
2021-12-02 15:00 | 2.5866 | 2.8427 | 2.8754 | 2.9153 | 2.9619 | 1.2973 | 1.579 | 1.6044 | 1.6392 | 1.2973 | 1.2003 | 1.3791 | 1.402 | 1.4324 | 1.5347
2021-12-02 16:00 | 2.7817 | 3.0488 | 3.0796 | 3.1173 | 3.1612 | 1.6957 | 2.047 | 2.071 | 2.1038 | 1.6957 | 1.2384 | 1.4189 | 1.4405 | 1.4692 | 1.5715
2021-12-02 17:00 | 2.7817 | 3.0479 | 3.0783 | 3.1154 | 3.1588 | 1.7528 | 2.1139 | 2.1376 | 2.1699 | 1.7528 | 1.5433 | 1.7571 | 1.7783 | 1.8066 | 1.9252
2021-12-02 18:00 | 2.5149 | 2.7649 | 2.7971 | 2.8364 | 2.8824 | 1.7719 | 2.139 | 2.1641 | 2.1983 | 1.7719 | 2.0958 | 2.3736 | 2.3961 | 2.4261 | 2.5771
2021-12-02 19:00 | 2.4387 | 2.6904 | 2.7263 | 2.7703 | 2.8216 | 1.7338 | 2.0993 | 2.1273 | 2.1656 | 1.7338 | 2.4959 | 2.8234 | 2.8486 | 2.882 | 3.0592
2021-12-02 20:00 | 2.5149 | 2.782 | 2.8229 | 2.873 | 2.9314 | 1.8104 | 2.1969 | 2.2289 | 2.2724 | 1.8104 | 2.6483 | 2.9997 | 3.0284 | 3.0664 | 3.2576
2021-12-02 21:00 | 2.4231 | 2.693 | 2.7389 | 2.795 | 2.8605 | 1.829 | 2.226 | 2.2617 | 2.3106 | 1.829 | 2.2101 | 2.5196 | 2.5517 | 2.5944 | 2.7669
2021-12-02 22:00 | 2.2351 | 2.4926 | 2.5393 | 2.5965 | 2.6631 | 1.6195 | 1.9796 | 2.016 | 2.0657 | 1.6195 | 1.9815 | 2.2667 | 2.2994 | 2.3428 | 2.5038
2021-12-02 23:00 | 2.0619 | 2.3006 | 2.3443 | 2.3977 | 2.46 | 1.3425 | 1.6481 | 1.6821 | 1.7286 | 1.3425 | 2.0196 | 2.3048 | 2.3354 | 2.376 | 2.5356
2021-12-03 | 1.8672 | 2.083 | 2.1223 | 2.1704 | 2.2266 | 1.1877 | 1.4591 | 1.4898 | 1.5316 | 1.1877 | 1.3908 | 1.6001 | 1.6277 | 1.6643 | 1.7846
2021-12-03 01:00 | 1.6957 | 1.8893 | 1.9238 | 1.966 | 2.0153 | 1.071 | 1.3144 | 1.3413 | 1.378 | 1.071 | 1.2765 | 1.4664 | 1.4906 | 1.5227 | 1.6313
2021-12-03 02:00 | 1.6576 | 1.8388 | 1.8684 | 1.9046 | 1.9469 | 0.99426 | 1.2167 | 1.2398 | 1.2713 | 0.99426 | 1.3527 | 1.5443 | 1.5651 | 1.5926 | 1.7
2021-12-03 03:00 | 1.6576 | 1.8267 | 1.8501 | 1.8788 | 1.9123 | 0.97989 | 1.1909 | 1.2092 | 1.2342 | 0.97989 | 1.3527 | 1.5357 | 1.5522 | 1.574 | 1.6745
2021-12-03 04:00 | 1.6385 | 1.7944 | 1.8118 | 1.8331 | 1.858 | 0.97168 | 1.1727 | 1.1862 | 1.2048 | 0.97168 | 1.3146 | 1.485 | 1.4972 | 1.5134 | 1.6051
2021-12-03 05:00 | 1.7125 | 1.8638 | 1.8761 | 1.8911 | 1.9086 | 1.0669 | 1.2779 | 1.2874 | 1.3005 | 1.0669 | 1.5433 | 1.732 | 1.7405 | 1.752 | 1.8504
2021-12-03 06:00 | 1.9053 | 2.0669 | 2.0772 | 2.0897 | 2.1043 | 1.2765 | 1.5226 | 1.5306 | 1.5415 | 1.2765 | 1.5242 | 1.708 | 1.7151 | 1.7247 | 1.8198
2021-12-03 07:00 | 1.9243 | 2.0907 | 2.1027 | 2.1173 | 2.1343 | 1.2956 | 1.5475 | 1.5568 | 1.5695 | 1.2956 | 1.7338 | 1.9432 | 1.9516 | 1.9627 | 2.0713
2021-12-03 08:00 | 1.9624 | 2.1408 | 2.1573 | 2.1776 | 2.2013 | 1.1622 | 1.3966 | 1.4095 | 1.4271 | 1.1622 | 1.1622 | 1.3145 | 1.3261 | 1.3416 | 1.4239
2021-12-03 09:00 | 1.9243 | 2.1132 | 2.1366 | 2.1652 | 2.1986 | 0.87642 | 1.0686 | 1.0869 | 1.1118 | 0.87642 | 1.0669 | 1.2181 | 1.2345 | 1.2563 | 1.341
2021-12-03 10:00 | 1.8481 | 2.0455 | 2.0762 | 2.1138 | 2.1575 | 0.7621 | 0.94393 | 0.96786 | 1.0005 | 0.7621 | 1.829 | 2.0751 | 2.0966 | 2.1251 | 2.2598
2021-12-03 11:00 | 1.8481 | 2.0565 | 2.0927 | 2.1371 | 2.1889 | 0.62873 | 0.79432 | 0.82261 | 0.86123 | 0.62873 | 1.7338 | 1.977 | 2.0024 | 2.0361 | 2.1718
2021-12-03 12:00 | 1.8481 | 2.0608 | 2.0993 | 2.1464 | 2.2013 | 0.67286 | 0.8496 | 0.87962 | 0.9206 | 0.67286 | 2.0767 | 2.3611 | 2.3881 | 2.4239 | 2.5809
2021-12-03 13:00 | 2.2863 | 2.5306 | 2.5685 | 2.6149 | 2.6691 | 0.87642 | 1.0893 | 1.1189 | 1.1593 | 0.87642 | 1.7719 | 2.0216 | 2.0482 | 2.0836 | 2.2232
2021-12-03 14:00 | 2.4578 | 2.7098 | 2.7452 | 2.7885 | 2.839 | 1.3337 | 1.6259 | 1.6535 | 1.6912 | 1.3337 | 1.6957 | 1.9334 | 1.9582 | 1.9912 | 2.1238
2021-12-03 15:00 | 3.1246 | 3.4208 | 3.4534 | 3.4934 | 3.54 | 1.6004 | 1.9371 | 1.9625 | 1.9973 | 1.6004 | 1.3718 | 1.5697 | 1.5925 | 1.6229 | 1.7347
2021-12-03 16:00 | 2.6864 | 2.9464 | 2.9772 | 3.0149 | 3.0589 | 1.848 | 2.2269 | 2.2509 | 2.2837 | 1.848 | 1.4289 | 1.6306 | 1.6522 | 1.6809 | 1.7937
2021-12-03 17:00 | 2.6102 | 2.8637 | 2.8941 | 2.9312 | 2.9746 | 1.9053 | 2.294 | 2.3176 | 2.35 | 1.9053 | 1.6385 | 1.8629 | 1.8842 | 1.9125 | 2.0363
2021-12-03 18:00 | 2.4197 | 2.6625 | 2.6947 | 2.7341 | 2.78 | 1.7719 | 2.139 | 2.1641 | 2.1983 | 1.7719 | 2.0386 | 2.3101 | 2.3326 | 2.3625 | 2.5104
2021-12-03 19:00 | 2.4197 | 2.6699 | 2.7058 | 2.7498 | 2.8011 | 1.6957 | 2.0543 | 2.0823 | 2.1206 | 1.6957 | 2.1148 | 2.4 | 2.4251 | 2.4586 | 2.6148
2021-12-03 20:00 | 2.4006 | 2.6592 | 2.7001 | 2.7502 | 2.8086 | 1.7147 | 2.0839 | 2.1158 | 2.1594 | 1.7147 | 2.4197 | 2.7456 | 2.7743 | 2.8124 | 2.9909
2021-12-03 21:00 | 2.2691 | 2.5275 | 2.5734 | 2.6295 | 2.695 | 1.6701 | 2.0382 | 2.074 | 2.1228 | 1.6701 | 2.3054 | 2.6254 | 2.6576 | 2.7003 | 2.878
2021-12-03 22:00 | 2.1618 | 2.4139 | 2.4606 | 2.5177 | 2.5844 | 1.5242 | 1.867 | 1.9034 | 1.9532 | 1.5242 | 2.0196 | 2.309 | 2.3417 | 2.3852 | 2.5482
2021-12-03 23:00 | 2.0218 | 2.2576 | 2.3012 | 2.3547 | 2.4169 | 1.3337 | 1.6376 | 1.6717 | 1.7181 | 1.3337 | 1.6766 | 1.9237 | 1.9543 | 1.9949 | 2.1357
2021-12-04 | 1.9243 | 2.1444 | 2.1837 | 2.2318 | 2.288 | 1.1813 | 1.4514 | 1.4821 | 1.524 | 1.1813 | 1.7147 | 1.9601 | 1.9876 | 2.0242 | 2.1623
2021-12-04 01:00 | 1.81 | 2.0121 | 2.0466 | 2.0888 | 2.1381 | 1.105 | 1.3545 | 1.3814 | 1.4182 | 1.105 | 1.2575 | 1.4452 | 1.4694 | 1.5015 | 1.6091
2021-12-04 02:00 | 1.6957 | 1.8797 | 1.9093 | 1.9456 | 1.9879 | 1.0288 | 1.2575 | 1.2806 | 1.3122 | 1.0288 | 1.3337 | 1.5231 | 1.5439 | 1.5715 | 1.6777
2021-12-04 03:00 | 1.6957 | 1.8676 | 1.8911 | 1.9198 | 1.9532 | 0.97168 | 1.1812 | 1.1995 | 1.2245 | 0.97168 | 1.1622 | 1.324 | 1.3405 | 1.3623 | 1.4523
2021-12-04 04:00 | 1.6195 | 1.7739 | 1.7913 | 1.8127 | 1.8375 | 0.97168 | 1.1727 | 1.1862 | 1.2048 | 0.97168 | 1.3146 | 1.485 | 1.4972 | 1.5134 | 1.6051
2021-12-04 05:00 | 1.6957 | 1.8457 | 1.858 | 1.873 | 1.8905 | 1.03 | 1.2342 | 1.2438 | 1.2568 | 1.03 | 1.3908 | 1.5626 | 1.5712 | 1.5826 | 1.6727
2021-12-04 06:00 | 1.6385 | 1.7804 | 1.7906 | 1.8031 | 1.8177 | 1.0669 | 1.275 | 1.283 | 1.2939 | 1.0669 | 1.5433 | 1.7291 | 1.7363 | 1.7458 | 1.8421
2021-12-04 07:00 | 1.5831 | 1.7241 | 1.7361 | 1.7507 | 1.7677 | 1.0669 | 1.2774 | 1.2867 | 1.2994 | 1.0669 | 2.0577 | 2.3032 | 2.3115 | 2.3226 | 2.449
2021-12-04 08:00 | 1.6004 | 1.7518 | 1.7684 | 1.7887 | 1.8124 | 1.0669 | 1.284 | 1.2969 | 1.3146 | 1.0669 | 1.5814 | 1.7803 | 1.7919 | 1.8073 | 1.9127
2021-12-04 09:00 | 1.5052 | 1.6629 | 1.6862 | 1.7149 | 1.7483 | 0.89547 | 1.0911 | 1.1094 | 1.1343 | 0.89547 | 1.7338 | 1.9591 | 1.9755 | 1.9973 | 2.1187
2021-12-04 10:00 | 1.2003 | 1.3496 | 1.3803 | 1.4178 | 1.4616 | 0.64779 | 0.80888 | 0.83281 | 0.86548 | 0.64779 | 1.448 | 1.6516 | 1.6731 | 1.7017 | 1.8154
2021-12-04 11:00 | 1.1813 | 1.3401 | 1.3763 | 1.4207 | 1.4725 | 0.58319 | 0.74052 | 0.76881 | 0.80743 | 0.58319 | 1.5242 | 1.7441 | 1.7695 | 1.8032 | 1.9274
2021-12-04 12:00 | 1.1241 | 1.283 | 1.3215 | 1.3686 | 1.4235 | 0.59063 | 0.75246 | 0.78248 | 0.82346 | 0.59063 | 1.2956 | 1.4931 | 1.52 | 1.5559 | 1.6699
2021-12-04 13:00 | 1.6576 | 1.8551 | 1.893 | 1.9395 | 1.9936 | 0.97168 | 1.2019 | 1.2315 | 1.2719 | 0.97168 | 1.6576 | 1.8946 | 1.9212 | 1.9565 | 2.0899
2021-12-04 14:00 | 1.6385 | 1.8296 | 1.865 | 1.9084 | 1.9589 | 1.0479 | 1.2883 | 1.3159 | 1.3536 | 1.0479 | 1.3908 | 1.5947 | 1.6195 | 1.6524 | 1.7683
2021-12-04 15:00 | 1.8184 | 2.0175 | 2.0501 | 2.0901 | 2.1367 | 0.91452 | 1.1268 | 1.1522 | 1.187 | 0.91452 | 1.3908 | 1.5908 | 1.6137 | 1.6441 | 1.7569
2021-12-04 16:00 | 2.2863 | 2.5166 | 2.5474 | 2.5851 | 2.629 | 1.6576 | 2.002 | 2.026 | 2.0588 | 1.6576 | 2.2101 | 2.4987 | 2.5203 | 2.549 | 2.7047
2021-12-04 17:00 | 2.1148 | 2.3315 | 2.3619 | 2.399 | 2.4424 | 1.5623 | 1.8888 | 1.9125 | 1.9448 | 1.5623 | 1.7528 | 1.99 | 2.0112 | 2.0395 | 2.1697
2021-12-04 18:00 | 2.0196 | 2.2327 | 2.2649 | 2.3042 | 2.3502 | 1.6004 | 1.9364 | 1.9615 | 1.9958 | 1.6004 | 1.7338 | 1.9713 | 1.9938 | 2.0238 | 2.1549
2021-12-04 19:00 | 2.172 | 2.4038 | 2.4397 | 2.4837 | 2.535 | 1.6576 | 2.0093 | 2.0373 | 2.0756 | 1.6576 | 2.2291 | 2.527 | 2.5522 | 2.5856 | 2.7482
2021-12-04 20:00 | 2.2482 | 2.4954 | 2.5363 | 2.5864 | 2.6448 | 1.6576 | 2.0164 | 2.0483 | 2.0919 | 1.6576 | 2.3435 | 2.6609 | 2.6896 | 2.7277 | 2.9021
2021-12-04 21:00 | 2.172 | 2.4232 | 2.4691 | 2.5252 | 2.5907 | 1.6766 | 2.0459 | 2.0817 | 2.1305 | 1.6766 | 2.0577 | 2.3502 | 2.3823 | 2.425 | 2.5892
2021-12-04 22:00 | 2.0958 | 2.343 | 2.3897 | 2.4468 | 2.5135 | 1.5553 | 1.9038 | 1.9402 | 1.9899 | 1.5553 | 1.8862 | 2.1608 | 2.1935 | 2.237 | 2.3927
2021-12-04 23:00 | 1.9624 | 2.1937 | 2.2374 | 2.2908 | 2.3531 | 1.3718 | 1.6826 | 1.7167 | 1.7632 | 1.3718 | 1.6576 | 1.9025 | 1.9331 | 1.9737 | 2.1134
2021-12-05 | 1.8672 | 2.083 | 2.1223 | 2.1704 | 2.2266 | 1.1748 | 1.4438 | 1.4744 | 1.5163 | 1.1748 | 1.5814 | 1.8118 | 1.8394 | 1.876 | 2.0067
2021-12-05 01:00 | 1.7338 | 1.9302 | 1.9647 | 2.007 | 2.0562 | 1.0561 | 1.2966 | 1.3236 | 1.3603 | 1.0561 | 1.3908 | 1.5934 | 1.6176 | 1.6497 | 1.7646
2021-12-05 02:00 | 1.6385 | 1.8183 | 1.8479 | 1.8842 | 1.9264 | 0.99073 | 1.2125 | 1.2356 | 1.2672 | 0.99073 | 1.2575 | 1.4384 | 1.4592 | 1.4868 | 1.5889
2021-12-05 03:00 | 1.6193 | 1.7856 | 1.809 | 1.8377 | 1.8712 | 0.97416 | 1.1842 | 1.2025 | 1.2274 | 0.97416 | 1.3718 | 1.5569 | 1.5733 | 1.5952 | 1.6967
2021-12-05 04:00 | 1.6195 | 1.7739 | 1.7913 | 1.8127 | 1.8375 | 0.99073 | 1.1952 | 1.2087 | 1.2273 | 0.99073 | 1.3337 | 1.5062 | 1.5184 | 1.5346 | 1.6273
2021-12-05 05:00 | 1.6385 | 1.7843 | 1.7966 | 1.8116 | 1.8291 | 1.0064 | 1.2063 | 1.2159 | 1.229 | 1.0064 | 1.3337 | 1.4991 | 1.5077 | 1.5191 | 1.606
2021-12-05 06:00 | 1.6004 | 1.7394 | 1.7497 | 1.7622 | 1.7768 | 1.0288 | 1.23 | 1.238 | 1.2489 | 1.0288 | 1.1622 | 1.3057 | 1.3129 | 1.3224 | 1.3977
2021-12-05 07:00 | 1.5623 | 1.7018 | 1.7138 | 1.7284 | 1.7454 | 1.0761 | 1.2883 | 1.2976 | 1.3103 | 1.0761 | 1.1622 | 1.3081 | 1.3164 | 1.3275 | 1.4047
2021-12-05 08:00 | 1.5814 | 1.7314 | 1.748 | 1.7682 | 1.7919 | 1.086 | 1.3065 | 1.3195 | 1.3371 | 1.086 | 1.0479 | 1.1875 | 1.1991 | 1.2145 | 1.2906
2021-12-05 09:00 | 1.448 | 1.6014 | 1.6248 | 1.6535 | 1.6869 | 1.0098 | 1.2262 | 1.2444 | 1.2694 | 1.0098 | 1.0098 | 1.1546 | 1.171 | 1.1928 | 1.2743
2021-12-05 10:00 | 1.4099 | 1.5748 | 1.6054 | 1.643 | 1.6868 | 1.0479 | 1.2815 | 1.3055 | 1.3381 | 1.0479 | 1.2003 | 1.3764 | 1.3979 | 1.4264 | 1.5266
2021-12-05 11:00 | 1.5242 | 1.7085 | 1.7448 | 1.7892 | 1.8409 | 0.92465 | 1.1439 | 1.1722 | 1.2108 | 0.92465 | 1.1622 | 1.3418 | 1.3672 | 1.401 | 1.5052
2021-12-05 12:00 | 1.448 | 1.631 | 1.6695 | 1.7166 | 1.7715 | 0.93358 | 1.1576 | 1.1876 | 1.2286 | 0.93358 | 1.086 | 1.2602 | 1.2872 | 1.323 | 1.4255
2021-12-05 13:00 | 1.4861 | 1.6709 | 1.7088 | 1.7552 | 1.8094 | 0.97168 | 1.2019 | 1.2315 | 1.2719 | 0.97168 | 0.83831 | 0.98421 | 1.0108 | 1.0461 | 1.1344
2021-12-05 14:00 | 1.5433 | 1.7273 | 1.7627 | 1.806 | 1.8565 | 1.0288 | 1.2658 | 1.2934 | 1.3311 | 1.0288 | 0.93358 | 1.0865 | 1.1113 | 1.1443 | 1.235
2021-12-05 15:00 | 1.656 | 1.843 | 1.8757 | 1.9156 | 1.9622 | 1.1622 | 1.4194 | 1.4448 | 1.4796 | 1.1622 | 0.95263 | 1.1039 | 1.1267 | 1.1571 | 1.2458
2021-12-05 16:00 | 1.6957 | 1.882 | 1.9128 | 1.9505 | 1.9945 | 1.2384 | 1.5068 | 1.5308 | 1.5636 | 1.2384 | 1.2384 | 1.4189 | 1.4405 | 1.4692 | 1.5715
2021-12-05 17:00 | 1.9824 | 2.1892 | 2.2196 | 2.2568 | 2.3001 | 1.5644 | 1.8912 | 1.9149 | 1.9473 | 1.5644 | 1.6576 | 1.8841 | 1.9054 | 1.9336 | 2.0586
2021-12-05 18:00 | 2.2101 | 2.4374 | 2.4696 | 2.5089 | 2.5549 | 1.7909 | 2.1615 | 2.1866 | 2.2208 | 1.7909 | 1.9445 | 2.2054 | 2.228 | 2.2579 | 2.4006
2021-12-05 19:00 | 2.3435 | 2.588 | 2.624 | 2.6679 | 2.7192 | 1.8102 | 2.1896 | 2.2176 | 2.2559 | 1.8102 | 2.7436 | 3.0986 | 3.1238 | 3.1573 | 3.3481
2021-12-05 20:00 | 2.5721 | 2.8434 | 2.8843 | 2.9344 | 2.9928 | 1.9053 | 2.309 | 2.3409 | 2.3845 | 1.9053 | 2.7436 | 3.1056 | 3.1342 | 3.1723 | 3.3687
2021-12-05 21:00 | 2.4197 | 2.6893 | 2.7352 | 2.7913 | 2.8568 | 1.81 | 2.2035 | 2.2392 | 2.2881 | 1.81 | 2.4387 | 2.7736 | 2.8058 | 2.8485 | 3.0336
2021-12-05 22:00 | 2.2673 | 2.5272 | 2.5739 | 2.631 | 2.6977 | 1.5622 | 1.9119 | 1.9483 | 1.9981 | 1.5622 | 2.0767 | 2.3725 | 2.4052 | 2.4487 | 2.6148
2021-12-05 23:00 | 2.0386 | 2.2756 | 2.3193 | 2.3727 | 2.435 | 1.448 | 1.7727 | 1.8067 | 1.8532 | 1.448 | 1.8481 | 2.1142 | 2.1448 | 2.1855 | 2.3356
2021-12-06 | 1.9053 | 2.1239 | 2.1632 | 2.2114 | 2.2675 | 1.2033 | 1.4774 | 1.5081 | 1.55 | 1.2033 | 1.6385 | 1.8754 | 1.9029 | 1.9395 | 2.0734
2021-12-06 01:00 | 1.81 | 2.0121 | 2.0466 | 2.0888 | 2.1381 | 1.091 | 1.3379 | 1.3649 | 1.4016 | 1.091 | 1.3718 | 1.5723 | 1.5964 | 1.6286 | 1.7424
2021-12-06 02:00 | 1.81 | 2.0025 | 2.0321 | 2.0684 | 2.1107 | 1.0098 | 1.235 | 1.2581 | 1.2897 | 1.0098 | 1.3908 | 1.5866 | 1.6074 | 1.635 | 1.7444
2021-12-06 03:00 | 1.7338 | 1.9086 | 1.932 | 1.9607 | 1.9942 | 0.99073 | 1.2037 | 1.222 | 1.247 | 0.99073 | 1.4099 | 1.5993 | 1.6157 | 1.6375 | 1.7411
2021-12-06 04:00 | 1.7719 | 1.9377 | 1.9551 | 1.9764 | 2.0013 | 1.0365 | 1.2492 | 1.2628 | 1.2814 | 1.0365 | 1.3718 | 1.5485 | 1.5607 | 1.5769 | 1.6717
2021-12-06 05:00 | 1.81 | 1.9686 | 1.9808 | 1.9958 | 2.0133 | 1.1813 | 1.4129 | 1.4225 | 1.4355 | 1.1813 | 1.5052 | 1.6896 | 1.6982 | 1.7096 | 1.806
2021-12-06 06:00 | 1.8827 | 2.0427 | 2.0529 | 2.0654 | 2.08 | 1.3146 | 1.5676 | 1.5756 | 1.5865 | 1.3146 | 1.6195 | 1.8138 | 1.821 | 1.8305 | 1.9309
2021-12-06 07:00 | 2.1148 | 2.2954 | 2.3074 | 2.322 | 2.339 | 1.4289 | 1.7051 | 1.7144 | 1.7271 | 1.4289 | 1.7528 | 1.9644 | 1.9728 | 1.9839 | 2.0935
2021-12-06 08:00 | 2.0767 | 2.2636 | 2.2802 | 2.3004 | 2.3241 | 1.3146 | 1.5766 | 1.5895 | 1.6072 | 1.3146 | 1.1432 | 1.2933 | 1.3049 | 1.3204 | 1.4017
2021-12-06 09:00 | 1.9434 | 2.1336 | 2.157 | 2.1857 | 2.2191 | 1.0669 | 1.2937 | 1.312 | 1.3369 | 1.0669 | 1.2956 | 1.4722 | 1.4886 | 1.5103 | 1.6076
2021-12-06 10:00 | 1.9053 | 2.1069 | 2.1376 | 2.1752 | 2.2189 | 1.086 | 1.3266 | 1.3505 | 1.3832 | 1.086 | 1.5052 | 1.7152 | 1.7366 | 1.7652 | 1.8821
2021-12-06 11:00 | 1.6617 | 1.8563 | 1.8925 | 1.9369 | 1.9887 | 1.086 | 1.3345 | 1.3628 | 1.4014 | 1.086 | 1.2956 | 1.49 | 1.5154 | 1.5492 | 1.6608
2021-12-06 12:00 | 1.8516 | 2.0646 | 2.1031 | 2.1502 | 2.2051 | 1.0479 | 1.2927 | 1.3227 | 1.3637 | 1.0479 | 1.6766 | 1.9165 | 1.9435 | 1.9793 | 2.1143
2021-12-06 13:00 | 2.0958 | 2.3259 | 2.3638 | 2.4103 | 2.4644 | 1.1582 | 1.4222 | 1.4518 | 1.4922 | 1.1582 | 0.91452 | 1.0689 | 1.0955 | 1.1308 | 1.2233
2021-12-06 14:00 | 2.0767 | 2.3004 | 2.3358 | 2.3791 | 2.4297 | 1.2003 | 1.4683 | 1.4959 | 1.5336 | 1.2003 | 0.99073 | 1.1501 | 1.1749 | 1.2078 | 1.3017
2021-12-06 15:00 | 2.0767 | 2.295 | 2.3276 | 2.3676 | 2.4142 | 1.2956 | 1.5769 | 1.6024 | 1.6372 | 1.2956 | 1.2003 | 1.3791 | 1.402 | 1.4324 | 1.5347
2021-12-06 16:00 | 2.0958 | 2.3119 | 2.3427 | 2.3804 | 2.4244 | 1.2765 | 1.5518 | 1.5759 | 1.6087 | 1.2765 | 1.2384 | 1.4189 | 1.4405 | 1.4692 | 1.5715
2021-12-06 17:00 | 2.0403 | 2.2514 | 2.2818 | 2.319 | 2.3623 | 1.5052 | 1.8213 | 1.845 | 1.8773 | 1.5052 | 1.5433 | 1.7571 | 1.7783 | 1.8066 | 1.9252
2021-12-06 18:00 | 2.2482 | 2.4783 | 2.5105 | 2.5499 | 2.5958 | 1.7126 | 2.069 | 2.0941 | 2.1284 | 1.7126 | 2.0958 | 2.3736 | 2.3961 | 2.4261 | 2.5771
2021-12-06 19:00 | 2.3625 | 2.6085 | 2.6444 | 2.6884 | 2.7397 | 1.7719 | 2.1443 | 2.1724 | 2.2106 | 1.7719 | 2.4959 | 2.8234 | 2.8486 | 2.882 | 3.0592
2021-12-06 20:00 | 2.3625 | 2.6182 | 2.6592 | 2.7092 | 2.7676 | 1.7719 | 2.1514 | 2.1833 | 2.2269 | 1.7719 | 2.6483 | 2.9997 | 3.0284 | 3.0664 | 3.2576
2021-12-06 21:00 | 2.2876 | 2.5474 | 2.5933 | 2.6494 | 2.7149 | 1.7528 | 2.1359 | 2.1717 | 2.2205 | 1.7528 | 2.2101 | 2.5196 | 2.5517 | 2.5944 | 2.7669
2021-12-06 22:00 | 2.1507 | 2.4019 | 2.4486 | 2.5058 | 2.5724 | 1.5553 | 1.9038 | 1.9402 | 1.9899 | 1.5553 | 1.9815 | 2.2667 | 2.2994 | 2.3428 | 2.5038
2021-12-06 23:00 | 2.0196 | 2.2552 | 2.2988 | 2.3522 | 2.4145 | 1.346 | 1.6522 | 1.6862 | 1.7327 | 1.346 | 2.0196 | 2.3048 | 2.3354 | 2.376 | 2.5356
2021-12-07 | 1.7719 | 1.9806 | 2.0199 | 2.0681 | 2.1242 | 1.1621 | 1.4287 | 1.4594 | 1.5013 | 1.1621 | 1.3908 | 1.6001 | 1.6277 | 1.6643 | 1.7846
2021-12-07 01:00 | 1.6195 | 1.8074 | 1.8419 | 1.8842 | 1.9334 | 1.0725 | 1.3161 | 1.343 | 1.3798 | 1.0725 | 1.2765 | 1.4664 | 1.4906 | 1.5227 | 1.6313
2021-12-07 02:00 | 1.6576 | 1.8388 | 1.8684 | 1.9046 | 1.9469 | 1.0012 | 1.2249 | 1.248 | 1.2795 | 1.0012 | 1.3527 | 1.5443 | 1.5651 | 1.5926 | 1.7
2021-12-07 03:00 | 1.5623 | 1.7244 | 1.7478 | 1.7765 | 1.81 | 0.99073 | 1.2037 | 1.222 | 1.247 | 0.99073 | 1.3527 | 1.5357 | 1.5522 | 1.574 | 1.6745
2021-12-07 04:00 | 1.5814 | 1.733 | 1.7504 | 1.7717 | 1.7966 | 1.0309 | 1.2426 | 1.2561 | 1.2747 | 1.0309 | 1.3146 | 1.485 | 1.4972 | 1.5134 | 1.6051
2021-12-07 05:00 | 1.6957 | 1.8457 | 1.858 | 1.873 | 1.8905 | 1.12 | 1.3405 | 1.3501 | 1.3632 | 1.12 | 1.5433 | 1.732 | 1.7405 | 1.752 | 1.8504
2021-12-07 06:00 | 1.8214 | 1.9768 | 1.987 | 1.9996 | 2.0142 | 1.303 | 1.5539 | 1.5618 | 1.5727 | 1.303 | 1.5242 | 1.708 | 1.7151 | 1.7247 | 1.8198
2021-12-07 07:00 | 2.0386 | 2.2135 | 2.2255 | 2.2401 | 2.2571 | 1.4289 | 1.7051 | 1.7144 | 1.7271 | 1.4289 | 1.7338 | 1.9432 | 1.9516 | 1.9627 | 2.0713
2021-12-07 08:00 | 2.0005 | 2.1817 | 2.1983 | 2.2186 | 2.2422 | 1.2748 | 1.5295 | 1.5424 | 1.5601 | 1.2748 | 1.1622 | 1.3145 | 1.3261 | 1.3416 | 1.4239
2021-12-07 09:00 | 2.2482 | 2.4611 | 2.4845 | 2.5132 | 2.5466 | 1.1241 | 1.3612 | 1.3795 | 1.4044 | 1.1241 | 1.0669 | 1.2181 | 1.2345 | 1.2563 | 1.341
2021-12-07 10:00 | 1.6385 | 1.8204 | 1.8511 | 1.8886 | 1.9324 | 0.78115 | 0.96644 | 0.99037 | 1.023 | 0.78115 | 1.829 | 2.0751 | 2.0966 | 2.1251 | 2.2598
2021-12-07 11:00 | 1.7909 | 1.9951 | 2.0313 | 2.0757 | 2.1275 | 1.0098 | 1.2445 | 1.2728 | 1.3114 | 1.0098 | 1.7338 | 1.977 | 2.0024 | 2.0361 | 2.1718
2021-12-07 12:00 | 2.0005 | 2.2246 | 2.2631 | 2.3102 | 2.3651 | 1.0479 | 1.2927 | 1.3227 | 1.3637 | 1.0479 | 2.0767 | 2.3611 | 2.3881 | 2.4239 | 2.5809
2021-12-07 13:00 | 2.172 | 2.4077 | 2.4457 | 2.4921 | 2.5463 | 0.89547 | 1.1118 | 1.1414 | 1.1818 | 0.89547 | 1.7719 | 2.0216 | 2.0482 | 2.0836 | 2.2232
2021-12-07 14:00 | 2.3436 | 2.5872 | 2.6226 | 2.6659 | 2.7164 | 1.1685 | 1.4308 | 1.4584 | 1.4961 | 1.1685 | 1.6957 | 1.9334 | 1.9582 | 1.9912 | 2.1238
2021-12-07 15:00 | 2.6102 | 2.8681 | 2.9008 | 2.9407 | 2.9873 | 1.3337 | 1.622 | 1.6474 | 1.6822 | 1.3337 | 1.3718 | 1.5697 | 1.5925 | 1.6229 | 1.7347
2021-12-07 16:00 | 2.2238 | 2.4494 | 2.4802 | 2.5179 | 2.5619 | 1.2384 | 1.5068 | 1.5308 | 1.5636 | 1.2384 | 1.4289 | 1.6306 | 1.6522 | 1.6809 | 1.7937
2021-12-07 17:00 | 2.3435 | 2.5771 | 2.6075 | 2.6447 | 2.688 | 1.5433 | 1.8663 | 1.89 | 1.9223 | 1.5433 | 1.6385 | 1.8629 | 1.8842 | 1.9125 | 2.0363
2021-12-07 18:00 | 2.4197 | 2.6625 | 2.6947 | 2.7341 | 2.78 | 1.6766 | 2.0264 | 2.0515 | 2.0858 | 1.6766 | 2.0386 | 2.3101 | 2.3326 | 2.3625 | 2.5104
2021-12-07 19:00 | 2.3054 | 2.5471 | 2.583 | 2.627 | 2.6783 | 1.7338 | 2.0993 | 2.1273 | 2.1656 | 1.7338 | 2.1148 | 2.4 | 2.4251 | 2.4586 | 2.6148
2021-12-07 20:00 | 2.4387 | 2.7001 | 2.741 | 2.7911 | 2.8495 | 1.81 | 2.1964 | 2.2283 | 2.2719 | 1.81 | 2.4197 | 2.7456 | 2.7743 | 2.8124 | 2.9909
2021-12-07 21:00 | 2.3244 | 2.587 | 2.6328 | 2.689 | 2.7544 | 1.7528 | 2.1359 | 2.1717 | 2.2205 | 1.7528 | 2.3054 | 2.6254 | 2.6576 | 2.7003 | 2.878
2021-12-07 22:00 | 2.2482 | 2.5067 | 2.5534 | 2.6106 | 2.6772 | 1.5623 | 1.912 | 1.9485 | 1.9982 | 1.5623 | 2.0196 | 2.309 | 2.3417 | 2.3852 | 2.5482
2021-12-07 23:00 | 2.0444 | 2.2818 | 2.3254 | 2.3789 | 2.4411 | 1.3527 | 1.6601 | 1.6942 | 1.7406 | 1.3527 | 1.6766 | 1.9237 | 1.9543 | 1.9949 | 2.1357
2021-12-08 | 1.7759 | 1.985 | 2.0243 | 2.0724 | 2.1286 | 1.1365 | 1.3986 | 1.4293 | 1.4711 | 1.1365 | 1.7147 | 1.9601 | 1.9876 | 2.0242 | 2.1623
2021-12-08 01:00 | 1.6766 | 1.8688 | 1.9033 | 1.9456 | 1.9948 | 1.0477 | 1.2868 | 1.3137 | 1.3505 | 1.0477 | 1.2575 | 1.4452 | 1.4694 | 1.5015 | 1.6091
2021-12-08 02:00 | 1.6195 | 1.7978 | 1.8275 | 1.8637 | 1.906 | 1.011 | 1.2365 | 1.2596 | 1.2911 | 1.011 | 1.3337 | 1.5231 | 1.5439 | 1.5715 | 1.6777
2021-12-08 03:00 | 1.6004 | 1.7653 | 1.7887 | 1.8174 | 1.8509 | 0.97168 | 1.1812 | 1.1995 | 1.2245 | 0.97168 | 1.1622 | 1.324 | 1.3405 | 1.3623 | 1.4523
2021-12-08 04:00 | 1.6004 | 1.7535 | 1.7709 | 1.7922 | 1.817 | 0.98863 | 1.1927 | 1.2063 | 1.2248 | 0.98863 | 1.3146 | 1.485 | 1.4972 | 1.5134 | 1.6051
2021-12-08 05:00 | 1.7147 | 1.8662 | 1.8785 | 1.8935 | 1.911 | 1.0669 | 1.2779 | 1.2874 | 1.3005 | 1.0669 | 1.3908 | 1.5626 | 1.5712 | 1.5826 | 1.6727
2021-12-08 06:00 | 1.8481 | 2.0055 | 2.0158 | 2.0283 | 2.0429 | 1.2296 | 1.4671 | 1.4751 | 1.486 | 1.2296 | 1.5433 | 1.7291 | 1.7363 | 1.7458 | 1.8421
2021-12-08 07:00 | 2.1339 | 2.3159 | 2.3278 | 2.3424 | 2.3595 | 1.3908 | 1.66 | 1.6694 | 1.6821 | 1.3908 | 2.0577 | 2.3032 | 2.3115 | 2.3226 | 2.449
2021-12-08 08:00 | 2.3816 | 2.5911 | 2.6077 | 2.6279 | 2.6516 | 1.4861 | 1.7792 | 1.7921 | 1.8098 | 1.4861 | 1.5814 | 1.7803 | 1.7919 | 1.8073 | 1.9127
2021-12-08 09:00 | 2.5149 | 2.7477 | 2.7711 | 2.7997 | 2.8331 | 1.5814 | 1.9014 | 1.9197 | 1.9446 | 1.5814 | 1.7338 | 1.9591 | 1.9755 | 1.9973 | 2.1187
2021-12-08 10:00 | 2.4197 | 2.6596 | 2.6903 | 2.7278 | 2.7716 | 1.4289 | 1.7317 | 1.7556 | 1.7883 | 1.4289 | 1.448 | 1.6516 | 1.6731 | 1.7017 | 1.8154
2021-12-08 11:00 | 2.1529 | 2.384 | 2.4202 | 2.4646 | 2.5164 | 1.1622 | 1.4245 | 1.4528 | 1.4915 | 1.1622 | 1.5242 | 1.7441 | 1.7695 | 1.8032 | 1.9274
2021-12-08 12:00 | 2.4197 | 2.6749 | 2.7134 | 2.7605 | 2.8154 | 1.4289 | 1.7428 | 1.7728 | 1.8138 | 1.4289 | 1.2956 | 1.4931 | 1.52 | 1.5559 | 1.6699
2021-12-08 13:00 | 2.191 | 2.4282 | 2.4662 | 2.5126 | 2.5668 | 1.1813 | 1.4494 | 1.479 | 1.5195 | 1.1813 | 1.6576 | 1.8946 | 1.9212 | 1.9565 | 2.0899
2021-12-08 14:00 | 1.9815 | 2.1981 | 2.2335 | 2.2768 | 2.3273 | 1.1432 | 1.4008 | 1.4284 | 1.4661 | 1.1432 | 1.3908 | 1.5947 | 1.6195 | 1.6524 | 1.7683
2021-12-08 15:00 | 1.9053 | 2.1108 | 2.1434 | 2.1834 | 2.2299 | 1.0669 | 1.3068 | 1.3323 | 1.3671 | 1.0669 | 1.3908 | 1.5908 | 1.6137 | 1.6441 | 1.7569
2021-12-08 16:00 | 2.0005 | 2.2095 | 2.2403 | 2.278 | 2.322 | 1.2765 | 1.5518 | 1.5759 | 1.6087 | 1.2765 | 1.1813 | 1.3554 | 1.377 | 1.4057 | 1.5049
2021-12-08 17:00 | 1.9815 | 2.1882 | 2.2186 | 2.2557 | 2.2991 | 1.2575 | 1.5287 | 1.5524 | 1.5847 | 1.2575 | 1.2384 | 1.4183 | 1.4396 | 1.4678 | 1.5697
2021-12-08 18:00 | 2.3435 | 2.5807 | 2.6128 | 2.6522 | 2.6981 | 1.7528 | 2.1165 | 2.1416 | 2.1758 | 1.7528 | 2.2863 | 2.5853 | 2.6078 | 2.6378 | 2.7993
2021-12-08 19:00 | 2.217 | 2.4522 | 2.4881 | 2.5321 | 2.5834 | 1.7147 | 2.0768 | 2.1048 | 2.1431 | 1.7147 | 2.4578 | 2.7811 | 2.8062 | 2.8397 | 3.0148
2021-12-08 20:00 | 2.3625 | 2.6182 | 2.6592 | 2.7092 | 2.7676 | 1.7719 | 2.1514 | 2.1833 | 2.2269 | 1.7719 | 2.8198 | 3.1902 | 3.2189 | 3.257 | 3.4576
2021-12-08 21:00 | 2.4006 | 2.6689 | 2.7147 | 2.7708 | 2.8363 | 1.7208 | 2.0981 | 2.1339 | 2.1827 | 1.7208 | 2.3244 | 2.6466 | 2.6787 | 2.7214 | 2.9003
2021-12-08 22:00 | 2.1529 | 2.4044 | 2.4511 | 2.5082 | 2.5749 | 1.5449 | 1.8915 | 1.9279 | 1.9776 | 1.5449 | 1.9053 | 2.182 | 2.2147 | 2.2582 | 2.4149
2021-12-08 23:00 | 2.0005 | 2.2347 | 2.2783 | 2.3318 | 2.394 | 1.3619 | 1.6709 | 1.705 | 1.7514 | 1.3619 | 1.5814 | 1.8178 | 1.8484 | 1.889 | 2.0246
2021-12-09 | 1.8481 | 2.0625 | 2.1018 | 2.15 | 2.2061 | 1.1457 | 1.4094 | 1.4401 | 1.482 | 1.1457 | 1.5814 | 1.8118 | 1.8394 | 1.876 | 2.0067
2021-12-09 01:00 | 1.7338 | 1.9302 | 1.9647 | 2.007 | 2.0562 | 1.0479 | 1.287 | 1.3139 | 1.3507 | 1.0479 | 1.3718 | 1.5723 | 1.5964 | 1.6286 | 1.7424
2021-12-09 02:00 | 1.6195 | 1.7978 | 1.8275 | 1.8637 | 1.906 | 1.003 | 1.227 | 1.2501 | 1.2817 | 1.003 | 1.2003 | 1.3749 | 1.3957 | 1.4233 | 1.5222
2021-12-09 03:00 | 1.6195 | 1.7858 | 1.8092 | 1.8379 | 1.8714 | 0.97168 | 1.1812 | 1.1995 | 1.2245 | 0.97168 | 1.2956 | 1.4722 | 1.4887 | 1.5105 | 1.6078
2021-12-09 04:00 | 1.6385 | 1.7944 | 1.8118 | 1.8331 | 1.858 | 1.0288 | 1.2402 | 1.2538 | 1.2723 | 1.0288 | 1.3718 | 1.5485 | 1.5607 | 1.5769 | 1.6717
2021-12-09 05:00 | 1.7528 | 1.9071 | 1.9194 | 1.9344 | 1.9519 | 1.1241 | 1.3454 | 1.355 | 1.368 | 1.1241 | 1.4099 | 1.5838 | 1.5923 | 1.6038 | 1.6949
2021-12-09 06:00 | 1.8927 | 2.0535 | 2.0637 | 2.0762 | 2.0908 | 1.2793 | 1.5258 | 1.5338 | 1.5447 | 1.2793 | 1.5242 | 1.708 | 1.7151 | 1.7247 | 1.8198
2021-12-09 07:00 | 2.2673 | 2.4592 | 2.4711 | 2.4857 | 2.5028 | 1.5433 | 1.8401 | 1.8494 | 1.8621 | 1.5433 | 2.1148 | 2.3667 | 2.375 | 2.3861 | 2.5157
2021-12-09 08:00 | 2.2863 | 2.4887 | 2.5053 | 2.5256 | 2.5493 | 1.467 | 1.7567 | 1.7696 | 1.7873 | 1.467 | 1.7147 | 1.9285 | 1.9401 | 1.9555 | 2.0683
2021-12-09 09:00 | 2.191 | 2.3997 | 2.4231 | 2.4518 | 2.4852 | 1.3718 | 1.6538 | 1.6721 | 1.697 | 1.3718 | 1.5814 | 1.7897 | 1.8061 | 1.8279 | 1.9409
2021-12-09 10:00 | 2.0767 | 2.2912 | 2.3218 | 2.3594 | 2.4032 | 1.2575 | 1.5291 | 1.5531 | 1.5857 | 1.2575 | 1.0479 | 1.207 | 1.2285 | 1.2571 | 1.3488
2021-12-09 11:00 | 1.9053 | 2.1179 | 2.1541 | 2.1985 | 2.2503 | 0.93358 | 1.1544 | 1.1827 | 1.2214 | 0.93358 | 1.6576 | 1.8923 | 1.9177 | 1.9514 | 2.0829
2021-12-09 12:00 | 2.4387 | 2.6954 | 2.7338 | 2.7809 | 2.8359 | 1.3337 | 1.6303 | 1.6603 | 1.7013 | 1.3337 | 1.7909 | 2.0436 | 2.0705 | 2.1064 | 2.2476
2021-12-09 13:00 | 2.3282 | 2.5755 | 2.6135 | 2.6599 | 2.7141 | 1.205 | 1.4774 | 1.507 | 1.5474 | 1.205 | 1.8481 | 2.1063 | 2.1329 | 2.1682 | 2.3121
2021-12-09 14:00 | 1.7317 | 1.9297 | 1.9651 | 2.0084 | 2.0589 | 1.0092 | 1.2426 | 1.2702 | 1.3079 | 1.0092 | 1.8672 | 2.124 | 2.1488 | 2.1817 | 2.3238
2021-12-09 15:00 | 2.2863 | 2.5202 | 2.5528 | 2.5927 | 2.6393 | 1.3146 | 1.5994 | 1.6249 | 1.6597 | 1.3146 | 1.6576 | 1.8872 | 1.9101 | 1.9405 | 2.068
2021-12-09 16:00 | 2.3816 | 2.6189 | 2.6497 | 2.6874 | 2.7314 | 1.6108 | 1.9467 | 1.9708 | 2.0036 | 1.6108 | 2.2291 | 2.5199 | 2.5415 | 2.5701 | 2.727
2021-12-09 17:00 | 2.4197 | 2.659 | 2.6894 | 2.7265 | 2.7699 | 1.7719 | 2.1364 | 2.1601 | 2.1924 | 1.7719 | 2.3625 | 2.6675 | 2.6887 | 2.717 | 2.8807
2021-12-09 18:00 | 2.3816 | 2.6216 | 2.6538 | 2.6932 | 2.7391 | 1.8672 | 2.2515 | 2.2766 | 2.3109 | 1.8672 | 2.3054 | 2.6065 | 2.629 | 2.659 | 2.8215
2021-12-09 19:00 | 2.3244 | 2.5676 | 2.6035 | 2.6475 | 2.6988 | 1.7808 | 2.1549 | 2.1829 | 2.2212 | 1.7808 | 2.4006 | 2.7175 | 2.7427 | 2.7762 | 2.9481
2021-12-09 20:00 | 2.4578 | 2.7206 | 2.7615 | 2.8116 | 2.87 | 1.8672 | 2.2639 | 2.2959 | 2.3394 | 1.8672 | 2.6293 | 2.9785 | 3.0072 | 3.0453 | 3.2354
2021-12-09 21:00 | 2.3054 | 2.5665 | 2.6124 | 2.6685 | 2.7339 | 1.8672 | 2.271 | 2.3067 | 2.3556 | 1.8672 | 2.896 | 3.2818 | 3.3139 | 3.3566 | 3.5669
2021-12-09 22:00 | 2.1376 | 2.3879 | 2.4346 | 2.4917 | 2.5584 | 1.6237 | 1.9846 | 2.021 | 2.0707 | 1.6237 | 2.0386 | 2.3302 | 2.3629 | 2.4064 | 2.5704
2021-12-09 23:00 | 2.0005 | 2.2347 | 2.2783 | 2.3318 | 2.394 | 1.3644 | 1.6739 | 1.7079 | 1.7544 | 1.3644 | 2.0767 | 2.3683 | 2.3989 | 2.4395 | 2.6023
2021-12-10 | 1.81 | 2.0215 | 2.0609 | 2.109 | 2.1652 | 1.2384 | 1.5189 | 1.5496 | 1.5915 | 1.2384 | 1.5623 | 1.7907 | 1.8182 | 1.8549 | 1.9845
2021-12-10 01:00 | 1.6957 | 1.8893 | 1.9238 | 1.966 | 2.0153 | 1.086 | 1.332 | 1.3589 | 1.3957 | 1.086 | 1.5814 | 1.8052 | 1.8293 | 1.8615 | 1.9868
2021-12-10 02:00 | 1.6576 | 1.8388 | 1.8684 | 1.9046 | 1.9469 | 1.0669 | 1.3026 | 1.3257 | 1.3572 | 1.0669 | 1.2575 | 1.4384 | 1.4592 | 1.4868 | 1.5889
2021-12-10 03:00 | 1.6576 | 1.8267 | 1.8501 | 1.8788 | 1.9123 | 1.0479 | 1.2713 | 1.2896 | 1.3145 | 1.0479 | 1.3527 | 1.5357 | 1.5522 | 1.574 | 1.6745
2021-12-10 04:00 | 1.6576 | 1.8149 | 1.8323 | 1.8536 | 1.8784 | 1.0669 | 1.2852 | 1.2988 | 1.3173 | 1.0669 | 1.3908 | 1.5697 | 1.5819 | 1.5981 | 1.694
2021-12-10 05:00 | 1.81 | 1.9686 | 1.9808 | 1.9958 | 2.0133 | 1.1692 | 1.3987 | 1.4083 | 1.4213 | 1.1692 | 1.4861 | 1.6684 | 1.677 | 1.6884 | 1.7838
2021-12-10 06:00 | 2.0993 | 2.2754 | 2.2857 | 2.2982 | 2.3128 | 1.4991 | 1.7855 | 1.7935 | 1.8043 | 1.4991 | 1.81 | 2.0256 | 2.0327 | 2.0422 | 2.1531
2021-12-10 07:00 | 2.4837 | 2.6917 | 2.7036 | 2.7182 | 2.7353 | 1.7909 | 2.1327 | 2.142 | 2.1547 | 1.7909 | 2.2291 | 2.4937 | 2.5021 | 2.5132 | 2.649
2021-12-10 08:00 | 2.6864 | 2.9186 | 2.9352 | 2.9555 | 2.9791 | 1.9053 | 2.2744 | 2.2873 | 2.3049 | 1.9053 | 2.6483 | 2.9659 | 2.9776 | 2.993 | 3.157
2021-12-10 09:00 | 2.8007 | 3.0547 | 3.0781 | 3.1068 | 3.1402 | 1.7909 | 2.149 | 2.1673 | 2.1922 | 1.7909 | 2.1529 | 2.4249 | 2.4413 | 2.4631 | 2.6075
2021-12-10 10:00 | 2.8388 | 3.1099 | 3.1406 | 3.1781 | 3.2219 | 1.829 | 2.2044 | 2.2283 | 2.261 | 1.829 | 2.8007 | 3.1549 | 3.1764 | 3.2049 | 3.393
2021-12-10 11:00 | 2.9913 | 3.2846 | 3.3209 | 3.3653 | 3.417 | 1.9611 | 2.3684 | 2.3966 | 2.4353 | 1.9611 | 2.7436 | 3.0991 | 3.1245 | 3.1583 | 3.3495
2021-12-10 12:00 | 3.0103 | 3.3094 | 3.3479 | 3.395 | 3.4499 | 1.9624 | 2.373 | 2.403 | 2.444 | 1.9624 | 2.2482 | 2.5517 | 2.5787 | 2.6145 | 2.7809
2021-12-10 13:00 | 2.7817 | 3.0627 | 3.1007 | 3.1471 | 3.2013 | 1.8481 | 2.2372 | 2.2668 | 2.3072 | 1.8481 | 2.0386 | 2.3181 | 2.3446 | 2.38 | 2.5343
2021-12-10 14:00 | 2.534 | 2.7917 | 2.8271 | 2.8704 | 2.9209 | 1.6385 | 1.986 | 2.0136 | 2.0513 | 1.6385 | 1.6195 | 1.8487 | 1.8735 | 1.9065 | 2.0349
2021-12-10 15:00 | 2.4174 | 2.6611 | 2.6937 | 2.7336 | 2.7802 | 1.6004 | 1.9371 | 1.9625 | 1.9973 | 1.6004 | 1.7719 | 2.0143 | 2.0371 | 2.0675 | 2.2013
2021-12-10 16:00 | 2.4959 | 2.7417 | 2.7725 | 2.8102 | 2.8542 | 1.7645 | 2.1283 | 2.1523 | 2.1851 | 1.7645 | 1.8862 | 2.1388 | 2.1604 | 2.189 | 2.327
2021-12-10 17:00 | 2.3625 | 2.5976 | 2.628 | 2.6651 | 2.7085 | 1.7719 | 2.1364 | 2.1601 | 2.1924 | 1.7719 | 2.6674 | 3.0062 | 3.0275 | 3.0558 | 3.2362
2021-12-10 18:00 | 2.2863 | 2.5193 | 2.5514 | 2.5908 | 2.6367 | 1.81 | 2.184 | 2.2091 | 2.2434 | 1.81 | 2.6483 | 2.9876 | 3.0101 | 3.0401 | 3.2215
2021-12-10 19:00 | 2.4959 | 2.7518 | 2.7877 | 2.8317 | 2.883 | 1.9815 | 2.3919 | 2.4199 | 2.4582 | 1.9815 | 2.896 | 3.268 | 3.2932 | 3.3266 | 3.5259
2021-12-10 20:00 | 2.6102 | 2.8843 | 2.9253 | 2.9753 | 3.0337 | 2.1529 | 2.6016 | 2.6335 | 2.6771 | 2.1529 | 3.1437 | 3.5502 | 3.5788 | 3.6169 | 3.8353
2021-12-10 21:00 | 2.5721 | 2.8531 | 2.8989 | 2.9551 | 3.0205 | 2.0313 | 2.4649 | 2.5007 | 2.5495 | 2.0313 | 3.0294 | 3.43 | 3.4621 | 3.5048 | 3.7224
2021-12-10 22:00 | 2.4006 | 2.6705 | 2.7172 | 2.7743 | 2.841 | 1.8889 | 2.2978 | 2.3342 | 2.384 | 1.8889 | 3.0484 | 3.4523 | 3.485 | 3.5285 | 3.7481
2021-12-10 23:00 | 2.3816 | 2.6441 | 2.6877 | 2.7411 | 2.8034 | 1.6591 | 2.0221 | 2.0561 | 2.1026 | 1.6591 | 2.7817 | 3.1517 | 3.1823 | 3.2229 | 3.4244
2021-12-11 | 2.0767 | 2.3081 | 2.3474 | 2.3956 | 2.4517 | 1.4203 | 1.7338 | 1.7645 | 1.8064 | 1.4203 | 2.0005 | 2.2776 | 2.3052 | 2.3418 | 2.4956
2021-12-11 01:00 | 1.9053 | 2.1144 | 2.149 | 2.1912 | 2.2404 | 1.2711 | 1.5507 | 1.5776 | 1.6144 | 1.2711 | 1.6195 | 1.8475 | 1.8717 | 1.9038 | 2.0312
2021-12-11 02:00 | 1.9243 | 2.1253 | 2.155 | 2.1912 | 2.2335 | 1.2194 | 1.4826 | 1.5057 | 1.5373 | 1.2194 | 1.5623 | 1.7772 | 1.798 | 1.8255 | 1.9444
2021-12-11 03:00 | 1.8862 | 2.0723 | 2.0958 | 2.1245 | 2.1579 | 1.1241 | 1.3613 | 1.3796 | 1.4046 | 1.1241 | 1.448 | 1.6416 | 1.658 | 1.6799 | 1.7856
2021-12-11 04:00 | 1.8147 | 1.9837 | 2.0011 | 2.0224 | 2.0473 | 1.1813 | 1.4202 | 1.4338 | 1.4524 | 1.1813 | 1.4861 | 1.6756 | 1.6878 | 1.704 | 1.8051
2021-12-11 05:00 | 1.8481 | 2.0095 | 2.0218 | 2.0368 | 2.0543 | 1.213 | 1.4504 | 1.46 | 1.4731 | 1.213 | 1.5814 | 1.7743 | 1.7829 | 1.7943 | 1.8949
2021-12-11 06:00 | 1.829 | 1.9851 | 1.9953 | 2.0078 | 2.0224 | 1.2575 | 1.5001 | 1.508 | 1.5189 | 1.2575 | 1.6766 | 1.8773 | 1.8845 | 1.894 | 1.9976
2021-12-11 07:00 | 1.8277 | 1.987 | 1.9989 | 2.0135 | 2.0305 | 1.3908 | 1.66 | 1.6694 | 1.6821 | 1.3908 | 1.4047 | 1.5776 | 1.5859 | 1.597 | 1.6875
2021-12-11 08:00 | 1.9243 | 2.0998 | 2.1164 | 2.1367 | 2.1604 | 1.3706 | 1.6428 | 1.6557 | 1.6734 | 1.3706 | 1.448 | 1.6321 | 1.6437 | 1.6591 | 1.7572
2021-12-11 09:00 | 1.6766 | 1.8471 | 1.8705 | 1.8991 | 1.9325 | 1.0669 | 1.2937 | 1.312 | 1.3369 | 1.0669 | 0.99073 | 1.1334 | 1.1498 | 1.1716 | 1.2521
2021-12-11 10:00 | 1.7338 | 1.9227 | 1.9534 | 1.9909 | 2.0347 | 1.0669 | 1.3041 | 1.328 | 1.3607 | 1.0669 | 1.0669 | 1.2282 | 1.2497 | 1.2782 | 1.371
2021-12-11 11:00 | 1.5242 | 1.7085 | 1.7448 | 1.7892 | 1.8409 | 1.0479 | 1.2895 | 1.3178 | 1.3564 | 1.0479 | 0.85737 | 1.003 | 1.0285 | 1.0622 | 1.1497
2021-12-11 12:00 | 1.7909 | 1.9994 | 2.0379 | 2.085 | 2.1399 | 0.99073 | 1.2251 | 1.2551 | 1.2961 | 0.99073 | 0.99073 | 1.1543 | 1.1813 | 1.2171 | 1.3144
2021-12-11 13:00 | 1.3718 | 1.548 | 1.586 | 1.6324 | 1.6866 | 0.87642 | 1.0893 | 1.1189 | 1.1593 | 0.87642 | 1.2384 | 1.4288 | 1.4554 | 1.4907 | 1.6011
2021-12-11 14:00 | 1.4861 | 1.6659 | 1.7013 | 1.7446 | 1.7951 | 0.99073 | 1.2207 | 1.2484 | 1.2861 | 0.99073 | 1.086 | 1.2559 | 1.2807 | 1.3137 | 1.4128
2021-12-11 15:00 | 1.6195 | 1.8037 | 1.8364 | 1.8763 | 1.9229 | 1.0669 | 1.3068 | 1.3323 | 1.3671 | 1.0669 | 1.0098 | 1.1674 | 1.1903 | 1.2206 | 1.3125
2021-12-11 16:00 | 1.5814 | 1.7592 | 1.79 | 1.8277 | 1.8717 | 1.1622 | 1.4168 | 1.4408 | 1.4736 | 1.1622 | 1.0669 | 1.2284 | 1.2499 | 1.2786 | 1.3716
2021-12-11 17:00 | 1.829 | 2.0245 | 2.0548 | 2.092 | 2.1353 | 1.3527 | 1.6412 | 1.6649 | 1.6973 | 1.3527 | 1.4289 | 1.63 | 1.6513 | 1.6796 | 1.7919
2021-12-11 18:00 | 1.9053 | 2.1099 | 2.1421 | 2.1814 | 2.2274 | 1.4861 | 1.8014 | 1.8265 | 1.8607 | 1.4861 | 1.6133 | 1.8374 | 1.8599 | 1.8899 | 2.0144
2021-12-11 19:00 | 2.0577 | 2.281 | 2.3169 | 2.3609 | 2.4122 | 1.6004 | 1.9418 | 1.9698 | 2.0081 | 1.6004 | 1.9624 | 2.2306 | 2.2558 | 2.2892 | 2.4371
2021-12-11 20:00 | 2.3054 | 2.5568 | 2.5978 | 2.6478 | 2.7062 | 1.7098 | 2.078 | 2.11 | 2.1535 | 1.7098 | 2.172 | 2.4704 | 2.4991 | 2.5371 | 2.7021
2021-12-11 21:00 | 2.2863 | 2.546 | 2.5919 | 2.648 | 2.7135 | 1.7338 | 2.1134 | 2.1492 | 2.198 | 1.7338 | 2.4768 | 2.816 | 2.8481 | 2.8908 | 3.078
2021-12-11 22:00 | 2.191 | 2.4453 | 2.492 | 2.5492 | 2.6158 | 1.6697 | 2.0389 | 2.0753 | 2.1251 | 1.6697 | 2.1339 | 2.436 | 2.4688 | 2.5122 | 2.6815
2021-12-11 23:00 | 1.9895 | 2.2229 | 2.2665 | 2.32 | 2.3822 | 1.4043 | 1.721 | 1.7551 | 1.8015 | 1.4043 | 1.8791 | 2.1487 | 2.1793 | 2.2199 | 2.3718
2021-12-12 | 1.8862 | 2.1034 | 2.1428 | 2.1909 | 2.247 | 1.2794 | 1.5673 | 1.598 | 1.6399 | 1.2794 | 1.7909 | 2.0447 | 2.0723 | 2.1089 | 2.2512
2021-12-12 01:00 | 1.7528 | 1.9507 | 1.9852 | 2.0274 | 2.0767 | 1.1432 | 1.3995 | 1.4265 | 1.4632 | 1.1432 | 1.467 | 1.6781 | 1.7023 | 1.7344 | 1.8535
2021-12-12 02:00 | 1.7147 | 1.9002 | 1.9298 | 1.9661 | 2.0083 | 1.086 | 1.3251 | 1.3482 | 1.3797 | 1.086 | 1.5623 | 1.7772 | 1.798 | 1.8255 | 1.9444
2021-12-12 03:00 | 1.6957 | 1.8676 | 1.8911 | 1.9198 | 1.9532 | 1.0669 | 1.2938 | 1.3121 | 1.337 | 1.0669 | 1.5242 | 1.7263 | 1.7427 | 1.7646 | 1.8744
2021-12-12 04:00 | 1.6957 | 1.8558 | 1.8732 | 1.8945 | 1.9194 | 1.0217 | 1.2318 | 1.2454 | 1.2639 | 1.0217 | 1.4099 | 1.5909 | 1.6031 | 1.6193 | 1.7162
2021-12-12 05:00 | 1.6957 | 1.8457 | 1.858 | 1.873 | 1.8905 | 1.1241 | 1.3454 | 1.355 | 1.368 | 1.1241 | 1.3718 | 1.5414 | 1.55 | 1.5614 | 1.6505
2021-12-12 06:00 | 1.6195 | 1.7599 | 1.7701 | 1.7826 | 1.7973 | 1.0669 | 1.275 | 1.283 | 1.2939 | 1.0669 | 1.3337 | 1.4962 | 1.5034 | 1.5129 | 1.5977
2021-12-12 07:00 | 1.5433 | 1.6814 | 1.6933 | 1.7079 | 1.7249 | 1.1241 | 1.3449 | 1.3542 | 1.367 | 1.1241 | 1.1241 | 1.2657 | 1.2741 | 1.2852 | 1.3603
2021-12-12 08:00 | 1.3718 | 1.5062 | 1.5228 | 1.5431 | 1.5668 | 1.0009 | 1.206 | 1.219 | 1.2366 | 1.0009 | 0.97168 | 1.1028 | 1.1144 | 1.1298 | 1.2017
2021-12-12 09:00 | 1.1622 | 1.2944 | 1.3178 | 1.3464 | 1.3798 | 0.87642 | 1.0686 | 1.0869 | 1.1118 | 0.87642 | 0.99073 | 1.1334 | 1.1498 | 1.1716 | 1.2521
2021-12-12 10:00 | 1.2003 | 1.3496 | 1.3803 | 1.4178 | 1.4616 | 0.78115 | 0.96644 | 0.99037 | 1.023 | 0.78115 | 1.1432 | 1.3129 | 1.3344 | 1.3629 | 1.4599
2021-12-12 11:00 | 1.2956 | 1.4629 | 1.4991 | 1.5435 | 1.5953 | 0.81926 | 1.0194 | 1.0477 | 1.0863 | 0.81926 | 1.3908 | 1.5959 | 1.6213 | 1.655 | 1.7719
2021-12-12 12:00 | 1.0288 | 1.1807 | 1.2191 | 1.2662 | 1.3212 | 0.70494 | 0.88751 | 0.91753 | 0.95851 | 0.70494 | 1.467 | 1.6836 | 1.7106 | 1.7464 | 1.8699
2021-12-12 13:00 | 1.3718 | 1.548 | 1.586 | 1.6324 | 1.6866 | 0.70494 | 0.88675 | 0.91634 | 0.95676 | 0.70494 | 1.5814 | 1.8099 | 1.8365 | 1.8718 | 2.001
2021-12-12 14:00 | 1.4099 | 1.584 | 1.6194 | 1.6627 | 1.7132 | 0.97168 | 1.1982 | 1.2258 | 1.2635 | 0.97168 | 1.4861 | 1.7005 | 1.7253 | 1.7583 | 1.8794
2021-12-12 15:00 | 1.7719 | 1.9675 | 2.0001 | 2.0401 | 2.0867 | 1.086 | 1.3294 | 1.3548 | 1.3896 | 1.086 | 1.3908 | 1.5908 | 1.6137 | 1.6441 | 1.7569
2021-12-12 16:00 | 1.5814 | 1.7592 | 1.79 | 1.8277 | 1.8717 | 1.3337 | 1.6193 | 1.6434 | 1.6762 | 1.3337 | 1.0288 | 1.186 | 1.2076 | 1.2363 | 1.3271
2021-12-12 17:00 | 2.0386 | 2.2496 | 2.28 | 2.3171 | 2.3605 | 1.6288 | 1.9674 | 1.9911 | 2.0234 | 1.6288 | 1.9434 | 2.2017 | 2.223 | 2.2512 | 2.3919
2021-12-12 18:00 | 2.2673 | 2.4988 | 2.531 | 2.5703 | 2.6163 | 1.81 | 2.184 | 2.2091 | 2.2434 | 1.81 | 2.191 | 2.4794 | 2.502 | 2.5319 | 2.6882
2021-12-12 19:00 | 2.2482 | 2.4857 | 2.5216 | 2.5656 | 2.6169 | 1.7105 | 2.0718 | 2.0998 | 2.1381 | 1.7105 | 2.6102 | 2.9504 | 2.9756 | 3.0091 | 3.1926
2021-12-12 20:00 | 2.4006 | 2.6592 | 2.7001 | 2.7502 | 2.8086 | 1.7909 | 2.1739 | 2.2058 | 2.2494 | 1.7909 | 2.4006 | 2.7245 | 2.7531 | 2.7912 | 2.9687
2021-12-12 21:00 | 2.2863 | 2.546 | 2.5919 | 2.648 | 2.7135 | 1.7909 | 2.1809 | 2.2167 | 2.2655 | 1.7909 | 2.8769 | 3.2606 | 3.2927 | 3.3354 | 3.5446
2021-12-12 22:00 | 2.2291 | 2.4863 | 2.533 | 2.5901 | 2.6567 | 1.6096 | 1.968 | 2.0044 | 2.0541 | 1.6096 | 1.9243 | 2.2032 | 2.2359 | 2.2793 | 2.4371
2021-12-12 23:00 | 1.9815 | 2.2142 | 2.2579 | 2.3113 | 2.3736 | 1.3348 | 1.6389 | 1.673 | 1.7195 | 1.3348 | 1.9815 | 2.2624 | 2.293 | 2.3337 | 2.4912
2021-12-13 | 1.829 | 2.042 | 2.0814 | 2.1295 | 2.1856 | 1.1949 | 1.4675 | 1.4982 | 1.5401 | 1.1949 | 1.5623 | 1.7907 | 1.8182 | 1.8549 | 1.9845
2021-12-13 01:00 | 1.6957 | 1.8893 | 1.9238 | 1.966 | 2.0153 | 1.0669 | 1.3095 | 1.3364 | 1.3732 | 1.0669 | 1.4289 | 1.6358 | 1.66 | 1.6921 | 1.8091
2021-12-13 02:00 | 1.6195 | 1.7978 | 1.8275 | 1.8637 | 1.906 | 0.99073 | 1.2125 | 1.2356 | 1.2672 | 0.99073 | 1.2575 | 1.4384 | 1.4592 | 1.4868 | 1.5889
2021-12-13 03:00 | 1.6004 | 1.7653 | 1.7887 | 1.8174 | 1.8509 | 0.99258 | 1.2059 | 1.2242 | 1.2492 | 0.99258 | 1.4289 | 1.6204 | 1.6369 | 1.6587 | 1.7634
2021-12-13 04:00 | 1.6385 | 1.7944 | 1.8118 | 1.8331 | 1.858 | 1.0288 | 1.2402 | 1.2538 | 1.2723 | 1.0288 | 1.4099 | 1.5909 | 1.6031 | 1.6193 | 1.7162
2021-12-13 05:00 | 1.7719 | 1.9276 | 1.9399 | 1.9549 | 1.9724 | 1.1959 | 1.4302 | 1.4398 | 1.4528 | 1.1959 | 1.4099 | 1.5838 | 1.5923 | 1.6038 | 1.6949
2021-12-13 06:00 | 1.7719 | 1.9236 | 1.9339 | 1.9464 | 1.961 | 1.2194 | 1.4551 | 1.463 | 1.4739 | 1.2194 | 1.3908 | 1.5598 | 1.5669 | 1.5765 | 1.6643
2021-12-13 07:00 | 2.0958 | 2.275 | 2.2869 | 2.3015 | 2.3185 | 1.467 | 1.7501 | 1.7594 | 1.7721 | 1.467 | 1.5433 | 1.7315 | 1.7399 | 1.751 | 1.8491
2021-12-13 08:00 | 2.2291 | 2.4273 | 2.4439 | 2.4642 | 2.4879 | 1.5623 | 1.8692 | 1.8821 | 1.8998 | 1.5623 | 1.6766 | 1.8862 | 1.8978 | 1.9132 | 2.0238
2021-12-13 09:00 | 2.0979 | 2.2996 | 2.323 | 2.3517 | 2.385 | 1.2956 | 1.5638 | 1.5821 | 1.607 | 1.2956 | 1.0098 | 1.1546 | 1.171 | 1.1928 | 1.2743
2021-12-13 10:00 | 1.5433 | 1.718 | 1.7487 | 1.7863 | 1.83 | 0.66684 | 0.83139 | 0.85532 | 0.88799 | 0.66684 | 1.4861 | 1.694 | 1.7155 | 1.744 | 1.8599
2021-12-13 11:00 | 1.3337 | 1.5038 | 1.5401 | 1.5845 | 1.6362 | 0.49948 | 0.64163 | 0.66992 | 0.70854 | 0.49948 | 1.9434 | 2.2099 | 2.2353 | 2.269 | 2.4162
2021-12-13 12:00 | 1.3527 | 1.5286 | 1.5671 | 1.6142 | 1.6691 | 0.49537 | 0.63992 | 0.66994 | 0.71093 | 0.49537 | 1.9624 | 2.2341 | 2.2611 | 2.2969 | 2.4476
2021-12-13 13:00 | 1.7147 | 1.9165 | 1.9544 | 2.0009 | 2.055 | 1.105 | 1.3594 | 1.389 | 1.4294 | 1.105 | 1.9053 | 2.1699 | 2.1964 | 2.2318 | 2.3787
2021-12-13 14:00 | 2.1339 | 2.3618 | 2.3972 | 2.4405 | 2.4911 | 1.086 | 1.3333 | 1.3609 | 1.3986 | 1.086 | 2.0386 | 2.3145 | 2.3393 | 2.3723 | 2.5238
2021-12-13 15:00 | 2.2101 | 2.4383 | 2.4709 | 2.5109 | 2.5574 | 1.2575 | 1.5319 | 1.5574 | 1.5921 | 1.2575 | 1.2575 | 1.4426 | 1.4655 | 1.4959 | 1.6013
2021-12-13 16:00 | 1.9053 | 2.1072 | 2.138 | 2.1757 | 2.2197 | 1.0098 | 1.2367 | 1.2607 | 1.2935 | 1.0098 | 1.1622 | 1.3342 | 1.3558 | 1.3845 | 1.4827
2021-12-13 17:00 | 2.2291 | 2.4543 | 2.4847 | 2.5218 | 2.5652 | 1.3681 | 1.6594 | 1.6831 | 1.7154 | 1.3681 | 1.105 | 1.2701 | 1.2914 | 1.3196 | 1.4142
2021-12-13 18:00 | 2.4006 | 2.6421 | 2.6742 | 2.7136 | 2.7595 | 1.6681 | 2.0164 | 2.0415 | 2.0758 | 1.6681 | 1.8481 | 2.0983 | 2.1209 | 2.1508 | 2.2882
2021-12-13 19:00 | 2.5149 | 2.7722 | 2.8082 | 2.8522 | 2.9034 | 1.8862 | 2.2794 | 2.3074 | 2.3457 | 1.8862 | 2.0577 | 2.3364 | 2.3616 | 2.3951 | 2.5482
2021-12-13 20:00 | 2.4578 | 2.7206 | 2.7615 | 2.8116 | 2.87 | 1.8862 | 2.2865 | 2.3184 | 2.3619 | 1.8862 | 2.3054 | 2.6186 | 2.6473 | 2.6853 | 2.8576
2021-12-13 21:00 | 2.3054 | 2.5665 | 2.6124 | 2.6685 | 2.7339 | 1.7528 | 2.1359 | 2.1717 | 2.2205 | 1.7528 | 2.3816 | 2.7101 | 2.7423 | 2.785 | 2.9669
2021-12-13 22:00 | 2.2249 | 2.4817 | 2.5284 | 2.5855 | 2.6522 | 1.5612 | 1.9107 | 1.9471 | 1.9968 | 1.5612 | 1.9434 | 2.2243 | 2.257 | 2.3005 | 2.4593
2021-12-13 23:00 | 1.9291 | 2.158 | 2.2016 | 2.2551 | 2.3173 | 1.3399 | 1.6449 | 1.679 | 1.7254 | 1.3399 | 1.9053 | 2.1778 | 2.2083 | 2.249 | 2.4023
2021-12-14 | 1.7754 | 1.9843 | 2.0237 | 2.0718 | 2.128 | 1.2118 | 1.4875 | 1.5181 | 1.56 | 1.2118 | 1.6576 | 1.8965 | 1.9241 | 1.9607 | 2.0956
2021-12-14 01:00 | 1.6576 | 1.8483 | 1.8829 | 1.9251 | 1.9743 | 1.0669 | 1.3095 | 1.3364 | 1.3732 | 1.0669 | 1.2956 | 1.4876 | 1.5117 | 1.5439 | 1.6535
2021-12-14 02:00 | 1.5814 | 1.7569 | 1.7865 | 1.8228 | 1.865 | 1.0098 | 1.235 | 1.2581 | 1.2897 | 1.0098 | 1.2384 | 1.4173 | 1.438 | 1.4656 | 1.5666
2021-12-14 03:00 | 1.5623 | 1.7244 | 1.7478 | 1.7765 | 1.81 | 0.97168 | 1.1812 | 1.1995 | 1.2245 | 0.97168 | 1.2194 | 1.3875 | 1.404 | 1.4258 | 1.5189
2021-12-14 04:00 | 1.5814 | 1.733 | 1.7504 | 1.7717 | 1.7966 | 1.0005 | 1.2067 | 1.2202 | 1.2388 | 1.0005 | 1.2575 | 1.4215 | 1.4337 | 1.4499 | 1.5384
2021-12-14 05:00 | 1.6576 | 1.8048 | 1.8171 | 1.8321 | 1.8496 | 1.0669 | 1.2779 | 1.2874 | 1.3005 | 1.0669 | 1.2003 | 1.3509 | 1.3594 | 1.3709 | 1.4505
2021-12-14 06:00 | 1.6957 | 1.8418 | 1.852 | 1.8645 | 1.8791 | 1.1622 | 1.3875 | 1.3955 | 1.4064 | 1.1622 | 1.3908 | 1.5598 | 1.5669 | 1.5765 | 1.6643
2021-12-14 07:00 | 1.829 | 1.9884 | 2.0003 | 2.0149 | 2.032 | 1.2003 | 1.435 | 1.4443 | 1.457 | 1.2003 | 1.2194 | 1.3716 | 1.3799 | 1.3911 | 1.4714
2021-12-14 08:00 | 1.6957 | 1.8542 | 1.8708 | 1.8911 | 1.9147 | 1.1241 | 1.3515 | 1.3645 | 1.3821 | 1.1241 | 1.0479 | 1.1875 | 1.1991 | 1.2145 | 1.2906
2021-12-14 09:00 | 1.7147 | 1.888 | 1.9114 | 1.94 | 1.9734 | 0.7621 | 0.93358 | 0.95183 | 0.97675 | 0.7621 | 1.2384 | 1.4086 | 1.425 | 1.4468 | 1.541
2021-12-14 10:00 | 1.8481 | 2.0455 | 2.0762 | 2.1138 | 2.1575 | 0.81926 | 1.0115 | 1.0354 | 1.068 | 0.81926 | 1.6195 | 1.8422 | 1.8637 | 1.8922 | 2.0154
2021-12-14 11:00 | 1.9815 | 2.1998 | 2.236 | 2.2804 | 2.3322 | 0.80021 | 0.99689 | 1.0252 | 1.0638 | 0.80021 | 1.6004 | 1.8288 | 1.8542 | 1.8879 | 2.0163
2021-12-14 12:00 | 2.1148 | 2.3474 | 2.3859 | 2.433 | 2.4879 | 0.91452 | 1.1351 | 1.1651 | 1.2061 | 0.91452 | 1.6957 | 1.9377 | 1.9647 | 2.0005 | 2.1366
2021-12-14 13:00 | 2.1339 | 2.3668 | 2.4047 | 2.4512 | 2.5054 | 0.93358 | 1.1568 | 1.1864 | 1.2269 | 0.93358 | 1.6766 | 1.9158 | 1.9424 | 1.9777 | 2.1121
2021-12-14 14:00 | 2.4006 | 2.6484 | 2.6838 | 2.7271 | 2.7776 | 1.1727 | 1.4357 | 1.4634 | 1.5011 | 1.1727 | 1.6385 | 1.8699 | 1.8947 | 1.9277 | 2.0571
2021-12-14 15:00 | 2.3656 | 2.6053 | 2.638 | 2.6779 | 2.7245 | 1.1813 | 1.4419 | 1.4673 | 1.5021 | 1.1813 | 1.2194 | 1.4003 | 1.4232 | 1.4535 | 1.5569
2021-12-14 16:00 | 2.8198 | 3.0897 | 3.1205 | 3.1582 | 3.2022 | 1.7909 | 2.1595 | 2.1836 | 2.2164 | 1.7909 | 1.8481 | 2.0964 | 2.118 | 2.1467 | 2.2826
2021-12-14 17:00 | 2.6674 | 2.9251 | 2.9555 | 2.9926 | 3.036 | 1.8862 | 2.2715 | 2.2951 | 2.3275 | 1.8862 | 2.6483 | 2.9851 | 3.0063 | 3.0346 | 3.214
2021-12-14 18:00 | 2.5721 | 2.8263 | 2.8585 | 2.8978 | 2.9438 | 2.0196 | 2.4316 | 2.4567 | 2.4909 | 2.0196 | 2.3244 | 2.6276 | 2.6502 | 2.6801 | 2.8437
2021-12-14 19:00 | 2.4387 | 2.6904 | 2.7263 | 2.7703 | 2.8216 | 1.9547 | 2.3603 | 2.3884 | 2.4266 | 1.9547 | 2.4768 | 2.8022 | 2.8274 | 2.8609 | 3.037
2021-12-14 20:00 | 2.4387 | 2.7001 | 2.741 | 2.7911 | 2.8495 | 1.8481 | 2.2414 | 2.2734 | 2.3169 | 1.8481 | 2.2291 | 2.5339 | 2.5626 | 2.6007 | 2.7688
2021-12-14 21:00 | 2.4006 | 2.6689 | 2.7147 | 2.7708 | 2.8363 | 1.7909 | 2.1809 | 2.2167 | 2.2655 | 1.7909 | 2.3054 | 2.6254 | 2.6576 | 2.7003 | 2.878
2021-12-14 22:00 | 2.2673 | 2.5272 | 2.5739 | 2.631 | 2.6977 | 1.6733 | 2.0431 | 2.0796 | 2.1293 | 1.6733 | 1.9434 | 2.2243 | 2.257 | 2.3005 | 2.4593
2021-12-14 23:00 | 1.945 | 2.1751 | 2.2187 | 2.2721 | 2.3344 | 1.3891 | 1.7031 | 1.7371 | 1.7836 | 1.3891 | 1.6957 | 1.9449 | 1.9754 | 2.0161 | 2.1579
2021-12-15 | 1.8009 | 2.0118 | 2.0511 | 2.0993 | 2.1554 | 1.1924 | 1.4646 | 1.4953 | 1.5372 | 1.1924 | 1.5623 | 1.7907 | 1.8182 | 1.8549 | 1.9845
2021-12-15 01:00 | 1.6576 | 1.8483 | 1.8829 | 1.9251 | 1.9743 | 1.0889 | 1.3354 | 1.3623 | 1.3991 | 1.0889 | 1.2765 | 1.4664 | 1.4906 | 1.5227 | 1.6313
2021-12-15 02:00 | 1.6004 | 1.7774 | 1.807 | 1.8432 | 1.8855 | 1.0098 | 1.235 | 1.2581 | 1.2897 | 1.0098 | 1.3718 | 1.5655 | 1.5862 | 1.6138 | 1.7222
2021-12-15 03:00 | 1.5814 | 1.7448 | 1.7683 | 1.797 | 1.8304 | 0.99073 | 1.2037 | 1.222 | 1.247 | 0.99073 | 1.2384 | 1.4087 | 1.4251 | 1.447 | 1.5412
2021-12-15 04:00 | 1.6004 | 1.7535 | 1.7709 | 1.7922 | 1.817 | 0.98438 | 1.1877 | 1.2012 | 1.2198 | 0.98438 | 1.4099 | 1.5909 | 1.6031 | 1.6193 | 1.7162
2021-12-15 05:00 | 1.6957 | 1.8457 | 1.858 | 1.873 | 1.8905 | 1.086 | 1.3004 | 1.3099 | 1.323 | 1.086 | 1.4861 | 1.6684 | 1.677 | 1.6884 | 1.7838
2021-12-15 06:00 | 1.714 | 1.8615 | 1.8717 | 1.8842 | 1.8988 | 1.2384 | 1.4776 | 1.4855 | 1.4964 | 1.2384 | 1.3146 | 1.4751 | 1.4822 | 1.4918 | 1.5754
2021-12-15 07:00 | 1.9434 | 2.1112 | 2.1231 | 2.1377 | 2.1548 | 1.2575 | 1.5025 | 1.5118 | 1.5245 | 1.2575 | 1.2575 | 1.4139 | 1.4223 | 1.4334 | 1.5158
2021-12-15 08:00 | 1.7528 | 1.9156 | 1.9322 | 1.9525 | 1.9761 | 1.1033 | 1.327 | 1.34 | 1.3576 | 1.1033 | 0.89547 | 1.0181 | 1.0297 | 1.0451 | 1.1128
2021-12-15 09:00 | 1.9815 | 2.1746 | 2.198 | 2.2266 | 2.26 | 1.0479 | 1.2712 | 1.2895 | 1.3144 | 1.0479 | 1.3527 | 1.5357 | 1.5521 | 1.5739 | 1.6743
2021-12-15 10:00 | 1.6004 | 1.7794 | 1.8101 | 1.8477 | 1.8914 | 0.75127 | 0.93114 | 0.95506 | 0.98773 | 0.75127 | 1.4289 | 1.6305 | 1.652 | 1.6805 | 1.7932
2021-12-15 11:00 | 1.7528 | 1.9541 | 1.9904 | 2.0348 | 2.0865 | 0.68589 | 0.86185 | 0.89013 | 0.92875 | 0.68589 | 2.1148 | 2.4004 | 2.4258 | 2.4596 | 2.6162
2021-12-15 12:00 | 1.9053 | 2.1222 | 2.1607 | 2.2078 | 2.2627 | 0.80021 | 1 | 1.0301 | 1.0711 | 0.80021 | 1.9624 | 2.2341 | 2.2611 | 2.2969 | 2.4476
2021-12-15 13:00 | 1.9243 | 2.1416 | 2.1796 | 2.226 | 2.2802 | 0.93358 | 1.1568 | 1.1864 | 1.2269 | 0.93358 | 1.5242 | 1.7464 | 1.773 | 1.8083 | 1.9344
2021-12-15 14:00 | 2.5721 | 2.8326 | 2.868 | 2.9113 | 2.9619 | 1.2956 | 1.5809 | 1.6085 | 1.6462 | 1.2956 | 1.2956 | 1.4888 | 1.5136 | 1.5466 | 1.6572
2021-12-15 15:00 | 2.9722 | 3.257 | 3.2897 | 3.3296 | 3.3762 | 1.7338 | 2.0946 | 2.1201 | 2.1548 | 1.7338 | 2.0767 | 2.353 | 2.3759 | 2.4063 | 2.5568
2021-12-15 16:00 | 2.8898 | 3.165 | 3.1958 | 3.2335 | 3.2774 | 1.7294 | 2.0869 | 2.1109 | 2.1437 | 1.7294 | 1.9434 | 2.2023 | 2.2239 | 2.2525 | 2.3937
2021-12-15 17:00 | 2.4959 | 2.7409 | 2.7712 | 2.8084 | 2.8517 | 1.7117 | 2.0653 | 2.089 | 2.1213 | 1.7117 | 2.0767 | 2.3499 | 2.3712 | 2.3994 | 2.5474
2021-12-15 18:00 | 2.4853 | 2.733 | 2.7652 | 2.8046 | 2.8505 | 1.81 | 2.184 | 2.2091 | 2.2434 | 1.81 | 2.534 | 2.8605 | 2.8831 | 2.913 | 3.0881
2021-12-15 19:00 | 2.3625 | 2.6085 | 2.6444 | 2.6884 | 2.7397 | 1.8481 | 2.2344 | 2.2624 | 2.3007 | 1.8481 | 2.191 | 2.4846 | 2.5098 | 2.5433 | 2.7037
2021-12-15 20:00 | 2.3625 | 2.6182 | 2.6592 | 2.7092 | 2.7676 | 1.829 | 2.2189 | 2.2508 | 2.2944 | 1.829 | 2.172 | 2.4704 | 2.4991 | 2.5371 | 2.7021
2021-12-15 21:00 | 2.3816 | 2.6484 | 2.6942 | 2.7504 | 2.8158 | 1.7649 | 2.1502 | 2.1859 | 2.2348 | 1.7649 | 2.3816 | 2.7101 | 2.7423 | 2.785 | 2.9669
2021-12-15 22:00 | 2.191 | 2.4453 | 2.492 | 2.5492 | 2.6158 | 1.5758 | 1.9279 | 1.9643 | 2.0141 | 1.5758 | 2.0386 | 2.3302 | 2.3629 | 2.4064 | 2.5704
2021-12-15 23:00 | 2.0196 | 2.2552 | 2.2988 | 2.3522 | 2.4145 | 1.4099 | 1.7276 | 1.7617 | 1.8082 | 1.4099 | 1.9053 | 2.1778 | 2.2083 | 2.249 | 2.4023
2021-12-16 | 1.81 | 2.0215 | 2.0609 | 2.109 | 2.1652 | 1.1874 | 1.4586 | 1.4893 | 1.5312 | 1.1874 | 1.5814 | 1.8118 | 1.8394 | 1.876 | 2.0067
2021-12-16 01:00 | 1.6576 | 1.8483 | 1.8829 | 1.9251 | 1.9743 | 1.0669 | 1.3095 | 1.3364 | 1.3732 | 1.0669 | 1.5242 | 1.7416 | 1.7658 | 1.7979 | 1.9201
2021-12-16 02:00 | 1.6004 | 1.7774 | 1.807 | 1.8432 | 1.8855 | 1.0098 | 1.235 | 1.2581 | 1.2897 | 1.0098 | 1.2384 | 1.4173 | 1.438 | 1.4656 | 1.5666
2021-12-16 03:00 | 1.5433 | 1.7039 | 1.7273 | 1.756 | 1.7895 | 0.99073 | 1.2037 | 1.222 | 1.247 | 0.99073 | 1.2575 | 1.4299 | 1.4463 | 1.4681 | 1.5634
2021-12-16 04:00 | 1.6394 | 1.7953 | 1.8127 | 1.834 | 1.8589 | 0.97168 | 1.1727 | 1.1862 | 1.2048 | 0.97168 | 1.1813 | 1.3368 | 1.349 | 1.3652 | 1.4495
2021-12-16 05:00 | 1.7015 | 1.852 | 1.8643 | 1.8793 | 1.8968 | 1.105 | 1.3229 | 1.3325 | 1.3455 | 1.105 | 1.3527 | 1.5202 | 1.5288 | 1.5402 | 1.6282
2021-12-16 06:00 | 1.8361 | 1.9927 | 2.0029 | 2.0154 | 2.03 | 1.2575 | 1.5001 | 1.508 | 1.5189 | 1.2575 | 1.4099 | 1.5809 | 1.5881 | 1.5976 | 1.6865
2021-12-16 07:00 | 2.0386 | 2.2135 | 2.2255 | 2.2401 | 2.2571 | 1.3527 | 1.615 | 1.6243 | 1.637 | 1.3527 | 1.6195 | 1.8162 | 1.8246 | 1.8357 | 1.938
2021-12-16 08:00 | 1.9053 | 2.0794 | 2.0959 | 2.1162 | 2.1399 | 1.2194 | 1.4641 | 1.477 | 1.4947 | 1.2194 | 1.2956 | 1.4627 | 1.4743 | 1.4898 | 1.5794
2021-12-16 09:00 | 2.1339 | 2.3383 | 2.3617 | 2.3904 | 2.4238 | 0.99073 | 1.2037 | 1.2219 | 1.2468 | 0.99073 | 1.3337 | 1.5145 | 1.5309 | 1.5527 | 1.652
2021-12-16 10:00 | 1.9243 | 2.1274 | 2.1581 | 2.1956 | 2.2394 | 0.7621 | 0.94393 | 0.96786 | 1.0005 | 0.7621 | 1.6195 | 1.8422 | 1.8637 | 1.8922 | 2.0154
2021-12-16 11:00 | 1.8672 | 2.0769 | 2.1132 | 2.1576 | 2.2094 | 0.60968 | 0.77182 | 0.8001 | 0.83872 | 0.60968 | 1.6195 | 1.8499 | 1.8753 | 1.9091 | 2.0385
2021-12-16 12:00 | 1.7719 | 1.9789 | 2.0174 | 2.0645 | 2.1195 | 0.62873 | 0.79748 | 0.8275 | 0.86848 | 0.62873 | 1.9624 | 2.2341 | 2.2611 | 2.2969 | 2.4476
2021-12-16 13:00 | 2.2673 | 2.5101 | 2.548 | 2.5945 | 2.6486 | 1.1813 | 1.4494 | 1.479 | 1.5195 | 1.1813 | 1.6004 | 1.8311 | 1.8577 | 1.893 | 2.0232
2021-12-16 14:00 | 2.2291 | 2.4642 | 2.4996 | 2.5429 | 2.5934 | 1.1547 | 1.4145 | 1.4421 | 1.4798 | 1.1547 | 1.0288 | 1.1924 | 1.2172 | 1.2502 | 1.3461
2021-12-16 15:00 | 2.2482 | 2.4792 | 2.5119 | 2.5518 | 2.5984 | 1.2384 | 1.5094 | 1.5349 | 1.5696 | 1.2384 | 0.93358 | 1.0827 | 1.1056 | 1.136 | 1.2236
2021-12-16 16:00 | 2.3816 | 2.6189 | 2.6497 | 2.6874 | 2.7314 | 1.3718 | 1.6644 | 1.6884 | 1.7212 | 1.3718 | 0.91452 | 1.059 | 1.0806 | 1.1092 | 1.1938
2021-12-16 17:00 | 2.4959 | 2.7409 | 2.7712 | 2.8084 | 2.8517 | 1.7528 | 2.1139 | 2.1376 | 2.1699 | 1.7528 | 1.8672 | 2.117 | 2.1383 | 2.1665 | 2.303
2021-12-16 18:00 | 2.4768 | 2.7239 | 2.7561 | 2.7955 | 2.8414 | 1.7338 | 2.094 | 2.1191 | 2.1533 | 1.7338 | 1.9053 | 2.1618 | 2.1844 | 2.2143 | 2.3549
2021-12-16 19:00 | 2.2244 | 2.4602 | 2.4961 | 2.5401 | 2.5914 | 1.7338 | 2.0993 | 2.1273 | 2.1656 | 1.7338 | 2.0767 | 2.3576 | 2.3828 | 2.4162 | 2.5704
2021-12-16 20:00 | 2.4578 | 2.7206 | 2.7615 | 2.8116 | 2.87 | 1.7909 | 2.1739 | 2.2058 | 2.2494 | 1.7909 | 2.2101 | 2.5127 | 2.5414 | 2.5795 | 2.7465
2021-12-16 21:00 | 2.2681 | 2.5265 | 2.5723 | 2.6284 | 2.6939 | 1.7655 | 2.1509 | 2.1867 | 2.2355 | 1.7655 | 2.3054 | 2.6254 | 2.6576 | 2.7003 | 2.878
2021-12-16 22:00 | 2.0958 | 2.343 | 2.3897 | 2.4468 | 2.5135 | 1.6033 | 1.9604 | 1.9969 | 2.0466 | 1.6033 | 1.9815 | 2.2667 | 2.2994 | 2.3428 | 2.5038
2021-12-16 23:00 | 1.9624 | 2.1937 | 2.2374 | 2.2908 | 2.3531 | 1.338 | 1.6427 | 1.6767 | 1.7232 | 1.338 | 1.6766 | 1.9237 | 1.9543 | 1.9949 | 2.1357
2021-12-17 | 1.7719 | 1.9806 | 2.0199 | 2.0681 | 2.1242 | 1.2023 | 1.4762 | 1.5069 | 1.5488 | 1.2023 | 1.4861 | 1.706 | 1.7335 | 1.7702 | 1.8956
2021-12-17 01:00 | 1.6766 | 1.8688 | 1.9033 | 1.9456 | 1.9948 | 1.0521 | 1.2919 | 1.3189 | 1.3556 | 1.0521 | 1.4861 | 1.6993 | 1.7235 | 1.7556 | 1.8757
2021-12-17 02:00 | 1.6385 | 1.8183 | 1.8479 | 1.8842 | 1.9264 | 0.99227 | 1.2143 | 1.2374 | 1.269 | 0.99227 | 1.2765 | 1.4596 | 1.4804 | 1.5079 | 1.6111
2021-12-17 03:00 | 1.6195 | 1.7858 | 1.8092 | 1.8379 | 1.8714 | 0.95263 | 1.1587 | 1.177 | 1.202 | 0.95263 | 1.1813 | 1.3452 | 1.3616 | 1.3835 | 1.4745
2021-12-17 04:00 | 1.6385 | 1.7944 | 1.8118 | 1.8331 | 1.858 | 0.97833 | 1.1805 | 1.1941 | 1.2126 | 0.97833 | 1.3146 | 1.485 | 1.4972 | 1.5134 | 1.6051
2021-12-17 05:00 | 1.6576 | 1.8048 | 1.8171 | 1.8321 | 1.8496 | 1.1002 | 1.3172 | 1.3268 | 1.3398 | 1.1002 | 1.3337 | 1.4991 | 1.5077 | 1.5191 | 1.606
2021-12-17 06:00 | 1.8608 | 2.0192 | 2.0294 | 2.042 | 2.0566 | 1.2324 | 1.4704 | 1.4784 | 1.4893 | 1.2324 | 1.3337 | 1.4962 | 1.5034 | 1.5129 | 1.5977
2021-12-17 07:00 | 2.0196 | 2.1931 | 2.205 | 2.2196 | 2.2367 | 1.3908 | 1.66 | 1.6694 | 1.6821 | 1.3908 | 1.3908 | 1.5621 | 1.5705 | 1.5816 | 1.6713
2021-12-17 08:00 | 2.1339 | 2.325 | 2.3416 | 2.3619 | 2.3855 | 1.4289 | 1.7117 | 1.7246 | 1.7423 | 1.4289 | 1.5052 | 1.6956 | 1.7072 | 1.7227 | 1.8239
2021-12-17 09:00 | 2.0196 | 2.2155 | 2.2389 | 2.2675 | 2.3009 | 1.1681 | 1.4133 | 1.4315 | 1.4564 | 1.1681 | 1.1432 | 1.3028 | 1.3192 | 1.341 | 1.4299
2021-12-17 10:00 | 1.6766 | 1.8613 | 1.892 | 1.9295 | 1.9733 | 0.99073 | 1.214 | 1.238 | 1.2706 | 0.99073 | 1.3908 | 1.5881 | 1.6096 | 1.6382 | 1.7488
2021-12-17 11:00 | 1.3527 | 1.5243 | 1.5605 | 1.6049 | 1.6567 | 0.53347 | 0.68178 | 0.71007 | 0.74869 | 0.53347 | 1.7338 | 1.977 | 2.0024 | 2.0361 | 2.1718
2021-12-17 12:00 | 1.3527 | 1.5286 | 1.5671 | 1.6142 | 1.6691 | 0.53347 | 0.68494 | 0.71496 | 0.75594 | 0.53347 | 1.8862 | 2.1494 | 2.1764 | 2.2122 | 2.3587
2021-12-17 13:00 | 1.4289 | 1.6095 | 1.6474 | 1.6938 | 1.748 | 0.48087 | 0.62203 | 0.65163 | 0.69204 | 0.48087 | 1.7719 | 2.0216 | 2.0482 | 2.0836 | 2.2232
2021-12-17 14:00 | 1.6004 | 1.7887 | 1.8241 | 1.8674 | 1.9179 | 0.54944 | 0.69942 | 0.72703 | 0.76473 | 0.54944 | 1.8481 | 2.1028 | 2.1276 | 2.1606 | 2.3016
2021-12-17 15:00 | 1.8672 | 2.0698 | 2.1025 | 2.1424 | 2.189 | 0.74305 | 0.92421 | 0.94967 | 0.98443 | 0.74305 | 1.5433 | 1.7602 | 1.7831 | 1.8135 | 1.9346
2021-12-17 16:00 | 2.1148 | 2.3324 | 2.3632 | 2.4009 | 2.4448 | 1.162 | 1.4166 | 1.4406 | 1.4734 | 1.162 | 0.97168 | 1.1225 | 1.1441 | 1.1728 | 1.2605
2021-12-17 17:00 | 2.281 | 2.51 | 2.5403 | 2.5775 | 2.6208 | 1.5514 | 1.8759 | 1.8996 | 1.9319 | 1.5514 | 1.2384 | 1.4183 | 1.4396 | 1.4678 | 1.5697
2021-12-17 18:00 | 2.4768 | 2.7239 | 2.7561 | 2.7955 | 2.8414 | 1.8862 | 2.274 | 2.2991 | 2.3334 | 1.8862 | 2.0577 | 2.3312 | 2.3538 | 2.3837 | 2.5327
2021-12-17 19:00 | 2.3625 | 2.6085 | 2.6444 | 2.6884 | 2.7397 | 1.81 | 2.1893 | 2.2174 | 2.2556 | 1.81 | 2.1339 | 2.4211 | 2.4463 | 2.4798 | 2.6371
2021-12-17 20:00 | 2.3625 | 2.6182 | 2.6592 | 2.7092 | 2.7676 | 1.81 | 2.1964 | 2.2283 | 2.2719 | 1.81 | 2.1148 | 2.4069 | 2.4355 | 2.4736 | 2.6354
2021-12-17 21:00 | 2.2863 | 2.546 | 2.5919 | 2.648 | 2.7135 | 1.81 | 2.2035 | 2.2392 | 2.2881 | 1.81 | 2.1148 | 2.4137 | 2.4458 | 2.4885 | 2.6558
2021-12-17 22:00 | 2.2291 | 2.4863 | 2.533 | 2.5901 | 2.6567 | 1.6508 | 2.0166 | 2.053 | 2.1027 | 1.6508 | 2.3435 | 2.6689 | 2.7017 | 2.7451 | 2.9259
2021-12-17 23:00 | 2.0767 | 2.3166 | 2.3602 | 2.4136 | 2.4759 | 1.4478 | 1.7724 | 1.8064 | 1.8529 | 1.4478 | 1.829 | 2.0931 | 2.1237 | 2.1643 | 2.3134
2021-12-18 | 1.8929 | 2.1106 | 2.1499 | 2.1981 | 2.2542 | 1.2765 | 1.564 | 1.5946 | 1.6365 | 1.2765 | 1.6195 | 1.8542 | 1.8818 | 1.9184 | 2.0512
2021-12-18 01:00 | 1.7736 | 1.973 | 2.0076 | 2.0498 | 2.099 | 1.1813 | 1.4446 | 1.4715 | 1.5082 | 1.1813 | 1.6004 | 1.8263 | 1.8505 | 1.8826 | 2.009
2021-12-18 02:00 | 1.6585 | 1.8398 | 1.8694 | 1.9057 | 1.9479 | 1.0479 | 1.28 | 1.3031 | 1.3347 | 1.0479 | 1.2003 | 1.3749 | 1.3957 | 1.4233 | 1.5222
2021-12-18 03:00 | 1.6576 | 1.8267 | 1.8501 | 1.8788 | 1.9123 | 1.0098 | 1.2263 | 1.2445 | 1.2695 | 1.0098 | 1.3718 | 1.5569 | 1.5733 | 1.5952 | 1.6967
2021-12-18 04:00 | 1.6766 | 1.8353 | 1.8528 | 1.8741 | 1.8989 | 0.98713 | 1.1909 | 1.2045 | 1.223 | 0.98713 | 1.2384 | 1.4003 | 1.4125 | 1.4287 | 1.5162
2021-12-18 05:00 | 1.7147 | 1.8662 | 1.8785 | 1.8935 | 1.911 | 1.0099 | 1.2105 | 1.2201 | 1.2331 | 1.0099 | 1.2575 | 1.4144 | 1.423 | 1.4344 | 1.5172
2021-12-18 06:00 | 1.6766 | 1.8213 | 1.8315 | 1.8441 | 1.8587 | 1.0479 | 1.2525 | 1.2605 | 1.2714 | 1.0479 | 1.2765 | 1.4327 | 1.4399 | 1.4494 | 1.531
2021-12-18 07:00 | 1.7147 | 1.8656 | 1.8775 | 1.8921 | 1.9092 | 1.086 | 1.2999 | 1.3092 | 1.3219 | 1.086 | 1.1432 | 1.2869 | 1.2953 | 1.3064 | 1.3825
2021-12-18 08:00 | 1.5623 | 1.7109 | 1.7275 | 1.7478 | 1.7714 | 0.99073 | 1.194 | 1.2069 | 1.2246 | 0.99073 | 0.95263 | 1.0816 | 1.0932 | 1.1087 | 1.1795
2021-12-18 09:00 | 1.9243 | 2.1132 | 2.1366 | 2.1652 | 2.1986 | 1.2194 | 1.4738 | 1.492 | 1.5169 | 1.2194 | 1.1432 | 1.3028 | 1.3192 | 1.341 | 1.4299
2021-12-18 10:00 | 1.5242 | 1.6976 | 1.7282 | 1.7658 | 1.8096 | 0.99073 | 1.214 | 1.238 | 1.2706 | 0.99073 | 1.2194 | 1.3976 | 1.4191 | 1.4476 | 1.5488
2021-12-18 11:00 | 2.1148 | 2.343 | 2.3793 | 2.4237 | 2.4755 | 1.2956 | 1.5821 | 1.6104 | 1.649 | 1.2956 | 0.92817 | 1.0817 | 1.1071 | 1.1409 | 1.2323
2021-12-18 12:00 | 2.3625 | 2.6135 | 2.652 | 2.6991 | 2.754 | 1.5433 | 1.8779 | 1.9079 | 1.9489 | 1.5433 | 1.2384 | 1.4296 | 1.4565 | 1.4924 | 1.6033
2021-12-18 13:00 | 2.3244 | 2.5715 | 2.6094 | 2.6559 | 2.71 | 1.5623 | 1.8996 | 1.9292 | 1.9696 | 1.5623 | 1.448 | 1.6617 | 1.6883 | 1.7236 | 1.8455
2021-12-18 14:00 | 2.4387 | 2.6893 | 2.7247 | 2.768 | 2.8186 | 1.5359 | 1.8648 | 1.8924 | 1.9301 | 1.5359 | 1.5623 | 1.7852 | 1.81 | 1.843 | 1.9683
2021-12-18 15:00 | 2.3778 | 2.6184 | 2.6511 | 2.691 | 2.7376 | 1.6195 | 1.9596 | 1.985 | 2.0198 | 1.6195 | 2.0386 | 2.3107 | 2.3336 | 2.3639 | 2.5123
2021-12-18 16:00 | 2.8198 | 3.0897 | 3.1205 | 3.1582 | 3.2022 | 2.0767 | 2.4972 | 2.5212 | 2.554 | 2.0767 | 2.6102 | 2.9433 | 2.9649 | 2.9936 | 3.1714
2021-12-18 17:00 | 2.8579 | 3.1298 | 3.1601 | 3.1973 | 3.2407 | 2.3435 | 2.8116 | 2.8353 | 2.8677 | 2.3435 | 3.0103 | 3.3873 | 3.4086 | 3.4369 | 3.6362
2021-12-18 18:00 | 2.7817 | 3.0515 | 3.0836 | 3.123 | 3.1689 | 2.2673 | 2.7242 | 2.7493 | 2.7835 | 2.2673 | 2.9913 | 3.3687 | 3.3912 | 3.4212 | 3.6214
2021-12-18 19:00 | 2.5721 | 2.8337 | 2.8696 | 2.9136 | 2.9649 | 2.1371 | 2.5757 | 2.6038 | 2.642 | 2.1371 | 2.5721 | 2.9081 | 2.9333 | 2.9667 | 3.1481
2021-12-18 20:00 | 2.4768 | 2.7411 | 2.782 | 2.8321 | 2.8905 | 1.9815 | 2.399 | 2.4309 | 2.4745 | 1.9815 | 2.9341 | 3.3173 | 3.3459 | 3.384 | 3.5909
2021-12-18 21:00 | 2.4006 | 2.6689 | 2.7147 | 2.7708 | 2.8363 | 1.9053 | 2.316 | 2.3518 | 2.4006 | 1.9053 | 2.534 | 2.8795 | 2.9116 | 2.9543 | 3.1447
2021-12-18 22:00 | 2.1337 | 2.3838 | 2.4304 | 2.4876 | 2.5542 | 1.6385 | 2.0021 | 2.0385 | 2.0882 | 1.6385 | 2.4387 | 2.7748 | 2.8075 | 2.851 | 3.037
2021-12-18 23:00 | 2.0767 | 2.3166 | 2.3602 | 2.4136 | 2.4759 | 1.448 | 1.7727 | 1.8067 | 1.8532 | 1.448 | 1.7909 | 2.0507 | 2.0813 | 2.1219 | 2.269
2021-12-19 | 1.9434 | 2.1648 | 2.2042 | 2.2523 | 2.3084 | 1.3146 | 1.609 | 1.6397 | 1.6815 | 1.3146 | 1.5433 | 1.7695 | 1.7971 | 1.8337 | 1.9623
2021-12-19 01:00 | 1.7933 | 1.9942 | 2.0287 | 2.0709 | 2.1202 | 1.1549 | 1.4134 | 1.4404 | 1.4771 | 1.1549 | 1.4289 | 1.6358 | 1.66 | 1.6921 | 1.8091
2021-12-19 02:00 | 1.7361 | 1.9231 | 1.9528 | 1.989 | 2.0313 | 1.059 | 1.2932 | 1.3163 | 1.3478 | 1.059 | 1.2003 | 1.3749 | 1.3957 | 1.4233 | 1.5222
2021-12-19 03:00 | 1.6766 | 1.8472 | 1.8706 | 1.8993 | 1.9328 | 1.0069 | 1.2228 | 1.2411 | 1.2661 | 1.0069 | 1.2194 | 1.3875 | 1.404 | 1.4258 | 1.5189
2021-12-19 04:00 | 1.6957 | 1.8558 | 1.8732 | 1.8945 | 1.9194 | 1.001 | 1.2073 | 1.2209 | 1.2394 | 1.001 | 1.2575 | 1.4215 | 1.4337 | 1.4499 | 1.5384
2021-12-19 05:00 | 1.6766 | 1.8253 | 1.8375 | 1.8525 | 1.87 | 1.0098 | 1.2103 | 1.2199 | 1.233 | 1.0098 | 1.4099 | 1.5838 | 1.5923 | 1.6038 | 1.6949
2021-12-19 06:00 | 1.6385 | 1.7804 | 1.7906 | 1.8031 | 1.8177 | 1.086 | 1.2975 | 1.3055 | 1.3164 | 1.086 | 1.2003 | 1.348 | 1.3552 | 1.3647 | 1.4421
2021-12-19 07:00 | 1.6385 | 1.7837 | 1.7956 | 1.8102 | 1.8273 | 1.0669 | 1.2774 | 1.2867 | 1.2994 | 1.0669 | 1.2003 | 1.3504 | 1.3588 | 1.3699 | 1.4492
2021-12-19 08:00 | 1.6195 | 1.7723 | 1.7889 | 1.8092 | 1.8329 | 1.1622 | 1.3966 | 1.4095 | 1.4271 | 1.1622 | 1.0479 | 1.1875 | 1.1991 | 1.2145 | 1.2906
2021-12-19 09:00 | 1.9743 | 2.1669 | 2.1903 | 2.2189 | 2.2523 | 1.3923 | 1.678 | 1.6963 | 1.7212 | 1.3923 | 1.448 | 1.6415 | 1.6579 | 1.6797 | 1.7854
2021-12-19 10:00 | 2.0958 | 2.3116 | 2.3423 | 2.3799 | 2.4236 | 1.5242 | 1.8442 | 1.8682 | 1.9008 | 1.5242 | 1.6766 | 1.9057 | 1.9272 | 1.9558 | 2.0821
2021-12-19 11:00 | 2.1529 | 2.384 | 2.4202 | 2.4646 | 2.5164 | 1.5242 | 1.8522 | 1.8805 | 1.9191 | 1.5242 | 1.6957 | 1.9346 | 1.96 | 1.9938 | 2.1274
2021-12-19 12:00 | 1.9624 | 2.1836 | 2.2221 | 2.2692 | 2.3241 | 1.448 | 1.7653 | 1.7953 | 1.8363 | 1.448 | 1.4289 | 1.6413 | 1.6683 | 1.7041 | 1.8255
2021-12-19 13:00 | 2.1148 | 2.3463 | 2.3843 | 2.4307 | 2.4849 | 1.467 | 1.7871 | 1.8167 | 1.8571 | 1.467 | 1.5433 | 1.7676 | 1.7942 | 1.8295 | 1.9566
2021-12-19 14:00 | 2.0196 | 2.239 | 2.2744 | 2.3177 | 2.3683 | 1.4289 | 1.7384 | 1.766 | 1.8037 | 1.4289 | 1.6957 | 1.9334 | 1.9582 | 1.9912 | 2.1238
2021-12-19 15:00 | 2.1339 | 2.3564 | 2.389 | 2.429 | 2.4756 | 1.4829 | 1.7982 | 1.8236 | 1.8584 | 1.4829 | 1.9243 | 2.1837 | 2.2065 | 2.2369 | 2.379
2021-12-19 16:00 | 2.0958 | 2.3119 | 2.3427 | 2.3804 | 2.4244 | 1.4861 | 1.7994 | 1.8234 | 1.8562 | 1.4861 | 1.8672 | 2.1176 | 2.1392 | 2.1679 | 2.3048
2021-12-19 17:00 | 2.2673 | 2.4952 | 2.5256 | 2.5628 | 2.6061 | 1.6957 | 2.0464 | 2.0701 | 2.1024 | 1.6957 | 2.3244 | 2.6251 | 2.6464 | 2.6747 | 2.8363
2021-12-19 18:00 | 2.252 | 2.4824 | 2.5146 | 2.554 | 2.5999 | 1.6081 | 1.9455 | 1.9705 | 2.0048 | 1.6081 | 2.3435 | 2.6488 | 2.6714 | 2.7013 | 2.866
2021-12-19 19:00 | 2.3054 | 2.5471 | 2.583 | 2.627 | 2.6783 | 1.6957 | 2.0543 | 2.0823 | 2.1206 | 1.6957 | 2.7245 | 3.0775 | 3.1026 | 3.1361 | 3.3259
2021-12-19 20:00 | 2.4006 | 2.6592 | 2.7001 | 2.7502 | 2.8086 | 1.81 | 2.1964 | 2.2283 | 2.2719 | 1.81 | 2.172 | 2.4704 | 2.4991 | 2.5371 | 2.7021
2021-12-19 21:00 | 2.3816 | 2.6484 | 2.6942 | 2.7504 | 2.8158 | 1.718 | 2.0947 | 2.1305 | 2.1793 | 1.718 | 2.1148 | 2.4137 | 2.4458 | 2.4885 | 2.6558
2021-12-19 22:00 | 2.1859 | 2.4398 | 2.4865 | 2.5436 | 2.6103 | 1.5026 | 1.8415 | 1.8779 | 1.9276 | 1.5026 | 1.9053 | 2.182 | 2.2147 | 2.2582 | 2.4149
2021-12-19 23:00 | 2.0196 | 2.2552 | 2.2988 | 2.3522 | 2.4145 | 1.3688 | 1.6791 | 1.7131 | 1.7596 | 1.3688 | 1.9815 | 2.2624 | 2.293 | 2.3337 | 2.4912
2021-12-20 | 1.8481 | 2.0625 | 2.1018 | 2.15 | 2.2061 | 1.1934 | 1.4658 | 1.4964 | 1.5383 | 1.1934 | 1.448 | 1.6636 | 1.6912 | 1.7278 | 1.8512
2021-12-20 01:00 | 1.6957 | 1.8893 | 1.9238 | 1.966 | 2.0153 | 1.0669 | 1.3095 | 1.3364 | 1.3732 | 1.0669 | 1.3718 | 1.5723 | 1.5964 | 1.6286 | 1.7424
2021-12-20 02:00 | 1.6576 | 1.8388 | 1.8684 | 1.9046 | 1.9469 | 1.0098 | 1.235 | 1.2581 | 1.2897 | 1.0098 | 1.2956 | 1.4808 | 1.5015 | 1.5291 | 1.6333
2021-12-20 03:00 | 1.6004 | 1.7653 | 1.7887 | 1.8174 | 1.8509 | 0.97168 | 1.1812 | 1.1995 | 1.2245 | 0.97168 | 1.3146 | 1.4934 | 1.5098 | 1.5317 | 1.63
2021-12-20 04:00 | 1.6505 | 1.8073 | 1.8247 | 1.846 | 1.8708 | 0.971 | 1.1719 | 1.1854 | 1.204 | 0.971 | 1.1622 | 1.3157 | 1.3278 | 1.3441 | 1.4273
2021-12-20 05:00 | 1.6576 | 1.8048 | 1.8171 | 1.8321 | 1.8496 | 1.0576 | 1.2669 | 1.2764 | 1.2895 | 1.0576 | 1.2575 | 1.4144 | 1.423 | 1.4344 | 1.5172
2021-12-20 06:00 | 1.6766 | 1.8213 | 1.8315 | 1.8441 | 1.8587 | 1.1241 | 1.3425 | 1.3505 | 1.3614 | 1.1241 | 1.1813 | 1.3269 | 1.334 | 1.3436 | 1.4199
2021-12-20 07:00 | 1.81 | 1.9679 | 1.9799 | 1.9945 | 2.0115 | 1.2194 | 1.4575 | 1.4668 | 1.4795 | 1.2194 | 1.1813 | 1.3292 | 1.3376 | 1.3487 | 1.4269
2021-12-20 08:00 | 1.7338 | 1.8951 | 1.9117 | 1.932 | 1.9557 | 1.1432 | 1.374 | 1.387 | 1.4046 | 1.1432 | 0.99073 | 1.124 | 1.1356 | 1.151 | 1.2239
2021-12-20 09:00 | 1.4861 | 1.6424 | 1.6658 | 1.6944 | 1.7278 | 0.78115 | 0.95609 | 0.97434 | 0.99926 | 0.78115 | 1.3527 | 1.5357 | 1.5521 | 1.5739 | 1.6743
2021-12-20 10:00 | 1.2575 | 1.411 | 1.4417 | 1.4792 | 1.523 | 0.57158 | 0.71885 | 0.74278 | 0.77545 | 0.57158 | 1.4861 | 1.694 | 1.7155 | 1.744 | 1.8599
2021-12-20 11:00 | 1.1549 | 1.3118 | 1.3481 | 1.3924 | 1.4442 | 0.51442 | 0.65928 | 0.68756 | 0.72618 | 0.51442 | 1.8672 | 2.1252 | 2.1506 | 2.1843 | 2.3274
2021-12-20 12:00 | 1.2194 | 1.3853 | 1.4238 | 1.4709 | 1.5259 | 0.51442 | 0.66243 | 0.69245 | 0.73343 | 0.51442 | 1.8862 | 2.1494 | 2.1764 | 2.2122 | 2.3587
2021-12-20 13:00 | 1.2194 | 1.3843 | 1.4222 | 1.4687 | 1.5228 | 0.43821 | 0.57164 | 0.60123 | 0.64165 | 0.43821 | 1.8672 | 2.1275 | 2.1541 | 2.1894 | 2.3343
2021-12-20 14:00 | 1.2765 | 1.4407 | 1.4761 | 1.5194 | 1.57 | 0.51442 | 0.65805 | 0.68566 | 0.72336 | 0.51442 | 1.8481 | 2.1028 | 2.1276 | 2.1606 | 2.3016
2021-12-20 15:00 | 1.5411 | 1.7195 | 1.7522 | 1.7921 | 1.8387 | 0.62873 | 0.78917 | 0.81462 | 0.84938 | 0.62873 | 1.9624 | 2.226 | 2.2489 | 2.2793 | 2.4235
2021-12-20 16:00 | 1.7719 | 1.9639 | 1.9947 | 2.0324 | 2.0764 | 0.79089 | 0.97813 | 1.0022 | 1.035 | 0.79089 | 1.086 | 1.2495 | 1.2711 | 1.2998 | 1.3938
2021-12-20 17:00 | 2.0577 | 2.2701 | 2.3005 | 2.3376 | 2.381 | 1.2637 | 1.5361 | 1.5598 | 1.5921 | 1.2637 | 0.97168 | 1.1219 | 1.1432 | 1.1714 | 1.2587
2021-12-20 18:00 | 2.3054 | 2.5397 | 2.5719 | 2.6113 | 2.6572 | 1.5623 | 1.8914 | 1.9165 | 1.9508 | 1.5623 | 1.6004 | 1.8231 | 1.8456 | 1.8756 | 1.9994
2021-12-20 19:00 | 2.3054 | 2.5471 | 2.583 | 2.627 | 2.6783 | 1.6385 | 1.9868 | 2.0148 | 2.0531 | 1.6385 | 2.3054 | 2.6117 | 2.6369 | 2.6703 | 2.837
2021-12-20 20:00 | 2.2482 | 2.4954 | 2.5363 | 2.5864 | 2.6448 | 1.7147 | 2.0839 | 2.1158 | 2.1594 | 1.7147 | 2.4197 | 2.7456 | 2.7743 | 2.8124 | 2.9909
2021-12-20 21:00 | 2.2101 | 2.4642 | 2.51 | 2.5662 | 2.6316 | 1.6197 | 1.9786 | 2.0144 | 2.0632 | 1.6197 | 2.2291 | 2.5408 | 2.5729 | 2.6156 | 2.7892
2021-12-20 22:00 | 2.2101 | 2.4658 | 2.5125 | 2.5696 | 2.6363 | 1.6195 | 1.9796 | 2.016 | 2.0657 | 1.6195 | 1.8862 | 2.1608 | 2.1935 | 2.237 | 2.3927
2021-12-20 23:00 | 1.9624 | 2.1937 | 2.2374 | 2.2908 | 2.3531 | 1.295 | 1.5919 | 1.6259 | 1.6724 | 1.295 | 1.6385 | 1.8813 | 1.9119 | 1.9526 | 2.0912
2021-12-21 | 1.735 | 1.941 | 1.9803 | 2.0285 | 2.0846 | 1.1579 | 1.4239 | 1.4545 | 1.4964 | 1.1579 | 1.448 | 1.6636 | 1.6912 | 1.7278 | 1.8512
2021-12-21 01:00 | 1.7147 | 1.9098 | 1.9443 | 1.9865 | 2.0358 | 1.086 | 1.332 | 1.3589 | 1.3957 | 1.086 | 1.3718 | 1.5723 | 1.5964 | 1.6286 | 1.7424
2021-12-21 02:00 | 1.6195 | 1.7978 | 1.8275 | 1.8637 | 1.906 | 0.99073 | 1.2125 | 1.2356 | 1.2672 | 0.99073 | 1.1813 | 1.3538 | 1.3745 | 1.4021 | 1.5
2021-12-21 03:00 | 1.6195 | 1.7858 | 1.8092 | 1.8379 | 1.8714 | 0.97168 | 1.1812 | 1.1995 | 1.2245 | 0.97168 | 1.2956 | 1.4722 | 1.4887 | 1.5105 | 1.6078
2021-12-21 04:00 | 1.5623 | 1.7125 | 1.7299 | 1.7512 | 1.7761 | 0.97168 | 1.1727 | 1.1862 | 1.2048 | 0.97168 | 1.2956 | 1.4639 | 1.4761 | 1.4923 | 1.5829
2021-12-21 05:00 | 1.6195 | 1.7639 | 1.7761 | 1.7911 | 1.8086 | 1.0288 | 1.2329 | 1.2424 | 1.2555 | 1.0288 | 1.2194 | 1.372 | 1.3806 | 1.392 | 1.4727
2021-12-21 06:00 | 1.6281 | 1.7692 | 1.7794 | 1.792 | 1.8066 | 1.105 | 1.32 | 1.328 | 1.3389 | 1.105 | 1.2575 | 1.4116 | 1.4187 | 1.4283 | 1.5088
2021-12-21 07:00 | 1.7338 | 1.886 | 1.898 | 1.9126 | 1.9296 | 1.1241 | 1.3449 | 1.3542 | 1.367 | 1.1241 | 1.1432 | 1.2869 | 1.2953 | 1.3064 | 1.3825
2021-12-21 08:00 | 1.6004 | 1.7518 | 1.7684 | 1.7887 | 1.8124 | 0.99073 | 1.194 | 1.2069 | 1.2246 | 0.99073 | 0.97168 | 1.1028 | 1.1144 | 1.1298 | 1.2017
2021-12-21 09:00 | 1.467 | 1.6219 | 1.6453 | 1.6739 | 1.7073 | 0.78115 | 0.95609 | 0.97434 | 0.99926 | 0.78115 | 1.1813 | 1.3451 | 1.3615 | 1.3833 | 1.4743
2021-12-21 10:00 | 1.3718 | 1.5338 | 1.5645 | 1.602 | 1.6458 | 0.60281 | 0.75575 | 0.77968 | 0.81235 | 0.60281 | 1.6957 | 1.9269 | 1.9484 | 1.9769 | 2.1043
2021-12-21 11:00 | 1.3337 | 1.5038 | 1.5401 | 1.5845 | 1.6362 | 0.53347 | 0.68178 | 0.71007 | 0.74869 | 0.53347 | 1.6576 | 1.8923 | 1.9177 | 1.9514 | 2.0829
2021-12-21 12:00 | 1.3908 | 1.5696 | 1.608 | 1.6552 | 1.7101 | 0.53347 | 0.68494 | 0.71496 | 0.75594 | 0.53347 | 1.6004 | 1.8318 | 1.8588 | 1.8946 | 2.0255
2021-12-21 13:00 | 1.467 | 1.6504 | 1.6883 | 1.7348 | 1.7889 | 0.53014 | 0.68024 | 0.70984 | 0.75025 | 0.53014 | 1.6576 | 1.8946 | 1.9212 | 1.9565 | 2.0899
2021-12-21 14:00 | 1.5814 | 1.7682 | 1.8036 | 1.8469 | 1.8975 | 0.60968 | 0.77059 | 0.7982 | 0.8359 | 0.60968 | 1.5623 | 1.7852 | 1.81 | 1.843 | 1.9683
2021-12-21 15:00 | 1.8862 | 2.0903 | 2.123 | 2.1629 | 2.2095 | 0.82037 | 1.0156 | 1.041 | 1.0758 | 0.82037 | 1.1622 | 1.3368 | 1.3596 | 1.39 | 1.4902
2021-12-21 16:00 | 2.1148 | 2.3324 | 2.3632 | 2.4009 | 2.4448 | 1.1066 | 1.351 | 1.3751 | 1.4079 | 1.1066 | 0.62873 | 0.7414 | 0.76299 | 0.79166 | 0.86052
2021-12-21 17:00 | 2.405 | 2.6432 | 2.6736 | 2.7108 | 2.7541 | 1.5122 | 1.8297 | 1.8533 | 1.8857 | 1.5122 | 1.3527 | 1.5453 | 1.5666 | 1.5949 | 1.7031
2021-12-21 18:00 | 2.6483 | 2.9082 | 2.9403 | 2.9797 | 3.0256 | 1.8672 | 2.2515 | 2.2766 | 2.3109 | 1.8672 | 2.1339 | 2.4159 | 2.4385 | 2.4684 | 2.6215
2021-12-21 19:00 | 2.6483 | 2.9155 | 2.9515 | 2.9954 | 3.0467 | 1.8672 | 2.2569 | 2.2849 | 2.3232 | 1.8672 | 2.6864 | 3.0351 | 3.0603 | 3.0938 | 3.2814
2021-12-21 20:00 | 2.4578 | 2.7206 | 2.7615 | 2.8116 | 2.87 | 1.8481 | 2.2414 | 2.2734 | 2.3169 | 1.8481 | 2.3054 | 2.6186 | 2.6473 | 2.6853 | 2.8576
2021-12-21 21:00 | 2.434 | 2.7047 | 2.7506 | 2.8067 | 2.8722 | 1.7909 | 2.1809 | 2.2167 | 2.2655 | 1.7909 | 2.4197 | 2.7525 | 2.7846 | 2.8273 | 3.0114
2021-12-21 22:00 | 2.2291 | 2.4863 | 2.533 | 2.5901 | 2.6567 | 1.6705 | 2.0399 | 2.0763 | 2.126 | 1.6705 | 2.3435 | 2.6689 | 2.7017 | 2.7451 | 2.9259
2021-12-21 23:00 | 1.9815 | 2.2142 | 2.2579 | 2.3113 | 2.3736 | 1.3916 | 1.706 | 1.7401 | 1.7865 | 1.3916 | 2.2482 | 2.5589 | 2.5894 | 2.6301 | 2.8023
2021-12-22 | 1.8189 | 2.0311 | 2.0705 | 2.1186 | 2.1748 | 1.1622 | 1.4289 | 1.4596 | 1.5015 | 1.1622 | 1.6766 | 1.9177 | 1.9453 | 1.9819 | 2.1178
2021-12-22 01:00 | 1.7 | 1.8939 | 1.9284 | 1.9707 | 2.0199 | 1.0919 | 1.339 | 1.3659 | 1.4027 | 1.0919 | 1.2765 | 1.4664 | 1.4906 | 1.5227 | 1.6313
2021-12-22 02:00 | 1.6004 | 1.7774 | 1.807 | 1.8432 | 1.8855 | 1.0098 | 1.235 | 1.2581 | 1.2897 | 1.0098 | 1.1813 | 1.3538 | 1.3745 | 1.4021 | 1.5
2021-12-22 03:00 | 1.6195 | 1.7858 | 1.8092 | 1.8379 | 1.8714 | 0.99073 | 1.2037 | 1.222 | 1.247 | 0.99073 | 1.2003 | 1.3664 | 1.3828 | 1.4046 | 1.4967
2021-12-22 04:00 | 1.5814 | 1.733 | 1.7504 | 1.7717 | 1.7966 | 0.97168 | 1.1727 | 1.1862 | 1.2048 | 0.97168 | 1.2765 | 1.4427 | 1.4549 | 1.4711 | 1.5606
2021-12-22 05:00 | 1.6195 | 1.7639 | 1.7761 | 1.7911 | 1.8086 | 1.0303 | 1.2346 | 1.2442 | 1.2573 | 1.0303 | 1.3527 | 1.5202 | 1.5288 | 1.5402 | 1.6282
2021-12-22 06:00 | 1.6453 | 1.7876 | 1.7978 | 1.8104 | 1.825 | 1.1432 | 1.365 | 1.373 | 1.3839 | 1.1432 | 1.3718 | 1.5386 | 1.5458 | 1.5553 | 1.6421
2021-12-22 07:00 | 1.7528 | 1.9065 | 1.9184 | 1.9331 | 1.9501 | 1.1432 | 1.3674 | 1.3768 | 1.3895 | 1.1432 | 1.2194 | 1.3716 | 1.3799 | 1.3911 | 1.4714
2021-12-22 08:00 | 1.6766 | 1.8337 | 1.8503 | 1.8706 | 1.8943 | 1.1241 | 1.3515 | 1.3645 | 1.3821 | 1.1241 | 0.95263 | 1.0816 | 1.0932 | 1.1087 | 1.1795
2021-12-22 09:00 | 1.6385 | 1.8061 | 1.8295 | 1.8582 | 1.8916 | 0.87642 | 1.0686 | 1.0869 | 1.1118 | 0.87642 | 1.0479 | 1.1969 | 1.2133 | 1.2351 | 1.3188
2021-12-22 10:00 | 1.6195 | 1.7999 | 1.8306 | 1.8681 | 1.9119 | 0.7621 | 0.94393 | 0.96786 | 1.0005 | 0.7621 | 1.3527 | 1.5458 | 1.5673 | 1.5958 | 1.7043
2021-12-22 11:00 | 1.5052 | 1.688 | 1.7243 | 1.7687 | 1.8204 | 0.60968 | 0.77182 | 0.8001 | 0.83872 | 0.60968 | 1.3718 | 1.5747 | 1.6001 | 1.6339 | 1.7496
2021-12-22 12:00 | 1.7528 | 1.9585 | 1.997 | 2.0441 | 2.099 | 0.64779 | 0.81999 | 0.85 | 0.89099 | 0.64779 | 1.3718 | 1.5778 | 1.6047 | 1.6406 | 1.7588
2021-12-22 13:00 | 1.8672 | 2.0802 | 2.1182 | 2.1646 | 2.2188 | 0.66303 | 0.83723 | 0.86683 | 0.90724 | 0.66303 | 1.2575 | 1.45 | 1.4766 | 1.5119 | 1.6233
2021-12-22 14:00 | 1.8672 | 2.0753 | 2.1107 | 2.154 | 2.2045 | 0.7621 | 0.95065 | 0.97826 | 1.016 | 0.7621 | 1.0288 | 1.1924 | 1.2172 | 1.2502 | 1.3461
2021-12-22 15:00 | 2.4387 | 2.6839 | 2.7166 | 2.7565 | 2.8031 | 1.086 | 1.3294 | 1.3548 | 1.3896 | 1.086 | 0.60968 | 0.72277 | 0.74564 | 0.77602 | 0.84587
2021-12-22 16:00 | 2.5721 | 2.8236 | 2.8544 | 2.8921 | 2.9361 | 1.467 | 1.7769 | 1.8009 | 1.8337 | 1.467 | 1.467 | 1.673 | 1.6946 | 1.7232 | 1.8382
2021-12-22 17:00 | 2.6483 | 2.9046 | 2.935 | 2.9722 | 3.0155 | 1.7895 | 2.1572 | 2.1809 | 2.2132 | 1.7895 | 2.1339 | 2.4134 | 2.4347 | 2.4629 | 2.6141
2021-12-22 18:00 | 2.915 | 3.1947 | 3.2269 | 3.2663 | 3.3122 | 1.9624 | 2.3641 | 2.3892 | 2.4234 | 1.9624 | 2.4387 | 2.7547 | 2.7772 | 2.8072 | 2.9771
2021-12-22 19:00 | 2.5721 | 2.8337 | 2.8696 | 2.9136 | 2.9649 | 1.9112 | 2.3089 | 2.3369 | 2.3752 | 1.9112 | 2.8579 | 3.2257 | 3.2509 | 3.2843 | 3.4814
2021-12-22 20:00 | 2.3625 | 2.6182 | 2.6592 | 2.7092 | 2.7676 | 1.829 | 2.2189 | 2.2508 | 2.2944 | 1.829 | 2.2482 | 2.5551 | 2.5837 | 2.6218 | 2.791
2021-12-22 21:00 | 2.3435 | 2.6074 | 2.6533 | 2.7094 | 2.7749 | 1.7147 | 2.0909 | 2.1267 | 2.1755 | 1.7147 | 2.6864 | 3.0489 | 3.081 | 3.1237 | 3.3224
2021-12-22 22:00 | 2.172 | 2.4249 | 2.4715 | 2.5287 | 2.5953 | 1.5623 | 1.912 | 1.9485 | 1.9982 | 1.5623 | 2.1529 | 2.4572 | 2.4899 | 2.5334 | 2.7037
2021-12-22 23:00 | 2.0045 | 2.2389 | 2.2826 | 2.336 | 2.3983 | 1.4089 | 1.7265 | 1.7606 | 1.807 | 1.4089 | 1.7338 | 1.9872 | 2.0178 | 2.0584 | 2.2023
2021-12-23 | 1.8143 | 2.0262 | 2.0655 | 2.1136 | 2.1698 | 1.2377 | 1.5181 | 1.5488 | 1.5906 | 1.2377 | 1.6195 | 1.8542 | 1.8818 | 1.9184 | 2.0512
2021-12-23 01:00 | 1.6766 | 1.8688 | 1.9033 | 1.9456 | 1.9948 | 1.1241 | 1.377 | 1.4039 | 1.4407 | 1.1241 | 1.3718 | 1.5723 | 1.5964 | 1.6286 | 1.7424
2021-12-23 02:00 | 1.6576 | 1.8388 | 1.8684 | 1.9046 | 1.9469 | 1.0224 | 1.2499 | 1.273 | 1.3045 | 1.0224 | 1.2384 | 1.4173 | 1.438 | 1.4656 | 1.5666
2021-12-23 03:00 | 1.5814 | 1.7448 | 1.7683 | 1.797 | 1.8304 | 0.99073 | 1.2037 | 1.222 | 1.247 | 0.99073 | 1.3908 | 1.5781 | 1.5945 | 1.6163 | 1.7189
2021-12-23 04:00 | 1.5814 | 1.733 | 1.7504 | 1.7717 | 1.7966 | 0.98363 | 1.1868 | 1.2003 | 1.2189 | 0.98363 | 1.3908 | 1.5697 | 1.5819 | 1.5981 | 1.694
2021-12-23 05:00 | 1.6385 | 1.7843 | 1.7966 | 1.8116 | 1.8291 | 1.0288 | 1.2329 | 1.2424 | 1.2555 | 1.0288 | 1.2765 | 1.4355 | 1.4441 | 1.4555 | 1.5394
2021-12-23 06:00 | 1.7264 | 1.8748 | 1.885 | 1.8976 | 1.9122 | 1.105 | 1.32 | 1.328 | 1.3389 | 1.105 | 1.3146 | 1.4751 | 1.4822 | 1.4918 | 1.5754
2021-12-23 07:00 | 1.8862 | 2.0498 | 2.0617 | 2.0763 | 2.0934 | 1.1845 | 1.4163 | 1.4256 | 1.4383 | 1.1845 | 1.2765 | 1.4351 | 1.4435 | 1.4546 | 1.538
2021-12-23 08:00 | 1.9624 | 2.1408 | 2.1573 | 2.1776 | 2.2013 | 1.2956 | 1.5541 | 1.567 | 1.5847 | 1.2956 | 1.3908 | 1.5686 | 1.5802 | 1.5956 | 1.6905
2021-12-23 09:00 | 1.8672 | 2.0518 | 2.0752 | 2.1038 | 2.1372 | 1.1622 | 1.4062 | 1.4245 | 1.4494 | 1.1622 | 1.0098 | 1.1546 | 1.171 | 1.1928 | 1.2743
2021-12-23 10:00 | 1.8848 | 2.0849 | 2.1156 | 2.1531 | 2.1969 | 1.0669 | 1.3041 | 1.328 | 1.3607 | 1.0669 | 1.1622 | 1.3341 | 1.3555 | 1.3841 | 1.4821
2021-12-23 11:00 | 1.9624 | 2.1793 | 2.2156 | 2.2599 | 2.3117 | 1.0501 | 1.2921 | 1.3203 | 1.359 | 1.0501 | 1.2765 | 1.4688 | 1.4942 | 1.528 | 1.6386
2021-12-23 12:00 | 1.6766 | 1.8766 | 1.9151 | 1.9622 | 2.0171 | 0.66564 | 0.84107 | 0.87109 | 0.91207 | 0.66564 | 1.3908 | 1.5989 | 1.6259 | 1.6617 | 1.781
2021-12-23 13:00 | 1.7719 | 1.9779 | 2.0158 | 2.0623 | 2.1164 | 0.724 | 0.90925 | 0.93885 | 0.97926 | 0.724 | 1.2003 | 1.3865 | 1.4131 | 1.4484 | 1.5566
2021-12-23 14:00 | 1.81 | 2.0138 | 2.0492 | 2.0926 | 2.1431 | 0.74305 | 0.92814 | 0.95575 | 0.99345 | 0.74305 | 1.0098 | 1.1712 | 1.196 | 1.229 | 1.3239
2021-12-23 15:00 | 2.0386 | 2.2541 | 2.2867 | 2.3266 | 2.3732 | 1.105 | 1.3519 | 1.3773 | 1.4121 | 1.105 | 0.68589 | 0.80746 | 0.83033 | 0.86071 | 0.93475
2021-12-23 16:00 | 2.1677 | 2.3891 | 2.4199 | 2.4576 | 2.5016 | 1.5242 | 1.8444 | 1.8685 | 1.9013 | 1.5242 | 0.86826 | 1.0076 | 1.0292 | 1.0578 | 1.1399
2021-12-23 17:00 | 2.6483 | 2.9046 | 2.935 | 2.9722 | 3.0155 | 1.9053 | 2.294 | 2.3176 | 2.35 | 1.9053 | 2.4387 | 2.7522 | 2.7734 | 2.8017 | 2.9696
2021-12-23 18:00 | 2.6674 | 2.9286 | 2.9608 | 3.0002 | 3.0461 | 2.0577 | 2.4766 | 2.5017 | 2.536 | 2.0577 | 2.3244 | 2.6276 | 2.6502 | 2.6801 | 2.8437
2021-12-23 19:00 | 2.5911 | 2.8541 | 2.8901 | 2.934 | 2.9853 | 1.9624 | 2.3694 | 2.3974 | 2.4357 | 1.9624 | 2.4768 | 2.8022 | 2.8274 | 2.8609 | 3.037
2021-12-23 20:00 | 2.3435 | 2.5978 | 2.6387 | 2.6888 | 2.7472 | 1.81 | 2.1964 | 2.2283 | 2.2719 | 1.81 | 2.3244 | 2.6398 | 2.6684 | 2.7065 | 2.8799
2021-12-23 21:00 | 2.3435 | 2.6074 | 2.6533 | 2.7094 | 2.7749 | 1.7458 | 2.1276 | 2.1633 | 2.2122 | 1.7458 | 2.4197 | 2.7525 | 2.7846 | 2.8273 | 3.0114
2021-12-23 22:00 | 2.2101 | 2.4658 | 2.5125 | 2.5696 | 2.6363 | 1.6004 | 1.9571 | 1.9935 | 2.0432 | 1.6004 | 2.3816 | 2.7113 | 2.744 | 2.7875 | 2.9704
2021-12-23 23:00 | 2.0767 | 2.3166 | 2.3602 | 2.4136 | 2.4759 | 1.3985 | 1.7142 | 1.7482 | 1.7947 | 1.3985 | 2.0577 | 2.3471 | 2.3777 | 2.4184 | 2.5801
2021-12-24 | 1.8776 | 2.0942 | 2.1335 | 2.1817 | 2.2378 | 1.2441 | 1.5257 | 1.5564 | 1.5983 | 1.2441 | 1.5814 | 1.8118 | 1.8394 | 1.876 | 2.0067
2021-12-24 01:00 | 1.7168 | 1.9119 | 1.9465 | 1.9887 | 2.0379 | 1.097 | 1.345 | 1.3719 | 1.4087 | 1.097 | 1.3146 | 1.5087 | 1.5329 | 1.565 | 1.6757
2021-12-24 02:00 | 1.6195 | 1.7978 | 1.8275 | 1.8637 | 1.906 | 1.0288 | 1.2575 | 1.2806 | 1.3122 | 1.0288 | 1.2194 | 1.3961 | 1.4169 | 1.4444 | 1.5444
2021-12-24 03:00 | 1.6195 | 1.7858 | 1.8092 | 1.8379 | 1.8714 | 0.99073 | 1.2037 | 1.222 | 1.247 | 0.99073 | 1.1813 | 1.3452 | 1.3616 | 1.3835 | 1.4745
2021-12-24 04:00 | 1.6195 | 1.7739 | 1.7913 | 1.8127 | 1.8375 | 0.99073 | 1.1952 | 1.2087 | 1.2273 | 0.99073 | 1.2003 | 1.358 | 1.3702 | 1.3864 | 1.4718
2021-12-24 05:00 | 1.6195 | 1.7639 | 1.7761 | 1.7911 | 1.8086 | 1.0479 | 1.2554 | 1.2649 | 1.278 | 1.0479 | 1.2003 | 1.3509 | 1.3594 | 1.3709 | 1.4505
2021-12-24 06:00 | 1.6957 | 1.8418 | 1.852 | 1.8645 | 1.8791 | 1.086 | 1.2975 | 1.3055 | 1.3164 | 1.086 | 1.2956 | 1.4539 | 1.4611 | 1.4706 | 1.5532
2021-12-24 07:00 | 1.829 | 1.9884 | 2.0003 | 2.0149 | 2.032 | 1.2003 | 1.435 | 1.4443 | 1.457 | 1.2003 | 1.3146 | 1.4774 | 1.4858 | 1.4969 | 1.5825
2021-12-24 08:00 | 1.7147 | 1.8747 | 1.8912 | 1.9115 | 1.9352 | 1.1651 | 1.4 | 1.4129 | 1.4306 | 1.1651 | 1.1622 | 1.3145 | 1.3261 | 1.3416 | 1.4239
2021-12-24 09:00 | 1.8481 | 2.0313 | 2.0547 | 2.0833 | 2.1167 | 1.105 | 1.3387 | 1.357 | 1.3819 | 1.105 | 0.97168 | 1.1122 | 1.1286 | 1.1504 | 1.2299
2021-12-24 10:00 | 1.9815 | 2.1888 | 2.2195 | 2.257 | 2.3008 | 1.2384 | 1.5066 | 1.5306 | 1.5632 | 1.2384 | 1.086 | 1.2494 | 1.2709 | 1.2994 | 1.3933
2021-12-24 11:00 | 1.9815 | 2.1998 | 2.236 | 2.2804 | 2.3322 | 1.0479 | 1.2895 | 1.3178 | 1.3564 | 1.0479 | 1.3337 | 1.5324 | 1.5578 | 1.5915 | 1.7052
2021-12-24 12:00 | 1.7528 | 1.9585 | 1.997 | 2.0441 | 2.099 | 1.0479 | 1.2927 | 1.3227 | 1.3637 | 1.0479 | 1.1432 | 1.3237 | 1.3507 | 1.3865 | 1.4922
2021-12-24 13:00 | 1.5242 | 1.7118 | 1.7497 | 1.7962 | 1.8503 | 0.80021 | 0.99929 | 1.0289 | 1.0693 | 0.80021 | 1.0669 | 1.2383 | 1.2649 | 1.3002 | 1.4011
2021-12-24 14:00 | 1.9434 | 2.1571 | 2.1925 | 2.2359 | 2.2864 | 1.0669 | 1.3108 | 1.3384 | 1.3761 | 1.0669 | 1.5242 | 1.7429 | 1.7677 | 1.8006 | 1.9238
2021-12-24 15:00 | 1.81 | 2.0084 | 2.0411 | 2.081 | 2.1276 | 1.1622 | 1.4194 | 1.4448 | 1.4796 | 1.1622 | 1.6004 | 1.8237 | 1.8466 | 1.877 | 2.0013
2021-12-24 16:00 | 2.0958 | 2.3119 | 2.3427 | 2.3804 | 2.4244 | 1.448 | 1.7544 | 1.7784 | 1.8112 | 1.448 | 0.99073 | 1.1437 | 1.1653 | 1.1939 | 1.2827
2021-12-24 17:00 | 2.4387 | 2.6795 | 2.7098 | 2.747 | 2.7903 | 1.8672 | 2.2489 | 2.2726 | 2.305 | 1.8672 | 1.8862 | 2.1382 | 2.1594 | 2.1877 | 2.3252
2021-12-24 18:00 | 2.6293 | 2.8877 | 2.9199 | 2.9593 | 3.0052 | 2.0386 | 2.4541 | 2.4792 | 2.5135 | 2.0386 | 2.7245 | 3.0723 | 3.0948 | 3.1248 | 3.3103
2021-12-24 19:00 | 2.534 | 2.7927 | 2.8286 | 2.8726 | 2.9239 | 1.9987 | 2.4123 | 2.4403 | 2.4786 | 1.9987 | 2.8769 | 3.2468 | 3.272 | 3.3055 | 3.5036
2021-12-24 20:00 | 2.3625 | 2.6182 | 2.6592 | 2.7092 | 2.7676 | 1.81 | 2.1964 | 2.2283 | 2.2719 | 1.81 | 2.4959 | 2.8303 | 2.859 | 2.8971 | 3.0798
2021-12-24 21:00 | 2.4006 | 2.6689 | 2.7147 | 2.7708 | 2.8363 | 1.7909 | 2.1809 | 2.2167 | 2.2655 | 1.7909 | 2.2673 | 2.5831 | 2.6152 | 2.6579 | 2.8336
2021-12-24 22:00 | 2.2673 | 2.5272 | 2.5739 | 2.631 | 2.6977 | 1.5759 | 1.9281 | 1.9645 | 2.0142 | 1.5759 | 2.7626 | 3.1347 | 3.1674 | 3.2109 | 3.4148
2021-12-24 23:00 | 2.0196 | 2.2552 | 2.2988 | 2.3522 | 2.4145 | 1.467 | 1.7952 | 1.8292 | 1.8757 | 1.467 | 1.9815 | 2.2624 | 2.293 | 2.3337 | 2.4912
2021-12-25 | 1.9053 | 2.1239 | 2.1632 | 2.2114 | 2.2675 | 1.3062 | 1.599 | 1.6297 | 1.6716 | 1.3062 | 1.6576 | 1.8965 | 1.9241 | 1.9607 | 2.0956
2021-12-25 01:00 | 1.7563 | 1.9544 | 1.9889 | 2.0312 | 2.0804 | 1.1494 | 1.4069 | 1.4338 | 1.4705 | 1.1494 | 1.3908 | 1.5934 | 1.6176 | 1.6497 | 1.7646
2021-12-25 02:00 | 1.6766 | 1.8592 | 1.8889 | 1.9251 | 1.9674 | 1.0479 | 1.28 | 1.3031 | 1.3347 | 1.0479 | 1.3146 | 1.502 | 1.5227 | 1.5503 | 1.6555
2021-12-25 03:00 | 1.6195 | 1.7858 | 1.8092 | 1.8379 | 1.8714 | 1.0098 | 1.2263 | 1.2445 | 1.2695 | 1.0098 | 1.3146 | 1.4934 | 1.5098 | 1.5317 | 1.63
2021-12-25 04:00 | 1.6576 | 1.8149 | 1.8323 | 1.8536 | 1.8784 | 0.9974 | 1.203 | 1.2166 | 1.2352 | 0.9974 | 1.3146 | 1.485 | 1.4972 | 1.5134 | 1.6051
2021-12-25 05:00 | 1.6004 | 1.7434 | 1.7557 | 1.7707 | 1.7882 | 1.0098 | 1.2103 | 1.2199 | 1.233 | 1.0098 | 1.4289 | 1.6049 | 1.6135 | 1.6249 | 1.7171
2021-12-25 06:00 | 1.5623 | 1.6985 | 1.7087 | 1.7212 | 1.7358 | 0.99073 | 1.185 | 1.1929 | 1.2038 | 0.99073 | 1.3718 | 1.5386 | 1.5458 | 1.5553 | 1.6421
2021-12-25 07:00 | 1.5052 | 1.6404 | 1.6523 | 1.667 | 1.684 | 0.99778 | 1.1957 | 1.205 | 1.2177 | 0.99778 | 1.2194 | 1.3716 | 1.3799 | 1.3911 | 1.4714
2021-12-25 08:00 | 1.4328 | 1.5718 | 1.5884 | 1.6087 | 1.6323 | 1.0288 | 1.239 | 1.2519 | 1.2696 | 1.0288 | 1.1241 | 1.2722 | 1.2838 | 1.2992 | 1.3795
2021-12-25 09:00 | 1.2956 | 1.4377 | 1.4611 | 1.4897 | 1.5231 | 0.85737 | 1.0461 | 1.0644 | 1.0893 | 0.85737 | 0.70494 | 0.81582 | 0.83222 | 0.854 | 0.9188
2021-12-25 10:00 | 1.3861 | 1.5492 | 1.5799 | 1.6175 | 1.6612 | 0.91452 | 1.124 | 1.1479 | 1.1806 | 0.91452 | 0.47631 | 0.57185 | 0.59334 | 0.6219 | 0.68223
2021-12-25 11:00 | 1.448 | 1.6266 | 1.6629 | 1.7073 | 1.759 | 0.97168 | 1.1995 | 1.2278 | 1.2664 | 0.97168 | 0.59063 | 0.70663 | 0.73204 | 0.7658 | 0.83864
2021-12-25 12:00 | 1.5623 | 1.7538 | 1.7923 | 1.8394 | 1.8943 | 1.1241 | 1.3827 | 1.4127 | 1.4537 | 1.1241 | 0.68589 | 0.81557 | 0.84254 | 0.87836 | 0.95891
2021-12-25 13:00 | 1.467 | 1.6504 | 1.6883 | 1.7348 | 1.7889 | 1.0288 | 1.2694 | 1.299 | 1.3394 | 1.0288 | 0.41916 | 0.51842 | 0.545 | 0.58033 | 0.64561
2021-12-25 14:00 | 2.3244 | 2.5665 | 2.6019 | 2.6452 | 2.6958 | 1.7698 | 2.1411 | 2.1687 | 2.2064 | 1.7698 | 2.191 | 2.4839 | 2.5087 | 2.5417 | 2.7015
2021-12-25 15:00 | 2.4197 | 2.6634 | 2.6961 | 2.736 | 2.7826 | 1.9434 | 2.3422 | 2.3677 | 2.4024 | 1.9434 | 2.7436 | 3.0941 | 3.1169 | 3.1473 | 3.3345
2021-12-25 16:00 | 2.2863 | 2.5166 | 2.5474 | 2.5851 | 2.629 | 1.8862 | 2.2721 | 2.2961 | 2.3289 | 1.8862 | 2.9531 | 3.3244 | 3.346 | 3.3747 | 3.5713
2021-12-25 17:00 | 2.0158 | 2.2251 | 2.2555 | 2.2926 | 2.336 | 1.528 | 1.8483 | 1.872 | 1.9044 | 1.528 | 2.0577 | 2.3287 | 2.35 | 2.3783 | 2.5252
2021-12-25 18:00 | 2.0958 | 2.3146 | 2.3467 | 2.3861 | 2.432 | 1.6766 | 2.0264 | 2.0515 | 2.0858 | 1.6766 | 1.9831 | 2.2484 | 2.2709 | 2.3009 | 2.4457
2021-12-25 19:00 | 2.1529 | 2.3833 | 2.4193 | 2.4633 | 2.5145 | 1.6766 | 2.0318 | 2.0598 | 2.0981 | 1.6766 | 2.3054 | 2.6117 | 2.6369 | 2.6703 | 2.837
2021-12-25 20:00 | 2.1339 | 2.3726 | 2.4135 | 2.4636 | 2.522 | 1.6004 | 1.9488 | 1.9808 | 2.0243 | 1.6004 | 2.3244 | 2.6398 | 2.6684 | 2.7065 | 2.8799
2021-12-25 21:00 | 2.1339 | 2.3823 | 2.4281 | 2.4843 | 2.5497 | 1.5242 | 1.8658 | 1.9016 | 1.9504 | 1.5242 | 2.2482 | 2.5619 | 2.5941 | 2.6367 | 2.8114
2021-12-25 22:00 | 2.0577 | 2.302 | 2.3487 | 2.4059 | 2.4725 | 1.4861 | 1.822 | 1.8584 | 1.9081 | 1.4861 | 2.0958 | 2.3937 | 2.4264 | 2.4699 | 2.6371
2021-12-25 23:00 | 1.9243 | 2.1528 | 2.1965 | 2.2499 | 2.3122 | 1.3187 | 1.6199 | 1.654 | 1.7004 | 1.3187 | 1.6385 | 1.8813 | 1.9119 | 1.9526 | 2.0912
2021-12-26 | 1.7798 | 1.9891 | 2.0284 | 2.0766 | 2.1327 | 1.2065 | 1.4812 | 1.5119 | 1.5538 | 1.2065 | 1.448 | 1.6636 | 1.6912 | 1.7278 | 1.8512
2021-12-26 01:00 | 1.6576 | 1.8483 | 1.8829 | 1.9251 | 1.9743 | 1.0733 | 1.317 | 1.3439 | 1.3806 | 1.0733 | 1.2956 | 1.4876 | 1.5117 | 1.5439 | 1.6535
2021-12-26 02:00 | 1.6385 | 1.8183 | 1.8479 | 1.8842 | 1.9264 | 0.98734 | 1.2085 | 1.2316 | 1.2632 | 0.98734 | 1.2384 | 1.4173 | 1.438 | 1.4656 | 1.5666
2021-12-26 03:00 | 1.6385 | 1.8062 | 1.8297 | 1.8584 | 1.8918 | 0.97168 | 1.1812 | 1.1995 | 1.2245 | 0.97168 | 1.3146 | 1.4934 | 1.5098 | 1.5317 | 1.63
2021-12-26 04:00 | 1.6385 | 1.7944 | 1.8118 | 1.8331 | 1.858 | 0.95066 | 1.1478 | 1.1614 | 1.1799 | 0.95066 | 1.2003 | 1.358 | 1.3702 | 1.3864 | 1.4718
2021-12-26 05:00 | 1.6385 | 1.7843 | 1.7966 | 1.8116 | 1.8291 | 0.97168 | 1.1653 | 1.1749 | 1.188 | 0.97168 | 1.3908 | 1.5626 | 1.5712 | 1.5826 | 1.6727
2021-12-26 06:00 | 1.5433 | 1.678 | 1.6882 | 1.7008 | 1.7154 | 0.97168 | 1.1624 | 1.1704 | 1.1813 | 0.97168 | 1.1432 | 1.2845 | 1.2917 | 1.3012 | 1.3755
2021-12-26 07:00 | 1.5433 | 1.6814 | 1.6933 | 1.7079 | 1.7249 | 0.95263 | 1.1424 | 1.1517 | 1.1644 | 0.95263 | 1.105 | 1.2445 | 1.2529 | 1.264 | 1.3381
2021-12-26 08:00 | 1.4485 | 1.5886 | 1.6052 | 1.6255 | 1.6491 | 0.99073 | 1.194 | 1.2069 | 1.2246 | 0.99073 | 0.95263 | 1.0816 | 1.0932 | 1.1087 | 1.1795
2021-12-26 09:00 | 1.5623 | 1.7243 | 1.7477 | 1.7763 | 1.8097 | 1.0479 | 1.2712 | 1.2895 | 1.3144 | 1.0479 | 0.85737 | 0.9852 | 1.0016 | 1.0234 | 1.0966
2021-12-26 10:00 | 1.5052 | 1.6771 | 1.7078 | 1.7453 | 1.7891 | 0.83831 | 1.034 | 1.0579 | 1.0906 | 0.83831 | 1.0288 | 1.1858 | 1.2073 | 1.2359 | 1.3266
2021-12-26 11:00 | 1.4099 | 1.5857 | 1.622 | 1.6663 | 1.7181 | 1.0479 | 1.2895 | 1.3178 | 1.3564 | 1.0479 | 1.0669 | 1.2359 | 1.2613 | 1.2951 | 1.3941
2021-12-26 12:00 | 1.5052 | 1.6924 | 1.7309 | 1.778 | 1.8329 | 0.93358 | 1.1576 | 1.1876 | 1.2286 | 0.93358 | 1.0288 | 1.1967 | 1.2236 | 1.2595 | 1.3589
2021-12-26 13:00 | 0.99073 | 1.1387 | 1.1766 | 1.2231 | 1.2772 | 0.55252 | 0.70668 | 0.73628 | 0.77669 | 0.55252 | 0.99073 | 1.1536 | 1.1802 | 1.2155 | 1.3122
2021-12-26 14:00 | 2.0958 | 2.3209 | 2.3563 | 2.3996 | 2.4501 | 1.5052 | 1.8285 | 1.8561 | 1.8938 | 1.5052 | 1.8481 | 2.1028 | 2.1276 | 2.1606 | 2.3016
2021-12-26 15:00 | 2.0906 | 2.3099 | 2.3426 | 2.3825 | 2.4291 | 1.5052 | 1.8245 | 1.85 | 1.8847 | 1.5052 | 1.9624 | 2.226 | 2.2489 | 2.2793 | 2.4235
2021-12-26 16:00 | 1.9434 | 2.1481 | 2.1789 | 2.2166 | 2.2606 | 1.4099 | 1.7094 | 1.7334 | 1.7662 | 1.4099 | 1.7909 | 2.0329 | 2.0545 | 2.0832 | 2.2159
2021-12-26 17:00 | 1.8481 | 2.0449 | 2.0753 | 2.1125 | 2.1558 | 1.3342 | 1.6193 | 1.643 | 1.6754 | 1.3342 | 1.6004 | 1.8206 | 1.8419 | 1.8701 | 1.9919
2021-12-26 18:00 | 1.9699 | 2.1794 | 2.2115 | 2.2509 | 2.2968 | 1.4702 | 1.7826 | 1.8077 | 1.842 | 1.4702 | 1.8862 | 2.1407 | 2.1632 | 2.1932 | 2.3327
2021-12-26 19:00 | 2.0196 | 2.2401 | 2.276 | 2.32 | 2.3713 | 1.4861 | 1.8067 | 1.8347 | 1.873 | 1.4861 | 2.1148 | 2.4 | 2.4251 | 2.4586 | 2.6148
2021-12-26 20:00 | 2.0005 | 2.2293 | 2.2703 | 2.3203 | 2.3787 | 1.5242 | 1.8588 | 1.8907 | 1.9343 | 1.5242 | 1.9815 | 2.2587 | 2.2873 | 2.3254 | 2.4799
2021-12-26 21:00 | 2.0196 | 2.2595 | 2.3053 | 2.3615 | 2.4269 | 1.5052 | 1.8433 | 1.8791 | 1.9279 | 1.5052 | 2.1339 | 2.4349 | 2.467 | 2.5097 | 2.6781
2021-12-26 22:00 | 1.9243 | 2.1588 | 2.2054 | 2.2626 | 2.3292 | 1.4099 | 1.732 | 1.7684 | 1.8181 | 1.4099 | 1.7909 | 2.0549 | 2.0877 | 2.1311 | 2.2816
2021-12-26 23:00 | 1.8672 | 2.0914 | 2.135 | 2.1885 | 2.2508 | 1.2018 | 1.4818 | 1.5158 | 1.5623 | 1.2018 | 1.6576 | 1.9025 | 1.9331 | 1.9737 | 2.1134
2021-12-27 | 1.7338 | 1.9397 | 1.979 | 2.0271 | 2.0833 | 1.1241 | 1.3839 | 1.4146 | 1.4565 | 1.1241 | 1.4289 | 1.6425 | 1.67 | 1.7066 | 1.829
2021-12-27 01:00 | 1.6576 | 1.8483 | 1.8829 | 1.9251 | 1.9743 | 1.014 | 1.2469 | 1.2738 | 1.3106 | 1.014 | 1.3908 | 1.5934 | 1.6176 | 1.6497 | 1.7646
2021-12-27 02:00 | 1.5433 | 1.716 | 1.7456 | 1.7818 | 1.8241 | 0.97802 | 1.1975 | 1.2206 | 1.2521 | 0.97802 | 1.2003 | 1.3749 | 1.3957 | 1.4233 | 1.5222
2021-12-27 03:00 | 1.5433 | 1.7039 | 1.7273 | 1.756 | 1.7895 | 0.9425 | 1.1468 | 1.1651 | 1.19 | 0.9425 | 1.2194 | 1.3875 | 1.404 | 1.4258 | 1.5189
2021-12-27 04:00 | 1.5433 | 1.6921 | 1.7095 | 1.7308 | 1.7556 | 0.95029 | 1.1474 | 1.161 | 1.1795 | 0.95029 | 1.2384 | 1.4003 | 1.4125 | 1.4287 | 1.5162
2021-12-27 05:00 | 1.5623 | 1.7025 | 1.7147 | 1.7297 | 1.7472 | 0.95263 | 1.1428 | 1.1524 | 1.1654 | 0.95263 | 1.4289 | 1.6049 | 1.6135 | 1.6249 | 1.7171
2021-12-27 06:00 | 1.448 | 1.5757 | 1.5859 | 1.5984 | 1.613 | 0.97168 | 1.1624 | 1.1704 | 1.1813 | 0.97168 | 1.1813 | 1.3269 | 1.334 | 1.3436 | 1.4199
2021-12-27 07:00 | 1.5052 | 1.6404 | 1.6523 | 1.667 | 1.684 | 1.0288 | 1.2324 | 1.2417 | 1.2544 | 1.0288 | 1.2575 | 1.4139 | 1.4223 | 1.4334 | 1.5158
2021-12-27 08:00 | 1.4884 | 1.6315 | 1.6481 | 1.6684 | 1.6921 | 1.105 | 1.329 | 1.342 | 1.3596 | 1.105 | 1.1622 | 1.3145 | 1.3261 | 1.3416 | 1.4239
2021-12-27 09:00 | 1.448 | 1.6014 | 1.6248 | 1.6535 | 1.6869 | 1.086 | 1.3162 | 1.3345 | 1.3594 | 1.086 | 1.0669 | 1.2181 | 1.2345 | 1.2563 | 1.341
2021-12-27 10:00 | 1.5814 | 1.759 | 1.7896 | 1.8272 | 1.871 | 1.105 | 1.3491 | 1.373 | 1.4057 | 1.105 | 1.0479 | 1.207 | 1.2285 | 1.2571 | 1.3488
2021-12-27 11:00 | 1.4861 | 1.6676 | 1.7038 | 1.7482 | 1.8 | 1.0391 | 1.2791 | 1.3074 | 1.346 | 1.0391 | 0.97168 | 1.1301 | 1.1555 | 1.1892 | 1.283
2021-12-27 12:00 | 1.6385 | 1.8357 | 1.8741 | 1.9212 | 1.9762 | 1.105 | 1.3602 | 1.3902 | 1.4312 | 1.105 | 1.1241 | 1.3025 | 1.3295 | 1.3653 | 1.47
2021-12-27 13:00 | 1.467 | 1.6504 | 1.6883 | 1.7348 | 1.7889 | 0.99073 | 1.2244 | 1.254 | 1.2944 | 0.99073 | 0.85737 | 1.0054 | 1.032 | 1.0673 | 1.1567
2021-12-27 14:00 | 1.4861 | 1.6659 | 1.7013 | 1.7446 | 1.7951 | 0.99073 | 1.2207 | 1.2484 | 1.2861 | 0.99073 | 1.4289 | 1.637 | 1.6618 | 1.6948 | 1.8127
2021-12-27 15:00 | 1.7338 | 1.9266 | 1.9592 | 1.9991 | 2.0457 | 1.2108 | 1.4768 | 1.5022 | 1.537 | 1.2108 | 1.105 | 1.2733 | 1.2961 | 1.3265 | 1.4236
2021-12-27 16:00 | 1.6181 | 1.7987 | 1.8295 | 1.8672 | 1.9112 | 1.2194 | 1.4843 | 1.5083 | 1.5411 | 1.2194 | 1.2003 | 1.3766 | 1.3982 | 1.4268 | 1.5271
2021-12-27 17:00 | 1.6155 | 1.7951 | 1.8254 | 1.8626 | 1.9059 | 1.2176 | 1.4816 | 1.5053 | 1.5377 | 1.2176 | 1.2575 | 1.4395 | 1.4608 | 1.489 | 1.592
2021-12-27 18:00 | 1.829 | 2.028 | 2.0602 | 2.0996 | 2.1455 | 1.3527 | 1.6438 | 1.6689 | 1.7032 | 1.3527 | 1.7528 | 1.9925 | 2.015 | 2.045 | 2.1771
2021-12-27 19:00 | 1.9815 | 2.1991 | 2.235 | 2.279 | 2.3303 | 1.5623 | 1.8967 | 1.9248 | 1.963 | 1.5623 | 2.1339 | 2.4211 | 2.4463 | 2.4798 | 2.6371
2021-12-27 20:00 | 2.0958 | 2.3317 | 2.3726 | 2.4227 | 2.4811 | 1.5814 | 1.9263 | 1.9582 | 2.0018 | 1.5814 | 2.191 | 2.4916 | 2.5202 | 2.5583 | 2.7243
2021-12-27 21:00 | 2.0725 | 2.3163 | 2.3622 | 2.4183 | 2.4837 | 1.5621 | 1.9106 | 1.9464 | 1.9952 | 1.5621 | 1.9815 | 2.2655 | 2.2976 | 2.3403 | 2.5003
2021-12-27 22:00 | 1.9815 | 2.2202 | 2.2669 | 2.324 | 2.3906 | 1.4099 | 1.732 | 1.7684 | 1.8181 | 1.4099 | 1.9624 | 2.2455 | 2.2782 | 2.3217 | 2.4815
2021-12-27 23:00 | 1.8672 | 2.0914 | 2.135 | 2.1885 | 2.2508 | 1.3084 | 1.6077 | 1.6417 | 1.6882 | 1.3084 | 1.6242 | 1.8655 | 1.8961 | 1.9367 | 2.0746
2021-12-28 | 1.7528 | 1.9601 | 1.9995 | 2.0476 | 2.1038 | 1.1519 | 1.4168 | 1.4475 | 1.4894 | 1.1519 | 1.467 | 1.6848 | 1.7124 | 1.749 | 1.8734
2021-12-28 01:00 | 1.6576 | 1.8483 | 1.8829 | 1.9251 | 1.9743 | 1.0317 | 1.2679 | 1.2948 | 1.3316 | 1.0317 | 1.3908 | 1.5934 | 1.6176 | 1.6497 | 1.7646
2021-12-28 02:00 | 1.6004 | 1.7774 | 1.807 | 1.8432 | 1.8855 | 0.99073 | 1.2125 | 1.2356 | 1.2672 | 0.99073 | 1.2575 | 1.4384 | 1.4592 | 1.4868 | 1.5889
2021-12-28 03:00 | 1.6004 | 1.7653 | 1.7887 | 1.8174 | 1.8509 | 0.97168 | 1.1812 | 1.1995 | 1.2245 | 0.97168 | 1.2003 | 1.3664 | 1.3828 | 1.4046 | 1.4967
2021-12-28 04:00 | 1.6004 | 1.7535 | 1.7709 | 1.7922 | 1.817 | 0.95263 | 1.1501 | 1.1637 | 1.1823 | 0.95263 | 1.3908 | 1.5697 | 1.5819 | 1.5981 | 1.694
2021-12-28 05:00 | 1.6195 | 1.7639 | 1.7761 | 1.7911 | 1.8086 | 0.97168 | 1.1653 | 1.1749 | 1.188 | 0.97168 | 1.2384 | 1.3932 | 1.4018 | 1.4132 | 1.4949
2021-12-28 06:00 | 1.4861 | 1.6166 | 1.6268 | 1.6394 | 1.654 | 1.0288 | 1.23 | 1.238 | 1.2489 | 1.0288 | 1.1813 | 1.3269 | 1.334 | 1.3436 | 1.4199
2021-12-28 07:00 | 1.4289 | 1.5585 | 1.5705 | 1.5851 | 1.6021 | 0.95041 | 1.1397 | 1.1491 | 1.1618 | 0.95041 | 1.0288 | 1.1599 | 1.1682 | 1.1793 | 1.2492
2021-12-28 08:00 | 1.3527 | 1.4858 | 1.5023 | 1.5226 | 1.5463 | 0.87642 | 1.0589 | 1.0719 | 1.0895 | 0.87642 | 0.97168 | 1.1028 | 1.1144 | 1.1298 | 1.2017
2021-12-28 09:00 | 1.4289 | 1.581 | 1.6044 | 1.633 | 1.6664 | 0.78115 | 0.95609 | 0.97434 | 0.99926 | 0.78115 | 1.2765 | 1.451 | 1.4674 | 1.4892 | 1.5854
2021-12-28 10:00 | 1.4099 | 1.5748 | 1.6054 | 1.643 | 1.6868 | 0.95263 | 1.169 | 1.1929 | 1.2256 | 0.95263 | 1.105 | 1.2705 | 1.292 | 1.3206 | 1.4155
2021-12-28 11:00 | 1.5433 | 1.729 | 1.7652 | 1.8096 | 1.8614 | 1.0098 | 1.2445 | 1.2728 | 1.3114 | 1.0098 | 0.93358 | 1.0877 | 1.1131 | 1.1469 | 1.2386
2021-12-28 12:00 | 1.4861 | 1.6719 | 1.7104 | 1.7575 | 1.8124 | 0.9766 | 1.2084 | 1.2385 | 1.2794 | 0.9766 | 1.086 | 1.2602 | 1.2872 | 1.323 | 1.4255
2021-12-28 13:00 | 1.086 | 1.241 | 1.279 | 1.3254 | 1.3796 | 0.68371 | 0.86167 | 0.89126 | 0.93168 | 0.68371 | 1.6766 | 1.9158 | 1.9424 | 1.9777 | 2.1121
2021-12-28 14:00 | 1.1241 | 1.277 | 1.3124 | 1.3557 | 1.4062 | 0.66684 | 0.83811 | 0.86572 | 0.90342 | 0.66684 | 1.4861 | 1.7005 | 1.7253 | 1.7583 | 1.8794
2021-12-28 15:00 | 1.086 | 1.2306 | 1.2633 | 1.3032 | 1.3498 | 0.64779 | 0.81167 | 0.83713 | 0.87189 | 0.64779 | 1.7528 | 1.9931 | 2.016 | 2.0464 | 2.1791
2021-12-28 16:00 | 1.1622 | 1.3089 | 1.3397 | 1.3774 | 1.4214 | 0.7621 | 0.94411 | 0.96814 | 1.0009 | 0.7621 | 1.3527 | 1.546 | 1.5675 | 1.5962 | 1.7049
2021-12-28 17:00 | 1.4429 | 1.6096 | 1.64 | 1.6772 | 1.7205 | 1.0098 | 1.2361 | 1.2598 | 1.2921 | 1.0098 | 0.80141 | 0.93268 | 0.95396 | 0.98222 | 1.0601
2021-12-28 18:00 | 1.7909 | 1.9871 | 2.0192 | 2.0586 | 2.1045 | 1.3527 | 1.6438 | 1.6689 | 1.7032 | 1.3527 | 1.448 | 1.6537 | 1.6763 | 1.7062 | 1.8216
2021-12-28 19:00 | 1.9053 | 2.1172 | 2.1532 | 2.1972 | 2.2484 | 1.5814 | 1.9192 | 1.9473 | 1.9855 | 1.5814 | 1.81 | 2.0612 | 2.0864 | 2.1198 | 2.2593
2021-12-28 20:00 | 2.0196 | 2.2498 | 2.2907 | 2.3408 | 2.3992 | 1.6004 | 1.9488 | 1.9808 | 2.0243 | 1.6004 | 2.3625 | 2.6821 | 2.7108 | 2.7489 | 2.9243
2021-12-28 21:00 | 2.0958 | 2.3414 | 2.3872 | 2.4433 | 2.5088 | 1.5433 | 1.8883 | 1.9241 | 1.9729 | 1.5433 | 1.9053 | 2.1808 | 2.213 | 2.2556 | 2.4114
2021-12-28 22:00 | 1.9815 | 2.2202 | 2.2669 | 2.324 | 2.3906 | 1.448 | 1.777 | 1.8134 | 1.8631 | 1.448 | 2.2291 | 2.5419 | 2.5746 | 2.6181 | 2.7926
2021-12-28 23:00 | 1.829 | 2.0505 | 2.0941 | 2.1475 | 2.2098 | 1.251 | 1.54 | 1.574 | 1.6205 | 1.251 | 1.6766 | 1.9237 | 1.9543 | 1.9949 | 2.1357
2021-12-29 | 1.7528 | 1.9601 | 1.9995 | 2.0476 | 2.1038 | 1.1558 | 1.4214 | 1.452 | 1.4939 | 1.1558 | 1.6004 | 1.833 | 1.8606 | 1.8972 | 2.029
2021-12-29 01:00 | 1.6957 | 1.8893 | 1.9238 | 1.966 | 2.0153 | 1.0627 | 1.3045 | 1.3314 | 1.3682 | 1.0627 | 1.3337 | 1.5299 | 1.5541 | 1.5862 | 1.698
2021-12-29 02:00 | 1.629 | 1.808 | 1.8376 | 1.8739 | 1.9162 | 0.99073 | 1.2125 | 1.2356 | 1.2672 | 0.99073 | 1.467 | 1.6713 | 1.6921 | 1.7197 | 1.8333
2021-12-29 03:00 | 1.6957 | 1.8676 | 1.8911 | 1.9198 | 1.9532 | 0.97168 | 1.1812 | 1.1995 | 1.2245 | 0.97168 | 1.3146 | 1.4934 | 1.5098 | 1.5317 | 1.63
2021-12-29 04:00 | 1.6576 | 1.8149 | 1.8323 | 1.8536 | 1.8784 | 0.97859 | 1.1808 | 1.1944 | 1.2129 | 0.97859 | 1.3337 | 1.5062 | 1.5184 | 1.5346 | 1.6273
2021-12-29 05:00 | 1.6385 | 1.7843 | 1.7966 | 1.8116 | 1.8291 | 1.0288 | 1.2329 | 1.2424 | 1.2555 | 1.0288 | 1.4289 | 1.6049 | 1.6135 | 1.6249 | 1.7171
2021-12-29 06:00 | 1.5242 | 1.6575 | 1.6678 | 1.6803 | 1.6949 | 1.0669 | 1.275 | 1.283 | 1.2939 | 1.0669 | 1.2765 | 1.4327 | 1.4399 | 1.4494 | 1.531
2021-12-29 07:00 | 1.4861 | 1.6199 | 1.6319 | 1.6465 | 1.6635 | 1.0479 | 1.2549 | 1.2642 | 1.2769 | 1.0479 | 1.086 | 1.2234 | 1.2317 | 1.2428 | 1.3158
2021-12-29 08:00 | 1.2575 | 1.3834 | 1.4 | 1.4203 | 1.4439 | 0.89547 | 1.0814 | 1.0944 | 1.112 | 0.89547 | 0.83831 | 0.95457 | 0.96619 | 0.98162 | 1.0462
2021-12-29 09:00 | 1.1622 | 1.2944 | 1.3178 | 1.3464 | 1.3798 | 0.7621 | 0.93358 | 0.95183 | 0.97675 | 0.7621 | 1.2956 | 1.4722 | 1.4886 | 1.5103 | 1.6076
2021-12-29 10:00 | 0.95263 | 1.0835 | 1.1142 | 1.1517 | 1.1955 | 0.56499 | 0.71107 | 0.735 | 0.76767 | 0.56499 | 1.5623 | 1.7787 | 1.8002 | 1.8287 | 1.9488
2021-12-29 11:00 | 0.82155 | 0.95362 | 0.98988 | 1.0343 | 1.086 | 0.51442 | 0.65928 | 0.68756 | 0.72618 | 0.51442 | 1.9624 | 2.231 | 2.2564 | 2.2902 | 2.4385
2021-12-29 12:00 | 0.85737 | 0.99643 | 1.0349 | 1.082 | 1.1369 | 0.43821 | 0.5724 | 0.60242 | 0.6434 | 0.43821 | 1.8481 | 2.1071 | 2.134 | 2.1699 | 2.3143
2021-12-29 13:00 | 0.97168 | 1.1182 | 1.1561 | 1.2026 | 1.2567 | 0.45726 | 0.59414 | 0.62374 | 0.66415 | 0.45726 | 1.829 | 2.0852 | 2.1117 | 2.1471 | 2.2899
2021-12-29 14:00 | 0.97703 | 1.119 | 1.1544 | 1.1977 | 1.2482 | 0.49122 | 0.63064 | 0.65825 | 0.69595 | 0.49122 | 2.0577 | 2.3357 | 2.3605 | 2.3935 | 2.546
2021-12-29 15:00 | 1.1813 | 1.333 | 1.3656 | 1.4055 | 1.4521 | 0.55252 | 0.69913 | 0.72459 | 0.75935 | 0.55252 | 1.6576 | 1.8872 | 1.9101 | 1.9405 | 2.068
2021-12-29 16:00 | 1.3131 | 1.471 | 1.5018 | 1.5395 | 1.5835 | 0.80886 | 0.99935 | 1.0234 | 1.0562 | 0.80886 | 1.2194 | 1.3977 | 1.4193 | 1.448 | 1.5493
2021-12-29 17:00 | 1.7596 | 1.9499 | 1.9802 | 2.0174 | 2.0607 | 1.1432 | 1.3936 | 1.4173 | 1.4497 | 1.1432 | 0.83831 | 0.97369 | 0.99496 | 1.0232 | 1.1031
2021-12-29 18:00 | 2.0196 | 2.2327 | 2.2649 | 2.3042 | 2.3502 | 1.467 | 1.7789 | 1.804 | 1.8382 | 1.467 | 1.4289 | 1.6325 | 1.6551 | 1.685 | 1.7994
2021-12-29 19:00 | 2.0767 | 2.3015 | 2.3374 | 2.3814 | 2.4327 | 1.5968 | 1.9374 | 1.9655 | 2.0037 | 1.5968 | 1.81 | 2.0612 | 2.0864 | 2.1198 | 2.2593
2021-12-29 20:00 | 2.0958 | 2.3317 | 2.3726 | 2.4227 | 2.4811 | 1.6195 | 1.9713 | 2.0033 | 2.0468 | 1.6195 | 2.534 | 2.8727 | 2.9013 | 2.9394 | 3.1243
2021-12-29 21:00 | 2.0196 | 2.2595 | 2.3053 | 2.3615 | 2.4269 | 1.5623 | 1.9108 | 1.9466 | 1.9955 | 1.5623 | 1.9815 | 2.2655 | 2.2976 | 2.3403 | 2.5003
2021-12-29 22:00 | 1.9624 | 2.1997 | 2.2464 | 2.3035 | 2.3702 | 1.5242 | 1.867 | 1.9034 | 1.9532 | 1.5242 | 1.9053 | 2.182 | 2.2147 | 2.2582 | 2.4149
2021-12-29 23:00 | 1.9624 | 2.1937 | 2.2374 | 2.2908 | 2.3531 | 1.3146 | 1.6151 | 1.6492 | 1.6956 | 1.3146 | 1.9624 | 2.2413 | 2.2719 | 2.3125 | 2.469
2021-12-30 | 1.7528 | 1.9601 | 1.9995 | 2.0476 | 2.1038 | 1.1493 | 1.4137 | 1.4444 | 1.4863 | 1.1493 | 1.3908 | 1.6001 | 1.6277 | 1.6643 | 1.7846
2021-12-30 01:00 | 1.6246 | 1.8129 | 1.8474 | 1.8896 | 1.9389 | 1.039 | 1.2765 | 1.3034 | 1.3402 | 1.039 | 1.5052 | 1.7205 | 1.7446 | 1.7768 | 1.8979
2021-12-30 02:00 | 1.5623 | 1.7364 | 1.766 | 1.8023 | 1.8446 | 0.96377 | 1.1807 | 1.2038 | 1.2353 | 0.96377 | 1.2575 | 1.4384 | 1.4592 | 1.4868 | 1.5889
2021-12-30 03:00 | 1.5052 | 1.6629 | 1.6864 | 1.7151 | 1.7486 | 0.95263 | 1.1587 | 1.177 | 1.202 | 0.95263 | 1.4099 | 1.5993 | 1.6157 | 1.6375 | 1.7411
2021-12-30 04:00 | 1.5242 | 1.6716 | 1.689 | 1.7103 | 1.7352 | 0.92569 | 1.1183 | 1.1319 | 1.1504 | 0.92569 | 1.2194 | 1.3792 | 1.3914 | 1.4076 | 1.494
2021-12-30 05:00 | 1.4861 | 1.6206 | 1.6328 | 1.6478 | 1.6653 | 0.95263 | 1.1428 | 1.1524 | 1.1654 | 0.95263 | 1.2575 | 1.4144 | 1.423 | 1.4344 | 1.5172
2021-12-30 06:00 | 1.4861 | 1.6166 | 1.6268 | 1.6394 | 1.654 | 0.94906 | 1.1357 | 1.1437 | 1.1546 | 0.94906 | 1.1241 | 1.2634 | 1.2705 | 1.28 | 1.3532
2021-12-30 07:00 | 1.448 | 1.579 | 1.5909 | 1.6056 | 1.6226 | 0.97168 | 1.1649 | 1.1742 | 1.1869 | 0.97168 | 1.0479 | 1.181 | 1.1894 | 1.2005 | 1.2714
2021-12-30 08:00 | 1.3337 | 1.4653 | 1.4819 | 1.5022 | 1.5258 | 0.91452 | 1.104 | 1.1169 | 1.1345 | 0.91452 | 0.83831 | 0.95457 | 0.96619 | 0.98162 | 1.0462
2021-12-30 09:00 | 1.1457 | 1.2767 | 1.3001 | 1.3288 | 1.3622 | 0.74733 | 0.91613 | 0.93439 | 0.9593 | 0.74733 | 1.2765 | 1.451 | 1.4674 | 1.4892 | 1.5854
2021-12-30 10:00 | 1.0098 | 1.1449 | 1.1756 | 1.2131 | 1.2569 | 0.60968 | 0.76387 | 0.7878 | 0.82046 | 0.60968 | 1.6195 | 1.8422 | 1.8637 | 1.8922 | 2.0154
2021-12-30 11:00 | 1.0098 | 1.1558 | 1.1921 | 1.2365 | 1.2883 | 0.57158 | 0.7268 | 0.75509 | 0.79371 | 0.57158 | 1.8481 | 2.104 | 2.1294 | 2.1632 | 2.3051
2021-12-30 12:00 | 1.0669 | 1.2216 | 1.2601 | 1.3072 | 1.3621 | 0.53347 | 0.68494 | 0.71496 | 0.75594 | 0.53347 | 1.5623 | 1.7895 | 1.8165 | 1.8523 | 1.981
2021-12-30 13:00 | 1.1813 | 1.3434 | 1.3813 | 1.4277 | 1.4819 | 0.55252 | 0.70668 | 0.73628 | 0.77669 | 0.55252 | 1.4861 | 1.7041 | 1.7306 | 1.766 | 1.8899
2021-12-30 14:00 | 1.6444 | 1.8359 | 1.8713 | 1.9146 | 1.9651 | 0.91452 | 1.1307 | 1.1583 | 1.196 | 0.91452 | 1.4099 | 1.6158 | 1.6406 | 1.6736 | 1.7905
2021-12-30 15:00 | 1.9434 | 2.1517 | 2.1844 | 2.2243 | 2.2709 | 1.4289 | 1.7345 | 1.76 | 1.7947 | 1.4289 | 1.0288 | 1.1886 | 1.2114 | 1.2418 | 1.3347
2021-12-30 16:00 | 1.9624 | 2.1686 | 2.1994 | 2.2371 | 2.2811 | 1.1089 | 1.3538 | 1.3779 | 1.4107 | 1.1089 | 1.1622 | 1.3342 | 1.3558 | 1.3845 | 1.4827
2021-12-30 17:00 | 2.0958 | 2.311 | 2.3414 | 2.3786 | 2.4219 | 1.5623 | 1.8888 | 1.9125 | 1.9448 | 1.5623 | 1.5623 | 1.7782 | 1.7995 | 1.8278 | 1.9475
2021-12-30 18:00 | 2.534 | 2.7854 | 2.8175 | 2.8569 | 2.9028 | 1.7991 | 2.1711 | 2.1962 | 2.2305 | 1.7991 | 2.1529 | 2.4371 | 2.4596 | 2.4896 | 2.6438
2021-12-30 19:00 | 2.4197 | 2.6699 | 2.7058 | 2.7498 | 2.8011 | 1.81 | 2.1893 | 2.2174 | 2.2556 | 1.81 | 2.3244 | 2.6329 | 2.658 | 2.6915 | 2.8593
2021-12-30 20:00 | 2.3625 | 2.6182 | 2.6592 | 2.7092 | 2.7676 | 1.7528 | 2.1289 | 2.1608 | 2.2044 | 1.7528 | 2.2673 | 2.5762 | 2.6049 | 2.643 | 2.8132
2021-12-30 21:00 | 2.2482 | 2.5051 | 2.551 | 2.6071 | 2.6725 | 1.7528 | 2.1359 | 2.1717 | 2.2205 | 1.7528 | 2.3625 | 2.689 | 2.7211 | 2.7638 | 2.9447
2021-12-30 22:00 | 2.1339 | 2.3839 | 2.4306 | 2.4878 | 2.5544 | 1.5941 | 1.9496 | 1.986 | 2.0358 | 1.5941 | 1.9243 | 2.2032 | 2.2359 | 2.2793 | 2.4371
2021-12-30 23:00 | 1.8862 | 2.1119 | 2.1555 | 2.2089 | 2.2712 | 1.3848 | 1.6981 | 1.7321 | 1.7786 | 1.3848 | 1.829 | 2.0931 | 2.1237 | 2.1643 | 2.3134
2021-12-31 | 1.7338 | 1.9397 | 1.979 | 2.0271 | 2.0833 | 1.2099 | 1.4853 | 1.516 | 1.5579 | 1.2099 | 1.6766 | 1.9177 | 1.9453 | 1.9819 | 2.1178
2021-12-31 01:00 | 1.6195 | 1.8074 | 1.8419 | 1.8842 | 1.9334 | 1.1138 | 1.3649 | 1.3918 | 1.4286 | 1.1138 | 1.3527 | 1.5511 | 1.5753 | 1.6074 | 1.7202
2021-12-31 02:00 | 1.5122 | 1.6826 | 1.7123 | 1.7485 | 1.7908 | 1.0098 | 1.235 | 1.2581 | 1.2897 | 1.0098 | 1.467 | 1.6713 | 1.6921 | 1.7197 | 1.8333
2021-12-31 03:00 | 1.5052 | 1.6629 | 1.6864 | 1.7151 | 1.7486 | 0.97992 | 1.191 | 1.2093 | 1.2342 | 0.97992 | 1.448 | 1.6416 | 1.658 | 1.6799 | 1.7856
2021-12-31 04:00 | 1.4861 | 1.6307 | 1.6481 | 1.6694 | 1.6942 | 0.94133 | 1.1368 | 1.1504 | 1.1689 | 0.94133 | 1.1432 | 1.2945 | 1.3067 | 1.3229 | 1.4051
2021-12-31 05:00 | 1.5052 | 1.641 | 1.6533 | 1.6683 | 1.6858 | 0.97168 | 1.1653 | 1.1749 | 1.188 | 0.97168 | 1.1813 | 1.3297 | 1.3383 | 1.3497 | 1.4283
2021-12-31 06:00 | 1.4099 | 1.5347 | 1.545 | 1.5575 | 1.5721 | 1.0098 | 1.2075 | 1.2154 | 1.2263 | 1.0098 | 1.2575 | 1.4116 | 1.4187 | 1.4283 | 1.5088
2021-12-31 07:00 | 1.3718 | 1.4971 | 1.5091 | 1.5237 | 1.5407 | 1.0098 | 1.2099 | 1.2192 | 1.2319 | 1.0098 | 0.97168 | 1.0963 | 1.1047 | 1.1158 | 1.1825
2021-12-31 08:00 | 1.2384 | 1.3629 | 1.3795 | 1.3998 | 1.4235 | 0.97168 | 1.1715 | 1.1844 | 1.2021 | 0.97168 | 0.93358 | 1.0604 | 1.072 | 1.0875 | 1.1573
2021-12-31 09:00 | 1.2575 | 1.3968 | 1.4202 | 1.4488 | 1.4822 | 0.76138 | 0.93273 | 0.95098 | 0.9759 | 0.76138 | 1.0098 | 1.1546 | 1.171 | 1.1928 | 1.2743
2021-12-31 10:00 | 1.1813 | 1.3291 | 1.3598 | 1.3973 | 1.4411 | 0.60317 | 0.75618 | 0.78011 | 0.81278 | 0.60317 | 1.2765 | 1.4611 | 1.4826 | 1.5111 | 1.6155
2021-12-31 11:00 | 1.2384 | 1.4015 | 1.4377 | 1.4821 | 1.5339 | 0.62873 | 0.79432 | 0.82261 | 0.86123 | 0.62873 | 1.3146 | 1.5112 | 1.5366 | 1.5703 | 1.683
2021-12-31 12:00 | 1.6004 | 1.7947 | 1.8332 | 1.8803 | 1.9352 | 0.64779 | 0.81999 | 0.85 | 0.89099 | 0.64779 | 1.2003 | 1.3872 | 1.4142 | 1.45 | 1.5588
2021-12-31 13:00 | 2.0767 | 2.3054 | 2.3433 | 2.3898 | 2.4439 | 1.3908 | 1.697 | 1.7266 | 1.767 | 1.3908 | 0.97168 | 1.1324 | 1.159 | 1.1943 | 1.29
2021-12-31 14:00 | 2.2673 | 2.5051 | 2.5405 | 2.5838 | 2.6344 | 1.3908 | 1.6934 | 1.721 | 1.7587 | 1.3908 | 0.38105 | 0.47254 | 0.49734 | 0.5303 | 0.59065
2021-12-31 15:00 | 1.9434 | 2.1517 | 2.1844 | 2.2243 | 2.2709 | 1.1432 | 1.3969 | 1.4223 | 1.4571 | 1.1432 | 0.57158 | 0.68043 | 0.7033 | 0.73368 | 0.80143
2021-12-31 16:00 | 2.1339 | 2.3528 | 2.3836 | 2.4213 | 2.4653 | 1.4295 | 1.7326 | 1.7566 | 1.7894 | 1.4295 | 1.3806 | 1.5769 | 1.5985 | 1.6272 | 1.7374
2021-12-31 17:00 | 2.5149 | 2.7613 | 2.7917 | 2.8289 | 2.8722 | 1.7338 | 2.0914 | 2.1151 | 2.1474 | 1.7338 | 2.0196 | 2.2864 | 2.3076 | 2.3359 | 2.4807
2021-12-31 18:00 | 2.553 | 2.8058 | 2.838 | 2.8774 | 2.9233 | 1.9368 | 2.3338 | 2.3589 | 2.3932 | 1.9368 | 2.4387 | 2.7547 | 2.7772 | 2.8072 | 2.9771
2021-12-31 19:00 | 2.553 | 2.8132 | 2.8491 | 2.8931 | 2.9444 | 1.9624 | 2.3694 | 2.3974 | 2.4357 | 1.9624 | 2.5911 | 2.9293 | 2.9544 | 2.9879 | 3.1703
2021-12-31 20:00 | 2.3244 | 2.5773 | 2.6182 | 2.6683 | 2.7267 | 1.7399 | 2.1137 | 2.1456 | 2.1892 | 1.7399 | 2.4006 | 2.7245 | 2.7531 | 2.7912 | 2.9687
2021-12-31 21:00 | 2.1169 | 2.3641 | 2.4099 | 2.4661 | 2.5315 | 1.5884 | 1.9416 | 1.9774 | 2.0262 | 1.5884 | 2.4959 | 2.8372 | 2.8693 | 2.912 | 3.1002
2021-12-31 22:00 | 2.0958 | 2.343 | 2.3897 | 2.4468 | 2.5135 | 1.5052 | 1.8445 | 1.8809 | 1.9306 | 1.5052 | 2.2673 | 2.5843 | 2.617 | 2.6604 | 2.837
2021-12-31 23:00 | 1.9243 | 2.1528 | 2.1965 | 2.2499 | 2.3122 | 1.3841 | 1.6972 | 1.7312 | 1.7777 | 1.3841 | 1.8481 | 2.1142 | 2.1448 | 2.1855 | 2.3356
2022-01-01 | 1.7532 | 1.9605 | 1.9999 | 2.048 | 2.1041 | 1.2575 | 1.5414 | 1.5721 | 1.614 | 1.2575 | 1.7338 | 1.9812 | 2.0088 | 2.0454 | 2.1845
2022-01-01 01:00 | 1.6957 | 1.8893 | 1.9238 | 1.966 | 2.0153 | 1.1812 | 1.4445 | 1.4714 | 1.5082 | 1.1812 | 1.5052 | 1.7205 | 1.7446 | 1.7768 | 1.8979
2022-01-01 02:00 | 1.603 | 1.7801 | 1.8097 | 1.846 | 1.8882 | 1.0925 | 1.3328 | 1.3559 | 1.3874 | 1.0925 | 1.3146 | 1.502 | 1.5227 | 1.5503 | 1.6555
2022-01-01 03:00 | 1.6004 | 1.7653 | 1.7887 | 1.8174 | 1.8509 | 1.008 | 1.2242 | 1.2424 | 1.2674 | 1.008 | 1.2765 | 1.4511 | 1.4675 | 1.4893 | 1.5856
2022-01-01 04:00 | 1.5052 | 1.6511 | 1.6685 | 1.6898 | 1.7147 | 0.98634 | 1.19 | 1.2036 | 1.2221 | 0.98634 | 1.1813 | 1.3368 | 1.349 | 1.3652 | 1.4495
2022-01-01 05:00 | 1.5052 | 1.641 | 1.6533 | 1.6683 | 1.6858 | 0.97168 | 1.1653 | 1.1749 | 1.188 | 0.97168 | 1.2194 | 1.372 | 1.3806 | 1.392 | 1.4727
2022-01-01 06:00 | 1.4026 | 1.5269 | 1.5371 | 1.5496 | 1.5642 | 0.94588 | 1.132 | 1.1399 | 1.1508 | 0.94588 | 1.2765 | 1.4327 | 1.4399 | 1.4494 | 1.531
2022-01-01 07:00 | 1.2329 | 1.3479 | 1.3598 | 1.3745 | 1.3915 | 0.93358 | 1.1199 | 1.1292 | 1.1419 | 0.93358 | 0.91452 | 1.0328 | 1.0412 | 1.0523 | 1.1159
2022-01-01 08:00 | 1.1293 | 1.2457 | 1.2623 | 1.2826 | 1.3063 | 0.87642 | 1.0589 | 1.0719 | 1.0895 | 0.87642 | 0.83831 | 0.95457 | 0.96619 | 0.98162 | 1.0462
2022-01-01 09:00 | 1.0669 | 1.1921 | 1.2155 | 1.2441 | 1.2775 | 0.66684 | 0.82104 | 0.8393 | 0.86421 | 0.66684 | 1.1241 | 1.2816 | 1.298 | 1.3198 | 1.4076
2022-01-01 10:00 | 1.0288 | 1.1654 | 1.196 | 1.2336 | 1.2774 | 0.62873 | 0.78638 | 0.8103 | 0.84297 | 0.62873 | 1.105 | 1.2705 | 1.292 | 1.3206 | 1.4155
2022-01-01 11:00 | 1.086 | 1.2377 | 1.274 | 1.3184 | 1.3701 | 0.59063 | 0.74931 | 0.77759 | 0.81622 | 0.59063 | 1.2384 | 1.4265 | 1.4519 | 1.4857 | 1.5941
2022-01-01 12:00 | 1.0944 | 1.2511 | 1.2895 | 1.3366 | 1.3916 | 0.62873 | 0.79748 | 0.8275 | 0.86848 | 0.62873 | 1.086 | 1.2602 | 1.2872 | 1.323 | 1.4255
2022-01-01 13:00 | 1.2194 | 1.3843 | 1.4222 | 1.4687 | 1.5228 | 0.72733 | 0.91319 | 0.94278 | 0.9832 | 0.72733 | 0.7621 | 0.89952 | 0.9261 | 0.96143 | 1.0456
2022-01-01 14:00 | 1.5433 | 1.7273 | 1.7627 | 1.806 | 1.8565 | 0.91452 | 1.1307 | 1.1583 | 1.196 | 0.91452 | 0.45726 | 0.55723 | 0.58203 | 0.61498 | 0.67953
2022-01-01 15:00 | 1.8672 | 2.0698 | 2.1025 | 2.1424 | 2.189 | 1.2575 | 1.5319 | 1.5574 | 1.5921 | 1.2575 | 1.829 | 2.0778 | 2.1007 | 2.131 | 2.2679
2022-01-01 16:00 | 2.4197 | 2.6599 | 2.6907 | 2.7284 | 2.7723 | 1.7719 | 2.137 | 2.1611 | 2.1939 | 1.7719 | 1.9053 | 2.1599 | 2.1815 | 2.2102 | 2.3492
2022-01-01 17:00 | 2.4901 | 2.7346 | 2.765 | 2.8022 | 2.8455 | 1.9044 | 2.2929 | 2.3166 | 2.3489 | 1.9044 | 2.6483 | 2.9851 | 3.0063 | 3.0346 | 3.214
2022-01-01 18:00 | 2.7626 | 3.031 | 3.0632 | 3.1025 | 3.1485 | 2.1148 | 2.5441 | 2.5692 | 2.6035 | 2.1148 | 3.1056 | 3.4957 | 3.5182 | 3.5482 | 3.7547
2022-01-01 19:00 | 2.7443 | 3.0186 | 3.0546 | 3.0985 | 3.1498 | 2.1529 | 2.5945 | 2.6225 | 2.6608 | 2.1529 | 3.2008 | 3.6068 | 3.632 | 3.6654 | 3.8814
2022-01-01 20:00 | 2.6483 | 2.9253 | 2.9662 | 3.0163 | 3.0747 | 2.0386 | 2.4665 | 2.4984 | 2.542 | 2.0386 | 3.4295 | 3.8678 | 3.8964 | 3.9345 | 4.1686
2022-01-01 21:00 | 2.6483 | 2.935 | 2.9808 | 3.0369 | 3.1024 | 2.0005 | 2.4285 | 2.4643 | 2.5131 | 2.0005 | 2.6674 | 3.0277 | 3.0598 | 3.1025 | 3.3002
2022-01-01 22:00 | 2.4197 | 2.691 | 2.7376 | 2.7948 | 2.8614 | 1.8329 | 2.2317 | 2.2681 | 2.3179 | 1.8329 | 2.5721 | 2.923 | 2.9557 | 2.9992 | 3.1926
2022-01-01 23:00 | 2.191 | 2.4394 | 2.483 | 2.5364 | 2.5987 | 1.6195 | 1.9752 | 2.0093 | 2.0558 | 1.6195 | 2.1529 | 2.453 | 2.4836 | 2.5242 | 2.6912
2022-01-02 | 1.9624 | 2.1853 | 2.2246 | 2.2728 | 2.3289 | 1.2987 | 1.5902 | 1.6209 | 1.6628 | 1.2987 | 1.6385 | 1.8754 | 1.9029 | 1.9395 | 2.0734
2022-01-02 01:00 | 1.829 | 2.0326 | 2.0671 | 2.1093 | 2.1586 | 1.1681 | 1.4291 | 1.456 | 1.4927 | 1.1681 | 1.6576 | 1.8898 | 1.914 | 1.9461 | 2.0757
2022-01-02 02:00 | 1.7147 | 1.9002 | 1.9298 | 1.9661 | 2.0083 | 1.0457 | 1.2775 | 1.3006 | 1.3321 | 1.0457 | 1.3527 | 1.5443 | 1.5651 | 1.5926 | 1.7
2022-01-02 03:00 | 1.6195 | 1.7858 | 1.8092 | 1.8379 | 1.8714 | 0.99962 | 1.2142 | 1.2325 | 1.2575 | 0.99962 | 1.448 | 1.6416 | 1.658 | 1.6799 | 1.7856
2022-01-02 04:00 | 1.5814 | 1.733 | 1.7504 | 1.7717 | 1.7966 | 0.9844 | 1.1877 | 1.2013 | 1.2198 | 0.9844 | 1.2003 | 1.358 | 1.3702 | 1.3864 | 1.4718
2022-01-02 05:00 | 1.546 | 1.6849 | 1.6972 | 1.7122 | 1.7297 | 0.99073 | 1.1878 | 1.1974 | 1.2105 | 0.99073 | 1.2575 | 1.4144 | 1.423 | 1.4344 | 1.5172
2022-01-02 06:00 | 1.4861 | 1.6166 | 1.6268 | 1.6394 | 1.654 | 0.99073 | 1.185 | 1.1929 | 1.2038 | 0.99073 | 1.2575 | 1.4116 | 1.4187 | 1.4283 | 1.5088
2022-01-02 07:00 | 1.3428 | 1.466 | 1.4779 | 1.4925 | 1.5096 | 0.99073 | 1.1874 | 1.1967 | 1.2094 | 0.99073 | 0.95263 | 1.0752 | 1.0835 | 1.0946 | 1.1603
2022-01-02 08:00 | 1.3337 | 1.4653 | 1.4819 | 1.5022 | 1.5258 | 0.89547 | 1.0814 | 1.0944 | 1.112 | 0.89547 | 0.95263 | 1.0816 | 1.0932 | 1.1087 | 1.1795
2022-01-02 09:00 | 1.2394 | 1.3773 | 1.4007 | 1.4293 | 1.4627 | 0.80906 | 0.98906 | 1.0073 | 1.0322 | 0.80906 | 0.7621 | 0.87934 | 0.89573 | 0.91752 | 0.98546
2022-01-02 10:00 | 1.3337 | 1.4929 | 1.5235 | 1.5611 | 1.6049 | 0.74305 | 0.92142 | 0.94535 | 0.97802 | 0.74305 | 0.85737 | 0.99529 | 1.0168 | 1.0453 | 1.1266
2022-01-02 11:00 | 1.4289 | 1.6062 | 1.6424 | 1.6868 | 1.7386 | 0.83831 | 1.0419 | 1.0702 | 1.1088 | 0.83831 | 0.724 | 0.85484 | 0.88025 | 0.91401 | 0.99418
2022-01-02 12:00 | 1.6622 | 1.8611 | 1.8995 | 1.9466 | 2.0016 | 1.0369 | 1.2797 | 1.3097 | 1.3507 | 1.0369 | 0.45726 | 0.56151 | 0.58847 | 0.62429 | 0.69227
2022-01-02 13:00 | 2.0754 | 2.3039 | 2.3419 | 2.3883 | 2.4425 | 1.2003 | 1.472 | 1.5015 | 1.542 | 1.2003 | 0.53347 | 0.64545 | 0.67204 | 0.70736 | 0.77893
2022-01-02 14:00 | 2.5911 | 2.8531 | 2.8885 | 2.9318 | 2.9823 | 1.9815 | 2.3912 | 2.4188 | 2.4565 | 1.9815 | 2.8007 | 3.1614 | 3.1862 | 3.2192 | 3.4125
2022-01-02 15:00 | 2.8007 | 3.0728 | 3.1055 | 3.1454 | 3.192 | 2.3816 | 2.8599 | 2.8853 | 2.9201 | 2.3816 | 3.7343 | 4.195 | 4.2179 | 4.2483 | 4.4899
2022-01-02 16:00 | 2.8388 | 3.1102 | 3.141 | 3.1787 | 3.2226 | 2.191 | 2.6322 | 2.6562 | 2.689 | 2.191 | 3.1627 | 3.5573 | 3.5789 | 3.6076 | 3.8157
2022-01-02 17:00 | 3.1627 | 3.4573 | 3.4877 | 3.5248 | 3.5682 | 2.3816 | 2.8567 | 2.8803 | 2.9127 | 2.3816 | 4.0582 | 4.5518 | 4.5731 | 4.6013 | 4.8582
2022-01-02 18:00 | 3.277 | 3.5836 | 3.6158 | 3.6552 | 3.7011 | 2.7055 | 3.2419 | 3.267 | 3.3012 | 2.7055 | 4.0963 | 4.5967 | 4.6192 | 4.6492 | 4.9102
2022-01-02 19:00 | 3.0942 | 3.3946 | 3.4305 | 3.4745 | 3.5258 | 2.5606 | 3.0761 | 3.1042 | 3.1424 | 2.5606 | 3.7724 | 4.2419 | 4.2671 | 4.3006 | 4.548
2022-01-02 20:00 | 2.5911 | 2.8639 | 2.9048 | 2.9549 | 3.0133 | 2.1148 | 2.5566 | 2.5885 | 2.632 | 2.1148 | 2.8198 | 3.1902 | 3.2189 | 3.257 | 3.4576
2022-01-02 21:00 | 2.428 | 2.6983 | 2.7441 | 2.8003 | 2.8657 | 2.0511 | 2.4882 | 2.524 | 2.5728 | 2.0511 | 2.534 | 2.8795 | 2.9116 | 2.9543 | 3.1447
2022-01-02 22:00 | 2.3816 | 2.65 | 2.6967 | 2.7539 | 2.8205 | 1.8655 | 2.2702 | 2.3066 | 2.3563 | 1.8655 | 2.4197 | 2.7536 | 2.7863 | 2.8298 | 3.0148
2022-01-02 23:00 | 2.172 | 2.4189 | 2.4626 | 2.516 | 2.5783 | 1.6036 | 1.9565 | 1.9906 | 2.037 | 1.6036 | 2.0005 | 2.2836 | 2.3142 | 2.3548 | 2.5134
2022-01-03 | 2.0386 | 2.2672 | 2.3065 | 2.3547 | 2.4108 | 1.337 | 1.6354 | 1.6661 | 1.7079 | 1.337 | 1.6576 | 1.8965 | 1.9241 | 1.9607 | 2.0956
2022-01-03 01:00 | 1.829 | 2.0326 | 2.0671 | 2.1093 | 2.1586 | 1.2283 | 1.5001 | 1.527 | 1.5637 | 1.2283 | 1.467 | 1.6781 | 1.7023 | 1.7344 | 1.8535
2022-01-03 02:00 | 1.7338 | 1.9207 | 1.9503 | 1.9865 | 2.0288 | 1.0872 | 1.3265 | 1.3496 | 1.3811 | 1.0872 | 1.3718 | 1.5655 | 1.5862 | 1.6138 | 1.7222
2022-01-03 03:00 | 1.6766 | 1.8472 | 1.8706 | 1.8993 | 1.9328 | 1.0399 | 1.2618 | 1.2801 | 1.3051 | 1.0399 | 1.4099 | 1.5993 | 1.6157 | 1.6375 | 1.7411
2022-01-03 04:00 | 1.6576 | 1.8149 | 1.8323 | 1.8536 | 1.8784 | 0.99073 | 1.1952 | 1.2087 | 1.2273 | 0.99073 | 1.3527 | 1.5274 | 1.5396 | 1.5558 | 1.6495
2022-01-03 05:00 | 1.6576 | 1.8048 | 1.8171 | 1.8321 | 1.8496 | 0.99073 | 1.1878 | 1.1974 | 1.2105 | 0.99073 | 1.3718 | 1.5414 | 1.55 | 1.5614 | 1.6505
2022-01-03 06:00 | 1.5433 | 1.678 | 1.6882 | 1.7008 | 1.7154 | 1.0098 | 1.2075 | 1.2154 | 1.2263 | 1.0098 | 1.1622 | 1.3057 | 1.3129 | 1.3224 | 1.3977
2022-01-03 07:00 | 1.4861 | 1.6199 | 1.6319 | 1.6465 | 1.6635 | 1.0098 | 1.2099 | 1.2192 | 1.2319 | 1.0098 | 0.99073 | 1.1175 | 1.1259 | 1.137 | 1.2047
2022-01-03 08:00 | 1.5623 | 1.7109 | 1.7275 | 1.7478 | 1.7714 | 0.99073 | 1.194 | 1.2069 | 1.2246 | 0.99073 | 0.97168 | 1.1028 | 1.1144 | 1.1298 | 1.2017
2022-01-03 09:00 | 1.5814 | 1.7447 | 1.7681 | 1.7968 | 1.8302 | 0.89547 | 1.0911 | 1.1094 | 1.1343 | 0.89547 | 0.78115 | 0.90051 | 0.91691 | 0.93869 | 1.0077
2022-01-03 10:00 | 1.7147 | 1.9023 | 1.9329 | 1.9705 | 2.0143 | 0.87642 | 1.079 | 1.1029 | 1.1356 | 0.87642 | 0.85737 | 0.99529 | 1.0168 | 1.0453 | 1.1266
2022-01-03 11:00 | 1.5242 | 1.7085 | 1.7448 | 1.7892 | 1.8409 | 0.95263 | 1.177 | 1.2052 | 1.2439 | 0.95263 | 0.83831 | 0.98187 | 1.0073 | 1.041 | 1.1275
2022-01-03 12:00 | 1.7528 | 1.9585 | 1.997 | 2.0441 | 2.099 | 1.2575 | 1.5402 | 1.5703 | 1.6112 | 1.2575 | 0.74305 | 0.87909 | 0.90605 | 0.94188 | 1.0256
2022-01-03 13:00 | 1.9434 | 2.1621 | 2.2001 | 2.2465 | 2.3007 | 1.2575 | 1.5395 | 1.5691 | 1.6095 | 1.2575 | 0.93358 | 1.0901 | 1.1167 | 1.152 | 1.2455
2022-01-03 14:00 | 2.7559 | 3.0301 | 3.0655 | 3.1088 | 3.1594 | 2.0767 | 2.5037 | 2.5313 | 2.569 | 2.0767 | 2.6102 | 2.9497 | 2.9745 | 3.0075 | 3.1903
2022-01-03 15:00 | 2.7626 | 3.0319 | 3.0645 | 3.1045 | 3.1511 | 2.0491 | 2.4671 | 2.4926 | 2.5274 | 2.0491 | 2.4858 | 2.8076 | 2.8304 | 2.8608 | 3.0338
2022-01-03 16:00 | 2.6674 | 2.926 | 2.9568 | 2.9945 | 3.0384 | 1.81 | 2.182 | 2.2061 | 2.2389 | 1.81 | 2.3435 | 2.6469 | 2.6685 | 2.6972 | 2.8603
2022-01-03 17:00 | 2.7817 | 3.0479 | 3.0783 | 3.1154 | 3.1588 | 2.2673 | 2.7216 | 2.7453 | 2.7776 | 2.2673 | 3.3723 | 3.7896 | 3.8109 | 3.8391 | 4.0583
2022-01-03 18:00 | 2.4197 | 2.6625 | 2.6947 | 2.7341 | 2.78 | 1.8862 | 2.274 | 2.2991 | 2.3334 | 1.8862 | 2.4578 | 2.7758 | 2.7984 | 2.8283 | 2.9993
2022-01-03 19:00 | 2.4197 | 2.6699 | 2.7058 | 2.7498 | 2.8011 | 1.8672 | 2.2569 | 2.2849 | 2.3232 | 1.8672 | 2.6674 | 3.014 | 3.0391 | 3.0726 | 3.2592
2022-01-03 20:00 | 2.5149 | 2.782 | 2.8229 | 2.873 | 2.9314 | 1.8862 | 2.2865 | 2.3184 | 2.3619 | 1.8862 | 2.8579 | 3.2326 | 3.2613 | 3.2993 | 3.502
2022-01-03 21:00 | 2.4006 | 2.6689 | 2.7147 | 2.7708 | 2.8363 | 1.8475 | 2.2477 | 2.2835 | 2.3323 | 1.8475 | 2.8769 | 3.2606 | 3.2927 | 3.3354 | 3.5446
2022-01-03 22:00 | 2.2209 | 2.4774 | 2.5241 | 2.5813 | 2.6479 | 1.6385 | 2.0021 | 2.0385 | 2.0882 | 1.6385 | 2.4578 | 2.796 | 2.8287 | 2.8722 | 3.0592
2022-01-03 23:00 | 2.0577 | 2.2961 | 2.3397 | 2.3932 | 2.4555 | 1.3858 | 1.6992 | 1.7332 | 1.7797 | 1.3858 | 2.172 | 2.4742 | 2.5048 | 2.5454 | 2.7134
2022-01-04 | 1.851 | 2.0656 | 2.1049 | 2.1531 | 2.2092 | 1.2404 | 1.5213 | 1.552 | 1.5939 | 1.2404 | 1.5433 | 1.7695 | 1.7971 | 1.8337 | 1.9623
2022-01-04 01:00 | 1.7528 | 1.9507 | 1.9852 | 2.0274 | 2.0767 | 1.1432 | 1.3995 | 1.4265 | 1.4632 | 1.1432 | 1.3718 | 1.5723 | 1.5964 | 1.6286 | 1.7424
2022-01-04 02:00 | 1.6766 | 1.8592 | 1.8889 | 1.9251 | 1.9674 | 1.0373 | 1.2676 | 1.2907 | 1.3222 | 1.0373 | 1.4289 | 1.629 | 1.6497 | 1.6773 | 1.7888
2022-01-04 03:00 | 1.6576 | 1.8267 | 1.8501 | 1.8788 | 1.9123 | 1.0098 | 1.2263 | 1.2445 | 1.2695 | 1.0098 | 1.4099 | 1.5993 | 1.6157 | 1.6375 | 1.7411
2022-01-04 04:00 | 1.6576 | 1.8149 | 1.8323 | 1.8536 | 1.8784 | 0.99098 | 1.1955 | 1.209 | 1.2276 | 0.99098 | 1.3527 | 1.5274 | 1.5396 | 1.5558 | 1.6495
2022-01-04 05:00 | 1.6385 | 1.7843 | 1.7966 | 1.8116 | 1.8291 | 1.0098 | 1.2103 | 1.2199 | 1.233 | 1.0098 | 1.5242 | 1.7108 | 1.7194 | 1.7308 | 1.8282
2022-01-04 06:00 | 1.6004 | 1.7394 | 1.7497 | 1.7622 | 1.7768 | 1.086 | 1.2975 | 1.3055 | 1.3164 | 1.086 | 1.3337 | 1.4962 | 1.5034 | 1.5129 | 1.5977
2022-01-04 07:00 | 1.6957 | 1.8451 | 1.857 | 1.8716 | 1.8887 | 1.1622 | 1.3899 | 1.3993 | 1.412 | 1.1622 | 1.1241 | 1.2657 | 1.2741 | 1.2852 | 1.3603
2022-01-04 08:00 | 1.7909 | 1.9565 | 1.9731 | 1.9934 | 2.0171 | 1.1622 | 1.3966 | 1.4095 | 1.4271 | 1.1622 | 1.105 | 1.251 | 1.2626 | 1.278 | 1.3572
2022-01-04 09:00 | 1.9243 | 2.1132 | 2.1366 | 2.1652 | 2.1986 | 1.0288 | 1.2487 | 1.2669 | 1.2919 | 1.0288 | 1.2956 | 1.4722 | 1.4886 | 1.5103 | 1.6076
2022-01-04 10:00 | 1.7147 | 1.9023 | 1.9329 | 1.9705 | 2.0143 | 1.0288 | 1.259 | 1.283 | 1.3156 | 1.0288 | 0.95263 | 1.1012 | 1.1226 | 1.1512 | 1.2377
2022-01-04 11:00 | 1.7528 | 1.9541 | 1.9904 | 2.0348 | 2.0865 | 0.70494 | 0.88436 | 0.91264 | 0.95126 | 0.70494 | 1.3718 | 1.5747 | 1.6001 | 1.6339 | 1.7496
2022-01-04 12:00 | 1.7909 | 1.9994 | 2.0379 | 2.085 | 2.1399 | 0.80021 | 1 | 1.0301 | 1.0711 | 0.80021 | 1.2956 | 1.4931 | 1.52 | 1.5559 | 1.6699
2022-01-04 13:00 | 1.8388 | 2.0498 | 2.0877 | 2.1342 | 2.1883 | 0.80021 | 0.99929 | 1.0289 | 1.0693 | 0.80021 | 1.2194 | 1.4077 | 1.4342 | 1.4696 | 1.5788
2022-01-04 14:00 | 2.0958 | 2.3209 | 2.3563 | 2.3996 | 2.4501 | 1.086 | 1.3333 | 1.3609 | 1.3986 | 1.086 | 1.1241 | 1.2983 | 1.3231 | 1.356 | 1.4572
2022-01-04 15:00 | 2.553 | 2.8067 | 2.8394 | 2.8793 | 2.9259 | 1.4861 | 1.802 | 1.8275 | 1.8622 | 1.4861 | 1.2194 | 1.4003 | 1.4232 | 1.4535 | 1.5569
2022-01-04 16:00 | 2.6102 | 2.8645 | 2.8954 | 2.9331 | 2.977 | 1.6195 | 1.957 | 1.981 | 2.0138 | 1.6195 | 1.2384 | 1.4189 | 1.4405 | 1.4692 | 1.5715
2022-01-04 17:00 | 2.6293 | 2.8842 | 2.9145 | 2.9517 | 2.995 | 1.829 | 2.2039 | 2.2276 | 2.2599 | 1.829 | 2.2482 | 2.5404 | 2.5617 | 2.59 | 2.7474
2022-01-04 18:00 | 2.8769 | 3.1538 | 3.186 | 3.2254 | 3.2713 | 2.2101 | 2.6567 | 2.6818 | 2.716 | 2.2101 | 2.915 | 3.284 | 3.3065 | 3.3365 | 3.5325
2022-01-04 19:00 | 2.674 | 2.9432 | 2.9791 | 3.0231 | 3.0744 | 2.0767 | 2.5045 | 2.5325 | 2.5707 | 2.0767 | 2.896 | 3.268 | 3.2932 | 3.3266 | 3.5259
2022-01-04 20:00 | 2.4768 | 2.7411 | 2.782 | 2.8321 | 2.8905 | 1.9624 | 2.3765 | 2.4084 | 2.452 | 1.9624 | 2.6102 | 2.9573 | 2.986 | 3.0241 | 3.2131
2022-01-04 21:00 | 2.4768 | 2.7507 | 2.7966 | 2.8527 | 2.9182 | 1.8481 | 2.2485 | 2.2842 | 2.3331 | 1.8481 | 2.5911 | 2.943 | 2.9752 | 3.0178 | 3.2113
2022-01-04 22:00 | 2.2926 | 2.5544 | 2.6011 | 2.6583 | 2.7249 | 1.658 | 2.0251 | 2.0615 | 2.1112 | 1.658 | 2.2863 | 2.6054 | 2.6381 | 2.6816 | 2.8593
2022-01-04 23:00 | 2.1339 | 2.378 | 2.4216 | 2.475 | 2.5373 | 1.3822 | 1.6949 | 1.729 | 1.7754 | 1.3822 | 1.81 | 2.0719 | 2.1025 | 2.1431 | 2.2912
2022-01-05 | 1.9072 | 2.126 | 2.1653 | 2.2135 | 2.2696 | 1.2194 | 1.4964 | 1.5271 | 1.569 | 1.2194 | 1.6004 | 1.833 | 1.8606 | 1.8972 | 2.029
2022-01-05 01:00 | 1.81 | 2.0121 | 2.0466 | 2.0888 | 2.1381 | 1.1191 | 1.3711 | 1.398 | 1.4348 | 1.1191 | 1.448 | 1.6569 | 1.6811 | 1.7133 | 1.8313
2022-01-05 02:00 | 1.681 | 1.8639 | 1.8935 | 1.9298 | 1.972 | 1.0274 | 1.2558 | 1.2789 | 1.3105 | 1.0274 | 1.4099 | 1.6078 | 1.6286 | 1.6561 | 1.7666
2022-01-05 03:00 | 1.6516 | 1.8203 | 1.8437 | 1.8724 | 1.9059 | 0.99073 | 1.2037 | 1.222 | 1.247 | 0.99073 | 1.3527 | 1.5357 | 1.5522 | 1.574 | 1.6745
2022-01-05 04:00 | 1.6576 | 1.8149 | 1.8323 | 1.8536 | 1.8784 | 1.0098 | 1.2177 | 1.2312 | 1.2498 | 1.0098 | 1.2765 | 1.4427 | 1.4549 | 1.4711 | 1.5606
2022-01-05 05:00 | 1.6385 | 1.7843 | 1.7966 | 1.8116 | 1.8291 | 1.0098 | 1.2103 | 1.2199 | 1.233 | 1.0098 | 1.2003 | 1.3509 | 1.3594 | 1.3709 | 1.4505
2022-01-05 06:00 | 1.5433 | 1.678 | 1.6882 | 1.7008 | 1.7154 | 1.1241 | 1.3425 | 1.3505 | 1.3614 | 1.1241 | 1.2003 | 1.348 | 1.3552 | 1.3647 | 1.4421
2022-01-05 07:00 | 1.7147 | 1.8656 | 1.8775 | 1.8921 | 1.9092 | 1.1241 | 1.3449 | 1.3542 | 1.367 | 1.1241 | 1.2575 | 1.4139 | 1.4223 | 1.4334 | 1.5158
2022-01-05 08:00 | 1.829 | 1.9975 | 2.0141 | 2.0343 | 2.058 | 1.2003 | 1.4416 | 1.4545 | 1.4722 | 1.2003 | 1.2575 | 1.4204 | 1.432 | 1.4474 | 1.535
2022-01-05 09:00 | 2.0767 | 2.2769 | 2.3003 | 2.329 | 2.3624 | 1.1432 | 1.3837 | 1.402 | 1.4269 | 1.1432 | 1.105 | 1.2604 | 1.2768 | 1.2986 | 1.3854
2022-01-05 10:00 | 2.0386 | 2.2502 | 2.2809 | 2.3184 | 2.3622 | 1.0479 | 1.2815 | 1.3055 | 1.3381 | 1.0479 | 1.1813 | 1.3552 | 1.3767 | 1.4053 | 1.5044
2022-01-05 11:00 | 1.8672 | 2.0769 | 2.1132 | 2.1576 | 2.2094 | 1.105 | 1.357 | 1.3853 | 1.4239 | 1.105 | 1.2194 | 1.4053 | 1.4307 | 1.4645 | 1.5719
2022-01-05 12:00 | 2.0767 | 2.3064 | 2.3449 | 2.392 | 2.447 | 1.086 | 1.3377 | 1.3677 | 1.4087 | 1.086 | 1.3146 | 1.5143 | 1.5412 | 1.577 | 1.6922
2022-01-05 13:00 | 2.1529 | 2.3873 | 2.4252 | 2.4717 | 2.5258 | 1.0551 | 1.3004 | 1.33 | 1.3704 | 1.0551 | 1.1622 | 1.3441 | 1.3707 | 1.406 | 1.5122
2022-01-05 14:00 | 2.191 | 2.4232 | 2.4586 | 2.502 | 2.5525 | 1.1432 | 1.4008 | 1.4284 | 1.4661 | 1.1432 | 1.1432 | 1.3194 | 1.3442 | 1.3772 | 1.4794
2022-01-05 15:00 | 2.4959 | 2.7453 | 2.778 | 2.8179 | 2.8645 | 1.4099 | 1.712 | 1.7374 | 1.7722 | 1.4099 | 1.3146 | 1.5061 | 1.529 | 1.5594 | 1.668
2022-01-05 16:00 | 2.4959 | 2.7417 | 2.7725 | 2.8102 | 2.8542 | 1.5814 | 1.912 | 1.936 | 1.9688 | 1.5814 | 1.3527 | 1.546 | 1.5675 | 1.5962 | 1.7049
2022-01-05 17:00 | 2.3625 | 2.5976 | 2.628 | 2.6651 | 2.7085 | 1.6576 | 2.0014 | 2.025 | 2.0574 | 1.6576 | 2.1529 | 2.4346 | 2.4559 | 2.4841 | 2.6363
2022-01-05 18:00 | 2.5149 | 2.7649 | 2.7971 | 2.8364 | 2.8824 | 2.0386 | 2.4541 | 2.4792 | 2.5135 | 2.0386 | 2.2291 | 2.5218 | 2.5443 | 2.5743 | 2.7326
2022-01-05 19:00 | 2.4197 | 2.6699 | 2.7058 | 2.7498 | 2.8011 | 1.9624 | 2.3694 | 2.3974 | 2.4357 | 1.9624 | 2.3244 | 2.6329 | 2.658 | 2.6915 | 2.8593
2022-01-05 20:00 | 2.4006 | 2.6592 | 2.7001 | 2.7502 | 2.8086 | 1.9243 | 2.3315 | 2.3634 | 2.407 | 1.9243 | 2.4197 | 2.7456 | 2.7743 | 2.8124 | 2.9909
2022-01-05 21:00 | 2.2882 | 2.5481 | 2.594 | 2.6501 | 2.7156 | 1.7909 | 2.1809 | 2.2167 | 2.2655 | 1.7909 | 2.5721 | 2.9219 | 2.954 | 2.9967 | 3.1891
2022-01-05 22:00 | 2.2101 | 2.4658 | 2.5125 | 2.5696 | 2.6363 | 1.6195 | 1.9796 | 2.016 | 2.0657 | 1.6195 | 2.1148 | 2.4149 | 2.4476 | 2.4911 | 2.6593
2022-01-05 23:00 | 2.0577 | 2.2961 | 2.3397 | 2.3932 | 2.4555 | 1.3999 | 1.7158 | 1.7499 | 1.7964 | 1.3999 | 1.9053 | 2.1778 | 2.2083 | 2.249 | 2.4023
2022-01-06 | 1.9434 | 2.1648 | 2.2042 | 2.2523 | 2.3084 | 1.2065 | 1.4812 | 1.5119 | 1.5538 | 1.2065 | 1.5433 | 1.7695 | 1.7971 | 1.8337 | 1.9623
2022-01-06 01:00 | 1.7719 | 1.9712 | 2.0057 | 2.0479 | 2.0972 | 1.1272 | 1.3807 | 1.4077 | 1.4444 | 1.1272 | 1.3337 | 1.5299 | 1.5541 | 1.5862 | 1.698
2022-01-06 02:00 | 1.7338 | 1.9207 | 1.9503 | 1.9865 | 2.0288 | 1.0363 | 1.2663 | 1.2894 | 1.3209 | 1.0363 | 1.3527 | 1.5443 | 1.5651 | 1.5926 | 1.7
2022-01-06 03:00 | 1.6957 | 1.8676 | 1.8911 | 1.9198 | 1.9532 | 1.0078 | 1.2239 | 1.2422 | 1.2672 | 1.0078 | 1.2765 | 1.4511 | 1.4675 | 1.4893 | 1.5856
2022-01-06 04:00 | 1.6957 | 1.8558 | 1.8732 | 1.8945 | 1.9194 | 0.99007 | 1.1944 | 1.208 | 1.2265 | 0.99007 | 1.2575 | 1.4215 | 1.4337 | 1.4499 | 1.5384
2022-01-06 05:00 | 1.6576 | 1.8048 | 1.8171 | 1.8321 | 1.8496 | 1.041 | 1.2472 | 1.2568 | 1.2699 | 1.041 | 1.4289 | 1.6049 | 1.6135 | 1.6249 | 1.7171
2022-01-06 06:00 | 1.6576 | 1.8008 | 1.8111 | 1.8236 | 1.8382 | 1.086 | 1.2975 | 1.3055 | 1.3164 | 1.086 | 1.3527 | 1.5174 | 1.5246 | 1.5341 | 1.6199
2022-01-06 07:00 | 1.9521 | 2.1206 | 2.1325 | 2.1471 | 2.1642 | 1.298 | 1.5503 | 1.5596 | 1.5724 | 1.298 | 1.448 | 1.6256 | 1.634 | 1.6451 | 1.738
2022-01-06 08:00 | 2.0577 | 2.2431 | 2.2597 | 2.28 | 2.3036 | 1.3337 | 1.5991 | 1.6121 | 1.6297 | 1.3337 | 1.4289 | 1.6109 | 1.6225 | 1.638 | 1.735
2022-01-06 09:00 | 2.0577 | 2.2565 | 2.2798 | 2.3085 | 2.3419 | 1.2929 | 1.5606 | 1.5789 | 1.6038 | 1.2929 | 1.2956 | 1.4722 | 1.4886 | 1.5103 | 1.6076
2022-01-06 10:00 | 1.9815 | 2.1888 | 2.2195 | 2.257 | 2.3008 | 1.086 | 1.3266 | 1.3505 | 1.3832 | 1.086 | 1.5242 | 1.7363 | 1.7578 | 1.7864 | 1.9043
2022-01-06 11:00 | 2.0196 | 2.2407 | 2.277 | 2.3213 | 2.3731 | 0.99073 | 1.222 | 1.2503 | 1.2889 | 0.99073 | 1.4289 | 1.6382 | 1.6636 | 1.6974 | 1.8163
2022-01-06 12:00 | 2.5911 | 2.8591 | 2.8976 | 2.9447 | 2.9996 | 1.4289 | 1.7428 | 1.7728 | 1.8138 | 1.4289 | 1.4861 | 1.7048 | 1.7318 | 1.7676 | 1.8921
2022-01-06 13:00 | 2.553 | 2.8171 | 2.8551 | 2.9015 | 2.9557 | 1.4861 | 1.8096 | 1.8392 | 1.8796 | 1.4861 | 1.9053 | 2.1699 | 2.1964 | 2.2318 | 2.3787
2022-01-06 14:00 | 2.553 | 2.8121 | 2.8475 | 2.8909 | 2.9414 | 1.5242 | 1.851 | 1.8786 | 1.9163 | 1.5242 | 1.7528 | 1.9969 | 2.0217 | 2.0547 | 2.1905
2022-01-06 15:00 | 2.7055 | 2.9705 | 3.0031 | 3.0431 | 3.0896 | 1.6385 | 1.9821 | 2.0075 | 2.0423 | 1.6385 | 1.9243 | 2.1837 | 2.2065 | 2.2369 | 2.379
2022-01-06 16:00 | 2.6864 | 2.9464 | 2.9772 | 3.0149 | 3.0589 | 1.6766 | 2.0245 | 2.0485 | 2.0813 | 1.6766 | 2.6102 | 2.9433 | 2.9649 | 2.9936 | 3.1714
2022-01-06 17:00 | 2.5149 | 2.7613 | 2.7917 | 2.8289 | 2.8722 | 1.7719 | 2.1364 | 2.1601 | 2.1924 | 1.7719 | 2.5721 | 2.9004 | 2.9216 | 2.9499 | 3.1251
2022-01-06 18:00 | 2.3435 | 2.5807 | 2.6128 | 2.6522 | 2.6981 | 1.7909 | 2.1615 | 2.1866 | 2.2208 | 1.7909 | 2.4197 | 2.7335 | 2.756 | 2.786 | 2.9548
2022-01-06 19:00 | 2.3584 | 2.604 | 2.64 | 2.684 | 2.7352 | 1.7909 | 2.1668 | 2.1949 | 2.2331 | 1.7909 | 2.5911 | 2.9293 | 2.9544 | 2.9879 | 3.1703
2022-01-06 20:00 | 2.4197 | 2.6797 | 2.7206 | 2.7707 | 2.829 | 1.7528 | 2.1289 | 2.1608 | 2.2044 | 1.7528 | 2.5149 | 2.8515 | 2.8802 | 2.9182 | 3.102
2022-01-06 21:00 | 2.3435 | 2.6074 | 2.6533 | 2.7094 | 2.7749 | 1.7338 | 2.1134 | 2.1492 | 2.198 | 1.7338 | 2.191 | 2.4984 | 2.5305 | 2.5732 | 2.7447
2022-01-06 22:00 | 2.1543 | 2.4059 | 2.4525 | 2.5097 | 2.5763 | 1.5814 | 1.9345 | 1.971 | 2.0207 | 1.5814 | 2.2673 | 2.5843 | 2.617 | 2.6604 | 2.837
2022-01-06 23:00 | 2.0005 | 2.2347 | 2.2783 | 2.3318 | 2.394 | 1.4227 | 1.7428 | 1.7769 | 1.8233 | 1.4227 | 1.8481 | 2.1142 | 2.1448 | 2.1855 | 2.3356
2022-01-07 | 1.8495 | 2.064 | 2.1033 | 2.1515 | 2.2076 | 1.2575 | 1.5414 | 1.5721 | 1.614 | 1.2575 | 1.5623 | 1.7907 | 1.8182 | 1.8549 | 1.9845
2022-01-07 01:00 | 1.7416 | 1.9386 | 1.9731 | 2.0154 | 2.0646 | 1.1096 | 1.3599 | 1.3868 | 1.4235 | 1.1096 | 1.3146 | 1.5087 | 1.5329 | 1.565 | 1.6757
2022-01-07 02:00 | 1.6957 | 1.8797 | 1.9093 | 1.9456 | 1.9879 | 1.0479 | 1.28 | 1.3031 | 1.3347 | 1.0479 | 1.3718 | 1.5655 | 1.5862 | 1.6138 | 1.7222
2022-01-07 03:00 | 1.6957 | 1.8676 | 1.8911 | 1.9198 | 1.9532 | 1.0256 | 1.245 | 1.2633 | 1.2882 | 1.0256 | 1.2575 | 1.4299 | 1.4463 | 1.4681 | 1.5634
2022-01-07 04:00 | 1.6385 | 1.7944 | 1.8118 | 1.8331 | 1.858 | 1.0288 | 1.2402 | 1.2538 | 1.2723 | 1.0288 | 1.2003 | 1.358 | 1.3702 | 1.3864 | 1.4718
2022-01-07 05:00 | 1.7338 | 1.8867 | 1.8989 | 1.9139 | 1.9314 | 1.0669 | 1.2779 | 1.2874 | 1.3005 | 1.0669 | 1.2003 | 1.3509 | 1.3594 | 1.3709 | 1.4505
2022-01-07 06:00 | 1.6724 | 1.8168 | 1.827 | 1.8395 | 1.8541 | 1.105 | 1.32 | 1.328 | 1.3389 | 1.105 | 1.2194 | 1.3692 | 1.3764 | 1.3859 | 1.4643
2022-01-07 07:00 | 1.8672 | 2.0293 | 2.0413 | 2.0559 | 2.0729 | 1.2003 | 1.435 | 1.4443 | 1.457 | 1.2003 | 1.3337 | 1.4986 | 1.507 | 1.5181 | 1.6047
2022-01-07 08:00 | 1.9219 | 2.0973 | 2.1139 | 2.1342 | 2.1578 | 1.2003 | 1.4416 | 1.4545 | 1.4722 | 1.2003 | 1.3908 | 1.5686 | 1.5802 | 1.5956 | 1.6905
2022-01-07 09:00 | 2.0386 | 2.236 | 2.2594 | 2.288 | 2.3214 | 1.2003 | 1.4513 | 1.4695 | 1.4944 | 1.2003 | 1.086 | 1.2393 | 1.2557 | 1.2774 | 1.3632
2022-01-07 10:00 | 2.1971 | 2.4205 | 2.4512 | 2.4887 | 2.5325 | 1.3337 | 1.6192 | 1.6431 | 1.6758 | 1.3337 | 1.2765 | 1.4611 | 1.4826 | 1.5111 | 1.6155
2022-01-07 11:00 | 2.2863 | 2.5273 | 2.5635 | 2.6079 | 2.6597 | 1.467 | 1.7847 | 1.813 | 1.8516 | 1.467 | 1.5433 | 1.7652 | 1.7907 | 1.8244 | 1.9496
2022-01-07 12:00 | 2.3054 | 2.5521 | 2.5906 | 2.6377 | 2.6926 | 1.4861 | 1.8103 | 1.8403 | 1.8813 | 1.4861 | 1.5623 | 1.7895 | 1.8165 | 1.8523 | 1.981
2022-01-07 13:00 | 2.2291 | 2.4691 | 2.5071 | 2.5535 | 2.6077 | 1.2384 | 1.517 | 1.5466 | 1.587 | 1.2384 | 1.6385 | 1.8734 | 1.9 | 1.9354 | 2.0677
2022-01-07 14:00 | 2.3816 | 2.6279 | 2.6633 | 2.7066 | 2.7572 | 1.4289 | 1.7384 | 1.766 | 1.8037 | 1.4289 | 1.448 | 1.6582 | 1.683 | 1.7159 | 1.835
2022-01-07 15:00 | 2.4006 | 2.643 | 2.6756 | 2.7156 | 2.7621 | 1.6004 | 1.9371 | 1.9625 | 1.9973 | 1.6004 | 1.8481 | 2.099 | 2.1218 | 2.1522 | 2.2901
2022-01-07 16:00 | 1.9815 | 2.1891 | 2.2199 | 2.2576 | 2.3015 | 1.3604 | 1.6509 | 1.6749 | 1.7077 | 1.3604 | 1.1241 | 1.2919 | 1.3135 | 1.3421 | 1.4382
2022-01-07 17:00 | 2.3451 | 2.5789 | 2.6092 | 2.6464 | 2.6898 | 1.7584 | 2.1205 | 2.1442 | 2.1765 | 1.7584 | 2.2291 | 2.5193 | 2.5405 | 2.5688 | 2.7252
2022-01-07 18:00 | 2.3625 | 2.6011 | 2.6333 | 2.6727 | 2.7186 | 1.9053 | 2.2965 | 2.3216 | 2.3559 | 1.9053 | 2.7055 | 3.0511 | 3.0736 | 3.1036 | 3.2881
2022-01-07 19:00 | 2.3435 | 2.588 | 2.624 | 2.6679 | 2.7192 | 1.81 | 2.1893 | 2.2174 | 2.2556 | 1.81 | 2.4578 | 2.7811 | 2.8062 | 2.8397 | 3.0148
2022-01-07 20:00 | 2.2673 | 2.5159 | 2.5568 | 2.6069 | 2.6653 | 1.7528 | 2.1289 | 2.1608 | 2.2044 | 1.7528 | 2.172 | 2.4704 | 2.4991 | 2.5371 | 2.7021
2022-01-07 21:00 | 2.2291 | 2.4846 | 2.5305 | 2.5866 | 2.6521 | 1.6576 | 2.0234 | 2.0592 | 2.108 | 1.6576 | 2.172 | 2.4772 | 2.5094 | 2.5521 | 2.7225
2022-01-07 22:00 | 2.1148 | 2.3635 | 2.4101 | 2.4673 | 2.5339 | 1.5179 | 1.8595 | 1.8959 | 1.9457 | 1.5179 | 1.9243 | 2.2032 | 2.2359 | 2.2793 | 2.4371
2022-01-07 23:00 | 1.9869 | 2.22 | 2.2637 | 2.3171 | 2.3794 | 1.3908 | 1.7051 | 1.7392 | 1.7857 | 1.3908 | 1.6576 | 1.9025 | 1.9331 | 1.9737 | 2.1134
2022-01-08 | 1.8481 | 2.0625 | 2.1018 | 2.15 | 2.2061 | 1.2575 | 1.5414 | 1.5721 | 1.614 | 1.2575 | 1.6004 | 1.833 | 1.8606 | 1.8972 | 2.029
2022-01-08 01:00 | 1.7338 | 1.9302 | 1.9647 | 2.007 | 2.0562 | 1.1241 | 1.377 | 1.4039 | 1.4407 | 1.1241 | 1.467 | 1.6781 | 1.7023 | 1.7344 | 1.8535
2022-01-08 02:00 | 1.6385 | 1.8183 | 1.8479 | 1.8842 | 1.9264 | 1.0479 | 1.28 | 1.3031 | 1.3347 | 1.0479 | 1.2765 | 1.4596 | 1.4804 | 1.5079 | 1.6111
2022-01-08 03:00 | 1.6195 | 1.7858 | 1.8092 | 1.8379 | 1.8714 | 0.99073 | 1.2037 | 1.222 | 1.247 | 0.99073 | 1.3146 | 1.4934 | 1.5098 | 1.5317 | 1.63
2022-01-08 04:00 | 1.6195 | 1.7739 | 1.7913 | 1.8127 | 1.8375 | 0.97168 | 1.1727 | 1.1862 | 1.2048 | 0.97168 | 1.1813 | 1.3368 | 1.349 | 1.3652 | 1.4495
2022-01-08 05:00 | 1.6195 | 1.7639 | 1.7761 | 1.7911 | 1.8086 | 0.99073 | 1.1878 | 1.1974 | 1.2105 | 0.99073 | 1.2575 | 1.4144 | 1.423 | 1.4344 | 1.5172
2022-01-08 06:00 | 1.5242 | 1.6575 | 1.6678 | 1.6803 | 1.6949 | 1.0098 | 1.2075 | 1.2154 | 1.2263 | 1.0098 | 1.3718 | 1.5386 | 1.5458 | 1.5553 | 1.6421
2022-01-08 07:00 | 1.5433 | 1.6814 | 1.6933 | 1.7079 | 1.7249 | 1.086 | 1.2999 | 1.3092 | 1.3219 | 1.086 | 1.2003 | 1.3504 | 1.3588 | 1.3699 | 1.4492
2022-01-08 08:00 | 1.5433 | 1.6904 | 1.707 | 1.7273 | 1.751 | 1.0669 | 1.284 | 1.2969 | 1.3146 | 1.0669 | 1.086 | 1.2298 | 1.2414 | 1.2569 | 1.335
2022-01-08 09:00 | 1.6576 | 1.8266 | 1.85 | 1.8786 | 1.912 | 1.1813 | 1.4288 | 1.447 | 1.4719 | 1.1813 | 1.086 | 1.2393 | 1.2557 | 1.2774 | 1.3632
2022-01-08 10:00 | 1.6195 | 1.7999 | 1.8306 | 1.8681 | 1.9119 | 1.086 | 1.3266 | 1.3505 | 1.3832 | 1.086 | 0.91452 | 1.0588 | 1.0803 | 1.1089 | 1.1933
2022-01-08 11:00 | 1.4859 | 1.6674 | 1.7036 | 1.748 | 1.7998 | 0.99073 | 1.222 | 1.2503 | 1.2889 | 0.99073 | 1.2194 | 1.4053 | 1.4307 | 1.4645 | 1.5719
2022-01-08 12:00 | 1.6385 | 1.8357 | 1.8741 | 1.9212 | 1.9762 | 1.0669 | 1.3152 | 1.3452 | 1.3862 | 1.0669 | 1.1622 | 1.3449 | 1.3718 | 1.4077 | 1.5144
2022-01-08 13:00 | 2.0005 | 2.2235 | 2.2615 | 2.3079 | 2.3621 | 1.4099 | 1.7195 | 1.7491 | 1.7895 | 1.4099 | 1.2194 | 1.4077 | 1.4342 | 1.4696 | 1.5788
2022-01-08 14:00 | 2.0196 | 2.239 | 2.2744 | 2.3177 | 2.3683 | 1.2956 | 1.5809 | 1.6085 | 1.6462 | 1.2956 | 1.2003 | 1.3829 | 1.4077 | 1.4407 | 1.5461
2022-01-08 15:00 | 2.1529 | 2.3769 | 2.4095 | 2.4495 | 2.496 | 1.448 | 1.757 | 1.7825 | 1.8172 | 1.448 | 1.7287 | 1.9663 | 1.9892 | 2.0196 | 2.1509
2022-01-08 16:00 | 2.0005 | 2.2095 | 2.2403 | 2.278 | 2.322 | 1.2765 | 1.5518 | 1.5759 | 1.6087 | 1.2765 | 1.7909 | 2.0329 | 2.0545 | 2.0832 | 2.2159
2022-01-08 17:00 | 2.2101 | 2.4338 | 2.4642 | 2.5014 | 2.5447 | 1.6385 | 1.9788 | 2.0025 | 2.0349 | 1.6385 | 1.9243 | 2.1805 | 2.2018 | 2.2301 | 2.3696
2022-01-08 18:00 | 2.5721 | 2.8263 | 2.8585 | 2.8978 | 2.9438 | 2.0958 | 2.5216 | 2.5467 | 2.581 | 2.0958 | 2.4768 | 2.797 | 2.8196 | 2.8495 | 3.0215
2022-01-08 19:00 | 2.5911 | 2.8541 | 2.8901 | 2.934 | 2.9853 | 2.0005 | 2.4144 | 2.4424 | 2.4807 | 2.0005 | 2.8198 | 3.1833 | 3.2085 | 3.242 | 3.437
2022-01-08 20:00 | 2.4578 | 2.7206 | 2.7615 | 2.8116 | 2.87 | 1.9243 | 2.3315 | 2.3634 | 2.407 | 1.9243 | 2.7626 | 3.1267 | 3.1554 | 3.1935 | 3.3909
2022-01-08 21:00 | 2.3244 | 2.587 | 2.6328 | 2.689 | 2.7544 | 1.8341 | 2.232 | 2.2677 | 2.3166 | 1.8341 | 2.3054 | 2.6254 | 2.6576 | 2.7003 | 2.878
2022-01-08 22:00 | 2.2291 | 2.4863 | 2.533 | 2.5901 | 2.6567 | 1.6576 | 2.0246 | 2.061 | 2.1107 | 1.6576 | 2.0611 | 2.3552 | 2.3879 | 2.4313 | 2.5966
2022-01-08 23:00 | 2.0958 | 2.337 | 2.3807 | 2.4341 | 2.4964 | 1.4861 | 1.8177 | 1.8517 | 1.8982 | 1.4861 | 2.172 | 2.4742 | 2.5048 | 2.5454 | 2.7134
2022-01-09 | 1.9161 | 2.1356 | 2.1749 | 2.2231 | 2.2792 | 1.3007 | 1.5925 | 1.6232 | 1.6651 | 1.3007 | 1.6004 | 1.833 | 1.8606 | 1.8972 | 2.029
2022-01-09 01:00 | 1.7272 | 1.9232 | 1.9577 | 1.9999 | 2.0492 | 1.1307 | 1.3849 | 1.4118 | 1.4485 | 1.1307 | 1.3908 | 1.5934 | 1.6176 | 1.6497 | 1.7646
2022-01-09 02:00 | 1.6385 | 1.8183 | 1.8479 | 1.8842 | 1.9264 | 1.0544 | 1.2877 | 1.3108 | 1.3423 | 1.0544 | 1.3337 | 1.5231 | 1.5439 | 1.5715 | 1.6777
2022-01-09 03:00 | 1.6216 | 1.788 | 1.8115 | 1.8402 | 1.8737 | 0.99159 | 1.2048 | 1.223 | 1.248 | 0.99159 | 1.4099 | 1.5993 | 1.6157 | 1.6375 | 1.7411
2022-01-09 04:00 | 1.6004 | 1.7535 | 1.7709 | 1.7922 | 1.817 | 0.99073 | 1.1952 | 1.2087 | 1.2273 | 0.99073 | 1.3718 | 1.5485 | 1.5607 | 1.5769 | 1.6717
2022-01-09 05:00 | 1.6004 | 1.7434 | 1.7557 | 1.7707 | 1.7882 | 1.0288 | 1.2329 | 1.2424 | 1.2555 | 1.0288 | 1.2384 | 1.3932 | 1.4018 | 1.4132 | 1.4949
2022-01-09 06:00 | 1.5242 | 1.6575 | 1.6678 | 1.6803 | 1.6949 | 1.0479 | 1.2525 | 1.2605 | 1.2714 | 1.0479 | 1.1432 | 1.2845 | 1.2917 | 1.3012 | 1.3755
2022-01-09 07:00 | 1.5001 | 1.635 | 1.6469 | 1.6615 | 1.6785 | 1.0669 | 1.2774 | 1.2867 | 1.2994 | 1.0669 | 1.0479 | 1.181 | 1.1894 | 1.2005 | 1.2714
2022-01-09 08:00 | 1.5814 | 1.7314 | 1.748 | 1.7682 | 1.7919 | 1.1813 | 1.4191 | 1.432 | 1.4496 | 1.1813 | 1.4289 | 1.6109 | 1.6225 | 1.638 | 1.735
2022-01-09 09:00 | 1.6957 | 1.8675 | 1.8909 | 1.9196 | 1.953 | 1.2384 | 1.4963 | 1.5145 | 1.5394 | 1.2384 | 1.3908 | 1.578 | 1.5944 | 1.6162 | 1.7187
2022-01-09 10:00 | 1.6957 | 1.8818 | 1.9125 | 1.95 | 1.9938 | 1.1622 | 1.4166 | 1.4405 | 1.4732 | 1.1622 | 1.2575 | 1.4399 | 1.4614 | 1.49 | 1.5932
2022-01-09 11:00 | 1.7147 | 1.9132 | 1.9495 | 1.9938 | 2.0456 | 1.1443 | 1.4033 | 1.4316 | 1.4702 | 1.1443 | 1.0098 | 1.1724 | 1.1978 | 1.2316 | 1.3275
2022-01-09 12:00 | 1.7147 | 1.9175 | 1.956 | 2.0031 | 2.058 | 1.2003 | 1.4727 | 1.5027 | 1.5437 | 1.2003 | 1.105 | 1.2814 | 1.3083 | 1.3442 | 1.4477
2022-01-09 13:00 | 1.5814 | 1.7732 | 1.8111 | 1.8576 | 1.9118 | 1.0098 | 1.2469 | 1.2765 | 1.3169 | 1.0098 | 0.87642 | 1.0265 | 1.0531 | 1.0885 | 1.1789
2022-01-09 14:00 | 1.5433 | 1.7273 | 1.7627 | 1.806 | 1.8565 | 1.1241 | 1.3783 | 1.4059 | 1.4436 | 1.1241 | 0.93358 | 1.0865 | 1.1113 | 1.1443 | 1.235
2022-01-09 15:00 | 1.622 | 1.8064 | 1.8391 | 1.879 | 1.9256 | 1.0098 | 1.2393 | 1.2648 | 1.2995 | 1.0098 | 0.81926 | 0.95567 | 0.97854 | 1.0089 | 1.0903
2022-01-09 16:00 | 2.0767 | 2.2914 | 2.3222 | 2.3599 | 2.4039 | 1.3525 | 1.6416 | 1.6656 | 1.6984 | 1.3525 | 1.0288 | 1.186 | 1.2076 | 1.2363 | 1.3271
2022-01-09 17:00 | 2.4387 | 2.6795 | 2.7098 | 2.747 | 2.7903 | 1.8293 | 2.2043 | 2.2279 | 2.2603 | 1.8293 | 1.8672 | 2.117 | 2.1383 | 2.1665 | 2.303
2022-01-09 18:00 | 2.534 | 2.7854 | 2.8175 | 2.8569 | 2.9028 | 2.0005 | 2.4091 | 2.4342 | 2.4684 | 2.0005 | 2.534 | 2.8605 | 2.8831 | 2.913 | 3.0881
2022-01-09 19:00 | 2.5721 | 2.8337 | 2.8696 | 2.9136 | 2.9649 | 2.0005 | 2.4144 | 2.4424 | 2.4807 | 2.0005 | 3.1056 | 3.5009 | 3.5261 | 3.5595 | 3.7703
2022-01-09 20:00 | 2.4959 | 2.7615 | 2.8024 | 2.8525 | 2.9109 | 1.9243 | 2.3315 | 2.3634 | 2.407 | 1.9243 | 2.6102 | 2.9573 | 2.986 | 3.0241 | 3.2131
2022-01-09 21:00 | 2.4768 | 2.7507 | 2.7966 | 2.8527 | 2.9182 | 1.8672 | 2.271 | 2.3067 | 2.3556 | 1.8672 | 2.3816 | 2.7101 | 2.7423 | 2.785 | 2.9669
2022-01-09 22:00 | 2.3244 | 2.5886 | 2.6353 | 2.6924 | 2.7591 | 1.6641 | 2.0323 | 2.0687 | 2.1184 | 1.6641 | 2.0767 | 2.3725 | 2.4052 | 2.4487 | 2.6148
2022-01-09 23:00 | 2.0346 | 2.2713 | 2.3149 | 2.3683 | 2.4306 | 1.4289 | 1.7502 | 1.7842 | 1.8307 | 1.4289 | 1.9053 | 2.1778 | 2.2083 | 2.249 | 2.4023
2022-01-10 | 1.8672 | 2.083 | 2.1223 | 2.1704 | 2.2266 | 1.2064 | 1.4811 | 1.5118 | 1.5536 | 1.2064 | 1.5052 | 1.7272 | 1.7547 | 1.7913 | 1.9179
2022-01-10 01:00 | 1.7528 | 1.9507 | 1.9852 | 2.0274 | 2.0767 | 1.0758 | 1.3199 | 1.3468 | 1.3836 | 1.0758 | 1.3146 | 1.5087 | 1.5329 | 1.565 | 1.6757
2022-01-10 02:00 | 1.6847 | 1.8679 | 1.8976 | 1.9338 | 1.9761 | 1.0245 | 1.2525 | 1.2756 | 1.3071 | 1.0245 | 1.2575 | 1.4384 | 1.4592 | 1.4868 | 1.5889
2022-01-10 03:00 | 1.6576 | 1.8267 | 1.8501 | 1.8788 | 1.9123 | 0.99073 | 1.2037 | 1.222 | 1.247 | 0.99073 | 1.3337 | 1.5146 | 1.531 | 1.5528 | 1.6523
2022-01-10 04:00 | 1.7528 | 1.9172 | 1.9346 | 1.9559 | 1.9808 | 0.98825 | 1.1922 | 1.2058 | 1.2243 | 0.98825 | 1.2384 | 1.4003 | 1.4125 | 1.4287 | 1.5162
2022-01-10 05:00 | 1.7528 | 1.9071 | 1.9194 | 1.9344 | 1.9519 | 1.0393 | 1.2452 | 1.2548 | 1.2678 | 1.0393 | 1.3337 | 1.4991 | 1.5077 | 1.5191 | 1.606
2022-01-10 06:00 | 1.8067 | 1.9611 | 1.9713 | 1.9838 | 1.9985 | 1.1813 | 1.41 | 1.418 | 1.4289 | 1.1813 | 1.2956 | 1.4539 | 1.4611 | 1.4706 | 1.5532
2022-01-10 07:00 | 1.9243 | 2.0907 | 2.1027 | 2.1173 | 2.1343 | 1.2765 | 1.525 | 1.5343 | 1.547 | 1.2765 | 1.3337 | 1.4986 | 1.507 | 1.5181 | 1.6047
2022-01-10 08:00 | 1.9209 | 2.0962 | 2.1128 | 2.1331 | 2.1567 | 1.1813 | 1.4191 | 1.432 | 1.4496 | 1.1813 | 1.1622 | 1.3145 | 1.3261 | 1.3416 | 1.4239
2022-01-10 09:00 | 2.1148 | 2.3179 | 2.3413 | 2.3699 | 2.4033 | 1.2956 | 1.5638 | 1.5821 | 1.607 | 1.2956 | 0.99073 | 1.1334 | 1.1498 | 1.1716 | 1.2521
2022-01-10 10:00 | 1.9815 | 2.1888 | 2.2195 | 2.257 | 2.3008 | 0.87642 | 1.079 | 1.1029 | 1.1356 | 0.87642 | 1.0288 | 1.1858 | 1.2073 | 1.2359 | 1.3266
2022-01-10 11:00 | 2.0005 | 2.2202 | 2.2565 | 2.3009 | 2.3526 | 0.89547 | 1.1094 | 1.1377 | 1.1763 | 0.89547 | 0.97168 | 1.1301 | 1.1555 | 1.1892 | 1.283
2022-01-10 12:00 | 2.3435 | 2.593 | 2.6315 | 2.6786 | 2.7335 | 1.0468 | 1.2913 | 1.3214 | 1.3623 | 1.0468 | 0.62873 | 0.75206 | 0.77902 | 0.81485 | 0.89225
2022-01-10 13:00 | 3.1246 | 3.4312 | 3.4691 | 3.5156 | 3.5697 | 1.4861 | 1.8096 | 1.8392 | 1.8796 | 1.4861 | 1.5814 | 1.8099 | 1.8365 | 1.8718 | 2.001
2022-01-10 14:00 | 2.6864 | 2.9554 | 2.9908 | 3.0341 | 3.0847 | 2.191 | 2.6387 | 2.6663 | 2.704 | 2.191 | 1.7909 | 2.0393 | 2.0641 | 2.097 | 2.2349
2022-01-10 15:00 | 3.4295 | 3.7483 | 3.7809 | 3.8209 | 3.8675 | 2.3244 | 2.7924 | 2.8178 | 2.8526 | 2.3244 | 2.7055 | 3.0517 | 3.0746 | 3.105 | 3.29
2022-01-10 16:00 | 3.2642 | 3.5672 | 3.598 | 3.6357 | 3.6797 | 2.2298 | 2.6779 | 2.702 | 2.7348 | 2.2298 | 2.8388 | 3.1974 | 3.219 | 3.2476 | 3.438
2022-01-10 17:00 | 3.4866 | 3.8053 | 3.8356 | 3.8728 | 3.9161 | 2.6864 | 3.2168 | 3.2405 | 3.2728 | 2.6864 | 4.1154 | 4.6153 | 4.6366 | 4.6649 | 4.9249
2022-01-10 18:00 | 3.2961 | 3.6041 | 3.6363 | 3.6757 | 3.7216 | 2.7245 | 3.2644 | 3.2895 | 3.3237 | 2.7245 | 4.363 | 4.8931 | 4.9156 | 4.9456 | 5.2212
2022-01-10 19:00 | 2.9913 | 3.284 | 3.3199 | 3.3639 | 3.4152 | 2.4959 | 2.9996 | 3.0277 | 3.0659 | 2.4959 | 3.7915 | 4.2631 | 4.2883 | 4.3217 | 4.5702
2022-01-10 20:00 | 2.915 | 3.2118 | 3.2528 | 3.3028 | 3.3612 | 2.3435 | 2.8266 | 2.8586 | 2.9021 | 2.3435 | 3.3342 | 3.7619 | 3.7906 | 3.8286 | 4.0575
2022-01-10 21:00 | 2.8579 | 3.1601 | 3.206 | 3.2621 | 3.3275 | 2.2671 | 2.7434 | 2.7792 | 2.828 | 2.2671 | 3.0103 | 3.4088 | 3.4409 | 3.4836 | 3.7002
2022-01-10 22:00 | 2.6483 | 2.9366 | 2.9833 | 3.0404 | 3.1071 | 1.9815 | 2.4072 | 2.4436 | 2.4933 | 1.9815 | 2.7436 | 3.1136 | 3.1463 | 3.1897 | 3.3925
2022-01-10 23:00 | 2.3402 | 2.5996 | 2.6433 | 2.6967 | 2.759 | 1.6385 | 1.9977 | 2.0318 | 2.0783 | 1.6385 | 2.7436 | 3.1093 | 3.1399 | 3.1806 | 3.38
2022-01-11 | 2.0246 | 2.2521 | 2.2914 | 2.3396 | 2.3957 | 1.4227 | 1.7366 | 1.7673 | 1.8092 | 1.4227 | 1.81 | 2.0659 | 2.0935 | 2.1301 | 2.2734
2022-01-11 01:00 | 1.8908 | 2.099 | 2.1335 | 2.1757 | 2.225 | 1.2608 | 1.5385 | 1.5654 | 1.6021 | 1.2608 | 1.7719 | 2.0169 | 2.0411 | 2.0732 | 2.209
2022-01-11 02:00 | 1.81 | 2.0025 | 2.0321 | 2.0684 | 2.1107 | 1.1308 | 1.378 | 1.4011 | 1.4327 | 1.1308 | 1.4099 | 1.6078 | 1.6286 | 1.6561 | 1.7666
2022-01-11 03:00 | 1.776 | 1.9539 | 1.9774 | 2.0061 | 2.0395 | 1.086 | 1.3163 | 1.3346 | 1.3595 | 1.086 | 1.448 | 1.6416 | 1.658 | 1.6799 | 1.7856
2022-01-11 04:00 | 1.829 | 1.9991 | 2.0165 | 2.0378 | 2.0627 | 1.0669 | 1.2852 | 1.2988 | 1.3173 | 1.0669 | 1.2765 | 1.4427 | 1.4549 | 1.4711 | 1.5606
2022-01-11 05:00 | 1.829 | 1.989 | 2.0013 | 2.0163 | 2.0338 | 1.086 | 1.3004 | 1.3099 | 1.323 | 1.086 | 1.5814 | 1.7743 | 1.7829 | 1.7943 | 1.8949
2022-01-11 06:00 | 1.8383 | 1.995 | 2.0052 | 2.0177 | 2.0323 | 1.1684 | 1.3949 | 1.4029 | 1.4138 | 1.1684 | 1.3337 | 1.4962 | 1.5034 | 1.5129 | 1.5977
2022-01-11 07:00 | 2.0278 | 2.2019 | 2.2138 | 2.2284 | 2.2455 | 1.2384 | 1.48 | 1.4893 | 1.502 | 1.2384 | 1.3146 | 1.4774 | 1.4858 | 1.4969 | 1.5825
2022-01-11 08:00 | 2.0767 | 2.2636 | 2.2802 | 2.3004 | 2.3241 | 1.2071 | 1.4496 | 1.4625 | 1.4802 | 1.2071 | 1.0479 | 1.1875 | 1.1991 | 1.2145 | 1.2906
2022-01-11 09:00 | 2.3244 | 2.543 | 2.5664 | 2.5951 | 2.6284 | 1.3527 | 1.6313 | 1.6496 | 1.6745 | 1.3527 | 1.1241 | 1.2816 | 1.298 | 1.3198 | 1.4076
2022-01-11 10:00 | 2.4959 | 2.7415 | 2.7722 | 2.8097 | 2.8535 | 1.3718 | 1.6642 | 1.6881 | 1.7208 | 1.3718 | 1.467 | 1.6728 | 1.6943 | 1.7229 | 1.8377
2022-01-11 11:00 | 2.534 | 2.7934 | 2.8296 | 2.874 | 2.9258 | 1.3974 | 1.7024 | 1.7307 | 1.7693 | 1.3974 | 1.4099 | 1.617 | 1.6424 | 1.6762 | 1.7941
2022-01-11 12:00 | 2.5149 | 2.7772 | 2.8157 | 2.8628 | 2.9177 | 1.4861 | 1.8103 | 1.8403 | 1.8813 | 1.4861 | 1.4099 | 1.6201 | 1.6471 | 1.6829 | 1.8033
2022-01-11 13:00 | 2.6123 | 2.8808 | 2.9188 | 2.9652 | 3.0194 | 1.4099 | 1.7195 | 1.7491 | 1.7895 | 1.4099 | 1.2575 | 1.45 | 1.4766 | 1.5119 | 1.6233
2022-01-11 14:00 | 2.8007 | 3.0782 | 3.1136 | 3.157 | 3.2075 | 1.5623 | 1.896 | 1.9236 | 1.9613 | 1.5623 | 1.8862 | 2.1451 | 2.1699 | 2.2029 | 2.346
2022-01-11 15:00 | 2.4578 | 2.7044 | 2.737 | 2.777 | 2.8235 | 1.4729 | 1.7865 | 1.8119 | 1.8467 | 1.4729 | 1.7338 | 1.9719 | 1.9948 | 2.0252 | 2.1568
2022-01-11 16:00 | 2.3975 | 2.636 | 2.6668 | 2.7045 | 2.7485 | 1.467 | 1.7769 | 1.8009 | 1.8337 | 1.467 | 1.1813 | 1.3554 | 1.377 | 1.4057 | 1.5049
2022-01-11 17:00 | 2.4197 | 2.659 | 2.6894 | 2.7265 | 2.7699 | 1.6171 | 1.9535 | 1.9772 | 2.0096 | 1.6171 | 2.0196 | 2.2864 | 2.3076 | 2.3359 | 2.4807
2022-01-11 18:00 | 2.8007 | 3.0719 | 3.1041 | 3.1435 | 3.1894 | 2.172 | 2.6116 | 2.6367 | 2.671 | 2.172 | 2.6864 | 3.0299 | 3.0525 | 3.0824 | 3.2659
2022-01-11 19:00 | 2.6711 | 2.94 | 2.9759 | 3.0199 | 3.0712 | 2.0867 | 2.5163 | 2.5443 | 2.5826 | 2.0867 | 2.9341 | 3.3104 | 3.3355 | 3.369 | 3.5703
2022-01-11 20:00 | 2.6483 | 2.9253 | 2.9662 | 3.0163 | 3.0747 | 1.9243 | 2.3315 | 2.3634 | 2.407 | 1.9243 | 2.4959 | 2.8303 | 2.859 | 2.8971 | 3.0798
2022-01-11 21:00 | 2.5721 | 2.8531 | 2.8989 | 2.9551 | 3.0205 | 1.9434 | 2.361 | 2.3968 | 2.4456 | 1.9434 | 2.4578 | 2.7948 | 2.8269 | 2.8696 | 3.0558
2022-01-11 22:00 | 2.3435 | 2.6091 | 2.6558 | 2.7129 | 2.7796 | 1.7024 | 2.0775 | 2.1139 | 2.1636 | 1.7024 | 2.2291 | 2.5419 | 2.5746 | 2.6181 | 2.7926
2022-01-11 23:00 | 2.123 | 2.3663 | 2.4099 | 2.4633 | 2.5256 | 1.4875 | 1.8194 | 1.8534 | 1.8999 | 1.4875 | 1.829 | 2.0931 | 2.1237 | 2.1643 | 2.3134
2022-01-12 | 1.9815 | 2.2058 | 2.2451 | 2.2932 | 2.3494 | 1.2996 | 1.5913 | 1.6219 | 1.6638 | 1.2996 | 1.5433 | 1.7695 | 1.7971 | 1.8337 | 1.9623
2022-01-12 01:00 | 1.7731 | 1.9725 | 2.007 | 2.0492 | 2.0985 | 1.1493 | 1.4069 | 1.4338 | 1.4705 | 1.1493 | 1.5242 | 1.7416 | 1.7658 | 1.7979 | 1.9201
2022-01-12 02:00 | 1.6957 | 1.8797 | 1.9093 | 1.9456 | 1.9879 | 1.0458 | 1.2775 | 1.3006 | 1.3322 | 1.0458 | 1.3718 | 1.5655 | 1.5862 | 1.6138 | 1.7222
2022-01-12 03:00 | 1.6766 | 1.8472 | 1.8706 | 1.8993 | 1.9328 | 1.0288 | 1.2488 | 1.2671 | 1.292 | 1.0288 | 1.3718 | 1.5569 | 1.5733 | 1.5952 | 1.6967
2022-01-12 04:00 | 1.6576 | 1.8149 | 1.8323 | 1.8536 | 1.8784 | 1.0163 | 1.2253 | 1.2389 | 1.2574 | 1.0163 | 1.2765 | 1.4427 | 1.4549 | 1.4711 | 1.5606
2022-01-12 05:00 | 1.6957 | 1.8457 | 1.858 | 1.873 | 1.8905 | 1.0654 | 1.2761 | 1.2856 | 1.2987 | 1.0654 | 1.2765 | 1.4355 | 1.4441 | 1.4555 | 1.5394
2022-01-12 06:00 | 1.7198 | 1.8677 | 1.878 | 1.8905 | 1.9051 | 1.2003 | 1.4325 | 1.4405 | 1.4514 | 1.2003 | 1.4099 | 1.5809 | 1.5881 | 1.5976 | 1.6865
2022-01-12 07:00 | 1.8862 | 2.0498 | 2.0617 | 2.0763 | 2.0934 | 1.2765 | 1.525 | 1.5343 | 1.547 | 1.2765 | 1.3527 | 1.5198 | 1.5281 | 1.5393 | 1.6269
2022-01-12 08:00 | 1.8862 | 2.0589 | 2.0755 | 2.0958 | 2.1194 | 1.3718 | 1.6441 | 1.6571 | 1.6747 | 1.3718 | 1.1622 | 1.3145 | 1.3261 | 1.3416 | 1.4239
2022-01-12 09:00 | 2.0005 | 2.195 | 2.2184 | 2.2471 | 2.2805 | 1.3146 | 1.5863 | 1.6046 | 1.6295 | 1.3146 | 0.89547 | 1.0275 | 1.0439 | 1.0657 | 1.141
2022-01-12 10:00 | 2.0005 | 2.2093 | 2.24 | 2.2775 | 2.3213 | 1.2575 | 1.5291 | 1.5531 | 1.5857 | 1.2575 | 0.95263 | 1.1012 | 1.1226 | 1.1512 | 1.2377
2022-01-12 11:00 | 1.7528 | 1.9541 | 1.9904 | 2.0348 | 2.0865 | 0.95263 | 1.177 | 1.2052 | 1.2439 | 0.95263 | 1.2575 | 1.4477 | 1.4731 | 1.5068 | 1.6163
2022-01-12 12:00 | 1.7528 | 1.9585 | 1.997 | 2.0441 | 2.099 | 0.80021 | 1 | 1.0301 | 1.0711 | 0.80021 | 1.3146 | 1.5143 | 1.5412 | 1.577 | 1.6922
2022-01-12 13:00 | 2.0196 | 2.244 | 2.2819 | 2.3284 | 2.3825 | 0.91452 | 1.1343 | 1.1639 | 1.2043 | 0.91452 | 1.5242 | 1.7464 | 1.773 | 1.8083 | 1.9344
2022-01-12 14:00 | 2.2482 | 2.4846 | 2.52 | 2.5634 | 2.6139 | 1.3146 | 1.6034 | 1.631 | 1.6687 | 1.3146 | 0.95263 | 1.1077 | 1.1325 | 1.1655 | 1.2572
2022-01-12 15:00 | 2.4578 | 2.7044 | 2.737 | 2.777 | 2.8235 | 1.5623 | 1.892 | 1.9175 | 1.9523 | 1.5623 | 1.3908 | 1.5908 | 1.6137 | 1.6441 | 1.7569
2022-01-12 16:00 | 2.553 | 2.8031 | 2.8339 | 2.8716 | 2.9156 | 1.6195 | 1.957 | 1.981 | 2.0138 | 1.6195 | 1.6957 | 1.9271 | 1.9486 | 1.9773 | 2.1048
2022-01-12 17:00 | 2.4156 | 2.6546 | 2.685 | 2.7222 | 2.7655 | 1.6957 | 2.0464 | 2.0701 | 2.1024 | 1.6957 | 1.5433 | 1.7571 | 1.7783 | 1.8066 | 1.9252
2022-01-12 18:00 | 2.5911 | 2.8468 | 2.8789 | 2.9183 | 2.9642 | 1.9624 | 2.3641 | 2.3892 | 2.4234 | 1.9624 | 2.4387 | 2.7547 | 2.7772 | 2.8072 | 2.9771
2022-01-12 19:00 | 2.4959 | 2.7518 | 2.7877 | 2.8317 | 2.883 | 1.8481 | 2.2344 | 2.2624 | 2.3007 | 1.8481 | 2.4768 | 2.8022 | 2.8274 | 2.8609 | 3.037
2022-01-12 20:00 | 2.3816 | 2.6387 | 2.6796 | 2.7297 | 2.7881 | 1.829 | 2.2189 | 2.2508 | 2.2944 | 1.829 | 2.5149 | 2.8515 | 2.8802 | 2.9182 | 3.102
2022-01-12 21:00 | 2.3244 | 2.587 | 2.6328 | 2.689 | 2.7544 | 1.7528 | 2.1359 | 2.1717 | 2.2205 | 1.7528 | 2.5721 | 2.9219 | 2.954 | 2.9967 | 3.1891
2022-01-12 22:00 | 2.172 | 2.4249 | 2.4715 | 2.5287 | 2.5953 | 1.6063 | 1.964 | 2.0005 | 2.0502 | 1.6063 | 2.191 | 2.4996 | 2.5323 | 2.5757 | 2.7482
2022-01-12 23:00 | 2.0005 | 2.2347 | 2.2783 | 2.3318 | 2.394 | 1.3725 | 1.6835 | 1.7175 | 1.764 | 1.3725 | 1.8862 | 2.1566 | 2.1872 | 2.2278 | 2.3801
2022-01-13 | 1.8481 | 2.0625 | 2.1018 | 2.15 | 2.2061 | 1.2008 | 1.4745 | 1.5052 | 1.5471 | 1.2008 | 1.467 | 1.6848 | 1.7124 | 1.749 | 1.8734
2022-01-13 01:00 | 1.6618 | 1.8529 | 1.8874 | 1.9296 | 1.9789 | 1.0969 | 1.3449 | 1.3718 | 1.4086 | 1.0969 | 1.467 | 1.6781 | 1.7023 | 1.7344 | 1.8535
2022-01-13 02:00 | 1.6237 | 1.8024 | 1.832 | 1.8683 | 1.9105 | 1.0098 | 1.235 | 1.2581 | 1.2897 | 1.0098 | 1.3337 | 1.5231 | 1.5439 | 1.5715 | 1.6777
2022-01-13 03:00 | 1.6004 | 1.7653 | 1.7887 | 1.8174 | 1.8509 | 1.0033 | 1.2186 | 1.2369 | 1.2619 | 1.0033 | 1.2003 | 1.3664 | 1.3828 | 1.4046 | 1.4967
2022-01-13 04:00 | 1.6195 | 1.7739 | 1.7913 | 1.8127 | 1.8375 | 0.99073 | 1.1952 | 1.2087 | 1.2273 | 0.99073 | 1.2956 | 1.4639 | 1.4761 | 1.4923 | 1.5829
2022-01-13 05:00 | 1.6669 | 1.8148 | 1.8271 | 1.8421 | 1.8596 | 1.0288 | 1.2329 | 1.2424 | 1.2555 | 1.0288 | 1.3337 | 1.4991 | 1.5077 | 1.5191 | 1.606
2022-01-13 06:00 | 1.684 | 1.8292 | 1.8394 | 1.852 | 1.8666 | 1.1432 | 1.365 | 1.373 | 1.3839 | 1.1432 | 1.2765 | 1.4327 | 1.4399 | 1.4494 | 1.531
2022-01-13 07:00 | 1.7909 | 1.9474 | 1.9594 | 1.974 | 1.991 | 1.1432 | 1.3674 | 1.3768 | 1.3895 | 1.1432 | 1.2003 | 1.3504 | 1.3588 | 1.3699 | 1.4492
2022-01-13 08:00 | 1.8481 | 2.0179 | 2.0345 | 2.0548 | 2.0785 | 1.1813 | 1.4191 | 1.432 | 1.4496 | 1.1813 | 1.0669 | 1.2086 | 1.2203 | 1.2357 | 1.3128
2022-01-13 09:00 | 2.0577 | 2.2565 | 2.2798 | 2.3085 | 2.3419 | 1.1622 | 1.4062 | 1.4245 | 1.4494 | 1.1622 | 1.2003 | 1.3663 | 1.3827 | 1.4045 | 1.4965
2022-01-13 10:00 | 2.0005 | 2.2093 | 2.24 | 2.2775 | 2.3213 | 1.1813 | 1.4391 | 1.463 | 1.4957 | 1.1813 | 1.086 | 1.2494 | 1.2709 | 1.2994 | 1.3933
2022-01-13 11:00 | 2.0958 | 2.3226 | 2.3588 | 2.4032 | 2.455 | 1.1241 | 1.3795 | 1.4078 | 1.4464 | 1.1241 | 1.2384 | 1.4265 | 1.4519 | 1.4857 | 1.5941
2022-01-13 12:00 | 2.0767 | 2.3064 | 2.3449 | 2.392 | 2.447 | 1.0669 | 1.3152 | 1.3452 | 1.3862 | 1.0669 | 1.6957 | 1.9377 | 1.9647 | 2.0005 | 2.1366
2022-01-13 13:00 | 1.8481 | 2.0598 | 2.0977 | 2.1442 | 2.1983 | 0.99073 | 1.2244 | 1.254 | 1.2944 | 0.99073 | 1.4099 | 1.6194 | 1.646 | 1.6813 | 1.801
2022-01-13 14:00 | 2.1339 | 2.3618 | 2.3972 | 2.4405 | 2.4911 | 0.94683 | 1.1689 | 1.1965 | 1.2342 | 0.94683 | 1.3718 | 1.5735 | 1.5983 | 1.6313 | 1.7461
2022-01-13 15:00 | 2.3816 | 2.6225 | 2.6551 | 2.6951 | 2.7417 | 1.4099 | 1.712 | 1.7374 | 1.7722 | 1.4099 | 1.1241 | 1.2944 | 1.3173 | 1.3477 | 1.4458
2022-01-13 16:00 | 2.0958 | 2.3119 | 2.3427 | 2.3804 | 2.4244 | 1.5052 | 1.8219 | 1.8459 | 1.8788 | 1.5052 | 1.6195 | 1.8424 | 1.8639 | 1.8926 | 2.0159
2022-01-13 17:00 | 2.6674 | 2.9251 | 2.9555 | 2.9926 | 3.036 | 1.5242 | 1.8438 | 1.8675 | 1.8998 | 1.5242 | 1.4099 | 1.6089 | 1.6301 | 1.6584 | 1.7697
2022-01-13 18:00 | 2.5537 | 2.8065 | 2.8387 | 2.878 | 2.924 | 1.9053 | 2.2965 | 2.3216 | 2.3559 | 1.9053 | 2.2044 | 2.4943 | 2.5168 | 2.5468 | 2.7038
2022-01-13 19:00 | 2.534 | 2.7927 | 2.8286 | 2.8726 | 2.9239 | 1.8481 | 2.2344 | 2.2624 | 2.3007 | 1.8481 | 2.3816 | 2.6964 | 2.7215 | 2.755 | 2.9259
2022-01-13 20:00 | 2.4578 | 2.7206 | 2.7615 | 2.8116 | 2.87 | 1.829 | 2.2189 | 2.2508 | 2.2944 | 1.829 | 2.6483 | 2.9997 | 3.0284 | 3.0664 | 3.2576
2022-01-13 21:00 | 2.4197 | 2.6893 | 2.7352 | 2.7913 | 2.8568 | 1.7511 | 2.1338 | 2.1696 | 2.2185 | 1.7511 | 2.4768 | 2.816 | 2.8481 | 2.8908 | 3.078
2022-01-13 22:00 | 2.2673 | 2.5272 | 2.5739 | 2.631 | 2.6977 | 1.6385 | 2.0021 | 2.0385 | 2.0882 | 1.6385 | 2.3054 | 2.6266 | 2.6593 | 2.7028 | 2.8815
2022-01-13 23:00 | 1.99 | 2.2234 | 2.267 | 2.3204 | 2.3827 | 1.406 | 1.7231 | 1.7571 | 1.8036 | 1.406 | 2.0577 | 2.3471 | 2.3777 | 2.4184 | 2.5801
2022-01-14 | 1.8712 | 2.0873 | 2.1266 | 2.1747 | 2.2309 | 1.2449 | 1.5266 | 1.5573 | 1.5992 | 1.2449 | 1.5814 | 1.8118 | 1.8394 | 1.876 | 2.0067
2022-01-14 01:00 | 1.7147 | 1.9098 | 1.9443 | 1.9865 | 2.0358 | 1.1465 | 1.4034 | 1.4304 | 1.4671 | 1.1465 | 1.3908 | 1.5934 | 1.6176 | 1.6497 | 1.7646
2022-01-14 02:00 | 1.6576 | 1.8388 | 1.8684 | 1.9046 | 1.9469 | 1.0479 | 1.28 | 1.3031 | 1.3347 | 1.0479 | 1.5623 | 1.7772 | 1.798 | 1.8255 | 1.9444
2022-01-14 03:00 | 1.6406 | 1.8085 | 1.8319 | 1.8606 | 1.8941 | 1.0184 | 1.2365 | 1.2547 | 1.2797 | 1.0184 | 1.4289 | 1.6204 | 1.6369 | 1.6587 | 1.7634
2022-01-14 04:00 | 1.6385 | 1.7944 | 1.8118 | 1.8331 | 1.858 | 0.99073 | 1.1952 | 1.2087 | 1.2273 | 0.99073 | 1.2765 | 1.4427 | 1.4549 | 1.4711 | 1.5606
2022-01-14 05:00 | 1.6576 | 1.8048 | 1.8171 | 1.8321 | 1.8496 | 1.0463 | 1.2535 | 1.2631 | 1.2761 | 1.0463 | 1.3527 | 1.5202 | 1.5288 | 1.5402 | 1.6282
2022-01-14 06:00 | 1.7719 | 1.9236 | 1.9339 | 1.9464 | 1.961 | 1.1564 | 1.3807 | 1.3886 | 1.3995 | 1.1564 | 1.3337 | 1.4962 | 1.5034 | 1.5129 | 1.5977
2022-01-14 07:00 | 1.9053 | 2.0703 | 2.0822 | 2.0968 | 2.1138 | 1.2765 | 1.525 | 1.5343 | 1.547 | 1.2765 | 1.5242 | 1.7103 | 1.7187 | 1.7298 | 1.8269
2022-01-14 08:00 | 1.9243 | 2.0998 | 2.1164 | 2.1367 | 2.1604 | 1.2956 | 1.5541 | 1.567 | 1.5847 | 1.2956 | 1.3718 | 1.5474 | 1.559 | 1.5744 | 1.6683
2022-01-14 09:00 | 1.9434 | 2.1336 | 2.157 | 2.1857 | 2.2191 | 1.2956 | 1.5638 | 1.5821 | 1.607 | 1.2956 | 1.2194 | 1.3875 | 1.4039 | 1.4257 | 1.5187
2022-01-14 10:00 | 2.1339 | 2.3526 | 2.3832 | 2.4208 | 2.4646 | 1.2384 | 1.5066 | 1.5306 | 1.5632 | 1.2384 | 0.97168 | 1.1223 | 1.1438 | 1.1724 | 1.2599
2022-01-14 11:00 | 2.3435 | 2.5887 | 2.6249 | 2.6693 | 2.7211 | 1.448 | 1.7622 | 1.7904 | 1.8291 | 1.448 | 1.467 | 1.6806 | 1.706 | 1.7397 | 1.8607
2022-01-14 12:00 | 2.2291 | 2.4702 | 2.5087 | 2.5558 | 2.6107 | 1.3067 | 1.5984 | 1.6284 | 1.6694 | 1.3067 | 1.2575 | 1.4507 | 1.4777 | 1.5135 | 1.6255
2022-01-14 13:00 | 2.2673 | 2.5101 | 2.548 | 2.5945 | 2.6486 | 1.1622 | 1.4269 | 1.4565 | 1.4969 | 1.1622 | 1.3337 | 1.5347 | 1.5613 | 1.5966 | 1.7122
2022-01-14 14:00 | 2.4006 | 2.6484 | 2.6838 | 2.7271 | 2.7776 | 1.2575 | 1.5359 | 1.5635 | 1.6012 | 1.2575 | 1.1622 | 1.3406 | 1.3654 | 1.3984 | 1.5017
2022-01-14 15:00 | 2.5721 | 2.8272 | 2.8598 | 2.8998 | 2.9464 | 1.4289 | 1.7345 | 1.76 | 1.7947 | 1.4289 | 1.7147 | 1.9508 | 1.9736 | 2.004 | 2.1346
2022-01-14 16:00 | 2.7817 | 3.0488 | 3.0796 | 3.1173 | 3.1612 | 1.7147 | 2.0695 | 2.0935 | 2.1263 | 1.7147 | 2.0577 | 2.3293 | 2.3509 | 2.3796 | 2.527
2022-01-14 17:00 | 3.0484 | 3.3345 | 3.3648 | 3.402 | 3.4453 | 2.172 | 2.6091 | 2.6328 | 2.6651 | 2.172 | 3.0103 | 3.3873 | 3.4086 | 3.4369 | 3.6362
2022-01-14 18:00 | 2.9913 | 3.2766 | 3.3088 | 3.3482 | 3.3941 | 2.2101 | 2.6567 | 2.6818 | 2.716 | 2.2101 | 3.5057 | 3.9403 | 3.9629 | 3.9928 | 4.2214
2022-01-14 19:00 | 2.8198 | 3.0997 | 3.1357 | 3.1797 | 3.231 | 2.2101 | 2.662 | 2.69 | 2.7283 | 2.2101 | 3.1246 | 3.5221 | 3.5473 | 3.5807 | 3.7925
2022-01-14 20:00 | 2.7055 | 2.9867 | 3.0276 | 3.0777 | 3.1361 | 2.1148 | 2.5566 | 2.5885 | 2.632 | 2.1148 | 3.1437 | 3.5502 | 3.5788 | 3.6169 | 3.8353
2022-01-14 21:00 | 2.6864 | 2.9759 | 3.0217 | 3.0779 | 3.1433 | 2.0767 | 2.5186 | 2.5543 | 2.6032 | 2.0767 | 2.8769 | 3.2606 | 3.2927 | 3.3354 | 3.5446
2022-01-14 22:00 | 2.4768 | 2.7524 | 2.799 | 2.8562 | 2.9228 | 1.8702 | 2.2758 | 2.3122 | 2.362 | 1.8702 | 2.4768 | 2.8171 | 2.8499 | 2.8933 | 3.0815
2022-01-14 23:00 | 2.3625 | 2.6236 | 2.6672 | 2.7207 | 2.783 | 1.5746 | 1.9222 | 1.9563 | 2.0028 | 1.5746 | 2.1339 | 2.4318 | 2.4624 | 2.503 | 2.6689
2022-01-15 | 2.049 | 2.2783 | 2.3177 | 2.3658 | 2.422 | 1.3623 | 1.6653 | 1.696 | 1.7379 | 1.3623 | 1.81 | 2.0659 | 2.0935 | 2.1301 | 2.2734
2022-01-15 01:00 | 1.9624 | 2.1759 | 2.2104 | 2.2526 | 2.3018 | 1.2516 | 1.5276 | 1.5545 | 1.5913 | 1.2516 | 1.6195 | 1.8475 | 1.8717 | 1.9038 | 2.0312
2022-01-15 02:00 | 1.8672 | 2.0639 | 2.0936 | 2.1298 | 2.1721 | 1.1115 | 1.3552 | 1.3783 | 1.4099 | 1.1115 | 1.448 | 1.6502 | 1.6709 | 1.6985 | 1.8111
2022-01-15 03:00 | 1.7719 | 1.9495 | 1.973 | 2.0017 | 2.0351 | 1.0502 | 1.274 | 1.2923 | 1.3172 | 1.0502 | 1.4289 | 1.6204 | 1.6369 | 1.6587 | 1.7634
2022-01-15 04:00 | 1.7338 | 1.8968 | 1.9142 | 1.9355 | 1.9603 | 1.0352 | 1.2477 | 1.2613 | 1.2798 | 1.0352 | 1.3718 | 1.5485 | 1.5607 | 1.5769 | 1.6717
2022-01-15 05:00 | 1.7528 | 1.9071 | 1.9194 | 1.9344 | 1.9519 | 1.086 | 1.3004 | 1.3099 | 1.323 | 1.086 | 1.3527 | 1.5202 | 1.5288 | 1.5402 | 1.6282
2022-01-15 06:00 | 1.6576 | 1.8008 | 1.8111 | 1.8236 | 1.8382 | 1.0669 | 1.275 | 1.283 | 1.2939 | 1.0669 | 1.5433 | 1.7291 | 1.7363 | 1.7458 | 1.8421
2022-01-15 07:00 | 1.7528 | 1.9065 | 1.9184 | 1.9331 | 1.9501 | 1.2384 | 1.48 | 1.4893 | 1.502 | 1.2384 | 1.5623 | 1.7527 | 1.761 | 1.7722 | 1.8713
2022-01-15 08:00 | 1.7967 | 1.9628 | 1.9793 | 1.9996 | 2.0233 | 1.2003 | 1.4416 | 1.4545 | 1.4722 | 1.2003 | 1.3527 | 1.5262 | 1.5378 | 1.5533 | 1.6461
2022-01-15 09:00 | 2.0958 | 2.2974 | 2.3208 | 2.3494 | 2.3828 | 1.4289 | 1.7214 | 1.7396 | 1.7645 | 1.4289 | 1.8672 | 2.1073 | 2.1237 | 2.1455 | 2.2742
2022-01-15 10:00 | 2.0958 | 2.3116 | 2.3423 | 2.3799 | 2.4236 | 1.3759 | 1.669 | 1.693 | 1.7256 | 1.3759 | 1.6385 | 1.8634 | 1.8848 | 1.9134 | 2.0376
2022-01-15 11:00 | 2.172 | 2.4045 | 2.4407 | 2.4851 | 2.5369 | 1.5242 | 1.8522 | 1.8805 | 1.9191 | 1.5242 | 1.4099 | 1.617 | 1.6424 | 1.6762 | 1.7941
2022-01-15 12:00 | 2.191 | 2.4293 | 2.4677 | 2.5148 | 2.5698 | 1.501 | 1.828 | 1.858 | 1.899 | 1.501 | 1.7528 | 2.0012 | 2.0282 | 2.064 | 2.2032
2022-01-15 13:00 | 2.0577 | 2.2849 | 2.3229 | 2.3693 | 2.4235 | 1.5242 | 1.8546 | 1.8842 | 1.9246 | 1.5242 | 1.6576 | 1.8946 | 1.9212 | 1.9565 | 2.0899
2022-01-15 14:00 | 1.7147 | 1.9115 | 1.9469 | 1.9902 | 2.0408 | 1.086 | 1.3333 | 1.3609 | 1.3986 | 1.086 | 1.0669 | 1.2347 | 1.2595 | 1.2925 | 1.3906
2022-01-15 15:00 | 1.9053 | 2.1108 | 2.1434 | 2.1834 | 2.2299 | 1.3527 | 1.6445 | 1.6699 | 1.7047 | 1.3527 | 1.7719 | 2.0143 | 2.0371 | 2.0675 | 2.2013
2022-01-15 16:00 | 2.3625 | 2.5985 | 2.6293 | 2.667 | 2.7109 | 1.7147 | 2.0695 | 2.0935 | 2.1263 | 1.7147 | 2.0196 | 2.287 | 2.3086 | 2.3372 | 2.4826
2022-01-15 17:00 | 2.5149 | 2.7613 | 2.7917 | 2.8289 | 2.8722 | 2.0458 | 2.46 | 2.4837 | 2.516 | 2.0458 | 2.0791 | 2.3525 | 2.3737 | 2.402 | 2.5501
2022-01-15 18:00 | 2.8579 | 3.1333 | 3.1655 | 3.2049 | 3.2508 | 2.2673 | 2.7242 | 2.7493 | 2.7835 | 2.2673 | 3.1246 | 3.5169 | 3.5394 | 3.5694 | 3.777
2022-01-15 19:00 | 2.7626 | 3.0383 | 3.0743 | 3.1183 | 3.1695 | 2.191 | 2.6395 | 2.6675 | 2.7058 | 2.191 | 3.3151 | 3.7338 | 3.759 | 3.7924 | 4.0147
2022-01-15 20:00 | 2.7245 | 3.0072 | 3.0481 | 3.0982 | 3.1566 | 2.191 | 2.6466 | 2.6785 | 2.7221 | 2.191 | 2.9341 | 3.3173 | 3.3459 | 3.384 | 3.5909
2022-01-15 21:00 | 2.6102 | 2.894 | 2.9399 | 2.996 | 3.0614 | 2.0767 | 2.5186 | 2.5543 | 2.6032 | 2.0767 | 2.7626 | 3.1336 | 3.1657 | 3.2084 | 3.4113
2022-01-15 22:00 | 2.4622 | 2.7367 | 2.7834 | 2.8405 | 2.9072 | 1.8454 | 2.2465 | 2.2829 | 2.3326 | 1.8454 | 2.4959 | 2.8383 | 2.871 | 2.9145 | 3.1037
2022-01-15 23:00 | 2.1927 | 2.4411 | 2.4848 | 2.5382 | 2.6005 | 1.6257 | 1.9826 | 2.0166 | 2.0631 | 1.6257 | 2.0958 | 2.3895 | 2.4201 | 2.4607 | 2.6245
2022-01-16 | 1.9792 | 2.2033 | 2.2426 | 2.2908 | 2.3469 | 1.3741 | 1.6792 | 1.7099 | 1.7518 | 1.3741 | 1.9624 | 2.2353 | 2.2629 | 2.2995 | 2.4511
2022-01-16 01:00 | 1.8045 | 2.0062 | 2.0407 | 2.083 | 2.1322 | 1.2394 | 1.5132 | 1.5401 | 1.5768 | 1.2394 | 1.5052 | 1.7205 | 1.7446 | 1.7768 | 1.8979
2022-01-16 02:00 | 1.7147 | 1.9002 | 1.9298 | 1.9661 | 2.0083 | 1.0976 | 1.3388 | 1.3619 | 1.3934 | 1.0976 | 1.5242 | 1.7349 | 1.7556 | 1.7832 | 1.8999
2022-01-16 03:00 | 1.6276 | 1.7945 | 1.818 | 1.8467 | 1.8801 | 1.0288 | 1.2488 | 1.2671 | 1.292 | 1.0288 | 1.3718 | 1.5569 | 1.5733 | 1.5952 | 1.6967
2022-01-16 04:00 | 1.6385 | 1.7944 | 1.8118 | 1.8331 | 1.858 | 1.0098 | 1.2177 | 1.2312 | 1.2498 | 1.0098 | 1.2575 | 1.4215 | 1.4337 | 1.4499 | 1.5384
2022-01-16 05:00 | 1.6004 | 1.7434 | 1.7557 | 1.7707 | 1.7882 | 0.99073 | 1.1878 | 1.1974 | 1.2105 | 0.99073 | 1.3146 | 1.4779 | 1.4865 | 1.4979 | 1.5838
2022-01-16 06:00 | 1.5433 | 1.678 | 1.6882 | 1.7008 | 1.7154 | 1.0479 | 1.2525 | 1.2605 | 1.2714 | 1.0479 | 1.5433 | 1.7291 | 1.7363 | 1.7458 | 1.8421
2022-01-16 07:00 | 1.448 | 1.579 | 1.5909 | 1.6056 | 1.6226 | 1.0288 | 1.2324 | 1.2417 | 1.2544 | 1.0288 | 1.1432 | 1.2869 | 1.2953 | 1.3064 | 1.3825
2022-01-16 08:00 | 1.5242 | 1.67 | 1.6866 | 1.7068 | 1.7305 | 0.99073 | 1.194 | 1.2069 | 1.2246 | 0.99073 | 0.85737 | 0.97574 | 0.98736 | 1.0028 | 1.0684
2022-01-16 09:00 | 1.7147 | 1.888 | 1.9114 | 1.94 | 1.9734 | 1.2384 | 1.4963 | 1.5145 | 1.5394 | 1.2384 | 1.1813 | 1.3451 | 1.3615 | 1.3833 | 1.4743
2022-01-16 10:00 | 1.5894 | 1.7676 | 1.7983 | 1.8359 | 1.8796 | 1.1241 | 1.3716 | 1.3955 | 1.4282 | 1.1241 | 0.87642 | 1.0165 | 1.038 | 1.0665 | 1.1488
2022-01-16 11:00 | 1.829 | 2.036 | 2.0723 | 2.1167 | 2.1684 | 1.1241 | 1.3795 | 1.4078 | 1.4464 | 1.1241 | 0.93358 | 1.0877 | 1.1131 | 1.1469 | 1.2386
2022-01-16 12:00 | 1.5814 | 1.7743 | 1.8127 | 1.8598 | 1.9148 | 1.1822 | 1.4513 | 1.4814 | 1.5223 | 1.1822 | 0.724 | 0.85792 | 0.88488 | 0.92071 | 1.0033
2022-01-16 13:00 | 2.0386 | 2.2645 | 2.3024 | 2.3488 | 2.403 | 1.2575 | 1.5395 | 1.5691 | 1.6095 | 1.2575 | 1.0479 | 1.2171 | 1.2437 | 1.279 | 1.3789
2022-01-16 14:00 | 1.9815 | 2.1981 | 2.2335 | 2.2768 | 2.3273 | 1.2765 | 1.5584 | 1.586 | 1.6237 | 1.2765 | 0.97168 | 1.1289 | 1.1537 | 1.1866 | 1.2795
2022-01-16 15:00 | 2.1444 | 2.3677 | 2.4003 | 2.4403 | 2.4869 | 1.4861 | 1.802 | 1.8275 | 1.8622 | 1.4861 | 1.6385 | 1.8661 | 1.8889 | 1.9193 | 2.0457
2022-01-16 16:00 | 2.4384 | 2.68 | 2.7108 | 2.7485 | 2.7925 | 1.98 | 2.3828 | 2.4069 | 2.4397 | 1.98 | 2.191 | 2.4775 | 2.4991 | 2.5278 | 2.6825
2022-01-16 17:00 | 2.8539 | 3.1255 | 3.1558 | 3.193 | 3.2363 | 2.3726 | 2.8461 | 2.8698 | 2.9021 | 2.3726 | 3.639 | 4.086 | 4.1073 | 4.1356 | 4.3694
2022-01-16 18:00 | 3.258 | 3.5632 | 3.5954 | 3.6347 | 3.6807 | 2.7055 | 3.2419 | 3.267 | 3.3012 | 2.7055 | 4.2297 | 4.7449 | 4.7674 | 4.7974 | 5.0657
2022-01-16 19:00 | 3.1437 | 3.4477 | 3.4837 | 3.5276 | 3.5789 | 2.6864 | 3.2247 | 3.2527 | 3.291 | 2.6864 | 3.9248 | 4.4113 | 4.4365 | 4.47 | 4.7257
2022-01-16 20:00 | 2.8769 | 3.1709 | 3.2118 | 3.2619 | 3.3203 | 2.344 | 2.8273 | 2.8592 | 2.9028 | 2.344 | 3.4104 | 3.8466 | 3.8752 | 3.9133 | 4.1464
2022-01-16 21:00 | 2.7612 | 3.0562 | 3.1021 | 3.1582 | 3.2236 | 2.2116 | 2.6779 | 2.7137 | 2.7625 | 2.2116 | 3.1246 | 3.5358 | 3.568 | 3.6107 | 3.8335
2022-01-16 22:00 | 2.6674 | 2.9571 | 3.0037 | 3.0609 | 3.1275 | 1.9626 | 2.385 | 2.4214 | 2.4711 | 1.9626 | 2.896 | 3.2829 | 3.3156 | 3.3591 | 3.5703
2022-01-16 23:00 | 2.3244 | 2.5827 | 2.6263 | 2.6797 | 2.742 | 1.5524 | 1.896 | 1.93 | 1.9765 | 1.5524 | 2.0577 | 2.3471 | 2.3777 | 2.4184 | 2.5801
2022-01-17 | 2.003 | 2.2289 | 2.2683 | 2.3164 | 2.3726 | 1.3294 | 1.6265 | 1.6571 | 1.699 | 1.3294 | 1.7528 | 2.0024 | 2.03 | 2.0666 | 2.2067
2022-01-17 01:00 | 1.8399 | 2.0442 | 2.0787 | 2.121 | 2.1702 | 1.2003 | 1.4671 | 1.494 | 1.5307 | 1.2003 | 1.6957 | 1.9322 | 1.9564 | 1.9885 | 2.1201
2022-01-17 02:00 | 1.7719 | 1.9616 | 1.9912 | 2.0275 | 2.0697 | 1.086 | 1.3251 | 1.3482 | 1.3797 | 1.086 | 1.5623 | 1.7772 | 1.798 | 1.8255 | 1.9444
2022-01-17 03:00 | 1.7147 | 1.8881 | 1.9116 | 1.9403 | 1.9737 | 1.0547 | 1.2793 | 1.2976 | 1.3225 | 1.0547 | 1.467 | 1.6628 | 1.6792 | 1.701 | 1.8078
2022-01-17 04:00 | 1.7338 | 1.8968 | 1.9142 | 1.9355 | 1.9603 | 1.0479 | 1.2627 | 1.2763 | 1.2948 | 1.0479 | 1.3718 | 1.5485 | 1.5607 | 1.5769 | 1.6717
2022-01-17 05:00 | 1.7528 | 1.9071 | 1.9194 | 1.9344 | 1.9519 | 1.1198 | 1.3403 | 1.3499 | 1.363 | 1.1198 | 1.3718 | 1.5414 | 1.55 | 1.5614 | 1.6505
2022-01-17 06:00 | 1.81 | 1.9646 | 1.9748 | 1.9873 | 2.0019 | 1.2003 | 1.4325 | 1.4405 | 1.4514 | 1.2003 | 1.6385 | 1.835 | 1.8422 | 1.8517 | 1.9532
2022-01-17 07:00 | 2.0767 | 2.2545 | 2.2664 | 2.281 | 2.2981 | 1.3527 | 1.615 | 1.6243 | 1.637 | 1.3527 | 1.3337 | 1.4986 | 1.507 | 1.5181 | 1.6047
2022-01-17 08:00 | 2.172 | 2.3659 | 2.3825 | 2.4028 | 2.4265 | 1.3337 | 1.5991 | 1.6121 | 1.6297 | 1.3337 | 1.2003 | 1.3568 | 1.3685 | 1.3839 | 1.4683
2022-01-17 09:00 | 2.191 | 2.3997 | 2.4231 | 2.4518 | 2.4852 | 1.3337 | 1.6088 | 1.6271 | 1.652 | 1.3337 | 1.1241 | 1.2816 | 1.298 | 1.3198 | 1.4076
2022-01-17 10:00 | 2.3054 | 2.5368 | 2.5675 | 2.605 | 2.6488 | 1.2003 | 1.4616 | 1.4855 | 1.5182 | 1.2003 | 0.80021 | 0.93178 | 0.95327 | 0.98183 | 1.06
2022-01-17 11:00 | 2.4197 | 2.6705 | 2.7068 | 2.7512 | 2.803 | 1.2384 | 1.5146 | 1.5429 | 1.5815 | 1.2384 | 0.87642 | 1.0242 | 1.0496 | 1.0834 | 1.1719
2022-01-17 12:00 | 2.7376 | 3.0165 | 3.055 | 3.1021 | 3.157 | 1.5352 | 1.8683 | 1.8983 | 1.9393 | 1.5352 | 1.4099 | 1.6201 | 1.6471 | 1.6829 | 1.8033
2022-01-17 13:00 | 2.8388 | 3.1242 | 3.1621 | 3.2085 | 3.2627 | 1.8481 | 2.2372 | 2.2668 | 2.3072 | 1.8481 | 1.829 | 2.0852 | 2.1117 | 2.1471 | 2.2899
2022-01-17 14:00 | 2.7302 | 3.0025 | 3.0379 | 3.0812 | 3.1317 | 1.7427 | 2.1091 | 2.1367 | 2.1744 | 1.7427 | 1.7528 | 1.9969 | 2.0217 | 2.0547 | 2.1905
2022-01-17 15:00 | 2.7436 | 3.0114 | 3.0441 | 3.084 | 3.1306 | 1.7338 | 2.0946 | 2.1201 | 2.1548 | 1.7338 | 1.9053 | 2.1625 | 2.1854 | 2.2157 | 2.3568
2022-01-17 16:00 | 2.7077 | 2.9693 | 3.0001 | 3.0378 | 3.0818 | 1.6855 | 2.035 | 2.059 | 2.0918 | 1.6855 | 2.1339 | 2.414 | 2.4356 | 2.4643 | 2.6159
2022-01-17 17:00 | 2.6483 | 2.9046 | 2.935 | 2.9722 | 3.0155 | 1.81 | 2.1814 | 2.2051 | 2.2374 | 1.81 | 2.5149 | 2.8368 | 2.8581 | 2.8864 | 3.0584
2022-01-17 18:00 | 2.5721 | 2.8263 | 2.8585 | 2.8978 | 2.9438 | 1.9434 | 2.3415 | 2.3666 | 2.4009 | 1.9434 | 2.3435 | 2.6488 | 2.6714 | 2.7013 | 2.866
2022-01-17 19:00 | 2.4959 | 2.7518 | 2.7877 | 2.8317 | 2.883 | 2.0577 | 2.4819 | 2.51 | 2.5482 | 2.0577 | 2.7436 | 3.0986 | 3.1238 | 3.1573 | 3.3481
2022-01-17 20:00 | 2.553 | 2.8229 | 2.8639 | 2.9139 | 2.9723 | 1.9434 | 2.354 | 2.3859 | 2.4295 | 1.9434 | 2.9341 | 3.3173 | 3.3459 | 3.384 | 3.5909
2022-01-17 21:00 | 2.4578 | 2.7303 | 2.7761 | 2.8322 | 2.8977 | 1.9434 | 2.361 | 2.3968 | 2.4456 | 1.9434 | 2.5149 | 2.8583 | 2.8905 | 2.9332 | 3.1225
2022-01-17 22:00 | 2.3054 | 2.5681 | 2.6148 | 2.672 | 2.7386 | 1.6795 | 2.0504 | 2.0868 | 2.1366 | 1.6795 | 2.2863 | 2.6054 | 2.6381 | 2.6816 | 2.8593
2022-01-17 23:00 | 2.0767 | 2.3166 | 2.3602 | 2.4136 | 2.4759 | 1.3665 | 1.6764 | 1.7105 | 1.757 | 1.3665 | 1.7719 | 2.0296 | 2.0601 | 2.1008 | 2.2468
2022-01-18 | 1.9243 | 2.1444 | 2.1837 | 2.2318 | 2.288 | 1.2448 | 1.5264 | 1.5571 | 1.599 | 1.2448 | 1.6385 | 1.8754 | 1.9029 | 1.9395 | 2.0734
2022-01-18 01:00 | 1.7719 | 1.9712 | 2.0057 | 2.0479 | 2.0972 | 1.1072 | 1.3571 | 1.384 | 1.4208 | 1.1072 | 1.3527 | 1.5511 | 1.5753 | 1.6074 | 1.7202
2022-01-18 02:00 | 1.6957 | 1.8797 | 1.9093 | 1.9456 | 1.9879 | 1.0479 | 1.28 | 1.3031 | 1.3347 | 1.0479 | 1.2765 | 1.4596 | 1.4804 | 1.5079 | 1.6111
2022-01-18 03:00 | 1.6576 | 1.8267 | 1.8501 | 1.8788 | 1.9123 | 1.0098 | 1.2263 | 1.2445 | 1.2695 | 1.0098 | 1.2956 | 1.4722 | 1.4887 | 1.5105 | 1.6078
2022-01-18 04:00 | 1.6957 | 1.8558 | 1.8732 | 1.8945 | 1.9194 | 1.0098 | 1.2177 | 1.2312 | 1.2498 | 1.0098 | 1.2765 | 1.4427 | 1.4549 | 1.4711 | 1.5606
2022-01-18 05:00 | 1.7682 | 1.9237 | 1.936 | 1.951 | 1.9685 | 1.0608 | 1.2706 | 1.2802 | 1.2932 | 1.0608 | 1.4099 | 1.5838 | 1.5923 | 1.6038 | 1.6949
2022-01-18 06:00 | 1.81 | 1.9646 | 1.9748 | 1.9873 | 2.0019 | 1.1813 | 1.41 | 1.418 | 1.4289 | 1.1813 | 1.4289 | 1.6021 | 1.6093 | 1.6188 | 1.7087
2022-01-18 07:00 | 1.9434 | 2.1112 | 2.1231 | 2.1377 | 2.1548 | 1.2194 | 1.4575 | 1.4668 | 1.4795 | 1.2194 | 1.4099 | 1.5833 | 1.5917 | 1.6028 | 1.6936
2022-01-18 08:00 | 2.2101 | 2.4069 | 2.4234 | 2.4437 | 2.4674 | 1.2384 | 1.4866 | 1.4995 | 1.5172 | 1.2384 | 1.3337 | 1.5051 | 1.5167 | 1.5321 | 1.6239
2022-01-18 09:00 | 2.3872 | 2.6105 | 2.6339 | 2.6625 | 2.6959 | 1.3527 | 1.6313 | 1.6496 | 1.6745 | 1.3527 | 1.4099 | 1.5992 | 1.6156 | 1.6374 | 1.7409
2022-01-18 10:00 | 2.4959 | 2.7415 | 2.7722 | 2.8097 | 2.8535 | 1.472 | 1.7826 | 1.8065 | 1.8392 | 1.472 | 1.6766 | 1.9057 | 1.9272 | 1.9558 | 2.0821
2022-01-18 11:00 | 2.4959 | 2.7524 | 2.7887 | 2.8331 | 2.8848 | 1.4861 | 1.8072 | 1.8355 | 1.8741 | 1.4861 | 1.8672 | 2.1252 | 2.1506 | 2.1843 | 2.3274
2022-01-18 12:00 | 2.534 | 2.7977 | 2.8362 | 2.8833 | 2.9382 | 1.6004 | 1.9454 | 1.9754 | 2.0164 | 1.6004 | 1.7147 | 1.9589 | 1.9858 | 2.0217 | 2.1588
2022-01-18 13:00 | 2.4006 | 2.6534 | 2.6913 | 2.7378 | 2.7919 | 1.5052 | 1.8321 | 1.8617 | 1.9021 | 1.5052 | 1.5623 | 1.7888 | 1.8153 | 1.8507 | 1.9788
2022-01-18 14:00 | 2.0958 | 2.3209 | 2.3563 | 2.3996 | 2.4501 | 1.1813 | 1.4458 | 1.4734 | 1.5111 | 1.1813 | 1.086 | 1.2559 | 1.2807 | 1.3137 | 1.4128
2022-01-18 15:00 | 1.9243 | 2.1313 | 2.1639 | 2.2038 | 2.2504 | 0.95263 | 1.1718 | 1.1973 | 1.232 | 0.95263 | 0.93358 | 1.0827 | 1.1056 | 1.136 | 1.2236
2022-01-18 16:00 | 2.1529 | 2.3733 | 2.4041 | 2.4418 | 2.4858 | 1.2162 | 1.4806 | 1.5046 | 1.5374 | 1.2162 | 1.448 | 1.6518 | 1.6734 | 1.7021 | 1.816
2022-01-18 17:00 | 2.1992 | 2.4221 | 2.4524 | 2.4896 | 2.5329 | 1.5422 | 1.8651 | 1.8887 | 1.9211 | 1.5422 | 1.6766 | 1.9053 | 1.9265 | 1.9548 | 2.0808
2022-01-18 18:00 | 2.2863 | 2.5193 | 2.5514 | 2.5908 | 2.6367 | 1.7147 | 2.0715 | 2.0966 | 2.1308 | 1.7147 | 2.0386 | 2.3101 | 2.3326 | 2.3625 | 2.5104
2022-01-18 19:00 | 2.3054 | 2.5471 | 2.583 | 2.627 | 2.6783 | 1.7528 | 2.1218 | 2.1498 | 2.1881 | 1.7528 | 2.3054 | 2.6117 | 2.6369 | 2.6703 | 2.837
2022-01-18 20:00 | 2.3435 | 2.5978 | 2.6387 | 2.6888 | 2.7472 | 1.7528 | 2.1289 | 2.1608 | 2.2044 | 1.7528 | 2.5721 | 2.915 | 2.9437 | 2.9818 | 3.1687
2022-01-18 21:00 | 2.2673 | 2.5256 | 2.5714 | 2.6276 | 2.693 | 1.7528 | 2.1359 | 2.1717 | 2.2205 | 1.7528 | 2.4197 | 2.7525 | 2.7846 | 2.8273 | 3.0114
2022-01-18 22:00 | 2.1148 | 2.3635 | 2.4101 | 2.4673 | 2.5339 | 1.4993 | 1.8376 | 1.874 | 1.9237 | 1.4993 | 2.3816 | 2.7113 | 2.744 | 2.7875 | 2.9704
2022-01-18 23:00 | 1.8862 | 2.1119 | 2.1555 | 2.2089 | 2.2712 | 1.3339 | 1.6378 | 1.6719 | 1.7184 | 1.3339 | 2.2291 | 2.5377 | 2.5683 | 2.6089 | 2.78
2022-01-19 | 1.7719 | 1.9806 | 2.0199 | 2.0681 | 2.1242 | 1.1442 | 1.4076 | 1.4383 | 1.4802 | 1.1442 | 1.467 | 1.6848 | 1.7124 | 1.749 | 1.8734
2022-01-19 01:00 | 1.6576 | 1.8483 | 1.8829 | 1.9251 | 1.9743 | 1.0429 | 1.2811 | 1.308 | 1.3448 | 1.0429 | 1.3337 | 1.5299 | 1.5541 | 1.5862 | 1.698
2022-01-19 02:00 | 1.6195 | 1.7978 | 1.8275 | 1.8637 | 1.906 | 0.99073 | 1.2125 | 1.2356 | 1.2672 | 0.99073 | 1.3908 | 1.5866 | 1.6074 | 1.635 | 1.7444
2022-01-19 03:00 | 1.5814 | 1.7448 | 1.7683 | 1.797 | 1.8304 | 0.97821 | 1.189 | 1.2072 | 1.2322 | 0.97821 | 1.2765 | 1.4511 | 1.4675 | 1.4893 | 1.5856
2022-01-19 04:00 | 1.6004 | 1.7535 | 1.7709 | 1.7922 | 1.817 | 0.99073 | 1.1952 | 1.2087 | 1.2273 | 0.99073 | 1.3908 | 1.5697 | 1.5819 | 1.5981 | 1.694
2022-01-19 05:00 | 1.6576 | 1.8048 | 1.8171 | 1.8321 | 1.8496 | 1.0288 | 1.2329 | 1.2424 | 1.2555 | 1.0288 | 1.3718 | 1.5414 | 1.55 | 1.5614 | 1.6505
2022-01-19 06:00 | 1.7147 | 1.8622 | 1.8725 | 1.885 | 1.8996 | 1.1112 | 1.3272 | 1.3352 | 1.3461 | 1.1112 | 1.3718 | 1.5386 | 1.5458 | 1.5553 | 1.6421
2022-01-19 07:00 | 1.829 | 1.9884 | 2.0003 | 2.0149 | 2.032 | 1.1813 | 1.4125 | 1.4218 | 1.4345 | 1.1813 | 1.3908 | 1.5621 | 1.5705 | 1.5816 | 1.6713
2022-01-19 08:00 | 1.9434 | 2.1203 | 2.1369 | 2.1572 | 2.1808 | 1.2003 | 1.4416 | 1.4545 | 1.4722 | 1.2003 | 1.1813 | 1.3357 | 1.3473 | 1.3627 | 1.4461
2022-01-19 09:00 | 1.7912 | 1.9701 | 1.9935 | 2.0221 | 2.0555 | 1.1314 | 1.3698 | 1.3881 | 1.413 | 1.1314 | 1.1813 | 1.3451 | 1.3615 | 1.3833 | 1.4743
2022-01-19 10:00 | 1.6957 | 1.8818 | 1.9125 | 1.95 | 1.9938 | 0.93358 | 1.1465 | 1.1704 | 1.2031 | 0.93358 | 1.7528 | 1.9904 | 2.0119 | 2.0404 | 2.1709
2022-01-19 11:00 | 1.7147 | 1.9132 | 1.9495 | 1.9938 | 2.0456 | 0.91452 | 1.1319 | 1.1602 | 1.1988 | 0.91452 | 1.4099 | 1.617 | 1.6424 | 1.6762 | 1.7941
2022-01-19 12:00 | 1.8672 | 2.0813 | 2.1198 | 2.1669 | 2.2218 | 1.0669 | 1.3152 | 1.3452 | 1.3862 | 1.0669 | 1.2956 | 1.4931 | 1.52 | 1.5559 | 1.6699
2022-01-19 13:00 | 2.0577 | 2.2849 | 2.3229 | 2.3693 | 2.4235 | 1.1432 | 1.4044 | 1.434 | 1.4744 | 1.1432 | 1.5433 | 1.7676 | 1.7942 | 1.8295 | 1.9566
2022-01-19 14:00 | 2.0196 | 2.239 | 2.2744 | 2.3177 | 2.3683 | 1.1813 | 1.4458 | 1.4734 | 1.5111 | 1.1813 | 1.8862 | 2.1451 | 2.1699 | 2.2029 | 2.346
2022-01-19 15:00 | 1.5623 | 1.7423 | 1.775 | 1.8149 | 1.8615 | 0.83831 | 1.0368 | 1.0622 | 1.097 | 0.83831 | 1.9434 | 2.2048 | 2.2277 | 2.2581 | 2.4012
2022-01-19 16:00 | 1.8727 | 2.0722 | 2.103 | 2.1407 | 2.1846 | 1.105 | 1.3493 | 1.3733 | 1.4061 | 1.105 | 1.5814 | 1.8 | 1.8216 | 1.8503 | 1.9715
2022-01-19 17:00 | 2.0577 | 2.2701 | 2.3005 | 2.3376 | 2.381 | 1.5433 | 1.8663 | 1.89 | 1.9223 | 1.5433 | 1.6385 | 1.8629 | 1.8842 | 1.9125 | 2.0363
2022-01-19 18:00 | 2.1339 | 2.3555 | 2.3877 | 2.4271 | 2.473 | 1.6576 | 2.0039 | 2.029 | 2.0633 | 1.6576 | 2.0577 | 2.3312 | 2.3538 | 2.3837 | 2.5327
2022-01-19 19:00 | 2.172 | 2.4038 | 2.4397 | 2.4837 | 2.535 | 1.6385 | 1.9868 | 2.0148 | 2.0531 | 1.6385 | 1.9406 | 2.2064 | 2.2316 | 2.265 | 2.4117
2022-01-19 20:00 | 2.2291 | 2.475 | 2.5159 | 2.566 | 2.6244 | 1.7338 | 2.1064 | 2.1383 | 2.1819 | 1.7338 | 2.2863 | 2.5974 | 2.6261 | 2.6642 | 2.8354
2022-01-19 21:00 | 2.172 | 2.4232 | 2.4691 | 2.5252 | 2.5907 | 1.6766 | 2.0459 | 2.0817 | 2.1305 | 1.6766 | 2.191 | 2.4984 | 2.5305 | 2.5732 | 2.7447
2022-01-19 22:00 | 2.0386 | 2.2816 | 2.3283 | 2.3854 | 2.452 | 1.5118 | 1.8524 | 1.8888 | 1.9385 | 1.5118 | 1.9624 | 2.2455 | 2.2782 | 2.3217 | 2.4815
2022-01-19 23:00 | 1.9434 | 2.1733 | 2.2169 | 2.2703 | 2.3326 | 1.3177 | 1.6188 | 1.6528 | 1.6993 | 1.3177 | 1.6004 | 1.839 | 1.8696 | 1.9102 | 2.0468
2022-01-20 | 1.6957 | 1.8987 | 1.9381 | 1.9862 | 2.0424 | 1.1347 | 1.3964 | 1.427 | 1.4689 | 1.1347 | 1.5433 | 1.7695 | 1.7971 | 1.8337 | 1.9623
2022-01-20 01:00 | 1.5814 | 1.7665 | 1.801 | 1.8432 | 1.8925 | 1.055 | 1.2953 | 1.3223 | 1.359 | 1.055 | 1.3337 | 1.5299 | 1.5541 | 1.5862 | 1.698
2022-01-20 02:00 | 1.5623 | 1.7364 | 1.766 | 1.8023 | 1.8446 | 0.97168 | 1.19 | 1.2131 | 1.2447 | 0.97168 | 1.2575 | 1.4384 | 1.4592 | 1.4868 | 1.5889
2022-01-20 03:00 | 1.5623 | 1.7244 | 1.7478 | 1.7765 | 1.81 | 0.96185 | 1.1696 | 1.1879 | 1.2129 | 0.96185 | 1.2575 | 1.4299 | 1.4463 | 1.4681 | 1.5634
2022-01-20 04:00 | 1.5814 | 1.733 | 1.7504 | 1.7717 | 1.7966 | 0.97168 | 1.1727 | 1.1862 | 1.2048 | 0.97168 | 1.3718 | 1.5485 | 1.5607 | 1.5769 | 1.6717
2022-01-20 05:00 | 1.6004 | 1.7434 | 1.7557 | 1.7707 | 1.7882 | 1.0828 | 1.2966 | 1.3062 | 1.3193 | 1.0828 | 1.467 | 1.6473 | 1.6559 | 1.6673 | 1.7616
2022-01-20 06:00 | 1.6004 | 1.7394 | 1.7497 | 1.7622 | 1.7768 | 1.1813 | 1.41 | 1.418 | 1.4289 | 1.1813 | 1.3337 | 1.4962 | 1.5034 | 1.5129 | 1.5977
2022-01-20 07:00 | 1.8481 | 2.0089 | 2.0208 | 2.0354 | 2.0524 | 1.2003 | 1.435 | 1.4443 | 1.457 | 1.2003 | 1.5052 | 1.6892 | 1.6975 | 1.7086 | 1.8047
2022-01-20 08:00 | 1.9434 | 2.1203 | 2.1369 | 2.1572 | 2.1808 | 1.3337 | 1.5991 | 1.6121 | 1.6297 | 1.3337 | 1.4289 | 1.6109 | 1.6225 | 1.638 | 1.735
2022-01-20 09:00 | 1.9434 | 2.1336 | 2.157 | 2.1857 | 2.2191 | 1.2956 | 1.5638 | 1.5821 | 1.607 | 1.2956 | 1.2194 | 1.3875 | 1.4039 | 1.4257 | 1.5187
2022-01-20 10:00 | 1.9624 | 2.1684 | 2.199 | 2.2366 | 2.2804 | 1.2384 | 1.5066 | 1.5306 | 1.5632 | 1.2384 | 1.1622 | 1.3341 | 1.3555 | 1.3841 | 1.4821
2022-01-20 11:00 | 1.9243 | 2.1384 | 2.1746 | 2.219 | 2.2708 | 1.086 | 1.3345 | 1.3628 | 1.4014 | 1.086 | 1.2003 | 1.3841 | 1.4096 | 1.4433 | 1.5497
2022-01-20 12:00 | 2.0005 | 2.2246 | 2.2631 | 2.3102 | 2.3651 | 1.2575 | 1.5402 | 1.5703 | 1.6112 | 1.2575 | 1.1622 | 1.3449 | 1.3718 | 1.4077 | 1.5144
2022-01-20 13:00 | 1.9243 | 2.1416 | 2.1796 | 2.226 | 2.2802 | 1.1432 | 1.4044 | 1.434 | 1.4744 | 1.1432 | 1.6385 | 1.8734 | 1.9 | 1.9354 | 2.0677
2022-01-20 14:00 | 1.9243 | 2.1367 | 2.1721 | 2.2154 | 2.2659 | 1.1813 | 1.4458 | 1.4734 | 1.5111 | 1.1813 | 1.2194 | 1.4041 | 1.4289 | 1.4619 | 1.5683
2022-01-20 15:00 | 1.9053 | 2.1108 | 2.1434 | 2.1834 | 2.2299 | 1.1813 | 1.4419 | 1.4673 | 1.5021 | 1.1813 | 1.0098 | 1.1674 | 1.1903 | 1.2206 | 1.3125
2022-01-20 16:00 | 2.0577 | 2.2709 | 2.3017 | 2.3395 | 2.3834 | 1.2765 | 1.5518 | 1.5759 | 1.6087 | 1.2765 | 1.4861 | 1.6942 | 1.7157 | 1.7444 | 1.8604
2022-01-20 17:00 | 2.0196 | 2.2291 | 2.2595 | 2.2967 | 2.34 | 1.5052 | 1.8213 | 1.845 | 1.8773 | 1.5052 | 1.6576 | 1.8841 | 1.9054 | 1.9336 | 2.0586
2022-01-20 18:00 | 2.2291 | 2.4579 | 2.49 | 2.5294 | 2.5753 | 1.6195 | 1.9589 | 1.984 | 2.0183 | 1.6195 | 1.8862 | 2.1407 | 2.1632 | 2.1932 | 2.3327
2022-01-20 19:00 | 2.1148 | 2.3424 | 2.3783 | 2.4223 | 2.4736 | 1.6576 | 2.0093 | 2.0373 | 2.0756 | 1.6576 | 2.2863 | 2.5905 | 2.6157 | 2.6491 | 2.8148
2022-01-20 20:00 | 2.2101 | 2.4545 | 2.4954 | 2.5455 | 2.6039 | 1.7147 | 2.0839 | 2.1158 | 2.1594 | 1.7147 | 2.0577 | 2.3433 | 2.372 | 2.4101 | 2.5688
2022-01-20 21:00 | 2.2101 | 2.4642 | 2.51 | 2.5662 | 2.6316 | 1.6429 | 2.0061 | 2.0419 | 2.0907 | 1.6429 | 2.191 | 2.4984 | 2.5305 | 2.5732 | 2.7447
2022-01-20 22:00 | 2.0767 | 2.3225 | 2.3692 | 2.4263 | 2.493 | 1.4861 | 1.822 | 1.8584 | 1.9081 | 1.4861 | 2.0577 | 2.3514 | 2.3841 | 2.4275 | 2.5926
2022-01-20 23:00 | 1.9053 | 2.1323 | 2.176 | 2.2294 | 2.2917 | 1.3473 | 1.6537 | 1.6878 | 1.7343 | 1.3473 | 1.7147 | 1.966 | 1.9966 | 2.0373 | 2.1801
2022-01-21 | 1.7192 | 1.924 | 1.9633 | 2.0115 | 2.0676 | 1.126 | 1.3861 | 1.4168 | 1.4587 | 1.126 | 1.5242 | 1.7483 | 1.7759 | 1.8125 | 1.9401
2022-01-21 01:00 | 1.6195 | 1.8074 | 1.8419 | 1.8842 | 1.9334 | 1.0288 | 1.2645 | 1.2914 | 1.3282 | 1.0288 | 1.3527 | 1.5511 | 1.5753 | 1.6074 | 1.7202
2022-01-21 02:00 | 1.5814 | 1.7569 | 1.7865 | 1.8228 | 1.865 | 0.99073 | 1.2125 | 1.2356 | 1.2672 | 0.99073 | 1.5433 | 1.756 | 1.7768 | 1.8044 | 1.9222
2022-01-21 03:00 | 1.5433 | 1.7039 | 1.7273 | 1.756 | 1.7895 | 0.97168 | 1.1812 | 1.1995 | 1.2245 | 0.97168 | 1.2575 | 1.4299 | 1.4463 | 1.4681 | 1.5634
2022-01-21 04:00 | 1.6004 | 1.7535 | 1.7709 | 1.7922 | 1.817 | 0.9579 | 1.1564 | 1.1699 | 1.1885 | 0.9579 | 1.3337 | 1.5062 | 1.5184 | 1.5346 | 1.6273
2022-01-21 05:00 | 1.6195 | 1.7639 | 1.7761 | 1.7911 | 1.8086 | 1.0479 | 1.2554 | 1.2649 | 1.278 | 1.0479 | 1.2956 | 1.4567 | 1.4653 | 1.4767 | 1.5616
2022-01-21 06:00 | 1.6311 | 1.7724 | 1.7826 | 1.7951 | 1.8097 | 1.1535 | 1.3772 | 1.3852 | 1.3961 | 1.1535 | 1.4289 | 1.6021 | 1.6093 | 1.6188 | 1.7087
2022-01-21 07:00 | 1.8862 | 2.0498 | 2.0617 | 2.0763 | 2.0934 | 1.2384 | 1.48 | 1.4893 | 1.502 | 1.2384 | 1.2765 | 1.4351 | 1.4435 | 1.4546 | 1.538
2022-01-21 08:00 | 1.7147 | 1.8747 | 1.8912 | 1.9115 | 1.9352 | 1.1241 | 1.3515 | 1.3645 | 1.3821 | 1.1241 | 1.1432 | 1.2933 | 1.3049 | 1.3204 | 1.4017
2022-01-21 09:00 | 1.9592 | 2.1507 | 2.1741 | 2.2027 | 2.2361 | 1.086 | 1.3162 | 1.3345 | 1.3594 | 1.086 | 1.0288 | 1.1758 | 1.1921 | 1.2139 | 1.2965
2022-01-21 10:00 | 1.9815 | 2.1888 | 2.2195 | 2.257 | 2.3008 | 1.2003 | 1.4616 | 1.4855 | 1.5182 | 1.2003 | 1.0098 | 1.1647 | 1.1862 | 1.2147 | 1.3044
2022-01-21 11:00 | 1.829 | 2.036 | 2.0723 | 2.1167 | 2.1684 | 1.0031 | 1.2366 | 1.2649 | 1.3035 | 1.0031 | 1.5433 | 1.7652 | 1.7907 | 1.8244 | 1.9496
2022-01-21 12:00 | 1.829 | 2.0404 | 2.0788 | 2.1259 | 2.1809 | 1.0479 | 1.2927 | 1.3227 | 1.3637 | 1.0479 | 1.5242 | 1.7472 | 1.7741 | 1.8099 | 1.9366
2022-01-21 13:00 | 1.6766 | 1.8755 | 1.9135 | 1.9599 | 2.0141 | 0.99073 | 1.2244 | 1.254 | 1.2944 | 0.99073 | 2.0386 | 2.3181 | 2.3446 | 2.38 | 2.5343
2022-01-21 14:00 | 1.7909 | 1.9934 | 2.0288 | 2.0721 | 2.1226 | 0.87642 | 1.0857 | 1.1133 | 1.151 | 0.87642 | 1.7147 | 1.9546 | 1.9794 | 2.0124 | 2.146
2022-01-21 15:00 | 1.9053 | 2.1108 | 2.1434 | 2.1834 | 2.2299 | 0.95263 | 1.1718 | 1.1973 | 1.232 | 0.95263 | 1.3908 | 1.5908 | 1.6137 | 1.6441 | 1.7569
2022-01-21 16:00 | 2.0005 | 2.2095 | 2.2403 | 2.278 | 2.322 | 1.2194 | 1.4843 | 1.5083 | 1.5411 | 1.2194 | 1.5623 | 1.7788 | 1.8004 | 1.8291 | 1.9493
2022-01-21 17:00 | 2.0386 | 2.2496 | 2.28 | 2.3171 | 2.3605 | 1.2765 | 1.5512 | 1.5749 | 1.6072 | 1.2765 | 1.448 | 1.6512 | 1.6725 | 1.7007 | 1.8141
2022-01-21 18:00 | 2.0386 | 2.2532 | 2.2853 | 2.3247 | 2.3706 | 1.467 | 1.7789 | 1.804 | 1.8382 | 1.467 | 2.0386 | 2.3101 | 2.3326 | 2.3625 | 2.5104
2022-01-21 19:00 | 2.0386 | 2.2605 | 2.2965 | 2.3404 | 2.3917 | 1.5814 | 1.9192 | 1.9473 | 1.9855 | 1.5814 | 2.0005 | 2.2729 | 2.2981 | 2.3316 | 2.4815
2022-01-21 20:00 | 2.2291 | 2.475 | 2.5159 | 2.566 | 2.6244 | 1.6385 | 1.9939 | 2.0258 | 2.0693 | 1.6385 | 2.1339 | 2.428 | 2.4567 | 2.4948 | 2.6577
2022-01-21 21:00 | 2.1629 | 2.4134 | 2.4593 | 2.5154 | 2.5809 | 1.6766 | 2.0459 | 2.0817 | 2.1305 | 1.6766 | 2.0196 | 2.3079 | 2.34 | 2.3827 | 2.5448
2022-01-21 22:00 | 2.0577 | 2.302 | 2.3487 | 2.4059 | 2.4725 | 1.4861 | 1.822 | 1.8584 | 1.9081 | 1.4861 | 2.0005 | 2.2878 | 2.3206 | 2.364 | 2.526
2022-01-21 23:00 | 1.9053 | 2.1323 | 2.176 | 2.2294 | 2.2917 | 1.3084 | 1.6077 | 1.6417 | 1.6882 | 1.3084 | 1.6766 | 1.9237 | 1.9543 | 1.9949 | 2.1357
2022-01-22 | 1.7528 | 1.9601 | 1.9995 | 2.0476 | 2.1038 | 1.1879 | 1.4593 | 1.4899 | 1.5318 | 1.1879 | 1.448 | 1.6636 | 1.6912 | 1.7278 | 1.8512
2022-01-22 01:00 | 1.6957 | 1.8893 | 1.9238 | 1.966 | 2.0153 | 1.0565 | 1.2972 | 1.3241 | 1.3609 | 1.0565 | 1.448 | 1.6569 | 1.6811 | 1.7133 | 1.8313
2022-01-22 02:00 | 1.6385 | 1.8183 | 1.8479 | 1.8842 | 1.9264 | 0.99073 | 1.2125 | 1.2356 | 1.2672 | 0.99073 | 1.4289 | 1.629 | 1.6497 | 1.6773 | 1.7888
2022-01-22 03:00 | 1.5814 | 1.7448 | 1.7683 | 1.797 | 1.8304 | 0.96529 | 1.1737 | 1.192 | 1.2169 | 0.96529 | 1.3527 | 1.5357 | 1.5522 | 1.574 | 1.6745
2022-01-22 04:00 | 1.5623 | 1.7125 | 1.7299 | 1.7512 | 1.7761 | 0.95263 | 1.1501 | 1.1637 | 1.1823 | 0.95263 | 1.3146 | 1.485 | 1.4972 | 1.5134 | 1.6051
2022-01-22 05:00 | 1.5814 | 1.7229 | 1.7352 | 1.7502 | 1.7677 | 0.99073 | 1.1878 | 1.1974 | 1.2105 | 0.99073 | 1.2384 | 1.3932 | 1.4018 | 1.4132 | 1.4949
2022-01-22 06:00 | 1.5402 | 1.6748 | 1.685 | 1.6975 | 1.7121 | 1.0158 | 1.2146 | 1.2226 | 1.2335 | 1.0158 | 1.2194 | 1.3692 | 1.3764 | 1.3859 | 1.4643
2022-01-22 07:00 | 1.5433 | 1.6814 | 1.6933 | 1.7079 | 1.7249 | 1.0288 | 1.2324 | 1.2417 | 1.2544 | 1.0288 | 1.2575 | 1.4139 | 1.4223 | 1.4334 | 1.5158
2022-01-22 08:00 | 1.3908 | 1.5267 | 1.5433 | 1.5636 | 1.5872 | 0.87642 | 1.0589 | 1.0719 | 1.0895 | 0.87642 | 0.97168 | 1.1028 | 1.1144 | 1.1298 | 1.2017
2022-01-22 09:00 | 1.5433 | 1.7038 | 1.7272 | 1.7558 | 1.7892 | 0.99073 | 1.2037 | 1.2219 | 1.2468 | 0.99073 | 1.2765 | 1.451 | 1.4674 | 1.4892 | 1.5854
2022-01-22 10:00 | 1.6195 | 1.7999 | 1.8306 | 1.8681 | 1.9119 | 1.0479 | 1.2815 | 1.3055 | 1.3381 | 1.0479 | 0.95884 | 1.1081 | 1.1295 | 1.1581 | 1.245
2022-01-22 11:00 | 1.5433 | 1.729 | 1.7652 | 1.8096 | 1.8614 | 0.89547 | 1.1094 | 1.1377 | 1.1763 | 0.89547 | 1.2384 | 1.4265 | 1.4519 | 1.4857 | 1.5941
2022-01-22 12:00 | 1.5814 | 1.7743 | 1.8127 | 1.8598 | 1.9148 | 0.89547 | 1.1126 | 1.1426 | 1.1836 | 0.89547 | 1.5814 | 1.8107 | 1.8376 | 1.8735 | 2.0032
2022-01-22 13:00 | 1.6004 | 1.7937 | 1.8316 | 1.8781 | 1.9322 | 1.0288 | 1.2694 | 1.299 | 1.3394 | 1.0288 | 1.4289 | 1.6405 | 1.6671 | 1.7025 | 1.8233
2022-01-22 14:00 | 1.5814 | 1.7682 | 1.8036 | 1.8469 | 1.8975 | 0.99073 | 1.2207 | 1.2484 | 1.2861 | 0.99073 | 1.6385 | 1.8699 | 1.8947 | 1.9277 | 2.0571
2022-01-22 15:00 | 1.7909 | 1.988 | 2.0206 | 2.0606 | 2.1071 | 0.99073 | 1.2168 | 1.2423 | 1.277 | 0.99073 | 1.4289 | 1.6332 | 1.656 | 1.6864 | 1.8013
2022-01-22 16:00 | 1.7719 | 1.9639 | 1.9947 | 2.0324 | 2.0764 | 1.2194 | 1.4843 | 1.5083 | 1.5411 | 1.2194 | 1.1622 | 1.3342 | 1.3558 | 1.3845 | 1.4827
2022-01-22 17:00 | 1.7909 | 1.9835 | 2.0139 | 2.051 | 2.0944 | 1.2628 | 1.535 | 1.5587 | 1.591 | 1.2628 | 1.0288 | 1.1854 | 1.2067 | 1.235 | 1.3253
2022-01-22 18:00 | 2.0427 | 2.2576 | 2.2897 | 2.3291 | 2.375 | 1.5623 | 1.8914 | 1.9165 | 1.9508 | 1.5623 | 1.6957 | 1.929 | 1.9515 | 1.9814 | 2.1105
2022-01-22 19:00 | 2.191 | 2.4243 | 2.4602 | 2.5042 | 2.5555 | 1.5623 | 1.8967 | 1.9248 | 1.963 | 1.5623 | 2.0958 | 2.3788 | 2.404 | 2.4374 | 2.5926
2022-01-22 20:00 | 2.2101 | 2.4545 | 2.4954 | 2.5455 | 2.6039 | 1.6831 | 2.0465 | 2.0784 | 2.122 | 1.6831 | 2.191 | 2.4916 | 2.5202 | 2.5583 | 2.7243
2022-01-22 21:00 | 2.2101 | 2.4642 | 2.51 | 2.5662 | 2.6316 | 1.6957 | 2.0684 | 2.1042 | 2.153 | 1.6957 | 2.6483 | 3.0065 | 3.0387 | 3.0814 | 3.278
2022-01-22 22:00 | 2.0958 | 2.343 | 2.3897 | 2.4468 | 2.5135 | 1.4714 | 1.8046 | 1.841 | 1.8907 | 1.4714 | 2.2863 | 2.6054 | 2.6381 | 2.6816 | 2.8593
2022-01-22 23:00 | 1.9434 | 2.1733 | 2.2169 | 2.2703 | 2.3326 | 1.3527 | 1.6601 | 1.6942 | 1.7406 | 1.3527 | 1.9624 | 2.2413 | 2.2719 | 2.3125 | 2.469
2022-01-23 | 1.7909 | 2.0011 | 2.0404 | 2.0886 | 2.1447 | 1.1941 | 1.4666 | 1.4973 | 1.5392 | 1.1941 | 1.5242 | 1.7483 | 1.7759 | 1.8125 | 1.9401
2022-01-23 01:00 | 1.6957 | 1.8893 | 1.9238 | 1.966 | 2.0153 | 1.0842 | 1.3299 | 1.3568 | 1.3936 | 1.0842 | 1.3337 | 1.5299 | 1.5541 | 1.5862 | 1.698
2022-01-23 02:00 | 1.6957 | 1.8797 | 1.9093 | 1.9456 | 1.9879 | 1.0098 | 1.235 | 1.2581 | 1.2897 | 1.0098 | 1.5814 | 1.7984 | 1.8191 | 1.8467 | 1.9666
2022-01-23 03:00 | 1.6004 | 1.7653 | 1.7887 | 1.8174 | 1.8509 | 0.99381 | 1.2074 | 1.2257 | 1.2506 | 0.99381 | 1.3146 | 1.4934 | 1.5098 | 1.5317 | 1.63
2022-01-23 04:00 | 1.6004 | 1.7535 | 1.7709 | 1.7922 | 1.817 | 0.97168 | 1.1727 | 1.1862 | 1.2048 | 0.97168 | 1.2956 | 1.4639 | 1.4761 | 1.4923 | 1.5829
2022-01-23 05:00 | 1.5623 | 1.7025 | 1.7147 | 1.7297 | 1.7472 | 0.98419 | 1.1801 | 1.1897 | 1.2027 | 0.98419 | 1.2956 | 1.4567 | 1.4653 | 1.4767 | 1.5616
2022-01-23 06:00 | 1.5324 | 1.6663 | 1.6765 | 1.6891 | 1.7037 | 0.99073 | 1.185 | 1.1929 | 1.2038 | 0.99073 | 1.2956 | 1.4539 | 1.4611 | 1.4706 | 1.5532
2022-01-23 07:00 | 1.4913 | 1.6255 | 1.6374 | 1.652 | 1.6691 | 0.99073 | 1.1874 | 1.1967 | 1.2094 | 0.99073 | 1.1813 | 1.3292 | 1.3376 | 1.3487 | 1.4269
2022-01-23 08:00 | 1.5242 | 1.67 | 1.6866 | 1.7068 | 1.7305 | 1.0098 | 1.2165 | 1.2294 | 1.2471 | 1.0098 | 1.1432 | 1.2933 | 1.3049 | 1.3204 | 1.4017
2022-01-23 09:00 | 1.5814 | 1.7447 | 1.7681 | 1.7968 | 1.8302 | 1.0098 | 1.2262 | 1.2444 | 1.2694 | 1.0098 | 1.105 | 1.2604 | 1.2768 | 1.2986 | 1.3854
2022-01-23 10:00 | 1.4861 | 1.6566 | 1.6873 | 1.7248 | 1.7686 | 1.086 | 1.3266 | 1.3505 | 1.3832 | 1.086 | 1.0479 | 1.207 | 1.2285 | 1.2571 | 1.3488
2022-01-23 11:00 | 1.3017 | 1.4694 | 1.5057 | 1.5501 | 1.6018 | 0.85737 | 1.0644 | 1.0927 | 1.1313 | 0.85737 | 1.2517 | 1.4412 | 1.4666 | 1.5004 | 1.6096
2022-01-23 12:00 | 1.2575 | 1.4263 | 1.4648 | 1.5119 | 1.5668 | 0.81926 | 1.0226 | 1.0526 | 1.0936 | 0.81926 | 1.5623 | 1.7895 | 1.8165 | 1.8523 | 1.981
2022-01-23 13:00 | 1.2384 | 1.4048 | 1.4427 | 1.4892 | 1.5433 | 0.81926 | 1.0218 | 1.0514 | 1.0918 | 0.81926 | 1.4861 | 1.7041 | 1.7306 | 1.766 | 1.8899
2022-01-23 14:00 | 1.3718 | 1.5431 | 1.5785 | 1.6218 | 1.6723 | 0.93358 | 1.1532 | 1.1808 | 1.2185 | 0.93358 | 1.6576 | 1.8911 | 1.9159 | 1.9488 | 2.0794
2022-01-23 15:00 | 1.4861 | 1.6605 | 1.6931 | 1.733 | 1.7796 | 0.80021 | 0.99174 | 1.0172 | 1.0519 | 0.80021 | 1.3146 | 1.5061 | 1.529 | 1.5594 | 1.668
2022-01-23 16:00 | 1.6195 | 1.8002 | 1.831 | 1.8687 | 1.9126 | 1.0429 | 1.2759 | 1.2999 | 1.3327 | 1.0429 | 0.91452 | 1.059 | 1.0806 | 1.1092 | 1.1938
2022-01-23 17:00 | 2.0767 | 2.2906 | 2.3209 | 2.3581 | 2.4014 | 1.5052 | 1.8213 | 1.845 | 1.8773 | 1.5052 | 1.2765 | 1.4607 | 1.4819 | 1.5102 | 1.6142
2022-01-23 18:00 | 2.3625 | 2.6011 | 2.6333 | 2.6727 | 2.7186 | 1.7577 | 2.1222 | 2.1473 | 2.1816 | 1.7577 | 2.2101 | 2.5006 | 2.5231 | 2.5531 | 2.7104
2022-01-23 19:00 | 2.4959 | 2.7518 | 2.7877 | 2.8317 | 2.883 | 1.9053 | 2.3019 | 2.3299 | 2.3682 | 1.9053 | 2.6293 | 2.9716 | 2.9968 | 3.0302 | 3.2148
2022-01-23 20:00 | 2.4768 | 2.7411 | 2.782 | 2.8321 | 2.8905 | 1.8372 | 2.2286 | 2.2605 | 2.3041 | 1.8372 | 2.4387 | 2.7668 | 2.7955 | 2.8336 | 3.0132
2022-01-23 21:00 | 2.3625 | 2.6279 | 2.6738 | 2.7299 | 2.7954 | 1.8166 | 2.2113 | 2.2471 | 2.2959 | 1.8166 | 2.3816 | 2.7101 | 2.7423 | 2.785 | 2.9669
2022-01-23 22:00 | 2.2291 | 2.4863 | 2.533 | 2.5901 | 2.6567 | 1.5814 | 1.9345 | 1.971 | 2.0207 | 1.5814 | 2.4197 | 2.7536 | 2.7863 | 2.8298 | 3.0148
2022-01-23 23:00 | 1.9624 | 2.1937 | 2.2374 | 2.2908 | 2.3531 | 1.3718 | 1.6826 | 1.7167 | 1.7632 | 1.3718 | 1.7338 | 1.9872 | 2.0178 | 2.0584 | 2.2023
2022-01-24 | 1.7909 | 2.0011 | 2.0404 | 2.0886 | 2.1447 | 1.1749 | 1.4438 | 1.4745 | 1.5164 | 1.1749 | 1.5433 | 1.7695 | 1.7971 | 1.8337 | 1.9623
2022-01-24 01:00 | 1.6957 | 1.8893 | 1.9238 | 1.966 | 2.0153 | 1.0911 | 1.338 | 1.3649 | 1.4017 | 1.0911 | 1.3337 | 1.5299 | 1.5541 | 1.5862 | 1.698
2022-01-24 02:00 | 1.6385 | 1.8183 | 1.8479 | 1.8842 | 1.9264 | 1.0098 | 1.235 | 1.2581 | 1.2897 | 1.0098 | 1.2003 | 1.3749 | 1.3957 | 1.4233 | 1.5222
2022-01-24 03:00 | 1.6004 | 1.7653 | 1.7887 | 1.8174 | 1.8509 | 0.98471 | 1.1966 | 1.2149 | 1.2399 | 0.98471 | 1.2575 | 1.4299 | 1.4463 | 1.4681 | 1.5634
2022-01-24 04:00 | 1.6195 | 1.7739 | 1.7913 | 1.8127 | 1.8375 | 0.97168 | 1.1727 | 1.1862 | 1.2048 | 0.97168 | 1.2765 | 1.4427 | 1.4549 | 1.4711 | 1.5606
2022-01-24 05:00 | 1.7338 | 1.8867 | 1.8989 | 1.9139 | 1.9314 | 1.0288 | 1.2329 | 1.2424 | 1.2555 | 1.0288 | 1.3337 | 1.4991 | 1.5077 | 1.5191 | 1.606
2022-01-24 06:00 | 1.6576 | 1.8008 | 1.8111 | 1.8236 | 1.8382 | 1.086 | 1.2975 | 1.3055 | 1.3164 | 1.086 | 1.2575 | 1.4116 | 1.4187 | 1.4283 | 1.5088
2022-01-24 07:00 | 1.7909 | 1.9474 | 1.9594 | 1.974 | 1.991 | 1.2003 | 1.435 | 1.4443 | 1.457 | 1.2003 | 1.1813 | 1.3292 | 1.3376 | 1.3487 | 1.4269
2022-01-24 08:00 | 1.7365 | 1.8981 | 1.9147 | 1.935 | 1.9586 | 1.105 | 1.329 | 1.342 | 1.3596 | 1.105 | 1.2575 | 1.4204 | 1.432 | 1.4474 | 1.535
2022-01-24 09:00 | 1.9243 | 2.1132 | 2.1366 | 2.1652 | 2.1986 | 0.99073 | 1.2037 | 1.2219 | 1.2468 | 0.99073 | 1.105 | 1.2604 | 1.2768 | 1.2986 | 1.3854
2022-01-24 10:00 | 1.9053 | 2.1069 | 2.1376 | 2.1752 | 2.2189 | 1.0098 | 1.2365 | 1.2605 | 1.2931 | 1.0098 | 1.1622 | 1.3341 | 1.3555 | 1.3841 | 1.4821
2022-01-24 11:00 | 1.9053 | 2.1179 | 2.1541 | 2.1985 | 2.2503 | 0.95795 | 1.1832 | 1.2115 | 1.2502 | 0.95795 | 1.7909 | 2.0405 | 2.0659 | 2.0997 | 2.2385
2022-01-24 12:00 | 1.8672 | 2.0813 | 2.1198 | 2.1669 | 2.2218 | 0.91452 | 1.1351 | 1.1651 | 1.2061 | 0.91452 | 1.81 | 2.0647 | 2.0917 | 2.1275 | 2.2699
2022-01-24 13:00 | 1.8481 | 2.0598 | 2.0977 | 2.1442 | 2.1983 | 0.91452 | 1.1343 | 1.1639 | 1.2043 | 0.91452 | 2.0005 | 2.2757 | 2.3023 | 2.3376 | 2.4898
2022-01-24 14:00 | 2.2673 | 2.5051 | 2.5405 | 2.5838 | 2.6344 | 1.0353 | 1.2734 | 1.301 | 1.3387 | 1.0353 | 1.5433 | 1.764 | 1.7888 | 1.8218 | 1.946
2022-01-24 15:00 | 2.2291 | 2.4588 | 2.4914 | 2.5313 | 2.5779 | 1.105 | 1.3519 | 1.3773 | 1.4121 | 1.105 | 0.80021 | 0.9345 | 0.95736 | 0.98775 | 1.0681
2022-01-24 16:00 | 2.191 | 2.4142 | 2.445 | 2.4827 | 2.5267 | 1.1622 | 1.4168 | 1.4408 | 1.4736 | 1.1622 | 1.1813 | 1.3554 | 1.377 | 1.4057 | 1.5049
2022-01-24 17:00 | 2.3054 | 2.5362 | 2.5665 | 2.6037 | 2.647 | 1.3289 | 1.613 | 1.6367 | 1.6691 | 1.3289 | 1.5623 | 1.7782 | 1.7995 | 1.8278 | 1.9475
2022-01-24 18:00 | 2.4197 | 2.6625 | 2.6947 | 2.7341 | 2.78 | 1.6766 | 2.0264 | 2.0515 | 2.0858 | 1.6766 | 2.2863 | 2.5853 | 2.6078 | 2.6378 | 2.7993
2022-01-24 19:00 | 2.5149 | 2.7722 | 2.8082 | 2.8522 | 2.9034 | 1.7083 | 2.0692 | 2.0972 | 2.1355 | 1.7083 | 2.2482 | 2.5482 | 2.5733 | 2.6068 | 2.7704
2022-01-24 20:00 | 2.4387 | 2.7001 | 2.741 | 2.7911 | 2.8495 | 1.81 | 2.1964 | 2.2283 | 2.2719 | 1.81 | 2.3054 | 2.6186 | 2.6473 | 2.6853 | 2.8576
2022-01-24 21:00 | 2.3511 | 2.6156 | 2.6615 | 2.7176 | 2.7831 | 1.7719 | 2.1584 | 2.1942 | 2.243 | 1.7719 | 2.4006 | 2.7313 | 2.7634 | 2.8061 | 2.9891
2022-01-24 22:00 | 2.2101 | 2.4658 | 2.5125 | 2.5696 | 2.6363 | 1.5617 | 1.9113 | 1.9477 | 1.9975 | 1.5617 | 2.2291 | 2.5419 | 2.5746 | 2.6181 | 2.7926
2022-01-24 23:00 | 2.0577 | 2.2961 | 2.3397 | 2.3932 | 2.4555 | 1.3868 | 1.7003 | 1.7344 | 1.7809 | 1.3868 | 1.6766 | 1.9237 | 1.9543 | 1.9949 | 2.1357
2022-01-25 | 1.8672 | 2.083 | 2.1223 | 2.1704 | 2.2266 | 1.2264 | 1.5048 | 1.5354 | 1.5773 | 1.2264 | 1.6385 | 1.8754 | 1.9029 | 1.9395 | 2.0734
2022-01-25 01:00 | 1.6957 | 1.8893 | 1.9238 | 1.966 | 2.0153 | 1.086 | 1.332 | 1.3589 | 1.3957 | 1.086 | 1.3718 | 1.5723 | 1.5964 | 1.6286 | 1.7424
2022-01-25 02:00 | 1.6385 | 1.8183 | 1.8479 | 1.8842 | 1.9264 | 1.0013 | 1.225 | 1.2481 | 1.2797 | 1.0013 | 1.467 | 1.6713 | 1.6921 | 1.7197 | 1.8333
2022-01-25 03:00 | 1.6385 | 1.8062 | 1.8297 | 1.8584 | 1.8918 | 0.97168 | 1.1812 | 1.1995 | 1.2245 | 0.97168 | 1.2575 | 1.4299 | 1.4463 | 1.4681 | 1.5634
2022-01-25 04:00 | 1.6385 | 1.7944 | 1.8118 | 1.8331 | 1.858 | 0.99073 | 1.1952 | 1.2087 | 1.2273 | 0.99073 | 1.2765 | 1.4427 | 1.4549 | 1.4711 | 1.5606
2022-01-25 05:00 | 1.7209 | 1.8728 | 1.8851 | 1.9001 | 1.9176 | 1.0789 | 1.292 | 1.3016 | 1.3147 | 1.0789 | 1.2384 | 1.3932 | 1.4018 | 1.4132 | 1.4949
2022-01-25 06:00 | 1.7719 | 1.9236 | 1.9339 | 1.9464 | 1.961 | 1.1622 | 1.3875 | 1.3955 | 1.4064 | 1.1622 | 1.2956 | 1.4539 | 1.4611 | 1.4706 | 1.5532
2022-01-25 07:00 | 2.0767 | 2.2545 | 2.2664 | 2.281 | 2.2981 | 1.2765 | 1.525 | 1.5343 | 1.547 | 1.2765 | 1.5623 | 1.7527 | 1.761 | 1.7722 | 1.8713
2022-01-25 08:00 | 2.0767 | 2.2636 | 2.2802 | 2.3004 | 2.3241 | 1.2765 | 1.5316 | 1.5445 | 1.5622 | 1.2765 | 1.2956 | 1.4627 | 1.4743 | 1.4898 | 1.5794
2022-01-25 09:00 | 1.8481 | 2.0313 | 2.0547 | 2.0833 | 2.1167 | 1.0608 | 1.2865 | 1.3047 | 1.3297 | 1.0608 | 0.99073 | 1.1334 | 1.1498 | 1.1716 | 1.2521
2022-01-25 10:00 | 2.172 | 2.3935 | 2.4242 | 2.4617 | 2.5055 | 1.105 | 1.3491 | 1.373 | 1.4057 | 1.105 | 1.5623 | 1.7787 | 1.8002 | 1.8287 | 1.9488
2022-01-25 11:00 | 2.2291 | 2.4659 | 2.5021 | 2.5465 | 2.5983 | 1.1813 | 1.4471 | 1.4753 | 1.514 | 1.1813 | 1.81 | 2.0617 | 2.0871 | 2.1208 | 2.2607
2022-01-25 12:00 | 1.9624 | 2.1836 | 2.2221 | 2.2692 | 2.3241 | 0.7621 | 0.95503 | 0.98505 | 1.026 | 0.7621 | 1.3584 | 1.5629 | 1.5898 | 1.6257 | 1.7432
2022-01-25 13:00 | 2.1148 | 2.3463 | 2.3843 | 2.4307 | 2.4849 | 0.89547 | 1.1118 | 1.1414 | 1.1818 | 0.89547 | 1.467 | 1.6829 | 1.7095 | 1.7448 | 1.8677
2022-01-25 14:00 | 2.553 | 2.8121 | 2.8475 | 2.8909 | 2.9414 | 1.0098 | 1.2433 | 1.2709 | 1.3086 | 1.0098 | 1.0479 | 1.2136 | 1.2384 | 1.2713 | 1.3683
2022-01-25 15:00 | 2.4959 | 2.7453 | 2.778 | 2.8179 | 2.8645 | 1.0288 | 1.2618 | 1.2873 | 1.322 | 1.0288 | 0.97168 | 1.125 | 1.1479 | 1.1783 | 1.268
2022-01-25 16:00 | 2.8579 | 3.1306 | 3.1614 | 3.1991 | 3.2431 | 1.5052 | 1.8219 | 1.8459 | 1.8788 | 1.5052 | 2.7245 | 3.0704 | 3.0919 | 3.1206 | 3.3047
2022-01-25 17:00 | 3.1056 | 3.3959 | 3.4262 | 3.4634 | 3.5067 | 2.2291 | 2.6766 | 2.7003 | 2.7326 | 2.2291 | 3.2199 | 3.6202 | 3.6415 | 3.6698 | 3.8806
2022-01-25 18:00 | 2.9267 | 3.2073 | 3.2394 | 3.2788 | 3.3247 | 2.172 | 2.6116 | 2.6367 | 2.671 | 2.172 | 3.7724 | 4.2367 | 4.2593 | 4.2892 | 4.5324
2022-01-25 19:00 | 2.7055 | 2.9769 | 3.0129 | 3.0569 | 3.1081 | 2.1148 | 2.5495 | 2.5775 | 2.6158 | 2.1148 | 3.1056 | 3.5009 | 3.5261 | 3.5595 | 3.7703
2022-01-25 20:00 | 2.6102 | 2.8843 | 2.9253 | 2.9753 | 3.0337 | 2.0386 | 2.4665 | 2.4984 | 2.542 | 2.0386 | 3.1056 | 3.5078 | 3.5365 | 3.5746 | 3.7909
2022-01-25 21:00 | 2.5911 | 2.8735 | 2.9194 | 2.9755 | 3.041 | 1.9692 | 2.3915 | 2.4273 | 2.4761 | 1.9692 | 3.1056 | 3.5147 | 3.5468 | 3.5895 | 3.8113
2022-01-25 22:00 | 2.3625 | 2.6295 | 2.6762 | 2.7334 | 2.8 | 1.765 | 2.1515 | 2.1879 | 2.2376 | 1.765 | 2.3625 | 2.6901 | 2.7228 | 2.7663 | 2.9481
2022-01-25 23:00 | 2.1148 | 2.3575 | 2.4011 | 2.4546 | 2.5169 | 1.5623 | 1.9077 | 1.9418 | 1.9882 | 1.5623 | 2.0005 | 2.2836 | 2.3142 | 2.3548 | 2.5134
2022-01-26 | 2.0005 | 2.2262 | 2.2656 | 2.3137 | 2.3699 | 1.3527 | 1.654 | 1.6847 | 1.7266 | 1.3527 | 1.604 | 1.8371 | 1.8646 | 1.9012 | 2.0332
2022-01-26 01:00 | 1.7909 | 1.9916 | 2.0261 | 2.0684 | 2.1176 | 1.1813 | 1.4446 | 1.4715 | 1.5082 | 1.1813 | 1.5814 | 1.8052 | 1.8293 | 1.8615 | 1.9868
2022-01-26 02:00 | 1.6957 | 1.8797 | 1.9093 | 1.9456 | 1.9879 | 1.105 | 1.3476 | 1.3707 | 1.4022 | 1.105 | 1.4099 | 1.6078 | 1.6286 | 1.6561 | 1.7666
2022-01-26 03:00 | 1.6385 | 1.8062 | 1.8297 | 1.8584 | 1.8918 | 1.0378 | 1.2593 | 1.2776 | 1.3026 | 1.0378 | 1.2956 | 1.4722 | 1.4887 | 1.5105 | 1.6078
2022-01-26 04:00 | 1.6065 | 1.76 | 1.7774 | 1.7987 | 1.8236 | 1.0044 | 1.2113 | 1.2249 | 1.2434 | 1.0044 | 1.448 | 1.6332 | 1.6454 | 1.6616 | 1.7606
2022-01-26 05:00 | 1.6576 | 1.8048 | 1.8171 | 1.8321 | 1.8496 | 1.0288 | 1.2329 | 1.2424 | 1.2555 | 1.0288 | 1.5433 | 1.732 | 1.7405 | 1.752 | 1.8504
2022-01-26 06:00 | 1.6576 | 1.8008 | 1.8111 | 1.8236 | 1.8382 | 1.0479 | 1.2525 | 1.2605 | 1.2714 | 1.0479 | 1.2384 | 1.3904 | 1.3976 | 1.4071 | 1.4866
2022-01-26 07:00 | 1.6957 | 1.8451 | 1.857 | 1.8716 | 1.8887 | 1.1152 | 1.3344 | 1.3437 | 1.3565 | 1.1152 | 1.2575 | 1.4139 | 1.4223 | 1.4334 | 1.5158
2022-01-26 08:00 | 1.7338 | 1.8951 | 1.9117 | 1.932 | 1.9557 | 1.1241 | 1.3515 | 1.3645 | 1.3821 | 1.1241 | 1.2003 | 1.3568 | 1.3685 | 1.3839 | 1.4683
2022-01-26 09:00 | 1.8862 | 2.0722 | 2.0956 | 2.1243 | 2.1577 | 1.2575 | 1.5188 | 1.537 | 1.562 | 1.2575 | 1.3908 | 1.578 | 1.5944 | 1.6162 | 1.7187
2022-01-26 10:00 | 1.8672 | 2.066 | 2.0967 | 2.1342 | 2.178 | 1.1714 | 1.4274 | 1.4513 | 1.484 | 1.1714 | 1.467 | 1.6728 | 1.6943 | 1.7229 | 1.8377
2022-01-26 11:00 | 1.8481 | 2.0565 | 2.0927 | 2.1371 | 2.1889 | 1.105 | 1.357 | 1.3853 | 1.4239 | 1.105 | 1.105 | 1.2783 | 1.3037 | 1.3375 | 1.4386
2022-01-26 12:00 | 1.8481 | 2.0608 | 2.0993 | 2.1464 | 2.2013 | 1.0479 | 1.2927 | 1.3227 | 1.3637 | 1.0479 | 0.93358 | 1.0908 | 1.1178 | 1.1536 | 1.2478
2022-01-26 13:00 | 1.8481 | 2.0598 | 2.0977 | 2.1442 | 2.1983 | 1.0669 | 1.3144 | 1.344 | 1.3844 | 1.0669 | 0.81926 | 0.96303 | 0.98962 | 1.0249 | 1.1122
2022-01-26 14:00 | 1.829 | 2.0343 | 2.0697 | 2.113 | 2.1636 | 0.99731 | 1.2285 | 1.2561 | 1.2938 | 0.99731 | 1.105 | 1.2771 | 1.3019 | 1.3348 | 1.435
2022-01-26 15:00 | 1.9624 | 2.1722 | 2.2048 | 2.2448 | 2.2914 | 1.1813 | 1.4419 | 1.4673 | 1.5021 | 1.1813 | 0.89547 | 1.0404 | 1.0632 | 1.0936 | 1.1792
2022-01-26 16:00 | 2.0958 | 2.3119 | 2.3427 | 2.3804 | 2.4244 | 1.3337 | 1.6193 | 1.6434 | 1.6762 | 1.3337 | 0.89547 | 1.0378 | 1.0594 | 1.0881 | 1.1716
2022-01-26 17:00 | 2.7436 | 3.007 | 3.0373 | 3.0745 | 3.1178 | 1.8776 | 2.2613 | 2.285 | 2.3173 | 1.8776 | 2.553 | 2.8792 | 2.9005 | 2.9287 | 3.1029
2022-01-26 18:00 | 2.6102 | 2.8672 | 2.8994 | 2.9388 | 2.9847 | 2.0386 | 2.4541 | 2.4792 | 2.5135 | 2.0386 | 2.8579 | 3.2205 | 3.243 | 3.273 | 3.4659
2022-01-26 19:00 | 2.7055 | 2.9769 | 3.0129 | 3.0569 | 3.1081 | 2.0958 | 2.527 | 2.555 | 2.5933 | 2.0958 | 3.0675 | 3.4586 | 3.4837 | 3.5172 | 3.7258
2022-01-26 20:00 | 2.534 | 2.8025 | 2.8434 | 2.8935 | 2.9519 | 1.9265 | 2.3341 | 2.366 | 2.4095 | 1.9265 | 2.7626 | 3.1267 | 3.1554 | 3.1935 | 3.3909
2022-01-26 21:00 | 2.4387 | 2.7098 | 2.7557 | 2.8118 | 2.8772 | 1.829 | 2.226 | 2.2617 | 2.3106 | 1.829 | 3.2389 | 3.6629 | 3.695 | 3.7377 | 3.9668
2022-01-26 22:00 | 2.3054 | 2.5681 | 2.6148 | 2.672 | 2.7386 | 1.673 | 2.0428 | 2.0793 | 2.129 | 1.673 | 2.3625 | 2.6901 | 2.7228 | 2.7663 | 2.9481
2022-01-26 23:00 | 2.0147 | 2.2499 | 2.2935 | 2.3469 | 2.4092 | 1.4169 | 1.7359 | 1.7699 | 1.8164 | 1.4169 | 1.7909 | 2.0507 | 2.0813 | 2.1219 | 2.269
2022-01-27 | 1.834 | 2.0473 | 2.0867 | 2.1348 | 2.1909 | 1.2384 | 1.5189 | 1.5496 | 1.5915 | 1.2384 | 1.8672 | 2.1294 | 2.157 | 2.1936 | 2.34
2022-01-27 01:00 | 1.7147 | 1.9098 | 1.9443 | 1.9865 | 2.0358 | 1.0892 | 1.3358 | 1.3627 | 1.3995 | 1.0892 | 1.3146 | 1.5087 | 1.5329 | 1.565 | 1.6757
2022-01-27 02:00 | 1.6385 | 1.8183 | 1.8479 | 1.8842 | 1.9264 | 1.0187 | 1.2456 | 1.2687 | 1.3002 | 1.0187 | 1.3908 | 1.5866 | 1.6074 | 1.635 | 1.7444
2022-01-27 03:00 | 1.6195 | 1.7858 | 1.8092 | 1.8379 | 1.8714 | 0.97535 | 1.1856 | 1.2039 | 1.2288 | 0.97535 | 1.4099 | 1.5993 | 1.6157 | 1.6375 | 1.7411
2022-01-27 04:00 | 1.6195 | 1.7739 | 1.7913 | 1.8127 | 1.8375 | 0.97168 | 1.1727 | 1.1862 | 1.2048 | 0.97168 | 1.448 | 1.6332 | 1.6454 | 1.6616 | 1.7606
2022-01-27 05:00 | 1.6766 | 1.8253 | 1.8375 | 1.8525 | 1.87 | 1.086 | 1.3004 | 1.3099 | 1.323 | 1.086 | 1.2575 | 1.4144 | 1.423 | 1.4344 | 1.5172
2022-01-27 06:00 | 1.6957 | 1.8418 | 1.852 | 1.8645 | 1.8791 | 1.1622 | 1.3875 | 1.3955 | 1.4064 | 1.1622 | 1.5242 | 1.708 | 1.7151 | 1.7247 | 1.8198
2022-01-27 07:00 | 1.9243 | 2.0907 | 2.1027 | 2.1173 | 2.1343 | 1.1702 | 1.3994 | 1.4088 | 1.4215 | 1.1702 | 1.2765 | 1.4351 | 1.4435 | 1.4546 | 1.538
2022-01-27 08:00 | 1.9243 | 2.0998 | 2.1164 | 2.1367 | 2.1604 | 1.2194 | 1.4641 | 1.477 | 1.4947 | 1.2194 | 1.2194 | 1.378 | 1.3896 | 1.4051 | 1.4906
2022-01-27 09:00 | 1.81 | 1.9904 | 2.0138 | 2.0424 | 2.0758 | 0.85737 | 1.0461 | 1.0644 | 1.0893 | 0.85737 | 1.0669 | 1.2181 | 1.2345 | 1.2563 | 1.341
2022-01-27 10:00 | 1.829 | 2.0251 | 2.0557 | 2.0933 | 2.1371 | 0.64779 | 0.80888 | 0.83281 | 0.86548 | 0.64779 | 1.3146 | 1.5034 | 1.5249 | 1.5535 | 1.6599
2022-01-27 11:00 | 1.7147 | 1.9132 | 1.9495 | 1.9938 | 2.0456 | 0.68589 | 0.86185 | 0.89013 | 0.92875 | 0.68589 | 1.5052 | 1.7229 | 1.7483 | 1.7821 | 1.9052
2022-01-27 12:00 | 2.0767 | 2.3064 | 2.3449 | 2.392 | 2.447 | 0.87642 | 1.0901 | 1.1201 | 1.1611 | 0.87642 | 1.3527 | 1.5566 | 1.5836 | 1.6194 | 1.7366
2022-01-27 13:00 | 2.4768 | 2.7352 | 2.7732 | 2.8196 | 2.8738 | 1.0798 | 1.3296 | 1.3592 | 1.3996 | 1.0798 | 1.2003 | 1.3865 | 1.4131 | 1.4484 | 1.5566
2022-01-27 14:00 | 2.099 | 2.3244 | 2.3598 | 2.4031 | 2.4536 | 1.1432 | 1.4008 | 1.4284 | 1.4661 | 1.1432 | 0.97168 | 1.1289 | 1.1537 | 1.1866 | 1.2795
2022-01-27 15:00 | 2.7055 | 2.9705 | 3.0031 | 3.0431 | 3.0896 | 1.5242 | 1.847 | 1.8725 | 1.9072 | 1.5242 | 1.3337 | 1.5273 | 1.5502 | 1.5806 | 1.6902
2022-01-27 16:00 | 2.915 | 3.1921 | 3.2229 | 3.2606 | 3.3045 | 1.7338 | 2.092 | 2.116 | 2.1488 | 1.7338 | 1.6195 | 1.8424 | 1.8639 | 1.8926 | 2.0159
2022-01-27 17:00 | 2.9722 | 3.2526 | 3.283 | 3.3201 | 3.3635 | 2.0767 | 2.4965 | 2.5202 | 2.5526 | 2.0767 | 2.8579 | 3.2179 | 3.2392 | 3.2675 | 3.4584
2022-01-27 18:00 | 2.947 | 3.229 | 3.2612 | 3.3006 | 3.3465 | 2.1452 | 2.58 | 2.6051 | 2.6394 | 2.1452 | 2.915 | 3.284 | 3.3065 | 3.3365 | 3.5325
2022-01-27 19:00 | 2.9531 | 3.243 | 3.279 | 3.3229 | 3.3742 | 2.2673 | 2.7295 | 2.7576 | 2.7958 | 2.2673 | 3.4295 | 3.8608 | 3.886 | 3.9195 | 4.148
2022-01-27 20:00 | 2.7245 | 3.0072 | 3.0481 | 3.0982 | 3.1566 | 2.1148 | 2.5566 | 2.5885 | 2.632 | 2.1148 | 3.0294 | 3.4231 | 3.4518 | 3.4899 | 3.702
2022-01-27 21:00 | 2.6102 | 2.894 | 2.9399 | 2.996 | 3.0614 | 2.0196 | 2.451 | 2.4868 | 2.5356 | 2.0196 | 2.7245 | 3.0912 | 3.1234 | 3.1661 | 3.3669
2022-01-27 22:00 | 2.4788 | 2.7545 | 2.8011 | 2.8583 | 2.9249 | 1.8436 | 2.2443 | 2.2808 | 2.3305 | 1.8436 | 2.9913 | 3.3888 | 3.4215 | 3.465 | 3.6814
2022-01-27 23:00 | 2.162 | 2.4082 | 2.4518 | 2.5053 | 2.5676 | 1.4791 | 1.8094 | 1.8435 | 1.89 | 1.4791 | 2.1529 | 2.453 | 2.4836 | 2.5242 | 2.6912
2022-01-28 | 2.0005 | 2.2262 | 2.2656 | 2.3137 | 2.3699 | 1.2956 | 1.5865 | 1.6171 | 1.659 | 1.2956 | 1.7528 | 2.0024 | 2.03 | 2.0666 | 2.2067
2022-01-28 01:00 | 1.8481 | 2.053 | 2.0875 | 2.1298 | 2.179 | 1.1503 | 1.408 | 1.4349 | 1.4717 | 1.1503 | 1.5242 | 1.7416 | 1.7658 | 1.7979 | 1.9201
2022-01-28 02:00 | 1.739 | 1.9263 | 1.9559 | 1.9921 | 2.0344 | 1.0754 | 1.3126 | 1.3357 | 1.3672 | 1.0754 | 1.5433 | 1.756 | 1.7768 | 1.8044 | 1.9222
2022-01-28 03:00 | 1.6957 | 1.8676 | 1.8911 | 1.9198 | 1.9532 | 1.0288 | 1.2488 | 1.2671 | 1.292 | 1.0288 | 1.4099 | 1.5993 | 1.6157 | 1.6375 | 1.7411
2022-01-28 04:00 | 1.6957 | 1.8558 | 1.8732 | 1.8945 | 1.9194 | 1.0098 | 1.2177 | 1.2312 | 1.2498 | 1.0098 | 1.3908 | 1.5697 | 1.5819 | 1.5981 | 1.694
2022-01-28 05:00 | 1.7719 | 1.9276 | 1.9399 | 1.9549 | 1.9724 | 1.0652 | 1.2758 | 1.2854 | 1.2984 | 1.0652 | 1.3527 | 1.5202 | 1.5288 | 1.5402 | 1.6282
2022-01-28 06:00 | 1.81 | 1.9646 | 1.9748 | 1.9873 | 2.0019 | 1.1622 | 1.3875 | 1.3955 | 1.4064 | 1.1622 | 1.3337 | 1.4962 | 1.5034 | 1.5129 | 1.5977
2022-01-28 07:00 | 2.1339 | 2.3159 | 2.3278 | 2.3424 | 2.3595 | 1.2765 | 1.525 | 1.5343 | 1.547 | 1.2765 | 1.448 | 1.6256 | 1.634 | 1.6451 | 1.738
2022-01-28 08:00 | 2.2482 | 2.4478 | 2.4644 | 2.4847 | 2.5083 | 1.3908 | 1.6666 | 1.6796 | 1.6972 | 1.3908 | 1.4861 | 1.6744 | 1.686 | 1.7015 | 1.8016
2022-01-28 09:00 | 2.4959 | 2.7272 | 2.7506 | 2.7793 | 2.8127 | 1.5052 | 1.8114 | 1.8296 | 1.8546 | 1.5052 | 1.5623 | 1.7686 | 1.785 | 1.8068 | 1.9187
2022-01-28 10:00 | 2.4959 | 2.7415 | 2.7722 | 2.8097 | 2.8535 | 1.5052 | 1.8217 | 1.8457 | 1.8783 | 1.5052 | 1.5242 | 1.7363 | 1.7578 | 1.7864 | 1.9043
2022-01-28 11:00 | 2.5911 | 2.8548 | 2.891 | 2.9354 | 2.9872 | 1.448 | 1.7622 | 1.7904 | 1.8291 | 1.448 | 1.467 | 1.6806 | 1.706 | 1.7397 | 1.8607
2022-01-28 12:00 | 2.7055 | 2.9819 | 3.0204 | 3.0675 | 3.1224 | 1.5433 | 1.8779 | 1.9079 | 1.9489 | 1.5433 | 1.8862 | 2.1494 | 2.1764 | 2.2122 | 2.3587
2022-01-28 13:00 | 2.2482 | 2.4896 | 2.5276 | 2.574 | 2.6282 | 1.1622 | 1.4269 | 1.4565 | 1.4969 | 1.1622 | 0.83831 | 0.98421 | 1.0108 | 1.0461 | 1.1344
2022-01-28 14:00 | 2.3625 | 2.6074 | 2.6428 | 2.6862 | 2.7367 | 1.1432 | 1.4008 | 1.4284 | 1.4661 | 1.1432 | 1.105 | 1.2771 | 1.3019 | 1.3348 | 1.435
2022-01-28 15:00 | 2.6864 | 2.95 | 2.9826 | 3.0226 | 3.0692 | 1.2194 | 1.4869 | 1.5124 | 1.5471 | 1.2194 | 1.2384 | 1.4215 | 1.4443 | 1.4747 | 1.5791
2022-01-28 16:00 | 2.7055 | 2.9669 | 2.9977 | 3.0354 | 3.0794 | 1.5517 | 1.8769 | 1.9009 | 1.9337 | 1.5517 | 1.2194 | 1.3977 | 1.4193 | 1.448 | 1.5493
2022-01-28 17:00 | 2.915 | 3.1912 | 3.2216 | 3.2587 | 3.3021 | 1.9053 | 2.294 | 2.3176 | 2.35 | 1.9053 | 2.553 | 2.8792 | 2.9005 | 2.9287 | 3.1029
2022-01-28 18:00 | 3.0865 | 3.379 | 3.4111 | 3.4505 | 3.4964 | 2.3435 | 2.8142 | 2.8393 | 2.8736 | 2.3435 | 2.9341 | 3.3052 | 3.3277 | 3.3576 | 3.5548
2022-01-28 19:00 | 3.0103 | 3.3044 | 3.3404 | 3.3844 | 3.4356 | 2.4768 | 2.9771 | 3.0051 | 3.0434 | 2.4768 | 3.3533 | 3.7762 | 3.8013 | 3.8348 | 4.0591
2022-01-28 20:00 | 2.9913 | 3.2937 | 3.3346 | 3.3847 | 3.4431 | 2.3054 | 2.7816 | 2.8135 | 2.8571 | 2.3054 | 3.2199 | 3.6349 | 3.6635 | 3.7016 | 3.9242
2022-01-28 21:00 | 2.8769 | 3.1806 | 3.2264 | 3.2826 | 3.348 | 2.2291 | 2.6986 | 2.7344 | 2.7832 | 2.2291 | 3.2199 | 3.6417 | 3.6738 | 3.7165 | 3.9446
2022-01-28 22:00 | 2.6003 | 2.885 | 2.9317 | 2.9888 | 3.0554 | 1.9867 | 2.4134 | 2.4498 | 2.4996 | 1.9867 | 2.9531 | 3.3465 | 3.3792 | 3.4226 | 3.637
2022-01-28 23:00 | 2.4768 | 2.7464 | 2.7901 | 2.8435 | 2.9058 | 1.7469 | 2.1258 | 2.1599 | 2.2064 | 1.7469 | 2.915 | 3.2999 | 3.3305 | 3.3711 | 3.5799
2022-01-29 | 2.2053 | 2.4463 | 2.4856 | 2.5338 | 2.5899 | 1.5433 | 1.8791 | 1.9097 | 1.9516 | 1.5433 | 2.172 | 2.4682 | 2.4957 | 2.5324 | 2.6956
2022-01-29 01:00 | 2.0196 | 2.2373 | 2.2718 | 2.314 | 2.3633 | 1.2913 | 1.5746 | 1.6015 | 1.6383 | 1.2913 | 1.6385 | 1.8687 | 1.8928 | 1.925 | 2.0535
2022-01-29 02:00 | 1.8915 | 2.0901 | 2.1198 | 2.156 | 2.1983 | 1.2003 | 1.4601 | 1.4832 | 1.5148 | 1.2003 | 1.7147 | 1.9466 | 1.9673 | 1.9949 | 2.1221
2022-01-29 03:00 | 1.829 | 2.0109 | 2.0344 | 2.0631 | 2.0965 | 1.1241 | 1.3613 | 1.3796 | 1.4046 | 1.1241 | 1.3908 | 1.5781 | 1.5945 | 1.6163 | 1.7189
2022-01-29 04:00 | 1.81 | 1.9786 | 1.996 | 2.0173 | 2.0422 | 1.0755 | 1.2953 | 1.3089 | 1.3275 | 1.0755 | 1.4099 | 1.5909 | 1.6031 | 1.6193 | 1.7162
2022-01-29 05:00 | 1.8481 | 2.0095 | 2.0218 | 2.0368 | 2.0543 | 1.1241 | 1.3454 | 1.355 | 1.368 | 1.1241 | 1.3908 | 1.5626 | 1.5712 | 1.5826 | 1.6727
2022-01-29 06:00 | 1.8481 | 2.0055 | 2.0158 | 2.0283 | 2.0429 | 1.1241 | 1.3425 | 1.3505 | 1.3614 | 1.1241 | 1.3527 | 1.5174 | 1.5246 | 1.5341 | 1.6199
2022-01-29 07:00 | 1.8619 | 2.0237 | 2.0357 | 2.0503 | 2.0673 | 1.2003 | 1.435 | 1.4443 | 1.457 | 1.2003 | 1.4099 | 1.5833 | 1.5917 | 1.6028 | 1.6936
2022-01-29 08:00 | 1.9624 | 2.1408 | 2.1573 | 2.1776 | 2.2013 | 1.2384 | 1.4866 | 1.4995 | 1.5172 | 1.2384 | 1.6195 | 1.8226 | 1.8343 | 1.8497 | 1.9572
2022-01-29 09:00 | 2.1148 | 2.3179 | 2.3413 | 2.3699 | 2.4033 | 1.3337 | 1.6088 | 1.6271 | 1.652 | 1.3337 | 1.467 | 1.6627 | 1.6791 | 1.7009 | 1.8076
2022-01-29 10:00 | 2.2101 | 2.4344 | 2.4651 | 2.5027 | 2.5464 | 1.3908 | 1.6867 | 1.7106 | 1.7433 | 1.3908 | 1.5052 | 1.7152 | 1.7366 | 1.7652 | 1.8821
2022-01-29 11:00 | 2.3435 | 2.5887 | 2.6249 | 2.6693 | 2.7211 | 1.5814 | 1.9197 | 1.948 | 1.9866 | 1.5814 | 1.2956 | 1.49 | 1.5154 | 1.5492 | 1.6608
2022-01-29 12:00 | 2.5721 | 2.8386 | 2.8771 | 2.9242 | 2.9792 | 1.9434 | 2.3505 | 2.3805 | 2.4215 | 1.9434 | 2.3054 | 2.6152 | 2.6422 | 2.678 | 2.8476
2022-01-29 13:00 | 2.5149 | 2.7762 | 2.8141 | 2.8606 | 2.9147 | 1.8862 | 2.2822 | 2.3118 | 2.3522 | 1.8862 | 2.553 | 2.8897 | 2.9163 | 2.9516 | 3.1342
2022-01-29 14:00 | 2.4387 | 2.6893 | 2.7247 | 2.768 | 2.8186 | 1.829 | 2.2111 | 2.2387 | 2.2764 | 1.829 | 2.534 | 2.865 | 2.8898 | 2.9228 | 3.1015
2022-01-29 15:00 | 2.3625 | 2.602 | 2.6347 | 2.6746 | 2.7212 | 1.7147 | 2.0721 | 2.0976 | 2.1323 | 1.7147 | 2.1148 | 2.3954 | 2.4182 | 2.4486 | 2.6012
2022-01-29 16:00 | 2.3244 | 2.5575 | 2.5883 | 2.626 | 2.67 | 1.6766 | 2.0245 | 2.0485 | 2.0813 | 1.6766 | 2.2101 | 2.4987 | 2.5203 | 2.549 | 2.7047
2022-01-29 17:00 | 2.3816 | 2.6181 | 2.6484 | 2.6856 | 2.7289 | 1.7909 | 2.1589 | 2.1826 | 2.2149 | 1.7909 | 2.191 | 2.4769 | 2.4982 | 2.5265 | 2.6807
2022-01-29 18:00 | 2.3625 | 2.6011 | 2.6333 | 2.6727 | 2.7186 | 1.819 | 2.1947 | 2.2198 | 2.2541 | 1.819 | 2.7626 | 3.1146 | 3.1371 | 3.1671 | 3.3548
2022-01-29 19:00 | 2.3816 | 2.629 | 2.6649 | 2.7089 | 2.7602 | 1.8862 | 2.2794 | 2.3074 | 2.3457 | 1.8862 | 2.3816 | 2.6964 | 2.7215 | 2.755 | 2.9259
2022-01-29 20:00 | 2.534 | 2.8025 | 2.8434 | 2.8935 | 2.9519 | 1.8672 | 2.2639 | 2.2959 | 2.3394 | 1.8672 | 2.9913 | 3.3808 | 3.4095 | 3.4475 | 3.6575
2022-01-29 21:00 | 2.5104 | 2.7868 | 2.8327 | 2.8888 | 2.9543 | 1.7719 | 2.1584 | 2.1942 | 2.243 | 1.7719 | 2.7245 | 3.0912 | 3.1234 | 3.1661 | 3.3669
2022-01-29 22:00 | 2.3504 | 2.6165 | 2.6632 | 2.7204 | 2.787 | 1.6751 | 2.0453 | 2.0817 | 2.1314 | 1.6751 | 2.191 | 2.4996 | 2.5323 | 2.5757 | 2.7482
2022-01-29 23:00 | 2.2383 | 2.4901 | 2.5338 | 2.5872 | 2.6495 | 1.4861 | 1.8177 | 1.8517 | 1.8982 | 1.4861 | 1.8862 | 2.1566 | 2.1872 | 2.2278 | 2.3801
2022-01-30 | 2.1529 | 2.39 | 2.4293 | 2.4775 | 2.5336 | 1.3597 | 1.6622 | 1.6929 | 1.7348 | 1.3597 | 1.7909 | 2.0447 | 2.0723 | 2.1089 | 2.2512
2022-01-30 01:00 | 1.9434 | 2.1554 | 2.1899 | 2.2321 | 2.2814 | 1.1943 | 1.46 | 1.4869 | 1.5237 | 1.1943 | 1.448 | 1.6569 | 1.6811 | 1.7133 | 1.8313
2022-01-30 02:00 | 1.8207 | 2.0141 | 2.0437 | 2.0799 | 2.1222 | 1.0923 | 1.3325 | 1.3556 | 1.3871 | 1.0923 | 1.5623 | 1.7772 | 1.798 | 1.8255 | 1.9444
2022-01-30 03:00 | 1.7719 | 1.9495 | 1.973 | 2.0017 | 2.0351 | 1.0339 | 1.2548 | 1.2731 | 1.298 | 1.0339 | 1.4099 | 1.5993 | 1.6157 | 1.6375 | 1.7411
2022-01-30 04:00 | 1.7719 | 1.9377 | 1.9551 | 1.9764 | 2.0013 | 1.0129 | 1.2213 | 1.2349 | 1.2534 | 1.0129 | 1.4289 | 1.6121 | 1.6243 | 1.6405 | 1.7384
2022-01-30 05:00 | 1.7719 | 1.9276 | 1.9399 | 1.9549 | 1.9724 | 1.0288 | 1.2329 | 1.2424 | 1.2555 | 1.0288 | 1.2575 | 1.4144 | 1.423 | 1.4344 | 1.5172
2022-01-30 06:00 | 1.829 | 1.9851 | 1.9953 | 2.0078 | 2.0224 | 1.0894 | 1.3015 | 1.3095 | 1.3204 | 1.0894 | 1.3718 | 1.5386 | 1.5458 | 1.5553 | 1.6421
2022-01-30 07:00 | 1.829 | 1.9884 | 2.0003 | 2.0149 | 2.032 | 1.1622 | 1.3899 | 1.3993 | 1.412 | 1.1622 | 1.3527 | 1.5198 | 1.5281 | 1.5393 | 1.6269
2022-01-30 08:00 | 1.8672 | 2.0384 | 2.055 | 2.0753 | 2.0989 | 1.3337 | 1.5991 | 1.6121 | 1.6297 | 1.3337 | 1.3146 | 1.4839 | 1.4955 | 1.5109 | 1.6017
2022-01-30 09:00 | 1.7528 | 1.9289 | 1.9523 | 1.981 | 2.0144 | 1.2446 | 1.5035 | 1.5218 | 1.5467 | 1.2446 | 1.467 | 1.6627 | 1.6791 | 1.7009 | 1.8076
2022-01-30 10:00 | 1.6195 | 1.7999 | 1.8306 | 1.8681 | 1.9119 | 1.0799 | 1.3193 | 1.3433 | 1.3759 | 1.0799 | 0.83113 | 0.96614 | 0.98763 | 1.0162 | 1.096
2022-01-30 11:00 | 1.7719 | 1.9746 | 2.0109 | 2.0553 | 2.107 | 1.1622 | 1.4245 | 1.4528 | 1.4915 | 1.1622 | 1.105 | 1.2783 | 1.3037 | 1.3375 | 1.4386
2022-01-30 12:00 | 1.9815 | 2.2041 | 2.2426 | 2.2897 | 2.3446 | 1.2765 | 1.5627 | 1.5928 | 1.6337 | 1.2765 | 0.97168 | 1.1332 | 1.1601 | 1.1959 | 1.2922
2022-01-30 13:00 | 1.9434 | 2.1621 | 2.2001 | 2.2465 | 2.3007 | 1.5052 | 1.8321 | 1.8617 | 1.9021 | 1.5052 | 1.2003 | 1.3865 | 1.4131 | 1.4484 | 1.5566
2022-01-30 14:00 | 1.9434 | 2.1571 | 2.1925 | 2.2359 | 2.2864 | 1.2956 | 1.5809 | 1.6085 | 1.6462 | 1.2956 | 1.0098 | 1.1712 | 1.196 | 1.229 | 1.3239
2022-01-30 15:00 | 2.553 | 2.8067 | 2.8394 | 2.8793 | 2.9259 | 1.6576 | 2.0046 | 2.03 | 2.0648 | 1.6576 | 1.0479 | 1.2097 | 1.2326 | 1.263 | 1.3569
2022-01-30 16:00 | 2.7245 | 2.9874 | 3.0182 | 3.0559 | 3.0998 | 1.9624 | 2.3621 | 2.3861 | 2.4189 | 1.9624 | 2.4578 | 2.7739 | 2.7955 | 2.8242 | 2.9936
2022-01-30 17:00 | 2.8388 | 3.1093 | 3.1397 | 3.1768 | 3.2202 | 2.2482 | 2.6991 | 2.7228 | 2.7551 | 2.2482 | 3.0675 | 3.4508 | 3.4721 | 3.5004 | 3.7028
2022-01-30 18:00 | 2.8388 | 3.1129 | 3.145 | 3.1844 | 3.2303 | 2.2291 | 2.6792 | 2.7043 | 2.7385 | 2.2291 | 3.2008 | 3.6016 | 3.6241 | 3.6541 | 3.8658
2022-01-30 19:00 | 2.8198 | 3.0997 | 3.1357 | 3.1797 | 3.231 | 2.191 | 2.6395 | 2.6675 | 2.7058 | 2.191 | 3.0675 | 3.4586 | 3.4837 | 3.5172 | 3.7258
2022-01-30 20:00 | 2.7626 | 3.0481 | 3.089 | 3.1391 | 3.1975 | 2.191 | 2.6466 | 2.6785 | 2.7221 | 2.191 | 3.2961 | 3.7195 | 3.7482 | 3.7863 | 4.0131
2022-01-30 21:00 | 2.6102 | 2.894 | 2.9399 | 2.996 | 3.0614 | 2.1148 | 2.5636 | 2.5993 | 2.6482 | 2.1148 | 2.8579 | 3.2394 | 3.2716 | 3.3143 | 3.5224
2022-01-30 22:00 | 2.4578 | 2.7319 | 2.7786 | 2.8357 | 2.9024 | 1.829 | 2.2271 | 2.2636 | 2.3133 | 1.829 | 2.4006 | 2.7325 | 2.7652 | 2.8086 | 2.9926
2022-01-30 23:00 | 2.2496 | 2.5023 | 2.5459 | 2.5993 | 2.6616 | 1.5603 | 1.9053 | 1.9394 | 1.9859 | 1.5603 | 1.9815 | 2.2624 | 2.293 | 2.3337 | 2.4912
2022-01-31 | 2.0577 | 2.2876 | 2.327 | 2.3751 | 2.4313 | 1.3572 | 1.6592 | 1.6899 | 1.7318 | 1.3572 | 1.829 | 2.0871 | 2.1146 | 2.1513 | 2.2956
2022-01-31 01:00 | 1.8893 | 2.0973 | 2.1318 | 2.174 | 2.2233 | 1.2384 | 1.5121 | 1.539 | 1.5757 | 1.2384 | 1.5242 | 1.7416 | 1.7658 | 1.7979 | 1.9201
2022-01-31 02:00 | 1.7719 | 1.9616 | 1.9912 | 2.0275 | 2.0697 | 1.1 | 1.3416 | 1.3647 | 1.3963 | 1.1 | 1.4861 | 1.6925 | 1.7133 | 1.7408 | 1.8555
2022-01-31 03:00 | 1.7528 | 1.929 | 1.9525 | 1.9812 | 2.0147 | 1.0479 | 1.2713 | 1.2896 | 1.3145 | 1.0479 | 1.3337 | 1.5146 | 1.531 | 1.5528 | 1.6523
2022-01-31 04:00 | 1.8672 | 2.04 | 2.0574 | 2.0788 | 2.1036 | 1.0414 | 1.2551 | 1.2686 | 1.2872 | 1.0414 | 1.3718 | 1.5485 | 1.5607 | 1.5769 | 1.6717
2022-01-31 05:00 | 1.9053 | 2.0709 | 2.0832 | 2.0982 | 2.1157 | 1.1464 | 1.3718 | 1.3813 | 1.3944 | 1.1464 | 1.5052 | 1.6896 | 1.6982 | 1.7096 | 1.806
2022-01-31 06:00 | 1.8862 | 2.0465 | 2.0567 | 2.0692 | 2.0838 | 1.2765 | 1.5226 | 1.5306 | 1.5415 | 1.2765 | 1.4099 | 1.5809 | 1.5881 | 1.5976 | 1.6865
2022-01-31 07:00 | 2.172 | 2.3568 | 2.3688 | 2.3834 | 2.4004 | 1.4184 | 1.6926 | 1.7019 | 1.7146 | 1.4184 | 1.467 | 1.6468 | 1.6552 | 1.6663 | 1.7602
2022-01-31 08:00 | 2.2482 | 2.4478 | 2.4644 | 2.4847 | 2.5083 | 1.448 | 1.7342 | 1.7471 | 1.7648 | 1.448 | 1.467 | 1.6533 | 1.6649 | 1.6803 | 1.7794
2022-01-31 09:00 | 2.4197 | 2.6454 | 2.6688 | 2.6974 | 2.7308 | 1.4099 | 1.6989 | 1.7171 | 1.742 | 1.4099 | 0.78115 | 0.90051 | 0.91691 | 0.93869 | 1.0077
2022-01-31 10:00 | 2.534 | 2.7824 | 2.8131 | 2.8506 | 2.8944 | 1.211 | 1.4742 | 1.4982 | 1.5308 | 1.211 | 1.2384 | 1.4187 | 1.4402 | 1.4688 | 1.571
2022-01-31 11:00 | 2.4006 | 2.6501 | 2.6863 | 2.7307 | 2.7825 | 1.2194 | 1.4921 | 1.5204 | 1.559 | 1.2194 | 1.0098 | 1.1724 | 1.1978 | 1.2316 | 1.3275
2022-01-31 12:00 | 2.553 | 2.8182 | 2.8567 | 2.9038 | 2.9587 | 1.2765 | 1.5627 | 1.5928 | 1.6337 | 1.2765 | 0.724 | 0.85792 | 0.88488 | 0.92071 | 1.0033
2022-01-31 13:00 | 2.5721 | 2.8376 | 2.8755 | 2.922 | 2.9761 | 1.4289 | 1.742 | 1.7716 | 1.8121 | 1.4289 | 0.68589 | 0.81483 | 0.84141 | 0.87674 | 0.95669
2022-01-31 14:00 | 3.3254 | 3.6419 | 3.6773 | 3.7207 | 3.7712 | 1.9815 | 2.3912 | 2.4188 | 2.4565 | 1.9815 | 2.2101 | 2.5051 | 2.5299 | 2.5628 | 2.7237
2022-01-31 15:00 | 3.3914 | 3.7074 | 3.74 | 3.7799 | 3.8265 | 2.172 | 2.6123 | 2.6378 | 2.6725 | 2.172 | 3.1818 | 3.581 | 3.6039 | 3.6343 | 3.8455
2022-01-31 16:00 | 2.903 | 3.1791 | 3.2099 | 3.2476 | 3.2916 | 1.8862 | 2.2721 | 2.2961 | 2.3289 | 1.8862 | 2.5721 | 2.901 | 2.9226 | 2.9512 | 3.1269
2022-01-31 17:00 | 2.7817 | 3.0479 | 3.0783 | 3.1154 | 3.1588 | 1.9304 | 2.3236 | 2.3473 | 2.3797 | 1.9304 | 2.534 | 2.858 | 2.8793 | 2.9076 | 3.0807
2022-01-31 18:00 | 3.0124 | 3.2993 | 3.3315 | 3.3709 | 3.4168 | 2.4387 | 2.9268 | 2.9519 | 2.9861 | 2.4387 | 3.5819 | 4.025 | 4.0475 | 4.0775 | 4.3102
2022-01-31 19:00 | 3.0294 | 3.3249 | 3.3608 | 3.4048 | 3.4561 | 2.4219 | 2.9122 | 2.9402 | 2.9785 | 2.4219 | 3.7152 | 4.1784 | 4.2036 | 4.2371 | 4.4813
2022-01-31 20:00 | 2.9341 | 3.2323 | 3.2732 | 3.3233 | 3.3817 | 2.289 | 2.7623 | 2.7942 | 2.8378 | 2.289 | 3.2199 | 3.6349 | 3.6635 | 3.7016 | 3.9242
2022-01-31 21:00 | 2.7626 | 3.0578 | 3.1036 | 3.1598 | 3.2252 | 2.217 | 2.6843 | 2.7201 | 2.7689 | 2.217 | 3.4104 | 3.8534 | 3.8856 | 3.9283 | 4.1668
2022-01-31 22:00 | 2.534 | 2.8138 | 2.8605 | 2.9176 | 2.9842 | 2.0099 | 2.4408 | 2.4772 | 2.5269 | 2.0099 | 2.896 | 3.2829 | 3.3156 | 3.3591 | 3.5703
2022-01-31 23:00 | 2.2343 | 2.4858 | 2.5295 | 2.5829 | 2.6452 | 1.5946 | 1.9458 | 1.9799 | 2.0264 | 1.5946 | 2.191 | 2.4953 | 2.5259 | 2.5666 | 2.7356
2022-02-01 | 2.0201 | 2.2472 | 2.2866 | 2.3347 | 2.3909 | 1.3972 | 1.7066 | 1.7372 | 1.7791 | 1.3972 | 2.0958 | 2.3835 | 2.4111 | 2.4477 | 2.6067
2022-02-01 01:00 | 1.8481 | 2.053 | 2.0875 | 2.1298 | 2.179 | 1.1928 | 1.4582 | 1.4851 | 1.5218 | 1.1928 | 1.5052 | 1.7205 | 1.7446 | 1.7768 | 1.8979
2022-02-01 02:00 | 1.7924 | 1.9836 | 2.0132 | 2.0495 | 2.0918 | 1.0989 | 1.3403 | 1.3634 | 1.3949 | 1.0989 | 1.5242 | 1.7349 | 1.7556 | 1.7832 | 1.8999
2022-02-01 03:00 | 1.7147 | 1.8881 | 1.9116 | 1.9403 | 1.9737 | 1.0591 | 1.2846 | 1.3028 | 1.3278 | 1.0591 | 1.467 | 1.6628 | 1.6792 | 1.701 | 1.8078
2022-02-01 04:00 | 1.7338 | 1.8968 | 1.9142 | 1.9355 | 1.9603 | 1.0479 | 1.2627 | 1.2763 | 1.2948 | 1.0479 | 1.3718 | 1.5485 | 1.5607 | 1.5769 | 1.6717
2022-02-01 05:00 | 1.7909 | 1.9481 | 1.9603 | 1.9753 | 1.9928 | 1.1367 | 1.3603 | 1.3699 | 1.383 | 1.1367 | 1.3527 | 1.5202 | 1.5288 | 1.5402 | 1.6282
2022-02-01 06:00 | 1.936 | 2.1 | 2.1102 | 2.1228 | 2.1374 | 1.3146 | 1.5676 | 1.5756 | 1.5865 | 1.3146 | 1.6004 | 1.7927 | 1.7998 | 1.8094 | 1.9087
2022-02-01 07:00 | 2.0872 | 2.2657 | 2.2777 | 2.2923 | 2.3093 | 1.4289 | 1.7051 | 1.7144 | 1.7271 | 1.4289 | 1.5433 | 1.7315 | 1.7399 | 1.751 | 1.8491
2022-02-01 08:00 | 2.191 | 2.3864 | 2.403 | 2.4233 | 2.4469 | 1.4289 | 1.7117 | 1.7246 | 1.7423 | 1.4289 | 1.3527 | 1.5262 | 1.5378 | 1.5533 | 1.6461
2022-02-01 09:00 | 2.3435 | 2.5635 | 2.5869 | 2.6155 | 2.6489 | 1.2194 | 1.4738 | 1.492 | 1.5169 | 1.2194 | 1.1432 | 1.3028 | 1.3192 | 1.341 | 1.4299
2022-02-01 10:00 | 1.9389 | 2.1431 | 2.1738 | 2.2113 | 2.2551 | 0.97168 | 1.1915 | 1.2154 | 1.2481 | 0.97168 | 1.3718 | 1.5669 | 1.5884 | 1.617 | 1.7266
2022-02-01 11:00 | 2.6483 | 2.9162 | 2.9524 | 2.9968 | 3.0486 | 1.2194 | 1.4921 | 1.5204 | 1.559 | 1.2194 | 1.3337 | 1.5324 | 1.5578 | 1.5915 | 1.7052
2022-02-01 12:00 | 2.896 | 3.1866 | 3.2251 | 3.2722 | 3.3271 | 1.2765 | 1.5627 | 1.5928 | 1.6337 | 1.2765 | 1.105 | 1.2814 | 1.3083 | 1.3442 | 1.4477
2022-02-01 13:00 | 2.8388 | 3.1242 | 3.1621 | 3.2085 | 3.2627 | 1.3718 | 1.6745 | 1.7041 | 1.7445 | 1.3718 | 0.95263 | 1.1112 | 1.1378 | 1.1732 | 1.2678
2022-02-01 14:00 | 2.9722 | 3.2625 | 3.2979 | 3.3412 | 3.3917 | 1.5623 | 1.896 | 1.9236 | 1.9613 | 1.5623 | 1.467 | 1.6794 | 1.7042 | 1.7371 | 1.8572
2022-02-01 15:00 | 3.2077 | 3.51 | 3.5427 | 3.5826 | 3.6292 | 1.7147 | 2.0721 | 2.0976 | 2.1323 | 1.7147 | 1.8638 | 2.1164 | 2.1393 | 2.1697 | 2.3085
2022-02-01 16:00 | 3.2961 | 3.6014 | 3.6322 | 3.6699 | 3.7139 | 2.0317 | 2.4439 | 2.4679 | 2.5007 | 2.0317 | 2.8198 | 3.1762 | 3.1978 | 3.2265 | 3.4158
2022-02-01 17:00 | 3.1627 | 3.4573 | 3.4877 | 3.5248 | 3.5682 | 2.2291 | 2.6766 | 2.7003 | 2.7326 | 2.2291 | 3.4866 | 3.9166 | 3.9379 | 3.9662 | 4.1917
2022-02-01 18:00 | 3.0865 | 3.379 | 3.4111 | 3.4505 | 3.4964 | 2.3435 | 2.8142 | 2.8393 | 2.8736 | 2.3435 | 3.1056 | 3.4957 | 3.5182 | 3.5482 | 3.7547
2022-02-01 19:00 | 3.0294 | 3.3249 | 3.3608 | 3.4048 | 3.4561 | 2.2482 | 2.707 | 2.735 | 2.7733 | 2.2482 | 3.2961 | 3.7126 | 3.7378 | 3.7713 | 3.9925
2022-02-01 20:00 | 2.8579 | 3.1504 | 3.1914 | 3.2414 | 3.2998 | 2.2291 | 2.6916 | 2.7235 | 2.7671 | 2.2291 | 2.915 | 3.2961 | 3.3248 | 3.3629 | 3.5687
2022-02-01 21:00 | 2.694 | 2.9841 | 3.0299 | 3.0861 | 3.1515 | 2.0104 | 2.4402 | 2.4759 | 2.5248 | 2.0104 | 3.3723 | 3.8111 | 3.8432 | 3.8859 | 4.1223
2022-02-01 22:00 | 2.4959 | 2.7728 | 2.8195 | 2.8767 | 2.9433 | 1.8481 | 2.2496 | 2.2861 | 2.3358 | 1.8481 | 2.6102 | 2.9654 | 2.9981 | 3.0415 | 3.237
2022-02-01 23:00 | 2.2004 | 2.4494 | 2.493 | 2.5464 | 2.6087 | 1.493 | 1.8258 | 1.8599 | 1.9064 | 1.493 | 2.0577 | 2.3471 | 2.3777 | 2.4184 | 2.5801
2022-02-02 | 2.0196 | 2.2467 | 2.286 | 2.3342 | 2.3903 | 1.2717 | 1.5583 | 1.5889 | 1.6308 | 1.2717 | 1.7338 | 1.9812 | 2.0088 | 2.0454 | 2.1845
2022-02-02 01:00 | 1.9053 | 2.1144 | 2.149 | 2.1912 | 2.2404 | 1.19 | 1.4549 | 1.4818 | 1.5185 | 1.19 | 1.5052 | 1.7205 | 1.7446 | 1.7768 | 1.8979
2022-02-02 02:00 | 1.81 | 2.0025 | 2.0321 | 2.0684 | 2.1107 | 1.086 | 1.3251 | 1.3482 | 1.3797 | 1.086 | 1.5052 | 1.7137 | 1.7344 | 1.762 | 1.8777
2022-02-02 03:00 | 1.7719 | 1.9495 | 1.973 | 2.0017 | 2.0351 | 1.0669 | 1.2938 | 1.3121 | 1.337 | 1.0669 | 1.5242 | 1.7263 | 1.7427 | 1.7646 | 1.8744
2022-02-02 04:00 | 1.7878 | 1.9548 | 1.9722 | 1.9935 | 2.0184 | 1.0479 | 1.2627 | 1.2763 | 1.2948 | 1.0479 | 1.3527 | 1.5274 | 1.5396 | 1.5558 | 1.6495
2022-02-02 05:00 | 1.9434 | 2.1118 | 2.1241 | 2.1391 | 2.1566 | 1.1622 | 1.3904 | 1.4 | 1.413 | 1.1622 | 1.3908 | 1.5626 | 1.5712 | 1.5826 | 1.6727
2022-02-02 06:00 | 2.0196 | 2.1897 | 2.2 | 2.2125 | 2.2271 | 1.3527 | 1.6126 | 1.6206 | 1.6315 | 1.3527 | 1.5433 | 1.7291 | 1.7363 | 1.7458 | 1.8421
2022-02-02 07:00 | 2.3816 | 2.582 | 2.5939 | 2.6085 | 2.6256 | 1.5348 | 1.8301 | 1.8394 | 1.8521 | 1.5348 | 1.7528 | 1.9644 | 1.9728 | 1.9839 | 2.0935
2022-02-02 08:00 | 2.4197 | 2.632 | 2.6486 | 2.6689 | 2.6925 | 1.6576 | 1.9818 | 1.9947 | 2.0123 | 1.6576 | 2.0005 | 2.2461 | 2.2577 | 2.2731 | 2.4016
2022-02-02 09:00 | 2.4578 | 2.6863 | 2.7097 | 2.7383 | 2.7717 | 1.4609 | 1.7591 | 1.7774 | 1.8023 | 1.4609 | 1.3908 | 1.578 | 1.5944 | 1.6162 | 1.7187
2022-02-02 10:00 | 2.4578 | 2.7005 | 2.7312 | 2.7688 | 2.8125 | 1.3718 | 1.6642 | 1.6881 | 1.7208 | 1.3718 | 1.5052 | 1.7152 | 1.7366 | 1.7652 | 1.8821
2022-02-02 11:00 | 2.191 | 2.4249 | 2.4612 | 2.5056 | 2.5573 | 1.105 | 1.357 | 1.3853 | 1.4239 | 1.105 | 1.467 | 1.6806 | 1.706 | 1.7397 | 1.8607
2022-02-02 12:00 | 2.3816 | 2.634 | 2.6724 | 2.7195 | 2.7745 | 1.086 | 1.3377 | 1.3677 | 1.4087 | 1.086 | 1.467 | 1.6836 | 1.7106 | 1.7464 | 1.8699
2022-02-02 13:00 | 2.3816 | 2.6329 | 2.6708 | 2.7173 | 2.7714 | 1.1622 | 1.4269 | 1.4565 | 1.4969 | 1.1622 | 1.5242 | 1.7464 | 1.773 | 1.8083 | 1.9344
2022-02-02 14:00 | 2.6102 | 2.8735 | 2.9089 | 2.9523 | 3.0028 | 1.2384 | 1.5133 | 1.541 | 1.5787 | 1.2384 | 1.4861 | 1.7005 | 1.7253 | 1.7583 | 1.8794
2022-02-02 15:00 | 2.3435 | 2.5816 | 2.6142 | 2.6542 | 2.7007 | 1.1432 | 1.3969 | 1.4223 | 1.4571 | 1.1432 | 1.1241 | 1.2944 | 1.3173 | 1.3477 | 1.4458
2022-02-02 16:00 | 2.4768 | 2.7213 | 2.7521 | 2.7898 | 2.8337 | 1.6195 | 1.957 | 1.981 | 2.0138 | 1.6195 | 1.6385 | 1.8635 | 1.8851 | 1.9138 | 2.0382
2022-02-02 17:00 | 2.4197 | 2.659 | 2.6894 | 2.7265 | 2.7699 | 1.7463 | 2.1062 | 2.1299 | 2.1622 | 1.7463 | 2.4768 | 2.7945 | 2.8158 | 2.844 | 3.014
2022-02-02 18:00 | 2.4197 | 2.6625 | 2.6947 | 2.7341 | 2.78 | 1.81 | 2.184 | 2.2091 | 2.2434 | 1.81 | 2.4959 | 2.8182 | 2.8407 | 2.8707 | 3.0437
2022-02-02 19:00 | 2.3284 | 2.5718 | 2.6077 | 2.6517 | 2.703 | 1.81 | 2.1893 | 2.2174 | 2.2556 | 1.81 | 2.3816 | 2.6964 | 2.7215 | 2.755 | 2.9259
2022-02-02 20:00 | 2.3435 | 2.5978 | 2.6387 | 2.6888 | 2.7472 | 1.7528 | 2.1289 | 2.1608 | 2.2044 | 1.7528 | 2.553 | 2.8938 | 2.9225 | 2.9606 | 3.1465
2022-02-02 21:00 | 2.2291 | 2.4846 | 2.5305 | 2.5866 | 2.6521 | 1.6648 | 2.0319 | 2.0677 | 2.1165 | 1.6648 | 2.3816 | 2.7101 | 2.7423 | 2.785 | 2.9669
2022-02-02 22:00 | 2.1148 | 2.3635 | 2.4101 | 2.4673 | 2.5339 | 1.448 | 1.777 | 1.8134 | 1.8631 | 1.448 | 2.0958 | 2.3937 | 2.4264 | 2.4699 | 2.6371
2022-02-02 23:00 | 1.8886 | 2.1145 | 2.1581 | 2.2115 | 2.2738 | 1.2645 | 1.5559 | 1.5899 | 1.6364 | 1.2645 | 1.81 | 2.0719 | 2.1025 | 2.1431 | 2.2912
2022-02-03 | 1.6816 | 1.8836 | 1.9229 | 1.9711 | 2.0272 | 1.1319 | 1.3932 | 1.4238 | 1.4657 | 1.1319 | 1.7147 | 1.9601 | 1.9876 | 2.0242 | 2.1623
2022-02-03 01:00 | 1.6385 | 1.8279 | 1.8624 | 1.9046 | 1.9539 | 1.0479 | 1.287 | 1.3139 | 1.3507 | 1.0479 | 1.2765 | 1.4664 | 1.4906 | 1.5227 | 1.6313
2022-02-03 02:00 | 1.6576 | 1.8388 | 1.8684 | 1.9046 | 1.9469 | 0.99073 | 1.2125 | 1.2356 | 1.2672 | 0.99073 | 1.3718 | 1.5655 | 1.5862 | 1.6138 | 1.7222
2022-02-03 03:00 | 1.6195 | 1.7858 | 1.8092 | 1.8379 | 1.8714 | 0.97168 | 1.1812 | 1.1995 | 1.2245 | 0.97168 | 1.3337 | 1.5146 | 1.531 | 1.5528 | 1.6523
2022-02-03 04:00 | 1.6385 | 1.7944 | 1.8118 | 1.8331 | 1.858 | 0.97168 | 1.1727 | 1.1862 | 1.2048 | 0.97168 | 1.3527 | 1.5274 | 1.5396 | 1.5558 | 1.6495
2022-02-03 05:00 | 1.6766 | 1.8253 | 1.8375 | 1.8525 | 1.87 | 1.0598 | 1.2695 | 1.279 | 1.2921 | 1.0598 | 1.2956 | 1.4567 | 1.4653 | 1.4767 | 1.5616
2022-02-03 06:00 | 1.7909 | 1.9441 | 1.9543 | 1.9669 | 1.9815 | 1.2956 | 1.5451 | 1.5531 | 1.564 | 1.2956 | 1.467 | 1.6445 | 1.6516 | 1.6611 | 1.7532
2022-02-03 07:00 | 2.0196 | 2.1931 | 2.205 | 2.2196 | 2.2367 | 1.3718 | 1.6375 | 1.6468 | 1.6596 | 1.3718 | 1.6576 | 1.8585 | 1.8669 | 1.878 | 1.9824
2022-02-03 08:00 | 2.0005 | 2.1817 | 2.1983 | 2.2186 | 2.2422 | 1.3571 | 1.6268 | 1.6398 | 1.6574 | 1.3571 | 1.2956 | 1.4627 | 1.4743 | 1.4898 | 1.5794
2022-02-03 09:00 | 2.0386 | 2.236 | 2.2594 | 2.288 | 2.3214 | 1.0479 | 1.2712 | 1.2895 | 1.3144 | 1.0479 | 1.0288 | 1.1758 | 1.1921 | 1.2139 | 1.2965
2022-02-03 10:00 | 1.696 | 1.8821 | 1.9128 | 1.9503 | 1.9941 | 0.7621 | 0.94393 | 0.96786 | 1.0005 | 0.7621 | 1.5623 | 1.7787 | 1.8002 | 1.8287 | 1.9488
2022-02-03 11:00 | 1.6385 | 1.8313 | 1.8676 | 1.912 | 1.9637 | 0.74305 | 0.92937 | 0.95766 | 0.99628 | 0.74305 | 1.7719 | 2.0193 | 2.0447 | 2.0785 | 2.2163
2022-02-03 12:00 | 1.7909 | 1.9994 | 2.0379 | 2.085 | 2.1399 | 0.85737 | 1.0676 | 1.0976 | 1.1386 | 0.85737 | 1.7266 | 1.9721 | 1.999 | 2.0349 | 2.1726
2022-02-03 13:00 | 1.6766 | 1.8755 | 1.9135 | 1.9599 | 2.0141 | 0.51442 | 0.66167 | 0.69127 | 0.73168 | 0.51442 | 1.9053 | 2.1699 | 2.1964 | 2.2318 | 2.3787
2022-02-03 14:00 | 1.8672 | 2.0753 | 2.1107 | 2.154 | 2.2045 | 0.724 | 0.90563 | 0.93324 | 0.97094 | 0.724 | 2.1529 | 2.4416 | 2.4664 | 2.4993 | 2.6571
2022-02-03 15:00 | 1.9053 | 2.1108 | 2.1434 | 2.1834 | 2.2299 | 0.59063 | 0.74415 | 0.76961 | 0.80436 | 0.59063 | 1.6957 | 1.9296 | 1.9525 | 1.9828 | 2.1124
2022-02-03 16:00 | 1.8862 | 2.0867 | 2.1175 | 2.1552 | 2.1992 | 1.1622 | 1.4168 | 1.4408 | 1.4736 | 1.1622 | 1.1622 | 1.3342 | 1.3558 | 1.3845 | 1.4827
2022-02-03 17:00 | 2.3054 | 2.5362 | 2.5665 | 2.6037 | 2.647 | 1.4555 | 1.7626 | 1.7863 | 1.8187 | 1.4555 | 1.5052 | 1.7147 | 1.736 | 1.7643 | 1.8808
2022-02-03 18:00 | 2.4006 | 2.6421 | 2.6742 | 2.7136 | 2.7595 | 1.7584 | 2.1231 | 2.1482 | 2.1824 | 1.7584 | 2.4006 | 2.7123 | 2.7349 | 2.7648 | 2.9326
2022-02-03 19:00 | 2.3816 | 2.629 | 2.6649 | 2.7089 | 2.7602 | 1.7719 | 2.1443 | 2.1724 | 2.2106 | 1.7719 | 2.2482 | 2.5482 | 2.5733 | 2.6068 | 2.7704
2022-02-03 20:00 | 2.3054 | 2.5568 | 2.5978 | 2.6478 | 2.7062 | 1.7338 | 2.1064 | 2.1383 | 2.1819 | 1.7338 | 2.1529 | 2.4492 | 2.4779 | 2.516 | 2.6799
2022-02-03 21:00 | 2.1529 | 2.4028 | 2.4486 | 2.5047 | 2.5702 | 1.6957 | 2.0684 | 2.1042 | 2.153 | 1.6957 | 2.2101 | 2.5196 | 2.5517 | 2.5944 | 2.7669
2022-02-03 22:00 | 2.0386 | 2.2816 | 2.3283 | 2.3854 | 2.452 | 1.5465 | 1.8934 | 1.9298 | 1.9795 | 1.5465 | 2.0196 | 2.309 | 2.3417 | 2.3852 | 2.5482
2022-02-03 23:00 | 1.9434 | 2.1733 | 2.2169 | 2.2703 | 2.3326 | 1.3751 | 1.6865 | 1.7206 | 1.7671 | 1.3751 | 1.6004 | 1.839 | 1.8696 | 1.9102 | 2.0468
2022-02-04 | 1.7909 | 2.0011 | 2.0404 | 2.0886 | 2.1447 | 1.154 | 1.4192 | 1.4499 | 1.4917 | 1.154 | 1.448 | 1.6636 | 1.6912 | 1.7278 | 1.8512
2022-02-04 01:00 | 1.6957 | 1.8893 | 1.9238 | 1.966 | 2.0153 | 1.0479 | 1.287 | 1.3139 | 1.3507 | 1.0479 | 1.448 | 1.6569 | 1.6811 | 1.7133 | 1.8313
2022-02-04 02:00 | 1.6576 | 1.8388 | 1.8684 | 1.9046 | 1.9469 | 0.99779 | 1.2209 | 1.244 | 1.2755 | 0.99779 | 1.2956 | 1.4808 | 1.5015 | 1.5291 | 1.6333
2022-02-04 03:00 | 1.6385 | 1.8062 | 1.8297 | 1.8584 | 1.8918 | 0.97168 | 1.1812 | 1.1995 | 1.2245 | 0.97168 | 1.2956 | 1.4722 | 1.4887 | 1.5105 | 1.6078
2022-02-04 04:00 | 1.6957 | 1.8558 | 1.8732 | 1.8945 | 1.9194 | 0.98252 | 1.1855 | 1.199 | 1.2176 | 0.98252 | 1.2003 | 1.358 | 1.3702 | 1.3864 | 1.4718
2022-02-04 05:00 | 1.7719 | 1.9276 | 1.9399 | 1.9549 | 1.9724 | 1.0728 | 1.2848 | 1.2944 | 1.3074 | 1.0728 | 1.3718 | 1.5414 | 1.55 | 1.5614 | 1.6505
2022-02-04 06:00 | 1.8675 | 2.0264 | 2.0366 | 2.0492 | 2.0638 | 1.2575 | 1.5001 | 1.508 | 1.5189 | 1.2575 | 1.5052 | 1.6868 | 1.694 | 1.7035 | 1.7976
2022-02-04 07:00 | 2.0577 | 2.234 | 2.2459 | 2.2606 | 2.2776 | 1.3527 | 1.615 | 1.6243 | 1.637 | 1.3527 | 1.7338 | 1.9432 | 1.9516 | 1.9627 | 2.0713
2022-02-04 08:00 | 2.0005 | 2.1817 | 2.1983 | 2.2186 | 2.2422 | 1.2575 | 1.5091 | 1.522 | 1.5397 | 1.2575 | 1.2956 | 1.4627 | 1.4743 | 1.4898 | 1.5794
2022-02-04 09:00 | 1.829 | 2.0108 | 2.0342 | 2.0629 | 2.0963 | 0.99073 | 1.2037 | 1.2219 | 1.2468 | 0.99073 | 1.2765 | 1.451 | 1.4674 | 1.4892 | 1.5854
2022-02-04 10:00 | 1.9434 | 2.1479 | 2.1786 | 2.2161 | 2.2599 | 1.0669 | 1.3041 | 1.328 | 1.3607 | 1.0669 | 1.3718 | 1.5669 | 1.5884 | 1.617 | 1.7266
2022-02-04 11:00 | 2.0577 | 2.2816 | 2.3179 | 2.3623 | 2.414 | 1.086 | 1.3345 | 1.3628 | 1.4014 | 1.086 | 1.8672 | 2.1252 | 2.1506 | 2.1843 | 2.3274
2022-02-04 12:00 | 1.9624 | 2.1836 | 2.2221 | 2.2692 | 2.3241 | 1.086 | 1.3377 | 1.3677 | 1.4087 | 1.086 | 2.0386 | 2.3188 | 2.3458 | 2.3816 | 2.5365
2022-02-04 13:00 | 1.81 | 2.0188 | 2.0568 | 2.1032 | 2.1574 | 0.93358 | 1.1568 | 1.1864 | 1.2269 | 0.93358 | 1.6385 | 1.8734 | 1.9 | 1.9354 | 2.0677
2022-02-04 14:00 | 1.9434 | 2.1571 | 2.1925 | 2.2359 | 2.2864 | 0.97168 | 1.1982 | 1.2258 | 1.2635 | 0.97168 | 1.9624 | 2.2298 | 2.2546 | 2.2876 | 2.4349
2022-02-04 15:00 | 2.0386 | 2.2541 | 2.2867 | 2.3266 | 2.3732 | 1.1241 | 1.3744 | 1.3998 | 1.4346 | 1.1241 | 1.7909 | 2.0355 | 2.0583 | 2.0887 | 2.2235
2022-02-04 16:00 | 1.8271 | 2.0232 | 2.054 | 2.0917 | 2.1357 | 0.99073 | 1.2142 | 1.2382 | 1.271 | 0.99073 | 1.086 | 1.2495 | 1.2711 | 1.2998 | 1.3938
2022-02-04 17:00 | 1.9238 | 2.1263 | 2.1566 | 2.1938 | 2.2371 | 1.2384 | 1.5062 | 1.5299 | 1.5622 | 1.2384 | 1.3527 | 1.5453 | 1.5666 | 1.5949 | 1.7031
2022-02-04 18:00 | 2.0005 | 2.2122 | 2.2444 | 2.2838 | 2.3297 | 1.4421 | 1.7494 | 1.7745 | 1.8088 | 1.4421 | 1.5814 | 1.8019 | 1.8245 | 1.8544 | 1.9772
2022-02-04 19:00 | 2.0958 | 2.3219 | 2.3579 | 2.4018 | 2.4531 | 1.6385 | 1.9868 | 2.0148 | 2.0531 | 1.6385 | 1.9434 | 2.2094 | 2.2346 | 2.268 | 2.4149
2022-02-04 20:00 | 2.1339 | 2.3726 | 2.4135 | 2.4636 | 2.522 | 1.6766 | 2.0389 | 2.0708 | 2.1144 | 1.6766 | 2.3625 | 2.6821 | 2.7108 | 2.7489 | 2.9243
2022-02-04 21:00 | 2.1339 | 2.3823 | 2.4281 | 2.4843 | 2.5497 | 1.5903 | 1.9439 | 1.9797 | 2.0285 | 1.5903 | 2.1339 | 2.4349 | 2.467 | 2.5097 | 2.6781
2022-02-04 22:00 | 2.0958 | 2.343 | 2.3897 | 2.4468 | 2.5135 | 1.5052 | 1.8445 | 1.8809 | 1.9306 | 1.5052 | 2.1339 | 2.436 | 2.4688 | 2.5122 | 2.6815
2022-02-04 23:00 | 1.91 | 2.1375 | 2.1811 | 2.2345 | 2.2968 | 1.3146 | 1.6151 | 1.6492 | 1.6956 | 1.3146 | 1.8481 | 2.1142 | 2.1448 | 2.1855 | 2.3356
2022-02-05 | 1.7432 | 1.9498 | 1.9892 | 2.0373 | 2.0934 | 1.1883 | 1.4598 | 1.4905 | 1.5323 | 1.1883 | 1.6576 | 1.8965 | 1.9241 | 1.9607 | 2.0956
2022-02-05 01:00 | 1.6195 | 1.8074 | 1.8419 | 1.8842 | 1.9334 | 1.086 | 1.332 | 1.3589 | 1.3957 | 1.086 | 1.3718 | 1.5723 | 1.5964 | 1.6286 | 1.7424
2022-02-05 02:00 | 1.6004 | 1.7774 | 1.807 | 1.8432 | 1.8855 | 0.98018 | 1.2001 | 1.2232 | 1.2547 | 0.98018 | 1.2384 | 1.4173 | 1.438 | 1.4656 | 1.5666
2022-02-05 03:00 | 1.6004 | 1.7653 | 1.7887 | 1.8174 | 1.8509 | 0.95776 | 1.1648 | 1.1831 | 1.2081 | 0.95776 | 1.6576 | 1.8745 | 1.8909 | 1.9128 | 2.03
2022-02-05 04:00 | 1.5242 | 1.6716 | 1.689 | 1.7103 | 1.7352 | 0.95263 | 1.1501 | 1.1637 | 1.1823 | 0.95263 | 1.2384 | 1.4003 | 1.4125 | 1.4287 | 1.5162
2022-02-05 05:00 | 1.5814 | 1.7229 | 1.7352 | 1.7502 | 1.7677 | 1.0649 | 1.2755 | 1.2851 | 1.2981 | 1.0649 | 1.2956 | 1.4567 | 1.4653 | 1.4767 | 1.5616
2022-02-05 06:00 | 1.5433 | 1.678 | 1.6882 | 1.7008 | 1.7154 | 1.0669 | 1.275 | 1.283 | 1.2939 | 1.0669 | 1.3527 | 1.5174 | 1.5246 | 1.5341 | 1.6199
2022-02-05 07:00 | 1.6576 | 1.8042 | 1.8161 | 1.8307 | 1.8477 | 1.1813 | 1.4125 | 1.4218 | 1.4345 | 1.1813 | 1.5433 | 1.7315 | 1.7399 | 1.751 | 1.8491
2022-02-05 08:00 | 1.6576 | 1.8133 | 1.8298 | 1.8501 | 1.8738 | 1.3146 | 1.5766 | 1.5895 | 1.6072 | 1.3146 | 1.7528 | 1.9708 | 1.9825 | 1.9979 | 2.1127
2022-02-05 09:00 | 1.5814 | 1.7447 | 1.7681 | 1.7968 | 1.8302 | 1.1813 | 1.4288 | 1.447 | 1.4719 | 1.1813 | 1.2003 | 1.3663 | 1.3827 | 1.4045 | 1.4965
2022-02-05 10:00 | 1.6004 | 1.7794 | 1.8101 | 1.8477 | 1.8914 | 1.0816 | 1.3214 | 1.3453 | 1.378 | 1.0816 | 1.5052 | 1.7152 | 1.7366 | 1.7652 | 1.8821
2022-02-05 11:00 | 1.5623 | 1.7494 | 1.7857 | 1.8301 | 1.8819 | 1.086 | 1.3345 | 1.3628 | 1.4014 | 1.086 | 1.4861 | 1.7017 | 1.7271 | 1.7609 | 1.883
2022-02-05 12:00 | 1.6957 | 1.8971 | 1.9356 | 1.9827 | 2.0376 | 1.1622 | 1.4277 | 1.4577 | 1.4987 | 1.1622 | 1.2003 | 1.3872 | 1.4142 | 1.45 | 1.5588
2022-02-05 13:00 | 1.4861 | 1.6709 | 1.7088 | 1.7552 | 1.8094 | 1.0288 | 1.2694 | 1.299 | 1.3394 | 1.0288 | 1.4861 | 1.7041 | 1.7306 | 1.766 | 1.8899
2022-02-05 14:00 | 1.3527 | 1.5226 | 1.558 | 1.6013 | 1.6518 | 0.93358 | 1.1532 | 1.1808 | 1.2185 | 0.93358 | 1.7719 | 2.0181 | 2.0429 | 2.0759 | 2.2127
2022-02-05 15:00 | 1.467 | 1.64 | 1.6726 | 1.7126 | 1.7592 | 0.95263 | 1.1718 | 1.1973 | 1.232 | 0.95263 | 1.5623 | 1.7814 | 1.8043 | 1.8346 | 1.9569
2022-02-05 16:00 | 1.4099 | 1.575 | 1.6058 | 1.6435 | 1.6875 | 0.83831 | 1.0341 | 1.0582 | 1.091 | 0.83831 | 1.448 | 1.6518 | 1.6734 | 1.7021 | 1.816
2022-02-05 17:00 | 1.7719 | 1.9631 | 1.9934 | 2.0306 | 2.0739 | 1.5433 | 1.8663 | 1.89 | 1.9223 | 1.5433 | 1.3718 | 1.5665 | 1.5878 | 1.6161 | 1.7253
2022-02-05 18:00 | 1.8672 | 2.0689 | 2.1011 | 2.1405 | 2.1864 | 1.4443 | 1.7519 | 1.777 | 1.8113 | 1.4443 | 2.1529 | 2.4371 | 2.4596 | 2.4896 | 2.6438
2022-02-05 19:00 | 2.0196 | 2.2401 | 2.276 | 2.32 | 2.3713 | 1.5528 | 1.8855 | 1.9135 | 1.9518 | 1.5528 | 2.4197 | 2.7387 | 2.7639 | 2.7973 | 2.9704
2022-02-05 20:00 | 2.1529 | 2.3931 | 2.434 | 2.4841 | 2.5425 | 1.6576 | 2.0164 | 2.0483 | 2.0919 | 1.6576 | 2.2101 | 2.5127 | 2.5414 | 2.5795 | 2.7465
2022-02-05 21:00 | 2.0767 | 2.3209 | 2.3667 | 2.4229 | 2.4883 | 1.6766 | 2.0459 | 2.0817 | 2.1305 | 1.6766 | 2.0386 | 2.329 | 2.3612 | 2.4038 | 2.567
2022-02-05 22:00 | 1.9815 | 2.2202 | 2.2669 | 2.324 | 2.3906 | 1.499 | 1.8373 | 1.8737 | 1.9234 | 1.499 | 2.2482 | 2.5631 | 2.5958 | 2.6393 | 2.8148
2022-02-05 23:00 | 1.8862 | 2.1119 | 2.1555 | 2.2089 | 2.2712 | 1.3337 | 1.6376 | 1.6717 | 1.7181 | 1.3337 | 1.7909 | 2.0507 | 2.0813 | 2.1219 | 2.269
2022-02-06 | 1.6576 | 1.8578 | 1.8971 | 1.9453 | 2.0014 | 1.2395 | 1.5203 | 1.5509 | 1.5928 | 1.2395 | 1.4861 | 1.706 | 1.7335 | 1.7702 | 1.8956
2022-02-06 01:00 | 1.6576 | 1.8483 | 1.8829 | 1.9251 | 1.9743 | 1.0998 | 1.3483 | 1.3752 | 1.412 | 1.0998 | 1.4289 | 1.6358 | 1.66 | 1.6921 | 1.8091
2022-02-06 02:00 | 1.5327 | 1.7046 | 1.7342 | 1.7705 | 1.8127 | 0.99426 | 1.2167 | 1.2398 | 1.2713 | 0.99426 | 1.2765 | 1.4596 | 1.4804 | 1.5079 | 1.6111
2022-02-06 03:00 | 1.4861 | 1.6425 | 1.6659 | 1.6946 | 1.7281 | 0.95981 | 1.1672 | 1.1855 | 1.2105 | 0.95981 | 1.2003 | 1.3664 | 1.3828 | 1.4046 | 1.4967
2022-02-06 04:00 | 1.5242 | 1.6716 | 1.689 | 1.7103 | 1.7352 | 0.96317 | 1.1626 | 1.1762 | 1.1947 | 0.96317 | 1.1813 | 1.3368 | 1.349 | 1.3652 | 1.4495
2022-02-06 05:00 | 1.5242 | 1.6615 | 1.6738 | 1.6888 | 1.7063 | 0.97956 | 1.1746 | 1.1842 | 1.1973 | 0.97956 | 1.4861 | 1.6684 | 1.677 | 1.6884 | 1.7838
2022-02-06 06:00 | 1.5052 | 1.6371 | 1.6473 | 1.6598 | 1.6744 | 1.0669 | 1.275 | 1.283 | 1.2939 | 1.0669 | 1.2575 | 1.4116 | 1.4187 | 1.4283 | 1.5088
2022-02-06 07:00 | 1.448 | 1.579 | 1.5909 | 1.6056 | 1.6226 | 1.0669 | 1.2774 | 1.2867 | 1.2994 | 1.0669 | 1.3146 | 1.4774 | 1.4858 | 1.4969 | 1.5825
2022-02-06 08:00 | 1.3908 | 1.5267 | 1.5433 | 1.5636 | 1.5872 | 1.0669 | 1.284 | 1.2969 | 1.3146 | 1.0669 | 1.1432 | 1.2933 | 1.3049 | 1.3204 | 1.4017
2022-02-06 09:00 | 1.5433 | 1.7038 | 1.7272 | 1.7558 | 1.7892 | 1.086 | 1.3162 | 1.3345 | 1.3594 | 1.086 | 1.4099 | 1.5992 | 1.6156 | 1.6374 | 1.7409
2022-02-06 10:00 | 1.5814 | 1.759 | 1.7896 | 1.8272 | 1.871 | 1.086 | 1.3266 | 1.3505 | 1.3832 | 1.086 | 1.3146 | 1.5034 | 1.5249 | 1.5535 | 1.6599
2022-02-06 11:00 | 1.4099 | 1.5857 | 1.622 | 1.6663 | 1.7181 | 0.99073 | 1.222 | 1.2503 | 1.2889 | 0.99073 | 1.5623 | 1.7864 | 1.8118 | 1.8456 | 1.9718
2022-02-06 12:00 | 1.7147 | 1.9175 | 1.956 | 2.0031 | 2.058 | 1.2194 | 1.4952 | 1.5252 | 1.5662 | 1.2194 | 1.3337 | 1.5354 | 1.5624 | 1.5982 | 1.7144
2022-02-06 13:00 | 1.7147 | 1.9165 | 1.9544 | 2.0009 | 2.055 | 1.2765 | 1.562 | 1.5916 | 1.632 | 1.2765 | 1.3718 | 1.577 | 1.6036 | 1.6389 | 1.7566
2022-02-06 14:00 | 1.467 | 1.6454 | 1.6808 | 1.7241 | 1.7747 | 1.086 | 1.3333 | 1.3609 | 1.3986 | 1.086 | 1.6576 | 1.8911 | 1.9159 | 1.9488 | 2.0794
2022-02-06 15:00 | 1.4099 | 1.5786 | 1.6112 | 1.6512 | 1.6978 | 0.97168 | 1.1943 | 1.2198 | 1.2545 | 0.97168 | 1.448 | 1.6544 | 1.6772 | 1.7076 | 1.8235
2022-02-06 16:00 | 1.6766 | 1.8616 | 1.8924 | 1.9301 | 1.974 | 1.2575 | 1.5293 | 1.5533 | 1.5861 | 1.2575 | 1.5623 | 1.7788 | 1.8004 | 1.8291 | 1.9493
2022-02-06 17:00 | 1.6195 | 1.7993 | 1.8297 | 1.8668 | 1.9102 | 1.1941 | 1.4538 | 1.4775 | 1.5098 | 1.1941 | 1.3718 | 1.5665 | 1.5878 | 1.6161 | 1.7253
2022-02-06 18:00 | 2.0005 | 2.2122 | 2.2444 | 2.2838 | 2.3297 | 1.6385 | 1.9814 | 2.0065 | 2.0408 | 1.6385 | 2.1529 | 2.4371 | 2.4596 | 2.4896 | 2.6438
2022-02-06 19:00 | 2.1529 | 2.3833 | 2.4193 | 2.4633 | 2.5145 | 1.7719 | 2.1443 | 2.1724 | 2.2106 | 1.7719 | 2.1148 | 2.4 | 2.4251 | 2.4586 | 2.6148
2022-02-06 20:00 | 2.2673 | 2.5159 | 2.5568 | 2.6069 | 2.6653 | 1.7909 | 2.1739 | 2.2058 | 2.2494 | 1.7909 | 2.2482 | 2.5551 | 2.5837 | 2.6218 | 2.791
2022-02-06 21:00 | 2.191 | 2.4437 | 2.4896 | 2.5457 | 2.6111 | 1.7245 | 2.1024 | 2.1382 | 2.187 | 1.7245 | 2.172 | 2.4772 | 2.5094 | 2.5521 | 2.7225
2022-02-06 22:00 | 2.0386 | 2.2816 | 2.3283 | 2.3854 | 2.452 | 1.5191 | 1.861 | 1.8974 | 1.9472 | 1.5191 | 1.9053 | 2.182 | 2.2147 | 2.2582 | 2.4149
2022-02-06 23:00 | 1.8481 | 2.0709 | 2.1146 | 2.168 | 2.2303 | 1.3146 | 1.6151 | 1.6492 | 1.6956 | 1.3146 | 1.7909 | 2.0507 | 2.0813 | 2.1219 | 2.269
2022-02-07 | 1.6195 | 1.8169 | 1.8562 | 1.9043 | 1.9605 | 1.1273 | 1.3877 | 1.4184 | 1.4603 | 1.1273 | 1.6576 | 1.8965 | 1.9241 | 1.9607 | 2.0956
2022-02-07 01:00 | 1.5623 | 1.746 | 1.7805 | 1.8227 | 1.872 | 1.034 | 1.2706 | 1.2975 | 1.3342 | 1.034 | 1.4289 | 1.6358 | 1.66 | 1.6921 | 1.8091
2022-02-07 02:00 | 1.5348 | 1.7069 | 1.7365 | 1.7728 | 1.8151 | 0.97966 | 1.1994 | 1.2225 | 1.2541 | 0.97966 | 1.3146 | 1.502 | 1.5227 | 1.5503 | 1.6555
2022-02-07 03:00 | 1.448 | 1.6015 | 1.625 | 1.6537 | 1.6872 | 0.95263 | 1.1587 | 1.177 | 1.202 | 0.95263 | 1.2194 | 1.3875 | 1.404 | 1.4258 | 1.5189
2022-02-07 04:00 | 1.5242 | 1.6716 | 1.689 | 1.7103 | 1.7352 | 0.97168 | 1.1727 | 1.1862 | 1.2048 | 0.97168 | 1.3527 | 1.5274 | 1.5396 | 1.5558 | 1.6495
2022-02-07 05:00 | 1.5846 | 1.7263 | 1.7386 | 1.7536 | 1.7711 | 1.1581 | 1.3856 | 1.3951 | 1.4082 | 1.1581 | 1.6004 | 1.7955 | 1.8041 | 1.8155 | 1.9171
2022-02-07 06:00 | 1.7909 | 1.9441 | 1.9543 | 1.9669 | 1.9815 | 1.2956 | 1.5451 | 1.5531 | 1.564 | 1.2956 | 1.6195 | 1.8138 | 1.821 | 1.8305 | 1.9309
2022-02-07 07:00 | 2.0958 | 2.275 | 2.2869 | 2.3015 | 2.3185 | 1.4099 | 1.6826 | 1.6919 | 1.7046 | 1.4099 | 1.7528 | 1.9644 | 1.9728 | 1.9839 | 2.0935
2022-02-07 08:00 | 2.0958 | 2.284 | 2.3006 | 2.3209 | 2.3446 | 1.4099 | 1.6892 | 1.7021 | 1.7197 | 1.4099 | 1.4099 | 1.5897 | 1.6014 | 1.6168 | 1.7128
2022-02-07 09:00 | 2.0767 | 2.2769 | 2.3003 | 2.329 | 2.3624 | 1.1813 | 1.4288 | 1.447 | 1.4719 | 1.1813 | 1.2575 | 1.4298 | 1.4462 | 1.468 | 1.5632
2022-02-07 10:00 | 2.0386 | 2.2502 | 2.2809 | 2.3184 | 2.3622 | 1.086 | 1.3266 | 1.3505 | 1.3832 | 1.086 | 1.5433 | 1.7575 | 1.779 | 1.8075 | 1.9265
2022-02-07 11:00 | 1.5433 | 1.729 | 1.7652 | 1.8096 | 1.8614 | 0.70494 | 0.88436 | 0.91264 | 0.95126 | 0.70494 | 1.7528 | 1.9981 | 2.0235 | 2.0573 | 2.194
2022-02-07 12:00 | 1.9815 | 2.2041 | 2.2426 | 2.2897 | 2.3446 | 0.85737 | 1.0676 | 1.0976 | 1.1386 | 0.85737 | 2.0005 | 2.2765 | 2.3034 | 2.3392 | 2.4921
2022-02-07 13:00 | 1.9243 | 2.1416 | 2.1796 | 2.226 | 2.2802 | 0.97168 | 1.2019 | 1.2315 | 1.2719 | 0.97168 | 1.9434 | 2.2122 | 2.2388 | 2.2741 | 2.4232
2022-02-07 14:00 | 1.9434 | 2.1571 | 2.1925 | 2.2359 | 2.2864 | 0.93358 | 1.1532 | 1.1808 | 1.2185 | 0.93358 | 2.0386 | 2.3145 | 2.3393 | 2.3723 | 2.5238
2022-02-07 15:00 | 2.2101 | 2.4383 | 2.4709 | 2.5109 | 2.5574 | 1.0479 | 1.2843 | 1.3098 | 1.3446 | 1.0479 | 2.0005 | 2.2683 | 2.2912 | 2.3216 | 2.4679
2022-02-07 16:00 | 1.9434 | 2.1481 | 2.1789 | 2.2166 | 2.2606 | 0.93358 | 1.1467 | 1.1707 | 1.2035 | 0.93358 | 1.8862 | 2.1388 | 2.1604 | 2.189 | 2.327
2022-02-07 17:00 | 1.7719 | 1.9631 | 1.9934 | 2.0306 | 2.0739 | 1.1781 | 1.4349 | 1.4586 | 1.4909 | 1.1781 | 1.3146 | 1.503 | 1.5243 | 1.5525 | 1.6586
2022-02-07 18:00 | 2.1148 | 2.335 | 2.3672 | 2.4066 | 2.4525 | 1.5892 | 1.9232 | 1.9483 | 1.9825 | 1.5892 | 1.7528 | 1.9925 | 2.015 | 2.045 | 2.1771
2022-02-07 19:00 | 2.2482 | 2.4857 | 2.5216 | 2.5656 | 2.6169 | 1.6766 | 2.0318 | 2.0598 | 2.0981 | 1.6766 | 2.4959 | 2.8234 | 2.8486 | 2.882 | 3.0592
2022-02-07 20:00 | 2.2482 | 2.4954 | 2.5363 | 2.5864 | 2.6448 | 1.7147 | 2.0839 | 2.1158 | 2.1594 | 1.7147 | 2.2291 | 2.5339 | 2.5626 | 2.6007 | 2.7688
2022-02-07 21:00 | 2.191 | 2.4437 | 2.4896 | 2.5457 | 2.6111 | 1.6766 | 2.0459 | 2.0817 | 2.1305 | 1.6766 | 2.1529 | 2.4561 | 2.4882 | 2.5309 | 2.7003
2022-02-07 22:00 | 2.0577 | 2.302 | 2.3487 | 2.4059 | 2.4725 | 1.5255 | 1.8686 | 1.905 | 1.9547 | 1.5255 | 1.9624 | 2.2455 | 2.2782 | 2.3217 | 2.4815
2022-02-07 23:00 | 1.8732 | 2.0978 | 2.1415 | 2.1949 | 2.2572 | 1.2647 | 1.5561 | 1.5902 | 1.6367 | 1.2647 | 1.6004 | 1.839 | 1.8696 | 1.9102 | 2.0468
2022-02-08 | 1.7719 | 1.9806 | 2.0199 | 2.0681 | 2.1242 | 1.1241 | 1.3839 | 1.4146 | 1.4565 | 1.1241 | 1.3908 | 1.6001 | 1.6277 | 1.6643 | 1.7846
2022-02-08 01:00 | 1.5814 | 1.7665 | 1.801 | 1.8432 | 1.8925 | 1.0201 | 1.2542 | 1.2811 | 1.3179 | 1.0201 | 1.3146 | 1.5087 | 1.5329 | 1.565 | 1.6757
2022-02-08 02:00 | 1.5352 | 1.7073 | 1.7369 | 1.7732 | 1.8155 | 0.97168 | 1.19 | 1.2131 | 1.2447 | 0.97168 | 1.3146 | 1.502 | 1.5227 | 1.5503 | 1.6555
2022-02-08 03:00 | 1.5623 | 1.7244 | 1.7478 | 1.7765 | 1.81 | 0.94484 | 1.1495 | 1.1678 | 1.1928 | 0.94484 | 1.2384 | 1.4087 | 1.4251 | 1.447 | 1.5412
2022-02-08 04:00 | 1.5623 | 1.7125 | 1.7299 | 1.7512 | 1.7761 | 0.95263 | 1.1501 | 1.1637 | 1.1823 | 0.95263 | 1.2765 | 1.4427 | 1.4549 | 1.4711 | 1.5606
2022-02-08 05:00 | 1.7178 | 1.8695 | 1.8818 | 1.8968 | 1.9143 | 1.0758 | 1.2884 | 1.298 | 1.311 | 1.0758 | 1.3527 | 1.5202 | 1.5288 | 1.5402 | 1.6282
2022-02-08 06:00 | 1.81 | 1.9646 | 1.9748 | 1.9873 | 2.0019 | 1.3337 | 1.5901 | 1.5981 | 1.609 | 1.3337 | 1.5623 | 1.7503 | 1.7575 | 1.767 | 1.8643
2022-02-08 07:00 | 2.0196 | 2.1931 | 2.205 | 2.2196 | 2.2367 | 1.3337 | 1.5925 | 1.6018 | 1.6145 | 1.3337 | 1.6576 | 1.8585 | 1.8669 | 1.878 | 1.9824
2022-02-08 08:00 | 2.0196 | 2.2022 | 2.2187 | 2.239 | 2.2627 | 1.2306 | 1.4773 | 1.4902 | 1.5079 | 1.2306 | 1.2384 | 1.3992 | 1.4108 | 1.4262 | 1.5128
2022-02-08 09:00 | 1.81 | 1.9904 | 2.0138 | 2.0424 | 2.0758 | 0.89547 | 1.0911 | 1.1094 | 1.1343 | 0.89547 | 1.2956 | 1.4722 | 1.4886 | 1.5103 | 1.6076
2022-02-08 10:00 | 1.7909 | 1.9841 | 2.0148 | 2.0524 | 2.0961 | 0.83831 | 1.034 | 1.0579 | 1.0906 | 0.83831 | 1.3718 | 1.5669 | 1.5884 | 1.617 | 1.7266
2022-02-08 11:00 | 1.9521 | 2.1682 | 2.2045 | 2.2489 | 2.3007 | 0.83831 | 1.0419 | 1.0702 | 1.1088 | 0.83831 | 1.829 | 2.0828 | 2.1082 | 2.142 | 2.2829
2022-02-08 12:00 | 1.9815 | 2.2041 | 2.2426 | 2.2897 | 2.3446 | 0.74305 | 0.93253 | 0.96254 | 1.0035 | 0.74305 | 1.6195 | 1.853 | 1.88 | 1.9158 | 2.0477
2022-02-08 13:00 | 2.0386 | 2.2645 | 2.3024 | 2.3488 | 2.403 | 0.91452 | 1.1343 | 1.1639 | 1.2043 | 0.91452 | 2.0767 | 2.3604 | 2.387 | 2.4223 | 2.5787
2022-02-08 14:00 | 1.5814 | 1.7682 | 1.8036 | 1.8469 | 1.8975 | 0.70494 | 0.88312 | 0.91074 | 0.94844 | 0.70494 | 1.7909 | 2.0393 | 2.0641 | 2.097 | 2.2349
2022-02-08 15:00 | 2.0958 | 2.3155 | 2.3481 | 2.3881 | 2.4346 | 0.70494 | 0.8792 | 0.90465 | 0.93941 | 0.70494 | 1.6766 | 1.9084 | 1.9313 | 1.9617 | 2.0902
2022-02-08 16:00 | 2.2482 | 2.4756 | 2.5064 | 2.5441 | 2.5881 | 1.1622 | 1.4168 | 1.4408 | 1.4736 | 1.1622 | 1.3527 | 1.546 | 1.5675 | 1.5962 | 1.7049
2022-02-08 17:00 | 2.2863 | 2.5157 | 2.5461 | 2.5832 | 2.6266 | 1.467 | 1.7763 | 1.8 | 1.8323 | 1.467 | 1.5623 | 1.7782 | 1.7995 | 1.8278 | 1.9475
2022-02-08 18:00 | 2.2863 | 2.5193 | 2.5514 | 2.5908 | 2.6367 | 1.5302 | 1.8534 | 1.8785 | 1.9128 | 1.5302 | 1.8672 | 2.1195 | 2.142 | 2.172 | 2.3105
2022-02-08 19:00 | 2.3816 | 2.629 | 2.6649 | 2.7089 | 2.7602 | 1.6824 | 2.0386 | 2.0666 | 2.1049 | 1.6824 | 2.1529 | 2.4423 | 2.4675 | 2.5009 | 2.6593
2022-02-08 20:00 | 2.3816 | 2.6387 | 2.6796 | 2.7297 | 2.7881 | 1.7909 | 2.1739 | 2.2058 | 2.2494 | 1.7909 | 2.7817 | 3.1479 | 3.1766 | 3.2147 | 3.4131
2022-02-08 21:00 | 2.2482 | 2.5051 | 2.551 | 2.6071 | 2.6725 | 1.7276 | 2.1062 | 2.1419 | 2.1908 | 1.7276 | 2.2673 | 2.5831 | 2.6152 | 2.6579 | 2.8336
2022-02-08 22:00 | 2.0577 | 2.302 | 2.3487 | 2.4059 | 2.4725 | 1.5814 | 1.9345 | 1.971 | 2.0207 | 1.5814 | 2.0767 | 2.3725 | 2.4052 | 2.4487 | 2.6148
2022-02-08 23:00 | 1.8862 | 2.1119 | 2.1555 | 2.2089 | 2.2712 | 1.3337 | 1.6376 | 1.6717 | 1.7181 | 1.3337 | 1.9624 | 2.2413 | 2.2719 | 2.3125 | 2.469
2022-02-09 | 1.6957 | 1.8987 | 1.9381 | 1.9862 | 2.0424 | 1.1118 | 1.3694 | 1.4001 | 1.442 | 1.1118 | 1.5052 | 1.7272 | 1.7547 | 1.7913 | 1.9179
2022-02-09 01:00 | 1.5242 | 1.7051 | 1.7396 | 1.7818 | 1.8311 | 1.034 | 1.2705 | 1.2975 | 1.3342 | 1.034 | 1.3146 | 1.5087 | 1.5329 | 1.565 | 1.6757
2022-02-09 02:00 | 1.4861 | 1.6546 | 1.6842 | 1.7204 | 1.7627 | 0.96853 | 1.1863 | 1.2094 | 1.2409 | 0.96853 | 1.1813 | 1.3538 | 1.3745 | 1.4021 | 1.5
2022-02-09 03:00 | 1.467 | 1.622 | 1.6455 | 1.6742 | 1.7076 | 0.95263 | 1.1587 | 1.177 | 1.202 | 0.95263 | 1.3337 | 1.5146 | 1.531 | 1.5528 | 1.6523
2022-02-09 04:00 | 1.448 | 1.5897 | 1.6071 | 1.6284 | 1.6533 | 0.96883 | 1.1693 | 1.1829 | 1.2014 | 0.96883 | 1.2384 | 1.4003 | 1.4125 | 1.4287 | 1.5162
2022-02-09 05:00 | 1.6344 | 1.7799 | 1.7922 | 1.8072 | 1.8247 | 1.0633 | 1.2736 | 1.2831 | 1.2962 | 1.0633 | 1.3337 | 1.4991 | 1.5077 | 1.5191 | 1.606
2022-02-09 06:00 | 1.6957 | 1.8418 | 1.852 | 1.8645 | 1.8791 | 1.3146 | 1.5676 | 1.5756 | 1.5865 | 1.3146 | 1.5433 | 1.7291 | 1.7363 | 1.7458 | 1.8421
2022-02-09 07:00 | 1.9815 | 2.1521 | 2.1641 | 2.1787 | 2.1957 | 1.4289 | 1.7051 | 1.7144 | 1.7271 | 1.4289 | 2.0005 | 2.2396 | 2.248 | 2.2591 | 2.3824
2022-02-09 08:00 | 1.9815 | 2.1612 | 2.1778 | 2.1981 | 2.2218 | 1.4099 | 1.6892 | 1.7021 | 1.7197 | 1.4099 | 1.448 | 1.6321 | 1.6437 | 1.6591 | 1.7572
2022-02-09 09:00 | 1.9434 | 2.1336 | 2.157 | 2.1857 | 2.2191 | 1.0696 | 1.2969 | 1.3151 | 1.3401 | 1.0696 | 1.2003 | 1.3663 | 1.3827 | 1.4045 | 1.4965
2022-02-09 10:00 | 1.467 | 1.6362 | 1.6668 | 1.7044 | 1.7482 | 0.724 | 0.89892 | 0.92284 | 0.95551 | 0.724 | 1.9434 | 2.2021 | 2.2236 | 2.2522 | 2.3931
2022-02-09 11:00 | 1.6004 | 1.7904 | 1.8266 | 1.871 | 1.9228 | 0.53347 | 0.68178 | 0.71007 | 0.74869 | 0.53347 | 1.9243 | 2.1887 | 2.2141 | 2.2479 | 2.394
2022-02-09 12:00 | 2.2291 | 2.4702 | 2.5087 | 2.5558 | 2.6107 | 1.0669 | 1.3152 | 1.3452 | 1.3862 | 1.0669 | 1.7338 | 1.98 | 2.007 | 2.0428 | 2.181
2022-02-09 13:00 | 2.1529 | 2.3873 | 2.4252 | 2.4717 | 2.5258 | 1.0288 | 1.2694 | 1.299 | 1.3394 | 1.0288 | 2.0005 | 2.2757 | 2.3023 | 2.3376 | 2.4898
2022-02-09 14:00 | 2.3054 | 2.546 | 2.5814 | 2.6248 | 2.6753 | 1.0288 | 1.2658 | 1.2934 | 1.3311 | 1.0288 | 1.7528 | 1.9969 | 2.0217 | 2.0547 | 2.1905
2022-02-09 15:00 | 2.2291 | 2.4588 | 2.4914 | 2.5313 | 2.5779 | 1.0098 | 1.2393 | 1.2648 | 1.2995 | 1.0098 | 1.5814 | 1.8026 | 1.8254 | 1.8558 | 1.9791
2022-02-09 16:00 | 2.534 | 2.7827 | 2.8135 | 2.8512 | 2.8951 | 1.3718 | 1.6644 | 1.6884 | 1.7212 | 1.3718 | 1.3146 | 1.5036 | 1.5252 | 1.5539 | 1.6604
2022-02-09 17:00 | 2.4578 | 2.6999 | 2.7303 | 2.7675 | 2.8108 | 1.608 | 1.9428 | 1.9665 | 1.9988 | 1.608 | 1.6119 | 1.8334 | 1.8547 | 1.8829 | 2.0053
2022-02-09 18:00 | 2.4768 | 2.7239 | 2.7561 | 2.7955 | 2.8414 | 1.7338 | 2.094 | 2.1191 | 2.1533 | 1.7338 | 2.3816 | 2.6912 | 2.7137 | 2.7437 | 2.9104
2022-02-09 19:00 | 2.4578 | 2.7108 | 2.7468 | 2.7908 | 2.842 | 1.8209 | 2.2022 | 2.2303 | 2.2685 | 1.8209 | 2.6864 | 3.0351 | 3.0603 | 3.0938 | 3.2814
2022-02-09 20:00 | 2.534 | 2.8025 | 2.8434 | 2.8935 | 2.9519 | 1.9053 | 2.309 | 2.3409 | 2.3845 | 1.9053 | 2.6864 | 3.042 | 3.0707 | 3.1088 | 3.302
2022-02-09 21:00 | 2.3435 | 2.6074 | 2.6533 | 2.7094 | 2.7749 | 1.8672 | 2.271 | 2.3067 | 2.3556 | 1.8672 | 2.4197 | 2.7525 | 2.7846 | 2.8273 | 3.0114
2022-02-09 22:00 | 2.172 | 2.4249 | 2.4715 | 2.5287 | 2.5953 | 1.6399 | 2.0037 | 2.0402 | 2.0899 | 1.6399 | 2.3435 | 2.6689 | 2.7017 | 2.7451 | 2.9259
2022-02-09 23:00 | 1.9243 | 2.1528 | 2.1965 | 2.2499 | 2.3122 | 1.3718 | 1.6826 | 1.7167 | 1.7632 | 1.3718 | 1.7528 | 2.0084 | 2.039 | 2.0796 | 2.2245
2022-02-10 | 1.7926 | 2.0029 | 2.0422 | 2.0903 | 2.1465 | 1.1693 | 1.4373 | 1.468 | 1.5098 | 1.1693 | 1.5814 | 1.8118 | 1.8394 | 1.876 | 2.0067
2022-02-10 01:00 | 1.6218 | 1.8099 | 1.8444 | 1.8867 | 1.9359 | 1.086 | 1.332 | 1.3589 | 1.3957 | 1.086 | 1.4099 | 1.6146 | 1.6388 | 1.6709 | 1.7868
2022-02-10 02:00 | 1.6004 | 1.7774 | 1.807 | 1.8432 | 1.8855 | 1.0036 | 1.2277 | 1.2508 | 1.2823 | 1.0036 | 1.2575 | 1.4384 | 1.4592 | 1.4868 | 1.5889
2022-02-10 03:00 | 1.5814 | 1.7448 | 1.7683 | 1.797 | 1.8304 | 0.97241 | 1.1821 | 1.2004 | 1.2254 | 0.97241 | 1.3718 | 1.5569 | 1.5733 | 1.5952 | 1.6967
2022-02-10 04:00 | 1.5814 | 1.733 | 1.7504 | 1.7717 | 1.7966 | 0.99073 | 1.1952 | 1.2087 | 1.2273 | 0.99073 | 1.2765 | 1.4427 | 1.4549 | 1.4711 | 1.5606
2022-02-10 05:00 | 1.6957 | 1.8457 | 1.858 | 1.873 | 1.8905 | 1.0539 | 1.2625 | 1.2721 | 1.2851 | 1.0539 | 1.3337 | 1.4991 | 1.5077 | 1.5191 | 1.606
2022-02-10 06:00 | 1.7528 | 1.9032 | 1.9134 | 1.9259 | 1.9405 | 1.2358 | 1.4744 | 1.4824 | 1.4933 | 1.2358 | 1.4861 | 1.6656 | 1.6728 | 1.6823 | 1.7754
2022-02-10 07:00 | 1.9624 | 2.1317 | 2.1436 | 2.1582 | 2.1752 | 1.2765 | 1.525 | 1.5343 | 1.547 | 1.2765 | 1.6004 | 1.795 | 1.8034 | 1.8145 | 1.9158
2022-02-10 08:00 | 1.9053 | 2.0794 | 2.0959 | 2.1162 | 2.1399 | 1.1813 | 1.4191 | 1.432 | 1.4496 | 1.1813 | 1.2003 | 1.3568 | 1.3685 | 1.3839 | 1.4683
2022-02-10 09:00 | 1.9434 | 2.1336 | 2.157 | 2.1857 | 2.2191 | 1.0479 | 1.2712 | 1.2895 | 1.3144 | 1.0479 | 0.99073 | 1.1334 | 1.1498 | 1.1716 | 1.2521
2022-02-10 10:00 | 1.9434 | 2.1479 | 2.1786 | 2.2161 | 2.2599 | 0.80021 | 0.98895 | 1.0129 | 1.0455 | 0.80021 | 1.467 | 1.6728 | 1.6943 | 1.7229 | 1.8377
2022-02-10 11:00 | 2.4197 | 2.6705 | 2.7068 | 2.7512 | 2.803 | 1.1432 | 1.402 | 1.4303 | 1.4689 | 1.1432 | 1.6576 | 1.8923 | 1.9177 | 1.9514 | 2.0829
2022-02-10 12:00 | 1.9434 | 2.1632 | 2.2016 | 2.2488 | 2.3037 | 0.68589 | 0.865 | 0.89502 | 0.936 | 0.68589 | 1.7719 | 2.0224 | 2.0494 | 2.0852 | 2.2254
2022-02-10 13:00 | 2.4387 | 2.6943 | 2.7323 | 2.7787 | 2.8329 | 1.2194 | 1.4945 | 1.5241 | 1.5645 | 1.2194 | 1.448 | 1.6617 | 1.6883 | 1.7236 | 1.8455
2022-02-10 14:00 | 2.7934 | 3.0704 | 3.1058 | 3.1491 | 3.1996 | 1.467 | 1.7834 | 1.8111 | 1.8487 | 1.467 | 1.2384 | 1.4253 | 1.4501 | 1.483 | 1.5905
2022-02-10 15:00 | 2.915 | 3.1956 | 3.2283 | 3.2682 | 3.3148 | 1.6576 | 2.0046 | 2.03 | 2.0648 | 1.6576 | 1.6004 | 1.8237 | 1.8466 | 1.877 | 2.0013
2022-02-10 16:00 | 3.1437 | 3.4377 | 3.4685 | 3.5062 | 3.5501 | 1.9815 | 2.3846 | 2.4086 | 2.4414 | 1.9815 | 2.4387 | 2.7528 | 2.7744 | 2.803 | 2.9714
2022-02-10 17:00 | 3.0103 | 3.2935 | 3.3239 | 3.3611 | 3.4044 | 2.0196 | 2.429 | 2.4527 | 2.485 | 2.0196 | 2.6674 | 3.0062 | 3.0275 | 3.0558 | 3.2362
2022-02-10 18:00 | 2.915 | 3.1947 | 3.2269 | 3.2663 | 3.3122 | 2.0196 | 2.4316 | 2.4567 | 2.4909 | 2.0196 | 2.8388 | 3.1993 | 3.2218 | 3.2518 | 3.4437
2022-02-10 19:00 | 2.6674 | 2.936 | 2.9719 | 3.0159 | 3.0672 | 1.9815 | 2.3919 | 2.4199 | 2.4582 | 1.9815 | 2.7055 | 3.0563 | 3.0815 | 3.1149 | 3.3037
2022-02-10 20:00 | 2.5721 | 2.8434 | 2.8843 | 2.9344 | 2.9928 | 2.0005 | 2.4215 | 2.4534 | 2.497 | 2.0005 | 2.9531 | 3.3384 | 3.3671 | 3.4052 | 3.6131
2022-02-10 21:00 | 2.4387 | 2.7098 | 2.7557 | 2.8118 | 2.8772 | 1.8862 | 2.2935 | 2.3293 | 2.3781 | 1.8862 | 2.5721 | 2.9219 | 2.954 | 2.9967 | 3.1891
2022-02-10 22:00 | 2.3054 | 2.5681 | 2.6148 | 2.672 | 2.7386 | 1.6778 | 2.0485 | 2.0849 | 2.1346 | 1.6778 | 2.191 | 2.4996 | 2.5323 | 2.5757 | 2.7482
2022-02-10 23:00 | 2.0577 | 2.2961 | 2.3397 | 2.3932 | 2.4555 | 1.3846 | 1.6978 | 1.7318 | 1.7783 | 1.3846 | 1.9243 | 2.1989 | 2.2295 | 2.2701 | 2.4245
2022-02-11 | 1.81 | 2.0215 | 2.0609 | 2.109 | 2.1652 | 1.2343 | 1.514 | 1.5447 | 1.5866 | 1.2343 | 1.6385 | 1.8754 | 1.9029 | 1.9395 | 2.0734
2022-02-11 01:00 | 1.7338 | 1.9302 | 1.9647 | 2.007 | 2.0562 | 1.105 | 1.3545 | 1.3814 | 1.4182 | 1.105 | 1.448 | 1.6569 | 1.6811 | 1.7133 | 1.8313
2022-02-11 02:00 | 1.6957 | 1.8797 | 1.9093 | 1.9456 | 1.9879 | 1.0428 | 1.274 | 1.2971 | 1.3287 | 1.0428 | 1.3718 | 1.5655 | 1.5862 | 1.6138 | 1.7222
2022-02-11 03:00 | 1.6385 | 1.8062 | 1.8297 | 1.8584 | 1.8918 | 0.97814 | 1.1889 | 1.2072 | 1.2321 | 0.97814 | 1.467 | 1.6628 | 1.6792 | 1.701 | 1.8078
2022-02-11 04:00 | 1.6304 | 1.7856 | 1.803 | 1.8244 | 1.8492 | 0.97801 | 1.1801 | 1.1937 | 1.2122 | 0.97801 | 1.3718 | 1.5485 | 1.5607 | 1.5769 | 1.6717
2022-02-11 05:00 | 1.7147 | 1.8662 | 1.8785 | 1.8935 | 1.911 | 1.0986 | 1.3152 | 1.3248 | 1.3379 | 1.0986 | 1.448 | 1.6261 | 1.6347 | 1.6461 | 1.7393
2022-02-11 06:00 | 1.858 | 2.0162 | 2.0264 | 2.0389 | 2.0535 | 1.2956 | 1.5451 | 1.5531 | 1.564 | 1.2956 | 1.5052 | 1.6868 | 1.694 | 1.7035 | 1.7976
2022-02-11 07:00 | 2.1274 | 2.3089 | 2.3209 | 2.3355 | 2.3525 | 1.4099 | 1.6826 | 1.6919 | 1.7046 | 1.4099 | 1.7338 | 1.9432 | 1.9516 | 1.9627 | 2.0713
2022-02-11 08:00 | 2.1339 | 2.325 | 2.3416 | 2.3619 | 2.3855 | 1.4099 | 1.6892 | 1.7021 | 1.7197 | 1.4099 | 1.6576 | 1.865 | 1.8766 | 1.892 | 2.0016
2022-02-11 09:00 | 2.1339 | 2.3383 | 2.3617 | 2.3904 | 2.4238 | 1.2035 | 1.455 | 1.4733 | 1.4982 | 1.2035 | 1.2003 | 1.3663 | 1.3827 | 1.4045 | 1.4965
2022-02-11 10:00 | 1.9624 | 2.1684 | 2.199 | 2.2366 | 2.2804 | 1.1241 | 1.3716 | 1.3955 | 1.4282 | 1.1241 | 1.5242 | 1.7363 | 1.7578 | 1.7864 | 1.9043
2022-02-11 11:00 | 2.0196 | 2.2407 | 2.277 | 2.3213 | 2.3731 | 1.0098 | 1.2445 | 1.2728 | 1.3114 | 1.0098 | 1.9243 | 2.1887 | 2.2141 | 2.2479 | 2.394
2022-02-11 12:00 | 2.2291 | 2.4702 | 2.5087 | 2.5558 | 2.6107 | 1.1813 | 1.4502 | 1.4802 | 1.5212 | 1.1813 | 1.5623 | 1.7895 | 1.8165 | 1.8523 | 1.981
2022-02-11 13:00 | 1.5433 | 1.7323 | 1.7702 | 1.8167 | 1.8708 | 0.66684 | 0.84173 | 0.87133 | 0.91174 | 0.66684 | 1.81 | 2.064 | 2.0906 | 2.1259 | 2.2676
2022-02-11 14:00 | 2.191 | 2.4232 | 2.4586 | 2.502 | 2.5525 | 1.2384 | 1.5133 | 1.541 | 1.5787 | 1.2384 | 1.6766 | 1.9123 | 1.9371 | 1.97 | 2.1016
2022-02-11 15:00 | 2.534 | 2.7863 | 2.8189 | 2.8588 | 2.9054 | 1.2575 | 1.5319 | 1.5574 | 1.5921 | 1.2575 | 1.2575 | 1.4426 | 1.4655 | 1.4959 | 1.6013
2022-02-11 16:00 | 2.4039 | 2.6429 | 2.6737 | 2.7114 | 2.7553 | 1.3337 | 1.6193 | 1.6434 | 1.6762 | 1.3337 | 0.74305 | 0.86844 | 0.89002 | 0.9187 | 0.99384
2022-02-11 17:00 | 2.25 | 2.4767 | 2.507 | 2.5442 | 2.5875 | 1.5242 | 1.8438 | 1.8675 | 1.8998 | 1.5242 | 1.7719 | 2.0111 | 2.0324 | 2.0607 | 2.1919
2022-02-11 18:00 | 2.3816 | 2.6216 | 2.6538 | 2.6932 | 2.7391 | 1.6957 | 2.0489 | 2.074 | 2.1083 | 1.6957 | 2.4578 | 2.7758 | 2.7984 | 2.8283 | 2.9993
2022-02-11 19:00 | 2.2482 | 2.4857 | 2.5216 | 2.5656 | 2.6169 | 1.6576 | 2.0093 | 2.0373 | 2.0756 | 1.6576 | 2.4768 | 2.8022 | 2.8274 | 2.8609 | 3.037
2022-02-11 20:00 | 2.3244 | 2.5773 | 2.6182 | 2.6683 | 2.7267 | 1.7719 | 2.1514 | 2.1833 | 2.2269 | 1.7719 | 2.3054 | 2.6186 | 2.6473 | 2.6853 | 2.8576
2022-02-11 21:00 | 2.2482 | 2.5051 | 2.551 | 2.6071 | 2.6725 | 1.6576 | 2.0234 | 2.0592 | 2.108 | 1.6576 | 2.0958 | 2.3925 | 2.4247 | 2.4674 | 2.6336
2022-02-11 22:00 | 2.0958 | 2.343 | 2.3897 | 2.4468 | 2.5135 | 1.5152 | 1.8564 | 1.8928 | 1.9425 | 1.5152 | 1.9624 | 2.2455 | 2.2782 | 2.3217 | 2.4815
2022-02-11 23:00 | 1.8931 | 2.1193 | 2.1629 | 2.2164 | 2.2787 | 1.3337 | 1.6376 | 1.6717 | 1.7181 | 1.3337 | 1.8672 | 2.1354 | 2.166 | 2.2066 | 2.3579
2022-02-12 | 1.7528 | 1.9601 | 1.9995 | 2.0476 | 2.1038 | 1.1747 | 1.4437 | 1.4744 | 1.5163 | 1.1747 | 1.5623 | 1.7907 | 1.8182 | 1.8549 | 1.9845
2022-02-12 01:00 | 1.7338 | 1.9302 | 1.9647 | 2.007 | 2.0562 | 1.086 | 1.332 | 1.3589 | 1.3957 | 1.086 | 1.3337 | 1.5299 | 1.5541 | 1.5862 | 1.698
2022-02-12 02:00 | 1.6004 | 1.7774 | 1.807 | 1.8432 | 1.8855 | 1.0018 | 1.2256 | 1.2487 | 1.2802 | 1.0018 | 1.4099 | 1.6078 | 1.6286 | 1.6561 | 1.7666
2022-02-12 03:00 | 1.5623 | 1.7244 | 1.7478 | 1.7765 | 1.81 | 0.9599 | 1.1673 | 1.1856 | 1.2106 | 0.9599 | 1.4289 | 1.6204 | 1.6369 | 1.6587 | 1.7634
2022-02-12 04:00 | 1.5814 | 1.733 | 1.7504 | 1.7717 | 1.7966 | 0.95263 | 1.1501 | 1.1637 | 1.1823 | 0.95263 | 1.2575 | 1.4215 | 1.4337 | 1.4499 | 1.5384
2022-02-12 05:00 | 1.6004 | 1.7434 | 1.7557 | 1.7707 | 1.7882 | 0.99073 | 1.1878 | 1.1974 | 1.2105 | 0.99073 | 1.3908 | 1.5626 | 1.5712 | 1.5826 | 1.6727
2022-02-12 06:00 | 1.6004 | 1.7394 | 1.7497 | 1.7622 | 1.7768 | 1.0647 | 1.2723 | 1.2803 | 1.2912 | 1.0647 | 1.467 | 1.6445 | 1.6516 | 1.6611 | 1.7532
2022-02-12 07:00 | 1.6004 | 1.7428 | 1.7547 | 1.7693 | 1.7863 | 1.1624 | 1.3902 | 1.3995 | 1.4122 | 1.1624 | 1.2765 | 1.4351 | 1.4435 | 1.4546 | 1.538
2022-02-12 08:00 | 1.5052 | 1.6495 | 1.6661 | 1.6864 | 1.71 | 1.1813 | 1.4191 | 1.432 | 1.4496 | 1.1813 | 1.105 | 1.251 | 1.2626 | 1.278 | 1.3572
2022-02-12 09:00 | 1.3718 | 1.5196 | 1.543 | 1.5716 | 1.605 | 0.88883 | 1.0833 | 1.1015 | 1.1265 | 0.88883 | 1.0098 | 1.1546 | 1.171 | 1.1928 | 1.2743
2022-02-12 10:00 | 1.6576 | 1.8408 | 1.8715 | 1.9091 | 1.9528 | 1.1813 | 1.4391 | 1.463 | 1.4957 | 1.1813 | 1.4099 | 1.6093 | 1.6308 | 1.6593 | 1.771
2022-02-12 11:00 | 1.637 | 1.8297 | 1.8659 | 1.9103 | 1.9621 | 1.0985 | 1.3493 | 1.3776 | 1.4162 | 1.0985 | 1.5623 | 1.7864 | 1.8118 | 1.8456 | 1.9718
2022-02-12 12:00 | 1.6385 | 1.8357 | 1.8741 | 1.9212 | 1.9762 | 0.97168 | 1.2026 | 1.2326 | 1.2736 | 0.97168 | 1.0479 | 1.2178 | 1.2448 | 1.2806 | 1.3811
2022-02-12 13:00 | 1.81 | 2.0188 | 2.0568 | 2.1032 | 2.1574 | 1.2194 | 1.4945 | 1.5241 | 1.5645 | 1.2194 | 1.0669 | 1.2383 | 1.2649 | 1.3002 | 1.4011
2022-02-12 14:00 | 1.829 | 2.0343 | 2.0697 | 2.113 | 2.1636 | 1.2003 | 1.4683 | 1.4959 | 1.5336 | 1.2003 | 1.2956 | 1.4888 | 1.5136 | 1.5466 | 1.6572
2022-02-12 15:00 | 1.8672 | 2.0698 | 2.1025 | 2.1424 | 2.189 | 1.2003 | 1.4644 | 1.4899 | 1.5246 | 1.2003 | 1.4289 | 1.6332 | 1.656 | 1.6864 | 1.8013
2022-02-12 16:00 | 1.9624 | 2.1686 | 2.1994 | 2.2371 | 2.2811 | 1.2956 | 1.5743 | 1.5984 | 1.6312 | 1.2956 | 1.448 | 1.6518 | 1.6734 | 1.7021 | 1.816
2022-02-12 17:00 | 2.0767 | 2.2906 | 2.3209 | 2.3581 | 2.4014 | 1.5623 | 1.8888 | 1.9125 | 1.9448 | 1.5623 | 1.4289 | 1.63 | 1.6513 | 1.6796 | 1.7919
2022-02-12 18:00 | 1.9815 | 2.1918 | 2.2239 | 2.2633 | 2.3092 | 1.6004 | 1.9364 | 1.9615 | 1.9958 | 1.6004 | 1.9053 | 2.1618 | 2.1844 | 2.2143 | 2.3549
2022-02-12 19:00 | 2.1339 | 2.3629 | 2.3988 | 2.4428 | 2.4941 | 1.6509 | 2.0014 | 2.0294 | 2.0677 | 1.6509 | 2.2101 | 2.5058 | 2.531 | 2.5644 | 2.7259
2022-02-12 20:00 | 2.2101 | 2.4545 | 2.4954 | 2.5455 | 2.6039 | 1.6766 | 2.0389 | 2.0708 | 2.1144 | 1.6766 | 2.1529 | 2.4492 | 2.4779 | 2.516 | 2.6799
2022-02-12 21:00 | 2.1148 | 2.3618 | 2.4077 | 2.4638 | 2.5293 | 1.6195 | 1.9784 | 2.0141 | 2.063 | 1.6195 | 2.5911 | 2.943 | 2.9752 | 3.0178 | 3.2113
2022-02-12 22:00 | 2.1148 | 2.3635 | 2.4101 | 2.4673 | 2.5339 | 1.5825 | 1.9358 | 1.9723 | 2.022 | 1.5825 | 1.9624 | 2.2455 | 2.2782 | 2.3217 | 2.4815
2022-02-12 23:00 | 1.9491 | 2.1794 | 2.2231 | 2.2765 | 2.3388 | 1.3908 | 1.7051 | 1.7392 | 1.7857 | 1.3908 | 1.6957 | 1.9449 | 1.9754 | 2.0161 | 2.1579
2022-02-13 | 1.7239 | 1.929 | 1.9684 | 2.0165 | 2.0727 | 1.2028 | 1.4768 | 1.5075 | 1.5494 | 1.2028 | 1.7338 | 1.9812 | 2.0088 | 2.0454 | 2.1845
2022-02-13 01:00 | 1.6576 | 1.8483 | 1.8829 | 1.9251 | 1.9743 | 1.0926 | 1.3398 | 1.3667 | 1.4034 | 1.0926 | 1.5433 | 1.7628 | 1.787 | 1.8191 | 1.9424
2022-02-13 02:00 | 1.5914 | 1.7677 | 1.7973 | 1.8336 | 1.8758 | 1.0206 | 1.2478 | 1.2709 | 1.3024 | 1.0206 | 1.3908 | 1.5866 | 1.6074 | 1.635 | 1.7444
2022-02-13 03:00 | 1.5433 | 1.7039 | 1.7273 | 1.756 | 1.7895 | 0.9514 | 1.1573 | 1.1756 | 1.2005 | 0.9514 | 1.3146 | 1.4934 | 1.5098 | 1.5317 | 1.63
2022-02-13 04:00 | 1.5433 | 1.6921 | 1.7095 | 1.7308 | 1.7556 | 0.95263 | 1.1501 | 1.1637 | 1.1823 | 0.95263 | 1.3718 | 1.5485 | 1.5607 | 1.5769 | 1.6717
2022-02-13 05:00 | 1.5433 | 1.682 | 1.6942 | 1.7093 | 1.7268 | 0.99531 | 1.1932 | 1.2028 | 1.2159 | 0.99531 | 1.3527 | 1.5202 | 1.5288 | 1.5402 | 1.6282
2022-02-13 06:00 | 1.5623 | 1.6985 | 1.7087 | 1.7212 | 1.7358 | 1.0479 | 1.2525 | 1.2605 | 1.2714 | 1.0479 | 1.3337 | 1.4962 | 1.5034 | 1.5129 | 1.5977
2022-02-13 07:00 | 1.5052 | 1.6404 | 1.6523 | 1.667 | 1.684 | 1.0669 | 1.2774 | 1.2867 | 1.2994 | 1.0669 | 1.3337 | 1.4986 | 1.507 | 1.5181 | 1.6047
2022-02-13 08:00 | 1.5668 | 1.7157 | 1.7323 | 1.7526 | 1.7762 | 1.1552 | 1.3882 | 1.4012 | 1.4188 | 1.1552 | 1.0669 | 1.2086 | 1.2203 | 1.2357 | 1.3128
2022-02-13 09:00 | 1.6766 | 1.8471 | 1.8705 | 1.8991 | 1.9325 | 1.2194 | 1.4738 | 1.492 | 1.5169 | 1.2194 | 1.2575 | 1.4298 | 1.4462 | 1.468 | 1.5632
2022-02-13 10:00 | 1.5242 | 1.6976 | 1.7282 | 1.7658 | 1.8096 | 1.0288 | 1.259 | 1.283 | 1.3156 | 1.0288 | 1.0479 | 1.207 | 1.2285 | 1.2571 | 1.3488
2022-02-13 11:00 | 1.467 | 1.6471 | 1.6834 | 1.7277 | 1.7795 | 0.93358 | 1.1544 | 1.1827 | 1.2214 | 0.93358 | 1.0098 | 1.1724 | 1.1978 | 1.2316 | 1.3275
2022-02-13 12:00 | 1.5623 | 1.7538 | 1.7923 | 1.8394 | 1.8943 | 0.88084 | 1.0953 | 1.1253 | 1.1663 | 0.88084 | 1.2575 | 1.4507 | 1.4777 | 1.5135 | 1.6255
2022-02-13 13:00 | 1.1432 | 1.3024 | 1.3404 | 1.3868 | 1.441 | 0.78115 | 0.97678 | 1.0064 | 1.0468 | 0.78115 | 1.7909 | 2.0428 | 2.0694 | 2.1047 | 2.2454
2022-02-13 14:00 | 1.2575 | 1.4202 | 1.4556 | 1.499 | 1.5495 | 0.80021 | 0.99566 | 1.0233 | 1.061 | 0.80021 | 1.3337 | 1.5312 | 1.556 | 1.5889 | 1.7016
2022-02-13 15:00 | 1.6385 | 1.8242 | 1.8569 | 1.8968 | 1.9434 | 0.80021 | 0.99174 | 1.0172 | 1.0519 | 0.80021 | 1.2956 | 1.485 | 1.5078 | 1.5382 | 1.6458
2022-02-13 16:00 | 2.0767 | 2.2914 | 2.3222 | 2.3599 | 2.4039 | 1.3146 | 1.5968 | 1.6209 | 1.6537 | 1.3146 | 0.91452 | 1.059 | 1.0806 | 1.1092 | 1.1938
2022-02-13 17:00 | 2.1513 | 2.3707 | 2.4011 | 2.4382 | 2.4816 | 1.5825 | 1.9126 | 1.9363 | 1.9687 | 1.5825 | 1.6576 | 1.8841 | 1.9054 | 1.9336 | 2.0586
2022-02-13 18:00 | 2.4768 | 2.7239 | 2.7561 | 2.7955 | 2.8414 | 1.8623 | 2.2458 | 2.2709 | 2.3051 | 1.8623 | 2.4959 | 2.8182 | 2.8407 | 2.8707 | 3.0437
2022-02-13 19:00 | 2.4578 | 2.7108 | 2.7468 | 2.7908 | 2.842 | 2.0005 | 2.4144 | 2.4424 | 2.4807 | 2.0005 | 2.7055 | 3.0563 | 3.0815 | 3.1149 | 3.3037
2022-02-13 20:00 | 2.5149 | 2.782 | 2.8229 | 2.873 | 2.9314 | 1.9243 | 2.3315 | 2.3634 | 2.407 | 1.9243 | 2.4578 | 2.788 | 2.8166 | 2.8547 | 3.0354
2022-02-13 21:00 | 2.4006 | 2.6689 | 2.7147 | 2.7708 | 2.8363 | 1.81 | 2.2035 | 2.2392 | 2.2881 | 1.81 | 2.5149 | 2.8583 | 2.8905 | 2.9332 | 3.1225
2022-02-13 22:00 | 2.2101 | 2.4658 | 2.5125 | 2.5696 | 2.6363 | 1.5814 | 1.9345 | 1.971 | 2.0207 | 1.5814 | 2.0767 | 2.3725 | 2.4052 | 2.4487 | 2.6148
2022-02-13 23:00 | 1.9624 | 2.1937 | 2.2374 | 2.2908 | 2.3531 | 1.3594 | 1.668 | 1.702 | 1.7485 | 1.3594 | 1.7147 | 1.966 | 1.9966 | 2.0373 | 2.1801
2022-02-14 | 1.7719 | 1.9806 | 2.0199 | 2.0681 | 2.1242 | 1.1432 | 1.4064 | 1.4371 | 1.479 | 1.1432 | 1.5814 | 1.8118 | 1.8394 | 1.876 | 2.0067
2022-02-14 01:00 | 1.7147 | 1.9098 | 1.9443 | 1.9865 | 2.0358 | 1.086 | 1.332 | 1.3589 | 1.3957 | 1.086 | 1.3908 | 1.5934 | 1.6176 | 1.6497 | 1.7646
2022-02-14 02:00 | 1.5814 | 1.7569 | 1.7865 | 1.8228 | 1.865 | 1.0299 | 1.2587 | 1.2818 | 1.3134 | 1.0299 | 1.3527 | 1.5443 | 1.5651 | 1.5926 | 1.7
2022-02-14 03:00 | 1.6004 | 1.7653 | 1.7887 | 1.8174 | 1.8509 | 0.97272 | 1.1825 | 1.2008 | 1.2257 | 0.97272 | 1.2384 | 1.4087 | 1.4251 | 1.447 | 1.5412
2022-02-14 04:00 | 1.5814 | 1.733 | 1.7504 | 1.7717 | 1.7966 | 1.0098 | 1.2177 | 1.2312 | 1.2498 | 1.0098 | 1.2575 | 1.4215 | 1.4337 | 1.4499 | 1.5384
2022-02-14 05:00 | 1.6385 | 1.7843 | 1.7966 | 1.8116 | 1.8291 | 1.0729 | 1.2849 | 1.2945 | 1.3076 | 1.0729 | 1.3718 | 1.5414 | 1.55 | 1.5614 | 1.6505
2022-02-14 06:00 | 1.8009 | 1.9548 | 1.965 | 1.9775 | 1.9921 | 1.2284 | 1.4657 | 1.4737 | 1.4846 | 1.2284 | 1.467 | 1.6445 | 1.6516 | 1.6611 | 1.7532
2022-02-14 07:00 | 1.9815 | 2.1521 | 2.1641 | 2.1787 | 2.1957 | 1.3527 | 1.615 | 1.6243 | 1.637 | 1.3527 | 1.5814 | 1.7739 | 1.7822 | 1.7933 | 1.8935
2022-02-14 08:00 | 1.9144 | 2.0891 | 2.1057 | 2.126 | 2.1497 | 1.3337 | 1.5991 | 1.6121 | 1.6297 | 1.3337 | 1.1813 | 1.3357 | 1.3473 | 1.3627 | 1.4461
2022-02-14 09:00 | 1.8672 | 2.0518 | 2.0752 | 2.1038 | 2.1372 | 0.97168 | 1.1812 | 1.1994 | 1.2243 | 0.97168 | 1.1241 | 1.2816 | 1.298 | 1.3198 | 1.4076
2022-02-14 10:00 | 1.7909 | 1.9841 | 2.0148 | 2.0524 | 2.0961 | 0.83831 | 1.034 | 1.0579 | 1.0906 | 0.83831 | 1.3146 | 1.5034 | 1.5249 | 1.5535 | 1.6599
2022-02-14 11:00 | 1.9053 | 2.1179 | 2.1541 | 2.1985 | 2.2503 | 0.78115 | 0.97439 | 1.0027 | 1.0413 | 0.78115 | 1.467 | 1.6806 | 1.706 | 1.7397 | 1.8607
2022-02-14 12:00 | 1.81 | 2.0199 | 2.0584 | 2.1055 | 2.1604 | 0.60968 | 0.77497 | 0.80499 | 0.84597 | 0.60968 | 1.6195 | 1.853 | 1.88 | 1.9158 | 2.0477
2022-02-14 13:00 | 1.8481 | 2.0598 | 2.0977 | 2.1442 | 2.1983 | 0.62873 | 0.79672 | 0.82631 | 0.86672 | 0.62873 | 1.5052 | 1.7252 | 1.7518 | 1.7871 | 1.9121
2022-02-14 14:00 | 2.2863 | 2.5256 | 2.561 | 2.6043 | 2.6548 | 1.0288 | 1.2658 | 1.2934 | 1.3311 | 1.0288 | 1.4099 | 1.6158 | 1.6406 | 1.6736 | 1.7905
2022-02-14 15:00 | 2.3435 | 2.5816 | 2.6142 | 2.6542 | 2.7007 | 1.0218 | 1.2535 | 1.279 | 1.3138 | 1.0218 | 0.95263 | 1.1039 | 1.1267 | 1.1571 | 1.2458
2022-02-14 16:00 | 2.7245 | 2.9874 | 3.0182 | 3.0559 | 3.0998 | 1.448 | 1.7544 | 1.7784 | 1.8112 | 1.448 | 1.2765 | 1.4613 | 1.4828 | 1.5115 | 1.616
2022-02-14 17:00 | 3.0865 | 3.3754 | 3.4058 | 3.4429 | 3.4863 | 1.9878 | 2.3915 | 2.4151 | 2.4475 | 1.9878 | 3.0675 | 3.4508 | 3.4721 | 3.5004 | 3.7028
2022-02-14 18:00 | 3.2199 | 3.5222 | 3.5544 | 3.5938 | 3.6397 | 2.3816 | 2.8592 | 2.8843 | 2.9186 | 2.3816 | 3.639 | 4.0885 | 4.1111 | 4.141 | 4.3769
2022-02-14 19:00 | 2.8979 | 3.1837 | 3.2196 | 3.2636 | 3.3149 | 2.3793 | 2.8619 | 2.8899 | 2.9282 | 2.3793 | 3.8677 | 4.3478 | 4.373 | 4.4064 | 4.6591
2022-02-14 20:00 | 2.7436 | 3.0276 | 3.0685 | 3.1186 | 3.177 | 2.1529 | 2.6016 | 2.6335 | 2.6771 | 2.1529 | 3.3342 | 3.7619 | 3.7906 | 3.8286 | 4.0575
2022-02-14 21:00 | 2.6102 | 2.894 | 2.9399 | 2.996 | 3.0614 | 2.0196 | 2.451 | 2.4868 | 2.5356 | 2.0196 | 3.3533 | 3.7899 | 3.822 | 3.8647 | 4.1001
2022-02-14 22:00 | 2.4006 | 2.6705 | 2.7172 | 2.7743 | 2.841 | 1.8179 | 2.2139 | 2.2503 | 2.3001 | 1.8179 | 2.221 | 2.5329 | 2.5656 | 2.6091 | 2.7831
2022-02-14 23:00 | 2.0958 | 2.337 | 2.3807 | 2.4341 | 2.4964 | 1.4534 | 1.779 | 1.8131 | 1.8595 | 1.4534 | 1.8481 | 2.1142 | 2.1448 | 2.1855 | 2.3356
2022-02-15 | 1.9243 | 2.1444 | 2.1837 | 2.2318 | 2.288 | 1.2983 | 1.5897 | 1.6204 | 1.6623 | 1.2983 | 1.7147 | 1.9601 | 1.9876 | 2.0242 | 2.1623
2022-02-15 01:00 | 1.6766 | 1.8688 | 1.9033 | 1.9456 | 1.9948 | 1.105 | 1.3545 | 1.3814 | 1.4182 | 1.105 | 1.3718 | 1.5723 | 1.5964 | 1.6286 | 1.7424
2022-02-15 02:00 | 1.6195 | 1.7978 | 1.8275 | 1.8637 | 1.906 | 1.086 | 1.3251 | 1.3482 | 1.3797 | 1.086 | 1.2765 | 1.4596 | 1.4804 | 1.5079 | 1.6111
2022-02-15 03:00 | 1.6385 | 1.8062 | 1.8297 | 1.8584 | 1.8918 | 1.0098 | 1.2263 | 1.2445 | 1.2695 | 1.0098 | 1.4289 | 1.6204 | 1.6369 | 1.6587 | 1.7634
2022-02-15 04:00 | 1.5769 | 1.7283 | 1.7457 | 1.767 | 1.7918 | 0.99872 | 1.2046 | 1.2182 | 1.2367 | 0.99872 | 1.3337 | 1.5062 | 1.5184 | 1.5346 | 1.6273
2022-02-15 05:00 | 1.6957 | 1.8457 | 1.858 | 1.873 | 1.8905 | 1.0669 | 1.2779 | 1.2874 | 1.3005 | 1.0669 | 1.3146 | 1.4779 | 1.4865 | 1.4979 | 1.5838
2022-02-15 06:00 | 1.829 | 1.9851 | 1.9953 | 2.0078 | 2.0224 | 1.2399 | 1.4793 | 1.4873 | 1.4982 | 1.2399 | 1.4861 | 1.6656 | 1.6728 | 1.6823 | 1.7754
2022-02-15 07:00 | 2.0005 | 2.1726 | 2.1845 | 2.1992 | 2.2162 | 1.3337 | 1.5925 | 1.6018 | 1.6145 | 1.3337 | 1.7719 | 1.9856 | 1.9939 | 2.005 | 2.1157
2022-02-15 08:00 | 2.0005 | 2.1817 | 2.1983 | 2.2186 | 2.2422 | 1.2575 | 1.5091 | 1.522 | 1.5397 | 1.2575 | 1.2956 | 1.4627 | 1.4743 | 1.4898 | 1.5794
2022-02-15 09:00 | 2.1148 | 2.3179 | 2.3413 | 2.3699 | 2.4033 | 1.5433 | 1.8564 | 1.8747 | 1.8996 | 1.5433 | 2.0577 | 2.3191 | 2.3354 | 2.3572 | 2.4964
2022-02-15 10:00 | 1.8862 | 2.0865 | 2.1171 | 2.1547 | 2.1985 | 0.724 | 0.89892 | 0.92284 | 0.95551 | 0.724 | 1.2575 | 1.4399 | 1.4614 | 1.49 | 1.5932
2022-02-15 11:00 | 1.8862 | 2.0974 | 2.1337 | 2.1781 | 2.2298 | 0.60968 | 0.77182 | 0.8001 | 0.83872 | 0.60968 | 1.4289 | 1.6382 | 1.6636 | 1.6974 | 1.8163
2022-02-15 12:00 | 2.0485 | 2.2762 | 2.3146 | 2.3617 | 2.4167 | 0.724 | 0.91002 | 0.94004 | 0.98102 | 0.724 | 1.5814 | 1.8107 | 1.8376 | 1.8735 | 2.0032
2022-02-15 13:00 | 2.2482 | 2.4896 | 2.5276 | 2.574 | 2.6282 | 0.83831 | 1.0443 | 1.0739 | 1.1143 | 0.83831 | 1.0669 | 1.2383 | 1.2649 | 1.3002 | 1.4011
2022-02-15 14:00 | 3.1056 | 3.4057 | 3.4411 | 3.4845 | 3.535 | 1.7528 | 2.1211 | 2.1487 | 2.1864 | 1.7528 | 1.6195 | 1.8487 | 1.8735 | 1.9065 | 2.0349
2022-02-15 15:00 | 3.3914 | 3.7074 | 3.74 | 3.7799 | 3.8265 | 1.9243 | 2.3197 | 2.3452 | 2.3799 | 1.9243 | 2.1148 | 2.3954 | 2.4182 | 2.4486 | 2.6012
2022-02-15 16:00 | 3.2961 | 3.6014 | 3.6322 | 3.6699 | 3.7139 | 2.1148 | 2.5422 | 2.5662 | 2.599 | 2.1148 | 2.3435 | 2.6469 | 2.6685 | 2.6972 | 2.8603
2022-02-15 17:00 | 3.3342 | 3.6415 | 3.6719 | 3.709 | 3.7524 | 2.3244 | 2.7891 | 2.8128 | 2.8452 | 2.3244 | 3.8867 | 4.3613 | 4.3825 | 4.4108 | 4.6583
2022-02-15 18:00 | 3.1246 | 3.4199 | 3.4521 | 3.4915 | 3.5374 | 2.3625 | 2.8367 | 2.8618 | 2.8961 | 2.3625 | 3.4104 | 3.8345 | 3.857 | 3.887 | 4.1103
2022-02-15 19:00 | 3.0764 | 3.3755 | 3.4114 | 3.4554 | 3.5067 | 2.3435 | 2.8196 | 2.8476 | 2.8859 | 2.3435 | 3.639 | 4.0937 | 4.1189 | 4.1524 | 4.3924
2022-02-15 20:00 | 2.915 | 3.2118 | 3.2528 | 3.3028 | 3.3612 | 2.2291 | 2.6916 | 2.7235 | 2.7671 | 2.2291 | 3.3342 | 3.7619 | 3.7906 | 3.8286 | 4.0575
2022-02-15 21:00 | 2.7055 | 2.9964 | 3.0422 | 3.0983 | 3.1638 | 2.1322 | 2.5841 | 2.6199 | 2.6687 | 2.1322 | 2.8769 | 3.2606 | 3.2927 | 3.3354 | 3.5446
2022-02-15 22:00 | 2.465 | 2.7397 | 2.7864 | 2.8435 | 2.9102 | 1.8481 | 2.2496 | 2.2861 | 2.3358 | 1.8481 | 2.3435 | 2.6689 | 2.7017 | 2.7451 | 2.9259
2022-02-15 23:00 | 2.1916 | 2.44 | 2.4836 | 2.5371 | 2.5994 | 1.5048 | 1.8398 | 1.8739 | 1.9203 | 1.5048 | 1.9624 | 2.2413 | 2.2719 | 2.3125 | 2.469
2022-02-16 | 2.0014 | 2.2272 | 2.2665 | 2.3147 | 2.3708 | 1.3017 | 1.5937 | 1.6244 | 1.6663 | 1.3017 | 1.7147 | 1.9601 | 1.9876 | 2.0242 | 2.1623
2022-02-16 01:00 | 1.829 | 2.0326 | 2.0671 | 2.1093 | 2.1586 | 1.1262 | 1.3795 | 1.4064 | 1.4431 | 1.1262 | 1.4059 | 1.6101 | 1.6343 | 1.6664 | 1.7821
2022-02-16 02:00 | 1.7528 | 1.9411 | 1.9707 | 2.007 | 2.0493 | 1.1241 | 1.3701 | 1.3932 | 1.4247 | 1.1241 | 1.6385 | 1.8619 | 1.8826 | 1.9102 | 2.0333
2022-02-16 03:00 | 1.6766 | 1.8472 | 1.8706 | 1.8993 | 1.9328 | 1.0357 | 1.2569 | 1.2751 | 1.3001 | 1.0357 | 1.448 | 1.6416 | 1.658 | 1.6799 | 1.7856
2022-02-16 04:00 | 1.6542 | 1.8113 | 1.8287 | 1.85 | 1.8748 | 1.0113 | 1.2194 | 1.233 | 1.2515 | 1.0113 | 1.4289 | 1.6121 | 1.6243 | 1.6405 | 1.7384
2022-02-16 05:00 | 1.7528 | 1.9071 | 1.9194 | 1.9344 | 1.9519 | 1.105 | 1.3229 | 1.3325 | 1.3455 | 1.105 | 1.5242 | 1.7108 | 1.7194 | 1.7308 | 1.8282
2022-02-16 06:00 | 1.8672 | 2.026 | 2.0362 | 2.0487 | 2.0633 | 1.3495 | 1.6088 | 1.6168 | 1.6277 | 1.3495 | 1.4861 | 1.6656 | 1.6728 | 1.6823 | 1.7754
2022-02-16 07:00 | 2.1148 | 2.2954 | 2.3074 | 2.322 | 2.339 | 1.448 | 1.7276 | 1.7369 | 1.7496 | 1.448 | 1.5814 | 1.7739 | 1.7822 | 1.7933 | 1.8935
2022-02-16 08:00 | 2.1148 | 2.3045 | 2.3211 | 2.3414 | 2.365 | 1.3337 | 1.5991 | 1.6121 | 1.6297 | 1.3337 | 1.2448 | 1.4063 | 1.4179 | 1.4333 | 1.5202
2022-02-16 09:00 | 2.0005 | 2.195 | 2.2184 | 2.2471 | 2.2805 | 1.0865 | 1.3168 | 1.3351 | 1.36 | 1.0865 | 0.89547 | 1.0275 | 1.0439 | 1.0657 | 1.141
2022-02-16 10:00 | 1.9243 | 2.1274 | 2.1581 | 2.1956 | 2.2394 | 0.81926 | 1.0115 | 1.0354 | 1.068 | 0.81926 | 1.3146 | 1.5034 | 1.5249 | 1.5535 | 1.6599
2022-02-16 11:00 | 1.829 | 2.036 | 2.0723 | 2.1167 | 2.1684 | 0.62295 | 0.78749 | 0.81578 | 0.8544 | 0.62295 | 1.448 | 1.6594 | 1.6848 | 1.7186 | 1.8385
2022-02-16 12:00 | 1.9053 | 2.1222 | 2.1607 | 2.2078 | 2.2627 | 0.64779 | 0.81999 | 0.85 | 0.89099 | 0.64779 | 1.7719 | 2.0224 | 2.0494 | 2.0852 | 2.2254
2022-02-16 13:00 | 2.0386 | 2.2645 | 2.3024 | 2.3488 | 2.403 | 0.77987 | 0.97526 | 1.0049 | 1.0453 | 0.77987 | 1.2003 | 1.3865 | 1.4131 | 1.4484 | 1.5566
2022-02-16 14:00 | 2.4006 | 2.6484 | 2.6838 | 2.7271 | 2.7776 | 1.0479 | 1.2883 | 1.3159 | 1.3536 | 1.0479 | 0.87117 | 1.0172 | 1.042 | 1.0749 | 1.1622
2022-02-16 15:00 | 2.7055 | 2.9705 | 3.0031 | 3.0431 | 3.0896 | 1.3206 | 1.6065 | 1.632 | 1.6667 | 1.3206 | 0.78115 | 0.91333 | 0.93619 | 0.96657 | 1.0459
2022-02-16 16:00 | 3.0294 | 3.3149 | 3.3457 | 3.3834 | 3.4273 | 1.8406 | 2.2182 | 2.2422 | 2.275 | 1.8406 | 2.0386 | 2.3082 | 2.3297 | 2.3584 | 2.5048
2022-02-16 17:00 | 3.4866 | 3.8053 | 3.8356 | 3.8728 | 3.9161 | 2.4387 | 2.9242 | 2.9479 | 2.9802 | 2.4387 | 3.4104 | 3.8319 | 3.8532 | 3.8815 | 4.1028
2022-02-16 18:00 | 3.4676 | 3.7883 | 3.8205 | 3.8599 | 3.9058 | 2.6864 | 3.2194 | 3.2445 | 3.2787 | 2.6864 | 3.8867 | 4.3638 | 4.3863 | 4.4163 | 4.6657
2022-02-16 19:00 | 3.3914 | 3.7138 | 3.7498 | 3.7937 | 3.845 | 2.6864 | 3.2247 | 3.2527 | 3.291 | 2.6864 | 3.62 | 4.0726 | 4.0977 | 4.1312 | 4.3702
2022-02-16 20:00 | 3.0484 | 3.3551 | 3.396 | 3.4461 | 3.5045 | 2.3625 | 2.8492 | 2.8811 | 2.9246 | 2.3625 | 3.3914 | 3.8254 | 3.8541 | 3.8922 | 4.1242
2022-02-16 21:00 | 2.896 | 3.201 | 3.2469 | 3.303 | 3.3685 | 2.2114 | 2.6777 | 2.7134 | 2.7623 | 2.2114 | 3.2389 | 3.6629 | 3.695 | 3.7377 | 3.9668
2022-02-16 22:00 | 2.553 | 2.8342 | 2.8809 | 2.9381 | 3.0047 | 1.9219 | 2.3369 | 2.3733 | 2.423 | 1.9219 | 2.8388 | 3.2194 | 3.2521 | 3.2956 | 3.5036
2022-02-16 23:00 | 2.1322 | 2.3761 | 2.4198 | 2.4732 | 2.5355 | 1.5494 | 1.8925 | 1.9265 | 1.973 | 1.5494 | 1.9434 | 2.2201 | 2.2507 | 2.2913 | 2.4467
2022-02-17 | 1.9243 | 2.1444 | 2.1837 | 2.2318 | 2.288 | 1.2746 | 1.5617 | 1.5924 | 1.6343 | 1.2746 | 1.7909 | 2.0447 | 2.0723 | 2.1089 | 2.2512
2022-02-17 01:00 | 1.7185 | 1.9138 | 1.9483 | 1.9905 | 2.0398 | 1.1245 | 1.3775 | 1.4044 | 1.4411 | 1.1245 | 1.5814 | 1.8052 | 1.8293 | 1.8615 | 1.9868
2022-02-17 02:00 | 1.6576 | 1.8388 | 1.8684 | 1.9046 | 1.9469 | 1.1241 | 1.3701 | 1.3932 | 1.4247 | 1.1241 | 1.4099 | 1.6078 | 1.6286 | 1.6561 | 1.7666
2022-02-17 03:00 | 1.5814 | 1.7448 | 1.7683 | 1.797 | 1.8304 | 1.0288 | 1.2488 | 1.2671 | 1.292 | 1.0288 | 1.3527 | 1.5357 | 1.5522 | 1.574 | 1.6745
2022-02-17 04:00 | 1.6004 | 1.7535 | 1.7709 | 1.7922 | 1.817 | 1.0288 | 1.2402 | 1.2538 | 1.2723 | 1.0288 | 1.2956 | 1.4639 | 1.4761 | 1.4923 | 1.5829
2022-02-17 05:00 | 1.7022 | 1.8528 | 1.865 | 1.88 | 1.8975 | 1.1294 | 1.3517 | 1.3612 | 1.3743 | 1.1294 | 1.3908 | 1.5626 | 1.5712 | 1.5826 | 1.6727
2022-02-17 06:00 | 1.81 | 1.9646 | 1.9748 | 1.9873 | 2.0019 | 1.3402 | 1.5978 | 1.6058 | 1.6167 | 1.3402 | 1.467 | 1.6445 | 1.6516 | 1.6611 | 1.7532
2022-02-17 07:00 | 2.1148 | 2.2954 | 2.3074 | 2.322 | 2.339 | 1.4289 | 1.7051 | 1.7144 | 1.7271 | 1.4289 | 1.6957 | 1.9009 | 1.9092 | 1.9204 | 2.0269
2022-02-17 08:00 | 2.172 | 2.3659 | 2.3825 | 2.4028 | 2.4265 | 1.3337 | 1.5991 | 1.6121 | 1.6297 | 1.3337 | 1.4861 | 1.6744 | 1.686 | 1.7015 | 1.8016
2022-02-17 09:00 | 2.1529 | 2.3588 | 2.3822 | 2.4108 | 2.4442 | 1.1241 | 1.3612 | 1.3795 | 1.4044 | 1.1241 | 0.93358 | 1.0699 | 1.0863 | 1.1081 | 1.1854
2022-02-17 10:00 | 2.1813 | 2.4035 | 2.4341 | 2.4717 | 2.5155 | 1.1622 | 1.4166 | 1.4405 | 1.4732 | 1.1622 | 0.91452 | 1.0588 | 1.0803 | 1.1089 | 1.1933
2022-02-17 11:00 | 2.3054 | 2.5477 | 2.584 | 2.6284 | 2.6801 | 1.1622 | 1.4245 | 1.4528 | 1.4915 | 1.1622 | 1.0288 | 1.1936 | 1.219 | 1.2528 | 1.3497
2022-02-17 12:00 | 2.0767 | 2.3064 | 2.3449 | 2.392 | 2.447 | 0.7621 | 0.95503 | 0.98505 | 1.026 | 0.7621 | 1.6385 | 1.8742 | 1.9011 | 1.937 | 2.0699
2022-02-17 13:00 | 2.4006 | 2.6534 | 2.6913 | 2.7378 | 2.7919 | 1.2194 | 1.4945 | 1.5241 | 1.5645 | 1.2194 | 1.5433 | 1.7676 | 1.7942 | 1.8295 | 1.9566
2022-02-17 14:00 | 2.3451 | 2.5887 | 2.6241 | 2.6675 | 2.718 | 1.0956 | 1.3446 | 1.3722 | 1.4099 | 1.0956 | 1.2384 | 1.4253 | 1.4501 | 1.483 | 1.5905
2022-02-17 15:00 | 2.9316 | 3.2134 | 3.2461 | 3.286 | 3.3326 | 1.8672 | 2.2522 | 2.2776 | 2.3124 | 1.8672 | 1.9053 | 2.1625 | 2.1854 | 2.2157 | 2.3568
2022-02-17 16:00 | 2.9531 | 3.233 | 3.2638 | 3.3015 | 3.3455 | 1.7155 | 2.0704 | 2.0944 | 2.1272 | 1.7155 | 1.9624 | 2.2235 | 2.245 | 2.2737 | 2.4159
2022-02-17 17:00 | 3.2199 | 3.5187 | 3.5491 | 3.5862 | 3.6296 | 2.2673 | 2.7216 | 2.7453 | 2.7776 | 2.2673 | 3.5438 | 3.9802 | 4.0014 | 4.0297 | 4.2583
2022-02-17 18:00 | 3.0496 | 3.3393 | 3.3715 | 3.4109 | 3.4568 | 2.1529 | 2.5891 | 2.6142 | 2.6485 | 2.1529 | 3.4104 | 3.8345 | 3.857 | 3.887 | 4.1103
2022-02-17 19:00 | 2.8579 | 3.1407 | 3.1766 | 3.2206 | 3.2719 | 2.1148 | 2.5495 | 2.5775 | 2.6158 | 2.1148 | 3.1056 | 3.5009 | 3.5261 | 3.5595 | 3.7703
2022-02-17 20:00 | 2.8769 | 3.1709 | 3.2118 | 3.2619 | 3.3203 | 2.2291 | 2.6916 | 2.7235 | 2.7671 | 2.2291 | 3.1818 | 3.5925 | 3.6212 | 3.6593 | 3.8797
2022-02-17 21:00 | 2.6674 | 2.9554 | 3.0013 | 3.0574 | 3.1229 | 2.1148 | 2.5636 | 2.5993 | 2.6482 | 2.1148 | 2.8579 | 3.2394 | 3.2716 | 3.3143 | 3.5224
2022-02-17 22:00 | 2.4006 | 2.6705 | 2.7172 | 2.7743 | 2.841 | 1.861 | 2.2648 | 2.3013 | 2.351 | 1.861 | 2.553 | 2.9018 | 2.9345 | 2.978 | 3.1703
2022-02-17 23:00 | 2.146 | 2.391 | 2.4347 | 2.4881 | 2.5504 | 1.5623 | 1.9077 | 1.9418 | 1.9882 | 1.5623 | 2.0005 | 2.2836 | 2.3142 | 2.3548 | 2.5134
2022-02-18 | 1.9243 | 2.1444 | 2.1837 | 2.2318 | 2.288 | 1.3146 | 1.609 | 1.6397 | 1.6815 | 1.3146 | 1.6957 | 1.9389 | 1.9664 | 2.0031 | 2.1401
2022-02-18 01:00 | 1.7528 | 1.9507 | 1.9852 | 2.0274 | 2.0767 | 1.1622 | 1.422 | 1.449 | 1.4857 | 1.1622 | 1.3718 | 1.5723 | 1.5964 | 1.6286 | 1.7424
2022-02-18 02:00 | 1.6957 | 1.8797 | 1.9093 | 1.9456 | 1.9879 | 1.0603 | 1.2947 | 1.3178 | 1.3494 | 1.0603 | 1.6385 | 1.8619 | 1.8826 | 1.9102 | 2.0333
2022-02-18 03:00 | 1.6037 | 1.7688 | 1.7923 | 1.821 | 1.8544 | 1.0098 | 1.2263 | 1.2445 | 1.2695 | 1.0098 | 1.3146 | 1.4934 | 1.5098 | 1.5317 | 1.63
2022-02-18 04:00 | 1.6385 | 1.7944 | 1.8118 | 1.8331 | 1.858 | 1.0288 | 1.2402 | 1.2538 | 1.2723 | 1.0288 | 1.3337 | 1.5062 | 1.5184 | 1.5346 | 1.6273
2022-02-18 05:00 | 1.6957 | 1.8457 | 1.858 | 1.873 | 1.8905 | 1.1023 | 1.3196 | 1.3292 | 1.3423 | 1.1023 | 1.4289 | 1.6049 | 1.6135 | 1.6249 | 1.7171
2022-02-18 06:00 | 1.81 | 1.9646 | 1.9748 | 1.9873 | 2.0019 | 1.3204 | 1.5744 | 1.5824 | 1.5933 | 1.3204 | 1.6195 | 1.8138 | 1.821 | 1.8305 | 1.9309
2022-02-18 07:00 | 2.0577 | 2.234 | 2.2459 | 2.2606 | 2.2776 | 1.4099 | 1.6826 | 1.6919 | 1.7046 | 1.4099 | 1.6195 | 1.8162 | 1.8246 | 1.8357 | 1.938
2022-02-18 08:00 | 2.0767 | 2.2636 | 2.2802 | 2.3004 | 2.3241 | 1.3146 | 1.5766 | 1.5895 | 1.6072 | 1.3146 | 1.2384 | 1.3992 | 1.4108 | 1.4262 | 1.5128
2022-02-18 09:00 | 1.9624 | 2.1541 | 2.1775 | 2.2061 | 2.2395 | 1.0373 | 1.2587 | 1.2769 | 1.3018 | 1.0373 | 0.99073 | 1.1334 | 1.1498 | 1.1716 | 1.2521
2022-02-18 10:00 | 1.7909 | 1.9841 | 2.0148 | 2.0524 | 2.0961 | 0.7309 | 0.90707 | 0.931 | 0.96367 | 0.7309 | 1.3337 | 1.5246 | 1.5461 | 1.5746 | 1.6821
2022-02-18 11:00 | 1.7032 | 1.9008 | 1.937 | 1.9814 | 2.0332 | 0.70494 | 0.88436 | 0.91264 | 0.95126 | 0.70494 | 1.6766 | 1.9135 | 1.9389 | 1.9726 | 2.1052
2022-02-18 12:00 | 1.7147 | 1.9175 | 1.956 | 2.0031 | 2.058 | 0.57158 | 0.72996 | 0.75997 | 0.80096 | 0.57158 | 1.5433 | 1.7683 | 1.7953 | 1.8311 | 1.9588
2022-02-18 13:00 | 1.829 | 2.0393 | 2.0772 | 2.1237 | 2.1778 | 0.68744 | 0.86607 | 0.89566 | 0.93608 | 0.68744 | 1.6576 | 1.8946 | 1.9212 | 1.9565 | 2.0899
2022-02-18 14:00 | 2.0386 | 2.2595 | 2.2949 | 2.3382 | 2.3887 | 0.78115 | 0.97316 | 1.0008 | 1.0385 | 0.78115 | 0.95263 | 1.1077 | 1.1325 | 1.1655 | 1.2572
2022-02-18 15:00 | 2.2286 | 2.4582 | 2.4908 | 2.5308 | 2.5774 | 1.0819 | 1.3245 | 1.35 | 1.3848 | 1.0819 | 0.91452 | 1.0615 | 1.0844 | 1.1148 | 1.2014
2022-02-18 16:00 | 2.4387 | 2.6803 | 2.7111 | 2.7488 | 2.7928 | 1.4562 | 1.7641 | 1.7882 | 1.821 | 1.4562 | 0.89547 | 1.0378 | 1.0594 | 1.0881 | 1.1716
2022-02-18 17:00 | 2.553 | 2.8023 | 2.8326 | 2.8698 | 2.9131 | 1.8535 | 2.2328 | 2.2564 | 2.2888 | 1.8535 | 1.9438 | 2.2022 | 2.2235 | 2.2517 | 2.3924
2022-02-18 18:00 | 2.8007 | 3.0719 | 3.1041 | 3.1435 | 3.1894 | 1.9815 | 2.3866 | 2.4117 | 2.4459 | 1.9815 | 2.8007 | 3.1569 | 3.1795 | 3.2094 | 3.3992
2022-02-18 19:00 | 2.6594 | 2.9274 | 2.9634 | 3.0074 | 3.0587 | 1.9815 | 2.3919 | 2.4199 | 2.4582 | 1.9815 | 2.6102 | 2.9504 | 2.9756 | 3.0091 | 3.1926
2022-02-18 20:00 | 2.4387 | 2.7001 | 2.741 | 2.7911 | 2.8495 | 1.9053 | 2.309 | 2.3409 | 2.3845 | 1.9053 | 2.4959 | 2.8303 | 2.859 | 2.8971 | 3.0798
2022-02-18 21:00 | 2.3313 | 2.5944 | 2.6403 | 2.6964 | 2.7619 | 1.8055 | 2.1982 | 2.2339 | 2.2828 | 1.8055 | 2.4006 | 2.7313 | 2.7634 | 2.8061 | 2.9891
2022-02-18 22:00 | 2.191 | 2.4453 | 2.492 | 2.5492 | 2.6158 | 1.6534 | 2.0196 | 2.056 | 2.1057 | 1.6534 | 2.191 | 2.4996 | 2.5323 | 2.5757 | 2.7482
2022-02-18 23:00 | 2.0386 | 2.2756 | 2.3193 | 2.3727 | 2.435 | 1.4289 | 1.7502 | 1.7842 | 1.8307 | 1.4289 | 2.0005 | 2.2836 | 2.3142 | 2.3548 | 2.5134
2022-02-19 | 1.8481 | 2.0625 | 2.1018 | 2.15 | 2.2061 | 1.2765 | 1.564 | 1.5946 | 1.6365 | 1.2765 | 1.7719 | 2.0236 | 2.0511 | 2.0877 | 2.2289
2022-02-19 01:00 | 1.7112 | 1.906 | 1.9405 | 1.9827 | 2.032 | 1.157 | 1.4159 | 1.4428 | 1.4796 | 1.157 | 1.3718 | 1.5723 | 1.5964 | 1.6286 | 1.7424
2022-02-19 02:00 | 1.6766 | 1.8592 | 1.8889 | 1.9251 | 1.9674 | 1.0697 | 1.3059 | 1.329 | 1.3605 | 1.0697 | 1.6195 | 1.8407 | 1.8615 | 1.889 | 2.011
2022-02-19 03:00 | 1.6576 | 1.8267 | 1.8501 | 1.8788 | 1.9123 | 1.0288 | 1.2488 | 1.2671 | 1.292 | 1.0288 | 1.3146 | 1.4934 | 1.5098 | 1.5317 | 1.63
2022-02-19 04:00 | 1.6576 | 1.8149 | 1.8323 | 1.8536 | 1.8784 | 1.0098 | 1.2177 | 1.2312 | 1.2498 | 1.0098 | 1.3718 | 1.5485 | 1.5607 | 1.5769 | 1.6717
2022-02-19 05:00 | 1.6766 | 1.8253 | 1.8375 | 1.8525 | 1.87 | 1.0288 | 1.2329 | 1.2424 | 1.2555 | 1.0288 | 1.4099 | 1.5838 | 1.5923 | 1.6038 | 1.6949
2022-02-19 06:00 | 1.6107 | 1.7505 | 1.7607 | 1.7732 | 1.7878 | 1.086 | 1.2975 | 1.3055 | 1.3164 | 1.086 | 1.4099 | 1.5809 | 1.5881 | 1.5976 | 1.6865
2022-02-19 07:00 | 1.6957 | 1.8451 | 1.857 | 1.8716 | 1.8887 | 1.144 | 1.3685 | 1.3778 | 1.3905 | 1.144 | 1.4289 | 1.6045 | 1.6128 | 1.6239 | 1.7158
2022-02-19 08:00 | 1.6178 | 1.7706 | 1.7871 | 1.8074 | 1.8311 | 1.1622 | 1.3966 | 1.4095 | 1.4271 | 1.1622 | 1.0669 | 1.2086 | 1.2203 | 1.2357 | 1.3128
2022-02-19 09:00 | 1.448 | 1.6014 | 1.6248 | 1.6535 | 1.6869 | 0.90414 | 1.1014 | 1.1196 | 1.1446 | 0.90414 | 0.97168 | 1.1122 | 1.1286 | 1.1504 | 1.2299
2022-02-19 10:00 | 1.3908 | 1.5543 | 1.585 | 1.6225 | 1.6663 | 0.78115 | 0.96644 | 0.99037 | 1.023 | 0.78115 | 1.2194 | 1.3976 | 1.4191 | 1.4476 | 1.5488
2022-02-19 11:00 | 1.6004 | 1.7904 | 1.8266 | 1.871 | 1.9228 | 0.91452 | 1.1319 | 1.1602 | 1.1988 | 0.91452 | 1.4099 | 1.617 | 1.6424 | 1.6762 | 1.7941
2022-02-19 12:00 | 1.5433 | 1.7333 | 1.7718 | 1.8189 | 1.8738 | 0.89547 | 1.1126 | 1.1426 | 1.1836 | 0.89547 | 1.3908 | 1.5989 | 1.6259 | 1.6617 | 1.781
2022-02-19 13:00 | 1.6576 | 1.8551 | 1.893 | 1.9395 | 1.9936 | 0.89547 | 1.1118 | 1.1414 | 1.1818 | 0.89547 | 1.3146 | 1.5135 | 1.5401 | 1.5754 | 1.6899
2022-02-19 14:00 | 1.6957 | 1.891 | 1.9264 | 1.9698 | 2.0203 | 1.0098 | 1.2433 | 1.2709 | 1.3086 | 1.0098 | 1.4289 | 1.637 | 1.6618 | 1.6948 | 1.8127
2022-02-19 15:00 | 1.7528 | 1.947 | 1.9797 | 2.0196 | 2.0662 | 1.2194 | 1.4869 | 1.5124 | 1.5471 | 1.2194 | 1.105 | 1.2733 | 1.2961 | 1.3265 | 1.4236
2022-02-19 16:00 | 1.8672 | 2.0663 | 2.0971 | 2.1348 | 2.1787 | 1.2956 | 1.5743 | 1.5984 | 1.6312 | 1.2956 | 1.4099 | 1.6095 | 1.631 | 1.6597 | 1.7715
2022-02-19 17:00 | 2.0767 | 2.2906 | 2.3209 | 2.3581 | 2.4014 | 1.467 | 1.7763 | 1.8 | 1.8323 | 1.467 | 1.1622 | 1.3336 | 1.3549 | 1.3832 | 1.4809
2022-02-19 18:00 | 2.2055 | 2.4324 | 2.4646 | 2.504 | 2.5499 | 1.6483 | 1.993 | 2.0181 | 2.0524 | 1.6483 | 2.0958 | 2.3736 | 2.3961 | 2.4261 | 2.5771
2022-02-19 19:00 | 2.3054 | 2.5471 | 2.583 | 2.627 | 2.6783 | 1.7147 | 2.0768 | 2.1048 | 2.1431 | 1.7147 | 2.3816 | 2.6964 | 2.7215 | 2.755 | 2.9259
2022-02-19 20:00 | 2.3244 | 2.5773 | 2.6182 | 2.6683 | 2.7267 | 1.7147 | 2.0839 | 2.1158 | 2.1594 | 1.7147 | 2.3435 | 2.6609 | 2.6896 | 2.7277 | 2.9021
2022-02-19 21:00 | 2.2863 | 2.546 | 2.5919 | 2.648 | 2.7135 | 1.7147 | 2.0909 | 2.1267 | 2.1755 | 1.7147 | 2.2673 | 2.5831 | 2.6152 | 2.6579 | 2.8336
2022-02-19 22:00 | 2.172 | 2.4249 | 2.4715 | 2.5287 | 2.5953 | 1.5374 | 1.8827 | 1.9191 | 1.9688 | 1.5374 | 2.4768 | 2.8171 | 2.8499 | 2.8933 | 3.0815
2022-02-19 23:00 | 1.9815 | 2.2142 | 2.2579 | 2.3113 | 2.3736 | 1.3557 | 1.6636 | 1.6977 | 1.7442 | 1.3557 | 2.0386 | 2.326 | 2.3565 | 2.3972 | 2.5578
2022-02-20 | 1.8128 | 2.0246 | 2.0639 | 2.1121 | 2.1682 | 1.2152 | 1.4915 | 1.5222 | 1.5641 | 1.2152 | 1.7528 | 2.0024 | 2.03 | 2.0666 | 2.2067
2022-02-20 01:00 | 1.6766 | 1.8688 | 1.9033 | 1.9456 | 1.9948 | 1.1032 | 1.3524 | 1.3793 | 1.4161 | 1.1032 | 1.3908 | 1.5934 | 1.6176 | 1.6497 | 1.7646
2022-02-20 02:00 | 1.629 | 1.8081 | 1.8377 | 1.8739 | 1.9162 | 1.0185 | 1.2453 | 1.2684 | 1.2999 | 1.0185 | 1.3908 | 1.5866 | 1.6074 | 1.635 | 1.7444
2022-02-20 03:00 | 1.5814 | 1.7448 | 1.7683 | 1.797 | 1.8304 | 1.0098 | 1.2263 | 1.2445 | 1.2695 | 1.0098 | 1.2575 | 1.4299 | 1.4463 | 1.4681 | 1.5634
2022-02-20 04:00 | 1.6004 | 1.7535 | 1.7709 | 1.7922 | 1.817 | 0.99073 | 1.1952 | 1.2087 | 1.2273 | 0.99073 | 1.2765 | 1.4427 | 1.4549 | 1.4711 | 1.5606
2022-02-20 05:00 | 1.5814 | 1.7229 | 1.7352 | 1.7502 | 1.7677 | 0.98328 | 1.179 | 1.1886 | 1.2017 | 0.98328 | 1.3527 | 1.5202 | 1.5288 | 1.5402 | 1.6282
2022-02-20 06:00 | 1.5623 | 1.6985 | 1.7087 | 1.7212 | 1.7358 | 1.0288 | 1.23 | 1.238 | 1.2489 | 1.0288 | 1.2956 | 1.4539 | 1.4611 | 1.4706 | 1.5532
2022-02-20 07:00 | 1.5623 | 1.7018 | 1.7138 | 1.7284 | 1.7454 | 1.1432 | 1.3674 | 1.3768 | 1.3895 | 1.1432 | 1.3146 | 1.4774 | 1.4858 | 1.4969 | 1.5825
2022-02-20 08:00 | 1.6576 | 1.8133 | 1.8298 | 1.8501 | 1.8738 | 1.1432 | 1.374 | 1.387 | 1.4046 | 1.1432 | 1.2575 | 1.4204 | 1.432 | 1.4474 | 1.535
2022-02-20 09:00 | 1.4289 | 1.581 | 1.6044 | 1.633 | 1.6664 | 1.0098 | 1.2262 | 1.2444 | 1.2694 | 1.0098 | 1.0479 | 1.1969 | 1.2133 | 1.2351 | 1.3188
2022-02-20 10:00 | 1.6766 | 1.8613 | 1.892 | 1.9295 | 1.9733 | 1.1432 | 1.3941 | 1.418 | 1.4507 | 1.1432 | 1.1622 | 1.3341 | 1.3555 | 1.3841 | 1.4821
2022-02-20 11:00 | 1.81 | 2.0155 | 2.0518 | 2.0962 | 2.1479 | 0.99073 | 1.222 | 1.2503 | 1.2889 | 0.99073 | 1.3146 | 1.5112 | 1.5366 | 1.5703 | 1.683
2022-02-20 12:00 | 1.829 | 2.0404 | 2.0788 | 2.1259 | 2.1809 | 1.086 | 1.3377 | 1.3677 | 1.4087 | 1.086 | 1.3146 | 1.5143 | 1.5412 | 1.577 | 1.6922
2022-02-20 13:00 | 1.9815 | 2.2031 | 2.241 | 2.2874 | 2.3416 | 1.3146 | 1.607 | 1.6366 | 1.677 | 1.3146 | 1.3908 | 1.5982 | 1.6248 | 1.6601 | 1.7788
2022-02-20 14:00 | 2.1529 | 2.3823 | 2.4177 | 2.461 | 2.5115 | 1.3908 | 1.6934 | 1.721 | 1.7587 | 1.3908 | 1.8672 | 2.124 | 2.1488 | 2.1817 | 2.3238
2022-02-20 15:00 | 2.4959 | 2.7453 | 2.778 | 2.8179 | 2.8645 | 1.7909 | 2.1621 | 2.1876 | 2.2224 | 1.7909 | 2.5149 | 2.84 | 2.8629 | 2.8932 | 3.0678
2022-02-20 16:00 | 2.6102 | 2.8645 | 2.8954 | 2.9331 | 2.977 | 2.0196 | 2.4296 | 2.4537 | 2.4865 | 2.0196 | 3.1627 | 3.5573 | 3.5789 | 3.6076 | 3.8157
2022-02-20 17:00 | 2.7539 | 3.0181 | 3.0485 | 3.0857 | 3.129 | 2.0577 | 2.474 | 2.4977 | 2.53 | 2.0577 | 2.8388 | 3.1968 | 3.2181 | 3.2463 | 3.4362
2022-02-20 18:00 | 2.9341 | 3.2152 | 3.2474 | 3.2868 | 3.3327 | 2.3625 | 2.8367 | 2.8618 | 2.8961 | 2.3625 | 3.6962 | 4.152 | 4.1746 | 4.2045 | 4.4435
2022-02-20 19:00 | 2.9531 | 3.243 | 3.279 | 3.3229 | 3.3742 | 2.25 | 2.7091 | 2.7372 | 2.7754 | 2.25 | 3.3723 | 3.7973 | 3.8225 | 3.856 | 4.0813
2022-02-20 20:00 | 2.8769 | 3.1709 | 3.2118 | 3.2619 | 3.3203 | 2.2673 | 2.7366 | 2.7685 | 2.8121 | 2.2673 | 2.9722 | 3.3596 | 3.3883 | 3.4264 | 3.6353
2022-02-20 21:00 | 2.7245 | 3.0168 | 3.0627 | 3.1188 | 3.1843 | 2.1537 | 2.6095 | 2.6452 | 2.6941 | 2.1537 | 3.1056 | 3.5147 | 3.5468 | 3.5895 | 3.8113
2022-02-20 22:00 | 2.354 | 2.6204 | 2.6671 | 2.7243 | 2.7909 | 1.8509 | 2.2529 | 2.2893 | 2.3391 | 1.8509 | 2.3509 | 2.6772 | 2.71 | 2.7534 | 2.9346
2022-02-20 23:00 | 2.172 | 2.4189 | 2.4626 | 2.516 | 2.5783 | 1.5522 | 1.8958 | 1.9299 | 1.9763 | 1.5522 | 2.1148 | 2.4107 | 2.4412 | 2.4819 | 2.6467
2022-02-21 | 1.9434 | 2.1648 | 2.2042 | 2.2523 | 2.3084 | 1.3527 | 1.654 | 1.6847 | 1.7266 | 1.3527 | 1.6766 | 1.9177 | 1.9453 | 1.9819 | 2.1178
2022-02-21 01:00 | 1.7909 | 1.9916 | 2.0261 | 2.0684 | 2.1176 | 1.1752 | 1.4373 | 1.4643 | 1.501 | 1.1752 | 1.448 | 1.6569 | 1.6811 | 1.7133 | 1.8313
2022-02-21 02:00 | 1.6957 | 1.8797 | 1.9093 | 1.9456 | 1.9879 | 1.0761 | 1.3134 | 1.3365 | 1.368 | 1.0761 | 1.5052 | 1.7137 | 1.7344 | 1.762 | 1.8777
2022-02-21 03:00 | 1.6195 | 1.7858 | 1.8092 | 1.8379 | 1.8714 | 1.0259 | 1.2452 | 1.2635 | 1.2885 | 1.0259 | 1.3146 | 1.4934 | 1.5098 | 1.5317 | 1.63
2022-02-21 04:00 | 1.6766 | 1.8353 | 1.8528 | 1.8741 | 1.8989 | 1.0089 | 1.2166 | 1.2302 | 1.2487 | 1.0089 | 1.3337 | 1.5062 | 1.5184 | 1.5346 | 1.6273
2022-02-21 05:00 | 1.7909 | 1.9481 | 1.9603 | 1.9753 | 1.9928 | 1.105 | 1.3229 | 1.3325 | 1.3455 | 1.105 | 1.5052 | 1.6896 | 1.6982 | 1.7096 | 1.806
2022-02-21 06:00 | 1.8069 | 1.9613 | 1.9715 | 1.9841 | 1.9987 | 1.3146 | 1.5676 | 1.5756 | 1.5865 | 1.3146 | 1.5242 | 1.708 | 1.7151 | 1.7247 | 1.8198
2022-02-21 07:00 | 2.191 | 2.3773 | 2.3892 | 2.4038 | 2.4209 | 1.5052 | 1.7951 | 1.8044 | 1.8171 | 1.5052 | 1.6576 | 1.8585 | 1.8669 | 1.878 | 1.9824
2022-02-21 08:00 | 2.191 | 2.3864 | 2.403 | 2.4233 | 2.4469 | 1.448 | 1.7342 | 1.7471 | 1.7648 | 1.448 | 1.5242 | 1.7168 | 1.7284 | 1.7438 | 1.8461
2022-02-21 09:00 | 2.172 | 2.3793 | 2.4027 | 2.4313 | 2.4647 | 1.1989 | 1.4496 | 1.4678 | 1.4927 | 1.1989 | 1.0098 | 1.1546 | 1.171 | 1.1928 | 1.2743
2022-02-21 10:00 | 1.9434 | 2.1479 | 2.1786 | 2.2161 | 2.2599 | 0.95263 | 1.169 | 1.1929 | 1.2256 | 0.95263 | 1.1622 | 1.3341 | 1.3555 | 1.3841 | 1.4821
2022-02-21 11:00 | 2.0196 | 2.2407 | 2.277 | 2.3213 | 2.3731 | 0.85737 | 1.0644 | 1.0927 | 1.1313 | 0.85737 | 1.7338 | 1.977 | 2.0024 | 2.0361 | 2.1718
2022-02-21 12:00 | 2.2482 | 2.4907 | 2.5292 | 2.5763 | 2.6312 | 0.93358 | 1.1576 | 1.1876 | 1.2286 | 0.93358 | 1.6004 | 1.8318 | 1.8588 | 1.8946 | 2.0255
2022-02-21 13:00 | 2.0386 | 2.2645 | 2.3024 | 2.3488 | 2.403 | 0.91452 | 1.1343 | 1.1639 | 1.2043 | 0.91452 | 1.7909 | 2.0428 | 2.0694 | 2.1047 | 2.2454
2022-02-21 14:00 | 2.172 | 2.4028 | 2.4382 | 2.4815 | 2.532 | 1.0479 | 1.2883 | 1.3159 | 1.3536 | 1.0479 | 1.81 | 2.0605 | 2.0853 | 2.1182 | 2.2571
2022-02-21 15:00 | 2.3054 | 2.5406 | 2.5733 | 2.6132 | 2.6598 | 1.0479 | 1.2843 | 1.3098 | 1.3446 | 1.0479 | 1.2194 | 1.4003 | 1.4232 | 1.4535 | 1.5569
2022-02-21 16:00 | 2.4959 | 2.7417 | 2.7725 | 2.8102 | 2.8542 | 1.448 | 1.7544 | 1.7784 | 1.8112 | 1.448 | 1.1813 | 1.3554 | 1.377 | 1.4057 | 1.5049
2022-02-21 17:00 | 2.7245 | 2.9865 | 3.0169 | 3.054 | 3.0974 | 1.7909 | 2.1589 | 2.1826 | 2.2149 | 1.7909 | 2.2101 | 2.4981 | 2.5194 | 2.5476 | 2.7029
2022-02-21 18:00 | 2.8388 | 3.1129 | 3.145 | 3.1844 | 3.2303 | 2.0196 | 2.4316 | 2.4567 | 2.4909 | 2.0196 | 2.7817 | 3.1358 | 3.1583 | 3.1883 | 3.377
2022-02-21 19:00 | 2.5252 | 2.7832 | 2.8192 | 2.8632 | 2.9144 | 1.916 | 2.3146 | 2.3426 | 2.3809 | 1.916 | 3.3723 | 3.7973 | 3.8225 | 3.856 | 4.0813
2022-02-21 20:00 | 2.4006 | 2.6592 | 2.7001 | 2.7502 | 2.8086 | 1.8672 | 2.2639 | 2.2959 | 2.3394 | 1.8672 | 2.4197 | 2.7456 | 2.7743 | 2.8124 | 2.9909
2022-02-21 21:00 | 2.3054 | 2.5665 | 2.6124 | 2.6685 | 2.7339 | 1.7719 | 2.1584 | 2.1942 | 2.243 | 1.7719 | 2.3816 | 2.7101 | 2.7423 | 2.785 | 2.9669
2022-02-21 22:00 | 2.1529 | 2.4044 | 2.4511 | 2.5082 | 2.5749 | 1.6136 | 1.9726 | 2.0091 | 2.0588 | 1.6136 | 2.172 | 2.4784 | 2.5111 | 2.5546 | 2.7259
2022-02-21 23:00 | 1.9624 | 2.1937 | 2.2374 | 2.2908 | 2.3531 | 1.3527 | 1.6601 | 1.6942 | 1.7406 | 1.3527 | 1.9053 | 2.1778 | 2.2083 | 2.249 | 2.4023
2022-02-22 | 1.8672 | 2.083 | 2.1223 | 2.1704 | 2.2266 | 1.2003 | 1.4739 | 1.5046 | 1.5465 | 1.2003 | 1.4861 | 1.706 | 1.7335 | 1.7702 | 1.8956
2022-02-22 01:00 | 1.7158 | 1.9109 | 1.9454 | 1.9876 | 2.0369 | 1.0771 | 1.3215 | 1.3484 | 1.3851 | 1.0771 | 1.4289 | 1.6358 | 1.66 | 1.6921 | 1.8091
2022-02-22 02:00 | 1.6766 | 1.8592 | 1.8889 | 1.9251 | 1.9674 | 1.0211 | 1.2484 | 1.2715 | 1.303 | 1.0211 | 1.3337 | 1.5231 | 1.5439 | 1.5715 | 1.6777
2022-02-22 03:00 | 1.6576 | 1.8267 | 1.8501 | 1.8788 | 1.9123 | 1.0098 | 1.2263 | 1.2445 | 1.2695 | 1.0098 | 1.2765 | 1.4511 | 1.4675 | 1.4893 | 1.5856
2022-02-22 04:00 | 1.6576 | 1.8149 | 1.8323 | 1.8536 | 1.8784 | 1.0098 | 1.2177 | 1.2312 | 1.2498 | 1.0098 | 1.2956 | 1.4639 | 1.4761 | 1.4923 | 1.5829
2022-02-22 05:00 | 1.7909 | 1.9481 | 1.9603 | 1.9753 | 1.9928 | 1.1017 | 1.3189 | 1.3285 | 1.3416 | 1.1017 | 1.5623 | 1.7531 | 1.7617 | 1.7731 | 1.8727
2022-02-22 06:00 | 1.9053 | 2.0669 | 2.0772 | 2.0897 | 2.1043 | 1.3146 | 1.5676 | 1.5756 | 1.5865 | 1.3146 | 1.9053 | 2.1314 | 2.1386 | 2.1481 | 2.2642
2022-02-22 07:00 | 2.3085 | 2.5035 | 2.5155 | 2.5301 | 2.5471 | 1.5242 | 1.8176 | 1.8269 | 1.8396 | 1.5242 | 1.81 | 2.0279 | 2.0363 | 2.0474 | 2.1602
2022-02-22 08:00 | 2.3244 | 2.5297 | 2.5462 | 2.5665 | 2.5902 | 1.467 | 1.7567 | 1.7696 | 1.7873 | 1.467 | 1.9815 | 2.2249 | 2.2365 | 2.252 | 2.3793
2022-02-22 09:00 | 2.3816 | 2.6044 | 2.6278 | 2.6565 | 2.6899 | 1.3337 | 1.6088 | 1.6271 | 1.652 | 1.3337 | 1.6004 | 1.8109 | 1.8273 | 1.8491 | 1.9631
2022-02-22 10:00 | 2.3625 | 2.5982 | 2.6289 | 2.6664 | 2.7102 | 1.3146 | 1.5967 | 1.6206 | 1.6533 | 1.3146 | 1.2575 | 1.4399 | 1.4614 | 1.49 | 1.5932
2022-02-22 11:00 | 2.172 | 2.4045 | 2.4407 | 2.4851 | 2.5369 | 1.1454 | 1.4047 | 1.433 | 1.4716 | 1.1454 | 1.3146 | 1.5112 | 1.5366 | 1.5703 | 1.683
2022-02-22 12:00 | 2.3435 | 2.593 | 2.6315 | 2.6786 | 2.7335 | 1.2003 | 1.4727 | 1.5027 | 1.5437 | 1.2003 | 1.1622 | 1.3449 | 1.3718 | 1.4077 | 1.5144
2022-02-22 13:00 | 2.1339 | 2.3668 | 2.4047 | 2.4512 | 2.5054 | 1.0669 | 1.3144 | 1.344 | 1.3844 | 1.0669 | 1.1241 | 1.3018 | 1.3284 | 1.3637 | 1.4677
2022-02-22 14:00 | 2.1148 | 2.3413 | 2.3767 | 2.4201 | 2.4706 | 1.0288 | 1.2658 | 1.2934 | 1.3311 | 1.0288 | 0.97168 | 1.1289 | 1.1537 | 1.1866 | 1.2795
2022-02-22 15:00 | 2.2673 | 2.4997 | 2.5323 | 2.5723 | 2.6189 | 1.211 | 1.4771 | 1.5025 | 1.5373 | 1.211 | 1.1432 | 1.3156 | 1.3385 | 1.3688 | 1.468
2022-02-22 16:00 | 2.2482 | 2.4756 | 2.5064 | 2.5441 | 2.5881 | 1.2956 | 1.5743 | 1.5984 | 1.6312 | 1.2956 | 1.0669 | 1.2284 | 1.2499 | 1.2786 | 1.3716
2022-02-22 17:00 | 2.304 | 2.5348 | 2.5651 | 2.6023 | 2.6456 | 1.471 | 1.781 | 1.8047 | 1.837 | 1.471 | 1.7528 | 1.99 | 2.0112 | 2.0395 | 2.1697
2022-02-22 18:00 | 2.4006 | 2.6421 | 2.6742 | 2.7136 | 2.7595 | 1.7482 | 2.111 | 2.1361 | 2.1703 | 1.7482 | 2.2863 | 2.5853 | 2.6078 | 2.6378 | 2.7993
2022-02-22 19:00 | 2.4006 | 2.6494 | 2.6854 | 2.7293 | 2.7806 | 1.8481 | 2.2344 | 2.2624 | 2.3007 | 1.8481 | 2.2291 | 2.527 | 2.5522 | 2.5856 | 2.7482
2022-02-22 20:00 | 2.4768 | 2.7411 | 2.782 | 2.8321 | 2.8905 | 1.8862 | 2.2865 | 2.3184 | 2.3619 | 1.8862 | 2.3054 | 2.6186 | 2.6473 | 2.6853 | 2.8576
2022-02-22 21:00 | 2.3625 | 2.6279 | 2.6738 | 2.7299 | 2.7954 | 1.7338 | 2.1134 | 2.1492 | 2.198 | 1.7338 | 2.4006 | 2.7313 | 2.7634 | 2.8061 | 2.9891
2022-02-22 22:00 | 2.172 | 2.4249 | 2.4715 | 2.5287 | 2.5953 | 1.6036 | 1.9608 | 1.9973 | 2.047 | 1.6036 | 2.1339 | 2.436 | 2.4688 | 2.5122 | 2.6815
2022-02-22 23:00 | 1.9488 | 2.1792 | 2.2228 | 2.2762 | 2.3385 | 1.3057 | 1.6046 | 1.6386 | 1.6851 | 1.3057 | 1.6576 | 1.9025 | 1.9331 | 1.9737 | 2.1134
2022-02-23 | 1.81 | 2.0215 | 2.0609 | 2.109 | 2.1652 | 1.1687 | 1.4365 | 1.4672 | 1.5091 | 1.1687 | 1.7338 | 1.9812 | 2.0088 | 2.0454 | 2.1845
2022-02-23 01:00 | 1.7147 | 1.9098 | 1.9443 | 1.9865 | 2.0358 | 1.0649 | 1.3071 | 1.334 | 1.3708 | 1.0649 | 1.2956 | 1.4876 | 1.5117 | 1.5439 | 1.6535
2022-02-23 02:00 | 1.6766 | 1.8592 | 1.8889 | 1.9251 | 1.9674 | 1.0288 | 1.2575 | 1.2806 | 1.3122 | 1.0288 | 1.3718 | 1.5655 | 1.5862 | 1.6138 | 1.7222
2022-02-23 03:00 | 1.6576 | 1.8267 | 1.8501 | 1.8788 | 1.9123 | 0.97269 | 1.1824 | 1.2007 | 1.2257 | 0.97269 | 1.3527 | 1.5357 | 1.5522 | 1.574 | 1.6745
2022-02-23 04:00 | 1.6576 | 1.8149 | 1.8323 | 1.8536 | 1.8784 | 0.96811 | 1.1684 | 1.182 | 1.2006 | 0.96811 | 1.4099 | 1.5909 | 1.6031 | 1.6193 | 1.7162
2022-02-23 05:00 | 1.7392 | 1.8924 | 1.9047 | 1.9197 | 1.9372 | 1.1432 | 1.3679 | 1.3775 | 1.3905 | 1.1432 | 1.4289 | 1.6049 | 1.6135 | 1.6249 | 1.7171
2022-02-23 06:00 | 1.9243 | 2.0874 | 2.0976 | 2.1102 | 2.1248 | 1.2922 | 1.5411 | 1.5491 | 1.56 | 1.2922 | 1.505 | 1.6866 | 1.6938 | 1.7033 | 1.7974
2022-02-23 07:00 | 2.2634 | 2.455 | 2.467 | 2.4816 | 2.4986 | 1.5052 | 1.7951 | 1.8044 | 1.8171 | 1.5052 | 1.8481 | 2.0703 | 2.0786 | 2.0897 | 2.2046
2022-02-23 08:00 | 2.4066 | 2.6179 | 2.6345 | 2.6548 | 2.6785 | 1.5052 | 1.8017 | 1.8146 | 1.8323 | 1.5052 | 1.6385 | 1.8438 | 1.8554 | 1.8709 | 1.9794
2022-02-23 09:00 | 2.4197 | 2.6454 | 2.6688 | 2.6974 | 2.7308 | 1.3718 | 1.6538 | 1.6721 | 1.697 | 1.3718 | 1.5433 | 1.7474 | 1.7638 | 1.7856 | 1.8965
2022-02-23 10:00 | 2.3244 | 2.5573 | 2.5879 | 2.6255 | 2.6693 | 1.3527 | 1.6417 | 1.6656 | 1.6983 | 1.3527 | 1.5814 | 1.7998 | 1.8213 | 1.8499 | 1.971
2022-02-23 11:00 | 2.191 | 2.4249 | 2.4612 | 2.5056 | 2.5573 | 1.2384 | 1.5146 | 1.5429 | 1.5815 | 1.2384 | 1.7338 | 1.977 | 2.0024 | 2.0361 | 2.1718
2022-02-23 12:00 | 2.3625 | 2.6135 | 2.652 | 2.6991 | 2.754 | 1.2575 | 1.5402 | 1.5703 | 1.6112 | 1.2575 | 1.4861 | 1.7048 | 1.7318 | 1.7676 | 1.8921
2022-02-23 13:00 | 2.191 | 2.4282 | 2.4662 | 2.5126 | 2.5668 | 1.0098 | 1.2469 | 1.2765 | 1.3169 | 1.0098 | 1.5242 | 1.7464 | 1.773 | 1.8083 | 1.9344
2022-02-23 14:00 | 2.4768 | 2.7303 | 2.7657 | 2.809 | 2.8595 | 1.2765 | 1.5584 | 1.586 | 1.6237 | 1.2765 | 1.3718 | 1.5735 | 1.5983 | 1.6313 | 1.7461
2022-02-23 15:00 | 2.6102 | 2.8681 | 2.9008 | 2.9407 | 2.9873 | 1.2765 | 1.5544 | 1.5799 | 1.6146 | 1.2765 | 1.0098 | 1.1674 | 1.1903 | 1.2206 | 1.3125
2022-02-23 16:00 | 2.5721 | 2.8236 | 2.8544 | 2.8921 | 2.9361 | 1.5433 | 1.8669 | 1.891 | 1.9238 | 1.5433 | 1.5623 | 1.7788 | 1.8004 | 1.8291 | 1.9493
2022-02-23 17:00 | 2.5064 | 2.7521 | 2.7825 | 2.8197 | 2.863 | 1.7147 | 2.0689 | 2.0926 | 2.1249 | 1.7147 | 2.0767 | 2.3499 | 2.3712 | 2.3994 | 2.5474
2022-02-23 18:00 | 2.553 | 2.8058 | 2.838 | 2.8774 | 2.9233 | 1.9624 | 2.3641 | 2.3892 | 2.4234 | 1.9624 | 2.3816 | 2.6912 | 2.7137 | 2.7437 | 2.9104
2022-02-23 19:00 | 2.5125 | 2.7696 | 2.8056 | 2.8495 | 2.9008 | 1.9053 | 2.3019 | 2.3299 | 2.3682 | 1.9053 | 2.8388 | 3.2045 | 3.2297 | 3.2631 | 3.4592
2022-02-23 20:00 | 2.6483 | 2.9253 | 2.9662 | 3.0163 | 3.0747 | 1.9053 | 2.309 | 2.3409 | 2.3845 | 1.9053 | 2.7817 | 3.1479 | 3.1766 | 3.2147 | 3.4131
2022-02-23 21:00 | 2.4197 | 2.6893 | 2.7352 | 2.7913 | 2.8568 | 1.8862 | 2.2935 | 2.3293 | 2.3781 | 1.8862 | 2.4959 | 2.8372 | 2.8693 | 2.912 | 3.1002
2022-02-23 22:00 | 2.3054 | 2.5681 | 2.6148 | 2.672 | 2.7386 | 1.6644 | 2.0326 | 2.069 | 2.1188 | 1.6644 | 2.2291 | 2.5419 | 2.5746 | 2.6181 | 2.7926
2022-02-23 23:00 | 2.0767 | 2.3166 | 2.3602 | 2.4136 | 2.4759 | 1.3866 | 1.7002 | 1.7342 | 1.7807 | 1.3866 | 1.8862 | 2.1566 | 2.1872 | 2.2278 | 2.3801
2022-02-24 | 1.8917 | 2.1093 | 2.1486 | 2.1968 | 2.2529 | 1.1784 | 1.448 | 1.4787 | 1.5206 | 1.1784 | 1.7147 | 1.9601 | 1.9876 | 2.0242 | 2.1623
2022-02-24 01:00 | 1.81 | 2.0121 | 2.0466 | 2.0888 | 2.1381 | 1.1118 | 1.3625 | 1.3894 | 1.4262 | 1.1118 | 1.3718 | 1.5723 | 1.5964 | 1.6286 | 1.7424
2022-02-24 02:00 | 1.6957 | 1.8797 | 1.9093 | 1.9456 | 1.9879 | 1.0502 | 1.2828 | 1.3059 | 1.3374 | 1.0502 | 1.3337 | 1.5231 | 1.5439 | 1.5715 | 1.6777
2022-02-24 03:00 | 1.6766 | 1.8472 | 1.8706 | 1.8993 | 1.9328 | 1.0288 | 1.2488 | 1.2671 | 1.292 | 1.0288 | 1.2575 | 1.4299 | 1.4463 | 1.4681 | 1.5634
2022-02-24 04:00 | 1.6576 | 1.8149 | 1.8323 | 1.8536 | 1.8784 | 1.0252 | 1.2359 | 1.2494 | 1.268 | 1.0252 | 1.4289 | 1.6121 | 1.6243 | 1.6405 | 1.7384
2022-02-24 05:00 | 1.81 | 1.9686 | 1.9808 | 1.9958 | 2.0133 | 1.1432 | 1.3679 | 1.3775 | 1.3905 | 1.1432 | 1.448 | 1.6261 | 1.6347 | 1.6461 | 1.7393
2022-02-24 06:00 | 1.9624 | 2.1283 | 2.1386 | 2.1511 | 2.1657 | 1.3337 | 1.5901 | 1.5981 | 1.609 | 1.3337 | 1.6004 | 1.7927 | 1.7998 | 1.8094 | 1.9087
2022-02-24 07:00 | 2.2849 | 2.4781 | 2.49 | 2.5046 | 2.5217 | 1.5433 | 1.8401 | 1.8494 | 1.8621 | 1.5433 | 1.7909 | 2.0067 | 2.0151 | 2.0262 | 2.138
2022-02-24 08:00 | 2.3054 | 2.5092 | 2.5258 | 2.5461 | 2.5697 | 1.4974 | 1.7925 | 1.8054 | 1.8231 | 1.4974 | 1.7528 | 1.9708 | 1.9825 | 1.9979 | 2.1127
2022-02-24 09:00 | 2.3435 | 2.5635 | 2.5869 | 2.6155 | 2.6489 | 1.2956 | 1.5638 | 1.5821 | 1.607 | 1.2956 | 1.1432 | 1.3028 | 1.3192 | 1.341 | 1.4299
2022-02-24 10:00 | 2.2482 | 2.4754 | 2.5061 | 2.5436 | 2.5874 | 1.2003 | 1.4616 | 1.4855 | 1.5182 | 1.2003 | 1.1813 | 1.3552 | 1.3767 | 1.4053 | 1.5044
2022-02-24 11:00 | 2.4248 | 2.676 | 2.7123 | 2.7567 | 2.8084 | 1.0669 | 1.312 | 1.3403 | 1.3789 | 1.0669 | 1.1777 | 1.359 | 1.3844 | 1.4182 | 1.5233
2022-02-24 12:00 | 2.4387 | 2.6954 | 2.7338 | 2.7809 | 2.8359 | 1.1241 | 1.3827 | 1.4127 | 1.4537 | 1.1241 | 1.2194 | 1.4084 | 1.4354 | 1.4712 | 1.5811
2022-02-24 13:00 | 2.4578 | 2.7148 | 2.7527 | 2.7992 | 2.8533 | 1.2384 | 1.517 | 1.5466 | 1.587 | 1.2384 | 1.086 | 1.2594 | 1.286 | 1.3214 | 1.4233
2022-02-24 14:00 | 2.8198 | 3.0987 | 3.1341 | 3.1774 | 3.228 | 1.6385 | 1.986 | 2.0136 | 2.0513 | 1.6385 | 1.5242 | 1.7429 | 1.7677 | 1.8006 | 1.9238
2022-02-24 15:00 | 2.7055 | 2.9705 | 3.0031 | 3.0431 | 3.0896 | 1.448 | 1.757 | 1.7825 | 1.8172 | 1.448 | 1.105 | 1.2733 | 1.2961 | 1.3265 | 1.4236
2022-02-24 16:00 | 2.9531 | 3.233 | 3.2638 | 3.3015 | 3.3455 | 1.7338 | 2.092 | 2.116 | 2.1488 | 1.7338 | 2.0386 | 2.3082 | 2.3297 | 2.3584 | 2.5048
2022-02-24 17:00 | 2.5721 | 2.8227 | 2.8531 | 2.8903 | 2.9336 | 1.8532 | 2.2325 | 2.2562 | 2.2885 | 1.8532 | 2.4578 | 2.7733 | 2.7946 | 2.8229 | 2.9918
2022-02-24 18:00 | 2.5911 | 2.8468 | 2.8789 | 2.9183 | 2.9642 | 1.9624 | 2.3641 | 2.3892 | 2.4234 | 1.9624 | 2.9722 | 3.3475 | 3.37 | 3.4 | 3.5992
2022-02-24 19:00 | 2.6102 | 2.8746 | 2.9105 | 2.9545 | 3.0058 | 1.9815 | 2.3919 | 2.4199 | 2.4582 | 1.9815 | 2.5721 | 2.9081 | 2.9333 | 2.9667 | 3.1481
2022-02-24 20:00 | 2.5583 | 2.8286 | 2.8695 | 2.9196 | 2.978 | 1.9624 | 2.3765 | 2.4084 | 2.452 | 1.9624 | 2.553 | 2.8938 | 2.9225 | 2.9606 | 3.1465
2022-02-24 21:00 | 2.4959 | 2.7712 | 2.8171 | 2.8732 | 2.9386 | 1.825 | 2.2211 | 2.2569 | 2.3057 | 1.825 | 3.0103 | 3.4088 | 3.4409 | 3.4836 | 3.7002
2022-02-24 22:00 | 2.3435 | 2.6091 | 2.6558 | 2.7129 | 2.7796 | 1.6957 | 2.0696 | 2.106 | 2.1557 | 1.6957 | 2.2863 | 2.6054 | 2.6381 | 2.6816 | 2.8593
2022-02-24 23:00 | 2.191 | 2.4394 | 2.483 | 2.5364 | 2.5987 | 1.417 | 1.736 | 1.7701 | 1.8166 | 1.417 | 1.9243 | 2.1989 | 2.2295 | 2.2701 | 2.4245
2022-02-25 | 1.9087 | 2.1276 | 2.1669 | 2.2151 | 2.2712 | 1.2451 | 1.5268 | 1.5575 | 1.5994 | 1.2451 | 1.6957 | 1.9389 | 1.9664 | 2.0031 | 2.1401
2022-02-25 01:00 | 1.81 | 2.0121 | 2.0466 | 2.0888 | 2.1381 | 1.129 | 1.3828 | 1.4098 | 1.4465 | 1.129 | 1.4289 | 1.6358 | 1.66 | 1.6921 | 1.8091
2022-02-25 02:00 | 1.7719 | 1.9616 | 1.9912 | 2.0275 | 2.0697 | 1.0532 | 1.2863 | 1.3094 | 1.341 | 1.0532 | 1.3527 | 1.5443 | 1.5651 | 1.5926 | 1.7
2022-02-25 03:00 | 1.6957 | 1.8676 | 1.8911 | 1.9198 | 1.9532 | 1.0417 | 1.264 | 1.2823 | 1.3072 | 1.0417 | 1.467 | 1.6628 | 1.6792 | 1.701 | 1.8078
2022-02-25 04:00 | 1.7719 | 1.9377 | 1.9551 | 1.9764 | 2.0013 | 1.0098 | 1.2177 | 1.2312 | 1.2498 | 1.0098 | 1.3908 | 1.5697 | 1.5819 | 1.5981 | 1.694
2022-02-25 05:00 | 1.7806 | 1.937 | 1.9492 | 1.9642 | 1.9817 | 1.0669 | 1.2779 | 1.2874 | 1.3005 | 1.0669 | 1.5052 | 1.6896 | 1.6982 | 1.7096 | 1.806
2022-02-25 06:00 | 1.8862 | 2.0465 | 2.0567 | 2.0692 | 2.0838 | 1.3651 | 1.6272 | 1.6352 | 1.6461 | 1.3651 | 1.6766 | 1.8773 | 1.8845 | 1.894 | 1.9976
2022-02-25 07:00 | 2.3244 | 2.5206 | 2.5325 | 2.5471 | 2.5642 | 1.6576 | 1.9752 | 1.9845 | 1.9972 | 1.6576 | 1.81 | 2.0279 | 2.0363 | 2.0474 | 2.1602
2022-02-25 08:00 | 2.3054 | 2.5092 | 2.5258 | 2.5461 | 2.5697 | 1.6523 | 1.9755 | 1.9885 | 2.0061 | 1.6523 | 1.7909 | 2.0132 | 2.0248 | 2.0402 | 2.1571
2022-02-25 09:00 | 2.5708 | 2.8077 | 2.8311 | 2.8598 | 2.8932 | 1.5433 | 1.8564 | 1.8747 | 1.8996 | 1.5433 | 1.5433 | 1.7474 | 1.7638 | 1.7856 | 1.8965
2022-02-25 10:00 | 2.6102 | 2.8643 | 2.895 | 2.9325 | 2.9763 | 1.467 | 1.7767 | 1.8006 | 1.8333 | 1.467 | 1.6385 | 1.8634 | 1.8848 | 1.9134 | 2.0376
2022-02-25 11:00 | 2.3054 | 2.5477 | 2.584 | 2.6284 | 2.6801 | 1.3527 | 1.6496 | 1.6779 | 1.7165 | 1.3527 | 1.2956 | 1.49 | 1.5154 | 1.5492 | 1.6608
2022-02-25 12:00 | 2.553 | 2.8182 | 2.8567 | 2.9038 | 2.9587 | 1.448 | 1.7653 | 1.7953 | 1.8363 | 1.448 | 1.2003 | 1.3872 | 1.4142 | 1.45 | 1.5588
2022-02-25 13:00 | 2.4959 | 2.7557 | 2.7937 | 2.8401 | 2.8943 | 1.4289 | 1.742 | 1.7716 | 1.8121 | 1.4289 | 1.1622 | 1.3441 | 1.3707 | 1.406 | 1.5122
2022-02-25 14:00 | 2.4197 | 2.6689 | 2.7043 | 2.7476 | 2.7981 | 1.4099 | 1.7159 | 1.7435 | 1.7812 | 1.4099 | 1.1241 | 1.2983 | 1.3231 | 1.356 | 1.4572
2022-02-25 15:00 | 2.5149 | 2.7658 | 2.7984 | 2.8384 | 2.885 | 1.448 | 1.757 | 1.7825 | 1.8172 | 1.448 | 1.5623 | 1.7814 | 1.8043 | 1.8346 | 1.9569
2022-02-25 16:00 | 2.335 | 2.5689 | 2.5997 | 2.6374 | 2.6813 | 1.5433 | 1.8669 | 1.891 | 1.9238 | 1.5433 | 1.5242 | 1.7365 | 1.7581 | 1.7868 | 1.9048
2022-02-25 17:00 | 2.4768 | 2.7204 | 2.7508 | 2.7879 | 2.8313 | 1.6766 | 2.0239 | 2.0475 | 2.0799 | 1.6766 | 2.3625 | 2.6675 | 2.6887 | 2.717 | 2.8807
2022-02-25 18:00 | 2.4578 | 2.7035 | 2.7357 | 2.775 | 2.821 | 1.829 | 2.2065 | 2.2316 | 2.2659 | 1.829 | 2.553 | 2.8817 | 2.9042 | 2.9342 | 3.1104
2022-02-25 19:00 | 2.3435 | 2.588 | 2.624 | 2.6679 | 2.7192 | 1.7719 | 2.1443 | 2.1724 | 2.2106 | 1.7719 | 2.2863 | 2.5905 | 2.6157 | 2.6491 | 2.8148
2022-02-25 20:00 | 2.3816 | 2.6387 | 2.6796 | 2.7297 | 2.7881 | 1.7528 | 2.1289 | 2.1608 | 2.2044 | 1.7528 | 2.8007 | 3.1691 | 3.1977 | 3.2358 | 3.4353
2022-02-25 21:00 | 2.2291 | 2.4846 | 2.5305 | 2.5866 | 2.6521 | 1.6576 | 2.0234 | 2.0592 | 2.108 | 1.6576 | 2.4578 | 2.7948 | 2.8269 | 2.8696 | 3.0558
2022-02-25 22:00 | 2.0823 | 2.3285 | 2.3752 | 2.4323 | 2.499 | 1.5309 | 1.8749 | 1.9114 | 1.9611 | 1.5309 | 2.2863 | 2.6054 | 2.6381 | 2.6816 | 2.8593
2022-02-25 23:00 | 1.9815 | 2.2142 | 2.2579 | 2.3113 | 2.3736 | 1.3908 | 1.7051 | 1.7392 | 1.7857 | 1.3908 | 1.7147 | 1.966 | 1.9966 | 2.0373 | 2.1801
2022-02-26 | 1.8862 | 2.1034 | 2.1428 | 2.1909 | 2.247 | 1.2454 | 1.5272 | 1.5578 | 1.5997 | 1.2454 | 1.5433 | 1.7695 | 1.7971 | 1.8337 | 1.9623
2022-02-26 01:00 | 1.6957 | 1.8893 | 1.9238 | 1.966 | 2.0153 | 1.105 | 1.3545 | 1.3814 | 1.4182 | 1.105 | 1.3718 | 1.5723 | 1.5964 | 1.6286 | 1.7424
2022-02-26 02:00 | 1.642 | 1.8221 | 1.8517 | 1.8879 | 1.9302 | 1.0403 | 1.2711 | 1.2942 | 1.3258 | 1.0403 | 1.3908 | 1.5866 | 1.6074 | 1.635 | 1.7444
2022-02-26 03:00 | 1.6004 | 1.7653 | 1.7887 | 1.8174 | 1.8509 | 1.0479 | 1.2713 | 1.2896 | 1.3145 | 1.0479 | 1.2765 | 1.4511 | 1.4675 | 1.4893 | 1.5856
2022-02-26 04:00 | 1.6175 | 1.7718 | 1.7892 | 1.8106 | 1.8354 | 1.0098 | 1.2177 | 1.2312 | 1.2498 | 1.0098 | 1.3718 | 1.5485 | 1.5607 | 1.5769 | 1.6717
2022-02-26 05:00 | 1.6576 | 1.8048 | 1.8171 | 1.8321 | 1.8496 | 1.0497 | 1.2575 | 1.267 | 1.2801 | 1.0497 | 1.5623 | 1.7531 | 1.7617 | 1.7731 | 1.8727
2022-02-26 06:00 | 1.7338 | 1.8827 | 1.8929 | 1.9055 | 1.9201 | 1.0985 | 1.3123 | 1.3203 | 1.3312 | 1.0985 | 1.4289 | 1.6021 | 1.6093 | 1.6188 | 1.7087
2022-02-26 07:00 | 1.81 | 1.9679 | 1.9799 | 1.9945 | 2.0115 | 1.2956 | 1.5475 | 1.5568 | 1.5695 | 1.2956 | 1.467 | 1.6468 | 1.6552 | 1.6663 | 1.7602
2022-02-26 08:00 | 1.8817 | 2.0541 | 2.0706 | 2.0909 | 2.1146 | 1.3718 | 1.6441 | 1.6571 | 1.6747 | 1.3718 | 1.5052 | 1.6956 | 1.7072 | 1.7227 | 1.8239
2022-02-26 09:00 | 1.9243 | 2.1132 | 2.1366 | 2.1652 | 2.1986 | 1.3908 | 1.6763 | 1.6946 | 1.7195 | 1.3908 | 1.5242 | 1.7262 | 1.7426 | 1.7644 | 1.8742
2022-02-26 10:00 | 1.9624 | 2.1684 | 2.199 | 2.2366 | 2.2804 | 1.3908 | 1.6867 | 1.7106 | 1.7433 | 1.3908 | 1.3908 | 1.5881 | 1.6096 | 1.6382 | 1.7488
2022-02-26 11:00 | 2.0767 | 2.3021 | 2.3384 | 2.3828 | 2.4345 | 1.3718 | 1.6721 | 1.7004 | 1.739 | 1.3718 | 1.1241 | 1.2995 | 1.3249 | 1.3586 | 1.4608
2022-02-26 12:00 | 2.1148 | 2.3474 | 2.3859 | 2.433 | 2.4879 | 1.3908 | 1.6978 | 1.7278 | 1.7688 | 1.3908 | 1.6957 | 1.9377 | 1.9647 | 2.0005 | 2.1366
2022-02-26 13:00 | 1.9053 | 2.1212 | 2.1591 | 2.2056 | 2.2597 | 1.3146 | 1.607 | 1.6366 | 1.677 | 1.3146 | 1.5052 | 1.7252 | 1.7518 | 1.7871 | 1.9121
2022-02-26 14:00 | 1.7528 | 1.9524 | 1.9878 | 2.0312 | 2.0817 | 1.1241 | 1.3783 | 1.4059 | 1.4436 | 1.1241 | 0.97168 | 1.1289 | 1.1537 | 1.1866 | 1.2795
2022-02-26 15:00 | 1.958 | 2.1675 | 2.2001 | 2.2401 | 2.2867 | 1.2384 | 1.5094 | 1.5349 | 1.5696 | 1.2384 | 1.448 | 1.6544 | 1.6772 | 1.7076 | 1.8235
2022-02-26 16:00 | 2.0127 | 2.2226 | 2.2535 | 2.2912 | 2.3351 | 1.4223 | 1.724 | 1.7481 | 1.7809 | 1.4223 | 1.448 | 1.6518 | 1.6734 | 1.7021 | 1.816
2022-02-26 17:00 | 2.0577 | 2.2701 | 2.3005 | 2.3376 | 2.381 | 1.587 | 1.9179 | 1.9416 | 1.974 | 1.587 | 1.8672 | 2.117 | 2.1383 | 2.1665 | 2.303
2022-02-26 18:00 | 2.242 | 2.4716 | 2.5038 | 2.5432 | 2.5891 | 1.81 | 2.184 | 2.2091 | 2.2434 | 1.81 | 2.7817 | 3.1358 | 3.1583 | 3.1883 | 3.377
2022-02-26 19:00 | 2.3625 | 2.6085 | 2.6444 | 2.6884 | 2.7397 | 1.81 | 2.1893 | 2.2174 | 2.2556 | 1.81 | 2.3054 | 2.6117 | 2.6369 | 2.6703 | 2.837
2022-02-26 20:00 | 2.3244 | 2.5773 | 2.6182 | 2.6683 | 2.7267 | 1.7528 | 2.1289 | 2.1608 | 2.2044 | 1.7528 | 2.4006 | 2.7245 | 2.7531 | 2.7912 | 2.9687
2022-02-26 21:00 | 2.2482 | 2.5051 | 2.551 | 2.6071 | 2.6725 | 1.6727 | 2.0412 | 2.077 | 2.1258 | 1.6727 | 2.2291 | 2.5408 | 2.5729 | 2.6156 | 2.7892
2022-02-26 22:00 | 2.1513 | 2.4026 | 2.4493 | 2.5065 | 2.5731 | 1.5814 | 1.9345 | 1.971 | 2.0207 | 1.5814 | 2.3054 | 2.6266 | 2.6593 | 2.7028 | 2.8815
2022-02-26 23:00 | 1.9815 | 2.2142 | 2.2579 | 2.3113 | 2.3736 | 1.4289 | 1.7502 | 1.7842 | 1.8307 | 1.4289 | 1.8481 | 2.1142 | 2.1448 | 2.1855 | 2.3356
2022-02-27 | 1.8672 | 2.083 | 2.1223 | 2.1704 | 2.2266 | 1.2384 | 1.5189 | 1.5496 | 1.5915 | 1.2384 | 1.7719 | 2.0236 | 2.0511 | 2.0877 | 2.2289
2022-02-27 01:00 | 1.7719 | 1.9712 | 2.0057 | 2.0479 | 2.0972 | 1.1432 | 1.3995 | 1.4265 | 1.4632 | 1.1432 | 1.3527 | 1.5511 | 1.5753 | 1.6074 | 1.7202
2022-02-27 02:00 | 1.6385 | 1.8183 | 1.8479 | 1.8842 | 1.9264 | 1.0479 | 1.28 | 1.3031 | 1.3347 | 1.0479 | 1.2956 | 1.4808 | 1.5015 | 1.5291 | 1.6333
2022-02-27 03:00 | 1.6004 | 1.7653 | 1.7887 | 1.8174 | 1.8509 | 1.0074 | 1.2235 | 1.2418 | 1.2667 | 1.0074 | 1.6576 | 1.8745 | 1.8909 | 1.9128 | 2.03
2022-02-27 04:00 | 1.6195 | 1.7739 | 1.7913 | 1.8127 | 1.8375 | 1.0098 | 1.2177 | 1.2312 | 1.2498 | 1.0098 | 1.3718 | 1.5485 | 1.5607 | 1.5769 | 1.6717
2022-02-27 05:00 | 1.6195 | 1.7639 | 1.7761 | 1.7911 | 1.8086 | 1.0254 | 1.2288 | 1.2384 | 1.2514 | 1.0254 | 1.4289 | 1.6049 | 1.6135 | 1.6249 | 1.7171
2022-02-27 06:00 | 1.6576 | 1.8008 | 1.8111 | 1.8236 | 1.8382 | 1.079 | 1.2892 | 1.2972 | 1.3081 | 1.079 | 1.3908 | 1.5598 | 1.5669 | 1.5765 | 1.6643
2022-02-27 07:00 | 1.6766 | 1.8246 | 1.8366 | 1.8512 | 1.8682 | 1.2194 | 1.4575 | 1.4668 | 1.4795 | 1.2194 | 1.3908 | 1.5621 | 1.5705 | 1.5816 | 1.6713
2022-02-27 08:00 | 1.6576 | 1.8133 | 1.8298 | 1.8501 | 1.8738 | 1.2194 | 1.4641 | 1.477 | 1.4947 | 1.2194 | 1.2003 | 1.3568 | 1.3685 | 1.3839 | 1.4683
2022-02-27 09:00 | 1.7528 | 1.9289 | 1.9523 | 1.981 | 2.0144 | 1.2384 | 1.4963 | 1.5145 | 1.5394 | 1.2384 | 1.4289 | 1.6204 | 1.6368 | 1.6585 | 1.7631
2022-02-27 10:00 | 1.7719 | 1.9637 | 1.9943 | 2.0319 | 2.0757 | 1.3146 | 1.5967 | 1.6206 | 1.6533 | 1.3146 | 1.3718 | 1.5669 | 1.5884 | 1.617 | 1.7266
2022-02-27 11:00 | 1.7719 | 1.9746 | 2.0109 | 2.0553 | 2.107 | 1.105 | 1.357 | 1.3853 | 1.4239 | 1.105 | 1.0288 | 1.1936 | 1.219 | 1.2528 | 1.3497
2022-02-27 12:00 | 1.6004 | 1.7947 | 1.8332 | 1.8803 | 1.9352 | 1.0479 | 1.2927 | 1.3227 | 1.3637 | 1.0479 | 0.97168 | 1.1332 | 1.1601 | 1.1959 | 1.2922
2022-02-27 13:00 | 1.829 | 2.0393 | 2.0772 | 2.1237 | 2.1778 | 1.2384 | 1.517 | 1.5466 | 1.587 | 1.2384 | 1.4289 | 1.6405 | 1.6671 | 1.7025 | 1.8233
2022-02-27 14:00 | 1.9053 | 2.1162 | 2.1516 | 2.1949 | 2.2454 | 1.2194 | 1.4908 | 1.5184 | 1.5561 | 1.2194 | 1.448 | 1.6582 | 1.683 | 1.7159 | 1.835
2022-02-27 15:00 | 1.7528 | 1.947 | 1.9797 | 2.0196 | 2.0662 | 1.2384 | 1.5094 | 1.5349 | 1.5696 | 1.2384 | 1.2956 | 1.485 | 1.5078 | 1.5382 | 1.6458
2022-02-27 16:00 | 1.7909 | 1.9844 | 2.0152 | 2.0529 | 2.0969 | 1.0452 | 1.2785 | 1.3026 | 1.3354 | 1.0452 | 0.89547 | 1.0378 | 1.0594 | 1.0881 | 1.1716
2022-02-27 17:00 | 2.2673 | 2.4952 | 2.5256 | 2.5628 | 2.6061 | 1.5052 | 1.8213 | 1.845 | 1.8773 | 1.5052 | 1.9053 | 2.1593 | 2.1806 | 2.2089 | 2.3474
2022-02-27 18:00 | 2.4959 | 2.7444 | 2.7766 | 2.816 | 2.8619 | 1.9434 | 2.3415 | 2.3666 | 2.4009 | 1.9434 | 2.7245 | 3.0723 | 3.0948 | 3.1248 | 3.3103
2022-02-27 19:00 | 2.534 | 2.7927 | 2.8286 | 2.8726 | 2.9239 | 1.9624 | 2.3694 | 2.3974 | 2.4357 | 1.9624 | 2.4959 | 2.8234 | 2.8486 | 2.882 | 3.0592
2022-02-27 20:00 | 2.4992 | 2.7651 | 2.806 | 2.8561 | 2.9145 | 1.9624 | 2.3765 | 2.4084 | 2.452 | 1.9624 | 2.6102 | 2.9573 | 2.986 | 3.0241 | 3.2131
2022-02-27 21:00 | 2.4006 | 2.6689 | 2.7147 | 2.7708 | 2.8363 | 1.8553 | 2.257 | 2.2928 | 2.3416 | 1.8553 | 2.7626 | 3.1336 | 3.1657 | 3.2084 | 3.4113
2022-02-27 22:00 | 2.2673 | 2.5272 | 2.5739 | 2.631 | 2.6977 | 1.617 | 1.9766 | 2.0131 | 2.0628 | 1.617 | 2.2101 | 2.5207 | 2.5534 | 2.5969 | 2.7704
2022-02-27 23:00 | 2.0196 | 2.2552 | 2.2988 | 2.3522 | 2.4145 | 1.425 | 1.7455 | 1.7795 | 1.826 | 1.425 | 1.7528 | 2.0084 | 2.039 | 2.0796 | 2.2245
2022-02-28 | 1.8862 | 2.1034 | 2.1428 | 2.1909 | 2.247 | 1.2575 | 1.5414 | 1.5721 | 1.614 | 1.2575 | 1.5814 | 1.8118 | 1.8394 | 1.876 | 2.0067
2022-02-28 01:00 | 1.7462 | 1.9436 | 1.9781 | 2.0204 | 2.0696 | 1.0662 | 1.3086 | 1.3355 | 1.3723 | 1.0662 | 1.4289 | 1.6358 | 1.66 | 1.6921 | 1.8091
2022-02-28 02:00 | 1.6576 | 1.8388 | 1.8684 | 1.9046 | 1.9469 | 1.0264 | 1.2547 | 1.2778 | 1.3093 | 1.0264 | 1.2384 | 1.4173 | 1.438 | 1.4656 | 1.5666
2022-02-28 03:00 | 1.6195 | 1.7858 | 1.8092 | 1.8379 | 1.8714 | 0.97643 | 1.1869 | 1.2051 | 1.2301 | 0.97643 | 1.467 | 1.6628 | 1.6792 | 1.701 | 1.8078
2022-02-28 04:00 | 1.6921 | 1.852 | 1.8694 | 1.8907 | 1.9155 | 1.0098 | 1.2177 | 1.2312 | 1.2498 | 1.0098 | 1.4861 | 1.6756 | 1.6878 | 1.704 | 1.8051
2022-02-28 05:00 | 1.7909 | 1.9481 | 1.9603 | 1.9753 | 1.9928 | 1.1432 | 1.3679 | 1.3775 | 1.3905 | 1.1432 | 1.448 | 1.6261 | 1.6347 | 1.6461 | 1.7393
2022-02-28 06:00 | 1.9815 | 2.1488 | 2.159 | 2.1716 | 2.1862 | 1.3539 | 1.6139 | 1.6219 | 1.6328 | 1.3539 | 1.7528 | 1.962 | 1.9692 | 1.9787 | 2.0865
2022-02-28 07:00 | 2.2482 | 2.4387 | 2.4506 | 2.4652 | 2.4823 | 1.3908 | 1.66 | 1.6694 | 1.6821 | 1.3908 | 1.6766 | 1.8797 | 1.8881 | 1.8992 | 2.0046
2022-02-28 08:00 | 2.1339 | 2.325 | 2.3416 | 2.3619 | 2.3855 | 1.4861 | 1.7792 | 1.7921 | 1.8098 | 1.4861 | 1.6195 | 1.8226 | 1.8343 | 1.8497 | 1.9572
2022-02-28 09:00 | 2.3435 | 2.5635 | 2.5869 | 2.6155 | 2.6489 | 1.2765 | 1.5413 | 1.5595 | 1.5845 | 1.2765 | 1.105 | 1.2604 | 1.2768 | 1.2986 | 1.3854
2022-02-28 10:00 | 2.2291 | 2.4549 | 2.4856 | 2.5231 | 2.5669 | 1.1241 | 1.3716 | 1.3955 | 1.4282 | 1.1241 | 0.89547 | 1.0376 | 1.0591 | 1.0877 | 1.1711
2022-02-28 11:00 | 2.2673 | 2.5068 | 2.5431 | 2.5874 | 2.6392 | 1.1241 | 1.3795 | 1.4078 | 1.4464 | 1.1241 | 0.85737 | 1.003 | 1.0285 | 1.0622 | 1.1497
2022-02-28 12:00 | 2.172 | 2.4088 | 2.4473 | 2.4944 | 2.5493 | 1.0669 | 1.3152 | 1.3452 | 1.3862 | 1.0669 | 1.0288 | 1.1967 | 1.2236 | 1.2595 | 1.3589
2022-02-28 13:00 | 2.3054 | 2.551 | 2.589 | 2.6354 | 2.6896 | 1.0669 | 1.3144 | 1.344 | 1.3844 | 1.0669 | 1.7338 | 1.9793 | 2.0059 | 2.0412 | 2.1788
2022-02-28 14:00 | 2.1529 | 2.3823 | 2.4177 | 2.461 | 2.5115 | 1.086 | 1.3333 | 1.3609 | 1.3986 | 1.086 | 1.3908 | 1.5947 | 1.6195 | 1.6524 | 1.7683
2022-02-28 15:00 | 2.4768 | 2.7249 | 2.7575 | 2.7974 | 2.844 | 1.2956 | 1.5769 | 1.6024 | 1.6372 | 1.2956 | 1.5623 | 1.7814 | 1.8043 | 1.8346 | 1.9569
2022-02-28 16:00 | 2.3244 | 2.5575 | 2.5883 | 2.626 | 2.67 | 1.3337 | 1.6193 | 1.6434 | 1.6762 | 1.3337 | 1.086 | 1.2495 | 1.2711 | 1.2998 | 1.3938
2022-02-28 17:00 | 2.4768 | 2.7204 | 2.7508 | 2.7879 | 2.8313 | 1.6339 | 1.9733 | 1.997 | 2.0294 | 1.6339 | 1.9243 | 2.1805 | 2.2018 | 2.2301 | 2.3696
2022-02-28 18:00 | 2.6293 | 2.8877 | 2.9199 | 2.9593 | 3.0052 | 1.9053 | 2.2965 | 2.3216 | 2.3559 | 1.9053 | 2.553 | 2.8817 | 2.9042 | 2.9342 | 3.1104
2022-02-28 19:00 | 2.534 | 2.7927 | 2.8286 | 2.8726 | 2.9239 | 1.8862 | 2.2794 | 2.3074 | 2.3457 | 1.8862 | 2.8198 | 3.1833 | 3.2085 | 3.242 | 3.437
2022-02-28 20:00 | 2.553 | 2.8229 | 2.8639 | 2.9139 | 2.9723 | 1.8481 | 2.2414 | 2.2734 | 2.3169 | 1.8481 | 2.4578 | 2.788 | 2.8166 | 2.8547 | 3.0354
2022-02-28 21:00 | 2.3435 | 2.6074 | 2.6533 | 2.7094 | 2.7749 | 1.7683 | 2.1542 | 2.1899 | 2.2388 | 1.7683 | 2.6293 | 2.9854 | 3.0175 | 3.0602 | 3.2558
2022-02-28 22:00 | 2.2101 | 2.4658 | 2.5125 | 2.5696 | 2.6363 | 1.5814 | 1.9345 | 1.971 | 2.0207 | 1.5814 | 2.191 | 2.4996 | 2.5323 | 2.5757 | 2.7482
2022-02-28 23:00 | 1.9881 | 2.2213 | 2.265 | 2.3184 | 2.3807 | 1.3729 | 1.6839 | 1.718 | 1.7645 | 1.3729 | 1.9624 | 2.2413 | 2.2719 | 2.3125 | 2.469
2022-03-01 | 1.8672 | 2.083 | 2.1223 | 2.1704 | 2.2266 | 1.1709 | 1.4392 | 1.4699 | 1.5118 | 1.1709 | 1.6385 | 1.8754 | 1.9029 | 1.9395 | 2.0734
2022-03-01 01:00 | 1.7954 | 1.9964 | 2.0309 | 2.0731 | 2.1224 | 1.0728 | 1.3164 | 1.3434 | 1.3801 | 1.0728 | 1.3908 | 1.5934 | 1.6176 | 1.6497 | 1.7646
2022-03-01 02:00 | 1.6612 | 1.8427 | 1.8723 | 1.9086 | 1.9508 | 1.0288 | 1.2575 | 1.2806 | 1.3122 | 1.0288 | 1.3337 | 1.5231 | 1.5439 | 1.5715 | 1.6777
2022-03-01 03:00 | 1.6576 | 1.8267 | 1.8501 | 1.8788 | 1.9123 | 1.0098 | 1.2263 | 1.2445 | 1.2695 | 1.0098 | 1.2765 | 1.4511 | 1.4675 | 1.4893 | 1.5856
2022-03-01 04:00 | 1.6576 | 1.8149 | 1.8323 | 1.8536 | 1.8784 | 1.0098 | 1.2177 | 1.2312 | 1.2498 | 1.0098 | 1.3337 | 1.5062 | 1.5184 | 1.5346 | 1.6273
2022-03-01 05:00 | 1.7719 | 1.9276 | 1.9399 | 1.9549 | 1.9724 | 1.0843 | 1.2984 | 1.3079 | 1.321 | 1.0843 | 1.3146 | 1.4779 | 1.4865 | 1.4979 | 1.5838
2022-03-01 06:00 | 1.9391 | 2.1032 | 2.1135 | 2.126 | 2.1406 | 1.3017 | 1.5523 | 1.5603 | 1.5712 | 1.3017 | 1.5433 | 1.7291 | 1.7363 | 1.7458 | 1.8421
2022-03-01 07:00 | 2.172 | 2.3568 | 2.3688 | 2.3834 | 2.4004 | 1.3586 | 1.6219 | 1.6312 | 1.644 | 1.3586 | 1.9434 | 2.1761 | 2.1845 | 2.1956 | 2.3157
2022-03-01 08:00 | 2.2863 | 2.4887 | 2.5053 | 2.5256 | 2.5493 | 1.3718 | 1.6441 | 1.6571 | 1.6747 | 1.3718 | 1.7528 | 1.9708 | 1.9825 | 1.9979 | 2.1127
2022-03-01 09:00 | 2.2101 | 2.4202 | 2.4436 | 2.4722 | 2.5056 | 1.1813 | 1.4288 | 1.447 | 1.4719 | 1.1813 | 1.2003 | 1.3663 | 1.3827 | 1.4045 | 1.4965
2022-03-01 10:00 | 2.1805 | 2.4026 | 2.4333 | 2.4708 | 2.5146 | 1.1432 | 1.3941 | 1.418 | 1.4507 | 1.1432 | 1.3146 | 1.5034 | 1.5249 | 1.5535 | 1.6599
2022-03-01 11:00 | 2.4006 | 2.6501 | 2.6863 | 2.7307 | 2.7825 | 1.1622 | 1.4245 | 1.4528 | 1.4915 | 1.1622 | 1.2575 | 1.4477 | 1.4731 | 1.5068 | 1.6163
2022-03-01 12:00 | 2.4387 | 2.6954 | 2.7338 | 2.7809 | 2.8359 | 1.1241 | 1.3827 | 1.4127 | 1.4537 | 1.1241 | 1.448 | 1.6625 | 1.6894 | 1.7253 | 1.8477
2022-03-01 13:00 | 2.4106 | 2.6641 | 2.702 | 2.7485 | 2.8026 | 1.2194 | 1.4945 | 1.5241 | 1.5645 | 1.2194 | 1.0669 | 1.2383 | 1.2649 | 1.3002 | 1.4011
2022-03-01 14:00 | 2.4197 | 2.6689 | 2.7043 | 2.7476 | 2.7981 | 1.2003 | 1.4683 | 1.4959 | 1.5336 | 1.2003 | 1.448 | 1.6582 | 1.683 | 1.7159 | 1.835
2022-03-01 15:00 | 2.2291 | 2.4588 | 2.4914 | 2.5313 | 2.5779 | 1.2003 | 1.4644 | 1.4899 | 1.5246 | 1.2003 | 1.7719 | 2.0143 | 2.0371 | 2.0675 | 2.2013
2022-03-01 16:00 | 2.3816 | 2.6189 | 2.6497 | 2.6874 | 2.7314 | 1.448 | 1.7544 | 1.7784 | 1.8112 | 1.448 | 1.5623 | 1.7788 | 1.8004 | 1.8291 | 1.9493
2022-03-01 17:00 | 2.3435 | 2.5771 | 2.6075 | 2.6447 | 2.688 | 1.5623 | 1.8888 | 1.9125 | 1.9448 | 1.5623 | 1.81 | 2.0535 | 2.0747 | 2.103 | 2.2363
2022-03-01 18:00 | 2.4578 | 2.7035 | 2.7357 | 2.775 | 2.821 | 1.8481 | 2.229 | 2.2541 | 2.2884 | 1.8481 | 2.3435 | 2.6488 | 2.6714 | 2.7013 | 2.866
2022-03-01 19:00 | 2.4768 | 2.7313 | 2.7672 | 2.8112 | 2.8625 | 1.9053 | 2.3019 | 2.3299 | 2.3682 | 1.9053 | 2.553 | 2.8869 | 2.9121 | 2.9455 | 3.1259
2022-03-01 20:00 | 2.4578 | 2.7206 | 2.7615 | 2.8116 | 2.87 | 1.7909 | 2.1739 | 2.2058 | 2.2494 | 1.7909 | 2.4197 | 2.7456 | 2.7743 | 2.8124 | 2.9909
2022-03-01 21:00 | 2.3435 | 2.6074 | 2.6533 | 2.7094 | 2.7749 | 1.7528 | 2.1359 | 2.1717 | 2.2205 | 1.7528 | 2.4768 | 2.816 | 2.8481 | 2.8908 | 3.078
2022-03-01 22:00 | 2.1754 | 2.4286 | 2.4752 | 2.5324 | 2.599 | 1.5006 | 1.8391 | 1.8755 | 1.9252 | 1.5006 | 2.0196 | 2.309 | 2.3417 | 2.3852 | 2.5482
2022-03-01 23:00 | 1.9053 | 2.1323 | 2.176 | 2.2294 | 2.2917 | 1.3484 | 1.655 | 1.689 | 1.7355 | 1.3484 | 1.7719 | 2.0296 | 2.0601 | 2.1008 | 2.2468
2022-03-02 | 1.7528 | 1.9601 | 1.9995 | 2.0476 | 2.1038 | 1.1506 | 1.4152 | 1.4459 | 1.4878 | 1.1506 | 1.7528 | 2.0024 | 2.03 | 2.0666 | 2.2067
2022-03-02 01:00 | 1.7147 | 1.9098 | 1.9443 | 1.9865 | 2.0358 | 1.0669 | 1.3095 | 1.3364 | 1.3732 | 1.0669 | 1.3908 | 1.5934 | 1.6176 | 1.6497 | 1.7646
2022-03-02 02:00 | 1.6576 | 1.8388 | 1.8684 | 1.9046 | 1.9469 | 1.0098 | 1.235 | 1.2581 | 1.2897 | 1.0098 | 1.2575 | 1.4384 | 1.4592 | 1.4868 | 1.5889
2022-03-02 03:00 | 1.6004 | 1.7653 | 1.7887 | 1.8174 | 1.8509 | 0.96362 | 1.1717 | 1.19 | 1.215 | 0.96362 | 1.2765 | 1.4511 | 1.4675 | 1.4893 | 1.5856
2022-03-02 04:00 | 1.6576 | 1.8149 | 1.8323 | 1.8536 | 1.8784 | 1.0137 | 1.2223 | 1.2359 | 1.2545 | 1.0137 | 1.2384 | 1.4003 | 1.4125 | 1.4287 | 1.5162
2022-03-02 05:00 | 1.7719 | 1.9276 | 1.9399 | 1.9549 | 1.9724 | 1.1002 | 1.3172 | 1.3267 | 1.3398 | 1.1002 | 1.5242 | 1.7108 | 1.7194 | 1.7308 | 1.8282
2022-03-02 06:00 | 1.9434 | 2.1079 | 2.1181 | 2.1306 | 2.1452 | 1.3189 | 1.5726 | 1.5806 | 1.5915 | 1.3189 | 1.5923 | 1.7837 | 1.7908 | 1.8004 | 1.8993
2022-03-02 07:00 | 2.3264 | 2.5227 | 2.5346 | 2.5492 | 2.5663 | 1.5433 | 1.8401 | 1.8494 | 1.8621 | 1.5433 | 2.0386 | 2.282 | 2.2903 | 2.3015 | 2.4268
2022-03-02 08:00 | 2.3816 | 2.5911 | 2.6077 | 2.6279 | 2.6516 | 1.5623 | 1.8692 | 1.8821 | 1.8998 | 1.5623 | 1.9053 | 2.1402 | 2.1518 | 2.1673 | 2.2905
2022-03-02 09:00 | 2.3816 | 2.6044 | 2.6278 | 2.6565 | 2.6899 | 1.467 | 1.7664 | 1.7846 | 1.8095 | 1.467 | 1.6195 | 1.8321 | 1.8485 | 1.8703 | 1.9853
2022-03-02 10:00 | 2.3816 | 2.6187 | 2.6493 | 2.6869 | 2.7307 | 1.3908 | 1.6867 | 1.7106 | 1.7433 | 1.3908 | 1.3908 | 1.5881 | 1.6096 | 1.6382 | 1.7488
2022-03-02 11:00 | 2.2291 | 2.4659 | 2.5021 | 2.5465 | 2.5983 | 1.2194 | 1.4921 | 1.5204 | 1.559 | 1.2194 | 1.1241 | 1.2995 | 1.3249 | 1.3586 | 1.4608
2022-03-02 12:00 | 2.2482 | 2.4907 | 2.5292 | 2.5763 | 2.6312 | 1.3337 | 1.6303 | 1.6603 | 1.7013 | 1.3337 | 1.1622 | 1.3449 | 1.3718 | 1.4077 | 1.5144
2022-03-02 13:00 | 2.2937 | 2.5385 | 2.5764 | 2.6229 | 2.677 | 1.3337 | 1.6295 | 1.6591 | 1.6995 | 1.3337 | 1.2575 | 1.45 | 1.4766 | 1.5119 | 1.6233
2022-03-02 14:00 | 2.3054 | 2.546 | 2.5814 | 2.6248 | 2.6753 | 1.3162 | 1.6053 | 1.6329 | 1.6706 | 1.3162 | 1.4289 | 1.637 | 1.6618 | 1.6948 | 1.8127
2022-03-02 15:00 | 2.2863 | 2.5202 | 2.5528 | 2.5927 | 2.6393 | 1.3527 | 1.6445 | 1.6699 | 1.7047 | 1.3527 | 1.448 | 1.6544 | 1.6772 | 1.7076 | 1.8235
2022-03-02 16:00 | 2.2863 | 2.5166 | 2.5474 | 2.5851 | 2.629 | 1.467 | 1.7769 | 1.8009 | 1.8337 | 1.467 | 1.9434 | 2.2023 | 2.2239 | 2.2525 | 2.3937
2022-03-02 17:00 | 2.3054 | 2.5362 | 2.5665 | 2.6037 | 2.647 | 1.7147 | 2.0689 | 2.0926 | 2.1249 | 1.7147 | 2.3054 | 2.604 | 2.6252 | 2.6535 | 2.814
2022-03-02 18:00 | 2.3816 | 2.6216 | 2.6538 | 2.6932 | 2.7391 | 1.829 | 2.2065 | 2.2316 | 2.2659 | 1.829 | 2.0958 | 2.3736 | 2.3961 | 2.4261 | 2.5771
2022-03-02 19:00 | 2.4959 | 2.7518 | 2.7877 | 2.8317 | 2.883 | 1.8273 | 2.2097 | 2.2378 | 2.276 | 1.8273 | 2.4578 | 2.7811 | 2.8062 | 2.8397 | 3.0148
2022-03-02 20:00 | 2.4959 | 2.7615 | 2.8024 | 2.8525 | 2.9109 | 1.829 | 2.2189 | 2.2508 | 2.2944 | 1.829 | 2.8007 | 3.1691 | 3.1977 | 3.2358 | 3.4353
2022-03-02 21:00 | 2.3816 | 2.6484 | 2.6942 | 2.7504 | 2.8158 | 1.6903 | 2.062 | 2.0978 | 2.1466 | 1.6903 | 2.3054 | 2.6254 | 2.6576 | 2.7003 | 2.878
2022-03-02 22:00 | 2.1529 | 2.4044 | 2.4511 | 2.5082 | 2.5749 | 1.5373 | 1.8825 | 1.9189 | 1.9686 | 1.5373 | 2.4578 | 2.796 | 2.8287 | 2.8722 | 3.0592
2022-03-02 23:00 | 1.9468 | 2.177 | 2.2206 | 2.2741 | 2.3364 | 1.3278 | 1.6307 | 1.6647 | 1.7112 | 1.3278 | 1.6766 | 1.9237 | 1.9543 | 1.9949 | 2.1357
2022-03-03 | 1.7528 | 1.9601 | 1.9995 | 2.0476 | 2.1038 | 1.139 | 1.4015 | 1.4322 | 1.4741 | 1.139 | 1.467 | 1.6848 | 1.7124 | 1.749 | 1.8734
2022-03-03 01:00 | 1.7147 | 1.9098 | 1.9443 | 1.9865 | 2.0358 | 1.0653 | 1.3076 | 1.3345 | 1.3713 | 1.0653 | 1.5623 | 1.784 | 1.8082 | 1.8403 | 1.9646
2022-03-03 02:00 | 1.6576 | 1.8388 | 1.8684 | 1.9046 | 1.9469 | 0.99715 | 1.2201 | 1.2432 | 1.2747 | 0.99715 | 1.448 | 1.6502 | 1.6709 | 1.6985 | 1.8111
2022-03-03 03:00 | 1.6004 | 1.7653 | 1.7887 | 1.8174 | 1.8509 | 0.99073 | 1.2037 | 1.222 | 1.247 | 0.99073 | 1.4289 | 1.6204 | 1.6369 | 1.6587 | 1.7634
2022-03-03 04:00 | 1.6576 | 1.8149 | 1.8323 | 1.8536 | 1.8784 | 1.0098 | 1.2177 | 1.2312 | 1.2498 | 1.0098 | 1.3527 | 1.5274 | 1.5396 | 1.5558 | 1.6495
2022-03-03 05:00 | 1.7719 | 1.9276 | 1.9399 | 1.9549 | 1.9724 | 1.1108 | 1.3296 | 1.3392 | 1.3523 | 1.1108 | 1.3908 | 1.5626 | 1.5712 | 1.5826 | 1.6727
2022-03-03 06:00 | 1.9434 | 2.1079 | 2.1181 | 2.1306 | 2.1452 | 1.3032 | 1.5541 | 1.5621 | 1.573 | 1.3032 | 1.7719 | 1.9832 | 1.9904 | 1.9999 | 2.1087
2022-03-03 07:00 | 2.3264 | 2.5227 | 2.5346 | 2.5492 | 2.5663 | 2.6102 | 3.1005 | 3.1099 | 3.1226 | 2.6102 | 1.7528 | 1.9644 | 1.9728 | 1.9839 | 2.0935
2022-03-03 08:00 | 2.3816 | 2.5911 | 2.6077 | 2.6279 | 2.6516 | 2.1148 | 2.5219 | 2.5349 | 2.5525 | 2.1148 | 1.6004 | 1.8015 | 1.8131 | 1.8285 | 1.9349
2022-03-03 09:00 | 2.3816 | 2.6044 | 2.6278 | 2.6565 | 2.6899 | 1.6957 | 2.0365 | 2.0547 | 2.0796 | 1.6957 | 1.1432 | 1.3028 | 1.3192 | 1.341 | 1.4299
2022-03-03 10:00 | 2.3816 | 2.6187 | 2.6493 | 2.6869 | 2.7307 | 1.6957 | 2.0468 | 2.0707 | 2.1034 | 1.6957 | 0.93358 | 1.08 | 1.1015 | 1.13 | 1.2155
2022-03-03 11:00 | 2.2291 | 2.4659 | 2.5021 | 2.5465 | 2.5983 | 1.4861 | 1.8072 | 1.8355 | 1.8741 | 1.4861 | 1.0479 | 1.2148 | 1.2402 | 1.2739 | 1.3719
2022-03-03 12:00 | 2.2482 | 2.4907 | 2.5292 | 2.5763 | 2.6312 | 1.2575 | 1.5402 | 1.5703 | 1.6112 | 1.2575 | 1.8862 | 2.1494 | 2.1764 | 2.2122 | 2.3587
2022-03-03 13:00 | 2.2937 | 2.5385 | 2.5764 | 2.6229 | 2.677 | 1.2765 | 1.562 | 1.5916 | 1.632 | 1.2765 | 1.9053 | 2.1699 | 2.1964 | 2.2318 | 2.3787
2022-03-03 14:00 | 2.3054 | 2.546 | 2.5814 | 2.6248 | 2.6753 | 1.2194 | 1.4908 | 1.5184 | 1.5561 | 1.2194 | 2.1339 | 2.4204 | 2.4452 | 2.4781 | 2.6349
2022-03-03 15:00 | 2.2863 | 2.5202 | 2.5528 | 2.5927 | 2.6393 | 1.467 | 1.7795 | 1.805 | 1.8397 | 1.467 | 1.7147 | 1.9508 | 1.9736 | 2.004 | 2.1346
2022-03-03 16:00 | 2.2863 | 2.5166 | 2.5474 | 2.5851 | 2.629 | 1.7147 | 2.0695 | 2.0935 | 2.1263 | 1.7147 | 1.3337 | 1.5248 | 1.5464 | 1.575 | 1.6826
2022-03-03 17:00 | 2.3054 | 2.5362 | 2.5665 | 2.6037 | 2.647 | 1.6957 | 2.0464 | 2.0701 | 2.1024 | 1.6957 | 1.3718 | 1.5665 | 1.5878 | 1.6161 | 1.7253
2022-03-03 18:00 | 2.3816 | 2.6216 | 2.6538 | 2.6932 | 2.7391 | 2.2863 | 2.7467 | 2.7718 | 2.8061 | 2.2863 | 2.3054 | 2.6065 | 2.629 | 2.659 | 2.8215
2022-03-03 19:00 | 2.4959 | 2.7518 | 2.7877 | 2.8317 | 2.883 | 2.3244 | 2.7971 | 2.8251 | 2.8633 | 2.3244 | 2.6483 | 2.9928 | 3.018 | 3.0514 | 3.237
2022-03-03 20:00 | 2.4959 | 2.7615 | 2.8024 | 2.8525 | 2.9109 | 2.3244 | 2.8041 | 2.8361 | 2.8796 | 2.3244 | 2.3816 | 2.7033 | 2.7319 | 2.77 | 2.9465
2022-03-03 21:00 | 2.3816 | 2.6484 | 2.6942 | 2.7504 | 2.8158 | 2.2101 | 2.6761 | 2.7119 | 2.7607 | 2.2101 | 2.534 | 2.8795 | 2.9116 | 2.9543 | 3.1447
2022-03-03 22:00 | 2.1529 | 2.4044 | 2.4511 | 2.5082 | 2.5749 | 2.0196 | 2.4522 | 2.4886 | 2.5384 | 2.0196 | 2.1148 | 2.4149 | 2.4476 | 2.4911 | 2.6593
2022-03-03 23:00 | 1.9468 | 2.177 | 2.2206 | 2.2741 | 2.3364 | 1.7056 | 2.0769 | 2.111 | 2.1575 | 1.7056 | 2.0196 | 2.3048 | 2.3354 | 2.376 | 2.5356
2022-03-04 | 1.7528 | 1.9601 | 1.9995 | 2.0476 | 2.1038 | 1.5433 | 1.8791 | 1.9097 | 1.9516 | 1.5433 | 1.4289 | 1.6425 | 1.67 | 1.7066 | 1.829
2022-03-04 01:00 | 1.7147 | 1.9098 | 1.9443 | 1.9865 | 2.0358 | 1.3527 | 1.6471 | 1.674 | 1.7108 | 1.3527 | 1.3337 | 1.5299 | 1.5541 | 1.5862 | 1.698
2022-03-04 02:00 | 1.6576 | 1.8388 | 1.8684 | 1.9046 | 1.9469 | 1.2492 | 1.5178 | 1.5409 | 1.5724 | 1.2492 | 1.2384 | 1.4173 | 1.438 | 1.4656 | 1.5666
2022-03-04 03:00 | 1.6004 | 1.7653 | 1.7887 | 1.8174 | 1.8509 | 1.2575 | 1.5189 | 1.5371 | 1.5621 | 1.2575 | 1.2765 | 1.4511 | 1.4675 | 1.4893 | 1.5856
2022-03-04 04:00 | 1.6576 | 1.8149 | 1.8323 | 1.8536 | 1.8784 | 1.2804 | 1.5373 | 1.5509 | 1.5694 | 1.2804 | 1.3146 | 1.485 | 1.4972 | 1.5134 | 1.6051
2022-03-04 05:00 | 1.7719 | 1.9276 | 1.9399 | 1.9549 | 1.9724 | 1.5602 | 1.8606 | 1.8701 | 1.8832 | 1.5602 | 1.3718 | 1.5414 | 1.55 | 1.5614 | 1.6505
2022-03-04 06:00 | 1.9434 | 2.1079 | 2.1181 | 2.1306 | 2.1452 | 1.8868 | 2.2435 | 2.2515 | 2.2624 | 1.8868 | 1.5814 | 1.7715 | 1.7787 | 1.7882 | 1.8865
2022-03-04 07:00 | 2.3264 | 2.5227 | 2.5346 | 2.5492 | 2.5663 | 2.1148 | 2.5153 | 2.5247 | 2.5374 | 2.1148 | 1.7338 | 1.9432 | 1.9516 | 1.9627 | 2.0713
2022-03-04 08:00 | 2.3816 | 2.5911 | 2.6077 | 2.6279 | 2.6516 | 2.0958 | 2.4994 | 2.5124 | 2.53 | 2.0958 | 1.5433 | 1.7379 | 1.7496 | 1.765 | 1.8683
2022-03-04 09:00 | 2.3816 | 2.6044 | 2.6278 | 2.6565 | 2.6899 | 1.6957 | 2.0365 | 2.0547 | 2.0796 | 1.6957 | 1.2003 | 1.3663 | 1.3827 | 1.4045 | 1.4965
2022-03-04 10:00 | 2.3816 | 2.6187 | 2.6493 | 2.6869 | 2.7307 | 1.5623 | 1.8893 | 1.9132 | 1.9459 | 1.5623 | 1.3146 | 1.5034 | 1.5249 | 1.5535 | 1.6599
2022-03-04 11:00 | 2.2291 | 2.4659 | 2.5021 | 2.5465 | 2.5983 | 1.5052 | 1.8297 | 1.858 | 1.8966 | 1.5052 | 1.5052 | 1.7229 | 1.7483 | 1.7821 | 1.9052
2022-03-04 12:00 | 2.2482 | 2.4907 | 2.5292 | 2.5763 | 2.6312 | 1.3718 | 1.6753 | 1.7053 | 1.7463 | 1.3718 | 1.3908 | 1.5989 | 1.6259 | 1.6617 | 1.781
2022-03-04 13:00 | 2.2937 | 2.5385 | 2.5764 | 2.6229 | 2.677 | 1.467 | 1.7871 | 1.8167 | 1.8571 | 1.467 | 1.2575 | 1.45 | 1.4766 | 1.5119 | 1.6233
2022-03-04 14:00 | 2.3054 | 2.546 | 2.5814 | 2.6248 | 2.6753 | 1.3146 | 1.6034 | 1.631 | 1.6687 | 1.3146 | 1.6766 | 1.9123 | 1.9371 | 1.97 | 2.1016
2022-03-04 15:00 | 2.2863 | 2.5202 | 2.5528 | 2.5927 | 2.6393 | 1.7377 | 2.0993 | 2.1247 | 2.1595 | 1.7377 | 1.4099 | 1.612 | 1.6349 | 1.6653 | 1.7791
2022-03-04 16:00 | 2.2863 | 2.5166 | 2.5474 | 2.5851 | 2.629 | 2.0386 | 2.4521 | 2.4762 | 2.509 | 2.0386 | 1.4289 | 1.6306 | 1.6522 | 1.6809 | 1.7937
2022-03-04 17:00 | 2.3054 | 2.5362 | 2.5665 | 2.6037 | 2.647 | 2.1009 | 2.5251 | 2.5488 | 2.5811 | 2.1009 | 2.3054 | 2.604 | 2.6252 | 2.6535 | 2.814
2022-03-04 18:00 | 2.3816 | 2.6216 | 2.6538 | 2.6932 | 2.7391 | 2.2673 | 2.7242 | 2.7493 | 2.7835 | 2.2673 | 2.6483 | 2.9876 | 3.0101 | 3.0401 | 3.2215
2022-03-04 19:00 | 2.4959 | 2.7518 | 2.7877 | 2.8317 | 2.883 | 2.2482 | 2.707 | 2.735 | 2.7733 | 2.2482 | 2.2863 | 2.5905 | 2.6157 | 2.6491 | 2.8148
2022-03-04 20:00 | 2.4959 | 2.7615 | 2.8024 | 2.8525 | 2.9109 | 2.3244 | 2.8041 | 2.8361 | 2.8796 | 2.3244 | 2.4197 | 2.7456 | 2.7743 | 2.8124 | 2.9909
2022-03-04 21:00 | 2.3816 | 2.6484 | 2.6942 | 2.7504 | 2.8158 | 2.191 | 2.6536 | 2.6894 | 2.7382 | 2.191 | 2.5149 | 2.8583 | 2.8905 | 2.9332 | 3.1225
2022-03-04 22:00 | 2.1529 | 2.4044 | 2.4511 | 2.5082 | 2.5749 | 2.0333 | 2.4684 | 2.5048 | 2.5546 | 2.0333 | 2.4768 | 2.8171 | 2.8499 | 2.8933 | 3.0815
2022-03-04 23:00 | 1.9468 | 2.177 | 2.2206 | 2.2741 | 2.3364 | 1.7947 | 2.1823 | 2.2163 | 2.2628 | 1.7947 | 1.8862 | 2.1566 | 2.1872 | 2.2278 | 2.3801
2022-03-05 | 1.7528 | 1.9601 | 1.9995 | 2.0476 | 2.1038 | 1.5852 | 1.9286 | 1.9592 | 2.0011 | 1.5852 | 1.7147 | 1.9601 | 1.9876 | 2.0242 | 2.1623
2022-03-05 01:00 | 1.7147 | 1.9098 | 1.9443 | 1.9865 | 2.0358 | 1.4289 | 1.7372 | 1.7641 | 1.8008 | 1.4289 | 1.6195 | 1.8475 | 1.8717 | 1.9038 | 2.0312
2022-03-05 02:00 | 1.6576 | 1.8388 | 1.8684 | 1.9046 | 1.9469 | 1.2898 | 1.5659 | 1.589 | 1.6205 | 1.2898 | 1.448 | 1.6502 | 1.6709 | 1.6985 | 1.8111
2022-03-05 03:00 | 1.6004 | 1.7653 | 1.7887 | 1.8174 | 1.8509 | 1.2575 | 1.5189 | 1.5371 | 1.5621 | 1.2575 | 1.3146 | 1.4934 | 1.5098 | 1.5317 | 1.63
2022-03-05 04:00 | 1.6576 | 1.8149 | 1.8323 | 1.8536 | 1.8784 | 1.2765 | 1.5328 | 1.5464 | 1.5649 | 1.2765 | 1.4861 | 1.6756 | 1.6878 | 1.704 | 1.8051
2022-03-05 05:00 | 1.7719 | 1.9276 | 1.9399 | 1.9549 | 1.9724 | 1.3673 | 1.6327 | 1.6423 | 1.6554 | 1.3673 | 1.5242 | 1.7108 | 1.7194 | 1.7308 | 1.8282
2022-03-05 06:00 | 1.9434 | 2.1079 | 2.1181 | 2.1306 | 2.1452 | 1.4928 | 1.778 | 1.786 | 1.7969 | 1.4928 | 1.4289 | 1.6021 | 1.6093 | 1.6188 | 1.7087
2022-03-05 07:00 | 2.3264 | 2.5227 | 2.5346 | 2.5492 | 2.5663 | 1.6957 | 2.0202 | 2.0295 | 2.0422 | 1.6957 | 1.5814 | 1.7739 | 1.7822 | 1.7933 | 1.8935
2022-03-05 08:00 | 2.3816 | 2.5911 | 2.6077 | 2.6279 | 2.6516 | 1.81 | 2.1618 | 2.1748 | 2.1924 | 1.81 | 1.6385 | 1.8438 | 1.8554 | 1.8709 | 1.9794
2022-03-05 09:00 | 2.3816 | 2.6044 | 2.6278 | 2.6565 | 2.6899 | 1.6195 | 1.9464 | 1.9647 | 1.9896 | 1.6195 | 1.3908 | 1.578 | 1.5944 | 1.6162 | 1.7187
2022-03-05 10:00 | 2.3816 | 2.6187 | 2.6493 | 2.6869 | 2.7307 | 1.7147 | 2.0693 | 2.0933 | 2.1259 | 1.7147 | 1.3908 | 1.5881 | 1.6096 | 1.6382 | 1.7488
2022-03-05 11:00 | 2.2291 | 2.4659 | 2.5021 | 2.5465 | 2.5983 | 1.5623 | 1.8972 | 1.9255 | 1.9641 | 1.5623 | 1.2384 | 1.4265 | 1.4519 | 1.4857 | 1.5941
2022-03-05 12:00 | 2.2482 | 2.4907 | 2.5292 | 2.5763 | 2.6312 | 1.0479 | 1.2927 | 1.3227 | 1.3637 | 1.0479 | 1.3337 | 1.5354 | 1.5624 | 1.5982 | 1.7144
2022-03-05 13:00 | 2.2937 | 2.5385 | 2.5764 | 2.6229 | 2.677 | 1.4099 | 1.7195 | 1.7491 | 1.7895 | 1.4099 | 1.2956 | 1.4923 | 1.5189 | 1.5543 | 1.6677
2022-03-05 14:00 | 2.3054 | 2.546 | 2.5814 | 2.6248 | 2.6753 | 1.9243 | 2.3236 | 2.3512 | 2.3889 | 1.9243 | 2.3435 | 2.6533 | 2.6781 | 2.711 | 2.8793
2022-03-05 15:00 | 2.2863 | 2.5202 | 2.5528 | 2.5927 | 2.6393 | 1.9624 | 2.3647 | 2.3902 | 2.4249 | 1.9624 | 2.191 | 2.4801 | 2.5029 | 2.5333 | 2.6901
2022-03-05 16:00 | 2.2863 | 2.5166 | 2.5474 | 2.5851 | 2.629 | 2.2482 | 2.6997 | 2.7238 | 2.7566 | 2.2482 | 2.4006 | 2.7104 | 2.732 | 2.7607 | 2.9269
2022-03-05 17:00 | 2.3054 | 2.5362 | 2.5665 | 2.6037 | 2.647 | 2.3054 | 2.7666 | 2.7903 | 2.8226 | 2.3054 | 3.0103 | 3.3873 | 3.4086 | 3.4369 | 3.6362
2022-03-05 18:00 | 2.3816 | 2.6216 | 2.6538 | 2.6932 | 2.7391 | 2.2673 | 2.7242 | 2.7493 | 2.7835 | 2.2673 | 2.7626 | 3.1146 | 3.1371 | 3.1671 | 3.3548
2022-03-05 19:00 | 2.4959 | 2.7518 | 2.7877 | 2.8317 | 2.883 | 2.1529 | 2.5945 | 2.6225 | 2.6608 | 2.1529 | 2.3435 | 2.654 | 2.6792 | 2.7127 | 2.8815
2022-03-05 20:00 | 2.4959 | 2.7615 | 2.8024 | 2.8525 | 2.9109 | 2.0958 | 2.534 | 2.566 | 2.6095 | 2.0958 | 2.3054 | 2.6186 | 2.6473 | 2.6853 | 2.8576
2022-03-05 21:00 | 2.3816 | 2.6484 | 2.6942 | 2.7504 | 2.8158 | 2.0331 | 2.467 | 2.5028 | 2.5516 | 2.0331 | 2.191 | 2.4984 | 2.5305 | 2.5732 | 2.7447
2022-03-05 22:00 | 2.1529 | 2.4044 | 2.4511 | 2.5082 | 2.5749 | 1.8325 | 2.2312 | 2.2676 | 2.3173 | 1.8325 | 2.0005 | 2.2878 | 2.3206 | 2.364 | 2.526
2022-03-05 23:00 | 1.9468 | 2.177 | 2.2206 | 2.2741 | 2.3364 | 1.6652 | 2.0292 | 2.0633 | 2.1098 | 1.6652 | 1.8862 | 2.1566 | 2.1872 | 2.2278 | 2.3801
2022-03-06 | 1.7528 | 1.9601 | 1.9995 | 2.0476 | 2.1038 | 1.5756 | 1.9172 | 1.9479 | 1.9898 | 1.5756 | 1.6576 | 1.8965 | 1.9241 | 1.9607 | 2.0956
2022-03-06 01:00 | 1.7147 | 1.9098 | 1.9443 | 1.9865 | 2.0358 | 1.3432 | 1.6359 | 1.6628 | 1.6996 | 1.3432 | 1.4099 | 1.6146 | 1.6388 | 1.6709 | 1.7868
2022-03-06 02:00 | 1.6576 | 1.8388 | 1.8684 | 1.9046 | 1.9469 | 1.2765 | 1.5501 | 1.5732 | 1.6048 | 1.2765 | 1.3337 | 1.5231 | 1.5439 | 1.5715 | 1.6777
2022-03-06 03:00 | 1.6004 | 1.7653 | 1.7887 | 1.8174 | 1.8509 | 1.2384 | 1.4963 | 1.5146 | 1.5396 | 1.2384 | 1.3527 | 1.5357 | 1.5522 | 1.574 | 1.6745
2022-03-06 04:00 | 1.6576 | 1.8149 | 1.8323 | 1.8536 | 1.8784 | 1.2118 | 1.4563 | 1.4699 | 1.4884 | 1.2118 | 1.2384 | 1.4003 | 1.4125 | 1.4287 | 1.5162
2022-03-06 05:00 | 1.7719 | 1.9276 | 1.9399 | 1.9549 | 1.9724 | 1.2888 | 1.54 | 1.5495 | 1.5626 | 1.2888 | 1.2956 | 1.4567 | 1.4653 | 1.4767 | 1.5616
2022-03-06 06:00 | 1.9434 | 2.1079 | 2.1181 | 2.1306 | 2.1452 | 1.3309 | 1.5869 | 1.5948 | 1.6057 | 1.3309 | 1.3146 | 1.4751 | 1.4822 | 1.4918 | 1.5754
2022-03-06 07:00 | 2.3264 | 2.5227 | 2.5346 | 2.5492 | 2.5663 | 1.4289 | 1.7051 | 1.7144 | 1.7271 | 1.4289 | 1.448 | 1.6256 | 1.634 | 1.6451 | 1.738
2022-03-06 08:00 | 2.3816 | 2.5911 | 2.6077 | 2.6279 | 2.6516 | 1.5433 | 1.8467 | 1.8596 | 1.8773 | 1.5433 | 1.5242 | 1.7168 | 1.7284 | 1.7438 | 1.8461
2022-03-06 09:00 | 2.3816 | 2.6044 | 2.6278 | 2.6565 | 2.6899 | 1.5052 | 1.8114 | 1.8296 | 1.8546 | 1.5052 | 1.1813 | 1.3451 | 1.3615 | 1.3833 | 1.4743
2022-03-06 10:00 | 2.3816 | 2.6187 | 2.6493 | 2.6869 | 2.7307 | 1.6385 | 1.9793 | 2.0032 | 2.0359 | 1.6385 | 1.3718 | 1.5669 | 1.5884 | 1.617 | 1.7266
2022-03-06 11:00 | 2.2291 | 2.4659 | 2.5021 | 2.5465 | 2.5983 | 1.4572 | 1.773 | 1.8013 | 1.8399 | 1.4572 | 1.3122 | 1.5085 | 1.5339 | 1.5676 | 1.6802
2022-03-06 12:00 | 2.2482 | 2.4907 | 2.5292 | 2.5763 | 2.6312 | 1.5052 | 1.8328 | 1.8629 | 1.9038 | 1.5052 | 1.4099 | 1.6201 | 1.6471 | 1.6829 | 1.8033
2022-03-06 13:00 | 2.2937 | 2.5385 | 2.5764 | 2.6229 | 2.677 | 1.5623 | 1.8996 | 1.9292 | 1.9696 | 1.5623 | 1.467 | 1.6829 | 1.7095 | 1.7448 | 1.8677
2022-03-06 14:00 | 2.3054 | 2.546 | 2.5814 | 2.6248 | 2.6753 | 1.1432 | 1.4008 | 1.4284 | 1.4661 | 1.1432 | 1.1622 | 1.3406 | 1.3654 | 1.3984 | 1.5017
2022-03-06 15:00 | 2.2863 | 2.5202 | 2.5528 | 2.5927 | 2.6393 | 1.6833 | 2.035 | 2.0605 | 2.0952 | 1.6833 | 1.7338 | 1.9719 | 1.9948 | 2.0252 | 2.1568
2022-03-06 16:00 | 2.2863 | 2.5166 | 2.5474 | 2.5851 | 2.629 | 1.7719 | 2.137 | 2.1611 | 2.1939 | 1.7719 | 1.5623 | 1.7788 | 1.8004 | 1.8291 | 1.9493
2022-03-06 17:00 | 2.3054 | 2.5362 | 2.5665 | 2.6037 | 2.647 | 1.9815 | 2.384 | 2.4077 | 2.44 | 1.9815 | 1.8862 | 2.1382 | 2.1594 | 2.1877 | 2.3252
2022-03-06 18:00 | 2.3816 | 2.6216 | 2.6538 | 2.6932 | 2.7391 | 2.1148 | 2.5441 | 2.5692 | 2.6035 | 2.1148 | 2.3054 | 2.6065 | 2.629 | 2.659 | 2.8215
2022-03-06 19:00 | 2.4959 | 2.7518 | 2.7877 | 2.8317 | 2.883 | 2.3238 | 2.7963 | 2.8243 | 2.8626 | 2.3238 | 2.4006 | 2.7175 | 2.7427 | 2.7762 | 2.9481
2022-03-06 20:00 | 2.4959 | 2.7615 | 2.8024 | 2.8525 | 2.9109 | 2.3625 | 2.8492 | 2.8811 | 2.9246 | 2.3625 | 2.534 | 2.8727 | 2.9013 | 2.9394 | 3.1243
2022-03-06 21:00 | 2.3816 | 2.6484 | 2.6942 | 2.7504 | 2.8158 | 2.2291 | 2.6986 | 2.7344 | 2.7832 | 2.2291 | 2.4387 | 2.7736 | 2.8058 | 2.8485 | 3.0336
2022-03-06 22:00 | 2.1529 | 2.4044 | 2.4511 | 2.5082 | 2.5749 | 1.9611 | 2.3832 | 2.4196 | 2.4693 | 1.9611 | 2.2101 | 2.5207 | 2.5534 | 2.5969 | 2.7704
2022-03-06 23:00 | 1.9468 | 2.177 | 2.2206 | 2.2741 | 2.3364 | 1.7323 | 2.1085 | 2.1425 | 2.189 | 1.7323 | 1.9243 | 2.1989 | 2.2295 | 2.2701 | 2.4245
2022-03-07 | 1.7528 | 1.9601 | 1.9995 | 2.0476 | 2.1038 | 1.5291 | 1.8624 | 1.893 | 1.9349 | 1.5291 | 1.6004 | 1.833 | 1.8606 | 1.8972 | 2.029
2022-03-07 01:00 | 1.7147 | 1.9098 | 1.9443 | 1.9865 | 2.0358 | 1.3337 | 1.6246 | 1.6515 | 1.6883 | 1.3337 | 1.2956 | 1.4876 | 1.5117 | 1.5439 | 1.6535
2022-03-07 02:00 | 1.6576 | 1.8388 | 1.8684 | 1.9046 | 1.9469 | 1.2708 | 1.5434 | 1.5665 | 1.598 | 1.2708 | 1.4289 | 1.629 | 1.6497 | 1.6773 | 1.7888
2022-03-07 03:00 | 1.6004 | 1.7653 | 1.7887 | 1.8174 | 1.8509 | 1.2384 | 1.4963 | 1.5146 | 1.5396 | 1.2384 | 1.3337 | 1.5146 | 1.531 | 1.5528 | 1.6523
2022-03-07 04:00 | 1.6576 | 1.8149 | 1.8323 | 1.8536 | 1.8784 | 1.2956 | 1.5553 | 1.5689 | 1.5874 | 1.2956 | 1.2956 | 1.4639 | 1.4761 | 1.4923 | 1.5829
2022-03-07 05:00 | 1.7719 | 1.9276 | 1.9399 | 1.9549 | 1.9724 | 1.4904 | 1.7782 | 1.7877 | 1.8008 | 1.4904 | 1.467 | 1.6473 | 1.6559 | 1.6673 | 1.7616
2022-03-07 06:00 | 1.9434 | 2.1079 | 2.1181 | 2.1306 | 2.1452 | 1.8874 | 2.2443 | 2.2523 | 2.2632 | 1.8874 | 1.7719 | 1.9832 | 1.9904 | 1.9999 | 2.1087
2022-03-07 07:00 | 2.3264 | 2.5227 | 2.5346 | 2.5492 | 2.5663 | 2.0386 | 2.4253 | 2.4346 | 2.4473 | 2.0386 | 1.8481 | 2.0703 | 2.0786 | 2.0897 | 2.2046
2022-03-07 08:00 | 2.3816 | 2.5911 | 2.6077 | 2.6279 | 2.6516 | 2.172 | 2.5895 | 2.6024 | 2.6201 | 2.172 | 1.6385 | 1.8438 | 1.8554 | 1.8709 | 1.9794
2022-03-07 09:00 | 2.3816 | 2.6044 | 2.6278 | 2.6565 | 2.6899 | 1.9243 | 2.3066 | 2.3248 | 2.3497 | 1.9243 | 0.99073 | 1.1334 | 1.1498 | 1.1716 | 1.2521
2022-03-07 10:00 | 2.3816 | 2.6187 | 2.6493 | 2.6869 | 2.7307 | 1.7147 | 2.0693 | 2.0933 | 2.1259 | 1.7147 | 1.3337 | 1.5246 | 1.5461 | 1.5746 | 1.6821
2022-03-07 11:00 | 2.2291 | 2.4659 | 2.5021 | 2.5465 | 2.5983 | 1.4706 | 1.7889 | 1.8171 | 1.8558 | 1.4706 | 1.5623 | 1.7864 | 1.8118 | 1.8456 | 1.9718
2022-03-07 12:00 | 2.2482 | 2.4907 | 2.5292 | 2.5763 | 2.6312 | 1.6766 | 2.0354 | 2.0654 | 2.1064 | 1.6766 | 1.829 | 2.0859 | 2.1129 | 2.1487 | 2.2921
2022-03-07 13:00 | 2.2937 | 2.5385 | 2.5764 | 2.6229 | 2.677 | 1.8672 | 2.2597 | 2.2893 | 2.3297 | 1.8672 | 0.97168 | 1.1324 | 1.159 | 1.1943 | 1.29
2022-03-07 14:00 | 2.3054 | 2.546 | 2.5814 | 2.6248 | 2.6753 | 1.6957 | 2.0535 | 2.0811 | 2.1188 | 1.6957 | 1.0098 | 1.1712 | 1.196 | 1.229 | 1.3239
2022-03-07 15:00 | 2.2863 | 2.5202 | 2.5528 | 2.5927 | 2.6393 | 1.7528 | 2.1171 | 2.1426 | 2.1773 | 1.7528 | 1.3718 | 1.5697 | 1.5925 | 1.6229 | 1.7347
2022-03-07 16:00 | 2.2863 | 2.5166 | 2.5474 | 2.5851 | 2.629 | 1.9243 | 2.3171 | 2.3411 | 2.3739 | 1.9243 | 1.8862 | 2.1388 | 2.1604 | 2.189 | 2.327
2022-03-07 17:00 | 2.3054 | 2.5362 | 2.5665 | 2.6037 | 2.647 | 2.0958 | 2.519 | 2.5427 | 2.5751 | 2.0958 | 1.9624 | 2.2229 | 2.2441 | 2.2724 | 2.4141
2022-03-07 18:00 | 2.3816 | 2.6216 | 2.6538 | 2.6932 | 2.7391 | 2.3054 | 2.7692 | 2.7943 | 2.8286 | 2.3054 | 2.4959 | 2.8182 | 2.8407 | 2.8707 | 3.0437
2022-03-07 19:00 | 2.4959 | 2.7518 | 2.7877 | 2.8317 | 2.883 | 2.3244 | 2.7971 | 2.8251 | 2.8633 | 2.3244 | 2.3816 | 2.6964 | 2.7215 | 2.755 | 2.9259
2022-03-07 20:00 | 2.4959 | 2.7615 | 2.8024 | 2.8525 | 2.9109 | 2.2863 | 2.7591 | 2.791 | 2.8346 | 2.2863 | 2.3625 | 2.6821 | 2.7108 | 2.7489 | 2.9243
2022-03-07 21:00 | 2.3816 | 2.6484 | 2.6942 | 2.7504 | 2.8158 | 2.191 | 2.6536 | 2.6894 | 2.7382 | 2.191 | 2.172 | 2.4772 | 2.5094 | 2.5521 | 2.7225
2022-03-07 22:00 | 2.1529 | 2.4044 | 2.4511 | 2.5082 | 2.5749 | 1.92 | 2.3346 | 2.371 | 2.4207 | 1.92 | 2.553 | 2.9018 | 2.9345 | 2.978 | 3.1703
2022-03-07 23:00 | 1.9468 | 2.177 | 2.2206 | 2.2741 | 2.3364 | 1.6957 | 2.0653 | 2.0993 | 2.1458 | 1.6957 | 1.8862 | 2.1566 | 2.1872 | 2.2278 | 2.3801
2022-03-08 | 1.7528 | 1.9601 | 1.9995 | 2.0476 | 2.1038 | 1.4999 | 1.8279 | 1.8586 | 1.9004 | 1.4999 | 1.6195 | 1.8542 | 1.8818 | 1.9184 | 2.0512
2022-03-08 01:00 | 1.7147 | 1.9098 | 1.9443 | 1.9865 | 2.0358 | 1.3152 | 1.6028 | 1.6297 | 1.6664 | 1.3152 | 1.2765 | 1.4664 | 1.4906 | 1.5227 | 1.6313
2022-03-08 02:00 | 1.6576 | 1.8388 | 1.8684 | 1.9046 | 1.9469 | 1.2765 | 1.5501 | 1.5732 | 1.6048 | 1.2765 | 1.3527 | 1.5443 | 1.5651 | 1.5926 | 1.7
2022-03-08 03:00 | 1.6004 | 1.7653 | 1.7887 | 1.8174 | 1.8509 | 1.2384 | 1.4963 | 1.5146 | 1.5396 | 1.2384 | 1.2575 | 1.4299 | 1.4463 | 1.4681 | 1.5634
2022-03-08 04:00 | 1.6576 | 1.8149 | 1.8323 | 1.8536 | 1.8784 | 1.2575 | 1.5103 | 1.5238 | 1.5424 | 1.2575 | 1.448 | 1.6332 | 1.6454 | 1.6616 | 1.7606
2022-03-08 05:00 | 1.7719 | 1.9276 | 1.9399 | 1.9549 | 1.9724 | 1.4986 | 1.7878 | 1.7974 | 1.8104 | 1.4986 | 1.3337 | 1.4991 | 1.5077 | 1.5191 | 1.606
2022-03-08 06:00 | 1.9434 | 2.1079 | 2.1181 | 2.1306 | 2.1452 | 1.8969 | 2.2554 | 2.2634 | 2.2743 | 1.8969 | 1.7719 | 1.9832 | 1.9904 | 1.9999 | 2.1087
2022-03-08 07:00 | 2.3264 | 2.5227 | 2.5346 | 2.5492 | 2.5663 | 2.2101 | 2.6279 | 2.6372 | 2.6499 | 2.2101 | 1.9434 | 2.1761 | 2.1845 | 2.1956 | 2.3157
2022-03-08 08:00 | 2.3816 | 2.5911 | 2.6077 | 2.6279 | 2.6516 | 2.2056 | 2.6292 | 2.6421 | 2.6598 | 2.2056 | 1.829 | 2.0555 | 2.0671 | 2.0826 | 2.2016
2022-03-08 09:00 | 2.3816 | 2.6044 | 2.6278 | 2.6565 | 2.6899 | 2.0577 | 2.4641 | 2.4824 | 2.5073 | 2.0577 | 1.7719 | 2.0015 | 2.0179 | 2.0396 | 2.1631
2022-03-08 10:00 | 2.3816 | 2.6187 | 2.6493 | 2.6869 | 2.7307 | 1.8422 | 2.2199 | 2.2438 | 2.2765 | 1.8422 | 1.0479 | 1.207 | 1.2285 | 1.2571 | 1.3488
2022-03-08 11:00 | 2.2291 | 2.4659 | 2.5021 | 2.5465 | 2.5983 | 1.691 | 2.0492 | 2.0775 | 2.1161 | 1.691 | 0.91452 | 1.0666 | 1.092 | 1.1257 | 1.2164
2022-03-08 12:00 | 2.2482 | 2.4907 | 2.5292 | 2.5763 | 2.6312 | 1.6957 | 2.0579 | 2.0879 | 2.1289 | 1.6957 | 0.91452 | 1.0696 | 1.0966 | 1.1324 | 1.2255
2022-03-08 13:00 | 2.2937 | 2.5385 | 2.5764 | 2.6229 | 2.677 | 1.6576 | 2.0121 | 2.0417 | 2.0821 | 1.6576 | 0.99073 | 1.1536 | 1.1802 | 1.2155 | 1.3122
2022-03-08 14:00 | 2.3054 | 2.546 | 2.5814 | 2.6248 | 2.6753 | 1.6766 | 2.031 | 2.0586 | 2.0963 | 1.6766 | 1.0288 | 1.1924 | 1.2172 | 1.2502 | 1.3461
2022-03-08 15:00 | 2.2863 | 2.5202 | 2.5528 | 2.5927 | 2.6393 | 1.5242 | 1.847 | 1.8725 | 1.9072 | 1.5242 | 1.086 | 1.2521 | 1.2749 | 1.3053 | 1.4014
2022-03-08 16:00 | 2.2863 | 2.5166 | 2.5474 | 2.5851 | 2.629 | 1.9628 | 2.3625 | 2.3866 | 2.4194 | 1.9628 | 1.5814 | 1.8 | 1.8216 | 1.8503 | 1.9715
2022-03-08 17:00 | 2.3054 | 2.5362 | 2.5665 | 2.6037 | 2.647 | 2.194 | 2.635 | 2.6587 | 2.6911 | 2.194 | 2.2116 | 2.4997 | 2.521 | 2.5493 | 2.7047
2022-03-08 18:00 | 2.3816 | 2.6216 | 2.6538 | 2.6932 | 2.7391 | 2.3054 | 2.7692 | 2.7943 | 2.8286 | 2.3054 | 2.8007 | 3.1569 | 3.1795 | 3.2094 | 3.3992
2022-03-08 19:00 | 2.4959 | 2.7518 | 2.7877 | 2.8317 | 2.883 | 2.3816 | 2.8646 | 2.8926 | 2.9309 | 2.3816 | 2.553 | 2.8869 | 2.9121 | 2.9455 | 3.1259
2022-03-08 20:00 | 2.4959 | 2.7615 | 2.8024 | 2.8525 | 2.9109 | 2.2452 | 2.7106 | 2.7425 | 2.7861 | 2.2452 | 2.4768 | 2.8091 | 2.8378 | 2.8759 | 3.0576
2022-03-08 21:00 | 2.3816 | 2.6484 | 2.6942 | 2.7504 | 2.8158 | 2.1158 | 2.5647 | 2.6005 | 2.6493 | 2.1158 | 2.6483 | 3.0065 | 3.0387 | 3.0814 | 3.278
2022-03-08 22:00 | 2.1529 | 2.4044 | 2.4511 | 2.5082 | 2.5749 | 1.8905 | 2.2997 | 2.3361 | 2.3859 | 1.8905 | 2.3625 | 2.6901 | 2.7228 | 2.7663 | 2.9481
2022-03-08 23:00 | 1.9468 | 2.177 | 2.2206 | 2.2741 | 2.3364 | 1.6487 | 2.0098 | 2.0438 | 2.0903 | 1.6487 | 1.8481 | 2.1142 | 2.1448 | 2.1855 | 2.3356
2022-03-09 | 1.7528 | 1.9601 | 1.9995 | 2.0476 | 2.1038 | 1.448 | 1.7665 | 1.7972 | 1.8391 | 1.448 | 1.467 | 1.6848 | 1.7124 | 1.749 | 1.8734
2022-03-09 01:00 | 1.7147 | 1.9098 | 1.9443 | 1.9865 | 2.0358 | 1.3527 | 1.6471 | 1.674 | 1.7108 | 1.3527 | 1.467 | 1.6781 | 1.7023 | 1.7344 | 1.8535
2022-03-09 02:00 | 1.6576 | 1.8388 | 1.8684 | 1.9046 | 1.9469 | 1.2575 | 1.5276 | 1.5507 | 1.5823 | 1.2575 | 1.2956 | 1.4808 | 1.5015 | 1.5291 | 1.6333
2022-03-09 03:00 | 1.6004 | 1.7653 | 1.7887 | 1.8174 | 1.8509 | 1.2765 | 1.5414 | 1.5597 | 1.5846 | 1.2765 | 1.4099 | 1.5993 | 1.6157 | 1.6375 | 1.7411
2022-03-09 04:00 | 1.6576 | 1.8149 | 1.8323 | 1.8536 | 1.8784 | 1.3146 | 1.5778 | 1.5914 | 1.6099 | 1.3146 | 1.3337 | 1.5062 | 1.5184 | 1.5346 | 1.6273
2022-03-09 05:00 | 1.7719 | 1.9276 | 1.9399 | 1.9549 | 1.9724 | 1.5532 | 1.8523 | 1.8619 | 1.8749 | 1.5532 | 1.3527 | 1.5202 | 1.5288 | 1.5402 | 1.6282
2022-03-09 06:00 | 1.9434 | 2.1079 | 2.1181 | 2.1306 | 2.1452 | 1.937 | 2.3029 | 2.3108 | 2.3217 | 1.937 | 1.6766 | 1.8773 | 1.8845 | 1.894 | 1.9976
2022-03-09 07:00 | 2.3264 | 2.5227 | 2.5346 | 2.5492 | 2.5663 | 2.2291 | 2.6504 | 2.6597 | 2.6724 | 2.2291 | 1.9434 | 2.1761 | 2.1845 | 2.1956 | 2.3157
2022-03-09 08:00 | 2.3816 | 2.5911 | 2.6077 | 2.6279 | 2.6516 | 2.0577 | 2.4544 | 2.4674 | 2.485 | 2.0577 | 1.5623 | 1.7591 | 1.7707 | 1.7862 | 1.8905
2022-03-09 09:00 | 2.3816 | 2.6044 | 2.6278 | 2.6565 | 2.6899 | 1.8676 | 2.2395 | 2.2578 | 2.2827 | 1.8676 | 1.3527 | 1.5357 | 1.5521 | 1.5739 | 1.6743
2022-03-09 10:00 | 2.3816 | 2.6187 | 2.6493 | 2.6869 | 2.7307 | 1.5052 | 1.8217 | 1.8457 | 1.8783 | 1.5052 | 1.5433 | 1.7575 | 1.779 | 1.8075 | 1.9265
2022-03-09 11:00 | 2.2291 | 2.4659 | 2.5021 | 2.5465 | 2.5983 | 0.81926 | 1.0194 | 1.0477 | 1.0863 | 0.81926 | 2.0005 | 2.2734 | 2.2988 | 2.3325 | 2.4829
2022-03-09 12:00 | 2.2482 | 2.4907 | 2.5292 | 2.5763 | 2.6312 | 1.467 | 1.7878 | 1.8178 | 1.8588 | 1.467 | 1.3309 | 1.5324 | 1.5594 | 1.5952 | 1.7112
2022-03-09 13:00 | 2.2937 | 2.5385 | 2.5764 | 2.6229 | 2.677 | 1.448 | 1.7646 | 1.7942 | 1.8346 | 1.448 | 1.105 | 1.2806 | 1.3072 | 1.3425 | 1.4455
2022-03-09 14:00 | 2.3054 | 2.546 | 2.5814 | 2.6248 | 2.6753 | 1.448 | 1.7609 | 1.7885 | 1.8262 | 1.448 | 1.2575 | 1.4465 | 1.4713 | 1.5042 | 1.6128
2022-03-09 15:00 | 2.2863 | 2.5202 | 2.5528 | 2.5927 | 2.6393 | 1.2575 | 1.5319 | 1.5574 | 1.5921 | 1.2575 | 2.0767 | 2.353 | 2.3759 | 2.4063 | 2.5568
2022-03-09 16:00 | 2.2863 | 2.5166 | 2.5474 | 2.5851 | 2.629 | 1.3581 | 1.6482 | 1.6722 | 1.705 | 1.3581 | 1.086 | 1.2495 | 1.2711 | 1.2998 | 1.3938
2022-03-09 17:00 | 2.3054 | 2.5362 | 2.5665 | 2.6037 | 2.647 | 1.8277 | 2.2023 | 2.226 | 2.2583 | 1.8277 | 1.7528 | 1.99 | 2.0112 | 2.0395 | 2.1697
2022-03-09 18:00 | 2.3816 | 2.6216 | 2.6538 | 2.6932 | 2.7391 | 2.1278 | 2.5595 | 2.5846 | 2.6189 | 2.1278 | 2.2482 | 2.5429 | 2.5655 | 2.5954 | 2.7549
2022-03-09 19:00 | 2.4959 | 2.7518 | 2.7877 | 2.8317 | 2.883 | 2.2673 | 2.7295 | 2.7576 | 2.7958 | 2.2673 | 2.3816 | 2.6964 | 2.7215 | 2.755 | 2.9259
2022-03-09 20:00 | 2.4959 | 2.7615 | 2.8024 | 2.8525 | 2.9109 | 2.2863 | 2.7591 | 2.791 | 2.8346 | 2.2863 | 2.915 | 3.2961 | 3.3248 | 3.3629 | 3.5687
2022-03-09 21:00 | 2.3816 | 2.6484 | 2.6942 | 2.7504 | 2.8158 | 2.0958 | 2.5411 | 2.5768 | 2.6257 | 2.0958 | 2.2291 | 2.5408 | 2.5729 | 2.6156 | 2.7892
2022-03-09 22:00 | 2.1529 | 2.4044 | 2.4511 | 2.5082 | 2.5749 | 1.8699 | 2.2754 | 2.3118 | 2.3616 | 1.8699 | 2.0767 | 2.3725 | 2.4052 | 2.4487 | 2.6148
2022-03-09 23:00 | 1.9468 | 2.177 | 2.2206 | 2.2741 | 2.3364 | 1.6898 | 2.0583 | 2.0923 | 2.1388 | 1.6898 | 1.8672 | 2.1354 | 2.166 | 2.2066 | 2.3579
2022-03-10 | 1.7528 | 1.9601 | 1.9995 | 2.0476 | 2.1038 | 1.4861 | 1.8115 | 1.8422 | 1.8841 | 1.4861 | 1.4099 | 1.6213 | 1.6489 | 1.6855 | 1.8068
2022-03-10 01:00 | 1.7147 | 1.9098 | 1.9443 | 1.9865 | 2.0358 | 1.3074 | 1.5936 | 1.6205 | 1.6573 | 1.3074 | 1.3718 | 1.5723 | 1.5964 | 1.6286 | 1.7424
2022-03-10 02:00 | 1.6576 | 1.8388 | 1.8684 | 1.9046 | 1.9469 | 1.2575 | 1.5276 | 1.5507 | 1.5823 | 1.2575 | 1.5623 | 1.7772 | 1.798 | 1.8255 | 1.9444
2022-03-10 03:00 | 1.6004 | 1.7653 | 1.7887 | 1.8174 | 1.8509 | 1.2765 | 1.5414 | 1.5597 | 1.5846 | 1.2765 | 1.2765 | 1.4511 | 1.4675 | 1.4893 | 1.5856
2022-03-10 04:00 | 1.6576 | 1.8149 | 1.8323 | 1.8536 | 1.8784 | 1.2765 | 1.5328 | 1.5464 | 1.5649 | 1.2765 | 1.2575 | 1.4215 | 1.4337 | 1.4499 | 1.5384
2022-03-10 05:00 | 1.7719 | 1.9276 | 1.9399 | 1.9549 | 1.9724 | 1.5242 | 1.8181 | 1.8276 | 1.8407 | 1.5242 | 1.3718 | 1.5414 | 1.55 | 1.5614 | 1.6505
2022-03-10 06:00 | 1.9434 | 2.1079 | 2.1181 | 2.1306 | 2.1452 | 1.8896 | 2.2468 | 2.2548 | 2.2657 | 1.8896 | 1.7147 | 1.9197 | 1.9269 | 1.9364 | 2.042
2022-03-10 07:00 | 2.3264 | 2.5227 | 2.5346 | 2.5492 | 2.5663 | 2.3244 | 2.7629 | 2.7722 | 2.7849 | 2.3244 | 2.0958 | 2.3455 | 2.3539 | 2.365 | 2.4935
2022-03-10 08:00 | 2.3816 | 2.5911 | 2.6077 | 2.6279 | 2.6516 | 2.3054 | 2.747 | 2.76 | 2.7776 | 2.3054 | 2.172 | 2.4366 | 2.4482 | 2.4637 | 2.6015
2022-03-10 09:00 | 2.3816 | 2.6044 | 2.6278 | 2.6565 | 2.6899 | 2.0588 | 2.4655 | 2.4837 | 2.5086 | 2.0588 | 1.448 | 1.6415 | 1.6579 | 1.6797 | 1.7854
2022-03-10 10:00 | 2.3816 | 2.6187 | 2.6493 | 2.6869 | 2.7307 | 1.3337 | 1.6192 | 1.6431 | 1.6758 | 1.3337 | 1.4156 | 1.6156 | 1.6371 | 1.6657 | 1.7776
2022-03-10 11:00 | 2.2291 | 2.4659 | 2.5021 | 2.5465 | 2.5983 | 1.2194 | 1.4921 | 1.5204 | 1.559 | 1.2194 | 1.6195 | 1.8499 | 1.8753 | 1.9091 | 2.0385
2022-03-10 12:00 | 2.2482 | 2.4907 | 2.5292 | 2.5763 | 2.6312 | 1.105 | 1.3602 | 1.3902 | 1.4312 | 1.105 | 1.6385 | 1.8742 | 1.9011 | 1.937 | 2.0699
2022-03-10 13:00 | 2.2937 | 2.5385 | 2.5764 | 2.6229 | 2.677 | 0.87642 | 1.0893 | 1.1189 | 1.1593 | 0.87642 | 1.9624 | 2.2334 | 2.26 | 2.2953 | 2.4454
2022-03-10 14:00 | 2.3054 | 2.546 | 2.5814 | 2.6248 | 2.6753 | 1.0479 | 1.2883 | 1.3159 | 1.3536 | 1.0479 | 2.4006 | 2.7168 | 2.7416 | 2.7746 | 2.9459
2022-03-10 15:00 | 2.2863 | 2.5202 | 2.5528 | 2.5927 | 2.6393 | 1.4099 | 1.712 | 1.7374 | 1.7722 | 1.4099 | 1.6766 | 1.9084 | 1.9313 | 1.9617 | 2.0902
2022-03-10 16:00 | 2.2863 | 2.5166 | 2.5474 | 2.5851 | 2.629 | 1.2384 | 1.5068 | 1.5308 | 1.5636 | 1.2384 | 1.3146 | 1.5036 | 1.5252 | 1.5539 | 1.6604
2022-03-10 17:00 | 2.3054 | 2.5362 | 2.5665 | 2.6037 | 2.647 | 1.8672 | 2.2489 | 2.2726 | 2.305 | 1.8672 | 1.6195 | 1.8418 | 1.863 | 1.8913 | 2.0141
2022-03-10 18:00 | 2.3816 | 2.6216 | 2.6538 | 2.6932 | 2.7391 | 2.1073 | 2.5352 | 2.5603 | 2.5946 | 2.1073 | 2.2291 | 2.5218 | 2.5443 | 2.5743 | 2.7326
2022-03-10 19:00 | 2.4959 | 2.7518 | 2.7877 | 2.8317 | 2.883 | 2.2291 | 2.6845 | 2.7125 | 2.7508 | 2.2291 | 2.6293 | 2.9716 | 2.9968 | 3.0302 | 3.2148
2022-03-10 20:00 | 2.4959 | 2.7615 | 2.8024 | 2.8525 | 2.9109 | 2.3244 | 2.8041 | 2.8361 | 2.8796 | 2.3244 | 2.3054 | 2.6186 | 2.6473 | 2.6853 | 2.8576
2022-03-10 21:00 | 2.3816 | 2.6484 | 2.6942 | 2.7504 | 2.8158 | 2.1292 | 2.5806 | 2.6164 | 2.6652 | 2.1292 | 2.4959 | 2.8372 | 2.8693 | 2.912 | 3.1002
2022-03-10 22:00 | 2.1529 | 2.4044 | 2.4511 | 2.5082 | 2.5749 | 1.9348 | 2.3521 | 2.3885 | 2.4382 | 1.9348 | 2.0386 | 2.3302 | 2.3629 | 2.4064 | 2.5704
2022-03-10 23:00 | 1.9468 | 2.177 | 2.2206 | 2.2741 | 2.3364 | 1.6325 | 1.9907 | 2.0247 | 2.0712 | 1.6325 | 1.8672 | 2.1354 | 2.166 | 2.2066 | 2.3579
2022-03-11 | 1.7528 | 1.9601 | 1.9995 | 2.0476 | 2.1038 | 1.448 | 1.7665 | 1.7972 | 1.8391 | 1.448 | 1.6766 | 1.9177 | 1.9453 | 1.9819 | 2.1178
2022-03-11 01:00 | 1.7147 | 1.9098 | 1.9443 | 1.9865 | 2.0358 | 1.3146 | 1.6021 | 1.629 | 1.6658 | 1.3146 | 1.2575 | 1.4452 | 1.4694 | 1.5015 | 1.6091
2022-03-11 02:00 | 1.6576 | 1.8388 | 1.8684 | 1.9046 | 1.9469 | 1.2486 | 1.5171 | 1.5402 | 1.5718 | 1.2486 | 1.2956 | 1.4808 | 1.5015 | 1.5291 | 1.6333
2022-03-11 03:00 | 1.6004 | 1.7653 | 1.7887 | 1.8174 | 1.8509 | 1.2575 | 1.5189 | 1.5371 | 1.5621 | 1.2575 | 1.2765 | 1.4511 | 1.4675 | 1.4893 | 1.5856
2022-03-11 04:00 | 1.6576 | 1.8149 | 1.8323 | 1.8536 | 1.8784 | 1.2765 | 1.5328 | 1.5464 | 1.5649 | 1.2765 | 1.3337 | 1.5062 | 1.5184 | 1.5346 | 1.6273
2022-03-11 05:00 | 1.7719 | 1.9276 | 1.9399 | 1.9549 | 1.9724 | 1.5197 | 1.8127 | 1.8223 | 1.8353 | 1.5197 | 1.448 | 1.6261 | 1.6347 | 1.6461 | 1.7393
2022-03-11 06:00 | 1.9434 | 2.1079 | 2.1181 | 2.1306 | 2.1452 | 1.8672 | 2.2203 | 2.2283 | 2.2392 | 1.8672 | 1.7528 | 1.962 | 1.9692 | 1.9787 | 2.0865
2022-03-11 07:00 | 2.3264 | 2.5227 | 2.5346 | 2.5492 | 2.5663 | 2.2291 | 2.6504 | 2.6597 | 2.6724 | 2.2291 | 1.8862 | 2.1126 | 2.121 | 2.1321 | 2.2491
2022-03-11 08:00 | 2.3816 | 2.5911 | 2.6077 | 2.6279 | 2.6516 | 2.0603 | 2.4575 | 2.4705 | 2.4881 | 2.0603 | 1.5814 | 1.7803 | 1.7919 | 1.8073 | 1.9127
2022-03-11 09:00 | 2.3816 | 2.6044 | 2.6278 | 2.6565 | 2.6899 | 1.6004 | 1.9239 | 1.9422 | 1.9671 | 1.6004 | 1.1622 | 1.324 | 1.3404 | 1.3621 | 1.4521
2022-03-11 10:00 | 2.3816 | 2.6187 | 2.6493 | 2.6869 | 2.7307 | 1.105 | 1.3491 | 1.373 | 1.4057 | 1.105 | 1.5242 | 1.7363 | 1.7578 | 1.7864 | 1.9043
2022-03-11 11:00 | 2.2291 | 2.4659 | 2.5021 | 2.5465 | 2.5983 | 0.75377 | 0.94204 | 0.97032 | 1.0089 | 0.75377 | 1.6957 | 1.9346 | 1.96 | 1.9938 | 2.1274
2022-03-11 12:00 | 2.2482 | 2.4907 | 2.5292 | 2.5763 | 2.6312 | 0.64779 | 0.81999 | 0.85 | 0.89099 | 0.64779 | 2.0005 | 2.2765 | 2.3034 | 2.3392 | 2.4921
2022-03-11 13:00 | 2.2937 | 2.5385 | 2.5764 | 2.6229 | 2.677 | 0.62873 | 0.79672 | 0.82631 | 0.86672 | 0.62873 | 1.8481 | 2.1063 | 2.1329 | 2.1682 | 2.3121
2022-03-11 14:00 | 2.3054 | 2.546 | 2.5814 | 2.6248 | 2.6753 | 0.78115 | 0.97316 | 1.0008 | 1.0385 | 0.78115 | 1.81 | 2.0605 | 2.0853 | 2.1182 | 2.2571
2022-03-11 15:00 | 2.2863 | 2.5202 | 2.5528 | 2.5927 | 2.6393 | 1.6004 | 1.9371 | 1.9625 | 1.9973 | 1.6004 | 1.9815 | 2.2472 | 2.27 | 2.3004 | 2.4457
2022-03-11 16:00 | 2.2863 | 2.5166 | 2.5474 | 2.5851 | 2.629 | 1.0726 | 1.311 | 1.335 | 1.3678 | 1.0726 | 1.2194 | 1.3977 | 1.4193 | 1.448 | 1.5493
2022-03-11 17:00 | 2.3054 | 2.5362 | 2.5665 | 2.6037 | 2.647 | 1.6195 | 1.9563 | 1.98 | 2.0124 | 1.6195 | 1.1432 | 1.3124 | 1.3337 | 1.362 | 1.4586
2022-03-11 18:00 | 2.3816 | 2.6216 | 2.6538 | 2.6932 | 2.7391 | 1.9679 | 2.3706 | 2.3957 | 2.43 | 1.9679 | 1.829 | 2.0772 | 2.0997 | 2.1297 | 2.266
2022-03-11 19:00 | 2.4959 | 2.7518 | 2.7877 | 2.8317 | 2.883 | 2.0958 | 2.527 | 2.555 | 2.5933 | 2.0958 | 2.0386 | 2.3153 | 2.3404 | 2.3739 | 2.526
2022-03-11 20:00 | 2.4959 | 2.7615 | 2.8024 | 2.8525 | 2.9109 | 2.1148 | 2.5566 | 2.5885 | 2.632 | 2.1148 | 2.3244 | 2.6398 | 2.6684 | 2.7065 | 2.8799
2022-03-11 21:00 | 2.3816 | 2.6484 | 2.6942 | 2.7504 | 2.8158 | 2.0767 | 2.5186 | 2.5543 | 2.6032 | 2.0767 | 2.7626 | 3.1336 | 3.1657 | 3.2084 | 3.4113
2022-03-11 22:00 | 2.1529 | 2.4044 | 2.4511 | 2.5082 | 2.5749 | 1.8672 | 2.2722 | 2.3086 | 2.3583 | 1.8672 | 2.172 | 2.4784 | 2.5111 | 2.5546 | 2.7259
2022-03-11 23:00 | 1.9468 | 2.177 | 2.2206 | 2.2741 | 2.3364 | 1.6385 | 1.9977 | 2.0318 | 2.0783 | 1.6385 | 1.7338 | 1.9872 | 2.0178 | 2.0584 | 2.2023
2022-03-12 | 1.7528 | 1.9601 | 1.9995 | 2.0476 | 2.1038 | 1.4823 | 1.807 | 1.8377 | 1.8796 | 1.4823 | 1.6182 | 1.8528 | 1.8803 | 1.917 | 2.0497
2022-03-12 01:00 | 1.7147 | 1.9098 | 1.9443 | 1.9865 | 2.0358 | 1.3403 | 1.6324 | 1.6593 | 1.6961 | 1.3403 | 1.5623 | 1.784 | 1.8082 | 1.8403 | 1.9646
2022-03-12 02:00 | 1.6576 | 1.8388 | 1.8684 | 1.9046 | 1.9469 | 1.2586 | 1.5289 | 1.552 | 1.5836 | 1.2586 | 1.448 | 1.6502 | 1.6709 | 1.6985 | 1.8111
2022-03-12 03:00 | 1.6004 | 1.7653 | 1.7887 | 1.8174 | 1.8509 | 1.2281 | 1.4842 | 1.5025 | 1.5274 | 1.2281 | 1.3337 | 1.5146 | 1.531 | 1.5528 | 1.6523
2022-03-12 04:00 | 1.6576 | 1.8149 | 1.8323 | 1.8536 | 1.8784 | 1.2194 | 1.4653 | 1.4788 | 1.4974 | 1.2194 | 1.2003 | 1.358 | 1.3702 | 1.3864 | 1.4718
2022-03-12 05:00 | 1.7719 | 1.9276 | 1.9399 | 1.9549 | 1.9724 | 1.3272 | 1.5853 | 1.5949 | 1.6079 | 1.3272 | 1.2575 | 1.4144 | 1.423 | 1.4344 | 1.5172
2022-03-12 06:00 | 1.9434 | 2.1079 | 2.1181 | 2.1306 | 2.1452 | 1.4861 | 1.7702 | 1.7781 | 1.789 | 1.4861 | 1.3146 | 1.4751 | 1.4822 | 1.4918 | 1.5754
2022-03-12 07:00 | 2.3264 | 2.5227 | 2.5346 | 2.5492 | 2.5663 | 1.4861 | 1.7726 | 1.7819 | 1.7946 | 1.4861 | 1.6195 | 1.8162 | 1.8246 | 1.8357 | 1.938
2022-03-12 08:00 | 2.3816 | 2.5911 | 2.6077 | 2.6279 | 2.6516 | 1.3718 | 1.6441 | 1.6571 | 1.6747 | 1.3718 | 1.1813 | 1.3357 | 1.3473 | 1.3627 | 1.4461
2022-03-12 09:00 | 2.3816 | 2.6044 | 2.6278 | 2.6565 | 2.6899 | 1.3527 | 1.6313 | 1.6496 | 1.6745 | 1.3527 | 1.0288 | 1.1758 | 1.1921 | 1.2139 | 1.2965
2022-03-12 10:00 | 2.3816 | 2.6187 | 2.6493 | 2.6869 | 2.7307 | 1.2384 | 1.5066 | 1.5306 | 1.5632 | 1.2384 | 1.3718 | 1.5669 | 1.5884 | 1.617 | 1.7266
2022-03-12 11:00 | 2.2291 | 2.4659 | 2.5021 | 2.5465 | 2.5983 | 0.7621 | 0.95188 | 0.98017 | 1.0188 | 0.7621 | 1.5052 | 1.7229 | 1.7483 | 1.7821 | 1.9052
2022-03-12 12:00 | 2.2482 | 2.4907 | 2.5292 | 2.5763 | 2.6312 | 0.74305 | 0.93253 | 0.96254 | 1.0035 | 0.74305 | 1.829 | 2.0859 | 2.1129 | 2.1487 | 2.2921
2022-03-12 13:00 | 2.2937 | 2.5385 | 2.5764 | 2.6229 | 2.677 | 1.1241 | 1.3819 | 1.4115 | 1.4519 | 1.1241 | 1.8672 | 2.1275 | 2.1541 | 2.1894 | 2.3343
2022-03-12 14:00 | 2.3054 | 2.546 | 2.5814 | 2.6248 | 2.6753 | 1.5052 | 1.8285 | 1.8561 | 1.8938 | 1.5052 | 1.4099 | 1.6158 | 1.6406 | 1.6736 | 1.7905
2022-03-12 15:00 | 2.2863 | 2.5202 | 2.5528 | 2.5927 | 2.6393 | 0.60968 | 0.76666 | 0.79211 | 0.82687 | 0.60968 | 1.7909 | 2.0355 | 2.0583 | 2.0887 | 2.2235
2022-03-12 16:00 | 2.2863 | 2.5166 | 2.5474 | 2.5851 | 2.629 | 1.5052 | 1.8219 | 1.8459 | 1.8788 | 1.5052 | 1.5242 | 1.7365 | 1.7581 | 1.7868 | 1.9048
2022-03-12 17:00 | 2.3054 | 2.5362 | 2.5665 | 2.6037 | 2.647 | 1.829 | 2.2039 | 2.2276 | 2.2599 | 1.829 | 2.0005 | 2.2652 | 2.2865 | 2.3147 | 2.4585
2022-03-12 18:00 | 2.3816 | 2.6216 | 2.6538 | 2.6932 | 2.7391 | 1.9243 | 2.319 | 2.3441 | 2.3784 | 1.9243 | 1.9815 | 2.2465 | 2.2691 | 2.299 | 2.4438
2022-03-12 19:00 | 2.4959 | 2.7518 | 2.7877 | 2.8317 | 2.883 | 2.0005 | 2.4144 | 2.4424 | 2.4807 | 2.0005 | 2.553 | 2.8869 | 2.9121 | 2.9455 | 3.1259
2022-03-12 20:00 | 2.4959 | 2.7615 | 2.8024 | 2.8525 | 2.9109 | 1.9815 | 2.399 | 2.4309 | 2.4745 | 1.9815 | 2.3625 | 2.6821 | 2.7108 | 2.7489 | 2.9243
2022-03-12 21:00 | 2.3816 | 2.6484 | 2.6942 | 2.7504 | 2.8158 | 1.9243 | 2.3385 | 2.3743 | 2.4231 | 1.9243 | 2.5149 | 2.8583 | 2.8905 | 2.9332 | 3.1225
2022-03-12 22:00 | 2.1529 | 2.4044 | 2.4511 | 2.5082 | 2.5749 | 1.7672 | 2.1541 | 2.1905 | 2.2402 | 1.7672 | 1.9243 | 2.2032 | 2.2359 | 2.2793 | 2.4371
2022-03-12 23:00 | 1.9468 | 2.177 | 2.2206 | 2.2741 | 2.3364 | 1.66 | 2.0231 | 2.0572 | 2.1037 | 1.66 | 1.6766 | 1.9237 | 1.9543 | 1.9949 | 2.1357
2022-03-13 | 1.7528 | 1.9601 | 1.9995 | 2.0476 | 2.1038 | 1.4861 | 1.8115 | 1.8422 | 1.8841 | 1.4861 | 1.6576 | 1.8965 | 1.9241 | 1.9607 | 2.0956
2022-03-13 01:00 | 1.7147 | 1.9098 | 1.9443 | 1.9865 | 2.0358 | 1.3405 | 1.6327 | 1.6596 | 1.6964 | 1.3405 | 1.3146 | 1.5087 | 1.5329 | 1.565 | 1.6757
2022-03-13 02:00 | 1.6576 | 1.8388 | 1.8684 | 1.9046 | 1.9469 | 1.2575 | 1.5276 | 1.5507 | 1.5823 | 1.2575 | 1.467 | 1.6713 | 1.6921 | 1.7197 | 1.8333
2022-03-13 03:00 | 1.6004 | 1.7653 | 1.7887 | 1.8174 | 1.8509 | 1.2384 | 1.4963 | 1.5146 | 1.5396 | 1.2384 | 1.2765 | 1.4511 | 1.4675 | 1.4893 | 1.5856
2022-03-13 04:00 | 1.6576 | 1.8149 | 1.8323 | 1.8536 | 1.8784 | 1.2003 | 1.4427 | 1.4563 | 1.4749 | 1.2003 | 1.2194 | 1.3792 | 1.3914 | 1.4076 | 1.494
2022-03-13 05:00 | 1.7719 | 1.9276 | 1.9399 | 1.9549 | 1.9724 | 1.2258 | 1.4655 | 1.4751 | 1.4881 | 1.2258 | 1.3337 | 1.4991 | 1.5077 | 1.5191 | 1.606
2022-03-13 06:00 | 1.9434 | 2.1079 | 2.1181 | 2.1306 | 2.1452 | 1.3527 | 1.6126 | 1.6206 | 1.6315 | 1.3527 | 1.3146 | 1.4751 | 1.4822 | 1.4918 | 1.5754
2022-03-13 07:00 | 2.3264 | 2.5227 | 2.5346 | 2.5492 | 2.5663 | 1.3527 | 1.615 | 1.6243 | 1.637 | 1.3527 | 1.3527 | 1.5198 | 1.5281 | 1.5393 | 1.6269
2022-03-13 08:00 | 2.3816 | 2.5911 | 2.6077 | 2.6279 | 2.6516 | 1.4326 | 1.716 | 1.729 | 1.7466 | 1.4326 | 1.2384 | 1.3992 | 1.4108 | 1.4262 | 1.5128
2022-03-13 09:00 | 2.3816 | 2.6044 | 2.6278 | 2.6565 | 2.6899 | 1.448 | 1.7439 | 1.7621 | 1.787 | 1.448 | 1.467 | 1.6627 | 1.6791 | 1.7009 | 1.8076
2022-03-13 10:00 | 2.3816 | 2.6187 | 2.6493 | 2.6869 | 2.7307 | 1.3302 | 1.6151 | 1.639 | 1.6717 | 1.3302 | 1.1432 | 1.3129 | 1.3344 | 1.3629 | 1.4599
2022-03-13 11:00 | 2.2291 | 2.4659 | 2.5021 | 2.5465 | 2.5983 | 1.0669 | 1.312 | 1.3403 | 1.3789 | 1.0669 | 0.91452 | 1.0666 | 1.092 | 1.1257 | 1.2164
2022-03-13 12:00 | 2.2482 | 2.4907 | 2.5292 | 2.5763 | 2.6312 | 0.97168 | 1.2026 | 1.2326 | 1.2736 | 0.97168 | 1.7147 | 1.9589 | 1.9858 | 2.0217 | 2.1588
2022-03-13 13:00 | 2.2937 | 2.5385 | 2.5764 | 2.6229 | 2.677 | 0.7621 | 0.95427 | 0.98387 | 1.0243 | 0.7621 | 1.6195 | 1.8523 | 1.8789 | 1.9142 | 2.0455
2022-03-13 14:00 | 2.3054 | 2.546 | 2.5814 | 2.6248 | 2.6753 | 0.87642 | 1.0857 | 1.1133 | 1.151 | 0.87642 | 1.2575 | 1.4465 | 1.4713 | 1.5042 | 1.6128
2022-03-13 15:00 | 2.2863 | 2.5202 | 2.5528 | 2.5927 | 2.6393 | 0.62873 | 0.78917 | 0.81462 | 0.84938 | 0.62873 | 1.5623 | 1.7814 | 1.8043 | 1.8346 | 1.9569
2022-03-13 16:00 | 2.2863 | 2.5166 | 2.5474 | 2.5851 | 2.629 | 1.4289 | 1.7319 | 1.7559 | 1.7887 | 1.4289 | 1.0479 | 1.2072 | 1.2288 | 1.2575 | 1.3494
2022-03-13 17:00 | 2.3054 | 2.5362 | 2.5665 | 2.6037 | 2.647 | 1.81 | 2.1814 | 2.2051 | 2.2374 | 1.81 | 1.5242 | 1.7359 | 1.7572 | 1.7854 | 1.903
2022-03-13 18:00 | 2.3816 | 2.6216 | 2.6538 | 2.6932 | 2.7391 | 1.9624 | 2.3641 | 2.3892 | 2.4234 | 1.9624 | 2.0196 | 2.2889 | 2.3114 | 2.3414 | 2.4882
2022-03-13 19:00 | 2.4959 | 2.7518 | 2.7877 | 2.8317 | 2.883 | 2.0577 | 2.4819 | 2.51 | 2.5482 | 2.0577 | 2.2291 | 2.527 | 2.5522 | 2.5856 | 2.7482
2022-03-13 20:00 | 2.4959 | 2.7615 | 2.8024 | 2.8525 | 2.9109 | 2.0196 | 2.444 | 2.4759 | 2.5195 | 2.0196 | 2.1148 | 2.4069 | 2.4355 | 2.4736 | 2.6354
2022-03-13 21:00 | 2.3816 | 2.6484 | 2.6942 | 2.7504 | 2.8158 | 1.9243 | 2.3385 | 2.3743 | 2.4231 | 1.9243 | 2.4006 | 2.7313 | 2.7634 | 2.8061 | 2.9891
2022-03-13 22:00 | 2.1529 | 2.4044 | 2.4511 | 2.5082 | 2.5749 | 1.7871 | 2.1776 | 2.214 | 2.2637 | 1.7871 | 1.8672 | 2.1396 | 2.1723 | 2.2158 | 2.3704
2022-03-13 23:00 | 1.9468 | 2.177 | 2.2206 | 2.2741 | 2.3364 | 1.6062 | 1.9596 | 1.9936 | 2.0401 | 1.6062 | 1.7338 | 1.9872 | 2.0178 | 2.0584 | 2.2023
2022-03-14 | 1.7528 | 1.9601 | 1.9995 | 2.0476 | 2.1038 | 1.4502 | 1.7691 | 1.7998 | 1.8417 | 1.4502 | 1.7147 | 1.9601 | 1.9876 | 2.0242 | 2.1623
2022-03-14 01:00 | 1.7147 | 1.9098 | 1.9443 | 1.9865 | 2.0358 | 1.3409 | 1.6332 | 1.6601 | 1.6968 | 1.3409 | 1.448 | 1.6569 | 1.6811 | 1.7133 | 1.8313
2022-03-14 02:00 | 1.6576 | 1.8388 | 1.8684 | 1.9046 | 1.9469 | 1.2458 | 1.5139 | 1.537 | 1.5685 | 1.2458 | 1.4289 | 1.629 | 1.6497 | 1.6773 | 1.7888
2022-03-14 03:00 | 1.6004 | 1.7653 | 1.7887 | 1.8174 | 1.8509 | 1.2194 | 1.4738 | 1.4921 | 1.5171 | 1.2194 | 1.2003 | 1.3664 | 1.3828 | 1.4046 | 1.4967
2022-03-14 04:00 | 1.6576 | 1.8149 | 1.8323 | 1.8536 | 1.8784 | 1.2194 | 1.4653 | 1.4788 | 1.4974 | 1.2194 | 1.4289 | 1.6121 | 1.6243 | 1.6405 | 1.7384
2022-03-14 05:00 | 1.7719 | 1.9276 | 1.9399 | 1.9549 | 1.9724 | 1.285 | 1.5355 | 1.545 | 1.5581 | 1.285 | 1.4099 | 1.5838 | 1.5923 | 1.6038 | 1.6949
2022-03-14 06:00 | 1.9434 | 2.1079 | 2.1181 | 2.1306 | 2.1452 | 1.3337 | 1.5901 | 1.5981 | 1.609 | 1.3337 | 1.5242 | 1.708 | 1.7151 | 1.7247 | 1.8198
2022-03-14 07:00 | 2.3264 | 2.5227 | 2.5346 | 2.5492 | 2.5663 | 1.3908 | 1.66 | 1.6694 | 1.6821 | 1.3908 | 1.3908 | 1.5621 | 1.5705 | 1.5816 | 1.6713
2022-03-14 08:00 | 2.3816 | 2.5911 | 2.6077 | 2.6279 | 2.6516 | 1.3337 | 1.5991 | 1.6121 | 1.6297 | 1.3337 | 1.2003 | 1.3568 | 1.3685 | 1.3839 | 1.4683
2022-03-14 09:00 | 2.3816 | 2.6044 | 2.6278 | 2.6565 | 2.6899 | 1.105 | 1.3387 | 1.357 | 1.3819 | 1.105 | 1.105 | 1.2604 | 1.2768 | 1.2986 | 1.3854
2022-03-14 10:00 | 2.3816 | 2.6187 | 2.6493 | 2.6869 | 2.7307 | 0.78115 | 0.96644 | 0.99037 | 1.023 | 0.78115 | 1.2194 | 1.3976 | 1.4191 | 1.4476 | 1.5488
2022-03-14 11:00 | 2.2291 | 2.4659 | 2.5021 | 2.5465 | 2.5983 | 0.56573 | 0.7199 | 0.74819 | 0.78681 | 0.56573 | 1.6004 | 1.8288 | 1.8542 | 1.8879 | 2.0163
2022-03-14 12:00 | 2.2482 | 2.4907 | 2.5292 | 2.5763 | 2.6312 | 0.62892 | 0.7977 | 0.82772 | 0.8687 | 0.62892 | 1.7147 | 1.9589 | 1.9858 | 2.0217 | 2.1588
2022-03-14 13:00 | 2.2937 | 2.5385 | 2.5764 | 2.6229 | 2.677 | 1.2194 | 1.4945 | 1.5241 | 1.5645 | 1.2194 | 1.5242 | 1.7464 | 1.773 | 1.8083 | 1.9344
2022-03-14 14:00 | 2.3054 | 2.546 | 2.5814 | 2.6248 | 2.6753 | 1.3337 | 1.6259 | 1.6535 | 1.6912 | 1.3337 | 1.5242 | 1.7429 | 1.7677 | 1.8006 | 1.9238
2022-03-14 15:00 | 2.2863 | 2.5202 | 2.5528 | 2.5927 | 2.6393 | 1.5133 | 1.8342 | 1.8596 | 1.8944 | 1.5133 | 1.7338 | 1.9719 | 1.9948 | 2.0252 | 2.1568
2022-03-14 16:00 | 2.2863 | 2.5166 | 2.5474 | 2.5851 | 2.629 | 1.5433 | 1.8669 | 1.891 | 1.9238 | 1.5433 | 1.5814 | 1.8 | 1.8216 | 1.8503 | 1.9715
2022-03-14 17:00 | 2.3054 | 2.5362 | 2.5665 | 2.6037 | 2.647 | 1.8216 | 2.1952 | 2.2189 | 2.2512 | 1.8216 | 1.5814 | 1.7994 | 1.8207 | 1.849 | 1.9697
2022-03-14 18:00 | 2.3816 | 2.6216 | 2.6538 | 2.6932 | 2.7391 | 2.1339 | 2.5666 | 2.5917 | 2.626 | 2.1339 | 2.191 | 2.4794 | 2.502 | 2.5319 | 2.6882
2022-03-14 19:00 | 2.4959 | 2.7518 | 2.7877 | 2.8317 | 2.883 | 2.3244 | 2.7971 | 2.8251 | 2.8633 | 2.3244 | 2.4197 | 2.7387 | 2.7639 | 2.7973 | 2.9704
2022-03-14 20:00 | 2.4959 | 2.7615 | 2.8024 | 2.8525 | 2.9109 | 2.2775 | 2.7487 | 2.7807 | 2.8242 | 2.2775 | 2.5149 | 2.8515 | 2.8802 | 2.9182 | 3.102
2022-03-14 21:00 | 2.3816 | 2.6484 | 2.6942 | 2.7504 | 2.8158 | 2.0795 | 2.5219 | 2.5576 | 2.6065 | 2.0795 | 2.5721 | 2.9219 | 2.954 | 2.9967 | 3.1891
2022-03-14 22:00 | 2.1529 | 2.4044 | 2.4511 | 2.5082 | 2.5749 | 1.8691 | 2.2745 | 2.3109 | 2.3606 | 1.8691 | 2.1339 | 2.436 | 2.4688 | 2.5122 | 2.6815
2022-03-14 23:00 | 1.9468 | 2.177 | 2.2206 | 2.2741 | 2.3364 | 1.6576 | 2.0202 | 2.0543 | 2.1008 | 1.6576 | 1.7528 | 2.0084 | 2.039 | 2.0796 | 2.2245
2022-03-15 | 1.7528 | 1.9601 | 1.9995 | 2.0476 | 2.1038 | 1.4744 | 1.7977 | 1.8284 | 1.8703 | 1.4744 | 1.5242 | 1.7483 | 1.7759 | 1.8125 | 1.9401
2022-03-15 01:00 | 1.7147 | 1.9098 | 1.9443 | 1.9865 | 2.0358 | 1.3003 | 1.5852 | 1.6121 | 1.6489 | 1.3003 | 1.467 | 1.6781 | 1.7023 | 1.7344 | 1.8535
2022-03-15 02:00 | 1.6576 | 1.8388 | 1.8684 | 1.9046 | 1.9469 | 1.2384 | 1.5051 | 1.5282 | 1.5598 | 1.2384 | 1.448 | 1.6502 | 1.6709 | 1.6985 | 1.8111
2022-03-15 03:00 | 1.6004 | 1.7653 | 1.7887 | 1.8174 | 1.8509 | 1.2575 | 1.5189 | 1.5371 | 1.5621 | 1.2575 | 1.3527 | 1.5357 | 1.5522 | 1.574 | 1.6745
2022-03-15 04:00 | 1.6576 | 1.8149 | 1.8323 | 1.8536 | 1.8784 | 1.2575 | 1.5103 | 1.5238 | 1.5424 | 1.2575 | 1.4099 | 1.5909 | 1.6031 | 1.6193 | 1.7162
2022-03-15 05:00 | 1.7719 | 1.9276 | 1.9399 | 1.9549 | 1.9724 | 1.4375 | 1.7157 | 1.7252 | 1.7383 | 1.4375 | 1.3908 | 1.5626 | 1.5712 | 1.5826 | 1.6727
2022-03-15 06:00 | 1.9434 | 2.1079 | 2.1181 | 2.1306 | 2.1452 | 1.8481 | 2.1978 | 2.2058 | 2.2167 | 1.8481 | 1.6004 | 1.7927 | 1.7998 | 1.8094 | 1.9087
2022-03-15 07:00 | 2.3264 | 2.5227 | 2.5346 | 2.5492 | 2.5663 | 2.2482 | 2.6729 | 2.6822 | 2.6949 | 2.2482 | 2.0005 | 2.2396 | 2.248 | 2.2591 | 2.3824
2022-03-15 08:00 | 2.3816 | 2.5911 | 2.6077 | 2.6279 | 2.6516 | 2.1943 | 2.6158 | 2.6288 | 2.6464 | 2.1943 | 1.6957 | 1.9073 | 1.9189 | 1.9344 | 2.046
2022-03-15 09:00 | 2.3816 | 2.6044 | 2.6278 | 2.6565 | 2.6899 | 1.7719 | 2.1265 | 2.1448 | 2.1697 | 1.7719 | 1.2765 | 1.451 | 1.4674 | 1.4892 | 1.5854
2022-03-15 10:00 | 2.3816 | 2.6187 | 2.6493 | 2.6869 | 2.7307 | 1.7719 | 2.1368 | 2.1608 | 2.1934 | 1.7719 | 0.99073 | 1.1435 | 1.165 | 1.1935 | 1.2822
2022-03-15 11:00 | 2.2291 | 2.4659 | 2.5021 | 2.5465 | 2.5983 | 1.5472 | 1.8794 | 1.9077 | 1.9463 | 1.5472 | 1.6385 | 1.8711 | 1.8965 | 1.9303 | 2.0607
2022-03-15 12:00 | 2.2482 | 2.4907 | 2.5292 | 2.5763 | 2.6312 | 1.3718 | 1.6753 | 1.7053 | 1.7463 | 1.3718 | 1.6957 | 1.9377 | 1.9647 | 2.0005 | 2.1366
2022-03-15 13:00 | 2.2937 | 2.5385 | 2.5764 | 2.6229 | 2.677 | 1.3527 | 1.652 | 1.6816 | 1.722 | 1.3527 | 1.6766 | 1.9158 | 1.9424 | 1.9777 | 2.1121
2022-03-15 14:00 | 2.3054 | 2.546 | 2.5814 | 2.6248 | 2.6753 | 1.6385 | 1.986 | 2.0136 | 2.0513 | 1.6385 | 1.6195 | 1.8487 | 1.8735 | 1.9065 | 2.0349
2022-03-15 15:00 | 2.2863 | 2.5202 | 2.5528 | 2.5927 | 2.6393 | 1.6195 | 1.9596 | 1.985 | 2.0198 | 1.6195 | 1.7147 | 1.9508 | 1.9736 | 2.004 | 2.1346
2022-03-15 16:00 | 2.2863 | 2.5166 | 2.5474 | 2.5851 | 2.629 | 1.5433 | 1.8669 | 1.891 | 1.9238 | 1.5433 | 1.5052 | 1.7153 | 1.7369 | 1.7656 | 1.8826
2022-03-15 17:00 | 2.3054 | 2.5362 | 2.5665 | 2.6037 | 2.647 | 1.8672 | 2.2489 | 2.2726 | 2.305 | 1.8672 | 1.6385 | 1.8629 | 1.8842 | 1.9125 | 2.0363
2022-03-15 18:00 | 2.3816 | 2.6216 | 2.6538 | 2.6932 | 2.7391 | 2.2291 | 2.6792 | 2.7043 | 2.7385 | 2.2291 | 2.1529 | 2.4371 | 2.4596 | 2.4896 | 2.6438
2022-03-15 19:00 | 2.4959 | 2.7518 | 2.7877 | 2.8317 | 2.883 | 2.2291 | 2.6845 | 2.7125 | 2.7508 | 2.2291 | 2.4006 | 2.7175 | 2.7427 | 2.7762 | 2.9481
2022-03-15 20:00 | 2.4959 | 2.7615 | 2.8024 | 2.8525 | 2.9109 | 2.191 | 2.6466 | 2.6785 | 2.7221 | 2.191 | 2.2863 | 2.5974 | 2.6261 | 2.6642 | 2.8354
2022-03-15 21:00 | 2.3816 | 2.6484 | 2.6942 | 2.7504 | 2.8158 | 2.0767 | 2.5186 | 2.5543 | 2.6032 | 2.0767 | 2.2863 | 2.6043 | 2.6364 | 2.6791 | 2.8558
2022-03-15 22:00 | 2.1529 | 2.4044 | 2.4511 | 2.5082 | 2.5749 | 1.8862 | 2.2947 | 2.3311 | 2.3808 | 1.8862 | 1.9434 | 2.2243 | 2.257 | 2.3005 | 2.4593
2022-03-15 23:00 | 1.9468 | 2.177 | 2.2206 | 2.2741 | 2.3364 | 1.6004 | 1.9527 | 1.9868 | 2.0333 | 1.6004 | 1.6385 | 1.8813 | 1.9119 | 1.9526 | 2.0912
2022-03-16 | 1.7528 | 1.9601 | 1.9995 | 2.0476 | 2.1038 | 1.3632 | 1.6663 | 1.697 | 1.7389 | 1.3632 | 1.7338 | 1.9812 | 2.0088 | 2.0454 | 2.1845
2022-03-16 01:00 | 1.7147 | 1.9098 | 1.9443 | 1.9865 | 2.0358 | 1.2226 | 1.4934 | 1.5204 | 1.5571 | 1.2226 | 1.3527 | 1.5511 | 1.5753 | 1.6074 | 1.7202
2022-03-16 02:00 | 1.6576 | 1.8388 | 1.8684 | 1.9046 | 1.9469 | 1.2194 | 1.4826 | 1.5057 | 1.5373 | 1.2194 | 1.2194 | 1.3961 | 1.4169 | 1.4444 | 1.5444
2022-03-16 03:00 | 1.6004 | 1.7653 | 1.7887 | 1.8174 | 1.8509 | 1.2194 | 1.4738 | 1.4921 | 1.5171 | 1.2194 | 1.2956 | 1.4722 | 1.4887 | 1.5105 | 1.6078
2022-03-16 04:00 | 1.6576 | 1.8149 | 1.8323 | 1.8536 | 1.8784 | 1.2688 | 1.5236 | 1.5372 | 1.5558 | 1.2688 | 1.4289 | 1.6121 | 1.6243 | 1.6405 | 1.7384
2022-03-16 05:00 | 1.7719 | 1.9276 | 1.9399 | 1.9549 | 1.9724 | 1.5245 | 1.8184 | 1.828 | 1.841 | 1.5245 | 1.3718 | 1.5414 | 1.55 | 1.5614 | 1.6505
2022-03-16 06:00 | 1.9434 | 2.1079 | 2.1181 | 2.1306 | 2.1452 | 1.9409 | 2.3074 | 2.3154 | 2.3263 | 1.9409 | 1.6004 | 1.7927 | 1.7998 | 1.8094 | 1.9087
2022-03-16 07:00 | 2.3264 | 2.5227 | 2.5346 | 2.5492 | 2.5663 | 2.2482 | 2.6729 | 2.6822 | 2.6949 | 2.2482 | 1.829 | 2.0491 | 2.0575 | 2.0686 | 2.1824
2022-03-16 08:00 | 2.3816 | 2.5911 | 2.6077 | 2.6279 | 2.6516 | 2.2482 | 2.6795 | 2.6924 | 2.7101 | 2.2482 | 1.7147 | 1.9285 | 1.9401 | 1.9555 | 2.0683
2022-03-16 09:00 | 2.3816 | 2.6044 | 2.6278 | 2.6565 | 2.6899 | 1.8672 | 2.239 | 2.2573 | 2.2822 | 1.8672 | 1.3527 | 1.5357 | 1.5521 | 1.5739 | 1.6743
2022-03-16 10:00 | 2.3816 | 2.6187 | 2.6493 | 2.6869 | 2.7307 | 1.9053 | 2.2944 | 2.3183 | 2.351 | 1.9053 | 1.2384 | 1.4187 | 1.4402 | 1.4688 | 1.571
2022-03-16 11:00 | 2.2291 | 2.4659 | 2.5021 | 2.5465 | 2.5983 | 1.7909 | 2.1673 | 2.1956 | 2.2342 | 1.7909 | 1.6216 | 1.8523 | 1.8777 | 1.9115 | 2.041
2022-03-16 12:00 | 2.2482 | 2.4907 | 2.5292 | 2.5763 | 2.6312 | 1.6766 | 2.0354 | 2.0654 | 2.1064 | 1.6766 | 1.8862 | 2.1494 | 2.1764 | 2.2122 | 2.3587
2022-03-16 13:00 | 2.2937 | 2.5385 | 2.5764 | 2.6229 | 2.677 | 1.81 | 2.1922 | 2.2218 | 2.2622 | 1.81 | 1.8862 | 2.1487 | 2.1753 | 2.2106 | 2.3565
2022-03-16 14:00 | 2.3054 | 2.546 | 2.5814 | 2.6248 | 2.6753 | 1.9243 | 2.3236 | 2.3512 | 2.3889 | 1.9243 | 1.5214 | 1.7397 | 1.7645 | 1.7975 | 1.9205
2022-03-16 15:00 | 2.2863 | 2.5202 | 2.5528 | 2.5927 | 2.6393 | 1.9434 | 2.3422 | 2.3677 | 2.4024 | 1.9434 | 1.3146 | 1.5061 | 1.529 | 1.5594 | 1.668
2022-03-16 16:00 | 2.2863 | 2.5166 | 2.5474 | 2.5851 | 2.629 | 1.9053 | 2.2946 | 2.3186 | 2.3514 | 1.9053 | 1.5433 | 1.7577 | 1.7793 | 1.8079 | 1.9271
2022-03-16 17:00 | 2.3054 | 2.5362 | 2.5665 | 2.6037 | 2.647 | 2.2291 | 2.6766 | 2.7003 | 2.7326 | 2.2291 | 2.4197 | 2.731 | 2.7523 | 2.7805 | 2.9474
2022-03-16 18:00 | 2.3816 | 2.6216 | 2.6538 | 2.6932 | 2.7391 | 2.3816 | 2.8592 | 2.8843 | 2.9186 | 2.3816 | 2.7055 | 3.0511 | 3.0736 | 3.1036 | 3.2881
2022-03-16 19:00 | 2.4959 | 2.7518 | 2.7877 | 2.8317 | 2.883 | 2.3054 | 2.7745 | 2.8026 | 2.8408 | 2.3054 | 2.7817 | 3.141 | 3.1662 | 3.1996 | 3.3925
2022-03-16 20:00 | 2.4959 | 2.7615 | 2.8024 | 2.8525 | 2.9109 | 2.2291 | 2.6916 | 2.7235 | 2.7671 | 2.2291 | 2.3244 | 2.6398 | 2.6684 | 2.7065 | 2.8799
2022-03-16 21:00 | 2.3816 | 2.6484 | 2.6942 | 2.7504 | 2.8158 | 2.1339 | 2.5861 | 2.6219 | 2.6707 | 2.1339 | 2.1529 | 2.4561 | 2.4882 | 2.5309 | 2.7003
2022-03-16 22:00 | 2.1529 | 2.4044 | 2.4511 | 2.5082 | 2.5749 | 1.8585 | 2.2619 | 2.2984 | 2.3481 | 1.8585 | 2.0577 | 2.3514 | 2.3841 | 2.4275 | 2.5926
2022-03-16 23:00 | 1.9468 | 2.177 | 2.2206 | 2.2741 | 2.3364 | 1.6225 | 1.9788 | 2.0128 | 2.0593 | 1.6225 | 1.7338 | 1.9872 | 2.0178 | 2.0584 | 2.2023
2022-03-17 | 1.7528 | 1.9601 | 1.9995 | 2.0476 | 2.1038 | 1.4289 | 1.744 | 1.7747 | 1.8166 | 1.4289 | 1.448 | 1.6636 | 1.6912 | 1.7278 | 1.8512
2022-03-17 01:00 | 1.7147 | 1.9098 | 1.9443 | 1.9865 | 2.0358 | 1.2956 | 1.5796 | 1.6065 | 1.6433 | 1.2956 | 1.2956 | 1.4876 | 1.5117 | 1.5439 | 1.6535
2022-03-17 02:00 | 1.6576 | 1.8388 | 1.8684 | 1.9046 | 1.9469 | 1.2209 | 1.4845 | 1.5076 | 1.5391 | 1.2209 | 1.3527 | 1.5443 | 1.5651 | 1.5926 | 1.7
2022-03-17 03:00 | 1.6004 | 1.7653 | 1.7887 | 1.8174 | 1.8509 | 1.2575 | 1.5189 | 1.5371 | 1.5621 | 1.2575 | 1.2765 | 1.4511 | 1.4675 | 1.4893 | 1.5856
2022-03-17 04:00 | 1.6576 | 1.8149 | 1.8323 | 1.8536 | 1.8784 | 1.2429 | 1.493 | 1.5066 | 1.5251 | 1.2429 | 1.2384 | 1.4003 | 1.4125 | 1.4287 | 1.5162
2022-03-17 05:00 | 1.7719 | 1.9276 | 1.9399 | 1.9549 | 1.9724 | 1.4719 | 1.7562 | 1.7658 | 1.7789 | 1.4719 | 1.3718 | 1.5414 | 1.55 | 1.5614 | 1.6505
2022-03-17 06:00 | 1.9434 | 2.1079 | 2.1181 | 2.1306 | 2.1452 | 1.9069 | 2.2673 | 2.2752 | 2.2861 | 1.9069 | 1.829 | 2.0467 | 2.0539 | 2.0634 | 2.1754
2022-03-17 07:00 | 2.3264 | 2.5227 | 2.5346 | 2.5492 | 2.5663 | 2.0386 | 2.4253 | 2.4346 | 2.4473 | 2.0386 | 1.81 | 2.0279 | 2.0363 | 2.0474 | 2.1602
2022-03-17 08:00 | 2.3816 | 2.5911 | 2.6077 | 2.6279 | 2.6516 | 1.9175 | 2.2888 | 2.3017 | 2.3194 | 1.9175 | 1.6957 | 1.9073 | 1.9189 | 1.9344 | 2.046
2022-03-17 09:00 | 2.3816 | 2.6044 | 2.6278 | 2.6565 | 2.6899 | 1.6385 | 1.9689 | 1.9872 | 2.0121 | 1.6385 | 1.1813 | 1.3451 | 1.3615 | 1.3833 | 1.4743
2022-03-17 10:00 | 2.3816 | 2.6187 | 2.6493 | 2.6869 | 2.7307 | 1.5052 | 1.8217 | 1.8457 | 1.8783 | 1.5052 | 1.5623 | 1.7787 | 1.8002 | 1.8287 | 1.9488
2022-03-17 11:00 | 2.2291 | 2.4659 | 2.5021 | 2.5465 | 2.5983 | 1.2956 | 1.5821 | 1.6104 | 1.649 | 1.2956 | 0.99073 | 1.1513 | 1.1767 | 1.2104 | 1.3053
2022-03-17 12:00 | 2.2482 | 2.4907 | 2.5292 | 2.5763 | 2.6312 | 1.2194 | 1.4952 | 1.5252 | 1.5662 | 1.2194 | 1.6766 | 1.9165 | 1.9435 | 1.9793 | 2.1143
2022-03-17 13:00 | 2.2937 | 2.5385 | 2.5764 | 2.6229 | 2.677 | 0.87642 | 1.0893 | 1.1189 | 1.1593 | 0.87642 | 1.7909 | 2.0428 | 2.0694 | 2.1047 | 2.2454
2022-03-17 14:00 | 2.3054 | 2.546 | 2.5814 | 2.6248 | 2.6753 | 1.2575 | 1.5359 | 1.5635 | 1.6012 | 1.2575 | 1.7289 | 1.9704 | 1.9952 | 2.0281 | 2.1626
2022-03-17 15:00 | 2.2863 | 2.5202 | 2.5528 | 2.5927 | 2.6393 | 1.4861 | 1.802 | 1.8275 | 1.8622 | 1.4861 | 1.1432 | 1.3156 | 1.3385 | 1.3688 | 1.468
2022-03-17 16:00 | 2.2863 | 2.5166 | 2.5474 | 2.5851 | 2.629 | 1.8166 | 2.1898 | 2.2138 | 2.2466 | 1.8166 | 1.2956 | 1.4824 | 1.504 | 1.5327 | 1.6382
2022-03-17 17:00 | 2.3054 | 2.5362 | 2.5665 | 2.6037 | 2.647 | 2.0547 | 2.4705 | 2.4942 | 2.5265 | 2.0547 | 2.0196 | 2.2864 | 2.3076 | 2.3359 | 2.4807
2022-03-17 18:00 | 2.3816 | 2.6216 | 2.6538 | 2.6932 | 2.7391 | 2.2101 | 2.6567 | 2.6818 | 2.716 | 2.2101 | 2.3244 | 2.6276 | 2.6502 | 2.6801 | 2.8437
2022-03-17 19:00 | 2.4959 | 2.7518 | 2.7877 | 2.8317 | 2.883 | 2.2863 | 2.752 | 2.7801 | 2.8183 | 2.2863 | 2.4959 | 2.8234 | 2.8486 | 2.882 | 3.0592
2022-03-17 20:00 | 2.4959 | 2.7615 | 2.8024 | 2.8525 | 2.9109 | 2.2291 | 2.6916 | 2.7235 | 2.7671 | 2.2291 | 2.534 | 2.8727 | 2.9013 | 2.9394 | 3.1243
2022-03-17 21:00 | 2.3816 | 2.6484 | 2.6942 | 2.7504 | 2.8158 | 2.0958 | 2.5411 | 2.5768 | 2.6257 | 2.0958 | 2.2291 | 2.5408 | 2.5729 | 2.6156 | 2.7892
2022-03-17 22:00 | 2.1529 | 2.4044 | 2.4511 | 2.5082 | 2.5749 | 1.9512 | 2.3715 | 2.4079 | 2.4576 | 1.9512 | 2.0386 | 2.3302 | 2.3629 | 2.4064 | 2.5704
2022-03-17 23:00 | 1.9468 | 2.177 | 2.2206 | 2.2741 | 2.3364 | 1.6837 | 2.0511 | 2.0851 | 2.1316 | 1.6837 | 1.7719 | 2.0296 | 2.0601 | 2.1008 | 2.2468
2022-03-18 | 1.7528 | 1.9601 | 1.9995 | 2.0476 | 2.1038 | 1.4411 | 1.7584 | 1.7891 | 1.831 | 1.4411 | 1.8481 | 2.1083 | 2.1358 | 2.1724 | 2.3178
2022-03-18 01:00 | 1.7147 | 1.9098 | 1.9443 | 1.9865 | 2.0358 | 1.3131 | 1.6003 | 1.6273 | 1.664 | 1.3131 | 1.3146 | 1.5087 | 1.5329 | 1.565 | 1.6757
2022-03-18 02:00 | 1.6576 | 1.8388 | 1.8684 | 1.9046 | 1.9469 | 1.2575 | 1.5276 | 1.5507 | 1.5823 | 1.2575 | 1.2194 | 1.3961 | 1.4169 | 1.4444 | 1.5444
2022-03-18 03:00 | 1.6004 | 1.7653 | 1.7887 | 1.8174 | 1.8509 | 1.2575 | 1.5189 | 1.5371 | 1.5621 | 1.2575 | 1.2575 | 1.4299 | 1.4463 | 1.4681 | 1.5634
2022-03-18 04:00 | 1.6576 | 1.8149 | 1.8323 | 1.8536 | 1.8784 | 1.2965 | 1.5564 | 1.57 | 1.5885 | 1.2965 | 1.3337 | 1.5062 | 1.5184 | 1.5346 | 1.6273
2022-03-18 05:00 | 1.7719 | 1.9276 | 1.9399 | 1.9549 | 1.9724 | 1.4957 | 1.7844 | 1.794 | 1.8071 | 1.4957 | 1.4099 | 1.5838 | 1.5923 | 1.6038 | 1.6949
2022-03-18 06:00 | 1.9434 | 2.1079 | 2.1181 | 2.1306 | 2.1452 | 1.9243 | 2.2878 | 2.2958 | 2.3067 | 1.9243 | 1.7338 | 1.9409 | 1.948 | 1.9576 | 2.0643
2022-03-18 07:00 | 2.3264 | 2.5227 | 2.5346 | 2.5492 | 2.5663 | 2.0767 | 2.4703 | 2.4796 | 2.4923 | 2.0767 | 1.8862 | 2.1126 | 2.121 | 2.1321 | 2.2491
2022-03-18 08:00 | 2.3816 | 2.5911 | 2.6077 | 2.6279 | 2.6516 | 2.0577 | 2.4544 | 2.4674 | 2.485 | 2.0577 | 1.6766 | 1.8862 | 1.8978 | 1.9132 | 2.0238
2022-03-18 09:00 | 2.3816 | 2.6044 | 2.6278 | 2.6565 | 2.6899 | 1.6195 | 1.9464 | 1.9647 | 1.9896 | 1.6195 | 1.0098 | 1.1546 | 1.171 | 1.1928 | 1.2743
2022-03-18 10:00 | 2.3816 | 2.6187 | 2.6493 | 2.6869 | 2.7307 | 1.1622 | 1.4166 | 1.4405 | 1.4732 | 1.1622 | 1.448 | 1.6516 | 1.6731 | 1.7017 | 1.8154
2022-03-18 11:00 | 2.2291 | 2.4659 | 2.5021 | 2.5465 | 2.5983 | 1.1128 | 1.3662 | 1.3945 | 1.4331 | 1.1128 | 1.3908 | 1.5959 | 1.6213 | 1.655 | 1.7719
2022-03-18 12:00 | 2.2482 | 2.4907 | 2.5292 | 2.5763 | 2.6312 | 1.7528 | 2.1254 | 2.1555 | 2.1964 | 1.7528 | 1.7338 | 1.98 | 2.007 | 2.0428 | 2.181
2022-03-18 13:00 | 2.2937 | 2.5385 | 2.5764 | 2.6229 | 2.677 | 1.9434 | 2.3498 | 2.3794 | 2.4198 | 1.9434 | 1.6004 | 1.8311 | 1.8577 | 1.893 | 2.0232
2022-03-18 14:00 | 2.3054 | 2.546 | 2.5814 | 2.6248 | 2.6753 | 1.7227 | 2.0854 | 2.113 | 2.1507 | 1.7227 | 1.6004 | 1.8276 | 1.8524 | 1.8853 | 2.0127
2022-03-18 15:00 | 2.2863 | 2.5202 | 2.5528 | 2.5927 | 2.6393 | 2.0577 | 2.4773 | 2.5027 | 2.5375 | 2.0577 | 2.0196 | 2.2895 | 2.3124 | 2.3428 | 2.4901
2022-03-18 16:00 | 2.2863 | 2.5166 | 2.5474 | 2.5851 | 2.629 | 1.6834 | 2.0324 | 2.0565 | 2.0893 | 1.6834 | 1.2956 | 1.4824 | 1.504 | 1.5327 | 1.6382
2022-03-18 17:00 | 2.3054 | 2.5362 | 2.5665 | 2.6037 | 2.647 | 1.9461 | 2.3422 | 2.3658 | 2.3982 | 1.9461 | 1.7719 | 2.0111 | 2.0324 | 2.0607 | 2.1919
2022-03-18 18:00 | 2.3816 | 2.6216 | 2.6538 | 2.6932 | 2.7391 | 2.1667 | 2.6054 | 2.6305 | 2.6648 | 2.1667 | 2.2291 | 2.5218 | 2.5443 | 2.5743 | 2.7326
2022-03-18 19:00 | 2.4959 | 2.7518 | 2.7877 | 2.8317 | 2.883 | 2.2291 | 2.6845 | 2.7125 | 2.7508 | 2.2291 | 2.3816 | 2.6964 | 2.7215 | 2.755 | 2.9259
2022-03-18 20:00 | 2.4959 | 2.7615 | 2.8024 | 2.8525 | 2.9109 | 2.191 | 2.6466 | 2.6785 | 2.7221 | 2.191 | 2.0958 | 2.3857 | 2.4144 | 2.4525 | 2.6132
2022-03-18 21:00 | 2.3816 | 2.6484 | 2.6942 | 2.7504 | 2.8158 | 2.0767 | 2.5186 | 2.5543 | 2.6032 | 2.0767 | 2.4768 | 2.816 | 2.8481 | 2.8908 | 3.078
2022-03-18 22:00 | 2.1529 | 2.4044 | 2.4511 | 2.5082 | 2.5749 | 1.9053 | 2.3172 | 2.3536 | 2.4033 | 1.9053 | 1.8862 | 2.1608 | 2.1935 | 2.237 | 2.3927
2022-03-18 23:00 | 1.9468 | 2.177 | 2.2206 | 2.2741 | 2.3364 | 1.6766 | 2.0428 | 2.0768 | 2.1233 | 1.6766 | 1.7719 | 2.0296 | 2.0601 | 2.1008 | 2.2468
2022-03-19 | 1.7528 | 1.9601 | 1.9995 | 2.0476 | 2.1038 | 1.5242 | 1.8566 | 1.8872 | 1.9291 | 1.5242 | 1.6004 | 1.833 | 1.8606 | 1.8972 | 2.029
2022-03-19 01:00 | 1.7147 | 1.9098 | 1.9443 | 1.9865 | 2.0358 | 1.3718 | 1.6696 | 1.6965 | 1.7333 | 1.3718 | 1.5052 | 1.7205 | 1.7446 | 1.7768 | 1.8979
2022-03-19 02:00 | 1.6576 | 1.8388 | 1.8684 | 1.9046 | 1.9469 | 1.2765 | 1.5501 | 1.5732 | 1.6048 | 1.2765 | 1.2384 | 1.4173 | 1.438 | 1.4656 | 1.5666
2022-03-19 03:00 | 1.6004 | 1.7653 | 1.7887 | 1.8174 | 1.8509 | 1.2105 | 1.4633 | 1.4816 | 1.5066 | 1.2105 | 1.3527 | 1.5357 | 1.5522 | 1.574 | 1.6745
2022-03-19 04:00 | 1.6576 | 1.8149 | 1.8323 | 1.8536 | 1.8784 | 1.221 | 1.4672 | 1.4808 | 1.4993 | 1.221 | 1.3527 | 1.5274 | 1.5396 | 1.5558 | 1.6495
2022-03-19 05:00 | 1.7719 | 1.9276 | 1.9399 | 1.9549 | 1.9724 | 1.3185 | 1.5751 | 1.5847 | 1.5977 | 1.3185 | 1.3146 | 1.4779 | 1.4865 | 1.4979 | 1.5838
2022-03-19 06:00 | 1.9434 | 2.1079 | 2.1181 | 2.1306 | 2.1452 | 1.4926 | 1.7779 | 1.7859 | 1.7968 | 1.4926 | 1.3908 | 1.5598 | 1.5669 | 1.5765 | 1.6643
2022-03-19 07:00 | 2.3264 | 2.5227 | 2.5346 | 2.5492 | 2.5663 | 1.6195 | 1.9301 | 1.9394 | 1.9522 | 1.6195 | 1.467 | 1.6468 | 1.6552 | 1.6663 | 1.7602
2022-03-19 08:00 | 2.3816 | 2.5911 | 2.6077 | 2.6279 | 2.6516 | 1.6576 | 1.9818 | 1.9947 | 2.0123 | 1.6576 | 1.3146 | 1.4839 | 1.4955 | 1.5109 | 1.6017
2022-03-19 09:00 | 2.3816 | 2.6044 | 2.6278 | 2.6565 | 2.6899 | 1.6576 | 1.9915 | 2.0097 | 2.0346 | 1.6576 | 1.5623 | 1.7686 | 1.785 | 1.8068 | 1.9187
2022-03-19 10:00 | 2.3816 | 2.6187 | 2.6493 | 2.6869 | 2.7307 | 1.5623 | 1.8893 | 1.9132 | 1.9459 | 1.5623 | 1.2765 | 1.4611 | 1.4826 | 1.5111 | 1.6155
2022-03-19 11:00 | 2.2291 | 2.4659 | 2.5021 | 2.5465 | 2.5983 | 1.2384 | 1.5146 | 1.5429 | 1.5815 | 1.2384 | 0.97168 | 1.1301 | 1.1555 | 1.1892 | 1.283
2022-03-19 12:00 | 2.2482 | 2.4907 | 2.5292 | 2.5763 | 2.6312 | 1.2765 | 1.5627 | 1.5928 | 1.6337 | 1.2765 | 0.87642 | 1.0273 | 1.0543 | 1.0901 | 1.1811
2022-03-19 13:00 | 2.2937 | 2.5385 | 2.5764 | 2.6229 | 2.677 | 1.2765 | 1.562 | 1.5916 | 1.632 | 1.2765 | 1.0669 | 1.2383 | 1.2649 | 1.3002 | 1.4011
2022-03-19 14:00 | 2.3054 | 2.546 | 2.5814 | 2.6248 | 2.6753 | 1.3718 | 1.6709 | 1.6985 | 1.7362 | 1.3718 | 1.448 | 1.6582 | 1.683 | 1.7159 | 1.835
2022-03-19 15:00 | 2.2863 | 2.5202 | 2.5528 | 2.5927 | 2.6393 | 0.91452 | 1.1268 | 1.1522 | 1.187 | 0.91452 | 1.3337 | 1.5273 | 1.5502 | 1.5806 | 1.6902
2022-03-19 16:00 | 2.2863 | 2.5166 | 2.5474 | 2.5851 | 2.629 | 1.6576 | 2.002 | 2.026 | 2.0588 | 1.6576 | 1.3146 | 1.5036 | 1.5252 | 1.5539 | 1.6604
2022-03-19 17:00 | 2.3054 | 2.5362 | 2.5665 | 2.6037 | 2.647 | 1.7045 | 2.0568 | 2.0805 | 2.1128 | 1.7045 | 1.4289 | 1.63 | 1.6513 | 1.6796 | 1.7919
2022-03-19 18:00 | 2.3816 | 2.6216 | 2.6538 | 2.6932 | 2.7391 | 2.1339 | 2.5666 | 2.5917 | 2.626 | 2.1339 | 2.5149 | 2.8394 | 2.8619 | 2.8919 | 3.0659
2022-03-19 19:00 | 2.4959 | 2.7518 | 2.7877 | 2.8317 | 2.883 | 2.1339 | 2.572 | 2.6 | 2.6383 | 2.1339 | 2.4578 | 2.7811 | 2.8062 | 2.8397 | 3.0148
2022-03-19 20:00 | 2.4959 | 2.7615 | 2.8024 | 2.8525 | 2.9109 | 2.1529 | 2.6016 | 2.6335 | 2.6771 | 2.1529 | 2.2673 | 2.5762 | 2.6049 | 2.643 | 2.8132
2022-03-19 21:00 | 2.3816 | 2.6484 | 2.6942 | 2.7504 | 2.8158 | 2.0577 | 2.4961 | 2.5318 | 2.5807 | 2.0577 | 2.1339 | 2.4349 | 2.467 | 2.5097 | 2.6781
2022-03-19 22:00 | 2.1529 | 2.4044 | 2.4511 | 2.5082 | 2.5749 | 1.9011 | 2.3123 | 2.3487 | 2.3984 | 1.9011 | 2.0386 | 2.3302 | 2.3629 | 2.4064 | 2.5704
2022-03-19 23:00 | 1.9468 | 2.177 | 2.2206 | 2.2741 | 2.3364 | 1.7262 | 2.1014 | 2.1354 | 2.1819 | 1.7262 | 1.7528 | 2.0084 | 2.039 | 2.0796 | 2.2245
2022-03-20 | 1.7528 | 1.9601 | 1.9995 | 2.0476 | 2.1038 | 1.4861 | 1.8115 | 1.8422 | 1.8841 | 1.4861 | 1.7147 | 1.9601 | 1.9876 | 2.0242 | 2.1623
2022-03-20 01:00 | 1.7147 | 1.9098 | 1.9443 | 1.9865 | 2.0358 | 1.3718 | 1.6696 | 1.6965 | 1.7333 | 1.3718 | 1.3337 | 1.5299 | 1.5541 | 1.5862 | 1.698
2022-03-20 02:00 | 1.6576 | 1.8388 | 1.8684 | 1.9046 | 1.9469 | 1.2979 | 1.5755 | 1.5986 | 1.6301 | 1.2979 | 1.5433 | 1.756 | 1.7768 | 1.8044 | 1.9222
2022-03-20 03:00 | 1.6004 | 1.7653 | 1.7887 | 1.8174 | 1.8509 | 1.2384 | 1.4963 | 1.5146 | 1.5396 | 1.2384 | 1.4099 | 1.5993 | 1.6157 | 1.6375 | 1.7411
2022-03-20 04:00 | 1.6576 | 1.8149 | 1.8323 | 1.8536 | 1.8784 | 1.2575 | 1.5103 | 1.5238 | 1.5424 | 1.2575 | 1.2003 | 1.358 | 1.3702 | 1.3864 | 1.4718
2022-03-20 05:00 | 1.7719 | 1.9276 | 1.9399 | 1.9549 | 1.9724 | 1.2575 | 1.503 | 1.5125 | 1.5256 | 1.2575 | 1.3337 | 1.4991 | 1.5077 | 1.5191 | 1.606
2022-03-20 06:00 | 1.9434 | 2.1079 | 2.1181 | 2.1306 | 2.1452 | 1.3502 | 1.6096 | 1.6176 | 1.6285 | 1.3502 | 1.3718 | 1.5386 | 1.5458 | 1.5553 | 1.6421
2022-03-20 07:00 | 2.3264 | 2.5227 | 2.5346 | 2.5492 | 2.5663 | 1.448 | 1.7276 | 1.7369 | 1.7496 | 1.448 | 1.5433 | 1.7315 | 1.7399 | 1.751 | 1.8491
2022-03-20 08:00 | 2.3816 | 2.5911 | 2.6077 | 2.6279 | 2.6516 | 1.6004 | 1.9142 | 1.9272 | 1.9448 | 1.6004 | 1.8862 | 2.119 | 2.1307 | 2.1461 | 2.2682
2022-03-20 09:00 | 2.3816 | 2.6044 | 2.6278 | 2.6565 | 2.6899 | 1.5052 | 1.8114 | 1.8296 | 1.8546 | 1.5052 | 1.4099 | 1.5992 | 1.6156 | 1.6374 | 1.7409
2022-03-20 10:00 | 2.3816 | 2.6187 | 2.6493 | 2.6869 | 2.7307 | 1.1037 | 1.3475 | 1.3714 | 1.4041 | 1.1037 | 0.99073 | 1.1435 | 1.165 | 1.1935 | 1.2822
2022-03-20 11:00 | 2.2291 | 2.4659 | 2.5021 | 2.5465 | 2.5983 | 0.62873 | 0.79432 | 0.82261 | 0.86123 | 0.62873 | 1.3337 | 1.5324 | 1.5578 | 1.5915 | 1.7052
2022-03-20 12:00 | 2.2482 | 2.4907 | 2.5292 | 2.5763 | 2.6312 | 0.60968 | 0.77497 | 0.80499 | 0.84597 | 0.60968 | 1.5242 | 1.7472 | 1.7741 | 1.8099 | 1.9366
2022-03-20 13:00 | 2.2937 | 2.5385 | 2.5764 | 2.6229 | 2.677 | 0.59063 | 0.7517 | 0.7813 | 0.82171 | 0.59063 | 1.5814 | 1.8099 | 1.8365 | 1.8718 | 2.001
2022-03-20 14:00 | 2.3054 | 2.546 | 2.5814 | 2.6248 | 2.6753 | 1.3337 | 1.6259 | 1.6535 | 1.6912 | 1.3337 | 1.2194 | 1.4041 | 1.4289 | 1.4619 | 1.5683
2022-03-20 15:00 | 2.2863 | 2.5202 | 2.5528 | 2.5927 | 2.6393 | 1.467 | 1.7795 | 1.805 | 1.8397 | 1.467 | 1.0669 | 1.2309 | 1.2538 | 1.2842 | 1.3791
2022-03-20 16:00 | 2.2863 | 2.5166 | 2.5474 | 2.5851 | 2.629 | 1.6957 | 2.047 | 2.071 | 2.1038 | 1.6957 | 1.6766 | 1.9059 | 1.9275 | 1.9561 | 2.0826
2022-03-20 17:00 | 2.3054 | 2.5362 | 2.5665 | 2.6037 | 2.647 | 2.4197 | 2.9017 | 2.9254 | 2.9577 | 2.4197 | 2.9722 | 3.345 | 3.3663 | 3.3945 | 3.5917
2022-03-20 18:00 | 2.3816 | 2.6216 | 2.6538 | 2.6932 | 2.7391 | 2.4197 | 2.9042 | 2.9293 | 2.9636 | 2.4197 | 2.7436 | 3.0934 | 3.116 | 3.1459 | 3.3326
2022-03-20 19:00 | 2.4959 | 2.7518 | 2.7877 | 2.8317 | 2.883 | 2.3586 | 2.8374 | 2.8654 | 2.9037 | 2.3586 | 2.553 | 2.8869 | 2.9121 | 2.9455 | 3.1259
2022-03-20 20:00 | 2.4959 | 2.7615 | 2.8024 | 2.8525 | 2.9109 | 2.0386 | 2.4665 | 2.4984 | 2.542 | 2.0386 | 2.4578 | 2.788 | 2.8166 | 2.8547 | 3.0354
2022-03-20 21:00 | 2.3816 | 2.6484 | 2.6942 | 2.7504 | 2.8158 | 1.8709 | 2.2754 | 2.3112 | 2.36 | 1.8709 | 2.2863 | 2.6043 | 2.6364 | 2.6791 | 2.8558
2022-03-20 22:00 | 2.1529 | 2.4044 | 2.4511 | 2.5082 | 2.5749 | 1.5246 | 1.8675 | 1.904 | 1.9537 | 1.5246 | 2.2673 | 2.5843 | 2.617 | 2.6604 | 2.837
2022-03-20 23:00 | 1.9468 | 2.177 | 2.2206 | 2.2741 | 2.3364 | 1.32 | 1.6214 | 1.6555 | 1.7019 | 1.32 | 1.7338 | 1.9872 | 2.0178 | 2.0584 | 2.2023
2022-03-21 | 1.8063 | 2.0176 | 2.057 | 2.1051 | 2.1612 | 1.1813 | 1.4514 | 1.4821 | 1.524 | 1.1813 | 1.6576 | 1.8965 | 1.9241 | 1.9607 | 2.0956
2022-03-21 01:00 | 1.6766 | 1.8688 | 1.9033 | 1.9456 | 1.9948 | 1.0646 | 1.3067 | 1.3337 | 1.3704 | 1.0646 | 1.5623 | 1.784 | 1.8082 | 1.8403 | 1.9646
2022-03-21 02:00 | 1.6195 | 1.7978 | 1.8275 | 1.8637 | 1.906 | 1.0098 | 1.235 | 1.2581 | 1.2897 | 1.0098 | 1.2956 | 1.4808 | 1.5015 | 1.5291 | 1.6333
2022-03-21 03:00 | 1.6576 | 1.8267 | 1.8501 | 1.8788 | 1.9123 | 0.99073 | 1.2037 | 1.222 | 1.247 | 0.99073 | 1.4099 | 1.5993 | 1.6157 | 1.6375 | 1.7411
2022-03-21 04:00 | 1.5623 | 1.7125 | 1.7299 | 1.7512 | 1.7761 | 0.99657 | 1.2021 | 1.2156 | 1.2342 | 0.99657 | 1.3718 | 1.5485 | 1.5607 | 1.5769 | 1.6717
2022-03-21 05:00 | 1.6766 | 1.8253 | 1.8375 | 1.8525 | 1.87 | 1.1208 | 1.3414 | 1.351 | 1.3641 | 1.1208 | 1.4289 | 1.6049 | 1.6135 | 1.6249 | 1.7171
2022-03-21 06:00 | 1.8255 | 1.9812 | 1.9915 | 2.004 | 2.0186 | 1.3337 | 1.5901 | 1.5981 | 1.609 | 1.3337 | 1.7338 | 1.9409 | 1.948 | 1.9576 | 2.0643
2022-03-21 07:00 | 2.2101 | 2.3978 | 2.4097 | 2.4243 | 2.4413 | 1.5242 | 1.8176 | 1.8269 | 1.8396 | 1.5242 | 1.81 | 2.0279 | 2.0363 | 2.0474 | 2.1602
2022-03-21 08:00 | 2.0958 | 2.284 | 2.3006 | 2.3209 | 2.3446 | 1.3786 | 1.6522 | 1.6651 | 1.6828 | 1.3786 | 1.3908 | 1.5686 | 1.5802 | 1.5956 | 1.6905
2022-03-21 09:00 | 2.172 | 2.3793 | 2.4027 | 2.4313 | 2.4647 | 1.2384 | 1.4963 | 1.5145 | 1.5394 | 1.2384 | 1.0288 | 1.1758 | 1.1921 | 1.2139 | 1.2965
2022-03-21 10:00 | 2.0958 | 2.3116 | 2.3423 | 2.3799 | 2.4236 | 1.1241 | 1.3716 | 1.3955 | 1.4282 | 1.1241 | 1.2765 | 1.4611 | 1.4826 | 1.5111 | 1.6155
2022-03-21 11:00 | 1.829 | 2.036 | 2.0723 | 2.1167 | 2.1684 | 0.91452 | 1.1319 | 1.1602 | 1.1988 | 0.91452 | 1.1813 | 1.363 | 1.3884 | 1.4221 | 1.5275
2022-03-21 12:00 | 1.829 | 2.0404 | 2.0788 | 2.1259 | 2.1809 | 0.7621 | 0.95503 | 0.98505 | 1.026 | 0.7621 | 1.7528 | 2.0012 | 2.0282 | 2.064 | 2.2032
2022-03-21 13:00 | 1.448 | 1.6299 | 1.6679 | 1.7143 | 1.7685 | 0.64779 | 0.81922 | 0.84882 | 0.88923 | 0.64779 | 2.0577 | 2.3392 | 2.3658 | 2.4011 | 2.5565
2022-03-21 14:00 | 1.6576 | 1.8501 | 1.8855 | 1.9288 | 1.9793 | 0.64779 | 0.8156 | 0.84321 | 0.88091 | 0.64779 | 1.6957 | 1.9334 | 1.9582 | 1.9912 | 2.1238
2022-03-21 15:00 | 1.9053 | 2.1108 | 2.1434 | 2.1834 | 2.2299 | 1.0288 | 1.2618 | 1.2873 | 1.322 | 1.0288 | 1.3527 | 1.5485 | 1.5714 | 1.6017 | 1.7124
2022-03-21 16:00 | 2.172 | 2.3938 | 2.4246 | 2.4623 | 2.5062 | 1.2194 | 1.4843 | 1.5083 | 1.5411 | 1.2194 | 1.0669 | 1.2284 | 1.2499 | 1.2786 | 1.3716
2022-03-21 17:00 | 2.4578 | 2.6999 | 2.7303 | 2.7675 | 2.8108 | 1.6759 | 2.023 | 2.0467 | 2.079 | 1.6759 | 1.7719 | 2.0111 | 2.0324 | 2.0607 | 2.1919
2022-03-21 18:00 | 2.553 | 2.8058 | 2.838 | 2.8774 | 2.9233 | 1.9053 | 2.2965 | 2.3216 | 2.3559 | 1.9053 | 2.6674 | 3.0087 | 3.0313 | 3.0612 | 3.2437
2022-03-21 19:00 | 2.6483 | 2.9155 | 2.9515 | 2.9954 | 3.0467 | 2.0005 | 2.4144 | 2.4424 | 2.4807 | 2.0005 | 2.4197 | 2.7387 | 2.7639 | 2.7973 | 2.9704
2022-03-21 20:00 | 2.5911 | 2.8639 | 2.9048 | 2.9549 | 3.0133 | 1.9815 | 2.399 | 2.4309 | 2.4745 | 1.9815 | 2.6864 | 3.042 | 3.0707 | 3.1088 | 3.302
2022-03-21 21:00 | 2.3309 | 2.5939 | 2.6398 | 2.6959 | 2.7614 | 1.8481 | 2.2485 | 2.2842 | 2.3331 | 1.8481 | 2.7626 | 3.1336 | 3.1657 | 3.2084 | 3.4113
2022-03-21 22:00 | 2.191 | 2.4453 | 2.492 | 2.5492 | 2.6158 | 1.5433 | 1.8895 | 1.9259 | 1.9757 | 1.5433 | 2.172 | 2.4784 | 2.5111 | 2.5546 | 2.7259
2022-03-21 23:00 | 1.8707 | 2.0952 | 2.1388 | 2.1923 | 2.2545 | 1.345 | 1.651 | 1.6851 | 1.7316 | 1.345 | 1.6576 | 1.9025 | 1.9331 | 1.9737 | 2.1134
2022-03-22 | 1.7528 | 1.9601 | 1.9995 | 2.0476 | 2.1038 | 1.1622 | 1.4289 | 1.4596 | 1.5015 | 1.1622 | 1.5052 | 1.7272 | 1.7547 | 1.7913 | 1.9179
2022-03-22 01:00 | 1.6537 | 1.8442 | 1.8787 | 1.921 | 1.9702 | 1.057 | 1.2978 | 1.3247 | 1.3615 | 1.057 | 1.4099 | 1.6146 | 1.6388 | 1.6709 | 1.7868
2022-03-22 02:00 | 1.6385 | 1.8183 | 1.8479 | 1.8842 | 1.9264 | 0.99073 | 1.2125 | 1.2356 | 1.2672 | 0.99073 | 1.3908 | 1.5866 | 1.6074 | 1.635 | 1.7444
2022-03-22 03:00 | 1.5242 | 1.6834 | 1.7069 | 1.7356 | 1.769 | 0.97168 | 1.1812 | 1.1995 | 1.2245 | 0.97168 | 1.2003 | 1.3664 | 1.3828 | 1.4046 | 1.4967
2022-03-22 04:00 | 1.5623 | 1.7125 | 1.7299 | 1.7512 | 1.7761 | 0.99073 | 1.1952 | 1.2087 | 1.2273 | 0.99073 | 1.3337 | 1.5062 | 1.5184 | 1.5346 | 1.6273
2022-03-22 05:00 | 1.6576 | 1.8048 | 1.8171 | 1.8321 | 1.8496 | 1.0886 | 1.3035 | 1.313 | 1.3261 | 1.0886 | 1.448 | 1.6261 | 1.6347 | 1.6461 | 1.7393
2022-03-22 06:00 | 1.8693 | 2.0283 | 2.0385 | 2.051 | 2.0656 | 1.3718 | 1.6351 | 1.6431 | 1.654 | 1.3718 | 1.5814 | 1.7715 | 1.7787 | 1.7882 | 1.8865
2022-03-22 07:00 | 2.2101 | 2.3978 | 2.4097 | 2.4243 | 2.4413 | 1.4861 | 1.7726 | 1.7819 | 1.7946 | 1.4861 | 1.9434 | 2.1761 | 2.1845 | 2.1956 | 2.3157
2022-03-22 08:00 | 2.1755 | 2.3697 | 2.3863 | 2.4066 | 2.4303 | 1.3908 | 1.6666 | 1.6796 | 1.6972 | 1.3908 | 1.5623 | 1.7591 | 1.7707 | 1.7862 | 1.8905
2022-03-22 09:00 | 1.8556 | 2.0394 | 2.0628 | 2.0914 | 2.1248 | 1.0479 | 1.2712 | 1.2895 | 1.3144 | 1.0479 | 1.1622 | 1.324 | 1.3404 | 1.3621 | 1.4521
2022-03-22 10:00 | 1.6766 | 1.8613 | 1.892 | 1.9295 | 1.9733 | 0.72879 | 0.90457 | 0.9285 | 0.96117 | 0.72879 | 1.3908 | 1.5881 | 1.6096 | 1.6382 | 1.7488
2022-03-22 11:00 | 1.6766 | 1.8723 | 1.9085 | 1.9529 | 2.0047 | 0.57158 | 0.7268 | 0.75509 | 0.79371 | 0.57158 | 1.6957 | 1.9346 | 1.96 | 1.9938 | 2.1274
2022-03-22 12:00 | 1.6957 | 1.8971 | 1.9356 | 1.9827 | 2.0376 | 0.53347 | 0.68494 | 0.71496 | 0.75594 | 0.53347 | 1.81 | 2.0647 | 2.0917 | 2.1275 | 2.2699
2022-03-22 13:00 | 1.6766 | 1.8755 | 1.9135 | 1.9599 | 2.0141 | 0.55252 | 0.70668 | 0.73628 | 0.77669 | 0.55252 | 2.0386 | 2.3181 | 2.3446 | 2.38 | 2.5343
2022-03-22 14:00 | 1.81 | 2.0138 | 2.0492 | 2.0926 | 2.1431 | 0.68589 | 0.86062 | 0.88823 | 0.92593 | 0.68589 | 1.5623 | 1.7852 | 1.81 | 1.843 | 1.9683
2022-03-22 15:00 | 2.3244 | 2.5611 | 2.5937 | 2.6337 | 2.6803 | 1.1622 | 1.4194 | 1.4448 | 1.4796 | 1.1622 | 1.3146 | 1.5061 | 1.529 | 1.5594 | 1.668
2022-03-22 16:00 | 2.5721 | 2.8236 | 2.8544 | 2.8921 | 2.9361 | 1.3718 | 1.6644 | 1.6884 | 1.7212 | 1.3718 | 1.3146 | 1.5036 | 1.5252 | 1.5539 | 1.6604
2022-03-22 17:00 | 2.5911 | 2.8432 | 2.8736 | 2.9107 | 2.9541 | 1.7186 | 2.0734 | 2.0971 | 2.1295 | 1.7186 | 2.3054 | 2.604 | 2.6252 | 2.6535 | 2.814
2022-03-22 18:00 | 2.6674 | 2.9286 | 2.9608 | 3.0002 | 3.0461 | 2.0767 | 2.4991 | 2.5242 | 2.5585 | 2.0767 | 2.7436 | 3.0934 | 3.116 | 3.1459 | 3.3326
2022-03-22 19:00 | 2.6102 | 2.8746 | 2.9105 | 2.9545 | 3.0058 | 2.0577 | 2.4819 | 2.51 | 2.5482 | 2.0577 | 2.8388 | 3.2045 | 3.2297 | 3.2631 | 3.4592
2022-03-22 20:00 | 2.534 | 2.8025 | 2.8434 | 2.8935 | 2.9519 | 1.9846 | 2.4027 | 2.4346 | 2.4782 | 1.9846 | 2.4387 | 2.7668 | 2.7955 | 2.8336 | 3.0132
2022-03-22 21:00 | 2.3054 | 2.5665 | 2.6124 | 2.6685 | 2.7339 | 1.8862 | 2.2935 | 2.3293 | 2.3781 | 1.8862 | 2.3054 | 2.6254 | 2.6576 | 2.7003 | 2.878
2022-03-22 22:00 | 2.1698 | 2.4225 | 2.4692 | 2.5263 | 2.5929 | 1.703 | 2.0782 | 2.1146 | 2.1644 | 1.703 | 2.1529 | 2.4572 | 2.4899 | 2.5334 | 2.7037
2022-03-22 23:00 | 1.9624 | 2.1937 | 2.2374 | 2.2908 | 2.3531 | 1.4165 | 1.7355 | 1.7695 | 1.816 | 1.4165 | 1.6576 | 1.9025 | 1.9331 | 1.9737 | 2.1134
2022-03-23 | 1.8481 | 2.0625 | 2.1018 | 2.15 | 2.2061 | 1.2213 | 1.4987 | 1.5293 | 1.5712 | 1.2213 | 1.5814 | 1.8118 | 1.8394 | 1.876 | 2.0067
2022-03-23 01:00 | 1.6805 | 1.873 | 1.9075 | 1.9497 | 1.9989 | 1.105 | 1.3545 | 1.3814 | 1.4182 | 1.105 | 1.5814 | 1.8052 | 1.8293 | 1.8615 | 1.9868
2022-03-23 02:00 | 1.6385 | 1.8183 | 1.8479 | 1.8842 | 1.9264 | 1.0288 | 1.2575 | 1.2806 | 1.3122 | 1.0288 | 1.3146 | 1.502 | 1.5227 | 1.5503 | 1.6555
2022-03-23 03:00 | 1.5774 | 1.7406 | 1.764 | 1.7927 | 1.8262 | 0.99802 | 1.2124 | 1.2306 | 1.2556 | 0.99802 | 1.2956 | 1.4722 | 1.4887 | 1.5105 | 1.6078
2022-03-23 04:00 | 1.6004 | 1.7535 | 1.7709 | 1.7922 | 1.817 | 1.0092 | 1.217 | 1.2305 | 1.2491 | 1.0092 | 1.3146 | 1.485 | 1.4972 | 1.5134 | 1.6051
2022-03-23 05:00 | 1.7072 | 1.8582 | 1.8704 | 1.8854 | 1.9029 | 1.1522 | 1.3786 | 1.3882 | 1.4012 | 1.1522 | 1.3527 | 1.5202 | 1.5288 | 1.5402 | 1.6282
2022-03-23 06:00 | 1.9291 | 2.0925 | 2.1028 | 2.1153 | 2.1299 | 1.3851 | 1.6509 | 1.6588 | 1.6697 | 1.3851 | 1.6385 | 1.835 | 1.8422 | 1.8517 | 1.9532
2022-03-23 07:00 | 2.3054 | 2.5001 | 2.512 | 2.5267 | 2.5437 | 1.5623 | 1.8626 | 1.8719 | 1.8846 | 1.5623 | 1.81 | 2.0279 | 2.0363 | 2.0474 | 2.1602
2022-03-23 08:00 | 2.3054 | 2.5092 | 2.5258 | 2.5461 | 2.5697 | 1.4861 | 1.7792 | 1.7921 | 1.8098 | 1.4861 | 1.6576 | 1.865 | 1.8766 | 1.892 | 2.0016
2022-03-23 09:00 | 2.3435 | 2.5635 | 2.5869 | 2.6155 | 2.6489 | 1.3625 | 1.6429 | 1.6611 | 1.686 | 1.3625 | 1.3718 | 1.5569 | 1.5732 | 1.595 | 1.6965
2022-03-23 10:00 | 2.191 | 2.414 | 2.4447 | 2.4822 | 2.526 | 1.0098 | 1.2365 | 1.2605 | 1.2931 | 1.0098 | 1.6195 | 1.8422 | 1.8637 | 1.8922 | 2.0154
2022-03-23 11:00 | 1.9243 | 2.1384 | 2.1746 | 2.219 | 2.2708 | 0.87642 | 1.0869 | 1.1152 | 1.1538 | 0.87642 | 1.8481 | 2.104 | 2.1294 | 2.1632 | 2.3051
2022-03-23 12:00 | 2.1529 | 2.3883 | 2.4268 | 2.4739 | 2.5288 | 1.0669 | 1.3152 | 1.3452 | 1.3862 | 1.0669 | 1.6576 | 1.8954 | 1.9223 | 1.9581 | 2.0921
2022-03-23 13:00 | 1.81 | 2.0188 | 2.0568 | 2.1032 | 2.1574 | 0.70494 | 0.88675 | 0.91634 | 0.95676 | 0.70494 | 1.6957 | 1.937 | 1.9635 | 1.9989 | 2.1343
2022-03-23 14:00 | 2.0005 | 2.2185 | 2.2539 | 2.2973 | 2.3478 | 0.7621 | 0.95065 | 0.97826 | 1.016 | 0.7621 | 1.4289 | 1.637 | 1.6618 | 1.6948 | 1.8127
2022-03-23 15:00 | 2.2101 | 2.4383 | 2.4709 | 2.5109 | 2.5574 | 0.99073 | 1.2168 | 1.2423 | 1.277 | 0.99073 | 1.3337 | 1.5273 | 1.5502 | 1.5806 | 1.6902
2022-03-23 16:00 | 2.6102 | 2.8645 | 2.8954 | 2.9331 | 2.977 | 1.3908 | 1.6869 | 1.7109 | 1.7437 | 1.3908 | 1.3527 | 1.546 | 1.5675 | 1.5962 | 1.7049
2022-03-23 17:00 | 2.3564 | 2.591 | 2.6214 | 2.6586 | 2.7019 | 1.7588 | 2.121 | 2.1447 | 2.177 | 1.7588 | 1.7909 | 2.0323 | 2.0536 | 2.0818 | 2.2141
2022-03-23 18:00 | 2.5721 | 2.8263 | 2.8585 | 2.8978 | 2.9438 | 1.9815 | 2.3866 | 2.4117 | 2.4459 | 1.9815 | 2.9531 | 3.3263 | 3.3489 | 3.3788 | 3.577
2022-03-23 19:00 | 2.5149 | 2.7722 | 2.8082 | 2.8522 | 2.9034 | 1.8672 | 2.2569 | 2.2849 | 2.3232 | 1.8672 | 2.6102 | 2.9504 | 2.9756 | 3.0091 | 3.1926
2022-03-23 20:00 | 2.3625 | 2.6182 | 2.6592 | 2.7092 | 2.7676 | 1.9053 | 2.309 | 2.3409 | 2.3845 | 1.9053 | 2.4006 | 2.7245 | 2.7531 | 2.7912 | 2.9687
2022-03-23 21:00 | 2.2482 | 2.5051 | 2.551 | 2.6071 | 2.6725 | 1.7147 | 2.0909 | 2.1267 | 2.1755 | 1.7147 | 2.4578 | 2.7948 | 2.8269 | 2.8696 | 3.0558
2022-03-23 22:00 | 2.0455 | 2.2889 | 2.3356 | 2.3928 | 2.4594 | 1.5235 | 1.8661 | 1.9026 | 1.9523 | 1.5235 | 2.0196 | 2.309 | 2.3417 | 2.3852 | 2.5482
2022-03-23 23:00 | 1.9133 | 2.141 | 2.1847 | 2.2381 | 2.3004 | 1.3453 | 1.6513 | 1.6853 | 1.7318 | 1.3453 | 2.0386 | 2.326 | 2.3565 | 2.3972 | 2.5578
2022-03-24 | 1.7147 | 1.9192 | 1.9585 | 2.0067 | 2.0628 | 1.1585 | 1.4245 | 1.4552 | 1.497 | 1.1585 | 1.7338 | 1.9812 | 2.0088 | 2.0454 | 2.1845
2022-03-24 01:00 | 1.6195 | 1.8074 | 1.8419 | 1.8842 | 1.9334 | 1.0742 | 1.318 | 1.345 | 1.3817 | 1.0742 | 1.5052 | 1.7205 | 1.7446 | 1.7768 | 1.8979
2022-03-24 02:00 | 1.6195 | 1.7978 | 1.8275 | 1.8637 | 1.906 | 1.0036 | 1.2278 | 1.2509 | 1.2824 | 1.0036 | 1.2575 | 1.4384 | 1.4592 | 1.4868 | 1.5889
2022-03-24 03:00 | 1.4861 | 1.6425 | 1.6659 | 1.6946 | 1.7281 | 0.99073 | 1.2037 | 1.222 | 1.247 | 0.99073 | 1.4099 | 1.5993 | 1.6157 | 1.6375 | 1.7411
2022-03-24 04:00 | 1.5242 | 1.6716 | 1.689 | 1.7103 | 1.7352 | 0.99073 | 1.1952 | 1.2087 | 1.2273 | 0.99073 | 1.2194 | 1.3792 | 1.3914 | 1.4076 | 1.494
2022-03-24 05:00 | 1.6195 | 1.7639 | 1.7761 | 1.7911 | 1.8086 | 1.1152 | 1.3349 | 1.3445 | 1.3575 | 1.1152 | 1.3337 | 1.4991 | 1.5077 | 1.5191 | 1.606
2022-03-24 06:00 | 1.8919 | 2.0525 | 2.0628 | 2.0753 | 2.0899 | 1.3296 | 1.5852 | 1.5932 | 1.6041 | 1.3296 | 1.6004 | 1.7927 | 1.7998 | 1.8094 | 1.9087
2022-03-24 07:00 | 2.3816 | 2.582 | 2.5939 | 2.6085 | 2.6256 | 1.6195 | 1.9301 | 1.9394 | 1.9522 | 1.6195 | 1.9053 | 2.1338 | 2.1421 | 2.1533 | 2.2713
2022-03-24 08:00 | 2.2713 | 2.4726 | 2.4892 | 2.5095 | 2.5332 | 1.4861 | 1.7792 | 1.7921 | 1.8098 | 1.4861 | 1.7909 | 2.0132 | 2.0248 | 2.0402 | 2.1571
2022-03-24 09:00 | 2.3244 | 2.543 | 2.5664 | 2.5951 | 2.6284 | 1.4289 | 1.7214 | 1.7396 | 1.7645 | 1.4289 | 1.6576 | 1.8744 | 1.8908 | 1.9126 | 2.0298
2022-03-24 10:00 | 2.2482 | 2.4754 | 2.5061 | 2.5436 | 2.5874 | 1.2765 | 1.5516 | 1.5756 | 1.6082 | 1.2765 | 1.7338 | 1.9692 | 1.9907 | 2.0193 | 2.1487
2022-03-24 11:00 | 2.3625 | 2.6091 | 2.6454 | 2.6898 | 2.7415 | 1.3908 | 1.6946 | 1.7229 | 1.7615 | 1.3908 | 1.3718 | 1.5747 | 1.6001 | 1.6339 | 1.7496
2022-03-24 12:00 | 2.2863 | 2.5316 | 2.5701 | 2.6172 | 2.6721 | 1.4099 | 1.7203 | 1.7503 | 1.7913 | 1.4099 | 1.2575 | 1.4507 | 1.4777 | 1.5135 | 1.6255
2022-03-24 13:00 | 2.3435 | 2.592 | 2.6299 | 2.6764 | 2.7305 | 1.3718 | 1.6745 | 1.7041 | 1.7445 | 1.3718 | 1.2956 | 1.4923 | 1.5189 | 1.5543 | 1.6677
2022-03-24 14:00 | 2.3435 | 2.587 | 2.6224 | 2.6657 | 2.7162 | 1.2956 | 1.5809 | 1.6085 | 1.6462 | 1.2956 | 1.2384 | 1.4253 | 1.4501 | 1.483 | 1.5905
2022-03-24 15:00 | 2.191 | 2.4178 | 2.4505 | 2.4904 | 2.537 | 1.2472 | 1.5197 | 1.5452 | 1.58 | 1.2472 | 1.1322 | 1.3035 | 1.3263 | 1.3567 | 1.4553
2022-03-24 16:00 | 2.2101 | 2.4347 | 2.4655 | 2.5032 | 2.5472 | 1.3908 | 1.6869 | 1.7109 | 1.7437 | 1.3908 | 1.5814 | 1.8 | 1.8216 | 1.8503 | 1.9715
2022-03-24 17:00 | 2.0958 | 2.311 | 2.3414 | 2.3786 | 2.4219 | 1.5242 | 1.8438 | 1.8675 | 1.8998 | 1.5242 | 1.6195 | 1.8418 | 1.863 | 1.8913 | 2.0141
2022-03-24 18:00 | 2.3131 | 2.5481 | 2.5802 | 2.6196 | 2.6655 | 1.7719 | 2.139 | 2.1641 | 2.1983 | 1.7719 | 2.0386 | 2.3101 | 2.3326 | 2.3625 | 2.5104
2022-03-24 19:00 | 2.4768 | 2.7313 | 2.7672 | 2.8112 | 2.8625 | 1.8862 | 2.2794 | 2.3074 | 2.3457 | 1.8862 | 2.5149 | 2.8446 | 2.8698 | 2.9032 | 3.0815
2022-03-24 20:00 | 2.4006 | 2.6592 | 2.7001 | 2.7502 | 2.8086 | 1.9053 | 2.309 | 2.3409 | 2.3845 | 1.9053 | 2.3625 | 2.6821 | 2.7108 | 2.7489 | 2.9243
2022-03-24 21:00 | 2.3816 | 2.6484 | 2.6942 | 2.7504 | 2.8158 | 1.7454 | 2.1272 | 2.1629 | 2.2118 | 1.7454 | 2.2101 | 2.5196 | 2.5517 | 2.5944 | 2.7669
2022-03-24 22:00 | 2.1148 | 2.3635 | 2.4101 | 2.4673 | 2.5339 | 1.603 | 1.9602 | 1.9966 | 2.0463 | 1.603 | 2.3244 | 2.6478 | 2.6805 | 2.7239 | 2.9037
2022-03-24 23:00 | 1.9259 | 2.1546 | 2.1982 | 2.2516 | 2.3139 | 1.3146 | 1.6151 | 1.6492 | 1.6956 | 1.3146 | 1.6576 | 1.9025 | 1.9331 | 1.9737 | 2.1134
2022-03-25 | 1.7338 | 1.9397 | 1.979 | 2.0271 | 2.0833 | 1.1503 | 1.4148 | 1.4455 | 1.4874 | 1.1503 | 1.467 | 1.6848 | 1.7124 | 1.749 | 1.8734
2022-03-25 01:00 | 1.6195 | 1.8074 | 1.8419 | 1.8842 | 1.9334 | 1.0391 | 1.2766 | 1.3035 | 1.3403 | 1.0391 | 1.3718 | 1.5723 | 1.5964 | 1.6286 | 1.7424
2022-03-25 02:00 | 1.5623 | 1.7364 | 1.766 | 1.8023 | 1.8446 | 0.99182 | 1.2138 | 1.2369 | 1.2685 | 0.99182 | 1.4099 | 1.6078 | 1.6286 | 1.6561 | 1.7666
2022-03-25 03:00 | 1.5242 | 1.6834 | 1.7069 | 1.7356 | 1.769 | 0.96903 | 1.1781 | 1.1964 | 1.2214 | 0.96903 | 1.6004 | 1.811 | 1.8274 | 1.8492 | 1.9633
2022-03-25 04:00 | 1.5433 | 1.6921 | 1.7095 | 1.7308 | 1.7556 | 0.99073 | 1.1952 | 1.2087 | 1.2273 | 0.99073 | 1.3527 | 1.5274 | 1.5396 | 1.5558 | 1.6495
2022-03-25 05:00 | 1.715 | 1.8665 | 1.8788 | 1.8938 | 1.9113 | 1.0893 | 1.3042 | 1.3138 | 1.3268 | 1.0893 | 1.4099 | 1.5838 | 1.5923 | 1.6038 | 1.6949
2022-03-25 06:00 | 1.9058 | 2.0675 | 2.0777 | 2.0902 | 2.1048 | 1.3055 | 1.5568 | 1.5648 | 1.5757 | 1.3055 | 1.6385 | 1.835 | 1.8422 | 1.8517 | 1.9532
2022-03-25 07:00 | 2.1833 | 2.369 | 2.3809 | 2.3955 | 2.4126 | 1.5433 | 1.8401 | 1.8494 | 1.8621 | 1.5433 | 1.9434 | 2.1761 | 2.1845 | 2.1956 | 2.3157
2022-03-25 08:00 | 2.2482 | 2.4478 | 2.4644 | 2.4847 | 2.5083 | 1.5433 | 1.8467 | 1.8596 | 1.8773 | 1.5433 | 1.7528 | 1.9708 | 1.9825 | 1.9979 | 2.1127
2022-03-25 09:00 | 2.0005 | 2.195 | 2.2184 | 2.2471 | 2.2805 | 1.0288 | 1.2487 | 1.2669 | 1.2919 | 1.0288 | 0.95263 | 1.0911 | 1.1075 | 1.1292 | 1.2077
2022-03-25 10:00 | 1.9243 | 2.1274 | 2.1581 | 2.1956 | 2.2394 | 1.1813 | 1.4391 | 1.463 | 1.4957 | 1.1813 | 1.3718 | 1.5669 | 1.5884 | 1.617 | 1.7266
2022-03-25 11:00 | 1.8747 | 2.0851 | 2.1214 | 2.1658 | 2.2175 | 1.0098 | 1.2445 | 1.2728 | 1.3114 | 1.0098 | 1.448 | 1.6594 | 1.6848 | 1.7186 | 1.8385
2022-03-25 12:00 | 2.0577 | 2.286 | 2.3245 | 2.3716 | 2.4265 | 1.0288 | 1.2701 | 1.3002 | 1.3411 | 1.0288 | 1.7528 | 2.0012 | 2.0282 | 2.064 | 2.2032
2022-03-25 13:00 | 1.5052 | 1.6913 | 1.7293 | 1.7757 | 1.8299 | 0.55252 | 0.70668 | 0.73628 | 0.77669 | 0.55252 | 1.8481 | 2.1063 | 2.1329 | 2.1682 | 2.3121
2022-03-25 14:00 | 1.9243 | 2.1367 | 2.1721 | 2.2154 | 2.2659 | 0.55252 | 0.70306 | 0.73067 | 0.76837 | 0.55252 | 1.9434 | 2.2087 | 2.2335 | 2.2664 | 2.4127
2022-03-25 15:00 | 1.5708 | 1.7515 | 1.7841 | 1.824 | 1.8706 | 0.74939 | 0.9317 | 0.95715 | 0.99191 | 0.74939 | 1.5814 | 1.8026 | 1.8254 | 1.8558 | 1.9791
2022-03-25 16:00 | 2.0577 | 2.2709 | 2.3017 | 2.3395 | 2.3834 | 1.0479 | 1.2817 | 1.3058 | 1.3386 | 1.0479 | 1.0098 | 1.1648 | 1.1864 | 1.2151 | 1.3049
2022-03-25 17:00 | 2.0958 | 2.311 | 2.3414 | 2.3786 | 2.4219 | 1.4289 | 1.7313 | 1.7549 | 1.7873 | 1.4289 | 1.7528 | 1.99 | 2.0112 | 2.0395 | 2.1697
2022-03-25 18:00 | 2.2101 | 2.4374 | 2.4696 | 2.5089 | 2.5549 | 1.6766 | 2.0264 | 2.0515 | 2.0858 | 1.6766 | 2.0196 | 2.2889 | 2.3114 | 2.3414 | 2.4882
2022-03-25 19:00 | 2.2673 | 2.5061 | 2.5421 | 2.5861 | 2.6374 | 1.7338 | 2.0993 | 2.1273 | 2.1656 | 1.7338 | 2.3244 | 2.6329 | 2.658 | 2.6915 | 2.8593
2022-03-25 20:00 | 2.2101 | 2.4545 | 2.4954 | 2.5455 | 2.6039 | 1.7338 | 2.1064 | 2.1383 | 2.1819 | 1.7338 | 2.1529 | 2.4492 | 2.4779 | 2.516 | 2.6799
2022-03-25 21:00 | 2.1339 | 2.3823 | 2.4281 | 2.4843 | 2.5497 | 1.6913 | 2.0633 | 2.0991 | 2.1479 | 1.6913 | 2.2673 | 2.5831 | 2.6152 | 2.6579 | 2.8336
2022-03-25 22:00 | 2.0081 | 2.2488 | 2.2955 | 2.3527 | 2.4193 | 1.5242 | 1.867 | 1.9034 | 1.9532 | 1.5242 | 1.9815 | 2.2667 | 2.2994 | 2.3428 | 2.5038
2022-03-25 23:00 | 1.8862 | 2.1119 | 2.1555 | 2.2089 | 2.2712 | 1.3475 | 1.6539 | 1.688 | 1.7345 | 1.3475 | 1.829 | 2.0931 | 2.1237 | 2.1643 | 2.3134
2022-03-26 | 1.6576 | 1.8578 | 1.8971 | 1.9453 | 2.0014 | 1.2003 | 1.4739 | 1.5046 | 1.5465 | 1.2003 | 1.5433 | 1.7695 | 1.7971 | 1.8337 | 1.9623
2022-03-26 01:00 | 1.6576 | 1.8483 | 1.8829 | 1.9251 | 1.9743 | 1.0896 | 1.3363 | 1.3632 | 1.3999 | 1.0896 | 1.4861 | 1.6993 | 1.7235 | 1.7556 | 1.8757
2022-03-26 02:00 | 1.5623 | 1.7364 | 1.766 | 1.8023 | 1.8446 | 1.0288 | 1.2575 | 1.2806 | 1.3122 | 1.0288 | 1.3337 | 1.5231 | 1.5439 | 1.5715 | 1.6777
2022-03-26 03:00 | 1.5242 | 1.6834 | 1.7069 | 1.7356 | 1.769 | 1.0098 | 1.2263 | 1.2445 | 1.2695 | 1.0098 | 1.3718 | 1.5569 | 1.5733 | 1.5952 | 1.6967
2022-03-26 04:00 | 1.4861 | 1.6307 | 1.6481 | 1.6694 | 1.6942 | 1.0098 | 1.2177 | 1.2312 | 1.2498 | 1.0098 | 1.467 | 1.6544 | 1.6666 | 1.6828 | 1.7828
2022-03-26 05:00 | 1.5623 | 1.7025 | 1.7147 | 1.7297 | 1.7472 | 1.046 | 1.2532 | 1.2627 | 1.2758 | 1.046 | 1.3337 | 1.4991 | 1.5077 | 1.5191 | 1.606
2022-03-26 06:00 | 1.7147 | 1.8622 | 1.8725 | 1.885 | 1.8996 | 1.1096 | 1.3254 | 1.3334 | 1.3443 | 1.1096 | 1.3718 | 1.5386 | 1.5458 | 1.5553 | 1.6421
2022-03-26 07:00 | 1.7338 | 1.886 | 1.898 | 1.9126 | 1.9296 | 1.2384 | 1.48 | 1.4893 | 1.502 | 1.2384 | 1.5242 | 1.7103 | 1.7187 | 1.7298 | 1.8269
2022-03-26 08:00 | 1.7567 | 1.9197 | 1.9363 | 1.9566 | 1.9803 | 1.2765 | 1.5316 | 1.5445 | 1.5622 | 1.2765 | 1.5052 | 1.6956 | 1.7072 | 1.7227 | 1.8239
2022-03-26 09:00 | 1.8672 | 2.0518 | 2.0752 | 2.1038 | 2.1372 | 1.4099 | 1.6989 | 1.7171 | 1.742 | 1.4099 | 1.7147 | 1.938 | 1.9543 | 1.9761 | 2.0964
2022-03-26 10:00 | 2.0005 | 2.2093 | 2.24 | 2.2775 | 2.3213 | 1.4099 | 1.7092 | 1.7331 | 1.7658 | 1.4099 | 1.3527 | 1.5458 | 1.5673 | 1.5958 | 1.7043
2022-03-26 11:00 | 1.7719 | 1.9746 | 2.0109 | 2.0553 | 2.107 | 1.1813 | 1.4471 | 1.4753 | 1.514 | 1.1813 | 1.467 | 1.6806 | 1.706 | 1.7397 | 1.8607
2022-03-26 12:00 | 1.7338 | 1.938 | 1.9765 | 2.0236 | 2.0785 | 1.2194 | 1.4952 | 1.5252 | 1.5662 | 1.2194 | 1.5623 | 1.7895 | 1.8165 | 1.8523 | 1.981
2022-03-26 13:00 | 1.6385 | 1.8346 | 1.8726 | 1.919 | 1.9732 | 0.97168 | 1.2019 | 1.2315 | 1.2719 | 0.97168 | 1.467 | 1.6829 | 1.7095 | 1.7448 | 1.8677
2022-03-26 14:00 | 1.7338 | 1.932 | 1.9674 | 2.0107 | 2.0612 | 1.2003 | 1.4683 | 1.4959 | 1.5336 | 1.2003 | 1.5433 | 1.764 | 1.7888 | 1.8218 | 1.946
2022-03-26 15:00 | 1.6957 | 1.8856 | 1.9183 | 1.9582 | 2.0048 | 1.2041 | 1.4689 | 1.4943 | 1.5291 | 1.2041 | 1.5433 | 1.7602 | 1.7831 | 1.8135 | 1.9346
2022-03-26 16:00 | 1.81 | 2.0049 | 2.0357 | 2.0734 | 2.1173 | 1.2194 | 1.4843 | 1.5083 | 1.5411 | 1.2194 | 1.2003 | 1.3766 | 1.3982 | 1.4268 | 1.5271
2022-03-26 17:00 | 1.829 | 2.0245 | 2.0548 | 2.092 | 2.1353 | 1.467 | 1.7763 | 1.8 | 1.8323 | 1.467 | 1.7909 | 2.0323 | 2.0536 | 2.0818 | 2.2141
2022-03-26 18:00 | 2.0767 | 2.2941 | 2.3263 | 2.3657 | 2.4116 | 1.7147 | 2.0715 | 2.0966 | 2.1308 | 1.7147 | 2.2482 | 2.5429 | 2.5655 | 2.5954 | 2.7549
2022-03-26 19:00 | 2.2101 | 2.4447 | 2.4807 | 2.5247 | 2.5759 | 1.7338 | 2.0993 | 2.1273 | 2.1656 | 1.7338 | 2.8388 | 3.2045 | 3.2297 | 3.2631 | 3.4592
2022-03-26 20:00 | 2.191 | 2.434 | 2.4749 | 2.525 | 2.5834 | 1.7147 | 2.0839 | 2.1158 | 2.1594 | 1.7147 | 2.191 | 2.4916 | 2.5202 | 2.5583 | 2.7243
2022-03-26 21:00 | 2.1148 | 2.3618 | 2.4077 | 2.4638 | 2.5293 | 1.6004 | 1.9559 | 1.9916 | 2.0405 | 1.6004 | 2.4387 | 2.7736 | 2.8058 | 2.8485 | 3.0336
2022-03-26 22:00 | 1.9624 | 2.1997 | 2.2464 | 2.3035 | 2.3702 | 1.4861 | 1.822 | 1.8584 | 1.9081 | 1.4861 | 1.9624 | 2.2455 | 2.2782 | 2.3217 | 2.4815
2022-03-26 23:00 | 1.8657 | 2.0899 | 2.1335 | 2.1869 | 2.2492 | 1.3337 | 1.6376 | 1.6717 | 1.7181 | 1.3337 | 1.7338 | 1.9872 | 2.0178 | 2.0584 | 2.2023
2022-03-27 | 1.7338 | 1.9397 | 1.979 | 2.0271 | 2.0833 | 1.2027 | 1.4768 | 1.5075 | 1.5493 | 1.2027 | 1.6195 | 1.8542 | 1.8818 | 1.9184 | 2.0512
2022-03-27 01:00 | 1.6004 | 1.7869 | 1.8214 | 1.8637 | 1.9129 | 1.0737 | 1.3175 | 1.3444 | 1.3811 | 1.0737 | 1.7338 | 1.9745 | 1.9987 | 2.0308 | 2.1646
2022-03-27 02:00 | 1.5433 | 1.716 | 1.7456 | 1.7818 | 1.8241 | 1.0288 | 1.2575 | 1.2806 | 1.3122 | 1.0288 | 1.3146 | 1.502 | 1.5227 | 1.5503 | 1.6555
2022-03-27 03:00 | 1.5279 | 1.6874 | 1.7108 | 1.7395 | 1.773 | 0.99073 | 1.2037 | 1.222 | 1.247 | 0.99073 | 1.2765 | 1.4511 | 1.4675 | 1.4893 | 1.5856
2022-03-27 04:00 | 1.5433 | 1.6921 | 1.7095 | 1.7308 | 1.7556 | 0.98568 | 1.1892 | 1.2028 | 1.2213 | 0.98568 | 1.2765 | 1.4427 | 1.4549 | 1.4711 | 1.5606
2022-03-27 05:00 | 1.5433 | 1.682 | 1.6942 | 1.7093 | 1.7268 | 1.0336 | 1.2384 | 1.248 | 1.261 | 1.0336 | 1.4099 | 1.5838 | 1.5923 | 1.6038 | 1.6949
2022-03-27 06:00 | 1.589 | 1.7272 | 1.7374 | 1.75 | 1.7646 | 1.105 | 1.32 | 1.328 | 1.3389 | 1.105 | 1.5052 | 1.6868 | 1.694 | 1.7035 | 1.7976
2022-03-27 07:00 | 1.6766 | 1.8246 | 1.8366 | 1.8512 | 1.8682 | 1.2226 | 1.4613 | 1.4706 | 1.4833 | 1.2226 | 1.448 | 1.6256 | 1.634 | 1.6451 | 1.738
2022-03-27 08:00 | 1.757 | 1.9201 | 1.9367 | 1.957 | 1.9806 | 1.2897 | 1.5472 | 1.5601 | 1.5778 | 1.2897 | 1.6385 | 1.8438 | 1.8554 | 1.8709 | 1.9794
2022-03-27 09:00 | 1.885 | 2.0709 | 2.0943 | 2.1229 | 2.1563 | 1.3146 | 1.5863 | 1.6046 | 1.6295 | 1.3146 | 1.81 | 2.0438 | 2.0602 | 2.082 | 2.2075
2022-03-27 10:00 | 1.9434 | 2.1479 | 2.1786 | 2.2161 | 2.2599 | 1.4861 | 1.7992 | 1.8232 | 1.8558 | 1.4861 | 1.6385 | 1.8634 | 1.8848 | 1.9134 | 2.0376
2022-03-27 11:00 | 1.9053 | 2.1179 | 2.1541 | 2.1985 | 2.2503 | 1.3718 | 1.6721 | 1.7004 | 1.739 | 1.3718 | 1.5242 | 1.7441 | 1.7695 | 1.8032 | 1.9274
2022-03-27 12:00 | 1.9434 | 2.1632 | 2.2016 | 2.2488 | 2.3037 | 1.2384 | 1.5177 | 1.5477 | 1.5887 | 1.2384 | 1.5052 | 1.726 | 1.7529 | 1.7888 | 1.9144
2022-03-27 13:00 | 1.5242 | 1.7118 | 1.7497 | 1.7962 | 1.8503 | 1.105 | 1.3594 | 1.389 | 1.4294 | 1.105 | 1.6004 | 1.8311 | 1.8577 | 1.893 | 2.0232
2022-03-27 14:00 | 1.6957 | 1.891 | 1.9264 | 1.9698 | 2.0203 | 1.2575 | 1.5359 | 1.5635 | 1.6012 | 1.2575 | 1.5052 | 1.7217 | 1.7465 | 1.7795 | 1.9016
2022-03-27 15:00 | 1.9243 | 2.1313 | 2.1639 | 2.2038 | 2.2504 | 1.2384 | 1.5094 | 1.5349 | 1.5696 | 1.2384 | 1.3117 | 1.5029 | 1.5257 | 1.5561 | 1.6646
2022-03-27 16:00 | 2.0767 | 2.2914 | 2.3222 | 2.3599 | 2.4039 | 1.4861 | 1.7994 | 1.8234 | 1.8562 | 1.4861 | 2.0005 | 2.2658 | 2.2874 | 2.3161 | 2.4603
2022-03-27 17:00 | 2.1529 | 2.3724 | 2.4028 | 2.44 | 2.4833 | 1.7572 | 2.1191 | 2.1428 | 2.1751 | 1.7572 | 2.0958 | 2.3711 | 2.3923 | 2.4206 | 2.5696
2022-03-27 18:00 | 2.3816 | 2.6216 | 2.6538 | 2.6932 | 2.7391 | 1.8672 | 2.2515 | 2.2766 | 2.3109 | 1.8672 | 2.4578 | 2.7758 | 2.7984 | 2.8283 | 2.9993
2022-03-27 19:00 | 2.4959 | 2.7518 | 2.7877 | 2.8317 | 2.883 | 1.9815 | 2.3919 | 2.4199 | 2.4582 | 1.9815 | 2.4959 | 2.8234 | 2.8486 | 2.882 | 3.0592
2022-03-27 20:00 | 2.4387 | 2.7001 | 2.741 | 2.7911 | 2.8495 | 1.8672 | 2.2639 | 2.2959 | 2.3394 | 1.8672 | 2.4006 | 2.7245 | 2.7531 | 2.7912 | 2.9687
2022-03-27 21:00 | 2.345 | 2.6091 | 2.6549 | 2.7111 | 2.7765 | 1.7528 | 2.1359 | 2.1717 | 2.2205 | 1.7528 | 2.4197 | 2.7525 | 2.7846 | 2.8273 | 3.0114
2022-03-27 22:00 | 2.1529 | 2.4044 | 2.4511 | 2.5082 | 2.5749 | 1.5518 | 1.8997 | 1.9361 | 1.9858 | 1.5518 | 2.4578 | 2.796 | 2.8287 | 2.8722 | 3.0592
2022-03-27 23:00 | 2.0196 | 2.2552 | 2.2988 | 2.3522 | 2.4145 | 1.2722 | 1.5649 | 1.599 | 1.6455 | 1.2722 | 1.8672 | 2.1354 | 2.166 | 2.2066 | 2.3579
2022-03-28 | 1.8069 | 2.0183 | 2.0576 | 2.1058 | 2.1619 | 1.1432 | 1.4064 | 1.4371 | 1.479 | 1.1432 | 1.467 | 1.6848 | 1.7124 | 1.749 | 1.8734
2022-03-28 01:00 | 1.6766 | 1.8688 | 1.9033 | 1.9456 | 1.9948 | 1.0669 | 1.3095 | 1.3364 | 1.3732 | 1.0669 | 1.3337 | 1.5299 | 1.5541 | 1.5862 | 1.698
2022-03-28 02:00 | 1.6766 | 1.8592 | 1.8889 | 1.9251 | 1.9674 | 1.0098 | 1.235 | 1.2581 | 1.2897 | 1.0098 | 1.4099 | 1.6078 | 1.6286 | 1.6561 | 1.7666
2022-03-28 03:00 | 1.6766 | 1.8472 | 1.8706 | 1.8993 | 1.9328 | 0.97168 | 1.1812 | 1.1995 | 1.2245 | 0.97168 | 1.2575 | 1.4299 | 1.4463 | 1.4681 | 1.5634
2022-03-28 04:00 | 1.6766 | 1.8353 | 1.8528 | 1.8741 | 1.8989 | 1.0009 | 1.2072 | 1.2208 | 1.2393 | 1.0009 | 1.2956 | 1.4639 | 1.4761 | 1.4923 | 1.5829
2022-03-28 05:00 | 1.775 | 1.931 | 1.9433 | 1.9583 | 1.9758 | 1.1503 | 1.3763 | 1.3859 | 1.3989 | 1.1503 | 1.3878 | 1.5592 | 1.5677 | 1.5792 | 1.6691
2022-03-28 06:00 | 2.0386 | 2.2102 | 2.2204 | 2.233 | 2.2476 | 1.3725 | 1.636 | 1.644 | 1.6549 | 1.3725 | 1.5623 | 1.7503 | 1.7575 | 1.767 | 1.8643
2022-03-28 07:00 | 2.4197 | 2.6229 | 2.6349 | 2.6495 | 2.6665 | 1.6385 | 1.9526 | 1.962 | 1.9747 | 1.6385 | 2.1529 | 2.409 | 2.4174 | 2.4285 | 2.5601
2022-03-28 08:00 | 2.3816 | 2.5911 | 2.6077 | 2.6279 | 2.6516 | 1.5989 | 1.9124 | 1.9253 | 1.943 | 1.5989 | 1.8481 | 2.0767 | 2.0883 | 2.1038 | 2.2238
2022-03-28 09:00 | 2.2291 | 2.4407 | 2.4641 | 2.4927 | 2.5261 | 1.3527 | 1.6313 | 1.6496 | 1.6745 | 1.3527 | 1.4099 | 1.5992 | 1.6156 | 1.6374 | 1.7409
2022-03-28 10:00 | 2.0196 | 2.2298 | 2.2604 | 2.298 | 2.3418 | 0.91879 | 1.129 | 1.153 | 1.1856 | 0.91879 | 1.5052 | 1.7152 | 1.7366 | 1.7652 | 1.8821
2022-03-28 11:00 | 1.9053 | 2.1179 | 2.1541 | 2.1985 | 2.2503 | 0.83831 | 1.0419 | 1.0702 | 1.1088 | 0.83831 | 1.448 | 1.6594 | 1.6848 | 1.7186 | 1.8385
2022-03-28 12:00 | 1.9434 | 2.1632 | 2.2016 | 2.2488 | 2.3037 | 0.83831 | 1.0451 | 1.0751 | 1.1161 | 0.83831 | 1.0669 | 1.239 | 1.266 | 1.3018 | 1.4033
2022-03-28 13:00 | 2.191 | 2.4282 | 2.4661 | 2.5126 | 2.5667 | 1.0799 | 1.3298 | 1.3594 | 1.3998 | 1.0799 | 1.2003 | 1.3865 | 1.4131 | 1.4484 | 1.5566
2022-03-28 14:00 | 2.4959 | 2.7507 | 2.7861 | 2.8295 | 2.88 | 1.467 | 1.7834 | 1.8111 | 1.8487 | 1.467 | 1.6576 | 1.8911 | 1.9159 | 1.9488 | 2.0794
2022-03-28 15:00 | 2.4959 | 2.7453 | 2.778 | 2.8179 | 2.8645 | 1.4861 | 1.802 | 1.8275 | 1.8622 | 1.4861 | 1.6957 | 1.9296 | 1.9525 | 1.9828 | 2.1124
2022-03-28 16:00 | 2.4006 | 2.6394 | 2.6702 | 2.7079 | 2.7519 | 1.467 | 1.7769 | 1.8009 | 1.8337 | 1.467 | 1.829 | 2.0753 | 2.0968 | 2.1255 | 2.2604
2022-03-28 17:00 | 2.5149 | 2.7613 | 2.7917 | 2.8289 | 2.8722 | 1.7147 | 2.0689 | 2.0926 | 2.1249 | 1.7147 | 2.3054 | 2.604 | 2.6252 | 2.6535 | 2.814
2022-03-28 18:00 | 2.5149 | 2.7649 | 2.7971 | 2.8364 | 2.8824 | 1.9624 | 2.3641 | 2.3892 | 2.4234 | 1.9624 | 2.8388 | 3.1993 | 3.2218 | 3.2518 | 3.4437
2022-03-28 19:00 | 2.5721 | 2.8337 | 2.8696 | 2.9136 | 2.9649 | 1.9243 | 2.3244 | 2.3524 | 2.3907 | 1.9243 | 2.4006 | 2.7175 | 2.7427 | 2.7762 | 2.9481
2022-03-28 20:00 | 2.3816 | 2.6387 | 2.6796 | 2.7297 | 2.7881 | 1.81 | 2.1964 | 2.2283 | 2.2719 | 1.81 | 2.3816 | 2.7033 | 2.7319 | 2.77 | 2.9465
2022-03-28 21:00 | 2.2482 | 2.5051 | 2.551 | 2.6071 | 2.6725 | 1.7528 | 2.1359 | 2.1717 | 2.2205 | 1.7528 | 2.2291 | 2.5408 | 2.5729 | 2.6156 | 2.7892
2022-03-28 22:00 | 2.0941 | 2.3411 | 2.3878 | 2.445 | 2.5116 | 1.5132 | 1.854 | 1.8904 | 1.9402 | 1.5132 | 1.9243 | 2.2032 | 2.2359 | 2.2793 | 2.4371
2022-03-28 23:00 | 1.9243 | 2.1528 | 2.1965 | 2.2499 | 2.3122 | 1.2494 | 1.538 | 1.5721 | 1.6186 | 1.2494 | 1.6385 | 1.8813 | 1.9119 | 1.9526 | 2.0912
2022-03-29 | 1.7719 | 1.9806 | 2.0199 | 2.0681 | 2.1242 | 1.1315 | 1.3927 | 1.4234 | 1.4652 | 1.1315 | 1.448 | 1.6636 | 1.6912 | 1.7278 | 1.8512
2022-03-29 01:00 | 1.6766 | 1.8688 | 1.9033 | 1.9456 | 1.9948 | 1.086 | 1.332 | 1.3589 | 1.3957 | 1.086 | 1.2575 | 1.4452 | 1.4694 | 1.5015 | 1.6091
2022-03-29 02:00 | 1.6195 | 1.7978 | 1.8275 | 1.8637 | 1.906 | 0.99853 | 1.2217 | 1.2448 | 1.2764 | 0.99853 | 1.3146 | 1.502 | 1.5227 | 1.5503 | 1.6555
2022-03-29 03:00 | 1.6385 | 1.8062 | 1.8297 | 1.8584 | 1.8918 | 0.97168 | 1.1812 | 1.1995 | 1.2245 | 0.97168 | 1.3718 | 1.5569 | 1.5733 | 1.5952 | 1.6967
2022-03-29 04:00 | 1.6748 | 1.8333 | 1.8507 | 1.8721 | 1.8969 | 0.99073 | 1.1952 | 1.2087 | 1.2273 | 0.99073 | 1.3337 | 1.5062 | 1.5184 | 1.5346 | 1.6273
2022-03-29 05:00 | 1.7719 | 1.9276 | 1.9399 | 1.9549 | 1.9724 | 1.1218 | 1.3427 | 1.3523 | 1.3653 | 1.1218 | 1.3146 | 1.4779 | 1.4865 | 1.4979 | 1.5838
2022-03-29 06:00 | 2.0145 | 2.1843 | 2.1946 | 2.2071 | 2.2217 | 1.3954 | 1.6631 | 1.671 | 1.6819 | 1.3954 | 1.6957 | 1.8985 | 1.9057 | 1.9152 | 2.0198
2022-03-29 07:00 | 2.4006 | 2.6025 | 2.6144 | 2.629 | 2.646 | 1.5433 | 1.8401 | 1.8494 | 1.8621 | 1.5433 | 2.1148 | 2.3667 | 2.375 | 2.3861 | 2.5157
2022-03-29 08:00 | 2.3435 | 2.5501 | 2.5667 | 2.587 | 2.6107 | 1.4861 | 1.7792 | 1.7921 | 1.8098 | 1.4861 | 1.6576 | 1.865 | 1.8766 | 1.892 | 2.0016
2022-03-29 09:00 | 2.2291 | 2.4407 | 2.4641 | 2.4927 | 2.5261 | 1.2813 | 1.5469 | 1.5651 | 1.5901 | 1.2813 | 1.3146 | 1.4933 | 1.5097 | 1.5315 | 1.6298
2022-03-29 10:00 | 2.191 | 2.414 | 2.4447 | 2.4822 | 2.526 | 1.2384 | 1.5066 | 1.5306 | 1.5632 | 1.2384 | 1.1241 | 1.2917 | 1.3132 | 1.3418 | 1.4377
2022-03-29 11:00 | 1.9833 | 2.2018 | 2.238 | 2.2824 | 2.3342 | 0.91258 | 1.1296 | 1.1579 | 1.1966 | 0.91258 | 0.87642 | 1.0242 | 1.0496 | 1.0834 | 1.1719
2022-03-29 12:00 | 2.1148 | 2.3474 | 2.3859 | 2.433 | 2.4879 | 0.93358 | 1.1576 | 1.1876 | 1.2286 | 0.93358 | 1.1432 | 1.3237 | 1.3507 | 1.3865 | 1.4922
2022-03-29 13:00 | 1.9815 | 2.2031 | 2.241 | 2.2874 | 2.3416 | 0.91452 | 1.1343 | 1.1639 | 1.2043 | 0.91452 | 1.7528 | 2.0005 | 2.0271 | 2.0624 | 2.201
2022-03-29 14:00 | 1.9624 | 2.1776 | 2.213 | 2.2563 | 2.3068 | 0.95658 | 1.1804 | 1.208 | 1.2457 | 0.95658 | 1.3337 | 1.5312 | 1.556 | 1.5889 | 1.7016
2022-03-29 15:00 | 2.2863 | 2.5202 | 2.5528 | 2.5927 | 2.6393 | 1.2194 | 1.4869 | 1.5124 | 1.5471 | 1.2194 | 1.0479 | 1.2097 | 1.2326 | 1.263 | 1.3569
2022-03-29 16:00 | 2.2291 | 2.4552 | 2.486 | 2.5237 | 2.5676 | 1.4289 | 1.7319 | 1.7559 | 1.7887 | 1.4289 | 1.3527 | 1.546 | 1.5675 | 1.5962 | 1.7049
2022-03-29 17:00 | 2.4835 | 2.7276 | 2.7579 | 2.7951 | 2.8384 | 1.6957 | 2.0464 | 2.0701 | 2.1024 | 1.6957 | 2.1148 | 2.3922 | 2.4135 | 2.4418 | 2.5918
2022-03-29 18:00 | 2.6102 | 2.8672 | 2.8994 | 2.9388 | 2.9847 | 1.8862 | 2.274 | 2.2991 | 2.3334 | 1.8862 | 2.7055 | 3.0511 | 3.0736 | 3.1036 | 3.2881
2022-03-29 19:00 | 2.5149 | 2.7722 | 2.8082 | 2.8522 | 2.9034 | 1.9053 | 2.3019 | 2.3299 | 2.3682 | 1.9053 | 2.896 | 3.268 | 3.2932 | 3.3266 | 3.5259
2022-03-29 20:00 | 2.4197 | 2.6797 | 2.7206 | 2.7707 | 2.829 | 1.8363 | 2.2275 | 2.2594 | 2.3029 | 1.8363 | 2.3816 | 2.7033 | 2.7319 | 2.77 | 2.9465
2022-03-29 21:00 | 2.2863 | 2.546 | 2.5919 | 2.648 | 2.7135 | 1.7147 | 2.0909 | 2.1267 | 2.1755 | 1.7147 | 2.3244 | 2.6466 | 2.6787 | 2.7214 | 2.9003
2022-03-29 22:00 | 2.1018 | 2.3495 | 2.3962 | 2.4533 | 2.52 | 1.6576 | 2.0246 | 2.061 | 2.1107 | 1.6576 | 1.9815 | 2.2667 | 2.2994 | 2.3428 | 2.5038
2022-03-29 23:00 | 1.955 | 2.1858 | 2.2294 | 2.2828 | 2.3451 | 1.292 | 1.5884 | 1.6225 | 1.669 | 1.292 | 1.6195 | 1.8602 | 1.8908 | 1.9314 | 2.069
2022-03-30 | 1.7719 | 1.9806 | 2.0199 | 2.0681 | 2.1242 | 1.1492 | 1.4135 | 1.4442 | 1.4861 | 1.1492 | 1.6195 | 1.8542 | 1.8818 | 1.9184 | 2.0512
2022-03-30 01:00 | 1.6766 | 1.8688 | 1.9033 | 1.9456 | 1.9948 | 1.0479 | 1.287 | 1.3139 | 1.3507 | 1.0479 | 1.3718 | 1.5723 | 1.5964 | 1.6286 | 1.7424
2022-03-30 02:00 | 1.6385 | 1.8183 | 1.8479 | 1.8842 | 1.9264 | 0.99073 | 1.2125 | 1.2356 | 1.2672 | 0.99073 | 1.3908 | 1.5866 | 1.6074 | 1.635 | 1.7444
2022-03-30 03:00 | 1.6195 | 1.7858 | 1.8092 | 1.8379 | 1.8714 | 0.99073 | 1.2037 | 1.222 | 1.247 | 0.99073 | 1.3146 | 1.4934 | 1.5098 | 1.5317 | 1.63
2022-03-30 04:00 | 1.6766 | 1.8353 | 1.8528 | 1.8741 | 1.8989 | 1.0169 | 1.2261 | 1.2397 | 1.2582 | 1.0169 | 1.2384 | 1.4003 | 1.4125 | 1.4287 | 1.5162
2022-03-30 05:00 | 1.7819 | 1.9383 | 1.9506 | 1.9656 | 1.9831 | 1.1086 | 1.327 | 1.3366 | 1.3496 | 1.1086 | 1.467 | 1.6473 | 1.6559 | 1.6673 | 1.7616
2022-03-30 06:00 | 1.9243 | 2.0874 | 2.0976 | 2.1102 | 2.1248 | 1.448 | 1.7251 | 1.7331 | 1.744 | 1.448 | 1.6766 | 1.8773 | 1.8845 | 1.894 | 1.9976
2022-03-30 07:00 | 2.3054 | 2.5001 | 2.512 | 2.5267 | 2.5437 | 1.6697 | 1.9895 | 1.9988 | 2.0115 | 1.6697 | 1.9434 | 2.1761 | 2.1845 | 2.1956 | 2.3157
2022-03-30 08:00 | 2.2896 | 2.4922 | 2.5088 | 2.5291 | 2.5528 | 1.6766 | 2.0043 | 2.0172 | 2.0349 | 1.6766 | 1.6195 | 1.8226 | 1.8343 | 1.8497 | 1.9572
2022-03-30 09:00 | 2.2863 | 2.5021 | 2.5255 | 2.5541 | 2.5875 | 1.3718 | 1.6538 | 1.6721 | 1.697 | 1.3718 | 1.2956 | 1.4722 | 1.4886 | 1.5103 | 1.6076
2022-03-30 10:00 | 2.1529 | 2.373 | 2.4037 | 2.4413 | 2.485 | 1.2956 | 1.5742 | 1.5981 | 1.6307 | 1.2956 | 0.93358 | 1.08 | 1.1015 | 1.13 | 1.2155
2022-03-30 11:00 | 2.0984 | 2.3254 | 2.3616 | 2.406 | 2.4578 | 0.95263 | 1.177 | 1.2052 | 1.2439 | 0.95263 | 1.4289 | 1.6382 | 1.6636 | 1.6974 | 1.8163
2022-03-30 12:00 | 2.2291 | 2.4702 | 2.5087 | 2.5558 | 2.6107 | 1.1813 | 1.4502 | 1.4802 | 1.5212 | 1.1813 | 0.99073 | 1.1543 | 1.1813 | 1.2171 | 1.3144
2022-03-30 13:00 | 2.1339 | 2.3668 | 2.4047 | 2.4512 | 2.5054 | 1.1622 | 1.4269 | 1.4565 | 1.4969 | 1.1622 | 1.7719 | 2.0216 | 2.0482 | 2.0836 | 2.2232
2022-03-30 14:00 | 2.2291 | 2.4642 | 2.4996 | 2.5429 | 2.5934 | 1.2384 | 1.5133 | 1.541 | 1.5787 | 1.2384 | 1.0288 | 1.1924 | 1.2172 | 1.2502 | 1.3461
2022-03-30 15:00 | 2.3168 | 2.5529 | 2.5855 | 2.6255 | 2.6721 | 1.3527 | 1.6445 | 1.6699 | 1.7047 | 1.3527 | 1.1813 | 1.3579 | 1.3808 | 1.4112 | 1.5125
2022-03-30 16:00 | 2.3244 | 2.5575 | 2.5883 | 2.626 | 2.67 | 1.4663 | 1.7761 | 1.8001 | 1.8329 | 1.4663 | 1.5623 | 1.7788 | 1.8004 | 1.8291 | 1.9493
2022-03-30 17:00 | 2.3435 | 2.5771 | 2.6075 | 2.6447 | 2.688 | 1.7147 | 2.0689 | 2.0926 | 2.1249 | 1.7147 | 2.0577 | 2.3287 | 2.35 | 2.3783 | 2.5252
2022-03-30 18:00 | 2.4578 | 2.7035 | 2.7357 | 2.775 | 2.821 | 1.8481 | 2.229 | 2.2541 | 2.2884 | 1.8481 | 2.3435 | 2.6488 | 2.6714 | 2.7013 | 2.866
2022-03-30 19:00 | 2.4768 | 2.7313 | 2.7672 | 2.8112 | 2.8625 | 1.9434 | 2.3469 | 2.3749 | 2.4132 | 1.9434 | 2.4959 | 2.8234 | 2.8486 | 2.882 | 3.0592
2022-03-30 20:00 | 2.3816 | 2.6387 | 2.6796 | 2.7297 | 2.7881 | 1.829 | 2.2189 | 2.2508 | 2.2944 | 1.829 | 2.3435 | 2.6609 | 2.6896 | 2.7277 | 2.9021
2022-03-30 21:00 | 2.2482 | 2.5051 | 2.551 | 2.6071 | 2.6725 | 1.688 | 2.0593 | 2.0951 | 2.1439 | 1.688 | 2.6674 | 3.0277 | 3.0598 | 3.1025 | 3.3002
2022-03-30 22:00 | 2.0977 | 2.345 | 2.3917 | 2.4489 | 2.5155 | 1.5623 | 1.912 | 1.9485 | 1.9982 | 1.5623 | 2.0958 | 2.3937 | 2.4264 | 2.4699 | 2.6371
2022-03-30 23:00 | 1.9333 | 2.1625 | 2.2061 | 2.2596 | 2.3219 | 1.2731 | 1.5661 | 1.6001 | 1.6466 | 1.2731 | 1.6576 | 1.9025 | 1.9331 | 1.9737 | 2.1134
2022-03-31 | 1.8672 | 2.083 | 2.1223 | 2.1704 | 2.2266 | 1.1622 | 1.4289 | 1.4596 | 1.5015 | 1.1622 | 1.7528 | 2.0024 | 2.03 | 2.0666 | 2.2067
2022-03-31 01:00 | 1.6783 | 1.8706 | 1.9051 | 1.9474 | 1.9966 | 1.0304 | 1.2663 | 1.2932 | 1.33 | 1.0304 | 1.467 | 1.6781 | 1.7023 | 1.7344 | 1.8535
2022-03-31 02:00 | 1.6576 | 1.8388 | 1.8684 | 1.9046 | 1.9469 | 0.99073 | 1.2125 | 1.2356 | 1.2672 | 0.99073 | 1.4289 | 1.629 | 1.6497 | 1.6773 | 1.7888
2022-03-31 03:00 | 1.6385 | 1.8062 | 1.8297 | 1.8584 | 1.8918 | 0.97168 | 1.1812 | 1.1995 | 1.2245 | 0.97168 | 1.2956 | 1.4722 | 1.4887 | 1.5105 | 1.6078
2022-03-31 04:00 | 1.6103 | 1.764 | 1.7814 | 1.8028 | 1.8276 | 1.0154 | 1.2243 | 1.2378 | 1.2564 | 1.0154 | 1.3146 | 1.485 | 1.4972 | 1.5134 | 1.6051
2022-03-31 05:00 | 1.7719 | 1.9276 | 1.9399 | 1.9549 | 1.9724 | 1.1648 | 1.3935 | 1.403 | 1.4161 | 1.1648 | 1.3146 | 1.4779 | 1.4865 | 1.4979 | 1.5838
2022-03-31 06:00 | 2.0248 | 2.1954 | 2.2056 | 2.2181 | 2.2327 | 1.4099 | 1.6801 | 1.6881 | 1.699 | 1.4099 | 1.6704 | 1.8704 | 1.8775 | 1.8871 | 1.9903
2022-03-31 07:00 | 2.3816 | 2.582 | 2.5939 | 2.6085 | 2.6256 | 1.6004 | 1.9076 | 1.9169 | 1.9297 | 1.6004 | 2.0767 | 2.3243 | 2.3327 | 2.3438 | 2.4713
2022-03-31 08:00 | 2.2482 | 2.4478 | 2.4644 | 2.4847 | 2.5083 | 1.5242 | 1.8242 | 1.8371 | 1.8548 | 1.5242 | 1.7338 | 1.9497 | 1.9613 | 1.9767 | 2.0905
2022-03-31 09:00 | 2.191 | 2.3997 | 2.4231 | 2.4518 | 2.4852 | 1.2956 | 1.5638 | 1.5821 | 1.607 | 1.2956 | 1.086 | 1.2393 | 1.2557 | 1.2774 | 1.3632
2022-03-31 10:00 | 1.8672 | 2.066 | 2.0967 | 2.1342 | 2.178 | 1.0804 | 1.32 | 1.3439 | 1.3766 | 1.0804 | 1.2194 | 1.3976 | 1.4191 | 1.4476 | 1.5488
2022-03-31 11:00 | 2.0907 | 2.3171 | 2.3534 | 2.3978 | 2.4495 | 1.2883 | 1.5736 | 1.6019 | 1.6405 | 1.2883 | 1.6385 | 1.8711 | 1.8965 | 1.9303 | 2.0607
2022-03-31 12:00 | 2.2673 | 2.5111 | 2.5496 | 2.5967 | 2.6517 | 1.3146 | 1.6078 | 1.6378 | 1.6788 | 1.3146 | 2.0196 | 2.2976 | 2.3246 | 2.3604 | 2.5143
2022-03-31 13:00 | 1.9624 | 2.1826 | 2.2205 | 2.267 | 2.3211 | 1.0479 | 1.2919 | 1.3215 | 1.3619 | 1.0479 | 1.8481 | 2.1063 | 2.1329 | 2.1682 | 2.3121
2022-03-31 14:00 | 1.9815 | 2.1981 | 2.2335 | 2.2768 | 2.3273 | 1.0098 | 1.2433 | 1.2709 | 1.3086 | 1.0098 | 2.0196 | 2.2934 | 2.3182 | 2.3511 | 2.5015
2022-03-31 15:00 | 2.172 | 2.3973 | 2.43 | 2.4699 | 2.5165 | 1.3527 | 1.6445 | 1.6699 | 1.7047 | 1.3527 | 1.6385 | 1.8661 | 1.8889 | 1.9193 | 2.0457
2022-03-31 16:00 | 2.191 | 2.4142 | 2.445 | 2.4827 | 2.5267 | 1.467 | 1.7769 | 1.8009 | 1.8337 | 1.467 | 1.6004 | 1.8212 | 1.8428 | 1.8714 | 1.9937
2022-03-31 17:00 | 2.191 | 2.4134 | 2.4437 | 2.4809 | 2.5242 | 1.6766 | 2.0239 | 2.0475 | 2.0799 | 1.6766 | 2.0386 | 2.3075 | 2.3288 | 2.3571 | 2.503
2022-03-31 18:00 | 2.4387 | 2.683 | 2.7152 | 2.7546 | 2.8005 | 1.8481 | 2.229 | 2.2541 | 2.2884 | 1.8481 | 2.5721 | 2.9029 | 2.9254 | 2.9554 | 3.1326
2022-03-31 19:00 | 2.6483 | 2.9155 | 2.9515 | 2.9954 | 3.0467 | 1.9053 | 2.3019 | 2.3299 | 2.3682 | 1.9053 | 2.6483 | 2.9928 | 3.018 | 3.0514 | 3.237
2022-03-31 20:00 | 2.6293 | 2.9048 | 2.9457 | 2.9958 | 3.0542 | 1.8862 | 2.2865 | 2.3184 | 2.3619 | 1.8862 | 2.4578 | 2.788 | 2.8166 | 2.8547 | 3.0354
2022-03-31 21:00 | 2.4387 | 2.7098 | 2.7557 | 2.8118 | 2.8772 | 1.8672 | 2.271 | 2.3067 | 2.3556 | 1.8672 | 2.5149 | 2.8583 | 2.8905 | 2.9332 | 3.1225
2022-03-31 22:00 | 2.3054 | 2.5681 | 2.6148 | 2.672 | 2.7386 | 1.6223 | 1.9829 | 2.0193 | 2.0691 | 1.6223 | 2.2673 | 2.5843 | 2.617 | 2.6604 | 2.837
2022-03-31 23:00 | 2.0005 | 2.2347 | 2.2783 | 2.3318 | 2.394 | 1.3908 | 1.7051 | 1.7392 | 1.7857 | 1.3908 | 1.81 | 2.0719 | 2.1025 | 2.1431 | 2.2912
2022-04-01 | 1.9053 | 2.1239 | 2.1632 | 2.2114 | 2.2675 | 1.1946 | 1.4671 | 1.4978 | 1.5397 | 1.1946 | 1.6957 | 1.9389 | 1.9664 | 2.0031 | 2.1401
2022-04-01 01:00 | 1.7338 | 1.9302 | 1.9647 | 2.007 | 2.0562 | 1.1241 | 1.377 | 1.4039 | 1.4407 | 1.1241 | 1.5052 | 1.7205 | 1.7446 | 1.7768 | 1.8979
2022-04-01 02:00 | 1.7909 | 1.9821 | 2.0117 | 2.0479 | 2.0902 | 1.0479 | 1.28 | 1.3031 | 1.3347 | 1.0479 | 1.448 | 1.6502 | 1.6709 | 1.6985 | 1.8111
2022-04-01 03:00 | 1.7338 | 1.9086 | 1.932 | 1.9607 | 1.9942 | 1.0479 | 1.2713 | 1.2896 | 1.3145 | 1.0479 | 1.3908 | 1.5781 | 1.5945 | 1.6163 | 1.7189
2022-04-01 04:00 | 1.8481 | 2.0196 | 2.037 | 2.0583 | 2.0831 | 1.0479 | 1.2627 | 1.2763 | 1.2948 | 1.0479 | 1.4099 | 1.5909 | 1.6031 | 1.6193 | 1.7162
2022-04-01 05:00 | 1.9243 | 2.0914 | 2.1036 | 2.1186 | 2.1361 | 1.2471 | 1.4908 | 1.5003 | 1.5134 | 1.2471 | 1.8481 | 2.0707 | 2.0793 | 2.0907 | 2.206
2022-04-01 06:00 | 2.1946 | 2.3777 | 2.388 | 2.4005 | 2.4151 | 1.5422 | 1.8364 | 1.8444 | 1.8553 | 1.5422 | 1.9434 | 2.1738 | 2.1809 | 2.1905 | 2.3087
2022-04-01 07:00 | 2.5911 | 2.8071 | 2.8191 | 2.8337 | 2.8507 | 1.7909 | 2.1327 | 2.142 | 2.1547 | 1.7909 | 2.9531 | 3.2983 | 3.3066 | 3.3177 | 3.4934
2022-04-01 08:00 | 2.6293 | 2.8572 | 2.8738 | 2.894 | 2.9177 | 1.6957 | 2.0268 | 2.0397 | 2.0574 | 1.6957 | 2.191 | 2.4578 | 2.4694 | 2.4849 | 2.6238
2022-04-01 09:00 | 2.4006 | 2.6249 | 2.6483 | 2.6769 | 2.7103 | 1.3146 | 1.5863 | 1.6046 | 1.6295 | 1.3146 | 1.3718 | 1.5569 | 1.5732 | 1.595 | 1.6965
2022-04-01 10:00 | 2.191 | 2.414 | 2.4447 | 2.4822 | 2.526 | 1.1813 | 1.4391 | 1.463 | 1.4957 | 1.1813 | 1.105 | 1.2705 | 1.292 | 1.3206 | 1.4155
2022-04-01 11:00 | 2.191 | 2.4249 | 2.4612 | 2.5056 | 2.5573 | 1.1813 | 1.4471 | 1.4753 | 1.514 | 1.1813 | 1.0098 | 1.1724 | 1.1978 | 1.2316 | 1.3275
2022-04-01 12:00 | 2.172 | 2.4088 | 2.4473 | 2.4944 | 2.5493 | 1.1432 | 1.4052 | 1.4352 | 1.4762 | 1.1432 | 1.1813 | 1.3661 | 1.393 | 1.4288 | 1.5366
2022-04-01 13:00 | 2.0767 | 2.3054 | 2.3433 | 2.3898 | 2.4439 | 1.086 | 1.3369 | 1.3665 | 1.4069 | 1.086 | 1.7528 | 2.0005 | 2.0271 | 2.0624 | 2.201
2022-04-01 14:00 | 2.0005 | 2.2185 | 2.2539 | 2.2973 | 2.3478 | 1.0479 | 1.2883 | 1.3159 | 1.3536 | 1.0479 | 1.5242 | 1.7429 | 1.7677 | 1.8006 | 1.9238
2022-04-01 15:00 | 2.191 | 2.4178 | 2.4505 | 2.4904 | 2.537 | 1.2575 | 1.5319 | 1.5574 | 1.5921 | 1.2575 | 1.2956 | 1.485 | 1.5078 | 1.5382 | 1.6458
2022-04-01 16:00 | 2.2863 | 2.5166 | 2.5474 | 2.5851 | 2.629 | 1.3527 | 1.6419 | 1.6659 | 1.6987 | 1.3527 | 1.4289 | 1.6306 | 1.6522 | 1.6809 | 1.7937
2022-04-01 17:00 | 2.1339 | 2.352 | 2.3823 | 2.4195 | 2.4628 | 1.4289 | 1.7313 | 1.7549 | 1.7873 | 1.4289 | 1.81 | 2.0535 | 2.0747 | 2.103 | 2.2363
2022-04-01 18:00 | 2.4006 | 2.6421 | 2.6742 | 2.7136 | 2.7595 | 1.829 | 2.2065 | 2.2316 | 2.2659 | 1.829 | 2.8579 | 3.2205 | 3.243 | 3.273 | 3.4659
2022-04-01 19:00 | 2.7055 | 2.9769 | 3.0129 | 3.0569 | 3.1081 | 1.9434 | 2.3469 | 2.3749 | 2.4132 | 1.9434 | 3.258 | 3.6703 | 3.6955 | 3.7289 | 3.948
2022-04-01 20:00 | 2.6864 | 2.9662 | 3.0071 | 3.0572 | 3.1156 | 1.9434 | 2.354 | 2.3859 | 2.4295 | 1.9434 | 2.9341 | 3.3173 | 3.3459 | 3.384 | 3.5909
2022-04-01 21:00 | 2.4959 | 2.7712 | 2.8171 | 2.8732 | 2.9386 | 1.8672 | 2.271 | 2.3067 | 2.3556 | 1.8672 | 3.1246 | 3.5358 | 3.568 | 3.6107 | 3.8335
2022-04-01 22:00 | 2.3435 | 2.6091 | 2.6558 | 2.7129 | 2.7796 | 1.7528 | 2.1371 | 2.1735 | 2.2233 | 1.7528 | 2.4387 | 2.7748 | 2.8075 | 2.851 | 3.037
2022-04-01 23:00 | 2.1339 | 2.378 | 2.4216 | 2.475 | 2.5373 | 1.5433 | 1.8852 | 1.9192 | 1.9657 | 1.5433 | 2.3435 | 2.6647 | 2.6953 | 2.7359 | 2.9134
2022-04-02 | 2.1148 | 2.3491 | 2.3884 | 2.4365 | 2.4927 | 1.3718 | 1.6765 | 1.7072 | 1.7491 | 1.3718 | 1.9434 | 2.2141 | 2.2417 | 2.2783 | 2.4289
2022-04-02 01:00 | 2.0196 | 2.2373 | 2.2718 | 2.314 | 2.3633 | 1.2384 | 1.5121 | 1.539 | 1.5757 | 1.2384 | 1.6766 | 1.911 | 1.9352 | 1.9673 | 2.0979
2022-04-02 02:00 | 1.8862 | 2.0844 | 2.114 | 2.1503 | 2.1925 | 1.1241 | 1.3701 | 1.3932 | 1.4247 | 1.1241 | 1.5242 | 1.7349 | 1.7556 | 1.7832 | 1.8999
2022-04-02 03:00 | 1.829 | 2.0109 | 2.0344 | 2.0631 | 2.0965 | 1.1031 | 1.3365 | 1.3548 | 1.3798 | 1.1031 | 1.6004 | 1.811 | 1.8274 | 1.8492 | 1.9633
2022-04-02 04:00 | 1.8672 | 2.04 | 2.0574 | 2.0788 | 2.1036 | 1.105 | 1.3302 | 1.3438 | 1.3623 | 1.105 | 1.467 | 1.6544 | 1.6666 | 1.6828 | 1.7828
2022-04-02 05:00 | 1.8862 | 2.0504 | 2.0627 | 2.0777 | 2.0952 | 1.2003 | 1.4354 | 1.445 | 1.458 | 1.2003 | 1.6576 | 1.859 | 1.8676 | 1.879 | 1.9838
2022-04-02 06:00 | 1.9434 | 2.1079 | 2.1181 | 2.1306 | 2.1452 | 1.2765 | 1.5226 | 1.5306 | 1.5415 | 1.2765 | 1.81 | 2.0256 | 2.0327 | 2.0422 | 2.1531
2022-04-02 07:00 | 2.0958 | 2.275 | 2.2869 | 2.3015 | 2.3185 | 1.4195 | 1.6939 | 1.7032 | 1.7159 | 1.4195 | 2.2291 | 2.4937 | 2.5021 | 2.5132 | 2.649
2022-04-02 08:00 | 2.3054 | 2.5092 | 2.5258 | 2.5461 | 2.5697 | 1.7123 | 2.0464 | 2.0594 | 2.077 | 1.7123 | 2.191 | 2.4578 | 2.4694 | 2.4849 | 2.6238
2022-04-02 09:00 | 2.3244 | 2.543 | 2.5664 | 2.5951 | 2.6284 | 1.7147 | 2.059 | 2.0772 | 2.1021 | 1.7147 | 2.553 | 2.8695 | 2.8859 | 2.9077 | 3.0741
2022-04-02 10:00 | 2.2482 | 2.4754 | 2.5061 | 2.5436 | 2.5874 | 1.6957 | 2.0468 | 2.0707 | 2.1034 | 1.6957 | 2.1529 | 2.435 | 2.4565 | 2.4851 | 2.6376
2022-04-02 11:00 | 2.0871 | 2.3133 | 2.3495 | 2.3939 | 2.4457 | 1.4702 | 1.7883 | 1.8166 | 1.8552 | 1.4702 | 2.0577 | 2.3369 | 2.3623 | 2.3961 | 2.5496
2022-04-02 12:00 | 2.172 | 2.4088 | 2.4473 | 2.4944 | 2.5493 | 1.6004 | 1.9454 | 1.9754 | 2.0164 | 1.6004 | 1.9624 | 2.2341 | 2.2611 | 2.2969 | 2.4476
2022-04-02 13:00 | 2.0767 | 2.3054 | 2.3433 | 2.3898 | 2.4439 | 1.3852 | 1.6904 | 1.7199 | 1.7604 | 1.3852 | 1.7909 | 2.0428 | 2.0694 | 2.1047 | 2.2454
2022-04-02 14:00 | 2.1148 | 2.3413 | 2.3767 | 2.4201 | 2.4706 | 1.5303 | 1.8581 | 1.8857 | 1.9234 | 1.5303 | 2.0386 | 2.3145 | 2.3393 | 2.3723 | 2.5238
2022-04-02 15:00 | 2.1615 | 2.3861 | 2.4187 | 2.4587 | 2.5053 | 1.6195 | 1.9596 | 1.985 | 2.0198 | 1.6195 | 2.2291 | 2.5224 | 2.5453 | 2.5757 | 2.7345
2022-04-02 16:00 | 2.2278 | 2.4537 | 2.4845 | 2.5222 | 2.5662 | 1.6602 | 2.0051 | 2.0291 | 2.0619 | 1.6602 | 2.0386 | 2.3082 | 2.3297 | 2.3584 | 2.5048
2022-04-02 17:00 | 2.3816 | 2.6181 | 2.6484 | 2.6856 | 2.7289 | 1.8709 | 2.2533 | 2.277 | 2.3094 | 1.8709 | 2.4768 | 2.7945 | 2.8158 | 2.844 | 3.014
2022-04-02 18:00 | 2.5149 | 2.7649 | 2.7971 | 2.8364 | 2.8824 | 2.1148 | 2.5441 | 2.5692 | 2.6035 | 2.1148 | 2.9531 | 3.3263 | 3.3489 | 3.3788 | 3.577
2022-04-02 19:00 | 2.6102 | 2.8746 | 2.9105 | 2.9545 | 3.0058 | 2.1529 | 2.5945 | 2.6225 | 2.6608 | 2.1529 | 2.8388 | 3.2045 | 3.2297 | 3.2631 | 3.4592
2022-04-02 20:00 | 2.5911 | 2.8639 | 2.9048 | 2.9549 | 3.0133 | 2.0386 | 2.4665 | 2.4984 | 2.542 | 2.0386 | 3.3533 | 3.7831 | 3.8117 | 3.8498 | 4.0797
2022-04-02 21:00 | 2.5149 | 2.7917 | 2.8375 | 2.8937 | 2.9591 | 2.0025 | 2.4309 | 2.4666 | 2.5155 | 2.0025 | 3.0294 | 3.43 | 3.4621 | 3.5048 | 3.7224
2022-04-02 22:00 | 2.3174 | 2.5811 | 2.6278 | 2.6849 | 2.7516 | 1.7976 | 2.19 | 2.2264 | 2.2761 | 1.7976 | 3.0675 | 3.4735 | 3.5062 | 3.5497 | 3.7703
2022-04-02 23:00 | 2.1339 | 2.378 | 2.4216 | 2.475 | 2.5373 | 1.512 | 1.8483 | 1.8824 | 1.9289 | 1.512 | 3.1246 | 3.5328 | 3.5634 | 3.604 | 3.8244
2022-04-03 | 2.0196 | 2.2467 | 2.286 | 2.3342 | 2.3903 | 1.3797 | 1.6859 | 1.7166 | 1.7584 | 1.3797 | 2.1148 | 2.4047 | 2.4322 | 2.4688 | 2.6289
2022-04-03 01:00 | 1.9243 | 2.1349 | 2.1694 | 2.2117 | 2.2609 | 1.2083 | 1.4766 | 1.5035 | 1.5402 | 1.2083 | 2.0005 | 2.2709 | 2.2951 | 2.3272 | 2.4756
2022-04-03 02:00 | 1.81 | 2.0025 | 2.0321 | 2.0684 | 2.1107 | 1.1241 | 1.3701 | 1.3932 | 1.4247 | 1.1241 | 1.5814 | 1.7984 | 1.8191 | 1.8467 | 1.9666
2022-04-03 02:00 | 1.7338 | 1.9086 | 1.932 | 1.9607 | 1.9942 | 1.086 | 1.3163 | 1.3346 | 1.3595 | 1.086 | 1.5623 | 1.7686 | 1.7851 | 1.8069 | 1.9189
2022-04-03 03:00 | 1.7719 | 1.9377 | 1.9551 | 1.9764 | 2.0013 | 1.0669 | 1.2852 | 1.2988 | 1.3173 | 1.0669 | 1.4861 | 1.6756 | 1.6878 | 1.704 | 1.8051
2022-04-03 04:00 | 1.7719 | 1.9276 | 1.9399 | 1.9549 | 1.9724 | 1.1466 | 1.372 | 1.3815 | 1.3946 | 1.1466 | 1.4289 | 1.6049 | 1.6135 | 1.6249 | 1.7171
2022-04-03 05:00 | 1.81 | 1.9646 | 1.9748 | 1.9873 | 2.0019 | 1.1899 | 1.4203 | 1.4282 | 1.4391 | 1.1899 | 1.5814 | 1.7715 | 1.7787 | 1.7882 | 1.8865
2022-04-03 06:00 | 1.81 | 1.9679 | 1.9799 | 1.9945 | 2.0115 | 1.3146 | 1.57 | 1.5793 | 1.592 | 1.3146 | 1.7338 | 1.9432 | 1.9516 | 1.9627 | 2.0713
2022-04-03 07:00 | 1.8688 | 2.0401 | 2.0567 | 2.077 | 2.1007 | 1.4289 | 1.7117 | 1.7246 | 1.7423 | 1.4289 | 1.829 | 2.0555 | 2.0671 | 2.0826 | 2.2016
2022-04-03 08:00 | 1.9243 | 2.1132 | 2.1366 | 2.1652 | 2.1986 | 1.448 | 1.7439 | 1.7621 | 1.787 | 1.448 | 2.0958 | 2.3614 | 2.3778 | 2.3996 | 2.5408
2022-04-03 09:00 | 1.9053 | 2.1069 | 2.1376 | 2.1752 | 2.2189 | 1.4099 | 1.7092 | 1.7331 | 1.7658 | 1.4099 | 2.3244 | 2.6256 | 2.647 | 2.6756 | 2.8375
2022-04-03 10:00 | 1.7909 | 1.9951 | 2.0313 | 2.0757 | 2.1275 | 1.1622 | 1.4245 | 1.4528 | 1.4915 | 1.1622 | 1.0479 | 1.2148 | 1.2402 | 1.2739 | 1.3719
2022-04-03 11:00 | 1.8481 | 2.0608 | 2.0993 | 2.1464 | 2.2013 | 1.3146 | 1.6078 | 1.6378 | 1.6788 | 1.3146 | 1.1711 | 1.3547 | 1.3817 | 1.4175 | 1.5247
2022-04-03 12:00 | 1.6766 | 1.8755 | 1.9135 | 1.9599 | 2.0141 | 1.1241 | 1.3819 | 1.4115 | 1.4519 | 1.1241 | 1.3908 | 1.5982 | 1.6248 | 1.6601 | 1.7788
2022-04-03 13:00 | 1.7338 | 1.932 | 1.9674 | 2.0107 | 2.0612 | 1.1622 | 1.4233 | 1.4509 | 1.4886 | 1.1622 | 1.2194 | 1.4041 | 1.4289 | 1.4619 | 1.5683
2022-04-03 14:00 | 1.8862 | 2.0903 | 2.123 | 2.1629 | 2.2095 | 1.1666 | 1.4246 | 1.45 | 1.4848 | 1.1666 | 1.2765 | 1.4638 | 1.4867 | 1.5171 | 1.6236
2022-04-03 15:00 | 1.8862 | 2.0867 | 2.1175 | 2.1552 | 2.1992 | 1.3527 | 1.6419 | 1.6659 | 1.6987 | 1.3527 | 1.4099 | 1.6095 | 1.631 | 1.6597 | 1.7715
2022-04-03 16:00 | 2.2863 | 2.5157 | 2.5461 | 2.5832 | 2.6266 | 1.6613 | 2.0058 | 2.0295 | 2.0618 | 1.6613 | 2.2101 | 2.4981 | 2.5194 | 2.5476 | 2.7029
2022-04-03 17:00 | 2.5942 | 2.85 | 2.8822 | 2.9216 | 2.9675 | 2.0499 | 2.4674 | 2.4925 | 2.5267 | 2.0499 | 2.8198 | 3.1781 | 3.2007 | 3.2306 | 3.4214
2022-04-03 18:00 | 2.8007 | 3.0793 | 3.1152 | 3.1592 | 3.2105 | 2.172 | 2.617 | 2.645 | 2.6833 | 2.172 | 3.3151 | 3.7338 | 3.759 | 3.7924 | 4.0147
2022-04-03 19:00 | 2.7436 | 3.0276 | 3.0685 | 3.1186 | 3.177 | 2.1148 | 2.5566 | 2.5885 | 2.632 | 2.1148 | 2.9722 | 3.3596 | 3.3883 | 3.4264 | 3.6353
2022-04-03 20:00 | 2.553 | 2.8326 | 2.8785 | 2.9346 | 3 | 2.0005 | 2.4285 | 2.4643 | 2.5131 | 2.0005 | 2.9531 | 3.3453 | 3.3774 | 3.4201 | 3.6335
2022-04-03 21:00 | 2.4197 | 2.691 | 2.7376 | 2.7948 | 2.8614 | 1.9053 | 2.3172 | 2.3536 | 2.4033 | 1.9053 | 2.4959 | 2.8383 | 2.871 | 2.9145 | 3.1037
2022-04-03 22:00 | 2.1668 | 2.4133 | 2.457 | 2.5104 | 2.5727 | 1.5814 | 1.9302 | 1.9643 | 2.0107 | 1.5814 | 2.191 | 2.4953 | 2.5259 | 2.5666 | 2.7356
2022-04-03 23:00 | 1.9815 | 2.2058 | 2.2451 | 2.2932 | 2.3494 | 1.3908 | 1.699 | 1.7297 | 1.7716 | 1.3908 | 1.829 | 2.0871 | 2.1146 | 2.1513 | 2.2956
2022-04-04 | 1.8672 | 2.0735 | 2.108 | 2.1503 | 2.1995 | 1.2194 | 1.4896 | 1.5165 | 1.5532 | 1.2194 | 1.7909 | 2.0381 | 2.0622 | 2.0944 | 2.2312
2022-04-04 01:00 | 1.7719 | 1.9616 | 1.9912 | 2.0275 | 2.0697 | 1.132 | 1.3793 | 1.4025 | 1.434 | 1.132 | 1.4099 | 1.6078 | 1.6286 | 1.6561 | 1.7666
2022-04-04 02:00 | 1.7147 | 1.8881 | 1.9116 | 1.9403 | 1.9737 | 1.0489 | 1.2725 | 1.2908 | 1.3157 | 1.0489 | 1.3337 | 1.5146 | 1.531 | 1.5528 | 1.6523
2022-04-04 03:00 | 1.6815 | 1.8406 | 1.858 | 1.8793 | 1.9042 | 1.0331 | 1.2452 | 1.2588 | 1.2773 | 1.0331 | 1.3337 | 1.5062 | 1.5184 | 1.5346 | 1.6273
2022-04-04 04:00 | 1.8062 | 1.9645 | 1.9768 | 1.9918 | 2.0093 | 1.1356 | 1.359 | 1.3686 | 1.3816 | 1.1356 | 1.6195 | 1.8166 | 1.8252 | 1.8366 | 1.9393
2022-04-04 05:00 | 1.9113 | 2.0734 | 2.0836 | 2.0962 | 2.1108 | 1.265 | 1.509 | 1.517 | 1.5279 | 1.265 | 1.829 | 2.0467 | 2.0539 | 2.0634 | 2.1754
2022-04-04 06:00 | 2.1529 | 2.3364 | 2.3483 | 2.3629 | 2.3799 | 1.5052 | 1.7951 | 1.8044 | 1.8171 | 1.5052 | 2.0577 | 2.3032 | 2.3115 | 2.3226 | 2.449
2022-04-04 07:00 | 2.2673 | 2.4683 | 2.4848 | 2.5051 | 2.5288 | 1.6004 | 1.9142 | 1.9272 | 1.9448 | 1.6004 | 2.0005 | 2.2461 | 2.2577 | 2.2731 | 2.4016
2022-04-04 08:00 | 2.3054 | 2.5225 | 2.5459 | 2.5746 | 2.608 | 1.5052 | 1.8114 | 1.8296 | 1.8546 | 1.5052 | 1.6004 | 1.8109 | 1.8273 | 1.8491 | 1.9631
2022-04-04 09:00 | 2.259 | 2.4869 | 2.5176 | 2.5552 | 2.5989 | 1.3718 | 1.6642 | 1.6881 | 1.7208 | 1.3718 | 1.2823 | 1.4675 | 1.489 | 1.5175 | 1.6222
2022-04-04 10:00 | 2.2863 | 2.5273 | 2.5635 | 2.6079 | 2.6597 | 1.3337 | 1.6271 | 1.6554 | 1.694 | 1.3337 | 1.1813 | 1.363 | 1.3884 | 1.4221 | 1.5275
2022-04-04 11:00 | 2.0577 | 2.286 | 2.3245 | 2.3716 | 2.4265 | 1.0288 | 1.2701 | 1.3002 | 1.3411 | 1.0288 | 1.6957 | 1.9377 | 1.9647 | 2.0005 | 2.1366
2022-04-04 12:00 | 1.726 | 1.9286 | 1.9666 | 2.013 | 2.0672 | 1.086 | 1.3369 | 1.3665 | 1.4069 | 1.086 | 1.8481 | 2.1063 | 2.1329 | 2.1682 | 2.3121
2022-04-04 13:00 | 1.8862 | 2.0957 | 2.1311 | 2.1744 | 2.225 | 1.3146 | 1.6034 | 1.631 | 1.6687 | 1.3146 | 1.9053 | 2.1663 | 2.1911 | 2.2241 | 2.3682
2022-04-04 14:00 | 2.191 | 2.4178 | 2.4505 | 2.4904 | 2.537 | 1.105 | 1.3519 | 1.3773 | 1.4121 | 1.105 | 1.4861 | 1.6967 | 1.7196 | 1.7499 | 1.868
2022-04-04 15:00 | 2.3054 | 2.537 | 2.5678 | 2.6055 | 2.6495 | 1.2956 | 1.5743 | 1.5984 | 1.6312 | 1.2956 | 1.3146 | 1.5036 | 1.5252 | 1.5539 | 1.6604
2022-04-04 16:00 | 2.2482 | 2.4748 | 2.5051 | 2.5423 | 2.5856 | 1.5242 | 1.8438 | 1.8675 | 1.8998 | 1.5242 | 1.7719 | 2.0111 | 2.0324 | 2.0607 | 2.1919
2022-04-04 17:00 | 2.4959 | 2.7444 | 2.7766 | 2.816 | 2.8619 | 1.8862 | 2.274 | 2.2991 | 2.3334 | 1.8862 | 2.5721 | 2.9029 | 2.9254 | 2.9554 | 3.1326
2022-04-04 18:00 | 2.7626 | 3.0383 | 3.0743 | 3.1183 | 3.1695 | 2.0958 | 2.527 | 2.555 | 2.5933 | 2.0958 | 2.8198 | 3.1833 | 3.2085 | 3.242 | 3.437
2022-04-04 19:00 | 2.6293 | 2.9048 | 2.9457 | 2.9958 | 3.0542 | 1.9815 | 2.399 | 2.4309 | 2.4745 | 1.9815 | 2.6674 | 3.0209 | 3.0495 | 3.0876 | 3.2798
2022-04-04 20:00 | 2.4006 | 2.6689 | 2.7147 | 2.7708 | 2.8363 | 1.9624 | 2.3835 | 2.4193 | 2.4681 | 1.9624 | 2.7817 | 3.1547 | 3.1869 | 3.2296 | 3.4335
2022-04-04 21:00 | 2.3054 | 2.5681 | 2.6148 | 2.672 | 2.7386 | 1.8481 | 2.2496 | 2.2861 | 2.3358 | 1.8481 | 2.7245 | 3.0924 | 3.1251 | 3.1686 | 3.3703
2022-04-04 22:00 | 2.2291 | 2.4803 | 2.524 | 2.5774 | 2.6397 | 1.6195 | 1.9752 | 2.0093 | 2.0558 | 1.6195 | 2.3244 | 2.6435 | 2.6741 | 2.7148 | 2.8911
2022-04-04 23:00 | 1.9362 | 2.1572 | 2.1965 | 2.2447 | 2.3008 | 1.4099 | 1.7215 | 1.7522 | 1.7941 | 1.4099 | 2.0005 | 2.2776 | 2.3052 | 2.3418 | 2.4956
2022-04-05 | 1.7719 | 1.9712 | 2.0057 | 2.0479 | 2.0972 | 1.2261 | 1.4976 | 1.5245 | 1.5612 | 1.2261 | 1.8481 | 2.1016 | 2.1257 | 2.1579 | 2.2979
2022-04-05 01:00 | 1.7719 | 1.9616 | 1.9912 | 2.0275 | 2.0697 | 1.1333 | 1.381 | 1.4041 | 1.4356 | 1.1333 | 1.5242 | 1.7349 | 1.7556 | 1.7832 | 1.8999
2022-04-05 02:00 | 1.7909 | 1.97 | 1.9934 | 2.0221 | 2.0556 | 1.0669 | 1.2938 | 1.3121 | 1.337 | 1.0669 | 1.3337 | 1.5146 | 1.531 | 1.5528 | 1.6523
2022-04-05 03:00 | 1.7528 | 1.9172 | 1.9346 | 1.9559 | 1.9808 | 1.105 | 1.3302 | 1.3438 | 1.3623 | 1.105 | 1.3337 | 1.5062 | 1.5184 | 1.5346 | 1.6273
2022-04-05 04:00 | 1.8481 | 2.0095 | 2.0218 | 2.0368 | 2.0543 | 1.1432 | 1.3679 | 1.3775 | 1.3905 | 1.1432 | 1.5814 | 1.7743 | 1.7829 | 1.7943 | 1.8949
2022-04-05 05:00 | 2.0577 | 2.2307 | 2.2409 | 2.2534 | 2.268 | 1.2956 | 1.5451 | 1.5531 | 1.564 | 1.2956 | 1.6576 | 1.8562 | 1.8633 | 1.8729 | 1.9754
2022-04-05 06:00 | 2.381 | 2.5814 | 2.5933 | 2.6079 | 2.6249 | 1.6195 | 1.9301 | 1.9394 | 1.9522 | 1.6195 | 2.2482 | 2.5149 | 2.5232 | 2.5344 | 2.6712
2022-04-05 07:00 | 2.5149 | 2.7344 | 2.7509 | 2.7712 | 2.7949 | 1.7147 | 2.0493 | 2.0622 | 2.0799 | 1.7147 | 2.191 | 2.4578 | 2.4694 | 2.4849 | 2.6238
2022-04-05 08:00 | 2.1529 | 2.3588 | 2.3822 | 2.4108 | 2.4442 | 1.3702 | 1.652 | 1.6702 | 1.6951 | 1.3702 | 1.81 | 2.0438 | 2.0602 | 2.082 | 2.2075
2022-04-05 09:00 | 1.81 | 2.0046 | 2.0353 | 2.0728 | 2.1166 | 0.89547 | 1.1015 | 1.1254 | 1.1581 | 0.89547 | 1.1241 | 1.2917 | 1.3132 | 1.3418 | 1.4377
2022-04-05 10:00 | 1.6195 | 1.8109 | 1.8471 | 1.8915 | 1.9433 | 0.61126 | 0.77368 | 0.80196 | 0.84059 | 0.61126 | 1.9243 | 2.1887 | 2.2141 | 2.2479 | 2.394
2022-04-05 11:00 | 1.4289 | 1.6105 | 1.649 | 1.6961 | 1.751 | 0.55252 | 0.70745 | 0.73747 | 0.77845 | 0.55252 | 2.0958 | 2.3823 | 2.4093 | 2.4451 | 2.6032
2022-04-05 12:00 | 1.3337 | 1.5071 | 1.5451 | 1.5915 | 1.6457 | 0.55252 | 0.70668 | 0.73628 | 0.77669 | 0.55252 | 1.7719 | 2.0216 | 2.0482 | 2.0836 | 2.2232
2022-04-05 13:00 | 1.4289 | 1.6045 | 1.6399 | 1.6832 | 1.7337 | 0.57158 | 0.72557 | 0.75318 | 0.79088 | 0.57158 | 1.829 | 2.0816 | 2.1064 | 2.1394 | 2.2793
2022-04-05 14:00 | 1.6732 | 1.8615 | 1.8941 | 1.9341 | 1.9807 | 0.74305 | 0.92421 | 0.94967 | 0.98443 | 0.74305 | 1.5814 | 1.8026 | 1.8254 | 1.8558 | 1.9791
2022-04-05 15:00 | 2.0767 | 2.2914 | 2.3222 | 2.3599 | 2.4039 | 0.99247 | 1.2163 | 1.2403 | 1.2731 | 0.99247 | 1.0479 | 1.2072 | 1.2288 | 1.2575 | 1.3494
2022-04-05 16:00 | 2.3435 | 2.5771 | 2.6075 | 2.6447 | 2.688 | 1.4869 | 1.7997 | 1.8234 | 1.8558 | 1.4869 | 2.4768 | 2.7945 | 2.8158 | 2.844 | 3.014
2022-04-05 17:00 | 2.4387 | 2.683 | 2.7152 | 2.7546 | 2.8005 | 1.8359 | 2.2146 | 2.2397 | 2.274 | 1.8359 | 2.6102 | 2.9452 | 2.9678 | 2.9977 | 3.177
2022-04-05 18:00 | 2.6674 | 2.936 | 2.9719 | 3.0159 | 3.0672 | 2.0767 | 2.5045 | 2.5325 | 2.5707 | 2.0767 | 2.7055 | 3.0563 | 3.0815 | 3.1149 | 3.3037
2022-04-05 19:00 | 2.553 | 2.8229 | 2.8639 | 2.9139 | 2.9723 | 1.9815 | 2.399 | 2.4309 | 2.4745 | 1.9815 | 2.534 | 2.8727 | 2.9013 | 2.9394 | 3.1243
2022-04-05 20:00 | 2.4197 | 2.6893 | 2.7352 | 2.7913 | 2.8568 | 1.7909 | 2.1809 | 2.2167 | 2.2655 | 1.7909 | 2.8007 | 3.1759 | 3.208 | 3.2507 | 3.4558
2022-04-05 21:00 | 2.2863 | 2.5477 | 2.5944 | 2.6515 | 2.7181 | 1.7147 | 2.0921 | 2.1285 | 2.1782 | 1.7147 | 2.3054 | 2.6266 | 2.6593 | 2.7028 | 2.8815
2022-04-05 22:00 | 2.0577 | 2.2961 | 2.3397 | 2.3932 | 2.4555 | 1.4894 | 1.8216 | 1.8557 | 1.9022 | 1.4894 | 2.191 | 2.4953 | 2.5259 | 2.5666 | 2.7356
2022-04-05 23:00 | 1.8862 | 2.1034 | 2.1428 | 2.1909 | 2.247 | 1.2765 | 1.5639 | 1.5946 | 1.6365 | 1.2765 | 1.9053 | 2.1718 | 2.1993 | 2.236 | 2.3845
2022-04-06 | 1.7528 | 1.9507 | 1.9852 | 2.0274 | 2.0767 | 1.1131 | 1.364 | 1.391 | 1.4277 | 1.1131 | 1.6766 | 1.911 | 1.9352 | 1.9673 | 2.0979
2022-04-06 01:00 | 1.6766 | 1.8592 | 1.8889 | 1.9251 | 1.9674 | 1.0479 | 1.28 | 1.3031 | 1.3347 | 1.0479 | 1.2956 | 1.4808 | 1.5015 | 1.5291 | 1.6333
2022-04-06 02:00 | 1.6195 | 1.7858 | 1.8092 | 1.8379 | 1.8714 | 1.0098 | 1.2263 | 1.2445 | 1.2695 | 1.0098 | 1.6576 | 1.8745 | 1.8909 | 1.9128 | 2.03
2022-04-06 03:00 | 1.6766 | 1.8353 | 1.8528 | 1.8741 | 1.8989 | 0.99073 | 1.1952 | 1.2087 | 1.2273 | 0.99073 | 1.3908 | 1.5697 | 1.5819 | 1.5981 | 1.694
2022-04-06 04:00 | 1.642 | 1.7881 | 1.8004 | 1.8154 | 1.8329 | 1.0288 | 1.2329 | 1.2424 | 1.2555 | 1.0288 | 1.3908 | 1.5626 | 1.5712 | 1.5826 | 1.6727
2022-04-06 05:00 | 1.81 | 1.9646 | 1.9748 | 1.9873 | 2.0019 | 1.2003 | 1.4325 | 1.4405 | 1.4514 | 1.2003 | 1.5433 | 1.7291 | 1.7363 | 1.7458 | 1.8421
2022-04-06 06:00 | 2.0016 | 2.1737 | 2.1857 | 2.2003 | 2.2173 | 1.3963 | 1.6665 | 1.6758 | 1.6885 | 1.3963 | 1.7147 | 1.9221 | 1.9304 | 1.9415 | 2.0491
2022-04-06 07:00 | 2.2269 | 2.4249 | 2.4415 | 2.4617 | 2.4854 | 1.5095 | 1.8068 | 1.8198 | 1.8374 | 1.5095 | 2.3054 | 2.5848 | 2.5965 | 2.6119 | 2.7571
2022-04-06 08:00 | 2.3244 | 2.543 | 2.5664 | 2.5951 | 2.6284 | 1.6195 | 1.9464 | 1.9647 | 1.9896 | 1.6195 | 1.9434 | 2.192 | 2.2084 | 2.2302 | 2.3631
2022-04-06 09:00 | 2.3483 | 2.5829 | 2.6136 | 2.6512 | 2.6949 | 1.448 | 1.7542 | 1.7781 | 1.8108 | 1.448 | 1.6195 | 1.8422 | 1.8637 | 1.8922 | 2.0154
2022-04-06 10:00 | 2.4197 | 2.6705 | 2.7068 | 2.7512 | 2.803 | 1.3527 | 1.6496 | 1.6779 | 1.7165 | 1.3527 | 1.4099 | 1.617 | 1.6424 | 1.6762 | 1.7941
2022-04-06 11:00 | 2.2863 | 2.5316 | 2.5701 | 2.6172 | 2.6721 | 1.4289 | 1.7428 | 1.7728 | 1.8138 | 1.4289 | 1.1813 | 1.3661 | 1.393 | 1.4288 | 1.5366
2022-04-06 12:00 | 2.4006 | 2.6534 | 2.6913 | 2.7378 | 2.7919 | 1.4099 | 1.7195 | 1.7491 | 1.7895 | 1.4099 | 1.2575 | 1.45 | 1.4766 | 1.5119 | 1.6233
2022-04-06 13:00 | 2.4197 | 2.6689 | 2.7043 | 2.7476 | 2.7981 | 1.5052 | 1.8285 | 1.8561 | 1.8938 | 1.5052 | 1.81 | 2.0605 | 2.0853 | 2.1182 | 2.2571
2022-04-06 14:00 | 2.2349 | 2.465 | 2.4976 | 2.5375 | 2.5841 | 1.1413 | 1.3947 | 1.4202 | 1.4549 | 1.1413 | 1.0669 | 1.2309 | 1.2538 | 1.2842 | 1.3791
2022-04-06 15:00 | 2.2853 | 2.5155 | 2.5463 | 2.584 | 2.6279 | 1.3127 | 1.5945 | 1.6186 | 1.6514 | 1.3127 | 1.2194 | 1.3977 | 1.4193 | 1.448 | 1.5493
2022-04-06 16:00 | 2.3435 | 2.5771 | 2.6075 | 2.6447 | 2.688 | 1.5242 | 1.8438 | 1.8675 | 1.8998 | 1.5242 | 1.7909 | 2.0323 | 2.0536 | 2.0818 | 2.2141
2022-04-06 17:00 | 2.625 | 2.8831 | 2.9153 | 2.9547 | 3.0006 | 1.8862 | 2.274 | 2.2991 | 2.3334 | 1.8862 | 2.8579 | 3.2205 | 3.243 | 3.273 | 3.4659
2022-04-06 18:00 | 2.7055 | 2.9769 | 3.0129 | 3.0569 | 3.1081 | 2.0196 | 2.4369 | 2.465 | 2.5032 | 2.0196 | 2.8388 | 3.2045 | 3.2297 | 3.2631 | 3.4592
2022-04-06 19:00 | 2.6483 | 2.9253 | 2.9662 | 3.0163 | 3.0747 | 2.0005 | 2.4215 | 2.4534 | 2.497 | 2.0005 | 2.915 | 3.2961 | 3.3248 | 3.3629 | 3.5687
2022-04-06 20:00 | 2.4578 | 2.7303 | 2.7761 | 2.8322 | 2.8977 | 1.89 | 2.2979 | 2.3337 | 2.3825 | 1.89 | 2.7245 | 3.0912 | 3.1234 | 3.1661 | 3.3669
2022-04-06 21:00 | 2.4197 | 2.691 | 2.7376 | 2.7948 | 2.8614 | 1.7301 | 2.1102 | 2.1466 | 2.1964 | 1.7301 | 2.4006 | 2.7325 | 2.7652 | 2.8086 | 2.9926
2022-04-06 22:00 | 2.1148 | 2.3575 | 2.4011 | 2.4546 | 2.5169 | 1.5242 | 1.8627 | 1.8967 | 1.9432 | 1.5242 | 2.0005 | 2.2836 | 2.3142 | 2.3548 | 2.5134
2022-04-06 23:00 | 2.0005 | 2.2262 | 2.2656 | 2.3137 | 2.3699 | 1.3646 | 1.6681 | 1.6987 | 1.7406 | 1.3646 | 1.7528 | 2.0024 | 2.03 | 2.0666 | 2.2067
2022-04-07 | 1.7804 | 1.9803 | 2.0148 | 2.057 | 2.1063 | 1.1903 | 1.4552 | 1.4821 | 1.5189 | 1.1903 | 1.6195 | 1.8475 | 1.8717 | 1.9038 | 2.0312
2022-04-07 01:00 | 1.7338 | 1.9207 | 1.9503 | 1.9865 | 2.0288 | 1.0991 | 1.3405 | 1.3636 | 1.3951 | 1.0991 | 1.6385 | 1.8619 | 1.8826 | 1.9102 | 2.0333
2022-04-07 02:00 | 1.6576 | 1.8267 | 1.8501 | 1.8788 | 1.9123 | 1.0479 | 1.2713 | 1.2896 | 1.3145 | 1.0479 | 1.5433 | 1.7475 | 1.7639 | 1.7857 | 1.8967
2022-04-07 03:00 | 1.6385 | 1.7944 | 1.8118 | 1.8331 | 1.858 | 1.0479 | 1.2627 | 1.2763 | 1.2948 | 1.0479 | 1.3146 | 1.485 | 1.4972 | 1.5134 | 1.6051
2022-04-07 04:00 | 1.7528 | 1.9071 | 1.9194 | 1.9344 | 1.9519 | 1.0669 | 1.2779 | 1.2874 | 1.3005 | 1.0669 | 1.4099 | 1.5838 | 1.5923 | 1.6038 | 1.6949
2022-04-07 05:00 | 1.8516 | 2.0093 | 2.0195 | 2.0321 | 2.0467 | 1.193 | 1.4239 | 1.4319 | 1.4428 | 1.193 | 1.6766 | 1.8773 | 1.8845 | 1.894 | 1.9976
2022-04-07 06:00 | 2.1148 | 2.2954 | 2.3074 | 2.322 | 2.339 | 1.5242 | 1.8176 | 1.8269 | 1.8396 | 1.5242 | 2.3054 | 2.5784 | 2.5868 | 2.5979 | 2.7379
2022-04-07 07:00 | 2.4387 | 2.6525 | 2.6691 | 2.6894 | 2.713 | 1.7909 | 2.1393 | 2.1522 | 2.1699 | 1.7909 | 2.2482 | 2.5213 | 2.5329 | 2.5484 | 2.6904
2022-04-07 08:00 | 2.3625 | 2.584 | 2.6074 | 2.636 | 2.6694 | 1.5894 | 1.911 | 1.9292 | 1.9541 | 1.5894 | 2.3435 | 2.6366 | 2.653 | 2.6748 | 2.8297
2022-04-07 09:00 | 2.4387 | 2.6801 | 2.7108 | 2.7483 | 2.7921 | 1.5433 | 1.8668 | 1.8907 | 1.9233 | 1.5433 | 1.6576 | 1.8845 | 1.906 | 1.9346 | 2.0598
2022-04-07 10:00 | 2.5911 | 2.8548 | 2.891 | 2.9354 | 2.9872 | 1.6195 | 1.9647 | 1.993 | 2.0316 | 1.6195 | 1.9243 | 2.1887 | 2.2141 | 2.2479 | 2.394
2022-04-07 11:00 | 2.5911 | 2.8591 | 2.8976 | 2.9447 | 2.9996 | 1.597 | 1.9413 | 1.9713 | 2.0123 | 1.597 | 1.7528 | 2.0012 | 2.0282 | 2.064 | 2.2032
2022-04-07 12:00 | 2.5149 | 2.7762 | 2.8141 | 2.8606 | 2.9147 | 1.6195 | 1.9671 | 1.9967 | 2.0371 | 1.6195 | 1.6766 | 1.9158 | 1.9424 | 1.9777 | 2.1121
2022-04-07 13:00 | 2.4578 | 2.7098 | 2.7452 | 2.7885 | 2.839 | 1.5052 | 1.8285 | 1.8561 | 1.8938 | 1.5052 | 1.7338 | 1.9758 | 2.0006 | 2.0335 | 2.1682
2022-04-07 14:00 | 2.3625 | 2.602 | 2.6347 | 2.6746 | 2.7212 | 1.4845 | 1.8002 | 1.8256 | 1.8604 | 1.4845 | 1.5623 | 1.7814 | 1.8043 | 1.8346 | 1.9569
2022-04-07 15:00 | 2.4578 | 2.7008 | 2.7316 | 2.7693 | 2.8133 | 1.5433 | 1.8669 | 1.891 | 1.9238 | 1.5433 | 1.9815 | 2.2446 | 2.2662 | 2.2949 | 2.4381
2022-04-07 16:00 | 2.6483 | 2.9046 | 2.935 | 2.9722 | 3.0155 | 1.8677 | 2.2496 | 2.2733 | 2.3056 | 1.8677 | 3.0865 | 3.472 | 3.4933 | 3.5216 | 3.725
2022-04-07 17:00 | 2.8579 | 3.1333 | 3.1655 | 3.2049 | 3.2508 | 2.3054 | 2.7692 | 2.7943 | 2.8286 | 2.3054 | 4.0391 | 4.5331 | 4.5557 | 4.5856 | 4.8435
2022-04-07 18:00 | 2.8769 | 3.1612 | 3.1971 | 3.2411 | 3.2924 | 2.3244 | 2.7971 | 2.8251 | 2.8633 | 2.3244 | 3.4866 | 3.9244 | 3.9495 | 3.983 | 4.2147
2022-04-07 19:00 | 2.7817 | 3.0686 | 3.1095 | 3.1596 | 3.218 | 2.3054 | 2.7816 | 2.8135 | 2.8571 | 2.3054 | 3.6771 | 4.143 | 4.1717 | 4.2098 | 4.4574
2022-04-07 20:00 | 2.6864 | 2.9759 | 3.0217 | 3.0779 | 3.1433 | 2.1529 | 2.6086 | 2.6444 | 2.6932 | 2.1529 | 3.1056 | 3.5147 | 3.5468 | 3.5895 | 3.8113
2022-04-07 21:00 | 2.6142 | 2.8999 | 2.9466 | 3.0038 | 3.0704 | 2.0005 | 2.4297 | 2.4661 | 2.5159 | 2.0005 | 2.7055 | 3.0712 | 3.1039 | 3.1474 | 3.3481
2022-04-07 22:00 | 2.3074 | 2.5644 | 2.6081 | 2.6615 | 2.7238 | 1.8481 | 2.2453 | 2.2794 | 2.3259 | 1.8481 | 2.5721 | 2.9188 | 2.9494 | 2.99 | 3.18
2022-04-07 23:00 | 2.0767 | 2.3081 | 2.3474 | 2.3956 | 2.4517 | 1.5145 | 1.845 | 1.8757 | 1.9176 | 1.5145 | 2.0577 | 2.3412 | 2.3687 | 2.4053 | 2.5622
2022-04-08 | 1.8689 | 2.0753 | 2.1098 | 2.1521 | 2.2013 | 1.282 | 1.5635 | 1.5905 | 1.6272 | 1.282 | 1.7528 | 1.9957 | 2.0199 | 2.052 | 2.1868
2022-04-08 01:00 | 1.7719 | 1.9616 | 1.9912 | 2.0275 | 2.0697 | 1.1813 | 1.4376 | 1.4607 | 1.4922 | 1.1813 | 1.5052 | 1.7137 | 1.7344 | 1.762 | 1.8777
2022-04-08 02:00 | 1.6877 | 1.859 | 1.8825 | 1.9112 | 1.9446 | 1.086 | 1.3163 | 1.3346 | 1.3595 | 1.086 | 1.5242 | 1.7263 | 1.7427 | 1.7646 | 1.8744
2022-04-08 03:00 | 1.7338 | 1.8968 | 1.9142 | 1.9355 | 1.9603 | 1.0669 | 1.2852 | 1.2988 | 1.3173 | 1.0669 | 1.5242 | 1.7179 | 1.7301 | 1.7463 | 1.8495
2022-04-08 04:00 | 1.7528 | 1.9071 | 1.9194 | 1.9344 | 1.9519 | 1.1241 | 1.3454 | 1.355 | 1.368 | 1.1241 | 1.5433 | 1.732 | 1.7405 | 1.752 | 1.8504
2022-04-08 05:00 | 1.9434 | 2.1079 | 2.1181 | 2.1306 | 2.1452 | 1.2575 | 1.5001 | 1.508 | 1.5189 | 1.2575 | 1.81 | 2.0256 | 2.0327 | 2.0422 | 2.1531
2022-04-08 06:00 | 2.1255 | 2.3069 | 2.3188 | 2.3334 | 2.3504 | 1.6576 | 1.9752 | 1.9845 | 1.9972 | 1.6576 | 2.2863 | 2.5572 | 2.5656 | 2.5767 | 2.7157
2022-04-08 07:00 | 2.534 | 2.7548 | 2.7714 | 2.7917 | 2.8154 | 1.8672 | 2.2293 | 2.2423 | 2.2599 | 1.8672 | 2.3816 | 2.6695 | 2.6811 | 2.6966 | 2.846
2022-04-08 08:00 | 2.5911 | 2.8296 | 2.853 | 2.8816 | 2.915 | 1.8862 | 2.2615 | 2.2798 | 2.3047 | 1.8862 | 2.7245 | 3.0601 | 3.0765 | 3.0983 | 3.2741
2022-04-08 09:00 | 2.5911 | 2.8438 | 2.8745 | 2.912 | 2.9558 | 1.7338 | 2.0918 | 2.1158 | 2.1484 | 1.7338 | 1.8862 | 2.1386 | 2.1601 | 2.1886 | 2.3265
2022-04-08 10:00 | 2.4768 | 2.732 | 2.7682 | 2.8126 | 2.8644 | 1.6195 | 1.9647 | 1.993 | 2.0316 | 1.6195 | 1.5814 | 1.8076 | 1.833 | 1.8668 | 1.9941
2022-04-08 11:00 | 2.4578 | 2.7158 | 2.7543 | 2.8014 | 2.8563 | 1.5242 | 1.8553 | 1.8854 | 1.9263 | 1.5242 | 1.5623 | 1.7895 | 1.8165 | 1.8523 | 1.981
2022-04-08 12:00 | 2.5721 | 2.8376 | 2.8755 | 2.922 | 2.9761 | 1.6385 | 1.9896 | 2.0192 | 2.0596 | 1.6385 | 1.6766 | 1.9158 | 1.9424 | 1.9777 | 2.1121
2022-04-08 13:00 | 2.4197 | 2.6689 | 2.7043 | 2.7476 | 2.7981 | 1.6385 | 1.986 | 2.0136 | 2.0513 | 1.6385 | 1.8672 | 2.124 | 2.1488 | 2.1817 | 2.3238
2022-04-08 14:00 | 2.6864 | 2.95 | 2.9826 | 3.0226 | 3.0692 | 1.5814 | 1.9146 | 1.94 | 1.9748 | 1.5814 | 1.8481 | 2.099 | 2.1218 | 2.1522 | 2.2901
2022-04-08 15:00 | 2.4768 | 2.7213 | 2.7521 | 2.7898 | 2.8337 | 1.6385 | 1.9795 | 2.0035 | 2.0363 | 1.6385 | 2.0958 | 2.3717 | 2.3933 | 2.4219 | 2.5714
2022-04-08 16:00 | 2.5721 | 2.8227 | 2.8531 | 2.8903 | 2.9336 | 1.8134 | 2.1855 | 2.2092 | 2.2415 | 1.8134 | 2.7055 | 3.0486 | 3.0698 | 3.0981 | 3.2806
2022-04-08 17:00 | 2.6864 | 2.9491 | 2.9813 | 3.0207 | 3.0666 | 2.1339 | 2.5666 | 2.5917 | 2.626 | 2.1339 | 2.8769 | 3.2416 | 3.2642 | 3.2941 | 3.4881
2022-04-08 18:00 | 2.7055 | 2.9769 | 3.0129 | 3.0569 | 3.1081 | 2.172 | 2.617 | 2.645 | 2.6833 | 2.172 | 3.9439 | 4.4325 | 4.4577 | 4.4911 | 4.7479
2022-04-08 19:00 | 2.6864 | 2.9662 | 3.0071 | 3.0572 | 3.1156 | 2.0196 | 2.444 | 2.4759 | 2.5195 | 2.0196 | 2.8769 | 3.2538 | 3.2824 | 3.3205 | 3.5242
2022-04-08 20:00 | 2.5721 | 2.8531 | 2.8989 | 2.9551 | 3.0205 | 2.0196 | 2.451 | 2.4868 | 2.5356 | 2.0196 | 3.0484 | 3.4512 | 3.4833 | 3.526 | 3.7446
2022-04-08 21:00 | 2.4578 | 2.7319 | 2.7786 | 2.8357 | 2.9024 | 1.9015 | 2.3127 | 2.3492 | 2.3989 | 1.9015 | 2.6293 | 2.9865 | 3.0192 | 3.0627 | 3.2592
2022-04-08 22:00 | 2.3435 | 2.6031 | 2.6468 | 2.7002 | 2.7625 | 1.6766 | 2.0428 | 2.0768 | 2.1233 | 1.6766 | 2.4578 | 2.7918 | 2.8223 | 2.863 | 3.0467
2022-04-08 23:00 | 2.0958 | 2.3286 | 2.3679 | 2.4161 | 2.4722 | 1.5814 | 1.9241 | 1.9548 | 1.9967 | 1.5814 | 2.2101 | 2.5105 | 2.5381 | 2.5747 | 2.74
2022-04-09 | 1.9053 | 2.1144 | 2.149 | 2.1912 | 2.2404 | 1.2795 | 1.5606 | 1.5875 | 1.6243 | 1.2795 | 1.8481 | 2.1016 | 2.1257 | 2.1579 | 2.2979
2022-04-09 01:00 | 1.8481 | 2.0435 | 2.0731 | 2.1093 | 2.1516 | 1.1622 | 1.4151 | 1.4382 | 1.4697 | 1.1622 | 1.5623 | 1.7772 | 1.798 | 1.8255 | 1.9444
2022-04-09 02:00 | 1.7147 | 1.8881 | 1.9116 | 1.9403 | 1.9737 | 1.086 | 1.3163 | 1.3346 | 1.3595 | 1.086 | 1.6195 | 1.8322 | 1.8486 | 1.8704 | 1.9855
2022-04-09 03:00 | 1.7338 | 1.8968 | 1.9142 | 1.9355 | 1.9603 | 1.0275 | 1.2386 | 1.2522 | 1.2708 | 1.0275 | 1.3718 | 1.5485 | 1.5607 | 1.5769 | 1.6717
2022-04-09 04:00 | 1.7528 | 1.9071 | 1.9194 | 1.9344 | 1.9519 | 1.0669 | 1.2779 | 1.2874 | 1.3005 | 1.0669 | 1.4289 | 1.6049 | 1.6135 | 1.6249 | 1.7171
2022-04-09 05:00 | 1.7338 | 1.8827 | 1.8929 | 1.9055 | 1.9201 | 1.105 | 1.32 | 1.328 | 1.3389 | 1.105 | 1.6957 | 1.8985 | 1.9057 | 1.9152 | 2.0198
2022-04-09 06:00 | 1.81 | 1.9679 | 1.9799 | 1.9945 | 2.0115 | 1.2003 | 1.435 | 1.4443 | 1.457 | 1.2003 | 1.7719 | 1.9856 | 1.9939 | 2.005 | 2.1157
2022-04-09 07:00 | 1.8672 | 2.0384 | 2.055 | 2.0753 | 2.0989 | 1.3146 | 1.5766 | 1.5895 | 1.6072 | 1.3146 | 1.7338 | 1.9497 | 1.9613 | 1.9767 | 2.0905
2022-04-09 08:00 | 2.0005 | 2.195 | 2.2184 | 2.2471 | 2.2805 | 1.4289 | 1.7214 | 1.7396 | 1.7645 | 1.4289 | 2.0196 | 2.2767 | 2.2931 | 2.3149 | 2.452
2022-04-09 09:00 | 2.1148 | 2.3321 | 2.3628 | 2.4003 | 2.4441 | 1.4289 | 1.7317 | 1.7556 | 1.7883 | 1.4289 | 1.6957 | 1.9269 | 1.9484 | 1.9769 | 2.1043
2022-04-09 10:00 | 2.0767 | 2.3021 | 2.3384 | 2.3828 | 2.4345 | 1.448 | 1.7622 | 1.7904 | 1.8291 | 1.448 | 1.5242 | 1.7441 | 1.7695 | 1.8032 | 1.9274
2022-04-09 11:00 | 2.0577 | 2.286 | 2.3245 | 2.3716 | 2.4265 | 1.3337 | 1.6303 | 1.6603 | 1.7013 | 1.3337 | 1.3146 | 1.5143 | 1.5412 | 1.577 | 1.6922
2022-04-09 12:00 | 1.9587 | 2.1786 | 2.2165 | 2.263 | 2.3171 | 1.2194 | 1.4945 | 1.5241 | 1.5645 | 1.2194 | 1.086 | 1.2594 | 1.286 | 1.3214 | 1.4233
2022-04-09 13:00 | 1.8672 | 2.0753 | 2.1107 | 2.154 | 2.2045 | 1.4099 | 1.7159 | 1.7435 | 1.7812 | 1.4099 | 1.3718 | 1.5735 | 1.5983 | 1.6313 | 1.7461
2022-04-09 14:00 | 1.8481 | 2.0494 | 2.082 | 2.122 | 2.1685 | 1.1565 | 1.4126 | 1.4381 | 1.4728 | 1.1565 | 1.448 | 1.6544 | 1.6772 | 1.7076 | 1.8235
2022-04-09 15:00 | 2.0196 | 2.23 | 2.2608 | 2.2985 | 2.3425 | 1.351 | 1.6398 | 1.6639 | 1.6967 | 1.351 | 1.4861 | 1.6942 | 1.7157 | 1.7444 | 1.8604
2022-04-09 16:00 | 2.2291 | 2.4543 | 2.4847 | 2.5218 | 2.5652 | 1.5776 | 1.9069 | 1.9306 | 1.9629 | 1.5776 | 2.0005 | 2.2652 | 2.2865 | 2.3147 | 2.4585
2022-04-09 17:00 | 2.3816 | 2.6216 | 2.6538 | 2.6932 | 2.7391 | 1.8672 | 2.2515 | 2.2766 | 2.3109 | 1.8672 | 3.1056 | 3.4957 | 3.5182 | 3.5482 | 3.7547
2022-04-09 18:00 | 2.534 | 2.7927 | 2.8286 | 2.8726 | 2.9239 | 1.9624 | 2.3694 | 2.3974 | 2.4357 | 1.9624 | 2.4959 | 2.8234 | 2.8486 | 2.882 | 3.0592
2022-04-09 19:00 | 2.5149 | 2.782 | 2.8229 | 2.873 | 2.9314 | 1.9624 | 2.3765 | 2.4084 | 2.452 | 1.9624 | 2.7245 | 3.0844 | 3.113 | 3.1511 | 3.3465
2022-04-09 20:00 | 2.4197 | 2.6893 | 2.7352 | 2.7913 | 2.8568 | 1.7528 | 2.1359 | 2.1717 | 2.2205 | 1.7528 | 2.8198 | 3.1971 | 3.2292 | 3.2719 | 3.478
2022-04-09 21:00 | 2.2863 | 2.5477 | 2.5944 | 2.6515 | 2.7181 | 1.6195 | 1.9796 | 2.016 | 2.0657 | 1.6195 | 2.2482 | 2.5631 | 2.5958 | 2.6393 | 2.8148
2022-04-09 22:00 | 2.1209 | 2.364 | 2.4077 | 2.4611 | 2.5234 | 1.5451 | 1.8874 | 1.9214 | 1.9679 | 1.5451 | 2.2482 | 2.5589 | 2.5894 | 2.6301 | 2.8023
2022-04-09 23:00 | 2.0196 | 2.2467 | 2.286 | 2.3342 | 2.3903 | 1.3568 | 1.6588 | 1.6895 | 1.7314 | 1.3568 | 1.829 | 2.0871 | 2.1146 | 2.1513 | 2.2956
2022-04-10 | 1.8481 | 2.053 | 2.0875 | 2.1298 | 2.179 | 1.2575 | 1.5346 | 1.5615 | 1.5983 | 1.2575 | 1.7719 | 2.0169 | 2.0411 | 2.0732 | 2.209
2022-04-10 01:00 | 1.7909 | 1.9821 | 2.0117 | 2.0479 | 2.0902 | 1.1095 | 1.3528 | 1.3759 | 1.4074 | 1.1095 | 1.4099 | 1.6078 | 1.6286 | 1.6561 | 1.7666
2022-04-10 02:00 | 1.6766 | 1.8472 | 1.8706 | 1.8993 | 1.9328 | 1.0669 | 1.2938 | 1.3121 | 1.337 | 1.0669 | 1.3337 | 1.5146 | 1.531 | 1.5528 | 1.6523
2022-04-10 03:00 | 1.6576 | 1.8149 | 1.8323 | 1.8536 | 1.8784 | 1.0288 | 1.2402 | 1.2538 | 1.2723 | 1.0288 | 1.5623 | 1.7603 | 1.7725 | 1.7887 | 1.8939
2022-04-10 04:00 | 1.7338 | 1.8867 | 1.8989 | 1.9139 | 1.9314 | 1.0288 | 1.2329 | 1.2424 | 1.2555 | 1.0288 | 1.4289 | 1.6049 | 1.6135 | 1.6249 | 1.7171
2022-04-10 05:00 | 1.7528 | 1.9032 | 1.9134 | 1.9259 | 1.9405 | 1.0653 | 1.2731 | 1.2811 | 1.2919 | 1.0653 | 1.3337 | 1.4962 | 1.5034 | 1.5129 | 1.5977
2022-04-10 06:00 | 1.7528 | 1.9065 | 1.9184 | 1.9331 | 1.9501 | 1.1241 | 1.3449 | 1.3542 | 1.367 | 1.1241 | 1.5433 | 1.7315 | 1.7399 | 1.751 | 1.8491
2022-04-10 07:00 | 1.6666 | 1.8229 | 1.8395 | 1.8598 | 1.8835 | 1.2384 | 1.4866 | 1.4995 | 1.5172 | 1.2384 | 1.5242 | 1.7168 | 1.7284 | 1.7438 | 1.8461
2022-04-10 08:00 | 1.7147 | 1.888 | 1.9114 | 1.94 | 1.9734 | 1.1432 | 1.3837 | 1.402 | 1.4269 | 1.1432 | 1.6957 | 1.9168 | 1.9332 | 1.955 | 2.0742
2022-04-10 09:00 | 1.6576 | 1.8408 | 1.8715 | 1.9091 | 1.9528 | 1.0218 | 1.2508 | 1.2747 | 1.3074 | 1.0218 | 1.105 | 1.2705 | 1.292 | 1.3206 | 1.4155
2022-04-10 10:00 | 1.5242 | 1.7085 | 1.7448 | 1.7892 | 1.8409 | 1.0288 | 1.267 | 1.2953 | 1.3339 | 1.0288 | 1.2003 | 1.3841 | 1.4096 | 1.4433 | 1.5497
2022-04-10 11:00 | 1.448 | 1.631 | 1.6695 | 1.7166 | 1.7715 | 0.87642 | 1.0901 | 1.1201 | 1.1611 | 0.87642 | 1.4099 | 1.6201 | 1.6471 | 1.6829 | 1.8033
2022-04-10 12:00 | 1.467 | 1.6504 | 1.6883 | 1.7348 | 1.7889 | 1.0669 | 1.3144 | 1.344 | 1.3844 | 1.0669 | 1.4099 | 1.6194 | 1.646 | 1.6813 | 1.801
2022-04-10 13:00 | 1.7338 | 1.932 | 1.9674 | 2.0107 | 2.0612 | 1.0647 | 1.3081 | 1.3357 | 1.3734 | 1.0647 | 1.448 | 1.6582 | 1.683 | 1.7159 | 1.835
2022-04-10 14:00 | 1.6852 | 1.8744 | 1.907 | 1.947 | 1.9935 | 1.1795 | 1.4398 | 1.4652 | 1.5 | 1.1795 | 1.105 | 1.2733 | 1.2961 | 1.3265 | 1.4236
2022-04-10 15:00 | 1.7338 | 1.923 | 1.9538 | 1.9915 | 2.0354 | 1.2003 | 1.4618 | 1.4858 | 1.5186 | 1.2003 | 1.1432 | 1.3131 | 1.3346 | 1.3633 | 1.4604
2022-04-10 16:00 | 2.1339 | 2.352 | 2.3823 | 2.4195 | 2.4628 | 1.5433 | 1.8663 | 1.89 | 1.9223 | 1.5433 | 1.6385 | 1.8629 | 1.8842 | 1.9125 | 2.0363
2022-04-10 17:00 | 2.4006 | 2.6421 | 2.6742 | 2.7136 | 2.7595 | 1.9053 | 2.2965 | 2.3216 | 2.3559 | 1.9053 | 2.553 | 2.8817 | 2.9042 | 2.9342 | 3.1104
2022-04-10 18:00 | 2.5149 | 2.7722 | 2.8082 | 2.8522 | 2.9034 | 1.9044 | 2.3008 | 2.3289 | 2.3671 | 1.9044 | 2.534 | 2.8657 | 2.8909 | 2.9244 | 3.1037
2022-04-10 19:00 | 2.4197 | 2.6797 | 2.7206 | 2.7707 | 2.829 | 1.9053 | 2.309 | 2.3409 | 2.3845 | 1.9053 | 3.2389 | 3.656 | 3.6847 | 3.7228 | 3.9464
2022-04-10 20:00 | 2.3435 | 2.6074 | 2.6533 | 2.7094 | 2.7749 | 1.7909 | 2.1809 | 2.2167 | 2.2655 | 1.7909 | 2.4578 | 2.7948 | 2.8269 | 2.8696 | 3.0558
2022-04-10 21:00 | 2.2482 | 2.5067 | 2.5534 | 2.6106 | 2.6772 | 1.6957 | 2.0696 | 2.106 | 2.1557 | 1.6957 | 2.172 | 2.4784 | 2.5111 | 2.5546 | 2.7259
2022-04-10 22:00 | 2.1264 | 2.37 | 2.4136 | 2.467 | 2.5293 | 1.4722 | 1.8013 | 1.8353 | 1.8818 | 1.4722 | 2.3625 | 2.6859 | 2.7165 | 2.7571 | 2.9356
2022-04-10 23:00 | 1.8672 | 2.083 | 2.1223 | 2.1704 | 2.2266 | 1.3046 | 1.5972 | 1.6278 | 1.6697 | 1.3046 | 1.9243 | 2.1929 | 2.2205 | 2.2571 | 2.4067
2022-04-11 | 1.7719 | 1.9712 | 2.0057 | 2.0479 | 2.0972 | 1.1622 | 1.422 | 1.449 | 1.4857 | 1.1622 | 1.6576 | 1.8898 | 1.914 | 1.9461 | 2.0757
2022-04-11 01:00 | 1.6004 | 1.7774 | 1.807 | 1.8432 | 1.8855 | 1.064 | 1.2991 | 1.3222 | 1.3538 | 1.064 | 1.467 | 1.6713 | 1.6921 | 1.7197 | 1.8333
2022-04-11 02:00 | 1.5814 | 1.7448 | 1.7683 | 1.797 | 1.8304 | 0.97854 | 1.1893 | 1.2076 | 1.2326 | 0.97854 | 1.2384 | 1.4087 | 1.4251 | 1.447 | 1.5412
2022-04-11 03:00 | 1.5814 | 1.733 | 1.7504 | 1.7717 | 1.7966 | 0.97671 | 1.1786 | 1.1922 | 1.2107 | 0.97671 | 1.2384 | 1.4003 | 1.4125 | 1.4287 | 1.5162
2022-04-11 04:00 | 1.6829 | 1.832 | 1.8443 | 1.8593 | 1.8768 | 1.0995 | 1.3163 | 1.3259 | 1.339 | 1.0995 | 1.4289 | 1.6049 | 1.6135 | 1.6249 | 1.7171
2022-04-11 05:00 | 1.7971 | 1.9508 | 1.961 | 1.9735 | 1.9881 | 1.1717 | 1.3987 | 1.4067 | 1.4176 | 1.1717 | 1.6195 | 1.8138 | 1.821 | 1.8305 | 1.9309
2022-04-11 06:00 | 1.9536 | 2.1222 | 2.1341 | 2.1487 | 2.1657 | 1.3337 | 1.5925 | 1.6018 | 1.6145 | 1.3337 | 1.6576 | 1.8585 | 1.8669 | 1.878 | 1.9824
2022-04-11 07:00 | 2.0005 | 2.1817 | 2.1983 | 2.2186 | 2.2422 | 1.4099 | 1.6892 | 1.7021 | 1.7197 | 1.4099 | 1.6576 | 1.865 | 1.8766 | 1.892 | 2.0016
2022-04-11 08:00 | 2.0005 | 2.195 | 2.2184 | 2.2471 | 2.2805 | 1.3527 | 1.6313 | 1.6496 | 1.6745 | 1.3527 | 1.2765 | 1.451 | 1.4674 | 1.4892 | 1.5854
2022-04-11 09:00 | 1.6957 | 1.8818 | 1.9125 | 1.95 | 1.9938 | 1.086 | 1.3266 | 1.3505 | 1.3832 | 1.086 | 1.1432 | 1.3129 | 1.3344 | 1.3629 | 1.4599
2022-04-11 10:00 | 1.6576 | 1.8518 | 1.8881 | 1.9324 | 1.9842 | 0.66899 | 0.84188 | 0.87017 | 0.90879 | 0.66899 | 1.5814 | 1.8076 | 1.833 | 1.8668 | 1.9941
2022-04-11 11:00 | 1.8481 | 2.0608 | 2.0993 | 2.1464 | 2.2013 | 0.85737 | 1.0676 | 1.0976 | 1.1386 | 0.85737 | 2.2101 | 2.5094 | 2.5363 | 2.5721 | 2.7365
2022-04-11 12:00 | 1.6385 | 1.8346 | 1.8726 | 1.919 | 1.9732 | 0.7621 | 0.95427 | 0.98387 | 1.0243 | 0.7621 | 1.9434 | 2.2122 | 2.2388 | 2.2741 | 2.4232
2022-04-11 13:00 | 2.172 | 2.4028 | 2.4382 | 2.4815 | 2.532 | 1.2384 | 1.5133 | 1.541 | 1.5787 | 1.2384 | 1.8481 | 2.1028 | 2.1276 | 2.1606 | 2.3016
2022-04-11 14:00 | 2.553 | 2.8067 | 2.8394 | 2.8793 | 2.9259 | 1.467 | 1.7795 | 1.805 | 1.8397 | 1.467 | 1.8481 | 2.099 | 2.1218 | 2.1522 | 2.2901
2022-04-11 15:00 | 2.4387 | 2.6803 | 2.7111 | 2.7488 | 2.7928 | 1.4786 | 1.7905 | 1.8146 | 1.8474 | 1.4786 | 1.6576 | 1.8847 | 1.9063 | 1.935 | 2.0604
2022-04-11 16:00 | 2.3136 | 2.545 | 2.5754 | 2.6125 | 2.6559 | 1.5888 | 1.9202 | 1.9438 | 1.9762 | 1.5888 | 1.8862 | 2.1382 | 2.1594 | 2.1877 | 2.3252
2022-04-11 17:00 | 2.5721 | 2.8263 | 2.8585 | 2.8978 | 2.9438 | 1.81 | 2.184 | 2.2091 | 2.2434 | 1.81 | 2.3816 | 2.6912 | 2.7137 | 2.7437 | 2.9104
2022-04-11 18:00 | 2.6293 | 2.8951 | 2.931 | 2.975 | 3.0263 | 1.9815 | 2.3919 | 2.4199 | 2.4582 | 1.9815 | 2.553 | 2.8869 | 2.9121 | 2.9455 | 3.1259
2022-04-11 19:00 | 2.5149 | 2.782 | 2.8229 | 2.873 | 2.9314 | 1.9434 | 2.354 | 2.3859 | 2.4295 | 1.9434 | 2.4364 | 2.7642 | 2.7929 | 2.831 | 3.0105
2022-04-11 20:00 | 2.4004 | 2.6686 | 2.7145 | 2.7706 | 2.8361 | 1.7125 | 2.0883 | 2.124 | 2.1729 | 1.7125 | 2.8769 | 3.2606 | 3.2927 | 3.3354 | 3.5446
2022-04-11 21:00 | 2.2291 | 2.4863 | 2.533 | 2.5901 | 2.6567 | 1.6766 | 2.0471 | 2.0835 | 2.1332 | 1.6766 | 2.3816 | 2.7113 | 2.744 | 2.7875 | 2.9704
2022-04-11 22:00 | 2.09 | 2.3309 | 2.3745 | 2.4279 | 2.4902 | 1.4893 | 1.8215 | 1.8555 | 1.902 | 1.4893 | 2.3625 | 2.6859 | 2.7165 | 2.7571 | 2.9356
2022-04-11 23:00 | 1.9053 | 2.1239 | 2.1632 | 2.2114 | 2.2675 | 1.2765 | 1.564 | 1.5946 | 1.6365 | 1.2765 | 1.6576 | 1.8965 | 1.9241 | 1.9607 | 2.0956
2022-04-12 | 1.7909 | 1.9916 | 2.0261 | 2.0684 | 2.1176 | 1.1403 | 1.3962 | 1.4231 | 1.4599 | 1.1403 | 1.448 | 1.6569 | 1.6811 | 1.7133 | 1.8313
2022-04-12 01:00 | 1.6385 | 1.8183 | 1.8479 | 1.8842 | 1.9264 | 1.0424 | 1.2736 | 1.2967 | 1.3282 | 1.0424 | 1.3337 | 1.5231 | 1.5439 | 1.5715 | 1.6777
2022-04-12 02:00 | 1.6385 | 1.8062 | 1.8297 | 1.8584 | 1.8918 | 1.0098 | 1.2263 | 1.2445 | 1.2695 | 1.0098 | 1.3527 | 1.5357 | 1.5522 | 1.574 | 1.6745
2022-04-12 03:00 | 1.6341 | 1.7897 | 1.8071 | 1.8284 | 1.8532 | 0.98148 | 1.1842 | 1.1978 | 1.2163 | 0.98148 | 1.3527 | 1.5274 | 1.5396 | 1.5558 | 1.6495
2022-04-12 04:00 | 1.6385 | 1.7843 | 1.7966 | 1.8116 | 1.8291 | 1.0288 | 1.2329 | 1.2424 | 1.2555 | 1.0288 | 1.3908 | 1.5626 | 1.5712 | 1.5826 | 1.6727
2022-04-12 05:00 | 1.7909 | 1.9441 | 1.9543 | 1.9669 | 1.9815 | 1.1241 | 1.3425 | 1.3505 | 1.3614 | 1.1241 | 1.5433 | 1.7291 | 1.7363 | 1.7458 | 1.8421
2022-04-12 06:00 | 1.8672 | 2.0293 | 2.0413 | 2.0559 | 2.0729 | 1.3718 | 1.6375 | 1.6468 | 1.6596 | 1.3718 | 1.8672 | 2.0914 | 2.0998 | 2.1109 | 2.2268
2022-04-12 07:00 | 2.0958 | 2.284 | 2.3006 | 2.3209 | 2.3446 | 1.3908 | 1.6666 | 1.6796 | 1.6972 | 1.3908 | 1.5052 | 1.6956 | 1.7072 | 1.7227 | 1.8239
2022-04-12 08:00 | 1.9624 | 2.1541 | 2.1775 | 2.2061 | 2.2395 | 1.2765 | 1.5413 | 1.5595 | 1.5845 | 1.2765 | 1.1813 | 1.3451 | 1.3615 | 1.3833 | 1.4743
2022-04-12 09:00 | 1.9815 | 2.1888 | 2.2195 | 2.257 | 2.3008 | 1.1813 | 1.4391 | 1.463 | 1.4957 | 1.1813 | 1.1432 | 1.3129 | 1.3344 | 1.3629 | 1.4599
2022-04-12 10:00 | 1.9243 | 2.1384 | 2.1746 | 2.219 | 2.2708 | 1.2003 | 1.4696 | 1.4978 | 1.5365 | 1.2003 | 1.2003 | 1.3841 | 1.4096 | 1.4433 | 1.5497
2022-04-12 11:00 | 1.829 | 2.0404 | 2.0788 | 2.1259 | 2.1809 | 1.0669 | 1.3152 | 1.3452 | 1.3862 | 1.0669 | 1.2384 | 1.4296 | 1.4565 | 1.4924 | 1.6033
2022-04-12 12:00 | 1.5692 | 1.7601 | 1.798 | 1.8445 | 1.8986 | 0.88217 | 1.0961 | 1.1257 | 1.1661 | 0.88217 | 1.5052 | 1.7252 | 1.7518 | 1.7871 | 1.9121
2022-04-12 13:00 | 1.3181 | 1.4853 | 1.5207 | 1.5641 | 1.6146 | 0.60968 | 0.77059 | 0.7982 | 0.8359 | 0.60968 | 1.6766 | 1.9123 | 1.9371 | 1.97 | 2.1016
2022-04-12 14:00 | 2.0005 | 2.2131 | 2.2458 | 2.2857 | 2.3323 | 1.1432 | 1.3969 | 1.4223 | 1.4571 | 1.1432 | 1.3908 | 1.5908 | 1.6137 | 1.6441 | 1.7569
2022-04-12 15:00 | 2.191 | 2.4142 | 2.445 | 2.4827 | 2.5267 | 1.3527 | 1.6419 | 1.6659 | 1.6987 | 1.3527 | 1.3718 | 1.5671 | 1.5887 | 1.6174 | 1.7271
2022-04-12 16:00 | 2.1529 | 2.3724 | 2.4028 | 2.44 | 2.4833 | 1.459 | 1.7668 | 1.7905 | 1.8228 | 1.459 | 1.7528 | 1.99 | 2.0112 | 2.0395 | 2.1697
2022-04-12 17:00 | 2.505 | 2.7543 | 2.7864 | 2.8258 | 2.8717 | 1.8481 | 2.229 | 2.2541 | 2.2884 | 1.8481 | 2.4006 | 2.7123 | 2.7349 | 2.7648 | 2.9326
2022-04-12 18:00 | 2.534 | 2.7927 | 2.8286 | 2.8726 | 2.9239 | 2.0386 | 2.4594 | 2.4875 | 2.5257 | 2.0386 | 2.6864 | 3.0351 | 3.0603 | 3.0938 | 3.2814
2022-04-12 19:00 | 2.4633 | 2.7265 | 2.7674 | 2.8175 | 2.8759 | 1.9624 | 2.3765 | 2.4084 | 2.452 | 1.9624 | 2.9341 | 3.3173 | 3.3459 | 3.384 | 3.5909
2022-04-12 20:00 | 2.4387 | 2.7098 | 2.7557 | 2.8118 | 2.8772 | 1.8481 | 2.2485 | 2.2842 | 2.3331 | 1.8481 | 3.0675 | 3.4723 | 3.5045 | 3.5472 | 3.7668
2022-04-12 21:00 | 2.3054 | 2.5681 | 2.6148 | 2.672 | 2.7386 | 1.7909 | 2.1821 | 2.2185 | 2.2683 | 1.7909 | 2.3435 | 2.6689 | 2.7017 | 2.7451 | 2.9259
2022-04-12 22:00 | 2.1529 | 2.3984 | 2.4421 | 2.4955 | 2.5578 | 1.5814 | 1.9302 | 1.9643 | 2.0107 | 1.5814 | 2.1148 | 2.4107 | 2.4412 | 2.4819 | 2.6467
2022-04-12 23:00 | 1.9624 | 2.1853 | 2.2246 | 2.2728 | 2.3289 | 1.426 | 1.7405 | 1.7712 | 1.8131 | 1.426 | 1.9053 | 2.1718 | 2.1993 | 2.236 | 2.3845
2022-04-13 | 1.8481 | 2.053 | 2.0875 | 2.1298 | 2.179 | 1.1568 | 1.4156 | 1.4425 | 1.4793 | 1.1568 | 1.5623 | 1.784 | 1.8082 | 1.8403 | 1.9646
2022-04-13 01:00 | 1.6957 | 1.8797 | 1.9093 | 1.9456 | 1.9879 | 1.0875 | 1.3268 | 1.3499 | 1.3815 | 1.0875 | 1.3718 | 1.5655 | 1.5862 | 1.6138 | 1.7222
2022-04-13 02:00 | 1.6385 | 1.8062 | 1.8297 | 1.8584 | 1.8918 | 1.0323 | 1.2529 | 1.2712 | 1.2962 | 1.0323 | 1.2956 | 1.4722 | 1.4887 | 1.5105 | 1.6078
2022-04-13 03:00 | 1.6195 | 1.7739 | 1.7913 | 1.8127 | 1.8375 | 1.0263 | 1.2371 | 1.2507 | 1.2692 | 1.0263 | 1.4099 | 1.5909 | 1.6031 | 1.6193 | 1.7162
2022-04-13 04:00 | 1.7338 | 1.8867 | 1.8989 | 1.9139 | 1.9314 | 1.1384 | 1.3623 | 1.3719 | 1.3849 | 1.1384 | 1.467 | 1.6473 | 1.6559 | 1.6673 | 1.7616
2022-04-13 05:00 | 1.8672 | 2.026 | 2.0362 | 2.0487 | 2.0633 | 1.2384 | 1.4776 | 1.4855 | 1.4964 | 1.2384 | 1.6195 | 1.8138 | 1.821 | 1.8305 | 1.9309
2022-04-13 06:00 | 1.9624 | 2.1317 | 2.1436 | 2.1582 | 2.1752 | 1.4289 | 1.7051 | 1.7144 | 1.7271 | 1.4289 | 1.9434 | 2.1761 | 2.1845 | 2.1956 | 2.3157
2022-04-13 07:00 | 2.0958 | 2.284 | 2.3006 | 2.3209 | 2.3446 | 1.467 | 1.7567 | 1.7696 | 1.7873 | 1.467 | 1.6576 | 1.865 | 1.8766 | 1.892 | 2.0016
2022-04-13 08:00 | 2.0577 | 2.2565 | 2.2798 | 2.3085 | 2.3419 | 1.5814 | 1.9014 | 1.9197 | 1.9446 | 1.5814 | 1.6385 | 1.8533 | 1.8697 | 1.8914 | 2.0076
2022-04-13 09:00 | 2.0767 | 2.2912 | 2.3218 | 2.3594 | 2.4032 | 1.3908 | 1.6867 | 1.7106 | 1.7433 | 1.3908 | 1.1432 | 1.3129 | 1.3344 | 1.3629 | 1.4599
2022-04-13 10:00 | 2.0196 | 2.2407 | 2.277 | 2.3213 | 2.3731 | 1.3146 | 1.6046 | 1.6329 | 1.6715 | 1.3146 | 1.3527 | 1.5535 | 1.5789 | 1.6127 | 1.7274
2022-04-13 11:00 | 2.0386 | 2.2655 | 2.304 | 2.3511 | 2.406 | 1.1622 | 1.4277 | 1.4577 | 1.4987 | 1.1622 | 1.6195 | 1.853 | 1.88 | 1.9158 | 2.0477
2022-04-13 12:00 | 1.9624 | 2.1826 | 2.2205 | 2.267 | 2.3211 | 1.1622 | 1.4269 | 1.4565 | 1.4969 | 1.1622 | 1.7719 | 2.0216 | 2.0482 | 2.0836 | 2.2232
2022-04-13 13:00 | 2.0767 | 2.3004 | 2.3358 | 2.3791 | 2.4297 | 1.1622 | 1.4233 | 1.4509 | 1.4886 | 1.1622 | 1.81 | 2.0605 | 2.0853 | 2.1182 | 2.2571
2022-04-13 14:00 | 2.0386 | 2.2541 | 2.2867 | 2.3266 | 2.3732 | 1.2194 | 1.4869 | 1.5124 | 1.5471 | 1.2194 | 1.6004 | 1.8237 | 1.8466 | 1.877 | 2.0013
2022-04-13 15:00 | 1.8481 | 2.0458 | 2.0766 | 2.1143 | 2.1583 | 1.0369 | 1.2687 | 1.2928 | 1.3256 | 1.0369 | 1.0098 | 1.1648 | 1.1864 | 1.2151 | 1.3049
2022-04-13 16:00 | 2.1339 | 2.352 | 2.3823 | 2.4195 | 2.4628 | 1.5052 | 1.8213 | 1.845 | 1.8773 | 1.5052 | 1.467 | 1.6724 | 1.6936 | 1.7219 | 1.8364
2022-04-13 17:00 | 2.4768 | 2.7239 | 2.7561 | 2.7955 | 2.8414 | 1.8742 | 2.2598 | 2.2849 | 2.3192 | 1.8742 | 2.4197 | 2.7335 | 2.756 | 2.786 | 2.9548
2022-04-13 18:00 | 2.4768 | 2.7313 | 2.7672 | 2.8112 | 2.8625 | 2.0386 | 2.4594 | 2.4875 | 2.5257 | 2.0386 | 3.2389 | 3.6491 | 3.6743 | 3.7077 | 3.9258
2022-04-13 19:00 | 2.534 | 2.8025 | 2.8434 | 2.8935 | 2.9519 | 2.0196 | 2.444 | 2.4759 | 2.5195 | 2.0196 | 2.8388 | 3.2114 | 3.2401 | 3.2782 | 3.4798
2022-04-13 20:00 | 2.4006 | 2.6689 | 2.7147 | 2.7708 | 2.8363 | 1.9053 | 2.316 | 2.3518 | 2.4006 | 1.9053 | 2.8769 | 3.2606 | 3.2927 | 3.3354 | 3.5446
2022-04-13 21:00 | 2.3054 | 2.5681 | 2.6148 | 2.672 | 2.7386 | 1.7965 | 2.1887 | 2.2251 | 2.2748 | 1.7965 | 2.9531 | 3.3465 | 3.3792 | 3.4226 | 3.637
2022-04-13 22:00 | 2.1529 | 2.3984 | 2.4421 | 2.4955 | 2.5578 | 1.6665 | 2.0308 | 2.0648 | 2.1113 | 1.6665 | 2.191 | 2.4953 | 2.5259 | 2.5666 | 2.7356
2022-04-13 23:00 | 2.0386 | 2.2672 | 2.3065 | 2.3547 | 2.4108 | 1.3985 | 1.7081 | 1.7387 | 1.7806 | 1.3985 | 2.0386 | 2.32 | 2.3475 | 2.3842 | 2.54
2022-04-14 | 1.7909 | 1.9916 | 2.0261 | 2.0684 | 2.1176 | 1.2956 | 1.5796 | 1.6065 | 1.6433 | 1.2956 | 1.7147 | 1.9534 | 1.9775 | 2.0097 | 2.1423
2022-04-14 01:00 | 1.81 | 2.0025 | 2.0321 | 2.0684 | 2.1107 | 1.1376 | 1.386 | 1.4091 | 1.4407 | 1.1376 | 1.6957 | 1.9254 | 1.9462 | 1.9737 | 2.0999
2022-04-14 02:00 | 1.7528 | 1.929 | 1.9525 | 1.9812 | 2.0147 | 1.0897 | 1.3207 | 1.339 | 1.364 | 1.0897 | 1.5623 | 1.7686 | 1.7851 | 1.8069 | 1.9189
2022-04-14 03:00 | 1.829 | 1.9991 | 2.0165 | 2.0378 | 2.0627 | 1.105 | 1.3302 | 1.3438 | 1.3623 | 1.105 | 1.5242 | 1.7179 | 1.7301 | 1.7463 | 1.8495
2022-04-14 04:00 | 1.829 | 1.989 | 2.0013 | 2.0163 | 2.0338 | 1.1432 | 1.3679 | 1.3775 | 1.3905 | 1.1432 | 1.5814 | 1.7743 | 1.7829 | 1.7943 | 1.8949
2022-04-14 05:00 | 1.8715 | 2.0306 | 2.0409 | 2.0534 | 2.068 | 1.3089 | 1.5608 | 1.5688 | 1.5797 | 1.3089 | 1.7147 | 1.9197 | 1.9269 | 1.9364 | 2.042
2022-04-14 06:00 | 2.1247 | 2.306 | 2.318 | 2.3326 | 2.3496 | 1.5086 | 1.7992 | 1.8085 | 1.8212 | 1.5086 | 1.9327 | 2.1643 | 2.1726 | 2.1838 | 2.3033
2022-04-14 07:00 | 2.2673 | 2.4683 | 2.4848 | 2.5051 | 2.5288 | 1.5433 | 1.8467 | 1.8596 | 1.8773 | 1.5433 | 2.191 | 2.4578 | 2.4694 | 2.4849 | 2.6238
2022-04-14 08:00 | 2.1339 | 2.3383 | 2.3617 | 2.3904 | 2.4238 | 1.4861 | 1.7889 | 1.8071 | 1.8321 | 1.4861 | 1.7719 | 2.0015 | 2.0179 | 2.0396 | 2.1631
2022-04-14 09:00 | 1.9815 | 2.1888 | 2.2195 | 2.257 | 2.3008 | 1.1869 | 1.4458 | 1.4697 | 1.5024 | 1.1869 | 1.2575 | 1.4399 | 1.4614 | 1.49 | 1.5932
2022-04-14 10:00 | 1.81 | 2.0155 | 2.0518 | 2.0962 | 2.1479 | 0.95263 | 1.177 | 1.2052 | 1.2439 | 0.95263 | 1.5433 | 1.7652 | 1.7907 | 1.8244 | 1.9496
2022-04-14 11:00 | 1.8481 | 2.0608 | 2.0993 | 2.1464 | 2.2013 | 0.70494 | 0.88751 | 0.91753 | 0.95851 | 0.70494 | 1.6576 | 1.8954 | 1.9223 | 1.9581 | 2.0921
2022-04-14 12:00 | 1.3718 | 1.548 | 1.586 | 1.6324 | 1.6866 | 0.68589 | 0.86424 | 0.89384 | 0.93425 | 0.68589 | 1.8672 | 2.1275 | 2.1541 | 2.1894 | 2.3343
2022-04-14 13:00 | 1.3908 | 1.5635 | 1.5989 | 1.6423 | 1.6928 | 0.60577 | 0.76597 | 0.79358 | 0.83128 | 0.60577 | 1.6385 | 1.8699 | 1.8947 | 1.9277 | 2.0571
2022-04-14 14:00 | 1.6385 | 1.8242 | 1.8569 | 1.8968 | 1.9434 | 0.80021 | 0.99174 | 1.0172 | 1.0519 | 0.80021 | 1.4099 | 1.612 | 1.6349 | 1.6653 | 1.7791
2022-04-14 15:00 | 1.8141 | 2.0093 | 2.0401 | 2.0778 | 2.1217 | 1.0022 | 1.2278 | 1.2518 | 1.2846 | 1.0022 | 0.87642 | 1.0166 | 1.0382 | 1.0669 | 1.1494
2022-04-14 16:00 | 2.1529 | 2.3724 | 2.4028 | 2.44 | 2.4833 | 1.387 | 1.6817 | 1.7054 | 1.7377 | 1.387 | 1.7909 | 2.0323 | 2.0536 | 2.0818 | 2.2141
2022-04-14 17:00 | 2.4006 | 2.6421 | 2.6742 | 2.7136 | 2.7595 | 1.712 | 2.0682 | 2.0933 | 2.1275 | 1.712 | 2.3435 | 2.6488 | 2.6714 | 2.7013 | 2.866
2022-04-14 18:00 | 2.4197 | 2.6699 | 2.7058 | 2.7498 | 2.8011 | 1.829 | 2.2118 | 2.2399 | 2.2781 | 1.829 | 2.3435 | 2.654 | 2.6792 | 2.7127 | 2.8815
2022-04-14 19:00 | 2.3054 | 2.5568 | 2.5978 | 2.6478 | 2.7062 | 1.7909 | 2.1739 | 2.2058 | 2.2494 | 1.7909 | 2.915 | 3.2961 | 3.3248 | 3.3629 | 3.5687
2022-04-14 20:00 | 2.2673 | 2.5256 | 2.5714 | 2.6276 | 2.693 | 1.7719 | 2.1584 | 2.1942 | 2.243 | 1.7719 | 2.8579 | 3.2394 | 3.2716 | 3.3143 | 3.5224
2022-04-14 21:00 | 2.2291 | 2.4863 | 2.533 | 2.5901 | 2.6567 | 1.6758 | 2.0461 | 2.0825 | 2.1323 | 1.6758 | 2.2673 | 2.5843 | 2.617 | 2.6604 | 2.837
2022-04-14 22:00 | 2.1339 | 2.378 | 2.4216 | 2.475 | 2.5373 | 1.4861 | 1.8177 | 1.8517 | 1.8982 | 1.4861 | 2.1339 | 2.4318 | 2.4624 | 2.503 | 2.6689
2022-04-14 23:00 | 1.964 | 2.187 | 2.2264 | 2.2745 | 2.3306 | 1.3527 | 1.654 | 1.6847 | 1.7266 | 1.3527 | 1.829 | 2.0871 | 2.1146 | 2.1513 | 2.2956
2022-04-15 | 1.8862 | 2.094 | 2.1285 | 2.1707 | 2.22 | 1.2384 | 1.5121 | 1.539 | 1.5757 | 1.2384 | 1.7528 | 1.9957 | 2.0199 | 2.052 | 2.1868
2022-04-15 01:00 | 1.7528 | 1.9411 | 1.9707 | 2.007 | 2.0493 | 1.1432 | 1.3926 | 1.4157 | 1.4472 | 1.1432 | 1.4861 | 1.6925 | 1.7133 | 1.7408 | 1.8555
2022-04-15 02:00 | 1.6957 | 1.8676 | 1.8911 | 1.9198 | 1.9532 | 1.0402 | 1.2622 | 1.2805 | 1.3055 | 1.0402 | 1.4289 | 1.6204 | 1.6369 | 1.6587 | 1.7634
2022-04-15 03:00 | 1.7338 | 1.8968 | 1.9142 | 1.9355 | 1.9603 | 1.0524 | 1.268 | 1.2816 | 1.3001 | 1.0524 | 1.4861 | 1.6756 | 1.6878 | 1.704 | 1.8051
2022-04-15 04:00 | 1.7909 | 1.9481 | 1.9603 | 1.9753 | 1.9928 | 1.0942 | 1.3101 | 1.3197 | 1.3327 | 1.0942 | 1.5433 | 1.732 | 1.7405 | 1.752 | 1.8504
2022-04-15 05:00 | 1.7909 | 1.9441 | 1.9543 | 1.9669 | 1.9815 | 1.1241 | 1.3425 | 1.3505 | 1.3614 | 1.1241 | 1.6195 | 1.8138 | 1.821 | 1.8305 | 1.9309
2022-04-15 06:00 | 1.81 | 1.9679 | 1.9799 | 1.9945 | 2.0115 | 1.1913 | 1.4243 | 1.4336 | 1.4463 | 1.1913 | 1.9053 | 2.1338 | 2.1421 | 2.1533 | 2.2713
2022-04-15 07:00 | 1.7909 | 1.9565 | 1.9731 | 1.9934 | 2.0171 | 1.3146 | 1.5766 | 1.5895 | 1.6072 | 1.3146 | 1.7147 | 1.9285 | 1.9401 | 1.9555 | 2.0683
2022-04-15 08:00 | 1.7909 | 1.9699 | 1.9933 | 2.0219 | 2.0553 | 1.1741 | 1.4203 | 1.4386 | 1.4635 | 1.1741 | 1.2956 | 1.4722 | 1.4886 | 1.5103 | 1.6076
2022-04-15 09:00 | 1.5433 | 1.718 | 1.7487 | 1.7863 | 1.83 | 0.85424 | 1.0528 | 1.0767 | 1.1094 | 0.85424 | 1.0098 | 1.1647 | 1.1862 | 1.2147 | 1.3044
2022-04-15 10:00 | 1.2384 | 1.4015 | 1.4377 | 1.4821 | 1.5339 | 0.65703 | 0.82775 | 0.85604 | 0.89466 | 0.65703 | 1.2956 | 1.49 | 1.5154 | 1.5492 | 1.6608
2022-04-15 11:00 | 1.5052 | 1.6924 | 1.7309 | 1.778 | 1.8329 | 0.99193 | 1.2265 | 1.2566 | 1.2975 | 0.99193 | 1.5814 | 1.8107 | 1.8376 | 1.8735 | 2.0032
2022-04-15 12:00 | 1.6576 | 1.8551 | 1.893 | 1.9395 | 1.9936 | 1.1432 | 1.4044 | 1.434 | 1.4744 | 1.1432 | 1.5623 | 1.7888 | 1.8153 | 1.8507 | 1.9788
2022-04-15 13:00 | 1.4861 | 1.6659 | 1.7013 | 1.7446 | 1.7951 | 1.0098 | 1.2433 | 1.2709 | 1.3086 | 1.0098 | 1.6385 | 1.8699 | 1.8947 | 1.9277 | 2.0571
2022-04-15 14:00 | 1.6195 | 1.8037 | 1.8364 | 1.8763 | 1.9229 | 0.93358 | 1.1493 | 1.1747 | 1.2095 | 0.93358 | 1.5242 | 1.739 | 1.7619 | 1.7923 | 1.9124
2022-04-15 15:00 | 1.8862 | 2.0867 | 2.1175 | 2.1552 | 2.1992 | 1.2765 | 1.5518 | 1.5759 | 1.6087 | 1.2765 | 1.3908 | 1.5883 | 1.6099 | 1.6386 | 1.7493
2022-04-15 16:00 | 2.0274 | 2.2375 | 2.2679 | 2.3051 | 2.3484 | 1.3872 | 1.682 | 1.7057 | 1.738 | 1.3872 | 1.6195 | 1.8418 | 1.863 | 1.8913 | 2.0141
2022-04-15 17:00 | 2.2863 | 2.5193 | 2.5514 | 2.5908 | 2.6367 | 1.7528 | 2.1165 | 2.1416 | 2.1758 | 1.7528 | 2.2673 | 2.5641 | 2.5867 | 2.6166 | 2.7771
2022-04-15 18:00 | 2.3054 | 2.5471 | 2.583 | 2.627 | 2.6783 | 1.7909 | 2.1668 | 2.1949 | 2.2331 | 1.7909 | 2.9341 | 3.3104 | 3.3355 | 3.369 | 3.5703
2022-04-15 19:00 | 2.2863 | 2.5364 | 2.5773 | 2.6274 | 2.6858 | 1.6957 | 2.0614 | 2.0933 | 2.1369 | 1.6957 | 2.7436 | 3.1056 | 3.1342 | 3.1723 | 3.3687
2022-04-15 20:00 | 2.191 | 2.4437 | 2.4896 | 2.5457 | 2.6111 | 1.6195 | 1.9784 | 2.0141 | 2.063 | 1.6195 | 3.0103 | 3.4088 | 3.4409 | 3.4836 | 3.7002
2022-04-15 21:00 | 2.1339 | 2.3839 | 2.4306 | 2.4878 | 2.5544 | 1.5433 | 1.8895 | 1.9259 | 1.9757 | 1.5433 | 2.0958 | 2.3937 | 2.4264 | 2.4699 | 2.6371
2022-04-15 22:00 | 2.0196 | 2.2552 | 2.2988 | 2.3522 | 2.4145 | 1.4182 | 1.7375 | 1.7715 | 1.818 | 1.4182 | 2.1148 | 2.4107 | 2.4412 | 2.4819 | 2.6467
2022-04-15 23:00 | 1.829 | 2.042 | 2.0814 | 2.1295 | 2.1856 | 1.3146 | 1.609 | 1.6397 | 1.6815 | 1.3146 | 1.9624 | 2.2353 | 2.2629 | 2.2995 | 2.4511
2022-04-16 | 1.7338 | 1.9302 | 1.9647 | 2.007 | 2.0562 | 1.2003 | 1.4671 | 1.494 | 1.5307 | 1.2003 | 1.5814 | 1.8052 | 1.8293 | 1.8615 | 1.9868
2022-04-16 01:00 | 1.6766 | 1.8592 | 1.8889 | 1.9251 | 1.9674 | 1.086 | 1.3251 | 1.3482 | 1.3797 | 1.086 | 1.5242 | 1.7349 | 1.7556 | 1.7832 | 1.8999
2022-04-16 02:00 | 1.6385 | 1.8062 | 1.8297 | 1.8584 | 1.8918 | 1.0403 | 1.2624 | 1.2806 | 1.3056 | 1.0403 | 1.3527 | 1.5357 | 1.5522 | 1.574 | 1.6745
2022-04-16 03:00 | 1.6385 | 1.7944 | 1.8118 | 1.8331 | 1.858 | 1.017 | 1.2261 | 1.2397 | 1.2583 | 1.017 | 1.3718 | 1.5485 | 1.5607 | 1.5769 | 1.6717
2022-04-16 04:00 | 1.6576 | 1.8048 | 1.8171 | 1.8321 | 1.8496 | 1.0479 | 1.2554 | 1.2649 | 1.278 | 1.0479 | 1.467 | 1.6473 | 1.6559 | 1.6673 | 1.7616
2022-04-16 05:00 | 1.6878 | 1.8333 | 1.8436 | 1.8561 | 1.8707 | 1.105 | 1.32 | 1.328 | 1.3389 | 1.105 | 1.5814 | 1.7715 | 1.7787 | 1.7882 | 1.8865
2022-04-16 06:00 | 1.7528 | 1.9065 | 1.9184 | 1.9331 | 1.9501 | 1.1924 | 1.4256 | 1.4349 | 1.4476 | 1.1924 | 1.7338 | 1.9432 | 1.9516 | 1.9627 | 2.0713
2022-04-16 07:00 | 1.7338 | 1.8951 | 1.9117 | 1.932 | 1.9557 | 1.2003 | 1.4416 | 1.4545 | 1.4722 | 1.2003 | 1.5052 | 1.6956 | 1.7072 | 1.7227 | 1.8239
2022-04-16 08:00 | 1.5052 | 1.6629 | 1.6862 | 1.7149 | 1.7483 | 1.0479 | 1.2712 | 1.2895 | 1.3144 | 1.0479 | 1.0775 | 1.2298 | 1.2462 | 1.268 | 1.3533
2022-04-16 09:00 | 1.3186 | 1.4767 | 1.5074 | 1.5449 | 1.5887 | 0.83135 | 1.0257 | 1.0497 | 1.0823 | 0.83135 | 1.3337 | 1.5246 | 1.5461 | 1.5746 | 1.6821
2022-04-16 10:00 | 1.2575 | 1.4219 | 1.4582 | 1.5026 | 1.5543 | 0.64779 | 0.81683 | 0.84512 | 0.88374 | 0.64779 | 1.6576 | 1.8923 | 1.9177 | 1.9514 | 2.0829
2022-04-16 11:00 | 1.0669 | 1.2216 | 1.2601 | 1.3072 | 1.3621 | 0.66684 | 0.84249 | 0.87251 | 0.9135 | 0.66684 | 1.6004 | 1.8318 | 1.8588 | 1.8946 | 2.0255
2022-04-16 12:00 | 1.105 | 1.2615 | 1.2994 | 1.3459 | 1.4 | 0.7621 | 0.95427 | 0.98387 | 1.0243 | 0.7621 | 1.6576 | 1.8946 | 1.9212 | 1.9565 | 2.0899
2022-04-16 13:00 | 1.467 | 1.6454 | 1.6808 | 1.7241 | 1.7747 | 1.0098 | 1.2433 | 1.2709 | 1.3086 | 1.0098 | 1.4861 | 1.7005 | 1.7253 | 1.7583 | 1.8794
2022-04-16 14:00 | 1.3908 | 1.5581 | 1.5908 | 1.6307 | 1.6773 | 0.89547 | 1.1043 | 1.1297 | 1.1645 | 0.89547 | 1.2765 | 1.4638 | 1.4867 | 1.5171 | 1.6236
2022-04-16 15:00 | 1.5623 | 1.7388 | 1.7696 | 1.8073 | 1.8512 | 0.99073 | 1.2142 | 1.2382 | 1.271 | 0.99073 | 0.97168 | 1.1225 | 1.1441 | 1.1728 | 1.2605
2022-04-16 16:00 | 1.8862 | 2.0859 | 2.1162 | 2.1534 | 2.1967 | 1.4861 | 1.7988 | 1.8225 | 1.8548 | 1.4861 | 1.4099 | 1.6089 | 1.6301 | 1.6584 | 1.7697
2022-04-16 17:00 | 2.1504 | 2.3732 | 2.4054 | 2.4448 | 2.4907 | 1.6877 | 2.0395 | 2.0646 | 2.0988 | 1.6877 | 2.4197 | 2.7335 | 2.756 | 2.786 | 2.9548
2022-04-16 18:00 | 2.2673 | 2.5061 | 2.5421 | 2.5861 | 2.6374 | 1.7338 | 2.0993 | 2.1273 | 2.1656 | 1.7338 | 2.4578 | 2.7811 | 2.8062 | 2.8397 | 3.0148
2022-04-16 19:00 | 2.2101 | 2.4545 | 2.4954 | 2.5455 | 2.6039 | 1.6195 | 1.9713 | 2.0033 | 2.0468 | 1.6195 | 2.1529 | 2.4492 | 2.4779 | 2.516 | 2.6799
2022-04-16 20:00 | 2.1148 | 2.3618 | 2.4077 | 2.4638 | 2.5293 | 1.6195 | 1.9784 | 2.0141 | 2.063 | 1.6195 | 2.6102 | 2.9642 | 2.9963 | 3.039 | 3.2336
2022-04-16 21:00 | 2.0386 | 2.2816 | 2.3283 | 2.3854 | 2.452 | 1.5242 | 1.867 | 1.9034 | 1.9532 | 1.5242 | 2.4197 | 2.7536 | 2.7863 | 2.8298 | 3.0148
2022-04-16 22:00 | 1.9662 | 2.1978 | 2.2415 | 2.2949 | 2.3572 | 1.4099 | 1.7276 | 1.7617 | 1.8082 | 1.4099 | 2.2101 | 2.5165 | 2.5471 | 2.5877 | 2.7578
2022-04-16 23:00 | 1.8862 | 2.1034 | 2.1428 | 2.1909 | 2.247 | 1.3337 | 1.6315 | 1.6622 | 1.704 | 1.3337 | 1.81 | 2.0659 | 2.0935 | 2.1301 | 2.2734
2022-04-17 | 1.7909 | 1.9916 | 2.0261 | 2.0684 | 2.1176 | 1.1813 | 1.4446 | 1.4715 | 1.5082 | 1.1813 | 1.81 | 2.0592 | 2.0834 | 2.1155 | 2.2534
2022-04-17 01:00 | 1.7719 | 1.9616 | 1.9912 | 2.0275 | 2.0697 | 1.1622 | 1.4151 | 1.4382 | 1.4697 | 1.1622 | 1.5433 | 1.756 | 1.7768 | 1.8044 | 1.9222
2022-04-17 02:00 | 1.6957 | 1.8676 | 1.8911 | 1.9198 | 1.9532 | 1.0669 | 1.2938 | 1.3121 | 1.337 | 1.0669 | 1.3718 | 1.5569 | 1.5733 | 1.5952 | 1.6967
2022-04-17 03:00 | 1.6576 | 1.8149 | 1.8323 | 1.8536 | 1.8784 | 1.0479 | 1.2627 | 1.2763 | 1.2948 | 1.0479 | 1.5052 | 1.6968 | 1.7089 | 1.7252 | 1.8273
2022-04-17 04:00 | 1.7147 | 1.8662 | 1.8785 | 1.8935 | 1.911 | 1.086 | 1.3004 | 1.3099 | 1.323 | 1.086 | 1.467 | 1.6473 | 1.6559 | 1.6673 | 1.7616
2022-04-17 05:00 | 1.9053 | 2.0669 | 2.0772 | 2.0897 | 2.1043 | 1.1152 | 1.332 | 1.3399 | 1.3508 | 1.1152 | 1.6385 | 1.835 | 1.8422 | 1.8517 | 1.9532
2022-04-17 06:00 | 1.7909 | 1.9474 | 1.9594 | 1.974 | 1.991 | 1.2003 | 1.435 | 1.4443 | 1.457 | 1.2003 | 1.6766 | 1.8797 | 1.8881 | 1.8992 | 2.0046
2022-04-17 07:00 | 1.7147 | 1.8747 | 1.8912 | 1.9115 | 1.9352 | 1.2575 | 1.5091 | 1.522 | 1.5397 | 1.2575 | 1.5242 | 1.7168 | 1.7284 | 1.7438 | 1.8461
2022-04-17 08:00 | 1.4861 | 1.6424 | 1.6658 | 1.6944 | 1.7278 | 1.0346 | 1.2555 | 1.2738 | 1.2987 | 1.0346 | 1.086 | 1.2393 | 1.2557 | 1.2774 | 1.3632
2022-04-17 09:00 | 1.3908 | 1.5543 | 1.585 | 1.6225 | 1.6663 | 0.86107 | 1.0608 | 1.0848 | 1.1174 | 0.86107 | 0.97168 | 1.1223 | 1.1438 | 1.1724 | 1.2599
2022-04-17 10:00 | 1.0669 | 1.2172 | 1.2535 | 1.2979 | 1.3497 | 0.66684 | 0.83934 | 0.86763 | 0.90625 | 0.66684 | 1.3527 | 1.5535 | 1.5789 | 1.6127 | 1.7274
2022-04-17 11:00 | 1.0669 | 1.2216 | 1.2601 | 1.3072 | 1.3621 | 0.57158 | 0.72996 | 0.75997 | 0.80096 | 0.57158 | 1.6385 | 1.8742 | 1.9011 | 1.937 | 2.0699
2022-04-17 12:00 | 0.93358 | 1.0773 | 1.1152 | 1.1616 | 1.2158 | 0.53347 | 0.68418 | 0.71377 | 0.75419 | 0.53347 | 1.5623 | 1.7888 | 1.8153 | 1.8507 | 1.9788
2022-04-17 13:00 | 1.0098 | 1.1541 | 1.1895 | 1.2329 | 1.2834 | 0.59063 | 0.74808 | 0.77569 | 0.81339 | 0.59063 | 1.8481 | 2.1028 | 2.1276 | 2.1606 | 2.3016
2022-04-17 14:00 | 1.2956 | 1.4558 | 1.4884 | 1.5284 | 1.5749 | 0.68589 | 0.85669 | 0.88215 | 0.9169 | 0.68589 | 1.2956 | 1.485 | 1.5078 | 1.5382 | 1.6458
2022-04-17 15:00 | 1.6576 | 1.8411 | 1.8719 | 1.9096 | 1.9536 | 0.95263 | 1.1692 | 1.1932 | 1.226 | 0.95263 | 0.85737 | 0.99547 | 1.0171 | 1.0457 | 1.1272
2022-04-17 16:00 | 1.9752 | 2.1814 | 2.2118 | 2.249 | 2.2923 | 1.3828 | 1.6768 | 1.7005 | 1.7328 | 1.3828 | 1.6195 | 1.8418 | 1.863 | 1.8913 | 2.0141
2022-04-17 17:00 | 2.2863 | 2.5193 | 2.5514 | 2.5908 | 2.6367 | 1.6195 | 1.959 | 1.9841 | 2.0183 | 1.6195 | 2.2482 | 2.5429 | 2.5655 | 2.5954 | 2.7549
2022-04-17 18:00 | 2.2863 | 2.5266 | 2.5626 | 2.6065 | 2.6578 | 1.7147 | 2.0768 | 2.1048 | 2.1431 | 1.7147 | 2.4006 | 2.7175 | 2.7427 | 2.7762 | 2.9481
2022-04-17 19:00 | 2.1643 | 2.4052 | 2.4462 | 2.4962 | 2.5546 | 1.7147 | 2.0839 | 2.1158 | 2.1594 | 1.7147 | 2.6483 | 2.9997 | 3.0284 | 3.0664 | 3.2576
2022-04-17 20:00 | 2.1529 | 2.4028 | 2.4486 | 2.5047 | 2.5702 | 1.6815 | 2.0516 | 2.0874 | 2.1362 | 1.6815 | 2.6864 | 3.0489 | 3.081 | 3.1237 | 3.3224
2022-04-17 21:00 | 2.0767 | 2.3225 | 2.3692 | 2.4263 | 2.493 | 1.5814 | 1.9345 | 1.971 | 2.0207 | 1.5814 | 2.4197 | 2.7536 | 2.7863 | 2.8298 | 3.0148
2022-04-17 22:00 | 2.0196 | 2.2552 | 2.2988 | 2.3522 | 2.4145 | 1.4069 | 1.7241 | 1.7581 | 1.8046 | 1.4069 | 2.2863 | 2.6012 | 2.6318 | 2.6724 | 2.8467
2022-04-17 23:00 | 1.9624 | 2.1853 | 2.2246 | 2.2728 | 2.3289 | 1.2899 | 1.5797 | 1.6104 | 1.6523 | 1.2899 | 1.7147 | 1.9601 | 1.9876 | 2.0242 | 2.1623
2022-04-18 | 1.829 | 2.0326 | 2.0671 | 2.1093 | 2.1586 | 1.2003 | 1.4671 | 1.494 | 1.5307 | 1.2003 | 1.7528 | 1.9957 | 2.0199 | 2.052 | 2.1868
2022-04-18 01:00 | 1.7147 | 1.9002 | 1.9298 | 1.9661 | 2.0083 | 1.105 | 1.3476 | 1.3707 | 1.4022 | 1.105 | 1.4289 | 1.629 | 1.6497 | 1.6773 | 1.7888
2022-04-18 02:00 | 1.7147 | 1.8881 | 1.9116 | 1.9403 | 1.9737 | 1.0288 | 1.2488 | 1.2671 | 1.292 | 1.0288 | 1.3718 | 1.5569 | 1.5733 | 1.5952 | 1.6967
2022-04-18 03:00 | 1.7147 | 1.8763 | 1.8937 | 1.915 | 1.9398 | 1.0098 | 1.2177 | 1.2312 | 1.2498 | 1.0098 | 1.5052 | 1.6968 | 1.7089 | 1.7252 | 1.8273
2022-04-18 04:00 | 1.7147 | 1.8662 | 1.8785 | 1.8935 | 1.911 | 1.086 | 1.3004 | 1.3099 | 1.323 | 1.086 | 1.5433 | 1.732 | 1.7405 | 1.752 | 1.8504
2022-04-18 05:00 | 1.8481 | 2.0055 | 2.0158 | 2.0283 | 2.0429 | 1.1152 | 1.332 | 1.3399 | 1.3508 | 1.1152 | 1.4861 | 1.6656 | 1.6728 | 1.6823 | 1.7754
2022-04-18 06:00 | 1.7528 | 1.9065 | 1.9184 | 1.9331 | 1.9501 | 1.1813 | 1.4125 | 1.4218 | 1.4345 | 1.1813 | 1.6766 | 1.8797 | 1.8881 | 1.8992 | 2.0046
2022-04-18 07:00 | 1.7338 | 1.8951 | 1.9117 | 1.932 | 1.9557 | 1.086 | 1.3065 | 1.3195 | 1.3371 | 1.086 | 1.3337 | 1.5051 | 1.5167 | 1.5321 | 1.6239
2022-04-18 08:00 | 1.6957 | 1.8675 | 1.8909 | 1.9196 | 1.953 | 1.0479 | 1.2712 | 1.2895 | 1.3144 | 1.0479 | 1.1432 | 1.3028 | 1.3192 | 1.341 | 1.4299
2022-04-18 09:00 | 1.6957 | 1.8818 | 1.9125 | 1.95 | 1.9938 | 1.0098 | 1.2365 | 1.2605 | 1.2931 | 1.0098 | 1.0098 | 1.1647 | 1.1862 | 1.2147 | 1.3044
2022-04-18 10:00 | 1.3831 | 1.5569 | 1.5931 | 1.6375 | 1.6893 | 0.87642 | 1.0869 | 1.1152 | 1.1538 | 0.87642 | 1.3146 | 1.5112 | 1.5366 | 1.5703 | 1.683
2022-04-18 11:00 | 1.6004 | 1.7947 | 1.8332 | 1.8803 | 1.9352 | 0.89547 | 1.1126 | 1.1426 | 1.1836 | 0.89547 | 1.1241 | 1.3025 | 1.3295 | 1.3653 | 1.47
2022-04-18 12:00 | 1.5814 | 1.7732 | 1.8111 | 1.8576 | 1.9118 | 1.0288 | 1.2694 | 1.299 | 1.3394 | 1.0288 | 1.6004 | 1.8311 | 1.8577 | 1.893 | 2.0232
2022-04-18 13:00 | 1.5814 | 1.7682 | 1.8036 | 1.8469 | 1.8975 | 1.0479 | 1.2883 | 1.3159 | 1.3536 | 1.0479 | 1.2575 | 1.4465 | 1.4713 | 1.5042 | 1.6128
2022-04-18 14:00 | 1.6195 | 1.8037 | 1.8364 | 1.8763 | 1.9229 | 1.1622 | 1.4194 | 1.4448 | 1.4796 | 1.1622 | 0.99073 | 1.1462 | 1.1691 | 1.1995 | 1.2903
2022-04-18 15:00 | 1.8143 | 2.0095 | 2.0403 | 2.078 | 2.122 | 1.2859 | 1.5629 | 1.587 | 1.6198 | 1.2859 | 1.3146 | 1.5036 | 1.5252 | 1.5539 | 1.6604
2022-04-18 16:00 | 2.0497 | 2.2615 | 2.2919 | 2.3291 | 2.3724 | 1.5533 | 1.8781 | 1.9018 | 1.9341 | 1.5533 | 2.1339 | 2.4134 | 2.4347 | 2.4629 | 2.6141
2022-04-18 17:00 | 2.4387 | 2.683 | 2.7152 | 2.7546 | 2.8005 | 1.9053 | 2.2965 | 2.3216 | 2.3559 | 1.9053 | 2.4768 | 2.797 | 2.8196 | 2.8495 | 3.0215
2022-04-18 18:00 | 2.4578 | 2.7108 | 2.7468 | 2.7908 | 2.842 | 1.9243 | 2.3244 | 2.3524 | 2.3907 | 1.9243 | 2.6674 | 3.014 | 3.0391 | 3.0726 | 3.2592
2022-04-18 19:00 | 2.4006 | 2.6592 | 2.7001 | 2.7502 | 2.8086 | 1.9053 | 2.309 | 2.3409 | 2.3845 | 1.9053 | 2.7245 | 3.0844 | 3.113 | 3.1511 | 3.3465
2022-04-18 20:00 | 2.3054 | 2.5665 | 2.6124 | 2.6685 | 2.7339 | 1.81 | 2.2035 | 2.2392 | 2.2881 | 1.81 | 2.6102 | 2.9642 | 2.9963 | 3.039 | 3.2336
2022-04-18 21:00 | 2.1371 | 2.3874 | 2.4341 | 2.4913 | 2.5579 | 1.6576 | 2.0246 | 2.061 | 2.1107 | 1.6576 | 2.172 | 2.4784 | 2.5111 | 2.5546 | 2.7259
2022-04-18 22:00 | 2.0577 | 2.2961 | 2.3397 | 2.3932 | 2.4555 | 1.4828 | 1.8137 | 1.8478 | 1.8943 | 1.4828 | 2.0196 | 2.3048 | 2.3354 | 2.376 | 2.5356
2022-04-18 23:00 | 1.8481 | 2.0625 | 2.1018 | 2.15 | 2.2061 | 1.2847 | 1.5736 | 1.6043 | 1.6462 | 1.2847 | 1.6766 | 1.9177 | 1.9453 | 1.9819 | 2.1178
2022-04-19 | 1.6905 | 1.8838 | 1.9183 | 1.9605 | 2.0098 | 1.1756 | 1.4379 | 1.4648 | 1.5016 | 1.1756 | 1.5052 | 1.7205 | 1.7446 | 1.7768 | 1.8979
2022-04-19 01:00 | 1.6957 | 1.8797 | 1.9093 | 1.9456 | 1.9879 | 1.0504 | 1.283 | 1.3061 | 1.3377 | 1.0504 | 1.5242 | 1.7349 | 1.7556 | 1.7832 | 1.8999
2022-04-19 02:00 | 1.6957 | 1.8676 | 1.8911 | 1.9198 | 1.9532 | 0.99463 | 1.2083 | 1.2266 | 1.2516 | 0.99463 | 1.3146 | 1.4934 | 1.5098 | 1.5317 | 1.63
2022-04-19 03:00 | 1.5814 | 1.733 | 1.7504 | 1.7717 | 1.7966 | 0.99184 | 1.1965 | 1.2101 | 1.2286 | 0.99184 | 1.467 | 1.6544 | 1.6666 | 1.6828 | 1.7828
2022-04-19 04:00 | 1.6957 | 1.8457 | 1.858 | 1.873 | 1.8905 | 1.0669 | 1.2779 | 1.2874 | 1.3005 | 1.0669 | 1.5623 | 1.7531 | 1.7617 | 1.7731 | 1.8727
2022-04-19 05:00 | 1.6957 | 1.8418 | 1.852 | 1.8645 | 1.8791 | 1.134 | 1.3542 | 1.3622 | 1.3731 | 1.134 | 1.81 | 2.0256 | 2.0327 | 2.0422 | 2.1531
2022-04-19 06:00 | 1.8866 | 2.0502 | 2.0621 | 2.0767 | 2.0938 | 1.3146 | 1.57 | 1.5793 | 1.592 | 1.3146 | 1.6004 | 1.795 | 1.8034 | 1.8145 | 1.9158
2022-04-19 07:00 | 2.1148 | 2.3045 | 2.3211 | 2.3414 | 2.365 | 1.4861 | 1.7792 | 1.7921 | 1.8098 | 1.4861 | 1.6576 | 1.865 | 1.8766 | 1.892 | 2.0016
2022-04-19 08:00 | 2.1339 | 2.3383 | 2.3617 | 2.3904 | 2.4238 | 1.467 | 1.7664 | 1.7846 | 1.8095 | 1.467 | 1.6195 | 1.8321 | 1.8485 | 1.8703 | 1.9853
2022-04-19 09:00 | 2.1339 | 2.3526 | 2.3832 | 2.4208 | 2.4646 | 1.3337 | 1.6192 | 1.6431 | 1.6758 | 1.3337 | 1.3146 | 1.5034 | 1.5249 | 1.5535 | 1.6599
2022-04-19 10:00 | 2.3244 | 2.5682 | 2.6045 | 2.6489 | 2.7006 | 1.3557 | 1.6532 | 1.6814 | 1.7201 | 1.3557 | 1.3337 | 1.5324 | 1.5578 | 1.5915 | 1.7052
2022-04-19 11:00 | 2.2673 | 2.5111 | 2.5496 | 2.5967 | 2.6517 | 1.448 | 1.7653 | 1.7953 | 1.8363 | 1.448 | 1.4289 | 1.6413 | 1.6683 | 1.7041 | 1.8255
2022-04-19 12:00 | 2.2673 | 2.5101 | 2.548 | 2.5945 | 2.6486 | 1.4099 | 1.7195 | 1.7491 | 1.7895 | 1.4099 | 1.3718 | 1.577 | 1.6036 | 1.6389 | 1.7566
2022-04-19 13:00 | 2.191 | 2.4232 | 2.4586 | 2.502 | 2.5525 | 1.4099 | 1.7159 | 1.7435 | 1.7812 | 1.4099 | 1.4289 | 1.637 | 1.6618 | 1.6948 | 1.8127
2022-04-19 14:00 | 2.4197 | 2.6634 | 2.6961 | 2.736 | 2.7826 | 1.5623 | 1.892 | 1.9175 | 1.9523 | 1.5623 | 1.7909 | 2.0355 | 2.0583 | 2.0887 | 2.2235
2022-04-19 15:00 | 2.4768 | 2.7213 | 2.7521 | 2.7898 | 2.8337 | 1.5623 | 1.8894 | 1.9135 | 1.9463 | 1.5623 | 2.0577 | 2.3293 | 2.3509 | 2.3796 | 2.527
2022-04-19 16:00 | 2.4768 | 2.7204 | 2.7508 | 2.7879 | 2.8313 | 1.7172 | 2.0717 | 2.0954 | 2.1278 | 1.7172 | 2.6864 | 3.0274 | 3.0487 | 3.0769 | 3.2584
2022-04-19 17:00 | 2.7245 | 2.99 | 3.0222 | 3.0616 | 3.1075 | 2.0386 | 2.4541 | 2.4792 | 2.5135 | 2.0386 | 3.0103 | 3.3898 | 3.4124 | 3.4423 | 3.6436
2022-04-19 18:00 | 2.7436 | 3.0179 | 3.0538 | 3.0978 | 3.1491 | 2.191 | 2.6395 | 2.6675 | 2.7058 | 2.191 | 3.0675 | 3.4586 | 3.4837 | 3.5172 | 3.7258
2022-04-19 19:00 | 2.7055 | 2.9867 | 3.0276 | 3.0777 | 3.1361 | 2.191 | 2.6466 | 2.6785 | 2.7221 | 2.191 | 3.5057 | 3.9524 | 3.9811 | 4.0192 | 4.2575
2022-04-19 20:00 | 2.5686 | 2.8493 | 2.8951 | 2.9513 | 3.0167 | 2.0958 | 2.5411 | 2.5768 | 2.6257 | 2.0958 | 3.1818 | 3.5994 | 3.6315 | 3.6742 | 3.9001
2022-04-19 21:00 | 2.4901 | 2.7666 | 2.8133 | 2.8704 | 2.9371 | 1.9815 | 2.4072 | 2.4436 | 2.4933 | 1.9815 | 3.0103 | 3.41 | 3.4427 | 3.4861 | 3.7036
2022-04-19 22:00 | 2.3054 | 2.5622 | 2.6058 | 2.6593 | 2.7216 | 1.6606 | 2.0238 | 2.0579 | 2.1044 | 1.6606 | 2.4768 | 2.8129 | 2.8435 | 2.8841 | 3.0689
2022-04-19 23:00 | 2.0235 | 2.2509 | 2.2903 | 2.3384 | 2.3945 | 1.4329 | 1.7487 | 1.7793 | 1.8212 | 1.4329 | 1.9053 | 2.1718 | 2.1993 | 2.236 | 2.3845
2022-04-20 | 1.9243 | 2.1349 | 2.1694 | 2.2117 | 2.2609 | 1.2682 | 1.5472 | 1.5741 | 1.6109 | 1.2682 | 1.81 | 2.0592 | 2.0834 | 2.1155 | 2.2534
2022-04-20 01:00 | 1.829 | 2.023 | 2.0526 | 2.0889 | 2.1311 | 1.1322 | 1.3797 | 1.4028 | 1.4343 | 1.1322 | 1.6004 | 1.8195 | 1.8403 | 1.8679 | 1.9888
2022-04-20 02:00 | 1.7147 | 1.8881 | 1.9116 | 1.9403 | 1.9737 | 1.068 | 1.295 | 1.3133 | 1.3383 | 1.068 | 1.467 | 1.6628 | 1.6792 | 1.701 | 1.8078
2022-04-20 03:00 | 1.6957 | 1.8558 | 1.8732 | 1.8945 | 1.9194 | 1.086 | 1.3077 | 1.3213 | 1.3398 | 1.086 | 1.5242 | 1.7179 | 1.7301 | 1.7463 | 1.8495
2022-04-20 04:00 | 1.829 | 1.989 | 2.0013 | 2.0163 | 2.0338 | 1.1362 | 1.3597 | 1.3692 | 1.3823 | 1.1362 | 1.6004 | 1.7955 | 1.8041 | 1.8155 | 1.9171
2022-04-20 05:00 | 1.9108 | 2.0729 | 2.0831 | 2.0956 | 2.1102 | 1.3225 | 1.5769 | 1.5849 | 1.5958 | 1.3225 | 1.6766 | 1.8773 | 1.8845 | 1.894 | 1.9976
2022-04-20 06:00 | 2.0767 | 2.2545 | 2.2664 | 2.281 | 2.2981 | 1.5433 | 1.8401 | 1.8494 | 1.8621 | 1.5433 | 1.9243 | 2.155 | 2.1633 | 2.1744 | 2.2935
2022-04-20 07:00 | 2.3054 | 2.5092 | 2.5258 | 2.5461 | 2.5697 | 1.8672 | 2.2293 | 2.2423 | 2.2599 | 1.8672 | 1.8481 | 2.0767 | 2.0883 | 2.1038 | 2.2238
2022-04-20 08:00 | 2.3244 | 2.543 | 2.5664 | 2.5951 | 2.6284 | 1.8399 | 2.2068 | 2.225 | 2.25 | 1.8399 | 1.9434 | 2.192 | 2.2084 | 2.2302 | 2.3631
2022-04-20 09:00 | 2.0767 | 2.2912 | 2.3218 | 2.3594 | 2.4032 | 1.448 | 1.7542 | 1.7781 | 1.8108 | 1.448 | 1.2194 | 1.3976 | 1.4191 | 1.4476 | 1.5488
2022-04-20 10:00 | 1.6385 | 1.8313 | 1.8676 | 1.912 | 1.9637 | 0.91452 | 1.1319 | 1.1602 | 1.1988 | 0.91452 | 1.4289 | 1.6382 | 1.6636 | 1.6974 | 1.8163
2022-04-20 11:00 | 1.5294 | 1.7185 | 1.757 | 1.8041 | 1.859 | 0.78115 | 0.97754 | 1.0076 | 1.0485 | 0.78115 | 1.829 | 2.0859 | 2.1129 | 2.1487 | 2.2921
2022-04-20 12:00 | 1.3908 | 1.5685 | 1.6065 | 1.6529 | 1.7071 | 0.62873 | 0.79672 | 0.82631 | 0.86672 | 0.62873 | 1.8672 | 2.1275 | 2.1541 | 2.1894 | 2.3343
2022-04-20 13:00 | 1.3908 | 1.5635 | 1.5989 | 1.6423 | 1.6928 | 0.62848 | 0.7928 | 0.82041 | 0.85811 | 0.62848 | 1.6195 | 1.8487 | 1.8735 | 1.9065 | 2.0349
2022-04-20 14:00 | 1.6957 | 1.8856 | 1.9183 | 1.9582 | 2.0048 | 0.85737 | 1.0593 | 1.0847 | 1.1195 | 0.85737 | 1.5623 | 1.7814 | 1.8043 | 1.8346 | 1.9569
2022-04-20 15:00 | 1.9434 | 2.1481 | 2.1789 | 2.2166 | 2.2606 | 1.1392 | 1.3896 | 1.4136 | 1.4464 | 1.1392 | 0.99073 | 1.1437 | 1.1653 | 1.1939 | 1.2827
2022-04-20 16:00 | 2.191 | 2.4134 | 2.4437 | 2.4809 | 2.5242 | 1.6001 | 1.9335 | 1.9572 | 1.9895 | 1.6001 | 1.7215 | 1.9552 | 1.9765 | 2.0047 | 2.1332
2022-04-20 17:00 | 2.6102 | 2.8672 | 2.8994 | 2.9388 | 2.9847 | 2.0195 | 2.4314 | 2.4565 | 2.4908 | 2.0195 | 2.7099 | 3.056 | 3.0786 | 3.1085 | 3.2933
2022-04-20 18:00 | 2.7151 | 2.9873 | 3.0232 | 3.0672 | 3.1185 | 2.172 | 2.617 | 2.645 | 2.6833 | 2.172 | 3.0865 | 3.4797 | 3.5049 | 3.5384 | 3.7481
2022-04-20 19:00 | 2.7245 | 3.0072 | 3.0481 | 3.0982 | 3.1566 | 2.172 | 2.6241 | 2.656 | 2.6996 | 2.172 | 3.5057 | 3.9524 | 3.9811 | 4.0192 | 4.2575
2022-04-20 20:00 | 2.6102 | 2.894 | 2.9399 | 2.996 | 3.0614 | 2.0386 | 2.4735 | 2.5093 | 2.5582 | 2.0386 | 2.9722 | 3.3665 | 3.3986 | 3.4413 | 3.6557
2022-04-20 21:00 | 2.4387 | 2.7114 | 2.7581 | 2.8153 | 2.8819 | 1.8672 | 2.2722 | 2.3086 | 2.3583 | 1.8672 | 2.8198 | 3.1982 | 3.231 | 3.2744 | 3.4814
2022-04-20 22:00 | 2.3244 | 2.5827 | 2.6263 | 2.6797 | 2.742 | 1.81 | 2.2003 | 2.2344 | 2.2808 | 1.81 | 2.2673 | 2.58 | 2.6106 | 2.6512 | 2.8245
2022-04-20 23:00 | 2.0958 | 2.3286 | 2.3679 | 2.4161 | 2.4722 | 1.519 | 1.8504 | 1.8811 | 1.9229 | 1.519 | 1.9809 | 2.2558 | 2.2834 | 2.32 | 2.4727
2022-04-21 | 1.9053 | 2.1144 | 2.149 | 2.1912 | 2.2404 | 1.2628 | 1.5409 | 1.5678 | 1.6046 | 1.2628 | 2.0386 | 2.3133 | 2.3375 | 2.3696 | 2.5201
2022-04-21 01:00 | 1.7528 | 1.9411 | 1.9707 | 2.007 | 2.0493 | 1.1432 | 1.3926 | 1.4157 | 1.4472 | 1.1432 | 1.5052 | 1.7137 | 1.7344 | 1.762 | 1.8777
2022-04-21 02:00 | 1.7427 | 1.9181 | 1.9416 | 1.9703 | 2.0037 | 1.086 | 1.3163 | 1.3346 | 1.3595 | 1.086 | 1.4099 | 1.5993 | 1.6157 | 1.6375 | 1.7411
2022-04-21 03:00 | 1.7528 | 1.9172 | 1.9346 | 1.9559 | 1.9808 | 1.086 | 1.3077 | 1.3213 | 1.3398 | 1.086 | 1.4861 | 1.6756 | 1.6878 | 1.704 | 1.8051
2022-04-21 04:00 | 1.7909 | 1.9481 | 1.9603 | 1.9753 | 1.9928 | 1.2194 | 1.4579 | 1.4675 | 1.4806 | 1.2194 | 1.6195 | 1.8166 | 1.8252 | 1.8366 | 1.9393
2022-04-21 05:00 | 1.9053 | 2.0669 | 2.0772 | 2.0897 | 2.1043 | 1.288 | 1.5361 | 1.5441 | 1.555 | 1.288 | 1.7147 | 1.9197 | 1.9269 | 1.9364 | 2.042
2022-04-21 06:00 | 2.0767 | 2.2545 | 2.2664 | 2.281 | 2.2981 | 1.481 | 1.7666 | 1.7759 | 1.7886 | 1.481 | 2.2863 | 2.5572 | 2.5656 | 2.5767 | 2.7157
2022-04-21 07:00 | 2.2673 | 2.4683 | 2.4848 | 2.5051 | 2.5288 | 1.7147 | 2.0493 | 2.0622 | 2.0799 | 1.7147 | 2.2673 | 2.5425 | 2.5541 | 2.5695 | 2.7126
2022-04-21 08:00 | 2.4006 | 2.6249 | 2.6483 | 2.6769 | 2.7103 | 1.7147 | 2.059 | 2.0772 | 2.1021 | 1.7147 | 2.0005 | 2.2555 | 2.2719 | 2.2937 | 2.4297
2022-04-21 09:00 | 2.191 | 2.414 | 2.4447 | 2.4822 | 2.526 | 1.3257 | 1.6097 | 1.6337 | 1.6663 | 1.3257 | 1.3527 | 1.5458 | 1.5673 | 1.5958 | 1.7043
2022-04-21 10:00 | 1.7338 | 1.9337 | 1.9699 | 2.0143 | 2.0661 | 0.80021 | 0.99689 | 1.0252 | 1.0638 | 0.80021 | 1.2765 | 1.4688 | 1.4942 | 1.528 | 1.6386
2022-04-21 11:00 | 1.8672 | 2.0813 | 2.1198 | 2.1669 | 2.2218 | 1.2575 | 1.5402 | 1.5703 | 1.6112 | 1.2575 | 1.5623 | 1.7895 | 1.8165 | 1.8523 | 1.981
2022-04-21 12:00 | 2.0005 | 2.2235 | 2.2615 | 2.3079 | 2.3621 | 1.2575 | 1.5395 | 1.5691 | 1.6095 | 1.2575 | 1.5623 | 1.7888 | 1.8153 | 1.8507 | 1.9788
2022-04-21 13:00 | 1.9053 | 2.1162 | 2.1516 | 2.1949 | 2.2454 | 1.2384 | 1.5133 | 1.541 | 1.5787 | 1.2384 | 1.5433 | 1.764 | 1.7888 | 1.8218 | 1.946
2022-04-21 14:00 | 1.8862 | 2.0903 | 2.123 | 2.1629 | 2.2095 | 0.97168 | 1.1943 | 1.2198 | 1.2545 | 0.97168 | 1.448 | 1.6544 | 1.6772 | 1.7076 | 1.8235
2022-04-21 15:00 | 2.123 | 2.3411 | 2.3719 | 2.4096 | 2.4535 | 1.3599 | 1.6503 | 1.6743 | 1.7071 | 1.3599 | 1.1497 | 1.3203 | 1.3419 | 1.3705 | 1.468
2022-04-21 16:00 | 2.3054 | 2.5362 | 2.5665 | 2.6037 | 2.647 | 1.6004 | 1.9338 | 1.9575 | 1.9899 | 1.6004 | 1.9624 | 2.2229 | 2.2441 | 2.2724 | 2.4141
2022-04-21 17:00 | 2.6102 | 2.8672 | 2.8994 | 2.9388 | 2.9847 | 2.1148 | 2.5441 | 2.5692 | 2.6035 | 2.1148 | 2.6761 | 3.0184 | 3.041 | 3.0709 | 3.2538
2022-04-21 18:00 | 2.6102 | 2.8746 | 2.9105 | 2.9545 | 3.0058 | 2.0958 | 2.527 | 2.555 | 2.5933 | 2.0958 | 3.2008 | 3.6068 | 3.632 | 3.6654 | 3.8814
2022-04-21 19:00 | 2.6102 | 2.8843 | 2.9253 | 2.9753 | 3.0337 | 2.0958 | 2.534 | 2.566 | 2.6095 | 2.0958 | 3.2008 | 3.6137 | 3.6424 | 3.6804 | 3.902
2022-04-21 20:00 | 2.4959 | 2.7712 | 2.8171 | 2.8732 | 2.9386 | 1.986 | 2.4114 | 2.4472 | 2.496 | 1.986 | 3.3533 | 3.7899 | 3.822 | 3.8647 | 4.1001
2022-04-21 21:00 | 2.3816 | 2.65 | 2.6967 | 2.7539 | 2.8205 | 1.8672 | 2.2722 | 2.3086 | 2.3583 | 1.8672 | 2.6293 | 2.9865 | 3.0192 | 3.0627 | 3.2592
2022-04-21 22:00 | 2.2863 | 2.5417 | 2.5854 | 2.6388 | 2.7011 | 1.7338 | 2.1103 | 2.1443 | 2.1908 | 1.7338 | 2.4387 | 2.7706 | 2.8012 | 2.8418 | 3.0245
2022-04-21 23:00 | 2.0386 | 2.2672 | 2.3065 | 2.3547 | 2.4108 | 1.4879 | 1.8136 | 1.8443 | 1.8862 | 1.4879 | 2.1529 | 2.447 | 2.4746 | 2.5112 | 2.6733
2022-04-22 | 1.8553 | 2.0608 | 2.0953 | 2.1376 | 2.1868 | 1.2765 | 1.5571 | 1.584 | 1.6208 | 1.2765 | 1.6195 | 1.8475 | 1.8717 | 1.9038 | 2.0312
2022-04-22 01:00 | 1.7338 | 1.9207 | 1.9503 | 1.9865 | 2.0288 | 1.1374 | 1.3858 | 1.4089 | 1.4404 | 1.1374 | 1.7528 | 1.9889 | 2.0097 | 2.0372 | 2.1666
2022-04-22 02:00 | 1.81 | 1.9905 | 2.0139 | 2.0426 | 2.0761 | 1.0669 | 1.2938 | 1.3121 | 1.337 | 1.0669 | 1.6957 | 1.9168 | 1.9333 | 1.9551 | 2.0744
2022-04-22 03:00 | 1.7909 | 1.9582 | 1.9756 | 1.9969 | 2.0217 | 1.086 | 1.3077 | 1.3213 | 1.3398 | 1.086 | 1.5433 | 1.7391 | 1.7513 | 1.7675 | 1.8717
2022-04-22 04:00 | 1.9243 | 2.0914 | 2.1036 | 2.1186 | 2.1361 | 1.1695 | 1.399 | 1.4086 | 1.4217 | 1.1695 | 1.6385 | 1.8378 | 1.8464 | 1.8578 | 1.9615
2022-04-22 05:00 | 2.0386 | 2.2102 | 2.2204 | 2.233 | 2.2476 | 1.3552 | 1.6155 | 1.6234 | 1.6343 | 1.3552 | 1.7528 | 1.962 | 1.9692 | 1.9787 | 2.0865
2022-04-22 06:00 | 2.1148 | 2.2954 | 2.3074 | 2.322 | 2.339 | 1.6393 | 1.9536 | 1.9629 | 1.9756 | 1.6393 | 2.0767 | 2.3243 | 2.3327 | 2.3438 | 2.4713
2022-04-22 07:00 | 2.2863 | 2.4887 | 2.5053 | 2.5256 | 2.5493 | 1.6576 | 1.9818 | 1.9947 | 2.0123 | 1.6576 | 1.9815 | 2.2249 | 2.2365 | 2.252 | 2.3793
2022-04-22 08:00 | 2.1339 | 2.3383 | 2.3617 | 2.3904 | 2.4238 | 1.4259 | 1.7177 | 1.736 | 1.7609 | 1.4259 | 1.3527 | 1.5357 | 1.5521 | 1.5739 | 1.6743
2022-04-22 09:00 | 1.829 | 2.0251 | 2.0557 | 2.0933 | 2.1371 | 1.035 | 1.2664 | 1.2903 | 1.323 | 1.035 | 0.87642 | 1.0165 | 1.038 | 1.0665 | 1.1488
2022-04-22 10:00 | 1.81 | 2.0155 | 2.0518 | 2.0962 | 2.1479 | 1.0669 | 1.312 | 1.3403 | 1.3789 | 1.0669 | 1.1622 | 1.3418 | 1.3672 | 1.401 | 1.5052
2022-04-22 11:00 | 1.9053 | 2.1222 | 2.1607 | 2.2078 | 2.2627 | 1.0315 | 1.2732 | 1.3033 | 1.3442 | 1.0315 | 1.5242 | 1.7472 | 1.7741 | 1.8099 | 1.9366
2022-04-22 12:00 | 1.8672 | 2.0802 | 2.1182 | 2.1646 | 2.2188 | 0.93358 | 1.1568 | 1.1864 | 1.2269 | 0.93358 | 1.7719 | 2.0216 | 2.0482 | 2.0836 | 2.2232
2022-04-22 13:00 | 2.0196 | 2.239 | 2.2744 | 2.3177 | 2.3683 | 1.2003 | 1.4683 | 1.4959 | 1.5336 | 1.2003 | 1.105 | 1.2771 | 1.3019 | 1.3348 | 1.435
2022-04-22 14:00 | 2.1148 | 2.3359 | 2.3686 | 2.4085 | 2.4551 | 1.2956 | 1.5769 | 1.6024 | 1.6372 | 1.2956 | 1.2384 | 1.4215 | 1.4443 | 1.4747 | 1.5791
2022-04-22 15:00 | 2.0767 | 2.2914 | 2.3222 | 2.3599 | 2.4039 | 1.1813 | 1.4393 | 1.4633 | 1.4961 | 1.1813 | 0.99073 | 1.1437 | 1.1653 | 1.1939 | 1.2827
2022-04-22 16:00 | 2.2482 | 2.4748 | 2.5051 | 2.5423 | 2.5856 | 1.6765 | 2.0237 | 2.0474 | 2.0798 | 1.6765 | 2.0005 | 2.2652 | 2.2865 | 2.3147 | 2.4585
2022-04-22 17:00 | 2.6102 | 2.8672 | 2.8994 | 2.9388 | 2.9847 | 2.1101 | 2.5386 | 2.5637 | 2.5979 | 2.1101 | 2.7626 | 3.1146 | 3.1371 | 3.1671 | 3.3548
2022-04-22 18:00 | 2.6483 | 2.9155 | 2.9515 | 2.9954 | 3.0467 | 2.172 | 2.617 | 2.645 | 2.6833 | 2.172 | 2.8769 | 3.2468 | 3.272 | 3.3055 | 3.5036
2022-04-22 19:00 | 2.6102 | 2.8843 | 2.9253 | 2.9753 | 3.0337 | 2.0767 | 2.5115 | 2.5434 | 2.587 | 2.0767 | 3.258 | 3.6772 | 3.7059 | 3.744 | 3.9686
2022-04-22 20:00 | 2.6102 | 2.894 | 2.9399 | 2.996 | 3.0614 | 2.0386 | 2.4735 | 2.5093 | 2.5582 | 2.0386 | 3.0294 | 3.43 | 3.4621 | 3.5048 | 3.7224
2022-04-22 21:00 | 2.3816 | 2.65 | 2.6967 | 2.7539 | 2.8205 | 2.0386 | 2.4747 | 2.5111 | 2.5609 | 2.0386 | 3.0865 | 3.4947 | 3.5274 | 3.5708 | 3.7925
2022-04-22 22:00 | 2.3244 | 2.5827 | 2.6263 | 2.6797 | 2.742 | 1.8209 | 2.2132 | 2.2472 | 2.2937 | 1.8209 | 3.0865 | 3.4904 | 3.521 | 3.5617 | 3.7799
2022-04-22 23:00 | 2.2673 | 2.5128 | 2.5521 | 2.6003 | 2.6564 | 1.6004 | 1.9466 | 1.9773 | 2.0192 | 1.6004 | 2.4197 | 2.7434 | 2.771 | 2.8076 | 2.9844
2022-04-23 | 2.0562 | 2.2767 | 2.3112 | 2.3534 | 2.4026 | 1.3742 | 1.6725 | 1.6994 | 1.7361 | 1.3742 | 1.9053 | 2.1651 | 2.1893 | 2.2214 | 2.3645
2022-04-23 01:00 | 2.0005 | 2.2072 | 2.2368 | 2.2731 | 2.3154 | 1.2759 | 1.5494 | 1.5725 | 1.6041 | 1.2759 | 1.6957 | 1.9254 | 1.9462 | 1.9737 | 2.0999
2022-04-23 02:00 | 1.9624 | 2.1542 | 2.1776 | 2.2063 | 2.2398 | 1.2003 | 1.4513 | 1.4696 | 1.4946 | 1.2003 | 1.5814 | 1.7898 | 1.8062 | 1.8281 | 1.9411
2022-04-23 03:00 | 1.8411 | 2.012 | 2.0294 | 2.0508 | 2.0756 | 1.1813 | 1.4202 | 1.4338 | 1.4524 | 1.1813 | 1.6766 | 1.8873 | 1.8995 | 1.9157 | 2.0273
2022-04-23 04:00 | 1.829 | 1.989 | 2.0013 | 2.0163 | 2.0338 | 1.2003 | 1.4354 | 1.445 | 1.458 | 1.2003 | 1.5607 | 1.7513 | 1.7599 | 1.7713 | 1.8707
2022-04-23 05:00 | 1.8862 | 2.0465 | 2.0567 | 2.0692 | 2.0838 | 1.2345 | 1.4729 | 1.4809 | 1.4918 | 1.2345 | 1.7338 | 1.9409 | 1.948 | 1.9576 | 2.0643
2022-04-23 06:00 | 1.9053 | 2.0703 | 2.0822 | 2.0968 | 2.1138 | 1.3367 | 1.5961 | 1.6054 | 1.6181 | 1.3367 | 1.8672 | 2.0914 | 2.0998 | 2.1109 | 2.2268
2022-04-23 07:00 | 1.9243 | 2.0998 | 2.1164 | 2.1367 | 2.1604 | 1.478 | 1.7696 | 1.7825 | 1.8002 | 1.478 | 1.8672 | 2.0979 | 2.1095 | 2.1249 | 2.246
2022-04-23 08:00 | 1.9434 | 2.1336 | 2.157 | 2.1857 | 2.2191 | 1.4861 | 1.7889 | 1.8071 | 1.8321 | 1.4861 | 1.9243 | 2.1708 | 2.1872 | 2.209 | 2.3409
2022-04-23 09:00 | 1.8776 | 2.0772 | 2.1079 | 2.1455 | 2.1892 | 1.3337 | 1.6192 | 1.6431 | 1.6758 | 1.3337 | 1.467 | 1.6728 | 1.6943 | 1.7229 | 1.8377
2022-04-23 10:00 | 1.6957 | 1.8927 | 1.929 | 1.9734 | 2.0251 | 1.1432 | 1.402 | 1.4303 | 1.4689 | 1.1432 | 1.0479 | 1.2148 | 1.2402 | 1.2739 | 1.3719
2022-04-23 11:00 | 1.6957 | 1.8971 | 1.9356 | 1.9827 | 2.0376 | 1.2003 | 1.4727 | 1.5027 | 1.5437 | 1.2003 | 1.0669 | 1.239 | 1.266 | 1.3018 | 1.4033
2022-04-23 12:00 | 1.81 | 2.0188 | 2.0568 | 2.1032 | 2.1574 | 1.2137 | 1.4878 | 1.5174 | 1.5578 | 1.2137 | 1.1241 | 1.3018 | 1.3284 | 1.3637 | 1.4677
2022-04-23 13:00 | 1.829 | 2.0343 | 2.0697 | 2.113 | 2.1636 | 1.2194 | 1.4908 | 1.5184 | 1.5561 | 1.2194 | 1.1622 | 1.3406 | 1.3654 | 1.3984 | 1.5017
2022-04-23 14:00 | 1.7528 | 1.947 | 1.9797 | 2.0196 | 2.0662 | 1.086 | 1.3294 | 1.3548 | 1.3896 | 1.086 | 1.2384 | 1.4215 | 1.4443 | 1.4747 | 1.5791
2022-04-23 15:00 | 1.6576 | 1.8411 | 1.8719 | 1.9096 | 1.9536 | 1.2384 | 1.5068 | 1.5308 | 1.5636 | 1.2384 | 0.99073 | 1.1437 | 1.1653 | 1.1939 | 1.2827
2022-04-23 16:00 | 2.1159 | 2.3326 | 2.363 | 2.4001 | 2.4435 | 1.5433 | 1.8663 | 1.89 | 1.9223 | 1.5433 | 1.8481 | 2.0958 | 2.1171 | 2.1454 | 2.2808
2022-04-23 17:00 | 2.4959 | 2.7444 | 2.7766 | 2.816 | 2.8619 | 1.9246 | 2.3193 | 2.3444 | 2.3787 | 1.9246 | 2.6293 | 2.9664 | 2.9889 | 3.0189 | 3.1992
2022-04-23 18:00 | 2.534 | 2.7927 | 2.8286 | 2.8726 | 2.9239 | 2.0386 | 2.4594 | 2.4875 | 2.5257 | 2.0386 | 2.7817 | 3.141 | 3.1662 | 3.1996 | 3.3925
2022-04-23 19:00 | 2.534 | 2.8025 | 2.8434 | 2.8935 | 2.9519 | 2.0386 | 2.4665 | 2.4984 | 2.542 | 2.0386 | 2.8198 | 3.1902 | 3.2189 | 3.257 | 3.4576
2022-04-23 20:00 | 2.4006 | 2.6689 | 2.7147 | 2.7708 | 2.8363 | 1.9624 | 2.3835 | 2.4193 | 2.4681 | 1.9624 | 2.9341 | 3.3241 | 3.3563 | 3.3989 | 3.6113
2022-04-23 21:00 | 2.3816 | 2.65 | 2.6967 | 2.7539 | 2.8205 | 1.829 | 2.2271 | 2.2636 | 2.3133 | 1.829 | 2.4768 | 2.8171 | 2.8499 | 2.8933 | 3.0815
2022-04-23 22:00 | 2.1339 | 2.378 | 2.4216 | 2.475 | 2.5373 | 1.6957 | 2.0653 | 2.0993 | 2.1458 | 1.6957 | 2.3625 | 2.6859 | 2.7165 | 2.7571 | 2.9356
2022-04-23 23:00 | 2.0767 | 2.3081 | 2.3474 | 2.3956 | 2.4517 | 1.5433 | 1.8791 | 1.9097 | 1.9516 | 1.5433 | 1.9815 | 2.2565 | 2.284 | 2.3206 | 2.4734
2022-04-24 | 1.9053 | 2.1144 | 2.149 | 2.1912 | 2.2404 | 1.3718 | 1.6696 | 1.6965 | 1.7333 | 1.3718 | 1.7909 | 2.0381 | 2.0622 | 2.0944 | 2.2312
2022-04-24 01:00 | 1.814 | 2.0068 | 2.0364 | 2.0727 | 2.1149 | 1.2356 | 1.5018 | 1.5249 | 1.5564 | 1.2356 | 1.5814 | 1.7984 | 1.8191 | 1.8467 | 1.9666
2022-04-24 02:00 | 1.7147 | 1.8881 | 1.9116 | 1.9403 | 1.9737 | 1.1241 | 1.3613 | 1.3796 | 1.4046 | 1.1241 | 1.6195 | 1.8322 | 1.8486 | 1.8704 | 1.9855
2022-04-24 03:00 | 1.6576 | 1.8149 | 1.8323 | 1.8536 | 1.8784 | 1.0972 | 1.321 | 1.3345 | 1.3531 | 1.0972 | 1.6004 | 1.8026 | 1.8148 | 1.831 | 1.9384
2022-04-24 04:00 | 1.6766 | 1.8253 | 1.8375 | 1.8525 | 1.87 | 1.1432 | 1.3679 | 1.3775 | 1.3905 | 1.1432 | 1.467 | 1.6473 | 1.6559 | 1.6673 | 1.7616
2022-04-24 05:00 | 1.7147 | 1.8622 | 1.8725 | 1.885 | 1.8996 | 1.1277 | 1.3468 | 1.3548 | 1.3657 | 1.1277 | 1.829 | 2.0467 | 2.0539 | 2.0634 | 2.1754
2022-04-24 06:00 | 1.7338 | 1.886 | 1.898 | 1.9126 | 1.9296 | 1.2384 | 1.48 | 1.4893 | 1.502 | 1.2384 | 1.5433 | 1.7315 | 1.7399 | 1.751 | 1.8491
2022-04-24 07:00 | 1.7719 | 1.9361 | 1.9526 | 1.9729 | 1.9966 | 1.2384 | 1.4866 | 1.4995 | 1.5172 | 1.2384 | 1.7528 | 1.9708 | 1.9825 | 1.9979 | 2.1127
2022-04-24 08:00 | 1.7719 | 1.9494 | 1.9728 | 2.0015 | 2.0348 | 1.2956 | 1.5638 | 1.5821 | 1.607 | 1.2956 | 1.5052 | 1.7051 | 1.7215 | 1.7432 | 1.852
2022-04-24 09:00 | 1.4583 | 1.6268 | 1.6574 | 1.695 | 1.7388 | 1.1035 | 1.3472 | 1.3711 | 1.4038 | 1.1035 | 1.0462 | 1.2052 | 1.2267 | 1.2552 | 1.3469
2022-04-24 10:00 | 1.5193 | 1.7032 | 1.7395 | 1.7839 | 1.8356 | 1.0831 | 1.3311 | 1.3594 | 1.398 | 1.0831 | 0.98109 | 1.1405 | 1.1659 | 1.1997 | 1.294
2022-04-24 11:00 | 1.5803 | 1.7731 | 1.8116 | 1.8587 | 1.9136 | 1.0627 | 1.3102 | 1.3402 | 1.3812 | 1.0627 | 0.91596 | 1.0712 | 1.0982 | 1.134 | 1.2272
2022-04-24 12:00 | 1.6413 | 1.8376 | 1.8755 | 1.9219 | 1.9761 | 1.0424 | 1.2853 | 1.3149 | 1.3554 | 1.0424 | 0.85082 | 0.99811 | 1.0247 | 1.06 | 1.149
2022-04-24 13:00 | 1.7022 | 1.8981 | 1.9335 | 1.9768 | 2.0273 | 1.022 | 1.2577 | 1.2853 | 1.323 | 1.022 | 0.78569 | 0.9222 | 0.947 | 0.97995 | 1.0626
2022-04-24 14:00 | 1.829 | 2.0289 | 2.0615 | 2.1015 | 2.1481 | 1.2608 | 1.5359 | 1.5613 | 1.5961 | 1.2608 | 1.6576 | 1.8872 | 1.9101 | 1.9405 | 2.068
2022-04-24 15:00 | 1.8862 | 2.0867 | 2.1175 | 2.1552 | 2.1992 | 1.2956 | 1.5743 | 1.5984 | 1.6312 | 1.2956 | 1.6766 | 1.9059 | 1.9275 | 1.9561 | 2.0826
2022-04-24 16:00 | 2.1148 | 2.3315 | 2.3619 | 2.399 | 2.4424 | 1.5408 | 1.8634 | 1.8871 | 1.9194 | 1.5408 | 1.9243 | 2.1805 | 2.2018 | 2.2301 | 2.3696
2022-04-24 17:00 | 2.4768 | 2.7239 | 2.7561 | 2.7955 | 2.8414 | 1.897 | 2.2868 | 2.3119 | 2.3462 | 1.897 | 2.6674 | 3.0087 | 3.0313 | 3.0612 | 3.2437
2022-04-24 18:00 | 2.4959 | 2.7518 | 2.7877 | 2.8317 | 2.883 | 2.0005 | 2.4144 | 2.4424 | 2.4807 | 2.0005 | 2.915 | 3.2892 | 3.3144 | 3.3478 | 3.5481
2022-04-24 19:00 | 2.4959 | 2.7615 | 2.8024 | 2.8525 | 2.9109 | 2.0005 | 2.4215 | 2.4534 | 2.497 | 2.0005 | 3.1818 | 3.5925 | 3.6212 | 3.6593 | 3.8797
2022-04-24 20:00 | 2.3816 | 2.6484 | 2.6942 | 2.7504 | 2.8158 | 1.8481 | 2.2485 | 2.2842 | 2.3331 | 1.8481 | 3.0484 | 3.4512 | 3.4833 | 3.526 | 3.7446
2022-04-24 21:00 | 2.3435 | 2.6091 | 2.6558 | 2.7129 | 2.7796 | 1.7909 | 2.1821 | 2.2185 | 2.2683 | 1.7909 | 2.7817 | 3.1559 | 3.1886 | 3.2321 | 3.437
2022-04-24 22:00 | 2.191 | 2.4394 | 2.483 | 2.5364 | 2.5987 | 1.6004 | 1.9527 | 1.9868 | 2.0333 | 1.6004 | 2.2482 | 2.5589 | 2.5894 | 2.6301 | 2.8023
2022-04-24 23:00 | 2.1148 | 2.3491 | 2.3884 | 2.4365 | 2.4927 | 1.499 | 1.8268 | 1.8575 | 1.8994 | 1.499 | 2.3625 | 2.6799 | 2.7075 | 2.7441 | 2.9178
2022-04-25 | 1.9815 | 2.1963 | 2.2308 | 2.2731 | 2.3223 | 1.3527 | 1.6471 | 1.674 | 1.7108 | 1.3527 | 1.7147 | 1.9534 | 1.9775 | 2.0097 | 2.1423
2022-04-25 01:00 | 1.8862 | 2.0844 | 2.114 | 2.1503 | 2.1925 | 1.1981 | 1.4575 | 1.4806 | 1.5122 | 1.1981 | 1.9053 | 2.1583 | 2.1791 | 2.2066 | 2.3443
2022-04-25 02:00 | 1.7909 | 1.97 | 1.9934 | 2.0221 | 2.0556 | 1.1241 | 1.3613 | 1.3796 | 1.4046 | 1.1241 | 1.6957 | 1.9168 | 1.9333 | 1.9551 | 2.0744
2022-04-25 03:00 | 1.81 | 1.9786 | 1.996 | 2.0173 | 2.0422 | 1.105 | 1.3302 | 1.3438 | 1.3623 | 1.105 | 1.7338 | 1.9508 | 1.963 | 1.9792 | 2.0939
2022-04-25 04:00 | 1.8862 | 2.0504 | 2.0627 | 2.0777 | 2.0952 | 1.1596 | 1.3873 | 1.3969 | 1.41 | 1.1596 | 1.7719 | 1.986 | 1.9946 | 2.006 | 2.1171
2022-04-25 05:00 | 1.8862 | 2.0465 | 2.0567 | 2.0692 | 2.0838 | 1.2344 | 1.4728 | 1.4808 | 1.4917 | 1.2344 | 1.8672 | 2.0891 | 2.0962 | 2.1058 | 2.2198
2022-04-25 06:00 | 1.9499 | 2.1182 | 2.1301 | 2.1447 | 2.1618 | 1.3283 | 1.5861 | 1.5954 | 1.6082 | 1.3283 | 1.7719 | 1.9856 | 1.9939 | 2.005 | 2.1157
2022-04-25 07:00 | 2.0005 | 2.1817 | 2.1983 | 2.2186 | 2.2422 | 1.4289 | 1.7117 | 1.7246 | 1.7423 | 1.4289 | 1.8862 | 2.119 | 2.1307 | 2.1461 | 2.2682
2022-04-25 08:00 | 1.9815 | 2.1746 | 2.198 | 2.2266 | 2.26 | 1.4289 | 1.7214 | 1.7396 | 1.7645 | 1.4289 | 2.1148 | 2.3826 | 2.399 | 2.4207 | 2.5631
2022-04-25 09:00 | 1.9624 | 2.1684 | 2.199 | 2.2366 | 2.2804 | 1.4099 | 1.7092 | 1.7331 | 1.7658 | 1.4099 | 1.7909 | 2.0327 | 2.0542 | 2.0828 | 2.2154
2022-04-25 10:00 | 1.81 | 2.0155 | 2.0518 | 2.0962 | 2.1479 | 1.1965 | 1.465 | 1.4933 | 1.5319 | 1.1965 | 1.1432 | 1.3206 | 1.346 | 1.3798 | 1.483
2022-04-25 11:00 | 1.6576 | 1.8561 | 1.8946 | 1.9417 | 1.9966 | 1.1813 | 1.4502 | 1.4802 | 1.5212 | 1.1813 | 1.1241 | 1.3025 | 1.3295 | 1.3653 | 1.47
2022-04-25 12:00 | 1.9434 | 2.1621 | 2.2001 | 2.2465 | 2.3007 | 1.2003 | 1.472 | 1.5015 | 1.542 | 1.2003 | 1.2003 | 1.3865 | 1.4131 | 1.4484 | 1.5566
2022-04-25 13:00 | 1.9624 | 2.1776 | 2.213 | 2.2563 | 2.3068 | 1.448 | 1.7609 | 1.7885 | 1.8262 | 1.448 | 1.4099 | 1.6158 | 1.6406 | 1.6736 | 1.7905
2022-04-25 14:00 | 2.1148 | 2.3359 | 2.3686 | 2.4085 | 2.4551 | 1.448 | 1.757 | 1.7825 | 1.8172 | 1.448 | 1.6957 | 1.9296 | 1.9525 | 1.9828 | 2.1124
2022-04-25 15:00 | 2.2291 | 2.4552 | 2.486 | 2.5237 | 2.5676 | 1.6852 | 2.0347 | 2.0587 | 2.0915 | 1.6852 | 2.2673 | 2.5622 | 2.5838 | 2.6125 | 2.7714
2022-04-25 16:00 | 2.4768 | 2.7204 | 2.7508 | 2.7879 | 2.8313 | 1.8328 | 2.2083 | 2.232 | 2.2643 | 1.8328 | 2.7626 | 3.1121 | 3.1334 | 3.1616 | 3.3473
2022-04-25 17:00 | 2.7697 | 3.0386 | 3.0707 | 3.1101 | 3.156 | 2.3435 | 2.8142 | 2.8393 | 2.8736 | 2.3435 | 3.2961 | 3.7074 | 3.73 | 3.7599 | 3.9769
2022-04-25 18:00 | 2.8198 | 3.0997 | 3.1357 | 3.1797 | 3.231 | 2.3025 | 2.7712 | 2.7992 | 2.8375 | 2.3025 | 3.5819 | 4.0302 | 4.0554 | 4.0888 | 4.3258
2022-04-25 19:00 | 2.7055 | 2.9867 | 3.0276 | 3.0777 | 3.1361 | 2.3244 | 2.8041 | 2.8361 | 2.8796 | 2.3244 | 3.4295 | 3.8678 | 3.8964 | 3.9345 | 4.1686
2022-04-25 20:00 | 2.553 | 2.8326 | 2.8785 | 2.9346 | 3 | 2.1148 | 2.5636 | 2.5993 | 2.6482 | 2.1148 | 3.8105 | 4.298 | 4.3302 | 4.3729 | 4.6334
2022-04-25 21:00 | 2.3625 | 2.6295 | 2.6762 | 2.7334 | 2.8 | 1.9053 | 2.3172 | 2.3536 | 2.4033 | 1.9053 | 2.8769 | 3.2618 | 3.2945 | 3.3379 | 3.5481
2022-04-25 22:00 | 2.1148 | 2.3575 | 2.4011 | 2.4546 | 2.5169 | 1.7338 | 2.1103 | 2.1443 | 2.1908 | 1.7338 | 2.6102 | 2.9611 | 2.9917 | 3.0323 | 3.2244
2022-04-25 23:00 | 1.9868 | 2.2115 | 2.2509 | 2.299 | 2.3551 | 1.4444 | 1.7622 | 1.7929 | 1.8348 | 1.4444 | 1.9053 | 2.1718 | 2.1993 | 2.236 | 2.3845
2022-04-26 | 1.829 | 2.0326 | 2.0671 | 2.1093 | 2.1586 | 1.2575 | 1.5346 | 1.5615 | 1.5983 | 1.2575 | 1.6195 | 1.8475 | 1.8717 | 1.9038 | 2.0312
2022-04-26 01:00 | 1.7338 | 1.9207 | 1.9503 | 1.9865 | 2.0288 | 1.1127 | 1.3566 | 1.3797 | 1.4113 | 1.1127 | 1.6576 | 1.8831 | 1.9038 | 1.9314 | 2.0555
2022-04-26 02:00 | 1.7338 | 1.9086 | 1.932 | 1.9607 | 1.9942 | 1.105 | 1.3388 | 1.3571 | 1.3821 | 1.105 | 1.4289 | 1.6204 | 1.6369 | 1.6587 | 1.7634
2022-04-26 03:00 | 1.6766 | 1.8353 | 1.8528 | 1.8741 | 1.8989 | 1.0781 | 1.2984 | 1.312 | 1.3305 | 1.0781 | 1.5052 | 1.6968 | 1.7089 | 1.7252 | 1.8273
2022-04-26 04:00 | 1.7414 | 1.8949 | 1.9071 | 1.9221 | 1.9396 | 1.1432 | 1.3679 | 1.3775 | 1.3905 | 1.1432 | 1.5433 | 1.732 | 1.7405 | 1.752 | 1.8504
2022-04-26 05:00 | 1.8884 | 2.0488 | 2.0591 | 2.0716 | 2.0862 | 1.3026 | 1.5534 | 1.5614 | 1.5722 | 1.3026 | 2.0767 | 2.322 | 2.3291 | 2.3387 | 2.4642
2022-04-26 06:00 | 2.2291 | 2.4182 | 2.4302 | 2.4448 | 2.4618 | 1.664 | 1.9827 | 1.992 | 2.0047 | 1.664 | 2.2291 | 2.4937 | 2.5021 | 2.5132 | 2.649
2022-04-26 07:00 | 2.5911 | 2.8162 | 2.8328 | 2.8531 | 2.8768 | 1.9815 | 2.3644 | 2.3773 | 2.395 | 1.9815 | 2.5721 | 2.8812 | 2.8929 | 2.9083 | 3.0682
2022-04-26 08:00 | 2.5149 | 2.7477 | 2.7711 | 2.7997 | 2.8331 | 1.8182 | 2.1812 | 2.1995 | 2.2244 | 1.8182 | 2.534 | 2.8484 | 2.8648 | 2.8865 | 3.0519
2022-04-26 09:00 | 2.2863 | 2.5163 | 2.547 | 2.5845 | 2.6283 | 1.3718 | 1.6642 | 1.6881 | 1.7208 | 1.3718 | 1.3527 | 1.5458 | 1.5673 | 1.5958 | 1.7043
2022-04-26 10:00 | 2.3054 | 2.5477 | 2.584 | 2.6284 | 2.6801 | 1.3908 | 1.6946 | 1.7229 | 1.7615 | 1.3908 | 1.2956 | 1.49 | 1.5154 | 1.5492 | 1.6608
2022-04-26 11:00 | 2.3816 | 2.634 | 2.6724 | 2.7195 | 2.7745 | 1.3527 | 1.6528 | 1.6828 | 1.7238 | 1.3527 | 1.3527 | 1.5566 | 1.5836 | 1.6194 | 1.7366
2022-04-26 12:00 | 2.2101 | 2.4487 | 2.4866 | 2.5331 | 2.5872 | 1.2765 | 1.562 | 1.5916 | 1.632 | 1.2765 | 0.99073 | 1.1536 | 1.1802 | 1.2155 | 1.3122
2022-04-26 13:00 | 2.1148 | 2.3413 | 2.3767 | 2.4201 | 2.4706 | 1.2575 | 1.5359 | 1.5635 | 1.6012 | 1.2575 | 1.1432 | 1.3194 | 1.3442 | 1.3772 | 1.4794
2022-04-26 14:00 | 2.1345 | 2.357 | 2.3897 | 2.4296 | 2.4762 | 1.2956 | 1.5769 | 1.6024 | 1.6372 | 1.2956 | 1.2765 | 1.4638 | 1.4867 | 1.5171 | 1.6236
2022-04-26 15:00 | 2.3816 | 2.6189 | 2.6497 | 2.6874 | 2.7314 | 1.467 | 1.7769 | 1.8009 | 1.8337 | 1.467 | 1.467 | 1.673 | 1.6946 | 1.7232 | 1.8382
2022-04-26 16:00 | 2.4959 | 2.7409 | 2.7712 | 2.8084 | 2.8517 | 1.7719 | 2.1364 | 2.1601 | 2.1924 | 1.7719 | 2.7055 | 3.0486 | 3.0698 | 3.0981 | 3.2806
2022-04-26 17:00 | 2.7626 | 3.031 | 3.0632 | 3.1025 | 3.1485 | 2.2341 | 2.685 | 2.7101 | 2.7444 | 2.2341 | 3.2961 | 3.7074 | 3.73 | 3.7599 | 3.9769
2022-04-26 18:00 | 2.8007 | 3.0793 | 3.1152 | 3.1592 | 3.2105 | 2.3054 | 2.7745 | 2.8026 | 2.8408 | 2.3054 | 3.3342 | 3.755 | 3.7802 | 3.8136 | 4.0369
2022-04-26 19:00 | 2.7626 | 3.0481 | 3.089 | 3.1391 | 3.1975 | 2.2482 | 2.7141 | 2.746 | 2.7896 | 2.2482 | 3.4104 | 3.8466 | 3.8752 | 3.9133 | 4.1464
2022-04-26 20:00 | 2.6102 | 2.894 | 2.9399 | 2.996 | 3.0614 | 2.1148 | 2.5636 | 2.5993 | 2.6482 | 2.1148 | 3.4104 | 3.8534 | 3.8856 | 3.9283 | 4.1668
2022-04-26 21:00 | 2.4176 | 2.6887 | 2.7354 | 2.7925 | 2.8592 | 1.9915 | 2.4191 | 2.4555 | 2.5053 | 1.9915 | 3.3914 | 3.8334 | 3.8661 | 3.9096 | 4.148
2022-04-26 22:00 | 2.2907 | 2.5464 | 2.5901 | 2.6435 | 2.7058 | 1.6766 | 2.0428 | 2.0768 | 2.1233 | 1.6766 | 2.4578 | 2.7918 | 2.8223 | 2.863 | 3.0467
2022-04-26 23:00 | 2.0386 | 2.2672 | 2.3065 | 2.3547 | 2.4108 | 1.5433 | 1.8791 | 1.9097 | 1.9516 | 1.5433 | 1.9434 | 2.2141 | 2.2417 | 2.2783 | 2.4289
2022-04-27 | 1.8173 | 2.02 | 2.0545 | 2.0967 | 2.146 | 1.2384 | 1.5121 | 1.539 | 1.5757 | 1.2384 | 1.81 | 2.0592 | 2.0834 | 2.1155 | 2.2534
2022-04-27 01:00 | 1.6957 | 1.8797 | 1.9093 | 1.9456 | 1.9879 | 1.1432 | 1.3926 | 1.4157 | 1.4472 | 1.1432 | 1.5242 | 1.7349 | 1.7556 | 1.7832 | 1.8999
2022-04-27 02:00 | 1.6766 | 1.8472 | 1.8706 | 1.8993 | 1.9328 | 1.0411 | 1.2632 | 1.2815 | 1.3065 | 1.0411 | 1.3779 | 1.5637 | 1.5802 | 1.602 | 1.7038
2022-04-27 03:00 | 1.6385 | 1.7944 | 1.8118 | 1.8331 | 1.858 | 1.0226 | 1.2328 | 1.2464 | 1.2649 | 1.0226 | 1.4289 | 1.6121 | 1.6243 | 1.6405 | 1.7384
2022-04-27 04:00 | 1.7528 | 1.9071 | 1.9194 | 1.9344 | 1.9519 | 1.1241 | 1.3454 | 1.355 | 1.368 | 1.1241 | 1.7528 | 1.9649 | 1.9734 | 1.9849 | 2.0949
2022-04-27 05:00 | 1.9302 | 2.0937 | 2.1039 | 2.1165 | 2.1311 | 1.309 | 1.561 | 1.569 | 1.5799 | 1.309 | 1.6004 | 1.7927 | 1.7998 | 1.8094 | 1.9087
2022-04-27 06:00 | 2.2291 | 2.4182 | 2.4302 | 2.4448 | 2.4618 | 1.6957 | 2.0202 | 2.0295 | 2.0422 | 1.6957 | 2.0958 | 2.3455 | 2.3539 | 2.365 | 2.4935
2022-04-27 07:00 | 2.4006 | 2.6115 | 2.6281 | 2.6484 | 2.6721 | 1.7338 | 2.0718 | 2.0847 | 2.1024 | 1.7338 | 2.3435 | 2.6272 | 2.6388 | 2.6542 | 2.8015
2022-04-27 08:00 | 2.4059 | 2.6306 | 2.654 | 2.6827 | 2.716 | 1.7147 | 2.059 | 2.0772 | 2.1021 | 1.7147 | 2.0386 | 2.2979 | 2.3143 | 2.3361 | 2.4742
2022-04-27 09:00 | 2.4387 | 2.6801 | 2.7108 | 2.7483 | 2.7921 | 1.5814 | 1.9118 | 1.9357 | 1.9684 | 1.5814 | 1.7147 | 1.948 | 1.9695 | 1.9981 | 2.1265
2022-04-27 10:00 | 2.4006 | 2.6501 | 2.6863 | 2.7307 | 2.7825 | 1.4861 | 1.8072 | 1.8355 | 1.8741 | 1.4861 | 2.0196 | 2.2946 | 2.32 | 2.3537 | 2.5051
2022-04-27 11:00 | 2.3435 | 2.593 | 2.6315 | 2.6786 | 2.7335 | 1.467 | 1.7878 | 1.8178 | 1.8588 | 1.467 | 1.4861 | 1.7048 | 1.7318 | 1.7676 | 1.8921
2022-04-27 12:00 | 2.4768 | 2.7352 | 2.7732 | 2.8196 | 2.8738 | 1.6004 | 1.9446 | 1.9742 | 2.0146 | 1.6004 | 1.6957 | 1.937 | 1.9635 | 1.9989 | 2.1343
2022-04-27 13:00 | 2.5072 | 2.7629 | 2.7983 | 2.8416 | 2.8921 | 1.6004 | 1.941 | 1.9686 | 2.0063 | 1.6004 | 1.6766 | 1.9123 | 1.9371 | 1.97 | 2.1016
2022-04-27 14:00 | 2.7055 | 2.9705 | 3.0031 | 3.0431 | 3.0896 | 1.6195 | 1.9596 | 1.985 | 2.0198 | 1.6195 | 2.0196 | 2.2895 | 2.3124 | 2.3428 | 2.4901
2022-04-27 15:00 | 2.6293 | 2.885 | 2.9158 | 2.9535 | 2.9975 | 1.7559 | 2.1182 | 2.1422 | 2.175 | 1.7559 | 2.3816 | 2.6893 | 2.7108 | 2.7395 | 2.9047
2022-04-27 16:00 | 2.6483 | 2.9046 | 2.935 | 2.9722 | 3.0155 | 1.9429 | 2.3385 | 2.3621 | 2.3945 | 1.9429 | 2.7245 | 3.0697 | 3.091 | 3.1193 | 3.3029
2022-04-27 17:00 | 2.8769 | 3.1538 | 3.186 | 3.2254 | 3.2713 | 2.4387 | 2.9268 | 2.9519 | 2.9861 | 2.4387 | 3.3342 | 3.7498 | 3.7723 | 3.8023 | 4.0214
2022-04-27 18:00 | 2.915 | 3.2021 | 3.238 | 3.282 | 3.3333 | 2.4197 | 2.9096 | 2.9376 | 2.9759 | 2.4197 | 4.0963 | 4.6019 | 4.627 | 4.6605 | 4.9257
2022-04-27 19:00 | 2.8007 | 3.089 | 3.1299 | 3.18 | 3.2384 | 2.3969 | 2.8898 | 2.9217 | 2.9653 | 2.3969 | 3.7152 | 4.1853 | 4.214 | 4.2521 | 4.5019
2022-04-27 20:00 | 2.6483 | 2.935 | 2.9808 | 3.0369 | 3.1024 | 2.2482 | 2.7211 | 2.7569 | 2.8057 | 2.2482 | 3.6771 | 4.1498 | 4.182 | 4.2247 | 4.4779
2022-04-27 21:00 | 2.534 | 2.8138 | 2.8605 | 2.9176 | 2.9842 | 2.0608 | 2.5009 | 2.5374 | 2.5871 | 2.0608 | 3.277 | 3.7064 | 3.7391 | 3.7826 | 4.0147
2022-04-27 22:00 | 2.3054 | 2.5622 | 2.6058 | 2.6593 | 2.7216 | 1.8111 | 2.2016 | 2.2357 | 2.2822 | 1.8111 | 2.3816 | 2.7071 | 2.7376 | 2.7783 | 2.9578
2022-04-27 23:00 | 2.0196 | 2.2467 | 2.286 | 2.3342 | 2.3903 | 1.448 | 1.7665 | 1.7972 | 1.8391 | 1.448 | 2.0386 | 2.32 | 2.3475 | 2.3842 | 2.54
2022-04-28 | 1.9053 | 2.1144 | 2.149 | 2.1912 | 2.2404 | 1.3039 | 1.5895 | 1.6164 | 1.6532 | 1.3039 | 1.7338 | 1.9745 | 1.9987 | 2.0308 | 2.1646
2022-04-28 01:00 | 1.7147 | 1.9002 | 1.9298 | 1.9661 | 2.0083 | 1.1813 | 1.4376 | 1.4607 | 1.4922 | 1.1813 | 1.6957 | 1.9254 | 1.9462 | 1.9737 | 2.0999
2022-04-28 02:00 | 1.6576 | 1.8267 | 1.8501 | 1.8788 | 1.9123 | 1.105 | 1.3388 | 1.3571 | 1.3821 | 1.105 | 1.467 | 1.6628 | 1.6792 | 1.701 | 1.8078
2022-04-28 03:00 | 1.6957 | 1.8558 | 1.8732 | 1.8945 | 1.9194 | 1.0479 | 1.2627 | 1.2763 | 1.2948 | 1.0479 | 1.4099 | 1.5909 | 1.6031 | 1.6193 | 1.7162
2022-04-28 04:00 | 1.7147 | 1.8662 | 1.8785 | 1.8935 | 1.911 | 1.1241 | 1.3454 | 1.355 | 1.368 | 1.1241 | 1.7528 | 1.9649 | 1.9734 | 1.9849 | 2.0949
2022-04-28 05:00 | 1.9261 | 2.0893 | 2.0995 | 2.112 | 2.1266 | 1.2828 | 1.53 | 1.538 | 1.5489 | 1.2828 | 1.5623 | 1.7503 | 1.7575 | 1.767 | 1.8643
2022-04-28 06:00 | 2.2183 | 2.4065 | 2.4185 | 2.4331 | 2.4501 | 1.6342 | 1.9475 | 1.9568 | 1.9695 | 1.6342 | 2.2101 | 2.4725 | 2.4809 | 2.492 | 2.6268
2022-04-28 07:00 | 2.6102 | 2.8367 | 2.8533 | 2.8736 | 2.8972 | 1.81 | 2.1618 | 2.1748 | 2.1924 | 1.81 | 2.5149 | 2.8177 | 2.8293 | 2.8448 | 3.0015
2022-04-28 08:00 | 2.5886 | 2.8268 | 2.8502 | 2.8788 | 2.9122 | 1.7195 | 2.0646 | 2.0828 | 2.1077 | 1.7195 | 2.3244 | 2.6155 | 2.6319 | 2.6536 | 2.8075
2022-04-28 09:00 | 2.6102 | 2.8643 | 2.895 | 2.9325 | 2.9763 | 1.5623 | 1.8893 | 1.9132 | 1.9459 | 1.5623 | 2.2101 | 2.4985 | 2.52 | 2.5486 | 2.7042
2022-04-28 10:00 | 2.4197 | 2.6705 | 2.7068 | 2.7512 | 2.803 | 1.4289 | 1.7397 | 1.7679 | 1.8066 | 1.4289 | 1.7147 | 1.9558 | 1.9812 | 2.015 | 2.1496
2022-04-28 11:00 | 2.4387 | 2.6954 | 2.7338 | 2.7809 | 2.8359 | 1.3718 | 1.6753 | 1.7053 | 1.7463 | 1.3718 | 1.467 | 1.6836 | 1.7106 | 1.7464 | 1.8699
2022-04-28 12:00 | 2.534 | 2.7967 | 2.8346 | 2.881 | 2.9352 | 1.5052 | 1.8321 | 1.8617 | 1.9021 | 1.5052 | 1.829 | 2.0852 | 2.1117 | 2.1471 | 2.2899
2022-04-28 13:00 | 2.5721 | 2.8326 | 2.868 | 2.9113 | 2.9619 | 1.4861 | 1.8059 | 1.8336 | 1.8713 | 1.4861 | 1.5433 | 1.764 | 1.7888 | 1.8218 | 1.946
2022-04-28 14:00 | 2.3625 | 2.602 | 2.6347 | 2.6746 | 2.7212 | 1.3718 | 1.667 | 1.6924 | 1.7272 | 1.3718 | 1.3337 | 1.5273 | 1.5502 | 1.5806 | 1.6902
2022-04-28 15:00 | 2.4197 | 2.6599 | 2.6907 | 2.7284 | 2.7723 | 1.467 | 1.7769 | 1.8009 | 1.8337 | 1.467 | 1.6385 | 1.8635 | 1.8851 | 1.9138 | 2.0382
2022-04-28 16:00 | 2.5149 | 2.7613 | 2.7917 | 2.8289 | 2.8722 | 1.7063 | 2.0589 | 2.0826 | 2.1149 | 1.7063 | 2.553 | 2.8792 | 2.9005 | 2.9287 | 3.1029
2022-04-28 17:00 | 2.7245 | 2.99 | 3.0222 | 3.0616 | 3.1075 | 2.0577 | 2.4766 | 2.5017 | 2.536 | 2.0577 | 2.896 | 3.2628 | 3.2853 | 3.3153 | 3.5103
2022-04-28 18:00 | 2.8388 | 3.1202 | 3.1562 | 3.2001 | 3.2514 | 2.191 | 2.6395 | 2.6675 | 2.7058 | 2.191 | 3.4676 | 3.9032 | 3.9284 | 3.9618 | 4.1924
2022-04-28 19:00 | 2.7626 | 3.0481 | 3.089 | 3.1391 | 3.1975 | 2.191 | 2.6466 | 2.6785 | 2.7221 | 2.191 | 3.4104 | 3.8466 | 3.8752 | 3.9133 | 4.1464
2022-04-28 20:00 | 2.7436 | 3.0373 | 3.0832 | 3.1393 | 3.2047 | 2.0386 | 2.4735 | 2.5093 | 2.5582 | 2.0386 | 3.5628 | 4.0228 | 4.0549 | 4.0976 | 4.3445
2022-04-28 21:00 | 2.4452 | 2.7184 | 2.7651 | 2.8222 | 2.8889 | 1.9434 | 2.3622 | 2.3986 | 2.4483 | 1.9434 | 2.9913 | 3.3888 | 3.4215 | 3.465 | 3.6814
2022-04-28 22:00 | 2.3054 | 2.5622 | 2.6058 | 2.6593 | 2.7216 | 1.7338 | 2.1103 | 2.1443 | 2.1908 | 1.7338 | 2.2863 | 2.6012 | 2.6318 | 2.6724 | 2.8467
2022-04-28 23:00 | 2.0577 | 2.2876 | 2.327 | 2.3751 | 2.4313 | 1.4532 | 1.7727 | 1.8034 | 1.8453 | 1.4532 | 2.3244 | 2.6376 | 2.6651 | 2.7017 | 2.8733
2022-04-29 | 1.8672 | 2.0735 | 2.108 | 2.1503 | 2.1995 | 1.2684 | 1.5474 | 1.5744 | 1.6111 | 1.2684 | 1.6957 | 1.9322 | 1.9564 | 1.9885 | 2.1201
2022-04-29 01:00 | 1.7719 | 1.9616 | 1.9912 | 2.0275 | 2.0697 | 1.1622 | 1.4151 | 1.4382 | 1.4697 | 1.1622 | 1.6766 | 1.9042 | 1.925 | 1.9526 | 2.0777
2022-04-29 02:00 | 1.7147 | 1.8881 | 1.9116 | 1.9403 | 1.9737 | 1.0669 | 1.2938 | 1.3121 | 1.337 | 1.0669 | 1.6004 | 1.811 | 1.8274 | 1.8492 | 1.9633
2022-04-29 03:00 | 1.7147 | 1.8763 | 1.8937 | 1.915 | 1.9398 | 1.0669 | 1.2852 | 1.2988 | 1.3173 | 1.0669 | 1.467 | 1.6544 | 1.6666 | 1.6828 | 1.7828
2022-04-29 04:00 | 1.769 | 1.9245 | 1.9368 | 1.9518 | 1.9693 | 1.105 | 1.3229 | 1.3325 | 1.3455 | 1.105 | 1.7147 | 1.9225 | 1.9311 | 1.9425 | 2.0504
2022-04-29 05:00 | 1.9212 | 2.0841 | 2.0943 | 2.1068 | 2.1214 | 1.2223 | 1.4585 | 1.4665 | 1.4774 | 1.2223 | 1.5052 | 1.6868 | 1.694 | 1.7035 | 1.7976
2022-04-29 06:00 | 2.1529 | 2.3364 | 2.3483 | 2.3629 | 2.3799 | 1.467 | 1.7501 | 1.7594 | 1.7721 | 1.467 | 1.8481 | 2.0703 | 2.0786 | 2.0897 | 2.2046
2022-04-29 07:00 | 2.3244 | 2.5297 | 2.5462 | 2.5665 | 2.5902 | 1.5052 | 1.8017 | 1.8146 | 1.8323 | 1.5052 | 2.0005 | 2.2461 | 2.2577 | 2.2731 | 2.4016
2022-04-29 08:00 | 2.3244 | 2.543 | 2.5664 | 2.5951 | 2.6284 | 1.467 | 1.7664 | 1.7846 | 1.8095 | 1.467 | 1.4099 | 1.5992 | 1.6156 | 1.6374 | 1.7409
2022-04-29 09:00 | 2.4006 | 2.6391 | 2.6698 | 2.7074 | 2.7511 | 1.3718 | 1.6642 | 1.6881 | 1.7208 | 1.3718 | 1.3337 | 1.5246 | 1.5461 | 1.5746 | 1.6821
2022-04-29 10:00 | 2.0767 | 2.3021 | 2.3384 | 2.3828 | 2.4345 | 1.0098 | 1.2445 | 1.2728 | 1.3114 | 1.0098 | 1.5814 | 1.8076 | 1.833 | 1.8668 | 1.9941
2022-04-29 11:00 | 2.0005 | 2.2246 | 2.2631 | 2.3102 | 2.3651 | 0.93358 | 1.1576 | 1.1876 | 1.2286 | 0.93358 | 1.4861 | 1.7048 | 1.7318 | 1.7676 | 1.8921
2022-04-29 12:00 | 1.9434 | 2.1621 | 2.2001 | 2.2465 | 2.3007 | 0.81926 | 1.0218 | 1.0514 | 1.0918 | 0.81926 | 1.6576 | 1.8946 | 1.9212 | 1.9565 | 2.0899
2022-04-29 13:00 | 1.7147 | 1.9115 | 1.9469 | 1.9902 | 2.0408 | 0.81926 | 1.0182 | 1.0458 | 1.0835 | 0.81926 | 1.5814 | 1.8064 | 1.8312 | 1.8641 | 1.9905
2022-04-29 14:00 | 2.0577 | 2.2745 | 2.3072 | 2.3471 | 2.3937 | 0.85737 | 1.0593 | 1.0847 | 1.1195 | 0.85737 | 1.2384 | 1.4215 | 1.4443 | 1.4747 | 1.5791
2022-04-29 15:00 | 2.1529 | 2.3733 | 2.4041 | 2.4418 | 2.4858 | 1.2765 | 1.5518 | 1.5759 | 1.6087 | 1.2765 | 1.0479 | 1.2072 | 1.2288 | 1.2575 | 1.3494
2022-04-29 16:00 | 2.3816 | 2.6181 | 2.6484 | 2.6856 | 2.7289 | 1.5269 | 1.8469 | 1.8706 | 1.903 | 1.5269 | 2.0386 | 2.3075 | 2.3288 | 2.3571 | 2.503
2022-04-29 17:00 | 2.6102 | 2.8672 | 2.8994 | 2.9388 | 2.9847 | 1.8672 | 2.2515 | 2.2766 | 2.3109 | 1.8672 | 2.8388 | 3.1993 | 3.2218 | 3.2518 | 3.4437
2022-04-29 18:00 | 2.6293 | 2.8951 | 2.931 | 2.975 | 3.0263 | 1.9053 | 2.3019 | 2.3299 | 2.3682 | 1.9053 | 3.1437 | 3.5433 | 3.5684 | 3.6019 | 3.8147
2022-04-29 19:00 | 2.4566 | 2.7193 | 2.7602 | 2.8103 | 2.8687 | 1.8481 | 2.2414 | 2.2734 | 2.3169 | 1.8481 | 3.0675 | 3.4655 | 3.4941 | 3.5322 | 3.7464
2022-04-29 20:00 | 2.3435 | 2.6074 | 2.6533 | 2.7094 | 2.7749 | 1.7635 | 2.1485 | 2.1842 | 2.2331 | 1.7635 | 2.6293 | 2.9854 | 3.0175 | 3.0602 | 3.2558
2022-04-29 21:00 | 2.191 | 2.4453 | 2.492 | 2.5492 | 2.6158 | 1.7719 | 2.1596 | 2.196 | 2.2458 | 1.7719 | 2.3054 | 2.6266 | 2.6593 | 2.7028 | 2.8815
2022-04-29 22:00 | 2.0958 | 2.337 | 2.3807 | 2.4341 | 2.4964 | 1.5891 | 1.9393 | 1.9734 | 2.0198 | 1.5891 | 2.3435 | 2.6647 | 2.6953 | 2.7359 | 2.9134
2022-04-29 23:00 | 2.0577 | 2.2876 | 2.327 | 2.3751 | 2.4313 | 1.3521 | 1.6532 | 1.6839 | 1.7258 | 1.3521 | 1.7338 | 1.9812 | 2.0088 | 2.0454 | 2.1845
2022-04-30 | 1.8523 | 2.0576 | 2.0921 | 2.1343 | 2.1836 | 1.2138 | 1.483 | 1.5099 | 1.5467 | 1.2138 | 1.5433 | 1.7628 | 1.787 | 1.8191 | 1.9424
2022-04-30 01:00 | 1.7719 | 1.9616 | 1.9912 | 2.0275 | 2.0697 | 1.1023 | 1.3443 | 1.3675 | 1.399 | 1.1023 | 1.467 | 1.6713 | 1.6921 | 1.7197 | 1.8333
2022-04-30 02:00 | 1.7147 | 1.8881 | 1.9116 | 1.9403 | 1.9737 | 1.0318 | 1.2522 | 1.2705 | 1.2955 | 1.0318 | 1.5052 | 1.7051 | 1.7216 | 1.7434 | 1.8522
2022-04-30 03:00 | 1.6385 | 1.7944 | 1.8118 | 1.8331 | 1.858 | 0.99841 | 1.2042 | 1.2178 | 1.2364 | 0.99841 | 1.3718 | 1.5485 | 1.5607 | 1.5769 | 1.6717
2022-04-30 04:00 | 1.7147 | 1.8662 | 1.8785 | 1.8935 | 1.911 | 1.0288 | 1.2329 | 1.2424 | 1.2555 | 1.0288 | 1.4289 | 1.6049 | 1.6135 | 1.6249 | 1.7171
2022-04-30 05:00 | 1.7338 | 1.8827 | 1.8929 | 1.9055 | 1.9201 | 1.0484 | 1.2531 | 1.2611 | 1.272 | 1.0484 | 1.4861 | 1.6656 | 1.6728 | 1.6823 | 1.7754
2022-04-30 06:00 | 1.8481 | 2.0089 | 2.0208 | 2.0354 | 2.0524 | 1.1622 | 1.3899 | 1.3993 | 1.412 | 1.1622 | 1.5623 | 1.7527 | 1.761 | 1.7722 | 1.8713
2022-04-30 07:00 | 1.9624 | 2.1408 | 2.1573 | 2.1776 | 2.2013 | 1.3908 | 1.6666 | 1.6796 | 1.6972 | 1.3908 | 1.829 | 2.0555 | 2.0671 | 2.0826 | 2.2016
2022-04-30 08:00 | 2.0958 | 2.2974 | 2.3208 | 2.3494 | 2.3828 | 1.4289 | 1.7214 | 1.7396 | 1.7645 | 1.4289 | 2.0958 | 2.3614 | 2.3778 | 2.3996 | 2.5408
2022-04-30 09:00 | 2.1148 | 2.3321 | 2.3628 | 2.4003 | 2.4441 | 1.5623 | 1.8893 | 1.9132 | 1.9459 | 1.5623 | 1.9243 | 2.1809 | 2.2024 | 2.231 | 2.3709
2022-04-30 10:00 | 1.9815 | 2.1998 | 2.236 | 2.2804 | 2.3322 | 1.5052 | 1.8297 | 1.858 | 1.8966 | 1.5052 | 1.5433 | 1.7652 | 1.7907 | 1.8244 | 1.9496
2022-04-30 11:00 | 1.9243 | 2.1427 | 2.1812 | 2.2283 | 2.2832 | 1.448 | 1.7653 | 1.7953 | 1.8363 | 1.448 | 1.467 | 1.6836 | 1.7106 | 1.7464 | 1.8699
2022-04-30 12:00 | 1.9434 | 2.1621 | 2.2001 | 2.2465 | 2.3007 | 1.3718 | 1.6745 | 1.7041 | 1.7445 | 1.3718 | 1.2956 | 1.4923 | 1.5189 | 1.5543 | 1.6677
2022-04-30 13:00 | 1.2003 | 1.3588 | 1.3942 | 1.4376 | 1.4881 | 0.78115 | 0.97316 | 1.0008 | 1.0385 | 0.78115 | 1.2384 | 1.4253 | 1.4501 | 1.483 | 1.5905
2022-04-30 14:00 | 1.5242 | 1.7014 | 1.734 | 1.774 | 1.8206 | 0.85737 | 1.0593 | 1.0847 | 1.1195 | 0.85737 | 0.93358 | 1.0827 | 1.1056 | 1.136 | 1.2236
2022-04-30 15:00 | 1.8672 | 2.0663 | 2.0971 | 2.1348 | 2.1787 | 1.2305 | 1.4974 | 1.5215 | 1.5543 | 1.2305 | 1.105 | 1.2707 | 1.2923 | 1.321 | 1.416
2022-04-30 16:00 | 2.2486 | 2.4752 | 2.5056 | 2.5427 | 2.5861 | 1.81 | 2.1814 | 2.2051 | 2.2374 | 1.81 | 2.8769 | 3.2391 | 3.2604 | 3.2887 | 3.4806
2022-04-30 17:00 | 2.7245 | 2.99 | 3.0222 | 3.0616 | 3.1075 | 2.1472 | 2.5824 | 2.6075 | 2.6417 | 2.1472 | 3.0484 | 3.4322 | 3.4547 | 3.4847 | 3.6881
2022-04-30 18:00 | 2.7626 | 3.0383 | 3.0743 | 3.1183 | 3.1695 | 2.172 | 2.617 | 2.645 | 2.6833 | 2.172 | 3.7915 | 4.2631 | 4.2883 | 4.3217 | 4.5702
2022-04-30 19:00 | 2.6674 | 2.9458 | 2.9867 | 3.0367 | 3.0951 | 2.1529 | 2.6016 | 2.6335 | 2.6771 | 2.1529 | 3.6009 | 4.0583 | 4.087 | 4.1251 | 4.3686
2022-04-30 20:00 | 2.6102 | 2.894 | 2.9399 | 2.996 | 3.0614 | 2.0577 | 2.4961 | 2.5318 | 2.5807 | 2.0577 | 3.1056 | 3.5147 | 3.5468 | 3.5895 | 3.8113
2022-04-30 21:00 | 2.5721 | 2.8547 | 2.9014 | 2.9585 | 3.0252 | 1.9594 | 2.3811 | 2.4175 | 2.4673 | 1.9594 | 2.7245 | 3.0924 | 3.1251 | 3.1686 | 3.3703
2022-04-30 22:00 | 2.3625 | 2.6236 | 2.6672 | 2.7207 | 2.783 | 1.7683 | 2.1511 | 2.1851 | 2.2316 | 1.7683 | 2.6864 | 3.0458 | 3.0764 | 3.117 | 3.3133
2022-04-30 23:00 | 2.3244 | 2.5742 | 2.6135 | 2.6617 | 2.7178 | 1.6061 | 1.9533 | 1.984 | 2.0259 | 1.6061 | 2.4006 | 2.7223 | 2.7498 | 2.7864 | 2.9622
2022-05-01 | 2.1148 | 2.3396 | 2.3741 | 2.4163 | 2.4656 | 1.4289 | 1.7372 | 1.7641 | 1.8008 | 1.4289 | 2.0577 | 2.3345 | 2.3586 | 2.3908 | 2.5423
2022-05-01 01:00 | 1.9434 | 2.1458 | 2.1754 | 2.2117 | 2.2539 | 1.3146 | 1.5952 | 1.6183 | 1.6498 | 1.3146 | 1.9053 | 2.1583 | 2.1791 | 2.2066 | 2.3443
2022-05-01 02:00 | 1.9624 | 2.1542 | 2.1776 | 2.2063 | 2.2398 | 1.1949 | 1.445 | 1.4633 | 1.4882 | 1.1949 | 1.6576 | 1.8745 | 1.8909 | 1.9128 | 2.03
2022-05-01 03:00 | 1.9243 | 2.1014 | 2.1189 | 2.1402 | 2.165 | 1.2003 | 1.4427 | 1.4563 | 1.4749 | 1.2003 | 1.6766 | 1.8873 | 1.8995 | 1.9157 | 2.0273
2022-05-01 04:00 | 2.0005 | 2.1732 | 2.1855 | 2.2005 | 2.218 | 1.2765 | 1.5255 | 1.535 | 1.5481 | 1.2765 | 1.81 | 2.0284 | 2.037 | 2.0484 | 2.1615
2022-05-01 05:00 | 1.9624 | 2.1283 | 2.1386 | 2.1511 | 2.1657 | 1.304 | 1.5551 | 1.5631 | 1.5739 | 1.304 | 1.9815 | 2.2161 | 2.2233 | 2.2328 | 2.3531
2022-05-01 06:00 | 2.0767 | 2.2545 | 2.2664 | 2.281 | 2.2981 | 1.4888 | 1.7758 | 1.7851 | 1.7978 | 1.4888 | 2.2863 | 2.5572 | 2.5656 | 2.5767 | 2.7157
2022-05-01 07:00 | 2.1148 | 2.3045 | 2.3211 | 2.3414 | 2.365 | 1.5814 | 1.8917 | 1.9047 | 1.9223 | 1.5814 | 2.2482 | 2.5213 | 2.5329 | 2.5484 | 2.6904
2022-05-01 08:00 | 2.0386 | 2.236 | 2.2594 | 2.288 | 2.3214 | 1.4322 | 1.7252 | 1.7434 | 1.7683 | 1.4322 | 1.9815 | 2.2344 | 2.2508 | 2.2725 | 2.4075
2022-05-01 09:00 | 1.7528 | 1.9432 | 1.9739 | 2.0114 | 2.0552 | 1.3307 | 1.6157 | 1.6396 | 1.6723 | 1.3307 | 1.086 | 1.2494 | 1.2709 | 1.2994 | 1.3933
2022-05-01 10:00 | 1.5433 | 1.729 | 1.7652 | 1.8096 | 1.8614 | 0.88137 | 1.0928 | 1.1211 | 1.1597 | 0.88137 | 0.89547 | 1.0454 | 1.0708 | 1.1046 | 1.1942
2022-05-01 11:00 | 1.8481 | 2.0608 | 2.0993 | 2.1464 | 2.2013 | 1.3337 | 1.6303 | 1.6603 | 1.7013 | 1.3337 | 1.2384 | 1.4296 | 1.4565 | 1.4924 | 1.6033
2022-05-01 12:00 | 1.5433 | 1.7323 | 1.7702 | 1.8167 | 1.8708 | 1.1432 | 1.4044 | 1.434 | 1.4744 | 1.1432 | 1.2384 | 1.4288 | 1.4554 | 1.4907 | 1.6011
2022-05-01 13:00 | 1.448 | 1.6249 | 1.6603 | 1.7037 | 1.7542 | 0.87642 | 1.0857 | 1.1133 | 1.151 | 0.87642 | 1.1432 | 1.3194 | 1.3442 | 1.3772 | 1.4794
2022-05-01 14:00 | 1.6385 | 1.8242 | 1.8569 | 1.8968 | 1.9434 | 1.0479 | 1.2843 | 1.3098 | 1.3446 | 1.0479 | 1.2003 | 1.3791 | 1.402 | 1.4324 | 1.5347
2022-05-01 15:00 | 1.9815 | 2.1891 | 2.2199 | 2.2576 | 2.3015 | 1.3698 | 1.662 | 1.686 | 1.7188 | 1.3698 | 1.5814 | 1.8 | 1.8216 | 1.8503 | 1.9715
2022-05-01 16:00 | 2.3244 | 2.5567 | 2.587 | 2.6242 | 2.6675 | 1.8481 | 2.2264 | 2.2501 | 2.2825 | 1.8481 | 2.4197 | 2.731 | 2.7523 | 2.7805 | 2.9474
2022-05-01 17:00 | 2.7626 | 3.031 | 3.0632 | 3.1025 | 3.1485 | 2.4578 | 2.9493 | 2.9744 | 3.0086 | 2.4578 | 3.4104 | 3.8345 | 3.857 | 3.887 | 4.1103
2022-05-01 18:00 | 2.896 | 3.1816 | 3.2176 | 3.2615 | 3.3128 | 2.4959 | 2.9996 | 3.0277 | 3.0659 | 2.4959 | 3.6771 | 4.1361 | 4.1613 | 4.1947 | 4.4369
2022-05-01 19:00 | 2.8769 | 3.1709 | 3.2118 | 3.2619 | 3.3203 | 2.3435 | 2.8266 | 2.8586 | 2.9021 | 2.3435 | 3.6962 | 4.1642 | 4.1928 | 4.2309 | 4.4797
2022-05-01 20:00 | 2.7626 | 3.0578 | 3.1036 | 3.1598 | 3.2252 | 2.2482 | 2.7211 | 2.7569 | 2.8057 | 2.2482 | 3.639 | 4.1075 | 4.1396 | 4.1823 | 4.4334
2022-05-01 21:00 | 2.6483 | 2.9366 | 2.9833 | 3.0404 | 3.1071 | 2.039 | 2.4752 | 2.5116 | 2.5613 | 2.039 | 3.1627 | 3.5793 | 3.6121 | 3.6555 | 3.8814
2022-05-01 22:00 | 2.4387 | 2.7055 | 2.7491 | 2.8025 | 2.8648 | 1.9053 | 2.3128 | 2.3469 | 2.3934 | 1.9053 | 3.0484 | 3.4481 | 3.4787 | 3.5193 | 3.7355
2022-05-01 23:00 | 2.3054 | 2.5537 | 2.5931 | 2.6412 | 2.6974 | 1.6228 | 1.973 | 2.0037 | 2.0456 | 1.6228 | 2.2482 | 2.5529 | 2.5804 | 2.6171 | 2.7844
2022-05-02 | 2.0196 | 2.2373 | 2.2718 | 2.314 | 2.3633 | 1.418 | 1.7242 | 1.7511 | 1.7878 | 1.418 | 1.8672 | 2.1227 | 2.1469 | 2.179 | 2.3201
2022-05-02 01:00 | 1.8862 | 2.0844 | 2.114 | 2.1503 | 2.1925 | 1.3065 | 1.5855 | 1.6086 | 1.6401 | 1.3065 | 1.8481 | 2.0948 | 2.1155 | 2.1431 | 2.2777
2022-05-02 02:00 | 1.9053 | 2.0928 | 2.1162 | 2.1449 | 2.1784 | 1.2384 | 1.4963 | 1.5146 | 1.5396 | 1.2384 | 1.6766 | 1.8957 | 1.9121 | 1.9339 | 2.0522
2022-05-02 03:00 | 1.9815 | 2.1629 | 2.1803 | 2.2016 | 2.2264 | 1.2575 | 1.5103 | 1.5238 | 1.5424 | 1.2575 | 1.7528 | 1.972 | 1.9842 | 2.0004 | 2.1161
2022-05-02 04:00 | 2.0196 | 2.1937 | 2.206 | 2.221 | 2.2385 | 1.3912 | 1.6609 | 1.6705 | 1.6836 | 1.3912 | 2.0386 | 2.2824 | 2.291 | 2.3024 | 2.4282
2022-05-02 05:00 | 2.349 | 2.5436 | 2.5538 | 2.5664 | 2.581 | 1.5836 | 1.8853 | 1.8933 | 1.9042 | 1.5836 | 2.3244 | 2.5972 | 2.6044 | 2.6139 | 2.7531
2022-05-02 06:00 | 2.8212 | 3.0543 | 3.0662 | 3.0808 | 3.0979 | 2.0902 | 2.4862 | 2.4955 | 2.5082 | 2.0902 | 3.4676 | 3.8699 | 3.8783 | 3.8894 | 4.0933
2022-05-02 07:00 | 3.0484 | 3.3075 | 3.3241 | 3.3444 | 3.368 | 2.3625 | 2.8145 | 2.8275 | 2.8451 | 2.3625 | 3.7534 | 4.1939 | 4.2055 | 4.221 | 4.4458
2022-05-02 08:00 | 3.0865 | 3.3618 | 3.3852 | 3.4138 | 3.4472 | 2.2101 | 2.6442 | 2.6624 | 2.6873 | 2.2101 | 2.6927 | 3.0247 | 3.0411 | 3.0629 | 3.2369
2022-05-02 09:00 | 2.3111 | 2.5429 | 2.5736 | 2.6111 | 2.6549 | 1.4204 | 1.7216 | 1.7455 | 1.7782 | 1.4204 | 1.0669 | 1.2282 | 1.2497 | 1.2782 | 1.371
2022-05-02 10:00 | 2.0005 | 2.2202 | 2.2565 | 2.3009 | 2.3526 | 0.88566 | 1.0978 | 1.1261 | 1.1648 | 0.88566 | 1.0155 | 1.1788 | 1.2042 | 1.238 | 1.3342
2022-05-02 11:00 | 1.6195 | 1.8152 | 1.8537 | 1.9008 | 1.9557 | 0.70494 | 0.88751 | 0.91753 | 0.95851 | 0.70494 | 1.3146 | 1.5143 | 1.5412 | 1.577 | 1.6922
2022-05-02 12:00 | 1.6037 | 1.7972 | 1.8352 | 1.8816 | 1.9358 | 0.74305 | 0.93176 | 0.96136 | 1.0018 | 0.74305 | 1.3718 | 1.577 | 1.6036 | 1.6389 | 1.7566
2022-05-02 13:00 | 1.5623 | 1.7477 | 1.7831 | 1.8265 | 1.877 | 0.78115 | 0.97316 | 1.0008 | 1.0385 | 0.78115 | 1.467 | 1.6794 | 1.7042 | 1.7371 | 1.8572
2022-05-02 14:00 | 1.7719 | 1.9675 | 2.0001 | 2.0401 | 2.0867 | 0.93358 | 1.1493 | 1.1747 | 1.2095 | 0.93358 | 1.086 | 1.2521 | 1.2749 | 1.3053 | 1.4014
2022-05-02 15:00 | 2.1148 | 2.3324 | 2.3632 | 2.4009 | 2.4448 | 1.297 | 1.576 | 1.6 | 1.6328 | 1.297 | 1.0669 | 1.2284 | 1.2499 | 1.2786 | 1.3716
2022-05-02 16:00 | 2.5059 | 2.7517 | 2.782 | 2.8192 | 2.8625 | 1.6869 | 2.036 | 2.0597 | 2.092 | 1.6869 | 1.9815 | 2.244 | 2.2653 | 2.2936 | 2.4363
2022-05-02 17:00 | 2.7817 | 3.0515 | 3.0836 | 3.123 | 3.1689 | 2.2482 | 2.7017 | 2.7268 | 2.761 | 2.2482 | 3.0484 | 3.4322 | 3.4547 | 3.4847 | 3.6881
2022-05-02 18:00 | 2.8769 | 3.1612 | 3.1971 | 3.2411 | 3.2924 | 2.3054 | 2.7745 | 2.8026 | 2.8408 | 2.3054 | 3.4295 | 3.8608 | 3.886 | 3.9195 | 4.148
2022-05-02 19:00 | 2.8388 | 3.13 | 3.1709 | 3.221 | 3.2794 | 2.3816 | 2.8717 | 2.9036 | 2.9472 | 2.3816 | 3.8296 | 4.3124 | 4.341 | 4.3791 | 4.6352
2022-05-02 20:00 | 2.915 | 3.2215 | 3.2674 | 3.3235 | 3.389 | 2.2491 | 2.7222 | 2.758 | 2.8068 | 2.2491 | 3.7343 | 4.2134 | 4.2455 | 4.2882 | 4.5445
2022-05-02 21:00 | 2.6293 | 2.9161 | 2.9628 | 3.0199 | 3.0866 | 2.1529 | 2.6098 | 2.6462 | 2.6959 | 2.1529 | 2.9341 | 3.3253 | 3.358 | 3.4015 | 3.6147
2022-05-02 22:00 | 2.4578 | 2.7259 | 2.7696 | 2.823 | 2.8853 | 1.9243 | 2.3354 | 2.3694 | 2.4159 | 1.9243 | 2.534 | 2.8764 | 2.907 | 2.9477 | 3.1356
2022-05-02 23:00 | 2.1836 | 2.4229 | 2.4622 | 2.5104 | 2.5665 | 1.5048 | 1.8336 | 1.8643 | 1.9062 | 1.5048 | 2.2482 | 2.5529 | 2.5804 | 2.6171 | 2.7844
2022-05-03 | 2.0005 | 2.2168 | 2.2513 | 2.2935 | 2.3428 | 1.3527 | 1.6471 | 1.674 | 1.7108 | 1.3527 | 2.0577 | 2.3345 | 2.3586 | 2.3908 | 2.5423
2022-05-03 01:00 | 2.0196 | 2.2277 | 2.2573 | 2.2936 | 2.3358 | 1.2393 | 1.5061 | 1.5293 | 1.5608 | 1.2393 | 1.7147 | 1.9466 | 1.9673 | 1.9949 | 2.1221
2022-05-03 02:00 | 1.9053 | 2.0928 | 2.1162 | 2.1449 | 2.1784 | 1.2194 | 1.4738 | 1.4921 | 1.5171 | 1.2194 | 1.6576 | 1.8745 | 1.8909 | 1.9128 | 2.03
2022-05-03 03:00 | 1.9624 | 2.1424 | 2.1598 | 2.1811 | 2.2059 | 1.2194 | 1.4653 | 1.4788 | 1.4974 | 1.2194 | 1.6056 | 1.8084 | 1.8206 | 1.8368 | 1.9445
2022-05-03 04:00 | 2.0577 | 2.2346 | 2.2469 | 2.2619 | 2.2794 | 1.2875 | 1.5384 | 1.5479 | 1.561 | 1.2875 | 1.7719 | 1.986 | 1.9946 | 2.006 | 2.1171
2022-05-03 05:00 | 2.2673 | 2.4558 | 2.4661 | 2.4786 | 2.4932 | 1.5623 | 1.8602 | 1.8682 | 1.8791 | 1.5623 | 2.2673 | 2.5337 | 2.5409 | 2.5504 | 2.6864
2022-05-03 06:00 | 2.9341 | 3.1756 | 3.1875 | 3.2022 | 3.2192 | 2.1808 | 2.5933 | 2.6026 | 2.6153 | 2.1808 | 3.4104 | 3.8064 | 3.8147 | 3.8259 | 4.0266
2022-05-03 07:00 | 3.1056 | 3.3689 | 3.3855 | 3.4058 | 3.4294 | 2.2673 | 2.702 | 2.7149 | 2.7326 | 2.2673 | 3.62 | 4.0457 | 4.0573 | 4.0728 | 4.2902
2022-05-03 08:00 | 2.8769 | 3.1366 | 3.16 | 3.1887 | 3.222 | 2.0549 | 2.4609 | 2.4791 | 2.5041 | 2.0549 | 2.6674 | 2.9966 | 3.013 | 3.0347 | 3.2074
2022-05-03 09:00 | 2.3435 | 2.5777 | 2.6084 | 2.646 | 2.6897 | 1.1496 | 1.4017 | 1.4257 | 1.4583 | 1.1496 | 1.2384 | 1.4187 | 1.4402 | 1.4688 | 1.571
2022-05-03 10:00 | 1.8481 | 2.0565 | 2.0927 | 2.1371 | 2.1889 | 0.91452 | 1.1319 | 1.1602 | 1.1988 | 0.91452 | 1.2003 | 1.3841 | 1.4096 | 1.4433 | 1.5497
2022-05-03 11:00 | 1.5814 | 1.7743 | 1.8127 | 1.8598 | 1.9148 | 0.68589 | 0.865 | 0.89502 | 0.936 | 0.68589 | 1.6195 | 1.853 | 1.88 | 1.9158 | 2.0477
2022-05-03 12:00 | 1.5433 | 1.7323 | 1.7702 | 1.8167 | 1.8708 | 0.70494 | 0.88675 | 0.91634 | 0.95676 | 0.70494 | 1.7528 | 2.0005 | 2.0271 | 2.0624 | 2.201
2022-05-03 13:00 | 1.5433 | 1.7273 | 1.7627 | 1.806 | 1.8565 | 0.68589 | 0.86062 | 0.88823 | 0.92593 | 0.68589 | 1.5623 | 1.7852 | 1.81 | 1.843 | 1.9683
2022-05-03 14:00 | 1.7909 | 1.988 | 2.0206 | 2.0606 | 2.1071 | 0.93358 | 1.1493 | 1.1747 | 1.2095 | 0.93358 | 1.3146 | 1.5061 | 1.529 | 1.5594 | 1.668
2022-05-03 15:00 | 2.0767 | 2.2914 | 2.3222 | 2.3599 | 2.4039 | 1.2148 | 1.4789 | 1.5029 | 1.5357 | 1.2148 | 1.086 | 1.2495 | 1.2711 | 1.2998 | 1.3938
2022-05-03 16:00 | 2.4578 | 2.6999 | 2.7303 | 2.7675 | 2.8108 | 1.6879 | 2.0372 | 2.0609 | 2.0933 | 1.6879 | 2.2863 | 2.5828 | 2.6041 | 2.6323 | 2.7918
2022-05-03 17:00 | 2.781 | 3.0508 | 3.083 | 3.1223 | 3.1683 | 2.1339 | 2.5666 | 2.5917 | 2.626 | 2.1339 | 2.8769 | 3.2416 | 3.2642 | 3.2941 | 3.4881
2022-05-03 18:00 | 2.9102 | 3.1969 | 3.2329 | 3.2768 | 3.3281 | 2.2863 | 2.752 | 2.7801 | 2.8183 | 2.2863 | 3.4676 | 3.9032 | 3.9284 | 3.9618 | 4.1924
2022-05-03 19:00 | 2.9913 | 3.2937 | 3.3346 | 3.3847 | 3.4431 | 2.2158 | 2.6758 | 2.7077 | 2.7513 | 2.2158 | 3.3533 | 3.7831 | 3.8117 | 3.8498 | 4.0797
2022-05-03 20:00 | 2.8007 | 3.0987 | 3.1446 | 3.2007 | 3.2661 | 2.2101 | 2.6761 | 2.7119 | 2.7607 | 2.2101 | 3.62 | 4.0863 | 4.1185 | 4.1611 | 4.4112
2022-05-03 21:00 | 2.6864 | 2.9775 | 3.0242 | 3.0814 | 3.148 | 2.1148 | 2.5648 | 2.6012 | 2.6509 | 2.1148 | 3.4104 | 3.8546 | 3.8873 | 3.9308 | 4.1702
2022-05-03 22:00 | 2.3718 | 2.6335 | 2.6772 | 2.7306 | 2.7929 | 1.7972 | 2.1852 | 2.2192 | 2.2657 | 1.7972 | 2.5149 | 2.8553 | 2.8859 | 2.9265 | 3.1133
2022-05-03 23:00 | 2.1263 | 2.3613 | 2.4007 | 2.4488 | 2.5049 | 1.5137 | 1.8442 | 1.8749 | 1.9167 | 1.5137 | 2.191 | 2.4894 | 2.5169 | 2.5535 | 2.7178
2022-05-04 | 1.9434 | 2.1554 | 2.1899 | 2.2321 | 2.2814 | 1.3168 | 1.6047 | 1.6316 | 1.6684 | 1.3168 | 1.9434 | 2.2074 | 2.2316 | 2.2637 | 2.409
2022-05-04 01:00 | 1.9434 | 2.1458 | 2.1754 | 2.2117 | 2.2539 | 1.2575 | 1.5276 | 1.5507 | 1.5823 | 1.2575 | 1.7147 | 1.9466 | 1.9673 | 1.9949 | 2.1221
2022-05-04 02:00 | 1.9053 | 2.0928 | 2.1162 | 2.1449 | 2.1784 | 1.1581 | 1.4014 | 1.4197 | 1.4447 | 1.1581 | 1.7719 | 2.0015 | 2.018 | 2.0398 | 2.1633
2022-05-04 03:00 | 1.8862 | 2.0605 | 2.0779 | 2.0992 | 2.1241 | 1.1721 | 1.4094 | 1.423 | 1.4416 | 1.1721 | 1.5623 | 1.7603 | 1.7725 | 1.7887 | 1.8939
2022-05-04 04:00 | 2.0005 | 2.1732 | 2.1855 | 2.2005 | 2.218 | 1.2299 | 1.4704 | 1.48 | 1.493 | 1.2299 | 1.7909 | 2.0072 | 2.0158 | 2.0272 | 2.1393
2022-05-04 05:00 | 2.3054 | 2.4968 | 2.507 | 2.5195 | 2.5341 | 1.513 | 1.8019 | 1.8099 | 1.8208 | 1.513 | 2.2101 | 2.4702 | 2.4773 | 2.4869 | 2.6198
2022-05-04 06:00 | 2.7657 | 2.9947 | 3.0066 | 3.0212 | 3.0383 | 2.0699 | 2.4623 | 2.4716 | 2.4843 | 2.0699 | 2.9722 | 3.3194 | 3.3278 | 3.3389 | 3.5156
2022-05-04 07:00 | 3.1056 | 3.3689 | 3.3855 | 3.4058 | 3.4294 | 2.3244 | 2.7695 | 2.7825 | 2.8001 | 2.3244 | 3.2961 | 3.6858 | 3.6974 | 3.7128 | 3.9125
2022-05-04 08:00 | 2.8769 | 3.1366 | 3.16 | 3.1887 | 3.222 | 2.0958 | 2.5091 | 2.5274 | 2.5523 | 2.0958 | 3.0103 | 3.3777 | 3.3941 | 3.4158 | 3.6074
2022-05-04 09:00 | 2.8198 | 3.0895 | 3.1201 | 3.1577 | 3.2015 | 1.7939 | 2.1628 | 2.1868 | 2.2194 | 1.7939 | 2.2101 | 2.4985 | 2.52 | 2.5486 | 2.7042
2022-05-04 10:00 | 2.7245 | 2.9981 | 3.0343 | 3.0787 | 3.1305 | 1.6576 | 2.0097 | 2.038 | 2.0767 | 1.6576 | 1.6957 | 1.9346 | 1.96 | 1.9938 | 2.1274
2022-05-04 11:00 | 2.7245 | 3.0024 | 3.0409 | 3.088 | 3.1429 | 1.7449 | 2.1161 | 2.1461 | 2.1871 | 1.7449 | 2.0196 | 2.2976 | 2.3246 | 2.3604 | 2.5143
2022-05-04 12:00 | 2.8579 | 3.1446 | 3.1826 | 3.229 | 3.2832 | 1.7719 | 2.1472 | 2.1768 | 2.2172 | 1.7719 | 2.3054 | 2.6145 | 2.6411 | 2.6764 | 2.8454
2022-05-04 13:00 | 2.6483 | 2.9145 | 2.9499 | 2.9932 | 3.0437 | 1.6957 | 2.0535 | 2.0811 | 2.1188 | 1.6957 | 2.2863 | 2.5898 | 2.6146 | 2.6475 | 2.8126
2022-05-04 14:00 | 2.4959 | 2.7453 | 2.778 | 2.8179 | 2.8645 | 1.4861 | 1.802 | 1.8275 | 1.8622 | 1.4861 | 1.448 | 1.6544 | 1.6772 | 1.7076 | 1.8235
2022-05-04 15:00 | 2.4452 | 2.6873 | 2.7181 | 2.7558 | 2.7998 | 1.6385 | 1.9795 | 2.0035 | 2.0363 | 1.6385 | 2.2863 | 2.5834 | 2.605 | 2.6336 | 2.7936
2022-05-04 16:00 | 2.8579 | 3.1298 | 3.1601 | 3.1973 | 3.2407 | 2.1018 | 2.5262 | 2.5498 | 2.5822 | 2.1018 | 3.3342 | 3.7473 | 3.7685 | 3.7968 | 4.0139
2022-05-04 17:00 | 3.0294 | 3.3175 | 3.3497 | 3.3891 | 3.435 | 2.4387 | 2.9268 | 2.9519 | 2.9861 | 2.4387 | 3.7343 | 4.1944 | 4.2169 | 4.2469 | 4.488
2022-05-04 18:00 | 3.1627 | 3.4682 | 3.5041 | 3.5481 | 3.5994 | 2.553 | 3.0671 | 3.0952 | 3.1334 | 2.553 | 3.639 | 4.0937 | 4.1189 | 4.1524 | 4.3924
2022-05-04 19:00 | 2.9722 | 3.2733 | 3.3142 | 3.3643 | 3.4226 | 2.4387 | 2.9392 | 2.9711 | 3.0147 | 2.4387 | 3.7915 | 4.27 | 4.2987 | 4.3368 | 4.5908
2022-05-04 20:00 | 2.8579 | 3.1601 | 3.206 | 3.2621 | 3.3275 | 2.3625 | 2.8562 | 2.8919 | 2.9408 | 2.3625 | 3.9058 | 4.4039 | 4.436 | 4.4787 | 4.7445
2022-05-04 21:00 | 2.6293 | 2.9161 | 2.9628 | 3.0199 | 3.0866 | 2.1228 | 2.5742 | 2.6106 | 2.6603 | 2.1228 | 3.5819 | 4.0451 | 4.0778 | 4.1213 | 4.3702
2022-05-04 22:00 | 2.3816 | 2.6441 | 2.6877 | 2.7411 | 2.8034 | 1.8802 | 2.2832 | 2.3173 | 2.3637 | 1.8802 | 2.9913 | 3.3846 | 3.4152 | 3.4558 | 3.6688
2022-05-04 23:00 | 2.1339 | 2.3695 | 2.4089 | 2.457 | 2.5131 | 1.6195 | 1.9691 | 1.9998 | 2.0417 | 1.6195 | 2.172 | 2.4682 | 2.4957 | 2.5324 | 2.6956
2022-05-05 | 1.9075 | 2.1168 | 2.1513 | 2.1936 | 2.2428 | 1.3345 | 1.6255 | 1.6525 | 1.6892 | 1.3345 | 1.7909 | 2.0381 | 2.0622 | 2.0944 | 2.2312
2022-05-05 01:00 | 1.7719 | 1.9616 | 1.9912 | 2.0275 | 2.0697 | 1.2044 | 1.465 | 1.4881 | 1.5196 | 1.2044 | 1.7147 | 1.9466 | 1.9673 | 1.9949 | 2.1221
2022-05-05 02:00 | 1.6957 | 1.8676 | 1.8911 | 1.9198 | 1.9532 | 1.1622 | 1.4063 | 1.4246 | 1.4496 | 1.1622 | 1.4861 | 1.684 | 1.7004 | 1.7222 | 1.83
2022-05-05 03:00 | 1.6957 | 1.8558 | 1.8732 | 1.8945 | 1.9194 | 1.1622 | 1.3977 | 1.4113 | 1.4298 | 1.1622 | 1.5814 | 1.7814 | 1.7936 | 1.8098 | 1.9162
2022-05-05 04:00 | 1.7826 | 1.9391 | 1.9514 | 1.9664 | 1.9839 | 1.1929 | 1.4266 | 1.4362 | 1.4492 | 1.1929 | 1.81 | 2.0284 | 2.037 | 2.0484 | 2.1615
2022-05-05 05:00 | 1.9434 | 2.1079 | 2.1181 | 2.1306 | 2.1452 | 1.36 | 1.6212 | 1.6292 | 1.6401 | 1.36 | 1.9053 | 2.1314 | 2.1386 | 2.1481 | 2.2642
2022-05-05 06:00 | 2.3195 | 2.5153 | 2.5272 | 2.5418 | 2.5589 | 1.7591 | 2.0951 | 2.1044 | 2.1171 | 1.7591 | 2.7817 | 3.1077 | 3.1161 | 3.1272 | 3.2934
2022-05-05 07:00 | 2.7626 | 3.0005 | 3.017 | 3.0373 | 3.061 | 1.8481 | 2.2068 | 2.2198 | 2.2374 | 1.8481 | 2.7436 | 3.0718 | 3.0834 | 3.0988 | 3.2681
2022-05-05 08:00 | 2.7245 | 2.9729 | 2.9963 | 3.0249 | 3.0583 | 1.7606 | 2.1132 | 2.1314 | 2.1563 | 1.7606 | 2.4197 | 2.7213 | 2.7377 | 2.7595 | 2.9186
2022-05-05 09:00 | 2.0384 | 2.25 | 2.2807 | 2.3182 | 2.362 | 1.0751 | 1.3137 | 1.3376 | 1.3702 | 1.0751 | 0.91452 | 1.0588 | 1.0803 | 1.1089 | 1.1933
2022-05-05 10:00 | 1.9633 | 2.1803 | 2.2165 | 2.2609 | 2.3127 | 1.1813 | 1.4471 | 1.4753 | 1.514 | 1.1813 | 1.1241 | 1.2995 | 1.3249 | 1.3586 | 1.4608
2022-05-05 11:00 | 1.9815 | 2.2041 | 2.2426 | 2.2897 | 2.3446 | 1.0482 | 1.293 | 1.323 | 1.364 | 1.0482 | 1.5623 | 1.7895 | 1.8165 | 1.8523 | 1.981
2022-05-05 12:00 | 2.0577 | 2.2849 | 2.3229 | 2.3693 | 2.4235 | 0.99073 | 1.2244 | 1.254 | 1.2944 | 0.99073 | 1.6576 | 1.8946 | 1.9212 | 1.9565 | 2.0899
2022-05-05 13:00 | 1.9624 | 2.1776 | 2.213 | 2.2563 | 2.3068 | 0.93358 | 1.1532 | 1.1808 | 1.2185 | 0.93358 | 1.5433 | 1.764 | 1.7888 | 1.8218 | 1.946
2022-05-05 14:00 | 2.1529 | 2.3769 | 2.4095 | 2.4495 | 2.496 | 1.086 | 1.3294 | 1.3548 | 1.3896 | 1.086 | 1.086 | 1.2521 | 1.2749 | 1.3053 | 1.4014
2022-05-05 15:00 | 2.2291 | 2.4552 | 2.486 | 2.5237 | 2.5676 | 1.339 | 1.6257 | 1.6497 | 1.6825 | 1.339 | 1.2956 | 1.4824 | 1.504 | 1.5327 | 1.6382
2022-05-05 16:00 | 2.553 | 2.8023 | 2.8326 | 2.8698 | 2.9131 | 1.8893 | 2.2751 | 2.2988 | 2.3311 | 1.8893 | 2.4959 | 2.8157 | 2.837 | 2.8652 | 3.0362
2022-05-05 17:00 | 2.9722 | 3.2561 | 3.2883 | 3.3277 | 3.3736 | 2.3625 | 2.8367 | 2.8618 | 2.8961 | 2.3625 | 3.4146 | 3.8391 | 3.8617 | 3.8916 | 4.1152
2022-05-05 18:00 | 3.1056 | 3.4068 | 3.4427 | 3.4867 | 3.538 | 2.553 | 3.0671 | 3.0952 | 3.1334 | 2.553 | 4.5155 | 5.0677 | 5.0928 | 5.1263 | 5.4145
2022-05-05 19:00 | 3.0103 | 3.3142 | 3.3551 | 3.4052 | 3.4636 | 2.4578 | 2.9617 | 2.9936 | 3.0372 | 2.4578 | 4.0963 | 4.6088 | 4.6374 | 4.6755 | 4.9463
2022-05-05 20:00 | 3.0103 | 3.3239 | 3.3697 | 3.4258 | 3.4913 | 2.4387 | 2.9462 | 2.982 | 3.0308 | 2.4387 | 3.9629 | 4.4674 | 4.4996 | 4.5422 | 4.8112
2022-05-05 21:00 | 2.8579 | 3.1617 | 3.2084 | 3.2656 | 3.3322 | 2.2673 | 2.7448 | 2.7812 | 2.831 | 2.2673 | 3.6009 | 4.0663 | 4.099 | 4.1425 | 4.3924
2022-05-05 22:00 | 2.534 | 2.8078 | 2.8515 | 2.9049 | 2.9672 | 1.9854 | 2.4075 | 2.4416 | 2.4881 | 1.9854 | 3.0484 | 3.4481 | 3.4787 | 3.5193 | 3.7355
2022-05-05 23:00 | 2.4578 | 2.7175 | 2.7568 | 2.805 | 2.8611 | 1.7267 | 2.0958 | 2.1265 | 2.1684 | 1.7267 | 2.4578 | 2.7858 | 2.8133 | 2.8499 | 3.0289
2022-05-06 | 2.2101 | 2.442 | 2.4765 | 2.5187 | 2.5679 | 1.438 | 1.7479 | 1.7748 | 1.8115 | 1.438 | 2.172 | 2.4615 | 2.4857 | 2.5178 | 2.6756
2022-05-06 01:00 | 2.0386 | 2.2482 | 2.2778 | 2.314 | 2.3563 | 1.2976 | 1.5751 | 1.5982 | 1.6297 | 1.2976 | 2.0196 | 2.2853 | 2.3061 | 2.3337 | 2.4777
2022-05-06 02:00 | 2.0767 | 2.277 | 2.3005 | 2.3292 | 2.3626 | 1.2575 | 1.5189 | 1.5371 | 1.5621 | 1.2575 | 2.0196 | 2.2768 | 2.2932 | 2.315 | 2.4522
2022-05-06 03:00 | 2.0767 | 2.2652 | 2.2826 | 2.3039 | 2.3288 | 1.3146 | 1.5778 | 1.5914 | 1.6099 | 1.3146 | 2.0196 | 2.2684 | 2.2806 | 2.2968 | 2.4272
2022-05-06 04:00 | 2.1148 | 2.2961 | 2.3083 | 2.3233 | 2.3408 | 1.4427 | 1.7217 | 1.7313 | 1.7443 | 1.4427 | 2.1339 | 2.3883 | 2.3969 | 2.4083 | 2.5393
2022-05-06 05:00 | 2.5149 | 2.7219 | 2.7322 | 2.7447 | 2.7593 | 1.7703 | 2.1059 | 2.1139 | 2.1248 | 1.7703 | 2.5291 | 2.8247 | 2.8319 | 2.8414 | 2.9918
2022-05-06 06:00 | 3.135 | 3.3914 | 3.4034 | 3.418 | 3.435 | 2.3781 | 2.8264 | 2.8357 | 2.8484 | 2.3781 | 4.0201 | 4.4839 | 4.4923 | 4.5034 | 4.7377
2022-05-06 07:00 | 3.5438 | 3.8397 | 3.8563 | 3.8766 | 3.9002 | 2.5149 | 2.9946 | 3.0075 | 3.0252 | 2.5149 | 4.2678 | 4.7656 | 4.7772 | 4.7926 | 5.0457
2022-05-06 08:00 | 3.5819 | 3.894 | 3.9174 | 3.946 | 3.9794 | 2.4071 | 2.8769 | 2.8951 | 2.92 | 2.4071 | 3.2732 | 3.6698 | 3.6862 | 3.7079 | 3.9139
2022-05-06 09:00 | 2.8579 | 3.1304 | 3.1611 | 3.1986 | 3.2424 | 1.5702 | 1.8986 | 1.9225 | 1.9552 | 1.5702 | 1.3527 | 1.5458 | 1.5673 | 1.5958 | 1.7043
2022-05-06 10:00 | 2.5721 | 2.8343 | 2.8706 | 2.915 | 2.9667 | 1.1813 | 1.4471 | 1.4753 | 1.514 | 1.1813 | 0.81926 | 0.9607 | 0.98611 | 1.0199 | 1.1053
2022-05-06 11:00 | 2.2863 | 2.5316 | 2.5701 | 2.6172 | 2.6721 | 1.1241 | 1.3827 | 1.4127 | 1.4537 | 1.1241 | 1.0479 | 1.2178 | 1.2448 | 1.2806 | 1.3811
2022-05-06 12:00 | 2.4959 | 2.7557 | 2.7937 | 2.8401 | 2.8943 | 1.4099 | 1.7195 | 1.7491 | 1.7895 | 1.4099 | 1.3527 | 1.5559 | 1.5824 | 1.6178 | 1.7344
2022-05-06 13:00 | 2.4722 | 2.7253 | 2.7606 | 2.804 | 2.8545 | 1.346 | 1.6404 | 1.668 | 1.7057 | 1.346 | 1.6576 | 1.8911 | 1.9159 | 1.9488 | 2.0794
2022-05-06 14:00 | 2.8198 | 3.0933 | 3.1259 | 3.1659 | 3.2125 | 1.6004 | 1.9371 | 1.9625 | 1.9973 | 1.6004 | 1.829 | 2.0778 | 2.1007 | 2.131 | 2.2679
2022-05-06 15:00 | 2.7626 | 3.0283 | 3.0591 | 3.0968 | 3.1408 | 1.7338 | 2.092 | 2.116 | 2.1488 | 1.7338 | 1.9053 | 2.1599 | 2.1815 | 2.2102 | 2.3492
2022-05-06 16:00 | 3.0103 | 3.2935 | 3.3239 | 3.3611 | 3.4044 | 2.3266 | 2.7917 | 2.8154 | 2.8477 | 2.3266 | 3.8867 | 4.3613 | 4.3825 | 4.4108 | 4.6583
2022-05-06 17:00 | 3.3723 | 3.686 | 3.7182 | 3.7575 | 3.8035 | 2.8876 | 3.457 | 3.4821 | 3.5163 | 2.8876 | 4.3059 | 4.8296 | 4.8521 | 4.882 | 5.1546
2022-05-06 18:00 | 3.3723 | 3.6934 | 3.7293 | 3.7733 | 3.8246 | 2.9913 | 3.5848 | 3.6129 | 3.6511 | 2.9913 | 4.344 | 4.8771 | 4.9023 | 4.9357 | 5.2145
2022-05-06 19:00 | 3.3914 | 3.7236 | 3.7645 | 3.8146 | 3.873 | 3.0103 | 3.6144 | 3.6463 | 3.6899 | 3.0103 | 4.9918 | 5.6039 | 5.6325 | 5.6706 | 5.9906
2022-05-06 20:00 | 3.4485 | 3.7947 | 3.8405 | 3.8966 | 3.9621 | 2.8769 | 3.4639 | 3.4997 | 3.5485 | 2.8769 | 4.4583 | 5.0179 | 5.05 | 5.0927 | 5.3889
2022-05-06 21:00 | 3.3151 | 3.653 | 3.6997 | 3.7568 | 3.8235 | 2.7626 | 3.33 | 3.3664 | 3.4162 | 2.7626 | 4.706 | 5.2943 | 5.327 | 5.3705 | 5.6812
2022-05-06 22:00 | 3.0294 | 3.34 | 3.3837 | 3.4371 | 3.4994 | 2.534 | 3.0556 | 3.0897 | 3.1361 | 2.534 | 3.982 | 4.4855 | 4.5161 | 4.5568 | 4.8242
2022-05-06 23:00 | 2.8346 | 3.1223 | 3.1616 | 3.2098 | 3.2659 | 2.172 | 2.6218 | 2.6525 | 2.6944 | 2.172 | 3.3914 | 3.8232 | 3.8508 | 3.8874 | 4.1176
2022-05-07 | 2.5911 | 2.8513 | 2.8858 | 2.9281 | 2.9773 | 1.7394 | 2.1039 | 2.1308 | 2.1675 | 1.7394 | 2.8769 | 3.2449 | 3.269 | 3.3012 | 3.4977
2022-05-07 01:00 | 2.4197 | 2.6575 | 2.6872 | 2.7234 | 2.7657 | 1.5567 | 1.8812 | 1.9043 | 1.9358 | 1.5567 | 2.4578 | 2.7723 | 2.793 | 2.8206 | 2.9887
2022-05-07 02:00 | 2.2144 | 2.4249 | 2.4484 | 2.4771 | 2.5105 | 1.4531 | 1.75 | 1.7683 | 1.7932 | 1.4531 | 2.3816 | 2.6791 | 2.6955 | 2.7173 | 2.8743
2022-05-07 03:00 | 2.2482 | 2.4494 | 2.4668 | 2.4881 | 2.513 | 1.448 | 1.7353 | 1.7489 | 1.7675 | 1.448 | 2.2482 | 2.5225 | 2.5347 | 2.5509 | 2.6938
2022-05-07 04:00 | 2.2101 | 2.3984 | 2.4107 | 2.4257 | 2.4432 | 1.4289 | 1.7055 | 1.7151 | 1.7281 | 1.4289 | 2.3625 | 2.6424 | 2.651 | 2.6624 | 2.8059
2022-05-07 05:00 | 2.3435 | 2.5377 | 2.5479 | 2.5605 | 2.5751 | 1.6766 | 1.9952 | 2.0032 | 2.0141 | 1.6766 | 2.6483 | 2.9571 | 2.9643 | 2.9738 | 3.1308
2022-05-07 06:00 | 2.534 | 2.7457 | 2.7577 | 2.7723 | 2.7893 | 1.9243 | 2.2903 | 2.2996 | 2.3123 | 1.9243 | 3.3533 | 3.7429 | 3.7512 | 3.7623 | 3.96
2022-05-07 07:00 | 2.6674 | 2.8981 | 2.9147 | 2.935 | 2.9586 | 2.2101 | 2.6345 | 2.6474 | 2.6651 | 2.2101 | 3.7152 | 4.1516 | 4.1632 | 4.1786 | 4.4013
2022-05-07 08:00 | 2.8007 | 3.0547 | 3.0781 | 3.1068 | 3.1402 | 2.1529 | 2.5767 | 2.5949 | 2.6198 | 2.1529 | 3.4866 | 3.907 | 3.9234 | 3.9451 | 4.1629
2022-05-07 09:00 | 2.8579 | 3.1304 | 3.1611 | 3.1986 | 3.2424 | 2.1529 | 2.587 | 2.6109 | 2.6436 | 2.1529 | 2.6483 | 2.9855 | 3.007 | 3.0355 | 3.2153
2022-05-07 10:00 | 2.5721 | 2.8343 | 2.8706 | 2.915 | 2.9667 | 1.9434 | 2.3474 | 2.3757 | 2.4143 | 1.9434 | 2.4768 | 2.8027 | 2.8281 | 2.8619 | 3.0384
2022-05-07 11:00 | 2.1529 | 2.3883 | 2.4268 | 2.4739 | 2.5288 | 1.6766 | 2.0354 | 2.0654 | 2.1064 | 1.6766 | 2.6102 | 2.954 | 2.9809 | 3.0168 | 3.2031
2022-05-07 12:00 | 2.9531 | 3.247 | 3.2849 | 3.3314 | 3.3855 | 2.1049 | 2.5406 | 2.5702 | 2.6106 | 2.1049 | 3.2239 | 3.6352 | 3.6618 | 3.6972 | 3.9166
2022-05-07 13:00 | 2.896 | 3.1806 | 3.216 | 3.2593 | 3.3098 | 2.1339 | 2.5712 | 2.5988 | 2.6365 | 2.1339 | 3.7724 | 4.2412 | 4.266 | 4.299 | 4.5457
2022-05-07 14:00 | 2.7817 | 3.0524 | 3.085 | 3.1249 | 3.1715 | 2.0958 | 2.5223 | 2.5477 | 2.5825 | 2.0958 | 3.0294 | 3.4117 | 3.4345 | 3.4649 | 3.6678
2022-05-07 15:00 | 2.7436 | 3.0078 | 3.0386 | 3.0763 | 3.1203 | 2.191 | 2.6322 | 2.6562 | 2.689 | 2.191 | 2.915 | 3.2821 | 3.3037 | 3.3323 | 3.5269
2022-05-07 16:00 | 3.0294 | 3.314 | 3.3444 | 3.3815 | 3.4249 | 2.5773 | 3.0879 | 3.1116 | 3.1439 | 2.5773 | 3.8677 | 4.3401 | 4.3614 | 4.3896 | 4.636
2022-05-07 17:00 | 3.6771 | 4.0135 | 4.0457 | 4.0851 | 4.131 | 3.0294 | 3.6245 | 3.6496 | 3.6839 | 3.0294 | 5.1251 | 5.74 | 5.7625 | 5.7925 | 6.11
2022-05-07 18:00 | 3.5628 | 3.898 | 3.934 | 3.978 | 4.0292 | 3.0675 | 3.6749 | 3.7029 | 3.7412 | 3.0675 | 4.9537 | 5.5546 | 5.5798 | 5.6133 | 5.9256
2022-05-07 19:00 | 3.3723 | 3.7031 | 3.744 | 3.7941 | 3.8525 | 2.8198 | 3.3893 | 3.4213 | 3.4648 | 2.8198 | 5.0299 | 5.6462 | 5.6749 | 5.713 | 6.035
2022-05-07 20:00 | 3.3342 | 3.6718 | 3.7177 | 3.7738 | 3.8393 | 2.8388 | 3.4189 | 3.4546 | 3.5035 | 2.8388 | 4.6869 | 5.272 | 5.3041 | 5.3468 | 5.6555
2022-05-07 21:00 | 3.2199 | 3.5507 | 3.5973 | 3.6545 | 3.7211 | 2.5911 | 3.1275 | 3.1639 | 3.2136 | 2.5911 | 4.344 | 4.892 | 4.9247 | 4.9682 | 5.259
2022-05-07 22:00 | 2.9341 | 3.2377 | 3.2813 | 3.3347 | 3.397 | 2.4174 | 2.9179 | 2.9519 | 2.9984 | 2.4174 | 3.7724 | 4.2526 | 4.2832 | 4.3239 | 4.5798
2022-05-07 23:00 | 2.6483 | 2.9222 | 2.9615 | 3.0097 | 3.0658 | 2.0972 | 2.5335 | 2.5642 | 2.6061 | 2.0972 | 3.3151 | 3.7385 | 3.7661 | 3.8027 | 4.0287
2022-05-08 | 2.4387 | 2.6876 | 2.7221 | 2.7643 | 2.8136 | 1.8338 | 2.2155 | 2.2424 | 2.2791 | 1.8338 | 2.553 | 2.8849 | 2.9091 | 2.9412 | 3.12
2022-05-08 01:00 | 2.2673 | 2.4938 | 2.5234 | 2.5597 | 2.6019 | 1.5785 | 1.9069 | 1.93 | 1.9616 | 1.5785 | 2.3816 | 2.6876 | 2.7084 | 2.7359 | 2.8998
2022-05-08 02:00 | 2.1148 | 2.318 | 2.3414 | 2.3701 | 2.4036 | 1.4835 | 1.7859 | 1.8042 | 1.8292 | 1.4835 | 2.2482 | 2.5308 | 2.5473 | 2.5691 | 2.7188
2022-05-08 03:00 | 2.1339 | 2.3266 | 2.344 | 2.3653 | 2.3902 | 1.4254 | 1.7086 | 1.7222 | 1.7407 | 1.4254 | 2.191 | 2.459 | 2.4711 | 2.4874 | 2.6272
2022-05-08 04:00 | 2.1148 | 2.2961 | 2.3083 | 2.3233 | 2.3408 | 1.4099 | 1.683 | 1.6926 | 1.7056 | 1.4099 | 2.1148 | 2.3671 | 2.3757 | 2.3871 | 2.517
2022-05-08 05:00 | 2.2291 | 2.4149 | 2.4251 | 2.4377 | 2.4523 | 1.5082 | 1.7963 | 1.8043 | 1.8152 | 1.5082 | 2.3244 | 2.5972 | 2.6044 | 2.6139 | 2.7531
2022-05-08 06:00 | 2.3244 | 2.5206 | 2.5325 | 2.5471 | 2.5642 | 1.7719 | 2.1102 | 2.1195 | 2.1322 | 1.7719 | 2.5721 | 2.8748 | 2.8832 | 2.8943 | 3.049
2022-05-08 07:00 | 2.3435 | 2.5501 | 2.5667 | 2.587 | 2.6107 | 1.9434 | 2.3194 | 2.3323 | 2.35 | 1.9434 | 2.9341 | 3.2835 | 3.2951 | 3.3106 | 3.4903
2022-05-08 08:00 | 2.191 | 2.3997 | 2.4231 | 2.4518 | 2.4852 | 1.8862 | 2.2615 | 2.2798 | 2.3047 | 1.8862 | 2.5227 | 2.8359 | 2.8522 | 2.874 | 3.0388
2022-05-08 09:00 | 1.9624 | 2.1684 | 2.199 | 2.2366 | 2.2804 | 1.5242 | 1.8442 | 1.8682 | 1.9008 | 1.5242 | 1.6766 | 1.9057 | 1.9272 | 1.9558 | 2.0821
2022-05-08 10:00 | 1.829 | 2.036 | 2.0723 | 2.1167 | 2.1684 | 1.1892 | 1.4565 | 1.4848 | 1.5234 | 1.1892 | 0.93358 | 1.0877 | 1.1131 | 1.1469 | 1.2386
2022-05-08 11:00 | 1.6195 | 1.8152 | 1.8537 | 1.9008 | 1.9557 | 0.89547 | 1.1126 | 1.1426 | 1.1836 | 0.89547 | 0.91452 | 1.0696 | 1.0966 | 1.1324 | 1.2255
2022-05-08 12:00 | 1.3527 | 1.5276 | 1.5655 | 1.612 | 1.6661 | 0.87642 | 1.0893 | 1.1189 | 1.1593 | 0.87642 | 1.086 | 1.2594 | 1.286 | 1.3214 | 1.4233
2022-05-08 13:00 | 1.4861 | 1.6659 | 1.7013 | 1.7446 | 1.7951 | 0.99073 | 1.2207 | 1.2484 | 1.2861 | 0.99073 | 1.0288 | 1.1924 | 1.2172 | 1.2502 | 1.3461
2022-05-08 14:00 | 2.0767 | 2.295 | 2.3276 | 2.3676 | 2.4142 | 1.2575 | 1.5319 | 1.5574 | 1.5921 | 1.2575 | 1.0479 | 1.2097 | 1.2326 | 1.263 | 1.3569
2022-05-08 15:00 | 2.2101 | 2.4347 | 2.4655 | 2.5032 | 2.5472 | 1.4861 | 1.7994 | 1.8234 | 1.8562 | 1.4861 | 1.7528 | 1.9906 | 2.0121 | 2.0408 | 2.1715
2022-05-08 16:00 | 2.5605 | 2.8103 | 2.8406 | 2.8778 | 2.9211 | 2.0464 | 2.4607 | 2.4844 | 2.5167 | 2.0464 | 2.896 | 3.2603 | 3.2816 | 3.3098 | 3.5028
2022-05-08 17:00 | 3.1056 | 3.3994 | 3.4316 | 3.471 | 3.5169 | 2.6864 | 3.2194 | 3.2445 | 3.2787 | 2.6864 | 3.8486 | 4.3214 | 4.344 | 4.3739 | 4.6213
2022-05-08 18:00 | 3.277 | 3.591 | 3.6269 | 3.6709 | 3.7222 | 2.7436 | 3.2922 | 3.3203 | 3.3585 | 2.7436 | 4.4583 | 5.0041 | 5.0293 | 5.0628 | 5.3479
2022-05-08 19:00 | 3.277 | 3.6008 | 3.6417 | 3.6918 | 3.7502 | 2.6864 | 3.2318 | 3.2637 | 3.3073 | 2.6864 | 4.8012 | 5.3922 | 5.4208 | 5.4589 | 5.7684
2022-05-08 20:00 | 3.2389 | 3.5695 | 3.6153 | 3.6715 | 3.7369 | 2.7245 | 3.2838 | 3.3196 | 3.3684 | 2.7245 | 3.8433 | 4.3345 | 4.3666 | 4.4093 | 4.6716
2022-05-08 21:00 | 3.1437 | 3.4688 | 3.5155 | 3.5726 | 3.6392 | 2.5527 | 3.0821 | 3.1185 | 3.1682 | 2.5527 | 4.1344 | 4.6591 | 4.6918 | 4.7353 | 5.0146
2022-05-08 22:00 | 2.9341 | 3.2377 | 3.2813 | 3.3347 | 3.397 | 2.191 | 2.6505 | 2.6845 | 2.731 | 2.191 | 3.2008 | 3.6175 | 3.6481 | 3.6887 | 3.9132
2022-05-08 23:00 | 2.553 | 2.8198 | 2.8592 | 2.9073 | 2.9635 | 1.7794 | 2.158 | 2.1887 | 2.2306 | 1.7794 | 2.6102 | 2.9552 | 2.9827 | 3.0193 | 3.2066
2022-05-09 | 2.193 | 2.4235 | 2.458 | 2.5003 | 2.5495 | 1.5814 | 1.9172 | 1.9441 | 1.9809 | 1.5814 | 2.1529 | 2.4403 | 2.4645 | 2.4966 | 2.6534
2022-05-09 01:00 | 2.0005 | 2.2072 | 2.2368 | 2.2731 | 2.3154 | 1.448 | 1.7527 | 1.7758 | 1.8074 | 1.448 | 2.0005 | 2.2642 | 2.2849 | 2.3125 | 2.4554
2022-05-09 02:00 | 2.0005 | 2.1951 | 2.2186 | 2.2473 | 2.2808 | 1.3527 | 1.6314 | 1.6497 | 1.6747 | 1.3527 | 1.9624 | 2.2133 | 2.2297 | 2.2515 | 2.3855
2022-05-09 03:00 | 2.0577 | 2.2447 | 2.2621 | 2.2834 | 2.3083 | 1.2956 | 1.5553 | 1.5689 | 1.5874 | 1.2956 | 2.0767 | 2.3319 | 2.3441 | 2.3603 | 2.4939
2022-05-09 04:00 | 2.0767 | 2.2551 | 2.2674 | 2.2824 | 2.2999 | 1.4077 | 1.6804 | 1.69 | 1.7031 | 1.4077 | 2.0386 | 2.2824 | 2.291 | 2.3024 | 2.4282
2022-05-09 05:00 | 2.5096 | 2.7162 | 2.7264 | 2.7389 | 2.7535 | 1.7025 | 2.0258 | 2.0338 | 2.0447 | 1.7025 | 2.4959 | 2.7878 | 2.7949 | 2.8045 | 2.953
2022-05-09 06:00 | 2.9531 | 3.1961 | 3.208 | 3.2226 | 3.2396 | 2.2291 | 2.6504 | 2.6597 | 2.6724 | 2.2291 | 3.5628 | 3.9758 | 3.9841 | 3.9952 | 4.2044
2022-05-09 07:00 | 3.4485 | 3.7373 | 3.7539 | 3.7742 | 3.7979 | 2.553 | 3.0396 | 3.0526 | 3.0702 | 2.553 | 4.4392 | 4.9561 | 4.9677 | 4.9832 | 5.2457
2022-05-09 08:00 | 3.1056 | 3.3822 | 3.4056 | 3.4343 | 3.4677 | 2.3549 | 2.8152 | 2.8335 | 2.8584 | 2.3549 | 3.1767 | 3.5626 | 3.579 | 3.6008 | 3.8015
2022-05-09 09:00 | 2.7055 | 2.9666 | 2.9973 | 3.0349 | 3.0786 | 1.6576 | 2.0018 | 2.0257 | 2.0584 | 1.6576 | 1.6195 | 1.8422 | 1.8637 | 1.8922 | 2.0154
2022-05-09 10:00 | 2.4387 | 2.691 | 2.7273 | 2.7717 | 2.8234 | 1.2194 | 1.4921 | 1.5204 | 1.559 | 1.2194 | 1.0479 | 1.2148 | 1.2402 | 1.2739 | 1.3719
2022-05-09 11:00 | 2.6483 | 2.9205 | 2.959 | 3.0061 | 3.061 | 1.4289 | 1.7428 | 1.7728 | 1.8138 | 1.4289 | 1.0669 | 1.239 | 1.266 | 1.3018 | 1.4033
2022-05-09 12:00 | 2.191 | 2.4282 | 2.4662 | 2.5126 | 2.5668 | 1.2575 | 1.5395 | 1.5691 | 1.6095 | 1.2575 | 1.2384 | 1.4288 | 1.4554 | 1.4907 | 1.6011
2022-05-09 13:00 | 2.2863 | 2.5256 | 2.561 | 2.6043 | 2.6548 | 1.3146 | 1.6034 | 1.631 | 1.6687 | 1.3146 | 1.1432 | 1.3194 | 1.3442 | 1.3772 | 1.4794
2022-05-09 14:00 | 2.534 | 2.7863 | 2.8189 | 2.8588 | 2.9054 | 1.5192 | 1.8411 | 1.8666 | 1.9013 | 1.5192 | 1.3527 | 1.5485 | 1.5714 | 1.6017 | 1.7124
2022-05-09 15:00 | 2.5911 | 2.8441 | 2.8749 | 2.9126 | 2.9565 | 1.7338 | 2.092 | 2.116 | 2.1488 | 1.7338 | 1.8862 | 2.1388 | 2.1604 | 2.189 | 2.327
2022-05-09 16:00 | 2.9531 | 3.2321 | 3.2625 | 3.2997 | 3.343 | 2.1741 | 2.6115 | 2.6352 | 2.6675 | 2.1741 | 2.8579 | 3.2179 | 3.2392 | 3.2675 | 3.4584
2022-05-09 17:00 | 3.3533 | 3.6655 | 3.6977 | 3.7371 | 3.783 | 2.6087 | 3.1275 | 3.1526 | 3.1869 | 2.6087 | 3.7724 | 4.2367 | 4.2593 | 4.2892 | 4.5324
2022-05-09 18:00 | 3.2961 | 3.6115 | 3.6474 | 3.6914 | 3.7427 | 2.7626 | 3.3147 | 3.3428 | 3.381 | 2.7626 | 4.7822 | 5.3641 | 5.3892 | 5.4227 | 5.7256
2022-05-09 19:00 | 3.1818 | 3.4984 | 3.5393 | 3.5894 | 3.6478 | 2.7245 | 3.2768 | 3.3087 | 3.3523 | 2.7245 | 5.2013 | 5.8368 | 5.8654 | 5.9035 | 6.235
2022-05-09 20:00 | 3.0484 | 3.3648 | 3.4107 | 3.4668 | 3.5322 | 2.4957 | 3.0135 | 3.0493 | 3.0981 | 2.4957 | 4.1344 | 4.658 | 4.6901 | 4.7328 | 5.0111
2022-05-09 21:00 | 2.8198 | 3.1208 | 3.1675 | 3.2246 | 3.2913 | 2.4006 | 2.9024 | 2.9388 | 2.9885 | 2.4006 | 3.4866 | 3.9393 | 3.972 | 4.0155 | 4.2591
2022-05-09 22:00 | 2.6483 | 2.9306 | 2.9743 | 3.0277 | 3.09 | 2.0577 | 2.4929 | 2.527 | 2.5734 | 2.0577 | 3.258 | 3.681 | 3.7116 | 3.7522 | 3.9799
2022-05-09 23:00 | 2.2673 | 2.5128 | 2.5521 | 2.6003 | 2.6564 | 1.6957 | 2.0591 | 2.0898 | 2.1317 | 1.6957 | 2.6102 | 2.9552 | 2.9827 | 3.0193 | 3.2066
2022-05-10 | 2.025 | 2.2431 | 2.2776 | 2.3198 | 2.3691 | 1.4849 | 1.8033 | 1.8302 | 1.867 | 1.4849 | 2.0196 | 2.2921 | 2.3163 | 2.3484 | 2.4979
2022-05-10 01:00 | 1.9053 | 2.1049 | 2.1345 | 2.1707 | 2.213 | 1.3718 | 1.6627 | 1.6858 | 1.7173 | 1.3718 | 2.5149 | 2.8358 | 2.8566 | 2.8841 | 3.0554
2022-05-10 02:00 | 1.829 | 2.0109 | 2.0344 | 2.0631 | 2.0965 | 1.2575 | 1.5189 | 1.5371 | 1.5621 | 1.2575 | 1.7338 | 1.9592 | 1.9756 | 1.9975 | 2.1189
2022-05-10 03:00 | 1.829 | 1.9991 | 2.0165 | 2.0378 | 2.0627 | 1.2376 | 1.4868 | 1.5004 | 1.519 | 1.2376 | 1.7147 | 1.9296 | 1.9418 | 1.958 | 2.0717
2022-05-10 04:00 | 1.9434 | 2.1118 | 2.1241 | 2.1391 | 2.1566 | 1.3146 | 1.5705 | 1.58 | 1.5931 | 1.3146 | 1.8862 | 2.1131 | 2.1216 | 2.1331 | 2.2504
2022-05-10 05:00 | 2.1751 | 2.3568 | 2.3671 | 2.3796 | 2.3942 | 1.5884 | 1.891 | 1.899 | 1.9098 | 1.5884 | 2.3054 | 2.576 | 2.5832 | 2.5927 | 2.7309
2022-05-10 06:00 | 2.6877 | 2.9109 | 2.9229 | 2.9375 | 2.9545 | 1.9624 | 2.3353 | 2.3446 | 2.3573 | 1.9624 | 2.896 | 3.2347 | 3.2431 | 3.2542 | 3.4267
2022-05-10 07:00 | 2.9531 | 3.2051 | 3.2217 | 3.242 | 3.2657 | 2.1529 | 2.567 | 2.5799 | 2.5975 | 2.1529 | 3.2008 | 3.5799 | 3.5915 | 3.607 | 3.8014
2022-05-10 08:00 | 2.9913 | 3.2594 | 3.2828 | 3.3115 | 3.3449 | 2.1209 | 2.5388 | 2.557 | 2.5819 | 2.1209 | 2.9531 | 3.3142 | 3.3305 | 3.3523 | 3.5407
2022-05-10 09:00 | 2.9913 | 3.2737 | 3.3044 | 3.3419 | 3.3857 | 1.7719 | 2.1368 | 2.1608 | 2.1934 | 1.7719 | 2.2482 | 2.5409 | 2.5624 | 2.5909 | 2.7487
2022-05-10 10:00 | 2.7817 | 3.0595 | 3.0957 | 3.1401 | 3.1919 | 1.6957 | 2.0548 | 2.083 | 2.1217 | 1.6957 | 1.9434 | 2.2099 | 2.2353 | 2.269 | 2.4162
2022-05-10 11:00 | 2.5149 | 2.7772 | 2.8157 | 2.8628 | 2.9177 | 1.6195 | 1.9679 | 1.9979 | 2.0389 | 1.6195 | 1.6195 | 1.853 | 1.88 | 1.9158 | 2.0477
2022-05-10 12:00 | 2.7245 | 3.0013 | 3.0393 | 3.0857 | 3.1399 | 1.6195 | 1.9671 | 1.9967 | 2.0371 | 1.6195 | 1.9243 | 2.191 | 2.2176 | 2.2529 | 2.401
2022-05-10 13:00 | 2.6483 | 2.9145 | 2.9499 | 2.9932 | 3.0437 | 1.6385 | 1.986 | 2.0136 | 2.0513 | 1.6385 | 1.7338 | 1.9758 | 2.0006 | 2.0335 | 2.1682
2022-05-10 14:00 | 2.7817 | 3.0524 | 3.085 | 3.1249 | 3.1715 | 1.7528 | 2.1171 | 2.1426 | 2.1773 | 1.7528 | 2.0577 | 2.3319 | 2.3547 | 2.3851 | 2.5346
2022-05-10 15:00 | 2.7055 | 2.9669 | 2.9977 | 3.0354 | 3.0794 | 1.8224 | 2.1966 | 2.2207 | 2.2535 | 1.8224 | 2.4959 | 2.8163 | 2.8379 | 2.8665 | 3.038
2022-05-10 16:00 | 2.8198 | 3.0888 | 3.1192 | 3.1564 | 3.1997 | 2.2291 | 2.6766 | 2.7003 | 2.7326 | 2.2291 | 3.2961 | 3.7049 | 3.7262 | 3.7545 | 3.9695
2022-05-10 17:00 | 3.3151 | 3.6246 | 3.6568 | 3.6961 | 3.7421 | 2.601 | 3.1184 | 3.1435 | 3.1778 | 2.601 | 4.0201 | 4.512 | 4.5345 | 4.5645 | 4.8213
2022-05-10 18:00 | 3.3342 | 3.6524 | 3.6883 | 3.7323 | 3.7836 | 2.7436 | 3.2922 | 3.3203 | 3.3585 | 2.7436 | 4.5155 | 5.0677 | 5.0928 | 5.1263 | 5.4145
2022-05-10 19:00 | 3.2199 | 3.5394 | 3.5803 | 3.6303 | 3.6887 | 2.8388 | 3.4118 | 3.4438 | 3.4873 | 2.8388 | 4.2106 | 4.7358 | 4.7645 | 4.8026 | 5.0796
2022-05-10 20:00 | 3.0865 | 3.4057 | 3.4516 | 3.5077 | 3.5732 | 2.553 | 3.0813 | 3.117 | 3.1659 | 2.553 | 4.2868 | 4.8274 | 4.8595 | 4.9022 | 5.1889
2022-05-10 21:00 | 2.8769 | 3.1822 | 3.2289 | 3.286 | 3.3527 | 2.4449 | 2.9547 | 2.9911 | 3.0408 | 2.4449 | 3.5057 | 3.9604 | 3.9932 | 4.0366 | 4.2813
2022-05-10 22:00 | 2.4721 | 2.7413 | 2.7849 | 2.8383 | 2.9006 | 1.9789 | 2.3999 | 2.4339 | 2.4804 | 1.9789 | 3.258 | 3.681 | 3.7116 | 3.7522 | 3.9799
2022-05-10 23:00 | 2.2673 | 2.5128 | 2.5521 | 2.6003 | 2.6564 | 1.7012 | 2.0656 | 2.0963 | 2.1382 | 1.7012 | 2.4959 | 2.8281 | 2.8557 | 2.8923 | 3.0733
2022-05-11 | 1.9665 | 2.1803 | 2.2148 | 2.257 | 2.3063 | 1.4099 | 1.7146 | 1.7416 | 1.7783 | 1.4099 | 1.9053 | 2.1651 | 2.1893 | 2.2214 | 2.3645
2022-05-11 01:00 | 1.8481 | 2.0435 | 2.0731 | 2.1093 | 2.1516 | 1.2765 | 1.5501 | 1.5732 | 1.6048 | 1.2765 | 1.829 | 2.0736 | 2.0944 | 2.1219 | 2.2555
2022-05-11 02:00 | 1.8481 | 2.0314 | 2.0548 | 2.0835 | 2.117 | 1.272 | 1.536 | 1.5543 | 1.5793 | 1.272 | 1.81 | 2.0439 | 2.0603 | 2.0821 | 2.2077
2022-05-11 03:00 | 1.7909 | 1.9582 | 1.9756 | 1.9969 | 2.0217 | 1.2003 | 1.4427 | 1.4563 | 1.4749 | 1.2003 | 1.7719 | 1.9932 | 2.0054 | 2.0216 | 2.1384
2022-05-11 04:00 | 1.8481 | 2.0095 | 2.0218 | 2.0368 | 2.0543 | 1.2602 | 1.5061 | 1.5157 | 1.5287 | 1.2602 | 1.8672 | 2.0919 | 2.1005 | 2.1119 | 2.2282
2022-05-11 05:00 | 2.172 | 2.3535 | 2.3637 | 2.3762 | 2.3909 | 1.53 | 1.822 | 1.83 | 1.8409 | 1.53 | 2.0386 | 2.2796 | 2.2868 | 2.2963 | 2.4198
2022-05-11 06:00 | 2.553 | 2.7662 | 2.7781 | 2.7928 | 2.8098 | 1.9029 | 2.265 | 2.2743 | 2.287 | 1.9029 | 2.896 | 3.2347 | 3.2431 | 3.2542 | 3.4267
2022-05-11 07:00 | 2.9341 | 3.1847 | 3.2013 | 3.2215 | 3.2452 | 2.1529 | 2.567 | 2.5799 | 2.5975 | 2.1529 | 3.639 | 4.0669 | 4.0785 | 4.0939 | 4.3125
2022-05-11 08:00 | 2.9531 | 3.2185 | 3.2419 | 3.2705 | 3.3039 | 2.0767 | 2.4866 | 2.5049 | 2.5298 | 2.0767 | 3.1818 | 3.5682 | 3.5846 | 3.6064 | 3.8074
2022-05-11 09:00 | 3.0103 | 3.2941 | 3.3248 | 3.3624 | 3.4061 | 1.81 | 2.1819 | 2.2058 | 2.2385 | 1.81 | 2.1148 | 2.3927 | 2.4142 | 2.4427 | 2.5931
2022-05-11 10:00 | 2.8769 | 3.1618 | 3.1981 | 3.2425 | 3.2942 | 1.8481 | 2.2348 | 2.2631 | 2.3017 | 1.8481 | 2.1148 | 2.4004 | 2.4258 | 2.4596 | 2.6162
2022-05-11 11:00 | 2.7817 | 3.0638 | 3.1023 | 3.1494 | 3.2043 | 1.7528 | 2.1254 | 2.1555 | 2.1964 | 1.7528 | 1.9053 | 2.1706 | 2.1976 | 2.2334 | 2.381
2022-05-11 12:00 | 3.0294 | 3.3288 | 3.3668 | 3.4132 | 3.4674 | 1.9243 | 2.3272 | 2.3568 | 2.3973 | 1.9243 | 2.2863 | 2.5933 | 2.6199 | 2.6552 | 2.8231
2022-05-11 13:00 | 2.8769 | 3.1601 | 3.1955 | 3.2388 | 3.2894 | 1.8481 | 2.2336 | 2.2612 | 2.2989 | 1.8481 | 2.2482 | 2.5474 | 2.5722 | 2.6052 | 2.7682
2022-05-11 14:00 | 2.8579 | 3.1342 | 3.1669 | 3.2068 | 3.2534 | 1.8481 | 2.2297 | 2.2551 | 2.2899 | 1.8481 | 2.3054 | 2.6071 | 2.63 | 2.6604 | 2.8234
2022-05-11 15:00 | 2.915 | 3.1921 | 3.2229 | 3.2606 | 3.3045 | 2.0577 | 2.4746 | 2.4987 | 2.5315 | 2.0577 | 2.7245 | 3.0704 | 3.0919 | 3.1206 | 3.3047
2022-05-11 16:00 | 3.1437 | 3.4368 | 3.4672 | 3.5043 | 3.5477 | 2.417 | 2.8985 | 2.9222 | 2.9545 | 2.417 | 3.4866 | 3.9166 | 3.9379 | 3.9662 | 4.1917
2022-05-11 17:00 | 3.3914 | 3.7065 | 3.7386 | 3.778 | 3.8239 | 2.6674 | 3.1968 | 3.2219 | 3.2562 | 2.6674 | 4.2868 | 4.8084 | 4.8309 | 4.8609 | 5.1324
2022-05-11 18:00 | 3.3533 | 3.6729 | 3.7088 | 3.7528 | 3.8041 | 2.9341 | 3.5173 | 3.5453 | 3.5836 | 2.9341 | 4.2868 | 4.8136 | 4.8388 | 4.8722 | 5.1479
2022-05-11 19:00 | 3.2961 | 3.6212 | 3.6621 | 3.7122 | 3.7706 | 2.896 | 3.4794 | 3.5113 | 3.5549 | 2.896 | 5.068 | 5.6886 | 5.7172 | 5.7553 | 6.0795
2022-05-11 20:00 | 3.1437 | 3.4671 | 3.513 | 3.5691 | 3.6346 | 2.5721 | 3.1038 | 3.1395 | 3.1884 | 2.5721 | 4.725 | 5.3143 | 5.3464 | 5.3891 | 5.6999
2022-05-11 21:00 | 2.824 | 3.1254 | 3.1721 | 3.2292 | 3.2959 | 2.4387 | 2.9474 | 2.9838 | 3.0335 | 2.4387 | 3.5247 | 3.9816 | 4.0143 | 4.0578 | 4.3035
2022-05-11 22:00 | 2.5149 | 2.7873 | 2.831 | 2.8844 | 2.9467 | 2.1369 | 2.5865 | 2.6205 | 2.667 | 2.1369 | 3.0484 | 3.4481 | 3.4787 | 3.5193 | 3.7355
2022-05-11 23:00 | 2.2291 | 2.4719 | 2.5112 | 2.5593 | 2.6155 | 1.7316 | 2.1016 | 2.1322 | 2.1741 | 1.7316 | 2.4959 | 2.8281 | 2.8557 | 2.8923 | 3.0733
2022-05-12 | 1.9434 | 2.1554 | 2.1899 | 2.2321 | 2.2814 | 1.448 | 1.7597 | 1.7866 | 1.8233 | 1.448 | 1.8862 | 2.1439 | 2.1681 | 2.2002 | 2.3423
2022-05-12 01:00 | 1.814 | 2.0068 | 2.0364 | 2.0727 | 2.1149 | 1.3146 | 1.5952 | 1.6183 | 1.6498 | 1.3146 | 1.6957 | 1.9254 | 1.9462 | 1.9737 | 2.0999
2022-05-12 02:00 | 1.7528 | 1.929 | 1.9525 | 1.9812 | 2.0147 | 1.2194 | 1.4738 | 1.4921 | 1.5171 | 1.2194 | 1.6385 | 1.8533 | 1.8698 | 1.8916 | 2.0078
2022-05-12 03:00 | 1.7338 | 1.8968 | 1.9142 | 1.9355 | 1.9603 | 1.1994 | 1.4417 | 1.4553 | 1.4738 | 1.1994 | 1.5814 | 1.7814 | 1.7936 | 1.8098 | 1.9162
2022-05-12 04:00 | 1.8001 | 1.9579 | 1.9701 | 1.9851 | 2.0026 | 1.251 | 1.4953 | 1.5049 | 1.5179 | 1.251 | 1.7528 | 1.9649 | 1.9734 | 1.9849 | 2.0949
2022-05-12 05:00 | 2.0141 | 2.1838 | 2.1941 | 2.2066 | 2.2212 | 1.3908 | 1.6576 | 1.6656 | 1.6765 | 1.3908 | 1.8481 | 2.0679 | 2.0751 | 2.0846 | 2.1976
2022-05-12 06:00 | 2.4695 | 2.6765 | 2.6884 | 2.703 | 2.72 | 1.7909 | 2.1327 | 2.142 | 2.1547 | 1.7909 | 2.5149 | 2.8113 | 2.8197 | 2.8308 | 2.9823
2022-05-12 07:00 | 2.8579 | 3.1028 | 3.1194 | 3.1397 | 3.1633 | 2.0958 | 2.4994 | 2.5124 | 2.53 | 2.0958 | 3.4104 | 3.8128 | 3.8244 | 3.8399 | 4.0458
2022-05-12 08:00 | 2.8198 | 3.0752 | 3.0986 | 3.1272 | 3.1606 | 2.2101 | 2.6442 | 2.6624 | 2.6873 | 2.2101 | 2.7245 | 3.0601 | 3.0765 | 3.0983 | 3.2741
2022-05-12 09:00 | 2.9722 | 3.2532 | 3.2839 | 3.3214 | 3.3652 | 1.9624 | 2.3619 | 2.3859 | 2.4185 | 1.9624 | 2.7436 | 3.0913 | 3.1128 | 3.1414 | 3.3264
2022-05-12 10:00 | 2.8769 | 3.1618 | 3.1981 | 3.2425 | 3.2942 | 1.8481 | 2.2348 | 2.2631 | 2.3017 | 1.8481 | 2.3244 | 2.6333 | 2.6587 | 2.6925 | 2.8606
2022-05-12 11:00 | 3.0865 | 3.3913 | 3.4298 | 3.4769 | 3.5318 | 1.8862 | 2.283 | 2.313 | 2.354 | 1.8862 | 2.3244 | 2.6364 | 2.6633 | 2.6992 | 2.8698
2022-05-12 12:00 | 3.0484 | 3.3493 | 3.3873 | 3.4337 | 3.4879 | 1.8711 | 2.2644 | 2.294 | 2.3344 | 1.8711 | 2.4006 | 2.7203 | 2.7469 | 2.7822 | 2.9565
2022-05-12 13:00 | 2.9341 | 3.2215 | 3.2569 | 3.3002 | 3.3508 | 1.8672 | 2.2561 | 2.2837 | 2.3214 | 1.8672 | 2.534 | 2.865 | 2.8898 | 2.9228 | 3.1015
2022-05-12 14:00 | 2.8769 | 3.1547 | 3.1873 | 3.2273 | 3.2739 | 1.8454 | 2.2265 | 2.252 | 2.2868 | 1.8454 | 2.3625 | 2.6706 | 2.6935 | 2.7239 | 2.8901
2022-05-12 15:00 | 2.8769 | 3.1511 | 3.1819 | 3.2196 | 3.2636 | 2.0196 | 2.4296 | 2.4537 | 2.4865 | 2.0196 | 2.7817 | 3.1339 | 3.1555 | 3.1841 | 3.3713
2022-05-12 16:00 | 3.1246 | 3.4164 | 3.4467 | 3.4839 | 3.5272 | 2.2442 | 2.6944 | 2.7181 | 2.7504 | 2.2442 | 3.4676 | 3.8955 | 3.9167 | 3.945 | 4.1694
2022-05-12 17:00 | 3.1437 | 3.4404 | 3.4725 | 3.5119 | 3.5578 | 2.6681 | 3.1977 | 3.2228 | 3.2571 | 2.6681 | 4.1916 | 4.7025 | 4.7251 | 4.755 | 5.0213
2022-05-12 18:00 | 3.277 | 3.591 | 3.6269 | 3.6709 | 3.7222 | 2.7245 | 3.2697 | 3.2977 | 3.336 | 2.7245 | 4.1154 | 4.623 | 4.6482 | 4.6817 | 4.9479
2022-05-12 19:00 | 3.1437 | 3.4575 | 3.4984 | 3.5485 | 3.6069 | 2.4959 | 3.0067 | 3.0386 | 3.0822 | 2.4959 | 3.7915 | 4.27 | 4.2987 | 4.3368 | 4.5908
2022-05-12 20:00 | 3.0484 | 3.3648 | 3.4107 | 3.4668 | 3.5322 | 2.4006 | 2.9012 | 2.937 | 2.9858 | 2.4006 | 3.7915 | 4.2769 | 4.309 | 4.3517 | 4.6112
2022-05-12 21:00 | 2.7055 | 2.998 | 3.0447 | 3.1018 | 3.1685 | 2.2482 | 2.7223 | 2.7587 | 2.8085 | 2.2482 | 3.1437 | 3.5582 | 3.5909 | 3.6344 | 3.8591
2022-05-12 22:00 | 2.4387 | 2.7055 | 2.7491 | 2.8025 | 2.8648 | 1.9986 | 2.4231 | 2.4571 | 2.5036 | 1.9986 | 2.6674 | 3.0246 | 3.0552 | 3.0959 | 3.2911
2022-05-12 23:00 | 2.2101 | 2.4514 | 2.4907 | 2.5389 | 2.595 | 1.6463 | 2.0007 | 2.0314 | 2.0733 | 1.6463 | 2.191 | 2.4894 | 2.5169 | 2.5535 | 2.7178
2022-05-13 | 1.9488 | 2.1612 | 2.1957 | 2.238 | 2.2872 | 1.3934 | 1.6951 | 1.722 | 1.7588 | 1.3934 | 1.7909 | 2.0381 | 2.0622 | 2.0944 | 2.2312
2022-05-13 01:00 | 1.81 | 2.0025 | 2.0321 | 2.0684 | 2.1107 | 1.2166 | 1.4794 | 1.5025 | 1.534 | 1.2166 | 1.6195 | 1.8407 | 1.8615 | 1.889 | 2.011
2022-05-13 02:00 | 1.7719 | 1.9495 | 1.973 | 2.0017 | 2.0351 | 1.1813 | 1.4288 | 1.4471 | 1.4721 | 1.1813 | 1.5814 | 1.7898 | 1.8062 | 1.8281 | 1.9411
2022-05-13 03:00 | 1.7528 | 1.9172 | 1.9346 | 1.9559 | 1.9808 | 1.1622 | 1.3977 | 1.4113 | 1.4298 | 1.1622 | 1.5814 | 1.7814 | 1.7936 | 1.8098 | 1.9162
2022-05-13 04:00 | 1.7909 | 1.9481 | 1.9603 | 1.9753 | 1.9928 | 1.1542 | 1.3809 | 1.3905 | 1.4036 | 1.1542 | 1.6957 | 1.9013 | 1.9099 | 1.9213 | 2.0282
2022-05-13 05:00 | 2.0031 | 2.172 | 2.1822 | 2.1948 | 2.2094 | 1.3337 | 1.5901 | 1.5981 | 1.609 | 1.3337 | 1.8481 | 2.0679 | 2.0751 | 2.0846 | 2.1976
2022-05-13 06:00 | 2.4006 | 2.6025 | 2.6144 | 2.629 | 2.646 | 1.6645 | 1.9834 | 1.9927 | 2.0054 | 1.6645 | 2.2673 | 2.5361 | 2.5444 | 2.5555 | 2.6935
2022-05-13 07:00 | 2.8007 | 3.0414 | 3.058 | 3.0783 | 3.1019 | 1.9624 | 2.3419 | 2.3548 | 2.3725 | 1.9624 | 2.896 | 3.2412 | 3.2528 | 3.2682 | 3.4459
2022-05-13 08:00 | 2.7245 | 2.9729 | 2.9963 | 3.0249 | 3.0583 | 2.0196 | 2.4191 | 2.4374 | 2.4623 | 2.0196 | 2.6293 | 2.9542 | 2.9706 | 2.9924 | 3.163
2022-05-13 09:00 | 2.5911 | 2.8438 | 2.8745 | 2.912 | 2.9558 | 1.6576 | 2.0018 | 2.0257 | 2.0584 | 1.6576 | 1.7528 | 1.9904 | 2.0119 | 2.0404 | 2.1709
2022-05-13 10:00 | 2.6864 | 2.9571 | 2.9934 | 3.0378 | 3.0895 | 1.5751 | 1.9123 | 1.9406 | 1.9792 | 1.5751 | 1.6576 | 1.8923 | 1.9177 | 1.9514 | 2.0829
2022-05-13 11:00 | 2.6102 | 2.8796 | 2.9181 | 2.9652 | 3.0201 | 1.5433 | 1.8779 | 1.9079 | 1.9489 | 1.5433 | 1.7909 | 2.0436 | 2.0705 | 2.1064 | 2.2476
2022-05-13 12:00 | 2.6102 | 2.8785 | 2.9165 | 2.9629 | 3.0171 | 1.5081 | 1.8355 | 1.8651 | 1.9055 | 1.5081 | 1.5814 | 1.8099 | 1.8365 | 1.8718 | 2.001
2022-05-13 13:00 | 2.3244 | 2.5665 | 2.6019 | 2.6452 | 2.6958 | 1.1813 | 1.4458 | 1.4734 | 1.5111 | 1.1813 | 1.2003 | 1.3829 | 1.4077 | 1.4407 | 1.5461
2022-05-13 14:00 | 2.3625 | 2.602 | 2.6347 | 2.6746 | 2.7212 | 1.4309 | 1.7368 | 1.7622 | 1.797 | 1.4309 | 1.2586 | 1.4439 | 1.4668 | 1.4971 | 1.6027
2022-05-13 15:00 | 2.534 | 2.7827 | 2.8135 | 2.8512 | 2.8951 | 1.5814 | 1.912 | 1.936 | 1.9688 | 1.5814 | 1.9815 | 2.2446 | 2.2662 | 2.2949 | 2.4381
2022-05-13 16:00 | 2.6652 | 2.9228 | 2.9531 | 2.9903 | 3.0336 | 1.7528 | 2.1139 | 2.1376 | 2.1699 | 1.7528 | 2.3816 | 2.6886 | 2.7099 | 2.7382 | 2.9029
2022-05-13 17:00 | 2.896 | 3.1743 | 3.2064 | 3.2458 | 3.2917 | 2.0577 | 2.4766 | 2.5017 | 2.536 | 2.0577 | 2.8007 | 3.1569 | 3.1795 | 3.2094 | 3.3992
2022-05-13 18:00 | 2.8027 | 3.0814 | 3.1174 | 3.1613 | 3.2126 | 2.0577 | 2.4819 | 2.51 | 2.5482 | 2.0577 | 2.8579 | 3.2257 | 3.2509 | 3.2843 | 3.4814
2022-05-13 19:00 | 2.6576 | 2.9352 | 2.9762 | 3.0262 | 3.0846 | 2.0196 | 2.444 | 2.4759 | 2.5195 | 2.0196 | 2.9531 | 3.3384 | 3.3671 | 3.4052 | 3.6131
2022-05-13 20:00 | 2.5149 | 2.7917 | 2.8375 | 2.8937 | 2.9591 | 1.9016 | 2.3117 | 2.3475 | 2.3963 | 1.9016 | 3.0294 | 3.43 | 3.4621 | 3.5048 | 3.7224
2022-05-13 21:00 | 2.4959 | 2.7728 | 2.8195 | 2.8767 | 2.9433 | 1.9053 | 2.3172 | 2.3536 | 2.4033 | 1.9053 | 2.8388 | 3.2194 | 3.2521 | 3.2956 | 3.5036
2022-05-13 22:00 | 2.3054 | 2.5622 | 2.6058 | 2.6593 | 2.7216 | 1.7909 | 2.1778 | 2.2118 | 2.2583 | 1.7909 | 2.7626 | 3.1305 | 3.1611 | 3.2017 | 3.4022
2022-05-13 23:00 | 2.1529 | 2.39 | 2.4293 | 2.4775 | 2.5336 | 1.598 | 1.9437 | 1.9744 | 2.0163 | 1.598 | 2.1529 | 2.447 | 2.4746 | 2.5112 | 2.6733
2022-05-14 | 1.9243 | 2.1349 | 2.1694 | 2.2117 | 2.2609 | 1.4289 | 1.7372 | 1.7641 | 1.8008 | 1.4289 | 2.0005 | 2.2709 | 2.2951 | 2.3272 | 2.4756
2022-05-14 01:00 | 1.8052 | 1.9974 | 2.027 | 2.0633 | 2.1055 | 1.2279 | 1.4927 | 1.5158 | 1.5473 | 1.2279 | 1.6004 | 1.8195 | 1.8403 | 1.8679 | 1.9888
2022-05-14 02:00 | 1.7147 | 1.8881 | 1.9116 | 1.9403 | 1.9737 | 1.1587 | 1.4022 | 1.4205 | 1.4454 | 1.1587 | 1.5242 | 1.7263 | 1.7427 | 1.7646 | 1.8744
2022-05-14 03:00 | 1.7338 | 1.8968 | 1.9142 | 1.9355 | 1.9603 | 1.105 | 1.3302 | 1.3438 | 1.3623 | 1.105 | 1.6195 | 1.8238 | 1.836 | 1.8522 | 1.9606
2022-05-14 04:00 | 1.7338 | 1.8867 | 1.8989 | 1.9139 | 1.9314 | 1.1241 | 1.3454 | 1.355 | 1.368 | 1.1241 | 1.467 | 1.6473 | 1.6559 | 1.6673 | 1.7616
2022-05-14 05:00 | 1.8481 | 2.0055 | 2.0158 | 2.0283 | 2.0429 | 1.1779 | 1.406 | 1.414 | 1.4249 | 1.1779 | 1.7909 | 2.0044 | 2.0116 | 2.0211 | 2.1309
2022-05-14 06:00 | 1.8481 | 2.0089 | 2.0208 | 2.0354 | 2.0524 | 1.2962 | 1.5482 | 1.5575 | 1.5702 | 1.2962 | 2.0767 | 2.3243 | 2.3327 | 2.3438 | 2.4713
2022-05-14 07:00 | 2.1148 | 2.3045 | 2.3211 | 2.3414 | 2.365 | 1.4861 | 1.7792 | 1.7921 | 1.8098 | 1.4861 | 1.9815 | 2.2249 | 2.2365 | 2.252 | 2.3793
2022-05-14 08:00 | 2.0767 | 2.2769 | 2.3003 | 2.329 | 2.3624 | 1.6766 | 2.014 | 2.0322 | 2.0571 | 1.6766 | 2.0958 | 2.3614 | 2.3778 | 2.3996 | 2.5408
2022-05-14 09:00 | 2.4006 | 2.6391 | 2.6698 | 2.7074 | 2.7511 | 1.6004 | 1.9343 | 1.9582 | 1.9909 | 1.6004 | 2.2482 | 2.5409 | 2.5624 | 2.5909 | 2.7487
2022-05-14 10:00 | 2.0386 | 2.2612 | 2.2974 | 2.3418 | 2.3936 | 1.448 | 1.7622 | 1.7904 | 1.8291 | 1.448 | 1.6766 | 1.9135 | 1.9389 | 1.9726 | 2.1052
2022-05-14 11:00 | 2.0196 | 2.245 | 2.2835 | 2.3306 | 2.3856 | 1.4861 | 1.8103 | 1.8403 | 1.8813 | 1.4861 | 1.9815 | 2.2553 | 2.2822 | 2.3181 | 2.4698
2022-05-14 12:00 | 2.0386 | 2.2645 | 2.3024 | 2.3488 | 2.403 | 1.5433 | 1.8771 | 1.9067 | 1.9471 | 1.5433 | 1.8862 | 2.1487 | 2.1753 | 2.2106 | 2.3565
2022-05-14 13:00 | 1.9514 | 2.1658 | 2.2012 | 2.2445 | 2.2951 | 1.3718 | 1.6709 | 1.6985 | 1.7362 | 1.3718 | 1.3718 | 1.5735 | 1.5983 | 1.6313 | 1.7461
2022-05-14 14:00 | 2.0851 | 2.304 | 2.3367 | 2.3766 | 2.4232 | 1.5052 | 1.8245 | 1.85 | 1.8847 | 1.5052 | 1.7338 | 1.9719 | 1.9948 | 2.0252 | 2.1568
2022-05-14 15:00 | 2.0958 | 2.3119 | 2.3427 | 2.3804 | 2.4244 | 1.5052 | 1.8219 | 1.8459 | 1.8788 | 1.5052 | 2.3054 | 2.6046 | 2.6261 | 2.6548 | 2.8158
2022-05-14 16:00 | 2.345 | 2.5788 | 2.6091 | 2.6463 | 2.6896 | 1.8481 | 2.2264 | 2.2501 | 2.2825 | 1.8481 | 2.5721 | 2.9004 | 2.9216 | 2.9499 | 3.1251
2022-05-14 17:00 | 2.6605 | 2.9213 | 2.9535 | 2.9929 | 3.0388 | 2.0958 | 2.5216 | 2.5467 | 2.581 | 2.0958 | 3.4104 | 3.8345 | 3.857 | 3.887 | 4.1103
2022-05-14 18:00 | 2.6864 | 2.9565 | 2.9924 | 3.0364 | 3.0877 | 2.0767 | 2.5045 | 2.5325 | 2.5707 | 2.0767 | 3.1627 | 3.5644 | 3.5896 | 3.6231 | 3.8369
2022-05-14 19:00 | 2.5721 | 2.8434 | 2.8843 | 2.9344 | 2.9928 | 1.9624 | 2.3765 | 2.4084 | 2.452 | 1.9624 | 3.2008 | 3.6137 | 3.6424 | 3.6804 | 3.902
2022-05-14 20:00 | 2.4387 | 2.7098 | 2.7557 | 2.8118 | 2.8772 | 1.9243 | 2.3385 | 2.3743 | 2.4231 | 1.9243 | 2.896 | 3.2818 | 3.3139 | 3.3566 | 3.5669
2022-05-14 21:00 | 2.4006 | 2.6705 | 2.7172 | 2.7743 | 2.841 | 1.8481 | 2.2496 | 2.2861 | 2.3358 | 1.8481 | 2.6293 | 2.9865 | 3.0192 | 3.0627 | 3.2592
2022-05-14 22:00 | 2.2673 | 2.5212 | 2.5649 | 2.6183 | 2.6806 | 1.6778 | 2.0441 | 2.0781 | 2.1246 | 1.6778 | 2.4768 | 2.8129 | 2.8435 | 2.8841 | 3.0689
2022-05-14 23:00 | 2.0386 | 2.2672 | 2.3065 | 2.3547 | 2.4108 | 1.448 | 1.7665 | 1.7972 | 1.8391 | 1.448 | 2.0577 | 2.3412 | 2.3687 | 2.4053 | 2.5622
2022-05-15 | 1.8858 | 2.0936 | 2.1281 | 2.1703 | 2.2196 | 1.3041 | 1.5897 | 1.6166 | 1.6534 | 1.3041 | 1.7147 | 1.9534 | 1.9775 | 2.0097 | 2.1423
2022-05-15 01:00 | 1.7845 | 1.9751 | 2.0047 | 2.041 | 2.0833 | 1.1622 | 1.4151 | 1.4382 | 1.4697 | 1.1622 | 1.5242 | 1.7349 | 1.7556 | 1.7832 | 1.8999
2022-05-15 02:00 | 1.688 | 1.8594 | 1.8829 | 1.9116 | 1.945 | 1.086 | 1.3163 | 1.3346 | 1.3595 | 1.086 | 1.4099 | 1.5993 | 1.6157 | 1.6375 | 1.7411
2022-05-15 03:00 | 1.6957 | 1.8558 | 1.8732 | 1.8945 | 1.9194 | 1.0669 | 1.2852 | 1.2988 | 1.3173 | 1.0669 | 1.4861 | 1.6756 | 1.6878 | 1.704 | 1.8051
2022-05-15 04:00 | 1.6957 | 1.8457 | 1.858 | 1.873 | 1.8905 | 1.086 | 1.3004 | 1.3099 | 1.323 | 1.086 | 1.5814 | 1.7743 | 1.7829 | 1.7943 | 1.8949
2022-05-15 05:00 | 1.7338 | 1.8827 | 1.8929 | 1.9055 | 1.9201 | 1.0631 | 1.2704 | 1.2784 | 1.2893 | 1.0631 | 1.6766 | 1.8773 | 1.8845 | 1.894 | 1.9976
2022-05-15 06:00 | 1.7719 | 1.927 | 1.9389 | 1.9535 | 1.9706 | 1.2194 | 1.4575 | 1.4668 | 1.4795 | 1.2194 | 1.5433 | 1.7315 | 1.7399 | 1.751 | 1.8491
2022-05-15 07:00 | 1.8481 | 2.0179 | 2.0345 | 2.0548 | 2.0785 | 1.3566 | 1.6262 | 1.6391 | 1.6568 | 1.3566 | 1.7909 | 2.0132 | 2.0248 | 2.0402 | 2.1571
2022-05-15 08:00 | 2.0386 | 2.236 | 2.2594 | 2.288 | 2.3214 | 1.5433 | 1.8564 | 1.8747 | 1.8996 | 1.5433 | 2.0958 | 2.3614 | 2.3778 | 2.3996 | 2.5408
2022-05-15 09:00 | 2.191 | 2.414 | 2.4447 | 2.4822 | 2.526 | 1.7338 | 2.0918 | 2.1158 | 2.1484 | 1.7338 | 2.2863 | 2.5832 | 2.6047 | 2.6333 | 2.7931
2022-05-15 10:00 | 2.191 | 2.4249 | 2.4612 | 2.5056 | 2.5573 | 1.6382 | 1.9869 | 2.0152 | 2.0538 | 1.6382 | 2.2101 | 2.5063 | 2.5317 | 2.5654 | 2.7273
2022-05-15 11:00 | 2.3244 | 2.5725 | 2.611 | 2.6581 | 2.7131 | 1.6957 | 2.0579 | 2.0879 | 2.1289 | 1.6957 | 2.2673 | 2.5729 | 2.5998 | 2.6357 | 2.8031
2022-05-15 12:00 | 2.4197 | 2.6738 | 2.7118 | 2.7582 | 2.8124 | 1.8862 | 2.2822 | 2.3118 | 2.3522 | 1.8862 | 2.553 | 2.8897 | 2.9163 | 2.9516 | 3.1342
2022-05-15 13:00 | 2.2906 | 2.5302 | 2.5656 | 2.6089 | 2.6595 | 1.7147 | 2.076 | 2.1037 | 2.1414 | 1.7147 | 2.534 | 2.865 | 2.8898 | 2.9228 | 3.1015
2022-05-15 14:00 | 2.3054 | 2.5406 | 2.5733 | 2.6132 | 2.6598 | 1.81 | 2.1847 | 2.2101 | 2.2449 | 1.81 | 2.4578 | 2.7765 | 2.7993 | 2.8297 | 3.0012
2022-05-15 15:00 | 2.3054 | 2.537 | 2.5678 | 2.6055 | 2.6495 | 1.829 | 2.2046 | 2.2286 | 2.2614 | 1.829 | 3.0484 | 3.4303 | 3.4519 | 3.4805 | 3.6824
2022-05-15 16:00 | 2.7607 | 3.0253 | 3.0557 | 3.0929 | 3.1362 | 2.2673 | 2.7216 | 2.7453 | 2.7776 | 2.2673 | 3.4866 | 3.9166 | 3.9379 | 3.9662 | 4.1917
2022-05-15 17:00 | 3.0865 | 3.379 | 3.4111 | 3.4505 | 3.4964 | 2.4899 | 2.9872 | 3.0123 | 3.0466 | 2.4899 | 3.6581 | 4.1097 | 4.1322 | 4.1622 | 4.3991
2022-05-15 18:00 | 3.1056 | 3.4068 | 3.4427 | 3.4867 | 3.538 | 2.6674 | 3.2022 | 3.2302 | 3.2685 | 2.6674 | 4.0582 | 4.5595 | 4.5847 | 4.6182 | 4.8813
2022-05-15 19:00 | 3.0294 | 3.3347 | 3.3756 | 3.4257 | 3.4841 | 2.534 | 3.0517 | 3.0836 | 3.1272 | 2.534 | 3.8677 | 4.3547 | 4.3834 | 4.4215 | 4.6796
2022-05-15 20:00 | 2.915 | 3.2215 | 3.2674 | 3.3235 | 3.389 | 2.534 | 3.0587 | 3.0945 | 3.1434 | 2.534 | 3.7915 | 4.2769 | 4.309 | 4.3517 | 4.6112
2022-05-15 21:00 | 2.7245 | 3.0185 | 3.0651 | 3.1223 | 3.1889 | 2.2863 | 2.7673 | 2.8037 | 2.8535 | 2.2863 | 3.2961 | 3.7276 | 3.7603 | 3.8037 | 4.0369
2022-05-15 22:00 | 2.4387 | 2.7055 | 2.7491 | 2.8025 | 2.8648 | 1.9594 | 2.3769 | 2.4109 | 2.4574 | 1.9594 | 2.8007 | 3.1729 | 3.2034 | 3.2441 | 3.4466
2022-05-15 23:00 | 2.2482 | 2.4923 | 2.5317 | 2.5798 | 2.636 | 1.6087 | 1.9564 | 1.9871 | 2.029 | 1.6087 | 2.2101 | 2.5105 | 2.5381 | 2.5747 | 2.74
2022-05-16 | 1.9434 | 2.1554 | 2.1899 | 2.2321 | 2.2814 | 1.448 | 1.7597 | 1.7866 | 1.8233 | 1.448 | 1.8481 | 2.1016 | 2.1257 | 2.1579 | 2.2979
2022-05-16 01:00 | 1.8672 | 2.0639 | 2.0936 | 2.1298 | 2.1721 | 1.2575 | 1.5276 | 1.5507 | 1.5823 | 1.2575 | 1.7909 | 2.0313 | 2.052 | 2.0796 | 2.211
2022-05-16 02:00 | 1.7719 | 1.9495 | 1.973 | 2.0017 | 2.0351 | 1.1813 | 1.4288 | 1.4471 | 1.4721 | 1.1813 | 1.6385 | 1.8533 | 1.8698 | 1.8916 | 2.0078
2022-05-16 03:00 | 1.7528 | 1.9172 | 1.9346 | 1.9559 | 1.9808 | 1.1622 | 1.3977 | 1.4113 | 1.4298 | 1.1622 | 1.7338 | 1.9508 | 1.963 | 1.9792 | 2.0939
2022-05-16 04:00 | 1.8862 | 2.0504 | 2.0627 | 2.0777 | 2.0952 | 1.2011 | 1.4364 | 1.446 | 1.459 | 1.2011 | 1.6957 | 1.9013 | 1.9099 | 1.9213 | 2.0282
2022-05-16 05:00 | 2.0525 | 2.2251 | 2.2353 | 2.2478 | 2.2624 | 1.405 | 1.6744 | 1.6823 | 1.6932 | 1.405 | 2.1339 | 2.3855 | 2.3927 | 2.4022 | 2.5309
2022-05-16 06:00 | 2.5382 | 2.7503 | 2.7622 | 2.7768 | 2.7939 | 1.8475 | 2.1995 | 2.2088 | 2.2215 | 1.8475 | 2.7245 | 3.0442 | 3.0525 | 3.0637 | 3.2267
2022-05-16 07:00 | 2.896 | 3.1437 | 3.1603 | 3.1806 | 3.2043 | 1.9624 | 2.3419 | 2.3548 | 2.3725 | 1.9624 | 2.915 | 3.2623 | 3.274 | 3.2894 | 3.4681
2022-05-16 08:00 | 2.6864 | 2.9319 | 2.9553 | 2.984 | 3.0174 | 1.8191 | 2.1823 | 2.2006 | 2.2255 | 1.8191 | 2.2482 | 2.5308 | 2.5472 | 2.569 | 2.7186
2022-05-16 09:00 | 2.2673 | 2.4959 | 2.5265 | 2.5641 | 2.6079 | 1.2765 | 1.5516 | 1.5756 | 1.6082 | 1.2765 | 0.99073 | 1.1435 | 1.165 | 1.1935 | 1.2822
2022-05-16 10:00 | 1.9053 | 2.1179 | 2.1541 | 2.1985 | 2.2503 | 1.0288 | 1.267 | 1.2953 | 1.3339 | 1.0288 | 1.2194 | 1.4053 | 1.4307 | 1.4645 | 1.5719
2022-05-16 11:00 | 2.2673 | 2.5111 | 2.5496 | 2.5967 | 2.6517 | 1.5814 | 1.9229 | 1.9529 | 1.9939 | 1.5814 | 1.5052 | 1.726 | 1.7529 | 1.7888 | 1.9144
2022-05-16 12:00 | 2.4387 | 2.6943 | 2.7323 | 2.7787 | 2.8329 | 1.5052 | 1.8321 | 1.8617 | 1.9021 | 1.5052 | 1.448 | 1.6617 | 1.6883 | 1.7236 | 1.8455
2022-05-16 13:00 | 2.3054 | 2.546 | 2.5814 | 2.6248 | 2.6753 | 0.95263 | 1.1757 | 1.2033 | 1.241 | 0.95263 | 1.5623 | 1.7852 | 1.81 | 1.843 | 1.9683
2022-05-16 14:00 | 1.9624 | 2.1722 | 2.2048 | 2.2448 | 2.2914 | 1.0296 | 1.2627 | 1.2882 | 1.3229 | 1.0296 | 1.0669 | 1.2309 | 1.2538 | 1.2842 | 1.3791
2022-05-16 15:00 | 2.5237 | 2.7716 | 2.8024 | 2.8401 | 2.884 | 1.6957 | 2.047 | 2.071 | 2.1038 | 1.6957 | 1.7719 | 2.0117 | 2.0333 | 2.062 | 2.1937
2022-05-16 16:00 | 2.8007 | 3.0684 | 3.0987 | 3.1359 | 3.1792 | 1.9815 | 2.384 | 2.4077 | 2.44 | 1.9815 | 2.5911 | 2.9215 | 2.9428 | 2.9711 | 3.1473
2022-05-16 17:00 | 3.0961 | 3.3892 | 3.4214 | 3.4608 | 3.5067 | 2.6102 | 3.1293 | 3.1544 | 3.1887 | 2.6102 | 3.6349 | 4.0839 | 4.1064 | 4.1364 | 4.372
2022-05-16 18:00 | 3.2199 | 3.5296 | 3.5655 | 3.6095 | 3.6608 | 2.7626 | 3.3147 | 3.3428 | 3.381 | 2.7626 | 3.9439 | 4.4325 | 4.4577 | 4.4911 | 4.7479
2022-05-16 19:00 | 3.1056 | 3.4165 | 3.4575 | 3.5075 | 3.5659 | 2.6293 | 3.1643 | 3.1962 | 3.2398 | 2.6293 | 4.0391 | 4.5453 | 4.5739 | 4.612 | 4.8796
2022-05-16 20:00 | 2.9722 | 3.2829 | 3.3288 | 3.3849 | 3.4504 | 2.4387 | 2.9462 | 2.982 | 3.0308 | 2.4387 | 3.62 | 4.0863 | 4.1185 | 4.1611 | 4.4112
2022-05-16 21:00 | 2.8249 | 3.1263 | 3.173 | 3.2301 | 3.2968 | 2.3435 | 2.8349 | 2.8713 | 2.921 | 2.3435 | 3.258 | 3.6852 | 3.7179 | 3.7614 | 3.9925
2022-05-16 22:00 | 2.5715 | 2.8481 | 2.8918 | 2.9452 | 3.0075 | 1.9982 | 2.4226 | 2.4567 | 2.5031 | 1.9982 | 2.9722 | 3.3634 | 3.394 | 3.4346 | 3.6466
2022-05-16 23:00 | 2.2482 | 2.4923 | 2.5317 | 2.5798 | 2.636 | 1.7237 | 2.0922 | 2.1229 | 2.1648 | 1.7237 | 2.5911 | 2.934 | 2.9615 | 2.9982 | 3.1844
2022-05-17 | 2.0958 | 2.3191 | 2.3536 | 2.3959 | 2.4451 | 1.44 | 1.7502 | 1.7772 | 1.8139 | 1.44 | 2.1148 | 2.398 | 2.4222 | 2.4543 | 2.609
2022-05-17 01:00 | 1.9053 | 2.1049 | 2.1345 | 2.1707 | 2.213 | 1.2956 | 1.5726 | 1.5957 | 1.6273 | 1.2956 | 2.3054 | 2.6029 | 2.6237 | 2.6512 | 2.8109
2022-05-17 02:00 | 1.8481 | 2.0314 | 2.0548 | 2.0835 | 2.117 | 1.2042 | 1.4559 | 1.4742 | 1.4992 | 1.2042 | 1.7338 | 1.9592 | 1.9756 | 1.9975 | 2.1189
2022-05-17 03:00 | 1.9817 | 2.1631 | 2.1805 | 2.2019 | 2.2267 | 1.2194 | 1.4653 | 1.4788 | 1.4974 | 1.2194 | 1.7719 | 1.9932 | 2.0054 | 2.0216 | 2.1384
2022-05-17 04:00 | 2.0005 | 2.1732 | 2.1855 | 2.2005 | 2.218 | 1.3146 | 1.5705 | 1.58 | 1.5931 | 1.3146 | 1.9434 | 2.1766 | 2.1852 | 2.1966 | 2.3171
2022-05-17 05:00 | 2.3244 | 2.5172 | 2.5275 | 2.54 | 2.5546 | 1.5844 | 1.8863 | 1.8943 | 1.9052 | 1.5844 | 2.4387 | 2.7242 | 2.7314 | 2.7409 | 2.8864
2022-05-17 06:00 | 2.9047 | 3.144 | 3.1559 | 3.1705 | 3.1875 | 2.1861 | 2.5995 | 2.6088 | 2.6215 | 2.1861 | 3.4676 | 3.8699 | 3.8783 | 3.8894 | 4.0933
2022-05-17 07:00 | 3.3342 | 3.6145 | 3.6311 | 3.6514 | 3.6751 | 2.3816 | 2.8371 | 2.85 | 2.8676 | 2.3816 | 3.8296 | 4.2786 | 4.2902 | 4.3057 | 4.5346
2022-05-17 08:00 | 3.1056 | 3.3822 | 3.4056 | 3.4343 | 3.4677 | 2.0469 | 2.4513 | 2.4696 | 2.4945 | 2.0469 | 3.0484 | 3.42 | 3.4364 | 3.4582 | 3.6518
2022-05-17 09:00 | 2.4768 | 2.721 | 2.7517 | 2.7892 | 2.833 | 1.4289 | 1.7317 | 1.7556 | 1.7883 | 1.4289 | 1.1241 | 1.2917 | 1.3132 | 1.3418 | 1.4377
2022-05-17 10:00 | 2.191 | 2.4249 | 2.4612 | 2.5056 | 2.5573 | 1.0288 | 1.267 | 1.2953 | 1.3339 | 1.0288 | 0.97168 | 1.1301 | 1.1555 | 1.1892 | 1.283
2022-05-17 11:00 | 1.8672 | 2.0813 | 2.1198 | 2.1669 | 2.2218 | 0.8442 | 1.052 | 1.082 | 1.123 | 0.8442 | 1.2194 | 1.4084 | 1.4354 | 1.4712 | 1.5811
2022-05-17 12:00 | 1.8672 | 2.0802 | 2.1182 | 2.1646 | 2.2188 | 0.83831 | 1.0443 | 1.0739 | 1.1143 | 0.83831 | 1.1432 | 1.323 | 1.3495 | 1.3849 | 1.49
2022-05-17 13:00 | 2.172 | 2.4028 | 2.4382 | 2.4815 | 2.532 | 1.2194 | 1.4908 | 1.5184 | 1.5561 | 1.2194 | 1.2003 | 1.3829 | 1.4077 | 1.4407 | 1.5461
2022-05-17 14:00 | 2.6102 | 2.8681 | 2.9008 | 2.9407 | 2.9873 | 1.467 | 1.7795 | 1.805 | 1.8397 | 1.467 | 1.2575 | 1.4426 | 1.4655 | 1.4959 | 1.6013
2022-05-17 15:00 | 2.5944 | 2.8476 | 2.8784 | 2.9161 | 2.96 | 1.6385 | 1.9795 | 2.0035 | 2.0363 | 1.6385 | 1.5242 | 1.7365 | 1.7581 | 1.7868 | 1.9048
2022-05-17 16:00 | 3.0484 | 3.3345 | 3.3648 | 3.402 | 3.4453 | 2.1486 | 2.5814 | 2.6051 | 2.6374 | 2.1486 | 2.9722 | 3.345 | 3.3663 | 3.3945 | 3.5917
2022-05-17 17:00 | 3.5247 | 3.8497 | 3.8819 | 3.9213 | 3.9672 | 2.9531 | 3.5345 | 3.5596 | 3.5938 | 2.9531 | 4.363 | 4.8931 | 4.9156 | 4.9456 | 5.2212
2022-05-17 18:00 | 3.6009 | 3.939 | 3.9749 | 4.0189 | 4.0702 | 3.0865 | 3.6974 | 3.7254 | 3.7637 | 3.0865 | 4.4964 | 5.0465 | 5.0717 | 5.1051 | 5.3923
2022-05-17 19:00 | 3.5628 | 3.9078 | 3.9487 | 3.9988 | 4.0572 | 2.9722 | 3.5694 | 3.6013 | 3.6449 | 2.9722 | 4.8965 | 5.498 | 5.5267 | 5.5648 | 5.8795
2022-05-17 20:00 | 3.5247 | 3.8765 | 3.9224 | 3.9785 | 4.044 | 2.8388 | 3.4189 | 3.4546 | 3.5035 | 2.8388 | 4.4202 | 4.9756 | 5.0077 | 5.0504 | 5.3444
2022-05-17 21:00 | 3.2199 | 3.5507 | 3.5973 | 3.6545 | 3.7211 | 2.6102 | 3.15 | 3.1864 | 3.2361 | 2.6102 | 4.3059 | 4.8497 | 4.8824 | 4.9259 | 5.2145
2022-05-17 22:00 | 2.815 | 3.1097 | 3.1534 | 3.2068 | 3.2691 | 2.3054 | 2.7855 | 2.8196 | 2.866 | 2.3054 | 3.2389 | 3.6598 | 3.6904 | 3.731 | 3.9577
2022-05-17 23:00 | 2.4959 | 2.7584 | 2.7978 | 2.8459 | 2.902 | 1.9417 | 2.3498 | 2.3805 | 2.4224 | 1.9417 | 2.7817 | 3.1457 | 3.1733 | 3.2099 | 3.4066
2022-05-18 | 2.2482 | 2.4829 | 2.5174 | 2.5596 | 2.6089 | 1.5559 | 1.8872 | 1.9141 | 1.9509 | 1.5559 | 2.3244 | 2.6309 | 2.6551 | 2.6872 | 2.8534
2022-05-18 01:00 | 2.1339 | 2.3505 | 2.3801 | 2.4164 | 2.4586 | 1.4262 | 1.7269 | 1.75 | 1.7816 | 1.4262 | 2.4006 | 2.7088 | 2.7295 | 2.7571 | 2.922
2022-05-18 02:00 | 2.1148 | 2.318 | 2.3414 | 2.3701 | 2.4036 | 1.2997 | 1.5687 | 1.587 | 1.612 | 1.2997 | 2.3244 | 2.6155 | 2.632 | 2.6538 | 2.8077
2022-05-18 03:00 | 2.1529 | 2.3471 | 2.3645 | 2.3858 | 2.4106 | 1.2956 | 1.5553 | 1.5689 | 1.5874 | 1.2956 | 1.8862 | 2.1202 | 2.1324 | 2.1486 | 2.2717
2022-05-18 04:00 | 2.1586 | 2.3431 | 2.3554 | 2.3704 | 2.3879 | 1.3865 | 1.6553 | 1.6649 | 1.678 | 1.3865 | 2.0196 | 2.2613 | 2.2699 | 2.2813 | 2.4059
2022-05-18 05:00 | 2.407 | 2.606 | 2.6162 | 2.6287 | 2.6433 | 1.7067 | 2.0308 | 2.0388 | 2.0497 | 1.7067 | 2.534 | 2.8301 | 2.8373 | 2.8468 | 2.9975
2022-05-18 06:00 | 2.9182 | 3.1585 | 3.1705 | 3.1851 | 3.2021 | 2.3244 | 2.7629 | 2.7722 | 2.7849 | 2.3244 | 3.6009 | 4.0181 | 4.0265 | 4.0376 | 4.2488
2022-05-18 07:00 | 3.3723 | 3.6555 | 3.672 | 3.6923 | 3.716 | 2.7245 | 3.2422 | 3.2551 | 3.2728 | 2.7245 | 4.1344 | 4.6174 | 4.629 | 4.6444 | 4.8902
2022-05-18 08:00 | 3.2389 | 3.5255 | 3.5489 | 3.5776 | 3.611 | 2.3816 | 2.8468 | 2.865 | 2.8899 | 2.3816 | 3.0537 | 3.4259 | 3.4423 | 3.464 | 3.658
2022-05-18 09:00 | 3.0675 | 3.3556 | 3.3862 | 3.4238 | 3.4676 | 1.7487 | 2.1095 | 2.1334 | 2.1661 | 1.7487 | 2.7245 | 3.0702 | 3.0917 | 3.1202 | 3.3041
2022-05-18 10:00 | 2.7626 | 3.039 | 3.0753 | 3.1196 | 3.1714 | 1.467 | 1.7847 | 1.813 | 1.8516 | 1.467 | 1.3527 | 1.5535 | 1.5789 | 1.6127 | 1.7274
2022-05-18 11:00 | 2.3816 | 2.634 | 2.6724 | 2.7195 | 2.7745 | 1.1241 | 1.3827 | 1.4127 | 1.4537 | 1.1241 | 1.1241 | 1.3025 | 1.3295 | 1.3653 | 1.47
2022-05-18 12:00 | 2.0577 | 2.2849 | 2.3229 | 2.3693 | 2.4235 | 1.105 | 1.3594 | 1.389 | 1.4294 | 1.105 | 1.1432 | 1.323 | 1.3495 | 1.3849 | 1.49
2022-05-18 13:00 | 2.6293 | 2.894 | 2.9294 | 2.9727 | 3.0233 | 1.5433 | 1.8735 | 1.9011 | 1.9388 | 1.5433 | 1.2384 | 1.4253 | 1.4501 | 1.483 | 1.5905
2022-05-18 14:00 | 2.915 | 3.1956 | 3.2283 | 3.2682 | 3.3148 | 1.7528 | 2.1171 | 2.1426 | 2.1773 | 1.7528 | 2.2291 | 2.5224 | 2.5453 | 2.5757 | 2.7345
2022-05-18 15:00 | 2.7817 | 3.0488 | 3.0796 | 3.1173 | 3.1612 | 1.9243 | 2.3171 | 2.3411 | 2.3739 | 1.9243 | 2.6674 | 3.0068 | 3.0284 | 3.0571 | 3.238
2022-05-18 16:00 | 3.0865 | 3.3754 | 3.4058 | 3.4429 | 3.4863 | 2.534 | 3.0367 | 3.0604 | 3.0927 | 2.534 | 3.5628 | 4.0013 | 4.0226 | 4.0509 | 4.2805
2022-05-18 17:00 | 3.7152 | 4.0544 | 4.0866 | 4.126 | 4.1719 | 3.0157 | 3.6084 | 3.6334 | 3.6677 | 3.0157 | 4.6107 | 5.1683 | 5.1909 | 5.2208 | 5.5101
2022-05-18 18:00 | 3.8105 | 4.1641 | 4.2001 | 4.2441 | 4.2953 | 3.2961 | 3.945 | 3.973 | 4.0112 | 3.2961 | 4.9727 | 5.5758 | 5.601 | 5.6344 | 5.9478
2022-05-18 19:00 | 3.6962 | 4.0511 | 4.092 | 4.1421 | 4.2005 | 3.258 | 3.907 | 3.9389 | 3.9825 | 3.258 | 5.0299 | 5.6462 | 5.6749 | 5.713 | 6.035
2022-05-18 20:00 | 3.5438 | 3.897 | 3.9429 | 3.999 | 4.0644 | 3.0675 | 3.689 | 3.7247 | 3.7736 | 3.0675 | 5.1442 | 5.7801 | 5.8122 | 5.8549 | 6.1888
2022-05-18 21:00 | 3.4104 | 3.7553 | 3.802 | 3.8592 | 3.9258 | 2.9531 | 3.5551 | 3.5915 | 3.6412 | 2.9531 | 4.5155 | 5.0826 | 5.1153 | 5.1588 | 5.459
2022-05-18 22:00 | 3.119 | 3.4363 | 3.48 | 3.5334 | 3.5957 | 2.5135 | 3.0314 | 3.0655 | 3.1119 | 2.5135 | 3.7343 | 4.2103 | 4.2409 | 4.2815 | 4.5354
2022-05-18 23:00 | 2.6102 | 2.8812 | 2.9206 | 2.9687 | 3.0249 | 2.0432 | 2.4697 | 2.5004 | 2.5423 | 2.0432 | 3.7343 | 4.2043 | 4.2319 | 4.2685 | 4.5176
2022-05-19 | 2.3276 | 2.5681 | 2.6026 | 2.6449 | 2.6941 | 1.7665 | 2.1359 | 2.1628 | 2.1995 | 1.7665 | 2.5911 | 2.9273 | 2.9515 | 2.9836 | 3.1644
2022-05-19 01:00 | 2.2482 | 2.4733 | 2.5029 | 2.5392 | 2.5815 | 1.5623 | 1.8878 | 1.9109 | 1.9424 | 1.5623 | 2.3415 | 2.643 | 2.6638 | 2.6914 | 2.853
2022-05-19 02:00 | 2.2673 | 2.4817 | 2.5052 | 2.5339 | 2.5673 | 1.4802 | 1.782 | 1.8003 | 1.8252 | 1.4802 | 2.4006 | 2.7002 | 2.7167 | 2.7385 | 2.8966
2022-05-19 03:00 | 2.2482 | 2.4494 | 2.4668 | 2.4881 | 2.513 | 1.4982 | 1.7946 | 1.8082 | 1.8267 | 1.4982 | 2.3625 | 2.6495 | 2.6617 | 2.6779 | 2.8272
2022-05-19 04:00 | 2.4006 | 2.6031 | 2.6154 | 2.6304 | 2.6479 | 1.6195 | 1.9306 | 1.9402 | 1.9532 | 1.6195 | 2.6674 | 2.9811 | 2.9897 | 3.0011 | 3.1614
2022-05-19 05:00 | 2.7245 | 2.9471 | 2.9573 | 2.9698 | 2.9845 | 1.942 | 2.3088 | 2.3168 | 2.3277 | 1.942 | 3.258 | 3.6346 | 3.6418 | 3.6513 | 3.8418
2022-05-19 06:00 | 3.4707 | 3.752 | 3.764 | 3.7786 | 3.7956 | 2.717 | 3.2267 | 3.236 | 3.2487 | 2.717 | 4.4583 | 4.9709 | 4.9792 | 4.9903 | 5.2487
2022-05-19 07:00 | 4.1237 | 4.4628 | 4.4793 | 4.4996 | 4.5233 | 3.0484 | 3.6248 | 3.6378 | 3.6554 | 3.0484 | 5.8872 | 6.5652 | 6.5768 | 6.5923 | 6.9344
2022-05-19 08:00 | 4.2678 | 4.6309 | 4.6543 | 4.6829 | 4.7163 | 3.0865 | 3.6795 | 3.6978 | 3.7227 | 3.0865 | 4.9918 | 5.5796 | 5.596 | 5.6178 | 5.9182
2022-05-19 09:00 | 3.9629 | 4.3176 | 4.3483 | 4.3858 | 4.4296 | 2.6163 | 3.1343 | 3.1583 | 3.1909 | 2.6163 | 3.9629 | 4.4464 | 4.4679 | 4.4964 | 4.7484
2022-05-19 10:00 | 3.5057 | 3.8373 | 3.8735 | 3.9179 | 3.9697 | 2.017 | 2.4344 | 2.4627 | 2.5013 | 2.017 | 2.7055 | 3.0568 | 3.0822 | 3.1159 | 3.305
2022-05-19 11:00 | 2.6293 | 2.9001 | 2.9385 | 2.9856 | 3.0406 | 1.2997 | 1.5902 | 1.6202 | 1.6612 | 1.2997 | 0.74305 | 0.87909 | 0.90605 | 0.94188 | 1.0256
2022-05-19 12:00 | 2.3435 | 2.592 | 2.6299 | 2.6764 | 2.7305 | 1.0669 | 1.3144 | 1.344 | 1.3844 | 1.0669 | 0.7621 | 0.89952 | 0.9261 | 0.96143 | 1.0456
2022-05-19 13:00 | 2.2101 | 2.4437 | 2.4791 | 2.5224 | 2.5729 | 1.0669 | 1.3108 | 1.3384 | 1.3761 | 1.0669 | 0.91452 | 1.0654 | 1.0902 | 1.1231 | 1.2128
2022-05-19 14:00 | 2.4006 | 2.643 | 2.6756 | 2.7156 | 2.7621 | 1.2194 | 1.4869 | 1.5124 | 1.5471 | 1.2194 | 0.81926 | 0.95567 | 0.97854 | 1.0089 | 1.0903
2022-05-19 15:00 | 2.553 | 2.8031 | 2.8339 | 2.8716 | 2.9156 | 1.7404 | 2.0998 | 2.1238 | 2.1566 | 1.7404 | 1.6385 | 1.8635 | 1.8851 | 1.9138 | 2.0382
2022-05-19 16:00 | 3.1594 | 3.4537 | 3.4841 | 3.5213 | 3.5646 | 2.3484 | 2.8175 | 2.8411 | 2.8735 | 2.3484 | 3.3342 | 3.7473 | 3.7685 | 3.7968 | 4.0139
2022-05-19 17:00 | 3.6962 | 4.034 | 4.0661 | 4.1055 | 4.1514 | 3.0504 | 3.6494 | 3.6745 | 3.7087 | 3.0504 | 4.9918 | 5.5918 | 5.6143 | 5.6442 | 5.9545
2022-05-19 18:00 | 4.001 | 4.3688 | 4.4048 | 4.4487 | 4.5 | 3.2199 | 3.8549 | 3.8829 | 3.9212 | 3.2199 | 5.3728 | 6.0204 | 6.0456 | 6.079 | 6.4144
2022-05-19 19:00 | 3.8867 | 4.2558 | 4.2967 | 4.3468 | 4.4052 | 3.2039 | 3.8431 | 3.875 | 3.9186 | 3.2039 | 5.8872 | 6.599 | 6.6276 | 6.6657 | 7.0349
2022-05-19 20:00 | 3.8105 | 4.1836 | 4.2294 | 4.2855 | 4.351 | 3.258 | 3.914 | 3.9498 | 3.9987 | 3.258 | 5.9635 | 6.6905 | 6.7226 | 6.7653 | 7.1442
2022-05-19 21:00 | 3.5819 | 3.9396 | 3.9863 | 4.0434 | 4.11 | 3.1029 | 3.732 | 3.7684 | 3.8181 | 3.1029 | 4.9537 | 5.5695 | 5.6023 | 5.6457 | 5.97
2022-05-19 22:00 | 3.1865 | 3.5089 | 3.5525 | 3.606 | 3.6682 | 2.534 | 3.0556 | 3.0897 | 3.1361 | 2.534 | 4.0391 | 4.5491 | 4.5796 | 4.6203 | 4.8909
2022-05-19 23:00 | 2.8007 | 3.0859 | 3.1253 | 3.1734 | 3.2296 | 2.0895 | 2.5243 | 2.555 | 2.5969 | 2.0895 | 3.277 | 3.6962 | 3.7237 | 3.7604 | 3.9843
2022-05-20 | 2.4578 | 2.708 | 2.7426 | 2.7848 | 2.834 | 1.7909 | 2.1648 | 2.1917 | 2.2285 | 1.7909 | 3.1627 | 3.5625 | 3.5866 | 3.6188 | 3.831
2022-05-20 01:00 | 2.3244 | 2.5552 | 2.5848 | 2.6211 | 2.6633 | 1.6385 | 1.9778 | 2.0009 | 2.0324 | 1.6385 | 2.3435 | 2.6453 | 2.666 | 2.6936 | 2.8554
2022-05-20 02:00 | 2.2291 | 2.4408 | 2.4642 | 2.4929 | 2.5264 | 1.5433 | 1.8565 | 1.8748 | 1.8997 | 1.5433 | 2.172 | 2.4462 | 2.4626 | 2.4844 | 2.6299
2022-05-20 03:00 | 2.2291 | 2.4289 | 2.4464 | 2.4677 | 2.4925 | 1.5242 | 1.8254 | 1.839 | 1.8575 | 1.5242 | 2.4006 | 2.6918 | 2.704 | 2.7203 | 2.8716
2022-05-20 04:00 | 2.3625 | 2.5622 | 2.5744 | 2.5894 | 2.6069 | 1.6184 | 1.9293 | 1.9389 | 1.952 | 1.6184 | 2.7436 | 3.0658 | 3.0744 | 3.0858 | 3.2503
2022-05-20 05:00 | 2.6102 | 2.8243 | 2.8345 | 2.847 | 2.8616 | 1.9829 | 2.3571 | 2.3651 | 2.3759 | 1.9829 | 3.2389 | 3.6135 | 3.6206 | 3.6302 | 3.8196
2022-05-20 06:00 | 3.3342 | 3.6054 | 3.6174 | 3.632 | 3.649 | 2.6591 | 3.1583 | 3.1676 | 3.1803 | 2.6591 | 4.0963 | 4.5686 | 4.577 | 4.5881 | 4.8265
2022-05-20 07:00 | 3.8677 | 4.1877 | 4.2042 | 4.2245 | 4.2482 | 3.0865 | 3.6698 | 3.6828 | 3.7004 | 3.0865 | 4.9537 | 5.5278 | 5.5394 | 5.5548 | 5.8456
2022-05-20 08:00 | 3.7343 | 4.0577 | 4.0811 | 4.1098 | 4.1432 | 2.8579 | 3.4094 | 3.4277 | 3.4526 | 2.8579 | 4.1535 | 4.648 | 4.6644 | 4.6862 | 4.9406
2022-05-20 09:00 | 3.4104 | 3.724 | 3.7547 | 3.7922 | 3.836 | 2.2101 | 2.6545 | 2.6785 | 2.7111 | 2.2101 | 3.1818 | 3.5783 | 3.5998 | 3.6284 | 3.8374
2022-05-20 10:00 | 3.258 | 3.5712 | 3.6074 | 3.6518 | 3.7036 | 2.0767 | 2.5049 | 2.5332 | 2.5718 | 2.0767 | 2.1529 | 2.4428 | 2.4682 | 2.5019 | 2.6607
2022-05-20 11:00 | 2.9913 | 3.289 | 3.3274 | 3.3745 | 3.4295 | 1.8481 | 2.238 | 2.268 | 2.309 | 1.8481 | 1.6385 | 1.8742 | 1.9011 | 1.937 | 2.0699
2022-05-20 12:00 | 2.915 | 3.206 | 3.244 | 3.2904 | 3.3446 | 1.7944 | 2.1738 | 2.2034 | 2.2438 | 1.7944 | 1.8481 | 2.1063 | 2.1329 | 2.1682 | 2.3121
2022-05-20 13:00 | 3.0675 | 3.3648 | 3.4002 | 3.4435 | 3.494 | 1.9243 | 2.3236 | 2.3512 | 2.3889 | 1.9243 | 2.0958 | 2.378 | 2.4028 | 2.4358 | 2.5904
2022-05-20 14:00 | 2.7436 | 3.0114 | 3.0441 | 3.084 | 3.1306 | 1.7338 | 2.0946 | 2.1201 | 2.1548 | 1.7338 | 1.9434 | 2.2048 | 2.2277 | 2.2581 | 2.4012
2022-05-20 15:00 | 3.0103 | 3.2944 | 3.3252 | 3.3629 | 3.4069 | 2.0767 | 2.4972 | 2.5212 | 2.554 | 2.0767 | 2.9531 | 3.3244 | 3.346 | 3.3747 | 3.5713
2022-05-20 16:00 | 3.3151 | 3.621 | 3.6514 | 3.6886 | 3.7319 | 2.4959 | 2.9917 | 3.0154 | 3.0477 | 2.4959 | 3.5438 | 3.9802 | 4.0014 | 4.0297 | 4.2583
2022-05-20 17:00 | 3.4866 | 3.8088 | 3.841 | 3.8804 | 3.9263 | 2.8255 | 3.3836 | 3.4087 | 3.443 | 2.8255 | 4.5726 | 5.126 | 5.1485 | 5.1785 | 5.4657
2022-05-20 18:00 | 3.5628 | 3.898 | 3.934 | 3.978 | 4.0292 | 3.0103 | 3.6073 | 3.6354 | 3.6736 | 3.0103 | 5.6205 | 6.2957 | 6.3208 | 6.3543 | 6.7033
2022-05-20 19:00 | 3.4485 | 3.785 | 3.8259 | 3.876 | 3.9344 | 2.9341 | 3.5244 | 3.5563 | 3.5999 | 2.9341 | 4.7441 | 5.3286 | 5.3573 | 5.3954 | 5.7017
2022-05-20 20:00 | 3.3533 | 3.6923 | 3.7382 | 3.7943 | 3.8597 | 2.8388 | 3.4189 | 3.4546 | 3.5035 | 2.8388 | 4.8584 | 5.4625 | 5.4947 | 5.5373 | 5.8555
2022-05-20 21:00 | 3.1437 | 3.4688 | 3.5155 | 3.5726 | 3.6392 | 2.6864 | 3.24 | 3.2764 | 3.3261 | 2.6864 | 4.1154 | 4.638 | 4.6707 | 4.7141 | 4.9924
2022-05-20 22:00 | 2.9913 | 3.2991 | 3.3427 | 3.3961 | 3.4584 | 2.4768 | 2.9881 | 3.0221 | 3.0686 | 2.4768 | 3.5819 | 4.0409 | 4.0715 | 4.1121 | 4.3576
2022-05-20 23:00 | 2.7408 | 3.0216 | 3.0609 | 3.1091 | 3.1652 | 2.1324 | 2.575 | 2.6057 | 2.6476 | 2.1324 | 3.258 | 3.675 | 3.7026 | 3.7392 | 3.9621
2022-05-21 | 2.4387 | 2.6876 | 2.7221 | 2.7643 | 2.8136 | 1.7539 | 2.1211 | 2.148 | 2.1848 | 1.7539 | 2.4578 | 2.7791 | 2.8033 | 2.8354 | 3.0089
2022-05-21 01:00 | 2.191 | 2.4119 | 2.4415 | 2.4778 | 2.52 | 1.5216 | 1.8396 | 1.8627 | 1.8943 | 1.5216 | 2.5721 | 2.8993 | 2.9201 | 2.9477 | 3.122
2022-05-21 02:00 | 2.1339 | 2.3384 | 2.3619 | 2.3906 | 2.424 | 1.4289 | 1.7214 | 1.7397 | 1.7647 | 1.4289 | 2.3244 | 2.6155 | 2.632 | 2.6538 | 2.8077
2022-05-21 03:00 | 2.1529 | 2.3471 | 2.3645 | 2.3858 | 2.4106 | 1.3718 | 1.6453 | 1.6589 | 1.6774 | 1.3718 | 2.4197 | 2.713 | 2.7252 | 2.7414 | 2.8938
2022-05-21 04:00 | 2.191 | 2.3779 | 2.3902 | 2.4052 | 2.4227 | 1.4169 | 1.6913 | 1.7008 | 1.7139 | 1.4169 | 2.1529 | 2.4095 | 2.4181 | 2.4295 | 2.5615
2022-05-21 05:00 | 2.3054 | 2.4968 | 2.507 | 2.5195 | 2.5341 | 1.6276 | 1.9373 | 1.9453 | 1.9562 | 1.6276 | 2.4387 | 2.7242 | 2.7314 | 2.7409 | 2.8864
2022-05-21 06:00 | 2.5149 | 2.7253 | 2.7372 | 2.7518 | 2.7688 | 1.9119 | 2.2757 | 2.285 | 2.2977 | 1.9119 | 3.1437 | 3.51 | 3.5183 | 3.5294 | 3.7156
2022-05-21 07:00 | 2.7626 | 3.0005 | 3.017 | 3.0373 | 3.061 | 2.1148 | 2.5219 | 2.5349 | 2.5525 | 2.1148 | 4.001 | 4.4692 | 4.4808 | 4.4962 | 4.7346
2022-05-21 08:00 | 2.6864 | 2.9319 | 2.9553 | 2.984 | 3.0174 | 2.0958 | 2.5091 | 2.5274 | 2.5523 | 2.0958 | 3.0225 | 3.3912 | 3.4076 | 3.4294 | 3.6216
2022-05-21 09:00 | 2.4197 | 2.6596 | 2.6903 | 2.7278 | 2.7716 | 1.5761 | 1.9055 | 1.9295 | 1.9621 | 1.5761 | 1.829 | 2.0751 | 2.0966 | 2.1251 | 2.2598
2022-05-21 10:00 | 2.0005 | 2.2202 | 2.2565 | 2.3009 | 2.3526 | 1.2765 | 1.5596 | 1.5879 | 1.6265 | 1.2765 | 0.89547 | 1.0454 | 1.0708 | 1.1046 | 1.1942
2022-05-21 11:00 | 1.7909 | 1.9994 | 2.0379 | 2.085 | 2.1399 | 1.105 | 1.3602 | 1.3902 | 1.4312 | 1.105 | 0.91452 | 1.0696 | 1.0966 | 1.1324 | 1.2255
2022-05-21 12:00 | 2.2482 | 2.4896 | 2.5276 | 2.574 | 2.6282 | 1.4861 | 1.8096 | 1.8392 | 1.8796 | 1.4861 | 1.448 | 1.6617 | 1.6883 | 1.7236 | 1.8455
2022-05-21 13:00 | 1.9243 | 2.1367 | 2.1721 | 2.2154 | 2.2659 | 1.467 | 1.7834 | 1.8111 | 1.8487 | 1.467 | 1.5242 | 1.7429 | 1.7677 | 1.8006 | 1.9238
2022-05-21 14:00 | 1.9001 | 2.1052 | 2.1379 | 2.1778 | 2.2244 | 1.2184 | 1.4857 | 1.5112 | 1.5459 | 1.2184 | 1.3908 | 1.5908 | 1.6137 | 1.6441 | 1.7569
2022-05-21 15:00 | 2.3054 | 2.537 | 2.5678 | 2.6055 | 2.6495 | 1.7338 | 2.092 | 2.116 | 2.1488 | 1.7338 | 2.0958 | 2.3717 | 2.3933 | 2.4219 | 2.5714
2022-05-21 16:00 | 2.6864 | 2.9456 | 2.9759 | 3.0131 | 3.0564 | 2.1339 | 2.5641 | 2.5877 | 2.6201 | 2.1339 | 3.5438 | 3.9802 | 4.0014 | 4.0297 | 4.2583
2022-05-21 17:00 | 3.277 | 3.5836 | 3.6158 | 3.6552 | 3.7011 | 2.7245 | 3.2644 | 3.2895 | 3.3237 | 2.7245 | 4.7631 | 5.3377 | 5.3602 | 5.3902 | 5.6878
2022-05-21 18:00 | 3.277 | 3.591 | 3.6269 | 3.6709 | 3.7222 | 2.7245 | 3.2697 | 3.2977 | 3.336 | 2.7245 | 4.5726 | 5.1312 | 5.1564 | 5.1898 | 5.4812
2022-05-21 19:00 | 3.1818 | 3.4984 | 3.5393 | 3.5894 | 3.6478 | 2.6102 | 3.1418 | 3.1737 | 3.2172 | 2.6102 | 4.8393 | 5.4345 | 5.4632 | 5.5013 | 5.8128
2022-05-21 20:00 | 3.1056 | 3.4262 | 3.4721 | 3.5282 | 3.5936 | 2.5911 | 3.1263 | 3.162 | 3.2109 | 2.5911 | 4.4774 | 5.0391 | 5.0712 | 5.1139 | 5.4111
2022-05-21 21:00 | 2.9913 | 3.305 | 3.3517 | 3.4089 | 3.4755 | 2.4387 | 2.9474 | 2.9838 | 3.0335 | 2.4387 | 3.7534 | 4.2357 | 4.2684 | 4.3119 | 4.5702
2022-05-21 22:00 | 2.8579 | 3.1558 | 3.1994 | 3.2529 | 3.3152 | 2.3109 | 2.7921 | 2.8261 | 2.8726 | 2.3109 | 3.1818 | 3.5963 | 3.6269 | 3.6675 | 3.891
2022-05-21 23:00 | 2.6102 | 2.8812 | 2.9206 | 2.9687 | 3.0249 | 2.0086 | 2.4288 | 2.4595 | 2.5014 | 2.0086 | 3.0294 | 3.4209 | 3.4485 | 3.4851 | 3.6954
2022-05-22 | 2.4197 | 2.6671 | 2.7016 | 2.7439 | 2.7931 | 1.7528 | 2.1198 | 2.1467 | 2.1835 | 1.7528 | 2.4006 | 2.7156 | 2.7397 | 2.7719 | 2.9423
2022-05-22 01:00 | 2.2482 | 2.4733 | 2.5029 | 2.5392 | 2.5815 | 1.4997 | 1.8138 | 1.8369 | 1.8685 | 1.4997 | 2.1148 | 2.3912 | 2.4119 | 2.4395 | 2.5887
2022-05-22 02:00 | 2.1529 | 2.3589 | 2.3823 | 2.411 | 2.4445 | 1.3908 | 1.6764 | 1.6947 | 1.7197 | 1.3908 | 2.0958 | 2.3615 | 2.3779 | 2.3997 | 2.541
2022-05-22 03:00 | 2.0958 | 2.2857 | 2.3031 | 2.3244 | 2.3492 | 1.3527 | 1.6228 | 1.6364 | 1.6549 | 1.3527 | 2.0386 | 2.2896 | 2.3018 | 2.318 | 2.4494
2022-05-22 04:00 | 2.1339 | 2.3165 | 2.3288 | 2.3438 | 2.3613 | 1.3146 | 1.5705 | 1.58 | 1.5931 | 1.3146 | 2.2673 | 2.5365 | 2.5451 | 2.5565 | 2.6948
2022-05-22 05:00 | 2.1543 | 2.3345 | 2.3447 | 2.3572 | 2.3718 | 1.4806 | 1.7637 | 1.7716 | 1.7825 | 1.4806 | 2.3816 | 2.6607 | 2.6679 | 2.6774 | 2.8197
2022-05-22 06:00 | 2.3054 | 2.5001 | 2.512 | 2.5267 | 2.5437 | 1.6576 | 1.9752 | 1.9845 | 1.9972 | 1.6576 | 2.6102 | 2.9172 | 2.9255 | 2.9366 | 3.0934
2022-05-22 07:00 | 2.7055 | 2.939 | 2.9556 | 2.9759 | 2.9996 | 2.0577 | 2.4544 | 2.4674 | 2.485 | 2.0577 | 2.9722 | 3.3259 | 3.3375 | 3.3529 | 3.5348
2022-05-22 08:00 | 2.7055 | 2.9524 | 2.9758 | 3.0044 | 3.0378 | 2.1148 | 2.5316 | 2.5499 | 2.5748 | 2.1148 | 2.9341 | 3.293 | 3.3094 | 3.3312 | 3.5185
2022-05-22 09:00 | 2.4578 | 2.7005 | 2.7312 | 2.7688 | 2.8125 | 2.0386 | 2.452 | 2.4759 | 2.5086 | 2.0386 | 2.172 | 2.4562 | 2.4777 | 2.5062 | 2.6598
2022-05-22 10:00 | 2.172 | 2.4045 | 2.4407 | 2.4851 | 2.5369 | 1.5814 | 1.9197 | 1.948 | 1.9866 | 1.5814 | 1.6195 | 1.8499 | 1.8753 | 1.9091 | 2.0385
2022-05-22 11:00 | 2.2101 | 2.4497 | 2.4882 | 2.5353 | 2.5902 | 1.5623 | 1.9004 | 1.9304 | 1.9714 | 1.5623 | 1.4861 | 1.7048 | 1.7318 | 1.7676 | 1.8921
2022-05-22 12:00 | 1.9624 | 2.1826 | 2.2205 | 2.267 | 2.3211 | 1.4588 | 1.7773 | 1.8069 | 1.8473 | 1.4588 | 1.5052 | 1.7252 | 1.7518 | 1.7871 | 1.9121
2022-05-22 13:00 | 1.7147 | 1.9115 | 1.9469 | 1.9902 | 2.0408 | 1.2765 | 1.5584 | 1.586 | 1.6237 | 1.2765 | 0.85737 | 1.0018 | 1.0266 | 1.0596 | 1.1461
2022-05-22 14:00 | 1.7048 | 1.8954 | 1.928 | 1.968 | 2.0146 | 1.2019 | 1.4662 | 1.4917 | 1.5265 | 1.2019 | 1.1241 | 1.2944 | 1.3173 | 1.3477 | 1.4458
2022-05-22 15:00 | 2.1426 | 2.3622 | 2.393 | 2.4307 | 2.4747 | 1.6623 | 2.0076 | 2.0316 | 2.0644 | 1.6623 | 1.9434 | 2.2023 | 2.2239 | 2.2525 | 2.3937
2022-05-22 16:00 | 2.8343 | 3.1044 | 3.1348 | 3.1719 | 3.2153 | 2.3415 | 2.8093 | 2.833 | 2.8653 | 2.3415 | 3.2961 | 3.7049 | 3.7262 | 3.7545 | 3.9695
2022-05-22 17:00 | 3.258 | 3.5632 | 3.5954 | 3.6347 | 3.6807 | 2.8007 | 3.3544 | 3.3795 | 3.4138 | 2.8007 | 4.0772 | 4.5755 | 4.598 | 4.628 | 4.8879
2022-05-22 18:00 | 3.4676 | 3.7957 | 3.8316 | 3.8756 | 3.9269 | 2.9531 | 3.5398 | 3.5678 | 3.6061 | 2.9531 | 4.2297 | 4.7501 | 4.7753 | 4.8087 | 5.0812
2022-05-22 19:00 | 3.3723 | 3.7031 | 3.744 | 3.7941 | 3.8525 | 2.8388 | 3.4118 | 3.4438 | 3.4873 | 2.8388 | 5.068 | 5.6886 | 5.7172 | 5.7553 | 6.0795
2022-05-22 20:00 | 3.2961 | 3.6309 | 3.6768 | 3.7329 | 3.7983 | 2.8198 | 3.3964 | 3.4321 | 3.481 | 2.8198 | 4.2678 | 4.8062 | 4.8383 | 4.881 | 5.1667
2022-05-22 21:00 | 3.1818 | 3.5097 | 3.5564 | 3.6135 | 3.6802 | 2.5721 | 3.1049 | 3.1414 | 3.1911 | 2.5721 | 3.9629 | 4.4686 | 4.5013 | 4.5448 | 4.8146
2022-05-22 22:00 | 2.7055 | 2.992 | 3.0357 | 3.0891 | 3.1514 | 2.3123 | 2.7938 | 2.8278 | 2.8743 | 2.3123 | 3.0484 | 3.4481 | 3.4787 | 3.5193 | 3.7355
2022-05-22 23:00 | 2.5721 | 2.8403 | 2.8796 | 2.9278 | 2.9839 | 1.8752 | 2.2712 | 2.3019 | 2.3438 | 1.8752 | 2.7245 | 3.0822 | 3.1097 | 3.1464 | 3.3399
2022-05-23 | 2.3054 | 2.5443 | 2.5788 | 2.621 | 2.6703 | 1.5759 | 1.9107 | 1.9376 | 1.9744 | 1.5759 | 2.2291 | 2.525 | 2.5492 | 2.5813 | 2.7423
2022-05-23 01:00 | 2.2101 | 2.4324 | 2.462 | 2.4982 | 2.5405 | 1.4099 | 1.7077 | 1.7308 | 1.7623 | 1.4099 | 2.0196 | 2.2853 | 2.3061 | 2.3337 | 2.4777
2022-05-23 02:00 | 2.0577 | 2.2565 | 2.28 | 2.3087 | 2.3422 | 1.3908 | 1.6764 | 1.6947 | 1.7197 | 1.3908 | 2.1339 | 2.4038 | 2.4202 | 2.4421 | 2.5855
2022-05-23 03:00 | 2.1339 | 2.3266 | 2.344 | 2.3653 | 2.3902 | 1.4099 | 1.6903 | 1.7039 | 1.7225 | 1.4099 | 2.3435 | 2.6283 | 2.6405 | 2.6567 | 2.8049
2022-05-23 04:00 | 2.2673 | 2.4598 | 2.4721 | 2.4871 | 2.5046 | 1.467 | 1.7505 | 1.7601 | 1.7732 | 1.467 | 2.4578 | 2.7482 | 2.7568 | 2.7682 | 2.917
2022-05-23 05:00 | 2.4535 | 2.6559 | 2.6661 | 2.6786 | 2.6932 | 1.8361 | 2.1836 | 2.1916 | 2.2025 | 1.8361 | 2.9913 | 3.3382 | 3.3454 | 3.3549 | 3.5308
2022-05-23 06:00 | 3.1818 | 3.4417 | 3.4536 | 3.4682 | 3.4853 | 2.5312 | 3.0072 | 3.0165 | 3.0292 | 2.5312 | 4.2487 | 4.738 | 4.7463 | 4.7574 | 5.0043
2022-05-23 07:00 | 3.8486 | 4.1672 | 4.1838 | 4.2041 | 4.2277 | 3.0294 | 3.6023 | 3.6153 | 3.6329 | 3.0294 | 5.3538 | 5.9724 | 5.984 | 5.9994 | 6.3122
2022-05-23 08:00 | 3.8105 | 4.1396 | 4.163 | 4.1916 | 4.225 | 2.915 | 3.477 | 3.4952 | 3.5201 | 2.915 | 4.5536 | 5.0926 | 5.109 | 5.1308 | 5.4072
2022-05-23 09:00 | 3.3533 | 3.6626 | 3.6933 | 3.7308 | 3.7746 | 2.2716 | 2.7272 | 2.7511 | 2.7838 | 2.2716 | 4.3249 | 4.8486 | 4.8701 | 4.8987 | 5.1706
2022-05-23 10:00 | 2.9722 | 3.2641 | 3.3004 | 3.3448 | 3.3966 | 1.6385 | 1.9872 | 2.0155 | 2.0541 | 1.6385 | 2.4006 | 2.718 | 2.7434 | 2.7772 | 2.9495
2022-05-23 11:00 | 3.1627 | 3.4732 | 3.5117 | 3.5588 | 3.6137 | 1.8862 | 2.283 | 2.313 | 2.354 | 1.8862 | 2.6293 | 2.9751 | 3.0021 | 3.0379 | 3.2253
2022-05-23 12:00 | 2.8007 | 3.0832 | 3.1212 | 3.1676 | 3.2218 | 1.6576 | 2.0121 | 2.0417 | 2.0821 | 1.6576 | 1.829 | 2.0852 | 2.1117 | 2.1471 | 2.2899
2022-05-23 13:00 | 2.6864 | 2.9554 | 2.9908 | 3.0341 | 3.0847 | 1.6004 | 1.941 | 1.9686 | 2.0063 | 1.6004 | 1.6957 | 1.9334 | 1.9582 | 1.9912 | 2.1238
2022-05-23 14:00 | 2.4578 | 2.7044 | 2.737 | 2.777 | 2.8235 | 1.3337 | 1.622 | 1.6474 | 1.6822 | 1.3337 | 1.2575 | 1.4426 | 1.4655 | 1.4959 | 1.6013
2022-05-23 15:00 | 2.8579 | 3.1306 | 3.1614 | 3.1991 | 3.2431 | 1.9434 | 2.3396 | 2.3636 | 2.3964 | 1.9434 | 2.4768 | 2.7951 | 2.8167 | 2.8454 | 3.0158
2022-05-23 16:00 | 3.1246 | 3.4164 | 3.4467 | 3.4839 | 3.5272 | 2.3816 | 2.8567 | 2.8803 | 2.9127 | 2.3816 | 3.4104 | 3.8319 | 3.8532 | 3.8815 | 4.1028
2022-05-23 17:00 | 3.4866 | 3.8088 | 3.841 | 3.8804 | 3.9263 | 2.915 | 3.4894 | 3.5145 | 3.5488 | 2.915 | 4.3821 | 4.9142 | 4.9368 | 4.9667 | 5.2435
2022-05-23 18:00 | 3.5247 | 3.8571 | 3.893 | 3.937 | 3.9883 | 3.0045 | 3.6005 | 3.6286 | 3.6668 | 3.0045 | 4.6298 | 5.1947 | 5.2199 | 5.2533 | 5.5478
2022-05-23 19:00 | 3.4295 | 3.7645 | 3.8054 | 3.8555 | 3.9139 | 3.0484 | 3.6594 | 3.6913 | 3.7349 | 3.0484 | 4.7441 | 5.3286 | 5.3573 | 5.3954 | 5.7017
2022-05-23 20:00 | 3.3914 | 3.7332 | 3.7791 | 3.8352 | 3.9007 | 2.7817 | 3.3514 | 3.3871 | 3.436 | 2.7817 | 5.5824 | 6.2671 | 6.2992 | 6.3419 | 6.6998
2022-05-23 21:00 | 3.2389 | 3.5711 | 3.6178 | 3.675 | 3.7416 | 2.5908 | 3.127 | 3.1635 | 3.2132 | 2.5908 | 4.0772 | 4.5956 | 4.6283 | 4.6718 | 4.9479
2022-05-23 22:00 | 2.8547 | 3.1524 | 3.196 | 3.2494 | 3.3117 | 2.2372 | 2.705 | 2.7391 | 2.7855 | 2.2372 | 3.4295 | 3.8715 | 3.9021 | 3.9428 | 4.1799
2022-05-23 23:00 | 2.5118 | 2.7755 | 2.8148 | 2.863 | 2.9191 | 1.9026 | 2.3036 | 2.3342 | 2.3761 | 1.9026 | 2.8769 | 3.2516 | 3.2791 | 3.3157 | 3.5177
2022-05-24 | 2.3244 | 2.5648 | 2.5993 | 2.6415 | 2.6908 | 1.6004 | 1.9397 | 1.9666 | 2.0034 | 1.6004 | 2.8198 | 3.1814 | 3.2055 | 3.2377 | 3.4311
2022-05-24 01:00 | 2.2101 | 2.4324 | 2.462 | 2.4982 | 2.5405 | 1.5313 | 1.8511 | 1.8742 | 1.9058 | 1.5313 | 2.2673 | 2.5606 | 2.5813 | 2.6089 | 2.7665
2022-05-24 02:00 | 2.0958 | 2.2975 | 2.3209 | 2.3496 | 2.3831 | 1.448 | 1.7439 | 1.7622 | 1.7872 | 1.448 | 2.2101 | 2.4885 | 2.5049 | 2.5268 | 2.6744
2022-05-24 03:00 | 2.1339 | 2.3266 | 2.344 | 2.3653 | 2.3902 | 1.3718 | 1.6453 | 1.6589 | 1.6774 | 1.3718 | 2.0958 | 2.3531 | 2.3653 | 2.3815 | 2.5161
2022-05-24 04:00 | 2.2673 | 2.4598 | 2.4721 | 2.4871 | 2.5046 | 1.5433 | 1.8406 | 1.8501 | 1.8632 | 1.5433 | 2.553 | 2.8541 | 2.8627 | 2.8741 | 3.0281
2022-05-24 05:00 | 2.5149 | 2.7219 | 2.7322 | 2.7447 | 2.7593 | 1.8698 | 2.2235 | 2.2315 | 2.2424 | 1.8698 | 2.7817 | 3.1053 | 3.1125 | 3.122 | 3.2863
2022-05-24 06:00 | 3.4286 | 3.7069 | 3.7188 | 3.7334 | 3.7505 | 2.6171 | 3.1087 | 3.118 | 3.1307 | 2.6171 | 4.3059 | 4.8015 | 4.8098 | 4.821 | 5.071
2022-05-24 07:00 | 3.8677 | 4.1877 | 4.2042 | 4.2245 | 4.2482 | 2.7245 | 3.2422 | 3.2551 | 3.2728 | 2.7245 | 5.068 | 5.6548 | 5.6664 | 5.6819 | 5.9789
2022-05-24 08:00 | 3.5057 | 3.8121 | 3.8355 | 3.8641 | 3.8975 | 2.4607 | 2.9403 | 2.9585 | 2.9834 | 2.4607 | 3.9439 | 4.4151 | 4.4315 | 4.4533 | 4.6961
2022-05-24 09:00 | 2.7245 | 2.9871 | 3.0178 | 3.0553 | 3.0991 | 1.7528 | 2.1143 | 2.1383 | 2.1709 | 1.7528 | 1.9815 | 2.2445 | 2.2659 | 2.2945 | 2.4376
2022-05-24 10:00 | 2.2863 | 2.5273 | 2.5635 | 2.6079 | 2.6597 | 1.3337 | 1.6271 | 1.6554 | 1.694 | 1.3337 | 1.2765 | 1.4688 | 1.4942 | 1.528 | 1.6386
2022-05-24 11:00 | 2.2101 | 2.4497 | 2.4882 | 2.5353 | 2.5902 | 1.2003 | 1.4727 | 1.5027 | 1.5437 | 1.2003 | 0.97168 | 1.1332 | 1.1601 | 1.1959 | 1.2922
2022-05-24 12:00 | 1.8862 | 2.1007 | 2.1387 | 2.1851 | 2.2393 | 1.0098 | 1.2469 | 1.2765 | 1.3169 | 1.0098 | 0.95263 | 1.1112 | 1.1378 | 1.1732 | 1.2678
2022-05-24 13:00 | 1.9624 | 2.1776 | 2.213 | 2.2563 | 2.3068 | 0.88485 | 1.0957 | 1.1233 | 1.161 | 0.88485 | 0.97168 | 1.1289 | 1.1537 | 1.1866 | 1.2795
2022-05-24 14:00 | 2.172 | 2.3973 | 2.43 | 2.4699 | 2.5165 | 1.1382 | 1.391 | 1.4165 | 1.4512 | 1.1382 | 0.93358 | 1.0827 | 1.1056 | 1.136 | 1.2236
2022-05-24 15:00 | 2.6102 | 2.8645 | 2.8954 | 2.9331 | 2.977 | 1.5598 | 1.8865 | 1.9105 | 1.9433 | 1.5598 | 1.6957 | 1.9271 | 1.9486 | 1.9773 | 2.1048
2022-05-24 16:00 | 2.896 | 3.1707 | 3.2011 | 3.2383 | 3.2816 | 2.125 | 2.5536 | 2.5773 | 2.6096 | 2.125 | 2.8769 | 3.2391 | 3.2604 | 3.2887 | 3.4806
2022-05-24 17:00 | 3.1437 | 3.4404 | 3.4725 | 3.5119 | 3.5578 | 2.8026 | 3.3566 | 3.3817 | 3.416 | 2.8026 | 4.4202 | 4.9566 | 4.9791 | 5.0091 | 5.2879
2022-05-24 18:00 | 3.3342 | 3.6524 | 3.6883 | 3.7323 | 3.7836 | 2.896 | 3.4723 | 3.5003 | 3.5386 | 2.896 | 4.1916 | 4.7077 | 4.7329 | 4.7664 | 5.0368
2022-05-24 19:00 | 3.3151 | 3.6417 | 3.6826 | 3.7327 | 3.7911 | 2.7436 | 3.2993 | 3.3312 | 3.3748 | 2.7436 | 4.8584 | 5.4557 | 5.4843 | 5.5224 | 5.8351
2022-05-24 20:00 | 3.2008 | 3.5286 | 3.5744 | 3.6305 | 3.696 | 2.7245 | 3.2838 | 3.3196 | 3.3684 | 2.7245 | 5.087 | 5.7166 | 5.7487 | 5.7914 | 6.1221
2022-05-24 21:00 | 3.0294 | 3.346 | 3.3927 | 3.4498 | 3.5164 | 2.6102 | 3.15 | 3.1864 | 3.2361 | 2.6102 | 3.982 | 4.4898 | 4.5225 | 4.5659 | 4.8368
2022-05-24 22:00 | 2.8007 | 3.0944 | 3.138 | 3.1915 | 3.2537 | 2.2291 | 2.6955 | 2.7295 | 2.776 | 2.2291 | 3.2961 | 3.7233 | 3.7539 | 3.7945 | 4.0243
2022-05-24 23:00 | 2.4577 | 2.7174 | 2.7568 | 2.8049 | 2.861 | 1.8775 | 2.274 | 2.3046 | 2.3465 | 1.8775 | 2.7626 | 3.1245 | 3.1521 | 3.1887 | 3.3844
2022-05-25 | 2.2291 | 2.4624 | 2.4969 | 2.5392 | 2.5884 | 1.6004 | 1.9397 | 1.9666 | 2.0034 | 1.6004 | 2.3244 | 2.6309 | 2.6551 | 2.6872 | 2.8534
2022-05-25 01:00 | 2.1148 | 2.33 | 2.3596 | 2.3959 | 2.4382 | 1.4508 | 1.7561 | 1.7792 | 1.8107 | 1.4508 | 2.2101 | 2.4971 | 2.5178 | 2.5454 | 2.6998
2022-05-25 02:00 | 2.0577 | 2.2565 | 2.28 | 2.3087 | 2.3422 | 1.3908 | 1.6764 | 1.6947 | 1.7197 | 1.3908 | 2.2673 | 2.552 | 2.5684 | 2.5903 | 2.741
2022-05-25 03:00 | 2.1529 | 2.3471 | 2.3645 | 2.3858 | 2.4106 | 1.3819 | 1.6573 | 1.6708 | 1.6894 | 1.3819 | 2.4387 | 2.7342 | 2.7464 | 2.7626 | 2.916
2022-05-25 04:00 | 2.172 | 2.3575 | 2.3697 | 2.3847 | 2.4022 | 1.4289 | 1.7055 | 1.7151 | 1.7281 | 1.4289 | 2.5149 | 2.8117 | 2.8203 | 2.8317 | 2.9836
2022-05-25 05:00 | 2.5289 | 2.737 | 2.7472 | 2.7597 | 2.7743 | 1.8376 | 2.1854 | 2.1934 | 2.2043 | 1.8376 | 2.6102 | 2.9148 | 2.922 | 2.9315 | 3.0864
2022-05-25 06:00 | 3.0294 | 3.2779 | 3.2899 | 3.3045 | 3.3215 | 2.5045 | 2.9757 | 2.985 | 2.9977 | 2.5045 | 3.8296 | 4.2722 | 4.2805 | 4.2917 | 4.5155
2022-05-25 07:00 | 3.6771 | 3.983 | 3.9995 | 4.0198 | 4.0435 | 2.7055 | 3.2197 | 3.2326 | 3.2503 | 2.7055 | 4.8012 | 5.3584 | 5.37 | 5.3855 | 5.6678
2022-05-25 08:00 | 3.4676 | 3.7712 | 3.7946 | 3.8232 | 3.8566 | 2.5721 | 3.0718 | 3.0901 | 3.115 | 2.5721 | 4.5536 | 5.0926 | 5.109 | 5.1308 | 5.4072
2022-05-25 09:00 | 2.7532 | 3.0179 | 3.0486 | 3.0861 | 3.1299 | 1.8785 | 2.2628 | 2.2867 | 2.3194 | 1.8785 | 1.9815 | 2.2445 | 2.2659 | 2.2945 | 2.4376
2022-05-25 10:00 | 2.6674 | 2.9366 | 2.9729 | 3.0173 | 3.0691 | 1.829 | 2.2123 | 2.2406 | 2.2792 | 1.829 | 1.7338 | 1.977 | 2.0024 | 2.0361 | 2.1718
2022-05-25 11:00 | 2.7817 | 3.0638 | 3.1023 | 3.1494 | 3.2043 | 1.6385 | 1.9904 | 2.0204 | 2.0614 | 1.6385 | 1.5052 | 1.726 | 1.7529 | 1.7888 | 1.9144
2022-05-25 12:00 | 2.3816 | 2.6329 | 2.6708 | 2.7173 | 2.7714 | 1.6195 | 1.9671 | 1.9967 | 2.0371 | 1.6195 | 1.5433 | 1.7676 | 1.7942 | 1.8295 | 1.9566
2022-05-25 13:00 | 2.2863 | 2.5256 | 2.561 | 2.6043 | 2.6548 | 1.4289 | 1.7384 | 1.766 | 1.8037 | 1.4289 | 1.3908 | 1.5947 | 1.6195 | 1.6524 | 1.7683
2022-05-25 14:00 | 2.3625 | 2.602 | 2.6347 | 2.6746 | 2.7212 | 1.448 | 1.757 | 1.7825 | 1.8172 | 1.448 | 1.5052 | 1.7179 | 1.7407 | 1.7711 | 1.8902
2022-05-25 15:00 | 2.5019 | 2.7482 | 2.779 | 2.8168 | 2.8607 | 1.81 | 2.182 | 2.2061 | 2.2389 | 1.81 | 2.1529 | 2.4352 | 2.4568 | 2.4854 | 2.6381
2022-05-25 16:00 | 2.878 | 3.1514 | 3.1818 | 3.219 | 3.2623 | 2.1775 | 2.6156 | 2.6393 | 2.6716 | 2.1775 | 3.2961 | 3.7049 | 3.7262 | 3.7545 | 3.9695
2022-05-25 17:00 | 3.2008 | 3.5018 | 3.5339 | 3.5733 | 3.6192 | 2.8769 | 3.4444 | 3.4695 | 3.5038 | 2.8769 | 4.5726 | 5.126 | 5.1485 | 5.1785 | 5.4657
2022-05-25 18:00 | 3.3914 | 3.7138 | 3.7498 | 3.7937 | 3.845 | 2.9913 | 3.5848 | 3.6129 | 3.6511 | 2.9913 | 4.8393 | 5.4276 | 5.4528 | 5.4862 | 5.7923
2022-05-25 19:00 | 3.3723 | 3.7031 | 3.744 | 3.7941 | 3.8525 | 2.9913 | 3.5919 | 3.6238 | 3.6674 | 2.9913 | 4.6298 | 5.2016 | 5.2303 | 5.2684 | 5.5684
2022-05-25 20:00 | 3.258 | 3.59 | 3.6358 | 3.6919 | 3.7574 | 2.8661 | 3.4511 | 3.4869 | 3.5357 | 2.8661 | 4.2868 | 4.8274 | 4.8595 | 4.9022 | 5.1889
2022-05-25 21:00 | 3.0294 | 3.346 | 3.3927 | 3.4498 | 3.5164 | 2.6648 | 3.2145 | 3.2509 | 3.3006 | 2.6648 | 4.6679 | 5.252 | 5.2847 | 5.3281 | 5.6367
2022-05-25 22:00 | 2.6864 | 2.9716 | 3.0152 | 3.0686 | 3.1309 | 2.3244 | 2.808 | 2.8421 | 2.8885 | 2.3244 | 3.9058 | 4.4008 | 4.4314 | 4.4721 | 4.7354
2022-05-25 23:00 | 2.4197 | 2.6766 | 2.7159 | 2.764 | 2.8202 | 1.893 | 2.2923 | 2.3229 | 2.3648 | 1.893 | 2.9913 | 3.3786 | 3.4062 | 3.4428 | 3.651
2022-05-26 | 2.0958 | 2.3191 | 2.3536 | 2.3959 | 2.4451 | 1.6004 | 1.9397 | 1.9666 | 2.0034 | 1.6004 | 2.4197 | 2.7367 | 2.7609 | 2.793 | 2.9645
2022-05-26 01:00 | 1.9815 | 2.1867 | 2.2164 | 2.2526 | 2.2949 | 1.4152 | 1.714 | 1.7371 | 1.7686 | 1.4152 | 2.172 | 2.4547 | 2.4755 | 2.503 | 2.6554
2022-05-26 02:00 | 2.0005 | 2.1951 | 2.2186 | 2.2473 | 2.2808 | 1.3337 | 1.6089 | 1.6272 | 1.6521 | 1.3337 | 2.0958 | 2.3615 | 2.3779 | 2.3997 | 2.541
2022-05-26 03:00 | 1.8862 | 2.0605 | 2.0779 | 2.0992 | 2.1241 | 1.3337 | 1.6003 | 1.6139 | 1.6324 | 1.3337 | 1.9624 | 2.2049 | 2.2171 | 2.2333 | 2.3605
2022-05-26 04:00 | 2.0196 | 2.1937 | 2.206 | 2.221 | 2.2385 | 1.3724 | 1.6387 | 1.6483 | 1.6614 | 1.3724 | 2.0386 | 2.2824 | 2.291 | 2.3024 | 2.4282
2022-05-26 05:00 | 2.3519 | 2.5468 | 2.557 | 2.5695 | 2.5841 | 1.7128 | 2.038 | 2.046 | 2.0569 | 1.7128 | 2.4197 | 2.7031 | 2.7102 | 2.7198 | 2.8642
2022-05-26 06:00 | 2.9722 | 3.2165 | 3.2285 | 3.2431 | 3.2601 | 2.3373 | 2.7781 | 2.7874 | 2.8001 | 2.3373 | 3.3478 | 3.7368 | 3.7451 | 3.7563 | 3.9536
2022-05-26 07:00 | 3.5057 | 3.7987 | 3.8153 | 3.8356 | 3.8593 | 2.5911 | 3.0846 | 3.0976 | 3.1152 | 2.5911 | 4.0963 | 4.575 | 4.5866 | 4.6021 | 4.8457
2022-05-26 08:00 | 3.3914 | 3.6893 | 3.7127 | 3.7413 | 3.7747 | 2.3827 | 2.8481 | 2.8663 | 2.8912 | 2.3827 | 3.6009 | 4.034 | 4.0504 | 4.0722 | 4.2962
2022-05-26 09:00 | 3.1246 | 3.417 | 3.4476 | 3.4852 | 3.529 | 2.0196 | 2.4294 | 2.4534 | 2.486 | 2.0196 | 2.4197 | 2.7314 | 2.7529 | 2.7815 | 2.9486
2022-05-26 10:00 | 2.7436 | 3.0185 | 3.0548 | 3.0992 | 3.1509 | 1.6766 | 2.0323 | 2.0605 | 2.0992 | 1.6766 | 1.81 | 2.0617 | 2.0871 | 2.1208 | 2.2607
2022-05-26 11:00 | 2.1148 | 2.3474 | 2.3859 | 2.433 | 2.4879 | 1.0669 | 1.3152 | 1.3452 | 1.3862 | 1.0669 | 0.95263 | 1.112 | 1.1389 | 1.1748 | 1.27
2022-05-26 12:00 | 2.0577 | 2.2849 | 2.3229 | 2.3693 | 2.4235 | 1.2003 | 1.472 | 1.5015 | 1.542 | 1.2003 | 1.0669 | 1.2383 | 1.2649 | 1.3002 | 1.4011
2022-05-26 13:00 | 2.1529 | 2.3823 | 2.4177 | 2.461 | 2.5115 | 1.3146 | 1.6034 | 1.631 | 1.6687 | 1.3146 | 1.0479 | 1.2136 | 1.2384 | 1.2713 | 1.3683
2022-05-26 14:00 | 2.3244 | 2.5611 | 2.5937 | 2.6337 | 2.6803 | 1.3337 | 1.622 | 1.6474 | 1.6822 | 1.3337 | 1.3119 | 1.5031 | 1.526 | 1.5564 | 1.6649
2022-05-26 15:00 | 2.4578 | 2.7008 | 2.7316 | 2.7693 | 2.8133 | 1.6057 | 1.9407 | 1.9647 | 1.9975 | 1.6057 | 1.8862 | 2.1388 | 2.1604 | 2.189 | 2.327
2022-05-26 16:00 | 2.6466 | 2.9028 | 2.9332 | 2.9704 | 3.0137 | 2.0929 | 2.5157 | 2.5394 | 2.5717 | 2.0929 | 2.6674 | 3.0062 | 3.0275 | 3.0558 | 3.2362
2022-05-26 17:00 | 2.9531 | 3.2357 | 3.2678 | 3.3072 | 3.3532 | 2.534 | 3.0393 | 3.0644 | 3.0987 | 2.534 | 3.6009 | 4.0462 | 4.0687 | 4.0987 | 4.3324
2022-05-26 18:00 | 3.1437 | 3.4477 | 3.4837 | 3.5276 | 3.5789 | 2.534 | 3.0446 | 3.0727 | 3.1109 | 2.534 | 3.7343 | 4.1996 | 4.2248 | 4.2582 | 4.5035
2022-05-26 19:00 | 3.0675 | 3.3756 | 3.4165 | 3.4666 | 3.525 | 2.6102 | 3.1418 | 3.1737 | 3.2172 | 2.6102 | 4.5536 | 5.1169 | 5.1456 | 5.1837 | 5.4795
2022-05-26 20:00 | 2.9719 | 3.2826 | 3.3284 | 3.3846 | 3.45 | 2.553 | 3.0813 | 3.117 | 3.1659 | 2.553 | 3.9248 | 4.4251 | 4.4572 | 4.4999 | 4.7667
2022-05-26 21:00 | 2.7626 | 3.0594 | 3.1061 | 3.1632 | 3.2299 | 2.3397 | 2.8304 | 2.8668 | 2.9166 | 2.3397 | 3.4295 | 3.8758 | 3.9085 | 3.9519 | 4.1924
2022-05-26 22:00 | 2.4655 | 2.7342 | 2.7779 | 2.8313 | 2.8936 | 2.0767 | 2.5154 | 2.5495 | 2.5959 | 2.0767 | 2.8007 | 3.1729 | 3.2034 | 3.2441 | 3.4466
2022-05-26 23:00 | 2.1783 | 2.4173 | 2.4566 | 2.5048 | 2.5609 | 1.7804 | 2.1593 | 2.1899 | 2.2318 | 1.7804 | 2.5149 | 2.8493 | 2.8768 | 2.9135 | 3.0955
2022-05-27 | 1.9624 | 2.1759 | 2.2104 | 2.2526 | 2.3018 | 1.4473 | 1.7589 | 1.7858 | 1.8225 | 1.4473 | 2.0577 | 2.3345 | 2.3586 | 2.3908 | 2.5423
2022-05-27 01:00 | 1.8672 | 2.0639 | 2.0936 | 2.1298 | 2.1721 | 1.3146 | 1.5952 | 1.6183 | 1.6498 | 1.3146 | 1.7528 | 1.9889 | 2.0097 | 2.0372 | 2.1666
2022-05-27 02:00 | 1.7909 | 1.97 | 1.9934 | 2.0221 | 2.0556 | 1.2384 | 1.4963 | 1.5146 | 1.5396 | 1.2384 | 1.7147 | 1.938 | 1.9544 | 1.9763 | 2.0966
2022-05-27 03:00 | 1.81 | 1.9786 | 1.996 | 2.0173 | 2.0422 | 1.2194 | 1.4653 | 1.4788 | 1.4974 | 1.2194 | 1.9624 | 2.2049 | 2.2171 | 2.2333 | 2.3605
2022-05-27 04:00 | 1.829 | 1.989 | 2.0013 | 2.0163 | 2.0338 | 1.2772 | 1.5262 | 1.5358 | 1.5489 | 1.2772 | 1.8481 | 2.0707 | 2.0793 | 2.0907 | 2.206
2022-05-27 05:00 | 2.1647 | 2.3456 | 2.3559 | 2.3684 | 2.383 | 1.5814 | 1.8828 | 1.8908 | 1.9017 | 1.5814 | 2.2673 | 2.5337 | 2.5409 | 2.5504 | 2.6864
2022-05-27 06:00 | 2.6872 | 2.9104 | 2.9223 | 2.9369 | 2.954 | 2.0675 | 2.4594 | 2.4687 | 2.4814 | 2.0675 | 3.4295 | 3.8276 | 3.8359 | 3.847 | 4.0488
2022-05-27 07:00 | 3.0294 | 3.287 | 3.3036 | 3.3239 | 3.3476 | 2.3625 | 2.8145 | 2.8275 | 2.8451 | 2.3625 | 3.9439 | 4.4057 | 4.4173 | 4.4327 | 4.668
2022-05-27 08:00 | 3.0675 | 3.3413 | 3.3647 | 3.3933 | 3.4267 | 2.4006 | 2.8693 | 2.8875 | 2.9124 | 2.4006 | 3.9058 | 4.3728 | 4.3892 | 4.4109 | 4.6517
2022-05-27 09:00 | 3.0865 | 3.376 | 3.4067 | 3.4442 | 3.488 | 1.9482 | 2.3451 | 2.369 | 2.4017 | 1.9482 | 2.896 | 3.2607 | 3.2822 | 3.3108 | 3.5041
2022-05-27 10:00 | 2.1339 | 2.3635 | 2.3998 | 2.4442 | 2.4959 | 1.3337 | 1.6271 | 1.6554 | 1.694 | 1.3337 | 1.0098 | 1.1724 | 1.1978 | 1.2316 | 1.3275
2022-05-27 11:00 | 2.4387 | 2.6954 | 2.7338 | 2.7809 | 2.8359 | 1.6004 | 1.9454 | 1.9754 | 2.0164 | 1.6004 | 1.4861 | 1.7048 | 1.7318 | 1.7676 | 1.8921
2022-05-27 12:00 | 2.4197 | 2.6738 | 2.7118 | 2.7582 | 2.8124 | 1.5242 | 1.8546 | 1.8842 | 1.9246 | 1.5242 | 1.5433 | 1.7676 | 1.7942 | 1.8295 | 1.9566
2022-05-27 13:00 | 2.3244 | 2.5665 | 2.6019 | 2.6452 | 2.6958 | 1.4289 | 1.7384 | 1.766 | 1.8037 | 1.4289 | 1.1646 | 1.3432 | 1.368 | 1.401 | 1.5044
2022-05-27 14:00 | 2.2101 | 2.4383 | 2.4709 | 2.5109 | 2.5574 | 1.3196 | 1.6054 | 1.6308 | 1.6656 | 1.3196 | 1.1432 | 1.3156 | 1.3385 | 1.3688 | 1.468
2022-05-27 15:00 | 2.3625 | 2.5985 | 2.6293 | 2.667 | 2.7109 | 1.4861 | 1.7994 | 1.8234 | 1.8562 | 1.4861 | 1.81 | 2.0541 | 2.0757 | 2.1043 | 2.2381
2022-05-27 16:00 | 2.4959 | 2.7409 | 2.7712 | 2.8084 | 2.8517 | 1.9053 | 2.294 | 2.3176 | 2.35 | 1.9053 | 2.5721 | 2.9004 | 2.9216 | 2.9499 | 3.1251
2022-05-27 17:00 | 2.7817 | 3.0515 | 3.0836 | 3.123 | 3.1689 | 2.2384 | 2.6901 | 2.7152 | 2.7494 | 2.2384 | 3.2389 | 3.6439 | 3.6664 | 3.6964 | 3.9103
2022-05-27 18:00 | 2.8198 | 3.0997 | 3.1357 | 3.1797 | 3.231 | 2.3435 | 2.8196 | 2.8476 | 2.8859 | 2.3435 | 3.7343 | 4.1996 | 4.2248 | 4.2582 | 4.5035
2022-05-27 19:00 | 2.8579 | 3.1504 | 3.1914 | 3.2414 | 3.2998 | 2.3816 | 2.8717 | 2.9036 | 2.9472 | 2.3816 | 3.277 | 3.6984 | 3.727 | 3.7651 | 3.9908
2022-05-27 20:00 | 2.7436 | 3.0373 | 3.0832 | 3.1393 | 3.2047 | 2.3054 | 2.7887 | 2.8244 | 2.8733 | 2.3054 | 3.5438 | 4.0016 | 4.0338 | 4.0765 | 4.3223
2022-05-27 21:00 | 2.6674 | 2.9571 | 3.0037 | 3.0609 | 3.1275 | 2.1529 | 2.6098 | 2.6462 | 2.6959 | 2.1529 | 3.8677 | 4.3627 | 4.3954 | 4.4389 | 4.7035
2022-05-27 22:00 | 2.5149 | 2.7873 | 2.831 | 2.8844 | 2.9467 | 1.9815 | 2.4029 | 2.4369 | 2.4834 | 1.9815 | 3.277 | 3.7022 | 3.7327 | 3.7734 | 4.0021
2022-05-27 23:00 | 2.2344 | 2.4775 | 2.5169 | 2.565 | 2.6211 | 1.7597 | 2.1348 | 2.1654 | 2.2073 | 1.7597 | 2.3054 | 2.6164 | 2.644 | 2.6806 | 2.8511
2022-05-28 | 2.0767 | 2.2987 | 2.3332 | 2.3754 | 2.4247 | 1.4992 | 1.8201 | 1.8471 | 1.8838 | 1.4992 | 2.6102 | 2.9485 | 2.9726 | 3.0048 | 3.1867
2022-05-28 01:00 | 1.8716 | 2.0687 | 2.0984 | 2.1346 | 2.1769 | 1.3146 | 1.5952 | 1.6183 | 1.6498 | 1.3146 | 1.81 | 2.0524 | 2.0732 | 2.1008 | 2.2332
2022-05-28 02:00 | 1.8481 | 2.0314 | 2.0548 | 2.0835 | 2.117 | 1.2194 | 1.4738 | 1.4921 | 1.5171 | 1.2194 | 1.9053 | 2.1497 | 2.1662 | 2.188 | 2.3188
2022-05-28 03:00 | 1.7909 | 1.9582 | 1.9756 | 1.9969 | 2.0217 | 1.2003 | 1.4427 | 1.4563 | 1.4749 | 1.2003 | 1.6957 | 1.9085 | 1.9207 | 1.9369 | 2.0495
2022-05-28 04:00 | 1.7719 | 1.9276 | 1.9399 | 1.9549 | 1.9724 | 1.2194 | 1.4579 | 1.4675 | 1.4806 | 1.2194 | 1.829 | 2.0495 | 2.0581 | 2.0695 | 2.1837
2022-05-28 05:00 | 1.9624 | 2.1283 | 2.1386 | 2.1511 | 2.1657 | 1.3392 | 1.5966 | 1.6046 | 1.6155 | 1.3392 | 1.9434 | 2.1738 | 2.1809 | 2.1905 | 2.3087
2022-05-28 06:00 | 2.1148 | 2.2954 | 2.3074 | 2.322 | 2.339 | 1.5628 | 1.8632 | 1.8725 | 1.8852 | 1.5628 | 2.0577 | 2.3032 | 2.3115 | 2.3226 | 2.449
2022-05-28 07:00 | 2.2291 | 2.4273 | 2.4439 | 2.4642 | 2.4879 | 1.7909 | 2.1393 | 2.1522 | 2.1699 | 1.7909 | 2.4578 | 2.7542 | 2.7658 | 2.7813 | 2.9348
2022-05-28 08:00 | 2.3435 | 2.5635 | 2.5869 | 2.6155 | 2.6489 | 1.9243 | 2.3066 | 2.3248 | 2.3497 | 1.9243 | 2.915 | 3.2718 | 3.2882 | 3.31 | 3.4963
2022-05-28 09:00 | 2.5721 | 2.8234 | 2.854 | 2.8916 | 2.9354 | 1.7909 | 2.1594 | 2.1833 | 2.2159 | 1.7909 | 2.7817 | 3.1337 | 3.1552 | 3.1837 | 3.3708
2022-05-28 10:00 | 2.2256 | 2.462 | 2.4983 | 2.5427 | 2.5944 | 1.7909 | 2.1673 | 2.1956 | 2.2342 | 1.7909 | 2.4197 | 2.7392 | 2.7646 | 2.7983 | 2.9717
2022-05-28 11:00 | 2.1529 | 2.3883 | 2.4268 | 2.4739 | 2.5288 | 1.5052 | 1.8328 | 1.8629 | 1.9038 | 1.5052 | 1.5814 | 1.8107 | 1.8376 | 1.8735 | 2.0032
2022-05-28 12:00 | 2.0767 | 2.3054 | 2.3433 | 2.3898 | 2.4439 | 1.6957 | 2.0572 | 2.0868 | 2.1272 | 1.6957 | 2.0577 | 2.3392 | 2.3658 | 2.4011 | 2.5565
2022-05-28 13:00 | 2.0958 | 2.3209 | 2.3563 | 2.3996 | 2.4501 | 1.5814 | 1.9185 | 1.9461 | 1.9838 | 1.5814 | 1.6385 | 1.8699 | 1.8947 | 1.9277 | 2.0571
2022-05-28 14:00 | 2.0958 | 2.3155 | 2.3481 | 2.3881 | 2.4346 | 1.5623 | 1.892 | 1.9175 | 1.9523 | 1.5623 | 1.7338 | 1.9719 | 1.9948 | 2.0252 | 2.1568
2022-05-28 15:00 | 2.1529 | 2.3733 | 2.4041 | 2.4418 | 2.4858 | 1.6195 | 1.957 | 1.981 | 2.0138 | 1.6195 | 2.4387 | 2.7528 | 2.7744 | 2.803 | 2.9714
2022-05-28 16:00 | 2.5912 | 2.8433 | 2.8737 | 2.9108 | 2.9542 | 2.2553 | 2.7075 | 2.7312 | 2.7635 | 2.2553 | 3.0103 | 3.3873 | 3.4086 | 3.4369 | 3.6362
2022-05-28 17:00 | 2.9531 | 3.2357 | 3.2678 | 3.3072 | 3.3532 | 2.5721 | 3.0843 | 3.1094 | 3.1437 | 2.5721 | 3.5628 | 4.0038 | 4.0264 | 4.0563 | 4.288
2022-05-28 18:00 | 2.9531 | 3.243 | 3.279 | 3.3229 | 3.3742 | 2.5911 | 3.1122 | 3.1402 | 3.1785 | 2.5911 | 4.1916 | 4.7077 | 4.7329 | 4.7664 | 5.0368
2022-05-28 19:00 | 2.9722 | 3.2733 | 3.3142 | 3.3643 | 3.4226 | 2.5149 | 3.0292 | 3.0611 | 3.1047 | 2.5149 | 3.7343 | 4.2065 | 4.2352 | 4.2733 | 4.5241
2022-05-28 20:00 | 3.0484 | 3.3648 | 3.4107 | 3.4668 | 3.5322 | 2.4578 | 2.9687 | 3.0045 | 3.0533 | 2.4578 | 3.8486 | 4.3404 | 4.3725 | 4.4152 | 4.6778
2022-05-28 21:00 | 2.896 | 3.2027 | 3.2494 | 3.3065 | 3.3732 | 2.3435 | 2.8349 | 2.8713 | 2.921 | 2.3435 | 3.8486 | 4.3415 | 4.3743 | 4.4177 | 4.6813
2022-05-28 22:00 | 2.7245 | 3.0125 | 3.0562 | 3.1096 | 3.1719 | 2.2291 | 2.6955 | 2.7295 | 2.776 | 2.2291 | 3.5057 | 3.9562 | 3.9868 | 4.0274 | 4.2688
2022-05-28 23:00 | 2.5721 | 2.8403 | 2.8796 | 2.9278 | 2.9839 | 1.9815 | 2.3967 | 2.4274 | 2.4693 | 1.9815 | 3.1246 | 3.5268 | 3.5544 | 3.591 | 3.8065
2022-05-29 | 2.3054 | 2.5443 | 2.5788 | 2.621 | 2.6703 | 1.7509 | 2.1175 | 2.1444 | 2.1812 | 1.7509 | 2.7626 | 3.1178 | 3.142 | 3.1741 | 3.3644
2022-05-29 01:00 | 2.2291 | 2.4528 | 2.4825 | 2.5187 | 2.561 | 1.5433 | 1.8652 | 1.8884 | 1.9199 | 1.5433 | 2.534 | 2.857 | 2.8777 | 2.9053 | 3.0776
2022-05-29 02:00 | 2.172 | 2.3794 | 2.4028 | 2.4315 | 2.465 | 1.4861 | 1.789 | 1.8072 | 1.8322 | 1.4861 | 2.3054 | 2.5944 | 2.6108 | 2.6326 | 2.7855
2022-05-29 03:00 | 2.1339 | 2.3266 | 2.344 | 2.3653 | 2.3902 | 1.4697 | 1.761 | 1.7746 | 1.7932 | 1.4697 | 2.1339 | 2.3954 | 2.4076 | 2.4238 | 2.5605
2022-05-29 04:00 | 2.2291 | 2.4189 | 2.4311 | 2.4461 | 2.4636 | 1.4861 | 1.773 | 1.7826 | 1.7957 | 1.4861 | 2.2863 | 2.5577 | 2.5663 | 2.5777 | 2.717
2022-05-29 05:00 | 2.3625 | 2.5582 | 2.5684 | 2.5809 | 2.5955 | 1.6704 | 1.9879 | 1.9958 | 2.0067 | 1.6704 | 2.4768 | 2.7666 | 2.7738 | 2.7833 | 2.9308
2022-05-29 06:00 | 2.5149 | 2.7253 | 2.7372 | 2.7518 | 2.7688 | 1.7982 | 2.1412 | 2.1505 | 2.1633 | 1.7982 | 3.0294 | 3.3829 | 3.3913 | 3.4024 | 3.5822
2022-05-29 07:00 | 2.5076 | 2.7265 | 2.7431 | 2.7634 | 2.7871 | 2.1665 | 2.583 | 2.5959 | 2.6136 | 2.1665 | 3.4866 | 3.8975 | 3.9091 | 3.9246 | 4.1347
2022-05-29 08:00 | 2.7436 | 2.9933 | 3.0167 | 3.0454 | 3.0788 | 2.2482 | 2.6892 | 2.7074 | 2.7324 | 2.2482 | 3.4485 | 3.8646 | 3.881 | 3.9028 | 4.1184
2022-05-29 09:00 | 2.534 | 2.7824 | 2.8131 | 2.8506 | 2.8944 | 2.1148 | 2.542 | 2.5659 | 2.5986 | 2.1148 | 2.5721 | 2.9008 | 2.9223 | 2.9508 | 3.1264
2022-05-29 10:00 | 2.2641 | 2.5034 | 2.5397 | 2.5841 | 2.6358 | 1.5909 | 1.931 | 1.9592 | 1.9979 | 1.5909 | 1.2194 | 1.4053 | 1.4307 | 1.4645 | 1.5719
2022-05-29 11:00 | 2.172 | 2.4088 | 2.4473 | 2.4944 | 2.5493 | 1.5052 | 1.8328 | 1.8629 | 1.9038 | 1.5052 | 1.3913 | 1.5994 | 1.6264 | 1.6622 | 1.7815
2022-05-29 12:00 | 2.2482 | 2.4896 | 2.5276 | 2.574 | 2.6282 | 1.448 | 1.7646 | 1.7942 | 1.8346 | 1.448 | 1.9434 | 2.2122 | 2.2388 | 2.2741 | 2.4232
2022-05-29 13:00 | 2.2101 | 2.4437 | 2.4791 | 2.5224 | 2.5729 | 1.4099 | 1.7159 | 1.7435 | 1.7812 | 1.4099 | 1.5433 | 1.764 | 1.7888 | 1.8218 | 1.946
2022-05-29 14:00 | 1.8672 | 2.0698 | 2.1025 | 2.1424 | 2.189 | 1.3718 | 1.667 | 1.6924 | 1.7272 | 1.3718 | 1.105 | 1.2733 | 1.2961 | 1.3265 | 1.4236
2022-05-29 15:00 | 2.4387 | 2.6803 | 2.7111 | 2.7488 | 2.7928 | 1.829 | 2.2046 | 2.2286 | 2.2614 | 1.829 | 2.2101 | 2.4987 | 2.5203 | 2.549 | 2.7047
2022-05-29 16:00 | 3.0215 | 3.3056 | 3.336 | 3.3731 | 3.4165 | 2.5138 | 3.0129 | 3.0366 | 3.0689 | 2.5138 | 3.7152 | 4.1707 | 4.192 | 4.2202 | 4.4583
2022-05-29 17:00 | 3.4866 | 3.8088 | 3.841 | 3.8804 | 3.9263 | 3.1437 | 3.7595 | 3.7846 | 3.8189 | 3.1437 | 4.6298 | 5.1895 | 5.212 | 5.242 | 5.5323
2022-05-29 18:00 | 3.639 | 3.9799 | 4.0158 | 4.0598 | 4.1111 | 3.1246 | 3.7424 | 3.7704 | 3.8087 | 3.1246 | 5.068 | 5.6817 | 5.7068 | 5.7403 | 6.0589
2022-05-29 19:00 | 3.5819 | 3.9283 | 3.9692 | 4.0193 | 4.0777 | 3.1437 | 3.772 | 3.8039 | 3.8475 | 3.1437 | 5.5633 | 6.239 | 6.2677 | 6.3058 | 6.6572
2022-05-29 20:00 | 3.4485 | 3.7947 | 3.8405 | 3.8966 | 3.9621 | 3.0103 | 3.6214 | 3.6572 | 3.7061 | 3.0103 | 5.5252 | 6.2036 | 6.2357 | 6.2784 | 6.6332
2022-05-29 21:00 | 3.4104 | 3.7553 | 3.802 | 3.8592 | 3.9258 | 2.9341 | 3.5326 | 3.569 | 3.6187 | 2.9341 | 4.3249 | 4.8709 | 4.9036 | 4.947 | 5.2368
2022-05-29 22:00 | 3.1627 | 3.4833 | 3.5269 | 3.5804 | 3.6427 | 2.5721 | 3.1006 | 3.1347 | 3.1812 | 2.5721 | 3.9629 | 4.4644 | 4.4949 | 4.5356 | 4.802
2022-05-29 23:00 | 2.8769 | 3.1678 | 3.2071 | 3.2553 | 3.3114 | 2.2951 | 2.7673 | 2.798 | 2.8399 | 2.2951 | 3.5628 | 4.0138 | 4.0413 | 4.0779 | 4.3176
2022-05-30 | 2.5721 | 2.8309 | 2.8654 | 2.9076 | 2.9569 | 1.9356 | 2.3357 | 2.3626 | 2.3994 | 1.9356 | 2.9341 | 3.3084 | 3.3326 | 3.3647 | 3.5644
2022-05-30 01:00 | 2.3244 | 2.5552 | 2.5848 | 2.6211 | 2.6633 | 1.7338 | 2.0903 | 2.1134 | 2.145 | 1.7338 | 2.8769 | 3.2381 | 3.2588 | 3.2864 | 3.4775
2022-05-30 02:00 | 2.3244 | 2.5431 | 2.5666 | 2.5953 | 2.6287 | 1.6385 | 1.969 | 1.9873 | 2.0123 | 1.6385 | 2.9341 | 3.293 | 3.3095 | 3.3313 | 3.5187
2022-05-30 03:00 | 2.3054 | 2.5108 | 2.5282 | 2.5495 | 2.5744 | 1.6004 | 1.9154 | 1.929 | 1.9475 | 1.6004 | 2.4768 | 2.7765 | 2.7887 | 2.8049 | 2.9605
2022-05-30 04:00 | 2.2673 | 2.4598 | 2.4721 | 2.4871 | 2.5046 | 1.5623 | 1.8631 | 1.8726 | 1.8857 | 1.5623 | 2.4387 | 2.7271 | 2.7356 | 2.7471 | 2.8948
2022-05-30 05:00 | 2.425 | 2.6253 | 2.6355 | 2.648 | 2.6626 | 1.6576 | 1.9727 | 1.9807 | 1.9916 | 1.6576 | 2.7817 | 3.1053 | 3.1125 | 3.122 | 3.2863
2022-05-30 06:00 | 2.6102 | 2.8276 | 2.8396 | 2.8542 | 2.8712 | 1.8862 | 2.2452 | 2.2546 | 2.2673 | 1.8862 | 3.2008 | 3.5735 | 3.5819 | 3.593 | 3.7822
2022-05-30 07:00 | 2.8007 | 3.0414 | 3.058 | 3.0783 | 3.1019 | 2.0386 | 2.4319 | 2.4448 | 2.4625 | 2.0386 | 3.7724 | 4.2151 | 4.2267 | 4.2422 | 4.468
2022-05-30 08:00 | 2.8769 | 3.1366 | 3.16 | 3.1887 | 3.222 | 2.3054 | 2.7567 | 2.775 | 2.7999 | 2.3054 | 3.6581 | 4.0975 | 4.1139 | 4.1357 | 4.3628
2022-05-30 09:00 | 3.2961 | 3.6012 | 3.6319 | 3.6694 | 3.7132 | 2.553 | 3.0597 | 3.0836 | 3.1163 | 2.553 | 4.6869 | 5.2509 | 5.2724 | 5.301 | 5.5928
2022-05-30 10:00 | 3.5628 | 3.8987 | 3.935 | 3.9793 | 4.0311 | 2.7436 | 3.2927 | 3.321 | 3.3596 | 2.7436 | 4.4774 | 5.0258 | 5.0512 | 5.0849 | 5.3715
2022-05-30 11:00 | 3.5247 | 3.8621 | 3.9006 | 3.9477 | 4.0026 | 2.7245 | 3.2733 | 3.3034 | 3.3443 | 2.7245 | 4.363 | 4.9018 | 4.9288 | 4.9646 | 5.2473
2022-05-30 12:00 | 3.6771 | 4.0248 | 4.0627 | 4.1092 | 4.1633 | 2.8509 | 3.4219 | 3.4515 | 3.4919 | 2.8509 | 5.0108 | 5.6209 | 5.6475 | 5.6828 | 6.0005
2022-05-30 13:00 | 3.7724 | 4.1222 | 4.1576 | 4.2009 | 4.2514 | 3.0865 | 3.6966 | 3.7242 | 3.7619 | 3.0865 | 4.6298 | 5.194 | 5.2188 | 5.2517 | 5.5456
2022-05-30 14:00 | 3.8486 | 4.1986 | 4.2313 | 4.2712 | 4.3178 | 3.0865 | 3.6927 | 3.7181 | 3.7529 | 3.0865 | 5.3347 | 5.9735 | 5.9964 | 6.0267 | 6.3563
2022-05-30 15:00 | 3.7152 | 4.0517 | 4.0826 | 4.1203 | 4.1642 | 3.1056 | 3.7126 | 3.7366 | 3.7694 | 3.1056 | 5.1442 | 5.7592 | 5.7808 | 5.8095 | 6.1266
2022-05-30 16:00 | 4.0582 | 4.4193 | 4.4497 | 4.4869 | 4.5302 | 3.3438 | 3.9934 | 4.0171 | 4.0495 | 3.3438 | 5.7729 | 6.4573 | 6.4786 | 6.5068 | 6.858
2022-05-30 17:00 | 4.2297 | 4.6071 | 4.6393 | 4.6787 | 4.7246 | 3.6962 | 4.4123 | 4.4374 | 4.4716 | 3.6962 | 7.3352 | 8.1959 | 8.2185 | 8.2484 | 8.6875
2022-05-30 18:00 | 4.2678 | 4.6554 | 4.6913 | 4.7353 | 4.7866 | 3.7152 | 4.4401 | 4.4682 | 4.5064 | 3.7152 | 6.4017 | 7.1637 | 7.1889 | 7.2223 | 7.6143
2022-05-30 19:00 | 4.2868 | 4.6856 | 4.7265 | 4.7766 | 4.835 | 3.6771 | 4.4022 | 4.4341 | 4.4777 | 3.6771 | 5.8872 | 6.599 | 6.6276 | 6.6657 | 7.0349
2022-05-30 20:00 | 4.0391 | 4.4292 | 4.475 | 4.5312 | 4.5966 | 3.5438 | 4.2517 | 4.2874 | 4.3363 | 3.5438 | 5.7158 | 6.4153 | 6.4474 | 6.4901 | 6.8554
2022-05-30 21:00 | 3.8486 | 4.2261 | 4.2728 | 4.33 | 4.3966 | 3.1476 | 3.7848 | 3.8212 | 3.8709 | 3.1476 | 6.0397 | 6.7764 | 6.8091 | 6.8525 | 7.2365
2022-05-30 22:00 | 3.3335 | 3.6668 | 3.7104 | 3.7638 | 3.8261 | 2.7313 | 3.2886 | 3.3227 | 3.3692 | 2.7313 | 4.0201 | 4.5279 | 4.5585 | 4.5991 | 4.8687
2022-05-30 23:00 | 2.915 | 3.2087 | 3.2481 | 3.2962 | 3.3524 | 2.2954 | 2.7676 | 2.7983 | 2.8402 | 2.2954 | 3.3342 | 3.7597 | 3.7873 | 3.8239 | 4.051
2022-05-31 | 2.6293 | 2.8923 | 2.9268 | 2.969 | 3.0183 | 1.8672 | 2.2548 | 2.2818 | 2.3185 | 1.8672 | 2.7665 | 3.1222 | 3.1464 | 3.1785 | 3.369
2022-05-31 01:00 | 2.4006 | 2.6371 | 2.6667 | 2.7029 | 2.7452 | 1.6766 | 2.0228 | 2.0459 | 2.0774 | 1.6766 | 2.4959 | 2.8146 | 2.8354 | 2.863 | 3.0331
2022-05-31 02:00 | 2.2863 | 2.5022 | 2.5256 | 2.5543 | 2.5878 | 1.5433 | 1.8565 | 1.8748 | 1.8997 | 1.5433 | 2.4578 | 2.7637 | 2.7802 | 2.802 | 2.9632
2022-05-31 03:00 | 2.2291 | 2.4289 | 2.4464 | 2.4677 | 2.4925 | 1.5386 | 1.8424 | 1.856 | 1.8745 | 1.5386 | 2.6674 | 2.9883 | 3.0005 | 3.0167 | 3.1827
2022-05-31 04:00 | 2.3625 | 2.5622 | 2.5744 | 2.5894 | 2.6069 | 1.669 | 1.9891 | 1.9987 | 2.0118 | 1.669 | 2.7436 | 3.0658 | 3.0744 | 3.0858 | 3.2503
2022-05-31 05:00 | 2.6864 | 2.9062 | 2.9164 | 2.9289 | 2.9435 | 1.9692 | 2.3408 | 2.3488 | 2.3597 | 1.9692 | 3.3533 | 3.7405 | 3.7477 | 3.7572 | 3.9529
2022-05-31 06:00 | 3.4395 | 3.7185 | 3.7305 | 3.7451 | 3.7621 | 2.8304 | 3.3607 | 3.37 | 3.3827 | 2.8304 | 4.4392 | 4.9497 | 4.9581 | 4.9692 | 5.2265
2022-05-31 07:00 | 4.1344 | 4.4742 | 4.4908 | 4.5111 | 4.5348 | 3.1818 | 3.7824 | 3.7953 | 3.813 | 3.1818 | 5.9825 | 6.6711 | 6.6827 | 6.6981 | 7.0455
2022-05-31 08:00 | 4.2297 | 4.5899 | 4.6133 | 4.642 | 4.6753 | 3.1818 | 3.7921 | 3.8103 | 3.8352 | 3.1818 | 4.8203 | 5.389 | 5.4054 | 5.4272 | 5.7182
2022-05-31 09:00 | 4.2106 | 4.5837 | 4.6144 | 4.6519 | 4.6957 | 2.896 | 3.4648 | 3.4887 | 3.5214 | 2.896 | 4.8965 | 5.4838 | 5.5053 | 5.5339 | 5.8372
2022-05-31 10:00 | 4.001 | 4.3695 | 4.4057 | 4.4501 | 4.5019 | 2.7436 | 3.2927 | 3.321 | 3.3596 | 2.7436 | 4.0772 | 4.5812 | 4.6066 | 4.6403 | 4.9048
2022-05-31 11:00 | 3.4866 | 3.8212 | 3.8596 | 3.9067 | 3.9617 | 2.1339 | 2.5756 | 2.6056 | 2.6466 | 2.1339 | 2.6293 | 2.9751 | 3.0021 | 3.0379 | 3.2253
2022-05-31 12:00 | 3.7724 | 4.1271 | 4.1651 | 4.2115 | 4.2657 | 2.4006 | 2.8899 | 2.9195 | 2.96 | 2.4006 | 2.8007 | 3.1649 | 3.1915 | 3.2269 | 3.4231
2022-05-31 13:00 | 3.7152 | 4.0607 | 4.0961 | 4.1395 | 4.19 | 2.5149 | 3.0214 | 3.049 | 3.0867 | 2.5149 | 3.3533 | 3.7754 | 3.8002 | 3.8332 | 4.0569
2022-05-31 14:00 | 3.8486 | 4.1986 | 4.2313 | 4.2712 | 4.3178 | 2.553 | 3.0625 | 3.0879 | 3.1227 | 2.553 | 4.2106 | 4.7243 | 4.7472 | 4.7776 | 5.0454
2022-05-31 15:00 | 4.2487 | 4.6249 | 4.6557 | 4.6934 | 4.7373 | 3.3028 | 3.9456 | 3.9696 | 4.0024 | 3.3028 | 5.1632 | 5.7804 | 5.802 | 5.8307 | 6.1488
2022-05-31 16:00 | 4.7631 | 5.1767 | 5.207 | 5.2442 | 5.2875 | 3.6962 | 4.4097 | 4.4334 | 4.4657 | 3.6962 | 6.0968 | 6.8172 | 6.8385 | 6.8668 | 7.2357
2022-05-31 17:00 | 4.9727 | 5.4054 | 5.4376 | 5.4769 | 5.5229 | 4.1278 | 4.9222 | 4.9473 | 4.9815 | 4.1278 | 6.9542 | 7.7725 | 7.795 | 7.825 | 8.2431
2022-05-31 18:00 | 6.3636 | 6.907 | 6.9429 | 6.9869 | 7.0382 | 4.4202 | 5.2729 | 5.3009 | 5.3392 | 4.4202 | 7.0304 | 7.8624 | 7.8876 | 7.921 | 8.3475
2022-05-31 19:00 | 6.2683 | 6.8144 | 6.8553 | 6.9054 | 6.9638 | 4.363 | 5.2125 | 5.2444 | 5.288 | 4.363 | 6.3254 | 7.0859 | 7.1146 | 7.1527 | 7.546
2022-05-31 20:00 | 5.811 | 6.3328 | 6.3787 | 6.4348 | 6.5002 | 4.0963 | 4.9044 | 4.9402 | 4.989 | 4.0963 | 5.3633 | 6.0235 | 6.0557 | 6.0984 | 6.4443
2022-05-31 21:00 | 5.4109 | 5.9046 | 5.9513 | 6.0084 | 6.0751 | 3.7724 | 4.5229 | 4.5594 | 4.6091 | 3.7724 | 5.1061 | 5.7389 | 5.7716 | 5.8151 | 6.1478
2022-05-31 22:00 | 4.5155 | 4.9366 | 4.9802 | 5.0337 | 5.096 | 3.277 | 3.9334 | 3.9675 | 4.0139 | 3.277 | 3.9118 | 4.4075 | 4.4381 | 4.4787 | 4.7424
2022-05-31 23:00 | 4.0163 | 4.3919 | 4.4312 | 4.4794 | 4.5355 | 2.5489 | 3.0671 | 3.0978 | 3.1397 | 2.5489 | 3.639 | 4.0985 | 4.126 | 4.1626 | 4.4065
2022-06-01 | 3.4206 | 3.7424 | 3.7769 | 3.8192 | 3.8684 | 2.0827 | 2.5095 | 2.5364 | 2.5732 | 2.0827 | 2.8579 | 3.2237 | 3.2479 | 3.28 | 3.4755
2022-06-01 01:00 | 3.1056 | 3.3944 | 3.424 | 3.4603 | 3.5026 | 1.8672 | 2.2479 | 2.271 | 2.3025 | 1.8672 | 2.3244 | 2.6241 | 2.6448 | 2.6724 | 2.8332
2022-06-01 02:00 | 3.0294 | 3.3005 | 3.3239 | 3.3526 | 3.3861 | 1.7719 | 2.1266 | 2.1449 | 2.1698 | 1.7719 | 2.6293 | 2.9543 | 2.9707 | 2.9925 | 3.1632
2022-06-01 03:00 | 3.0103 | 3.2682 | 3.2856 | 3.3069 | 3.3317 | 1.8481 | 2.208 | 2.2216 | 2.2401 | 1.8481 | 2.4578 | 2.7554 | 2.7676 | 2.7838 | 2.9383
2022-06-01 04:00 | 3.1607 | 3.4197 | 3.4319 | 3.4469 | 3.4644 | 1.9624 | 2.3357 | 2.3453 | 2.3584 | 1.9624 | 2.4387 | 2.7271 | 2.7356 | 2.7471 | 2.8948
2022-06-01 05:00 | 3.7675 | 4.0676 | 4.0778 | 4.0903 | 4.1049 | 2.3501 | 2.7908 | 2.7988 | 2.8097 | 2.3501 | 3.2199 | 3.5923 | 3.5995 | 3.609 | 3.7974
2022-06-01 06:00 | 4.706 | 5.0792 | 5.0911 | 5.1057 | 5.1228 | 3.2945 | 3.9089 | 3.9182 | 3.931 | 3.2945 | 4.8965 | 5.4578 | 5.4662 | 5.4773 | 5.7598
2022-06-01 07:00 | 5.5931 | 6.0414 | 6.058 | 6.0783 | 6.1019 | 3.6771 | 4.3676 | 4.3805 | 4.3982 | 3.6771 | 4.9727 | 5.549 | 5.5606 | 5.576 | 5.8678
2022-06-01 08:00 | 5.6015 | 6.0637 | 6.0871 | 6.1157 | 6.1491 | 3.6581 | 4.3548 | 4.373 | 4.3979 | 3.6581 | 5.2395 | 5.8548 | 5.8712 | 5.893 | 6.2071
2022-06-01 09:00 | 5.0489 | 5.4843 | 5.515 | 5.5525 | 5.5963 | 3.1056 | 3.7124 | 3.7363 | 3.769 | 3.1056 | 3.5438 | 3.9806 | 4.0021 | 4.0306 | 4.2596
2022-06-01 10:00 | 3.9058 | 4.2671 | 4.3034 | 4.3478 | 4.3995 | 2.3244 | 2.7975 | 2.8258 | 2.8644 | 2.3244 | 1.9434 | 2.2099 | 2.2353 | 2.269 | 2.4162
2022-06-01 11:00 | 4.4583 | 4.8651 | 4.9036 | 4.9507 | 5.0056 | 2.4578 | 2.9582 | 2.9882 | 3.0292 | 2.4578 | 2.8579 | 3.2292 | 3.2562 | 3.292 | 3.4919
2022-06-01 12:00 | 4.4583 | 4.864 | 4.902 | 4.9484 | 5.0026 | 2.3054 | 2.7774 | 2.807 | 2.8474 | 2.3054 | 2.2291 | 2.5298 | 2.5564 | 2.5917 | 2.7565
2022-06-01 13:00 | 4.2678 | 4.6543 | 4.6897 | 4.7331 | 4.7836 | 2.191 | 2.6387 | 2.6663 | 2.704 | 2.191 | 2.0386 | 2.3145 | 2.3393 | 2.3723 | 2.5238
2022-06-01 14:00 | 3.6771 | 4.0144 | 4.047 | 4.087 | 4.1336 | 2.0183 | 2.4307 | 2.4562 | 2.491 | 2.0183 | 1.7719 | 2.0143 | 2.0371 | 2.0675 | 2.2013
2022-06-01 15:00 | 4.0963 | 4.4611 | 4.4919 | 4.5296 | 4.5736 | 2.5737 | 3.0843 | 3.1083 | 3.1411 | 2.5737 | 2.7436 | 3.0915 | 3.1131 | 3.1418 | 3.3269
2022-06-01 16:00 | 5.1632 | 5.6065 | 5.6369 | 5.6741 | 5.7174 | 3.3914 | 4.0496 | 4.0733 | 4.1056 | 3.3914 | 4.5536 | 5.1023 | 5.1236 | 5.1518 | 5.436
2022-06-01 17:00 | 5.9382 | 6.4427 | 6.4748 | 6.5142 | 6.5601 | 4.1496 | 4.9479 | 4.973 | 5.0072 | 4.1496 | 5.6586 | 6.3328 | 6.3553 | 6.3853 | 6.7322
2022-06-01 18:00 | 6.2111 | 6.7432 | 6.7792 | 6.8231 | 6.8744 | 4.3249 | 5.1604 | 5.1884 | 5.2267 | 4.3249 | 6.0016 | 6.7191 | 6.7443 | 6.7777 | 7.1477
2022-06-01 19:00 | 6.0778 | 6.6097 | 6.6506 | 6.7007 | 6.7591 | 4.3059 | 5.145 | 5.1769 | 5.2204 | 4.3059 | 6.2873 | 7.0436 | 7.0723 | 7.1103 | 7.5015
2022-06-01 20:00 | 5.792 | 6.3123 | 6.3582 | 6.4143 | 6.4798 | 4.2678 | 5.107 | 5.1427 | 5.1916 | 4.2678 | 5.6205 | 6.3094 | 6.3415 | 6.3842 | 6.7443
2022-06-01 21:00 | 5.2395 | 5.7204 | 5.7671 | 5.8242 | 5.8908 | 3.9423 | 4.7236 | 4.76 | 4.8097 | 3.9423 | 4.9537 | 5.5695 | 5.6023 | 5.6457 | 5.97
2022-06-01 22:00 | 4.6107 | 5.0389 | 5.0826 | 5.136 | 5.1983 | 3.3151 | 3.9784 | 4.0125 | 4.059 | 3.3151 | 4.706 | 5.2901 | 5.3207 | 5.3613 | 5.6686
2022-06-01 23:00 | 3.982 | 4.355 | 4.3943 | 4.4425 | 4.4986 | 2.5251 | 3.039 | 3.0697 | 3.1116 | 2.5251 | 3.3723 | 3.802 | 3.8296 | 3.8662 | 4.0954
2022-06-02 | 3.3914 | 3.711 | 3.7455 | 3.7878 | 3.837 | 2.1039 | 2.5346 | 2.5615 | 2.5982 | 2.1039 | 2.6102 | 2.9485 | 2.9726 | 3.0048 | 3.1867
2022-06-02 01:00 | 3.2008 | 3.4968 | 3.5264 | 3.5626 | 3.6049 | 1.889 | 2.2737 | 2.2968 | 2.3284 | 1.889 | 2.2868 | 2.5823 | 2.6031 | 2.6307 | 2.7893
2022-06-02 02:00 | 3.1056 | 3.3823 | 3.4058 | 3.4345 | 3.468 | 1.845 | 2.213 | 2.2313 | 2.2563 | 1.845 | 2.2863 | 2.5732 | 2.5896 | 2.6114 | 2.7632
2022-06-02 03:00 | 3.1056 | 3.3705 | 3.3879 | 3.4092 | 3.4341 | 1.8481 | 2.208 | 2.2216 | 2.2401 | 1.8481 | 2.6864 | 3.0094 | 3.0216 | 3.0378 | 3.2049
2022-06-02 04:00 | 3.2961 | 3.5651 | 3.5774 | 3.5924 | 3.6099 | 1.9624 | 2.3357 | 2.3453 | 2.3584 | 1.9624 | 2.6102 | 2.9176 | 2.9262 | 2.9376 | 3.0947
2022-06-02 05:00 | 3.8361 | 4.1413 | 4.1516 | 4.1641 | 4.1787 | 2.4776 | 2.9414 | 2.9494 | 2.9603 | 2.4776 | 3.5438 | 3.9522 | 3.9594 | 3.9689 | 4.1751
2022-06-02 06:00 | 4.8443 | 5.2278 | 5.2397 | 5.2543 | 5.2714 | 3.2384 | 3.8427 | 3.852 | 3.8647 | 3.2384 | 4.706 | 5.2461 | 5.2545 | 5.2656 | 5.5376
2022-06-02 07:00 | 5.6967 | 6.1527 | 6.1693 | 6.1896 | 6.2132 | 3.7343 | 4.4351 | 4.448 | 4.4657 | 3.7343 | 5.43 | 6.0571 | 6.0687 | 6.0841 | 6.4011
2022-06-02 08:00 | 5.5252 | 5.9818 | 6.0052 | 6.0338 | 6.0672 | 3.5628 | 4.2422 | 4.2605 | 4.2854 | 3.5628 | 5.1061 | 5.7066 | 5.723 | 5.7448 | 6.0515
2022-06-02 09:00 | 5.1632 | 5.6071 | 5.6378 | 5.6754 | 5.7191 | 3.0484 | 3.6449 | 3.6688 | 3.7015 | 3.0484 | 3.9058 | 4.3829 | 4.4043 | 4.4329 | 4.6818
2022-06-02 10:00 | 4.9537 | 5.3929 | 5.4292 | 5.4736 | 5.5253 | 2.8354 | 3.4012 | 3.4295 | 3.4681 | 2.8354 | 3.5247 | 3.9672 | 3.9926 | 4.0263 | 4.2605
2022-06-02 11:00 | 4.4011 | 4.8037 | 4.8421 | 4.8893 | 4.9442 | 2.553 | 3.0708 | 3.1008 | 3.1418 | 2.553 | 2.915 | 3.2927 | 3.3197 | 3.3555 | 3.5586
2022-06-02 12:00 | 3.9629 | 4.3318 | 4.3698 | 4.4162 | 4.4704 | 2.2101 | 2.6649 | 2.6945 | 2.7349 | 2.2101 | 1.7719 | 2.0216 | 2.0482 | 2.0836 | 2.2232
2022-06-02 13:00 | 3.4676 | 3.7946 | 3.83 | 3.8734 | 3.9239 | 1.7719 | 2.1436 | 2.1712 | 2.2089 | 1.7719 | 1.0288 | 1.1924 | 1.2172 | 1.2502 | 1.3461
2022-06-02 14:00 | 3.5247 | 3.8506 | 3.8833 | 3.9232 | 3.9698 | 2.0426 | 2.4594 | 2.4849 | 2.5196 | 2.0426 | 1.7528 | 1.9931 | 2.016 | 2.0464 | 2.1791
2022-06-02 15:00 | 4.1995 | 4.572 | 4.6028 | 4.6405 | 4.6845 | 2.6293 | 3.1499 | 3.1739 | 3.2067 | 2.6293 | 2.8007 | 3.155 | 3.1766 | 3.2053 | 3.3936
2022-06-02 16:00 | 5.1101 | 5.5494 | 5.5798 | 5.6169 | 5.6603 | 3.3342 | 3.982 | 4.0057 | 4.0381 | 3.3342 | 4.2106 | 4.7212 | 4.7425 | 4.7707 | 5.036
2022-06-02 17:00 | 5.7729 | 6.2651 | 6.2973 | 6.3366 | 6.3826 | 3.7343 | 4.4573 | 4.4824 | 4.5166 | 3.7343 | 5.2013 | 5.8246 | 5.8472 | 5.8771 | 6.1989
2022-06-02 18:00 | 5.8682 | 6.3748 | 6.4107 | 6.4547 | 6.506 | 3.982 | 4.7552 | 4.7833 | 4.8215 | 3.982 | 5.6205 | 6.2957 | 6.3208 | 6.3543 | 6.7033
2022-06-02 19:00 | 5.811 | 6.3231 | 6.364 | 6.4141 | 6.4725 | 4.0963 | 4.8974 | 4.9293 | 4.9729 | 4.0963 | 5.792 | 6.4931 | 6.5218 | 6.5599 | 6.9238
2022-06-02 20:00 | 5.4871 | 5.9848 | 6.0307 | 6.0868 | 6.1523 | 4.0277 | 4.8233 | 4.8591 | 4.9079 | 4.0277 | 5.3538 | 6.013 | 6.0451 | 6.0878 | 6.4332
2022-06-02 21:00 | 5.2585 | 5.7408 | 5.7875 | 5.8447 | 5.9113 | 3.62 | 4.3429 | 4.3793 | 4.429 | 3.62 | 5.0489 | 5.6754 | 5.7081 | 5.7516 | 6.0811
2022-06-02 22:00 | 4.6794 | 5.1127 | 5.1563 | 5.2098 | 5.2721 | 3.1748 | 3.8126 | 3.8466 | 3.8931 | 3.1748 | 3.8867 | 4.3797 | 4.4103 | 4.4509 | 4.7131
2022-06-02 23:00 | 4.0201 | 4.396 | 4.4353 | 4.4834 | 4.5396 | 2.6173 | 3.1479 | 3.1786 | 3.2205 | 2.6173 | 3.6009 | 4.0561 | 4.0837 | 4.1203 | 4.362
2022-06-03 | 3.5247 | 3.8543 | 3.8888 | 3.9311 | 3.9803 | 2.1312 | 2.5668 | 2.5937 | 2.6305 | 2.1312 | 2.915 | 3.2872 | 3.3114 | 3.3435 | 3.5422
2022-06-03 01:00 | 3.3914 | 3.7015 | 3.7311 | 3.7673 | 3.8096 | 1.9815 | 2.3829 | 2.406 | 2.4376 | 1.9815 | 2.7436 | 3.0899 | 3.1106 | 3.1382 | 3.322
2022-06-03 02:00 | 3.2008 | 3.4847 | 3.5081 | 3.5368 | 3.5703 | 1.8672 | 2.2391 | 2.2574 | 2.2824 | 1.8672 | 2.4959 | 2.8061 | 2.8225 | 2.8443 | 3.0077
2022-06-03 03:00 | 3.2961 | 3.5752 | 3.5926 | 3.6139 | 3.6388 | 1.8672 | 2.2305 | 2.2441 | 2.2626 | 1.8672 | 2.4578 | 2.7554 | 2.7676 | 2.7838 | 2.9383
2022-06-03 04:00 | 3.3533 | 3.6265 | 3.6388 | 3.6538 | 3.6713 | 1.9542 | 2.326 | 2.3356 | 2.3486 | 1.9542 | 2.8198 | 3.1505 | 3.1591 | 3.1705 | 3.3392
2022-06-03 05:00 | 3.7534 | 4.0524 | 4.0627 | 4.0752 | 4.0898 | 2.4059 | 2.8568 | 2.8648 | 2.8757 | 2.4059 | 3.3533 | 3.7405 | 3.7477 | 3.7572 | 3.9529
2022-06-03 06:00 | 4.7822 | 5.1611 | 5.173 | 5.1876 | 5.2047 | 3.1389 | 3.7252 | 3.7345 | 3.7472 | 3.1389 | 4.2868 | 4.7803 | 4.7887 | 4.7998 | 5.0487
2022-06-03 07:00 | 5.7158 | 6.1731 | 6.1897 | 6.21 | 6.2337 | 3.7724 | 4.4801 | 4.4931 | 4.5107 | 3.7724 | 5.3728 | 5.9936 | 6.0052 | 6.0206 | 6.3344
2022-06-03 08:00 | 5.6015 | 6.0637 | 6.0871 | 6.1157 | 6.1491 | 3.639 | 4.3323 | 4.3505 | 4.3754 | 3.639 | 5.7539 | 6.4265 | 6.4429 | 6.4646 | 6.807
2022-06-03 09:00 | 5.4681 | 5.9346 | 5.9653 | 6.0029 | 6.0466 | 3.2961 | 3.9375 | 3.9614 | 3.9941 | 3.2961 | 4.706 | 5.2721 | 5.2936 | 5.3221 | 5.615
2022-06-03 10:00 | 4.9727 | 5.4134 | 5.4497 | 5.494 | 5.5458 | 2.9722 | 3.5628 | 3.5911 | 3.6297 | 2.9722 | 3.5247 | 3.9672 | 3.9926 | 4.0263 | 4.2605
2022-06-03 11:00 | 4.4875 | 4.8965 | 4.935 | 4.9821 | 5.037 | 2.6102 | 3.1383 | 3.1683 | 3.2093 | 2.6102 | 3.1246 | 3.5256 | 3.5526 | 3.5884 | 3.803
2022-06-03 12:00 | 4.2868 | 4.6798 | 4.7177 | 4.7642 | 4.8183 | 2.2482 | 2.7099 | 2.7395 | 2.7799 | 2.2482 | 2.8769 | 3.2496 | 3.2762 | 3.3115 | 3.5119
2022-06-03 13:00 | 4.4011 | 4.7976 | 4.833 | 4.8764 | 4.9269 | 2.5755 | 3.0929 | 3.1206 | 3.1583 | 2.5755 | 2.6483 | 2.992 | 3.0168 | 3.0498 | 3.2348
2022-06-03 14:00 | 4.4392 | 4.8332 | 4.8658 | 4.9057 | 4.9523 | 2.6102 | 3.13 | 3.1554 | 3.1902 | 2.6102 | 3.4295 | 3.8563 | 3.8791 | 3.9095 | 4.1344
2022-06-03 15:00 | 4.6107 | 5.0138 | 5.0446 | 5.0823 | 5.1263 | 2.944 | 3.5218 | 3.5458 | 3.5786 | 2.944 | 3.8486 | 4.3195 | 4.3411 | 4.3698 | 4.6156
2022-06-03 16:00 | 5.087 | 5.5247 | 5.555 | 5.5922 | 5.6355 | 3.4104 | 4.0721 | 4.0958 | 4.1281 | 3.4104 | 4.4964 | 5.0388 | 5.06 | 5.0883 | 5.3693
2022-06-03 17:00 | 5.3347 | 5.7943 | 5.8265 | 5.8659 | 5.9118 | 3.6581 | 4.3673 | 4.3924 | 4.4266 | 3.6581 | 5.1061 | 5.7188 | 5.7413 | 5.7713 | 6.0878
2022-06-03 18:00 | 5.43 | 5.904 | 5.9399 | 5.9839 | 6.0352 | 3.8296 | 4.5752 | 4.6032 | 4.6415 | 3.8296 | 5.2585 | 5.8934 | 5.9186 | 5.952 | 6.2811
2022-06-03 19:00 | 5.3919 | 5.8728 | 5.9137 | 5.9638 | 6.0222 | 3.7094 | 4.4403 | 4.4722 | 4.5158 | 3.7094 | 5.8301 | 6.5355 | 6.5641 | 6.6022 | 6.9683
2022-06-03 20:00 | 5.0108 | 5.4731 | 5.519 | 5.5751 | 5.6405 | 3.6581 | 4.3867 | 4.4225 | 4.4713 | 3.6581 | 5.2013 | 5.8436 | 5.8758 | 5.9184 | 6.2554
2022-06-03 21:00 | 4.6298 | 5.0654 | 5.112 | 5.1692 | 5.2358 | 3.4866 | 4.1853 | 4.2217 | 4.2715 | 3.4866 | 5.1442 | 5.7813 | 5.814 | 5.8574 | 6.1922
2022-06-03 22:00 | 4.3059 | 4.7114 | 4.7551 | 4.8085 | 4.8708 | 3.0738 | 3.6934 | 3.7274 | 3.7739 | 3.0738 | 3.7915 | 4.2738 | 4.3044 | 4.345 | 4.602
2022-06-03 23:00 | 3.8296 | 4.1913 | 4.2306 | 4.2787 | 4.3349 | 2.6191 | 3.15 | 3.1807 | 3.2226 | 2.6191 | 3.2199 | 3.6327 | 3.6602 | 3.6968 | 3.9176
2022-06-04 | 3.4374 | 3.7605 | 3.795 | 3.8373 | 3.8865 | 2.2856 | 2.7492 | 2.7761 | 2.8129 | 2.2856 | 2.6483 | 2.9908 | 3.015 | 3.0471 | 3.2311
2022-06-04 01:00 | 3.0675 | 3.3535 | 3.3831 | 3.4193 | 3.4616 | 1.8597 | 2.2391 | 2.2622 | 2.2938 | 1.8597 | 2.4387 | 2.7511 | 2.7719 | 2.7994 | 2.9665
2022-06-04 02:00 | 3.0103 | 3.28 | 3.3034 | 3.3321 | 3.3656 | 1.724 | 2.0699 | 2.0882 | 2.1132 | 1.724 | 2.4006 | 2.7002 | 2.7167 | 2.7385 | 2.8966
2022-06-04 03:00 | 2.896 | 3.1454 | 3.1628 | 3.1841 | 3.2089 | 1.6957 | 2.028 | 2.0415 | 2.0601 | 1.6957 | 2.191 | 2.459 | 2.4711 | 2.4874 | 2.6272
2022-06-04 04:00 | 2.896 | 3.1353 | 3.1475 | 3.1626 | 3.18 | 1.7147 | 2.0431 | 2.0527 | 2.0658 | 1.7147 | 2.1339 | 2.3883 | 2.3969 | 2.4083 | 2.5393
2022-06-04 05:00 | 3.1627 | 3.4179 | 3.4281 | 3.4406 | 3.4552 | 1.9675 | 2.3389 | 2.3469 | 2.3578 | 1.9675 | 2.4578 | 2.7454 | 2.7526 | 2.7621 | 2.9086
2022-06-04 06:00 | 3.4866 | 3.7692 | 3.7811 | 3.7957 | 3.8128 | 2.191 | 2.6054 | 2.6147 | 2.6274 | 2.191 | 3.2199 | 3.5947 | 3.603 | 3.6141 | 3.8044
2022-06-04 07:00 | 3.9439 | 4.2695 | 4.2861 | 4.3064 | 4.3301 | 2.5091 | 2.9877 | 3.0006 | 3.0183 | 2.5091 | 3.4676 | 3.8763 | 3.888 | 3.9034 | 4.1125
2022-06-04 08:00 | 4.1344 | 4.4876 | 4.511 | 4.5396 | 4.573 | 2.6864 | 3.2069 | 3.2251 | 3.25 | 2.6864 | 3.8677 | 4.3304 | 4.3468 | 4.3686 | 4.6073
2022-06-04 09:00 | 3.9058 | 4.2562 | 4.2869 | 4.3244 | 4.3682 | 2.6445 | 3.1678 | 3.1917 | 3.2243 | 2.6445 | 3.3533 | 3.7689 | 3.7904 | 3.8189 | 4.0374
2022-06-04 10:00 | 4.1725 | 4.5537 | 4.59 | 4.6343 | 4.6861 | 2.553 | 3.0676 | 3.0959 | 3.1345 | 2.553 | 3.1246 | 3.5225 | 3.548 | 3.5817 | 3.7939
2022-06-04 11:00 | 4.3821 | 4.7832 | 4.8217 | 4.8688 | 4.9237 | 2.7436 | 3.2958 | 3.3259 | 3.3669 | 2.7436 | 3.5438 | 3.9914 | 4.0184 | 4.0542 | 4.2919
2022-06-04 12:00 | 4.4202 | 4.8231 | 4.861 | 4.9075 | 4.9616 | 2.6102 | 3.1375 | 3.1671 | 3.2075 | 2.6102 | 3.5247 | 3.9695 | 3.9961 | 4.0314 | 4.2674
2022-06-04 13:00 | 4.6298 | 5.0433 | 5.0787 | 5.122 | 5.1725 | 2.915 | 3.494 | 3.5216 | 3.5593 | 2.915 | 3.62 | 4.0718 | 4.0966 | 4.1296 | 4.368
2022-06-04 14:00 | 4.4392 | 4.8332 | 4.8658 | 4.9057 | 4.9523 | 2.9722 | 3.5576 | 3.5831 | 3.6178 | 2.9722 | 3.982 | 4.4703 | 4.4931 | 4.5235 | 4.7787
2022-06-04 15:00 | 4.5917 | 4.9933 | 5.0241 | 5.0618 | 5.1058 | 3.0103 | 3.6 | 3.6241 | 3.6569 | 3.0103 | 4.1535 | 4.6583 | 4.6799 | 4.7085 | 4.9712
2022-06-04 16:00 | 5.0108 | 5.4428 | 5.4731 | 5.5103 | 5.5536 | 3.3533 | 4.0046 | 4.0282 | 4.0606 | 3.3533 | 5.068 | 5.6739 | 5.6952 | 5.7235 | 6.0359
2022-06-04 17:00 | 5.2204 | 5.6715 | 5.7037 | 5.743 | 5.789 | 3.6009 | 4.2997 | 4.3248 | 4.3591 | 3.6009 | 4.8584 | 5.4435 | 5.4661 | 5.496 | 5.7989
2022-06-04 18:00 | 5.1442 | 5.597 | 5.6329 | 5.6769 | 5.7282 | 3.6009 | 4.3051 | 4.3331 | 4.3714 | 3.6009 | 7.1257 | 7.9683 | 7.9934 | 8.0269 | 8.4586
2022-06-04 19:00 | 4.8584 | 5.2997 | 5.3406 | 5.3907 | 5.4491 | 3.4676 | 4.1546 | 4.1865 | 4.2301 | 3.4676 | 5.1823 | 5.8156 | 5.8443 | 5.8824 | 6.2128
2022-06-04 20:00 | 4.6869 | 5.1251 | 5.171 | 5.2271 | 5.2926 | 3.3342 | 4.0041 | 4.0398 | 4.0887 | 3.3342 | 5.3538 | 6.013 | 6.0451 | 6.0878 | 6.4332
2022-06-04 21:00 | 4.296 | 4.7068 | 4.7535 | 4.8106 | 4.8773 | 3.1056 | 3.7352 | 3.7716 | 3.8213 | 3.1056 | 4.6488 | 5.2308 | 5.2635 | 5.307 | 5.6145
2022-06-04 22:00 | 4.0201 | 4.4044 | 4.448 | 4.5015 | 4.5638 | 3.0103 | 3.6183 | 3.6523 | 3.6988 | 3.0103 | 4.1916 | 4.7184 | 4.749 | 4.7896 | 5.0687
2022-06-04 23:00 | 3.5819 | 3.9252 | 3.9645 | 4.0126 | 4.0688 | 2.5322 | 3.0474 | 3.0781 | 3.1199 | 2.5322 | 3.639 | 4.0985 | 4.126 | 4.1626 | 4.4065
2022-06-05 | 3.3342 | 3.6496 | 3.6841 | 3.7264 | 3.7756 | 2.1764 | 2.6202 | 2.6471 | 2.6838 | 2.1764 | 3.0294 | 3.4142 | 3.4384 | 3.4705 | 3.6755
2022-06-05 01:00 | 2.8007 | 3.0669 | 3.0965 | 3.1328 | 3.1751 | 1.829 | 2.2029 | 2.226 | 2.2575 | 1.829 | 2.4959 | 2.8146 | 2.8354 | 2.863 | 3.0331
2022-06-05 02:00 | 2.6864 | 2.932 | 2.9555 | 2.9842 | 3.0176 | 1.6576 | 1.9915 | 2.0098 | 2.0348 | 1.6576 | 2.6483 | 2.9755 | 2.9919 | 3.0137 | 3.1854
2022-06-05 03:00 | 2.5149 | 2.736 | 2.7534 | 2.7747 | 2.7995 | 1.6576 | 1.9829 | 1.9965 | 2.0151 | 1.6576 | 2.2863 | 2.5648 | 2.577 | 2.5932 | 2.7383
2022-06-05 04:00 | 2.5721 | 2.7873 | 2.7996 | 2.8146 | 2.8321 | 1.6258 | 1.938 | 1.9476 | 1.9606 | 1.6258 | 2.2673 | 2.5365 | 2.5451 | 2.5565 | 2.6948
2022-06-05 05:00 | 2.8198 | 3.0494 | 3.0597 | 3.0722 | 3.0868 | 1.8176 | 2.1618 | 2.1698 | 2.1807 | 1.8176 | 2.4578 | 2.7454 | 2.7526 | 2.7621 | 2.9086
2022-06-05 06:00 | 2.9913 | 3.237 | 3.2489 | 3.2635 | 3.2806 | 2.0386 | 2.4253 | 2.4346 | 2.4473 | 2.0386 | 2.896 | 3.2347 | 3.2431 | 3.2542 | 3.4267
2022-06-05 07:00 | 3.3914 | 3.6759 | 3.6925 | 3.7128 | 3.7365 | 2.3654 | 2.818 | 2.8309 | 2.8485 | 2.3654 | 4.001 | 4.4692 | 4.4808 | 4.4962 | 4.7346
2022-06-05 08:00 | 3.7534 | 4.0782 | 4.1016 | 4.1302 | 4.1636 | 2.6674 | 3.1844 | 3.2026 | 3.2275 | 2.6674 | 3.8677 | 4.3304 | 4.3468 | 4.3686 | 4.6073
2022-06-05 09:00 | 3.9058 | 4.2562 | 4.2869 | 4.3244 | 4.3682 | 2.7626 | 3.3073 | 3.3312 | 3.3638 | 2.7626 | 4.2487 | 4.764 | 4.7854 | 4.814 | 5.0817
2022-06-05 10:00 | 4.001 | 4.3695 | 4.4057 | 4.4501 | 4.5019 | 2.7626 | 3.3152 | 3.3435 | 3.3821 | 2.7626 | 3.9439 | 4.433 | 4.4584 | 4.4921 | 4.7493
2022-06-05 11:00 | 3.5057 | 3.8416 | 3.8801 | 3.9272 | 3.9821 | 2.4006 | 2.8907 | 2.9207 | 2.9617 | 2.4006 | 2.915 | 3.2927 | 3.3197 | 3.3555 | 3.5586
2022-06-05 12:00 | 3.62 | 3.9634 | 4.0013 | 4.0478 | 4.1019 | 2.2673 | 2.7324 | 2.762 | 2.8024 | 2.2673 | 3.5438 | 3.9907 | 4.0173 | 4.0526 | 4.2896
2022-06-05 13:00 | 3.8486 | 4.204 | 4.2394 | 4.2828 | 4.3333 | 2.5721 | 3.0889 | 3.1165 | 3.1542 | 2.5721 | 3.3723 | 3.7966 | 3.8214 | 3.8543 | 4.0791
2022-06-05 14:00 | 3.7534 | 4.0963 | 4.1289 | 4.1689 | 4.2154 | 2.6102 | 3.13 | 3.1554 | 3.1902 | 2.6102 | 3.4866 | 3.9198 | 3.9427 | 3.973 | 4.201
2022-06-05 15:00 | 4.2678 | 4.6453 | 4.6762 | 4.7139 | 4.7578 | 2.8543 | 3.4157 | 3.4398 | 3.4726 | 2.8543 | 4.725 | 5.2934 | 5.315 | 5.3437 | 5.6377
2022-06-05 16:00 | 4.7631 | 5.1767 | 5.207 | 5.2442 | 5.2875 | 3.2961 | 3.937 | 3.9607 | 3.9931 | 3.2961 | 5.2395 | 5.8645 | 5.8858 | 5.914 | 6.2359
2022-06-05 17:00 | 5.1251 | 5.5691 | 5.6013 | 5.6407 | 5.6866 | 3.7724 | 4.5023 | 4.5274 | 4.5617 | 3.7724 | 6.6493 | 7.4337 | 7.4563 | 7.4862 | 7.8876
2022-06-05 18:00 | 5.3157 | 5.7812 | 5.8171 | 5.8611 | 5.9124 | 3.6962 | 4.4176 | 4.4456 | 4.4839 | 3.6962 | 6.3636 | 7.1214 | 7.1465 | 7.18 | 7.5698
2022-06-05 19:00 | 5.2204 | 5.6886 | 5.7295 | 5.7796 | 5.838 | 3.6962 | 4.4247 | 4.4566 | 4.5002 | 3.6962 | 5.7729 | 6.4719 | 6.5006 | 6.5387 | 6.9016
2022-06-05 20:00 | 5.0299 | 5.4936 | 5.5394 | 5.5956 | 5.661 | 3.4676 | 4.1616 | 4.1974 | 4.2462 | 3.4676 | 6.4588 | 7.241 | 7.2731 | 7.3158 | 7.7219
2022-06-05 21:00 | 4.6107 | 5.0449 | 5.0916 | 5.1487 | 5.2154 | 3.277 | 3.9377 | 3.9742 | 4.0239 | 3.277 | 5.7729 | 6.4799 | 6.5127 | 6.5561 | 6.9255
2022-06-05 22:00 | 4.0582 | 4.4453 | 4.489 | 4.5424 | 4.6047 | 2.7479 | 3.3084 | 3.3424 | 3.3889 | 2.7479 | 4.0391 | 4.5491 | 4.5796 | 4.6203 | 4.8909
2022-06-05 23:00 | 3.6962 | 4.048 | 4.0873 | 4.1355 | 4.1916 | 2.3256 | 2.8033 | 2.834 | 2.8759 | 2.3256 | 3.3342 | 3.7597 | 3.7873 | 3.8239 | 4.051
2022-06-06 | 3.0675 | 3.3631 | 3.3976 | 3.4398 | 3.4891 | 1.988 | 2.3975 | 2.4245 | 2.4612 | 1.988 | 3.0103 | 3.3931 | 3.4173 | 3.4494 | 3.6533
2022-06-06 01:00 | 2.7626 | 3.026 | 3.0556 | 3.0918 | 3.1341 | 1.7528 | 2.1128 | 2.1359 | 2.1675 | 1.7528 | 2.4197 | 2.73 | 2.7507 | 2.7783 | 2.9443
2022-06-06 02:00 | 2.7817 | 3.0344 | 3.0578 | 3.0865 | 3.12 | 1.6385 | 1.969 | 1.9873 | 2.0123 | 1.6385 | 2.7245 | 3.0602 | 3.0766 | 3.0984 | 3.2743
2022-06-06 03:00 | 2.8579 | 3.1044 | 3.1218 | 3.1431 | 3.168 | 1.6576 | 1.9829 | 1.9965 | 2.0151 | 1.6576 | 2.553 | 2.8612 | 2.8734 | 2.8896 | 3.0494
2022-06-06 04:00 | 3.0103 | 3.2581 | 3.2704 | 3.2854 | 3.3029 | 1.7494 | 2.0841 | 2.0937 | 2.1067 | 1.7494 | 2.6864 | 3.0023 | 3.0109 | 3.0223 | 3.1836
2022-06-06 05:00 | 3.4827 | 3.7616 | 3.7718 | 3.7844 | 3.799 | 2.2046 | 2.6189 | 2.6269 | 2.6378 | 2.2046 | 3.3914 | 3.7829 | 3.79 | 3.7995 | 3.9974
2022-06-06 06:00 | 4.5555 | 4.9176 | 4.9295 | 4.9441 | 4.9611 | 2.9959 | 3.5562 | 3.5656 | 3.5783 | 2.9959 | 4.6107 | 5.1402 | 5.1486 | 5.1597 | 5.4265
2022-06-06 07:00 | 5.3347 | 5.7638 | 5.7803 | 5.8006 | 5.8243 | 3.4485 | 4.0975 | 4.1104 | 4.1281 | 3.4485 | 5.8872 | 6.5652 | 6.5768 | 6.5923 | 6.9344
2022-06-06 08:00 | 5.4109 | 5.859 | 5.8824 | 5.911 | 5.9444 | 3.4104 | 4.0622 | 4.0804 | 4.1053 | 3.4104 | 5.2395 | 5.8548 | 5.8712 | 5.893 | 6.2071
2022-06-06 09:00 | 4.7441 | 5.1568 | 5.1875 | 5.225 | 5.2688 | 2.7817 | 3.3298 | 3.3537 | 3.3864 | 2.7817 | 3.6146 | 4.0593 | 4.0808 | 4.1094 | 4.3422
2022-06-06 10:00 | 4.5726 | 4.9835 | 5.0198 | 5.0642 | 5.116 | 2.4578 | 2.9551 | 2.9834 | 3.022 | 2.4578 | 3.8486 | 4.3271 | 4.3525 | 4.3863 | 4.6382
2022-06-06 11:00 | 4.2487 | 4.6399 | 4.6784 | 4.7255 | 4.7804 | 2.5721 | 3.0933 | 3.1233 | 3.1643 | 2.5721 | 3.277 | 3.695 | 3.722 | 3.7578 | 3.9808
2022-06-06 12:00 | 4.4202 | 4.8231 | 4.861 | 4.9075 | 4.9616 | 2.534 | 3.0475 | 3.0771 | 3.1175 | 2.534 | 2.7979 | 3.1618 | 3.1884 | 3.2238 | 3.4198
2022-06-06 13:00 | 4.4583 | 4.859 | 4.8944 | 4.9378 | 4.9883 | 2.4197 | 2.9088 | 2.9364 | 2.9741 | 2.4197 | 2.8007 | 3.1614 | 3.1862 | 3.2192 | 3.4125
2022-06-06 14:00 | 4.4392 | 4.8332 | 4.8658 | 4.9057 | 4.9523 | 2.7626 | 3.31 | 3.3355 | 3.3703 | 2.7626 | 3.1056 | 3.4963 | 3.5192 | 3.5496 | 3.7566
2022-06-06 15:00 | 4.8203 | 5.239 | 5.2698 | 5.3075 | 5.3514 | 3.1437 | 3.7576 | 3.7816 | 3.8144 | 3.1437 | 4.1916 | 4.7006 | 4.7222 | 4.7509 | 5.0156
2022-06-06 16:00 | 5.2966 | 5.7498 | 5.7802 | 5.8173 | 5.8607 | 3.6771 | 4.3872 | 4.4109 | 4.4432 | 3.6771 | 5.5234 | 6.18 | 6.2013 | 6.2296 | 6.567
2022-06-06 17:00 | 5.8872 | 6.3879 | 6.4201 | 6.4595 | 6.5054 | 4.1648 | 4.9658 | 4.9909 | 5.0252 | 4.1648 | 7.3543 | 8.2171 | 8.2397 | 8.2696 | 8.7097
2022-06-06 18:00 | 6.1921 | 6.7228 | 6.7587 | 6.8027 | 6.854 | 4.4011 | 5.2504 | 5.2784 | 5.3167 | 4.4011 | 6.535 | 7.3119 | 7.3371 | 7.3706 | 7.7698
2022-06-06 19:00 | 6.0397 | 6.5688 | 6.6097 | 6.6598 | 6.7182 | 4.3059 | 5.145 | 5.1769 | 5.2204 | 4.3059 | 6.8208 | 7.6364 | 7.6651 | 7.7032 | 8.1237
2022-06-06 20:00 | 5.7729 | 6.2919 | 6.3377 | 6.3939 | 6.4593 | 4.1978 | 5.0243 | 5.0601 | 5.1089 | 4.1978 | 7.0304 | 7.8762 | 7.9083 | 7.951 | 8.3885
2022-06-06 21:00 | 5.2834 | 5.7676 | 5.8143 | 5.8714 | 5.938 | 3.7881 | 4.5414 | 4.5779 | 4.6276 | 3.7881 | 6.897 | 7.7291 | 7.7618 | 7.8053 | 8.2364
2022-06-06 22:00 | 4.4825 | 4.9011 | 4.9448 | 4.9982 | 5.0605 | 3.2918 | 3.9509 | 3.9849 | 4.0314 | 3.2918 | 4.4392 | 4.9937 | 5.0243 | 5.0649 | 5.3575
2022-06-06 23:00 | 3.8486 | 4.2117 | 4.2511 | 4.2992 | 4.3553 | 2.6022 | 3.1301 | 3.1607 | 3.2026 | 2.6022 | 3.8296 | 4.3102 | 4.3377 | 4.3744 | 4.6287
2022-06-07 | 3.3342 | 3.6496 | 3.6841 | 3.7264 | 3.7756 | 2.1776 | 2.6216 | 2.6485 | 2.6853 | 2.1776 | 3.0103 | 3.3931 | 3.4173 | 3.4494 | 3.6533
2022-06-07 01:00 | 3.0294 | 3.3125 | 3.3422 | 3.3784 | 3.4207 | 1.9434 | 2.3379 | 2.361 | 2.3926 | 1.9434 | 3.1246 | 3.5133 | 3.5341 | 3.5616 | 3.7664
2022-06-07 02:00 | 2.9341 | 3.1981 | 3.2216 | 3.2503 | 3.2837 | 1.7877 | 2.1453 | 2.1636 | 2.1885 | 1.7877 | 2.4768 | 2.7849 | 2.8013 | 2.8232 | 2.9854
2022-06-07 03:00 | 2.8769 | 3.1249 | 3.1423 | 3.1636 | 3.1885 | 1.7647 | 2.1095 | 2.123 | 2.1416 | 1.7647 | 2.553 | 2.8612 | 2.8734 | 2.8896 | 3.0494
2022-06-07 04:00 | 3.0484 | 3.299 | 3.3113 | 3.3263 | 3.3438 | 1.8672 | 2.2232 | 2.2328 | 2.2458 | 1.8672 | 2.7055 | 3.0235 | 3.0321 | 3.0435 | 3.2058
2022-06-07 05:00 | 3.5057 | 3.7863 | 3.7966 | 3.8091 | 3.8237 | 2.2423 | 2.6635 | 2.6715 | 2.6824 | 2.2423 | 3.4295 | 3.8252 | 3.8324 | 3.8419 | 4.0418
2022-06-07 06:00 | 4.6768 | 5.0479 | 5.0598 | 5.0744 | 5.0914 | 3.1674 | 3.7588 | 3.7681 | 3.7808 | 3.1674 | 4.5155 | 5.0344 | 5.0427 | 5.0539 | 5.3154
2022-06-07 07:00 | 5.4871 | 5.9275 | 5.9441 | 5.9644 | 5.9881 | 3.6581 | 4.3451 | 4.358 | 4.3757 | 3.6581 | 6.1159 | 6.8193 | 6.8309 | 6.8463 | 7.201
2022-06-07 08:00 | 5.3153 | 5.7563 | 5.7797 | 5.8083 | 5.8417 | 3.4866 | 4.1522 | 4.1705 | 4.1954 | 3.4866 | 4.9805 | 5.567 | 5.5834 | 5.6052 | 5.9051
2022-06-07 09:00 | 5.068 | 5.5048 | 5.5355 | 5.573 | 5.6168 | 3.0103 | 3.5999 | 3.6238 | 3.6565 | 3.0103 | 3.982 | 4.4675 | 4.489 | 4.5176 | 4.7706
2022-06-07 10:00 | 4.7522 | 5.1765 | 5.2128 | 5.2572 | 5.3089 | 2.8199 | 3.3829 | 3.4112 | 3.4498 | 2.8199 | 3.8867 | 4.3694 | 4.3948 | 4.4286 | 4.6826
2022-06-07 11:00 | 4.4202 | 4.8241 | 4.8626 | 4.9097 | 4.9646 | 2.4768 | 2.9807 | 3.0108 | 3.0517 | 2.4768 | 2.6293 | 2.9751 | 3.0021 | 3.0379 | 3.2253
2022-06-07 12:00 | 4.8393 | 5.2734 | 5.3113 | 5.3578 | 5.4119 | 2.7245 | 3.2726 | 3.3022 | 3.3426 | 2.7245 | 3.3151 | 3.7366 | 3.7632 | 3.7985 | 4.023
2022-06-07 13:00 | 4.9346 | 5.3708 | 5.4062 | 5.4495 | 5.5 | 2.8388 | 3.404 | 3.4316 | 3.4693 | 2.8388 | 3.6009 | 4.0507 | 4.0755 | 4.1084 | 4.3458
2022-06-07 14:00 | 5.1823 | 5.6314 | 5.6641 | 5.704 | 5.7506 | 3.1056 | 3.7152 | 3.7406 | 3.7754 | 3.1056 | 4.6298 | 5.1901 | 5.213 | 5.2434 | 5.5342
2022-06-07 15:00 | 4.93 | 5.3568 | 5.3876 | 5.4253 | 5.4692 | 2.9531 | 3.5325 | 3.5565 | 3.5893 | 2.9531 | 3.9439 | 4.4254 | 4.447 | 4.4756 | 4.7267
2022-06-07 16:00 | 5.6586 | 6.1387 | 6.1691 | 6.2063 | 6.2496 | 3.6962 | 4.4097 | 4.4334 | 4.4657 | 3.6962 | 5.7348 | 6.415 | 6.4362 | 6.4645 | 6.8136
2022-06-07 17:00 | 6.3254 | 6.8587 | 6.8909 | 6.9302 | 6.9762 | 4.5155 | 5.3801 | 5.4052 | 5.4395 | 4.5155 | 6.7446 | 7.5396 | 7.5621 | 7.5921 | 7.9987
2022-06-07 18:00 | 6.6112 | 7.1731 | 7.209 | 7.253 | 7.3043 | 4.6869 | 5.588 | 5.6161 | 5.6543 | 4.6869 | 7.6401 | 8.5399 | 8.5651 | 8.5985 | 9.0585
2022-06-07 19:00 | 6.535 | 7.101 | 7.1419 | 7.192 | 7.2503 | 4.6107 | 5.5051 | 5.537 | 5.5806 | 4.6107 | 7.0304 | 7.8693 | 7.898 | 7.9361 | 8.3681
2022-06-07 20:00 | 6.1159 | 6.6603 | 6.7062 | 6.7623 | 6.8277 | 4.6298 | 5.5346 | 5.5704 | 5.6192 | 4.6298 | 7.5448 | 8.4478 | 8.4799 | 8.5226 | 8.9884
2022-06-07 21:00 | 5.811 | 6.3344 | 6.3811 | 6.4383 | 6.5049 | 4.0391 | 4.8381 | 4.8745 | 4.9242 | 4.0391 | 5.9635 | 6.6917 | 6.7244 | 6.7678 | 7.1477
2022-06-07 22:00 | 4.7822 | 5.2232 | 5.2668 | 5.3202 | 5.3825 | 3.5628 | 4.271 | 4.3051 | 4.3516 | 3.5628 | 4.7631 | 5.3536 | 5.3842 | 5.4248 | 5.7353
2022-06-07 23:00 | 3.9629 | 4.3345 | 4.3739 | 4.422 | 4.4782 | 2.7717 | 3.3302 | 3.3609 | 3.4028 | 2.7717 | 3.8105 | 4.289 | 4.3166 | 4.3532 | 4.6064
2022-06-08 | 3.4258 | 3.748 | 3.7825 | 3.8248 | 3.874 | 2.2863 | 2.75 | 2.7769 | 2.8137 | 2.2863 | 3.2389 | 3.6471 | 3.6713 | 3.7034 | 3.9199
2022-06-08 01:00 | 3.2008 | 3.4968 | 3.5264 | 3.5626 | 3.6049 | 2.0097 | 2.4162 | 2.4393 | 2.4709 | 2.0097 | 2.8769 | 3.2381 | 3.2588 | 3.2864 | 3.4775
2022-06-08 02:00 | 3.0865 | 3.3619 | 3.3853 | 3.414 | 3.4475 | 1.9053 | 2.2841 | 2.3024 | 2.3274 | 1.9053 | 3.1437 | 3.5259 | 3.5424 | 3.5642 | 3.7631
2022-06-08 03:00 | 3.0484 | 3.3091 | 3.3265 | 3.3478 | 3.3727 | 1.8481 | 2.208 | 2.2216 | 2.2401 | 1.8481 | 2.7817 | 3.1153 | 3.1275 | 3.1437 | 3.316
2022-06-08 04:00 | 3.258 | 3.5242 | 3.5365 | 3.5515 | 3.569 | 2.0307 | 2.4164 | 2.4259 | 2.439 | 2.0307 | 3.2389 | 3.6163 | 3.6249 | 3.6363 | 3.828
2022-06-08 05:00 | 3.797 | 4.0993 | 4.1095 | 4.122 | 4.1366 | 2.554 | 3.0318 | 3.0397 | 3.0506 | 2.554 | 3.5438 | 3.9522 | 3.9594 | 3.9689 | 4.1751
2022-06-08 06:00 | 4.5917 | 4.9564 | 4.9683 | 4.9829 | 5 | 3.4104 | 4.0459 | 4.0552 | 4.0679 | 3.4104 | 4.93 | 5.4951 | 5.5034 | 5.5145 | 5.7988
2022-06-08 07:00 | 5.5062 | 5.948 | 5.9646 | 5.9849 | 6.0085 | 3.7724 | 4.4801 | 4.4931 | 4.5107 | 3.7724 | 5.8872 | 6.5652 | 6.5768 | 6.5923 | 6.9344
2022-06-08 08:00 | 5.1442 | 5.5724 | 5.5958 | 5.6245 | 5.6579 | 3.6581 | 4.3548 | 4.373 | 4.3979 | 3.6581 | 4.8336 | 5.4039 | 5.4203 | 5.442 | 5.7338
2022-06-08 09:00 | 4.4583 | 4.8498 | 4.8805 | 4.918 | 4.9618 | 2.5893 | 3.1025 | 3.1265 | 3.1591 | 2.5893 | 2.6944 | 3.0367 | 3.0582 | 3.0867 | 3.269
2022-06-08 10:00 | 3.6771 | 4.0215 | 4.0578 | 4.1022 | 4.1539 | 2.0005 | 2.4149 | 2.4432 | 2.4818 | 2.0005 | 1.5601 | 1.7839 | 1.8093 | 1.8431 | 1.9692
2022-06-08 11:00 | 3.8677 | 4.2305 | 4.269 | 4.3161 | 4.371 | 1.9243 | 2.328 | 2.358 | 2.399 | 1.9243 | 0.81926 | 0.96378 | 0.99074 | 1.0266 | 1.1144
2022-06-08 12:00 | 3.8105 | 4.1681 | 4.206 | 4.2525 | 4.3066 | 1.7909 | 2.1697 | 2.1993 | 2.2397 | 1.7909 | 0.91452 | 1.0689 | 1.0955 | 1.1308 | 1.2233
2022-06-08 13:00 | 3.1818 | 3.4876 | 3.523 | 3.5663 | 3.6169 | 1.7909 | 2.1661 | 2.1937 | 2.2314 | 1.7909 | 1.467 | 1.6794 | 1.7042 | 1.7371 | 1.8572
2022-06-08 14:00 | 3.5628 | 3.8916 | 3.9242 | 3.9642 | 4.0107 | 2.0767 | 2.4998 | 2.5252 | 2.56 | 2.0767 | 1.2575 | 1.4426 | 1.4655 | 1.4959 | 1.6013
2022-06-08 15:00 | 4.1435 | 4.5119 | 4.5427 | 4.5804 | 4.6244 | 2.4387 | 2.9248 | 2.9488 | 2.9816 | 2.4387 | 4.2297 | 4.743 | 4.7645 | 4.7932 | 5.06
2022-06-08 16:00 | 5.3116 | 5.7659 | 5.7963 | 5.8335 | 5.8768 | 3.4295 | 4.0946 | 4.1183 | 4.1506 | 3.4295 | 4.5536 | 5.1023 | 5.1236 | 5.1518 | 5.436
2022-06-08 17:00 | 5.9635 | 6.4698 | 6.5019 | 6.5413 | 6.5873 | 4.0582 | 4.8399 | 4.865 | 4.8993 | 4.0582 | 5.7729 | 6.4598 | 6.4824 | 6.5123 | 6.8655
2022-06-08 18:00 | 6.3445 | 6.8865 | 6.9224 | 6.9664 | 7.0177 | 4.4202 | 5.2729 | 5.3009 | 5.3392 | 4.4202 | 5.9635 | 6.6768 | 6.7019 | 6.7354 | 7.1032
2022-06-08 19:00 | 6.0968 | 6.6302 | 6.6711 | 6.7212 | 6.7796 | 4.3249 | 5.1675 | 5.1994 | 5.243 | 4.3249 | 6.2111 | 6.9589 | 6.9876 | 7.0257 | 7.4127
2022-06-08 20:00 | 5.8301 | 6.3533 | 6.3991 | 6.4553 | 6.5207 | 4.2106 | 5.0394 | 5.0752 | 5.124 | 4.2106 | 6.5541 | 7.3469 | 7.379 | 7.4217 | 7.833
2022-06-08 21:00 | 5.5633 | 6.0683 | 6.115 | 6.1722 | 6.2388 | 3.9473 | 4.7295 | 4.7659 | 4.8157 | 3.9473 | 6.1159 | 6.861 | 6.8938 | 6.9372 | 7.3254
2022-06-08 22:00 | 4.7736 | 5.2139 | 5.2575 | 5.311 | 5.3733 | 3.4427 | 4.1291 | 4.1632 | 4.2097 | 3.4427 | 4.4202 | 4.9725 | 5.0031 | 5.0437 | 5.3353
2022-06-08 23:00 | 4.001 | 4.3755 | 4.4148 | 4.463 | 4.5191 | 2.7144 | 3.2626 | 3.2933 | 3.3352 | 2.7144 | 3.5438 | 3.9926 | 4.0201 | 4.0568 | 4.2954
2022-06-09 | 3.3931 | 3.7129 | 3.7474 | 3.7896 | 3.8389 | 2.2189 | 2.6704 | 2.6973 | 2.7341 | 2.2189 | 2.8579 | 3.2237 | 3.2479 | 3.28 | 3.4755
2022-06-09 01:00 | 3.0959 | 3.384 | 3.4136 | 3.4499 | 3.4922 | 1.9624 | 2.3604 | 2.3835 | 2.4151 | 1.9624 | 2.6102 | 2.9417 | 2.9624 | 2.99 | 3.1665
2022-06-09 02:00 | 2.9531 | 3.2186 | 3.242 | 3.2707 | 3.3042 | 1.7909 | 2.1491 | 2.1674 | 2.1923 | 1.7909 | 2.3244 | 2.6155 | 2.632 | 2.6538 | 2.8077
2022-06-09 03:00 | 2.9722 | 3.2272 | 3.2446 | 3.266 | 3.2908 | 1.7909 | 2.1405 | 2.1541 | 2.1726 | 1.7909 | 2.4197 | 2.713 | 2.7252 | 2.7414 | 2.8938
2022-06-09 04:00 | 3.0324 | 3.2818 | 3.2941 | 3.3091 | 3.3266 | 1.9434 | 2.3132 | 2.3228 | 2.3359 | 1.9434 | 2.4197 | 2.7059 | 2.7145 | 2.7259 | 2.8725
2022-06-09 05:00 | 3.7152 | 4.0115 | 4.0217 | 4.0342 | 4.0488 | 2.3569 | 2.7989 | 2.8068 | 2.8177 | 2.3569 | 3.0294 | 3.3806 | 3.3877 | 3.3973 | 3.5752
2022-06-09 06:00 | 4.5726 | 4.9359 | 4.9479 | 4.9625 | 4.9795 | 3.2843 | 3.8968 | 3.9062 | 3.9189 | 3.2843 | 4.2678 | 4.7591 | 4.7675 | 4.7786 | 5.0265
2022-06-09 07:00 | 5.3157 | 5.7433 | 5.7599 | 5.7802 | 5.8038 | 3.62 | 4.3001 | 4.313 | 4.3307 | 3.62 | 5.0489 | 5.6336 | 5.6453 | 5.6607 | 5.9567
2022-06-09 08:00 | 5.2776 | 5.7157 | 5.7391 | 5.7677 | 5.8011 | 3.5247 | 4.1972 | 4.2155 | 4.2404 | 3.5247 | 4.4216 | 4.946 | 4.9624 | 4.9842 | 5.2533
2022-06-09 09:00 | 4.9156 | 5.341 | 5.3717 | 5.4093 | 5.453 | 2.8007 | 3.3523 | 3.3762 | 3.4089 | 2.8007 | 3.639 | 4.0864 | 4.1079 | 4.1365 | 4.3707
2022-06-09 10:00 | 4.1535 | 4.5332 | 4.5695 | 4.6139 | 4.6656 | 2.3435 | 2.82 | 2.8483 | 2.8869 | 2.3435 | 2.553 | 2.8874 | 2.9128 | 2.9465 | 3.1273
2022-06-09 11:00 | 3.8105 | 4.1691 | 4.2076 | 4.2547 | 4.3096 | 2.1339 | 2.5756 | 2.6056 | 2.6466 | 2.1339 | 1.829 | 2.0859 | 2.1129 | 2.1487 | 2.2921
2022-06-09 12:00 | 3.6771 | 4.0248 | 4.0627 | 4.1092 | 4.1633 | 2.0386 | 2.4623 | 2.4919 | 2.5323 | 2.0386 | 1.1813 | 1.3653 | 1.3919 | 1.4272 | 1.5344
2022-06-09 13:00 | 3.9248 | 4.2859 | 4.3213 | 4.3646 | 4.4152 | 2.3435 | 2.8188 | 2.8464 | 2.8841 | 2.3435 | 2.0196 | 2.2934 | 2.3182 | 2.3511 | 2.5015
2022-06-09 14:00 | 4.3249 | 4.7103 | 4.743 | 4.7829 | 4.8295 | 2.3625 | 2.8374 | 2.8628 | 2.8976 | 2.3625 | 2.9531 | 3.327 | 3.3498 | 3.3802 | 3.5789
2022-06-09 15:00 | 4.4583 | 4.85 | 4.8808 | 4.9185 | 4.9625 | 2.6666 | 3.1941 | 3.2181 | 3.2509 | 2.6666 | 3.2008 | 3.5997 | 3.6212 | 3.6499 | 3.8602
2022-06-09 16:00 | 5.1632 | 5.6065 | 5.6369 | 5.6741 | 5.7174 | 3.4676 | 4.1396 | 4.1633 | 4.1956 | 3.4676 | 4.725 | 5.2928 | 5.3141 | 5.3424 | 5.6359
2022-06-09 17:00 | 5.8491 | 6.347 | 6.3791 | 6.4185 | 6.4644 | 3.8802 | 4.6296 | 4.6547 | 4.689 | 3.8802 | 5.3538 | 5.994 | 6.0166 | 6.0465 | 6.3767
2022-06-09 18:00 | 5.8682 | 6.3748 | 6.4107 | 6.4547 | 6.506 | 4.1535 | 4.9578 | 4.9858 | 5.0241 | 4.1535 | 5.6205 | 6.2957 | 6.3208 | 6.3543 | 6.7033
2022-06-09 19:00 | 5.7829 | 6.2929 | 6.3338 | 6.3839 | 6.4423 | 4.0131 | 4.7991 | 4.831 | 4.8746 | 4.0131 | 5.792 | 6.4931 | 6.5218 | 6.5599 | 6.9238
2022-06-09 20:00 | 5.3728 | 5.862 | 5.9079 | 5.964 | 6.0295 | 3.8199 | 4.5778 | 4.6136 | 4.6624 | 3.8199 | 6.0968 | 6.8387 | 6.8708 | 6.9135 | 7.2998
2022-06-09 21:00 | 5.068 | 5.5361 | 5.5828 | 5.64 | 5.7066 | 3.5628 | 4.2754 | 4.3118 | 4.3615 | 3.5628 | 4.4392 | 4.9979 | 5.0306 | 5.0741 | 5.3701
2022-06-09 22:00 | 4.2809 | 4.6846 | 4.7282 | 4.7816 | 4.8439 | 3.0865 | 3.7083 | 3.7424 | 3.7889 | 3.0865 | 4.0582 | 4.5702 | 4.6008 | 4.6414 | 4.9131
2022-06-09 23:00 | 3.7406 | 4.0957 | 4.1351 | 4.1832 | 4.2393 | 2.58 | 3.1039 | 3.1346 | 3.1765 | 2.58 | 3.0103 | 3.3998 | 3.4273 | 3.4639 | 3.6732
2022-06-10 | 3.1231 | 3.4228 | 3.4573 | 3.4996 | 3.5488 | 2.0154 | 2.43 | 2.4569 | 2.4937 | 2.0154 | 2.7245 | 3.0755 | 3.0997 | 3.1318 | 3.32
2022-06-10 01:00 | 3.0103 | 3.2921 | 3.3217 | 3.3579 | 3.4002 | 1.8142 | 2.1853 | 2.2084 | 2.2399 | 1.8142 | 2.4387 | 2.7511 | 2.7719 | 2.7994 | 2.9665
2022-06-10 02:00 | 2.8388 | 3.0958 | 3.1192 | 3.1479 | 3.1814 | 1.6766 | 2.014 | 2.0323 | 2.0573 | 1.6766 | 2.2482 | 2.5308 | 2.5473 | 2.5691 | 2.7188
2022-06-10 03:00 | 2.8579 | 3.1044 | 3.1218 | 3.1431 | 3.168 | 1.6576 | 1.9829 | 1.9965 | 2.0151 | 1.6576 | 2.191 | 2.459 | 2.4711 | 2.4874 | 2.6272
2022-06-10 04:00 | 2.9545 | 3.1982 | 3.2104 | 3.2254 | 3.2429 | 1.81 | 2.1557 | 2.1652 | 2.1783 | 1.81 | 2.2482 | 2.5153 | 2.5239 | 2.5353 | 2.6726
2022-06-10 05:00 | 3.639 | 3.9296 | 3.9398 | 3.9524 | 3.967 | 2.2295 | 2.6484 | 2.6563 | 2.6672 | 2.2295 | 3.0675 | 3.4229 | 3.4301 | 3.4396 | 3.6196
2022-06-10 06:00 | 4.3821 | 4.7312 | 4.7432 | 4.7578 | 4.7748 | 3.0484 | 3.6182 | 3.6275 | 3.6402 | 3.0484 | 4.1154 | 4.5898 | 4.5981 | 4.6092 | 4.8488
2022-06-10 07:00 | 5.0108 | 5.4158 | 5.4324 | 5.4527 | 5.4763 | 3.4295 | 4.075 | 4.0879 | 4.1056 | 3.4295 | 4.5536 | 5.0832 | 5.0948 | 5.1102 | 5.379
2022-06-10 08:00 | 4.9156 | 5.3268 | 5.3502 | 5.3788 | 5.4122 | 3.2721 | 3.8988 | 3.9171 | 3.942 | 3.2721 | 4.029 | 4.5096 | 4.526 | 4.5478 | 4.7954
2022-06-10 09:00 | 4.0963 | 4.4609 | 4.4916 | 4.5291 | 4.5729 | 2.3526 | 2.8228 | 2.8467 | 2.8794 | 2.3526 | 2.0767 | 2.3503 | 2.3718 | 2.4004 | 2.5487
2022-06-10 10:00 | 3.4866 | 3.8168 | 3.8531 | 3.8975 | 3.9492 | 1.81 | 2.1898 | 2.2181 | 2.2567 | 1.81 | 1.2003 | 1.3841 | 1.4096 | 1.4433 | 1.5497
2022-06-10 11:00 | 2.9673 | 3.2632 | 3.3017 | 3.3488 | 3.4037 | 1.5814 | 1.9229 | 1.9529 | 1.9939 | 1.5814 | 0.68589 | 0.81557 | 0.84254 | 0.87836 | 0.95891
2022-06-10 12:00 | 2.9722 | 3.2674 | 3.3054 | 3.3518 | 3.406 | 1.6957 | 2.0572 | 2.0868 | 2.1272 | 1.6957 | 1.2384 | 1.4288 | 1.4554 | 1.4907 | 1.6011
2022-06-10 13:00 | 2.8579 | 3.1396 | 3.175 | 3.2184 | 3.2689 | 1.5814 | 1.9185 | 1.9461 | 1.9838 | 1.5814 | 0.55252 | 0.66309 | 0.68789 | 0.72085 | 0.79063
2022-06-10 14:00 | 3.2389 | 3.5436 | 3.5762 | 3.6162 | 3.6628 | 2.172 | 2.6123 | 2.6378 | 2.6725 | 2.172 | 1.1432 | 1.3156 | 1.3385 | 1.3688 | 1.468
2022-06-10 15:00 | 3.9248 | 4.2769 | 4.3077 | 4.3454 | 4.3894 | 2.5911 | 3.1049 | 3.1289 | 3.1617 | 2.5911 | 2.7626 | 3.1127 | 3.1343 | 3.163 | 3.3491
2022-06-10 16:00 | 4.4964 | 4.8901 | 4.9205 | 4.9576 | 5.001 | 3.0675 | 3.6669 | 3.6906 | 3.723 | 3.0675 | 4.0582 | 4.5518 | 4.5731 | 4.6013 | 4.8582
2022-06-10 17:00 | 4.9156 | 5.344 | 5.3762 | 5.4155 | 5.4615 | 3.3601 | 4.0152 | 4.0403 | 4.0746 | 3.3601 | 4.4011 | 4.9354 | 4.958 | 4.9879 | 5.2657
2022-06-10 18:00 | 5.068 | 5.5151 | 5.551 | 5.595 | 5.6463 | 3.4104 | 4.08 | 4.108 | 4.1463 | 3.4104 | 5.2395 | 5.8722 | 5.8974 | 5.9308 | 6.2589
2022-06-10 19:00 | 5.0489 | 5.5044 | 5.5453 | 5.5954 | 5.6538 | 3.4866 | 4.1771 | 4.209 | 4.2526 | 3.4866 | 5.2395 | 5.8791 | 5.9078 | 5.9459 | 6.2795
2022-06-10 20:00 | 4.706 | 5.1456 | 5.1915 | 5.2476 | 5.313 | 3.4104 | 4.0941 | 4.1299 | 4.1787 | 3.4104 | 4.8775 | 5.4837 | 5.5158 | 5.5585 | 5.8777
2022-06-10 21:00 | 4.439 | 4.8604 | 4.9071 | 4.9642 | 5.0309 | 3.3342 | 4.0053 | 4.0417 | 4.0914 | 3.3342 | 4.3059 | 4.8497 | 4.8824 | 4.9259 | 5.2145
2022-06-10 22:00 | 4.1535 | 4.5477 | 4.5913 | 4.6447 | 4.707 | 3.0294 | 3.6408 | 3.6749 | 3.7213 | 3.0294 | 3.9058 | 4.4008 | 4.4314 | 4.4721 | 4.7354
2022-06-10 23:00 | 3.639 | 3.9866 | 4.0259 | 4.074 | 4.1302 | 2.501 | 3.0105 | 3.0412 | 3.0831 | 2.501 | 3.5628 | 4.0138 | 4.0413 | 4.0779 | 4.3176
2022-06-11 | 3.1818 | 3.4859 | 3.5204 | 3.5626 | 3.6119 | 2.0941 | 2.5229 | 2.5498 | 2.5866 | 2.0941 | 2.6674 | 3.012 | 3.0362 | 3.0683 | 3.2533
2022-06-11 01:00 | 2.9722 | 3.2511 | 3.2808 | 3.317 | 3.3593 | 1.8672 | 2.2479 | 2.271 | 2.3025 | 1.8672 | 2.2482 | 2.5394 | 2.5602 | 2.5877 | 2.7443
2022-06-11 02:00 | 2.7626 | 3.0139 | 3.0373 | 3.066 | 3.0995 | 1.7338 | 2.0816 | 2.0998 | 2.1248 | 1.7338 | 2.1339 | 2.4038 | 2.4202 | 2.4421 | 2.5855
2022-06-11 03:00 | 2.8007 | 3.043 | 3.0604 | 3.0817 | 3.1066 | 1.6549 | 1.9798 | 1.9934 | 2.0119 | 1.6549 | 2.1529 | 2.4166 | 2.4288 | 2.445 | 2.5827
2022-06-11 04:00 | 2.8334 | 3.0681 | 3.0803 | 3.0953 | 3.1128 | 1.6957 | 2.0206 | 2.0302 | 2.0433 | 1.6957 | 2.2291 | 2.4942 | 2.5027 | 2.5142 | 2.6504
2022-06-11 05:00 | 3.0675 | 3.3155 | 3.3258 | 3.3383 | 3.3529 | 1.92 | 2.2827 | 2.2907 | 2.3016 | 1.92 | 2.534 | 2.8301 | 2.8373 | 2.8468 | 2.9975
2022-06-11 06:00 | 3.2961 | 3.5645 | 3.5764 | 3.591 | 3.6081 | 2.2248 | 2.6453 | 2.6546 | 2.6673 | 2.2248 | 3.3342 | 3.7217 | 3.7301 | 3.7412 | 3.9378
2022-06-11 07:00 | 3.62 | 3.9216 | 3.9381 | 3.9584 | 3.9821 | 2.553 | 3.0396 | 3.0526 | 3.0702 | 2.553 | 4.0582 | 4.5327 | 4.5443 | 4.5597 | 4.8013
2022-06-11 08:00 | 3.6009 | 3.9144 | 3.9378 | 3.9665 | 3.9999 | 2.6483 | 3.1619 | 3.1801 | 3.205 | 2.6483 | 3.5819 | 4.0128 | 4.0292 | 4.051 | 4.274
2022-06-11 09:00 | 3.639 | 3.9696 | 4.0003 | 4.0378 | 4.0816 | 2.4006 | 2.8796 | 2.9035 | 2.9362 | 2.4006 | 3.0675 | 3.4513 | 3.4728 | 3.5013 | 3.7041
2022-06-11 10:00 | 3.2389 | 3.5507 | 3.587 | 3.6314 | 3.6831 | 2.3816 | 2.865 | 2.8933 | 2.932 | 2.3816 | 3.3342 | 3.7554 | 3.7808 | 3.8146 | 4.0383
2022-06-11 11:00 | 3.0675 | 3.3708 | 3.4093 | 3.4564 | 3.5113 | 1.9243 | 2.328 | 2.358 | 2.399 | 1.9243 | 1.7528 | 2.0012 | 2.0282 | 2.064 | 2.2032
2022-06-11 12:00 | 3.258 | 3.5745 | 3.6124 | 3.6589 | 3.713 | 2.0386 | 2.4623 | 2.4919 | 2.5323 | 2.0386 | 2.4006 | 2.7203 | 2.7469 | 2.7822 | 2.9565
2022-06-11 13:00 | 2.6293 | 2.894 | 2.9294 | 2.9727 | 3.0233 | 2.1148 | 2.5487 | 2.5763 | 2.614 | 2.1148 | 0.89547 | 1.0442 | 1.069 | 1.1019 | 1.1906
2022-06-11 14:00 | 2.8007 | 3.0728 | 3.1055 | 3.1454 | 3.192 | 1.9815 | 2.3872 | 2.4127 | 2.4474 | 1.9815 | 1.3337 | 1.5273 | 1.5502 | 1.5806 | 1.6902
2022-06-11 15:00 | 3.4485 | 3.7652 | 3.796 | 3.8337 | 3.8777 | 2.4197 | 2.9023 | 2.9263 | 2.9591 | 2.4197 | 2.5911 | 2.9221 | 2.9437 | 2.9724 | 3.1491
2022-06-11 16:00 | 4.429 | 4.8177 | 4.8481 | 4.8852 | 4.9286 | 3.2775 | 3.9151 | 3.9387 | 3.9711 | 3.2775 | 4.8584 | 5.441 | 5.4623 | 5.4906 | 5.7915
2022-06-11 17:00 | 5.2013 | 5.651 | 5.6832 | 5.7226 | 5.7685 | 3.6962 | 4.4123 | 4.4374 | 4.4716 | 3.6962 | 4.4774 | 5.0201 | 5.0426 | 5.0726 | 5.3546
2022-06-11 18:00 | 5.2013 | 5.6584 | 5.6943 | 5.7383 | 5.7896 | 3.639 | 4.3501 | 4.3781 | 4.4164 | 3.639 | 5.2585 | 5.8934 | 5.9186 | 5.952 | 6.2811
2022-06-11 19:00 | 5.1869 | 5.6526 | 5.6935 | 5.7436 | 5.802 | 3.5057 | 4.1996 | 4.2315 | 4.2751 | 3.5057 | 4.6107 | 5.1804 | 5.2091 | 5.2472 | 5.5462
2022-06-11 20:00 | 4.8393 | 5.2889 | 5.3347 | 5.3909 | 5.4563 | 3.4866 | 4.1841 | 4.2199 | 4.2687 | 3.4866 | 4.4583 | 5.0179 | 5.05 | 5.0927 | 5.3889
2022-06-11 21:00 | 4.5726 | 5.004 | 5.0506 | 5.1078 | 5.1744 | 3.3723 | 4.0503 | 4.0867 | 4.1364 | 3.3723 | 4.363 | 4.9132 | 4.9459 | 4.9894 | 5.2812
2022-06-11 22:00 | 4.1535 | 4.5477 | 4.5913 | 4.6447 | 4.707 | 2.9913 | 3.5958 | 3.6298 | 3.6763 | 2.9913 | 3.7534 | 4.2315 | 4.262 | 4.3027 | 4.5576
2022-06-11 23:00 | 3.7534 | 4.1094 | 4.1487 | 4.1969 | 4.253 | 2.5899 | 3.1155 | 3.1462 | 3.1881 | 2.5899 | 3.3533 | 3.7809 | 3.8084 | 3.845 | 4.0732
2022-06-12 | 3.3716 | 3.6898 | 3.7243 | 3.7666 | 3.8158 | 2.1759 | 2.6196 | 2.6465 | 2.6833 | 2.1759 | 2.8198 | 3.1814 | 3.2055 | 3.2377 | 3.4311
2022-06-12 01:00 | 3.1056 | 3.3944 | 3.424 | 3.4603 | 3.5026 | 1.9047 | 2.2922 | 2.3153 | 2.3469 | 1.9047 | 2.3606 | 2.6643 | 2.6851 | 2.7126 | 2.8754
2022-06-12 02:00 | 2.9722 | 3.2391 | 3.2625 | 3.2912 | 3.3247 | 1.7528 | 2.1041 | 2.1224 | 2.1473 | 1.7528 | 2.5911 | 2.9119 | 2.9284 | 2.9502 | 3.1187
2022-06-12 03:00 | 2.896 | 3.1454 | 3.1628 | 3.1841 | 3.2089 | 1.6957 | 2.028 | 2.0415 | 2.0601 | 1.6957 | 2.0767 | 2.3319 | 2.3441 | 2.3603 | 2.4939
2022-06-12 04:00 | 2.7817 | 3.0125 | 3.0247 | 3.0397 | 3.0572 | 1.6766 | 1.9981 | 2.0077 | 2.0207 | 1.6766 | 2.2863 | 2.5577 | 2.5663 | 2.5777 | 2.717
2022-06-12 05:00 | 3.0865 | 3.336 | 3.3462 | 3.3588 | 3.3734 | 1.8672 | 2.2203 | 2.2283 | 2.2392 | 1.8672 | 2.4006 | 2.6819 | 2.6891 | 2.6986 | 2.842
2022-06-12 06:00 | 3.258 | 3.5236 | 3.5355 | 3.5501 | 3.5671 | 2.1339 | 2.5378 | 2.5472 | 2.5599 | 2.1339 | 3.9058 | 4.3569 | 4.3652 | 4.3763 | 4.6043
2022-06-12 07:00 | 3.5247 | 3.8192 | 3.8358 | 3.8561 | 3.8797 | 2.4649 | 2.9355 | 2.9485 | 2.9661 | 2.4649 | 3.5628 | 3.9822 | 3.9938 | 4.0093 | 4.2236
2022-06-12 08:00 | 3.7915 | 4.1191 | 4.1425 | 4.1712 | 4.2046 | 2.4959 | 2.9818 | 3 | 3.025 | 2.4959 | 4.7822 | 5.3467 | 5.3631 | 5.3849 | 5.6738
2022-06-12 09:00 | 4.0391 | 4.3995 | 4.4301 | 4.4677 | 4.5115 | 2.6483 | 3.1722 | 3.1961 | 3.2288 | 2.6483 | 4.7441 | 5.3144 | 5.3359 | 5.3645 | 5.6594
2022-06-12 10:00 | 4.001 | 4.3695 | 4.4057 | 4.4501 | 4.5019 | 2.6674 | 3.2027 | 3.2309 | 3.2696 | 2.6674 | 3.4485 | 3.8825 | 3.9079 | 3.9416 | 4.1716
2022-06-12 11:00 | 3.0865 | 3.3913 | 3.4298 | 3.4769 | 3.5318 | 1.6576 | 2.0129 | 2.0429 | 2.0839 | 1.6576 | 1.5242 | 1.7472 | 1.7741 | 1.8099 | 1.9366
2022-06-12 12:00 | 3.3723 | 3.6973 | 3.7352 | 3.7817 | 3.8358 | 2.0386 | 2.4623 | 2.4919 | 2.5323 | 2.0386 | 1.4861 | 1.7041 | 1.7306 | 1.766 | 1.8899
2022-06-12 13:00 | 2.3144 | 2.5557 | 2.5911 | 2.6344 | 2.685 | 1.6957 | 2.0535 | 2.0811 | 2.1188 | 1.6957 | 1.2003 | 1.3829 | 1.4077 | 1.4407 | 1.5461
2022-06-12 14:00 | 2.896 | 3.1752 | 3.2078 | 3.2478 | 3.2943 | 2.0005 | 2.4097 | 2.4352 | 2.4699 | 2.0005 | 1.8481 | 2.099 | 2.1218 | 2.1522 | 2.2901
2022-06-12 15:00 | 3.3948 | 3.7075 | 3.7383 | 3.776 | 3.8199 | 2.3422 | 2.8108 | 2.8348 | 2.8676 | 2.3422 | 2.3435 | 2.6469 | 2.6685 | 2.6972 | 2.8603
2022-06-12 16:00 | 4.2678 | 4.6445 | 4.6749 | 4.712 | 4.7554 | 2.9523 | 3.5309 | 3.5546 | 3.5869 | 2.9523 | 3.6151 | 4.0594 | 4.0807 | 4.1089 | 4.3415
2022-06-12 17:00 | 4.9346 | 5.3644 | 5.3966 | 5.436 | 5.4819 | 3.5247 | 4.2097 | 4.2348 | 4.2691 | 3.5247 | 4.9918 | 5.5918 | 5.6143 | 5.6442 | 5.9545
2022-06-12 18:00 | 4.9346 | 5.3718 | 5.4077 | 5.4517 | 5.503 | 3.4295 | 4.1025 | 4.1305 | 4.1688 | 3.4295 | 4.5917 | 5.1524 | 5.1775 | 5.211 | 5.5034
2022-06-12 19:00 | 4.8965 | 5.3406 | 5.3815 | 5.4316 | 5.49 | 3.4104 | 4.0871 | 4.119 | 4.1626 | 3.4104 | 4.8012 | 5.3922 | 5.4208 | 5.4589 | 5.7684
2022-06-12 20:00 | 4.7822 | 5.2275 | 5.2733 | 5.3295 | 5.3949 | 3.3151 | 3.9816 | 4.0173 | 4.0662 | 3.3151 | 4.3821 | 4.9332 | 4.9653 | 5.008 | 5.3
2022-06-12 21:00 | 4.4964 | 4.9221 | 4.9688 | 5.0259 | 5.0925 | 3.1056 | 3.7352 | 3.7716 | 3.8213 | 3.1056 | 4.1535 | 4.6803 | 4.713 | 4.7565 | 5.0368
2022-06-12 22:00 | 4.1916 | 4.5886 | 4.6323 | 4.6857 | 4.748 | 2.8007 | 3.3707 | 3.4048 | 3.4512 | 2.8007 | 3.5247 | 3.9774 | 4.008 | 4.0486 | 4.291
2022-06-12 23:00 | 3.7343 | 4.0889 | 4.1282 | 4.1764 | 4.2325 | 2.4768 | 2.9819 | 3.0126 | 3.0545 | 2.4768 | 3.0294 | 3.4209 | 3.4485 | 3.4851 | 3.6954
2022-06-13 | 3.3151 | 3.6292 | 3.6637 | 3.7059 | 3.7551 | 2.0517 | 2.4728 | 2.4997 | 2.5365 | 2.0517 | 2.6864 | 3.0331 | 3.0573 | 3.0894 | 3.2755
2022-06-13 01:00 | 3.0865 | 3.374 | 3.4036 | 3.4398 | 3.4821 | 1.8936 | 2.2791 | 2.3022 | 2.3338 | 1.8936 | 2.4578 | 2.7723 | 2.793 | 2.8206 | 2.9887
2022-06-13 02:00 | 2.8388 | 3.0958 | 3.1192 | 3.1479 | 3.1814 | 1.6898 | 2.0296 | 2.0479 | 2.0729 | 1.6898 | 2.1339 | 2.4038 | 2.4202 | 2.4421 | 2.5855
2022-06-13 03:00 | 2.8769 | 3.1249 | 3.1423 | 3.1636 | 3.1885 | 1.6385 | 1.9604 | 1.974 | 1.9925 | 1.6385 | 2.2101 | 2.4801 | 2.4923 | 2.5085 | 2.6494
2022-06-13 04:00 | 2.9531 | 3.1967 | 3.209 | 3.224 | 3.2415 | 1.7147 | 2.0431 | 2.0527 | 2.0658 | 1.7147 | 2.172 | 2.4306 | 2.4392 | 2.4506 | 2.5837
2022-06-13 05:00 | 3.2961 | 3.5612 | 3.5714 | 3.5839 | 3.5985 | 1.9727 | 2.345 | 2.353 | 2.3639 | 1.9727 | 2.6102 | 2.9148 | 2.922 | 2.9315 | 3.0864
2022-06-13 06:00 | 3.6009 | 3.892 | 3.9039 | 3.9185 | 3.9356 | 2.2093 | 2.6269 | 2.6362 | 2.649 | 2.2093 | 3.277 | 3.6582 | 3.6665 | 3.6777 | 3.8711
2022-06-13 07:00 | 3.982 | 4.3105 | 4.3271 | 4.3473 | 4.371 | 2.8406 | 3.3793 | 3.3923 | 3.4099 | 2.8406 | 3.4676 | 3.8763 | 3.888 | 3.9034 | 4.1125
2022-06-13 08:00 | 4.4202 | 4.7946 | 4.818 | 4.8466 | 4.88 | 3.1056 | 3.702 | 3.7203 | 3.7452 | 3.1056 | 4.5155 | 5.0503 | 5.0667 | 5.0885 | 5.3627
2022-06-13 09:00 | 4.6298 | 5.034 | 5.0647 | 5.1022 | 5.146 | 3.277 | 3.915 | 3.9389 | 3.9716 | 3.277 | 4.1344 | 4.6369 | 4.6584 | 4.687 | 4.9484
2022-06-13 10:00 | 4.6107 | 5.0245 | 5.0607 | 5.1051 | 5.1569 | 3.1627 | 3.7879 | 3.8162 | 3.8548 | 3.1627 | 4.363 | 4.8987 | 4.9241 | 4.9579 | 5.2381
2022-06-13 11:00 | 4.5345 | 4.9469 | 4.9854 | 5.0325 | 5.0875 | 2.9722 | 3.5659 | 3.596 | 3.6369 | 2.9722 | 4.8584 | 5.4523 | 5.4793 | 5.5151 | 5.825
2022-06-13 12:00 | 4.5536 | 4.9664 | 5.0043 | 5.0508 | 5.1049 | 2.915 | 3.4977 | 3.5273 | 3.5677 | 2.915 | 3.5628 | 4.0118 | 4.0384 | 4.0738 | 4.3119
2022-06-13 13:00 | 3.7937 | 4.145 | 4.1804 | 4.2238 | 4.2743 | 2.0577 | 2.4812 | 2.5088 | 2.5465 | 2.0577 | 1.5623 | 1.7852 | 1.81 | 1.843 | 1.9683
2022-06-13 14:00 | 3.1627 | 3.4617 | 3.4944 | 3.5343 | 3.5809 | 1.9624 | 2.3647 | 2.3902 | 2.4249 | 1.9624 | 1.5052 | 1.7179 | 1.7407 | 1.7711 | 1.8902
2022-06-13 15:00 | 3.639 | 3.9699 | 4.0007 | 4.0384 | 4.0823 | 2.5187 | 3.0192 | 3.0433 | 3.0761 | 2.5187 | 2.3435 | 2.6469 | 2.6685 | 2.6972 | 2.8603
2022-06-13 16:00 | 4.6625 | 5.0686 | 5.0989 | 5.1361 | 5.1794 | 3.1437 | 3.757 | 3.7807 | 3.813 | 3.1437 | 4.0201 | 4.5095 | 4.5307 | 4.559 | 4.8138
2022-06-13 17:00 | 5.7729 | 6.2651 | 6.2973 | 6.3366 | 6.3826 | 3.7724 | 4.5023 | 4.5274 | 4.5617 | 3.7724 | 5.2395 | 5.867 | 5.8895 | 5.9195 | 6.2433
2022-06-13 18:00 | 5.8491 | 6.3543 | 6.3903 | 6.4342 | 6.4855 | 4.1344 | 4.9353 | 4.9633 | 5.0016 | 4.1344 | 5.1442 | 5.7663 | 5.7915 | 5.825 | 6.1478
2022-06-13 19:00 | 5.7348 | 6.2413 | 6.2822 | 6.3323 | 6.3907 | 4.1251 | 4.9314 | 4.9633 | 5.0069 | 4.1251 | 5.3538 | 6.0062 | 6.0348 | 6.0729 | 6.4128
2022-06-13 20:00 | 5.3728 | 5.862 | 5.9079 | 5.964 | 6.0295 | 4.001 | 4.7919 | 4.8276 | 4.8765 | 4.001 | 5.2776 | 5.9283 | 5.9604 | 6.0031 | 6.3443
2022-06-13 21:00 | 5.1251 | 5.5976 | 5.6442 | 5.7014 | 5.768 | 3.6593 | 4.3893 | 4.4257 | 4.4754 | 3.6593 | 4.725 | 5.3155 | 5.3482 | 5.3917 | 5.7034
2022-06-13 22:00 | 4.6488 | 5.0799 | 5.1235 | 5.1769 | 5.2392 | 3.1181 | 3.7457 | 3.7797 | 3.8262 | 3.1181 | 4.1916 | 4.7184 | 4.749 | 4.7896 | 5.0687
2022-06-13 23:00 | 4.0708 | 4.4505 | 4.4898 | 4.5379 | 4.5941 | 2.6483 | 3.1845 | 3.2152 | 3.2571 | 2.6483 | 3.5628 | 4.0138 | 4.0413 | 4.0779 | 4.3176
2022-06-14 | 3.6009 | 3.9362 | 3.9707 | 4.0129 | 4.0622 | 2.2101 | 2.66 | 2.6869 | 2.7236 | 2.2101 | 3.0103 | 3.3931 | 3.4173 | 3.4494 | 3.6533
2022-06-14 01:00 | 3.2389 | 3.5377 | 3.5673 | 3.6036 | 3.6458 | 1.99 | 2.3931 | 2.4162 | 2.4477 | 1.99 | 2.5863 | 2.9151 | 2.9358 | 2.9634 | 3.1385
2022-06-14 02:00 | 3.1246 | 3.4028 | 3.4263 | 3.455 | 3.4884 | 1.8655 | 2.2372 | 2.2555 | 2.2805 | 1.8655 | 2.4387 | 2.7426 | 2.759 | 2.7808 | 2.941
2022-06-14 03:00 | 3.0103 | 3.2682 | 3.2856 | 3.3069 | 3.3317 | 1.8481 | 2.208 | 2.2216 | 2.2401 | 1.8481 | 2.3244 | 2.6072 | 2.6194 | 2.6356 | 2.7827
2022-06-14 04:00 | 3.0865 | 3.34 | 3.3522 | 3.3672 | 3.3847 | 1.9053 | 2.2682 | 2.2778 | 2.2908 | 1.9053 | 2.8007 | 3.1293 | 3.1379 | 3.1493 | 3.3169
2022-06-14 05:00 | 3.6364 | 3.9267 | 3.937 | 3.9495 | 3.9641 | 2.2787 | 2.7065 | 2.7145 | 2.7254 | 2.2787 | 3.1627 | 3.5288 | 3.536 | 3.5455 | 3.7307
2022-06-14 06:00 | 4.5723 | 4.9356 | 4.9475 | 4.9621 | 4.9791 | 3.0938 | 3.6719 | 3.6812 | 3.6939 | 3.0938 | 4.158 | 4.6372 | 4.6455 | 4.6566 | 4.8985
2022-06-14 07:00 | 5.5252 | 5.9685 | 5.985 | 6.0053 | 6.029 | 3.5819 | 4.255 | 4.268 | 4.2856 | 3.5819 | 4.9537 | 5.5278 | 5.5394 | 5.5548 | 5.8456
2022-06-14 08:00 | 5.5443 | 6.0023 | 6.0257 | 6.0543 | 6.0877 | 3.5819 | 4.2647 | 4.283 | 4.3079 | 3.5819 | 5.068 | 5.6643 | 5.6807 | 5.7024 | 6.0071
2022-06-14 09:00 | 5.5252 | 5.9961 | 6.0267 | 6.0643 | 6.1081 | 3.3533 | 4.005 | 4.0289 | 4.0616 | 3.3533 | 4.4964 | 5.0392 | 5.0607 | 5.0892 | 5.3706
2022-06-14 10:00 | 5.43 | 5.9046 | 5.9409 | 5.9853 | 6.0371 | 3.258 | 3.9004 | 3.9287 | 3.9673 | 3.258 | 4.1344 | 4.6447 | 4.6701 | 4.7038 | 4.9715
2022-06-14 11:00 | 5.1442 | 5.602 | 5.6404 | 5.6875 | 5.7425 | 2.915 | 3.4984 | 3.5284 | 3.5694 | 2.915 | 3.7343 | 4.2031 | 4.2301 | 4.2659 | 4.5141
2022-06-14 12:00 | 4.9537 | 5.3962 | 5.4342 | 5.4806 | 5.5348 | 2.7245 | 3.2726 | 3.3022 | 3.3426 | 2.7245 | 3.0294 | 3.419 | 3.4456 | 3.4809 | 3.6897
2022-06-14 13:00 | 4.8012 | 5.2275 | 5.2629 | 5.3062 | 5.3567 | 2.7055 | 3.2464 | 3.2741 | 3.3118 | 2.7055 | 2.9913 | 3.3731 | 3.3979 | 3.4309 | 3.6347
2022-06-14 14:00 | 4.7631 | 5.1811 | 5.2138 | 5.2537 | 5.3003 | 2.6293 | 3.1525 | 3.1779 | 3.2127 | 2.6293 | 3.4104 | 3.8351 | 3.858 | 3.8883 | 4.1122
2022-06-14 15:00 | 4.706 | 5.1161 | 5.1469 | 5.1846 | 5.2286 | 2.7489 | 3.2912 | 3.3153 | 3.3481 | 2.7489 | 2.9341 | 3.3032 | 3.3248 | 3.3535 | 3.5491
2022-06-14 16:00 | 5.3549 | 5.8124 | 5.8428 | 5.88 | 5.9233 | 3.5057 | 4.1846 | 4.2083 | 4.2406 | 3.5057 | 5.0489 | 5.6528 | 5.674 | 5.7023 | 6.0137
2022-06-14 17:00 | 6.3826 | 6.9201 | 6.9523 | 6.9916 | 7.0376 | 4.1344 | 4.93 | 4.955 | 4.9893 | 4.1344 | 5.811 | 6.5022 | 6.5247 | 6.5547 | 6.9099
2022-06-14 18:00 | 6.7256 | 7.2959 | 7.3318 | 7.3758 | 7.4271 | 4.4011 | 5.2504 | 5.2784 | 5.3167 | 4.4011 | 6.3064 | 7.0579 | 7.083 | 7.1165 | 7.5032
2022-06-14 19:00 | 6.6684 | 7.2442 | 7.2852 | 7.3352 | 7.3936 | 4.5155 | 5.3925 | 5.4245 | 5.468 | 4.5155 | 6.535 | 7.3188 | 7.3475 | 7.3856 | 7.7904
2022-06-14 20:00 | 6.3826 | 6.9469 | 6.9927 | 7.0489 | 7.1143 | 4.4253 | 5.293 | 5.3288 | 5.3776 | 4.4253 | 6.6493 | 7.4527 | 7.4848 | 7.5275 | 7.9441
2022-06-14 21:00 | 5.9009 | 6.431 | 6.4777 | 6.5348 | 6.6015 | 4.3099 | 5.158 | 5.1944 | 5.2441 | 4.3099 | 5.5824 | 6.2682 | 6.3009 | 6.3444 | 6.7033
2022-06-14 22:00 | 5.1442 | 5.6121 | 5.6557 | 5.7091 | 5.7714 | 3.7342 | 4.4735 | 4.5075 | 4.554 | 3.7342 | 4.8775 | 5.4806 | 5.5112 | 5.5518 | 5.8686
2022-06-14 23:00 | 4.4392 | 4.8463 | 4.8856 | 4.9337 | 4.9899 | 2.9784 | 3.5744 | 3.6051 | 3.647 | 2.9784 | 4.0201 | 4.5219 | 4.5495 | 4.5861 | 4.8509
2022-06-15 | 3.8677 | 4.2228 | 4.2573 | 4.2995 | 4.3487 | 2.456 | 2.9505 | 2.9774 | 3.0142 | 2.456 | 3.4295 | 3.8589 | 3.883 | 3.9152 | 4.1421
2022-06-15 01:00 | 3.5057 | 3.8243 | 3.8539 | 3.8901 | 3.9324 | 2.1735 | 2.6097 | 2.6328 | 2.6644 | 2.1735 | 3.2199 | 3.6192 | 3.6399 | 3.6675 | 3.8775
2022-06-15 02:00 | 3.3342 | 3.628 | 3.6514 | 3.6801 | 3.7136 | 2.0577 | 2.4642 | 2.4825 | 2.5074 | 2.0577 | 3.0103 | 3.3777 | 3.3942 | 3.416 | 3.6076
2022-06-15 03:00 | 3.4021 | 3.6891 | 3.7066 | 3.7279 | 3.7527 | 2.0058 | 2.3943 | 2.4079 | 2.4264 | 2.0058 | 2.8769 | 3.2212 | 3.2334 | 3.2496 | 3.4271
2022-06-15 04:00 | 3.4676 | 3.7494 | 3.7616 | 3.7766 | 3.7941 | 2.1529 | 2.5608 | 2.5704 | 2.5834 | 2.1529 | 3.4485 | 3.8492 | 3.8578 | 3.8692 | 4.0724
2022-06-15 05:00 | 4.0076 | 4.3255 | 4.3357 | 4.3483 | 4.3629 | 2.6502 | 3.1454 | 3.1534 | 3.1643 | 2.6502 | 3.6009 | 4.0157 | 4.0229 | 4.0324 | 4.2418
2022-06-15 06:00 | 5.1251 | 5.5295 | 5.5415 | 5.5561 | 5.5731 | 3.5918 | 4.2601 | 4.2695 | 4.2822 | 3.5918 | 5.6205 | 6.2624 | 6.2707 | 6.2818 | 6.6041
2022-06-15 07:00 | 5.8682 | 6.3369 | 6.3535 | 6.3738 | 6.3974 | 4.0582 | 4.8177 | 4.8307 | 4.8483 | 4.0582 | 5.449 | 6.0783 | 6.0899 | 6.1053 | 6.4233
2022-06-15 08:00 | 5.8491 | 6.3298 | 6.3532 | 6.3818 | 6.4152 | 3.8979 | 4.6381 | 4.6564 | 4.6813 | 3.8979 | 5.8872 | 6.5747 | 6.5911 | 6.6129 | 6.9625
2022-06-15 09:00 | 4.8393 | 5.2592 | 5.2898 | 5.3274 | 5.3712 | 2.8656 | 3.4289 | 3.4528 | 3.4855 | 2.8656 | 3.0149 | 3.3928 | 3.4143 | 3.4429 | 3.6428
2022-06-15 10:00 | 4.1916 | 4.5742 | 4.6104 | 4.6548 | 4.7066 | 2.4113 | 2.9001 | 2.9284 | 2.967 | 2.4113 | 1.9434 | 2.2099 | 2.2353 | 2.269 | 2.4162
2022-06-15 11:00 | 4.5345 | 4.9469 | 4.9854 | 5.0325 | 5.0875 | 2.5149 | 3.0258 | 3.0558 | 3.0968 | 2.5149 | 2.6483 | 2.9963 | 3.0233 | 3.0591 | 3.2475
2022-06-15 12:00 | 4.0963 | 4.4751 | 4.5131 | 4.5595 | 4.6137 | 2.1028 | 2.5381 | 2.5677 | 2.6081 | 2.1028 | 1.6576 | 1.8946 | 1.9212 | 1.9565 | 2.0899
2022-06-15 13:00 | 3.7724 | 4.1222 | 4.1576 | 4.2009 | 4.2514 | 2.2482 | 2.7063 | 2.7339 | 2.7716 | 2.2482 | 2.3244 | 2.6321 | 2.6569 | 2.6899 | 2.8571
2022-06-15 14:00 | 3.7343 | 4.0758 | 4.1084 | 4.1484 | 4.195 | 2.1021 | 2.5298 | 2.5552 | 2.59 | 2.1021 | 2.9722 | 3.3481 | 3.371 | 3.4014 | 3.6011
2022-06-15 15:00 | 3.9456 | 4.2992 | 4.33 | 4.3677 | 4.4117 | 2.4387 | 2.9248 | 2.9488 | 2.9816 | 2.4387 | 2.8388 | 3.1974 | 3.219 | 3.2476 | 3.438
2022-06-15 16:00 | 4.8203 | 5.2381 | 5.2685 | 5.3056 | 5.349 | 3.161 | 3.7774 | 3.8011 | 3.8334 | 3.161 | 4.0963 | 4.5941 | 4.6154 | 4.6437 | 4.9027
2022-06-15 17:00 | 5.6015 | 6.0809 | 6.113 | 6.1524 | 6.1983 | 3.7534 | 4.4798 | 4.5049 | 4.5392 | 3.7534 | 5.6015 | 6.2693 | 6.2918 | 6.3218 | 6.6655
2022-06-15 18:00 | 5.8491 | 6.3543 | 6.3903 | 6.4342 | 6.4855 | 4.018 | 4.7978 | 4.8258 | 4.8641 | 4.018 | 5.1061 | 5.724 | 5.7492 | 5.7826 | 6.1033
2022-06-15 19:00 | 5.7539 | 6.2617 | 6.3026 | 6.3527 | 6.4111 | 4.0201 | 4.8073 | 4.8392 | 4.8828 | 4.0201 | 5.6777 | 6.3661 | 6.3947 | 6.4328 | 6.7905
2022-06-15 20:00 | 5.449 | 5.9439 | 5.9898 | 6.0459 | 6.1113 | 4.0201 | 4.8144 | 4.8501 | 4.899 | 4.0201 | 5.2776 | 5.9283 | 5.9604 | 6.0031 | 6.3443
2022-06-15 21:00 | 5.068 | 5.5361 | 5.5828 | 5.64 | 5.7066 | 3.5819 | 4.2979 | 4.3343 | 4.384 | 3.5819 | 4.6869 | 5.2731 | 5.3058 | 5.3493 | 5.6589
2022-06-15 22:00 | 4.4964 | 4.9161 | 4.9598 | 5.0132 | 5.0755 | 3.0295 | 3.641 | 3.6751 | 3.7216 | 3.0295 | 3.8296 | 4.3162 | 4.3467 | 4.3874 | 4.6465
2022-06-15 23:00 | 3.6771 | 4.0275 | 4.0668 | 4.115 | 4.1711 | 2.542 | 3.0589 | 3.0896 | 3.1314 | 2.542 | 3.1056 | 3.5056 | 3.5332 | 3.5698 | 3.7843
2022-06-16 | 3.0865 | 3.3835 | 3.418 | 3.4603 | 3.5095 | 2.0288 | 2.4458 | 2.4727 | 2.5095 | 2.0288 | 2.3435 | 2.652 | 2.6762 | 2.7083 | 2.8756
2022-06-16 01:00 | 2.7817 | 3.0464 | 3.0761 | 3.1123 | 3.1546 | 1.7634 | 2.1253 | 2.1484 | 2.18 | 1.7634 | 2.0958 | 2.37 | 2.3908 | 2.4183 | 2.5665
2022-06-16 02:00 | 2.7626 | 3.0139 | 3.0373 | 3.066 | 3.0995 | 1.6589 | 1.9931 | 2.0114 | 2.0363 | 1.6589 | 2.191 | 2.4673 | 2.4838 | 2.5056 | 2.6521
2022-06-16 03:00 | 2.7817 | 3.0225 | 3.04 | 3.0613 | 3.0861 | 1.6385 | 1.9604 | 1.974 | 1.9925 | 1.6385 | 2.0767 | 2.3319 | 2.3441 | 2.3603 | 2.4939
2022-06-16 04:00 | 2.7436 | 2.9715 | 2.9838 | 2.9988 | 3.0163 | 1.692 | 2.0163 | 2.0259 | 2.0389 | 1.692 | 2.2863 | 2.5577 | 2.5663 | 2.5777 | 2.717
2022-06-16 05:00 | 3.277 | 3.5407 | 3.5509 | 3.5634 | 3.5781 | 2.171 | 2.5793 | 2.5872 | 2.5981 | 2.171 | 2.8279 | 3.1567 | 3.1639 | 3.1734 | 3.3402
2022-06-16 06:00 | 4.2466 | 4.5856 | 4.5976 | 4.6122 | 4.6292 | 3.0675 | 3.6407 | 3.65 | 3.6628 | 3.0675 | 4.4202 | 4.9285 | 4.9369 | 4.948 | 5.2043
2022-06-16 07:00 | 5.068 | 5.4772 | 5.4938 | 5.5141 | 5.5377 | 3.277 | 3.8949 | 3.9079 | 3.9255 | 3.277 | 4.1725 | 4.6597 | 4.6713 | 4.6868 | 4.9346
2022-06-16 08:00 | 4.9346 | 5.3473 | 5.3707 | 5.3993 | 5.4327 | 3.2961 | 3.9271 | 3.9454 | 3.9703 | 3.2961 | 4.0391 | 4.521 | 4.5374 | 4.5591 | 4.8072
2022-06-16 09:00 | 4.6488 | 5.0545 | 5.0852 | 5.1227 | 5.1665 | 2.8198 | 3.3748 | 3.3987 | 3.4314 | 2.8198 | 3.2008 | 3.5995 | 3.621 | 3.6495 | 3.8596
2022-06-16 10:00 | 4.001 | 4.3695 | 4.4057 | 4.4501 | 4.5019 | 2.3816 | 2.865 | 2.8933 | 2.932 | 2.3816 | 2.553 | 2.8874 | 2.9128 | 2.9465 | 3.1273
2022-06-16 11:00 | 3.9439 | 4.3124 | 4.3509 | 4.398 | 4.4529 | 2.4197 | 2.9132 | 2.9432 | 2.9842 | 2.4197 | 2.4197 | 2.7422 | 2.7692 | 2.805 | 2.9809
2022-06-16 12:00 | 3.9248 | 4.2909 | 4.3288 | 4.3753 | 4.4294 | 2.2101 | 2.6649 | 2.6945 | 2.7349 | 2.2101 | 2.0196 | 2.2969 | 2.3235 | 2.3588 | 2.5121
2022-06-16 13:00 | 3.9248 | 4.2859 | 4.3213 | 4.3646 | 4.4152 | 2.2101 | 2.6612 | 2.6889 | 2.7266 | 2.2101 | 2.2863 | 2.5898 | 2.6146 | 2.6475 | 2.8126
2022-06-16 14:00 | 3.9058 | 4.26 | 4.2927 | 4.3326 | 4.3792 | 2.2673 | 2.7248 | 2.7503 | 2.7851 | 2.2673 | 2.6674 | 3.0094 | 3.0322 | 3.0626 | 3.2456
2022-06-16 15:00 | 3.982 | 4.3383 | 4.3691 | 4.4068 | 4.4508 | 2.6498 | 3.1742 | 3.1982 | 3.231 | 2.6498 | 3.2389 | 3.642 | 3.6636 | 3.6923 | 3.9046
2022-06-16 16:00 | 4.7441 | 5.1562 | 5.1866 | 5.2237 | 5.2671 | 3.0103 | 3.5994 | 3.6231 | 3.6554 | 3.0103 | 4.7631 | 5.3352 | 5.3564 | 5.3847 | 5.6804
2022-06-16 17:00 | 5.2553 | 5.709 | 5.7411 | 5.7805 | 5.8264 | 3.5073 | 4.1891 | 4.2142 | 4.2485 | 3.5073 | 4.9537 | 5.5494 | 5.572 | 5.6019 | 5.91
2022-06-16 18:00 | 5.3347 | 5.8017 | 5.8376 | 5.8816 | 5.9329 | 3.7915 | 4.5302 | 4.5582 | 4.5965 | 3.7915 | 4.7631 | 5.3429 | 5.3681 | 5.4015 | 5.7034
2022-06-16 19:00 | 5.1061 | 5.5658 | 5.6067 | 5.6568 | 5.7152 | 3.8296 | 4.5823 | 4.6142 | 4.6577 | 3.8296 | 4.8012 | 5.3922 | 5.4208 | 5.4589 | 5.7684
2022-06-16 20:00 | 4.8012 | 5.2479 | 5.2938 | 5.3499 | 5.4154 | 3.62 | 4.3417 | 4.3775 | 4.4263 | 3.62 | 4.8203 | 5.4202 | 5.4523 | 5.495 | 5.811
2022-06-16 21:00 | 4.5661 | 4.997 | 5.0437 | 5.1008 | 5.1674 | 3.3914 | 4.0728 | 4.1092 | 4.1589 | 3.3914 | 3.8586 | 4.3526 | 4.3853 | 4.4288 | 4.6929
2022-06-16 22:00 | 4.0391 | 4.4249 | 4.4685 | 4.5219 | 4.5842 | 2.9341 | 3.5283 | 3.5623 | 3.6088 | 2.9341 | 3.5819 | 4.0409 | 4.0715 | 4.1121 | 4.3576
2022-06-16 23:00 | 3.5247 | 3.8638 | 3.9031 | 3.9512 | 4.0074 | 2.534 | 3.0495 | 3.0802 | 3.122 | 2.534 | 2.7245 | 3.0822 | 3.1097 | 3.1464 | 3.3399
2022-06-17 | 3.123 | 3.4227 | 3.4572 | 3.4994 | 3.5487 | 2.0767 | 2.5024 | 2.5293 | 2.5661 | 2.0767 | 2.8198 | 3.1814 | 3.2055 | 3.2377 | 3.4311
2022-06-17 01:00 | 2.8769 | 3.1488 | 3.1784 | 3.2147 | 3.2569 | 1.8481 | 2.2254 | 2.2485 | 2.28 | 1.8481 | 2.3625 | 2.6664 | 2.6872 | 2.7148 | 2.8776
2022-06-17 02:00 | 2.7817 | 3.0344 | 3.0578 | 3.0865 | 3.12 | 1.6195 | 1.9465 | 1.9648 | 1.9898 | 1.6195 | 2.1148 | 2.3826 | 2.3991 | 2.4209 | 2.5633
2022-06-17 03:00 | 2.8579 | 3.1044 | 3.1218 | 3.1431 | 3.168 | 1.6195 | 1.9379 | 1.9515 | 1.97 | 1.6195 | 1.9815 | 2.2261 | 2.2383 | 2.2545 | 2.3828
2022-06-17 04:00 | 2.896 | 3.1353 | 3.1475 | 3.1626 | 3.18 | 1.7533 | 2.0887 | 2.0983 | 2.1113 | 1.7533 | 2.1306 | 2.3846 | 2.3932 | 2.4046 | 2.5354
2022-06-17 05:00 | 3.3342 | 3.6021 | 3.6123 | 3.6249 | 3.6395 | 2.1513 | 2.556 | 2.564 | 2.5748 | 2.1513 | 2.534 | 2.8301 | 2.8373 | 2.8468 | 2.9975
2022-06-17 06:00 | 4.2868 | 4.6289 | 4.6408 | 4.6554 | 4.6725 | 2.9341 | 3.4832 | 3.4925 | 3.5052 | 2.9341 | 3.6771 | 4.1028 | 4.1112 | 4.1223 | 4.3377
2022-06-17 07:00 | 4.9727 | 5.3749 | 5.3914 | 5.4117 | 5.4354 | 3.3723 | 4.0075 | 4.0204 | 4.0381 | 3.3723 | 4.6107 | 5.1467 | 5.1583 | 5.1737 | 5.4457
2022-06-17 08:00 | 4.9537 | 5.3677 | 5.3911 | 5.4198 | 5.4532 | 3.2389 | 3.8596 | 3.8779 | 3.9028 | 3.2389 | 3.8677 | 4.3304 | 4.3468 | 4.3686 | 4.6073
2022-06-17 09:00 | 4.5726 | 4.9726 | 5.0033 | 5.0408 | 5.0846 | 2.6483 | 3.1722 | 3.1961 | 3.2288 | 2.6483 | 2.6914 | 3.0334 | 3.0549 | 3.0834 | 3.2655
2022-06-17 10:00 | 3.5057 | 3.8373 | 3.8735 | 3.9179 | 3.9697 | 2.1802 | 2.6271 | 2.6554 | 2.694 | 2.1802 | 2.2673 | 2.5698 | 2.5952 | 2.629 | 2.794
2022-06-17 11:00 | 2.8388 | 3.1252 | 3.1637 | 3.2108 | 3.2657 | 1.467 | 1.7878 | 1.8178 | 1.8588 | 1.467 | 0.85737 | 1.0061 | 1.0331 | 1.0689 | 1.1589
2022-06-17 12:00 | 2.6022 | 2.87 | 2.9079 | 2.9544 | 3.0085 | 1.448 | 1.7646 | 1.7942 | 1.8346 | 1.448 | 1.0288 | 1.1959 | 1.2225 | 1.2578 | 1.3566
2022-06-17 13:00 | 3.3723 | 3.6923 | 3.7277 | 3.771 | 3.8216 | 1.8515 | 2.2376 | 2.2652 | 2.3029 | 1.8515 | 1.6957 | 1.9334 | 1.9582 | 1.9912 | 2.1238
2022-06-17 14:00 | 3.4676 | 3.7892 | 3.8219 | 3.8618 | 3.9084 | 1.9624 | 2.3647 | 2.3902 | 2.4249 | 1.9624 | 2.1339 | 2.4166 | 2.4394 | 2.4698 | 2.6234
2022-06-17 15:00 | 3.7343 | 4.0722 | 4.103 | 4.1407 | 4.1847 | 2.2129 | 2.658 | 2.682 | 2.7148 | 2.2129 | 2.9913 | 3.3668 | 3.3883 | 3.417 | 3.6158
2022-06-17 16:00 | 4.2487 | 4.624 | 4.6544 | 4.6915 | 4.7349 | 2.7055 | 3.2393 | 3.263 | 3.2953 | 2.7055 | 3.6962 | 4.1495 | 4.1708 | 4.1991 | 4.4361
2022-06-17 17:00 | 4.5345 | 4.9346 | 4.9668 | 5.0062 | 5.0521 | 3.1267 | 3.7395 | 3.7646 | 3.7988 | 3.1267 | 4.2868 | 4.8084 | 4.8309 | 4.8609 | 5.1324
2022-06-17 18:00 | 4.5726 | 4.9829 | 5.0188 | 5.0628 | 5.1141 | 3.277 | 3.9224 | 3.9505 | 3.9887 | 3.277 | 4.2106 | 4.7289 | 4.7541 | 4.7875 | 5.059
2022-06-17 19:00 | 4.5536 | 4.9722 | 5.0131 | 5.0632 | 5.1216 | 3.1437 | 3.772 | 3.8039 | 3.8475 | 3.1437 | 4.1916 | 4.7146 | 4.7433 | 4.7814 | 5.0574
2022-06-17 20:00 | 4.3821 | 4.7976 | 4.8435 | 4.8996 | 4.9651 | 3.0484 | 3.6665 | 3.7022 | 3.7511 | 3.0484 | 4.2106 | 4.7427 | 4.7748 | 4.8175 | 5.1
2022-06-17 21:00 | 4.2487 | 4.656 | 4.7027 | 4.7598 | 4.8265 | 3.0484 | 3.6676 | 3.7041 | 3.7538 | 3.0484 | 3.5057 | 3.9604 | 3.9932 | 4.0366 | 4.2813
2022-06-17 22:00 | 4.001 | 4.3839 | 4.4276 | 4.481 | 4.5433 | 2.9341 | 3.5283 | 3.5623 | 3.6088 | 2.9341 | 3.3533 | 3.7869 | 3.8174 | 3.8581 | 4.091
2022-06-17 23:00 | 3.7343 | 4.0889 | 4.1282 | 4.1764 | 4.2325 | 2.4197 | 2.9144 | 2.9451 | 2.987 | 2.4197 | 3.0103 | 3.3998 | 3.4273 | 3.4639 | 3.6732
2022-06-18 | 3.3533 | 3.6701 | 3.7046 | 3.7468 | 3.7961 | 2.1148 | 2.5474 | 2.5744 | 2.6111 | 2.1148 | 2.6102 | 2.9485 | 2.9726 | 3.0048 | 3.1867
2022-06-18 01:00 | 3.1437 | 3.4354 | 3.465 | 3.5012 | 3.5435 | 1.835 | 2.2099 | 2.233 | 2.2646 | 1.835 | 2.2482 | 2.5394 | 2.5602 | 2.5877 | 2.7443
2022-06-18 02:00 | 2.9531 | 3.2186 | 3.242 | 3.2707 | 3.3042 | 1.7528 | 2.1041 | 2.1224 | 2.1473 | 1.7528 | 2.0958 | 2.3615 | 2.3779 | 2.3997 | 2.541
2022-06-18 03:00 | 2.9341 | 3.1863 | 3.2037 | 3.225 | 3.2499 | 1.7719 | 2.118 | 2.1316 | 2.1501 | 1.7719 | 2.0577 | 2.3107 | 2.3229 | 2.3392 | 2.4716
2022-06-18 04:00 | 3.0484 | 3.299 | 3.3113 | 3.3263 | 3.3438 | 1.7885 | 2.1303 | 2.1399 | 2.1529 | 1.7885 | 2.4197 | 2.7059 | 2.7145 | 2.7259 | 2.8725
2022-06-18 05:00 | 3.2619 | 3.5244 | 3.5346 | 3.5472 | 3.5618 | 2.0005 | 2.3779 | 2.3859 | 2.3968 | 2.0005 | 2.6483 | 2.9571 | 2.9643 | 2.9738 | 3.1308
2022-06-18 06:00 | 3.639 | 3.9329 | 3.9449 | 3.9595 | 3.9765 | 2.3896 | 2.8399 | 2.8492 | 2.862 | 2.3896 | 3.4104 | 3.8064 | 3.8147 | 3.8259 | 4.0266
2022-06-18 07:00 | 4.0772 | 4.4128 | 4.4294 | 4.4497 | 4.4733 | 2.7055 | 3.2197 | 3.2326 | 3.2503 | 2.7055 | 3.5057 | 3.9187 | 3.9303 | 3.9457 | 4.1569
2022-06-18 08:00 | 4.0963 | 4.4466 | 4.47 | 4.4987 | 4.5321 | 2.7245 | 3.2519 | 3.2701 | 3.2951 | 2.7245 | 3.5057 | 3.9281 | 3.9445 | 3.9663 | 4.1851
2022-06-18 09:00 | 3.8867 | 4.2357 | 4.2664 | 4.3039 | 4.3477 | 2.6293 | 3.1497 | 3.1736 | 3.2063 | 2.6293 | 2.5911 | 2.922 | 2.9435 | 2.972 | 3.1486
2022-06-18 10:00 | 3.1818 | 3.4893 | 3.5256 | 3.57 | 3.6217 | 1.923 | 2.3233 | 2.3516 | 2.3903 | 1.923 | 1.5433 | 1.7652 | 1.7907 | 1.8244 | 1.9496
2022-06-18 11:00 | 2.5721 | 2.8386 | 2.8771 | 2.9242 | 2.9792 | 1.5115 | 1.8403 | 1.8704 | 1.9113 | 1.5115 | 0.724 | 0.85792 | 0.88488 | 0.92071 | 1.0033
2022-06-18 12:00 | 2.2673 | 2.5101 | 2.548 | 2.5945 | 2.6486 | 1.3527 | 1.652 | 1.6816 | 1.722 | 1.3527 | 0.60968 | 0.73014 | 0.75672 | 0.79205 | 0.86781
2022-06-18 13:00 | 2.172 | 2.4028 | 2.4382 | 2.4815 | 2.532 | 1.3718 | 1.6709 | 1.6985 | 1.7362 | 1.3718 | 0.64779 | 0.76895 | 0.79375 | 0.82671 | 0.90173
2022-06-18 14:00 | 2.2863 | 2.5202 | 2.5528 | 2.5927 | 2.6393 | 1.5295 | 1.8533 | 1.8788 | 1.9135 | 1.5295 | 1.2003 | 1.3791 | 1.402 | 1.4324 | 1.5347
2022-06-18 15:00 | 2.991 | 3.2737 | 3.3045 | 3.3422 | 3.3862 | 1.9759 | 2.378 | 2.4021 | 2.4349 | 1.9759 | 2.1148 | 2.3928 | 2.4144 | 2.4431 | 2.5937
2022-06-18 16:00 | 3.9058 | 4.2556 | 4.2859 | 4.3231 | 4.3664 | 2.6863 | 3.2167 | 3.2404 | 3.2727 | 2.6863 | 3.1056 | 3.4932 | 3.5145 | 3.5427 | 3.7473
2022-06-18 17:00 | 4.6488 | 5.0574 | 5.0896 | 5.129 | 5.1749 | 3.2389 | 3.8721 | 3.8972 | 3.9314 | 3.2389 | 4.7822 | 5.3589 | 5.3814 | 5.4114 | 5.7101
2022-06-18 18:00 | 4.6298 | 5.0443 | 5.0802 | 5.1242 | 5.1755 | 3.258 | 3.8999 | 3.928 | 3.9662 | 3.258 | 4.0772 | 4.5807 | 4.6059 | 4.6393 | 4.9035
2022-06-18 19:00 | 4.6679 | 5.095 | 5.1359 | 5.186 | 5.2444 | 3.277 | 3.9295 | 3.9614 | 4.005 | 3.277 | 4.2868 | 4.8205 | 4.8492 | 4.8873 | 5.1685
2022-06-18 20:00 | 4.5155 | 4.9409 | 4.9868 | 5.0429 | 5.1083 | 3.277 | 3.9366 | 3.9723 | 4.0212 | 3.277 | 4.5536 | 5.1238 | 5.1559 | 5.1986 | 5.5
2022-06-18 21:00 | 4.3059 | 4.7174 | 4.7641 | 4.8212 | 4.8879 | 3.0675 | 3.6902 | 3.7266 | 3.7763 | 3.0675 | 4.1344 | 4.6591 | 4.6918 | 4.7353 | 5.0146
2022-06-18 22:00 | 4.2297 | 4.6296 | 4.6732 | 4.7266 | 4.7889 | 2.8899 | 3.476 | 3.5101 | 3.5565 | 2.8899 | 4.0582 | 4.5702 | 4.6008 | 4.6414 | 4.9131
2022-06-18 23:00 | 3.8296 | 4.1913 | 4.2306 | 4.2787 | 4.3349 | 2.553 | 3.072 | 3.1027 | 3.1446 | 2.553 | 3.0484 | 3.4421 | 3.4697 | 3.5063 | 3.7177
2022-06-19 | 3.4966 | 3.8241 | 3.8586 | 3.9008 | 3.9501 | 2.191 | 2.6375 | 2.6644 | 2.7011 | 2.191 | 3.1246 | 3.5201 | 3.5443 | 3.5764 | 3.7866
2022-06-19 01:00 | 3.3151 | 3.6196 | 3.6492 | 3.6854 | 3.7277 | 2.0767 | 2.4955 | 2.5186 | 2.5501 | 2.0767 | 2.3816 | 2.6876 | 2.7084 | 2.7359 | 2.8998
2022-06-19 02:00 | 3.1437 | 3.4233 | 3.4467 | 3.4754 | 3.5089 | 1.8672 | 2.2391 | 2.2574 | 2.2824 | 1.8672 | 2.2863 | 2.5732 | 2.5896 | 2.6114 | 2.7632
2022-06-19 03:00 | 3.1246 | 3.391 | 3.4084 | 3.4297 | 3.4546 | 1.829 | 2.1855 | 2.1991 | 2.2176 | 1.829 | 2.6864 | 3.0094 | 3.0216 | 3.0378 | 3.2049
2022-06-19 04:00 | 3.2389 | 3.5037 | 3.516 | 3.531 | 3.5485 | 1.9243 | 2.2907 | 2.3003 | 2.3133 | 1.9243 | 2.4578 | 2.7482 | 2.7568 | 2.7682 | 2.917
2022-06-19 05:00 | 3.3163 | 3.5828 | 3.5931 | 3.6056 | 3.6202 | 2.0767 | 2.4679 | 2.4759 | 2.4868 | 2.0767 | 2.8769 | 3.2112 | 3.2184 | 3.2279 | 3.3974
2022-06-19 06:00 | 3.7152 | 4.0148 | 4.0268 | 4.0414 | 4.0584 | 2.3625 | 2.8079 | 2.8173 | 2.83 | 2.3625 | 3.639 | 4.0605 | 4.0688 | 4.0799 | 4.2933
2022-06-19 07:00 | 3.9727 | 4.3005 | 4.3171 | 4.3373 | 4.361 | 2.7245 | 3.2422 | 3.2551 | 3.2728 | 2.7245 | 3.7343 | 4.1728 | 4.1844 | 4.1998 | 4.4235
2022-06-19 08:00 | 3.982 | 4.3238 | 4.3472 | 4.3759 | 4.4093 | 2.7055 | 3.2294 | 3.2476 | 3.2726 | 2.7055 | 4.4202 | 4.9444 | 4.9608 | 4.9826 | 5.2516
2022-06-19 09:00 | 3.6915 | 4.026 | 4.0566 | 4.0942 | 4.138 | 2.5651 | 3.0739 | 3.0979 | 3.1305 | 2.5651 | 3.2389 | 3.6418 | 3.6633 | 3.6919 | 3.9041
2022-06-19 10:00 | 3.1437 | 3.4484 | 3.4846 | 3.529 | 3.5808 | 2.1861 | 2.6341 | 2.6624 | 2.701 | 2.1861 | 2.1148 | 2.4004 | 2.4258 | 2.4596 | 2.6162
2022-06-19 11:00 | 2.6293 | 2.9001 | 2.9385 | 2.9856 | 3.0406 | 1.6286 | 1.9787 | 2.0087 | 2.0497 | 1.6286 | 0.99073 | 1.1543 | 1.1813 | 1.2171 | 1.3144
2022-06-19 12:00 | 2.6483 | 2.9195 | 2.9574 | 3.0039 | 3.058 | 1.6957 | 2.0572 | 2.0868 | 2.1272 | 1.6957 | 0.83831 | 0.98421 | 1.0108 | 1.0461 | 1.1344
2022-06-19 13:00 | 2.5128 | 2.7689 | 2.8043 | 2.8476 | 2.8981 | 1.5052 | 1.8285 | 1.8561 | 1.8938 | 1.5052 | 0.70494 | 0.83247 | 0.85727 | 0.89022 | 0.96839
2022-06-19 14:00 | 2.7055 | 2.9705 | 3.0031 | 3.0431 | 3.0896 | 1.7528 | 2.1171 | 2.1426 | 2.1773 | 1.7528 | 1.7147 | 1.9508 | 1.9736 | 2.004 | 2.1346
2022-06-19 15:00 | 3.1246 | 3.4172 | 3.448 | 3.4857 | 3.5297 | 2.1935 | 2.6351 | 2.6592 | 2.692 | 2.1935 | 2.7245 | 3.0704 | 3.0919 | 3.1206 | 3.3047
2022-06-19 16:00 | 4.2678 | 4.6445 | 4.6749 | 4.712 | 4.7554 | 2.7626 | 3.3068 | 3.3305 | 3.3628 | 2.7626 | 3.5057 | 3.9378 | 3.9591 | 3.9873 | 4.2139
2022-06-19 17:00 | 4.8965 | 5.3235 | 5.3557 | 5.3951 | 5.441 | 3.4866 | 4.1647 | 4.1898 | 4.224 | 3.4866 | 4.4011 | 4.9354 | 4.958 | 4.9879 | 5.2657
2022-06-19 18:00 | 4.9537 | 5.3923 | 5.4282 | 5.4722 | 5.5235 | 3.6009 | 4.3051 | 4.3331 | 4.3714 | 3.6009 | 4.5155 | 5.0677 | 5.0928 | 5.1263 | 5.4145
2022-06-19 19:00 | 4.9537 | 5.402 | 5.4429 | 5.493 | 5.5514 | 3.4866 | 4.1771 | 4.209 | 4.2526 | 3.4866 | 4.7631 | 5.3498 | 5.3785 | 5.4166 | 5.724
2022-06-19 20:00 | 4.8012 | 5.2479 | 5.2938 | 5.3499 | 5.4154 | 3.3723 | 4.0491 | 4.0849 | 4.1337 | 3.3723 | 4.7441 | 5.3355 | 5.3676 | 5.4103 | 5.7222
2022-06-19 21:00 | 4.6298 | 5.0654 | 5.112 | 5.1692 | 5.2358 | 3.2199 | 3.8702 | 3.9066 | 3.9564 | 3.2199 | 4.363 | 4.9132 | 4.9459 | 4.9894 | 5.2812
2022-06-19 22:00 | 4.001 | 4.3839 | 4.4276 | 4.481 | 4.5433 | 2.7618 | 3.3248 | 3.3588 | 3.4053 | 2.7618 | 3.277 | 3.7022 | 3.7327 | 3.7734 | 4.0021
2022-06-19 23:00 | 3.4295 | 3.7614 | 3.8007 | 3.8489 | 3.905 | 2.2801 | 2.7495 | 2.7802 | 2.8221 | 2.2801 | 2.6102 | 2.9552 | 2.9827 | 3.0193 | 3.2066
2022-06-20 | 2.915 | 3.1993 | 3.2338 | 3.276 | 3.3253 | 1.8946 | 2.2873 | 2.3142 | 2.351 | 1.8946 | 2.3435 | 2.652 | 2.6762 | 2.7083 | 2.8756
2022-06-20 01:00 | 2.7055 | 2.9646 | 2.9942 | 3.0304 | 3.0727 | 1.7264 | 2.0816 | 2.1047 | 2.1363 | 1.7264 | 2.0196 | 2.2853 | 2.3061 | 2.3337 | 2.4777
2022-06-20 02:00 | 2.7055 | 2.9525 | 2.9759 | 3.0046 | 3.0381 | 1.6385 | 1.969 | 1.9873 | 2.0123 | 1.6385 | 1.8862 | 2.1286 | 2.145 | 2.1668 | 2.2966
2022-06-20 03:00 | 2.6483 | 2.8793 | 2.8967 | 2.918 | 2.9428 | 1.6957 | 2.028 | 2.0415 | 2.0601 | 1.6957 | 1.9053 | 2.1414 | 2.1536 | 2.1698 | 2.2939
2022-06-20 04:00 | 2.8579 | 3.0943 | 3.1066 | 3.1216 | 3.1391 | 1.7528 | 2.0882 | 2.0977 | 2.1108 | 1.7528 | 2.1339 | 2.3883 | 2.3969 | 2.4083 | 2.5393
2022-06-20 05:00 | 3.2786 | 3.5424 | 3.5526 | 3.5651 | 3.5797 | 2.1638 | 2.5707 | 2.5787 | 2.5896 | 2.1638 | 2.7553 | 3.076 | 3.0832 | 3.0927 | 3.2555
2022-06-20 06:00 | 4.2716 | 4.6125 | 4.6244 | 4.6391 | 4.6561 | 2.9465 | 3.4978 | 3.5071 | 3.5198 | 2.9465 | 4.2297 | 4.7168 | 4.7252 | 4.7363 | 4.9821
2022-06-20 07:00 | 4.9537 | 5.3544 | 5.371 | 5.3913 | 5.4149 | 3.3723 | 4.0075 | 4.0204 | 4.0381 | 3.3723 | 4.4964 | 5.0196 | 5.0313 | 5.0467 | 5.3123
2022-06-20 08:00 | 4.9918 | 5.4087 | 5.4321 | 5.4607 | 5.4941 | 3.1056 | 3.702 | 3.7203 | 3.7452 | 3.1056 | 4.6298 | 5.1773 | 5.1937 | 5.2155 | 5.496
2022-06-20 09:00 | 4.5536 | 4.9521 | 4.9828 | 5.0204 | 5.0641 | 2.5911 | 3.1047 | 3.1286 | 3.1613 | 2.5911 | 2.6293 | 2.9643 | 2.9858 | 3.0144 | 3.1931
2022-06-20 10:00 | 4.4774 | 4.8812 | 4.9175 | 4.9618 | 5.0136 | 2.5911 | 3.1126 | 3.1409 | 3.1795 | 2.5911 | 2.7436 | 3.0991 | 3.1245 | 3.1583 | 3.3495
2022-06-20 11:00 | 3.9327 | 4.3004 | 4.3389 | 4.386 | 4.4409 | 2.2673 | 2.7332 | 2.7632 | 2.8042 | 2.2673 | 2.4006 | 2.7211 | 2.748 | 2.7839 | 2.9587
2022-06-20 12:00 | 3.9629 | 4.3318 | 4.3698 | 4.4162 | 4.4704 | 2.3054 | 2.7774 | 2.807 | 2.8474 | 2.3054 | 2.0767 | 2.3604 | 2.387 | 2.4223 | 2.5787
2022-06-20 13:00 | 3.62 | 3.9584 | 3.9938 | 4.0371 | 4.0876 | 2.191 | 2.6387 | 2.6663 | 2.704 | 2.191 | 1.9243 | 2.1875 | 2.2123 | 2.2452 | 2.3904
2022-06-20 14:00 | 3.6581 | 3.9939 | 4.0266 | 4.0665 | 4.1131 | 2.172 | 2.6123 | 2.6378 | 2.6725 | 2.172 | 2.1529 | 2.4377 | 2.4606 | 2.491 | 2.6457
2022-06-20 15:00 | 3.7724 | 4.1132 | 4.144 | 4.1817 | 4.2256 | 2.3996 | 2.8786 | 2.9027 | 2.9355 | 2.3996 | 2.5149 | 2.8375 | 2.859 | 2.8877 | 3.0603
2022-06-20 16:00 | 4.1523 | 4.5205 | 4.5508 | 4.588 | 4.6313 | 2.8579 | 3.4194 | 3.443 | 3.4754 | 2.8579 | 3.4295 | 3.8531 | 3.8744 | 3.9027 | 4.125
2022-06-20 17:00 | 4.9918 | 5.4259 | 5.458 | 5.4974 | 5.5433 | 3.3533 | 4.0071 | 4.0322 | 4.0665 | 3.3533 | 4.4011 | 4.9354 | 4.958 | 4.9879 | 5.2657
2022-06-20 18:00 | 5.2204 | 5.6788 | 5.7148 | 5.7588 | 5.81 | 3.639 | 4.3501 | 4.3781 | 4.4164 | 3.639 | 6.3445 | 7.1002 | 7.1254 | 7.1588 | 7.5476
2022-06-20 19:00 | 5.1632 | 5.6272 | 5.6681 | 5.7182 | 5.7766 | 3.62 | 4.3347 | 4.3666 | 4.4102 | 3.62 | 4.9537 | 5.5615 | 5.5902 | 5.6283 | 5.9462
2022-06-20 20:00 | 5.015 | 5.4776 | 5.5235 | 5.5796 | 5.6451 | 3.4485 | 4.1391 | 4.1749 | 4.2237 | 3.4485 | 4.6488 | 5.2296 | 5.2618 | 5.3044 | 5.6111
2022-06-20 21:00 | 4.6869 | 5.1268 | 5.1735 | 5.2306 | 5.2972 | 3.1487 | 3.7861 | 3.8225 | 3.8722 | 3.1487 | 4.3821 | 4.9344 | 4.9671 | 5.0105 | 5.3034
2022-06-20 22:00 | 4.0963 | 4.4863 | 4.5299 | 4.5833 | 4.6456 | 2.8184 | 3.3915 | 3.4256 | 3.4721 | 2.8184 | 3.3342 | 3.7657 | 3.7963 | 3.8369 | 4.0688
2022-06-20 23:00 | 3.4676 | 3.8024 | 3.8417 | 3.8898 | 3.946 | 2.2661 | 2.733 | 2.7637 | 2.8055 | 2.2661 | 2.915 | 3.2939 | 3.3215 | 3.3581 | 3.5621
2022-06-21 | 3.1627 | 3.4654 | 3.4999 | 3.5421 | 3.5914 | 1.8953 | 2.2881 | 2.315 | 2.3517 | 1.8953 | 2.8388 | 3.2025 | 3.2267 | 3.2588 | 3.4533
2022-06-21 01:00 | 2.8579 | 3.1283 | 3.1579 | 3.1942 | 3.2365 | 1.7528 | 2.1128 | 2.1359 | 2.1675 | 1.7528 | 2.1529 | 2.4335 | 2.4543 | 2.4819 | 2.6332
2022-06-21 02:00 | 2.8198 | 3.0753 | 3.0988 | 3.1275 | 3.1609 | 1.6576 | 1.9915 | 2.0098 | 2.0348 | 1.6576 | 2.0577 | 2.3191 | 2.3356 | 2.3574 | 2.4966
2022-06-21 03:00 | 2.8388 | 3.084 | 3.1014 | 3.1227 | 3.1475 | 1.6195 | 1.9379 | 1.9515 | 1.97 | 1.6195 | 2.0005 | 2.2472 | 2.2594 | 2.2756 | 2.405
2022-06-21 04:00 | 2.9341 | 3.1762 | 3.1885 | 3.2035 | 3.221 | 1.7338 | 2.0656 | 2.0752 | 2.0883 | 1.7338 | 2.6674 | 2.9811 | 2.9897 | 3.0011 | 3.1614
2022-06-21 05:00 | 3.4104 | 3.684 | 3.6942 | 3.7067 | 3.7213 | 2.0542 | 2.4413 | 2.4493 | 2.4602 | 2.0542 | 2.7626 | 3.0842 | 3.0913 | 3.1009 | 3.2641
2022-06-21 06:00 | 4.3448 | 4.6912 | 4.7031 | 4.7177 | 4.7348 | 2.9977 | 3.5583 | 3.5676 | 3.5803 | 2.9977 | 4.6679 | 5.2038 | 5.2121 | 5.2232 | 5.4931
2022-06-21 07:00 | 5.0108 | 5.4158 | 5.4324 | 5.4527 | 5.4763 | 3.2961 | 3.9174 | 3.9304 | 3.948 | 3.2961 | 4.725 | 5.2737 | 5.2853 | 5.3008 | 5.579
2022-06-21 08:00 | 4.7822 | 5.1835 | 5.2069 | 5.2356 | 5.2689 | 3.258 | 3.8821 | 3.9004 | 3.9253 | 3.258 | 4.0963 | 4.5845 | 4.6009 | 4.6227 | 4.8739
2022-06-21 09:00 | 4.725 | 5.1364 | 5.167 | 5.2046 | 5.2484 | 2.8007 | 3.3523 | 3.3762 | 3.4089 | 2.8007 | 3.5247 | 3.9594 | 3.9809 | 4.0095 | 4.2374
2022-06-21 10:00 | 4.2487 | 4.6356 | 4.6718 | 4.7162 | 4.768 | 2.6864 | 3.2252 | 3.2535 | 3.2921 | 2.6864 | 2.8769 | 3.2473 | 3.2727 | 3.3065 | 3.505
2022-06-21 11:00 | 4.4011 | 4.8037 | 4.8421 | 4.8893 | 4.9442 | 2.534 | 3.0483 | 3.0783 | 3.1193 | 2.534 | 2.896 | 3.2716 | 3.2985 | 3.3343 | 3.5364
2022-06-21 12:00 | 4.2297 | 4.6184 | 4.6563 | 4.7028 | 4.7569 | 2.4578 | 2.9575 | 2.9871 | 3.0275 | 2.4578 | 2.6674 | 3.0167 | 3.0433 | 3.0787 | 3.2675
2022-06-21 13:00 | 4.0772 | 4.4497 | 4.4851 | 4.5284 | 4.5789 | 2.2101 | 2.6612 | 2.6889 | 2.7266 | 2.2101 | 2.3625 | 2.6745 | 2.6993 | 2.7322 | 2.9015
2022-06-21 14:00 | 3.6581 | 3.9939 | 4.0266 | 4.0665 | 4.1131 | 2.0577 | 2.4773 | 2.5027 | 2.5375 | 2.0577 | 2.2291 | 2.5224 | 2.5453 | 2.5757 | 2.7345
2022-06-21 15:00 | 4.3083 | 4.6889 | 4.7197 | 4.7574 | 4.8013 | 2.6922 | 3.2242 | 3.2482 | 3.281 | 2.6922 | 2.8769 | 3.2397 | 3.2613 | 3.29 | 3.4824
2022-06-21 16:00 | 4.6298 | 5.0334 | 5.0638 | 5.1009 | 5.1443 | 3.1056 | 3.712 | 3.7356 | 3.768 | 3.1056 | 4.2487 | 4.7635 | 4.7848 | 4.8131 | 5.0804
2022-06-21 17:00 | 5.4871 | 5.958 | 5.9902 | 6.0296 | 6.0755 | 3.8296 | 4.5698 | 4.5949 | 4.6292 | 3.8296 | 4.9156 | 5.5071 | 5.5296 | 5.5596 | 5.8656
2022-06-21 18:00 | 5.5443 | 6.0268 | 6.0627 | 6.1067 | 6.158 | 3.9248 | 4.6877 | 4.7157 | 4.754 | 3.9248 | 5.0299 | 5.6393 | 5.6645 | 5.6979 | 6.0145
2022-06-21 19:00 | 5.6586 | 6.1594 | 6.2003 | 6.2504 | 6.3088 | 3.8867 | 4.6498 | 4.6817 | 4.7253 | 3.8867 | 5.1823 | 5.8156 | 5.8443 | 5.8824 | 6.2128
2022-06-21 20:00 | 5.5252 | 6.0258 | 6.0716 | 6.1278 | 6.1932 | 3.8486 | 4.6118 | 4.6476 | 4.6964 | 3.8486 | 5.1823 | 5.8225 | 5.8546 | 5.8973 | 6.2332
2022-06-21 21:00 | 4.8775 | 5.3315 | 5.3781 | 5.4353 | 5.5019 | 3.4755 | 4.1722 | 4.2087 | 4.2584 | 3.4755 | 4.1725 | 4.7015 | 4.7342 | 4.7777 | 5.059
2022-06-21 22:00 | 4.2946 | 4.6993 | 4.7429 | 4.7964 | 4.8586 | 2.9963 | 3.6018 | 3.6358 | 3.6823 | 2.9963 | 3.5247 | 3.9774 | 4.008 | 4.0486 | 4.291
2022-06-21 23:00 | 3.639 | 3.9866 | 4.0259 | 4.074 | 4.1302 | 2.3841 | 2.8724 | 2.9031 | 2.945 | 2.3841 | 3.4676 | 3.9079 | 3.9355 | 3.9721 | 4.2065
2022-06-22 | 3.2008 | 3.5063 | 3.5408 | 3.5831 | 3.6323 | 2.0386 | 2.4574 | 2.4843 | 2.5211 | 2.0386 | 2.9913 | 3.3719 | 3.3961 | 3.4282 | 3.6311
2022-06-22 01:00 | 3.0103 | 3.2921 | 3.3217 | 3.3579 | 3.4002 | 1.8481 | 2.2254 | 2.2485 | 2.28 | 1.8481 | 2.2482 | 2.5394 | 2.5602 | 2.5877 | 2.7443
2022-06-22 02:00 | 2.8769 | 3.1367 | 3.1602 | 3.1889 | 3.2223 | 1.7287 | 2.0756 | 2.0939 | 2.1188 | 1.7287 | 2.3054 | 2.5944 | 2.6108 | 2.6326 | 2.7855
2022-06-22 03:00 | 3.0103 | 3.2682 | 3.2856 | 3.3069 | 3.3317 | 1.7528 | 2.0955 | 2.1091 | 2.1276 | 1.7528 | 2.4768 | 2.7765 | 2.7887 | 2.8049 | 2.9605
2022-06-22 04:00 | 3.0294 | 3.2786 | 3.2908 | 3.3058 | 3.3233 | 1.8862 | 2.2457 | 2.2553 | 2.2683 | 1.8862 | 2.6864 | 3.0023 | 3.0109 | 3.0223 | 3.1836
2022-06-22 05:00 | 3.5819 | 3.8682 | 3.8784 | 3.891 | 3.9056 | 2.3864 | 2.8338 | 2.8417 | 2.8526 | 2.3864 | 3.0294 | 3.3806 | 3.3877 | 3.3973 | 3.5752
2022-06-22 06:00 | 4.6398 | 5.0081 | 5.02 | 5.0346 | 5.0517 | 3.3342 | 3.9558 | 3.9652 | 3.9779 | 3.3342 | 4.7631 | 5.3096 | 5.318 | 5.3291 | 5.6042
2022-06-22 07:00 | 5.3157 | 5.7433 | 5.7599 | 5.7802 | 5.8038 | 3.5247 | 4.1875 | 4.2005 | 4.2181 | 3.5247 | 4.8775 | 5.4431 | 5.4547 | 5.4701 | 5.7567
2022-06-22 08:00 | 5.1442 | 5.5724 | 5.5958 | 5.6245 | 5.6579 | 3.3186 | 3.9538 | 3.972 | 3.9969 | 3.3186 | 4.2678 | 4.775 | 4.7914 | 4.8132 | 5.0739
2022-06-22 09:00 | 5.0299 | 5.4639 | 5.4945 | 5.5321 | 5.5759 | 2.9913 | 3.5773 | 3.6013 | 3.6339 | 2.9913 | 3.8105 | 4.277 | 4.2985 | 4.327 | 4.5707
2022-06-22 10:00 | 4.1725 | 4.5537 | 4.59 | 4.6343 | 4.6861 | 2.534 | 3.0451 | 3.0734 | 3.112 | 2.534 | 2.3244 | 2.6333 | 2.6587 | 2.6925 | 2.8606
2022-06-22 11:00 | 3.258 | 3.5755 | 3.614 | 3.6611 | 3.716 | 1.7147 | 2.0804 | 2.1104 | 2.1514 | 1.7147 | 0.83831 | 0.98495 | 1.0119 | 1.0477 | 1.1367
2022-06-22 12:00 | 3.2389 | 3.554 | 3.592 | 3.6384 | 3.6926 | 2.0005 | 2.4173 | 2.4469 | 2.4873 | 2.0005 | 1.8862 | 2.1487 | 2.1753 | 2.2106 | 2.3565
2022-06-22 13:00 | 2.8007 | 3.0782 | 3.1136 | 3.157 | 3.2075 | 1.3908 | 1.6934 | 1.721 | 1.7587 | 1.3908 | 0.62873 | 0.74778 | 0.77258 | 0.80554 | 0.87951
2022-06-22 14:00 | 2.8388 | 3.1138 | 3.1464 | 3.1863 | 3.2329 | 1.6195 | 1.9596 | 1.985 | 2.0198 | 1.6195 | 1.0479 | 1.2097 | 1.2326 | 1.263 | 1.3569
2022-06-22 15:00 | 3.5628 | 3.888 | 3.9188 | 3.9565 | 4.0005 | 2.2968 | 2.7571 | 2.7811 | 2.8139 | 2.2968 | 2.1145 | 2.3924 | 2.414 | 2.4427 | 2.5932
2022-06-22 16:00 | 4.0963 | 4.4603 | 4.4906 | 4.5278 | 4.5711 | 2.8198 | 3.3743 | 3.398 | 3.4304 | 2.8198 | 3.2389 | 3.6414 | 3.6627 | 3.6909 | 3.9028
2022-06-22 17:00 | 4.9727 | 5.4054 | 5.4376 | 5.4769 | 5.5229 | 3.5628 | 4.2547 | 4.2798 | 4.3141 | 3.5628 | 4.6107 | 5.1683 | 5.1909 | 5.2208 | 5.5101
2022-06-22 18:00 | 5.2204 | 5.6788 | 5.7148 | 5.7588 | 5.81 | 3.7152 | 4.4401 | 4.4682 | 4.5064 | 3.7152 | 5.2585 | 5.8934 | 5.9186 | 5.952 | 6.2811
2022-06-22 19:00 | 5.1632 | 5.6272 | 5.6681 | 5.7182 | 5.7766 | 3.9058 | 4.6723 | 4.7042 | 4.7478 | 3.9058 | 4.7822 | 5.371 | 5.3996 | 5.4377 | 5.7462
2022-06-22 20:00 | 5.0108 | 5.4731 | 5.519 | 5.5751 | 5.6405 | 3.6665 | 4.3966 | 4.4324 | 4.4812 | 3.6665 | 5.087 | 5.7166 | 5.7487 | 5.7914 | 6.1221
2022-06-22 21:00 | 4.706 | 5.1472 | 5.1939 | 5.2511 | 5.3177 | 3.5319 | 4.2388 | 4.2753 | 4.325 | 3.5319 | 4.0582 | 4.5744 | 4.6072 | 4.6506 | 4.9257
2022-06-22 22:00 | 4.1344 | 4.5272 | 4.5709 | 4.6243 | 4.6866 | 2.9709 | 3.5718 | 3.6058 | 3.6523 | 2.9709 | 3.3723 | 3.808 | 3.8386 | 3.8792 | 4.1132
2022-06-22 23:00 | 3.4632 | 3.7977 | 3.837 | 3.8851 | 3.9413 | 2.4197 | 2.9144 | 2.9451 | 2.987 | 2.4197 | 2.7118 | 3.0681 | 3.0956 | 3.1323 | 3.3251
2022-06-23 | 2.9768 | 3.2656 | 3.3001 | 3.3424 | 3.3916 | 1.996 | 2.407 | 2.4339 | 2.4707 | 1.996 | 2.3435 | 2.652 | 2.6762 | 2.7083 | 2.8756
2022-06-23 01:00 | 2.7817 | 3.0464 | 3.0761 | 3.1123 | 3.1546 | 1.7383 | 2.0956 | 2.1187 | 2.1503 | 1.7383 | 2.0958 | 2.37 | 2.3908 | 2.4183 | 2.5665
2022-06-23 02:00 | 2.7245 | 2.973 | 2.9964 | 3.0251 | 3.0586 | 1.6044 | 1.9288 | 1.947 | 1.972 | 1.6044 | 2.0005 | 2.2556 | 2.272 | 2.2939 | 2.4299
2022-06-23 03:00 | 2.6293 | 2.8588 | 2.8762 | 2.8975 | 2.9224 | 1.6195 | 1.9379 | 1.9515 | 1.97 | 1.6195 | 1.9434 | 2.1837 | 2.1959 | 2.2121 | 2.3383
2022-06-23 04:00 | 2.7245 | 2.9511 | 2.9633 | 2.9783 | 2.9958 | 1.7159 | 2.0445 | 2.0541 | 2.0672 | 1.7159 | 2.1339 | 2.3883 | 2.3969 | 2.4083 | 2.5393
2022-06-23 05:00 | 3.2199 | 3.4793 | 3.4895 | 3.502 | 3.5166 | 2.1629 | 2.5697 | 2.5777 | 2.5886 | 2.1629 | 2.9722 | 3.3171 | 3.3242 | 3.3338 | 3.5085
2022-06-23 06:00 | 4.0814 | 4.4082 | 4.4201 | 4.4347 | 4.4518 | 3.0484 | 3.6182 | 3.6275 | 3.6402 | 3.0484 | 3.8296 | 4.2722 | 4.2805 | 4.2917 | 4.5155
2022-06-23 07:00 | 4.9918 | 5.3953 | 5.4119 | 5.4322 | 5.4559 | 3.2389 | 3.8499 | 3.8628 | 3.8805 | 3.2389 | 4.5536 | 5.0832 | 5.0948 | 5.1102 | 5.379
2022-06-23 08:00 | 4.5345 | 4.9174 | 4.9408 | 4.9695 | 5.0029 | 2.9913 | 3.567 | 3.5853 | 3.6102 | 2.9913 | 3.639 | 4.0764 | 4.0927 | 4.1145 | 4.3406
2022-06-23 09:00 | 4.1344 | 4.5018 | 4.5325 | 4.57 | 4.6138 | 2.3054 | 2.7671 | 2.791 | 2.8237 | 2.3054 | 2.3054 | 2.6044 | 2.6259 | 2.6544 | 2.8153
2022-06-23 10:00 | 3.7724 | 4.1238 | 4.1601 | 4.2045 | 4.2563 | 2.1148 | 2.5499 | 2.5782 | 2.6168 | 2.1148 | 1.9053 | 2.1675 | 2.1929 | 2.2267 | 2.3718
2022-06-23 11:00 | 3.7343 | 4.0873 | 4.1257 | 4.1728 | 4.2278 | 2.0767 | 2.5081 | 2.5381 | 2.5791 | 2.0767 | 2.0196 | 2.2976 | 2.3246 | 2.3604 | 2.5143
2022-06-23 12:00 | 3.7915 | 4.1476 | 4.1856 | 4.232 | 4.2862 | 2.1148 | 2.5523 | 2.5819 | 2.6223 | 2.1148 | 1.9053 | 2.1699 | 2.1964 | 2.2318 | 2.3787
2022-06-23 13:00 | 3.5819 | 3.9175 | 3.9529 | 3.9962 | 4.0467 | 1.9944 | 2.4065 | 2.4341 | 2.4718 | 1.9944 | 1.7528 | 1.9969 | 2.0217 | 2.0547 | 2.1905
2022-06-23 14:00 | 3.5628 | 3.8916 | 3.9242 | 3.9642 | 4.0107 | 2.1529 | 2.5898 | 2.6152 | 2.65 | 2.1529 | 1.9434 | 2.2048 | 2.2277 | 2.2581 | 2.4012
2022-06-23 15:00 | 3.9058 | 4.2564 | 4.2872 | 4.3249 | 4.3689 | 2.4464 | 2.9338 | 2.9578 | 2.9906 | 2.4464 | 2.8198 | 3.1762 | 3.1978 | 3.2265 | 3.4158
2022-06-23 16:00 | 4.3821 | 4.7673 | 4.7977 | 4.8348 | 4.8782 | 2.9052 | 3.4753 | 3.499 | 3.5313 | 2.9052 | 3.639 | 4.086 | 4.1073 | 4.1356 | 4.3694
2022-06-23 17:00 | 4.8965 | 5.3235 | 5.3557 | 5.3951 | 5.441 | 3.3854 | 4.0451 | 4.0702 | 4.1045 | 3.3854 | 4.4964 | 5.0413 | 5.0638 | 5.0938 | 5.3768
2022-06-23 18:00 | 5.0299 | 5.4742 | 5.5101 | 5.5541 | 5.6054 | 3.6009 | 4.3051 | 4.3331 | 4.3714 | 3.6009 | 4.6107 | 5.1735 | 5.1987 | 5.2322 | 5.5256
2022-06-23 19:00 | 4.9346 | 5.3816 | 5.4225 | 5.4726 | 5.531 | 3.4104 | 4.0871 | 4.119 | 4.1626 | 3.4104 | 4.9346 | 5.5404 | 5.569 | 5.6071 | 5.9239
2022-06-23 20:00 | 4.7822 | 5.2275 | 5.2733 | 5.3295 | 5.3949 | 3.4676 | 4.1616 | 4.1974 | 4.2462 | 3.4676 | 4.6107 | 5.1873 | 5.2194 | 5.2621 | 5.5666
2022-06-23 21:00 | 4.4583 | 4.8811 | 4.9278 | 4.985 | 5.0516 | 3.2008 | 3.8477 | 3.8841 | 3.9338 | 3.2008 | 4.0391 | 4.5533 | 4.586 | 4.6294 | 4.9035
2022-06-23 22:00 | 3.8677 | 4.2406 | 4.2843 | 4.3377 | 4.4 | 2.7242 | 3.2803 | 3.3144 | 3.3608 | 2.7242 | 3.2961 | 3.7233 | 3.7539 | 3.7945 | 4.0243
2022-06-23 23:00 | 3.4295 | 3.7614 | 3.8007 | 3.8489 | 3.905 | 2.2655 | 2.7322 | 2.7629 | 2.8048 | 2.2655 | 2.7245 | 3.0822 | 3.1097 | 3.1464 | 3.3399
2022-06-24 | 3.1246 | 3.4245 | 3.459 | 3.5012 | 3.5505 | 1.9434 | 2.3449 | 2.3718 | 2.4085 | 1.9434 | 2.2673 | 2.5674 | 2.5915 | 2.6237 | 2.7867
2022-06-24 01:00 | 2.6483 | 2.9032 | 2.9328 | 2.969 | 3.0113 | 1.7719 | 2.1353 | 2.1584 | 2.19 | 1.7719 | 2.0767 | 2.3489 | 2.3696 | 2.3972 | 2.5443
2022-06-24 02:00 | 2.5149 | 2.7478 | 2.7713 | 2.7999 | 2.8334 | 1.5623 | 1.879 | 1.8973 | 1.9222 | 1.5623 | 1.8481 | 2.0862 | 2.1027 | 2.1245 | 2.2522
2022-06-24 03:00 | 2.534 | 2.7565 | 2.7739 | 2.7952 | 2.82 | 1.4861 | 1.7804 | 1.7939 | 1.8125 | 1.4861 | 1.9243 | 2.1625 | 2.1747 | 2.1909 | 2.3161
2022-06-24 04:00 | 2.5691 | 2.7841 | 2.7963 | 2.8113 | 2.8288 | 1.5489 | 1.8472 | 1.8568 | 1.8699 | 1.5489 | 1.9815 | 2.2189 | 2.2275 | 2.2389 | 2.3615
2022-06-24 05:00 | 3.0294 | 3.2746 | 3.2848 | 3.2974 | 3.312 | 1.909 | 2.2697 | 2.2777 | 2.2886 | 1.909 | 2.3244 | 2.5972 | 2.6044 | 2.6139 | 2.7531
2022-06-24 06:00 | 3.9003 | 4.2136 | 4.2255 | 4.2401 | 4.2572 | 2.6102 | 3.1005 | 3.1099 | 3.1226 | 2.6102 | 3.8296 | 4.2722 | 4.2805 | 4.2917 | 4.5155
2022-06-24 07:00 | 4.4202 | 4.7813 | 4.7978 | 4.8181 | 4.8418 | 3.0675 | 3.6473 | 3.6603 | 3.6779 | 3.0675 | 3.9248 | 4.3845 | 4.3961 | 4.4115 | 4.6457
2022-06-24 08:00 | 5.5824 | 6.0432 | 6.0666 | 6.0953 | 6.1286 | 2.9449 | 3.5123 | 3.5305 | 3.5554 | 2.9449 | 4.1154 | 4.6057 | 4.6221 | 4.6438 | 4.8961
2022-06-24 09:00 | 5.7539 | 6.2417 | 6.2724 | 6.3099 | 6.3537 | 2.8388 | 3.3973 | 3.4212 | 3.4539 | 2.8388 | 3.1627 | 3.5571 | 3.5786 | 3.6072 | 3.8152
2022-06-24 10:00 | 5.449 | 5.9251 | 5.9614 | 6.0058 | 6.0575 | 2.5911 | 3.1126 | 3.1409 | 3.1795 | 2.5911 | 2.8769 | 3.2473 | 3.2727 | 3.3065 | 3.505
2022-06-24 11:00 | 4.0391 | 4.4148 | 4.4532 | 4.5003 | 4.5553 | 2.4768 | 2.9807 | 3.0108 | 3.0517 | 2.4768 | 2.7817 | 3.1445 | 3.1715 | 3.2073 | 3.4031
2022-06-24 12:00 | 3.982 | 4.3523 | 4.3902 | 4.4367 | 4.4908 | 2.3625 | 2.8449 | 2.8745 | 2.9149 | 2.3625 | 2.8007 | 3.1649 | 3.1915 | 3.2269 | 3.4231
2022-06-24 13:00 | 3.8486 | 4.204 | 4.2394 | 4.2828 | 4.3333 | 2.2673 | 2.7288 | 2.7564 | 2.7941 | 2.2673 | 2.4768 | 2.8015 | 2.8263 | 2.8592 | 3.0348
2022-06-24 14:00 | 3.62 | 3.953 | 3.9856 | 4.0256 | 4.0722 | 2.172 | 2.6123 | 2.6378 | 2.6725 | 2.172 | 2.3435 | 2.6495 | 2.6723 | 2.7027 | 2.8679
2022-06-24 15:00 | 3.8486 | 4.195 | 4.2258 | 4.2635 | 4.3075 | 2.3816 | 2.8573 | 2.8813 | 2.9141 | 2.3816 | 3.1246 | 3.515 | 3.5366 | 3.5652 | 3.7713
2022-06-24 16:00 | 4.0201 | 4.3784 | 4.4088 | 4.4459 | 4.4893 | 2.6667 | 3.1936 | 3.2172 | 3.2496 | 2.6667 | 3.258 | 3.6626 | 3.6838 | 3.7121 | 3.925
2022-06-24 17:00 | 4.5726 | 4.9755 | 5.0077 | 5.0471 | 5.093 | 3.0103 | 3.602 | 3.6271 | 3.6614 | 3.0103 | 4.0772 | 4.5755 | 4.598 | 4.628 | 4.8879
2022-06-24 18:00 | 4.5345 | 4.942 | 4.9779 | 5.0219 | 5.0732 | 3.1246 | 3.7424 | 3.7704 | 3.8087 | 3.1246 | 4.1916 | 4.7077 | 4.7329 | 4.7664 | 5.0368
2022-06-24 19:00 | 4.344 | 4.747 | 4.7879 | 4.838 | 4.8964 | 3.0484 | 3.6594 | 3.6913 | 3.7349 | 3.0484 | 4.6679 | 5.2439 | 5.2726 | 5.3107 | 5.6129
2022-06-24 20:00 | 4.1916 | 4.5929 | 4.6388 | 4.6949 | 4.7604 | 3.1437 | 3.779 | 3.8148 | 3.8636 | 3.1437 | 3.7724 | 4.2557 | 4.2878 | 4.3305 | 4.589
2022-06-24 21:00 | 4.001 | 4.3899 | 4.4366 | 4.4937 | 4.5604 | 2.8668 | 3.453 | 3.4895 | 3.5392 | 2.8668 | 3.8867 | 4.3839 | 4.4166 | 4.4601 | 4.7257
2022-06-24 22:00 | 3.6581 | 4.0155 | 4.0591 | 4.1126 | 4.1749 | 2.5852 | 3.1161 | 3.1501 | 3.1966 | 2.5852 | 3.277 | 3.7022 | 3.7327 | 3.7734 | 4.0021
2022-06-24 23:00 | 3.256 | 3.575 | 3.6144 | 3.6625 | 3.7186 | 2.191 | 2.6443 | 2.675 | 2.7169 | 2.191 | 2.6102 | 2.9552 | 2.9827 | 3.0193 | 3.2066
2022-06-25 | 2.8863 | 3.1684 | 3.2029 | 3.2452 | 3.2944 | 1.9243 | 2.3224 | 2.3493 | 2.386 | 1.9243 | 2.5149 | 2.8426 | 2.8668 | 2.8989 | 3.0756
2022-06-25 01:00 | 2.6864 | 2.9441 | 2.9737 | 3.01 | 3.0522 | 1.645 | 1.9854 | 2.0085 | 2.0401 | 1.645 | 1.9053 | 2.1583 | 2.1791 | 2.2066 | 2.3443
2022-06-25 02:00 | 2.4578 | 2.6864 | 2.7098 | 2.7385 | 2.772 | 1.5052 | 1.8115 | 1.8297 | 1.8547 | 1.5052 | 1.8481 | 2.0862 | 2.1027 | 2.1245 | 2.2522
2022-06-25 03:00 | 2.4578 | 2.6746 | 2.692 | 2.7133 | 2.7381 | 1.467 | 1.7579 | 1.7714 | 1.79 | 1.467 | 1.7528 | 1.972 | 1.9842 | 2.0004 | 2.1161
2022-06-25 04:00 | 2.4578 | 2.6645 | 2.6768 | 2.6918 | 2.7093 | 1.4861 | 1.773 | 1.7826 | 1.7957 | 1.4861 | 1.9053 | 2.1342 | 2.1428 | 2.1542 | 2.2726
2022-06-25 05:00 | 2.8007 | 3.029 | 3.0392 | 3.0517 | 3.0663 | 1.7125 | 2.0376 | 2.0456 | 2.0565 | 1.7125 | 2.0577 | 2.3008 | 2.308 | 2.3175 | 2.442
2022-06-25 06:00 | 3.1246 | 3.3803 | 3.3922 | 3.4068 | 3.4239 | 2.1062 | 2.5052 | 2.5145 | 2.5272 | 2.1062 | 2.7055 | 3.023 | 3.0314 | 3.0425 | 3.2045
2022-06-25 07:00 | 3.5438 | 3.8397 | 3.8563 | 3.8766 | 3.9002 | 2.3244 | 2.7695 | 2.7825 | 2.8001 | 2.3244 | 3.4485 | 3.8552 | 3.8668 | 3.8822 | 4.0903
2022-06-25 08:00 | 3.4485 | 3.7507 | 3.7741 | 3.8027 | 3.8361 | 2.4387 | 2.9143 | 2.9325 | 2.9574 | 2.4387 | 2.7436 | 3.0813 | 3.0976 | 3.1194 | 3.2963
2022-06-25 09:00 | 2.9531 | 3.2327 | 3.2634 | 3.301 | 3.3447 | 1.9946 | 2.3999 | 2.4239 | 2.4565 | 1.9946 | 1.9815 | 2.2445 | 2.2659 | 2.2945 | 2.4376
2022-06-25 10:00 | 2.5149 | 2.7729 | 2.8092 | 2.8535 | 2.9053 | 1.5242 | 1.8522 | 1.8805 | 1.9191 | 1.5242 | 1.467 | 1.6806 | 1.706 | 1.7397 | 1.8607
2022-06-25 11:00 | 2.4387 | 2.6954 | 2.7338 | 2.7809 | 2.8359 | 1.28 | 1.5669 | 1.5969 | 1.6379 | 1.28 | 0.724 | 0.85792 | 0.88488 | 0.92071 | 1.0033
2022-06-25 12:00 | 2.6293 | 2.899 | 2.9369 | 2.9834 | 3.0375 | 1.2765 | 1.562 | 1.5916 | 1.632 | 1.2765 | 0.80021 | 0.94186 | 0.96845 | 1.0038 | 1.09
2022-06-25 13:00 | 2.0767 | 2.3004 | 2.3358 | 2.3791 | 2.4297 | 1.3718 | 1.6709 | 1.6985 | 1.7362 | 1.3718 | 0.81926 | 0.9595 | 0.9843 | 1.0173 | 1.1017
2022-06-25 14:00 | 2.1529 | 2.3769 | 2.4095 | 2.4495 | 2.496 | 1.4099 | 1.712 | 1.7374 | 1.7722 | 1.4099 | 0.78115 | 0.91333 | 0.93619 | 0.96657 | 1.0459
2022-06-25 15:00 | 2.7626 | 3.0283 | 3.0591 | 3.0968 | 3.1408 | 1.8351 | 2.2117 | 2.2358 | 2.2686 | 1.8351 | 1.7719 | 2.0117 | 2.0333 | 2.062 | 2.1937
2022-06-25 16:00 | 3.6581 | 3.9895 | 4.0198 | 4.057 | 4.1003 | 2.5149 | 3.0142 | 3.0379 | 3.0702 | 2.5149 | 2.8388 | 3.1968 | 3.2181 | 3.2463 | 3.4362
2022-06-25 17:00 | 4.3821 | 4.7708 | 4.803 | 4.8424 | 4.8883 | 3.0865 | 3.692 | 3.7171 | 3.7514 | 3.0865 | 3.9248 | 4.4061 | 4.4286 | 4.4586 | 4.7102
2022-06-25 18:00 | 4.4964 | 4.901 | 4.937 | 4.9809 | 5.0322 | 3.2199 | 3.8549 | 3.8829 | 3.9212 | 3.2199 | 4.344 | 4.8771 | 4.9023 | 4.9357 | 5.2145
2022-06-25 19:00 | 4.3249 | 4.7266 | 4.7675 | 4.8175 | 4.8759 | 3.1131 | 3.7359 | 3.7678 | 3.8113 | 3.1131 | 4.725 | 5.3075 | 5.3361 | 5.3742 | 5.6795
2022-06-25 20:00 | 4.4392 | 4.859 | 4.9049 | 4.961 | 5.0265 | 3.1437 | 3.779 | 3.8148 | 3.8636 | 3.1437 | 4.0201 | 4.5309 | 4.5631 | 4.6058 | 4.8778
2022-06-25 21:00 | 4.2106 | 4.615 | 4.6617 | 4.7189 | 4.7855 | 3.0484 | 3.6676 | 3.7041 | 3.7538 | 3.0484 | 3.8677 | 4.3627 | 4.3954 | 4.4389 | 4.7035
2022-06-25 22:00 | 3.8867 | 4.2611 | 4.3048 | 4.3582 | 4.4205 | 2.9913 | 3.5958 | 3.6298 | 3.6763 | 2.9913 | 3.6771 | 4.1468 | 4.1774 | 4.218 | 4.4687
2022-06-25 23:00 | 3.639 | 3.9866 | 4.0259 | 4.074 | 4.1302 | 2.4857 | 2.9924 | 3.0231 | 3.065 | 2.4857 | 3.258 | 3.675 | 3.7026 | 3.7392 | 3.9621
2022-06-26 | 3.258 | 3.5677 | 3.6023 | 3.6445 | 3.6937 | 2.1429 | 2.5806 | 2.6075 | 2.6442 | 2.1429 | 2.553 | 2.8849 | 2.9091 | 2.9412 | 3.12
2022-06-26 01:00 | 2.9531 | 3.2307 | 3.2603 | 3.2965 | 3.3388 | 1.9284 | 2.3203 | 2.3434 | 2.3749 | 1.9284 | 2.3435 | 2.6453 | 2.666 | 2.6936 | 2.8554
2022-06-26 02:00 | 2.9341 | 3.1981 | 3.2216 | 3.2503 | 3.2837 | 1.829 | 2.1941 | 2.2124 | 2.2374 | 1.829 | 2.2482 | 2.5308 | 2.5473 | 2.5691 | 2.7188
2022-06-26 03:00 | 2.7974 | 3.0395 | 3.0569 | 3.0782 | 3.103 | 1.7147 | 2.0505 | 2.064 | 2.0826 | 1.7147 | 1.9815 | 2.2261 | 2.2383 | 2.2545 | 2.3828
2022-06-26 04:00 | 2.8198 | 3.0534 | 3.0657 | 3.0807 | 3.0982 | 1.6766 | 1.9981 | 2.0077 | 2.0207 | 1.6766 | 1.9815 | 2.2189 | 2.2275 | 2.2389 | 2.3615
2022-06-26 05:00 | 2.9913 | 3.2337 | 3.2439 | 3.2564 | 3.271 | 1.8312 | 2.1778 | 2.1858 | 2.1967 | 1.8312 | 2.3054 | 2.576 | 2.5832 | 2.5927 | 2.7309
2022-06-26 06:00 | 3.2389 | 3.5031 | 3.515 | 3.5296 | 3.5467 | 2.0577 | 2.4478 | 2.4571 | 2.4698 | 2.0577 | 2.7626 | 3.0865 | 3.0949 | 3.106 | 3.2712
2022-06-26 07:00 | 3.4676 | 3.7578 | 3.7744 | 3.7947 | 3.8183 | 2.4006 | 2.8596 | 2.8725 | 2.8902 | 2.4006 | 3.0675 | 3.4317 | 3.4433 | 3.4588 | 3.6459
2022-06-26 08:00 | 3.4676 | 3.7712 | 3.7946 | 3.8232 | 3.8566 | 2.4578 | 2.9368 | 2.955 | 2.98 | 2.4578 | 2.9722 | 3.3353 | 3.3517 | 3.3735 | 3.5629
2022-06-26 09:00 | 3.1246 | 3.417 | 3.4476 | 3.4852 | 3.529 | 2.1427 | 2.5749 | 2.5988 | 2.6315 | 2.1427 | 2.2679 | 2.5628 | 2.5843 | 2.6128 | 2.7717
2022-06-26 10:00 | 2.534 | 2.7934 | 2.8296 | 2.874 | 2.9258 | 1.6004 | 1.9422 | 1.9705 | 2.0091 | 1.6004 | 1.2575 | 1.4477 | 1.4731 | 1.5068 | 1.6163
2022-06-26 11:00 | 2.8198 | 3.1047 | 3.1432 | 3.1903 | 3.2453 | 1.6004 | 1.9454 | 1.9754 | 2.0164 | 1.6004 | 0.89547 | 1.0485 | 1.0754 | 1.1113 | 1.2033
2022-06-26 12:00 | 2.8388 | 3.1242 | 3.1621 | 3.2085 | 3.2627 | 1.4861 | 1.8096 | 1.8392 | 1.8796 | 1.4861 | 1.5242 | 1.7464 | 1.773 | 1.8083 | 1.9344
2022-06-26 13:00 | 2.7817 | 3.0578 | 3.0932 | 3.1365 | 3.187 | 1.467 | 1.7834 | 1.8111 | 1.8487 | 1.467 | 1.1813 | 1.3618 | 1.3866 | 1.4195 | 1.5239
2022-06-26 14:00 | 2.6742 | 2.9369 | 2.9696 | 3.0095 | 3.0561 | 1.6195 | 1.9596 | 1.985 | 2.0198 | 1.6195 | 2.0005 | 2.2683 | 2.2912 | 2.3216 | 2.4679
2022-06-26 15:00 | 3.1193 | 3.4115 | 3.4423 | 3.48 | 3.524 | 2.0343 | 2.447 | 2.471 | 2.5038 | 2.0343 | 2.7055 | 3.0492 | 3.0708 | 3.0994 | 3.2825
2022-06-26 16:00 | 4.0055 | 4.3627 | 4.3931 | 4.4303 | 4.4736 | 2.7533 | 3.2958 | 3.3195 | 3.3518 | 2.7533 | 3.3363 | 3.7496 | 3.7708 | 3.7991 | 4.0163
2022-06-26 17:00 | 4.7822 | 5.2007 | 5.2329 | 5.2723 | 5.3182 | 3.5438 | 4.2322 | 4.2573 | 4.2916 | 3.5438 | 4.3059 | 4.8296 | 4.8521 | 4.882 | 5.1546
2022-06-26 18:00 | 5.0299 | 5.4742 | 5.5101 | 5.5541 | 5.6054 | 3.5628 | 4.2601 | 4.2881 | 4.3264 | 3.5628 | 4.3249 | 4.8559 | 4.8811 | 4.9146 | 5.1923
2022-06-26 19:00 | 4.9918 | 5.443 | 5.4839 | 5.534 | 5.5924 | 3.5438 | 4.2446 | 4.2766 | 4.3201 | 3.5438 | 4.344 | 4.884 | 4.9127 | 4.9508 | 5.2351
2022-06-26 20:00 | 4.9537 | 5.4117 | 5.4576 | 5.5137 | 5.5791 | 3.4485 | 4.1391 | 4.1749 | 4.2237 | 3.4485 | 4.5917 | 5.1661 | 5.1982 | 5.2409 | 5.5444
2022-06-26 21:00 | 4.5536 | 4.9835 | 5.0302 | 5.0873 | 5.154 | 3.3151 | 3.9828 | 4.0192 | 4.0689 | 3.3151 | 3.6771 | 4.151 | 4.1837 | 4.2272 | 4.4813
2022-06-26 22:00 | 4.0305 | 4.4155 | 4.4592 | 4.5126 | 4.5749 | 2.7876 | 3.3552 | 3.3892 | 3.4357 | 2.7876 | 3.1246 | 3.5328 | 3.5634 | 3.604 | 3.8244
2022-06-26 23:00 | 3.3914 | 3.7205 | 3.7598 | 3.808 | 3.8641 | 2.3343 | 2.8136 | 2.8442 | 2.8861 | 2.3343 | 2.5911 | 2.934 | 2.9615 | 2.9982 | 3.1844
2022-06-27 | 3.0294 | 3.3221 | 3.3566 | 3.3989 | 3.4481 | 1.9111 | 2.3068 | 2.3337 | 2.3705 | 1.9111 | 2.2101 | 2.5038 | 2.528 | 2.5601 | 2.7201
2022-06-27 01:00 | 2.8007 | 3.0669 | 3.0965 | 3.1328 | 3.1751 | 1.6498 | 1.9911 | 2.0142 | 2.0457 | 1.6498 | 1.9624 | 2.2218 | 2.2426 | 2.2701 | 2.411
2022-06-27 02:00 | 2.7245 | 2.973 | 2.9964 | 3.0251 | 3.0586 | 1.5814 | 1.9015 | 1.9198 | 1.9448 | 1.5814 | 2.0386 | 2.2979 | 2.3144 | 2.3362 | 2.4744
2022-06-27 03:00 | 2.7626 | 3.0021 | 3.0195 | 3.0408 | 3.0656 | 1.5433 | 1.8479 | 1.8615 | 1.88 | 1.5433 | 2.5911 | 2.9036 | 2.9158 | 2.932 | 3.0938
2022-06-27 04:00 | 2.9341 | 3.1762 | 3.1885 | 3.2035 | 3.221 | 1.7147 | 2.0431 | 2.0527 | 2.0658 | 1.7147 | 2.191 | 2.4518 | 2.4604 | 2.4718 | 2.6059
2022-06-27 05:00 | 3.4866 | 3.7659 | 3.7761 | 3.7886 | 3.8032 | 2.044 | 2.4293 | 2.4373 | 2.4482 | 2.044 | 2.7747 | 3.0976 | 3.1047 | 3.1143 | 3.2782
2022-06-27 06:00 | 4.344 | 4.6903 | 4.7022 | 4.7168 | 4.7339 | 2.875 | 3.4134 | 3.4227 | 3.4354 | 2.875 | 3.9248 | 4.378 | 4.3864 | 4.3975 | 4.6266
2022-06-27 07:00 | 4.9537 | 5.3544 | 5.371 | 5.3913 | 5.4149 | 3.2961 | 3.9174 | 3.9304 | 3.948 | 3.2961 | 4.4202 | 4.935 | 4.9466 | 4.962 | 5.2235
2022-06-27 08:00 | 4.7441 | 5.1426 | 5.166 | 5.1946 | 5.228 | 3.1174 | 3.7161 | 3.7343 | 3.7593 | 3.1174 | 3.7915 | 4.2457 | 4.2621 | 4.2839 | 4.5184
2022-06-27 09:00 | 4.1916 | 4.5632 | 4.5939 | 4.6314 | 4.6752 | 2.2863 | 2.7446 | 2.7685 | 2.8012 | 2.2863 | 2.3244 | 2.6256 | 2.647 | 2.6756 | 2.8375
2022-06-27 10:00 | 3.5057 | 3.8373 | 3.8735 | 3.9179 | 3.9697 | 1.6957 | 2.0548 | 2.083 | 2.1217 | 1.6957 | 1.1813 | 1.363 | 1.3884 | 1.4221 | 1.5275
2022-06-27 11:00 | 3.0675 | 3.3708 | 3.4093 | 3.4564 | 3.5113 | 1.5814 | 1.9229 | 1.9529 | 1.9939 | 1.5814 | 1.1622 | 1.3449 | 1.3718 | 1.4077 | 1.5144
2022-06-27 12:00 | 3.2389 | 3.554 | 3.592 | 3.6384 | 3.6926 | 1.448 | 1.7646 | 1.7942 | 1.8346 | 1.448 | 0.60968 | 0.73014 | 0.75672 | 0.79205 | 0.86781
2022-06-27 13:00 | 3.2008 | 3.5081 | 3.5435 | 3.5868 | 3.6373 | 1.4861 | 1.8059 | 1.8336 | 1.8713 | 1.4861 | 0.60968 | 0.72661 | 0.75141 | 0.78436 | 0.85729
2022-06-27 14:00 | 2.9913 | 3.2775 | 3.3102 | 3.3501 | 3.3967 | 1.6217 | 1.9622 | 1.9877 | 2.0224 | 1.6217 | 0.74305 | 0.87098 | 0.89385 | 0.92423 | 1.0014
2022-06-27 15:00 | 3.6009 | 3.9289 | 3.9597 | 3.9974 | 4.0414 | 2.2056 | 2.6494 | 2.6735 | 2.7063 | 2.2056 | 1.9624 | 2.2235 | 2.245 | 2.2737 | 2.4159
2022-06-27 16:00 | 4.5917 | 4.9925 | 5.0228 | 5.06 | 5.1033 | 2.9273 | 3.5013 | 3.525 | 3.5573 | 2.9273 | 3.8677 | 4.3401 | 4.3614 | 4.3896 | 4.636
2022-06-27 17:00 | 5.6967 | 6.1832 | 6.2154 | 6.2548 | 6.3007 | 3.8296 | 4.5698 | 4.5949 | 4.6292 | 3.8296 | 5.068 | 5.6764 | 5.699 | 5.7289 | 6.0434
2022-06-27 18:00 | 5.6777 | 6.1701 | 6.206 | 6.25 | 6.3013 | 3.8867 | 4.6427 | 4.6707 | 4.709 | 3.8867 | 5.9444 | 6.6556 | 6.6808 | 6.7142 | 7.081
2022-06-27 19:00 | 5.4871 | 5.9752 | 6.0161 | 6.0662 | 6.1246 | 4.1344 | 4.9424 | 4.9743 | 5.0179 | 4.1344 | 5.2776 | 5.9215 | 5.9501 | 5.9882 | 6.3239
2022-06-27 20:00 | 5.3538 | 5.8415 | 5.8874 | 5.9435 | 6.009 | 4.0582 | 4.8594 | 4.8951 | 4.944 | 4.0582 | 6.3826 | 7.1563 | 7.1884 | 7.2311 | 7.633
2022-06-27 21:00 | 5.0108 | 5.4747 | 5.5214 | 5.5786 | 5.6452 | 3.6073 | 4.3279 | 4.3643 | 4.414 | 3.6073 | 4.8393 | 5.4425 | 5.4752 | 5.5187 | 5.8367
2022-06-27 22:00 | 4.4011 | 4.8138 | 4.8574 | 4.9108 | 4.9731 | 3.1364 | 3.7673 | 3.8013 | 3.8478 | 3.1364 | 3.9074 | 4.4027 | 4.4333 | 4.4739 | 4.7373
2022-06-27 23:00 | 3.8486 | 4.2117 | 4.2511 | 4.2992 | 4.3553 | 2.5865 | 3.1115 | 3.1422 | 3.1841 | 2.5865 | 3.2199 | 3.6327 | 3.6602 | 3.6968 | 3.9176
2022-06-28 | 3.4104 | 3.7315 | 3.766 | 3.8082 | 3.8575 | 2.1283 | 2.5633 | 2.5903 | 2.627 | 2.1283 | 2.7055 | 3.0543 | 3.0785 | 3.1106 | 3.2978
2022-06-28 01:00 | 3.1056 | 3.3944 | 3.424 | 3.4603 | 3.5026 | 1.9243 | 2.3154 | 2.3385 | 2.37 | 1.9243 | 2.4578 | 2.7723 | 2.793 | 2.8206 | 2.9887
2022-06-28 02:00 | 3.2008 | 3.4847 | 3.5081 | 3.5368 | 3.5703 | 1.829 | 2.1941 | 2.2124 | 2.2374 | 1.829 | 2.6864 | 3.0178 | 3.0342 | 3.0561 | 3.2298
2022-06-28 03:00 | 3.1071 | 3.3721 | 3.3895 | 3.4108 | 3.4357 | 1.9183 | 2.2909 | 2.3045 | 2.3231 | 1.9183 | 2.5721 | 2.8824 | 2.8946 | 2.9108 | 3.0716
2022-06-28 04:00 | 3.3809 | 3.6562 | 3.6685 | 3.6835 | 3.701 | 2.0577 | 2.4483 | 2.4578 | 2.4709 | 2.0577 | 2.8579 | 3.1928 | 3.2014 | 3.2128 | 3.3836
2022-06-28 05:00 | 3.8296 | 4.1343 | 4.1445 | 4.1571 | 4.1717 | 2.5469 | 3.0233 | 3.0313 | 3.0422 | 2.5469 | 3.5057 | 3.9099 | 3.9171 | 3.9266 | 4.1307
2022-06-28 06:00 | 4.8965 | 5.2839 | 5.2958 | 5.3104 | 5.3275 | 3.4866 | 4.1359 | 4.1452 | 4.1579 | 3.4866 | 4.5536 | 5.0767 | 5.0851 | 5.0962 | 5.3598
2022-06-28 07:00 | 5.5443 | 5.9889 | 6.0055 | 6.0258 | 6.0495 | 3.7534 | 4.4576 | 4.4706 | 4.4882 | 3.7534 | 5.792 | 6.4594 | 6.471 | 6.4864 | 6.8233
2022-06-28 08:00 | 5.3347 | 5.7771 | 5.8005 | 5.8292 | 5.8625 | 3.5519 | 4.2293 | 4.2475 | 4.2724 | 3.5519 | 4.7441 | 5.3043 | 5.3207 | 5.3425 | 5.6294
2022-06-28 09:00 | 4.6107 | 5.0135 | 5.0442 | 5.0818 | 5.1255 | 2.8639 | 3.4269 | 3.4508 | 3.4835 | 2.8639 | 3.1246 | 3.5148 | 3.5363 | 3.5648 | 3.7708
2022-06-28 10:00 | 4.1725 | 4.5537 | 4.59 | 4.6343 | 4.6861 | 2.2863 | 2.7525 | 2.7808 | 2.8194 | 2.2863 | 2.1529 | 2.4428 | 2.4682 | 2.5019 | 2.6607
2022-06-28 11:00 | 3.587 | 3.929 | 3.9675 | 4.0146 | 4.0695 | 1.8146 | 2.1984 | 2.2284 | 2.2694 | 1.8146 | 1.2761 | 1.4714 | 1.4984 | 1.5342 | 1.6472
2022-06-28 12:00 | 3.0865 | 3.3903 | 3.4282 | 3.4746 | 3.5288 | 1.5937 | 1.9367 | 1.9663 | 2.0067 | 1.5937 | 0.68589 | 0.81483 | 0.84141 | 0.87674 | 0.95669
2022-06-28 13:00 | 2.8388 | 3.1192 | 3.1546 | 3.1979 | 3.2484 | 1.4289 | 1.7384 | 1.766 | 1.8037 | 1.4289 | 0.57158 | 0.68426 | 0.70906 | 0.74202 | 0.81285
2022-06-28 14:00 | 2.9722 | 3.257 | 3.2897 | 3.3296 | 3.3762 | 1.6166 | 1.9562 | 1.9817 | 2.0165 | 1.6166 | 0.97168 | 1.125 | 1.1479 | 1.1783 | 1.268
2022-06-28 15:00 | 3.5819 | 3.9085 | 3.9393 | 3.977 | 4.0209 | 2.1017 | 2.5266 | 2.5507 | 2.5835 | 2.1017 | 2.0767 | 2.3505 | 2.3721 | 2.4008 | 2.5492
2022-06-28 16:00 | 4.4964 | 4.8901 | 4.9205 | 4.9576 | 5.001 | 2.7845 | 3.3326 | 3.3563 | 3.3886 | 2.7845 | 3.4295 | 3.8531 | 3.8744 | 3.9027 | 4.125
2022-06-28 17:00 | 5.5633 | 6.0399 | 6.0721 | 6.1115 | 6.1574 | 3.7682 | 4.4973 | 4.5224 | 4.5567 | 3.7682 | 5.2204 | 5.8458 | 5.8684 | 5.8983 | 6.2211
2022-06-28 18:00 | 5.7729 | 6.2724 | 6.3084 | 6.3524 | 6.4036 | 4.1344 | 4.9353 | 4.9633 | 5.0016 | 4.1344 | 5.3728 | 6.0204 | 6.0456 | 6.079 | 6.4144
2022-06-28 19:00 | 5.9253 | 6.4459 | 6.4869 | 6.5369 | 6.5953 | 4.1154 | 4.9199 | 4.9518 | 4.9954 | 4.1154 | 5.811 | 6.5143 | 6.543 | 6.581 | 6.946
2022-06-28 20:00 | 5.7539 | 6.2714 | 6.3173 | 6.3734 | 6.4388 | 4.1154 | 4.9269 | 4.9627 | 5.0115 | 4.1154 | 6.1349 | 6.8811 | 6.9132 | 6.9559 | 7.3442
2022-06-28 21:00 | 5.3538 | 5.8432 | 5.8899 | 5.947 | 6.0137 | 3.9086 | 4.6839 | 4.7203 | 4.77 | 3.9086 | 4.8584 | 5.4637 | 5.4964 | 5.5399 | 5.8589
2022-06-28 22:00 | 4.6869 | 5.1208 | 5.1645 | 5.2179 | 5.2802 | 3.4135 | 4.0946 | 4.1287 | 4.1752 | 3.4135 | 4.0772 | 4.5914 | 4.622 | 4.6626 | 4.9353
2022-06-28 23:00 | 4.0483 | 4.4262 | 4.4656 | 4.5137 | 4.5699 | 2.7771 | 3.3367 | 3.3673 | 3.4092 | 2.7771 | 3.6009 | 4.0561 | 4.0837 | 4.1203 | 4.362
2022-06-29 | 3.6009 | 3.9362 | 3.9707 | 4.0129 | 4.0622 | 2.3435 | 2.8175 | 2.8444 | 2.8812 | 2.3435 | 3.2008 | 3.6048 | 3.629 | 3.6611 | 3.8755
2022-06-29 01:00 | 3.318 | 3.6226 | 3.6523 | 3.6885 | 3.7308 | 2.1339 | 2.563 | 2.5861 | 2.6176 | 2.1339 | 3.1627 | 3.5557 | 3.5764 | 3.604 | 3.8108
2022-06-29 02:00 | 3.3151 | 3.6075 | 3.6309 | 3.6596 | 3.6931 | 2.0196 | 2.4192 | 2.4375 | 2.4624 | 2.0196 | 2.6864 | 3.0178 | 3.0342 | 3.0561 | 3.2298
2022-06-29 03:00 | 3.3151 | 3.5957 | 3.6131 | 3.6344 | 3.6592 | 2.0005 | 2.3881 | 2.4017 | 2.4202 | 2.0005 | 2.6864 | 3.0094 | 3.0216 | 3.0378 | 3.2049
2022-06-29 04:00 | 3.5438 | 3.8312 | 3.8435 | 3.8585 | 3.876 | 2.1395 | 2.545 | 2.5545 | 2.5676 | 2.1395 | 2.9722 | 3.3199 | 3.3285 | 3.3399 | 3.5169
2022-06-29 05:00 | 4.0772 | 4.4004 | 4.4106 | 4.4231 | 4.4378 | 2.6835 | 3.1848 | 3.1927 | 3.2036 | 2.6835 | 3.7343 | 4.164 | 4.1711 | 4.1806 | 4.3973
2022-06-29 06:00 | 5.068 | 5.4681 | 5.48 | 5.4947 | 5.5117 | 3.5391 | 4.198 | 4.2073 | 4.22 | 3.5391 | 4.9537 | 5.5213 | 5.5297 | 5.5408 | 5.8264
2022-06-29 07:00 | 5.6205 | 6.0708 | 6.0874 | 6.1077 | 6.1313 | 3.7915 | 4.5026 | 4.5156 | 4.5332 | 3.7915 | 5.6967 | 6.3535 | 6.3651 | 6.3805 | 6.7122
2022-06-29 08:00 | 5.6967 | 6.166 | 6.1894 | 6.2181 | 6.2515 | 3.7915 | 4.5123 | 4.5306 | 4.5555 | 3.7915 | 5.2776 | 5.8972 | 5.9136 | 5.9353 | 6.2515
2022-06-29 09:00 | 5.2585 | 5.7095 | 5.7402 | 5.7777 | 5.8215 | 3.1056 | 3.7124 | 3.7363 | 3.769 | 3.1056 | 4.1535 | 4.6581 | 4.6796 | 4.7081 | 4.9706
2022-06-29 10:00 | 5.0299 | 5.4748 | 5.5111 | 5.5555 | 5.6072 | 3.0103 | 3.6078 | 3.6361 | 3.6747 | 3.0103 | 3.8486 | 4.3271 | 4.3525 | 4.3863 | 4.6382
2022-06-29 11:00 | 4.7234 | 5.1499 | 5.1884 | 5.2355 | 5.2904 | 2.7688 | 3.3257 | 3.3557 | 3.3967 | 2.7688 | 3.0675 | 3.4621 | 3.4891 | 3.5249 | 3.7364
2022-06-29 12:00 | 3.9629 | 4.3318 | 4.3698 | 4.4162 | 4.4704 | 2.1148 | 2.5523 | 2.5819 | 2.6223 | 2.1148 | 1.7528 | 2.0005 | 2.0271 | 2.0624 | 2.201
2022-06-29 13:00 | 4.0772 | 4.4497 | 4.4851 | 4.5284 | 4.5789 | 2.4006 | 2.8863 | 2.9139 | 2.9516 | 2.4006 | 2.2101 | 2.5051 | 2.5299 | 2.5628 | 2.7237
2022-06-29 14:00 | 4.1377 | 4.5092 | 4.5418 | 4.5818 | 4.6283 | 2.4608 | 2.9534 | 2.9789 | 3.0137 | 2.4608 | 2.6674 | 3.0094 | 3.0322 | 3.0626 | 3.2456
2022-06-29 15:00 | 4.7441 | 5.1571 | 5.1879 | 5.2256 | 5.2695 | 2.9827 | 3.5674 | 3.5914 | 3.6242 | 2.9827 | 4.001 | 4.4889 | 4.5105 | 4.5392 | 4.7934
2022-06-29 16:00 | 5.0489 | 5.4837 | 5.5141 | 5.5512 | 5.5946 | 3.5057 | 4.1846 | 4.2083 | 4.2406 | 3.5057 | 5.1442 | 5.7586 | 5.7799 | 5.8082 | 6.1248
2022-06-29 17:00 | 5.5252 | 5.999 | 6.0312 | 6.0705 | 6.1165 | 3.9051 | 4.659 | 4.6841 | 4.7184 | 3.9051 | 5.0108 | 5.6129 | 5.6355 | 5.6654 | 5.9767
2022-06-29 18:00 | 5.7158 | 6.211 | 6.247 | 6.291 | 6.3422 | 4.0772 | 4.8678 | 4.8958 | 4.9341 | 4.0772 | 5.4871 | 6.1474 | 6.1726 | 6.2061 | 6.5477
2022-06-29 19:00 | 5.5062 | 5.9956 | 6.0365 | 6.0866 | 6.145 | 4.1154 | 4.9199 | 4.9518 | 4.9954 | 4.1154 | 5.8682 | 6.5778 | 6.6065 | 6.6446 | 7.0127
2022-06-29 20:00 | 5.2966 | 5.7801 | 5.826 | 5.8821 | 5.9476 | 3.8367 | 4.5977 | 4.6335 | 4.6823 | 3.8367 | 5.6205 | 6.3094 | 6.3415 | 6.3842 | 6.7443
2022-06-29 21:00 | 5.1061 | 5.5771 | 5.6238 | 5.6809 | 5.7476 | 3.6551 | 4.3844 | 4.4208 | 4.4705 | 3.6551 | 4.5536 | 5.1249 | 5.1576 | 5.2011 | 5.5034
2022-06-29 22:00 | 4.4333 | 4.8483 | 4.892 | 4.9454 | 5.0077 | 3.0667 | 3.6849 | 3.719 | 3.7655 | 3.0667 | 3.7152 | 4.1891 | 4.2197 | 4.2603 | 4.5132
2022-06-29 23:00 | 3.7152 | 4.0684 | 4.1078 | 4.1559 | 4.2121 | 2.4611 | 2.9634 | 2.994 | 3.0359 | 2.4611 | 2.8388 | 3.2092 | 3.2368 | 3.2734 | 3.4732
2022-06-30 | 3.1437 | 3.4449 | 3.4794 | 3.5217 | 3.5709 | 2.0767 | 2.5024 | 2.5293 | 2.5661 | 2.0767 | 2.3625 | 2.6732 | 2.6974 | 2.7295 | 2.8978
2022-06-30 01:00 | 3.0103 | 3.2921 | 3.3217 | 3.3579 | 3.4002 | 1.7998 | 2.1683 | 2.1914 | 2.223 | 1.7998 | 2.1529 | 2.4335 | 2.4543 | 2.4819 | 2.6332
2022-06-30 02:00 | 2.8579 | 3.1162 | 3.1397 | 3.1684 | 3.2019 | 1.6957 | 2.0365 | 2.0548 | 2.0798 | 1.6957 | 2.1148 | 2.3826 | 2.3991 | 2.4209 | 2.5633
2022-06-30 03:00 | 2.8007 | 3.043 | 3.0604 | 3.0817 | 3.1066 | 1.6957 | 2.028 | 2.0415 | 2.0601 | 1.6957 | 2.1148 | 2.3743 | 2.3865 | 2.4027 | 2.5383
2022-06-30 04:00 | 2.915 | 3.1558 | 3.168 | 3.183 | 3.2005 | 1.7672 | 2.1051 | 2.1147 | 2.1277 | 1.7672 | 2.4006 | 2.6847 | 2.6933 | 2.7047 | 2.8503
2022-06-30 05:00 | 3.4232 | 3.6977 | 3.708 | 3.7205 | 3.7351 | 2.1514 | 2.5561 | 2.564 | 2.5749 | 2.1514 | 2.7817 | 3.1053 | 3.1125 | 3.122 | 3.2863
2022-06-30 06:00 | 4.4073 | 4.7584 | 4.7703 | 4.7849 | 4.8019 | 2.9531 | 3.5057 | 3.515 | 3.5277 | 2.9531 | 3.8296 | 4.2722 | 4.2805 | 4.2917 | 4.5155
2022-06-30 07:00 | 5.0489 | 5.4567 | 5.4733 | 5.4936 | 5.5173 | 3.4104 | 4.0525 | 4.0654 | 4.0831 | 3.4104 | 5.3919 | 6.0147 | 6.0264 | 6.0418 | 6.3567
2022-06-30 08:00 | 5.0299 | 5.4496 | 5.473 | 5.5016 | 5.535 | 3.2651 | 3.8905 | 3.9088 | 3.9337 | 3.2651 | 5.5633 | 6.2147 | 6.2311 | 6.2529 | 6.5848
2022-06-30 09:00 | 4.6001 | 5.0021 | 5.0328 | 5.0703 | 5.1141 | 2.7245 | 3.2622 | 3.2862 | 3.3188 | 2.7245 | 3.0543 | 3.4367 | 3.4582 | 3.4868 | 3.6888
2022-06-30 10:00 | 4.001 | 4.3695 | 4.4057 | 4.4501 | 4.5019 | 2.4197 | 2.9101 | 2.9383 | 2.977 | 2.4197 | 2.5149 | 2.845 | 2.8704 | 2.9042 | 3.0828
2022-06-30 11:00 | 3.7343 | 4.0873 | 4.1257 | 4.1728 | 4.2278 | 2.0767 | 2.5081 | 2.5381 | 2.5791 | 2.0767 | 1.8862 | 2.1494 | 2.1764 | 2.2122 | 2.3587
2022-06-30 12:00 | 3.2389 | 3.554 | 3.592 | 3.6384 | 3.6926 | 1.7338 | 2.1022 | 2.1318 | 2.1722 | 1.7338 | 1.1622 | 1.3441 | 1.3707 | 1.406 | 1.5122
2022-06-30 13:00 | 3.5057 | 3.8356 | 3.871 | 3.9143 | 3.9648 | 1.8481 | 2.2336 | 2.2612 | 2.2989 | 1.8481 | 1.6576 | 1.8911 | 1.9159 | 1.9488 | 2.0794
2022-06-30 14:00 | 3.7152 | 4.0553 | 4.088 | 4.1279 | 4.1745 | 2.2208 | 2.67 | 2.6954 | 2.7302 | 2.2208 | 2.0196 | 2.2895 | 2.3124 | 2.3428 | 2.4901
2022-06-30 15:00 | 4.0963 | 4.4611 | 4.4919 | 4.5296 | 4.5736 | 2.43 | 2.9145 | 2.9385 | 2.9713 | 2.43 | 3.0294 | 3.4091 | 3.4307 | 3.4594 | 3.6602
2022-06-30 16:00 | 4.4774 | 4.8696 | 4.9 | 4.9372 | 4.9805 | 2.7882 | 3.3371 | 3.3608 | 3.3931 | 2.7882 | 3.6581 | 4.1072 | 4.1285 | 4.1567 | 4.3916
2022-06-30 17:00 | 5.1823 | 5.6305 | 5.6627 | 5.7021 | 5.748 | 3.4295 | 4.0972 | 4.1223 | 4.1565 | 3.4295 | 4.5536 | 5.1048 | 5.1273 | 5.1573 | 5.4434
2022-06-30 18:00 | 5.3157 | 5.7812 | 5.8171 | 5.8611 | 5.9124 | 3.6962 | 4.4176 | 4.4456 | 4.4839 | 3.6962 | 5.4871 | 6.1474 | 6.1726 | 6.2061 | 6.5477
2022-06-30 19:00 | 5.4681 | 5.9547 | 5.9956 | 6.0457 | 6.1041 | 3.8105 | 4.5597 | 4.5917 | 4.6352 | 3.8105 | 4.9346 | 5.5404 | 5.569 | 5.6071 | 5.9239
2022-06-30 20:00 | 5.2395 | 5.7187 | 5.7646 | 5.8207 | 5.8862 | 3.686 | 4.4197 | 4.4554 | 4.5043 | 3.686 | 5.0489 | 5.6742 | 5.7064 | 5.7491 | 6.0777
2022-06-30 21:00 | 4.8775 | 5.3315 | 5.3781 | 5.4353 | 5.5019 | 3.5438 | 4.2528 | 4.2893 | 4.339 | 3.5438 | 4.1725 | 4.7015 | 4.7342 | 4.7777 | 5.059
2022-06-30 22:00 | 4.3249 | 4.7319 | 4.7755 | 4.829 | 4.8913 | 3.0927 | 3.7156 | 3.7497 | 3.7961 | 3.0927 | 3.4934 | 3.9426 | 3.9732 | 4.0138 | 4.2545
2022-06-30 23:00 | 3.7915 | 4.1503 | 4.1897 | 4.2378 | 4.2939 | 2.5526 | 3.0715 | 3.1022 | 3.1441 | 2.5526 | 3.5628 | 4.0138 | 4.0413 | 4.0779 | 4.3176
2022-07-01 | 3.3284 | 3.6434 | 3.6779 | 3.7202 | 3.7694 | 2.1163 | 2.5492 | 2.5761 | 2.6128 | 2.1163 | 3.1818 | 3.5836 | 3.6078 | 3.6399 | 3.8533
2022-07-01 01:00 | 3.0675 | 3.3535 | 3.3831 | 3.4193 | 3.4616 | 1.9053 | 2.2929 | 2.316 | 2.3475 | 1.9053 | 2.172 | 2.4547 | 2.4755 | 2.503 | 2.6554
2022-07-01 02:00 | 2.915 | 3.1777 | 3.2011 | 3.2298 | 3.2633 | 1.7719 | 2.1266 | 2.1449 | 2.1698 | 1.7719 | 2.2101 | 2.4885 | 2.5049 | 2.5268 | 2.6744
2022-07-01 03:00 | 2.8198 | 3.0635 | 3.0809 | 3.1022 | 3.127 | 1.7147 | 2.0505 | 2.064 | 2.0826 | 1.7147 | 2.1148 | 2.3743 | 2.3865 | 2.4027 | 2.5383
2022-07-01 04:00 | 3.0294 | 3.2786 | 3.2908 | 3.3058 | 3.3233 | 1.8394 | 2.1904 | 2.2 | 2.213 | 1.8394 | 2.3816 | 2.6635 | 2.6721 | 2.6835 | 2.8281
2022-07-01 05:00 | 3.3834 | 3.6549 | 3.6652 | 3.6777 | 3.6923 | 2.2022 | 2.6162 | 2.6241 | 2.635 | 2.2022 | 3.1818 | 3.55 | 3.5571 | 3.5667 | 3.753
2022-07-01 06:00 | 4.4202 | 4.7722 | 4.7841 | 4.7987 | 4.8157 | 2.8769 | 3.4157 | 3.425 | 3.4377 | 2.8769 | 3.9058 | 4.3569 | 4.3652 | 4.3763 | 4.6043
2022-07-01 07:00 | 4.9346 | 5.3339 | 5.3505 | 5.3708 | 5.3945 | 3.4295 | 4.075 | 4.0879 | 4.1056 | 3.4295 | 4.7822 | 5.3372 | 5.3488 | 5.3643 | 5.6456
2022-07-01 08:00 | 5.068 | 5.4906 | 5.5139 | 5.5426 | 5.576 | 3.3855 | 4.0328 | 4.0511 | 4.076 | 3.3855 | 4.2868 | 4.7962 | 4.8126 | 4.8344 | 5.0961
2022-07-01 09:00 | 5.1632 | 5.6071 | 5.6378 | 5.6754 | 5.7191 | 3.1818 | 3.8024 | 3.8264 | 3.859 | 3.1818 | 3.982 | 4.4675 | 4.489 | 4.5176 | 4.7706
2022-07-01 10:00 | 4.8965 | 5.3315 | 5.3678 | 5.4122 | 5.4639 | 3.1818 | 3.8104 | 3.8387 | 3.8773 | 3.1818 | 3.7915 | 4.2636 | 4.289 | 4.3227 | 4.5715
2022-07-01 11:00 | 5.0299 | 5.4791 | 5.5176 | 5.5647 | 5.6197 | 3.0865 | 3.701 | 3.731 | 3.772 | 3.0865 | 3.9439 | 4.436 | 4.463 | 4.4988 | 4.7585
2022-07-01 12:00 | 5.1632 | 5.6214 | 5.6593 | 5.7058 | 5.7599 | 3.0865 | 3.7002 | 3.7298 | 3.7702 | 3.0865 | 4.344 | 4.8799 | 4.9065 | 4.9418 | 5.2229
2022-07-01 13:00 | 5.0299 | 5.4731 | 5.5085 | 5.5518 | 5.6024 | 3.2199 | 3.8542 | 3.8818 | 3.9195 | 3.2199 | 3.8867 | 4.3682 | 4.393 | 4.426 | 4.6791
2022-07-01 14:00 | 4.8775 | 5.3039 | 5.3366 | 5.3765 | 5.4231 | 3.1437 | 3.7602 | 3.7857 | 3.8204 | 3.1437 | 3.9248 | 4.4067 | 4.4296 | 4.46 | 4.7121
2022-07-01 15:00 | 5.1442 | 5.5869 | 5.6177 | 5.6554 | 5.6994 | 3.2897 | 3.93 | 3.9541 | 3.9869 | 3.2897 | 4.344 | 4.87 | 4.8916 | 4.9203 | 5.1933
2022-07-01 16:00 | 5.2966 | 5.7498 | 5.7802 | 5.8173 | 5.8607 | 3.4485 | 4.1171 | 4.1408 | 4.1731 | 3.4485 | 4.6488 | 5.2081 | 5.2294 | 5.2577 | 5.547
2022-07-01 17:00 | 5.3157 | 5.7738 | 5.806 | 5.8454 | 5.8913 | 3.8105 | 4.5473 | 4.5724 | 4.6067 | 3.8105 | 5.8301 | 6.5233 | 6.5459 | 6.5758 | 6.9321
2022-07-01 18:00 | 5.3919 | 5.8631 | 5.899 | 5.943 | 5.9943 | 3.8105 | 4.5527 | 4.5807 | 4.619 | 3.8105 | 5.9825 | 6.6979 | 6.7231 | 6.7566 | 7.1254
2022-07-01 19:00 | 5.1442 | 5.6067 | 5.6476 | 5.6977 | 5.7561 | 3.8867 | 4.6498 | 4.6817 | 4.7253 | 3.8867 | 5.6205 | 6.3026 | 6.3312 | 6.3693 | 6.7238
2022-07-01 20:00 | 4.9537 | 5.4117 | 5.4576 | 5.5137 | 5.5791 | 3.8677 | 4.6343 | 4.6701 | 4.7189 | 3.8677 | 5.6396 | 6.3306 | 6.3627 | 6.4054 | 6.7665
2022-07-01 21:00 | 4.7441 | 5.1882 | 5.2349 | 5.292 | 5.3586 | 3.4922 | 4.1919 | 4.2283 | 4.278 | 3.4922 | 4.3234 | 4.8691 | 4.9018 | 4.9453 | 5.2349
2022-07-01 22:00 | 4.4964 | 4.9161 | 4.9598 | 5.0132 | 5.0755 | 3.277 | 3.9334 | 3.9675 | 4.0139 | 3.277 | 3.8677 | 4.3585 | 4.3891 | 4.4297 | 4.6909
2022-07-01 23:00 | 3.9006 | 4.2676 | 4.3069 | 4.3551 | 4.4112 | 2.7619 | 3.3187 | 3.3494 | 3.3913 | 2.7619 | 3.1818 | 3.5903 | 3.6179 | 3.6545 | 3.8732
2022-07-02 | 3.4866 | 3.8134 | 3.8479 | 3.8901 | 3.9394 | 2.2863 | 2.75 | 2.7769 | 2.8137 | 2.2863 | 2.8388 | 3.2025 | 3.2267 | 3.2588 | 3.4533
2022-07-02 01:00 | 3.0484 | 3.333 | 3.3626 | 3.3989 | 3.4412 | 1.971 | 2.3705 | 2.3936 | 2.4252 | 1.971 | 2.2863 | 2.5817 | 2.6025 | 2.6301 | 2.7887
2022-07-02 02:00 | 2.9913 | 3.2595 | 3.283 | 3.3117 | 3.3451 | 1.8481 | 2.2166 | 2.2349 | 2.2599 | 1.8481 | 2.2863 | 2.5732 | 2.5896 | 2.6114 | 2.7632
2022-07-02 03:00 | 2.8769 | 3.1249 | 3.1423 | 3.1636 | 3.1885 | 1.7719 | 2.118 | 2.1316 | 2.1501 | 1.7719 | 2.1529 | 2.4166 | 2.4288 | 2.445 | 2.5827
2022-07-02 04:00 | 2.8946 | 3.1338 | 3.1461 | 3.1611 | 3.1786 | 1.8153 | 2.162 | 2.1715 | 2.1846 | 1.8153 | 2.1339 | 2.3883 | 2.3969 | 2.4083 | 2.5393
2022-07-02 05:00 | 2.9913 | 3.2337 | 3.2439 | 3.2564 | 3.271 | 1.9406 | 2.3071 | 2.3151 | 2.326 | 1.9406 | 2.3054 | 2.576 | 2.5832 | 2.5927 | 2.7309
2022-07-02 06:00 | 3.4676 | 3.7487 | 3.7607 | 3.7753 | 3.7923 | 2.2762 | 2.7059 | 2.7152 | 2.7279 | 2.2762 | 2.7436 | 3.0654 | 3.0737 | 3.0848 | 3.2489
2022-07-02 07:00 | 3.7343 | 4.0444 | 4.061 | 4.0812 | 4.1049 | 2.6331 | 3.1342 | 3.1472 | 3.1648 | 2.6331 | 3.4295 | 3.834 | 3.8456 | 3.861 | 4.068
2022-07-02 08:00 | 3.7724 | 4.0987 | 4.1221 | 4.1507 | 4.1841 | 2.6864 | 3.2069 | 3.2251 | 3.25 | 2.6864 | 3.3151 | 3.7164 | 3.7328 | 3.7546 | 3.9629
2022-07-02 09:00 | 4.0582 | 4.4199 | 4.4506 | 4.4882 | 4.5319 | 2.7626 | 3.3073 | 3.3312 | 3.3638 | 2.7626 | 3.6771 | 4.1288 | 4.1503 | 4.1788 | 4.4151
2022-07-02 10:00 | 4.2297 | 4.6151 | 4.6514 | 4.6958 | 4.7475 | 2.7626 | 3.3152 | 3.3435 | 3.3821 | 2.7626 | 3.3533 | 3.7766 | 3.802 | 3.8358 | 4.0605
2022-07-02 11:00 | 4.1916 | 4.5785 | 4.617 | 4.6641 | 4.719 | 2.7245 | 3.2733 | 3.3034 | 3.3443 | 2.7245 | 3.277 | 3.695 | 3.722 | 3.7578 | 3.9808
2022-07-02 12:00 | 4.4011 | 4.8026 | 4.8406 | 4.887 | 4.9412 | 2.8579 | 3.4301 | 3.4597 | 3.5001 | 2.8579 | 3.277 | 3.6943 | 3.7208 | 3.7562 | 3.9786
2022-07-02 13:00 | 4.3059 | 4.6953 | 4.7307 | 4.774 | 4.8245 | 2.8198 | 3.3815 | 3.4091 | 3.4468 | 2.8198 | 3.6009 | 4.0507 | 4.0755 | 4.1084 | 4.3458
2022-07-02 14:00 | 4.3249 | 4.7103 | 4.743 | 4.7829 | 4.8295 | 2.8388 | 3.4001 | 3.4255 | 3.4603 | 2.8388 | 3.4676 | 3.8986 | 3.9215 | 3.9519 | 4.1788
2022-07-02 15:00 | 4.344 | 4.7272 | 4.758 | 4.7957 | 4.8397 | 2.9913 | 3.5775 | 3.6016 | 3.6344 | 2.9913 | 3.8105 | 4.2772 | 4.2988 | 4.3274 | 4.5712
2022-07-02 16:00 | 4.7631 | 5.1767 | 5.207 | 5.2442 | 5.2875 | 3.1246 | 3.7345 | 3.7581 | 3.7905 | 3.1246 | 4.2297 | 4.7424 | 4.7636 | 4.7919 | 5.0582
2022-07-02 17:00 | 5.0108 | 5.4463 | 5.4785 | 5.5179 | 5.5638 | 3.4676 | 4.1422 | 4.1673 | 4.2015 | 3.4676 | 4.5917 | 5.1471 | 5.1697 | 5.1996 | 5.4879
2022-07-02 18:00 | 5.0489 | 5.4946 | 5.5306 | 5.5745 | 5.6258 | 3.5247 | 4.215 | 4.2431 | 4.2813 | 3.5247 | 4.9346 | 5.5335 | 5.5586 | 5.5921 | 5.9034
2022-07-02 19:00 | 4.9156 | 5.3611 | 5.402 | 5.4521 | 5.5105 | 3.4485 | 4.1321 | 4.164 | 4.2076 | 3.4485 | 4.8775 | 5.4768 | 5.5055 | 5.5436 | 5.8573
2022-07-02 20:00 | 4.706 | 5.1456 | 5.1915 | 5.2476 | 5.313 | 3.4194 | 4.1047 | 4.1405 | 4.1893 | 3.4194 | 4.4964 | 5.0603 | 5.0924 | 5.1351 | 5.4333
2022-07-02 21:00 | 4.5917 | 5.0244 | 5.0711 | 5.1283 | 5.1949 | 3.2199 | 3.8702 | 3.9066 | 3.9564 | 3.2199 | 4.363 | 4.9132 | 4.9459 | 4.9894 | 5.2812
2022-07-02 22:00 | 4.2297 | 4.6296 | 4.6732 | 4.7266 | 4.7889 | 2.89 | 3.4762 | 3.5103 | 3.5567 | 2.89 | 3.639 | 4.1044 | 4.135 | 4.1757 | 4.4243
2022-07-02 23:00 | 3.7915 | 4.1503 | 4.1897 | 4.2378 | 4.2939 | 2.4768 | 2.9819 | 3.0126 | 3.0545 | 2.4768 | 3.1246 | 3.5268 | 3.5544 | 3.591 | 3.8065
2022-07-03 | 3.3151 | 3.6292 | 3.6637 | 3.7059 | 3.7551 | 2.1529 | 2.5925 | 2.6194 | 2.6561 | 2.1529 | 2.9531 | 3.3296 | 3.3537 | 3.3859 | 3.5866
2022-07-03 01:00 | 3.0484 | 3.333 | 3.3626 | 3.3989 | 3.4412 | 1.9053 | 2.2929 | 2.316 | 2.3475 | 1.9053 | 2.4006 | 2.7088 | 2.7295 | 2.7571 | 2.922
2022-07-03 02:00 | 2.896 | 3.1572 | 3.1806 | 3.2093 | 3.2428 | 1.7338 | 2.0816 | 2.0998 | 2.1248 | 1.7338 | 2.3625 | 2.6579 | 2.6743 | 2.6961 | 2.8521
2022-07-03 03:00 | 2.7626 | 3.0021 | 3.0195 | 3.0408 | 3.0656 | 1.6385 | 1.9604 | 1.974 | 1.9925 | 1.6385 | 2.191 | 2.459 | 2.4711 | 2.4874 | 2.6272
2022-07-03 04:00 | 2.7436 | 2.9715 | 2.9838 | 2.9988 | 3.0163 | 1.6766 | 1.9981 | 2.0077 | 2.0207 | 1.6766 | 2.0767 | 2.3248 | 2.3334 | 2.3448 | 2.4726
2022-07-03 05:00 | 2.896 | 3.1313 | 3.1415 | 3.1541 | 3.1687 | 1.7932 | 2.133 | 2.1409 | 2.1518 | 1.7932 | 2.4197 | 2.7031 | 2.7102 | 2.7198 | 2.8642
2022-07-03 06:00 | 3.1246 | 3.3803 | 3.3922 | 3.4068 | 3.4239 | 2.0386 | 2.4253 | 2.4346 | 2.4473 | 2.0386 | 2.7436 | 3.0654 | 3.0737 | 3.0848 | 3.2489
2022-07-03 07:00 | 3.2961 | 3.5736 | 3.5902 | 3.6105 | 3.6341 | 2.3839 | 2.8398 | 2.8528 | 2.8704 | 2.3839 | 3.0675 | 3.4317 | 3.4433 | 3.4588 | 3.6459
2022-07-03 08:00 | 3.5057 | 3.8121 | 3.8355 | 3.8641 | 3.8975 | 2.5721 | 3.0718 | 3.0901 | 3.115 | 2.5721 | 3.0865 | 3.4624 | 3.4787 | 3.5005 | 3.6963
2022-07-03 09:00 | 3.5057 | 3.8263 | 3.857 | 3.8946 | 3.9383 | 2.5721 | 3.0822 | 3.1061 | 3.1388 | 2.5721 | 2.9341 | 3.3031 | 3.3246 | 3.3531 | 3.5486
2022-07-03 10:00 | 3.4676 | 3.7963 | 3.8326 | 3.877 | 3.9288 | 2.4578 | 2.9551 | 2.9834 | 3.022 | 2.4578 | 2.8388 | 3.205 | 3.2304 | 3.2641 | 3.4606
2022-07-03 11:00 | 3.5057 | 3.8416 | 3.8801 | 3.9272 | 3.9821 | 2.2047 | 2.6592 | 2.6892 | 2.7302 | 2.2047 | 2.4197 | 2.7422 | 2.7692 | 2.805 | 2.9809
2022-07-03 12:00 | 3.3914 | 3.7178 | 3.7557 | 3.8021 | 3.8563 | 2.0958 | 2.5298 | 2.5594 | 2.5998 | 2.0958 | 1.8862 | 2.1487 | 2.1753 | 2.2106 | 2.3565
2022-07-03 13:00 | 3.0484 | 3.3443 | 3.3797 | 3.4231 | 3.4736 | 2.0386 | 2.4587 | 2.4863 | 2.524 | 2.0386 | 1.7528 | 1.9969 | 2.0217 | 2.0547 | 2.1905
2022-07-03 14:00 | 3.3151 | 3.6255 | 3.6581 | 3.6981 | 3.7447 | 2.1318 | 2.5649 | 2.5903 | 2.6251 | 2.1318 | 2.4387 | 2.7553 | 2.7782 | 2.8086 | 2.979
2022-07-03 15:00 | 3.8105 | 4.1541 | 4.1849 | 4.2226 | 4.2666 | 2.553 | 3.0599 | 3.0839 | 3.1167 | 2.553 | 3.0294 | 3.4091 | 3.4307 | 3.4594 | 3.6602
2022-07-03 16:00 | 4.4179 | 4.8058 | 4.8362 | 4.8733 | 4.9167 | 3.0675 | 3.6669 | 3.6906 | 3.723 | 3.0675 | 4.1535 | 4.6577 | 4.6789 | 4.7072 | 4.9693
2022-07-03 17:00 | 4.9537 | 5.3849 | 5.4171 | 5.4565 | 5.5024 | 3.4676 | 4.1422 | 4.1673 | 4.2015 | 3.4676 | 5.1823 | 5.8035 | 5.826 | 5.856 | 6.1767
2022-07-03 18:00 | 5.087 | 5.5356 | 5.5715 | 5.6155 | 5.6668 | 3.6581 | 4.3726 | 4.4006 | 4.4389 | 3.6581 | 4.8775 | 5.4699 | 5.4951 | 5.5286 | 5.8367
2022-07-03 19:00 | 4.9727 | 5.4225 | 5.4634 | 5.5135 | 5.5719 | 3.5628 | 4.2671 | 4.2991 | 4.3426 | 3.5628 | 5.3919 | 6.0485 | 6.0772 | 6.1153 | 6.4572
2022-07-03 20:00 | 4.7441 | 5.1865 | 5.2324 | 5.2885 | 5.354 | 3.4676 | 4.1616 | 4.1974 | 4.2462 | 3.4676 | 5.1061 | 5.7378 | 5.7699 | 5.8126 | 6.1443
2022-07-03 21:00 | 4.5726 | 5.004 | 5.0506 | 5.1078 | 5.1744 | 3.2008 | 3.8477 | 3.8841 | 3.9338 | 3.2008 | 3.9439 | 4.4474 | 4.4801 | 4.5236 | 4.7924
2022-07-03 22:00 | 4.2297 | 4.6296 | 4.6732 | 4.7266 | 4.7889 | 2.749 | 3.3096 | 3.3436 | 3.3901 | 2.749 | 3.277 | 3.7022 | 3.7327 | 3.7734 | 4.0021
2022-07-03 23:00 | 3.6771 | 4.0275 | 4.0668 | 4.115 | 4.1711 | 2.3625 | 2.8469 | 2.8776 | 2.9195 | 2.3625 | 2.9722 | 3.3574 | 3.385 | 3.4216 | 3.6288
2022-07-04 | 3.258 | 3.5677 | 3.6023 | 3.6445 | 3.6937 | 1.9624 | 2.3674 | 2.3943 | 2.431 | 1.9624 | 2.2291 | 2.525 | 2.5492 | 2.5813 | 2.7423
2022-07-04 01:00 | 2.8579 | 3.1283 | 3.1579 | 3.1942 | 3.2365 | 1.7528 | 2.1128 | 2.1359 | 2.1675 | 1.7528 | 2.0958 | 2.37 | 2.3908 | 2.4183 | 2.5665
2022-07-04 02:00 | 2.7436 | 2.9934 | 3.0169 | 3.0456 | 3.079 | 1.6004 | 1.924 | 1.9423 | 1.9673 | 1.6004 | 2.1529 | 2.425 | 2.4414 | 2.4632 | 2.6077
2022-07-04 03:00 | 2.7055 | 2.9407 | 2.9581 | 2.9794 | 3.0042 | 1.5623 | 1.8704 | 1.884 | 1.9025 | 1.5623 | 2.0386 | 2.2896 | 2.3018 | 2.318 | 2.4494
2022-07-04 04:00 | 2.7626 | 2.992 | 3.0043 | 3.0193 | 3.0368 | 1.6637 | 1.9828 | 1.9924 | 2.0054 | 1.6637 | 2.3054 | 2.5788 | 2.5874 | 2.5988 | 2.7392
2022-07-04 05:00 | 3.3563 | 3.6259 | 3.6361 | 3.6486 | 3.6632 | 1.9948 | 2.3712 | 2.3792 | 2.3901 | 1.9948 | 2.7817 | 3.1053 | 3.1125 | 3.122 | 3.2863
2022-07-04 06:00 | 4.1014 | 4.4297 | 4.4416 | 4.4562 | 4.4733 | 2.6461 | 3.143 | 3.1523 | 3.165 | 2.6461 | 3.2961 | 3.6794 | 3.6877 | 3.6988 | 3.8933
2022-07-04 07:00 | 4.6679 | 5.0474 | 5.0639 | 5.0842 | 5.1079 | 2.8007 | 3.3322 | 3.3452 | 3.3628 | 2.8007 | 4.001 | 4.4692 | 4.4808 | 4.4962 | 4.7346
2022-07-04 08:00 | 4.725 | 5.1221 | 5.1455 | 5.1741 | 5.2075 | 2.9341 | 3.4995 | 3.5177 | 3.5426 | 2.9341 | 3.6581 | 4.0975 | 4.1139 | 4.1357 | 4.3628
2022-07-04 09:00 | 4.8203 | 5.2387 | 5.2694 | 5.3069 | 5.3507 | 2.9341 | 3.5098 | 3.5338 | 3.5664 | 2.9341 | 4.0391 | 4.5311 | 4.5526 | 4.5811 | 4.8373
2022-07-04 10:00 | 4.2208 | 4.6056 | 4.6419 | 4.6862 | 4.738 | 2.1529 | 2.595 | 2.6232 | 2.6619 | 2.1529 | 2.8198 | 3.1838 | 3.2092 | 3.243 | 3.4383
2022-07-04 11:00 | 3.3151 | 3.6369 | 3.6754 | 3.7225 | 3.7774 | 1.829 | 2.2155 | 2.2455 | 2.2865 | 1.829 | 0.724 | 0.85792 | 0.88488 | 0.92071 | 1.0033
2022-07-04 12:00 | 3.3533 | 3.6768 | 3.7148 | 3.7612 | 3.8154 | 1.6766 | 2.0346 | 2.0642 | 2.1047 | 1.6766 | 1.4861 | 1.7041 | 1.7306 | 1.766 | 1.8899
2022-07-04 13:00 | 3.4485 | 3.7742 | 3.8096 | 3.8529 | 3.9034 | 2.0005 | 2.4137 | 2.4413 | 2.479 | 2.0005 | 1.6004 | 1.8276 | 1.8524 | 1.8853 | 2.0127
2022-07-04 14:00 | 3.9248 | 4.2805 | 4.3131 | 4.3531 | 4.3997 | 2.3244 | 2.7924 | 2.8178 | 2.8526 | 2.3244 | 2.3244 | 2.6283 | 2.6511 | 2.6815 | 2.8456
2022-07-04 15:00 | 4.001 | 4.3588 | 4.3896 | 4.4273 | 4.4713 | 2.3244 | 2.7898 | 2.8138 | 2.8466 | 2.3244 | 2.6864 | 3.028 | 3.0496 | 3.0783 | 3.2602
2022-07-04 16:00 | 4.5536 | 4.9515 | 4.9819 | 5.0191 | 5.0624 | 2.8606 | 3.4225 | 3.4462 | 3.4785 | 2.8606 | 3.6962 | 4.1495 | 4.1708 | 4.1991 | 4.4361
2022-07-04 17:00 | 5.068 | 5.5077 | 5.5399 | 5.5793 | 5.6252 | 3.5819 | 4.2772 | 4.3023 | 4.3366 | 3.5819 | 4.6541 | 5.2165 | 5.239 | 5.269 | 5.5607
2022-07-04 18:00 | 5.2013 | 5.6584 | 5.6943 | 5.7383 | 5.7896 | 3.7152 | 4.4401 | 4.4682 | 4.5064 | 3.7152 | 4.8203 | 5.4064 | 5.4316 | 5.465 | 5.77
2022-07-04 19:00 | 5.1061 | 5.5658 | 5.6067 | 5.6568 | 5.7152 | 3.6009 | 4.3122 | 4.3441 | 4.3877 | 3.6009 | 5.8682 | 6.5778 | 6.6065 | 6.6446 | 7.0127
2022-07-04 20:00 | 4.8775 | 5.3298 | 5.3757 | 5.4318 | 5.4973 | 3.3723 | 4.0491 | 4.0849 | 4.1337 | 3.3723 | 4.7631 | 5.3567 | 5.3888 | 5.4315 | 5.7444
2022-07-04 21:00 | 4.4392 | 4.8607 | 4.9074 | 4.9645 | 5.0311 | 3.1375 | 3.7729 | 3.8093 | 3.859 | 3.1375 | 3.9629 | 4.4686 | 4.5013 | 4.5448 | 4.8146
2022-07-04 22:00 | 3.9248 | 4.3021 | 4.3457 | 4.3991 | 4.4614 | 2.7321 | 3.2896 | 3.3237 | 3.3702 | 2.7321 | 4.0201 | 4.5279 | 4.5585 | 4.5991 | 4.8687
2022-07-04 23:00 | 3.5438 | 3.8842 | 3.9236 | 3.9717 | 4.0278 | 2.3289 | 2.8072 | 2.8379 | 2.8798 | 2.3289 | 2.7436 | 3.1034 | 3.1309 | 3.1675 | 3.3621
2022-07-05 | 3.2389 | 3.5473 | 3.5818 | 3.624 | 3.6733 | 1.8567 | 2.2425 | 2.2694 | 2.3062 | 1.8567 | 2.3054 | 2.6097 | 2.6339 | 2.666 | 2.8312
2022-07-05 01:00 | 2.8388 | 3.1079 | 3.1375 | 3.1737 | 3.216 | 1.6957 | 2.0453 | 2.0684 | 2.1 | 1.6957 | 2.2291 | 2.5182 | 2.539 | 2.5666 | 2.7221
2022-07-05 02:00 | 2.7817 | 3.0344 | 3.0578 | 3.0865 | 3.12 | 1.5803 | 1.9002 | 1.9185 | 1.9435 | 1.5803 | 2.3816 | 2.6791 | 2.6955 | 2.7173 | 2.8743
2022-07-05 03:00 | 2.7436 | 2.9816 | 2.999 | 3.0203 | 3.0452 | 1.5814 | 1.8929 | 1.9065 | 1.925 | 1.5814 | 1.9815 | 2.2261 | 2.2383 | 2.2545 | 2.3828
2022-07-05 04:00 | 2.8388 | 3.0739 | 3.0861 | 3.1011 | 3.1186 | 1.6766 | 1.9981 | 2.0077 | 2.0207 | 1.6766 | 2.191 | 2.4518 | 2.4604 | 2.4718 | 2.6059
2022-07-05 05:00 | 3.36 | 3.6298 | 3.6401 | 3.6526 | 3.6672 | 2.0071 | 2.3856 | 2.3936 | 2.4045 | 2.0071 | 2.915 | 3.2535 | 3.2607 | 3.2702 | 3.4419
2022-07-05 06:00 | 4.1535 | 4.4856 | 4.4975 | 4.5121 | 4.5292 | 2.7436 | 3.2581 | 3.2674 | 3.2801 | 2.7436 | 3.7724 | 4.2087 | 4.217 | 4.2281 | 4.4488
2022-07-05 07:00 | 4.5536 | 4.9245 | 4.9411 | 4.9614 | 4.9851 | 2.7817 | 3.3097 | 3.3227 | 3.3403 | 2.7817 | 3.9629 | 4.4268 | 4.4384 | 4.4539 | 4.6902
2022-07-05 08:00 | 4.344 | 4.7127 | 4.7361 | 4.7648 | 4.7982 | 2.6293 | 3.1394 | 3.1576 | 3.1825 | 2.6293 | 3.4676 | 3.8858 | 3.9022 | 3.924 | 4.1406
2022-07-05 09:00 | 4.0201 | 4.379 | 4.4097 | 4.4472 | 4.491 | 2.4006 | 2.8796 | 2.9035 | 2.9362 | 2.4006 | 2.2482 | 2.5409 | 2.5624 | 2.5909 | 2.7487
2022-07-05 10:00 | 3.9058 | 4.2671 | 4.3034 | 4.3478 | 4.3995 | 2.2673 | 2.73 | 2.7583 | 2.7969 | 2.2673 | 2.0958 | 2.3792 | 2.4047 | 2.4384 | 2.594
2022-07-05 11:00 | 3.4295 | 3.7597 | 3.7982 | 3.8453 | 3.9003 | 1.8481 | 2.238 | 2.268 | 2.309 | 1.8481 | 1.4099 | 1.6201 | 1.6471 | 1.6829 | 1.8033
2022-07-05 12:00 | 3.4866 | 3.8201 | 3.858 | 3.9045 | 3.9587 | 1.7719 | 2.1472 | 2.1768 | 2.2172 | 1.7719 | 1.2956 | 1.4923 | 1.5189 | 1.5543 | 1.6677
2022-07-05 13:00 | 3.6581 | 3.9993 | 4.0347 | 4.0781 | 4.1286 | 1.9624 | 2.3686 | 2.3963 | 2.434 | 1.9624 | 1.4861 | 1.7005 | 1.7253 | 1.7583 | 1.8794
2022-07-05 14:00 | 3.7037 | 4.043 | 4.0756 | 4.1156 | 4.1621 | 2.04 | 2.4564 | 2.4818 | 2.5166 | 2.04 | 2.2101 | 2.5012 | 2.5241 | 2.5545 | 2.7123
2022-07-05 15:00 | 3.9801 | 4.3363 | 4.3671 | 4.4048 | 4.4488 | 2.3816 | 2.8573 | 2.8813 | 2.9141 | 2.3816 | 2.9913 | 3.3668 | 3.3883 | 3.417 | 3.6158
2022-07-05 16:00 | 4.4964 | 4.8901 | 4.9205 | 4.9576 | 5.001 | 2.8388 | 3.3968 | 3.4205 | 3.4529 | 2.8388 | 3.9439 | 4.4248 | 4.446 | 4.4743 | 4.7249
2022-07-05 17:00 | 5.1442 | 5.5896 | 5.6218 | 5.6612 | 5.7071 | 3.4874 | 4.1656 | 4.1907 | 4.225 | 3.4874 | 5.3347 | 5.9729 | 5.9954 | 6.0254 | 6.3544
2022-07-05 18:00 | 5.2204 | 5.6788 | 5.7148 | 5.7588 | 5.81 | 3.7534 | 4.4851 | 4.5132 | 4.5514 | 3.7534 | 4.706 | 5.2794 | 5.3046 | 5.338 | 5.6367
2022-07-05 19:00 | 5.1632 | 5.6272 | 5.6681 | 5.7182 | 5.7766 | 3.6278 | 4.3439 | 4.3758 | 4.4194 | 3.6278 | 5.7539 | 6.4508 | 6.4794 | 6.5175 | 6.8794
2022-07-05 20:00 | 5.0108 | 5.4731 | 5.519 | 5.5751 | 5.6405 | 3.5299 | 4.2353 | 4.2711 | 4.3199 | 3.5299 | 5.3347 | 5.9918 | 6.024 | 6.0667 | 6.411
2022-07-05 21:00 | 4.4964 | 4.9221 | 4.9688 | 5.0259 | 5.0925 | 3.2649 | 3.9234 | 3.9598 | 4.0096 | 3.2649 | 3.9439 | 4.4474 | 4.4801 | 4.5236 | 4.7924
2022-07-05 22:00 | 3.9439 | 4.3225 | 4.3662 | 4.4196 | 4.4819 | 2.7817 | 3.3482 | 3.3823 | 3.4287 | 2.7817 | 3.8486 | 4.3373 | 4.3679 | 4.4085 | 4.6687
2022-07-05 23:00 | 3.5243 | 3.8634 | 3.9027 | 3.9508 | 4.007 | 2.3435 | 2.8244 | 2.8551 | 2.897 | 2.3435 | 3.0294 | 3.4209 | 3.4485 | 3.4851 | 3.6954
2022-07-06 | 2.9722 | 3.2607 | 3.2952 | 3.3375 | 3.3867 | 1.9431 | 2.3445 | 2.3714 | 2.4082 | 1.9431 | 2.4768 | 2.8003 | 2.8244 | 2.8566 | 3.0311
2022-07-06 01:00 | 2.8007 | 3.0669 | 3.0965 | 3.1328 | 3.1751 | 1.767 | 2.1295 | 2.1526 | 2.1842 | 1.767 | 1.9624 | 2.2218 | 2.2426 | 2.2701 | 2.411
2022-07-06 02:00 | 2.6483 | 2.8911 | 2.9145 | 2.9432 | 2.9767 | 1.6004 | 1.924 | 1.9423 | 1.9673 | 1.6004 | 2.0196 | 2.2768 | 2.2932 | 2.315 | 2.4522
2022-07-06 03:00 | 2.6668 | 2.8991 | 2.9165 | 2.9378 | 2.9627 | 1.6195 | 1.9379 | 1.9515 | 1.97 | 1.6195 | 1.9053 | 2.1414 | 2.1536 | 2.1698 | 2.2939
2022-07-06 04:00 | 2.7055 | 2.9306 | 2.9429 | 2.9579 | 2.9754 | 1.6004 | 1.9081 | 1.9177 | 1.9307 | 1.6004 | 2.0196 | 2.2613 | 2.2699 | 2.2813 | 2.4059
2022-07-06 05:00 | 3.2199 | 3.4793 | 3.4895 | 3.502 | 3.5166 | 1.9523 | 2.321 | 2.3289 | 2.3398 | 1.9523 | 2.6293 | 2.936 | 2.9431 | 2.9527 | 3.1086
2022-07-06 06:00 | 4.0201 | 4.3423 | 4.3543 | 4.3689 | 4.3859 | 2.6864 | 3.1906 | 3.1999 | 3.2126 | 2.6864 | 3.4676 | 3.8699 | 3.8783 | 3.8894 | 4.0933
2022-07-06 07:00 | 4.344 | 4.6994 | 4.716 | 4.7363 | 4.7599 | 2.8579 | 3.3998 | 3.4127 | 3.4303 | 2.8579 | 3.6581 | 4.0881 | 4.0997 | 4.1151 | 4.3347
2022-07-06 08:00 | 4.4774 | 4.856 | 4.8794 | 4.908 | 4.9414 | 2.915 | 3.477 | 3.4952 | 3.5201 | 2.915 | 3.8105 | 4.2669 | 4.2833 | 4.3051 | 4.5406
2022-07-06 09:00 | 4.3249 | 4.7065 | 4.7372 | 4.7747 | 4.8185 | 2.534 | 3.0372 | 3.0611 | 3.0938 | 2.534 | 3.5628 | 4.0018 | 4.0232 | 4.0518 | 4.2818
2022-07-06 10:00 | 3.8672 | 4.2257 | 4.2619 | 4.3063 | 4.3581 | 2.4197 | 2.9101 | 2.9383 | 2.977 | 2.4197 | 2.3244 | 2.6333 | 2.6587 | 2.6925 | 2.8606
2022-07-06 11:00 | 3.4485 | 3.7802 | 3.8187 | 3.8658 | 3.9207 | 2.0386 | 2.4631 | 2.4931 | 2.5341 | 2.0386 | 1.6576 | 1.8954 | 1.9223 | 1.9581 | 2.0921
2022-07-06 12:00 | 3.5628 | 3.902 | 3.9399 | 3.9864 | 4.0405 | 2.1148 | 2.5523 | 2.5819 | 2.6223 | 2.1148 | 2.191 | 2.4874 | 2.514 | 2.5493 | 2.712
2022-07-06 13:00 | 3.5628 | 3.897 | 3.9324 | 3.9757 | 4.0262 | 2.0767 | 2.5037 | 2.5313 | 2.569 | 2.0767 | 2.1236 | 2.409 | 2.4338 | 2.4668 | 2.6229
2022-07-06 14:00 | 3.7724 | 4.1167 | 4.1494 | 4.1893 | 4.2359 | 2.2863 | 2.7473 | 2.7728 | 2.8076 | 2.2863 | 2.3054 | 2.6071 | 2.63 | 2.6604 | 2.8234
2022-07-06 15:00 | 3.7343 | 4.0722 | 4.103 | 4.1407 | 4.1847 | 2.2427 | 2.6932 | 2.7173 | 2.7501 | 2.2427 | 2.2494 | 2.5424 | 2.5639 | 2.5926 | 2.7506
2022-07-06 16:00 | 4.0796 | 4.4423 | 4.4727 | 4.5099 | 4.5532 | 2.5059 | 3.0035 | 3.0272 | 3.0595 | 2.5059 | 3.277 | 3.6837 | 3.705 | 3.7333 | 3.9472
2022-07-06 17:00 | 4.6107 | 5.0165 | 5.0487 | 5.088 | 5.134 | 3.2267 | 3.8576 | 3.8827 | 3.9169 | 3.2267 | 4.3821 | 4.9142 | 4.9368 | 4.9667 | 5.2435
2022-07-06 18:00 | 4.7441 | 5.1671 | 5.2031 | 5.247 | 5.2983 | 3.4485 | 4.125 | 4.153 | 4.1913 | 3.4485 | 4.3249 | 4.8559 | 4.8811 | 4.9146 | 5.1923
2022-07-06 19:00 | 4.6679 | 5.095 | 5.1359 | 5.186 | 5.2444 | 3.4866 | 4.1771 | 4.209 | 4.2526 | 3.4866 | 5.1442 | 5.7733 | 5.8019 | 5.84 | 6.1684
2022-07-06 20:00 | 4.579 | 5.0092 | 5.055 | 5.1112 | 5.1766 | 3.2465 | 3.9005 | 3.9363 | 3.9851 | 3.2465 | 4.0582 | 4.5733 | 4.6054 | 4.6481 | 4.9223
2022-07-06 21:00 | 4.2106 | 4.615 | 4.6617 | 4.7189 | 4.7855 | 2.9913 | 3.6001 | 3.6365 | 3.6863 | 2.9913 | 3.9248 | 4.4262 | 4.4589 | 4.5024 | 4.7702
2022-07-06 22:00 | 3.7724 | 4.1383 | 4.1819 | 4.2354 | 4.2977 | 2.5149 | 3.0331 | 3.0671 | 3.1136 | 2.5149 | 3.4485 | 3.8927 | 3.9233 | 3.9639 | 4.2021
2022-07-06 23:00 | 3.3533 | 3.6795 | 3.7189 | 3.767 | 3.8232 | 2.3054 | 2.7794 | 2.8101 | 2.8519 | 2.3054 | 2.534 | 2.8705 | 2.898 | 2.9346 | 3.1177
2022-07-07 | 2.8769 | 3.1584 | 3.1929 | 3.2351 | 3.2844 | 1.8194 | 2.1984 | 2.2253 | 2.2621 | 1.8194 | 2.1148 | 2.398 | 2.4222 | 2.4543 | 2.609
2022-07-07 01:00 | 2.7245 | 2.985 | 3.0147 | 3.0509 | 3.0932 | 1.6004 | 1.9328 | 1.9559 | 1.9874 | 1.6004 | 1.7909 | 2.0313 | 2.052 | 2.0796 | 2.211
2022-07-07 02:00 | 2.553 | 2.7887 | 2.8122 | 2.8409 | 2.8744 | 1.5052 | 1.8115 | 1.8297 | 1.8547 | 1.5052 | 2.1529 | 2.425 | 2.4414 | 2.4632 | 2.6077
2022-07-07 03:00 | 2.553 | 2.7769 | 2.7943 | 2.8156 | 2.8405 | 1.525 | 1.8263 | 1.8399 | 1.8584 | 1.525 | 1.7528 | 1.972 | 1.9842 | 2.0004 | 2.1161
2022-07-07 04:00 | 2.553 | 2.7668 | 2.7791 | 2.7941 | 2.8116 | 1.5635 | 1.8645 | 1.874 | 1.8871 | 1.5635 | 1.9434 | 2.1766 | 2.1852 | 2.1966 | 2.3171
2022-07-07 05:00 | 3.0865 | 3.336 | 3.3462 | 3.3588 | 3.3734 | 1.8626 | 2.215 | 2.223 | 2.2339 | 1.8626 | 2.534 | 2.8301 | 2.8373 | 2.8468 | 2.9975
2022-07-07 06:00 | 3.9916 | 4.3117 | 4.3236 | 4.3382 | 4.3552 | 2.5149 | 2.988 | 2.9973 | 3.01 | 2.5149 | 3.639 | 4.0605 | 4.0688 | 4.0799 | 4.2933
2022-07-07 07:00 | 4.3284 | 4.6827 | 4.6993 | 4.7196 | 4.7432 | 2.7436 | 3.2647 | 3.2776 | 3.2953 | 2.7436 | 3.4866 | 3.8975 | 3.9091 | 3.9246 | 4.1347
2022-07-07 08:00 | 4.4011 | 4.7741 | 4.7975 | 4.8262 | 4.8596 | 2.553 | 3.0493 | 3.0676 | 3.0925 | 2.553 | 3.9058 | 4.3728 | 4.3892 | 4.4109 | 4.6517
2022-07-07 09:00 | 3.5889 | 3.9157 | 3.9464 | 3.984 | 4.0277 | 1.9875 | 2.3916 | 2.4155 | 2.4482 | 1.9875 | 1.8672 | 2.1174 | 2.1389 | 2.1675 | 2.3043
2022-07-07 10:00 | 2.7626 | 3.039 | 3.0753 | 3.1196 | 3.1714 | 1.426 | 1.7361 | 1.7644 | 1.803 | 1.426 | 0.78115 | 0.91836 | 0.94376 | 0.97753 | 1.0608
2022-07-07 11:00 | 2.4006 | 2.6544 | 2.6929 | 2.74 | 2.7949 | 1.105 | 1.3602 | 1.3902 | 1.4312 | 1.105 | 0.87642 | 1.0273 | 1.0543 | 1.0901 | 1.1811
2022-07-07 12:00 | 2.6864 | 2.9604 | 2.9984 | 3.0448 | 3.099 | 1.4861 | 1.8096 | 1.8392 | 1.8796 | 1.4861 | 1.1622 | 1.3441 | 1.3707 | 1.406 | 1.5122
2022-07-07 13:00 | 2.8388 | 3.1192 | 3.1546 | 3.1979 | 3.2484 | 1.4129 | 1.7195 | 1.7471 | 1.7848 | 1.4129 | 1.105 | 1.2771 | 1.3019 | 1.3348 | 1.435
2022-07-07 14:00 | 2.4387 | 2.6839 | 2.7166 | 2.7565 | 2.8031 | 1.2954 | 1.5768 | 1.6022 | 1.637 | 1.2954 | 0.85737 | 0.99801 | 1.0209 | 1.0513 | 1.1347
2022-07-07 15:00 | 2.896 | 3.1716 | 3.2024 | 3.2401 | 3.2841 | 1.7528 | 2.1145 | 2.1385 | 2.1714 | 1.7528 | 1.2384 | 1.4189 | 1.4405 | 1.4692 | 1.5715
2022-07-07 16:00 | 3.6009 | 3.9281 | 3.9584 | 3.9956 | 4.0389 | 2.3699 | 2.8429 | 2.8666 | 2.8989 | 2.3699 | 3.1246 | 3.5144 | 3.5356 | 3.5639 | 3.7695
2022-07-07 17:00 | 4.343 | 4.7288 | 4.761 | 4.8004 | 4.8463 | 3.0109 | 3.6027 | 3.6277 | 3.662 | 3.0109 | 3.5628 | 4.0038 | 4.0264 | 4.0563 | 4.288
2022-07-07 18:00 | 4.6298 | 5.0443 | 5.0802 | 5.1242 | 5.1755 | 3.1818 | 3.8099 | 3.8379 | 3.8762 | 3.1818 | 4.6298 | 5.1947 | 5.2199 | 5.2533 | 5.5478
2022-07-07 19:00 | 4.6488 | 5.0745 | 5.1154 | 5.1655 | 5.2239 | 3.1056 | 3.727 | 3.7589 | 3.8024 | 3.1056 | 4.6679 | 5.2439 | 5.2726 | 5.3107 | 5.6129
2022-07-07 20:00 | 4.5917 | 5.0228 | 5.0686 | 5.1248 | 5.1902 | 3.0675 | 3.689 | 3.7247 | 3.7736 | 3.0675 | 4.0772 | 4.5945 | 4.6266 | 4.6693 | 4.9445
2022-07-07 21:00 | 4.5155 | 4.9425 | 4.9892 | 5.0464 | 5.113 | 2.9531 | 3.5551 | 3.5915 | 3.6412 | 2.9531 | 4.0772 | 4.5956 | 4.6283 | 4.6718 | 4.9479
2022-07-07 22:00 | 4.0391 | 4.4249 | 4.4685 | 4.5219 | 4.5842 | 2.7245 | 3.2807 | 3.3147 | 3.3612 | 2.7245 | 3.277 | 3.7022 | 3.7327 | 3.7734 | 4.0021
2022-07-07 23:00 | 3.639 | 3.9866 | 4.0259 | 4.074 | 4.1302 | 2.3291 | 2.8075 | 2.8381 | 2.88 | 2.3291 | 3.3151 | 3.7385 | 3.7661 | 3.8027 | 4.0287
2022-07-08 | 3.3151 | 3.6292 | 3.6637 | 3.7059 | 3.7551 | 2.0005 | 2.4124 | 2.4393 | 2.4761 | 2.0005 | 2.6483 | 2.9908 | 3.015 | 3.0471 | 3.2311
2022-07-08 01:00 | 3.1437 | 3.4354 | 3.465 | 3.5012 | 3.5435 | 1.81 | 2.1804 | 2.2035 | 2.235 | 1.81 | 2.191 | 2.4759 | 2.4966 | 2.5242 | 2.6776
2022-07-08 02:00 | 3.0484 | 3.3209 | 3.3444 | 3.3731 | 3.4065 | 1.7213 | 2.0668 | 2.0851 | 2.1101 | 1.7213 | 2.4387 | 2.7426 | 2.759 | 2.7808 | 2.941
2022-07-08 03:00 | 2.9341 | 3.1863 | 3.2037 | 3.225 | 3.2499 | 1.6733 | 2.0015 | 2.0151 | 2.0336 | 1.6733 | 2.2482 | 2.5225 | 2.5347 | 2.5509 | 2.6938
2022-07-08 04:00 | 3.1437 | 3.4014 | 3.4136 | 3.4286 | 3.4461 | 1.81 | 2.1557 | 2.1652 | 2.1783 | 1.81 | 2.3625 | 2.6424 | 2.651 | 2.6624 | 2.8059
2022-07-08 05:00 | 3.5437 | 3.8272 | 3.8374 | 3.85 | 3.8646 | 2.2217 | 2.6391 | 2.6471 | 2.658 | 2.2217 | 2.8579 | 3.19 | 3.1972 | 3.2067 | 3.3752
2022-07-08 06:00 | 4.2262 | 4.5638 | 4.5757 | 4.5903 | 4.6074 | 2.8398 | 3.3718 | 3.3811 | 3.3938 | 2.8398 | 4.0391 | 4.5051 | 4.5134 | 4.5245 | 4.7599
2022-07-08 07:00 | 4.8203 | 5.2111 | 5.2277 | 5.248 | 5.2716 | 3.2008 | 3.8049 | 3.8178 | 3.8355 | 3.2008 | 4.0582 | 4.5327 | 4.5443 | 4.5597 | 4.8013
2022-07-08 08:00 | 4.7 | 5.0952 | 5.1186 | 5.1472 | 5.1806 | 3.0865 | 3.6795 | 3.6978 | 3.7227 | 3.0865 | 4.1344 | 4.6268 | 4.6432 | 4.665 | 4.9183
2022-07-08 09:00 | 4.0582 | 4.4199 | 4.4506 | 4.4882 | 4.5319 | 2.6102 | 3.1272 | 3.1511 | 3.1838 | 2.6102 | 2.3244 | 2.6256 | 2.647 | 2.6756 | 2.8375
2022-07-08 10:00 | 3.3533 | 3.6735 | 3.7098 | 3.7542 | 3.8059 | 2.2101 | 2.6625 | 2.6908 | 2.7294 | 2.2101 | 1.3146 | 1.5112 | 1.5366 | 1.5703 | 1.683
2022-07-08 11:00 | 3.7987 | 4.1564 | 4.1949 | 4.242 | 4.2969 | 2.191 | 2.6431 | 2.6731 | 2.7141 | 2.191 | 1.2384 | 1.4296 | 1.4565 | 1.4924 | 1.6033
2022-07-08 12:00 | 4.1344 | 4.516 | 4.554 | 4.6004 | 4.6546 | 2.2863 | 2.7549 | 2.7845 | 2.8249 | 2.2863 | 2.172 | 2.4663 | 2.4928 | 2.5282 | 2.6898
2022-07-08 13:00 | 2.6864 | 2.9554 | 2.9908 | 3.0341 | 3.0847 | 1.9243 | 2.3236 | 2.3512 | 2.3889 | 1.9243 | 0.74305 | 0.87481 | 0.89961 | 0.93257 | 1.0128
2022-07-08 14:00 | 2.8579 | 3.1342 | 3.1669 | 3.2068 | 3.2534 | 1.6576 | 2.0046 | 2.03 | 2.0648 | 1.6576 | 1.2194 | 1.4003 | 1.4232 | 1.4535 | 1.5569
2022-07-08 15:00 | 3.5819 | 3.9085 | 3.9393 | 3.977 | 4.0209 | 2.1627 | 2.5987 | 2.6228 | 2.6556 | 2.1627 | 2.896 | 3.2609 | 3.2825 | 3.3112 | 3.5047
2022-07-08 16:00 | 4.4011 | 4.7878 | 4.8181 | 4.8553 | 4.8986 | 2.8413 | 3.3997 | 3.4234 | 3.4557 | 2.8413 | 3.7534 | 4.213 | 4.2343 | 4.2626 | 4.5027
2022-07-08 17:00 | 4.8775 | 5.303 | 5.3352 | 5.3746 | 5.4205 | 3.3151 | 3.9621 | 3.9872 | 4.0215 | 3.3151 | 4.4694 | 5.0113 | 5.0338 | 5.0638 | 5.3453
2022-07-08 18:00 | 5.0489 | 5.4946 | 5.5306 | 5.5745 | 5.6258 | 3.3533 | 4.0125 | 4.0405 | 4.0788 | 3.3533 | 5.5633 | 6.2321 | 6.2573 | 6.2908 | 6.6366
2022-07-08 19:00 | 5.1632 | 5.6272 | 5.6681 | 5.7182 | 5.7766 | 3.4485 | 4.1321 | 4.164 | 4.2076 | 3.4485 | 5.1251 | 5.7521 | 5.7808 | 5.8188 | 6.1461
2022-07-08 20:00 | 4.7631 | 5.207 | 5.2529 | 5.309 | 5.3744 | 3.4485 | 4.1391 | 4.1749 | 4.2237 | 3.4485 | 4.6679 | 5.2508 | 5.2829 | 5.3256 | 5.6333
2022-07-08 21:00 | 4.5917 | 5.0244 | 5.0711 | 5.1283 | 5.1949 | 3.3269 | 3.9967 | 4.0331 | 4.0828 | 3.3269 | 5.2013 | 5.8448 | 5.8775 | 5.921 | 6.2589
2022-07-08 22:00 | 4.3141 | 4.7202 | 4.7639 | 4.8173 | 4.8796 | 3.0186 | 3.6281 | 3.6622 | 3.7086 | 3.0186 | 3.7534 | 4.2315 | 4.262 | 4.3027 | 4.5576
2022-07-08 23:00 | 3.7152 | 4.0684 | 4.1078 | 4.1559 | 4.2121 | 2.534 | 3.0495 | 3.0802 | 3.122 | 2.534 | 3.3151 | 3.7385 | 3.7661 | 3.8027 | 4.0287
2022-07-09 | 3.3723 | 3.6906 | 3.7251 | 3.7673 | 3.8166 | 2.2472 | 2.7038 | 2.7307 | 2.7674 | 2.2472 | 3.0865 | 3.4778 | 3.5019 | 3.5341 | 3.7422
2022-07-09 01:00 | 3.1437 | 3.4354 | 3.465 | 3.5012 | 3.5435 | 1.9139 | 2.3031 | 2.3262 | 2.3578 | 1.9139 | 2.3435 | 2.6453 | 2.666 | 2.6936 | 2.8554
2022-07-09 02:00 | 2.9722 | 3.2391 | 3.2625 | 3.2912 | 3.3247 | 1.7604 | 2.113 | 2.1313 | 2.1563 | 1.7604 | 2.6864 | 3.0178 | 3.0342 | 3.0561 | 3.2298
2022-07-09 03:00 | 3.0865 | 3.3501 | 3.3675 | 3.3888 | 3.4136 | 1.6957 | 2.028 | 2.0415 | 2.0601 | 1.6957 | 2.4578 | 2.7554 | 2.7676 | 2.7838 | 2.9383
2022-07-09 04:00 | 3.2199 | 3.4833 | 3.4955 | 3.5105 | 3.528 | 1.777 | 2.1167 | 2.1262 | 2.1393 | 1.777 | 2.4197 | 2.7059 | 2.7145 | 2.7259 | 2.8725
2022-07-09 05:00 | 3.3533 | 3.6226 | 3.6328 | 3.6453 | 3.6599 | 2.0744 | 2.4652 | 2.4732 | 2.4841 | 2.0744 | 2.8388 | 3.1689 | 3.176 | 3.1856 | 3.353
2022-07-09 06:00 | 3.7152 | 4.0148 | 4.0268 | 4.0414 | 4.0584 | 2.4069 | 2.8604 | 2.8697 | 2.8824 | 2.4069 | 3.3533 | 3.7429 | 3.7512 | 3.7623 | 3.96
2022-07-09 07:00 | 4.1725 | 4.5152 | 4.5317 | 4.552 | 4.5757 | 2.7055 | 3.2197 | 3.2326 | 3.2503 | 2.7055 | 3.8677 | 4.321 | 4.3326 | 4.348 | 4.5791
2022-07-09 08:00 | 4.1377 | 4.4911 | 4.5145 | 4.5431 | 4.5765 | 2.8007 | 3.3419 | 3.3602 | 3.3851 | 2.8007 | 3.5438 | 3.9705 | 3.9869 | 4.0087 | 4.2295
2022-07-09 09:00 | 3.7152 | 4.0515 | 4.0822 | 4.1197 | 4.1635 | 2.4768 | 2.9696 | 2.9936 | 3.0262 | 2.4768 | 3.0865 | 3.4724 | 3.4939 | 3.5225 | 3.7263
2022-07-09 10:00 | 2.9913 | 3.2846 | 3.3209 | 3.3653 | 3.417 | 2.0767 | 2.5049 | 2.5332 | 2.5718 | 2.0767 | 1.9815 | 2.2522 | 2.2776 | 2.3114 | 2.4607
2022-07-09 11:00 | 2.5721 | 2.8386 | 2.8771 | 2.9242 | 2.9792 | 1.5229 | 1.8538 | 1.8838 | 1.9248 | 1.5229 | 0.74305 | 0.87909 | 0.90605 | 0.94188 | 1.0256
2022-07-09 12:00 | 2.2482 | 2.4896 | 2.5276 | 2.574 | 2.6282 | 1.2956 | 1.5845 | 1.6141 | 1.6545 | 1.2956 | 0.64779 | 0.77248 | 0.79907 | 0.8344 | 0.91225
2022-07-09 13:00 | 2.7436 | 3.0168 | 3.0522 | 3.0956 | 3.1461 | 1.6576 | 2.0085 | 2.0361 | 2.0738 | 1.6576 | 1.3497 | 1.549 | 1.5738 | 1.6067 | 1.7203
2022-07-09 14:00 | 3.3533 | 3.6664 | 3.6991 | 3.739 | 3.7856 | 2.0958 | 2.5223 | 2.5477 | 2.5825 | 2.0958 | 2.2673 | 2.5648 | 2.5876 | 2.618 | 2.779
2022-07-09 15:00 | 3.62 | 3.9494 | 3.9802 | 4.0179 | 4.0619 | 2.2482 | 2.6997 | 2.7238 | 2.7566 | 2.2482 | 3.1056 | 3.4938 | 3.5154 | 3.5441 | 3.7491
2022-07-09 16:00 | 3.9906 | 4.3468 | 4.3771 | 4.4143 | 4.4576 | 2.6935 | 3.2252 | 3.2489 | 3.2812 | 2.6935 | 3.8296 | 4.2977 | 4.319 | 4.3473 | 4.5916
2022-07-09 17:00 | 4.6298 | 5.0369 | 5.0691 | 5.1085 | 5.1544 | 3.258 | 3.8946 | 3.9197 | 3.954 | 3.258 | 4.4011 | 4.9354 | 4.958 | 4.9879 | 5.2657
2022-07-09 18:00 | 4.6679 | 5.0852 | 5.1212 | 5.1652 | 5.2164 | 3.2961 | 3.945 | 3.973 | 4.0112 | 3.2961 | 4.4583 | 5.0041 | 5.0293 | 5.0628 | 5.3479
2022-07-09 19:00 | 4.706 | 5.1359 | 5.1768 | 5.2269 | 5.2853 | 3.1949 | 3.8325 | 3.8644 | 3.908 | 3.1949 | 4.6107 | 5.1804 | 5.2091 | 5.2472 | 5.5462
2022-07-09 20:00 | 4.5726 | 5.0023 | 5.0482 | 5.1043 | 5.1698 | 3.1627 | 3.8015 | 3.8373 | 3.8861 | 3.1627 | 5.3728 | 6.0342 | 6.0663 | 6.109 | 6.4554
2022-07-09 21:00 | 4.4223 | 4.8424 | 4.8891 | 4.9463 | 5.0129 | 3.0675 | 3.6902 | 3.7266 | 3.7763 | 3.0675 | 4.0772 | 4.5956 | 4.6283 | 4.6718 | 4.9479
2022-07-09 22:00 | 4.001 | 4.3839 | 4.4276 | 4.481 | 4.5433 | 2.7817 | 3.3482 | 3.3823 | 3.4287 | 2.7817 | 4.344 | 4.8878 | 4.9184 | 4.959 | 5.2464
2022-07-09 23:00 | 3.8867 | 4.2527 | 4.292 | 4.3401 | 4.3963 | 2.4197 | 2.9144 | 2.9451 | 2.987 | 2.4197 | 3.277 | 3.6962 | 3.7237 | 3.7604 | 3.9843
2022-07-10 | 3.4104 | 3.7315 | 3.766 | 3.8082 | 3.8575 | 2.0856 | 2.5129 | 2.5398 | 2.5766 | 2.0856 | 2.5911 | 2.9273 | 2.9515 | 2.9836 | 3.1644
2022-07-10 01:00 | 3.1056 | 3.3944 | 3.424 | 3.4603 | 3.5026 | 1.8672 | 2.2479 | 2.271 | 2.3025 | 1.8672 | 2.2673 | 2.5606 | 2.5813 | 2.6089 | 2.7665
2022-07-10 02:00 | 3.0103 | 3.28 | 3.3034 | 3.3321 | 3.3656 | 1.7147 | 2.059 | 2.0773 | 2.1023 | 1.7147 | 2.1529 | 2.425 | 2.4414 | 2.4632 | 2.6077
2022-07-10 03:00 | 2.8769 | 3.1249 | 3.1423 | 3.1636 | 3.1885 | 1.6004 | 1.9154 | 1.929 | 1.9475 | 1.6004 | 2.1148 | 2.3743 | 2.3865 | 2.4027 | 2.5383
2022-07-10 04:00 | 2.9428 | 3.1856 | 3.1978 | 3.2128 | 3.2303 | 1.6385 | 1.9531 | 1.9627 | 1.9757 | 1.6385 | 2.191 | 2.4518 | 2.4604 | 2.4718 | 2.6059
2022-07-10 05:00 | 3.1818 | 3.4383 | 3.4486 | 3.4611 | 3.4757 | 1.81 | 2.1528 | 2.1608 | 2.1717 | 1.81 | 2.2482 | 2.5125 | 2.5197 | 2.5292 | 2.6642
2022-07-10 06:00 | 3.3533 | 3.6259 | 3.6378 | 3.6524 | 3.6695 | 2.1339 | 2.5378 | 2.5472 | 2.5599 | 2.1339 | 3.3342 | 3.7217 | 3.7301 | 3.7412 | 3.9378
2022-07-10 07:00 | 3.5247 | 3.8192 | 3.8358 | 3.8561 | 3.8797 | 2.2482 | 2.6795 | 2.6924 | 2.7101 | 2.2482 | 3.5438 | 3.961 | 3.9726 | 3.9881 | 4.2014
2022-07-10 08:00 | 3.4104 | 3.7097 | 3.7331 | 3.7618 | 3.7952 | 2.3625 | 2.8242 | 2.8425 | 2.8674 | 2.3625 | 3.3151 | 3.7164 | 3.7328 | 3.7546 | 3.9629
2022-07-10 09:00 | 3.1246 | 3.417 | 3.4476 | 3.4852 | 3.529 | 2.2101 | 2.6545 | 2.6785 | 2.7111 | 2.2101 | 2.4387 | 2.7526 | 2.7741 | 2.8026 | 2.9709
2022-07-10 10:00 | 3.4676 | 3.7963 | 3.8326 | 3.877 | 3.9288 | 2.2101 | 2.6625 | 2.6908 | 2.7294 | 2.2101 | 2.0196 | 2.2946 | 2.32 | 2.3537 | 2.5051
2022-07-10 11:00 | 2.5911 | 2.8591 | 2.8976 | 2.9447 | 2.9996 | 1.5242 | 1.8553 | 1.8854 | 1.9263 | 1.5242 | 1.4861 | 1.7048 | 1.7318 | 1.7676 | 1.8921
2022-07-10 12:00 | 3.1437 | 3.4517 | 3.4896 | 3.5361 | 3.5902 | 1.7909 | 2.1697 | 2.1993 | 2.2397 | 1.7909 | 2.3054 | 2.6145 | 2.6411 | 2.6764 | 2.8454
2022-07-10 13:00 | 2.4768 | 2.7303 | 2.7657 | 2.809 | 2.8595 | 1.5242 | 1.851 | 1.8786 | 1.9163 | 1.5242 | 1.829 | 2.0816 | 2.1064 | 2.1394 | 2.2793
2022-07-10 14:00 | 2.8769 | 3.1547 | 3.1873 | 3.2273 | 3.2739 | 1.9434 | 2.3422 | 2.3677 | 2.4024 | 1.9434 | 1.5433 | 1.7602 | 1.7831 | 1.8135 | 1.9346
2022-07-10 15:00 | 3.1246 | 3.4172 | 3.448 | 3.4857 | 3.5297 | 1.94 | 2.3356 | 2.3596 | 2.3925 | 1.94 | 2.0577 | 2.3293 | 2.3509 | 2.3796 | 2.527
2022-07-10 16:00 | 4.1535 | 4.5217 | 4.552 | 4.5892 | 4.6325 | 2.7501 | 3.2921 | 3.3157 | 3.3481 | 2.7501 | 3.5057 | 3.9378 | 3.9591 | 3.9873 | 4.2139
2022-07-10 17:00 | 5.0489 | 5.4873 | 5.5194 | 5.5588 | 5.6047 | 3.3151 | 3.9621 | 3.9872 | 4.0215 | 3.3151 | 4.2487 | 4.766 | 4.7886 | 4.8185 | 5.0879
2022-07-10 18:00 | 5.1251 | 5.5765 | 5.6124 | 5.6564 | 5.7077 | 3.4104 | 4.08 | 4.108 | 4.1463 | 3.4104 | 5.3347 | 5.9781 | 6.0032 | 6.0367 | 6.37
2022-07-10 19:00 | 4.9727 | 5.4225 | 5.4634 | 5.5135 | 5.5719 | 3.4397 | 4.1217 | 4.1536 | 4.1972 | 3.4397 | 5.2013 | 5.8368 | 5.8654 | 5.9035 | 6.235
2022-07-10 20:00 | 4.9346 | 5.3912 | 5.4371 | 5.4932 | 5.5587 | 3.4676 | 4.1616 | 4.1974 | 4.2462 | 3.4676 | 5.4681 | 6.14 | 6.1722 | 6.2149 | 6.5665
2022-07-10 21:00 | 4.7441 | 5.1882 | 5.2349 | 5.292 | 5.3586 | 3.2288 | 3.8808 | 3.9172 | 3.9669 | 3.2288 | 4.5345 | 5.1037 | 5.1365 | 5.1799 | 5.4812
2022-07-10 22:00 | 4.2235 | 4.6229 | 4.6666 | 4.72 | 4.7823 | 2.8751 | 3.4586 | 3.4927 | 3.5391 | 2.8751 | 3.8105 | 4.295 | 4.3256 | 4.3662 | 4.6243
2022-07-10 23:00 | 3.8677 | 4.2322 | 4.2715 | 4.3197 | 4.3758 | 2.47 | 2.9739 | 3.0046 | 3.0465 | 2.47 | 3.1246 | 3.5268 | 3.5544 | 3.591 | 3.8065
2022-07-11 | 3.5073 | 3.8356 | 3.8701 | 3.9123 | 3.9616 | 2.0691 | 2.4934 | 2.5204 | 2.5571 | 2.0691 | 2.6293 | 2.9696 | 2.9938 | 3.0259 | 3.2089
2022-07-11 01:00 | 3.2389 | 3.5377 | 3.5673 | 3.6036 | 3.6458 | 1.8862 | 2.2704 | 2.2935 | 2.325 | 1.8862 | 2.3244 | 2.6241 | 2.6448 | 2.6724 | 2.8332
2022-07-11 02:00 | 3.1056 | 3.3823 | 3.4058 | 3.4345 | 3.468 | 1.7904 | 2.1484 | 2.1667 | 2.1917 | 1.7904 | 2.3244 | 2.6155 | 2.632 | 2.6538 | 2.8077
2022-07-11 03:00 | 3.0865 | 3.3501 | 3.3675 | 3.3888 | 3.4136 | 1.7147 | 2.0505 | 2.064 | 2.0826 | 1.7147 | 2.2291 | 2.5013 | 2.5135 | 2.5297 | 2.6716
2022-07-11 04:00 | 3.1818 | 3.4423 | 3.4546 | 3.4696 | 3.4871 | 1.8686 | 2.2249 | 2.2344 | 2.2475 | 1.8686 | 3.0865 | 3.4469 | 3.4555 | 3.4669 | 3.6502
2022-07-11 05:00 | 3.7152 | 4.0115 | 4.0217 | 4.0342 | 4.0488 | 2.2912 | 2.7213 | 2.7292 | 2.7401 | 2.2912 | 3.4295 | 3.8252 | 3.8324 | 3.8419 | 4.0418
2022-07-11 06:00 | 4.4716 | 4.8274 | 4.8393 | 4.8539 | 4.871 | 2.915 | 3.4607 | 3.47 | 3.4827 | 2.915 | 4.6298 | 5.1614 | 5.1698 | 5.1809 | 5.4487
2022-07-11 07:00 | 5.0108 | 5.4158 | 5.4324 | 5.4527 | 5.4763 | 3.1818 | 3.7824 | 3.7953 | 3.813 | 3.1818 | 4.363 | 4.8714 | 4.8831 | 4.8985 | 5.1568
2022-07-11 08:00 | 4.9156 | 5.3268 | 5.3502 | 5.3788 | 5.4122 | 3.1056 | 3.702 | 3.7203 | 3.7452 | 3.1056 | 4.1154 | 4.6057 | 4.6221 | 4.6438 | 4.8961
2022-07-11 09:00 | 4.566 | 4.9655 | 4.9962 | 5.0338 | 5.0775 | 2.8007 | 3.3523 | 3.3762 | 3.4089 | 2.8007 | 2.9531 | 3.3242 | 3.3457 | 3.3743 | 3.5708
2022-07-11 10:00 | 3.5438 | 3.8782 | 3.9145 | 3.9589 | 4.0106 | 2.0767 | 2.5049 | 2.5332 | 2.5718 | 2.0767 | 1.7909 | 2.0405 | 2.0659 | 2.0997 | 2.2385
2022-07-11 11:00 | 3.6771 | 4.0258 | 4.0643 | 4.1114 | 4.1664 | 2.1339 | 2.5756 | 2.6056 | 2.6466 | 2.1339 | 1.9243 | 2.1918 | 2.2187 | 2.2546 | 2.4032
2022-07-11 12:00 | 2.9722 | 3.2674 | 3.3054 | 3.3518 | 3.406 | 1.5052 | 1.8321 | 1.8617 | 1.9021 | 1.5052 | 1.1241 | 1.3018 | 1.3284 | 1.3637 | 1.4677
2022-07-11 13:00 | 3.3533 | 3.6718 | 3.7072 | 3.7506 | 3.8011 | 1.8862 | 2.2786 | 2.3062 | 2.3439 | 1.8862 | 1.3527 | 1.5523 | 1.5771 | 1.6101 | 1.7239
2022-07-11 14:00 | 3.0484 | 3.3389 | 3.3716 | 3.4115 | 3.4581 | 1.7338 | 2.0946 | 2.1201 | 2.1548 | 1.7338 | 1.2956 | 1.485 | 1.5078 | 1.5382 | 1.6458
2022-07-11 15:00 | 3.5057 | 3.8266 | 3.8574 | 3.8951 | 3.9391 | 2.1299 | 2.5599 | 2.584 | 2.6168 | 2.1299 | 1.9815 | 2.2446 | 2.2662 | 2.2949 | 2.4381
2022-07-11 16:00 | 4.3821 | 4.7673 | 4.7977 | 4.8348 | 4.8782 | 2.7435 | 3.2842 | 3.3079 | 3.3402 | 2.7435 | 3.258 | 3.6626 | 3.6838 | 3.7121 | 3.925
2022-07-11 17:00 | 5.1632 | 5.6101 | 5.6423 | 5.6816 | 5.7276 | 3.3723 | 4.0296 | 4.0547 | 4.089 | 3.3723 | 4.7441 | 5.3165 | 5.3391 | 5.369 | 5.6656
2022-07-11 18:00 | 5.6015 | 6.0882 | 6.1242 | 6.1681 | 6.2194 | 3.7343 | 4.4626 | 4.4907 | 4.5289 | 3.7343 | 5.3728 | 6.0204 | 6.0456 | 6.079 | 6.4144
2022-07-11 19:00 | 5.5062 | 5.9956 | 6.0365 | 6.0866 | 6.145 | 3.7724 | 4.5147 | 4.5466 | 4.5902 | 3.7724 | 6.1921 | 6.9377 | 6.9664 | 7.0045 | 7.3904
2022-07-11 20:00 | 5.3347 | 5.8211 | 5.8669 | 5.9231 | 5.9885 | 3.6771 | 4.4092 | 4.445 | 4.4938 | 3.6771 | 5.2013 | 5.8436 | 5.8758 | 5.9184 | 6.2554
2022-07-11 21:00 | 5.0489 | 5.5157 | 5.5624 | 5.6195 | 5.6861 | 3.3223 | 3.9912 | 4.0276 | 4.0773 | 3.3223 | 5.1632 | 5.8024 | 5.8351 | 5.8786 | 6.2144
2022-07-11 22:00 | 4.5345 | 4.9571 | 5.0007 | 5.0541 | 5.1164 | 3.0645 | 3.6823 | 3.7164 | 3.7628 | 3.0645 | 3.8296 | 4.3162 | 4.3467 | 4.3874 | 4.6465
2022-07-11 23:00 | 3.963 | 4.3346 | 4.374 | 4.4221 | 4.4782 | 2.4746 | 2.9793 | 3.01 | 3.0519 | 2.4746 | 3.3723 | 3.802 | 3.8296 | 3.8662 | 4.0954
2022-07-12 | 3.5247 | 3.8543 | 3.8888 | 3.9311 | 3.9803 | 2.0958 | 2.5249 | 2.5518 | 2.5886 | 2.0958 | 2.915 | 3.2872 | 3.3114 | 3.3435 | 3.5422
2022-07-12 01:00 | 3.3151 | 3.6196 | 3.6492 | 3.6854 | 3.7277 | 1.9003 | 2.2871 | 2.3102 | 2.3417 | 1.9003 | 2.5911 | 2.9205 | 2.9413 | 2.9688 | 3.1442
2022-07-12 02:00 | 3.258 | 3.5461 | 3.5695 | 3.5982 | 3.6317 | 1.829 | 2.1941 | 2.2124 | 2.2374 | 1.829 | 2.7817 | 3.1237 | 3.1401 | 3.1619 | 3.3409
2022-07-12 03:00 | 3.277 | 3.5547 | 3.5722 | 3.5935 | 3.6183 | 1.8672 | 2.2305 | 2.2441 | 2.2626 | 1.8672 | 3.0484 | 3.4117 | 3.4239 | 3.4401 | 3.6271
2022-07-12 04:00 | 3.4295 | 3.7084 | 3.7207 | 3.7357 | 3.7532 | 1.9301 | 2.2975 | 2.3071 | 2.3201 | 1.9301 | 3.6009 | 4.0186 | 4.0271 | 4.0386 | 4.2502
2022-07-12 05:00 | 3.9997 | 4.3171 | 4.3273 | 4.3398 | 4.3544 | 2.3849 | 2.832 | 2.8399 | 2.8508 | 2.3849 | 3.7915 | 4.2275 | 4.2346 | 4.2442 | 4.464
2022-07-12 06:00 | 4.8393 | 5.2225 | 5.2344 | 5.249 | 5.2661 | 3.1056 | 3.6857 | 3.6951 | 3.7078 | 3.1056 | 4.4964 | 5.0132 | 5.0216 | 5.0327 | 5.2931
2022-07-12 07:00 | 5.2776 | 5.7024 | 5.7189 | 5.7392 | 5.7629 | 3.2961 | 3.9174 | 3.9304 | 3.948 | 3.2961 | 4.8012 | 5.3584 | 5.37 | 5.3855 | 5.6678
2022-07-12 08:00 | 5.3919 | 5.8385 | 5.8619 | 5.8906 | 5.924 | 3.2961 | 3.9271 | 3.9454 | 3.9703 | 3.2961 | 5.087 | 5.6854 | 5.7018 | 5.7236 | 6.0293
2022-07-12 09:00 | 5.3919 | 5.8528 | 5.8834 | 5.921 | 5.9648 | 3.2008 | 3.8249 | 3.8489 | 3.8815 | 3.2008 | 4.1483 | 4.6523 | 4.6738 | 4.7024 | 4.9646
2022-07-12 10:00 | 4.1338 | 4.5121 | 4.5484 | 4.5928 | 4.6446 | 2.3435 | 2.82 | 2.8483 | 2.8869 | 2.3435 | 2.5149 | 2.845 | 2.8704 | 2.9042 | 3.0828
2022-07-12 11:00 | 4.4964 | 4.906 | 4.9445 | 4.9916 | 5.0465 | 2.4768 | 2.9807 | 3.0108 | 3.0517 | 2.4768 | 2.191 | 2.4882 | 2.5151 | 2.551 | 2.7143
2022-07-12 12:00 | 3.1627 | 3.4721 | 3.5101 | 3.5565 | 3.6107 | 1.6004 | 1.9446 | 1.9742 | 2.0146 | 1.6004 | 0.78115 | 0.92069 | 0.94727 | 0.9826 | 1.0678
2022-07-12 13:00 | 3.4676 | 3.7946 | 3.83 | 3.8734 | 3.9239 | 1.7317 | 2.0961 | 2.1237 | 2.1614 | 1.7317 | 1.105 | 1.2771 | 1.3019 | 1.3348 | 1.435
2022-07-12 14:00 | 3.8677 | 4.2191 | 4.2517 | 4.2917 | 4.3383 | 2.2564 | 2.712 | 2.7375 | 2.7722 | 2.2564 | 2.1148 | 2.3954 | 2.4182 | 2.4486 | 2.6012
2022-07-12 15:00 | 4.1725 | 4.543 | 4.5738 | 4.6115 | 4.6555 | 2.5149 | 3.0148 | 3.0389 | 3.0717 | 2.5149 | 2.9341 | 3.3032 | 3.3248 | 3.3535 | 3.5491
2022-07-12 16:00 | 4.7631 | 5.1767 | 5.207 | 5.2442 | 5.2875 | 3.1203 | 3.7294 | 3.7531 | 3.7854 | 3.1203 | 4.0582 | 4.5518 | 4.5731 | 4.6013 | 4.8582
2022-07-12 17:00 | 5.3728 | 5.8352 | 5.8674 | 5.9068 | 5.9527 | 3.7152 | 4.4348 | 4.4599 | 4.4941 | 3.7152 | 4.7822 | 5.3589 | 5.3814 | 5.4114 | 5.7101
2022-07-12 18:00 | 5.5633 | 6.0473 | 6.0832 | 6.1272 | 6.1785 | 3.8486 | 4.5977 | 4.6257 | 4.664 | 3.8486 | 4.8393 | 5.4276 | 5.4528 | 5.4862 | 5.7923
2022-07-12 19:00 | 5.3728 | 5.8523 | 5.8933 | 5.9433 | 6.0017 | 3.7724 | 4.5147 | 4.5466 | 4.5902 | 3.7724 | 4.8775 | 5.4768 | 5.5055 | 5.5436 | 5.8573
2022-07-12 20:00 | 5.1823 | 5.6573 | 5.7032 | 5.7593 | 5.8248 | 3.639 | 4.3642 | 4.4 | 4.4488 | 3.639 | 4.7441 | 5.3355 | 5.3676 | 5.4103 | 5.7222
2022-07-12 21:00 | 4.8752 | 5.329 | 5.3757 | 5.4329 | 5.4995 | 3.3421 | 4.0146 | 4.051 | 4.1007 | 3.3421 | 4.6679 | 5.252 | 5.2847 | 5.3281 | 5.6367
2022-07-12 22:00 | 4.2106 | 4.6091 | 4.6527 | 4.7062 | 4.7685 | 2.8942 | 3.4812 | 3.5152 | 3.5617 | 2.8942 | 3.8867 | 4.3797 | 4.4103 | 4.4509 | 4.7131
2022-07-12 23:00 | 3.7534 | 4.1094 | 4.1487 | 4.1969 | 4.253 | 2.3671 | 2.8523 | 2.883 | 2.9249 | 2.3671 | 2.9531 | 3.3363 | 3.3638 | 3.4004 | 3.6066
2022-07-13 | 3.2961 | 3.6087 | 3.6432 | 3.6854 | 3.7347 | 1.9743 | 2.3814 | 2.4083 | 2.4451 | 1.9743 | 2.4768 | 2.8003 | 2.8244 | 2.8566 | 3.0311
2022-07-13 01:00 | 3.1818 | 3.4763 | 3.5059 | 3.5422 | 3.5844 | 1.8231 | 2.1958 | 2.2189 | 2.2505 | 1.8231 | 2.4006 | 2.7088 | 2.7295 | 2.7571 | 2.922
2022-07-13 02:00 | 3.0484 | 3.3209 | 3.3444 | 3.3731 | 3.4065 | 1.7288 | 2.0756 | 2.0939 | 2.1189 | 1.7288 | 2.3435 | 2.6367 | 2.6531 | 2.675 | 2.8299
2022-07-13 03:00 | 3.0103 | 3.2682 | 3.2856 | 3.3069 | 3.3317 | 1.7147 | 2.0505 | 2.064 | 2.0826 | 1.7147 | 2.3435 | 2.6283 | 2.6405 | 2.6567 | 2.8049
2022-07-13 04:00 | 3.0865 | 3.34 | 3.3522 | 3.3672 | 3.3847 | 1.7996 | 2.1433 | 2.1529 | 2.166 | 1.7996 | 2.3816 | 2.6635 | 2.6721 | 2.6835 | 2.8281
2022-07-13 05:00 | 3.5819 | 3.8682 | 3.8784 | 3.891 | 3.9056 | 2.2291 | 2.6479 | 2.6559 | 2.6668 | 2.2291 | 3.0484 | 3.4018 | 3.4089 | 3.4184 | 3.5974
2022-07-13 06:00 | 4.2678 | 4.6084 | 4.6204 | 4.635 | 4.652 | 2.8419 | 3.3743 | 3.3836 | 3.3963 | 2.8419 | 4.4583 | 4.9709 | 4.9792 | 4.9903 | 5.2487
2022-07-13 07:00 | 4.7822 | 5.1702 | 5.1867 | 5.207 | 5.2307 | 3.2172 | 3.8242 | 3.8372 | 3.8548 | 3.2172 | 4.3059 | 4.8079 | 4.8195 | 4.835 | 5.0901
2022-07-13 08:00 | 5.068 | 5.4906 | 5.5139 | 5.5426 | 5.576 | 3.2961 | 3.9271 | 3.9454 | 3.9703 | 3.2961 | 4.4011 | 4.9232 | 4.9396 | 4.9614 | 5.2294
2022-07-13 09:00 | 4.8203 | 5.2387 | 5.2694 | 5.3069 | 5.3507 | 2.9683 | 3.5502 | 3.5741 | 3.6068 | 2.9683 | 3.62 | 4.0653 | 4.0868 | 4.1153 | 4.3485
2022-07-13 10:00 | 3.62 | 3.9601 | 3.9964 | 4.0407 | 4.0925 | 2.0577 | 2.4824 | 2.5107 | 2.5493 | 2.0577 | 1.5814 | 1.8076 | 1.833 | 1.8668 | 1.9941
2022-07-13 11:00 | 3.7724 | 4.1282 | 4.1667 | 4.2138 | 4.2687 | 2.0767 | 2.5081 | 2.5381 | 2.5791 | 2.0767 | 1.6576 | 1.8954 | 1.9223 | 1.9581 | 2.0921
2022-07-13 12:00 | 3.8296 | 4.1885 | 4.2265 | 4.2729 | 4.3271 | 2.0767 | 2.5073 | 2.5369 | 2.5773 | 2.0767 | 1.467 | 1.6829 | 1.7095 | 1.7448 | 1.8677
2022-07-13 13:00 | 3.3151 | 3.6309 | 3.6663 | 3.7096 | 3.7601 | 1.81 | 2.1886 | 2.2162 | 2.2539 | 1.81 | 1.1432 | 1.3194 | 1.3442 | 1.3772 | 1.4794
2022-07-13 14:00 | 3.7534 | 4.0963 | 4.1289 | 4.1689 | 4.2154 | 2.0957 | 2.5221 | 2.5476 | 2.5823 | 2.0957 | 1.8481 | 2.099 | 2.1218 | 2.1522 | 2.2901
2022-07-13 15:00 | 3.8105 | 4.1541 | 4.1849 | 4.2226 | 4.2666 | 2.2863 | 2.7447 | 2.7688 | 2.8016 | 2.2863 | 2.4959 | 2.8163 | 2.8379 | 2.8665 | 3.038
2022-07-13 16:00 | 4.5345 | 4.9311 | 4.9614 | 4.9986 | 5.0419 | 2.7416 | 3.282 | 3.3057 | 3.338 | 2.7416 | 3.2389 | 3.6414 | 3.6627 | 3.6909 | 3.9028
2022-07-13 17:00 | 5.307 | 5.7645 | 5.7967 | 5.8361 | 5.882 | 3.5057 | 4.1872 | 4.2123 | 4.2466 | 3.5057 | 4.5345 | 5.0836 | 5.1062 | 5.1361 | 5.4212
2022-07-13 18:00 | 5.5443 | 6.0268 | 6.0627 | 6.1067 | 6.158 | 3.7534 | 4.4851 | 4.5132 | 4.5514 | 3.7534 | 4.9727 | 5.5758 | 5.601 | 5.6344 | 5.9478
2022-07-13 19:00 | 5.6205 | 6.1184 | 6.1594 | 6.2094 | 6.2678 | 3.8677 | 4.6273 | 4.6592 | 4.7028 | 3.8677 | 5.2966 | 5.9426 | 5.9713 | 6.0094 | 6.3461
2022-07-13 20:00 | 5.5252 | 6.0258 | 6.0716 | 6.1278 | 6.1932 | 3.8867 | 4.6568 | 4.6926 | 4.7414 | 3.8867 | 6.154 | 6.9022 | 6.9344 | 6.9771 | 7.3664
2022-07-13 21:00 | 5.2204 | 5.6999 | 5.7466 | 5.8037 | 5.8704 | 3.5438 | 4.2528 | 4.2893 | 4.339 | 3.5438 | 4.7822 | 5.379 | 5.4117 | 5.4552 | 5.77
2022-07-13 22:00 | 4.7326 | 5.1699 | 5.2135 | 5.267 | 5.3293 | 3.0761 | 3.696 | 3.7301 | 3.7765 | 3.0761 | 3.9058 | 4.4008 | 4.4314 | 4.4721 | 4.7354
2022-07-13 23:00 | 4.0391 | 4.4164 | 4.4558 | 4.5039 | 4.56 | 2.5812 | 3.1052 | 3.1359 | 3.1778 | 2.5812 | 3.156 | 3.5617 | 3.5893 | 3.6259 | 3.8432
2022-07-14 | 3.639 | 3.9771 | 4.0116 | 4.0539 | 4.1031 | 2.172 | 2.615 | 2.6419 | 2.6786 | 2.172 | 2.6864 | 3.0331 | 3.0573 | 3.0894 | 3.2755
2022-07-14 01:00 | 3.2199 | 3.5172 | 3.5468 | 3.5831 | 3.6254 | 1.967 | 2.3658 | 2.3889 | 2.4205 | 1.967 | 2.4768 | 2.7935 | 2.8142 | 2.8418 | 3.0109
2022-07-14 02:00 | 3.1627 | 3.4437 | 3.4672 | 3.4959 | 3.5294 | 1.836 | 2.2023 | 2.2206 | 2.2456 | 1.836 | 2.7817 | 3.1237 | 3.1401 | 3.1619 | 3.3409
2022-07-14 03:00 | 3.1437 | 3.4115 | 3.4289 | 3.4502 | 3.475 | 1.8672 | 2.2305 | 2.2441 | 2.2626 | 1.8672 | 2.3244 | 2.6072 | 2.6194 | 2.6356 | 2.7827
2022-07-14 04:00 | 3.2008 | 3.4628 | 3.475 | 3.4901 | 3.5076 | 1.9774 | 2.3534 | 2.363 | 2.3761 | 1.9774 | 2.4387 | 2.7271 | 2.7356 | 2.7471 | 2.8948
2022-07-14 05:00 | 3.62 | 3.9091 | 3.9194 | 3.9319 | 3.9465 | 2.3822 | 2.8288 | 2.8368 | 2.8477 | 2.3822 | 3.6009 | 4.0157 | 4.0229 | 4.0324 | 4.2418
2022-07-14 06:00 | 4.4392 | 4.7926 | 4.8046 | 4.8192 | 4.8362 | 2.9722 | 3.5282 | 3.5375 | 3.5502 | 2.9722 | 3.9439 | 4.3992 | 4.4076 | 4.4187 | 4.6488
2022-07-14 07:00 | 5.068 | 5.4772 | 5.4938 | 5.5141 | 5.5377 | 3.0865 | 3.6698 | 3.6828 | 3.7004 | 3.0865 | 4.1916 | 4.6809 | 4.6925 | 4.7079 | 4.9568
2022-07-14 08:00 | 4.8393 | 5.2449 | 5.2683 | 5.297 | 5.3304 | 3.0149 | 3.5949 | 3.6132 | 3.6381 | 3.0149 | 4.2868 | 4.7962 | 4.8126 | 4.8344 | 5.0961
2022-07-14 09:00 | 4.4774 | 4.8703 | 4.9009 | 4.9385 | 4.9823 | 2.5721 | 3.0822 | 3.1061 | 3.1388 | 2.5721 | 2.594 | 2.9251 | 2.9466 | 2.9752 | 3.1519
2022-07-14 10:00 | 3.5502 | 3.8851 | 3.9214 | 3.9657 | 4.0175 | 1.9951 | 2.4085 | 2.4368 | 2.4755 | 1.9951 | 1.3146 | 1.5112 | 1.5366 | 1.5703 | 1.683
2022-07-14 11:00 | 2.9913 | 3.289 | 3.3274 | 3.3745 | 3.4295 | 1.6385 | 1.9904 | 2.0204 | 2.0614 | 1.6385 | 0.62873 | 0.75206 | 0.77902 | 0.81485 | 0.89225
2022-07-14 12:00 | 2.7436 | 3.0218 | 3.0598 | 3.1062 | 3.1604 | 1.3337 | 1.6295 | 1.6591 | 1.6995 | 1.3337 | 0.74305 | 0.87834 | 0.90493 | 0.94026 | 1.0233
2022-07-14 13:00 | 2.5721 | 2.8326 | 2.868 | 2.9113 | 2.9619 | 1.3586 | 1.6553 | 1.6829 | 1.7206 | 1.3586 | 0.724 | 0.85364 | 0.87844 | 0.9114 | 0.99061
2022-07-14 14:00 | 2.7436 | 3.0114 | 3.0441 | 3.084 | 3.1306 | 1.4503 | 1.7598 | 1.7852 | 1.82 | 1.4503 | 0.7621 | 0.89215 | 0.91502 | 0.9454 | 1.0236
2022-07-14 15:00 | 3.1818 | 3.4786 | 3.5094 | 3.5471 | 3.5911 | 1.8209 | 2.1949 | 2.219 | 2.2518 | 1.8209 | 1.4861 | 1.6942 | 1.7157 | 1.7444 | 1.8604
2022-07-14 16:00 | 4.0772 | 4.4398 | 4.4702 | 4.5073 | 4.5507 | 2.5445 | 3.0492 | 3.0728 | 3.1052 | 2.5445 | 3.0484 | 3.4297 | 3.4509 | 3.4792 | 3.6806
2022-07-14 17:00 | 5.068 | 5.5077 | 5.5399 | 5.5793 | 5.6252 | 3.3914 | 4.0521 | 4.0772 | 4.1115 | 3.3914 | 4.7441 | 5.3165 | 5.3391 | 5.369 | 5.6656
2022-07-14 18:00 | 5.4871 | 5.9654 | 6.0013 | 6.0453 | 6.0966 | 3.6569 | 4.3712 | 4.3993 | 4.4375 | 3.6569 | 5.1061 | 5.724 | 5.7492 | 5.7826 | 6.1033
2022-07-14 19:00 | 5.4681 | 5.9547 | 5.9956 | 6.0457 | 6.1041 | 3.8105 | 4.5597 | 4.5917 | 4.6352 | 3.8105 | 6.2302 | 6.9801 | 7.0087 | 7.0468 | 7.4349
2022-07-14 20:00 | 5.449 | 5.9439 | 5.9898 | 6.0459 | 6.1113 | 3.8105 | 4.5668 | 4.6025 | 4.6514 | 3.8105 | 5.5824 | 6.2671 | 6.2992 | 6.3419 | 6.6998
2022-07-14 21:00 | 5.068 | 5.5361 | 5.5828 | 5.64 | 5.7066 | 3.5232 | 4.2286 | 4.265 | 4.3147 | 3.5232 | 5.2204 | 5.866 | 5.8987 | 5.9421 | 6.2811
2022-07-14 22:00 | 4.732 | 5.1692 | 5.2129 | 5.2663 | 5.3286 | 3.277 | 3.9334 | 3.9675 | 4.0139 | 3.277 | 4.344 | 4.8878 | 4.9184 | 4.959 | 5.2464
2022-07-14 23:00 | 4.1916 | 4.5802 | 4.6195 | 4.6676 | 4.7238 | 2.7518 | 3.3067 | 3.3374 | 3.3793 | 2.7518 | 3.6962 | 4.162 | 4.1895 | 4.2261 | 4.4731
2022-07-15 | 3.7761 | 4.1244 | 4.1589 | 4.2011 | 4.2504 | 2.3244 | 2.795 | 2.8219 | 2.8587 | 2.3244 | 3.1818 | 3.5836 | 3.6078 | 3.6399 | 3.8533
2022-07-15 01:00 | 3.5247 | 3.8447 | 3.8744 | 3.9106 | 3.9529 | 2.0577 | 2.473 | 2.4961 | 2.5276 | 2.0577 | 2.7245 | 3.0687 | 3.0895 | 3.117 | 3.2998
2022-07-15 02:00 | 3.3914 | 3.6894 | 3.7128 | 3.7415 | 3.775 | 1.9434 | 2.3291 | 2.3474 | 2.3724 | 1.9434 | 2.6483 | 2.9755 | 2.9919 | 3.0137 | 3.1854
2022-07-15 03:00 | 3.3533 | 3.6366 | 3.654 | 3.6753 | 3.7002 | 1.951 | 2.3296 | 2.3432 | 2.3618 | 1.951 | 2.7055 | 3.0306 | 3.0428 | 3.059 | 3.2271
2022-07-15 04:00 | 3.5628 | 3.8517 | 3.864 | 3.879 | 3.8965 | 2.1065 | 2.506 | 2.5155 | 2.5286 | 2.1065 | 2.8769 | 3.214 | 3.2226 | 3.234 | 3.4058
2022-07-15 05:00 | 4.001 | 4.3185 | 4.3287 | 4.3413 | 4.3559 | 2.5864 | 3.07 | 3.078 | 3.0889 | 2.5864 | 3.8677 | 4.3122 | 4.3193 | 4.3289 | 4.5529
2022-07-15 06:00 | 4.9014 | 5.2891 | 5.3011 | 5.3157 | 5.3327 | 3.1226 | 3.7059 | 3.7152 | 3.7279 | 3.1226 | 4.6675 | 5.2033 | 5.2117 | 5.2228 | 5.4927
2022-07-15 07:00 | 5.3728 | 5.8047 | 5.8213 | 5.8416 | 5.8652 | 3.4866 | 4.1425 | 4.1554 | 4.1731 | 3.4866 | 5.5062 | 6.1418 | 6.1534 | 6.1688 | 6.49
2022-07-15 08:00 | 5.3919 | 5.8385 | 5.8619 | 5.8906 | 5.924 | 3.4104 | 4.0622 | 4.0804 | 4.1053 | 3.4104 | 4.6107 | 5.1561 | 5.1725 | 5.1943 | 5.4738
2022-07-15 09:00 | 4.9918 | 5.4229 | 5.4536 | 5.4911 | 5.5349 | 3.0103 | 3.5998 | 3.6237 | 3.6564 | 3.0103 | 3.8677 | 4.3405 | 4.362 | 4.3906 | 4.6373
2022-07-15 10:00 | 4.1344 | 4.5128 | 4.549 | 4.5934 | 4.6452 | 2.4841 | 2.9862 | 3.0145 | 3.0531 | 2.4841 | 2.4959 | 2.8239 | 2.8493 | 2.883 | 3.0606
2022-07-15 11:00 | 3.4295 | 3.7597 | 3.7982 | 3.8453 | 3.9003 | 1.9243 | 2.328 | 2.358 | 2.399 | 1.9243 | 1.0479 | 1.2178 | 1.2448 | 1.2806 | 1.3811
2022-07-15 12:00 | 3.1246 | 3.4312 | 3.4691 | 3.5156 | 3.5697 | 1.5433 | 1.8771 | 1.9067 | 1.9471 | 1.5433 | 0.64779 | 0.77248 | 0.79907 | 0.8344 | 0.91225
2022-07-15 13:00 | 2.915 | 3.201 | 3.2364 | 3.2798 | 3.3303 | 1.5242 | 1.851 | 1.8786 | 1.9163 | 1.5242 | 0.87642 | 1.023 | 1.0478 | 1.0808 | 1.1684
2022-07-15 14:00 | 3.1056 | 3.4003 | 3.433 | 3.4729 | 3.5195 | 1.6576 | 2.0046 | 2.03 | 2.0648 | 1.6576 | 0.93358 | 1.0827 | 1.1056 | 1.136 | 1.2236
2022-07-15 15:00 | 3.5628 | 3.888 | 3.9188 | 3.9565 | 4.0005 | 2.1281 | 2.5578 | 2.5818 | 2.6147 | 2.1281 | 2.0005 | 2.2658 | 2.2874 | 2.3161 | 2.4603
2022-07-15 16:00 | 4.344 | 4.7264 | 4.7567 | 4.7939 | 4.8372 | 2.7324 | 3.2711 | 3.2948 | 3.3271 | 2.7324 | 3.2199 | 3.6202 | 3.6415 | 3.6698 | 3.8806
2022-07-15 17:00 | 5.1061 | 5.5487 | 5.5808 | 5.6202 | 5.6661 | 3.5628 | 4.2547 | 4.2798 | 4.3141 | 3.5628 | 4.5726 | 5.126 | 5.1485 | 5.1785 | 5.4657
2022-07-15 18:00 | 5.3157 | 5.7812 | 5.8171 | 5.8611 | 5.9124 | 3.6771 | 4.3951 | 4.4231 | 4.4614 | 3.6771 | 5.1823 | 5.8087 | 5.8339 | 5.8673 | 6.1922
2022-07-15 19:00 | 5.3919 | 5.8728 | 5.9137 | 5.9638 | 6.0222 | 3.7343 | 4.4697 | 4.5016 | 4.5452 | 3.7343 | 5.9444 | 6.6625 | 6.6912 | 6.7292 | 7.1016
2022-07-15 20:00 | 5.2395 | 5.7187 | 5.7646 | 5.8207 | 5.8862 | 3.7915 | 4.5443 | 4.58 | 4.6289 | 3.7915 | 5.7729 | 6.4788 | 6.5109 | 6.5536 | 6.922
2022-07-15 21:00 | 5.0299 | 5.4952 | 5.5419 | 5.599 | 5.6657 | 3.5479 | 4.2577 | 4.2941 | 4.3438 | 3.5479 | 5.6586 | 6.3529 | 6.3856 | 6.4291 | 6.7921
2022-07-15 22:00 | 4.7441 | 5.1822 | 5.2259 | 5.2793 | 5.3416 | 3.3427 | 4.011 | 4.045 | 4.0915 | 3.3427 | 4.363 | 4.909 | 4.9396 | 4.9802 | 5.2686
2022-07-15 23:00 | 4.2868 | 4.6825 | 4.7218 | 4.77 | 4.8261 | 2.915 | 3.4996 | 3.5303 | 3.5722 | 2.915 | 3.5438 | 3.9926 | 4.0201 | 4.0568 | 4.2954
2022-07-16 | 3.8677 | 4.2228 | 4.2573 | 4.2995 | 4.3487 | 2.5149 | 3.0201 | 3.047 | 3.0838 | 2.5149 | 3.0484 | 3.4354 | 3.4596 | 3.4917 | 3.6977
2022-07-16 01:00 | 3.5247 | 3.8447 | 3.8744 | 3.9106 | 3.9529 | 2.1827 | 2.6207 | 2.6438 | 2.6753 | 2.1827 | 3.2961 | 3.7039 | 3.7246 | 3.7522 | 3.9664
2022-07-16 02:00 | 3.4485 | 3.7508 | 3.7742 | 3.8029 | 3.8364 | 2.0767 | 2.4867 | 2.505 | 2.53 | 2.0767 | 2.553 | 2.8696 | 2.886 | 2.9079 | 3.0743
2022-07-16 03:00 | 3.277 | 3.5547 | 3.5722 | 3.5935 | 3.6183 | 1.9624 | 2.3431 | 2.3566 | 2.3752 | 1.9624 | 2.534 | 2.8401 | 2.8523 | 2.8685 | 3.0271
2022-07-16 04:00 | 3.2961 | 3.5651 | 3.5774 | 3.5924 | 3.6099 | 1.968 | 2.3424 | 2.3519 | 2.365 | 1.968 | 2.6293 | 2.9388 | 2.9474 | 2.9588 | 3.117
2022-07-16 05:00 | 3.5438 | 3.8273 | 3.8375 | 3.85 | 3.8646 | 2.2291 | 2.648 | 2.6559 | 2.6668 | 2.2291 | 3.0675 | 3.4229 | 3.4301 | 3.4396 | 3.6196
2022-07-16 06:00 | 3.7343 | 4.0353 | 4.0472 | 4.0618 | 4.0789 | 2.5149 | 2.988 | 2.9973 | 3.01 | 2.5149 | 3.5628 | 3.9758 | 3.9841 | 3.9952 | 4.2044
2022-07-16 07:00 | 4.1916 | 4.5356 | 4.5522 | 4.5725 | 4.5962 | 2.8487 | 3.3889 | 3.4018 | 3.4195 | 2.8487 | 4.001 | 4.4692 | 4.4808 | 4.4962 | 4.7346
2022-07-16 08:00 | 4.6679 | 5.0607 | 5.0841 | 5.1127 | 5.1461 | 3.0865 | 3.6795 | 3.6978 | 3.7227 | 3.0865 | 5.2966 | 5.9183 | 5.9347 | 5.9565 | 6.2737
2022-07-16 09:00 | 4.725 | 5.1364 | 5.167 | 5.2046 | 5.2484 | 2.9919 | 3.5781 | 3.6021 | 3.6347 | 2.9919 | 5.4109 | 6.0555 | 6.077 | 6.1055 | 6.4371
2022-07-16 10:00 | 3.9104 | 4.2721 | 4.3084 | 4.3527 | 4.4045 | 2.5623 | 3.0786 | 3.1069 | 3.1455 | 2.5623 | 3.1056 | 3.5014 | 3.5268 | 3.5605 | 3.7716
2022-07-16 11:00 | 3.4104 | 3.7393 | 3.7778 | 3.8249 | 3.8798 | 2.1339 | 2.5756 | 2.6056 | 2.6466 | 2.1339 | 2.2863 | 2.594 | 2.621 | 2.6568 | 2.8254
2022-07-16 12:00 | 3.6962 | 4.0453 | 4.0832 | 4.1297 | 4.1838 | 2.4768 | 2.98 | 3.0096 | 3.05 | 2.4768 | 2.534 | 2.8685 | 2.8951 | 2.9304 | 3.112
2022-07-16 13:00 | 3.4295 | 3.7537 | 3.7891 | 3.8324 | 3.883 | 2.172 | 2.6162 | 2.6438 | 2.6815 | 2.172 | 2.172 | 2.4627 | 2.4875 | 2.5205 | 2.6793
2022-07-16 14:00 | 3.3342 | 3.646 | 3.6786 | 3.7185 | 3.7651 | 2.2101 | 2.6573 | 2.6828 | 2.7175 | 2.2101 | 2.1339 | 2.4166 | 2.4394 | 2.4698 | 2.6234
2022-07-16 15:00 | 3.4295 | 3.7447 | 3.7755 | 3.8132 | 3.8572 | 2.3254 | 2.7909 | 2.815 | 2.8478 | 2.3254 | 2.5149 | 2.8375 | 2.859 | 2.8877 | 3.0603
2022-07-16 16:00 | 4.344 | 4.7264 | 4.7567 | 4.7939 | 4.8372 | 2.8388 | 3.3968 | 3.4205 | 3.4529 | 2.8388 | 3.7298 | 4.1868 | 4.2081 | 4.2364 | 4.4752
2022-07-16 17:00 | 5.1632 | 5.6101 | 5.6423 | 5.6816 | 5.7276 | 3.5628 | 4.2547 | 4.2798 | 4.3141 | 3.5628 | 4.8203 | 5.4012 | 5.4237 | 5.4537 | 5.7545
2022-07-16 18:00 | 5.4109 | 5.8835 | 5.9195 | 5.9634 | 6.0147 | 3.6771 | 4.3951 | 4.4231 | 4.4614 | 3.6771 | 5.1251 | 5.7452 | 5.7703 | 5.8038 | 6.1256
2022-07-16 19:00 | 5.3919 | 5.8728 | 5.9137 | 5.9638 | 6.0222 | 3.6771 | 4.4022 | 4.4341 | 4.4777 | 3.6771 | 5.5633 | 6.239 | 6.2677 | 6.3058 | 6.6572
2022-07-16 20:00 | 5.1823 | 5.6573 | 5.7032 | 5.7593 | 5.8248 | 3.7152 | 4.4542 | 4.49 | 4.5388 | 3.7152 | 6.2873 | 7.0504 | 7.0826 | 7.1253 | 7.522
2022-07-16 21:00 | 5.0805 | 5.5496 | 5.5963 | 5.6534 | 5.7201 | 3.5542 | 4.2651 | 4.3015 | 4.3513 | 3.5542 | 4.9537 | 5.5695 | 5.6023 | 5.6457 | 5.97
2022-07-16 22:00 | 4.6488 | 5.0799 | 5.1235 | 5.1769 | 5.2392 | 3.2832 | 3.9407 | 3.9747 | 4.0212 | 3.2832 | 4.8393 | 5.4383 | 5.4689 | 5.5095 | 5.8241
2022-07-16 23:00 | 4.2868 | 4.6825 | 4.7218 | 4.77 | 4.8261 | 2.6838 | 3.2265 | 3.2572 | 3.2991 | 2.6838 | 3.6962 | 4.162 | 4.1895 | 4.2261 | 4.4731
2022-07-17 | 3.7152 | 4.059 | 4.0935 | 4.1357 | 4.185 | 2.4197 | 2.9076 | 2.9345 | 2.9712 | 2.4197 | 2.9341 | 3.3084 | 3.3326 | 3.3647 | 3.5644
2022-07-17 01:00 | 3.43 | 3.743 | 3.7726 | 3.8089 | 3.8512 | 2.0958 | 2.518 | 2.5411 | 2.5726 | 2.0958 | 2.5149 | 2.8358 | 2.8566 | 2.8841 | 3.0554
2022-07-17 02:00 | 3.258 | 3.5461 | 3.5695 | 3.5982 | 3.6317 | 1.9594 | 2.3481 | 2.3664 | 2.3914 | 1.9594 | 2.3435 | 2.6367 | 2.6531 | 2.675 | 2.8299
2022-07-17 03:00 | 3.0865 | 3.3501 | 3.3675 | 3.3888 | 3.4136 | 1.81 | 2.163 | 2.1766 | 2.1951 | 1.81 | 2.6102 | 2.9247 | 2.9369 | 2.9531 | 3.116
2022-07-17 04:00 | 3.0675 | 3.3195 | 3.3318 | 3.3468 | 3.3643 | 1.8862 | 2.2457 | 2.2553 | 2.2683 | 1.8862 | 2.4578 | 2.7482 | 2.7568 | 2.7682 | 2.917
2022-07-17 05:00 | 3.2008 | 3.4588 | 3.4691 | 3.4816 | 3.4962 | 2.0705 | 2.4605 | 2.4685 | 2.4794 | 2.0705 | 2.4578 | 2.7454 | 2.7526 | 2.7621 | 2.9086
2022-07-17 06:00 | 3.3723 | 3.6464 | 3.6583 | 3.6729 | 3.69 | 2.2673 | 2.6954 | 2.7047 | 2.7174 | 2.2673 | 2.9913 | 3.3406 | 3.349 | 3.3601 | 3.5378
2022-07-17 07:00 | 3.62 | 3.9216 | 3.9381 | 3.9584 | 3.9821 | 2.4387 | 2.9046 | 2.9175 | 2.9352 | 2.4387 | 3.3723 | 3.7705 | 3.7821 | 3.7975 | 4.0014
2022-07-17 08:00 | 3.5628 | 3.8735 | 3.8969 | 3.9255 | 3.9589 | 2.4959 | 2.9818 | 3 | 3.025 | 2.4959 | 3.1437 | 3.5259 | 3.5423 | 3.564 | 3.7629
2022-07-17 09:00 | 3.2008 | 3.4988 | 3.5295 | 3.5671 | 3.6108 | 2.2752 | 2.7314 | 2.7553 | 2.788 | 2.2752 | 2.6293 | 2.9643 | 2.9858 | 3.0144 | 3.1931
2022-07-17 10:00 | 2.7817 | 3.0595 | 3.0957 | 3.1401 | 3.1919 | 1.7719 | 2.1448 | 2.1731 | 2.2117 | 1.7719 | 1.8862 | 2.1463 | 2.1718 | 2.2055 | 2.3496
2022-07-17 11:00 | 2.4387 | 2.6954 | 2.7338 | 2.7809 | 2.8359 | 1.4099 | 1.7203 | 1.7503 | 1.7913 | 1.4099 | 0.93358 | 1.0908 | 1.1178 | 1.1536 | 1.2478
2022-07-17 12:00 | 2.3625 | 2.6124 | 2.6504 | 2.6968 | 2.751 | 1.4099 | 1.7195 | 1.7491 | 1.7895 | 1.4099 | 0.62873 | 0.75131 | 0.7779 | 0.81322 | 0.89003
2022-07-17 13:00 | 3.3151 | 3.6309 | 3.6663 | 3.7096 | 3.7601 | 2.172 | 2.6162 | 2.6438 | 2.6815 | 2.172 | 2.4197 | 2.738 | 2.7628 | 2.7957 | 2.9682
2022-07-17 14:00 | 3.2199 | 3.5231 | 3.5558 | 3.5957 | 3.6423 | 2.1339 | 2.5673 | 2.5927 | 2.6275 | 2.1339 | 2.3054 | 2.6071 | 2.63 | 2.6604 | 2.8234
2022-07-17 15:00 | 3.8296 | 4.1746 | 4.2054 | 4.2431 | 4.287 | 2.5721 | 3.0824 | 3.1064 | 3.1392 | 2.5721 | 3.3342 | 3.7479 | 3.7694 | 3.7981 | 4.0157
2022-07-17 16:00 | 4.3659 | 4.7499 | 4.7803 | 4.8175 | 4.8608 | 3.0492 | 3.6453 | 3.669 | 3.7014 | 3.0492 | 4.8393 | 5.4199 | 5.4411 | 5.4694 | 5.7692
2022-07-17 17:00 | 5.2013 | 5.651 | 5.6832 | 5.7226 | 5.7685 | 3.62 | 4.3222 | 4.3473 | 4.3816 | 3.62 | 5.2395 | 5.867 | 5.8895 | 5.9195 | 6.2433
2022-07-17 18:00 | 5.2395 | 5.6993 | 5.7352 | 5.7792 | 5.8305 | 3.7343 | 4.4626 | 4.4907 | 4.5289 | 3.7343 | 5.3919 | 6.0416 | 6.0668 | 6.1002 | 6.4366
2022-07-17 19:00 | 5.068 | 5.5248 | 5.5658 | 5.6158 | 5.6742 | 3.6001 | 4.3111 | 4.3431 | 4.3866 | 3.6001 | 5.2013 | 5.8368 | 5.8654 | 5.9035 | 6.235
2022-07-17 20:00 | 4.9918 | 5.4526 | 5.4985 | 5.5546 | 5.6201 | 3.5628 | 4.2742 | 4.3099 | 4.3588 | 3.5628 | 5.2776 | 5.9283 | 5.9604 | 6.0031 | 6.3443
2022-07-17 21:00 | 4.7441 | 5.1882 | 5.2349 | 5.292 | 5.3586 | 3.4569 | 4.1502 | 4.1866 | 4.2363 | 3.4569 | 4.3821 | 4.9344 | 4.9671 | 5.0105 | 5.3034
2022-07-17 22:00 | 4.1916 | 4.5886 | 4.6323 | 4.6857 | 4.748 | 2.9067 | 3.4959 | 3.5299 | 3.5764 | 2.9067 | 3.5819 | 4.0409 | 4.0715 | 4.1121 | 4.3576
2022-07-17 23:00 | 3.6771 | 4.0275 | 4.0668 | 4.115 | 4.1711 | 2.4515 | 2.952 | 2.9827 | 3.0246 | 2.4515 | 3.0103 | 3.3998 | 3.4273 | 3.4639 | 3.6732
2022-07-18 | 3.2199 | 3.5268 | 3.5613 | 3.6036 | 3.6528 | 2.0349 | 2.4531 | 2.48 | 2.5167 | 2.0349 | 2.6483 | 2.9908 | 3.015 | 3.0471 | 3.2311
2022-07-18 01:00 | 3.0294 | 3.3125 | 3.3422 | 3.3784 | 3.4207 | 1.8622 | 2.2421 | 2.2652 | 2.2967 | 1.8622 | 2.191 | 2.4759 | 2.4966 | 2.5242 | 2.6776
2022-07-18 02:00 | 2.8769 | 3.1367 | 3.1602 | 3.1889 | 3.2223 | 1.6957 | 2.0365 | 2.0548 | 2.0798 | 1.6957 | 2.2291 | 2.5097 | 2.5261 | 2.5479 | 2.6966
2022-07-18 03:00 | 2.915 | 3.1658 | 3.1832 | 3.2045 | 3.2294 | 1.7528 | 2.0955 | 2.1091 | 2.1276 | 1.7528 | 2.1529 | 2.4166 | 2.4288 | 2.445 | 2.5827
2022-07-18 04:00 | 3.1246 | 3.3809 | 3.3932 | 3.4082 | 3.4257 | 1.8405 | 2.1917 | 2.2013 | 2.2143 | 1.8405 | 2.5937 | 2.8993 | 2.9079 | 2.9193 | 3.0755
2022-07-18 05:00 | 3.5819 | 3.8682 | 3.8784 | 3.891 | 3.9056 | 2.2842 | 2.7129 | 2.7209 | 2.7318 | 2.2842 | 3.2199 | 3.5923 | 3.5995 | 3.609 | 3.7974
2022-07-18 06:00 | 4.4011 | 4.7517 | 4.7636 | 4.7782 | 4.7953 | 3.2199 | 3.8208 | 3.8301 | 3.8428 | 3.2199 | 4.5726 | 5.0979 | 5.1063 | 5.1174 | 5.382
2022-07-18 07:00 | 5.3919 | 5.8252 | 5.8418 | 5.862 | 5.8857 | 3.6009 | 4.2776 | 4.2905 | 4.3081 | 3.6009 | 4.706 | 5.2525 | 5.2642 | 5.2796 | 5.5568
2022-07-18 08:00 | 5.2395 | 5.6748 | 5.6982 | 5.7268 | 5.7602 | 3.3533 | 3.9947 | 4.0129 | 4.0378 | 3.3533 | 3.982 | 4.4575 | 4.4738 | 4.4956 | 4.7406
2022-07-18 09:00 | 4.9346 | 5.3615 | 5.3922 | 5.4297 | 5.4735 | 2.9722 | 3.5548 | 3.5788 | 3.6114 | 2.9722 | 2.8769 | 3.2396 | 3.261 | 3.2896 | 3.4819
2022-07-18 10:00 | 3.7724 | 4.1238 | 4.1601 | 4.2045 | 4.2563 | 2.0577 | 2.4824 | 2.5107 | 2.5493 | 2.0577 | 1.4289 | 1.6382 | 1.6636 | 1.6974 | 1.8163
2022-07-18 11:00 | 3.4104 | 3.7393 | 3.7778 | 3.8249 | 3.8798 | 1.6004 | 1.9454 | 1.9754 | 2.0164 | 1.6004 | 0.64779 | 0.77323 | 0.80019 | 0.83602 | 0.91447
2022-07-18 12:00 | 3.1056 | 3.4107 | 3.4487 | 3.4951 | 3.5493 | 1.7338 | 2.1022 | 2.1318 | 2.1722 | 1.7338 | 0.83831 | 0.98421 | 1.0108 | 1.0461 | 1.1344
2022-07-18 13:00 | 3.1182 | 3.4193 | 3.4547 | 3.498 | 3.5485 | 1.9624 | 2.3686 | 2.3963 | 2.434 | 1.9624 | 1.5052 | 1.7217 | 1.7465 | 1.7795 | 1.9016
2022-07-18 14:00 | 3.4104 | 3.7278 | 3.7605 | 3.8004 | 3.847 | 1.9524 | 2.3528 | 2.3783 | 2.4131 | 1.9524 | 1.3337 | 1.5273 | 1.5502 | 1.5806 | 1.6902
2022-07-18 15:00 | 3.5628 | 3.888 | 3.9188 | 3.9565 | 4.0005 | 2.29 | 2.7491 | 2.7731 | 2.8059 | 2.29 | 2.0196 | 2.287 | 2.3086 | 2.3372 | 2.4826
2022-07-18 16:00 | 4.6107 | 5.0129 | 5.0433 | 5.0805 | 5.1238 | 2.9593 | 3.5392 | 3.5629 | 3.5952 | 2.9593 | 3.9248 | 4.4036 | 4.4249 | 4.4531 | 4.7027
2022-07-18 17:00 | 5.5824 | 6.0604 | 6.0926 | 6.1319 | 6.1779 | 3.7808 | 4.5123 | 4.5374 | 4.5716 | 3.7808 | 5.068 | 5.6764 | 5.699 | 5.7289 | 6.0434
2022-07-18 18:00 | 5.811 | 6.3134 | 6.3493 | 6.3933 | 6.4446 | 4.0772 | 4.8678 | 4.8958 | 4.9341 | 4.0772 | 5.43 | 6.0839 | 6.1091 | 6.1426 | 6.4811
2022-07-18 19:00 | 5.6967 | 6.2003 | 6.2412 | 6.2913 | 6.3497 | 4.1344 | 4.9424 | 4.9743 | 5.0179 | 4.1344 | 5.6777 | 6.3661 | 6.3947 | 6.4328 | 6.7905
2022-07-18 20:00 | 5.3919 | 5.8825 | 5.9283 | 5.9845 | 6.0499 | 3.7583 | 4.5051 | 4.5408 | 4.5897 | 3.7583 | 6.0397 | 6.7752 | 6.8073 | 6.85 | 7.2331
2022-07-18 21:00 | 4.9784 | 5.4399 | 5.4866 | 5.5438 | 5.6104 | 3.5057 | 4.2078 | 4.2443 | 4.294 | 3.5057 | 4.5345 | 5.1037 | 5.1365 | 5.1799 | 5.4812
2022-07-18 22:00 | 4.5345 | 4.9571 | 5.0007 | 5.0541 | 5.1164 | 3.0052 | 3.6122 | 3.6463 | 3.6928 | 3.0052 | 3.7343 | 4.2103 | 4.2409 | 4.2815 | 4.5354
2022-07-18 23:00 | 3.672 | 4.022 | 4.0613 | 4.1094 | 4.1656 | 2.41 | 2.903 | 2.9337 | 2.9756 | 2.41 | 3.0484 | 3.4421 | 3.4697 | 3.5063 | 3.7177
2022-07-19 | 3.4295 | 3.752 | 3.7865 | 3.8287 | 3.878 | 2.1148 | 2.5474 | 2.5744 | 2.6111 | 2.1148 | 2.4959 | 2.8214 | 2.8456 | 2.8777 | 3.0533
2022-07-19 01:00 | 3.1246 | 3.4149 | 3.4445 | 3.4808 | 3.523 | 1.9192 | 2.3093 | 2.3324 | 2.364 | 1.9192 | 2.2863 | 2.5817 | 2.6025 | 2.6301 | 2.7887
2022-07-19 02:00 | 2.9531 | 3.2186 | 3.242 | 3.2707 | 3.3042 | 1.7719 | 2.1266 | 2.1449 | 2.1698 | 1.7719 | 2.3244 | 2.6155 | 2.632 | 2.6538 | 2.8077
2022-07-19 03:00 | 3.0484 | 3.3091 | 3.3265 | 3.3478 | 3.3727 | 1.8481 | 2.208 | 2.2216 | 2.2401 | 1.8481 | 2.3435 | 2.6283 | 2.6405 | 2.6567 | 2.8049
2022-07-19 04:00 | 3.2389 | 3.5037 | 3.516 | 3.531 | 3.5485 | 1.9674 | 2.3416 | 2.3512 | 2.3642 | 1.9674 | 2.7245 | 3.0446 | 3.0532 | 3.0646 | 3.2281
2022-07-19 05:00 | 3.8105 | 4.1138 | 4.1241 | 4.1366 | 4.1512 | 2.3721 | 2.8168 | 2.8248 | 2.8357 | 2.3721 | 3.4485 | 3.8464 | 3.8535 | 3.8631 | 4.064
2022-07-19 06:00 | 4.892 | 5.279 | 5.291 | 5.3056 | 5.3226 | 3.3533 | 3.9784 | 3.9877 | 4.0004 | 3.3533 | 4.5109 | 5.0293 | 5.0377 | 5.0488 | 5.3101
2022-07-19 07:00 | 5.449 | 5.8866 | 5.9032 | 5.9235 | 5.9471 | 3.6009 | 4.2776 | 4.2905 | 4.3081 | 3.6009 | 5.5062 | 6.1418 | 6.1534 | 6.1688 | 6.49
2022-07-19 08:00 | 5.3728 | 5.8181 | 5.8415 | 5.8701 | 5.9035 | 3.3339 | 3.9718 | 3.99 | 4.0149 | 3.3339 | 5.1251 | 5.7278 | 5.7442 | 5.766 | 6.0738
2022-07-19 09:00 | 4.4202 | 4.8089 | 4.8395 | 4.8771 | 4.9209 | 2.6102 | 3.1272 | 3.1511 | 3.1838 | 2.6102 | 2.6864 | 3.0278 | 3.0493 | 3.0779 | 3.2597
2022-07-19 10:00 | 3.7915 | 4.1443 | 4.1806 | 4.225 | 4.2767 | 1.883 | 2.2761 | 2.3044 | 2.343 | 1.883 | 1.4289 | 1.6382 | 1.6636 | 1.6974 | 1.8163
2022-07-19 11:00 | 3.1818 | 3.4937 | 3.5321 | 3.5792 | 3.6342 | 1.5052 | 1.8328 | 1.8629 | 1.9038 | 1.5052 | 0.724 | 0.85792 | 0.88488 | 0.92071 | 1.0033
2022-07-19 12:00 | 2.915 | 3.206 | 3.244 | 3.2904 | 3.3446 | 1.3146 | 1.607 | 1.6366 | 1.677 | 1.3146 | 0.7621 | 0.89952 | 0.9261 | 0.96143 | 1.0456
2022-07-19 13:00 | 3.3342 | 3.6514 | 3.6868 | 3.7301 | 3.7806 | 1.7338 | 2.0985 | 2.1262 | 2.1639 | 1.7338 | 1.2765 | 1.4676 | 1.4924 | 1.5254 | 1.635
2022-07-19 14:00 | 3.8486 | 4.1986 | 4.2313 | 4.2712 | 4.3178 | 2.0386 | 2.4547 | 2.4802 | 2.515 | 2.0386 | 2.2291 | 2.5224 | 2.5453 | 2.5757 | 2.7345
2022-07-19 15:00 | 4.0158 | 4.3747 | 4.4055 | 4.4432 | 4.4871 | 2.3625 | 2.8348 | 2.8588 | 2.8916 | 2.3625 | 3.2008 | 3.5997 | 3.6212 | 3.6499 | 3.8602
2022-07-19 16:00 | 4.5485 | 4.9461 | 4.9765 | 5.0136 | 5.057 | 3.0865 | 3.6894 | 3.7131 | 3.7455 | 3.0865 | 3.6581 | 4.1072 | 4.1285 | 4.1567 | 4.3916
2022-07-19 17:00 | 5.5062 | 5.9785 | 6.0107 | 6.0501 | 6.096 | 3.841 | 4.5834 | 4.6085 | 4.6427 | 3.841 | 5.9063 | 6.608 | 6.6306 | 6.6605 | 7.021
2022-07-19 18:00 | 5.9253 | 6.4362 | 6.4721 | 6.5161 | 6.5674 | 4.1154 | 4.9128 | 4.9408 | 4.9791 | 4.1154 | 5.5633 | 6.2321 | 6.2573 | 6.2908 | 6.6366
2022-07-19 19:00 | 5.8491 | 6.3641 | 6.405 | 6.4551 | 6.5135 | 4.0963 | 4.8974 | 4.9293 | 4.9729 | 4.0963 | 6.6493 | 7.4459 | 7.4745 | 7.5126 | 7.9237
2022-07-19 20:00 | 5.6205 | 6.1281 | 6.174 | 6.2301 | 6.2955 | 3.982 | 4.7693 | 4.8051 | 4.854 | 3.982 | 5.4871 | 6.1612 | 6.1933 | 6.236 | 6.5887
2022-07-19 21:00 | 5.4109 | 5.9046 | 5.9513 | 6.0084 | 6.0751 | 3.6962 | 4.4329 | 4.4693 | 4.5191 | 3.6962 | 5.0489 | 5.6754 | 5.7081 | 5.7516 | 6.0811
2022-07-19 22:00 | 4.7441 | 5.1822 | 5.2259 | 5.2793 | 5.3416 | 3.3342 | 4.0009 | 4.035 | 4.0815 | 3.3342 | 4.0772 | 4.5914 | 4.622 | 4.6626 | 4.9353
2022-07-19 23:00 | 3.8835 | 4.2492 | 4.2885 | 4.3366 | 4.3928 | 2.6102 | 3.1395 | 3.1702 | 3.2121 | 2.6102 | 3.2389 | 3.6538 | 3.6814 | 3.718 | 3.9399
2022-07-20 | 3.639 | 3.9771 | 4.0116 | 4.0539 | 4.1031 | 2.2252 | 2.6778 | 2.7047 | 2.7415 | 2.2252 | 2.9341 | 3.3084 | 3.3326 | 3.3647 | 3.5644
2022-07-20 01:00 | 3.2961 | 3.5991 | 3.6287 | 3.665 | 3.7072 | 1.9815 | 2.3829 | 2.406 | 2.4376 | 1.9815 | 2.6102 | 2.9417 | 2.9624 | 2.99 | 3.1665
2022-07-20 02:00 | 3.2199 | 3.5052 | 3.5286 | 3.5573 | 3.5908 | 1.9053 | 2.2841 | 2.3024 | 2.3274 | 1.9053 | 2.6674 | 2.9966 | 3.0131 | 3.0349 | 3.2076
2022-07-20 03:00 | 3.2199 | 3.4933 | 3.5107 | 3.5321 | 3.5569 | 1.9434 | 2.3206 | 2.3341 | 2.3527 | 1.9434 | 2.4578 | 2.7554 | 2.7676 | 2.7838 | 2.9383
2022-07-20 04:00 | 3.2984 | 3.5676 | 3.5798 | 3.5949 | 3.6123 | 2.0196 | 2.4033 | 2.4128 | 2.4259 | 2.0196 | 2.7505 | 3.0735 | 3.0821 | 3.0935 | 3.2584
2022-07-20 05:00 | 3.9629 | 4.2776 | 4.2878 | 4.3003 | 4.3149 | 2.5961 | 3.0815 | 3.0895 | 3.1004 | 2.5961 | 3.4883 | 3.8906 | 3.8978 | 3.9073 | 4.1105
2022-07-20 06:00 | 4.8203 | 5.202 | 5.214 | 5.2286 | 5.2456 | 3.5734 | 4.2384 | 4.2478 | 4.2605 | 3.5734 | 4.7441 | 5.2884 | 5.2968 | 5.3079 | 5.582
2022-07-20 07:00 | 5.6967 | 6.1527 | 6.1693 | 6.1896 | 6.2132 | 3.7152 | 4.4126 | 4.4255 | 4.4432 | 3.7152 | 6.6493 | 7.4121 | 7.4237 | 7.4392 | 7.8232
2022-07-20 08:00 | 5.457 | 5.9084 | 5.9318 | 5.9605 | 5.9939 | 3.5057 | 4.1747 | 4.193 | 4.2179 | 3.5057 | 4.9156 | 5.4949 | 5.5113 | 5.5331 | 5.8293
2022-07-20 09:00 | 4.6298 | 5.034 | 5.0647 | 5.1022 | 5.146 | 2.7436 | 3.2847 | 3.3087 | 3.3413 | 2.7436 | 3.2199 | 3.6207 | 3.6421 | 3.6707 | 3.8819
2022-07-20 10:00 | 3.7343 | 4.0829 | 4.1192 | 4.1636 | 4.2153 | 1.9434 | 2.3474 | 2.3757 | 2.4143 | 1.9434 | 1.5433 | 1.7652 | 1.7907 | 1.8244 | 1.9496
2022-07-20 11:00 | 3.3914 | 3.7188 | 3.7573 | 3.8044 | 3.8593 | 1.7528 | 2.1254 | 2.1555 | 2.1964 | 1.7528 | 1.5623 | 1.7895 | 1.8165 | 1.8523 | 1.981
2022-07-20 12:00 | 3.2961 | 3.6154 | 3.6534 | 3.6998 | 3.754 | 1.7528 | 2.1247 | 2.1543 | 2.1947 | 1.7528 | 1.105 | 1.2806 | 1.3072 | 1.3425 | 1.4455
2022-07-20 13:00 | 2.6674 | 2.935 | 2.9703 | 3.0137 | 3.0642 | 1.3718 | 1.6709 | 1.6985 | 1.7362 | 1.3718 | 0.85737 | 1.0018 | 1.0266 | 1.0596 | 1.1461
2022-07-20 14:00 | 2.8007 | 3.0728 | 3.1055 | 3.1454 | 3.192 | 1.5433 | 1.8695 | 1.895 | 1.9298 | 1.5433 | 1.0288 | 1.1886 | 1.2114 | 1.2418 | 1.3347
2022-07-20 15:00 | 3.5057 | 3.8266 | 3.8574 | 3.8951 | 3.9391 | 2.0596 | 2.4769 | 2.5009 | 2.5337 | 2.0596 | 1.8862 | 2.1388 | 2.1604 | 2.189 | 2.327
2022-07-20 16:00 | 4.4583 | 4.8492 | 4.8795 | 4.9167 | 4.96 | 2.8007 | 3.3518 | 3.3755 | 3.4078 | 2.8007 | 3.5247 | 3.959 | 3.9803 | 4.0085 | 4.2361
2022-07-20 17:00 | 5.3241 | 5.7829 | 5.815 | 5.8544 | 5.9003 | 3.7534 | 4.4798 | 4.5049 | 4.5392 | 3.7534 | 5.5824 | 6.2481 | 6.2706 | 6.3006 | 6.6433
2022-07-20 18:00 | 5.6777 | 6.1701 | 6.206 | 6.25 | 6.3013 | 3.9058 | 4.6652 | 4.6932 | 4.7315 | 3.9058 | 5.0299 | 5.6393 | 5.6645 | 5.6979 | 6.0145
2022-07-20 19:00 | 5.4681 | 5.9547 | 5.9956 | 6.0457 | 6.1041 | 3.9248 | 4.6948 | 4.7267 | 4.7703 | 3.9248 | 6.0016 | 6.726 | 6.7547 | 6.7928 | 7.1682
2022-07-20 20:00 | 5.3919 | 5.8825 | 5.9283 | 5.9845 | 6.0499 | 3.8677 | 4.6343 | 4.6701 | 4.7189 | 3.8677 | 4.9537 | 5.5684 | 5.6005 | 5.6432 | 5.9666
2022-07-20 21:00 | 5.1061 | 5.5771 | 5.6238 | 5.6809 | 5.7476 | 3.5074 | 4.2098 | 4.2463 | 4.296 | 3.5074 | 4.363 | 4.9132 | 4.9459 | 4.9894 | 5.2812
2022-07-20 22:00 | 4.4202 | 4.8342 | 4.8779 | 4.9313 | 4.9936 | 3.1017 | 3.7262 | 3.7603 | 3.8068 | 3.1017 | 3.658 | 4.1255 | 4.156 | 4.1967 | 4.4464
2022-07-20 23:00 | 3.7152 | 4.0684 | 4.1078 | 4.1559 | 4.2121 | 2.4496 | 2.9498 | 2.9804 | 3.0223 | 2.4496 | 2.9531 | 3.3363 | 3.3638 | 3.4004 | 3.6066
2022-07-21 | 3.3342 | 3.6496 | 3.6841 | 3.7264 | 3.7756 | 2.1575 | 2.5979 | 2.6248 | 2.6615 | 2.1575 | 2.553 | 2.8849 | 2.9091 | 2.9412 | 3.12
2022-07-21 01:00 | 2.9531 | 3.2307 | 3.2603 | 3.2965 | 3.3388 | 1.8622 | 2.2421 | 2.2652 | 2.2967 | 1.8622 | 2.172 | 2.4547 | 2.4755 | 2.503 | 2.6554
2022-07-21 02:00 | 2.896 | 3.1572 | 3.1806 | 3.2093 | 3.2428 | 1.7009 | 2.0427 | 2.061 | 2.086 | 1.7009 | 2.2291 | 2.5097 | 2.5261 | 2.5479 | 2.6966
2022-07-21 03:00 | 2.8579 | 3.1044 | 3.1218 | 3.1431 | 3.168 | 1.6766 | 2.0054 | 2.019 | 2.0376 | 1.6766 | 2.2863 | 2.5648 | 2.577 | 2.5932 | 2.7383
2022-07-21 04:00 | 2.9722 | 3.2172 | 3.2294 | 3.2444 | 3.2619 | 1.8993 | 2.2612 | 2.2708 | 2.2838 | 1.8993 | 2.2101 | 2.473 | 2.4816 | 2.493 | 2.6281
2022-07-21 05:00 | 3.476 | 3.7545 | 3.7647 | 3.7773 | 3.7919 | 2.1891 | 2.6007 | 2.6086 | 2.6195 | 2.1891 | 2.9913 | 3.3382 | 3.3454 | 3.3549 | 3.5308
2022-07-21 06:00 | 4.3249 | 4.6698 | 4.6818 | 4.6964 | 4.7134 | 3.0675 | 3.6407 | 3.65 | 3.6628 | 3.0675 | 4.6488 | 5.1826 | 5.1909 | 5.2021 | 5.4709
2022-07-21 07:00 | 5.0489 | 5.4567 | 5.4733 | 5.4936 | 5.5173 | 3.3723 | 4.0075 | 4.0204 | 4.0381 | 3.3723 | 4.6869 | 5.2314 | 5.243 | 5.2584 | 5.5345
2022-07-21 08:00 | 4.9537 | 5.3677 | 5.3911 | 5.4198 | 5.4532 | 3.3151 | 3.9496 | 3.9679 | 3.9928 | 3.3151 | 4.2678 | 4.775 | 4.7914 | 4.8132 | 5.0739
2022-07-21 09:00 | 4.6488 | 5.0545 | 5.0852 | 5.1227 | 5.1665 | 2.7817 | 3.3298 | 3.3537 | 3.3864 | 2.7817 | 3.8296 | 4.2982 | 4.3197 | 4.3482 | 4.5929
2022-07-21 10:00 | 4.3059 | 4.697 | 4.7332 | 4.7776 | 4.8294 | 2.5149 | 3.0226 | 3.0509 | 3.0895 | 2.5149 | 3.0484 | 3.4379 | 3.4633 | 3.497 | 3.705
2022-07-21 11:00 | 4.1916 | 4.5785 | 4.617 | 4.6641 | 4.719 | 2.4387 | 2.9357 | 2.9657 | 3.0067 | 2.4387 | 2.5149 | 2.8481 | 2.8751 | 2.9109 | 3.092
2022-07-21 12:00 | 4.2868 | 4.6798 | 4.7177 | 4.7642 | 4.8183 | 2.4768 | 2.98 | 3.0096 | 3.05 | 2.4768 | 2.6293 | 2.9744 | 3.001 | 3.0363 | 3.2231
2022-07-21 13:00 | 4.0872 | 4.4603 | 4.4957 | 4.5391 | 4.5896 | 2.3625 | 2.8413 | 2.8689 | 2.9066 | 2.3625 | 2.172 | 2.4627 | 2.4875 | 2.5205 | 2.6793
2022-07-21 14:00 | 3.9058 | 4.26 | 4.2927 | 4.3326 | 4.3792 | 2.2773 | 2.7367 | 2.7621 | 2.7969 | 2.2773 | 2.3816 | 2.6918 | 2.7147 | 2.745 | 2.9123
2022-07-21 15:00 | 4.1154 | 4.4816 | 4.5124 | 4.5501 | 4.5941 | 2.6293 | 3.1499 | 3.1739 | 3.2067 | 2.6293 | 2.6293 | 2.9645 | 2.9861 | 3.0148 | 3.1936
2022-07-21 16:00 | 4.6869 | 5.0948 | 5.1252 | 5.1623 | 5.2057 | 3.1056 | 3.712 | 3.7356 | 3.768 | 3.1056 | 3.8105 | 4.2766 | 4.2978 | 4.3261 | 4.5694
2022-07-21 17:00 | 5.43 | 5.8966 | 5.9288 | 5.9682 | 6.0141 | 3.5819 | 4.2772 | 4.3023 | 4.3366 | 3.5819 | 4.8203 | 5.4012 | 5.4237 | 5.4537 | 5.7545
2022-07-21 18:00 | 5.4675 | 5.9443 | 5.9802 | 6.0242 | 6.0755 | 3.7152 | 4.4401 | 4.4682 | 4.5064 | 3.7152 | 5.1061 | 5.724 | 5.7492 | 5.7826 | 6.1033
2022-07-21 19:00 | 5.5443 | 6.0366 | 6.0775 | 6.1276 | 6.186 | 3.7343 | 4.4697 | 4.5016 | 4.5452 | 3.7343 | 5.2966 | 5.9426 | 5.9713 | 6.0094 | 6.3461
2022-07-21 20:00 | 5.2013 | 5.6778 | 5.7237 | 5.7798 | 5.8452 | 3.7226 | 4.463 | 4.4987 | 4.5476 | 3.7226 | 5.6777 | 6.3729 | 6.4051 | 6.4478 | 6.8109
2022-07-21 21:00 | 4.8548 | 5.3072 | 5.3538 | 5.411 | 5.4776 | 3.4243 | 4.1117 | 4.1481 | 4.1979 | 3.4243 | 4.5726 | 5.1461 | 5.1788 | 5.2223 | 5.5256
2022-07-21 22:00 | 4.2297 | 4.6296 | 4.6732 | 4.7266 | 4.7889 | 2.9611 | 3.5602 | 3.5942 | 3.6407 | 2.9611 | 3.9629 | 4.4644 | 4.4949 | 4.5356 | 4.802
2022-07-21 23:00 | 3.6925 | 4.044 | 4.0834 | 4.1315 | 4.1876 | 2.4088 | 2.9016 | 2.9323 | 2.9742 | 2.4088 | 2.9341 | 3.3151 | 3.3426 | 3.3793 | 3.5843
2022-07-22 | 3.223 | 3.5301 | 3.5646 | 3.6069 | 3.6561 | 2.0192 | 2.4344 | 2.4613 | 2.4981 | 2.0192 | 2.3625 | 2.6732 | 2.6974 | 2.7295 | 2.8978
2022-07-22 01:00 | 2.915 | 3.1897 | 3.2193 | 3.2556 | 3.2979 | 1.7655 | 2.1278 | 2.1509 | 2.1824 | 1.7655 | 2.3625 | 2.6664 | 2.6872 | 2.7148 | 2.8776
2022-07-22 02:00 | 2.8198 | 3.0753 | 3.0988 | 3.1275 | 3.1609 | 1.7147 | 2.059 | 2.0773 | 2.1023 | 1.7147 | 2.4197 | 2.7214 | 2.7378 | 2.7597 | 2.9188
2022-07-22 03:00 | 2.7817 | 3.0225 | 3.04 | 3.0613 | 3.0861 | 1.6576 | 1.9829 | 1.9965 | 2.0151 | 1.6576 | 2.1339 | 2.3954 | 2.4076 | 2.4238 | 2.5605
2022-07-22 04:00 | 2.9531 | 3.1967 | 3.209 | 3.224 | 3.2415 | 1.7625 | 2.0996 | 2.1091 | 2.1222 | 1.7625 | 2.3054 | 2.5788 | 2.5874 | 2.5988 | 2.7392
2022-07-22 05:00 | 3.4383 | 3.7139 | 3.7241 | 3.7367 | 3.7513 | 2.2119 | 2.6275 | 2.6355 | 2.6464 | 2.2119 | 2.9531 | 3.2959 | 3.3031 | 3.3126 | 3.4863
2022-07-22 06:00 | 4.2782 | 4.6196 | 4.6316 | 4.6462 | 4.6632 | 3.1353 | 3.7209 | 3.7302 | 3.7429 | 3.1353 | 4.6298 | 5.1614 | 5.1698 | 5.1809 | 5.4487
2022-07-22 07:00 | 4.9918 | 5.3953 | 5.4119 | 5.4322 | 5.4559 | 3.277 | 3.8949 | 3.9079 | 3.9255 | 3.277 | 4.7822 | 5.3372 | 5.3488 | 5.3643 | 5.6456
2022-07-22 08:00 | 4.9727 | 5.3882 | 5.4116 | 5.4402 | 5.4736 | 3.075 | 3.666 | 3.6842 | 3.7091 | 3.075 | 3.982 | 4.4575 | 4.4738 | 4.4956 | 4.7406
2022-07-22 09:00 | 4.1154 | 4.4813 | 4.512 | 4.5496 | 4.5933 | 2.2367 | 2.686 | 2.7099 | 2.7425 | 2.2367 | 2.7245 | 3.0702 | 3.0917 | 3.1202 | 3.3041
2022-07-22 10:00 | 3.5819 | 3.9192 | 3.9554 | 3.9998 | 4.0516 | 2.0958 | 2.5274 | 2.5557 | 2.5943 | 2.0958 | 1.6576 | 1.8923 | 1.9177 | 1.9514 | 2.0829
2022-07-22 11:00 | 3.2961 | 3.6165 | 3.6549 | 3.7021 | 3.757 | 1.5242 | 1.8553 | 1.8854 | 1.9263 | 1.5242 | 0.99073 | 1.1543 | 1.1813 | 1.2171 | 1.3144
2022-07-22 12:00 | 3.4485 | 3.7792 | 3.8171 | 3.8636 | 3.9177 | 1.9053 | 2.3047 | 2.3343 | 2.3748 | 1.9053 | 1.7338 | 1.9793 | 2.0059 | 2.0412 | 2.1788
2022-07-22 13:00 | 3.8105 | 4.1631 | 4.1985 | 4.2418 | 4.2923 | 2.0767 | 2.5037 | 2.5313 | 2.569 | 2.0767 | 2.1339 | 2.4204 | 2.4452 | 2.4781 | 2.6349
2022-07-22 14:00 | 3.6581 | 3.9939 | 4.0266 | 4.0665 | 4.1131 | 2.0958 | 2.5223 | 2.5477 | 2.5825 | 2.0958 | 2.2482 | 2.5436 | 2.5665 | 2.5968 | 2.7568
2022-07-22 15:00 | 3.6387 | 3.9695 | 4.0003 | 4.038 | 4.082 | 2.3373 | 2.8049 | 2.829 | 2.8618 | 2.3373 | 2.8388 | 3.1974 | 3.219 | 3.2476 | 3.438
2022-07-22 16:00 | 4.1045 | 4.4691 | 4.4994 | 4.5366 | 4.5799 | 2.6995 | 3.2322 | 3.2559 | 3.2883 | 2.6995 | 3.2961 | 3.7049 | 3.7262 | 3.7545 | 3.9695
2022-07-22 17:00 | 4.725 | 5.1393 | 5.1715 | 5.2108 | 5.2568 | 3.258 | 3.8946 | 3.9197 | 3.954 | 3.258 | 4.5155 | 5.0624 | 5.085 | 5.1149 | 5.399
2022-07-22 18:00 | 4.8965 | 5.3309 | 5.3668 | 5.4108 | 5.4621 | 3.229 | 3.8657 | 3.8937 | 3.932 | 3.229 | 4.6107 | 5.1735 | 5.1987 | 5.2322 | 5.5256
2022-07-22 19:00 | 4.725 | 5.1564 | 5.1973 | 5.2474 | 5.3058 | 3.3342 | 3.9971 | 4.029 | 4.0725 | 3.3342 | 5.0108 | 5.625 | 5.6537 | 5.6918 | 6.0128
2022-07-22 20:00 | 4.6488 | 5.0842 | 5.1301 | 5.1862 | 5.2516 | 3.3342 | 4.0041 | 4.0398 | 4.0887 | 3.3342 | 5.0299 | 5.6531 | 5.6852 | 5.7279 | 6.0555
2022-07-22 21:00 | 4.4964 | 4.9221 | 4.9688 | 5.0259 | 5.0925 | 3.1437 | 3.7802 | 3.8166 | 3.8663 | 3.1437 | 4.4202 | 4.9767 | 5.0094 | 5.0529 | 5.3479
2022-07-22 22:00 | 4.1916 | 4.5886 | 4.6323 | 4.6857 | 4.748 | 2.8578 | 3.4382 | 3.4722 | 3.5187 | 2.8578 | 3.7343 | 4.2103 | 4.2409 | 4.2815 | 4.5354
2022-07-22 23:00 | 3.6962 | 4.048 | 4.0873 | 4.1355 | 4.1916 | 2.4067 | 2.8991 | 2.9297 | 2.9716 | 2.4067 | 3.2199 | 3.6327 | 3.6602 | 3.6968 | 3.9176
2022-07-23 | 3.2961 | 3.6087 | 3.6432 | 3.6854 | 3.7347 | 2.0831 | 2.5099 | 2.5368 | 2.5736 | 2.0831 | 2.553 | 2.8849 | 2.9091 | 2.9412 | 3.12
2022-07-23 01:00 | 3.0484 | 3.333 | 3.3626 | 3.3989 | 3.4412 | 1.8481 | 2.2254 | 2.2485 | 2.28 | 1.8481 | 2.3435 | 2.6453 | 2.666 | 2.6936 | 2.8554
2022-07-23 02:00 | 2.8769 | 3.1367 | 3.1602 | 3.1889 | 3.2223 | 1.6766 | 2.014 | 2.0323 | 2.0573 | 1.6766 | 2.0958 | 2.3615 | 2.3779 | 2.3997 | 2.541
2022-07-23 03:00 | 2.7436 | 2.9816 | 2.999 | 3.0203 | 3.0452 | 1.5814 | 1.8929 | 1.9065 | 1.925 | 1.5814 | 1.9815 | 2.2261 | 2.2383 | 2.2545 | 2.3828
2022-07-23 04:00 | 2.7626 | 2.992 | 3.0043 | 3.0193 | 3.0368 | 1.6127 | 1.9226 | 1.9321 | 1.9452 | 1.6127 | 2.2673 | 2.5365 | 2.5451 | 2.5565 | 2.6948
2022-07-23 05:00 | 2.915 | 3.1518 | 3.162 | 3.1745 | 3.1891 | 1.7719 | 2.1078 | 2.1158 | 2.1267 | 1.7719 | 2.3244 | 2.5972 | 2.6044 | 2.6139 | 2.7531
2022-07-23 06:00 | 3.2199 | 3.4826 | 3.4946 | 3.5092 | 3.5262 | 2.1339 | 2.5378 | 2.5472 | 2.5599 | 2.1339 | 3.1056 | 3.4676 | 3.476 | 3.4871 | 3.6711
2022-07-23 07:00 | 3.7915 | 4.1058 | 4.1224 | 4.1427 | 4.1663 | 2.4387 | 2.9046 | 2.9175 | 2.9352 | 2.4387 | 3.2008 | 3.5799 | 3.5915 | 3.607 | 3.8014
2022-07-23 08:00 | 3.7152 | 4.0373 | 4.0607 | 4.0893 | 4.1227 | 2.5149 | 3.0043 | 3.0226 | 3.0475 | 2.5149 | 4.2678 | 4.775 | 4.7914 | 4.8132 | 5.0739
2022-07-23 09:00 | 3.7152 | 4.0515 | 4.0822 | 4.1197 | 4.1635 | 2.2947 | 2.7545 | 2.7784 | 2.8111 | 2.2947 | 2.6483 | 2.9855 | 3.007 | 3.0355 | 3.2153
2022-07-23 10:00 | 3.3533 | 3.6735 | 3.7098 | 3.7542 | 3.8059 | 2.1529 | 2.595 | 2.6232 | 2.6619 | 2.1529 | 2.2291 | 2.5274 | 2.5529 | 2.5866 | 2.7495
2022-07-23 11:00 | 2.7626 | 3.0433 | 3.0818 | 3.1289 | 3.1838 | 1.7909 | 2.1705 | 2.2005 | 2.2415 | 1.7909 | 1.1432 | 1.3237 | 1.3507 | 1.3865 | 1.4922
2022-07-23 12:00 | 2.7626 | 3.0423 | 3.0802 | 3.1267 | 3.1808 | 1.6004 | 1.9446 | 1.9742 | 2.0146 | 1.6004 | 1.3718 | 1.577 | 1.6036 | 1.6389 | 1.7566
2022-07-23 13:00 | 2.915 | 3.201 | 3.2364 | 3.2798 | 3.3303 | 1.8672 | 2.2561 | 2.2837 | 2.3214 | 1.8672 | 1.8672 | 2.124 | 2.1488 | 2.1817 | 2.3238
2022-07-23 14:00 | 3.0019 | 3.2889 | 3.3215 | 3.3615 | 3.4081 | 1.9287 | 2.3249 | 2.3504 | 2.3851 | 1.9287 | 1.6766 | 1.9084 | 1.9313 | 1.9617 | 2.0902
2022-07-23 15:00 | 3.1627 | 3.4581 | 3.489 | 3.5267 | 3.5706 | 2.0958 | 2.5197 | 2.5437 | 2.5765 | 2.0958 | 2.4197 | 2.7316 | 2.7532 | 2.7819 | 2.9492
2022-07-23 16:00 | 3.6004 | 3.9275 | 3.9578 | 3.995 | 4.0383 | 2.463 | 2.9529 | 2.9766 | 3.0089 | 2.463 | 3.0294 | 3.4085 | 3.4298 | 3.458 | 3.6584
2022-07-23 17:00 | 4.4011 | 4.7913 | 4.8235 | 4.8629 | 4.9088 | 3.0294 | 3.6245 | 3.6496 | 3.6839 | 3.0294 | 4.1535 | 4.6602 | 4.6827 | 4.7127 | 4.9768
2022-07-23 18:00 | 4.4774 | 4.8806 | 4.9165 | 4.9605 | 5.0118 | 3.1246 | 3.7424 | 3.7704 | 3.8087 | 3.1246 | 4.4202 | 4.9618 | 4.987 | 5.0204 | 5.3034
2022-07-23 19:00 | 4.4392 | 4.8494 | 4.8903 | 4.9404 | 4.9988 | 3.1437 | 3.772 | 3.8039 | 3.8475 | 3.1437 | 4.8775 | 5.4768 | 5.5055 | 5.5436 | 5.8573
2022-07-23 20:00 | 4.2678 | 4.6748 | 4.7207 | 4.7768 | 4.8423 | 3.0103 | 3.6214 | 3.6572 | 3.7061 | 3.0103 | 3.7915 | 4.2769 | 4.309 | 4.3517 | 4.6112
2022-07-23 21:00 | 4.1154 | 4.5127 | 4.5594 | 4.6165 | 4.6832 | 2.7892 | 3.3615 | 3.3979 | 3.4476 | 2.7892 | 3.9248 | 4.4262 | 4.4589 | 4.5024 | 4.7702
2022-07-23 22:00 | 3.9629 | 4.343 | 4.3866 | 4.4401 | 4.5024 | 2.5324 | 3.0537 | 3.0878 | 3.1342 | 2.5324 | 3.8296 | 4.3162 | 4.3467 | 4.3874 | 4.6465
2022-07-23 23:00 | 3.4676 | 3.8024 | 3.8417 | 3.8898 | 3.946 | 2.3421 | 2.8228 | 2.8535 | 2.8954 | 2.3421 | 2.9722 | 3.3574 | 3.385 | 3.4216 | 3.6288
2022-07-24 | 3.1627 | 3.4654 | 3.4999 | 3.5421 | 3.5914 | 1.9623 | 2.3672 | 2.3941 | 2.4309 | 1.9623 | 2.534 | 2.8638 | 2.8879 | 2.9201 | 3.0978
2022-07-24 01:00 | 2.8579 | 3.1283 | 3.1579 | 3.1942 | 3.2365 | 1.7434 | 2.1017 | 2.1248 | 2.1564 | 1.7434 | 2.1529 | 2.4335 | 2.4543 | 2.4819 | 2.6332
2022-07-24 02:00 | 2.7436 | 2.9934 | 3.0169 | 3.0456 | 3.079 | 1.6957 | 2.0365 | 2.0548 | 2.0798 | 1.6957 | 1.9434 | 2.1921 | 2.2085 | 2.2303 | 2.3633
2022-07-24 03:00 | 2.6293 | 2.8588 | 2.8762 | 2.8975 | 2.9224 | 1.5647 | 1.8732 | 1.8868 | 1.9053 | 1.5647 | 1.8672 | 2.099 | 2.1112 | 2.1274 | 2.2495
2022-07-24 04:00 | 2.6293 | 2.8487 | 2.861 | 2.876 | 2.8935 | 1.5814 | 1.8856 | 1.8951 | 1.9082 | 1.5814 | 1.9434 | 2.1766 | 2.1852 | 2.1966 | 2.3171
2022-07-24 05:00 | 2.7817 | 3.0085 | 3.0187 | 3.0313 | 3.0459 | 1.7174 | 2.0434 | 2.0514 | 2.0623 | 1.7174 | 1.9815 | 2.2161 | 2.2233 | 2.2328 | 2.3531
2022-07-24 06:00 | 2.9341 | 3.1756 | 3.1875 | 3.2021 | 3.2192 | 1.9624 | 2.3353 | 2.3446 | 2.3573 | 1.9624 | 2.534 | 2.8325 | 2.8408 | 2.8519 | 3.0045
2022-07-24 07:00 | 3.277 | 3.5531 | 3.5697 | 3.59 | 3.6137 | 2.191 | 2.612 | 2.6249 | 2.6426 | 2.191 | 2.7245 | 3.0506 | 3.0622 | 3.0777 | 3.2459
2022-07-24 08:00 | 3.3914 | 3.6893 | 3.7127 | 3.7413 | 3.7747 | 2.4116 | 2.8823 | 2.9005 | 2.9254 | 2.4116 | 3.2008 | 3.5894 | 3.6058 | 3.6276 | 3.8296
2022-07-24 09:00 | 3.5247 | 3.8468 | 3.8775 | 3.915 | 3.9588 | 2.4197 | 2.9021 | 2.926 | 2.9587 | 2.4197 | 2.8198 | 3.176 | 3.1975 | 3.2261 | 3.4152
2022-07-24 10:00 | 3.3914 | 3.7145 | 3.7507 | 3.7951 | 3.8469 | 2.191 | 2.64 | 2.6683 | 2.7069 | 2.191 | 2.4959 | 2.8239 | 2.8493 | 2.883 | 3.0606
2022-07-24 11:00 | 2.896 | 3.1866 | 3.2251 | 3.2722 | 3.3271 | 1.8264 | 2.2124 | 2.2424 | 2.2834 | 1.8264 | 1.9815 | 2.2553 | 2.2822 | 2.3181 | 2.4698
2022-07-24 12:00 | 1.9243 | 2.1416 | 2.1796 | 2.226 | 2.2802 | 1.2575 | 1.5395 | 1.5691 | 1.6095 | 1.2575 | 0.7621 | 0.89952 | 0.9261 | 0.96143 | 1.0456
2022-07-24 13:00 | 1.8099 | 2.0138 | 2.0492 | 2.0925 | 2.143 | 1.1432 | 1.4008 | 1.4284 | 1.4661 | 1.1432 | 0.80021 | 0.93833 | 0.96313 | 0.99609 | 1.0795
2022-07-24 14:00 | 2.1529 | 2.3769 | 2.4095 | 2.4495 | 2.496 | 1.2862 | 1.5659 | 1.5913 | 1.6261 | 1.2862 | 0.81926 | 0.95567 | 0.97854 | 1.0089 | 1.0903
2022-07-24 15:00 | 2.5911 | 2.8441 | 2.8749 | 2.9126 | 2.9565 | 1.6053 | 1.9402 | 1.9642 | 1.997 | 1.6053 | 1.3337 | 1.5248 | 1.5464 | 1.575 | 1.6826
2022-07-24 16:00 | 3.3533 | 3.662 | 3.6923 | 3.7295 | 3.7728 | 2.3622 | 2.8337 | 2.8574 | 2.8898 | 2.3622 | 2.534 | 2.858 | 2.8793 | 2.9076 | 3.0807
2022-07-24 17:00 | 4.4486 | 4.8423 | 4.8745 | 4.9138 | 4.9598 | 3.0631 | 3.6643 | 3.6894 | 3.7237 | 3.0631 | 3.5057 | 3.9403 | 3.9629 | 3.9928 | 4.2214
2022-07-24 18:00 | 4.7441 | 5.1671 | 5.2031 | 5.247 | 5.2983 | 3.1627 | 3.7874 | 3.8154 | 3.8537 | 3.1627 | 4.5726 | 5.1312 | 5.1564 | 5.1898 | 5.4812
2022-07-24 19:00 | 4.6679 | 5.095 | 5.1359 | 5.186 | 5.2444 | 3.3151 | 3.9745 | 4.0065 | 4.05 | 3.3151 | 4.7441 | 5.3286 | 5.3573 | 5.3954 | 5.7017
2022-07-24 20:00 | 4.5917 | 5.0228 | 5.0686 | 5.1248 | 5.1902 | 3.1818 | 3.824 | 3.8598 | 3.9086 | 3.1818 | 4.2868 | 4.8274 | 4.8595 | 4.9022 | 5.1889
2022-07-24 21:00 | 4.6488 | 5.0858 | 5.1325 | 5.1897 | 5.2563 | 3.1056 | 3.7352 | 3.7716 | 3.8213 | 3.1056 | 4.5536 | 5.1249 | 5.1576 | 5.2011 | 5.5034
2022-07-24 22:00 | 3.982 | 4.3635 | 4.4071 | 4.4605 | 4.5228 | 2.5081 | 3.025 | 3.059 | 3.1055 | 2.5081 | 3.2961 | 3.7233 | 3.7539 | 3.7945 | 4.0243
2022-07-24 23:00 | 3.5438 | 3.8842 | 3.9236 | 3.9717 | 4.0278 | 2.2291 | 2.6893 | 2.72 | 2.7619 | 2.2291 | 2.7436 | 3.1034 | 3.1309 | 3.1675 | 3.3621
2022-07-25 | 3.0103 | 3.3016 | 3.3362 | 3.3784 | 3.4276 | 1.9237 | 2.3216 | 2.3485 | 2.3853 | 1.9237 | 2.2291 | 2.525 | 2.5492 | 2.5813 | 2.7423
2022-07-25 01:00 | 2.9531 | 3.2307 | 3.2603 | 3.2965 | 3.3388 | 1.6715 | 2.0168 | 2.0399 | 2.0714 | 1.6715 | 2.2482 | 2.5394 | 2.5602 | 2.5877 | 2.7443
2022-07-25 02:00 | 2.8198 | 3.0753 | 3.0988 | 3.1275 | 3.1609 | 1.6385 | 1.969 | 1.9873 | 2.0123 | 1.6385 | 2.191 | 2.4673 | 2.4838 | 2.5056 | 2.6521
2022-07-25 03:00 | 2.9341 | 3.1863 | 3.2037 | 3.225 | 3.2499 | 1.6385 | 1.9604 | 1.974 | 1.9925 | 1.6385 | 2.1339 | 2.3954 | 2.4076 | 2.4238 | 2.5605
2022-07-25 04:00 | 3.1437 | 3.4014 | 3.4136 | 3.4286 | 3.4461 | 1.7528 | 2.0882 | 2.0977 | 2.1108 | 1.7528 | 2.915 | 3.2564 | 3.2649 | 3.2764 | 3.4503
2022-07-25 05:00 | 3.5438 | 3.8273 | 3.8375 | 3.85 | 3.8646 | 2.1911 | 2.603 | 2.611 | 2.6219 | 2.1911 | 3.1627 | 3.5288 | 3.536 | 3.5455 | 3.7307
2022-07-25 06:00 | 4.2967 | 4.6394 | 4.6514 | 4.666 | 4.683 | 3.0675 | 3.6407 | 3.65 | 3.6628 | 3.0675 | 4.0201 | 4.4839 | 4.4923 | 4.5034 | 4.7377
2022-07-25 07:00 | 5.0489 | 5.4567 | 5.4733 | 5.4936 | 5.5173 | 3.2199 | 3.8274 | 3.8403 | 3.858 | 3.2199 | 4.5345 | 5.062 | 5.0736 | 5.089 | 5.3568
2022-07-25 08:00 | 5.1442 | 5.5724 | 5.5958 | 5.6245 | 5.6579 | 3.0103 | 3.5895 | 3.6078 | 3.6327 | 3.0103 | 4.6869 | 5.2408 | 5.2572 | 5.279 | 5.5627
2022-07-25 09:00 | 4.6107 | 5.0135 | 5.0442 | 5.0818 | 5.1255 | 2.8388 | 3.3973 | 3.4212 | 3.4539 | 2.8388 | 3.4104 | 3.8324 | 3.8539 | 3.8824 | 4.1041
2022-07-25 10:00 | 4.3655 | 4.7611 | 4.7973 | 4.8417 | 4.8935 | 2.5721 | 3.0901 | 3.1184 | 3.157 | 2.5721 | 2.8007 | 3.1626 | 3.188 | 3.2218 | 3.4161
2022-07-25 11:00 | 3.8105 | 4.1691 | 4.2076 | 4.2547 | 4.3096 | 2.0684 | 2.4982 | 2.5283 | 2.5692 | 2.0684 | 1.6385 | 1.8742 | 1.9011 | 1.937 | 2.0699
2022-07-25 12:00 | 2.8224 | 3.1065 | 3.1444 | 3.1908 | 3.245 | 1.4861 | 1.8096 | 1.8392 | 1.8796 | 1.4861 | 0.83831 | 0.98421 | 1.0108 | 1.0461 | 1.1344
2022-07-25 13:00 | 3.0484 | 3.3443 | 3.3797 | 3.4231 | 3.4736 | 1.467 | 1.7834 | 1.8111 | 1.8487 | 1.467 | 1.2384 | 1.4253 | 1.4501 | 1.483 | 1.5905
2022-07-25 14:00 | 2.915 | 3.1956 | 3.2283 | 3.2682 | 3.3148 | 1.6766 | 2.0271 | 2.0526 | 2.0873 | 1.6766 | 1.2194 | 1.4003 | 1.4232 | 1.4535 | 1.5569
2022-07-25 15:00 | 3.2188 | 3.5184 | 3.5492 | 3.5869 | 3.6309 | 1.9278 | 2.3213 | 2.3453 | 2.3781 | 1.9278 | 1.9815 | 2.2446 | 2.2662 | 2.2949 | 2.4381
2022-07-25 16:00 | 3.7513 | 4.0897 | 4.12 | 4.1572 | 4.2005 | 2.3054 | 2.7666 | 2.7903 | 2.8226 | 2.3054 | 3.3533 | 3.7684 | 3.7897 | 3.818 | 4.0361
2022-07-25 17:00 | 4.7362 | 5.1513 | 5.1835 | 5.2228 | 5.2688 | 3.0144 | 3.6069 | 3.632 | 3.6662 | 3.0144 | 3.9058 | 4.3849 | 4.4075 | 4.4374 | 4.688
2022-07-25 18:00 | 4.9156 | 5.3513 | 5.3873 | 5.4313 | 5.4825 | 3.277 | 3.9224 | 3.9505 | 3.9887 | 3.277 | 4.6869 | 5.2582 | 5.2834 | 5.3168 | 5.6145
2022-07-25 19:00 | 4.7631 | 5.1973 | 5.2383 | 5.2883 | 5.3467 | 3.3151 | 3.9745 | 4.0065 | 4.05 | 3.3151 | 4.5536 | 5.1169 | 5.1456 | 5.1837 | 5.4795
2022-07-25 20:00 | 4.6127 | 5.0454 | 5.0913 | 5.1474 | 5.2129 | 3.2199 | 3.869 | 3.9048 | 3.9536 | 3.2199 | 4.2106 | 4.7427 | 4.7748 | 4.8175 | 5.1
2022-07-25 21:00 | 4.1916 | 4.5946 | 4.6413 | 4.6984 | 4.765 | 3.0484 | 3.6676 | 3.7041 | 3.7538 | 3.0484 | 4.2487 | 4.7862 | 4.8189 | 4.8623 | 5.1479
2022-07-25 22:00 | 3.8677 | 4.2406 | 4.2843 | 4.3377 | 4.4 | 2.6475 | 3.1897 | 3.2238 | 3.2702 | 2.6475 | 3.1246 | 3.5328 | 3.5634 | 3.604 | 3.8244
2022-07-25 23:00 | 3.3533 | 3.6795 | 3.7189 | 3.767 | 3.8232 | 2.172 | 2.6218 | 2.6525 | 2.6944 | 2.172 | 2.7626 | 3.1245 | 3.1521 | 3.1887 | 3.3844
2022-07-26 | 3.0294 | 3.3221 | 3.3566 | 3.3989 | 3.4481 | 1.7719 | 2.1423 | 2.1692 | 2.206 | 1.7719 | 2.4006 | 2.7156 | 2.7397 | 2.7719 | 2.9423
2022-07-26 01:00 | 2.8007 | 3.0669 | 3.0965 | 3.1328 | 3.1751 | 1.6433 | 1.9834 | 2.0065 | 2.038 | 1.6433 | 2.2101 | 2.4971 | 2.5178 | 2.5454 | 2.6998
2022-07-26 02:00 | 2.6293 | 2.8706 | 2.8941 | 2.9228 | 2.9562 | 1.51 | 1.8172 | 1.8355 | 1.8604 | 1.51 | 2.0196 | 2.2768 | 2.2932 | 2.315 | 2.4522
2022-07-26 03:00 | 2.5149 | 2.736 | 2.7534 | 2.7747 | 2.7995 | 1.5052 | 1.8029 | 1.8165 | 1.835 | 1.5052 | 1.8862 | 2.1202 | 2.1324 | 2.1486 | 2.2717
2022-07-26 04:00 | 2.6436 | 2.8641 | 2.8764 | 2.8914 | 2.9089 | 1.5554 | 1.8549 | 1.8645 | 1.8775 | 1.5554 | 2.0386 | 2.2824 | 2.291 | 2.3024 | 2.4282
2022-07-26 05:00 | 3.0251 | 3.27 | 3.2802 | 3.2927 | 3.3073 | 1.9271 | 2.2911 | 2.2991 | 2.31 | 1.9271 | 2.4387 | 2.7242 | 2.7314 | 2.7409 | 2.8864
2022-07-26 06:00 | 3.8459 | 4.1552 | 4.1671 | 4.1818 | 4.1988 | 2.7055 | 3.2131 | 3.2224 | 3.2351 | 2.7055 | 3.4572 | 3.8583 | 3.8667 | 3.8778 | 4.0812
2022-07-26 07:00 | 4.363 | 4.7199 | 4.7364 | 4.7567 | 4.7804 | 2.8579 | 3.3998 | 3.4127 | 3.4303 | 2.8579 | 3.9058 | 4.3633 | 4.3749 | 4.3904 | 4.6235
2022-07-26 08:00 | 3.9161 | 4.253 | 4.2764 | 4.3051 | 4.3385 | 2.4937 | 2.9792 | 2.9974 | 3.0223 | 2.4937 | 2.9034 | 3.2589 | 3.2753 | 3.2971 | 3.4827
2022-07-26 09:00 | 3.6009 | 3.9287 | 3.9594 | 3.9969 | 4.0407 | 1.8672 | 2.2494 | 2.2733 | 2.306 | 1.8672 | 1.6576 | 1.8845 | 1.906 | 1.9346 | 2.0598
2022-07-26 10:00 | 3.8105 | 4.1648 | 4.201 | 4.2454 | 4.2972 | 2.0005 | 2.4149 | 2.4432 | 2.4818 | 2.0005 | 2.0386 | 2.3157 | 2.3411 | 2.3749 | 2.5273
2022-07-26 11:00 | 3.4295 | 3.7597 | 3.7982 | 3.8453 | 3.9003 | 1.7719 | 2.1479 | 2.178 | 2.219 | 1.7719 | 1.2384 | 1.4296 | 1.4565 | 1.4924 | 1.6033
2022-07-26 12:00 | 3.2961 | 3.6154 | 3.6534 | 3.6998 | 3.754 | 1.7607 | 2.134 | 2.1636 | 2.204 | 1.7607 | 1.105 | 1.2806 | 1.3072 | 1.3425 | 1.4455
2022-07-26 13:00 | 3.0051 | 3.2978 | 3.3332 | 3.3765 | 3.427 | 1.6766 | 2.031 | 2.0586 | 2.0963 | 1.6766 | 1.105 | 1.2771 | 1.3019 | 1.3348 | 1.435
2022-07-26 14:00 | 3.5057 | 3.8302 | 3.8628 | 3.9028 | 3.9493 | 2.0196 | 2.4322 | 2.4577 | 2.4925 | 2.0196 | 1.5623 | 1.7814 | 1.8043 | 1.8346 | 1.9569
2022-07-26 15:00 | 4.1527 | 4.5218 | 4.5526 | 4.5903 | 4.6342 | 2.4197 | 2.9023 | 2.9263 | 2.9591 | 2.4197 | 2.8007 | 3.155 | 3.1766 | 3.2053 | 3.3936
2022-07-26 16:00 | 4.5536 | 4.9515 | 4.9819 | 5.0191 | 5.0624 | 2.761 | 3.305 | 3.3286 | 3.361 | 2.761 | 4.0772 | 4.573 | 4.5942 | 4.6225 | 4.8805
2022-07-26 17:00 | 5.2966 | 5.7534 | 5.7855 | 5.8249 | 5.8708 | 3.4596 | 4.1328 | 4.1579 | 4.1922 | 3.4596 | 4.7441 | 5.3165 | 5.3391 | 5.369 | 5.6656
2022-07-26 18:00 | 5.5633 | 6.0473 | 6.0832 | 6.1272 | 6.1785 | 3.8105 | 4.5527 | 4.5807 | 4.619 | 3.8105 | 4.8203 | 5.4064 | 5.4316 | 5.465 | 5.77
2022-07-26 19:00 | 5.2776 | 5.75 | 5.7909 | 5.841 | 5.8994 | 3.6962 | 4.4247 | 4.4566 | 4.5002 | 3.6962 | 4.8584 | 5.4557 | 5.4843 | 5.5224 | 5.8351
2022-07-26 20:00 | 5.1632 | 5.6369 | 5.6827 | 5.7388 | 5.8043 | 3.5819 | 4.2967 | 4.3324 | 4.3813 | 3.5819 | 5.5062 | 6.1824 | 6.2145 | 6.2572 | 6.6109
2022-07-26 21:00 | 4.9156 | 5.3724 | 5.4191 | 5.4762 | 5.5429 | 3.3342 | 4.0053 | 4.0417 | 4.0914 | 3.3342 | 4.4964 | 5.0614 | 5.0941 | 5.1376 | 5.4367
2022-07-26 22:00 | 4.3249 | 4.7319 | 4.7755 | 4.829 | 4.8913 | 2.9754 | 3.5771 | 3.6112 | 3.6576 | 2.9754 | 4.1916 | 4.7184 | 4.749 | 4.7896 | 5.0687
2022-07-26 23:00 | 3.7592 | 4.1157 | 4.155 | 4.2032 | 4.2593 | 2.4374 | 2.9354 | 2.9661 | 3.008 | 2.4374 | 3.1818 | 3.5903 | 3.6179 | 3.6545 | 3.8732
2022-07-27 | 3.2266 | 3.534 | 3.5685 | 3.6108 | 3.66 | 2.005 | 2.4177 | 2.4446 | 2.4814 | 2.005 | 2.4197 | 2.7367 | 2.7609 | 2.793 | 2.9645
2022-07-27 01:00 | 3.0294 | 3.3125 | 3.3422 | 3.3784 | 3.4207 | 1.7909 | 2.1579 | 2.181 | 2.2125 | 1.7909 | 2.1148 | 2.3912 | 2.4119 | 2.4395 | 2.5887
2022-07-27 02:00 | 2.9913 | 3.2595 | 3.283 | 3.3117 | 3.3451 | 1.6766 | 2.014 | 2.0323 | 2.0573 | 1.6766 | 2.2291 | 2.5097 | 2.5261 | 2.5479 | 2.6966
2022-07-27 03:00 | 2.9531 | 3.2068 | 3.2242 | 3.2455 | 3.2703 | 1.7338 | 2.073 | 2.0865 | 2.1051 | 1.7338 | 2.2291 | 2.5013 | 2.5135 | 2.5297 | 2.6716
2022-07-27 04:00 | 3.0675 | 3.3195 | 3.3318 | 3.3468 | 3.3643 | 1.8599 | 2.2146 | 2.2242 | 2.2372 | 1.8599 | 2.5149 | 2.8117 | 2.8203 | 2.8317 | 2.9836
2022-07-27 05:00 | 3.6441 | 3.9351 | 3.9453 | 3.9578 | 3.9724 | 2.2799 | 2.7079 | 2.7159 | 2.7268 | 2.2799 | 3.258 | 3.6346 | 3.6418 | 3.6513 | 3.8418
2022-07-27 06:00 | 4.6179 | 4.9845 | 4.9965 | 5.0111 | 5.0281 | 3.1458 | 3.7332 | 3.7426 | 3.7553 | 3.1458 | 4.2909 | 4.7848 | 4.7932 | 4.8043 | 5.0534
2022-07-27 07:00 | 5.0489 | 5.4567 | 5.4733 | 5.4936 | 5.5173 | 3.5438 | 4.21 | 4.223 | 4.2406 | 3.5438 | 5.2776 | 5.8877 | 5.8993 | 5.9148 | 6.2233
2022-07-27 08:00 | 4.8655 | 5.273 | 5.2964 | 5.3251 | 5.3585 | 3.2425 | 3.8638 | 3.8821 | 3.907 | 3.2425 | 3.8558 | 4.3172 | 4.3336 | 4.3554 | 4.5934
2022-07-27 09:00 | 3.8561 | 4.2028 | 4.2335 | 4.271 | 4.3148 | 2.2193 | 2.6654 | 2.6894 | 2.722 | 2.2193 | 2.0375 | 2.3068 | 2.3283 | 2.3568 | 2.503
2022-07-27 10:00 | 3.1686 | 3.4752 | 3.5114 | 3.5558 | 3.6076 | 1.7909 | 2.1673 | 2.1956 | 2.2342 | 1.7909 | 0.87642 | 1.0242 | 1.0496 | 1.0834 | 1.1719
2022-07-27 11:00 | 2.6102 | 2.8796 | 2.9181 | 2.9652 | 3.0201 | 1.2574 | 1.5402 | 1.5702 | 1.6112 | 1.2574 | 0.91452 | 1.0696 | 1.0966 | 1.1324 | 1.2255
2022-07-27 12:00 | 2.5149 | 2.7762 | 2.8141 | 2.8606 | 2.9147 | 1.1622 | 1.4269 | 1.4565 | 1.4969 | 1.1622 | 1.105 | 1.2806 | 1.3072 | 1.3425 | 1.4455
2022-07-27 13:00 | 2.2863 | 2.5256 | 2.561 | 2.6043 | 2.6548 | 1.1622 | 1.4233 | 1.4509 | 1.4886 | 1.1622 | 1.0098 | 1.1712 | 1.196 | 1.229 | 1.3239
2022-07-27 14:00 | 2.4578 | 2.7044 | 2.737 | 2.777 | 2.8235 | 1.2963 | 1.5778 | 1.6032 | 1.638 | 1.2963 | 0.80021 | 0.9345 | 0.95736 | 0.98775 | 1.0681
2022-07-27 15:00 | 2.9722 | 3.2535 | 3.2843 | 3.322 | 3.3659 | 1.7976 | 2.1674 | 2.1914 | 2.2242 | 1.7976 | 1.3337 | 1.5248 | 1.5464 | 1.575 | 1.6826
2022-07-27 16:00 | 3.8479 | 4.1934 | 4.2237 | 4.2609 | 4.3042 | 2.4768 | 2.9692 | 2.9929 | 3.0252 | 2.4768 | 2.896 | 3.2603 | 3.2816 | 3.3098 | 3.5028
2022-07-27 17:00 | 4.7822 | 5.2007 | 5.2329 | 5.2723 | 5.3182 | 3.3101 | 3.9562 | 3.9813 | 4.0156 | 3.3101 | 4.3249 | 4.8507 | 4.8733 | 4.9032 | 5.1768
2022-07-27 18:00 | 5.1823 | 5.6379 | 5.6738 | 5.7178 | 5.7691 | 3.6009 | 4.3051 | 4.3331 | 4.3714 | 3.6009 | 4.9537 | 5.5546 | 5.5798 | 5.6133 | 5.9256
2022-07-27 19:00 | 5.068 | 5.5248 | 5.5658 | 5.6158 | 5.6742 | 3.5819 | 4.2897 | 4.3216 | 4.3651 | 3.5819 | 4.706 | 5.2863 | 5.315 | 5.3531 | 5.6573
2022-07-27 20:00 | 5.0489 | 5.514 | 5.5599 | 5.616 | 5.6815 | 3.62 | 4.3417 | 4.3775 | 4.4263 | 3.62 | 4.8393 | 5.4414 | 5.4735 | 5.5162 | 5.8333
2022-07-27 21:00 | 4.7355 | 5.1789 | 5.2256 | 5.2828 | 5.3494 | 3.3182 | 3.9864 | 4.0228 | 4.0726 | 3.3182 | 5.0108 | 5.6331 | 5.6658 | 5.7092 | 6.0367
2022-07-27 22:00 | 4.1916 | 4.5886 | 4.6323 | 4.6857 | 4.748 | 2.8383 | 3.4152 | 3.4492 | 3.4957 | 2.8383 | 3.4866 | 3.9351 | 3.9656 | 4.0063 | 4.2465
2022-07-27 23:00 | 3.4866 | 3.8228 | 3.8622 | 3.9103 | 3.9664 | 2.3047 | 2.7786 | 2.8093 | 2.8512 | 2.3047 | 2.8579 | 3.2304 | 3.2579 | 3.2946 | 3.4955
2022-07-28 | 3.1246 | 3.4245 | 3.459 | 3.5012 | 3.5505 | 2.0196 | 2.4349 | 2.4618 | 2.4986 | 2.0196 | 2.915 | 3.2872 | 3.3114 | 3.3435 | 3.5422
2022-07-28 01:00 | 2.8769 | 3.1488 | 3.1784 | 3.2147 | 3.2569 | 1.7909 | 2.1579 | 2.181 | 2.2125 | 1.7909 | 2.191 | 2.4759 | 2.4966 | 2.5242 | 2.6776
2022-07-28 02:00 | 2.8007 | 3.0548 | 3.0783 | 3.107 | 3.1404 | 1.6766 | 2.014 | 2.0323 | 2.0573 | 1.6766 | 2.4006 | 2.7002 | 2.7167 | 2.7385 | 2.8966
2022-07-28 03:00 | 2.8198 | 3.0635 | 3.0809 | 3.1022 | 3.127 | 1.6576 | 1.9829 | 1.9965 | 2.0151 | 1.6576 | 2.191 | 2.459 | 2.4711 | 2.4874 | 2.6272
2022-07-28 04:00 | 3.0865 | 3.34 | 3.3522 | 3.3672 | 3.3847 | 1.7614 | 2.0983 | 2.1079 | 2.1209 | 1.7614 | 2.21 | 2.4729 | 2.4814 | 2.4929 | 2.628
2022-07-28 05:00 | 3.2961 | 3.5612 | 3.5714 | 3.5839 | 3.5985 | 2.1385 | 2.5409 | 2.5489 | 2.5598 | 2.1385 | 3.2389 | 3.6135 | 3.6206 | 3.6302 | 3.8196
2022-07-28 06:00 | 4.1344 | 4.4651 | 4.4771 | 4.4917 | 4.5087 | 2.9819 | 3.5397 | 3.549 | 3.5617 | 2.9819 | 4.001 | 4.4627 | 4.4711 | 4.4822 | 4.7154
2022-07-28 07:00 | 4.8584 | 5.252 | 5.2686 | 5.2889 | 5.3126 | 3.2199 | 3.8274 | 3.8403 | 3.858 | 3.2199 | 4.4011 | 4.9138 | 4.9254 | 4.9408 | 5.2012
2022-07-28 08:00 | 4.5917 | 4.9788 | 5.0022 | 5.0309 | 5.0643 | 2.8529 | 3.4035 | 3.4218 | 3.4467 | 2.8529 | 4.4774 | 5.0079 | 5.0243 | 5.0461 | 5.3183
2022-07-28 09:00 | 4.0201 | 4.379 | 4.4097 | 4.4472 | 4.491 | 2.3816 | 2.8571 | 2.881 | 2.9137 | 2.3816 | 1.9815 | 2.2445 | 2.2659 | 2.2945 | 2.4376
2022-07-28 10:00 | 3.5057 | 3.8373 | 3.8735 | 3.9179 | 3.9697 | 1.8862 | 2.2798 | 2.3081 | 2.3467 | 1.8862 | 1.3718 | 1.5747 | 1.6001 | 1.6339 | 1.7496
2022-07-28 11:00 | 3.3151 | 3.6369 | 3.6754 | 3.7225 | 3.7774 | 1.6957 | 2.0579 | 2.0879 | 2.1289 | 1.6957 | 1.4861 | 1.7048 | 1.7318 | 1.7676 | 1.8921
2022-07-28 12:00 | 3.0675 | 3.3698 | 3.4077 | 3.4542 | 3.5083 | 1.6576 | 2.0121 | 2.0417 | 2.0821 | 1.6576 | 1.2194 | 1.4077 | 1.4342 | 1.4696 | 1.5788
2022-07-28 13:00 | 3.1818 | 3.4876 | 3.523 | 3.5663 | 3.6169 | 1.6957 | 2.0535 | 2.0811 | 2.1188 | 1.6957 | 1.2956 | 1.4888 | 1.5136 | 1.5466 | 1.6572
2022-07-28 14:00 | 2.8769 | 3.1547 | 3.1873 | 3.2273 | 3.2739 | 1.3146 | 1.5994 | 1.6249 | 1.6597 | 1.3146 | 1.2003 | 1.3791 | 1.402 | 1.4324 | 1.5347
2022-07-28 15:00 | 3.3914 | 3.7038 | 3.7346 | 3.7723 | 3.8162 | 1.9243 | 2.3171 | 2.3411 | 2.3739 | 1.9243 | 2.172 | 2.4564 | 2.4779 | 2.5066 | 2.6603
2022-07-28 16:00 | 3.9629 | 4.317 | 4.3473 | 4.3845 | 4.4279 | 2.2863 | 2.7441 | 2.7678 | 2.8001 | 2.2863 | 2.9722 | 3.345 | 3.3663 | 3.3945 | 3.5917
2022-07-28 17:00 | 4.8203 | 5.2416 | 5.2738 | 5.3132 | 5.3591 | 3.2187 | 3.8482 | 3.8733 | 3.9076 | 3.2187 | 4.5536 | 5.1048 | 5.1273 | 5.1573 | 5.4434
2022-07-28 18:00 | 5.1632 | 5.6174 | 5.6534 | 5.6974 | 5.7486 | 3.3723 | 4.035 | 4.063 | 4.1013 | 3.3723 | 4.9537 | 5.5546 | 5.5798 | 5.6133 | 5.9256
2022-07-28 19:00 | 4.9727 | 5.4225 | 5.4634 | 5.5135 | 5.5719 | 3.4104 | 4.0871 | 4.119 | 4.1626 | 3.4104 | 4.7631 | 5.3498 | 5.3785 | 5.4166 | 5.724
2022-07-28 20:00 | 4.9346 | 5.3912 | 5.4371 | 5.4932 | 5.5587 | 3.4104 | 4.0941 | 4.1299 | 4.1787 | 3.4104 | 4.8965 | 5.5049 | 5.537 | 5.5797 | 5.8999
2022-07-28 21:00 | 4.5145 | 4.9415 | 4.9882 | 5.0453 | 5.112 | 3.139 | 3.7747 | 3.8111 | 3.8608 | 3.139 | 3.7927 | 4.2794 | 4.3121 | 4.3556 | 4.6161
2022-07-28 22:00 | 3.9248 | 4.3021 | 4.3457 | 4.3991 | 4.4614 | 2.7013 | 3.2533 | 3.2873 | 3.3338 | 2.7013 | 3.3151 | 3.7445 | 3.7751 | 3.8157 | 4.0466
2022-07-28 23:00 | 3.4509 | 3.7844 | 3.8238 | 3.8719 | 3.928 | 2.2482 | 2.7119 | 2.7425 | 2.7844 | 2.2482 | 2.553 | 2.8916 | 2.9192 | 2.9558 | 3.1399
2022-07-29 | 3.1437 | 3.4449 | 3.4794 | 3.5217 | 3.5709 | 1.8862 | 2.2773 | 2.3043 | 2.341 | 1.8862 | 2.2291 | 2.525 | 2.5492 | 2.5813 | 2.7423
2022-07-29 01:00 | 2.8769 | 3.1488 | 3.1784 | 3.2147 | 3.2569 | 1.6667 | 2.0111 | 2.0342 | 2.0658 | 1.6667 | 2.0386 | 2.3065 | 2.3273 | 2.3548 | 2.4999
2022-07-29 02:00 | 2.8729 | 3.1324 | 3.1559 | 3.1846 | 3.218 | 1.6576 | 1.9915 | 2.0098 | 2.0348 | 1.6576 | 2.172 | 2.4462 | 2.4626 | 2.4844 | 2.6299
2022-07-29 03:00 | 3.0484 | 3.3091 | 3.3265 | 3.3478 | 3.3727 | 1.6766 | 2.0054 | 2.019 | 2.0376 | 1.6766 | 2.1529 | 2.4166 | 2.4288 | 2.445 | 2.5827
2022-07-29 04:00 | 3.2008 | 3.4628 | 3.475 | 3.4901 | 3.5076 | 1.829 | 2.1782 | 2.1877 | 2.2008 | 1.829 | 2.553 | 2.8541 | 2.8627 | 2.8741 | 3.0281
2022-07-29 05:00 | 3.639 | 3.9296 | 3.9398 | 3.9524 | 3.967 | 2.1861 | 2.5971 | 2.6051 | 2.616 | 2.1861 | 3.6009 | 4.0157 | 4.0229 | 4.0324 | 4.2418
2022-07-29 06:00 | 4.6522 | 5.0215 | 5.0334 | 5.048 | 5.065 | 3.2389 | 3.8433 | 3.8526 | 3.8653 | 3.2389 | 4.5818 | 5.1081 | 5.1165 | 5.1276 | 5.3928
2022-07-29 07:00 | 5.2395 | 5.6614 | 5.678 | 5.6983 | 5.722 | 3.4104 | 4.0525 | 4.0654 | 4.0831 | 3.4104 | 5.3347 | 5.9512 | 5.9628 | 5.9783 | 6.29
2022-07-29 08:00 | 5.0489 | 5.4701 | 5.4935 | 5.5221 | 5.5555 | 3.2483 | 3.8706 | 3.8889 | 3.9138 | 3.2483 | 4.2868 | 4.7962 | 4.8126 | 4.8344 | 5.0961
2022-07-29 09:00 | 4.1535 | 4.5223 | 4.553 | 4.5905 | 4.6343 | 2.553 | 3.0597 | 3.0836 | 3.1163 | 2.553 | 2.5721 | 2.9008 | 2.9223 | 2.9508 | 3.1264
2022-07-29 10:00 | 3.5628 | 3.8987 | 3.935 | 3.9793 | 4.0311 | 1.7955 | 2.1727 | 2.201 | 2.2396 | 1.7955 | 1.1622 | 1.3418 | 1.3672 | 1.401 | 1.5052
2022-07-29 11:00 | 2.9341 | 3.2276 | 3.266 | 3.3131 | 3.3681 | 1.6004 | 1.9454 | 1.9754 | 2.0164 | 1.6004 | 0.62873 | 0.75206 | 0.77902 | 0.81485 | 0.89225
2022-07-29 12:00 | 2.7626 | 3.0423 | 3.0802 | 3.1267 | 3.1808 | 1.3337 | 1.6295 | 1.6591 | 1.6995 | 1.3337 | 1.0288 | 1.1959 | 1.2225 | 1.2578 | 1.3566
2022-07-29 13:00 | 2.5721 | 2.8326 | 2.868 | 2.9113 | 2.9619 | 1.1857 | 1.4511 | 1.4787 | 1.5164 | 1.1857 | 0.85737 | 1.0018 | 1.0266 | 1.0596 | 1.1461
2022-07-29 14:00 | 2.4578 | 2.7044 | 2.737 | 2.777 | 2.8235 | 1.448 | 1.757 | 1.7825 | 1.8172 | 1.448 | 0.81926 | 0.95567 | 0.97854 | 1.0089 | 1.0903
2022-07-29 15:00 | 3.258 | 3.5605 | 3.5913 | 3.629 | 3.673 | 1.9434 | 2.3396 | 2.3636 | 2.3964 | 1.9434 | 2.0767 | 2.3505 | 2.3721 | 2.4008 | 2.5492
2022-07-29 16:00 | 4.0357 | 4.3952 | 4.4255 | 4.4627 | 4.506 | 2.49 | 2.9848 | 3.0085 | 3.0408 | 2.49 | 2.9809 | 3.3547 | 3.3759 | 3.4042 | 3.6019
2022-07-29 17:00 | 4.6679 | 5.0779 | 5.1101 | 5.1494 | 5.1954 | 3.1627 | 3.7821 | 3.8071 | 3.8414 | 3.1627 | 4.8012 | 5.38 | 5.4026 | 5.4325 | 5.7323
2022-07-29 18:00 | 4.9537 | 5.3923 | 5.4282 | 5.4722 | 5.5235 | 3.6009 | 4.3051 | 4.3331 | 4.3714 | 3.6009 | 5.811 | 6.5074 | 6.5326 | 6.566 | 6.9255
2022-07-29 19:00 | 5.087 | 5.5453 | 5.5862 | 5.6363 | 5.6947 | 3.5057 | 4.1996 | 4.2315 | 4.2751 | 3.5057 | 5.7539 | 6.4508 | 6.4794 | 6.5175 | 6.8794
2022-07-29 20:00 | 5.2013 | 5.6778 | 5.7237 | 5.7798 | 5.8452 | 3.62 | 4.3417 | 4.3775 | 4.4263 | 3.62 | 6.4779 | 7.2622 | 7.2943 | 7.337 | 7.7441
2022-07-29 21:00 | 5.1251 | 5.5976 | 5.6442 | 5.7014 | 5.768 | 3.4198 | 4.1064 | 4.1428 | 4.1926 | 3.4198 | 4.9727 | 5.5907 | 5.6234 | 5.6669 | 5.9922
2022-07-29 22:00 | 4.7436 | 5.1817 | 5.2254 | 5.2788 | 5.3411 | 3.277 | 3.9334 | 3.9675 | 4.0139 | 3.277 | 4.344 | 4.8878 | 4.9184 | 4.959 | 5.2464
2022-07-29 23:00 | 4.2487 | 4.6416 | 4.6809 | 4.7291 | 4.7852 | 2.8542 | 3.4277 | 3.4584 | 3.5003 | 2.8542 | 3.5819 | 4.0349 | 4.0625 | 4.0991 | 4.3398
2022-07-30 | 3.8105 | 4.1613 | 4.1959 | 4.2381 | 4.2873 | 2.4959 | 2.9976 | 3.0245 | 3.0613 | 2.4959 | 3.3151 | 3.7318 | 3.756 | 3.7881 | 4.0088
2022-07-30 01:00 | 3.5247 | 3.8447 | 3.8744 | 3.9106 | 3.9529 | 2.1529 | 2.5855 | 2.6086 | 2.6401 | 2.1529 | 2.896 | 3.2593 | 3.28 | 3.3076 | 3.4998
2022-07-30 02:00 | 3.4104 | 3.7098 | 3.7333 | 3.762 | 3.7955 | 2.0767 | 2.4867 | 2.505 | 2.53 | 2.0767 | 2.9913 | 3.3566 | 3.373 | 3.3948 | 3.5854
2022-07-30 03:00 | 3.4562 | 3.7472 | 3.7646 | 3.7859 | 3.8108 | 2.0577 | 2.4556 | 2.4692 | 2.4877 | 2.0577 | 2.8388 | 3.1788 | 3.191 | 3.2072 | 3.3827
2022-07-30 04:00 | 3.5819 | 3.8722 | 3.8844 | 3.8994 | 3.9169 | 2.0577 | 2.4483 | 2.4578 | 2.4709 | 2.0577 | 2.9531 | 3.2987 | 3.3073 | 3.3187 | 3.4947
2022-07-30 05:00 | 3.8296 | 4.1343 | 4.1445 | 4.1571 | 4.1717 | 2.3722 | 2.817 | 2.8249 | 2.8358 | 2.3722 | 3.9629 | 4.418 | 4.4252 | 4.4347 | 4.664
2022-07-30 06:00 | 4.1344 | 4.4651 | 4.4771 | 4.4917 | 4.5087 | 2.8007 | 3.3256 | 3.3349 | 3.3476 | 2.8007 | 4.1344 | 4.6109 | 4.6193 | 4.6304 | 4.871
2022-07-30 07:00 | 4.6679 | 5.0474 | 5.0639 | 5.0842 | 5.1079 | 3.0675 | 3.6473 | 3.6603 | 3.6779 | 3.0675 | 4.8965 | 5.4643 | 5.4759 | 5.4913 | 5.7789
2022-07-30 08:00 | 4.5536 | 4.9379 | 4.9613 | 4.9899 | 5.0233 | 3.0539 | 3.641 | 3.6592 | 3.6841 | 3.0539 | 4.3331 | 4.8476 | 4.864 | 4.8858 | 5.1501
2022-07-30 09:00 | 4.1725 | 4.5428 | 4.5734 | 4.611 | 4.6548 | 2.7432 | 3.2843 | 3.3082 | 3.3409 | 2.7432 | 4.1725 | 4.6793 | 4.7008 | 4.7293 | 4.9928
2022-07-30 10:00 | 3.4676 | 3.7963 | 3.8326 | 3.877 | 3.9288 | 2.199 | 2.6494 | 2.6777 | 2.7163 | 2.199 | 2.5149 | 2.845 | 2.8704 | 2.9042 | 3.0828
2022-07-30 11:00 | 2.7428 | 3.022 | 3.0605 | 3.1076 | 3.1626 | 1.7147 | 2.0804 | 2.1104 | 2.1514 | 1.7147 | 0.91452 | 1.0696 | 1.0966 | 1.1324 | 1.2255
2022-07-30 12:00 | 2.4768 | 2.7352 | 2.7732 | 2.8196 | 2.8738 | 1.3337 | 1.6295 | 1.6591 | 1.6995 | 1.3337 | 0.62873 | 0.75131 | 0.7779 | 0.81322 | 0.89003
2022-07-30 13:00 | 2.6864 | 2.9554 | 2.9908 | 3.0341 | 3.0847 | 1.467 | 1.7834 | 1.8111 | 1.8487 | 1.467 | 0.97168 | 1.1289 | 1.1537 | 1.1866 | 1.2795
2022-07-30 14:00 | 2.4006 | 2.643 | 2.6756 | 2.7156 | 2.7621 | 1.4273 | 1.7325 | 1.758 | 1.7927 | 1.4273 | 0.724 | 0.84981 | 0.87267 | 0.90306 | 0.97919
2022-07-30 15:00 | 2.9751 | 3.2566 | 3.2874 | 3.3251 | 3.3691 | 1.9719 | 2.3733 | 2.3973 | 2.4301 | 1.9719 | 1.5433 | 1.7577 | 1.7793 | 1.8079 | 1.9271
2022-07-30 16:00 | 3.9661 | 4.3204 | 4.3507 | 4.3879 | 4.4312 | 2.7054 | 3.2392 | 3.2629 | 3.2952 | 2.7054 | 3.1056 | 3.4932 | 3.5145 | 3.5427 | 3.7473
2022-07-30 17:00 | 4.9537 | 5.3849 | 5.4171 | 5.4565 | 5.5024 | 3.5628 | 4.2547 | 4.2798 | 4.3141 | 3.5628 | 4.8965 | 5.4859 | 5.5084 | 5.5384 | 5.8434
2022-07-30 18:00 | 5.2013 | 5.6584 | 5.6943 | 5.7383 | 5.7896 | 3.7152 | 4.4401 | 4.4682 | 4.5064 | 3.7152 | 5.0299 | 5.6393 | 5.6645 | 5.6979 | 6.0145
2022-07-30 19:00 | 5.3919 | 5.8728 | 5.9137 | 5.9638 | 6.0222 | 3.803 | 4.5508 | 4.5827 | 4.6263 | 3.803 | 5.5633 | 6.239 | 6.2677 | 6.3058 | 6.6572
2022-07-30 20:00 | 5.2013 | 5.6778 | 5.7237 | 5.7798 | 5.8452 | 3.8105 | 4.5668 | 4.6025 | 4.6514 | 3.8105 | 5.3728 | 6.0342 | 6.0663 | 6.109 | 6.4554
2022-07-30 21:00 | 5.2585 | 5.7408 | 5.7875 | 5.8447 | 5.9113 | 3.7152 | 4.4554 | 4.4918 | 4.5416 | 3.7152 | 5.6967 | 6.3953 | 6.428 | 6.4714 | 6.8366
2022-07-30 22:00 | 4.8203 | 5.2641 | 5.3077 | 5.3612 | 5.4235 | 3.4156 | 4.0971 | 4.1311 | 4.1776 | 3.4156 | 4.7441 | 5.3324 | 5.363 | 5.4036 | 5.713
2022-07-30 23:00 | 4.4011 | 4.8053 | 4.8447 | 4.8928 | 4.9489 | 2.9722 | 3.5672 | 3.5978 | 3.6397 | 2.9722 | 4.0963 | 4.6066 | 4.6341 | 4.6708 | 4.9397
2022-07-31 | 3.982 | 4.3456 | 4.3801 | 4.4223 | 4.4716 | 2.6438 | 3.1723 | 3.1992 | 3.236 | 2.6438 | 3.5057 | 3.9436 | 3.9677 | 3.9999 | 4.231
2022-07-31 01:00 | 3.741 | 4.0771 | 4.1067 | 4.143 | 4.1852 | 2.3848 | 2.8594 | 2.8825 | 2.9141 | 2.3848 | 3.258 | 3.6615 | 3.6823 | 3.7099 | 3.9219
2022-07-31 02:00 | 3.5247 | 3.8327 | 3.8561 | 3.8848 | 3.9183 | 2.1529 | 2.5767 | 2.595 | 2.62 | 2.1529 | 2.8579 | 3.2084 | 3.2248 | 3.2466 | 3.4298
2022-07-31 03:00 | 3.5438 | 3.8413 | 3.8587 | 3.88 | 3.9049 | 2.0577 | 2.4556 | 2.4692 | 2.4877 | 2.0577 | 3.0103 | 3.3694 | 3.3816 | 3.3978 | 3.5826
2022-07-31 04:00 | 3.5628 | 3.8517 | 3.864 | 3.879 | 3.8965 | 2.1392 | 2.5445 | 2.5541 | 2.5672 | 2.1392 | 3.0675 | 3.4257 | 3.4343 | 3.4457 | 3.628
2022-07-31 05:00 | 3.7534 | 4.0524 | 4.0627 | 4.0752 | 4.0898 | 2.3661 | 2.8097 | 2.8177 | 2.8286 | 2.3661 | 3.4104 | 3.804 | 3.8112 | 3.8207 | 4.0196
2022-07-31 06:00 | 3.9629 | 4.2809 | 4.2928 | 4.3075 | 4.3245 | 2.6828 | 3.1863 | 3.1957 | 3.2084 | 2.6828 | 3.8486 | 4.2933 | 4.3017 | 4.3128 | 4.5377
2022-07-31 07:00 | 4.2782 | 4.6287 | 4.6453 | 4.6656 | 4.6892 | 3.0103 | 3.5798 | 3.5927 | 3.6104 | 3.0103 | 4.3059 | 4.8079 | 4.8195 | 4.835 | 5.0901
2022-07-31 08:00 | 4.6488 | 5.0402 | 5.0636 | 5.0923 | 5.1257 | 3.258 | 3.8821 | 3.9004 | 3.9253 | 3.258 | 4.9918 | 5.5796 | 5.596 | 5.6178 | 5.9182
2022-07-31 09:00 | 4.8393 | 5.2592 | 5.2898 | 5.3274 | 5.3712 | 3.2008 | 3.8249 | 3.8489 | 3.8815 | 3.2008 | 5.9253 | 6.6271 | 6.6486 | 6.6772 | 7.037
2022-07-31 10:00 | 4.5917 | 5.004 | 5.0403 | 5.0847 | 5.1364 | 3.1056 | 3.7203 | 3.7486 | 3.7873 | 3.1056 | 4.6298 | 5.1952 | 5.2206 | 5.2543 | 5.5492
2022-07-31 11:00 | 4.363 | 4.7627 | 4.8012 | 4.8483 | 4.9032 | 2.8769 | 3.4534 | 3.4834 | 3.5244 | 2.8769 | 3.7724 | 4.2455 | 4.2724 | 4.3083 | 4.5585
2022-07-31 12:00 | 4.4011 | 4.8026 | 4.8406 | 4.887 | 4.9412 | 2.7817 | 3.3401 | 3.3697 | 3.4101 | 2.7817 | 3.4676 | 3.906 | 3.9326 | 3.9679 | 4.2008
2022-07-31 13:00 | 4.5155 | 4.9204 | 4.9558 | 4.9992 | 5.0497 | 2.8579 | 3.4265 | 3.4541 | 3.4918 | 2.8579 | 3.5438 | 3.9871 | 4.0119 | 4.0449 | 4.2791
2022-07-31 14:00 | 4.6298 | 5.0378 | 5.0705 | 5.1104 | 5.157 | 3.0292 | 3.625 | 3.6505 | 3.6852 | 3.0292 | 4.2297 | 4.7455 | 4.7684 | 4.7988 | 5.0676
2022-07-31 15:00 | 4.8203 | 5.239 | 5.2698 | 5.3075 | 5.3514 | 3.258 | 3.8926 | 3.9167 | 3.9495 | 3.258 | 5.0299 | 5.6322 | 5.6538 | 5.6825 | 5.9933
2022-07-31 16:00 | 5.1823 | 5.627 | 5.6574 | 5.6945 | 5.7379 | 3.6009 | 4.2972 | 4.3208 | 4.3532 | 3.6009 | 5.1442 | 5.7586 | 5.7799 | 5.8082 | 6.1248
2022-07-31 17:00 | 5.6396 | 6.1218 | 6.154 | 6.1934 | 6.2393 | 3.9439 | 4.7049 | 4.73 | 4.7642 | 3.9439 | 5.4109 | 6.0575 | 6.0801 | 6.11 | 6.4433
2022-07-31 18:00 | 5.6777 | 6.1701 | 6.206 | 6.25 | 6.3013 | 4.0201 | 4.8003 | 4.8283 | 4.8665 | 4.0201 | 5.3157 | 5.9569 | 5.9821 | 6.0155 | 6.3477
2022-07-31 19:00 | 5.5443 | 6.0366 | 6.0775 | 6.1276 | 6.186 | 3.8296 | 4.5823 | 4.6142 | 4.6577 | 3.8296 | 5.9063 | 6.6201 | 6.6488 | 6.6869 | 7.0571
2022-07-31 20:00 | 5.3347 | 5.8211 | 5.8669 | 5.9231 | 5.9885 | 3.8296 | 4.5893 | 4.6251 | 4.6739 | 3.8296 | 5.8491 | 6.5635 | 6.5956 | 6.6383 | 7.0109
2022-07-31 21:00 | 5.0489 | 5.5157 | 5.5624 | 5.6195 | 5.6861 | 3.5057 | 4.2078 | 4.2443 | 4.294 | 3.5057 | 4.4964 | 5.0614 | 5.0941 | 5.1376 | 5.4367
2022-07-31 22:00 | 4.2468 | 4.6479 | 4.6916 | 4.745 | 4.8073 | 2.9717 | 3.5727 | 3.6068 | 3.6532 | 2.9717 | 3.982 | 4.4855 | 4.5161 | 4.5568 | 4.8242
2022-07-31 23:00 | 3.7724 | 4.1299 | 4.1692 | 4.2173 | 4.2735 | 2.4768 | 2.9819 | 3.0126 | 3.0545 | 2.4768 | 2.9531 | 3.3363 | 3.3638 | 3.4004 | 3.6066

## Daily Load - Winter
| Anthony Rolfe | [9 empty] | Nona | [9 empty] | Hamer
| Average Winter Day Load (MW/MVA) |  |  |  |  | Peak Winter Day (MW/MVA) |  |  |  |  | Average Winter Day Load (MW/MVA) |  |  |  |  | Peak Winter Day (MW/MVA) |  |  |  |  | Average Winter Day Load (MW/MVA) |  |  |  |  | Peak Winter Day (MW/MVA)
Time | 2021 | 2026 | 2027 | 2028 | 2029 | 2021 | 2026 | 2027 | 2028 | 2029 | 2021 | 2026 | 2027 | 2028 | 2029 | 2022 | 2026 | 2027 | 2028 | 2029 | 2021 | 2026 | 2027 | 2028 | 2029 | 2021 | 2026 | 2027 | 2028 | 2029
0:00 | 2.5926 | 2.9279 | 2.9624 | 3.0046 | 3.0539 | 3.6009 | 3.9362 | 3.9707 | 4.0129 | 4.0622 | 1.769 | 2.213 | 2.24 | 2.2767 | 2.3225 | 2.1776 | 2.6216 | 2.6485 | 2.6853 | 2.7311 | 2.4306 | 2.8133 | 2.8375 | 2.8696 | 3.0735 | 3.0103 | 3.3931 | 3.4173 | 3.4494 | 3.6533
1:00 | 2.411 | 2.7098 | 2.7394 | 2.7757 | 2.8179 | 3.2389 | 3.5377 | 3.5673 | 3.6036 | 3.6458 | 1.5886 | 1.9831 | 2.0062 | 2.0378 | 2.0771 | 1.9434 | 2.3379 | 2.361 | 2.3926 | 2.4319 | 2.1609 | 2.5496 | 2.5704 | 2.5979 | 2.8027 | 3.1246 | 3.5133 | 3.5341 | 3.5616 | 3.7664
2:00 | 2.3294 | 2.6076 | 2.6311 | 2.6598 | 2.6932 | 3.1246 | 3.4028 | 3.4263 | 3.455 | 3.4884 | 1.4852 | 1.8427 | 1.861 | 1.886 | 1.9171 | 1.7877 | 2.1453 | 2.1636 | 2.1885 | 2.2197 | 2.0667 | 2.3748 | 2.3912 | 2.4131 | 2.5753 | 2.4768 | 2.7849 | 2.8013 | 2.8232 | 2.9854
3:00 | 2.3199 | 2.5778 | 2.5952 | 2.6165 | 2.6413 | 3.0103 | 3.2682 | 3.2856 | 3.3069 | 3.3317 | 1.4657 | 1.8105 | 1.8241 | 1.8426 | 1.8658 | 1.7647 | 2.1095 | 2.123 | 2.1416 | 2.1647 | 2.0573 | 2.3655 | 2.3777 | 2.3939 | 2.5536 | 2.553 | 2.8612 | 2.8734 | 2.8896 | 3.0494
4:00 | 2.393 | 2.6465 | 2.6587 | 2.6737 | 2.6912 | 3.0865 | 3.34 | 3.3522 | 3.3672 | 3.3847 | 1.5362 | 1.8923 | 1.9018 | 1.9149 | 1.9312 | 1.8672 | 2.2232 | 2.2328 | 2.2458 | 2.2621 | 2.1856 | 2.5036 | 2.5122 | 2.5236 | 2.686 | 2.7055 | 3.0235 | 3.0321 | 3.0435 | 3.2058
5:00 | 2.6485 | 2.9388 | 2.9491 | 2.9616 | 2.9762 | 3.6364 | 3.9267 | 3.937 | 3.9495 | 3.9641 | 1.7976 | 2.2188 | 2.2268 | 2.2377 | 2.2513 | 2.2423 | 2.6635 | 2.6715 | 2.6824 | 2.696 | 2.5983 | 2.9941 | 3.0012 | 3.0108 | 3.2107 | 3.4295 | 3.8252 | 3.8324 | 3.8419 | 4.0418
6:00 | 3.0716 | 3.4349 | 3.4468 | 3.4614 | 3.4785 | 4.5723 | 4.9356 | 4.9475 | 4.9621 | 4.9791 | 2.2261 | 2.8175 | 2.8268 | 2.8395 | 2.8554 | 3.1674 | 3.7588 | 3.7681 | 3.7808 | 3.7966 | 3.2898 | 3.8088 | 3.8171 | 3.8282 | 4.0898 | 4.5155 | 5.0344 | 5.0427 | 5.0539 | 5.3154
7:00 | 3.4294 | 3.8726 | 3.8892 | 3.9095 | 3.9331 | 5.5252 | 5.9685 | 5.985 | 6.0053 | 6.029 | 2.4409 | 3.1279 | 3.1408 | 3.1585 | 3.1805 | 3.6581 | 4.3451 | 4.358 | 4.3757 | 4.3977 | 3.6014 | 4.3048 | 4.3164 | 4.3319 | 4.6865 | 6.1159 | 6.8193 | 6.8309 | 6.8463 | 7.201
8:00 | 3.3966 | 3.8545 | 3.8779 | 3.9066 | 3.94 | 5.5443 | 6.0023 | 6.0257 | 6.0543 | 6.0877 | 2.3979 | 3.0635 | 3.0818 | 3.1067 | 3.1378 | 3.4866 | 4.1522 | 4.1705 | 4.1954 | 4.2264 | 3.3571 | 3.9437 | 3.9601 | 3.9819 | 4.2817 | 4.9805 | 5.567 | 5.5834 | 5.6052 | 5.9051
9:00 | 3.1714 | 3.6422 | 3.6729 | 3.7104 | 3.7542 | 5.5252 | 5.9961 | 6.0267 | 6.0643 | 6.1081 | 2.0859 | 2.6754 | 2.6994 | 2.732 | 2.7728 | 3.0103 | 3.5999 | 3.6238 | 3.6565 | 3.6972 | 2.5816 | 3.0671 | 3.0886 | 3.1172 | 3.3703 | 3.982 | 4.4675 | 4.489 | 4.5176 | 4.7706
10:00 | 2.8564 | 3.3311 | 3.3673 | 3.4117 | 3.4635 | 5.43 | 5.9046 | 5.9409 | 5.9853 | 6.0371 | 1.8143 | 2.3773 | 2.4055 | 2.4442 | 2.4923 | 2.8199 | 3.3829 | 3.4112 | 3.4498 | 3.4979 | 2.0348 | 2.5176 | 2.543 | 2.5767 | 2.8308 | 3.8867 | 4.3694 | 4.3948 | 4.4286 | 4.6826
11:00 | 2.6709 | 3.1287 | 3.1672 | 3.2143 | 3.2692 | 5.1442 | 5.602 | 5.6404 | 5.6875 | 5.7425 | 1.664 | 2.1679 | 2.1979 | 2.2389 | 2.29 | 2.4768 | 2.9807 | 3.0108 | 3.0517 | 3.1028 | 1.7352 | 2.0811 | 2.1081 | 2.1439 | 2.3313 | 2.6293 | 2.9751 | 3.0021 | 3.0379 | 3.2253
12:00 | 2.6007 | 3.0432 | 3.0812 | 3.1276 | 3.1818 | 4.9537 | 5.3962 | 5.4342 | 5.4806 | 5.5348 | 1.6162 | 2.1643 | 2.1939 | 2.2343 | 2.2847 | 2.7245 | 3.2726 | 3.3022 | 3.3426 | 3.393 | 1.6984 | 2.1198 | 2.1464 | 2.1817 | 2.4062 | 3.3151 | 3.7366 | 3.7632 | 3.7985 | 4.023
13:00 | 2.5611 | 2.9874 | 3.0228 | 3.0661 | 3.1166 | 4.8012 | 5.2275 | 5.2629 | 5.3062 | 5.3567 | 1.6113 | 2.1764 | 2.2041 | 2.2418 | 2.2888 | 2.8388 | 3.404 | 3.4316 | 3.4693 | 3.5163 | 1.717 | 2.1668 | 2.1916 | 2.2245 | 2.4619 | 3.6009 | 4.0507 | 4.0755 | 4.1084 | 4.3458
14:00 | 2.6425 | 3.0605 | 3.0931 | 3.133 | 3.1796 | 4.7631 | 5.1811 | 5.2138 | 5.2537 | 5.3003 | 1.6824 | 2.292 | 2.3175 | 2.3522 | 2.3956 | 3.1056 | 3.7152 | 3.7406 | 3.7754 | 3.8187 | 1.8362 | 2.3966 | 2.4195 | 2.4498 | 2.7407 | 4.6298 | 5.1901 | 5.213 | 5.2434 | 5.5342
15:00 | 2.8512 | 3.2613 | 3.2921 | 3.3298 | 3.3738 | 4.706 | 5.1161 | 5.1469 | 5.1846 | 5.2286 | 1.9155 | 2.4949 | 2.5189 | 2.5517 | 2.5926 | 2.9531 | 3.5325 | 3.5565 | 3.5893 | 3.6303 | 2.2964 | 2.7779 | 2.7995 | 2.8282 | 3.0793 | 3.9439 | 4.4254 | 4.447 | 4.4756 | 4.7267
16:00 | 3.2734 | 3.7309 | 3.7613 | 3.7984 | 3.8418 | 5.3549 | 5.8124 | 5.8428 | 5.88 | 5.9233 | 2.353 | 3.0665 | 3.0901 | 3.1225 | 3.1628 | 3.6962 | 4.4097 | 4.4334 | 4.4657 | 4.506 | 3.2364 | 3.9166 | 3.9379 | 3.9661 | 4.3152 | 5.7348 | 6.415 | 6.4362 | 6.4645 | 6.8136
17:00 | 3.7794 | 4.3169 | 4.349 | 4.3884 | 4.4343 | 6.3826 | 6.9201 | 6.9523 | 6.9916 | 7.0376 | 2.915 | 3.7796 | 3.8047 | 3.839 | 3.8817 | 4.5155 | 5.3801 | 5.4052 | 5.4395 | 5.4822 | 4.2494 | 5.0444 | 5.0669 | 5.0969 | 5.5034 | 6.7446 | 7.5396 | 7.5621 | 7.5921 | 7.9987
18:00 | 3.9645 | 4.5348 | 4.5708 | 4.6147 | 4.666 | 6.7256 | 7.2959 | 7.3318 | 7.3758 | 7.4271 | 3.094 | 3.9951 | 4.0231 | 4.0614 | 4.1091 | 4.6869 | 5.588 | 5.6161 | 5.6543 | 5.702 | 4.5626 | 5.4625 | 5.4876 | 5.5211 | 5.9811 | 7.6401 | 8.5399 | 8.5651 | 8.5985 | 9.0585
19:00 | 3.9148 | 4.4906 | 4.5316 | 4.5816 | 4.64 | 6.6684 | 7.2442 | 7.2852 | 7.3352 | 7.3936 | 3.0672 | 3.9615 | 3.9934 | 4.037 | 4.0913 | 4.6107 | 5.5051 | 5.537 | 5.5806 | 5.6349 | 4.6314 | 5.4703 | 5.499 | 5.5371 | 5.9691 | 7.0304 | 7.8693 | 7.898 | 7.9361 | 8.3681
20:00 | 3.7846 | 4.3489 | 4.3948 | 4.4509 | 4.5163 | 6.3826 | 6.9469 | 6.9927 | 7.0489 | 7.1143 | 2.9609 | 3.8657 | 3.9015 | 3.9503 | 4.0112 | 4.6298 | 5.5346 | 5.5704 | 5.6192 | 5.6801 | 4.5423 | 5.4453 | 5.4775 | 5.5202 | 5.986 | 7.5448 | 8.4478 | 8.4799 | 8.5226 | 8.9884
21:00 | 3.5852 | 4.1152 | 4.1619 | 4.2191 | 4.2857 | 5.9009 | 6.431 | 6.4777 | 6.5348 | 6.6015 | 2.7813 | 3.5802 | 3.6166 | 3.6663 | 3.7283 | 4.0391 | 4.8381 | 4.8745 | 4.9242 | 4.9862 | 4.0552 | 4.7834 | 4.8161 | 4.8596 | 5.2394 | 5.9635 | 6.6917 | 6.7244 | 6.7678 | 7.1477
22:00 | 3.2531 | 3.7209 | 3.7646 | 3.818 | 3.8803 | 5.1442 | 5.6121 | 5.6557 | 5.7091 | 5.7714 | 2.4606 | 3.1688 | 3.2029 | 3.2494 | 3.3073 | 3.5628 | 4.271 | 4.3051 | 4.3516 | 4.4095 | 3.4603 | 4.0507 | 4.0813 | 4.1219 | 4.4324 | 4.7631 | 5.3536 | 5.3842 | 5.4248 | 5.7353
23:00 | 2.8978 | 3.3048 | 3.3441 | 3.3923 | 3.4484 | 4.4392 | 4.8463 | 4.8856 | 4.9337 | 4.9899 | 2.0791 | 2.6376 | 2.6683 | 2.7102 | 2.7625 | 2.7717 | 3.3302 | 3.3609 | 3.4028 | 3.455 | 2.8964 | 3.3749 | 3.4024 | 3.4391 | 3.6923 | 3.8105 | 4.289 | 4.3166 | 4.3532 | 4.6064

## Daily Load - Summer
| Anthony Rolfe | [9 empty] | Nona | [9 empty] | Hamer
| Average Summer Day Load (MW/MVA) |  |  |  |  | Peak Summer Day (MW/MVA) |  |  |  |  | Average Summer Day Load (MW/MVA) |  |  |  |  | Peak Summer Day (MW/MVA) |  |  |  |  | Average Summer Day Load (MW/MVA) |  |  |  |  | Peak Summer Day (MW/MVA)
Time | 2021 | 2026 | 2027 | 2028 | 2029 | 2021 | 2026 | 2027 | 2028 | 2029 | 2021 | 2026 | 2027 | 2028 | 2029 | 2021 | 2026 | 2027 | 2028 | 2029 | 2021 | 2026 | 2027 | 2028 | 2029 | 2021 | 2026 | 2027 | 2028 | 2029
0:00 | 1.9362 | 2.3032 | 2.3377 | 2.38 | 2.4292 | 2.3625 | 2.7296 | 2.7641 | 2.8063 | 2.8556 | 1.347 | 1.8622 | 1.8891 | 1.9259 | 1.9717 | 1.9434 | 2.4586 | 2.4855 | 2.5222 | 2.568 | 1.6886 | 2.094 | 2.1181 | 2.1503 | 2.3654 | 2.0196 | 2.425 | 2.4491 | 2.4813 | 2.6964
1:00 | 1.8089 | 2.1323 | 2.1619 | 2.1981 | 2.2404 | 2.0935 | 2.4169 | 2.4466 | 2.4828 | 2.5251 | 1.2086 | 1.6449 | 1.668 | 1.6996 | 1.7389 | 1.6437 | 2.0801 | 2.1032 | 2.1347 | 2.174 | 1.4761 | 1.8444 | 1.8651 | 1.8927 | 2.0874 | 1.8481 | 2.2164 | 2.2371 | 2.2647 | 2.4593
2:00 | 1.7389 | 2.0432 | 2.0667 | 2.0954 | 2.1289 | 2.0386 | 2.343 | 2.3664 | 2.3951 | 2.4286 | 1.1253 | 1.5075 | 1.5258 | 1.5508 | 1.5819 | 1.4547 | 1.8369 | 1.8552 | 1.8802 | 1.9113 | 1.417 | 1.7835 | 1.7999 | 1.8218 | 2.0129 | 1.8862 | 2.2527 | 2.2691 | 2.2909 | 2.482
3:00 | 1.7045 | 1.9826 | 2 | 2.0213 | 2.0461 | 1.9243 | 2.2023 | 2.2198 | 2.2411 | 2.2659 | 1.0899 | 1.4574 | 1.471 | 1.4895 | 1.5127 | 1.4289 | 1.7964 | 1.81 | 1.8286 | 1.8517 | 1.3894 | 1.734 | 1.7461 | 1.7624 | 1.9401 | 1.81 | 2.1546 | 2.1668 | 2.183 | 2.3607
4:00 | 1.7163 | 1.9818 | 1.994 | 2.009 | 2.0265 | 1.9048 | 2.1703 | 2.1826 | 2.1976 | 2.2151 | 1.0902 | 1.4275 | 1.4371 | 1.4502 | 1.4664 | 1.3337 | 1.671 | 1.6806 | 1.6936 | 1.7099 | 1.3841 | 1.7047 | 1.7133 | 1.7247 | 1.8884 | 1.7147 | 2.0353 | 2.0439 | 2.0553 | 2.219
5:00 | 1.7832 | 2.0545 | 2.0647 | 2.0772 | 2.0918 | 1.9815 | 2.2527 | 2.2629 | 2.2755 | 2.2901 | 1.1805 | 1.5286 | 1.5366 | 1.5475 | 1.5611 | 1.3908 | 1.739 | 1.747 | 1.7579 | 1.7715 | 1.4688 | 1.8777 | 1.8848 | 1.8944 | 2.1007 | 2.2291 | 2.638 | 2.6452 | 2.6547 | 2.8611
6:00 | 1.876 | 2.1723 | 2.1843 | 2.1989 | 2.2159 | 2.1529 | 2.4492 | 2.4612 | 2.4758 | 2.4928 | 1.3434 | 1.7534 | 1.7627 | 1.7754 | 1.7913 | 1.6385 | 2.0485 | 2.0578 | 2.0705 | 2.0864 | 1.6118 | 2.0601 | 2.0685 | 2.0796 | 2.3062 | 2.4387 | 2.887 | 2.8954 | 2.9065 | 3.1331
7:00 | 2.0668 | 2.3722 | 2.3888 | 2.4091 | 2.4328 | 2.1529 | 2.4583 | 2.4749 | 2.4952 | 2.5189 | 1.4755 | 1.9469 | 1.9599 | 1.9775 | 1.9995 | 1.8672 | 2.3386 | 2.3515 | 2.3692 | 2.3912 | 1.7003 | 2.2359 | 2.2476 | 2.263 | 2.5348 | 2.896 | 3.4317 | 3.4433 | 3.4587 | 3.7305
8:00 | 2.0775 | 2.4156 | 2.439 | 2.4676 | 2.501 | 2.3054 | 2.6434 | 2.6668 | 2.6955 | 2.7289 | 1.4518 | 1.895 | 1.9133 | 1.9382 | 1.9693 | 1.7091 | 2.1523 | 2.1706 | 2.1955 | 2.2266 | 1.5312 | 2.1235 | 2.1399 | 2.1617 | 2.4644 | 3.1627 | 3.7551 | 3.7715 | 3.7933 | 4.096
9:00 | 2.0652 | 2.4151 | 2.4457 | 2.4833 | 2.5271 | 2.2863 | 2.6362 | 2.6669 | 2.7044 | 2.7482 | 1.3285 | 1.7442 | 1.7681 | 1.8008 | 1.8415 | 1.5511 | 1.9668 | 1.9907 | 2.0234 | 2.0641 | 1.3373 | 1.8184 | 1.8398 | 1.8684 | 2.1192 | 2.4768 | 2.9579 | 2.9794 | 3.0079 | 3.2587
10:00 | 1.9881 | 2.361 | 2.3972 | 2.4416 | 2.4934 | 2.3816 | 2.7545 | 2.7908 | 2.8351 | 2.8869 | 1.2066 | 1.5917 | 1.62 | 1.6586 | 1.7068 | 1.3906 | 1.7757 | 1.804 | 1.8426 | 1.8907 | 1.3616 | 1.8638 | 1.8892 | 1.923 | 2.1867 | 2.553 | 3.0553 | 3.0807 | 3.1145 | 3.3782
11:00 | 1.9396 | 2.2928 | 2.3312 | 2.3783 | 2.4333 | 2.191 | 2.5442 | 2.5826 | 2.6297 | 2.6847 | 1.123 | 1.5296 | 1.5596 | 1.6006 | 1.6517 | 1.467 | 1.8736 | 1.9037 | 1.9447 | 1.9958 | 1.4163 | 1.7699 | 1.7968 | 1.8327 | 2.0238 | 1.6957 | 2.0492 | 2.0762 | 2.112 | 2.3032
12:00 | 1.9848 | 2.4069 | 2.4448 | 2.4913 | 2.5455 | 2.7436 | 3.1657 | 3.2036 | 3.2501 | 3.3042 | 1.1317 | 1.4997 | 1.5293 | 1.5697 | 1.6201 | 1.3094 | 1.6774 | 1.707 | 1.7474 | 1.7978 | 1.4745 | 1.7295 | 1.756 | 1.7914 | 1.9336 | 1.1432 | 1.3982 | 1.4247 | 1.4601 | 1.6023
13:00 | 1.9889 | 2.4302 | 2.4656 | 2.5089 | 2.5595 | 2.9341 | 3.3754 | 3.4108 | 3.4541 | 3.5046 | 1.1447 | 1.652 | 1.6796 | 1.7173 | 1.7643 | 1.9053 | 2.4126 | 2.4402 | 2.4779 | 2.5249 | 1.4644 | 1.763 | 1.7878 | 1.8208 | 1.9835 | 1.4099 | 1.7086 | 1.7334 | 1.7663 | 1.9291
14:00 | 2.0519 | 2.495 | 2.5276 | 2.5676 | 2.6141 | 2.9913 | 3.4344 | 3.467 | 3.5069 | 3.5535 | 1.2082 | 1.7192 | 1.7447 | 1.7794 | 1.8228 | 1.937 | 2.4481 | 2.4735 | 2.5083 | 2.5516 | 1.4747 | 1.7999 | 1.8228 | 1.8532 | 2.0279 | 1.5814 | 1.9066 | 1.9295 | 1.9598 | 2.1345
15:00 | 2.1592 | 2.6036 | 2.6344 | 2.6721 | 2.716 | 3.0294 | 3.4737 | 3.5045 | 3.5422 | 3.5862 | 1.3068 | 1.9366 | 1.9606 | 1.9934 | 2.0343 | 2.4428 | 3.0725 | 3.0965 | 3.1293 | 3.1702 | 1.4947 | 1.8646 | 1.8862 | 1.9149 | 2.1108 | 1.8481 | 2.218 | 2.2396 | 2.2683 | 2.4642
16:00 | 2.2367 | 2.6657 | 2.6961 | 2.7332 | 2.7766 | 2.915 | 3.344 | 3.3744 | 3.4116 | 3.4549 | 1.4751 | 2.1307 | 2.1544 | 2.1867 | 2.227 | 2.553 | 3.2086 | 3.2323 | 3.2646 | 3.3049 | 1.5699 | 2.0302 | 2.0515 | 2.0798 | 2.3203 | 2.3625 | 2.8229 | 2.8442 | 2.8724 | 3.1129
17:00 | 2.3742 | 2.8212 | 2.8534 | 2.8928 | 2.9387 | 3.0294 | 3.4764 | 3.5086 | 3.548 | 3.5939 | 1.7533 | 2.4434 | 2.4685 | 2.5028 | 2.5455 | 2.6864 | 3.3765 | 3.4016 | 3.4359 | 3.4786 | 2.0792 | 2.8322 | 2.8547 | 2.8846 | 3.2705 | 4.001 | 4.754 | 4.7765 | 4.8065 | 5.1923
18:00 | 2.5329 | 3.0477 | 3.0837 | 3.1276 | 3.1789 | 3.5057 | 4.0205 | 4.0564 | 4.1004 | 4.1517 | 2 | 2.8223 | 2.8503 | 2.8886 | 2.9363 | 3.2149 | 4.0372 | 4.0652 | 4.1035 | 4.1512 | 2.55 | 3.4127 | 3.4379 | 3.4714 | 3.913 | 4.5917 | 5.4544 | 5.4796 | 5.513 | 5.9547
19:00 | 2.5926 | 3.1727 | 3.2136 | 3.2637 | 3.3221 | 3.9439 | 4.524 | 4.5649 | 4.615 | 4.6734 | 2.0709 | 2.9745 | 3.0065 | 3.05 | 3.1044 | 3.5247 | 4.4283 | 4.4602 | 4.5038 | 4.5582 | 2.7059 | 3.5384 | 3.5671 | 3.6052 | 4.034 | 4.3821 | 5.2146 | 5.2433 | 5.2814 | 5.7103
20:00 | 2.5845 | 3.1622 | 3.208 | 3.2642 | 3.3296 | 3.8486 | 4.4263 | 4.4722 | 4.5283 | 4.5937 | 2.0556 | 2.9708 | 3.0066 | 3.0554 | 3.1163 | 3.5438 | 4.459 | 4.4948 | 4.5436 | 4.6045 | 2.685 | 3.5986 | 3.6308 | 3.6735 | 4.1445 | 4.8012 | 5.7148 | 5.747 | 5.7897 | 6.2607
21:00 | 2.4849 | 3.0449 | 3.0916 | 3.1488 | 3.2154 | 3.6962 | 4.2562 | 4.3029 | 4.36 | 4.4267 | 1.9628 | 2.8198 | 2.8562 | 2.9059 | 2.9679 | 3.2961 | 4.1531 | 4.1895 | 4.2392 | 4.3012 | 2.5781 | 3.3107 | 3.3434 | 3.3869 | 3.7689 | 3.7724 | 4.505 | 4.5377 | 4.5812 | 4.9632
22:00 | 2.3248 | 2.8531 | 2.8968 | 2.9502 | 3.0125 | 3.4932 | 4.0215 | 4.0652 | 4.1186 | 4.1809 | 1.7799 | 2.5536 | 2.5877 | 2.6341 | 2.6921 | 2.967 | 3.7407 | 3.7748 | 3.8213 | 3.8792 | 2.2895 | 2.9066 | 2.9372 | 2.9778 | 3.3014 | 3.1437 | 3.7608 | 3.7913 | 3.832 | 4.1556
23:00 | 2.1226 | 2.5936 | 2.633 | 2.6811 | 2.7373 | 3.1078 | 3.5788 | 3.6181 | 3.6663 | 3.7224 | 1.5427 | 2.2224 | 2.2531 | 2.295 | 2.3472 | 2.6008 | 3.2805 | 3.3112 | 3.3531 | 3.4053 | 1.9437 | 2.4671 | 2.4946 | 2.5313 | 2.8067 | 2.6483 | 3.1717 | 3.1993 | 3.2359 | 3.5113

## Feeder Loadings
Feeder | Summer |  | Winter |  | 2025 |  | 2026 |  | 2027 |  | 2028 |  | 2029 |  | 2030 |  | 2031 |  | 2032
| Firm Rating | Thermal Rating | Firm Rating | Thermal Rating | Summer | Winter | Summer | Winter | Summer | Winter | Summer | Winter | Summer | Winter | Summer | Winter | Summer | Winter | Summer | Winter
Nona | 4.4964 | 5.9825 | 4.4964 | 5.9825 | 3.5779 | 4.721 | 4.4602 | 5.6033 | 4.4966 | 5.6397 | 4.5463 | 5.6895 | 4.6083 | 5.7515 | 4.6936 | 5.8367 | 5.6171 | 6.7602 | 5.6914 | 6.8345
Hamer | 5.1442 | 6.897 | 5.6205 | 7.5067 | 5.6858 | 8.5247 | 5.716 | 8.5548 | 5.7487 | 8.5875 | 5.7922 | 8.631 | 6.2642 | 9.103 | 6.3335 | 9.1723 | 8.6573 | 11.4961 | 8.7091 | 11.5479
Anthony Rolfe | 4.9537 | 6.6684 | 5.43 | 7.24 | 4.4906 | 7.2723 | 4.5353 | 7.3169 | 4.582 | 7.3636 | 4.6391 | 7.4208 | 4.7057 | 7.4874 | 5.2134 | 7.9951 | 6.2016 | 8.9833 | 6.2637 | 9.0454
Above Firm
Above Thermal
Units: MVA/MW

## Methodology
Tabs | Description
Annual Load | Hourly historical demand of relevant feeders and their hourly forecasts. These forecasts preserve relative percentage of seasonal peak demand in any given hour across a year, and scale the peak demand itself based on addition of point loads as described in the business case
Daily Load | Average Summer / Winter Day load: Calculated by averaging the demand at the same hour throughtout the year. Peak Summer / Winter Day load: The daily load profile on the day when the peak summer/winter demand occurs.
Feeder Loadings | Forecast peak seasonal loadings of relevant feeders in winter and summer.